## Index
Mitigation Workpapers
SUG_RA_RAMP
CCC_RA_RAMP
CCC_RA_RAMP_Alt2
OH Hardening_RA_RAMP
SPRP_RA_RAMP
Pole Brushing
Fuel Management
Trim and Removal
Off Cycle Patrol
Veg Detail Inspection
OH Patrol
RIDI
Wood pole Intrusive Primary
OH Detail Inspection
FCP
EFD
Microgrid (Capital)
WiNGS-Planning
raw_WP_RA
Inflation_and_Discount
FCP Cost
Microgrid Assumptions
TrancheID
FeederSegment miles
SUG&CCC_Lifecycle_cost

## SUG_RA_RAMP
SUG - Risk & Cost Benefit | [27 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[28 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [27 empty] | 2026 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | ---
|  |  | Note: The feeder segments listed below have been selected for detailed scoping and feasibility engineering studies. The total mileage presented here exceeds SDG&E targets because some segments may not be feasible for selected mitigation due to permitting issues, difficult terrain, customer resistance, and other factors not accounted for in the current WiNGS-Planning model. | [5 empty] | Assumptions | Value | Units | Last Update | Comments | [14 empty] | 2027 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Capital Cost only in Year 0 | 2 | M$/mile | 2025-05-01 | Includes Primary, Secondary for BCR | [14 empty] | 2028 | 178.2671 | 279642.3002 | 275104.6185 | 98.38% | 4796481.6297 | 408902.243 | 11.7301 | 4905782.629 | 408902.243 | 11.9974 | 17574342.2771 | 561401.7283 | 31.3044
[9 empty] | Service Drop factor | 1.26% | % | 2025-05-01 | Factor to account for Service drop miles | [15 empty] | 178.2671 | 279642.3002 | 275104.6185 | 98.38% | 4796481.6297 | 408902.243 | 11.7301 | 4905782.629 | 408902.243 | 11.9974 | 17574342.2771 | 561401.7283 | 31.3044
[9 empty] | OH to UG conversion factor | 20% | % | 2025-05-01 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.003337 | M$/mile-year | 2025-05-01 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 55 | Years | 2025-05-01 | SB 884 end of the expected lifetime (defined as 55 years) of the infrastructure
[9 empty] | Mitigation Effectiveness Estimate (%) | 98.9% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.022 | M$/mile | 2025-05-01 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[7 empty] | OH miles | SUG miles | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | HFTD Tier | Feeder | Feeder Segment | Tranche ID HTM | Tranche ID Quintile | Total miles in scope | Units (OH Primary + Secondary miles + Service Drop) | SUG miles (Miles + OH to UG Conversion) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2028 | Tier-3 | 1022 | 1022-17F | Tier-3---4 | Tier-3---1 | 100% | 4.6079 | 5.5295 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 9696.2455 | 580.6799 | 28.3255 | 9087.2401 | 49.6617 | 169055.1894 | 10571.3663 | 15.9918 | 172224.4529 | 10571.3663 | 16.2916 | 619419.3976 | 14518.3598 | 42.6646 | 98.93%
2028 | Tier-3 | 1030 | 1030-18R | Tier-3---7 | Tier-3---1 | 100% | 3.5215 | 4.2258 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 6511.3858 | 357.8982 | 71.7688 | 6081.7188 | 37.7969 | 113526.7827 | 8076.171 | 14.057 | 115762.7693 | 8076.171 | 14.3339 | 415962.9268 | 11085.3197 | 37.5238 | 98.35%
2028 | Tier-3 | 1166 | 1166-18R | Tier-3---5 | Tier-3---1 | 100% | 7.6873 | 9.2248 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 9936.8492 | 641.3949 | 18.2938 | 9277.1606 | 80.9466 | 173250.1439 | 17602.9145 | 9.8421 | 176683.1629 | 17602.9145 | 10.0372 | 634789.7404 | 24099.2292 | 26.3407 | 98.3%
2028 | Tier-3 | 176 | 176-161R | Tier-3---5 | Tier-3---1 | 100% | 9.9016 | 11.8819 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 11315.3536 | 630.9643 | 127.4161 | 10556.9731 | 106.1648 | 197284.5305 | 22706.5089 | 8.6885 | 201231.1414 | 22706.5089 | 8.8623 | 722851.9011 | 31162.3963 | 23.1963 | 98.2%
2028 | Tier-2 | 211 | 211-312R | Tier-2---8 | Tier-2---5 | 100% | 18.3875 | 22.065 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 1754.4406 | 94.5554 | 223.7179 | 1436.1673 | 197.0171 | 30588.8797 | 42164.1431 | 0.72547 | 32245.1733 | 42164.1431 | 0.76475 | 112077.8693 | 57860.7152 | 1.937 | 96.96%
2028 | Tier-2 | 215 | 215-1531R | Tier-2---2 | Tier-2---1 | 100% | 8.5663 | 10.2795 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 12461.1332 | 752.4948 | 185.3802 | 11523.2582 | 92.9117 | 217261.3346 | 19662.7924 | 11.0494 | 222142.0351 | 19662.7924 | 11.2976 | 796047.0514 | 27027.7381 | 29.453 | 98.1%
2028 | Tier-2 | 215 | 215-1534R | Tier-2---1 | Tier-2---1 | 100% | 7.9364 | 9.5237 | 19489.7064 | 99% | 0.9737% | 0.02962% | 19188.6868 | 1190.9404 | 158.3793 | 17839.3672 | 86.1673 | 334557.0293 | 18218.6587 | 18.3634 | 341578.8873 | 18218.6587 | 18.7488 | 1225819.2981 | 25046.1451 | 48.9424 | 98.46%
2028 | Tier-3 | 215 | 215-38R | Tier-3---10 | Tier-3---1 | 100% | 6.5117 | 7.8141 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 5353.9653 | 333.2167 | 56.6974 | 4964.0512 | 69.6773 | 93347.0199 | 14930.2702 | 6.2522 | 95376.1325 | 14930.2702 | 6.3881 | 342024.1346 | 20484.6573 | 16.6966 | 98.51%
2028 | Tier-3 | 217 | 217-835R | Tier-3---5 | Tier-3---1 | 100% | 18.5484 | 22.2581 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 10437.126 | 610.3322 | 103.8217 | 9722.9721 | 197.0251 | 181972.5294 | 42503.1898 | 4.2814 | 185688.9857 | 42503.1898 | 4.3688 | 666748.622 | 58257.4132 | 11.4449 | 97.66%
2028 | Tier-2 | 351 | 351-819R | Tier-2---1 | Tier-2---1 | 100% | 10.6216 | 12.7459 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 23213.0626 | 2360.7628 | 143.9475 | 20708.3523 | 114.5088 | 404722.4974 | 24368.3834 | 16.6085 | 417757.0069 | 24368.3834 | 17.1434 | 1482906.0642 | 33468.1115 | 44.308 | 98.71%
2028 | Tier-3 | 351 | 351-871R | Tier-3---6 | Tier-3---1 | 100% | 4.1929 | 5.0315 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 9032.8126 | 447.3947 | 17.8978 | 8567.52 | 44.9474 | 157488.1578 | 9615.0411 | 16.3794 | 159909.5398 | 9615.0411 | 16.6312 | 577037.7128 | 13195.3279 | 43.7305 | 98.78%
2028 | Tier-3 | 357 | 357-2049F | Tier-3---8 | Tier-3---1 | 100% | 5.6917 | 6.83 | 16869.708 | 98.79% | 1.184% | 0.02933% | 16548.2683 | 1109.6369 | 166.686 | 15271.9454 | 61.9382 | 288521.0199 | 13068.0837 | 22.0783 | 295163.0028 | 13068.0837 | 22.5866 | 1057143.0371 | 17971.0861 | 58.8247 | 98.09%
2028 | Tier-3 | 358 | 358-682F | Tier-3---3 | Tier-3---1 | 100% | 10.5849 | 12.7019 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 37025.294 | 2182.3207 | 426.4067 | 34416.5666 | 114.3608 | 645540.3888 | 24288.6506 | 26.5779 | 659116.2029 | 24288.6506 | 27.1368 | 2365264.5048 | 33368.4661 | 70.8832 | 98.47%
2028 | Tier-2 | 452 | 452-38AE | Tier-2---4 | Tier-2---7 | 100% | 2.8002 | 3.3602 | 2823.7515 | 99.93% | 0% | 0.06613% | 2762.7249 | 244.9401 | 0.13586 | 2517.6489 | 30.1235 | 48168.4352 | 6423.1608 | 7.4992 | 49443.81 | 6423.1608 | 7.6977 | 176489.484 | 8819.1384 | 20.0121 | 97.84%
2028 | Tier-2 | 520 | 520-45 | Tier-2---8 | Tier-2---1 | 100% | 8.8332 | 10.5999 | 2044.6463 | 97.57% | 2.13% | 0.298% | 1998.2455 | 100.7319 | 34.6983 | 1862.8153 | 94.6495 | 34839.647 | 20255.3787 | 1.72 | 35544.4257 | 20255.3787 | 1.7548 | 127652.7105 | 27796.0752 | 4.5925 | 97.73%
2028 | Tier-3 | 79 | 79-679R | Tier-3---3 | Tier-3---1 | 100% | 6.1617 | 7.3941 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 18164.8209 | 1003.2156 | 164.9678 | 16996.6375 | 66.3969 | 316705.8053 | 14135.8821 | 22.4044 | 322785.0305 | 14135.8821 | 22.8344 | 1160412.2883 | 19413.3088 | 59.7741 | 98.46%
2028 | Tier-2 | 908 | 908-1172R | Tier-2---2 | Tier-2---1 | 100% | 10.3047 | 12.3657 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 15484.2716 | 1085.4362 | 216.7435 | 14182.0919 | 111.8583 | 269970.1098 | 23654.8601 | 11.4129 | 276746.6511 | 23654.8601 | 11.6994 | 989172.3726 | 32518.6971 | 30.4186 | 98.21%
2028 | Tier-3 | 908 | 908-2055F | Tier-3---2 | Tier-3---1 | 100% | 11.6844 | 14.0213 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 22266.7077 | 1555.3433 | 181.4004 | 20529.964 | 126.2326 | 388222.6886 | 26811.4358 | 14.4797 | 397260.7012 | 26811.4358 | 14.8168 | 1422450.6494 | 36834.0627 | 38.6178 | 98.68%
2028 | Tier-3 | 215 | CB 215 | Tier-3---20 | Tier-3---11 | 100% | 0.15036 | 0.18043 | 133.9133 | 99.89% | 0% | 0.1056% | 133.7339 | 7.1117 | 0.52699 | 126.0952 | 1.586 | 2331.6663 | 344.342 | 6.7714 | 2371.4178 | 344.342 | 6.8868 | 8543.2415 | 471.5306 | 18.1181 | 99.87%
2028 | Tier-2 | 236 | CB 236 | Tier-2---1 | Tier-2---1 | 100% | 6.4026 | 7.6831 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 12505.6832 | 749.616 | 270.4879 | 11485.5793 | 69.9834 | 218038.068 | 14705.7647 | 14.8267 | 223346.6873 | 14705.7647 | 15.1877 | 798893.008 | 20235.5245 | 39.4797 | 98.38%
2028 | Tier-2 | 351 | CB 351 | Tier-2---3 | Tier-2---1 | 100% | 6.5658 | 7.8789 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 14328.4977 | 1406.6405 | 44.724 | 12877.1332 | 70.3985 | 249819.056 | 15056.7555 | 16.5918 | 257371.9551 | 15056.7555 | 17.0935 | 915338.7705 | 20663.8912 | 44.2965 | 98.14%
2028 | Tier-2 | 971 | CB 971 | Tier-2---3 | Tier-2---1 | 100% | 5.1717 | 6.2061 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 11239.3326 | 635.1388 | 73.3211 | 10530.8726 | 55.6989 | 195959.0952 | 11864.2131 | 16.5168 | 199645.9201 | 11864.2131 | 16.8276 | 717995.4968 | 16292.3308 | 44.0695 | 98.1%
2028 | Tier-3 | TM1 | TM1-10R | Tier-3---12 | Tier-3---1 | 100% | 3.4327 | 4.1192 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 3745.9771 | 192.6295 | 14.1312 | 3539.2164 | 36.944 | 65311.5551 | 7874.2764 | 8.2943 | 66387.5375 | 7874.2764 | 8.4309 | 239301.9951 | 10812.2034 | 22.1326 | 99.03%

## CCC_RA_RAMP
CCC - Risk & Cost Benefit | [27 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[28 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [27 empty] | 2026 | 53.5892 | 13538.5148 | 3224.8802 | 23.82% | 61787.924 | 96619.247 | 0.6395 | 63902.1449 | 96619.247 | 0.66138 | 204008.0959 | 198805.1854 | 1.0262
|  |  | Note: The feeder segments listed below have been selected for detailed scoping and feasibility engineering studies. The total mileage presented here exceeds SDG&E targets because some segments may not be feasible for selected mitigation due to permitting issues, difficult terrain, customer resistance, and other factors not accounted for in the current WiNGS-Planning model. | [5 empty] | Assumptions | Value | Units | Last Update | Comments | [14 empty] | 2027 | 55.7812 | 30087.8368 | 10358.6318 | 34.43% | 189325.8231 | 95559.2845 | 1.9812 | 194056.8204 | 95559.2845 | 2.0307 | 658506.2488 | 206633.3375 | 3.1868
[9 empty] | Capital Cost only in Year 0 | 1 | M$/mile | 2025-05-01 | Includes Primary, Secondary for BCR | [14 empty] | 2028 | 30.2052 | 16665.9414 | 7314.6296 | 43.89% | 127531.4334 | 56239.1444 | 2.2677 | 130822.9206 | 56239.1444 | 2.3262 | 467276.0649 | 137640.7274 | 3.3949
[9 empty] | Service Drop factor | 1.26% | % | 2025-05-01 | Factor to account for Service drop miles | [14 empty] | Total 2026-2028 | 139.5756 | 60292.293 | 20898.1416 | 34.66% | 378645.1805 | 248417.6759 | 1.5242 | 388781.8859 | 248417.6759 | 1.565 | 1329790.4097 | 543079.2503 | 2.4486
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.0080298 | M$/mile | 2025-05-01 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 55 | Years | 2025-05-01 | End of the expected lifetime (defined as 55 years) of the infrastructure
[9 empty] | Mitigation Effectiveness Estimate (%) | 58% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.045872 | M$/mile | 2025-05-01 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[7 empty] | OH miles | OH miles (OH to UG factor = 0%) | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | HFTD Tier | Feeder | Feeder Segment | Tranche ID HTM | Tranche ID Quintile | Total miles in scope | Units (OH Primary + Secondary miles + Service Drop) | OH miles (Miles + OH to UG Conversion) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2027 | Tier-3 | 973 | 973-1245R | Tier-3---6 | Tier-3---1 | 100% | 3.3857 | 3.3857 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 2864.9044 | 162.2092 | 18.3726 | 2684.3226 | 155.0542 | 52362.1653 | 6056.2011 | 8.646 | 53293.0523 | 6056.2011 | 8.7997 | 182124.1947 | 13432.7123 | 13.5583 | 33.24%
2027 | Tier-3 | 973 | 973-626R | Tier-3---7 | Tier-3---1 | 100% | 11.0435 | 11.0435 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 2944.0139 | 190.5475 | 47.7875 | 2705.6788 | 477.9511 | 53808.0569 | 19245.9611 | 2.7958 | 55036.6578 | 19245.9611 | 2.8596 | 187153.2426 | 42047.2938 | 4.451 | 45.14%
2027 | Tier-3 | 448 | 448-9R | Tier-3---9 | Tier-3---3 | 100% | 16.6498 | 16.6498 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 967.4443 | 46.4193 | 144.1893 | 776.8358 | 655.3823 | 17682.0835 | 27824.5828 | 0.63548 | 18664.6575 | 27824.5828 | 0.6708 | 61501.185 | 59247.8469 | 1.038 | 17.14%
2027 | Tier-3 | 973 | 973-1226R | Tier-3---10 | Tier-3---1 | 100% | 8.59 | 8.59 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 2234.9415 | 118.7612 | 53.9084 | 2062.2719 | 380.9704 | 40848.2654 | 15138.4204 | 2.6983 | 41738.3651 | 15138.4204 | 2.7571 | 142076.9632 | 33290.9525 | 4.2677 | 43.16%
2027 | Tier-2 | 1243 | 1243-45R | Tier-2---7 | Tier-2---2 | 100% | 4.279 | 4.279 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 629.8616 | 32.9784 | 5.663 | 591.2202 | 164.7615 | 11512.0473 | 7083.8143 | 1.6251 | 11711.2408 | 7083.8143 | 1.6532 | 40040.7876 | 14993.2862 | 2.6706 | 33.53%
2027 | Tier-2 | 1243 | 1243-319R | Tier-2---9 | Tier-2---4 | 100% | 3.3629 | 3.3629 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 518.7426 | 26.4617 | 2.3112 | 489.9696 | 134.4015 | 9481.1134 | 5657.0101 | 1.676 | 9629.436 | 5657.0101 | 1.7022 | 32976.8665 | 12095.704 | 2.7263 | 44.03%
2027 | Tier-3 | 448 | 448-724R | Tier-3---18 | Tier-3---10 | 100% | 8.0851 | 8.0851 | 520.639 | 76.18% | 22.78% | 1.038% | 86.4586 | 1.8927 | 44.6947 | 39.8712 | 332.0824 | 1580.2125 | 13764.3065 | 0.11481 | 1820.3674 | 13764.3065 | 0.13225 | 5496.2383 | 29649.7934 | 0.18537 | 16.61%
2027 | Tier-3 | 973 | 973-530AE | Tier-3---17 | Tier-3---5 | 100% | 0.034712 | 0.034712 | 388.0062 | 6.476% | 93.52% | 0.007746% | 22.6749 | 0.28183 | 16.2536 | 6.1395 | 3.677 | 414.4321 | 100.2408 | 4.1344 | 499.6713 | 100.2408 | 4.9847 | 1441.4628 | 270.4085 | 5.3307 | 5.844%
2027 | Tier-2 | 1243 | 1243-38R | Tier-2---16 | Tier-2---8 | 100% | 0.35057 | 0.35057 | 158.2514 | 99.48% | 0.3681% | 0.155% | 89.59 | 4.8249 | 0.20439 | 84.5607 | 19.4284 | 1637.4467 | 688.7474 | 2.3774 | 1663.3724 | 688.7474 | 2.4151 | 5695.308 | 1605.3399 | 3.5477 | 56.61%
2026 | Tier-3 | 157 | 157-204R | Tier-3---11 | Tier-3---3 | 100% | 13.3849 | 13.3849 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 1382.1699 | 80.7309 | 24.2925 | 1277.1465 | 473.3766 | 26482.0409 | 22423.7937 | 1.181 | 27016.9222 | 22423.7937 | 1.2048 | 87437.0004 | 44013.6595 | 1.9866 | 35.66%
2026 | Tier-3 | 157 | 157-257R | Tier-3---14 | Tier-3---3 | 100% | 23.2973 | 23.2973 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 645.243 | 27.8837 | 142.9115 | 474.4479 | 1049.5099 | 12362.7002 | 43351.8337 | 0.28517 | 13232.5554 | 43351.8337 | 0.30524 | 40818.5088 | 90878.1134 | 0.44916 | 31.3%
2026 | Tier-3 | 157 | 157-273R | Tier-3---14 | Tier-3---3 | 100% | 8.5826 | 8.5826 | 1867.403 | 95.01% | 4.712% | 0.2778% | 542.7493 | 30.4805 | 36.8063 | 475.4624 | 381.6242 | 10398.9455 | 15874.5602 | 0.65507 | 10741.6359 | 15874.5602 | 0.67666 | 34334.6877 | 33162.0576 | 1.0354 | 29.06%
2026 | Tier-3 | 73 | 73-23R | Tier-3---9 | Tier-3---1 | 100% | 8.3244 | 8.3244 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 654.718 | 38.1891 | 33.8305 | 582.6984 | 347.8054 | 12544.2375 | 14969.0595 | 0.83801 | 12911.0314 | 14969.0595 | 0.86251 | 41417.899 | 30751.3549 | 1.3469 | 11.42%
2028 | Tier-3 | TM1 | TM1-10R | Tier-3---12 | Tier-3---1 | 100% | 3.4327 | 3.4327 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 1802.1944 | 92.6267 | 6.8016 | 1702.7661 | 240.169 | 31421.4737 | 7303.8488 | 4.302 | 31938.8987 | 7303.8488 | 4.3729 | 115128.4998 | 18985.7632 | 6.0639 | 47.64%
2028 | Tier-3 | 1233 | 1233-585R | Tier-3---12 | Tier-3---1 | 100% | 6.3138 | 6.3138 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 1632.1907 | 95.715 | 20.9301 | 1515.5457 | 359.4802 | 28457.4381 | 11999.7758 | 2.3715 | 29064.4587 | 11999.7758 | 2.4221 | 104268.2525 | 29665.4594 | 3.5148 | 45.82%
2028 | Tier-2 | 452 | 452-38AE | Tier-2---4 | Tier-2---7 | 100% | 2.8002 | 2.8002 | 2823.7515 | 99.93% | 0% | 0.06613% | 1397.1055 | 123.6967 | 0.07293 | 1273.3359 | 162.2991 | 24358.7006 | 5371.9496 | 4.5344 | 25002.7974 | 5371.9496 | 4.6543 | 89250.4496 | 13339.971 | 6.6905 | 49.48%
2028 | Tier-3 | 1458 | 1458-1058F | Tier-3---13 | Tier-3---1 | 100% | 1.4878 | 1.4878 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 855.9473 | 45.3663 | 134.8762 | 675.7048 | 63.1247 | 14923.5425 | 2451.3664 | 6.0878 | 15861.524 | 2451.3664 | 6.4705 | 54679.9644 | 5611.634 | 9.744 | 36.18%
2028 | Tier-3 | 79 | 79-660R | Tier-3---14 | Tier-3---5 | 100% | 7.3375 | 7.3375 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 1069.3541 | 47.4471 | 20.6645 | 1001.2425 | 394.6586 | 18644.3156 | 13542.538 | 1.3767 | 18998.7683 | 13542.538 | 1.4029 | 68312.903 | 32999.2449 | 2.0701 | 51.24%
2028 | Tier-2 | 520 | 520-45 | Tier-2---8 | Tier-2---1 | 100% | 8.8332 | 8.8332 | 2044.6463 | 97.57% | 2.13% | 0.298% | 557.8375 | 27.7948 | 16.5001 | 513.5426 | 433.0414 | 9725.9628 | 15569.6658 | 0.62467 | 9956.4733 | 15569.6658 | 0.63948 | 35635.9957 | 37038.6549 | 0.96213 | 27.28%

## OH Hardening_RA_RAMP
OH Hardening - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 7.2752 | 31211.0643 | 972.5759 | 3.116% | 17086.1046 | 7227.7171 | 2.364 | 17086.1046 | 7227.7171 | 2.364 | 43073.5699 | 7616.4205 | 5.6554
[9 empty] | Assumptions | Value | Units | Last Update | Comments | [13 empty] | 2027 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Capital Cost only in Year 0 | 1 | M$/unit | 2025-05-01 | [5 empty] | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [8 empty] | 2028 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 | Factor to account for Service drop miles | [13 empty] | Total 2026-2028 | 7.2752 | 31211.0643 | 972.5759 | 3.116% | 17086.1046 | 7227.7171 | 2.364 | 17086.1046 | 7227.7171 | 2.364 | 43073.5699 | 7616.4205 | 5.6554
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.0080298 | $/unit | 2025-05-01 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 40 | Years | 2025-05-01 | Expected lifetime (defined as 40 years) of the infrastructure
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 39% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.041292 | M$/unit | 2025-05-01 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized. | [21 empty] | `
[13 empty] | [1] | [1] | [1]
[6 empty] | OH miles | OH miles | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Units (OH Primary + Secondary miles + Service Drop) | OH miles in scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 18.1587 | 0.46231 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.1399 | 0 | 0 | 15.1399 | 0.0037122 | 265.9756 | 459.2937 | 0.5791 | 265.9756 | 459.2937 | 0.5791 | 670.5166 | 483.9943 | 1.3854 | 0.8367%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 8.3509 | 3.0742 | 333.8465 | 96.62% | 2.31% | 1.072% | 46.3094 | 0 | 0 | 46.3094 | 0.024685 | 813.5583 | 3054.1831 | 0.26638 | 813.5583 | 3054.1831 | 0.26638 | 2050.9567 | 3218.4357 | 0.63725 | 13.87%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 13.2994 | 0.20758 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 55.6775 | 0 | 0 | 55.6775 | 0.0016668 | 978.136 | 206.2217 | 4.7431 | 978.136 | 206.2217 | 4.7431 | 2465.8523 | 217.3122 | 11.3471 | 0.578%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 8.4553 | 0.97197 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 232.9534 | 0 | 0 | 232.9534 | 0.0078047 | 4092.4997 | 965.6274 | 4.2382 | 4092.4997 | 965.6274 | 4.2382 | 10317.072 | 1017.5584 | 10.139 | 4.428%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 5.3305 | 1.0949 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 177.5724 | 0 | 0 | 177.5724 | 0.0087917 | 3119.5719 | 1087.7434 | 2.8679 | 3119.5719 | 1087.7434 | 2.8679 | 7864.3495 | 1146.2418 | 6.861 | 7.654%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 11.5801 | 0.98996 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 340.9958 | 0 | 0 | 340.9958 | 0.0079491 | 5990.5769 | 983.5 | 6.0911 | 5990.5769 | 983.5 | 6.0911 | 15102.0692 | 1036.3922 | 14.5718 | 3.303%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 2.6672 | 0.47424 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 103.9275 | 0 | 0 | 103.9275 | 0.003808 | 1825.7862 | 471.1478 | 3.8752 | 1825.7862 | 471.1478 | 3.8752 | 4602.7537 | 496.4859 | 9.2707 | 6.785%
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A

## SPRP_RA_RAMP
Strategic Pole Replacement - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 200 | 98550.2033 | 1326.0872 | 1.346% | 23296.553 | 5259.5998 | 4.4293 | 23296.553 | 5259.5998 | 4.4293 | 58729.9288 | 5540.6275 | 10.5999
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 200 | 100008.7722 | 1504.1815 | 1.504% | 25207.9347 | 5017.3009 | 5.0242 | 25207.9347 | 5017.3009 | 5.0242 | 66943.9477 | 5567.7874 | 12.0234
[9 empty] | Capital Cost only in Year 0 | 25 | K$/unit | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 200 | 81394.9393 | 1107.8034 | 1.361% | 17709.9434 | 4786.1642 | 3.7002 | 17709.9434 | 4786.1642 | 3.7002 | 49544.7312 | 5595.0805 | 8.8551
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 | Factor to account for Service drop miles |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 600 | 279953.9148 | 3938.0722 | 1.407% | 66214.4311 | 15063.0649 | 4.3958 | 66214.4311 | 15063.0649 | 4.3958 | 175218.6077 | 16703.4953 | 10.4899
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 40 | Years | 2025-05-01 | Expected lifetime (defined as 40 years) of the infrastructure
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 39% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 2.568 | K$/unit | 2025-05-01 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 4 | 860.3234 | 98.08% | 1.495% | 0.4234% | 10.365 | 0 | 0 | 10.365 | 0 | 182.0907 | 105.192 | 1.731 | 182.0907 | 105.192 | 1.731 | 459.0454 | 110.8125 | 4.1425 | 1.205%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 2 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 22.1817 | 0 | 0 | 22.1817 | 0 | 389.6857 | 52.596 | 7.409 | 389.6857 | 52.596 | 7.409 | 982.3861 | 55.4063 | 17.7306 | 1.399%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 34 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 256.9728 | 0 | 0 | 256.9728 | 0 | 4514.4689 | 894.132 | 5.049 | 4514.4689 | 894.132 | 5.049 | 11380.8442 | 941.9067 | 12.0828 | 2.714%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 12 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 45.2649 | 0 | 0 | 45.2649 | 0 | 795.2084 | 315.576 | 2.5199 | 795.2084 | 315.576 | 2.5199 | 2004.6971 | 332.4376 | 6.0303 | 1.199%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 2 | 585.5086 | 87.68% | 11.85% | 0.4758% | 3.3649 | 0 | 0 | 3.3649 | 0 | 59.1141 | 52.596 | 1.1239 | 59.1141 | 52.596 | 1.1239 | 149.025 | 55.4063 | 2.6897 | 0.5747%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 8 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 120.9483 | 0 | 0 | 120.9483 | 0 | 2124.8058 | 210.384 | 10.0997 | 2124.8058 | 210.384 | 10.0997 | 5356.5732 | 221.6251 | 24.1695 | 3.002%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 239 | 22 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 153.5351 | 0 | 0 | 153.5351 | 0 | 2697.2879 | 578.556 | 4.6621 | 2697.2879 | 578.556 | 4.6621 | 6799.7839 | 609.469 | 11.1569 | 3.501%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 7 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 50.6076 | 0 | 0 | 50.6076 | 0 | 889.0682 | 184.086 | 4.8296 | 889.0682 | 184.086 | 4.8296 | 2241.3148 | 193.922 | 11.5578 | 0.8814%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 1 | 836.2457 | 79.76% | 20.09% | 0.1547% | 5.0023 | 0 | 0 | 5.0023 | 0 | 87.8803 | 26.298 | 3.3417 | 87.8803 | 26.298 | 3.3417 | 221.5436 | 27.7031 | 7.9971 | 0.5982%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 7 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 14.5065 | 0 | 0 | 14.5065 | 0 | 254.8486 | 184.086 | 1.3844 | 254.8486 | 184.086 | 1.3844 | 642.466 | 193.922 | 3.313 | 0.781%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 14 | 6370.0414 | 98.47% | 1.262% | 0.272% | 40.008 | 0 | 0 | 40.008 | 0 | 702.8562 | 368.172 | 1.909 | 702.8562 | 368.172 | 1.909 | 1771.88 | 387.8439 | 4.5685 | 0.6281%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 12 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 13.2145 | 0 | 0 | 13.2145 | 0 | 232.1511 | 315.576 | 0.73564 | 232.1511 | 315.576 | 0.73564 | 585.2462 | 332.4376 | 1.7605 | 0.9786%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 5 | 18774.394 | 95.55% | 4.388% | 0.06321% | 87.891 | 0 | 0 | 87.891 | 0 | 1544.0593 | 131.49 | 11.7428 | 1544.0593 | 131.49 | 11.7428 | 3892.5284 | 138.5157 | 28.1017 | 0.4681%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 26 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 344.5715 | 0 | 0 | 344.5715 | 0 | 6053.3944 | 683.748 | 8.8533 | 6053.3944 | 683.748 | 8.8533 | 15260.4303 | 720.2816 | 21.1868 | 1.338%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 20 | 4323.2442 | 99.81% | 0% | 0.1903% | 91.2117 | 0 | 0 | 91.2117 | 0 | 1602.3976 | 525.96 | 3.0466 | 1602.3976 | 525.96 | 3.0466 | 4039.5975 | 554.0627 | 7.2909 | 2.11%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 24 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 49.4757 | 0 | 0 | 49.4757 | 0 | 829.1427 | 602.0761 | 1.3771 | 829.1427 | 602.0761 | 1.3771 | 2201.9291 | 668.1345 | 3.2956 | 1.061%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 23 | 8462.8018 | 99.74% | 0% | 0.2593% | 70.8274 | 0 | 0 | 70.8274 | 0 | 1186.9667 | 576.9896 | 2.0572 | 1186.9667 | 576.9896 | 2.0572 | 3152.1914 | 640.2955 | 4.923 | 0.8369%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 5 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 28.681 | 0 | 0 | 28.681 | 0 | 480.6524 | 125.4325 | 3.832 | 480.6524 | 125.4325 | 3.832 | 1276.4541 | 139.1947 | 9.1703 | 0.5807%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 6 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 17.1863 | 0 | 0 | 17.1863 | 0 | 301.9273 | 157.788 | 1.9135 | 301.9273 | 157.788 | 1.9135 | 761.1499 | 166.2188 | 4.5792 | 0.5074%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 10 | 3753.23 | 95.85% | 3.876% | 0.273% | 30.2377 | 0 | 0 | 30.2377 | 0 | 531.2126 | 262.98 | 2.02 | 531.2126 | 262.98 | 2.02 | 1339.1715 | 277.0314 | 4.834 | 0.8056%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 9 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 180.83 | 0 | 0 | 180.83 | 0 | 3030.4527 | 225.7785 | 13.4222 | 3030.4527 | 225.7785 | 13.4222 | 8047.8815 | 250.5504 | 32.1208 | 0.9715%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 40 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 659.6545 | 0 | 0 | 659.6545 | 0 | 11054.8682 | 1003.4602 | 11.0167 | 11054.8682 | 1003.4602 | 11.0167 | 29358.0782 | 1113.5575 | 26.3642 | 3.216%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 5 | 3653.654 | 88.54% | 11.39% | 0.07412% | 70.8747 | 0 | 0 | 70.8747 | 0 | 1187.758 | 125.4325 | 9.4693 | 1187.758 | 125.4325 | 9.4693 | 3154.2929 | 139.1947 | 22.661 | 1.94%
2027 | 450 | 450-114F | Tier-1 | Non-HFTD---7 | Non-HFTD---17 | 25 | 2 | 28.615 | 98.32% | 0% | 1.684% | 0.87775 | 0 | 0 | 0.87775 | 0 | 14.7098 | 50.173 | 0.29318 | 14.7098 | 50.173 | 0.29318 | 39.0645 | 55.6779 | 0.70162 | 3.067%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 6 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 91.926 | 0 | 0 | 91.926 | 0 | 1540.5481 | 150.519 | 10.2349 | 1540.5481 | 150.519 | 10.2349 | 4091.1868 | 167.0336 | 24.4932 | 1.111%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 13 | 792.2018 | 92.77% | 7.138% | 0.09408% | 84.6819 | 0 | 0 | 84.6819 | 0 | 1419.1473 | 326.1246 | 4.3516 | 1419.1473 | 326.1246 | 4.3516 | 3768.7865 | 361.9062 | 10.4137 | 10.69%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 18 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 108.1599 | 0 | 0 | 108.1599 | 0 | 1812.6047 | 451.5571 | 4.0141 | 1812.6047 | 451.5571 | 4.0141 | 4813.6794 | 501.1009 | 9.6062 | 9.552%
2027 | 450 | 450-88R | Tier-2 | Tier-2---10 | Tier-2---4 | 143 | 2 | 894.3745 | 42.96% | 56.7% | 0.3423% | 2.0958 | 0 | 0 | 2.0958 | 0 | 35.1229 | 50.173 | 0.70004 | 35.1229 | 50.173 | 0.70004 | 93.2749 | 55.6779 | 1.6753 | 0.2343%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 1 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.11052 | 0 | 0 | 0.11052 | 0 | 1.8522 | 25.0865 | 0.073831 | 1.8522 | 25.0865 | 0.073831 | 4.9187 | 27.8389 | 0.17668 | 0.0945%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 6 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 21.0026 | 0 | 0 | 21.0026 | 0 | 351.9739 | 150.519 | 2.3384 | 351.9739 | 150.519 | 2.3384 | 934.7264 | 167.0336 | 5.596 | 0.3724%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 2 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 17.4289 | 0 | 0 | 17.4289 | 0 | 292.0841 | 50.173 | 5.8215 | 292.0841 | 50.173 | 5.8215 | 775.6788 | 55.6779 | 13.9315 | 0.5559%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 2 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 15.7961 | 0 | 0 | 15.7961 | 0 | 264.7202 | 50.173 | 5.2761 | 264.7202 | 50.173 | 5.2761 | 703.0093 | 55.6779 | 12.6264 | 0.9246%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 6 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 16.0943 | 0 | 0 | 16.0943 | 0 | 269.7172 | 150.519 | 1.7919 | 269.7172 | 150.519 | 1.7919 | 716.2799 | 167.0336 | 4.2882 | 0.7279%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 1 | 1554.328 | 69.02% | 30.62% | 0.3611% | 1.4183 | 0 | 0 | 1.4183 | 0 | 23.7687 | 25.0865 | 0.94747 | 23.7687 | 25.0865 | 0.94747 | 63.1219 | 27.8389 | 2.2674 | 0.09125%
2027 | 920 | 920-823 | Tier-2 | Tier-2---11 | Tier-2---4 | 127 | 5 | 458.2189 | 68.35% | 31.14% | 0.5113% | 4.8086 | 0 | 0 | 4.8086 | 0 | 80.5851 | 125.4325 | 0.64246 | 80.5851 | 125.4325 | 0.64246 | 214.0073 | 139.1947 | 1.5375 | 1.049%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 6 | 765.4961 | 75% | 24.28% | 0.7274% | 4.6164 | 0 | 0 | 4.6164 | 0 | 77.3639 | 150.519 | 0.51398 | 77.3639 | 150.519 | 0.51398 | 205.4531 | 167.0336 | 1.23 | 0.6031%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 12 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 49.548 | 0 | 0 | 49.548 | 0 | 830.3535 | 301.0381 | 2.7583 | 830.3535 | 301.0381 | 2.7583 | 2205.1446 | 334.0672 | 6.6009 | 0.7456%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 3 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 10.8286 | 0 | 0 | 10.8286 | 0 | 181.4725 | 75.2595 | 2.4113 | 181.4725 | 75.2595 | 2.4113 | 481.9311 | 83.5168 | 5.7705 | 0.3287%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 6 | 1438.4419 | 90% | 9.47% | 0.5268% | 9.9982 | 0 | 0 | 9.9982 | 0 | 167.5562 | 150.519 | 1.1132 | 167.5562 | 150.519 | 1.1132 | 444.9738 | 167.0336 | 2.664 | 0.6951%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 3 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 4.4463 | 0 | 0 | 4.4463 | 0 | 74.5136 | 75.2595 | 0.99009 | 74.5136 | 75.2595 | 0.99009 | 197.8834 | 83.5168 | 2.3694 | 0.4139%
2028 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 2 | 2758.283 | 96.49% | 3.415% | 0.0991% | 19.9601 | 0 | 0 | 19.9601 | 0 | 319.0928 | 47.8616 | 6.667 | 319.0928 | 47.8616 | 6.667 | 892.683 | 55.9508 | 15.9548 | 0.7236%
2028 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | Tier-2---3 | 31 | 3 | 1005.6854 | 94.09% | 5.81% | 0.1042% | 35.7115 | 0 | 0 | 35.7115 | 0 | 570.904 | 71.7925 | 7.9521 | 570.904 | 71.7925 | 7.9521 | 1597.1415 | 83.9262 | 19.0303 | 3.551%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 10 | 2 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 31.6356 | 0 | 0 | 31.6356 | 0 | 505.7436 | 47.8616 | 10.5668 | 505.7436 | 47.8616 | 10.5668 | 1414.8509 | 55.9508 | 25.2874 | 7.734%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 17 | 4222.2471 | 91.41% | 8.486% | 0.103% | 175.2674 | 0 | 0 | 175.2674 | 0 | 2801.9189 | 406.824 | 6.8873 | 2801.9189 | 406.824 | 6.8873 | 7838.5522 | 475.5818 | 16.482 | 4.151%
2028 | RC1 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 20 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 227.1478 | 0 | 0 | 227.1478 | 0 | 3631.3066 | 478.6164 | 7.5871 | 3631.3066 | 478.6164 | 7.5871 | 10158.8191 | 559.508 | 18.1567 | 1.423%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 8 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 19.0174 | 0 | 0 | 19.0174 | 0 | 334.0958 | 210.384 | 1.588 | 334.0958 | 210.384 | 1.588 | 842.2457 | 221.6251 | 3.8003 | 1.103%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 5 | 1279.0443 | 99.78% | 0% | 0.2159% | 18.8542 | 0 | 0 | 18.8542 | 0 | 301.4132 | 119.6541 | 2.519 | 301.4132 | 119.6541 | 2.519 | 843.2232 | 139.877 | 6.0283 | 1.474%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 7 | 2976.5734 | 99.75% | 0% | 0.2502% | 19.6264 | 0 | 0 | 19.6264 | 0 | 313.7587 | 167.5157 | 1.873 | 313.7587 | 167.5157 | 1.873 | 877.7606 | 195.8278 | 4.4823 | 0.6594%
2028 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 302 | 1 | 1585.8519 | 99.67% | 0% | 0.3254% | 2.0413 | 0 | 0 | 2.0413 | 0 | 32.6332 | 23.9308 | 1.3636 | 32.6332 | 23.9308 | 1.3636 | 91.2935 | 27.9754 | 3.2633 | 0.1287%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 77 | 8462.8018 | 99.74% | 0% | 0.2593% | 237.1179 | 0 | 0 | 237.1179 | 0 | 3790.6951 | 1842.6732 | 2.0572 | 3790.6951 | 1842.6732 | 2.0572 | 10604.7188 | 2154.106 | 4.923 | 2.802%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 12 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 25.9459 | 0 | 0 | 25.9459 | 0 | 414.7856 | 287.1699 | 1.4444 | 414.7856 | 287.1699 | 1.4444 | 1160.3899 | 335.7048 | 3.4566 | 1.907%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 9 | 1 | 105.2026 | 98.18% | 1.532% | 0.2854% | 4.4759 | 0 | 0 | 4.4759 | 0 | 71.5548 | 23.9308 | 2.9901 | 71.5548 | 23.9308 | 2.9901 | 200.1792 | 27.9754 | 7.1555 | 4.255%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 6 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 96.7915 | 0 | 0 | 96.7915 | 0 | 1547.3606 | 143.5849 | 10.7766 | 1547.3606 | 143.5849 | 10.7766 | 4328.843 | 167.8524 | 25.7896 | 4.021%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 2 | 4762.848 | 95.55% | 4.384% | 0.07015% | 32.5646 | 0 | 0 | 32.5646 | 0 | 520.5958 | 47.8616 | 10.8771 | 520.5958 | 47.8616 | 10.8771 | 1456.401 | 55.9508 | 26.03 | 0.6837%
2028 | 387 | 387-11 | Tier-2 | Tier-2---7 | Tier-2---2 | 523 | 2 | 2227.2808 | 89.28% | 10.33% | 0.3978% | 2.9655 | 0 | 0 | 2.9655 | 0 | 47.4086 | 47.8616 | 0.99053 | 47.4086 | 47.8616 | 0.99053 | 132.6287 | 55.9508 | 2.3705 | 0.1331%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 140 | 2 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 7.2162 | 0 | 0 | 7.2162 | 0 | 115.3615 | 47.8616 | 2.4103 | 115.3615 | 47.8616 | 2.4103 | 322.7313 | 55.9508 | 5.7681 | 0.4959%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 16 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 23.0761 | 0 | 0 | 23.0761 | 0 | 368.9074 | 382.8931 | 0.96347 | 368.9074 | 382.8931 | 0.96347 | 1032.0428 | 447.6064 | 2.3057 | 0.7356%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 1 | 625.5425 | 99.9% | 0% | 0.09615% | 12.1864 | 0 | 0 | 12.1864 | 0 | 194.8176 | 23.9308 | 8.1409 | 194.8176 | 23.9308 | 8.1409 | 545.015 | 27.9754 | 19.4819 | 1.948%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 3 | 2823.7515 | 99.93% | 0% | 0.06613% | 46.5015 | 0 | 0 | 46.5015 | 0 | 743.3976 | 71.7925 | 10.3548 | 743.3976 | 71.7925 | 10.3548 | 2079.7037 | 83.9262 | 24.7801 | 1.647%
2028 | 452 | 452-717 | Tier-2 | Tier-2---19 | Tier-2---11 | 17 | 1 | 24.802 | 99.04% | 0% | 0.9608% | 0.56352 | 0 | 0 | 0.56352 | 0 | 9.0087 | 23.9308 | 0.37645 | 9.0087 | 23.9308 | 0.37645 | 25.2026 | 27.9754 | 0.90088 | 2.272%
2028 | FB2 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 1 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.11052 | 0 | 0 | 0.11052 | 0 | 1.7668 | 23.9308 | 0.073831 | 1.7668 | 23.9308 | 0.073831 | 4.9428 | 27.9754 | 0.17668 | 0.0945%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 2 | 379.7423 | 70.28% | 29.01% | 0.71% | 2.313 | 0 | 0 | 2.313 | 0 | 36.9764 | 47.8616 | 0.77257 | 36.9764 | 47.8616 | 0.77257 | 103.444 | 55.9508 | 1.8488 | 0.6091%
2028 | 387 | CB 387 | Tier-1 | Non-HFTD---2 | Non-HFTD---4 | 257 | 3 | 522.65 | 70.14% | 28.94% | 0.9137% | 1.669 | 0 | 0 | 1.669 | 0 | 26.6809 | 71.7925 | 0.37164 | 26.6809 | 71.7925 | 0.37164 | 74.6415 | 83.9262 | 0.88937 | 0.3193%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 145 | 1 | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.25839 | 0 | 0 | 0.25839 | 0 | 4.1308 | 23.9308 | 0.17262 | 4.1308 | 23.9308 | 0.17262 | 11.5562 | 27.9754 | 0.41309 | 0.03858%
2028 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 5 | 305.5692 | 37.2% | 61.32% | 1.484% | 0.85577 | 0 | 0 | 0.85577 | 0 | 13.6809 | 119.6541 | 0.11434 | 13.6809 | 119.6541 | 0.11434 | 38.2731 | 139.877 | 0.27362 | 0.2801%
2028 | FB1 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 3 | 2730.9177 | 98.3% | 1.373% | 0.325% | 8.7981 | 0 | 0 | 8.7981 | 0 | 140.6508 | 71.7925 | 1.9591 | 140.6508 | 71.7925 | 1.9591 | 393.4799 | 83.9262 | 4.6884 | 0.3222%
2028 | JU1 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 244 | 1 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 6.1021 | 0 | 0 | 6.1021 | 0 | 97.5521 | 23.9308 | 4.0764 | 97.5521 | 23.9308 | 4.0764 | 272.9084 | 27.9754 | 9.7553 | 0.1551%
2028 | MOR1 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 4 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 68.0473 | 0 | 0 | 68.0473 | 0 | 1087.8405 | 95.7233 | 11.3644 | 1087.8405 | 95.7233 | 11.3644 | 3043.3054 | 111.9016 | 27.1963 | 0.4492%

## Veg--->
back to index

## Pole Brushing
Pole Brushing - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 22000 | 2820058.3619 | 27497.727 | 0.9751% | 26230.9634 | 8604.4672 | 3.0485 | 26230.9634 | 8604.4672 | 3.0485 | 27632.5197 | 9064.2157 | 3.0485
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 22000 | 2820058.3619 | 27497.727 | 0.9751% | 25022.5569 | 8208.0771 | 3.0485 | 25022.5569 | 8208.0771 | 3.0485 | 27767.9733 | 9108.6481 | 3.0485
[9 empty] | Capital Cost only in Year 0 | 0.41 | k$/structure | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 22000 | 2820058.3619 | 27497.727 | 0.9751% | 23869.8193 | 7829.9479 | 3.0485 | 23869.8193 | 7829.9479 | 3.0485 | 27904.0908 | 9153.2984 | 3.0485
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 66000 | 8460175.0857 | 82493.1809 | 0.9751% | 75123.3396 | 24642.4923 | 3.0485 | 75123.3396 | 24642.4923 | 3.0485 | 83304.5838 | 27326.1622 | 3.0485
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 1% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total HFTD Poles | Poles in the Scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 11 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 36.8178 | 4.3022 | 8.5578 | 36.8178 | 4.3022 | 8.5578 | 38.785 | 4.5321 | 8.5578 | 0.9141%
2026 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 1.0899 | 0.78222 | 1.3934 | 1.0899 | 0.78222 | 1.3934 | 1.1482 | 0.82402 | 1.3934 | 0.9976%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 332.0782 | 37.1557 | 8.9375 | 332.0782 | 37.1557 | 8.9375 | 349.8216 | 39.1409 | 8.9375 | 0.9902%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 17 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 66.0788 | 6.6489 | 9.9383 | 66.0788 | 6.6489 | 9.9383 | 69.6095 | 7.0042 | 9.9383 | 0.9818%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 43 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 179.0433 | 16.8178 | 10.646 | 179.0433 | 16.8178 | 10.646 | 188.6098 | 17.7164 | 10.646 | 0.997%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 11 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 47.787 | 4.3022 | 11.1075 | 47.787 | 4.3022 | 11.1075 | 50.3403 | 4.5321 | 11.1075 | 0.9951%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 3 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 13.1718 | 1.1733 | 11.226 | 13.1718 | 1.1733 | 11.226 | 13.8756 | 1.236 | 11.226 | 0.9958%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 33 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 93.1374 | 12.9067 | 7.2162 | 93.1374 | 12.9067 | 7.2162 | 98.1139 | 13.5963 | 7.2162 | 0.9962%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 1 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.5753 | 0.39111 | 16.8118 | 6.5753 | 0.39111 | 16.8118 | 6.9266 | 0.41201 | 16.8118 | 0.9922%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 32 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 47.9789 | 12.5156 | 3.8335 | 47.9789 | 12.5156 | 3.8335 | 50.5425 | 13.1843 | 3.8335 | 0.9916%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 18 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 27.3593 | 7.04 | 3.8862 | 27.3593 | 7.04 | 3.8862 | 28.8211 | 7.4162 | 3.8862 | 0.9924%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 80 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 86.7029 | 31.289 | 2.771 | 86.7029 | 31.289 | 2.771 | 91.3356 | 32.9608 | 2.771 | 0.9598%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 64 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 35.0604 | 25.0312 | 1.4007 | 35.0604 | 25.0312 | 1.4007 | 36.9337 | 26.3686 | 1.4007 | 0.9739%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 19 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.8971 | 7.4311 | 0.659 | 4.8971 | 7.4311 | 0.659 | 5.1588 | 7.8282 | 0.659 | 0.8768%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 21 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 48.0307 | 8.2134 | 5.8479 | 48.0307 | 8.2134 | 5.8479 | 50.597 | 8.6522 | 5.8479 | 0.9826%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 46 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 111.1363 | 17.9912 | 6.1773 | 111.1363 | 17.9912 | 6.1773 | 117.0745 | 18.9525 | 6.1773 | 0.9858%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 22 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 20.4052 | 8.6045 | 2.3715 | 20.4052 | 8.6045 | 2.3715 | 21.4955 | 9.0642 | 2.3715 | 0.9945%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 62.3119 | 33.2445 | 1.8744 | 62.3119 | 33.2445 | 1.8744 | 65.6414 | 35.0208 | 1.8744 | 0.9866%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 124 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 239.4495 | 48.4979 | 4.9373 | 239.4495 | 48.4979 | 4.9373 | 252.2436 | 51.0892 | 4.9373 | 0.9914%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 119 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 266.8268 | 46.5423 | 5.733 | 266.8268 | 46.5423 | 5.733 | 281.0837 | 49.0292 | 5.733 | 0.9849%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 103 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 252.5213 | 40.2846 | 6.2684 | 252.5213 | 40.2846 | 6.2684 | 266.0138 | 42.437 | 6.2684 | 0.9916%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 68 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 148.3449 | 26.5956 | 5.5778 | 148.3449 | 26.5956 | 5.5778 | 156.2711 | 28.0167 | 5.5778 | 0.9745%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 1 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14883 | 0.39111 | 0.38054 | 0.14883 | 0.39111 | 0.38054 | 0.15678 | 0.41201 | 0.38054 | 0.8684%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 10 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.9161 | 3.9111 | 1.7683 | 6.9161 | 3.9111 | 1.7683 | 7.2856 | 4.1201 | 1.7683 | 0.9924%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 24 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 8.238 | 9.3867 | 0.87762 | 8.238 | 9.3867 | 0.87762 | 8.6781 | 9.8882 | 0.87762 | 0.9393%
2026 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 11 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 4.6858 | 0 | 0 | 4.6858 | 0 | 4.47 | 4.3022 | 1.039 | 4.47 | 4.3022 | 1.039 | 4.7088 | 4.5321 | 1.039 | 0.9197%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 4 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1825 | 1.5644 | 0.75588 | 1.1825 | 1.5644 | 0.75588 | 1.2457 | 1.648 | 0.75588 | 0.8802%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 81 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 56.0593 | 31.6801 | 1.7695 | 56.0593 | 31.6801 | 1.7695 | 59.0546 | 33.3728 | 1.7695 | 0.9962%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 63 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 47.4306 | 24.6401 | 1.9249 | 47.4306 | 24.6401 | 1.9249 | 49.9649 | 25.9566 | 1.9249 | 0.9962%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 16 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 23.945 | 6.2578 | 3.8264 | 23.945 | 6.2578 | 3.8264 | 25.2244 | 6.5922 | 3.8264 | 0.9984%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 20.3953 | 1.1733 | 17.3823 | 20.3953 | 1.1733 | 17.3823 | 21.485 | 1.236 | 17.3823 | 0.9968%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 1 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 40.3024 | 0.39111 | 103.0456 | 40.3024 | 0.39111 | 103.0456 | 42.4558 | 0.41201 | 103.0456 | 0.9992%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 1 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.759 | 0.39111 | 9.6109 | 3.759 | 0.39111 | 9.6109 | 3.9598 | 0.41201 | 9.6109 | 0.945%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 3 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.4758 | 1.1733 | 6.3714 | 7.4758 | 1.1733 | 6.3714 | 7.8752 | 1.236 | 6.3714 | 0.994%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 93 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 40.5406 | 36.3734 | 1.1146 | 40.5406 | 36.3734 | 1.1146 | 42.7067 | 38.3169 | 1.1146 | 0.9112%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 9 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 2.0214 | 3.52 | 0.57427 | 2.0214 | 3.52 | 0.57427 | 2.1294 | 3.7081 | 0.57427 | 0.8819%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 6 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.9041 | 2.3467 | 0.81141 | 1.9041 | 2.3467 | 0.81141 | 2.0059 | 2.4721 | 0.81141 | 0.9662%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 8 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.3124 | 3.1289 | 0.73906 | 2.3124 | 3.1289 | 0.73906 | 2.436 | 3.2961 | 0.73906 | 0.9775%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 23 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 37.1689 | 8.9956 | 4.1319 | 37.1689 | 8.9956 | 4.1319 | 39.1549 | 9.4762 | 4.1319 | 0.9826%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 16 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 96.2066 | 6.2578 | 15.3739 | 96.2066 | 6.2578 | 15.3739 | 101.3471 | 6.5922 | 15.3739 | 0.9977%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 73 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 97.5658 | 28.5512 | 3.4172 | 97.5658 | 28.5512 | 3.4172 | 102.7789 | 30.0767 | 3.4172 | 0.9908%
2026 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | Tier-3---19 | 2 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 1.2393 | 0 | 0 | 1.2393 | 0 | 1.1822 | 0.78222 | 1.5114 | 1.1822 | 0.78222 | 1.5114 | 1.2454 | 0.82402 | 1.5114 | 0.7849%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 43 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 57.3987 | 16.8178 | 3.413 | 57.3987 | 16.8178 | 3.413 | 60.4656 | 17.7164 | 3.413 | 0.9788%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 15 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 20.009 | 5.8667 | 3.4106 | 20.009 | 5.8667 | 3.4106 | 21.0782 | 6.1801 | 3.4106 | 0.9469%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 64 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 80.0347 | 25.0312 | 3.1974 | 80.0347 | 25.0312 | 3.1974 | 84.311 | 26.3686 | 3.1974 | 0.9648%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 24 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 14.6539 | 9.3867 | 1.5611 | 14.6539 | 9.3867 | 1.5611 | 15.4368 | 9.8882 | 1.5611 | 0.9856%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 33 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 33.4415 | 12.9067 | 2.591 | 33.4415 | 12.9067 | 2.591 | 35.2284 | 13.5963 | 2.591 | 0.9842%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 39 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 27.8656 | 15.2534 | 1.8268 | 27.8656 | 15.2534 | 1.8268 | 29.3545 | 16.0684 | 1.8268 | 0.979%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 12 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 13.083 | 4.6933 | 2.7876 | 13.083 | 4.6933 | 2.7876 | 13.782 | 4.9441 | 2.7876 | 0.9892%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 30 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 40.471 | 11.7334 | 3.4492 | 40.471 | 11.7334 | 3.4492 | 42.6334 | 12.3603 | 3.4492 | 0.9866%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 10 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.9122 | 3.9111 | 1.0003 | 3.9122 | 3.9111 | 1.0003 | 4.1212 | 4.1201 | 1.0003 | 0.9965%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 14 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.3418 | 5.4756 | 0.79295 | 4.3418 | 5.4756 | 0.79295 | 4.5738 | 5.7681 | 0.79295 | 0.9977%
2026 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 1 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.02425 | 0 | 0 | 0.02425 | 0 | 0.023133 | 0.39111 | 0.059146 | 0.023133 | 0.39111 | 0.059146 | 0.024369 | 0.41201 | 0.059146 | 0.9862%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 11.1645 | 1.1733 | 9.5152 | 11.1645 | 1.1733 | 9.5152 | 11.761 | 1.236 | 9.5152 | 0.9935%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.5017 | 0.39111 | 3.8396 | 1.5017 | 0.39111 | 3.8396 | 1.582 | 0.41201 | 3.8396 | 0.9948%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 17.7477 | 6.2578 | 2.8361 | 17.7477 | 6.2578 | 2.8361 | 18.696 | 6.5922 | 2.8361 | 0.9905%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 4 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 61.4624 | 1.5644 | 39.287 | 61.4624 | 1.5644 | 39.287 | 64.7464 | 1.648 | 39.287 | 0.9454%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 28 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 111.2495 | 10.9511 | 10.1587 | 111.2495 | 10.9511 | 10.1587 | 117.1938 | 11.5363 | 10.1587 | 0.9926%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 13 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 34.5034 | 5.0845 | 6.7861 | 34.5034 | 5.0845 | 6.7861 | 36.3469 | 5.3561 | 6.7861 | 0.9815%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 16 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.6887 | 6.2578 | 0.58945 | 3.6887 | 6.2578 | 0.58945 | 3.8858 | 6.5922 | 0.58945 | 0.9046%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 3 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 19.3034 | 1.1733 | 16.4517 | 19.3034 | 1.1733 | 16.4517 | 20.3348 | 1.236 | 16.4517 | 0.8554%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 33 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 41.1347 | 12.9067 | 3.1871 | 41.1347 | 12.9067 | 3.1871 | 43.3326 | 13.5963 | 3.1871 | 0.9867%
2026 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.78222 | 0 | 0 | 0.78222 | 0 | 0 | 0.82402 | 0 | 0%
2026 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 3 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1.1733 | 0 | 0 | 1.1733 | 0 | 0 | 1.236 | 0 | 0%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 51 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 151.1246 | 19.9467 | 7.5764 | 151.1246 | 19.9467 | 7.5764 | 159.1994 | 21.0125 | 7.5764 | 0.9909%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.47647 | 0.39111 | 1.2182 | 0.47647 | 0.39111 | 1.2182 | 0.50193 | 0.41201 | 1.2182 | 0.2981%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.77236 | 0.39111 | 1.9748 | 0.77236 | 0.39111 | 1.9748 | 0.81363 | 0.41201 | 1.9748 | 0.9995%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 38 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 77.2532 | 14.8623 | 5.1979 | 77.2532 | 14.8623 | 5.1979 | 81.381 | 15.6564 | 5.1979 | 0.9925%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 127 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 351.4153 | 49.6712 | 7.0748 | 351.4153 | 49.6712 | 7.0748 | 370.1919 | 52.3252 | 7.0748 | 0.9936%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.070593 | 0.39111 | 0.18049 | 0.070593 | 0.39111 | 0.18049 | 0.074365 | 0.41201 | 0.18049 | 0.895%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 20 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.502 | 7.8222 | 0.44769 | 3.502 | 7.8222 | 0.44769 | 3.6891 | 8.2402 | 0.44769 | 0.8771%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 177 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 48.5729 | 69.2268 | 0.70165 | 48.5729 | 69.2268 | 0.70165 | 51.1682 | 72.9257 | 0.70165 | 0.9246%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 10 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 28.8489 | 3.9111 | 7.3761 | 28.8489 | 3.9111 | 7.3761 | 30.3904 | 4.1201 | 7.3761 | 0.9907%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 20 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 36.6006 | 7.8222 | 4.679 | 36.6006 | 7.8222 | 4.679 | 38.5562 | 8.2402 | 4.679 | 0.9899%
2026 | 157 | 157-207R | Tier-3 | Tier-3---16 | Tier-3---7 | 2 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 7.1828 | 0 | 0 | 7.1828 | 0 | 6.8519 | 0.78222 | 8.7595 | 6.8519 | 0.78222 | 8.7595 | 7.218 | 0.82402 | 8.7595 | 0.9989%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 80 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 28.7225 | 31.289 | 0.91798 | 28.7225 | 31.289 | 0.91798 | 30.2572 | 32.9608 | 0.91798 | 0.9527%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 151 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 16.0328 | 59.0579 | 0.27148 | 16.0328 | 59.0579 | 0.27148 | 16.8894 | 62.2135 | 0.27148 | 0.8154%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.9249 | 20.7289 | 0.81649 | 16.9249 | 20.7289 | 0.81649 | 17.8293 | 21.8365 | 0.81649 | 0.9501%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 205 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 173.5015 | 80.178 | 2.164 | 173.5015 | 80.178 | 2.164 | 182.772 | 84.462 | 2.164 | 0.97%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 19 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 38.089 | 7.4311 | 5.1256 | 38.089 | 7.4311 | 5.1256 | 40.1242 | 7.8282 | 5.1256 | 0.991%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 6 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.8695 | 2.3467 | 7.6148 | 17.8695 | 2.3467 | 7.6148 | 18.8243 | 2.4721 | 7.6148 | 0.7065%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 40.7977 | 24.6401 | 1.6557 | 40.7977 | 24.6401 | 1.6557 | 42.9776 | 25.9566 | 1.6557 | 0.9752%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 113 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 53.0508 | 44.1957 | 1.2004 | 53.0508 | 44.1957 | 1.2004 | 55.8853 | 46.5571 | 1.2004 | 0.9686%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 9 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.3625 | 3.52 | 1.8075 | 6.3625 | 3.52 | 1.8075 | 6.7025 | 3.7081 | 1.8075 | 0.7976%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 108.5713 | 24.249 | 4.4774 | 108.5713 | 24.249 | 4.4774 | 114.3724 | 25.5446 | 4.4774 | 0.9877%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 55 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 39.1596 | 21.5112 | 1.8204 | 39.1596 | 21.5112 | 1.8204 | 41.252 | 22.6605 | 1.8204 | 0.981%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 32 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 93.29 | 12.5156 | 7.4539 | 93.29 | 12.5156 | 7.4539 | 98.2747 | 13.1843 | 7.4539 | 0.9713%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 51 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 31.7101 | 19.9467 | 1.5897 | 31.7101 | 19.9467 | 1.5897 | 33.4045 | 21.0125 | 1.5897 | 0.9774%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 44 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 45.9869 | 17.2089 | 2.6723 | 45.9869 | 17.2089 | 2.6723 | 48.444 | 18.1284 | 2.6723 | 0.977%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 115 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 121.6439 | 44.9779 | 2.7045 | 121.6439 | 44.9779 | 2.7045 | 128.1435 | 47.3811 | 2.7045 | 0.968%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.9263 | 1.9556 | 7.1214 | 13.9263 | 1.9556 | 7.1214 | 14.6704 | 2.06 | 7.1214 | 0.8924%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 3 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 22.1145 | 1.1733 | 18.8475 | 22.1145 | 1.1733 | 18.8475 | 23.2961 | 1.236 | 18.8475 | 0.7823%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 40 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 107.1917 | 15.6445 | 6.8517 | 107.1917 | 15.6445 | 6.8517 | 112.9191 | 16.4804 | 6.8517 | 0.9429%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 4 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 18.4509 | 1.5644 | 11.7938 | 18.4509 | 1.5644 | 11.7938 | 19.4367 | 1.648 | 11.7938 | 0.9974%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 17 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 40.0342 | 6.6489 | 6.0212 | 40.0342 | 6.6489 | 6.0212 | 42.1733 | 7.0042 | 6.0212 | 0.9922%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 8 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 15.1178 | 3.1289 | 4.8317 | 15.1178 | 3.1289 | 4.8317 | 15.9255 | 3.2961 | 4.8317 | 0.9193%
2026 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 4 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.7392 | 1.5644 | 1.1117 | 1.7392 | 1.5644 | 1.1117 | 1.8321 | 1.648 | 1.1117 | 0.9934%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 1 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.060854 | 0.39111 | 0.15559 | 0.060854 | 0.39111 | 0.15559 | 0.064106 | 0.41201 | 0.15559 | 0.9638%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 8 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 28.3235 | 3.1289 | 9.0522 | 28.3235 | 3.1289 | 9.0522 | 29.8368 | 3.2961 | 9.0522 | 0.9975%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 51 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 80.5201 | 19.9467 | 4.0368 | 80.5201 | 19.9467 | 4.0368 | 84.8224 | 21.0125 | 4.0368 | 0.9974%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 19 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.2815 | 7.4311 | 0.57616 | 4.2815 | 7.4311 | 0.57616 | 4.5103 | 7.8282 | 0.57616 | 0.901%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 60 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.4882 | 23.4667 | 0.36171 | 8.4882 | 23.4667 | 0.36171 | 8.9417 | 24.7206 | 0.36171 | 0.8573%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 18 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.1468 | 7.04 | 0.1629 | 1.1468 | 7.04 | 0.1629 | 1.2081 | 7.4162 | 0.1629 | 0.7047%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 38 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.5407 | 14.8623 | 0.10366 | 1.5407 | 14.8623 | 0.10366 | 1.623 | 15.6564 | 0.10366 | 0.5082%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 65 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 10.2406 | 25.4223 | 0.40282 | 10.2406 | 25.4223 | 0.40282 | 10.7877 | 26.7806 | 0.40282 | 0.8949%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 145 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 14.5454 | 56.7113 | 0.25648 | 14.5454 | 56.7113 | 0.25648 | 15.3226 | 59.7414 | 0.25648 | 0.8426%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 16.4236 | 25.8134 | 0.63624 | 16.4236 | 25.8134 | 0.63624 | 17.3012 | 27.1926 | 0.63624 | 0.9106%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 79 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.8295 | 30.8979 | 0.51232 | 15.8295 | 30.8979 | 0.51232 | 16.6753 | 32.5488 | 0.51232 | 0.9543%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 14.2272 | 27.3779 | 0.51966 | 14.2272 | 27.3779 | 0.51966 | 14.9874 | 28.8407 | 0.51966 | 0.9497%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 4 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.7626 | 1.5644 | 3.6835 | 5.7626 | 1.5644 | 3.6835 | 6.0705 | 1.648 | 3.6835 | 0.9907%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 46 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 46.2307 | 17.9912 | 2.5696 | 46.2307 | 17.9912 | 2.5696 | 48.7009 | 18.9525 | 2.5696 | 0.9915%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 42 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.825 | 16.4267 | 0.71987 | 11.825 | 16.4267 | 0.71987 | 12.4568 | 17.3044 | 0.71987 | 0.9792%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 39 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 9.206 | 15.2534 | 0.60354 | 9.206 | 15.2534 | 0.60354 | 9.6979 | 16.0684 | 0.60354 | 0.9662%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 6 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.4204 | 2.3467 | 1.0314 | 2.4204 | 2.3467 | 1.0314 | 2.5497 | 2.4721 | 1.0314 | 0.9706%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 68 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.756 | 26.5956 | 0.51723 | 13.756 | 26.5956 | 0.51723 | 14.491 | 28.0167 | 0.51723 | 0.9727%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 103 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 25.2035 | 40.2846 | 0.62564 | 25.2035 | 40.2846 | 0.62564 | 26.5502 | 42.437 | 0.62564 | 0.9578%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 39 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.624 | 15.2534 | 0.63094 | 9.624 | 15.2534 | 0.63094 | 10.1382 | 16.0684 | 0.63094 | 0.9712%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 3 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.97889 | 1.1733 | 0.83428 | 0.97889 | 1.1733 | 0.83428 | 1.0312 | 1.236 | 0.83428 | 0.9778%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 17 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 20.3743 | 6.6489 | 3.0643 | 20.3743 | 6.6489 | 3.0643 | 21.463 | 7.0042 | 3.0643 | 0.9872%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 45 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.7268 | 17.6 | 0.77993 | 13.7268 | 17.6 | 0.77993 | 14.4603 | 18.5404 | 0.77993 | 0.9782%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 127 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 247.9614 | 49.6712 | 4.9921 | 247.9614 | 49.6712 | 4.9921 | 261.2103 | 52.3252 | 4.9921 | 0.9891%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 75 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 63.2206 | 29.3334 | 2.1552 | 63.2206 | 29.3334 | 2.1552 | 66.5986 | 30.9007 | 2.1552 | 0.9941%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 30 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.4973 | 11.7334 | 0.38329 | 4.4973 | 11.7334 | 0.38329 | 4.7376 | 12.3603 | 0.38329 | 0.974%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 22 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.7358 | 8.6045 | 0.43417 | 3.7358 | 8.6045 | 0.43417 | 3.9354 | 9.0642 | 0.43417 | 0.9786%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 9 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.8339 | 3.52 | 1.3733 | 4.8339 | 3.52 | 1.3733 | 5.0922 | 3.7081 | 1.3733 | 0.9871%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 32 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 20.875 | 12.5156 | 1.6679 | 20.875 | 12.5156 | 1.6679 | 21.9903 | 13.1843 | 1.6679 | 0.9909%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 50 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 14.0738 | 19.5556 | 0.71968 | 14.0738 | 19.5556 | 0.71968 | 14.8257 | 20.6005 | 0.71968 | 0.8569%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 73 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 211.6306 | 28.5512 | 7.4123 | 211.6306 | 28.5512 | 7.4123 | 222.9383 | 30.0767 | 7.4123 | 0.9924%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 72 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 119.0085 | 28.1601 | 4.2261 | 119.0085 | 28.1601 | 4.2261 | 125.3673 | 29.6647 | 4.2261 | 0.9821%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 184.0533 | 22.6845 | 8.1136 | 184.0533 | 22.6845 | 8.1136 | 193.8875 | 23.8966 | 8.1136 | 0.99%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 16 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 13.2167 | 6.2578 | 2.112 | 13.2167 | 6.2578 | 2.112 | 13.9229 | 6.5922 | 2.112 | 0.9809%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 26 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 51.2828 | 10.1689 | 5.0431 | 51.2828 | 10.1689 | 5.0431 | 54.0229 | 10.7123 | 5.0431 | 0.9892%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 67 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 132.853 | 26.2045 | 5.0699 | 132.853 | 26.2045 | 5.0699 | 139.9515 | 27.6047 | 5.0699 | 0.9919%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 126 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 17.1386 | 49.2801 | 0.34778 | 17.1386 | 49.2801 | 0.34778 | 18.0544 | 51.9132 | 0.34778 | 0.8922%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 84 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 22.8579 | 32.8534 | 0.69575 | 22.8579 | 32.8534 | 0.69575 | 24.0792 | 34.6088 | 0.69575 | 0.8785%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 71 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 100.6039 | 27.769 | 3.6229 | 100.6039 | 27.769 | 3.6229 | 105.9793 | 29.2527 | 3.6229 | 0.9868%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 68 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 33.0238 | 26.5956 | 1.2417 | 33.0238 | 26.5956 | 1.2417 | 34.7883 | 28.0167 | 1.2417 | 0.9466%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 12.4717 | 27.3779 | 0.45554 | 12.4717 | 27.3779 | 0.45554 | 13.1381 | 28.8407 | 0.45554 | 0.9088%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 48 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 95.5917 | 18.7734 | 5.0919 | 95.5917 | 18.7734 | 5.0919 | 100.6993 | 19.7765 | 5.0919 | 0.9905%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 29 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 20.2056 | 11.3423 | 1.7814 | 20.2056 | 11.3423 | 1.7814 | 21.2852 | 11.9483 | 1.7814 | 0.9634%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 81 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 15.4856 | 31.6801 | 0.48881 | 15.4856 | 31.6801 | 0.48881 | 16.313 | 33.3728 | 0.48881 | 0.8429%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 155 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 30.5685 | 60.6224 | 0.50424 | 30.5685 | 60.6224 | 0.50424 | 32.2018 | 63.8615 | 0.50424 | 0.8937%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 35.1769 | 6.6489 | 5.2906 | 35.1769 | 6.6489 | 5.2906 | 37.0565 | 7.0042 | 5.2906 | 0.9991%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 77 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 28.7509 | 30.1156 | 0.95468 | 28.7509 | 30.1156 | 0.95468 | 30.2871 | 31.7248 | 0.95468 | 0.9216%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 93 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 25.0832 | 36.3734 | 0.6896 | 25.0832 | 36.3734 | 0.6896 | 26.4234 | 38.3169 | 0.6896 | 0.9611%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.7393 | 1.1733 | 5.7437 | 6.7393 | 1.1733 | 5.7437 | 7.0994 | 1.236 | 5.7437 | 0.9946%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 72 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 36.4187 | 28.1601 | 1.2933 | 36.4187 | 28.1601 | 1.2933 | 38.3646 | 29.6647 | 1.2933 | 0.9703%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 9 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 1.0134 | 3.52 | 0.28791 | 1.0134 | 3.52 | 0.28791 | 1.0676 | 3.7081 | 0.28791 | 0.334%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 4 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 19.5112 | 1.5644 | 12.4716 | 19.5112 | 1.5644 | 12.4716 | 20.5537 | 1.648 | 12.4716 | 0.9951%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 1 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 37.1986 | 0.39111 | 95.1098 | 37.1986 | 0.39111 | 95.1098 | 39.1862 | 0.41201 | 95.1098 | 0.9988%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 5 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.8178 | 1.9556 | 2.975 | 5.8178 | 1.9556 | 2.975 | 6.1286 | 2.06 | 2.975 | 0.9868%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 12 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 42.518 | 4.6933 | 9.0592 | 42.518 | 4.6933 | 9.0592 | 44.7898 | 4.9441 | 9.0592 | 0.9945%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 31 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 21.4759 | 12.1245 | 1.7713 | 21.4759 | 12.1245 | 1.7713 | 22.6234 | 12.7723 | 1.7713 | 0.9686%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 18 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 91.3747 | 7.04 | 12.9793 | 91.3747 | 7.04 | 12.9793 | 96.257 | 7.4162 | 12.9793 | 0.9959%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 12.3393 | 8.9956 | 1.3717 | 12.3393 | 8.9956 | 1.3717 | 12.9986 | 9.4762 | 1.3717 | 0.9515%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 137 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 68.2692 | 53.5824 | 1.2741 | 68.2692 | 53.5824 | 1.2741 | 71.9169 | 56.4453 | 1.2741 | 0.9662%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 212 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 749.8113 | 82.9158 | 9.043 | 749.8113 | 82.9158 | 9.043 | 789.8747 | 87.3461 | 9.043 | 0.9925%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 34.2741 | 5.0845 | 6.741 | 34.2741 | 5.0845 | 6.741 | 36.1055 | 5.3561 | 6.741 | 0.9927%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 81 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 428.6915 | 31.6801 | 13.5319 | 428.6915 | 31.6801 | 13.5319 | 451.5971 | 33.3728 | 13.5319 | 0.9963%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.3843 | 1.1733 | 2.0321 | 2.3843 | 1.1733 | 2.0321 | 2.5117 | 1.236 | 2.0321 | 0.8656%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 132 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 68.0491 | 51.6268 | 1.3181 | 68.0491 | 51.6268 | 1.3181 | 71.685 | 54.3853 | 1.3181 | 0.9605%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 1 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 46.2897 | 0.39111 | 118.3541 | 46.2897 | 0.39111 | 118.3541 | 48.763 | 0.41201 | 118.3541 | 0.9985%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 1220 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 154.7093 | 477.1568 | 0.32423 | 154.7093 | 477.1568 | 0.32423 | 162.9756 | 502.652 | 0.32423 | 0.967%
2026 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.6265 | 0.39111 | 4.1586 | 1.6265 | 0.39111 | 4.1586 | 1.7134 | 0.41201 | 4.1586 | 0.9937%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 52 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 18.1259 | 20.3378 | 0.89124 | 18.1259 | 20.3378 | 0.89124 | 19.0944 | 21.4245 | 0.89124 | 0.9498%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 84 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 59.885 | 32.8534 | 1.8228 | 59.885 | 32.8534 | 1.8228 | 63.0847 | 34.6088 | 1.8228 | 0.9826%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 57 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 18.007 | 22.2934 | 0.80773 | 18.007 | 22.2934 | 0.80773 | 18.9692 | 23.4846 | 0.80773 | 0.9106%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 17 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 4.0406 | 6.6489 | 0.60771 | 4.0406 | 6.6489 | 0.60771 | 4.2565 | 7.0042 | 0.60771 | 0.7897%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 6 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.3877 | 2.3467 | 3.1481 | 7.3877 | 2.3467 | 3.1481 | 7.7824 | 2.4721 | 3.1481 | 0.9819%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 52 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 32.3646 | 20.3378 | 1.5913 | 32.3646 | 20.3378 | 1.5913 | 34.0939 | 21.4245 | 1.5913 | 0.9768%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0786 | 0.39111 | 2.7577 | 1.0786 | 0.39111 | 2.7577 | 1.1362 | 0.41201 | 2.7577 | 0.9298%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 8 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.5257 | 3.1289 | 0.48761 | 1.5257 | 3.1289 | 0.48761 | 1.6072 | 3.2961 | 0.48761 | 0.8171%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 25.6087 | 9.3867 | 2.7282 | 25.6087 | 9.3867 | 2.7282 | 26.977 | 9.8882 | 2.7282 | 0.983%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 151 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 48.405 | 59.0579 | 0.81962 | 48.405 | 59.0579 | 0.81962 | 50.9914 | 62.2135 | 0.81962 | 0.9868%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 57 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 28.6233 | 22.2934 | 1.2839 | 28.6233 | 22.2934 | 1.2839 | 30.1527 | 23.4846 | 1.2839 | 0.9884%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 47 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.692 | 18.3823 | 0.36405 | 6.692 | 18.3823 | 0.36405 | 7.0496 | 19.3645 | 0.36405 | 0.9757%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 32 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 4.0561 | 12.5156 | 0.32408 | 4.0561 | 12.5156 | 0.32408 | 4.2728 | 13.1843 | 0.32408 | 0.9496%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 79 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 19.1889 | 30.8979 | 0.62104 | 19.1889 | 30.8979 | 0.62104 | 20.2142 | 32.5488 | 0.62104 | 0.859%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 40 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 46.8623 | 15.6445 | 2.9955 | 46.8623 | 15.6445 | 2.9955 | 49.3662 | 16.4804 | 2.9955 | 0.9946%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 14 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 36.9882 | 5.4756 | 6.7551 | 36.9882 | 5.4756 | 6.7551 | 38.9646 | 5.7681 | 6.7551 | 0.8863%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 48 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 222.188 | 18.7734 | 11.8353 | 222.188 | 18.7734 | 11.8353 | 234.0599 | 19.7765 | 11.8353 | 0.9837%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 48 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 91.5381 | 18.7734 | 4.876 | 91.5381 | 18.7734 | 4.876 | 96.4291 | 19.7765 | 4.876 | 0.9873%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 37 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 26.1976 | 14.4711 | 1.8103 | 26.1976 | 14.4711 | 1.8103 | 27.5973 | 15.2444 | 1.8103 | 0.9726%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 25 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 21.2648 | 9.7778 | 2.1748 | 21.2648 | 9.7778 | 2.1748 | 22.401 | 10.3002 | 2.1748 | 0.9861%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 51 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 49.8843 | 19.9467 | 2.5009 | 49.8843 | 19.9467 | 2.5009 | 52.5497 | 21.0125 | 2.5009 | 0.9807%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 124 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 199.1398 | 48.4979 | 4.1062 | 199.1398 | 48.4979 | 4.1062 | 209.7801 | 51.0892 | 4.1062 | 0.9836%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 56 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 64.6625 | 21.9023 | 2.9523 | 64.6625 | 21.9023 | 2.9523 | 68.1175 | 23.0725 | 2.9523 | 0.9784%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 16 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 34.4579 | 6.2578 | 5.5064 | 34.4579 | 6.2578 | 5.5064 | 36.299 | 6.5922 | 5.5064 | 0.994%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 62 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 267.7119 | 24.249 | 11.0401 | 267.7119 | 24.249 | 11.0401 | 282.0161 | 25.5446 | 11.0401 | 0.9934%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 71 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 255.4695 | 27.769 | 9.1998 | 255.4695 | 27.769 | 9.1998 | 269.1196 | 29.2527 | 9.1998 | 0.9889%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 13 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 23.8534 | 5.0845 | 4.6914 | 23.8534 | 5.0845 | 4.6914 | 25.1279 | 5.3561 | 4.6914 | 0.9883%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 165 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 292.0914 | 64.5335 | 4.5262 | 292.0914 | 64.5335 | 4.5262 | 307.6982 | 67.9816 | 4.5262 | 0.9911%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 182 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 618.2973 | 71.1824 | 8.6861 | 618.2973 | 71.1824 | 8.6861 | 651.3338 | 74.9858 | 8.6861 | 0.9893%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 21 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 8.0494 | 8.2134 | 0.98004 | 8.0494 | 8.2134 | 0.98004 | 8.4795 | 8.6522 | 0.98004 | 0.9808%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 19 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.9204 | 7.4311 | 2.0078 | 14.9204 | 7.4311 | 2.0078 | 15.7176 | 7.8282 | 2.0078 | 0.9867%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 10.2731 | 8.9956 | 1.142 | 10.2731 | 8.9956 | 1.142 | 10.822 | 9.4762 | 1.142 | 0.9646%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 72 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 58.7462 | 28.1601 | 2.0862 | 58.7462 | 28.1601 | 2.0862 | 61.8851 | 29.6647 | 2.0862 | 0.9824%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 17 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.8035 | 6.6489 | 1.0232 | 6.8035 | 6.6489 | 1.0232 | 7.167 | 7.0042 | 1.0232 | 0.6927%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 18 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.5462 | 7.04 | 0.50372 | 3.5462 | 7.04 | 0.50372 | 3.7357 | 7.4162 | 0.50372 | 0.9876%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 15 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 11.0889 | 5.8667 | 1.8902 | 11.0889 | 5.8667 | 1.8902 | 11.6814 | 6.1801 | 1.8902 | 0.9838%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 6 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.451 | 2.3467 | 3.1751 | 7.451 | 2.3467 | 3.1751 | 7.8491 | 2.4721 | 3.1751 | 0.987%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 17 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.4814 | 6.6489 | 0.52361 | 3.4814 | 6.6489 | 0.52361 | 3.6675 | 7.0042 | 0.52361 | 0.9688%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 73 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 41.4475 | 28.5512 | 1.4517 | 41.4475 | 28.5512 | 1.4517 | 43.6621 | 30.0767 | 1.4517 | 0.9791%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 50 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 35.3681 | 19.5556 | 1.8086 | 35.3681 | 19.5556 | 1.8086 | 37.2578 | 20.6005 | 1.8086 | 0.9907%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 104 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 33.8556 | 40.6757 | 0.83233 | 33.8556 | 40.6757 | 0.83233 | 35.6645 | 42.849 | 0.83233 | 0.9682%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 15 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 6.0425 | 5.8667 | 1.03 | 6.0425 | 5.8667 | 1.03 | 6.3654 | 6.1801 | 1.03 | 0.6596%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 71 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 30.5472 | 27.769 | 1.1 | 30.5472 | 27.769 | 1.1 | 32.1793 | 29.2527 | 1.1 | 0.9454%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 33 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 12.0051 | 12.9067 | 0.93015 | 12.0051 | 12.9067 | 0.93015 | 12.6466 | 13.5963 | 0.93015 | 0.9251%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 2 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.98533 | 0.78222 | 1.2596 | 0.98533 | 0.78222 | 1.2596 | 1.038 | 0.82402 | 1.2596 | 0.9818%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 99 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 34.3178 | 38.7201 | 0.8863 | 34.3178 | 38.7201 | 0.8863 | 36.1515 | 40.789 | 0.8863 | 0.9585%
2026 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 3 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.4091 | 1.1733 | 0.34867 | 0.4091 | 1.1733 | 0.34867 | 0.43096 | 1.236 | 0.34867 | 0.8666%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 29 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 49.8241 | 11.3423 | 4.3928 | 49.8241 | 11.3423 | 4.3928 | 52.4863 | 11.9483 | 4.3928 | 0.9855%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 40 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.865 | 15.6445 | 1.078 | 16.865 | 15.6445 | 1.078 | 17.7662 | 16.4804 | 1.078 | 0.878%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 3 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.6479 | 1.1733 | 5.6658 | 6.6479 | 1.1733 | 5.6658 | 7.0031 | 1.236 | 5.6658 | 0.9241%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 20.9129 | 2.7378 | 7.6386 | 20.9129 | 2.7378 | 7.6386 | 22.0303 | 2.8841 | 7.6386 | 0.9107%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 26 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 43.4106 | 10.1689 | 4.2689 | 43.4106 | 10.1689 | 4.2689 | 45.7301 | 10.7123 | 4.2689 | 0.9555%
2026 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 2 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.37322 | 0.78222 | 0.47712 | 0.37322 | 0.78222 | 0.47712 | 0.39316 | 0.82402 | 0.47712 | 0.8469%
2026 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 4 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.43274 | 1.5644 | 0.27661 | 0.43274 | 1.5644 | 0.27661 | 0.45586 | 1.648 | 0.27661 | 0.1628%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 1 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.8639 | 0.39111 | 7.3224 | 2.8639 | 0.39111 | 7.3224 | 3.0169 | 0.41201 | 7.3224 | 0.9927%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 138 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 32.8093 | 53.9735 | 0.60788 | 32.8093 | 53.9735 | 0.60788 | 34.5623 | 56.8574 | 0.60788 | 0.9548%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 245 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 129.861 | 95.8225 | 1.3552 | 129.861 | 95.8225 | 1.3552 | 136.7997 | 100.9424 | 1.3552 | 0.9814%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 229 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 51.5398 | 89.5647 | 0.57545 | 51.5398 | 89.5647 | 0.57545 | 54.2936 | 94.3502 | 0.57545 | 0.9699%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 128.0651 | 35.9823 | 3.5591 | 128.0651 | 35.9823 | 3.5591 | 134.9078 | 37.9049 | 3.5591 | 0.9928%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 107 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 105.6518 | 41.849 | 2.5246 | 105.6518 | 41.849 | 2.5246 | 111.297 | 44.085 | 2.5246 | 0.9888%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 222.6577 | 22.6845 | 9.8154 | 222.6577 | 22.6845 | 9.8154 | 234.5546 | 23.8966 | 9.8154 | 0.9925%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 22 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 86.9953 | 8.6045 | 10.1105 | 86.9953 | 8.6045 | 10.1105 | 91.6436 | 9.0642 | 10.1105 | 0.9973%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 76 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 176.4312 | 29.7245 | 5.9355 | 176.4312 | 29.7245 | 5.9355 | 185.8581 | 31.3127 | 5.9355 | 0.9936%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 40 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 85.7598 | 15.6445 | 5.4818 | 85.7598 | 15.6445 | 5.4818 | 90.342 | 16.4804 | 5.4818 | 0.9749%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 23.8334 | 2.7378 | 8.7054 | 23.8334 | 2.7378 | 8.7054 | 25.1069 | 2.8841 | 8.7054 | 0.9918%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 1 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 21.1215 | 0.39111 | 54.0037 | 21.1215 | 0.39111 | 54.0037 | 22.2501 | 0.41201 | 54.0037 | 0.9993%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 7 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.8485 | 2.7378 | 6.1541 | 16.8485 | 2.7378 | 6.1541 | 17.7488 | 2.8841 | 6.1541 | 0.8869%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 23 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 40.9814 | 8.9956 | 4.5557 | 40.9814 | 8.9956 | 4.5557 | 43.1711 | 9.4762 | 4.5557 | 0.943%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 1 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.788 | 0.39111 | 7.1285 | 2.788 | 0.39111 | 7.1285 | 2.937 | 0.41201 | 7.1285 | 0.6284%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 42 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 128.3764 | 16.4267 | 7.8151 | 128.3764 | 16.4267 | 7.8151 | 135.2357 | 17.3044 | 7.8151 | 0.9943%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 121 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 194.0236 | 47.3246 | 4.0998 | 194.0236 | 47.3246 | 4.0998 | 204.3905 | 49.8532 | 4.0998 | 0.9917%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 15 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 30.8577 | 5.8667 | 5.2598 | 30.8577 | 5.8667 | 5.2598 | 32.5065 | 6.1801 | 5.2598 | 0.8854%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 64 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 70.4778 | 25.0312 | 2.8156 | 70.4778 | 25.0312 | 2.8156 | 74.2435 | 26.3686 | 2.8156 | 0.985%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.9537 | 6.2578 | 2.07 | 12.9537 | 6.2578 | 2.07 | 13.6459 | 6.5922 | 2.07 | 0.7994%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 50 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 50.9054 | 19.5556 | 2.6031 | 50.9054 | 19.5556 | 2.6031 | 53.6253 | 20.6005 | 2.6031 | 0.9814%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 140 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 149.3338 | 54.7557 | 2.7273 | 149.3338 | 54.7557 | 2.7273 | 157.313 | 57.6814 | 2.7273 | 0.9776%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 84.5967 | 35.9823 | 2.3511 | 84.5967 | 35.9823 | 2.3511 | 89.1168 | 37.9049 | 2.3511 | 0.9541%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 5 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.8235 | 1.9556 | 6.0461 | 11.8235 | 1.9556 | 6.0461 | 12.4552 | 2.06 | 6.0461 | 0.9906%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 11 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 48.4832 | 4.3022 | 11.2693 | 48.4832 | 4.3022 | 11.2693 | 51.0737 | 4.5321 | 11.2693 | 0.9968%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 3 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 8.0059 | 1.1733 | 6.8232 | 8.0059 | 1.1733 | 6.8232 | 8.4336 | 1.236 | 6.8232 | 0.9549%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 84 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 158.9726 | 32.8534 | 4.8388 | 158.9726 | 32.8534 | 4.8388 | 167.4668 | 34.6088 | 4.8388 | 0.9879%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 116 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 164.5511 | 45.369 | 3.6269 | 164.5511 | 45.369 | 3.6269 | 173.3433 | 47.7931 | 3.6269 | 0.9747%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 116 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 96.5713 | 45.369 | 2.1286 | 96.5713 | 45.369 | 2.1286 | 101.7312 | 47.7931 | 2.1286 | 0.9704%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 94 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 109.6988 | 36.7645 | 2.9838 | 109.6988 | 36.7645 | 2.9838 | 115.5602 | 38.7289 | 2.9838 | 0.9781%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 4 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.5598 | 1.5644 | 3.5539 | 5.5598 | 1.5644 | 3.5539 | 5.8569 | 1.648 | 3.5539 | 0.9721%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 3 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.7834 | 1.1733 | 10.8949 | 12.7834 | 1.1733 | 10.8949 | 13.4665 | 1.236 | 10.8949 | 0.9966%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 99 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 353.6518 | 38.7201 | 9.1335 | 353.6518 | 38.7201 | 9.1335 | 372.5479 | 40.789 | 9.1335 | 0.9859%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 4 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 12.3554 | 1.5644 | 7.8976 | 12.3554 | 1.5644 | 7.8976 | 13.0156 | 1.648 | 7.8976 | 0.8901%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 2 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.6574 | 0.78222 | 2.1189 | 1.6574 | 0.78222 | 2.1189 | 1.746 | 0.82402 | 2.1189 | 0.1879%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 65 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 26.3874 | 25.4223 | 1.038 | 26.3874 | 25.4223 | 1.038 | 27.7974 | 26.7806 | 1.038 | 0.8818%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 21 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 17.3358 | 8.2134 | 2.1107 | 17.3358 | 8.2134 | 2.1107 | 18.2621 | 8.6522 | 2.1107 | 0.9783%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 90 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 59.8337 | 35.2001 | 1.6998 | 59.8337 | 35.2001 | 1.6998 | 63.0306 | 37.0809 | 1.6998 | 0.9847%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 2 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 12.3633 | 0.78222 | 15.8054 | 12.3633 | 0.78222 | 15.8054 | 13.0239 | 0.82402 | 15.8054 | 0.9597%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 15 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 32.7047 | 5.8667 | 5.5746 | 32.7047 | 5.8667 | 5.5746 | 34.4521 | 6.1801 | 5.5746 | 0.9745%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 6 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 5.0723 | 2.3467 | 2.1615 | 5.0723 | 2.3467 | 2.1615 | 5.3433 | 2.4721 | 2.1615 | 0.9134%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 27 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 44.4079 | 10.56 | 4.2053 | 44.4079 | 10.56 | 4.2053 | 46.7806 | 11.1243 | 4.2053 | 0.98%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 26 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 50.2962 | 10.1689 | 4.9461 | 50.2962 | 10.1689 | 4.9461 | 52.9836 | 10.7123 | 4.9461 | 0.9857%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 26 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.8191 | 10.1689 | 1.654 | 16.8191 | 10.1689 | 1.654 | 17.7178 | 10.7123 | 1.654 | 0.9609%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 1 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.014671 | 0.39111 | 0.037511 | 0.014671 | 0.39111 | 0.037511 | 0.015455 | 0.41201 | 0.037511 | 0.01745%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 31 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.9098 | 12.1245 | 0.5699 | 6.9098 | 12.1245 | 0.5699 | 7.2789 | 12.7723 | 0.5699 | 0.8492%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 22 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.9086 | 8.6045 | 0.33803 | 2.9086 | 8.6045 | 0.33803 | 3.064 | 9.0642 | 0.33803 | 0.5795%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 161 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 97.67 | 62.9691 | 1.5511 | 97.67 | 62.9691 | 1.5511 | 102.8886 | 66.3336 | 1.5511 | 0.8848%
2026 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 14 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 6.494 | 5.4756 | 1.186 | 6.494 | 5.4756 | 1.186 | 6.841 | 5.7681 | 1.186 | 0.9662%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 1 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 5.1901 | 0.39111 | 13.2701 | 5.1901 | 0.39111 | 13.2701 | 5.4674 | 0.41201 | 13.2701 | 0.9893%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 12 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 4.1351 | 4.6933 | 0.88106 | 4.1351 | 4.6933 | 0.88106 | 4.3561 | 4.9441 | 0.88106 | 0.9131%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 16 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.68786 | 6.2578 | 0.10992 | 0.68786 | 6.2578 | 0.10992 | 0.72461 | 6.5922 | 0.10992 | 0.51%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 13 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 3.0769 | 5.0845 | 0.60517 | 3.0769 | 5.0845 | 0.60517 | 3.2414 | 5.3561 | 0.60517 | 0.9662%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 102 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 31.8067 | 39.8934 | 0.79729 | 31.8067 | 39.8934 | 0.79729 | 33.5062 | 42.025 | 0.79729 | 0.9767%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 90 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.853 | 35.2001 | 0.10946 | 3.853 | 35.2001 | 0.10946 | 4.0589 | 37.0809 | 0.10946 | 0.7071%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 85 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 87.2546 | 33.2445 | 2.6246 | 87.2546 | 33.2445 | 2.6246 | 91.9168 | 35.0208 | 2.6246 | 0.9496%
2026 | 445 | 445-1315 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 0.26142 | 0 | 0 | 0.26142 | 0 | 0.24938 | 0.39111 | 0.63762 | 0.24938 | 0.39111 | 0.63762 | 0.2627 | 0.41201 | 0.63762 | 0.9959%
2026 | 445 | 445-1323 | Tier-2 | Tier-2---18 | Tier-2---12 | 1 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 0.77964 | 0 | 0 | 0.77964 | 0 | 0.74372 | 0.39111 | 1.9016 | 0.74372 | 0.39111 | 1.9016 | 0.78346 | 0.41201 | 1.9016 | 0.9926%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 76 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 66.4731 | 29.7245 | 2.2363 | 66.4731 | 29.7245 | 2.2363 | 70.0248 | 31.3127 | 2.2363 | 0.9611%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 43 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 13.5715 | 16.8178 | 0.80697 | 13.5715 | 16.8178 | 0.80697 | 14.2966 | 17.7164 | 0.80697 | 0.8872%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 116 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 96.9373 | 45.369 | 2.1366 | 96.9373 | 45.369 | 2.1366 | 102.1167 | 47.7931 | 2.1366 | 0.9569%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 65 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 14.2791 | 25.4223 | 0.56168 | 14.2791 | 25.4223 | 0.56168 | 15.0421 | 26.7806 | 0.56168 | 0.8473%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 91 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 30.7191 | 35.5912 | 0.86311 | 30.7191 | 35.5912 | 0.86311 | 32.3605 | 37.4929 | 0.86311 | 0.8754%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 156 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 37.1637 | 61.0135 | 0.60911 | 37.1637 | 61.0135 | 0.60911 | 39.1494 | 64.2735 | 0.60911 | 0.8812%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 9 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 12.5395 | 3.52 | 3.5623 | 12.5395 | 3.52 | 3.5623 | 13.2095 | 3.7081 | 3.5623 | 0.9724%
2026 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.16597 | 0 | 0 | 0.16597 | 0 | 0.15833 | 0.39111 | 0.40481 | 0.15833 | 0.39111 | 0.40481 | 0.16679 | 0.41201 | 0.40481 | 0.9941%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 9 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 11.2563 | 3.52 | 3.1978 | 11.2563 | 3.52 | 3.1978 | 11.8578 | 3.7081 | 3.1978 | 0.9739%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 43 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 22.903 | 16.8178 | 1.3618 | 22.903 | 16.8178 | 1.3618 | 24.1267 | 17.7164 | 1.3618 | 0.9191%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 85 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 11.2627 | 33.2445 | 0.33878 | 11.2627 | 33.2445 | 0.33878 | 11.8645 | 35.0208 | 0.33878 | 0.557%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.7837 | 19.1645 | 0.19743 | 3.7837 | 19.1645 | 0.19743 | 3.9859 | 20.1885 | 0.19743 | 0.7618%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 45 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.7608 | 17.6 | 0.2705 | 4.7608 | 17.6 | 0.2705 | 5.0152 | 18.5404 | 0.2705 | 0.7912%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 224 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 79.6266 | 87.6091 | 0.90888 | 79.6266 | 87.6091 | 0.90888 | 83.8812 | 92.2902 | 0.90888 | 0.9168%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 106 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 50.3074 | 41.4579 | 1.2135 | 50.3074 | 41.4579 | 1.2135 | 52.9954 | 43.673 | 1.2135 | 0.9343%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 147 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 58.0947 | 57.4935 | 1.0105 | 58.0947 | 57.4935 | 1.0105 | 61.1988 | 60.5654 | 1.0105 | 0.9049%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 22 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.8342 | 8.6045 | 1.6078 | 13.8342 | 8.6045 | 1.6078 | 14.5734 | 9.0642 | 1.6078 | 0.9697%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 7 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.768 | 2.7378 | 2.1068 | 5.768 | 2.7378 | 2.1068 | 6.0762 | 2.8841 | 2.1068 | 0.967%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 34 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 49.5677 | 13.2978 | 3.7275 | 49.5677 | 13.2978 | 3.7275 | 52.2162 | 14.0083 | 3.7275 | 0.9877%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 45 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 21.1459 | 17.6 | 1.2015 | 21.1459 | 17.6 | 1.2015 | 22.2758 | 18.5404 | 1.2015 | 0.9555%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 26 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 78.3224 | 10.1689 | 7.7021 | 78.3224 | 10.1689 | 7.7021 | 82.5073 | 10.7123 | 7.7021 | 0.9923%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 5 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 7.0106 | 1.9556 | 3.5849 | 7.0106 | 1.9556 | 3.5849 | 7.3851 | 2.06 | 3.5849 | 0.9277%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 2 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 10.2883 | 0.78222 | 13.1526 | 10.2883 | 0.78222 | 13.1526 | 10.838 | 0.82402 | 13.1526 | 0.9525%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 2 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 26.9189 | 0.78222 | 34.4132 | 26.9189 | 0.78222 | 34.4132 | 28.3572 | 0.82402 | 34.4132 | 0.9993%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 1 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 32.7275 | 0.39111 | 83.678 | 32.7275 | 0.39111 | 83.678 | 34.4762 | 0.41201 | 83.678 | 0.997%
2026 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.81736 | 0.78222 | 1.0449 | 0.81736 | 0.78222 | 1.0449 | 0.86104 | 0.82402 | 1.0449 | 0.9735%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 20 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 13.019 | 7.8222 | 1.6644 | 13.019 | 7.8222 | 1.6644 | 13.7146 | 8.2402 | 1.6644 | 0.9902%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 20 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 49.3848 | 7.8222 | 6.3134 | 49.3848 | 7.8222 | 6.3134 | 52.0235 | 8.2402 | 6.3134 | 0.9833%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 53 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 158.6864 | 20.7289 | 7.6553 | 158.6864 | 20.7289 | 7.6553 | 167.1652 | 21.8365 | 7.6553 | 0.9937%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 6 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 38.5309 | 2.3467 | 16.4194 | 38.5309 | 2.3467 | 16.4194 | 40.5897 | 2.4721 | 16.4194 | 0.9496%
2026 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 3 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.6496 | 1.1733 | 1.4059 | 1.6496 | 1.1733 | 1.4059 | 1.7378 | 1.236 | 1.4059 | 0.216%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 1 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.9397 | 0.39111 | 4.9593 | 1.9397 | 0.39111 | 4.9593 | 2.0433 | 0.41201 | 4.9593 | 0.9963%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 2 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.9644 | 0.78222 | 8.9034 | 6.9644 | 0.78222 | 8.9034 | 7.3365 | 0.82402 | 8.9034 | 0.9951%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 47 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 27.6613 | 18.3823 | 1.5048 | 27.6613 | 18.3823 | 1.5048 | 29.1393 | 19.3645 | 1.5048 | 0.9734%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 27 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.8205 | 10.56 | 1.3088 | 13.8205 | 10.56 | 1.3088 | 14.5589 | 11.1243 | 1.3088 | 0.9797%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 129 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 24.3479 | 50.4535 | 0.48258 | 24.3479 | 50.4535 | 0.48258 | 25.6488 | 53.1493 | 0.48258 | 0.9676%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 84 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 30.1957 | 32.8534 | 0.9191 | 30.1957 | 32.8534 | 0.9191 | 31.8091 | 34.6088 | 0.9191 | 0.9272%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 31 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 15.3089 | 12.1245 | 1.2626 | 15.3089 | 12.1245 | 1.2626 | 16.1269 | 12.7723 | 1.2626 | 0.9829%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 53 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 62.3968 | 20.7289 | 3.0101 | 62.3968 | 20.7289 | 3.0101 | 65.7308 | 21.8365 | 3.0101 | 0.9672%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.5208 | 1.1733 | 4.7052 | 5.5208 | 1.1733 | 4.7052 | 5.8158 | 1.236 | 4.7052 | 0.7734%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 19 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 19.1856 | 7.4311 | 2.5818 | 19.1856 | 7.4311 | 2.5818 | 20.2108 | 7.8282 | 2.5818 | 0.9648%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 89 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 46.0042 | 34.809 | 1.3216 | 46.0042 | 34.809 | 1.3216 | 48.4623 | 36.6689 | 1.3216 | 0.9649%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 74 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 19.0309 | 28.9423 | 0.65755 | 19.0309 | 28.9423 | 0.65755 | 20.0478 | 30.4887 | 0.65755 | 0.9757%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 49 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 104.6914 | 19.1645 | 5.4628 | 104.6914 | 19.1645 | 5.4628 | 110.2852 | 20.1885 | 5.4628 | 0.9669%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 87 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 79.0871 | 34.0268 | 2.3243 | 79.0871 | 34.0268 | 2.3243 | 83.3128 | 35.8449 | 2.3243 | 0.9779%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 73 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 82.5858 | 28.5512 | 2.8926 | 82.5858 | 28.5512 | 2.8926 | 86.9984 | 30.0767 | 2.8926 | 0.9936%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 25 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 52.9434 | 9.7778 | 5.4147 | 52.9434 | 9.7778 | 5.4147 | 55.7723 | 10.3002 | 5.4147 | 0.9878%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 42 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 116.0523 | 16.4267 | 7.0649 | 116.0523 | 16.4267 | 7.0649 | 122.2532 | 17.3044 | 7.0649 | 0.9938%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 37 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 85.1588 | 14.4711 | 5.8847 | 85.1588 | 14.4711 | 5.8847 | 89.7089 | 15.2444 | 5.8847 | 0.9905%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 51.8857 | 0.39111 | 132.6619 | 51.8857 | 0.39111 | 132.6619 | 54.658 | 0.41201 | 132.6619 | 0.9644%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 46 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 52.0453 | 17.9912 | 2.8928 | 52.0453 | 17.9912 | 2.8928 | 54.8261 | 18.9525 | 2.8928 | 0.9978%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 114 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 107.7138 | 44.5868 | 2.4158 | 107.7138 | 44.5868 | 2.4158 | 113.4691 | 46.9691 | 2.4158 | 0.9977%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 89 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 129.4684 | 34.809 | 3.7194 | 129.4684 | 34.809 | 3.7194 | 136.386 | 36.6689 | 3.7194 | 0.9899%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 82.4531 | 32.8534 | 2.5097 | 82.4531 | 32.8534 | 2.5097 | 86.8586 | 34.6088 | 2.5097 | 0.982%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 283 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 381.43 | 110.6847 | 3.4461 | 381.43 | 110.6847 | 3.4461 | 401.8103 | 116.5988 | 3.4461 | 0.9903%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 92 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 171.1238 | 35.9823 | 4.7558 | 171.1238 | 35.9823 | 4.7558 | 180.2671 | 37.9049 | 4.7558 | 0.9555%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 124 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 244.0922 | 48.4979 | 5.033 | 244.0922 | 48.4979 | 5.033 | 257.1344 | 51.0892 | 5.033 | 0.994%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 112 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 23.3101 | 43.8046 | 0.53214 | 23.3101 | 43.8046 | 0.53214 | 24.5556 | 46.1451 | 0.53214 | 0.936%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 188 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 37.4045 | 73.5291 | 0.5087 | 37.4045 | 73.5291 | 0.5087 | 39.403 | 77.4578 | 0.5087 | 0.938%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 55 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 5.1753 | 21.5112 | 0.24059 | 5.1753 | 21.5112 | 0.24059 | 5.4518 | 22.6605 | 0.24059 | 0.8718%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 78 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 14.4092 | 30.5067 | 0.47233 | 14.4092 | 30.5067 | 0.47233 | 15.1791 | 32.1368 | 0.47233 | 0.9279%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 84 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 57.5552 | 32.8534 | 1.7519 | 57.5552 | 32.8534 | 1.7519 | 60.6304 | 34.6088 | 1.7519 | 0.9729%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 90 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 144.2009 | 35.2001 | 4.0966 | 144.2009 | 35.2001 | 4.0966 | 151.9058 | 37.0809 | 4.0966 | 0.9856%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 21 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 23.0424 | 8.2134 | 2.8055 | 23.0424 | 8.2134 | 2.8055 | 24.2735 | 8.6522 | 2.8055 | 0.9864%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 56 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 53.8256 | 21.9023 | 2.4575 | 53.8256 | 21.9023 | 2.4575 | 56.7015 | 23.0725 | 2.4575 | 0.9841%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 93 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 99.3275 | 36.3734 | 2.7308 | 99.3275 | 36.3734 | 2.7308 | 104.6347 | 38.3169 | 2.7308 | 0.9831%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 87.2089 | 32.8534 | 2.6545 | 87.2089 | 32.8534 | 2.6545 | 91.8686 | 34.6088 | 2.6545 | 0.9843%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.16865 | 0.78222 | 0.2156 | 0.16865 | 0.78222 | 0.2156 | 0.17766 | 0.82402 | 0.2156 | 0.9934%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 32 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 29.8416 | 12.5156 | 2.3844 | 29.8416 | 12.5156 | 2.3844 | 31.436 | 13.1843 | 2.3844 | 0.9977%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 15 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 16.2275 | 5.8667 | 2.766 | 16.2275 | 5.8667 | 2.766 | 17.0946 | 6.1801 | 2.766 | 0.9957%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 4 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 18.457 | 1.5644 | 11.7978 | 18.457 | 1.5644 | 11.7978 | 19.4432 | 1.648 | 11.7978 | 0.9986%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 46 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 20.9297 | 17.9912 | 1.1633 | 20.9297 | 17.9912 | 1.1633 | 22.048 | 18.9525 | 1.1633 | 0.9923%
2026 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 1 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 0.41445 | 0 | 0 | 0.41445 | 0 | 0.39536 | 0.39111 | 1.0109 | 0.39536 | 0.39111 | 1.0109 | 0.41648 | 0.41201 | 1.0109 | 0.9749%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 60 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 136.5755 | 23.4667 | 5.82 | 136.5755 | 23.4667 | 5.82 | 143.873 | 24.7206 | 5.82 | 0.9856%
2026 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 1 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 56.9533 | 0 | 0 | 56.9533 | 0 | 54.3295 | 0.39111 | 138.9104 | 54.3295 | 0.39111 | 138.9104 | 57.2325 | 0.41201 | 138.9104 | 0.9998%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 13 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 68.3702 | 5.0845 | 13.4469 | 68.3702 | 5.0845 | 13.4469 | 72.0233 | 5.3561 | 13.4469 | 0.9951%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 37 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 82.1782 | 14.4711 | 5.6788 | 82.1782 | 14.4711 | 5.6788 | 86.5691 | 15.2444 | 5.6788 | 0.9433%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 5 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 29.5835 | 1.9556 | 15.1279 | 29.5835 | 1.9556 | 15.1279 | 31.1642 | 2.06 | 15.1279 | 0.9258%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 34 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 116.6696 | 13.2978 | 8.7736 | 116.6696 | 13.2978 | 8.7736 | 122.9034 | 14.0083 | 8.7736 | 0.9926%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 20 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 19.4046 | 7.8222 | 2.4807 | 19.4046 | 7.8222 | 2.4807 | 20.4414 | 8.2402 | 2.4807 | 0.9747%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 77 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.8721 | 30.1156 | 0.36101 | 10.8721 | 30.1156 | 0.36101 | 11.453 | 31.7248 | 0.36101 | 0.7093%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 28 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 91.0778 | 10.9511 | 8.3167 | 91.0778 | 10.9511 | 8.3167 | 95.9442 | 11.5363 | 8.3167 | 0.9829%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 59 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 174.0462 | 23.0756 | 7.5424 | 174.0462 | 23.0756 | 7.5424 | 183.3457 | 24.3086 | 7.5424 | 0.989%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 2 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 24.3129 | 0.78222 | 31.0817 | 24.3129 | 0.78222 | 31.0817 | 25.612 | 0.82402 | 31.0817 | 0.9937%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 50 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 50.8689 | 19.5556 | 2.6012 | 50.8689 | 19.5556 | 2.6012 | 53.5869 | 20.6005 | 2.6012 | 0.9631%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 107 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 174.04 | 41.849 | 4.1588 | 174.04 | 41.849 | 4.1588 | 183.3392 | 44.085 | 4.1588 | 0.9714%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 15 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 28.1165 | 5.8667 | 4.7926 | 28.1165 | 5.8667 | 4.7926 | 29.6188 | 6.1801 | 4.7926 | 0.9712%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 56 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 189.1139 | 21.9023 | 8.6344 | 189.1139 | 21.9023 | 8.6344 | 199.2185 | 23.0725 | 8.6344 | 0.9923%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.2067 | 0.78222 | 1.5426 | 1.2067 | 0.78222 | 1.5426 | 1.2711 | 0.82402 | 1.5426 | 0.9928%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.063433 | 0.39111 | 0.16219 | 0.063433 | 0.39111 | 0.16219 | 0.066823 | 0.41201 | 0.16219 | 0.9902%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 2 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 3.1321 | 0.78222 | 4.0041 | 3.1321 | 0.78222 | 4.0041 | 3.2994 | 0.82402 | 4.0041 | 0.9939%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 12 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.1444 | 4.6933 | 0.4569 | 2.1444 | 4.6933 | 0.4569 | 2.259 | 4.9441 | 0.4569 | 0.9666%
2026 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 1.8833 | 0 | 0 | 1.8833 | 0 | 1.7966 | 0.78222 | 2.2967 | 1.7966 | 0.78222 | 2.2967 | 1.8926 | 0.82402 | 2.2967 | 0.9988%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 41 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 81.9888 | 16.0356 | 5.1129 | 81.9888 | 16.0356 | 5.1129 | 86.3696 | 16.8924 | 5.1129 | 0.9986%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 37 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 78.5903 | 14.4711 | 5.4308 | 78.5903 | 14.4711 | 5.4308 | 82.7895 | 15.2444 | 5.4308 | 0.9762%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.4212 | 0.39111 | 6.1905 | 2.4212 | 0.39111 | 6.1905 | 2.5505 | 0.41201 | 6.1905 | 0.9867%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 35 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 86.5756 | 13.6889 | 6.3245 | 86.5756 | 13.6889 | 6.3245 | 91.2014 | 14.4203 | 6.3245 | 0.9973%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 74 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 256.1133 | 28.9423 | 8.8491 | 256.1133 | 28.9423 | 8.8491 | 269.7978 | 30.4887 | 8.8491 | 0.9919%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 2 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 60.5455 | 0.78222 | 77.4018 | 60.5455 | 0.78222 | 77.4018 | 63.7806 | 0.82402 | 77.4018 | 0.9998%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 76 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 147.8841 | 29.7245 | 4.9752 | 147.8841 | 29.7245 | 4.9752 | 155.7857 | 31.3127 | 4.9752 | 0.9833%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 28 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 110.8755 | 10.9511 | 10.1246 | 110.8755 | 10.9511 | 10.1246 | 116.7997 | 11.5363 | 10.1246 | 0.988%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 109 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 51.148 | 42.6312 | 1.1998 | 51.148 | 42.6312 | 1.1998 | 53.8809 | 44.9091 | 1.1998 | 0.9625%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 40 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.8412 | 15.6445 | 0.82081 | 12.8412 | 15.6445 | 0.82081 | 13.5273 | 16.4804 | 0.82081 | 0.9181%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 21 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 74.6808 | 8.2134 | 9.0926 | 74.6808 | 8.2134 | 9.0926 | 78.6711 | 8.6522 | 9.0926 | 0.9835%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 146 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 389.2135 | 57.1024 | 6.8161 | 389.2135 | 57.1024 | 6.8161 | 410.0097 | 60.1534 | 6.8161 | 0.9889%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 46 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 31.9736 | 17.9912 | 1.7772 | 31.9736 | 17.9912 | 1.7772 | 33.682 | 18.9525 | 1.7772 | 0.9191%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 213.2749 | 37.1557 | 5.74 | 213.2749 | 37.1557 | 5.74 | 224.6704 | 39.1409 | 5.74 | 0.9908%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 1 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.4417 | 0.39111 | 3.6861 | 1.4417 | 0.39111 | 3.6861 | 1.5187 | 0.41201 | 3.6861 | 0.9858%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 10 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.8036 | 3.9111 | 1.9952 | 7.8036 | 3.9111 | 1.9952 | 8.2206 | 4.1201 | 1.9952 | 0.9652%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 126 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 523.2391 | 49.2801 | 10.6176 | 523.2391 | 49.2801 | 10.6176 | 551.1964 | 51.9132 | 10.6176 | 0.9927%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 99 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 305.9761 | 38.7201 | 7.9023 | 305.9761 | 38.7201 | 7.9023 | 322.3248 | 40.789 | 7.9023 | 0.9926%
2026 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 0.62909 | 0 | 0 | 0.62909 | 0 | 0.60011 | 0.39111 | 1.5344 | 0.60011 | 0.39111 | 1.5344 | 0.63218 | 0.41201 | 1.5344 | 0.9988%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 28 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.8658 | 10.9511 | 1.0835 | 11.8658 | 10.9511 | 1.0835 | 12.4998 | 11.5363 | 1.0835 | 0.9598%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 12 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 32.2825 | 4.6933 | 6.8783 | 32.2825 | 4.6933 | 6.8783 | 34.0074 | 4.9441 | 6.8783 | 0.9934%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 10.234 | 1.1733 | 8.7221 | 10.234 | 1.1733 | 8.7221 | 10.7808 | 1.236 | 8.7221 | 0.6902%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 2 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 14.5549 | 0.78222 | 18.607 | 14.5549 | 0.78222 | 18.607 | 15.3325 | 0.82402 | 18.607 | 0.7661%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 4.1265 | 0.78222 | 5.2754 | 4.1265 | 0.78222 | 5.2754 | 4.347 | 0.82402 | 5.2754 | 0.9947%
2026 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 5 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.5777 | 1.9556 | 0.29541 | 0.5777 | 1.9556 | 0.29541 | 0.60856 | 2.06 | 0.29541 | 0.9691%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 11 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 123.222 | 4.3022 | 28.6414 | 123.222 | 4.3022 | 28.6414 | 129.8059 | 4.5321 | 28.6414 | 0.9966%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 100 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 143.1403 | 39.1112 | 3.6598 | 143.1403 | 39.1112 | 3.6598 | 150.7885 | 41.201 | 3.6598 | 0.9905%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 189 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 268.7684 | 73.9202 | 3.6359 | 268.7684 | 73.9202 | 3.6359 | 283.129 | 77.8699 | 3.6359 | 0.9891%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 28 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 76.0524 | 10.9511 | 6.9447 | 76.0524 | 10.9511 | 6.9447 | 80.116 | 11.5363 | 6.9447 | 0.9946%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 11 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 41.3095 | 4.3022 | 9.6019 | 41.3095 | 4.3022 | 9.6019 | 43.5167 | 4.5321 | 9.6019 | 0.9952%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 45 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 138.6921 | 17.6 | 7.8802 | 138.6921 | 17.6 | 7.8802 | 146.1026 | 18.5404 | 7.8802 | 0.9843%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 103 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 106.3896 | 40.2846 | 2.641 | 106.3896 | 40.2846 | 2.641 | 112.0742 | 42.437 | 2.641 | 0.9898%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 81 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 75.3766 | 31.6801 | 2.3793 | 75.3766 | 31.6801 | 2.3793 | 79.4041 | 33.3728 | 2.3793 | 0.9853%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 106 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 219.7181 | 41.4579 | 5.2998 | 219.7181 | 41.4579 | 5.2998 | 231.4579 | 43.673 | 5.2998 | 0.9839%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 54 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 213.075 | 21.1201 | 10.0887 | 213.075 | 21.1201 | 10.0887 | 224.4598 | 22.2485 | 10.0887 | 0.9748%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 86.5106 | 23.0756 | 3.749 | 86.5106 | 23.0756 | 3.749 | 91.1329 | 24.3086 | 3.749 | 0.9912%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 50 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 48.0711 | 19.5556 | 2.4582 | 48.0711 | 19.5556 | 2.4582 | 50.6396 | 20.6005 | 2.4582 | 0.9732%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 19 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 81.8457 | 7.4311 | 11.0139 | 81.8457 | 7.4311 | 11.0139 | 86.2189 | 7.8282 | 11.0139 | 0.9953%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 82 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 60.9876 | 32.0712 | 1.9016 | 60.9876 | 32.0712 | 1.9016 | 64.2463 | 33.7848 | 1.9016 | 0.9803%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 104 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 31.2181 | 40.6757 | 0.76749 | 31.2181 | 40.6757 | 0.76749 | 32.8861 | 42.849 | 0.76749 | 0.9369%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 29 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 67.491 | 11.3423 | 5.9504 | 67.491 | 11.3423 | 5.9504 | 71.0971 | 11.9483 | 5.9504 | 0.9955%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 1 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 49.1533 | 0.39111 | 125.6757 | 49.1533 | 0.39111 | 125.6757 | 51.7796 | 0.41201 | 125.6757 | 0.803%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 11 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.9388 | 4.3022 | 0.91553 | 3.9388 | 4.3022 | 0.91553 | 4.1493 | 4.5321 | 0.91553 | 0.6587%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 17 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 43.563 | 6.6489 | 6.5519 | 43.563 | 6.6489 | 6.5519 | 45.8907 | 7.0042 | 6.5519 | 0.9978%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 1 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 31.7322 | 0.39111 | 81.1333 | 31.7322 | 0.39111 | 81.1333 | 33.4277 | 0.41201 | 81.1333 | 0.9981%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 24 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 13.4423 | 9.3867 | 1.4321 | 13.4423 | 9.3867 | 1.4321 | 14.1606 | 9.8882 | 1.4321 | 0.9962%
2026 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 1 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.7804 | 0.39111 | 27.5635 | 10.7804 | 0.39111 | 27.5635 | 11.3564 | 0.41201 | 27.5635 | 0.9972%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 4 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.4261 | 1.5644 | 3.4684 | 5.4261 | 1.5644 | 3.4684 | 5.716 | 1.648 | 3.4684 | 0.3454%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.4764 | 7.4311 | 0.73696 | 5.4764 | 7.4311 | 0.73696 | 5.769 | 7.8282 | 0.73696 | 0.75%
2026 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | Tier-2---20 | 2 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.030773 | 0 | 0 | 0.030773 | 0 | 0.029355 | 0.78222 | 0.037528 | 0.029355 | 0.78222 | 0.037528 | 0.030924 | 0.82402 | 0.037528 | 0.1687%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 3 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.69331 | 1.1733 | 0.59089 | 0.69331 | 1.1733 | 0.59089 | 0.73035 | 1.236 | 0.59089 | 0.9665%
2026 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 0.21747 | 0 | 0 | 0.21747 | 0 | 0.20745 | 0.39111 | 0.53042 | 0.20745 | 0.39111 | 0.53042 | 0.21854 | 0.41201 | 0.53042 | 0.9966%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 79 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 50.7476 | 30.8979 | 1.6424 | 50.7476 | 30.8979 | 1.6424 | 53.4591 | 32.5488 | 1.6424 | 0.8429%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 92 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 62.8186 | 35.9823 | 1.7458 | 62.8186 | 35.9823 | 1.7458 | 66.175 | 37.9049 | 1.7458 | 0.9909%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 30 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.6866 | 11.7334 | 1.1665 | 13.6866 | 11.7334 | 1.1665 | 14.4179 | 12.3603 | 1.1665 | 0.9975%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 1.0286 | 0.78222 | 1.315 | 1.0286 | 0.78222 | 1.315 | 1.0836 | 0.82402 | 1.315 | 0.9975%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 2 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 38.8495 | 0.78222 | 49.6654 | 38.8495 | 0.78222 | 49.6654 | 40.9253 | 0.82402 | 49.6654 | 0.9993%
2026 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | Non-HFTD---22 | 1 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.037296 | 0 | 0 | 0.037296 | 0 | 0.035578 | 0.39111 | 0.090965 | 0.035578 | 0.39111 | 0.090965 | 0.037479 | 0.41201 | 0.090965 | 0.8877%
2026 | 157 | CB 157 | Tier-3 | Tier-3---21 | Tier-3---11 | 1 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.06043 | 0 | 0 | 0.06043 | 0 | 0.057646 | 0.39111 | 0.14739 | 0.057646 | 0.39111 | 0.14739 | 0.060726 | 0.41201 | 0.14739 | 0.9943%
2026 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 5 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.8291 | 1.9556 | 1.9581 | 3.8291 | 1.9556 | 1.9581 | 4.0337 | 2.06 | 1.9581 | 0.299%
2026 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 1 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 8.1689 | 0.39111 | 20.8863 | 8.1689 | 0.39111 | 20.8863 | 8.6054 | 0.41201 | 20.8863 | 0.8082%
2026 | 212 | CB 212 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 0.22772 | 0 | 0 | 0.22772 | 0 | 0.21723 | 0.39111 | 0.55543 | 0.21723 | 0.39111 | 0.55543 | 0.22884 | 0.41201 | 0.55543 | 0.9909%
2026 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 1 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 2.0264 | 0.39111 | 5.1812 | 2.0264 | 0.39111 | 5.1812 | 2.1347 | 0.41201 | 5.1812 | 0.9981%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 50 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 23.6778 | 19.5556 | 1.2108 | 23.6778 | 19.5556 | 1.2108 | 24.9429 | 20.6005 | 1.2108 | 0.9929%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 23 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 15.2578 | 8.9956 | 1.6961 | 15.2578 | 8.9956 | 1.6961 | 16.0731 | 9.4762 | 1.6961 | 0.9737%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 38.8784 | 39.8934 | 0.97456 | 38.8784 | 39.8934 | 0.97456 | 40.9557 | 42.025 | 0.97456 | 0.9874%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 17 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 31.0776 | 6.6489 | 4.6741 | 31.0776 | 6.6489 | 4.6741 | 32.7382 | 7.0042 | 4.6741 | 0.9888%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 32 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 118.3696 | 12.5156 | 9.4578 | 118.3696 | 12.5156 | 9.4578 | 124.6943 | 13.1843 | 9.4578 | 0.9762%
2026 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 4 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 20.0507 | 1.5644 | 12.8165 | 20.0507 | 1.5644 | 12.8165 | 21.1221 | 1.648 | 12.8165 | 0.9954%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 23 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.7686 | 8.9956 | 1.3083 | 11.7686 | 8.9956 | 1.3083 | 12.3974 | 9.4762 | 1.3083 | 0.9768%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 9 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.4978 | 3.52 | 0.7096 | 2.4978 | 3.52 | 0.7096 | 2.6312 | 3.7081 | 0.7096 | 0.6436%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 5 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0574 | 1.9556 | 0.54069 | 1.0574 | 1.9556 | 0.54069 | 1.1139 | 2.06 | 0.54069 | 0.375%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 12.35 | 9.3867 | 1.3157 | 12.35 | 9.3867 | 1.3157 | 13.0099 | 9.8882 | 1.3157 | 0.9%
2026 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 1 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.5459 | 0.39111 | 6.5093 | 2.5459 | 0.39111 | 6.5093 | 2.6819 | 0.41201 | 6.5093 | 0.7028%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 30 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 9.1325 | 11.7334 | 0.77833 | 9.1325 | 11.7334 | 0.77833 | 9.6204 | 12.3603 | 0.77833 | 0.995%
2026 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 24 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.6547 | 9.3867 | 0.81549 | 7.6547 | 9.3867 | 0.81549 | 8.0637 | 9.8882 | 0.81549 | 0.9704%
2026 | 283 | CB 283 | Tier-3 | Tier-3---21 | Tier-3---11 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.060097 | 0 | 0 | 0.060097 | 0 | 0.057329 | 0.39111 | 0.14658 | 0.057329 | 0.39111 | 0.14658 | 0.060392 | 0.41201 | 0.14658 | 0.9941%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.8672 | 0.39111 | 35.4558 | 13.8672 | 0.39111 | 35.4558 | 14.6082 | 0.41201 | 35.4558 | 0.9979%
2026 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 5 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.4763 | 1.9556 | 1.2663 | 2.4763 | 1.9556 | 1.2663 | 2.6086 | 2.06 | 1.2663 | 0.9938%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 28 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 138.8006 | 10.9511 | 12.6745 | 138.8006 | 10.9511 | 12.6745 | 146.2169 | 11.5363 | 12.6745 | 0.9966%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 83 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 106.4306 | 32.4623 | 3.2786 | 106.4306 | 32.4623 | 3.2786 | 112.1173 | 34.1968 | 3.2786 | 0.9884%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 53 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 55.9658 | 20.7289 | 2.6999 | 55.9658 | 20.7289 | 2.6999 | 58.9561 | 21.8365 | 2.6999 | 0.9601%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 2 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.5513 | 0.78222 | 1.9831 | 1.5513 | 0.78222 | 1.9831 | 1.6341 | 0.82402 | 1.9831 | 0.1888%
2026 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 7 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 10.1685 | 2.7378 | 3.7141 | 10.1685 | 2.7378 | 3.7141 | 10.7118 | 2.8841 | 3.7141 | 0.9408%
2026 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 1 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 0.65999 | 0 | 0 | 0.65999 | 0 | 0.62958 | 0.39111 | 1.6097 | 0.62958 | 0.39111 | 1.6097 | 0.66322 | 0.41201 | 1.6097 | 0.9829%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 3 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 1.0944 | 1.1733 | 0.93269 | 1.0944 | 1.1733 | 0.93269 | 1.1528 | 1.236 | 0.93269 | 0.9768%
2026 | 461 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 1 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 1.005 | 0 | 0 | 1.005 | 0 | 0.95869 | 0.39111 | 2.4512 | 0.95869 | 0.39111 | 2.4512 | 1.0099 | 0.41201 | 2.4512 | 0.9865%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 5 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 63.0506 | 1.9556 | 32.2417 | 63.0506 | 1.9556 | 32.2417 | 66.4195 | 2.06 | 32.2417 | 0.9549%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 3 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.3276 | 1.1733 | 3.6883 | 4.3276 | 1.1733 | 3.6883 | 4.5588 | 1.236 | 3.6883 | 0.9425%
2026 | 533 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0035677 | 0 | 0 | 0.0035677 | 0 | 0.0034033 | 0.39111 | 0.0087017 | 0.0034033 | 0.39111 | 0.0087017 | 0.0035852 | 0.41201 | 0.0087017 | 0.03364%
2026 | 534 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.022693 | 0 | 0 | 0.022693 | 0 | 0.021648 | 0.78222 | 0.027675 | 0.021648 | 0.78222 | 0.027675 | 0.022804 | 0.82402 | 0.027675 | 0.3599%
2026 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.051127 | 0 | 0 | 0.051127 | 0 | 0.048771 | 0.39111 | 0.1247 | 0.048771 | 0.39111 | 0.1247 | 0.051377 | 0.41201 | 0.1247 | 0.04585%
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 5 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.39328 | 1.9556 | 0.20111 | 0.39328 | 1.9556 | 0.20111 | 0.4143 | 2.06 | 0.20111 | 0.7619%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 4 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.63661 | 1.5644 | 0.40692 | 0.63661 | 1.5644 | 0.40692 | 0.67063 | 1.648 | 0.40692 | 0.9924%
2026 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 8 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.6457 | 3.1289 | 2.7632 | 8.6457 | 3.1289 | 2.7632 | 9.1076 | 3.2961 | 2.7632 | 0.9545%
2026 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 3 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 3.1226 | 1.1733 | 2.6613 | 3.1226 | 1.1733 | 2.6613 | 3.2895 | 1.236 | 2.6613 | 0.7837%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 22 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 41.1623 | 8.6045 | 4.7838 | 41.1623 | 8.6045 | 4.7838 | 43.3617 | 9.0642 | 4.7838 | 0.9981%
2026 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 4 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.48675 | 1.5644 | 0.31113 | 0.48675 | 1.5644 | 0.31113 | 0.51276 | 1.648 | 0.31113 | 0.9266%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 12 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 77.7152 | 4.6933 | 16.5586 | 77.7152 | 4.6933 | 16.5586 | 81.8676 | 4.9441 | 16.5586 | 0.9507%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 8 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 26.1161 | 3.1289 | 8.3468 | 26.1161 | 3.1289 | 8.3468 | 27.5116 | 3.2961 | 8.3468 | 0.9983%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 3.01 | 1.5644 | 1.924 | 3.01 | 1.5644 | 1.924 | 3.1708 | 1.648 | 1.924 | 0.9343%
2026 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 7 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 12.5918 | 2.7378 | 4.5993 | 12.5918 | 2.7378 | 4.5993 | 13.2646 | 2.8841 | 4.5993 | 0.7976%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 27 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 108.7518 | 10.56 | 10.2984 | 108.7518 | 10.56 | 10.2984 | 114.5625 | 11.1243 | 10.2984 | 0.9951%
2026 | 974 | CB 974 | Tier-2 | Tier-2---12 | Tier-2---11 | 4 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 3.3409 | 0 | 0 | 3.3409 | 0 | 3.187 | 1.5644 | 2.0371 | 3.187 | 1.5644 | 2.0371 | 3.3572 | 1.648 | 2.0371 | 0.9993%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 3 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 12.3822 | 1.1733 | 10.553 | 12.3822 | 1.1733 | 10.553 | 13.0438 | 1.236 | 10.553 | 0.9951%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 9 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.6886 | 3.52 | 1.0479 | 3.6886 | 3.52 | 1.0479 | 3.8857 | 3.7081 | 1.0479 | 0.997%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.23647 | 0.78222 | 0.30231 | 0.23647 | 0.78222 | 0.30231 | 0.24911 | 0.82402 | 0.30231 | 0.9021%
2026 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.15462 | 0 | 0 | 0.15462 | 0 | 0.1475 | 0.39111 | 0.37713 | 0.1475 | 0.39111 | 0.37713 | 0.15538 | 0.41201 | 0.37713 | 0.9981%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 29 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 14.297 | 11.3423 | 1.2605 | 14.297 | 11.3423 | 1.2605 | 15.0609 | 11.9483 | 1.2605 | 0.9785%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 32 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 48.1334 | 12.5156 | 3.8459 | 48.1334 | 12.5156 | 3.8459 | 50.7052 | 13.1843 | 3.8459 | 0.9856%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 109 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 65.3114 | 42.6312 | 1.532 | 65.3114 | 42.6312 | 1.532 | 68.8011 | 44.9091 | 1.532 | 0.99%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 66 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 27.3578 | 25.8134 | 1.0598 | 27.3578 | 25.8134 | 1.0598 | 28.8196 | 27.1926 | 1.0598 | 0.9473%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 65 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 98.6268 | 25.4223 | 3.8795 | 98.6268 | 25.4223 | 3.8795 | 103.8966 | 26.7806 | 3.8795 | 0.9831%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 17 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 48.9483 | 6.6489 | 7.3619 | 48.9483 | 6.6489 | 7.3619 | 51.5636 | 7.0042 | 7.3619 | 0.9811%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 5 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 6.074 | 1.9556 | 3.106 | 6.074 | 1.9556 | 3.106 | 6.3986 | 2.06 | 3.106 | 0.695%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 19 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 35.3682 | 7.4311 | 4.7595 | 35.3682 | 7.4311 | 4.7595 | 37.258 | 7.8282 | 4.7595 | 0.9914%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 128 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 30.0514 | 50.0624 | 0.60028 | 30.0514 | 50.0624 | 0.60028 | 31.6571 | 52.7373 | 0.60028 | 0.9371%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 15.535 | 20.7289 | 0.74944 | 15.535 | 20.7289 | 0.74944 | 16.3651 | 21.8365 | 0.74944 | 0.789%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 90 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 33.7655 | 35.2001 | 0.95925 | 33.7655 | 35.2001 | 0.95925 | 35.5697 | 37.0809 | 0.95925 | 0.9517%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 30 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 88.4904 | 11.7334 | 7.5418 | 88.4904 | 11.7334 | 7.5418 | 93.2185 | 12.3603 | 7.5418 | 0.9933%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 64.412 | 33.2445 | 1.9375 | 64.412 | 33.2445 | 1.9375 | 67.8536 | 35.0208 | 1.9375 | 0.9757%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 27 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 56.3376 | 10.56 | 5.335 | 56.3376 | 10.56 | 5.335 | 59.3477 | 11.1243 | 5.335 | 0.9932%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 20 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 35.8983 | 7.8222 | 4.5893 | 35.8983 | 7.8222 | 4.5893 | 37.8164 | 8.2402 | 4.5893 | 0.9948%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 11 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 35.1217 | 4.104 | 8.5578 | 35.1217 | 4.104 | 8.5578 | 38.9752 | 4.5543 | 8.5578 | 0.9141%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 1.0397 | 0.74619 | 1.3934 | 1.0397 | 0.74619 | 1.3934 | 1.1538 | 0.82806 | 1.3934 | 0.9976%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 316.78 | 35.444 | 8.9375 | 316.78 | 35.444 | 8.9375 | 351.5364 | 39.3328 | 8.9375 | 0.9902%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 17 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 63.0347 | 6.3426 | 9.9383 | 63.0347 | 6.3426 | 9.9383 | 69.9507 | 7.0385 | 9.9383 | 0.9818%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 43 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 170.7952 | 16.0431 | 10.646 | 170.7952 | 16.0431 | 10.646 | 189.5344 | 17.8033 | 10.646 | 0.997%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 11 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 45.5855 | 4.104 | 11.1075 | 45.5855 | 4.104 | 11.1075 | 50.5871 | 4.5543 | 11.1075 | 0.9951%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 3 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 12.565 | 1.1193 | 11.226 | 12.565 | 1.1193 | 11.226 | 13.9437 | 1.2421 | 11.226 | 0.9958%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 33 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 88.8468 | 12.3121 | 7.2162 | 88.8468 | 12.3121 | 7.2162 | 98.5948 | 13.663 | 7.2162 | 0.9962%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 1 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.2724 | 0.37309 | 16.8118 | 6.2724 | 0.37309 | 16.8118 | 6.9606 | 0.41403 | 16.8118 | 0.9922%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 32 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 45.7686 | 11.939 | 3.8335 | 45.7686 | 11.939 | 3.8335 | 50.7903 | 13.2489 | 3.8335 | 0.9916%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 18 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 26.0989 | 6.7157 | 3.8862 | 26.0989 | 6.7157 | 3.8862 | 28.9624 | 7.4525 | 3.8862 | 0.9924%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 80 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 82.7087 | 29.8476 | 2.771 | 82.7087 | 29.8476 | 2.771 | 91.7833 | 33.1224 | 2.771 | 0.9598%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 64 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 33.4452 | 23.878 | 1.4007 | 33.4452 | 23.878 | 1.4007 | 37.1147 | 26.4979 | 1.4007 | 0.9739%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 19 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.6715 | 7.0888 | 0.659 | 4.6715 | 7.0888 | 0.659 | 5.1841 | 7.8666 | 0.659 | 0.8768%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 21 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 45.818 | 7.835 | 5.8479 | 45.818 | 7.835 | 5.8479 | 50.845 | 8.6946 | 5.8479 | 0.9826%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 46 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 106.0165 | 17.1623 | 6.1773 | 106.0165 | 17.1623 | 6.1773 | 117.6484 | 19.0454 | 6.1773 | 0.9858%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 22 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 19.4652 | 8.2081 | 2.3715 | 19.4652 | 8.2081 | 2.3715 | 21.6009 | 9.1086 | 2.3715 | 0.9945%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 59.4414 | 31.713 | 1.8744 | 59.4414 | 31.713 | 1.8744 | 65.9631 | 35.1925 | 1.8744 | 0.9866%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 124 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 228.4185 | 46.2637 | 4.9373 | 228.4185 | 46.2637 | 4.9373 | 253.4801 | 51.3397 | 4.9373 | 0.9914%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 119 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 254.5346 | 44.3982 | 5.733 | 254.5346 | 44.3982 | 5.733 | 282.4616 | 49.2695 | 5.733 | 0.9849%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 103 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 240.8882 | 38.4287 | 6.2684 | 240.8882 | 38.4287 | 6.2684 | 267.3178 | 42.645 | 6.2684 | 0.9916%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 68 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 141.5109 | 25.3704 | 5.5778 | 141.5109 | 25.3704 | 5.5778 | 157.0372 | 28.154 | 5.5778 | 0.9745%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 1 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14198 | 0.37309 | 0.38054 | 0.14198 | 0.37309 | 0.38054 | 0.15755 | 0.41403 | 0.38054 | 0.8684%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 10 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.5975 | 3.7309 | 1.7683 | 6.5975 | 3.7309 | 1.7683 | 7.3213 | 4.1403 | 1.7683 | 0.9924%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 24 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.8584 | 8.9543 | 0.87762 | 7.8584 | 8.9543 | 0.87762 | 8.7207 | 9.9367 | 0.87762 | 0.9393%
2027 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 11 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 4.6858 | 0 | 0 | 4.6858 | 0 | 4.264 | 4.104 | 1.039 | 4.264 | 4.104 | 1.039 | 4.7319 | 4.5543 | 1.039 | 0.9197%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 4 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1281 | 1.4924 | 0.75588 | 1.1281 | 1.4924 | 0.75588 | 1.2518 | 1.6561 | 0.75588 | 0.8802%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 81 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 53.4767 | 30.2206 | 1.7695 | 53.4767 | 30.2206 | 1.7695 | 59.3441 | 33.5364 | 1.7695 | 0.9962%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 63 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 45.2456 | 23.5049 | 1.9249 | 45.2456 | 23.5049 | 1.9249 | 50.2098 | 26.0839 | 1.9249 | 0.9962%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 16 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 22.8419 | 5.9695 | 3.8264 | 22.8419 | 5.9695 | 3.8264 | 25.3481 | 6.6245 | 3.8264 | 0.9984%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 19.4557 | 1.1193 | 17.3823 | 19.4557 | 1.1193 | 17.3823 | 21.5904 | 1.2421 | 17.3823 | 0.9968%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 1 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 38.4457 | 0.37309 | 103.0456 | 38.4457 | 0.37309 | 103.0456 | 42.6639 | 0.41403 | 103.0456 | 0.9992%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 1 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.5858 | 0.37309 | 9.6109 | 3.5858 | 0.37309 | 9.6109 | 3.9792 | 0.41403 | 9.6109 | 0.945%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 3 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.1314 | 1.1193 | 6.3714 | 7.1314 | 1.1193 | 6.3714 | 7.9138 | 1.2421 | 6.3714 | 0.994%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 93 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 38.673 | 34.6978 | 1.1146 | 38.673 | 34.6978 | 1.1146 | 42.9161 | 38.5047 | 1.1146 | 0.9112%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 9 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 1.9283 | 3.3578 | 0.57427 | 1.9283 | 3.3578 | 0.57427 | 2.1399 | 3.7263 | 0.57427 | 0.8819%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 6 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.8164 | 2.2386 | 0.81141 | 1.8164 | 2.2386 | 0.81141 | 2.0157 | 2.4842 | 0.81141 | 0.9662%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 8 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.2059 | 2.9848 | 0.73906 | 2.2059 | 2.9848 | 0.73906 | 2.4479 | 3.3122 | 0.73906 | 0.9775%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 23 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 35.4566 | 8.5812 | 4.1319 | 35.4566 | 8.5812 | 4.1319 | 39.3468 | 9.5227 | 4.1319 | 0.9826%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 16 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 91.7746 | 5.9695 | 15.3739 | 91.7746 | 5.9695 | 15.3739 | 101.8439 | 6.6245 | 15.3739 | 0.9977%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 73 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 93.0711 | 27.2359 | 3.4172 | 93.0711 | 27.2359 | 3.4172 | 103.2827 | 30.2242 | 3.4172 | 0.9908%
2027 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | Tier-3---19 | 2 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 1.2393 | 0 | 0 | 1.2393 | 0 | 1.1278 | 0.74619 | 1.5114 | 1.1278 | 0.74619 | 1.5114 | 1.2515 | 0.82806 | 1.5114 | 0.7849%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 43 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 54.7545 | 16.0431 | 3.413 | 54.7545 | 16.0431 | 3.413 | 60.762 | 17.8033 | 3.413 | 0.9788%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 15 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 19.0873 | 5.5964 | 3.4106 | 19.0873 | 5.5964 | 3.4106 | 21.1815 | 6.2104 | 3.4106 | 0.9469%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 64 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 76.3476 | 23.878 | 3.1974 | 76.3476 | 23.878 | 3.1974 | 84.7243 | 26.4979 | 3.1974 | 0.9648%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 24 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.9788 | 8.9543 | 1.5611 | 13.9788 | 8.9543 | 1.5611 | 15.5125 | 9.9367 | 1.5611 | 0.9856%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 33 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 31.901 | 12.3121 | 2.591 | 31.901 | 12.3121 | 2.591 | 35.4011 | 13.663 | 2.591 | 0.9842%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 39 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 26.5819 | 14.5507 | 1.8268 | 26.5819 | 14.5507 | 1.8268 | 29.4984 | 16.1471 | 1.8268 | 0.979%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 12 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 12.4803 | 4.4771 | 2.7876 | 12.4803 | 4.4771 | 2.7876 | 13.8496 | 4.9684 | 2.7876 | 0.9892%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 30 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 38.6065 | 11.1928 | 3.4492 | 38.6065 | 11.1928 | 3.4492 | 42.8424 | 12.4209 | 3.4492 | 0.9866%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 10 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.732 | 3.7309 | 1.0003 | 3.732 | 3.7309 | 1.0003 | 4.1414 | 4.1403 | 1.0003 | 0.9965%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 14 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.1418 | 5.2233 | 0.79295 | 4.1418 | 5.2233 | 0.79295 | 4.5962 | 5.7964 | 0.79295 | 0.9977%
2027 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 1 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.02425 | 0 | 0 | 0.02425 | 0 | 0.022067 | 0.37309 | 0.059146 | 0.022067 | 0.37309 | 0.059146 | 0.024488 | 0.41403 | 0.059146 | 0.9862%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.6502 | 1.1193 | 9.5152 | 10.6502 | 1.1193 | 9.5152 | 11.8187 | 1.2421 | 9.5152 | 0.9935%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.4325 | 0.37309 | 3.8396 | 1.4325 | 0.37309 | 3.8396 | 1.5897 | 0.41403 | 3.8396 | 0.9948%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.9301 | 5.9695 | 2.8361 | 16.9301 | 5.9695 | 2.8361 | 18.7877 | 6.6245 | 2.8361 | 0.9905%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 4 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 58.631 | 1.4924 | 39.287 | 58.631 | 1.4924 | 39.287 | 65.0638 | 1.6561 | 39.287 | 0.9454%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 28 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 106.1245 | 10.4466 | 10.1587 | 106.1245 | 10.4466 | 10.1587 | 117.7682 | 11.5928 | 10.1587 | 0.9926%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 13 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 32.9139 | 4.8502 | 6.7861 | 32.9139 | 4.8502 | 6.7861 | 36.5251 | 5.3824 | 6.7861 | 0.9815%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 16 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.5188 | 5.9695 | 0.58945 | 3.5188 | 5.9695 | 0.58945 | 3.9048 | 6.6245 | 0.58945 | 0.9046%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 3 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 18.4141 | 1.1193 | 16.4517 | 18.4141 | 1.1193 | 16.4517 | 20.4345 | 1.2421 | 16.4517 | 0.8554%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 33 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 39.2397 | 12.3121 | 3.1871 | 39.2397 | 12.3121 | 3.1871 | 43.545 | 13.663 | 3.1871 | 0.9867%
2027 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.74619 | 0 | 0 | 0.74619 | 0 | 0 | 0.82806 | 0 | 0%
2027 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 3 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1.1193 | 0 | 0 | 1.1193 | 0 | 0 | 1.2421 | 0 | 0%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 51 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 144.1626 | 19.0278 | 7.5764 | 144.1626 | 19.0278 | 7.5764 | 159.9798 | 21.1155 | 7.5764 | 0.9909%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.45452 | 0.37309 | 1.2182 | 0.45452 | 0.37309 | 1.2182 | 0.50439 | 0.41403 | 1.2182 | 0.2981%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.73678 | 0.37309 | 1.9748 | 0.73678 | 0.37309 | 1.9748 | 0.81761 | 0.41403 | 1.9748 | 0.9995%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 38 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 73.6943 | 14.1776 | 5.1979 | 73.6943 | 14.1776 | 5.1979 | 81.7799 | 15.7331 | 5.1979 | 0.9925%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 127 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 335.2263 | 47.383 | 7.0748 | 335.2263 | 47.383 | 7.0748 | 372.0065 | 52.5817 | 7.0748 | 0.9936%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.067341 | 0.37309 | 0.18049 | 0.067341 | 0.37309 | 0.18049 | 0.07473 | 0.41403 | 0.18049 | 0.895%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 20 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.3406 | 7.4619 | 0.44769 | 3.3406 | 7.4619 | 0.44769 | 3.7072 | 8.2806 | 0.44769 | 0.8771%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 177 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 46.3352 | 66.0377 | 0.70165 | 46.3352 | 66.0377 | 0.70165 | 51.419 | 73.2832 | 0.70165 | 0.9246%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 10 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 27.5199 | 3.7309 | 7.3761 | 27.5199 | 3.7309 | 7.3761 | 30.5393 | 4.1403 | 7.3761 | 0.9907%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 20 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 34.9145 | 7.4619 | 4.679 | 34.9145 | 7.4619 | 4.679 | 38.7452 | 8.2806 | 4.679 | 0.9899%
2027 | 157 | 157-207R | Tier-3 | Tier-3---16 | Tier-3---7 | 2 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 7.1828 | 0 | 0 | 7.1828 | 0 | 6.5362 | 0.74619 | 8.7595 | 6.5362 | 0.74619 | 8.7595 | 7.2534 | 0.82806 | 8.7595 | 0.9989%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 80 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 27.3993 | 29.8476 | 0.91798 | 27.3993 | 29.8476 | 0.91798 | 30.4055 | 33.1224 | 0.91798 | 0.9527%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 151 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 15.2942 | 56.3373 | 0.27148 | 15.2942 | 56.3373 | 0.27148 | 16.9722 | 62.5184 | 0.27148 | 0.8154%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.1452 | 19.774 | 0.81649 | 16.1452 | 19.774 | 0.81649 | 17.9167 | 21.9436 | 0.81649 | 0.9501%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 205 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 165.5087 | 76.4844 | 2.164 | 165.5087 | 76.4844 | 2.164 | 183.6679 | 84.876 | 2.164 | 0.97%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 19 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 36.3343 | 7.0888 | 5.1256 | 36.3343 | 7.0888 | 5.1256 | 40.3209 | 7.8666 | 5.1256 | 0.991%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 6 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.0463 | 2.2386 | 7.6148 | 17.0463 | 2.2386 | 7.6148 | 18.9166 | 2.4842 | 7.6148 | 0.7065%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 38.9182 | 23.5049 | 1.6557 | 38.9182 | 23.5049 | 1.6557 | 43.1883 | 26.0839 | 1.6557 | 0.9752%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 113 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 50.6068 | 42.1597 | 1.2004 | 50.6068 | 42.1597 | 1.2004 | 56.1593 | 46.7853 | 1.2004 | 0.9686%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 9 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.0694 | 3.3578 | 1.8075 | 6.0694 | 3.3578 | 1.8075 | 6.7353 | 3.7263 | 1.8075 | 0.7976%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 103.5696 | 23.1319 | 4.4774 | 103.5696 | 23.1319 | 4.4774 | 114.9331 | 25.6698 | 4.4774 | 0.9877%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 55 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 37.3556 | 20.5202 | 1.8204 | 37.3556 | 20.5202 | 1.8204 | 41.4542 | 22.7716 | 1.8204 | 0.981%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 32 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 88.9924 | 11.939 | 7.4539 | 88.9924 | 11.939 | 7.4539 | 98.7564 | 13.2489 | 7.4539 | 0.9713%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 51 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 30.2493 | 19.0278 | 1.5897 | 30.2493 | 19.0278 | 1.5897 | 33.5682 | 21.1155 | 1.5897 | 0.9774%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 44 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 43.8683 | 16.4162 | 2.6723 | 43.8683 | 16.4162 | 2.6723 | 48.6815 | 18.2173 | 2.6723 | 0.977%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 115 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 116.04 | 42.9059 | 2.7045 | 116.04 | 42.9059 | 2.7045 | 128.7717 | 47.6134 | 2.7045 | 0.968%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.2848 | 1.8655 | 7.1214 | 13.2848 | 1.8655 | 7.1214 | 14.7424 | 2.0701 | 7.1214 | 0.8924%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 3 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 21.0957 | 1.1193 | 18.8475 | 21.0957 | 1.1193 | 18.8475 | 23.4103 | 1.2421 | 18.8475 | 0.7823%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 40 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 102.2536 | 14.9238 | 6.8517 | 102.2536 | 14.9238 | 6.8517 | 113.4727 | 16.5612 | 6.8517 | 0.9429%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 4 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 17.6009 | 1.4924 | 11.7938 | 17.6009 | 1.4924 | 11.7938 | 19.532 | 1.6561 | 11.7938 | 0.9974%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 17 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 38.1899 | 6.3426 | 6.0212 | 38.1899 | 6.3426 | 6.0212 | 42.38 | 7.0385 | 6.0212 | 0.9922%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 8 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 14.4213 | 2.9848 | 4.8317 | 14.4213 | 2.9848 | 4.8317 | 16.0036 | 3.3122 | 4.8317 | 0.9193%
2027 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 4 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.6591 | 1.4924 | 1.1117 | 1.6591 | 1.4924 | 1.1117 | 1.8411 | 1.6561 | 1.1117 | 0.9934%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 1 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.058051 | 0.37309 | 0.15559 | 0.058051 | 0.37309 | 0.15559 | 0.06442 | 0.41403 | 0.15559 | 0.9638%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 8 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 27.0186 | 2.9848 | 9.0522 | 27.0186 | 2.9848 | 9.0522 | 29.9831 | 3.3122 | 9.0522 | 0.9975%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 51 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 76.8107 | 19.0278 | 4.0368 | 76.8107 | 19.0278 | 4.0368 | 85.2382 | 21.1155 | 4.0368 | 0.9974%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 19 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.0842 | 7.0888 | 0.57616 | 4.0842 | 7.0888 | 0.57616 | 4.5324 | 7.8666 | 0.57616 | 0.901%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 60 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.0972 | 22.3857 | 0.36171 | 8.0972 | 22.3857 | 0.36171 | 8.9856 | 24.8418 | 0.36171 | 0.8573%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 18 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.094 | 6.7157 | 0.1629 | 1.094 | 6.7157 | 0.1629 | 1.214 | 7.4525 | 0.1629 | 0.7047%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 38 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.4697 | 14.1776 | 0.10366 | 1.4697 | 14.1776 | 0.10366 | 1.6309 | 15.7331 | 0.10366 | 0.5082%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 65 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.7688 | 24.2511 | 0.40282 | 9.7688 | 24.2511 | 0.40282 | 10.8406 | 26.9119 | 0.40282 | 0.8949%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 145 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.8754 | 54.0987 | 0.25648 | 13.8754 | 54.0987 | 0.25648 | 15.3977 | 60.0343 | 0.25648 | 0.8426%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 15.667 | 24.6242 | 0.63624 | 15.667 | 24.6242 | 0.63624 | 17.386 | 27.3259 | 0.63624 | 0.9106%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 79 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.1003 | 29.4745 | 0.51232 | 15.1003 | 29.4745 | 0.51232 | 16.7571 | 32.7083 | 0.51232 | 0.9543%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 13.5718 | 26.1166 | 0.51966 | 13.5718 | 26.1166 | 0.51966 | 15.0609 | 28.9821 | 0.51966 | 0.9497%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 4 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.4971 | 1.4924 | 3.6835 | 5.4971 | 1.4924 | 3.6835 | 6.1003 | 1.6561 | 3.6835 | 0.9907%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 46 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 44.1009 | 17.1623 | 2.5696 | 44.1009 | 17.1623 | 2.5696 | 48.9396 | 19.0454 | 2.5696 | 0.9915%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 42 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.2803 | 15.67 | 0.71987 | 11.2803 | 15.67 | 0.71987 | 12.5179 | 17.3892 | 0.71987 | 0.9792%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 39 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.7819 | 14.5507 | 0.60354 | 8.7819 | 14.5507 | 0.60354 | 9.7454 | 16.1471 | 0.60354 | 0.9662%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 6 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.3089 | 2.2386 | 1.0314 | 2.3089 | 2.2386 | 1.0314 | 2.5622 | 2.4842 | 1.0314 | 0.9706%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 68 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.1223 | 25.3704 | 0.51723 | 13.1223 | 25.3704 | 0.51723 | 14.562 | 28.154 | 0.51723 | 0.9727%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 103 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 24.0425 | 38.4287 | 0.62564 | 24.0425 | 38.4287 | 0.62564 | 26.6803 | 42.645 | 0.62564 | 0.9578%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 39 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.1807 | 14.5507 | 0.63094 | 9.1807 | 14.5507 | 0.63094 | 10.1879 | 16.1471 | 0.63094 | 0.9712%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 3 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.9338 | 1.1193 | 0.83428 | 0.9338 | 1.1193 | 0.83428 | 1.0363 | 1.2421 | 0.83428 | 0.9778%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 17 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 19.4357 | 6.3426 | 3.0643 | 19.4357 | 6.3426 | 3.0643 | 21.5682 | 7.0385 | 3.0643 | 0.9872%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 45 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.0944 | 16.7892 | 0.77993 | 13.0944 | 16.7892 | 0.77993 | 14.5311 | 18.6313 | 0.77993 | 0.9782%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 127 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 236.5383 | 47.383 | 4.9921 | 236.5383 | 47.383 | 4.9921 | 262.4908 | 52.5817 | 4.9921 | 0.9891%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 75 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 60.3082 | 27.9821 | 2.1552 | 60.3082 | 27.9821 | 2.1552 | 66.9251 | 31.0522 | 2.1552 | 0.9941%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 30 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.2902 | 11.1928 | 0.38329 | 4.2902 | 11.1928 | 0.38329 | 4.7609 | 12.4209 | 0.38329 | 0.974%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 22 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.5637 | 8.2081 | 0.43417 | 3.5637 | 8.2081 | 0.43417 | 3.9547 | 9.1086 | 0.43417 | 0.9786%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 9 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.6112 | 3.3578 | 1.3733 | 4.6112 | 3.3578 | 1.3733 | 5.1171 | 3.7263 | 1.3733 | 0.9871%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 32 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 19.9133 | 11.939 | 1.6679 | 19.9133 | 11.939 | 1.6679 | 22.0981 | 13.2489 | 1.6679 | 0.9909%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 50 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 13.4254 | 18.6547 | 0.71968 | 13.4254 | 18.6547 | 0.71968 | 14.8984 | 20.7015 | 0.71968 | 0.8569%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 73 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 201.8812 | 27.2359 | 7.4123 | 201.8812 | 27.2359 | 7.4123 | 224.0311 | 30.2242 | 7.4123 | 0.9924%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 72 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 113.526 | 26.8628 | 4.2261 | 113.526 | 26.8628 | 4.2261 | 125.9818 | 29.8101 | 4.2261 | 0.9821%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 175.5743 | 21.6395 | 8.1136 | 175.5743 | 21.6395 | 8.1136 | 194.8379 | 24.0137 | 8.1136 | 0.99%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 16 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.6078 | 5.9695 | 2.112 | 12.6078 | 5.9695 | 2.112 | 13.9911 | 6.6245 | 2.112 | 0.9809%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 26 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 48.9203 | 9.7005 | 5.0431 | 48.9203 | 9.7005 | 5.0431 | 54.2878 | 10.7648 | 5.0431 | 0.9892%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 67 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 126.7327 | 24.9973 | 5.0699 | 126.7327 | 24.9973 | 5.0699 | 140.6375 | 27.74 | 5.0699 | 0.9919%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 126 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 16.3491 | 47.0099 | 0.34778 | 16.3491 | 47.0099 | 0.34778 | 18.1429 | 52.1677 | 0.34778 | 0.8922%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 84 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 21.8049 | 31.3399 | 0.69575 | 21.8049 | 31.3399 | 0.69575 | 24.1973 | 34.7785 | 0.69575 | 0.8785%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 71 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 95.9693 | 26.4897 | 3.6229 | 95.9693 | 26.4897 | 3.6229 | 106.4988 | 29.3961 | 3.6229 | 0.9868%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 68 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 31.5024 | 25.3704 | 1.2417 | 31.5024 | 25.3704 | 1.2417 | 34.9588 | 28.154 | 1.2417 | 0.9466%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.8972 | 26.1166 | 0.45554 | 11.8972 | 26.1166 | 0.45554 | 13.2025 | 28.9821 | 0.45554 | 0.9088%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 48 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 91.1879 | 17.9085 | 5.0919 | 91.1879 | 17.9085 | 5.0919 | 101.1929 | 19.8734 | 5.0919 | 0.9905%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 29 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 19.2748 | 10.8197 | 1.7814 | 19.2748 | 10.8197 | 1.7814 | 21.3895 | 12.0069 | 1.7814 | 0.9634%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 81 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.7722 | 30.2206 | 0.48881 | 14.7722 | 30.2206 | 0.48881 | 16.393 | 33.5364 | 0.48881 | 0.8429%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 155 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 29.1603 | 57.8296 | 0.50424 | 29.1603 | 57.8296 | 0.50424 | 32.3597 | 64.1746 | 0.50424 | 0.8937%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 33.5564 | 6.3426 | 5.2906 | 33.5564 | 6.3426 | 5.2906 | 37.2381 | 7.0385 | 5.2906 | 0.9991%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 77 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 27.4264 | 28.7283 | 0.95468 | 27.4264 | 28.7283 | 0.95468 | 30.4355 | 31.8803 | 0.95468 | 0.9216%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 93 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 23.9276 | 34.6978 | 0.6896 | 23.9276 | 34.6978 | 0.6896 | 26.5529 | 38.5047 | 0.6896 | 0.9611%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.4289 | 1.1193 | 5.7437 | 6.4289 | 1.1193 | 5.7437 | 7.1342 | 1.2421 | 5.7437 | 0.9946%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 72 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 34.741 | 26.8628 | 1.2933 | 34.741 | 26.8628 | 1.2933 | 38.5527 | 29.8101 | 1.2933 | 0.9703%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 9 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.96674 | 3.3578 | 0.28791 | 0.96674 | 3.3578 | 0.28791 | 1.0728 | 3.7263 | 0.28791 | 0.334%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 4 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 18.6124 | 1.4924 | 12.4716 | 18.6124 | 1.4924 | 12.4716 | 20.6545 | 1.6561 | 12.4716 | 0.9951%
2027 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 1 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 35.4849 | 0.37309 | 95.1098 | 35.4849 | 0.37309 | 95.1098 | 39.3783 | 0.41403 | 95.1098 | 0.9988%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 5 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.5498 | 1.8655 | 2.975 | 5.5498 | 1.8655 | 2.975 | 6.1587 | 2.0701 | 2.975 | 0.9868%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 12 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 40.5593 | 4.4771 | 9.0592 | 40.5593 | 4.4771 | 9.0592 | 45.0094 | 4.9684 | 9.0592 | 0.9945%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 31 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 20.4866 | 11.5659 | 1.7713 | 20.4866 | 11.5659 | 1.7713 | 22.7343 | 12.8349 | 1.7713 | 0.9686%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 18 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 87.1653 | 6.7157 | 12.9793 | 87.1653 | 6.7157 | 12.9793 | 96.7288 | 7.4525 | 12.9793 | 0.9959%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.7708 | 8.5812 | 1.3717 | 11.7708 | 8.5812 | 1.3717 | 13.0623 | 9.5227 | 1.3717 | 0.9515%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 137 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 65.1242 | 51.1139 | 1.2741 | 65.1242 | 51.1139 | 1.2741 | 72.2695 | 56.722 | 1.2741 | 0.9662%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 212 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 715.269 | 79.096 | 9.043 | 715.269 | 79.096 | 9.043 | 793.7467 | 87.7742 | 9.043 | 0.9925%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 32.6952 | 4.8502 | 6.741 | 32.6952 | 4.8502 | 6.741 | 36.2824 | 5.3824 | 6.741 | 0.9927%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 81 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 408.9425 | 30.2206 | 13.5319 | 408.9425 | 30.2206 | 13.5319 | 453.8108 | 33.5364 | 13.5319 | 0.9963%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.2745 | 1.1193 | 2.0321 | 2.2745 | 1.1193 | 2.0321 | 2.5241 | 1.2421 | 2.0321 | 0.8656%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 132 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 64.9142 | 49.2485 | 1.3181 | 64.9142 | 49.2485 | 1.3181 | 72.0364 | 54.6519 | 1.3181 | 0.9605%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 1 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 44.1572 | 0.37309 | 118.3541 | 44.1572 | 0.37309 | 118.3541 | 49.0021 | 0.41403 | 118.3541 | 0.9985%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 1220 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 147.5821 | 455.1752 | 0.32423 | 147.5821 | 455.1752 | 0.32423 | 163.7745 | 505.1159 | 0.32423 | 0.967%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.5515 | 0.37309 | 4.1586 | 1.5515 | 0.37309 | 4.1586 | 1.7218 | 0.41403 | 4.1586 | 0.9937%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 52 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 17.2908 | 19.4009 | 0.89124 | 17.2908 | 19.4009 | 0.89124 | 19.188 | 21.5295 | 0.89124 | 0.9498%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 84 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 57.1262 | 31.3399 | 1.8228 | 57.1262 | 31.3399 | 1.8228 | 63.3939 | 34.7785 | 1.8228 | 0.9826%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 57 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 17.1775 | 21.2664 | 0.80773 | 17.1775 | 21.2664 | 0.80773 | 19.0622 | 23.5997 | 0.80773 | 0.9106%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 17 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.8545 | 6.3426 | 0.60771 | 3.8545 | 6.3426 | 0.60771 | 4.2774 | 7.0385 | 0.60771 | 0.7897%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 6 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.0473 | 2.2386 | 3.1481 | 7.0473 | 2.2386 | 3.1481 | 7.8205 | 2.4842 | 3.1481 | 0.9819%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 52 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 30.8736 | 19.4009 | 1.5913 | 30.8736 | 19.4009 | 1.5913 | 34.261 | 21.5295 | 1.5913 | 0.9768%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0289 | 0.37309 | 2.7577 | 1.0289 | 0.37309 | 2.7577 | 1.1418 | 0.41403 | 2.7577 | 0.9298%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 8 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.4554 | 2.9848 | 0.48761 | 1.4554 | 2.9848 | 0.48761 | 1.6151 | 3.3122 | 0.48761 | 0.8171%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 24.429 | 8.9543 | 2.7282 | 24.429 | 8.9543 | 2.7282 | 27.1093 | 9.9367 | 2.7282 | 0.983%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 151 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 46.1751 | 56.3373 | 0.81962 | 46.1751 | 56.3373 | 0.81962 | 51.2413 | 62.5184 | 0.81962 | 0.9868%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 57 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 27.3047 | 21.2664 | 1.2839 | 27.3047 | 21.2664 | 1.2839 | 30.3005 | 23.5997 | 1.2839 | 0.9884%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 47 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.3838 | 17.5354 | 0.36405 | 6.3838 | 17.5354 | 0.36405 | 7.0842 | 19.4594 | 0.36405 | 0.9757%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 32 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.8693 | 11.939 | 0.32408 | 3.8693 | 11.939 | 0.32408 | 4.2938 | 13.2489 | 0.32408 | 0.9496%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 79 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 18.3049 | 29.4745 | 0.62104 | 18.3049 | 29.4745 | 0.62104 | 20.3133 | 32.7083 | 0.62104 | 0.859%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 40 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 44.7034 | 14.9238 | 2.9955 | 44.7034 | 14.9238 | 2.9955 | 49.6082 | 16.5612 | 2.9955 | 0.9946%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 14 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 35.2843 | 5.2233 | 6.7551 | 35.2843 | 5.2233 | 6.7551 | 39.1556 | 5.7964 | 6.7551 | 0.8863%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 48 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 211.9523 | 17.9085 | 11.8353 | 211.9523 | 17.9085 | 11.8353 | 235.2072 | 19.8734 | 11.8353 | 0.9837%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 48 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 87.3211 | 17.9085 | 4.876 | 87.3211 | 17.9085 | 4.876 | 96.9018 | 19.8734 | 4.876 | 0.9873%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 37 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 24.9907 | 13.8045 | 1.8103 | 24.9907 | 13.8045 | 1.8103 | 27.7326 | 15.3191 | 1.8103 | 0.9726%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 25 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 20.2852 | 9.3274 | 2.1748 | 20.2852 | 9.3274 | 2.1748 | 22.5108 | 10.3507 | 2.1748 | 0.9861%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 51 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 47.5862 | 19.0278 | 2.5009 | 47.5862 | 19.0278 | 2.5009 | 52.8073 | 21.1155 | 2.5009 | 0.9807%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 124 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 189.9659 | 46.2637 | 4.1062 | 189.9659 | 46.2637 | 4.1062 | 210.8085 | 51.3397 | 4.1062 | 0.9836%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 56 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 61.6836 | 20.8933 | 2.9523 | 61.6836 | 20.8933 | 2.9523 | 68.4514 | 23.1856 | 2.9523 | 0.9784%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 16 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 32.8705 | 5.9695 | 5.5064 | 32.8705 | 5.9695 | 5.5064 | 36.477 | 6.6245 | 5.5064 | 0.994%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 62 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 255.3789 | 23.1319 | 11.0401 | 255.3789 | 23.1319 | 11.0401 | 283.3985 | 25.6698 | 11.0401 | 0.9934%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 71 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 243.7006 | 26.4897 | 9.1998 | 243.7006 | 26.4897 | 9.1998 | 270.4388 | 29.3961 | 9.1998 | 0.9889%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 13 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 22.7545 | 4.8502 | 4.6914 | 22.7545 | 4.8502 | 4.6914 | 25.251 | 5.3824 | 4.6914 | 0.9883%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 165 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 278.6354 | 61.5606 | 4.5262 | 278.6354 | 61.5606 | 4.5262 | 309.2066 | 68.3149 | 4.5262 | 0.9911%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 182 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 589.8137 | 67.9032 | 8.6861 | 589.8137 | 67.9032 | 8.6861 | 654.5266 | 75.3534 | 8.6861 | 0.9893%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 21 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.6786 | 7.835 | 0.98004 | 7.6786 | 7.835 | 0.98004 | 8.5211 | 8.6946 | 0.98004 | 0.9808%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 19 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.233 | 7.0888 | 2.0078 | 14.233 | 7.0888 | 2.0078 | 15.7947 | 7.8666 | 2.0078 | 0.9867%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.7998 | 8.5812 | 1.142 | 9.7998 | 8.5812 | 1.142 | 10.875 | 9.5227 | 1.142 | 0.9646%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 72 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 56.0399 | 26.8628 | 2.0862 | 56.0399 | 26.8628 | 2.0862 | 62.1884 | 29.8101 | 2.0862 | 0.9824%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 17 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.49 | 6.3426 | 1.0232 | 6.49 | 6.3426 | 1.0232 | 7.2021 | 7.0385 | 1.0232 | 0.6927%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 18 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.3828 | 6.7157 | 0.50372 | 3.3828 | 6.7157 | 0.50372 | 3.754 | 7.4525 | 0.50372 | 0.9876%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 15 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.5781 | 5.5964 | 1.8902 | 10.5781 | 5.5964 | 1.8902 | 11.7387 | 6.2104 | 1.8902 | 0.9838%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 6 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.1078 | 2.2386 | 3.1751 | 7.1078 | 2.2386 | 3.1751 | 7.8876 | 2.4842 | 3.1751 | 0.987%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 17 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.3211 | 6.3426 | 0.52361 | 3.3211 | 6.3426 | 0.52361 | 3.6854 | 7.0385 | 0.52361 | 0.9688%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 73 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 39.5381 | 27.2359 | 1.4517 | 39.5381 | 27.2359 | 1.4517 | 43.8761 | 30.2242 | 1.4517 | 0.9791%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 50 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 33.7387 | 18.6547 | 1.8086 | 33.7387 | 18.6547 | 1.8086 | 37.4405 | 20.7015 | 1.8086 | 0.9907%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 104 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 32.2959 | 38.8018 | 0.83233 | 32.2959 | 38.8018 | 0.83233 | 35.8393 | 43.0591 | 0.83233 | 0.9682%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 15 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.7642 | 5.5964 | 1.03 | 5.7642 | 5.5964 | 1.03 | 6.3966 | 6.2104 | 1.03 | 0.6596%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 71 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 29.1399 | 26.4897 | 1.1 | 29.1399 | 26.4897 | 1.1 | 32.3371 | 29.3961 | 1.1 | 0.9454%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 33 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 11.4521 | 12.3121 | 0.93015 | 11.4521 | 12.3121 | 0.93015 | 12.7086 | 13.663 | 0.93015 | 0.9251%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 2 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.93993 | 0.74619 | 1.2596 | 0.93993 | 0.74619 | 1.2596 | 1.0431 | 0.82806 | 1.2596 | 0.9818%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 99 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 32.7369 | 36.9363 | 0.8863 | 32.7369 | 36.9363 | 0.8863 | 36.3287 | 40.9889 | 0.8863 | 0.9585%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 3 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.39026 | 1.1193 | 0.34867 | 0.39026 | 1.1193 | 0.34867 | 0.43308 | 1.2421 | 0.34867 | 0.8666%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 29 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 47.5288 | 10.8197 | 4.3928 | 47.5288 | 10.8197 | 4.3928 | 52.7435 | 12.0069 | 4.3928 | 0.9855%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 40 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.0881 | 14.9238 | 1.078 | 16.0881 | 14.9238 | 1.078 | 17.8533 | 16.5612 | 1.078 | 0.878%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 3 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.3417 | 1.1193 | 5.6658 | 6.3417 | 1.1193 | 5.6658 | 7.0375 | 1.2421 | 5.6658 | 0.9241%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.9495 | 2.6117 | 7.6386 | 19.9495 | 2.6117 | 7.6386 | 22.1383 | 2.8982 | 7.6386 | 0.9107%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 26 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 41.4107 | 9.7005 | 4.2689 | 41.4107 | 9.7005 | 4.2689 | 45.9542 | 10.7648 | 4.2689 | 0.9555%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 2 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.35602 | 0.74619 | 0.47712 | 0.35602 | 0.74619 | 0.47712 | 0.39508 | 0.82806 | 0.47712 | 0.8469%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 4 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.4128 | 1.4924 | 0.27661 | 0.4128 | 1.4924 | 0.27661 | 0.4581 | 1.6561 | 0.27661 | 0.1628%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 1 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.732 | 0.37309 | 7.3224 | 2.732 | 0.37309 | 7.3224 | 3.0317 | 0.41403 | 7.3224 | 0.9927%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 138 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 31.2978 | 51.487 | 0.60788 | 31.2978 | 51.487 | 0.60788 | 34.7317 | 57.1361 | 0.60788 | 0.9548%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 245 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 123.8786 | 91.4081 | 1.3552 | 123.8786 | 91.4081 | 1.3552 | 137.4703 | 101.4372 | 1.3552 | 0.9814%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 229 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 49.1654 | 85.4386 | 0.57545 | 49.1654 | 85.4386 | 0.57545 | 54.5597 | 94.8127 | 0.57545 | 0.9699%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 122.1654 | 34.3247 | 3.5591 | 122.1654 | 34.3247 | 3.5591 | 135.5691 | 38.0907 | 3.5591 | 0.9928%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 107 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 100.7847 | 39.9211 | 2.5246 | 100.7847 | 39.9211 | 2.5246 | 111.8425 | 44.3012 | 2.5246 | 0.9888%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 212.4003 | 21.6395 | 9.8154 | 212.4003 | 21.6395 | 9.8154 | 235.7044 | 24.0137 | 9.8154 | 0.9925%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 22 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 82.9876 | 8.2081 | 10.1105 | 82.9876 | 8.2081 | 10.1105 | 92.0928 | 9.1086 | 10.1105 | 0.9973%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 76 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 168.3033 | 28.3552 | 5.9355 | 168.3033 | 28.3552 | 5.9355 | 186.7692 | 31.4662 | 5.9355 | 0.9936%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 40 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 81.809 | 14.9238 | 5.4818 | 81.809 | 14.9238 | 5.4818 | 90.7849 | 16.5612 | 5.4818 | 0.9749%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 22.7355 | 2.6117 | 8.7054 | 22.7355 | 2.6117 | 8.7054 | 25.2299 | 2.8982 | 8.7054 | 0.9918%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 1 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 20.1485 | 0.37309 | 54.0037 | 20.1485 | 0.37309 | 54.0037 | 22.3591 | 0.41403 | 54.0037 | 0.9993%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 7 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.0724 | 2.6117 | 6.1541 | 16.0724 | 2.6117 | 6.1541 | 17.8358 | 2.8982 | 6.1541 | 0.8869%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 23 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 39.0935 | 8.5812 | 4.5557 | 39.0935 | 8.5812 | 4.5557 | 43.3827 | 9.5227 | 4.5557 | 0.943%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 1 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.6596 | 0.37309 | 7.1285 | 2.6596 | 0.37309 | 7.1285 | 2.9514 | 0.41403 | 7.1285 | 0.6284%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 42 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 122.4623 | 15.67 | 7.8151 | 122.4623 | 15.67 | 7.8151 | 135.8986 | 17.3892 | 7.8151 | 0.9943%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 121 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 185.0853 | 45.1444 | 4.0998 | 185.0853 | 45.1444 | 4.0998 | 205.3924 | 50.0976 | 4.0998 | 0.9917%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 15 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 29.4362 | 5.5964 | 5.2598 | 29.4362 | 5.5964 | 5.2598 | 32.6658 | 6.2104 | 5.2598 | 0.8854%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 64 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 67.231 | 23.878 | 2.8156 | 67.231 | 23.878 | 2.8156 | 74.6075 | 26.4979 | 2.8156 | 0.985%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.357 | 5.9695 | 2.07 | 12.357 | 5.9695 | 2.07 | 13.7128 | 6.6245 | 2.07 | 0.7994%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 50 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 48.5603 | 18.6547 | 2.6031 | 48.5603 | 18.6547 | 2.6031 | 53.8882 | 20.7015 | 2.6031 | 0.9814%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 140 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 142.4543 | 52.2332 | 2.7273 | 142.4543 | 52.2332 | 2.7273 | 158.0841 | 57.9641 | 2.7273 | 0.9776%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 80.6995 | 34.3247 | 2.3511 | 80.6995 | 34.3247 | 2.3511 | 89.5536 | 38.0907 | 2.3511 | 0.9541%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 5 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.2788 | 1.8655 | 6.0461 | 11.2788 | 1.8655 | 6.0461 | 12.5163 | 2.0701 | 6.0461 | 0.9906%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 11 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 46.2497 | 4.104 | 11.2693 | 46.2497 | 4.104 | 11.2693 | 51.3241 | 4.5543 | 11.2693 | 0.9968%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 3 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.6371 | 1.1193 | 6.8232 | 7.6371 | 1.1193 | 6.8232 | 8.475 | 1.2421 | 6.8232 | 0.9549%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 84 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 151.6491 | 31.3399 | 4.8388 | 151.6491 | 31.3399 | 4.8388 | 168.2877 | 34.7785 | 4.8388 | 0.9879%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 116 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 156.9706 | 43.279 | 3.6269 | 156.9706 | 43.279 | 3.6269 | 174.193 | 48.0274 | 3.6269 | 0.9747%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 116 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 92.1224 | 43.279 | 2.1286 | 92.1224 | 43.279 | 2.1286 | 102.2299 | 48.0274 | 2.1286 | 0.9704%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 94 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 104.6452 | 35.0709 | 2.9838 | 104.6452 | 35.0709 | 2.9838 | 116.1267 | 38.9188 | 2.9838 | 0.9781%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 4 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.3037 | 1.4924 | 3.5539 | 5.3037 | 1.4924 | 3.5539 | 5.8856 | 1.6561 | 3.5539 | 0.9721%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 3 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.1945 | 1.1193 | 10.8949 | 12.1945 | 1.1193 | 10.8949 | 13.5325 | 1.2421 | 10.8949 | 0.9966%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 99 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 337.3598 | 36.9363 | 9.1335 | 337.3598 | 36.9363 | 9.1335 | 374.3741 | 40.9889 | 9.1335 | 0.9859%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 4 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.7862 | 1.4924 | 7.8976 | 11.7862 | 1.4924 | 7.8976 | 13.0794 | 1.6561 | 7.8976 | 0.8901%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 2 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5811 | 0.74619 | 2.1189 | 1.5811 | 0.74619 | 2.1189 | 1.7545 | 0.82806 | 2.1189 | 0.1879%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 65 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 25.1718 | 24.2511 | 1.038 | 25.1718 | 24.2511 | 1.038 | 27.9336 | 26.9119 | 1.038 | 0.8818%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 21 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 16.5372 | 7.835 | 2.1107 | 16.5372 | 7.835 | 2.1107 | 18.3516 | 8.6946 | 2.1107 | 0.9783%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 90 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 57.0772 | 33.5785 | 1.6998 | 57.0772 | 33.5785 | 1.6998 | 63.3396 | 37.2627 | 1.6998 | 0.9847%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 2 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.7938 | 0.74619 | 15.8054 | 11.7938 | 0.74619 | 15.8054 | 13.0878 | 0.82806 | 15.8054 | 0.9597%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 15 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 31.198 | 5.5964 | 5.5746 | 31.198 | 5.5964 | 5.5746 | 34.621 | 6.2104 | 5.5746 | 0.9745%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 6 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.8386 | 2.2386 | 2.1615 | 4.8386 | 2.2386 | 2.1615 | 5.3695 | 2.4842 | 2.1615 | 0.9134%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 27 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 42.3621 | 10.0735 | 4.2053 | 42.3621 | 10.0735 | 4.2053 | 47.01 | 11.1788 | 4.2053 | 0.98%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 26 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 47.9792 | 9.7005 | 4.9461 | 47.9792 | 9.7005 | 4.9461 | 53.2434 | 10.7648 | 4.9461 | 0.9857%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 26 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.0443 | 9.7005 | 1.654 | 16.0443 | 9.7005 | 1.654 | 17.8046 | 10.7648 | 1.654 | 0.9609%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 1 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.013995 | 0.37309 | 0.037511 | 0.013995 | 0.37309 | 0.037511 | 0.015531 | 0.41403 | 0.037511 | 0.01745%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 31 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.5914 | 11.5659 | 0.5699 | 6.5914 | 11.5659 | 0.5699 | 7.3146 | 12.8349 | 0.5699 | 0.8492%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 22 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.7746 | 8.2081 | 0.33803 | 2.7746 | 8.2081 | 0.33803 | 3.079 | 9.1086 | 0.33803 | 0.5795%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 161 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 93.1705 | 60.0682 | 1.5511 | 93.1705 | 60.0682 | 1.5511 | 103.393 | 66.6587 | 1.5511 | 0.8848%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 14 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 6.1949 | 5.2233 | 1.186 | 6.1949 | 5.2233 | 1.186 | 6.8746 | 5.7964 | 1.186 | 0.9662%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 1 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.951 | 0.37309 | 13.2701 | 4.951 | 0.37309 | 13.2701 | 5.4942 | 0.41403 | 13.2701 | 0.9893%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 12 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.9446 | 4.4771 | 0.88106 | 3.9446 | 4.4771 | 0.88106 | 4.3774 | 4.9684 | 0.88106 | 0.9131%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 16 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.65617 | 5.9695 | 0.10992 | 0.65617 | 5.9695 | 0.10992 | 0.72816 | 6.6245 | 0.10992 | 0.51%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 13 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 2.9352 | 4.8502 | 0.60517 | 2.9352 | 4.8502 | 0.60517 | 3.2572 | 5.3824 | 0.60517 | 0.9662%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 102 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 30.3414 | 38.0556 | 0.79729 | 30.3414 | 38.0556 | 0.79729 | 33.6704 | 42.231 | 0.79729 | 0.9767%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 90 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.6755 | 33.5785 | 0.10946 | 3.6755 | 33.5785 | 0.10946 | 4.0788 | 37.2627 | 0.10946 | 0.7071%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 85 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 83.235 | 31.713 | 2.6246 | 83.235 | 31.713 | 2.6246 | 92.3673 | 35.1925 | 2.6246 | 0.9496%
2027 | 445 | 445-1315 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 0.26142 | 0 | 0 | 0.26142 | 0 | 0.23789 | 0.37309 | 0.63762 | 0.23789 | 0.37309 | 0.63762 | 0.26399 | 0.41403 | 0.63762 | 0.9959%
2027 | 445 | 445-1323 | Tier-2 | Tier-2---18 | Tier-2---12 | 1 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 0.77964 | 0 | 0 | 0.77964 | 0 | 0.70946 | 0.37309 | 1.9016 | 0.70946 | 0.37309 | 1.9016 | 0.7873 | 0.41403 | 1.9016 | 0.9926%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 76 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 63.4108 | 28.3552 | 2.2363 | 63.4108 | 28.3552 | 2.2363 | 70.3681 | 31.4662 | 2.2363 | 0.9611%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 43 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.9463 | 16.0431 | 0.80697 | 12.9463 | 16.0431 | 0.80697 | 14.3667 | 17.8033 | 0.80697 | 0.8872%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 116 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 92.4716 | 43.279 | 2.1366 | 92.4716 | 43.279 | 2.1366 | 102.6173 | 48.0274 | 2.1366 | 0.9569%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 65 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 13.6213 | 24.2511 | 0.56168 | 13.6213 | 24.2511 | 0.56168 | 15.1158 | 26.9119 | 0.56168 | 0.8473%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 91 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 29.3039 | 33.9516 | 0.86311 | 29.3039 | 33.9516 | 0.86311 | 32.5191 | 37.6767 | 0.86311 | 0.8754%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 156 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 35.4517 | 58.2027 | 0.60911 | 35.4517 | 58.2027 | 0.60911 | 39.3413 | 64.5886 | 0.60911 | 0.8812%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 9 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.9618 | 3.3578 | 3.5623 | 11.9618 | 3.3578 | 3.5623 | 13.2742 | 3.7263 | 3.5623 | 0.9724%
2027 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.16597 | 0 | 0 | 0.16597 | 0 | 0.15103 | 0.37309 | 0.40481 | 0.15103 | 0.37309 | 0.40481 | 0.1676 | 0.41403 | 0.40481 | 0.9941%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 9 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.7378 | 3.3578 | 3.1978 | 10.7378 | 3.3578 | 3.1978 | 11.9159 | 3.7263 | 3.1978 | 0.9739%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 43 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 21.8479 | 16.0431 | 1.3618 | 21.8479 | 16.0431 | 1.3618 | 24.245 | 17.8033 | 1.3618 | 0.9191%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 85 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.7439 | 31.713 | 0.33878 | 10.7439 | 31.713 | 0.33878 | 11.9227 | 35.1925 | 0.33878 | 0.557%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.6094 | 18.2816 | 0.19743 | 3.6094 | 18.2816 | 0.19743 | 4.0054 | 20.2874 | 0.19743 | 0.7618%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 45 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.5415 | 16.7892 | 0.2705 | 4.5415 | 16.7892 | 0.2705 | 5.0398 | 18.6313 | 0.2705 | 0.7912%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 224 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 75.9584 | 83.5731 | 0.90888 | 75.9584 | 83.5731 | 0.90888 | 84.2924 | 92.7426 | 0.90888 | 0.9168%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 106 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 47.9898 | 39.548 | 1.2135 | 47.9898 | 39.548 | 1.2135 | 53.2551 | 43.8871 | 1.2135 | 0.9343%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 147 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 55.4184 | 54.8449 | 1.0105 | 55.4184 | 54.8449 | 1.0105 | 61.4988 | 60.8623 | 1.0105 | 0.9049%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 22 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.1969 | 8.2081 | 1.6078 | 13.1969 | 8.2081 | 1.6078 | 14.6448 | 9.1086 | 1.6078 | 0.9697%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 7 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.5023 | 2.6117 | 2.1068 | 5.5023 | 2.6117 | 2.1068 | 6.106 | 2.8982 | 2.1068 | 0.967%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 34 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 47.2842 | 12.6852 | 3.7275 | 47.2842 | 12.6852 | 3.7275 | 52.4721 | 14.077 | 3.7275 | 0.9877%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 45 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 20.1718 | 16.7892 | 1.2015 | 20.1718 | 16.7892 | 1.2015 | 22.385 | 18.6313 | 1.2015 | 0.9555%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 26 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 74.7143 | 9.7005 | 7.7021 | 74.7143 | 9.7005 | 7.7021 | 82.9117 | 10.7648 | 7.7021 | 0.9923%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 5 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.6876 | 1.8655 | 3.5849 | 6.6876 | 1.8655 | 3.5849 | 7.4213 | 2.0701 | 3.5849 | 0.9277%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 2 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.8144 | 0.74619 | 13.1526 | 9.8144 | 0.74619 | 13.1526 | 10.8912 | 0.82806 | 13.1526 | 0.9525%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 2 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 25.6788 | 0.74619 | 34.4132 | 25.6788 | 0.74619 | 34.4132 | 28.4962 | 0.82806 | 34.4132 | 0.9993%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 1 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 31.2198 | 0.37309 | 83.678 | 31.2198 | 0.37309 | 83.678 | 34.6452 | 0.41403 | 83.678 | 0.997%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.77971 | 0.74619 | 1.0449 | 0.77971 | 0.74619 | 1.0449 | 0.86526 | 0.82806 | 1.0449 | 0.9735%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 20 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 12.4192 | 7.4619 | 1.6644 | 12.4192 | 7.4619 | 1.6644 | 13.7819 | 8.2806 | 1.6644 | 0.9902%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 20 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 47.1097 | 7.4619 | 6.3134 | 47.1097 | 7.4619 | 6.3134 | 52.2785 | 8.2806 | 6.3134 | 0.9833%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 53 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 151.376 | 19.774 | 7.6553 | 151.376 | 19.774 | 7.6553 | 167.9846 | 21.9436 | 7.6553 | 0.9937%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 6 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 36.7559 | 2.2386 | 16.4194 | 36.7559 | 2.2386 | 16.4194 | 40.7887 | 2.4842 | 16.4194 | 0.9496%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 3 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.5736 | 1.1193 | 1.4059 | 1.5736 | 1.1193 | 1.4059 | 1.7463 | 1.2421 | 1.4059 | 0.216%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 1 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.8503 | 0.37309 | 4.9593 | 1.8503 | 0.37309 | 4.9593 | 2.0533 | 0.41403 | 4.9593 | 0.9963%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 2 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.6436 | 0.74619 | 8.9034 | 6.6436 | 0.74619 | 8.9034 | 7.3725 | 0.82806 | 8.9034 | 0.9951%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 47 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 26.387 | 17.5354 | 1.5048 | 26.387 | 17.5354 | 1.5048 | 29.2822 | 19.4594 | 1.5048 | 0.9734%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 27 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.1838 | 10.0735 | 1.3088 | 13.1838 | 10.0735 | 1.3088 | 14.6303 | 11.1788 | 1.3088 | 0.9797%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 129 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 23.2262 | 48.1292 | 0.48258 | 23.2262 | 48.1292 | 0.48258 | 25.7745 | 53.4098 | 0.48258 | 0.9676%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 84 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 28.8046 | 31.3399 | 0.9191 | 28.8046 | 31.3399 | 0.9191 | 31.965 | 34.7785 | 0.9191 | 0.9272%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 31 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 14.6037 | 11.5659 | 1.2626 | 14.6037 | 11.5659 | 1.2626 | 16.206 | 12.8349 | 1.2626 | 0.9829%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 53 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 59.5224 | 19.774 | 3.0101 | 59.5224 | 19.774 | 3.0101 | 66.053 | 21.9436 | 3.0101 | 0.9672%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.2665 | 1.1193 | 4.7052 | 5.2665 | 1.1193 | 4.7052 | 5.8443 | 1.2421 | 4.7052 | 0.7734%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 19 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 18.3018 | 7.0888 | 2.5818 | 18.3018 | 7.0888 | 2.5818 | 20.3098 | 7.8666 | 2.5818 | 0.9648%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 89 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 43.8849 | 33.2054 | 1.3216 | 43.8849 | 33.2054 | 1.3216 | 48.6999 | 36.8486 | 1.3216 | 0.9649%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 74 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 18.1542 | 27.609 | 0.65755 | 18.1542 | 27.609 | 0.65755 | 20.1461 | 30.6382 | 0.65755 | 0.9757%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 49 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 99.8685 | 18.2816 | 5.4628 | 99.8685 | 18.2816 | 5.4628 | 110.8258 | 20.2874 | 5.4628 | 0.9669%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 87 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 75.4437 | 32.4592 | 2.3243 | 75.4437 | 32.4592 | 2.3243 | 83.7212 | 36.0206 | 2.3243 | 0.9779%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 73 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 78.7812 | 27.2359 | 2.8926 | 78.7812 | 27.2359 | 2.8926 | 87.4249 | 30.2242 | 2.8926 | 0.9936%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 25 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 50.5044 | 9.3274 | 5.4147 | 50.5044 | 9.3274 | 5.4147 | 56.0457 | 10.3507 | 5.4147 | 0.9878%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 42 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 110.706 | 15.67 | 7.0649 | 110.706 | 15.67 | 7.0649 | 122.8524 | 17.3892 | 7.0649 | 0.9938%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 37 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 81.2357 | 13.8045 | 5.8847 | 81.2357 | 13.8045 | 5.8847 | 90.1487 | 15.3191 | 5.8847 | 0.9905%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 49.4954 | 0.37309 | 132.6619 | 49.4954 | 0.37309 | 132.6619 | 54.926 | 0.41403 | 132.6619 | 0.9644%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 46 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 49.6477 | 17.1623 | 2.8928 | 49.6477 | 17.1623 | 2.8928 | 55.0949 | 19.0454 | 2.8928 | 0.9978%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 114 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 102.7516 | 42.5328 | 2.4158 | 102.7516 | 42.5328 | 2.4158 | 114.0253 | 47.1994 | 2.4158 | 0.9977%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 89 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 123.504 | 33.2054 | 3.7194 | 123.504 | 33.2054 | 3.7194 | 137.0546 | 36.8486 | 3.7194 | 0.9899%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 78.6546 | 31.3399 | 2.5097 | 78.6546 | 31.3399 | 2.5097 | 87.2844 | 34.7785 | 2.5097 | 0.982%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 283 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 363.8583 | 105.5857 | 3.4461 | 363.8583 | 105.5857 | 3.4461 | 403.78 | 117.1703 | 3.4461 | 0.9903%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 92 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 163.2404 | 34.3247 | 4.7558 | 163.2404 | 34.3247 | 4.7558 | 181.1508 | 38.0907 | 4.7558 | 0.9555%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 124 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 232.8474 | 46.2637 | 5.033 | 232.8474 | 46.2637 | 5.033 | 258.3948 | 51.3397 | 5.033 | 0.994%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 112 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 22.2363 | 41.7866 | 0.53214 | 22.2363 | 41.7866 | 0.53214 | 24.676 | 46.3713 | 0.53214 | 0.936%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 188 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 35.6813 | 70.1418 | 0.5087 | 35.6813 | 70.1418 | 0.5087 | 39.5962 | 77.8375 | 0.5087 | 0.938%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 55 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.9369 | 20.5202 | 0.24059 | 4.9369 | 20.5202 | 0.24059 | 5.4786 | 22.7716 | 0.24059 | 0.8718%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 78 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.7454 | 29.1014 | 0.47233 | 13.7454 | 29.1014 | 0.47233 | 15.2535 | 32.2943 | 0.47233 | 0.9279%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 84 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 54.9037 | 31.3399 | 1.7519 | 54.9037 | 31.3399 | 1.7519 | 60.9276 | 34.7785 | 1.7519 | 0.9729%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 90 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 137.5579 | 33.5785 | 4.0966 | 137.5579 | 33.5785 | 4.0966 | 152.6504 | 37.2627 | 4.0966 | 0.9856%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 21 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 21.9808 | 7.835 | 2.8055 | 21.9808 | 7.835 | 2.8055 | 24.3925 | 8.6946 | 2.8055 | 0.9864%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 56 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 51.3459 | 20.8933 | 2.4575 | 51.3459 | 20.8933 | 2.4575 | 56.9795 | 23.1856 | 2.4575 | 0.9841%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 93 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 94.7516 | 34.6978 | 2.7308 | 94.7516 | 34.6978 | 2.7308 | 105.1476 | 38.5047 | 2.7308 | 0.9831%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 83.1913 | 31.3399 | 2.6545 | 83.1913 | 31.3399 | 2.6545 | 92.3189 | 34.7785 | 2.6545 | 0.9843%
2027 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.16088 | 0.74619 | 0.2156 | 0.16088 | 0.74619 | 0.2156 | 0.17853 | 0.82806 | 0.2156 | 0.9934%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 32 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 28.4668 | 11.939 | 2.3844 | 28.4668 | 11.939 | 2.3844 | 31.5901 | 13.2489 | 2.3844 | 0.9977%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 15 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 15.48 | 5.5964 | 2.766 | 15.48 | 5.5964 | 2.766 | 17.1784 | 6.2104 | 2.766 | 0.9957%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 4 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 17.6067 | 1.4924 | 11.7978 | 17.6067 | 1.4924 | 11.7978 | 19.5385 | 1.6561 | 11.7978 | 0.9986%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 46 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.9656 | 17.1623 | 1.1633 | 19.9656 | 17.1623 | 1.1633 | 22.1561 | 19.0454 | 1.1633 | 0.9923%
2027 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 1 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 0.41445 | 0 | 0 | 0.41445 | 0 | 0.37715 | 0.37309 | 1.0109 | 0.37715 | 0.37309 | 1.0109 | 0.41852 | 0.41403 | 1.0109 | 0.9749%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 60 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 130.2838 | 22.3857 | 5.82 | 130.2838 | 22.3857 | 5.82 | 144.5782 | 24.8418 | 5.82 | 0.9856%
2027 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 1 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 56.9533 | 0 | 0 | 56.9533 | 0 | 51.8267 | 0.37309 | 138.9104 | 51.8267 | 0.37309 | 138.9104 | 57.513 | 0.41403 | 138.9104 | 0.9998%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 13 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 65.2205 | 4.8502 | 13.4469 | 65.2205 | 4.8502 | 13.4469 | 72.3764 | 5.3824 | 13.4469 | 0.9951%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 37 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 78.3924 | 13.8045 | 5.6788 | 78.3924 | 13.8045 | 5.6788 | 86.9934 | 15.3191 | 5.6788 | 0.9433%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 5 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 28.2206 | 1.8655 | 15.1279 | 28.2206 | 1.8655 | 15.1279 | 31.317 | 2.0701 | 15.1279 | 0.9258%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 34 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 111.2949 | 12.6852 | 8.7736 | 111.2949 | 12.6852 | 8.7736 | 123.5059 | 14.077 | 8.7736 | 0.9926%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 20 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 18.5106 | 7.4619 | 2.4807 | 18.5106 | 7.4619 | 2.4807 | 20.5416 | 8.2806 | 2.4807 | 0.9747%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 77 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.3713 | 28.7283 | 0.36101 | 10.3713 | 28.7283 | 0.36101 | 11.5092 | 31.8803 | 0.36101 | 0.7093%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 28 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 86.8821 | 10.4466 | 8.3167 | 86.8821 | 10.4466 | 8.3167 | 96.4146 | 11.5928 | 8.3167 | 0.9829%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 59 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 166.0282 | 22.0126 | 7.5424 | 166.0282 | 22.0126 | 7.5424 | 184.2444 | 24.4277 | 7.5424 | 0.989%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 2 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 23.1929 | 0.74619 | 31.0817 | 23.1929 | 0.74619 | 31.0817 | 25.7375 | 0.82806 | 31.0817 | 0.9937%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 50 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 48.5255 | 18.6547 | 2.6012 | 48.5255 | 18.6547 | 2.6012 | 53.8496 | 20.7015 | 2.6012 | 0.9631%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 107 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 166.0224 | 39.9211 | 4.1588 | 166.0224 | 39.9211 | 4.1588 | 184.2379 | 44.3012 | 4.1588 | 0.9714%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 15 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 26.8212 | 5.5964 | 4.7926 | 26.8212 | 5.5964 | 4.7926 | 29.764 | 6.2104 | 4.7926 | 0.9712%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 56 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 180.4018 | 20.8933 | 8.6344 | 180.4018 | 20.8933 | 8.6344 | 200.1951 | 23.1856 | 8.6344 | 0.9923%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.1511 | 0.74619 | 1.5426 | 1.1511 | 0.74619 | 1.5426 | 1.2774 | 0.82806 | 1.5426 | 0.9928%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.060511 | 0.37309 | 0.16219 | 0.060511 | 0.37309 | 0.16219 | 0.06715 | 0.41403 | 0.16219 | 0.9902%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 2 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.9878 | 0.74619 | 4.0041 | 2.9878 | 0.74619 | 4.0041 | 3.3156 | 0.82806 | 4.0041 | 0.9939%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 12 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.0456 | 4.4771 | 0.4569 | 2.0456 | 4.4771 | 0.4569 | 2.27 | 4.9684 | 0.4569 | 0.9666%
2027 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 1.8833 | 0 | 0 | 1.8833 | 0 | 1.7138 | 0.74619 | 2.2967 | 1.7138 | 0.74619 | 2.2967 | 1.9018 | 0.82806 | 2.2967 | 0.9988%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 41 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 78.2117 | 15.2969 | 5.1129 | 78.2117 | 15.2969 | 5.1129 | 86.793 | 16.9752 | 5.1129 | 0.9986%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 37 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 74.9698 | 13.8045 | 5.4308 | 74.9698 | 13.8045 | 5.4308 | 83.1953 | 15.3191 | 5.4308 | 0.9762%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.3096 | 0.37309 | 6.1905 | 2.3096 | 0.37309 | 6.1905 | 2.563 | 0.41403 | 6.1905 | 0.9867%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 35 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 82.5872 | 13.0583 | 6.3245 | 82.5872 | 13.0583 | 6.3245 | 91.6485 | 14.491 | 6.3245 | 0.9973%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 74 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 244.3147 | 27.609 | 8.8491 | 244.3147 | 27.609 | 8.8491 | 271.1204 | 30.6382 | 8.8491 | 0.9919%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 2 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 57.7563 | 0.74619 | 77.4018 | 57.7563 | 0.74619 | 77.4018 | 64.0932 | 0.82806 | 77.4018 | 0.9998%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 76 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 141.0713 | 28.3552 | 4.9752 | 141.0713 | 28.3552 | 4.9752 | 156.5494 | 31.4662 | 4.9752 | 0.9833%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 28 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 105.7677 | 10.4466 | 10.1246 | 105.7677 | 10.4466 | 10.1246 | 117.3723 | 11.5928 | 10.1246 | 0.988%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 109 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 48.7918 | 40.6673 | 1.1998 | 48.7918 | 40.6673 | 1.1998 | 54.1451 | 45.1292 | 1.1998 | 0.9625%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 40 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.2496 | 14.9238 | 0.82081 | 12.2496 | 14.9238 | 0.82081 | 13.5936 | 16.5612 | 0.82081 | 0.9181%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 21 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 71.2405 | 7.835 | 9.0926 | 71.2405 | 7.835 | 9.0926 | 79.0568 | 8.6946 | 9.0926 | 0.9835%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 146 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 371.2832 | 54.4718 | 6.8161 | 371.2832 | 54.4718 | 6.8161 | 412.0195 | 60.4483 | 6.8161 | 0.9889%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 46 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 30.5007 | 17.1623 | 1.7772 | 30.5007 | 17.1623 | 1.7772 | 33.8472 | 19.0454 | 1.7772 | 0.9191%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 203.4497 | 35.444 | 5.74 | 203.4497 | 35.444 | 5.74 | 225.7718 | 39.3328 | 5.74 | 0.9908%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 1 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3753 | 0.37309 | 3.6861 | 1.3753 | 0.37309 | 3.6861 | 1.5261 | 0.41403 | 3.6861 | 0.9858%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 10 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.4441 | 3.7309 | 1.9952 | 7.4441 | 3.7309 | 1.9952 | 8.2609 | 4.1403 | 1.9952 | 0.9652%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 126 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 499.1345 | 47.0099 | 10.6176 | 499.1345 | 47.0099 | 10.6176 | 553.8984 | 52.1677 | 10.6176 | 0.9927%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 99 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 291.8804 | 36.9363 | 7.9023 | 291.8804 | 36.9363 | 7.9023 | 323.9049 | 40.9889 | 7.9023 | 0.9926%
2027 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 0.62909 | 0 | 0 | 0.62909 | 0 | 0.57247 | 0.37309 | 1.5344 | 0.57247 | 0.37309 | 1.5344 | 0.63527 | 0.41403 | 1.5344 | 0.9988%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 28 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.3192 | 10.4466 | 1.0835 | 11.3192 | 10.4466 | 1.0835 | 12.5611 | 11.5928 | 1.0835 | 0.9598%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 12 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 30.7953 | 4.4771 | 6.8783 | 30.7953 | 4.4771 | 6.8783 | 34.1741 | 4.9684 | 6.8783 | 0.9934%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.7625 | 1.1193 | 8.7221 | 9.7625 | 1.1193 | 8.7221 | 10.8336 | 1.2421 | 8.7221 | 0.6902%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 2 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.8843 | 0.74619 | 18.607 | 13.8843 | 0.74619 | 18.607 | 15.4077 | 0.82806 | 18.607 | 0.7661%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.9364 | 0.74619 | 5.2754 | 3.9364 | 0.74619 | 5.2754 | 4.3683 | 0.82806 | 5.2754 | 0.9947%
2027 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 5 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.55108 | 1.8655 | 0.29541 | 0.55108 | 1.8655 | 0.29541 | 0.61155 | 2.0701 | 0.29541 | 0.9691%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 11 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 117.5454 | 4.104 | 28.6414 | 117.5454 | 4.104 | 28.6414 | 130.4422 | 4.5543 | 28.6414 | 0.9966%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 100 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 136.5462 | 37.3094 | 3.6598 | 136.5462 | 37.3094 | 3.6598 | 151.5277 | 41.4029 | 3.6598 | 0.9905%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 189 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 256.3868 | 70.5148 | 3.6359 | 256.3868 | 70.5148 | 3.6359 | 284.5169 | 78.2516 | 3.6359 | 0.9891%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 28 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 72.5488 | 10.4466 | 6.9447 | 72.5488 | 10.4466 | 6.9447 | 80.5087 | 11.5928 | 6.9447 | 0.9946%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 11 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 39.4065 | 4.104 | 9.6019 | 39.4065 | 4.104 | 9.6019 | 43.7301 | 4.5543 | 9.6019 | 0.9952%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 45 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 132.3028 | 16.7892 | 7.8802 | 132.3028 | 16.7892 | 7.8802 | 146.8188 | 18.6313 | 7.8802 | 0.9843%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 103 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 101.4885 | 38.4287 | 2.641 | 101.4885 | 38.4287 | 2.641 | 112.6235 | 42.645 | 2.641 | 0.9898%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 81 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 71.9042 | 30.2206 | 2.3793 | 71.9042 | 30.2206 | 2.3793 | 79.7933 | 33.5364 | 2.3793 | 0.9853%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 106 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 209.5961 | 39.548 | 5.2998 | 209.5961 | 39.548 | 5.2998 | 232.5925 | 43.8871 | 5.2998 | 0.9839%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 54 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 203.259 | 20.1471 | 10.0887 | 203.259 | 20.1471 | 10.0887 | 225.5601 | 22.3576 | 10.0887 | 0.9748%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 82.5252 | 22.0126 | 3.749 | 82.5252 | 22.0126 | 3.749 | 91.5797 | 24.4277 | 3.749 | 0.9912%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 50 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 45.8566 | 18.6547 | 2.4582 | 45.8566 | 18.6547 | 2.4582 | 50.8879 | 20.7015 | 2.4582 | 0.9732%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 19 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 78.0753 | 7.0888 | 11.0139 | 78.0753 | 7.0888 | 11.0139 | 86.6415 | 7.8666 | 11.0139 | 0.9953%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 82 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 58.178 | 30.5937 | 1.9016 | 58.178 | 30.5937 | 1.9016 | 64.5612 | 33.9504 | 1.9016 | 0.9803%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 104 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 29.7799 | 38.8018 | 0.76749 | 29.7799 | 38.8018 | 0.76749 | 33.0473 | 43.0591 | 0.76749 | 0.9369%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 29 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 64.3818 | 10.8197 | 5.9504 | 64.3818 | 10.8197 | 5.9504 | 71.4456 | 12.0069 | 5.9504 | 0.9955%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 1 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 46.8889 | 0.37309 | 125.6757 | 46.8889 | 0.37309 | 125.6757 | 52.0335 | 0.41403 | 125.6757 | 0.803%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 11 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.7574 | 4.104 | 0.91553 | 3.7574 | 4.104 | 0.91553 | 4.1696 | 4.5543 | 0.91553 | 0.6587%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 17 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 41.5562 | 6.3426 | 6.5519 | 41.5562 | 6.3426 | 6.5519 | 46.1156 | 7.0385 | 6.5519 | 0.9978%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 1 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 30.2704 | 0.37309 | 81.1333 | 30.2704 | 0.37309 | 81.1333 | 33.5916 | 0.41403 | 81.1333 | 0.9981%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 24 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.8231 | 8.9543 | 1.4321 | 12.8231 | 8.9543 | 1.4321 | 14.23 | 9.9367 | 1.4321 | 0.9962%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 1 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.2838 | 0.37309 | 27.5635 | 10.2838 | 0.37309 | 27.5635 | 11.4121 | 0.41403 | 27.5635 | 0.9972%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 4 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.1761 | 1.4924 | 3.4684 | 5.1761 | 1.4924 | 3.4684 | 5.7441 | 1.6561 | 3.4684 | 0.3454%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.2241 | 7.0888 | 0.73696 | 5.2241 | 7.0888 | 0.73696 | 5.7973 | 7.8666 | 0.73696 | 0.75%
2027 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | Tier-2---20 | 2 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.030773 | 0 | 0 | 0.030773 | 0 | 0.028003 | 0.74619 | 0.037528 | 0.028003 | 0.74619 | 0.037528 | 0.031075 | 0.82806 | 0.037528 | 0.1687%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 3 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.66137 | 1.1193 | 0.59089 | 0.66137 | 1.1193 | 0.59089 | 0.73393 | 1.2421 | 0.59089 | 0.9665%
2027 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 0.21747 | 0 | 0 | 0.21747 | 0 | 0.1979 | 0.37309 | 0.53042 | 0.1979 | 0.37309 | 0.53042 | 0.21961 | 0.41403 | 0.53042 | 0.9966%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 79 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 48.4098 | 29.4745 | 1.6424 | 48.4098 | 29.4745 | 1.6424 | 53.7212 | 32.7083 | 1.6424 | 0.8429%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 92 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 59.9246 | 34.3247 | 1.7458 | 59.9246 | 34.3247 | 1.7458 | 66.4994 | 38.0907 | 1.7458 | 0.9909%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 30 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.0561 | 11.1928 | 1.1665 | 13.0561 | 11.1928 | 1.1665 | 14.4885 | 12.4209 | 1.1665 | 0.9975%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.98124 | 0.74619 | 1.315 | 0.98124 | 0.74619 | 1.315 | 1.0889 | 0.82806 | 1.315 | 0.9975%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 2 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 37.0598 | 0.74619 | 49.6654 | 37.0598 | 0.74619 | 49.6654 | 41.1259 | 0.82806 | 49.6654 | 0.9993%
2027 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | Non-HFTD---22 | 1 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.037296 | 0 | 0 | 0.037296 | 0 | 0.033939 | 0.37309 | 0.090965 | 0.033939 | 0.37309 | 0.090965 | 0.037662 | 0.41403 | 0.090965 | 0.8877%
2027 | 157 | CB 157 | Tier-3 | Tier-3---21 | Tier-3---11 | 1 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.06043 | 0 | 0 | 0.06043 | 0 | 0.05499 | 0.37309 | 0.14739 | 0.05499 | 0.37309 | 0.14739 | 0.061023 | 0.41403 | 0.14739 | 0.9943%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 5 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.6527 | 1.8655 | 1.9581 | 3.6527 | 1.8655 | 1.9581 | 4.0535 | 2.0701 | 1.9581 | 0.299%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 1 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.7926 | 0.37309 | 20.8863 | 7.7926 | 0.37309 | 20.8863 | 8.6476 | 0.41403 | 20.8863 | 0.8082%
2027 | 212 | CB 212 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 0.22772 | 0 | 0 | 0.22772 | 0 | 0.20723 | 0.37309 | 0.55543 | 0.20723 | 0.37309 | 0.55543 | 0.22996 | 0.41403 | 0.55543 | 0.9909%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 1 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.9331 | 0.37309 | 5.1812 | 1.9331 | 0.37309 | 5.1812 | 2.1452 | 0.41403 | 5.1812 | 0.9981%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 50 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 22.587 | 18.6547 | 1.2108 | 22.587 | 18.6547 | 1.2108 | 25.0652 | 20.7015 | 1.2108 | 0.9929%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 23 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 14.5549 | 8.5812 | 1.6961 | 14.5549 | 8.5812 | 1.6961 | 16.1519 | 9.5227 | 1.6961 | 0.9737%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 37.0873 | 38.0556 | 0.97456 | 37.0873 | 38.0556 | 0.97456 | 41.1564 | 42.231 | 0.97456 | 0.9874%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 17 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 29.646 | 6.3426 | 4.6741 | 29.646 | 6.3426 | 4.6741 | 32.8986 | 7.0385 | 4.6741 | 0.9888%
2027 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 32 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 112.9166 | 11.939 | 9.4578 | 112.9166 | 11.939 | 9.4578 | 125.3055 | 13.2489 | 9.4578 | 0.9762%
2027 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 4 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 19.127 | 1.4924 | 12.8165 | 19.127 | 1.4924 | 12.8165 | 21.2256 | 1.6561 | 12.8165 | 0.9954%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 23 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.2264 | 8.5812 | 1.3083 | 11.2264 | 8.5812 | 1.3083 | 12.4582 | 9.5227 | 1.3083 | 0.9768%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 9 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.3827 | 3.3578 | 0.7096 | 2.3827 | 3.3578 | 0.7096 | 2.6441 | 3.7263 | 0.7096 | 0.6436%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 5 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0086 | 1.8655 | 0.54069 | 1.0086 | 1.8655 | 0.54069 | 1.1193 | 2.0701 | 0.54069 | 0.375%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.7811 | 8.9543 | 1.3157 | 11.7811 | 8.9543 | 1.3157 | 13.0737 | 9.9367 | 1.3157 | 0.9%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 1 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.4286 | 0.37309 | 6.5093 | 2.4286 | 0.37309 | 6.5093 | 2.695 | 0.41403 | 6.5093 | 0.7028%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 30 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.7118 | 11.1928 | 0.77833 | 8.7118 | 11.1928 | 0.77833 | 9.6676 | 12.4209 | 0.77833 | 0.995%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 24 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.3021 | 8.9543 | 0.81549 | 7.3021 | 8.9543 | 0.81549 | 8.1033 | 9.9367 | 0.81549 | 0.9704%
2027 | 283 | CB 283 | Tier-3 | Tier-3---21 | Tier-3---11 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.060097 | 0 | 0 | 0.060097 | 0 | 0.054688 | 0.37309 | 0.14658 | 0.054688 | 0.37309 | 0.14658 | 0.060688 | 0.41403 | 0.14658 | 0.9941%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.2284 | 0.37309 | 35.4558 | 13.2284 | 0.37309 | 35.4558 | 14.6798 | 0.41403 | 35.4558 | 0.9979%
2027 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 5 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.3623 | 1.8655 | 1.2663 | 2.3623 | 1.8655 | 1.2663 | 2.6214 | 2.0701 | 1.2663 | 0.9938%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 28 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 132.4063 | 10.4466 | 12.6745 | 132.4063 | 10.4466 | 12.6745 | 146.9336 | 11.5928 | 12.6745 | 0.9966%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 83 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 101.5275 | 30.9668 | 3.2786 | 101.5275 | 30.9668 | 3.2786 | 112.6669 | 34.3644 | 3.2786 | 0.9884%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 53 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 53.3875 | 19.774 | 2.6999 | 53.3875 | 19.774 | 2.6999 | 59.2451 | 21.9436 | 2.6999 | 0.9601%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 2 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4798 | 0.74619 | 1.9831 | 1.4798 | 0.74619 | 1.9831 | 1.6422 | 0.82806 | 1.9831 | 0.1888%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 7 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.7001 | 2.6117 | 3.7141 | 9.7001 | 2.6117 | 3.7141 | 10.7643 | 2.8982 | 3.7141 | 0.9408%
2027 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 1 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 0.65999 | 0 | 0 | 0.65999 | 0 | 0.60058 | 0.37309 | 1.6097 | 0.60058 | 0.37309 | 1.6097 | 0.66647 | 0.41403 | 1.6097 | 0.9829%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 3 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 1.0439 | 1.1193 | 0.93269 | 1.0439 | 1.1193 | 0.93269 | 1.1585 | 1.2421 | 0.93269 | 0.9768%
2027 | 461 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 1 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 1.005 | 0 | 0 | 1.005 | 0 | 0.91452 | 0.37309 | 2.4512 | 0.91452 | 0.37309 | 2.4512 | 1.0149 | 0.41403 | 2.4512 | 0.9865%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 5 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 60.146 | 1.8655 | 32.2417 | 60.146 | 1.8655 | 32.2417 | 66.7451 | 2.0701 | 32.2417 | 0.9549%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 3 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.1282 | 1.1193 | 3.6883 | 4.1282 | 1.1193 | 3.6883 | 4.5811 | 1.2421 | 3.6883 | 0.9425%
2027 | 533 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0035677 | 0 | 0 | 0.0035677 | 0 | 0.0032465 | 0.37309 | 0.0087017 | 0.0032465 | 0.37309 | 0.0087017 | 0.0036028 | 0.41403 | 0.0087017 | 0.03364%
2027 | 534 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.022693 | 0 | 0 | 0.022693 | 0 | 0.020651 | 0.74619 | 0.027675 | 0.020651 | 0.74619 | 0.027675 | 0.022916 | 0.82806 | 0.027675 | 0.3599%
2027 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.051127 | 0 | 0 | 0.051127 | 0 | 0.046524 | 0.37309 | 0.1247 | 0.046524 | 0.37309 | 0.1247 | 0.051629 | 0.41403 | 0.1247 | 0.04585%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 5 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.37517 | 1.8655 | 0.20111 | 0.37517 | 1.8655 | 0.20111 | 0.41633 | 2.0701 | 0.20111 | 0.7619%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 4 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.60728 | 1.4924 | 0.40692 | 0.60728 | 1.4924 | 0.40692 | 0.67391 | 1.6561 | 0.40692 | 0.9924%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 8 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.2474 | 2.9848 | 2.7632 | 8.2474 | 2.9848 | 2.7632 | 9.1523 | 3.3122 | 2.7632 | 0.9545%
2027 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 3 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.9788 | 1.1193 | 2.6613 | 2.9788 | 1.1193 | 2.6613 | 3.3056 | 1.2421 | 2.6613 | 0.7837%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 22 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 39.2661 | 8.2081 | 4.7838 | 39.2661 | 8.2081 | 4.7838 | 43.5742 | 9.1086 | 4.7838 | 0.9981%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 4 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.46433 | 1.4924 | 0.31113 | 0.46433 | 1.4924 | 0.31113 | 0.51527 | 1.6561 | 0.31113 | 0.9266%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 12 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 74.135 | 4.4771 | 16.5586 | 74.135 | 4.4771 | 16.5586 | 82.2689 | 4.9684 | 16.5586 | 0.9507%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 8 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 24.913 | 2.9848 | 8.3468 | 24.913 | 2.9848 | 8.3468 | 27.6464 | 3.3122 | 8.3468 | 0.9983%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.8713 | 1.4924 | 1.924 | 2.8713 | 1.4924 | 1.924 | 3.1863 | 1.6561 | 1.924 | 0.9343%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 7 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 12.0117 | 2.6117 | 4.5993 | 12.0117 | 2.6117 | 4.5993 | 13.3296 | 2.8982 | 4.5993 | 0.7976%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 27 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 103.7418 | 10.0735 | 10.2984 | 103.7418 | 10.0735 | 10.2984 | 115.1241 | 11.1788 | 10.2984 | 0.9951%
2027 | 974 | CB 974 | Tier-2 | Tier-2---12 | Tier-2---11 | 4 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 3.3409 | 0 | 0 | 3.3409 | 0 | 3.0401 | 1.4924 | 2.0371 | 3.0401 | 1.4924 | 2.0371 | 3.3737 | 1.6561 | 2.0371 | 0.9993%
2027 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 3 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.8118 | 1.1193 | 10.553 | 11.8118 | 1.1193 | 10.553 | 13.1078 | 1.2421 | 10.553 | 0.9951%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 9 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.5186 | 3.3578 | 1.0479 | 3.5186 | 3.3578 | 1.0479 | 3.9047 | 3.7263 | 1.0479 | 0.997%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.22558 | 0.74619 | 0.30231 | 0.22558 | 0.74619 | 0.30231 | 0.25033 | 0.82806 | 0.30231 | 0.9021%
2027 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.15462 | 0 | 0 | 0.15462 | 0 | 0.1407 | 0.37309 | 0.37713 | 0.1407 | 0.37309 | 0.37713 | 0.15614 | 0.41403 | 0.37713 | 0.9981%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 29 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.6384 | 10.8197 | 1.2605 | 13.6384 | 10.8197 | 1.2605 | 15.1347 | 12.0069 | 1.2605 | 0.9785%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 32 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 45.916 | 11.939 | 3.8459 | 45.916 | 11.939 | 3.8459 | 50.9538 | 13.2489 | 3.8459 | 0.9856%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 109 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 62.3027 | 40.6673 | 1.532 | 62.3027 | 40.6673 | 1.532 | 69.1384 | 45.1292 | 1.532 | 0.99%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 66 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 26.0975 | 24.6242 | 1.0598 | 26.0975 | 24.6242 | 1.0598 | 28.9608 | 27.3259 | 1.0598 | 0.9473%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 65 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 94.0833 | 24.2511 | 3.8795 | 94.0833 | 24.2511 | 3.8795 | 104.4059 | 26.9119 | 3.8795 | 0.9831%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 17 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 46.6933 | 6.3426 | 7.3619 | 46.6933 | 6.3426 | 7.3619 | 51.8164 | 7.0385 | 7.3619 | 0.9811%
2027 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 5 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.7942 | 1.8655 | 3.106 | 5.7942 | 1.8655 | 3.106 | 6.4299 | 2.0701 | 3.106 | 0.695%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 19 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 33.7388 | 7.0888 | 4.7595 | 33.7388 | 7.0888 | 4.7595 | 37.4406 | 7.8666 | 4.7595 | 0.9914%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 128 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 28.667 | 47.7561 | 0.60028 | 28.667 | 47.7561 | 0.60028 | 31.8123 | 52.9958 | 0.60028 | 0.9371%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.8194 | 19.774 | 0.74944 | 14.8194 | 19.774 | 0.74944 | 16.4453 | 21.9436 | 0.74944 | 0.789%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 90 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 32.21 | 33.5785 | 0.95925 | 32.21 | 33.5785 | 0.95925 | 35.744 | 37.2627 | 0.95925 | 0.9517%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 30 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 84.4138 | 11.1928 | 7.5418 | 84.4138 | 11.1928 | 7.5418 | 93.6755 | 12.4209 | 7.5418 | 0.9933%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 61.4447 | 31.713 | 1.9375 | 61.4447 | 31.713 | 1.9375 | 68.1863 | 35.1925 | 1.9375 | 0.9757%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 27 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 53.7422 | 10.0735 | 5.335 | 53.7422 | 10.0735 | 5.335 | 59.6387 | 11.1788 | 5.335 | 0.9932%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 20 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 34.2446 | 7.4619 | 4.5893 | 34.2446 | 7.4619 | 4.5893 | 38.0018 | 8.2806 | 4.5893 | 0.9948%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 11 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 33.5037 | 3.915 | 8.5578 | 33.5037 | 3.915 | 8.5578 | 39.1662 | 4.5766 | 8.5578 | 0.9141%
2028 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 0.99181 | 0.71181 | 1.3934 | 0.99181 | 0.71181 | 1.3934 | 1.1594 | 0.83212 | 1.3934 | 0.9976%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 302.1866 | 33.8111 | 8.9375 | 302.1866 | 33.8111 | 8.9375 | 353.2596 | 39.5256 | 8.9375 | 0.9902%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 17 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 60.1308 | 6.0504 | 9.9383 | 60.1308 | 6.0504 | 9.9383 | 70.2936 | 7.073 | 9.9383 | 0.9818%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 43 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 162.927 | 15.304 | 10.646 | 162.927 | 15.304 | 10.646 | 190.4635 | 17.8905 | 10.646 | 0.997%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 11 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 43.4855 | 3.915 | 11.1075 | 43.4855 | 3.915 | 11.1075 | 50.835 | 4.5766 | 11.1075 | 0.9951%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 3 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 11.9862 | 1.0677 | 11.226 | 11.9862 | 1.0677 | 11.226 | 14.012 | 1.2482 | 11.226 | 0.9958%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 33 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 84.7538 | 11.7449 | 7.2162 | 84.7538 | 11.7449 | 7.2162 | 99.0781 | 13.7299 | 7.2162 | 0.9962%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 1 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 5.9834 | 0.35591 | 16.8118 | 5.9834 | 0.35591 | 16.8118 | 6.9947 | 0.41606 | 16.8118 | 0.9922%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 32 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 43.6602 | 11.389 | 3.8335 | 43.6602 | 11.389 | 3.8335 | 51.0392 | 13.3139 | 3.8335 | 0.9916%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 18 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 24.8966 | 6.4063 | 3.8862 | 24.8966 | 6.4063 | 3.8862 | 29.1044 | 7.4891 | 3.8862 | 0.9924%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 80 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 78.8985 | 28.4725 | 2.771 | 78.8985 | 28.4725 | 2.771 | 92.2332 | 33.2847 | 2.771 | 0.9598%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 64 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 31.9045 | 22.778 | 1.4007 | 31.9045 | 22.778 | 1.4007 | 37.2967 | 26.6278 | 1.4007 | 0.9739%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 19 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.4563 | 6.7622 | 0.659 | 4.4563 | 6.7622 | 0.659 | 5.2095 | 7.9051 | 0.659 | 0.8768%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 21 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 43.7073 | 7.474 | 5.8479 | 43.7073 | 7.474 | 5.8479 | 51.0943 | 8.7372 | 5.8479 | 0.9826%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 46 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 101.1325 | 16.3717 | 6.1773 | 101.1325 | 16.3717 | 6.1773 | 118.2251 | 19.1387 | 6.1773 | 0.9858%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 22 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 18.5685 | 7.8299 | 2.3715 | 18.5685 | 7.8299 | 2.3715 | 21.7068 | 9.1533 | 2.3715 | 0.9945%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 56.703 | 30.2521 | 1.8744 | 56.703 | 30.2521 | 1.8744 | 66.2865 | 35.365 | 1.8744 | 0.9866%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 124 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 217.8957 | 44.1324 | 4.9373 | 217.8957 | 44.1324 | 4.9373 | 254.7226 | 51.5913 | 4.9373 | 0.9914%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 119 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 242.8087 | 42.3529 | 5.733 | 242.8087 | 42.3529 | 5.733 | 283.8462 | 49.511 | 5.733 | 0.9849%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 103 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 229.7909 | 36.6584 | 6.2684 | 229.7909 | 36.6584 | 6.2684 | 268.6282 | 42.8541 | 6.2684 | 0.9916%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 68 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 134.9918 | 24.2017 | 5.5778 | 134.9918 | 24.2017 | 5.5778 | 157.807 | 28.292 | 5.5778 | 0.9745%
2028 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 1 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.13544 | 0.35591 | 0.38054 | 0.13544 | 0.35591 | 0.38054 | 0.15833 | 0.41606 | 0.38054 | 0.8684%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 10 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.2935 | 3.5591 | 1.7683 | 6.2935 | 3.5591 | 1.7683 | 7.3572 | 4.1606 | 1.7683 | 0.9924%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 24 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.4964 | 8.5418 | 0.87762 | 7.4964 | 8.5418 | 0.87762 | 8.7634 | 9.9854 | 0.87762 | 0.9393%
2028 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 11 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 4.6858 | 0 | 0 | 4.6858 | 0 | 4.0676 | 3.915 | 1.039 | 4.0676 | 3.915 | 1.039 | 4.7551 | 4.5766 | 1.039 | 0.9197%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 4 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.0761 | 1.4236 | 0.75588 | 1.0761 | 1.4236 | 0.75588 | 1.258 | 1.6642 | 0.75588 | 0.8802%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 81 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 51.0132 | 28.8284 | 1.7695 | 51.0132 | 28.8284 | 1.7695 | 59.635 | 33.7008 | 1.7695 | 0.9962%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 63 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 43.1612 | 22.4221 | 1.9249 | 43.1612 | 22.4221 | 1.9249 | 50.456 | 26.2117 | 1.9249 | 0.9962%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 16 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 21.7896 | 5.6945 | 3.8264 | 21.7896 | 5.6945 | 3.8264 | 25.4723 | 6.6569 | 3.8264 | 0.9984%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 18.5594 | 1.0677 | 17.3823 | 18.5594 | 1.0677 | 17.3823 | 21.6962 | 1.2482 | 17.3823 | 0.9968%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 1 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 36.6746 | 0.35591 | 103.0456 | 36.6746 | 0.35591 | 103.0456 | 42.8731 | 0.41606 | 103.0456 | 0.9992%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 1 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.4206 | 0.35591 | 9.6109 | 3.4206 | 0.35591 | 9.6109 | 3.9987 | 0.41606 | 9.6109 | 0.945%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 3 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 6.8028 | 1.0677 | 6.3714 | 6.8028 | 1.0677 | 6.3714 | 7.9526 | 1.2482 | 6.3714 | 0.994%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 93 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 36.8914 | 33.0993 | 1.1146 | 36.8914 | 33.0993 | 1.1146 | 43.1264 | 38.6935 | 1.1146 | 0.9112%
2028 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 9 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 1.8395 | 3.2032 | 0.57427 | 1.8395 | 3.2032 | 0.57427 | 2.1504 | 3.7445 | 0.57427 | 0.8819%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 6 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.7327 | 2.1354 | 0.81141 | 1.7327 | 2.1354 | 0.81141 | 2.0256 | 2.4964 | 0.81141 | 0.9662%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 8 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.1043 | 2.8473 | 0.73906 | 2.1043 | 2.8473 | 0.73906 | 2.4599 | 3.3285 | 0.73906 | 0.9775%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 23 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 33.8232 | 8.1859 | 4.1319 | 33.8232 | 8.1859 | 4.1319 | 39.5397 | 9.5694 | 4.1319 | 0.9826%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 16 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 87.5467 | 5.6945 | 15.3739 | 87.5467 | 5.6945 | 15.3739 | 102.3431 | 6.6569 | 15.3739 | 0.9977%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 73 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 88.7835 | 25.9812 | 3.4172 | 88.7835 | 25.9812 | 3.4172 | 103.789 | 30.3723 | 3.4172 | 0.9908%
2028 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | Tier-3---19 | 2 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 1.2393 | 0 | 0 | 1.2393 | 0 | 1.0758 | 0.71181 | 1.5114 | 1.0758 | 0.71181 | 1.5114 | 1.2576 | 0.83212 | 1.5114 | 0.7849%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 43 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 52.232 | 15.304 | 3.413 | 52.232 | 15.304 | 3.413 | 61.0598 | 17.8905 | 3.413 | 0.9788%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 15 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 18.208 | 5.3386 | 3.4106 | 18.208 | 5.3386 | 3.4106 | 21.2853 | 6.2409 | 3.4106 | 0.9469%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 64 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 72.8304 | 22.778 | 3.1974 | 72.8304 | 22.778 | 3.1974 | 85.1396 | 26.6278 | 3.1974 | 0.9648%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 24 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.3348 | 8.5418 | 1.5611 | 13.3348 | 8.5418 | 1.5611 | 15.5885 | 9.9854 | 1.5611 | 0.9856%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 33 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 30.4313 | 11.7449 | 2.591 | 30.4313 | 11.7449 | 2.591 | 35.5746 | 13.7299 | 2.591 | 0.9842%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 39 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 25.3573 | 13.8804 | 1.8268 | 25.3573 | 13.8804 | 1.8268 | 29.643 | 16.2263 | 1.8268 | 0.979%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 12 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 11.9053 | 4.2709 | 2.7876 | 11.9053 | 4.2709 | 2.7876 | 13.9174 | 4.9927 | 2.7876 | 0.9892%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 30 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 36.828 | 10.6772 | 3.4492 | 36.828 | 10.6772 | 3.4492 | 43.0524 | 12.4818 | 3.4492 | 0.9866%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 10 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.5601 | 3.5591 | 1.0003 | 3.5601 | 3.5591 | 1.0003 | 4.1617 | 4.1606 | 1.0003 | 0.9965%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 14 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 3.951 | 4.9827 | 0.79295 | 3.951 | 4.9827 | 0.79295 | 4.6188 | 5.8248 | 0.79295 | 0.9977%
2028 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 1 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.02425 | 0 | 0 | 0.02425 | 0 | 0.021051 | 0.35591 | 0.059146 | 0.021051 | 0.35591 | 0.059146 | 0.024608 | 0.41606 | 0.059146 | 0.9862%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.1595 | 1.0677 | 9.5152 | 10.1595 | 1.0677 | 9.5152 | 11.8766 | 1.2482 | 9.5152 | 0.9935%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.3665 | 0.35591 | 3.8396 | 1.3665 | 0.35591 | 3.8396 | 1.5975 | 0.41606 | 3.8396 | 0.9948%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.1502 | 5.6945 | 2.8361 | 16.1502 | 5.6945 | 2.8361 | 18.8798 | 6.6569 | 2.8361 | 0.9905%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 4 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 55.93 | 1.4236 | 39.287 | 55.93 | 1.4236 | 39.287 | 65.3828 | 1.6642 | 39.287 | 0.9454%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 28 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 101.2356 | 9.9654 | 10.1587 | 101.2356 | 9.9654 | 10.1587 | 118.3455 | 11.6497 | 10.1587 | 0.9926%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 13 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 31.3976 | 4.6268 | 6.7861 | 31.3976 | 4.6268 | 6.7861 | 36.7042 | 5.4088 | 6.7861 | 0.9815%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 16 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.3566 | 5.6945 | 0.58945 | 3.3566 | 5.6945 | 0.58945 | 3.924 | 6.6569 | 0.58945 | 0.9046%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 3 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 17.5658 | 1.0677 | 16.4517 | 17.5658 | 1.0677 | 16.4517 | 20.5346 | 1.2482 | 16.4517 | 0.8554%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 33 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 37.432 | 11.7449 | 3.1871 | 37.432 | 11.7449 | 3.1871 | 43.7585 | 13.7299 | 3.1871 | 0.9867%
2028 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.71181 | 0 | 0 | 0.71181 | 0 | 0 | 0.83212 | 0 | 0%
2028 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 3 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 1.0677 | 0 | 0 | 1.0677 | 0 | 0 | 1.2482 | 0 | 0%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 51 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 137.5213 | 18.1512 | 7.5764 | 137.5213 | 18.1512 | 7.5764 | 160.764 | 21.219 | 7.5764 | 0.9909%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.43358 | 0.35591 | 1.2182 | 0.43358 | 0.35591 | 1.2182 | 0.50686 | 0.41606 | 1.2182 | 0.2981%
2028 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.70284 | 0.35591 | 1.9748 | 0.70284 | 0.35591 | 1.9748 | 0.82162 | 0.41606 | 1.9748 | 0.9995%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 38 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 70.2994 | 13.5245 | 5.1979 | 70.2994 | 13.5245 | 5.1979 | 82.1808 | 15.8102 | 5.1979 | 0.9925%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 127 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 319.7831 | 45.2002 | 7.0748 | 319.7831 | 45.2002 | 7.0748 | 373.8301 | 52.8395 | 7.0748 | 0.9936%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.064239 | 0.35591 | 0.18049 | 0.064239 | 0.35591 | 0.18049 | 0.075096 | 0.41606 | 0.18049 | 0.895%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 20 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.1867 | 7.1181 | 0.44769 | 3.1867 | 7.1181 | 0.44769 | 3.7253 | 8.3212 | 0.44769 | 0.8771%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 177 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 44.2007 | 62.9955 | 0.70165 | 44.2007 | 62.9955 | 0.70165 | 51.6711 | 73.6424 | 0.70165 | 0.9246%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 10 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 26.2521 | 3.5591 | 7.3761 | 26.2521 | 3.5591 | 7.3761 | 30.689 | 4.1606 | 7.3761 | 0.9907%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 20 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 33.306 | 7.1181 | 4.679 | 33.306 | 7.1181 | 4.679 | 38.9351 | 8.3212 | 4.679 | 0.9899%
2028 | 157 | 157-207R | Tier-3 | Tier-3---16 | Tier-3---7 | 2 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 7.1828 | 0 | 0 | 7.1828 | 0 | 6.2351 | 0.71181 | 8.7595 | 6.2351 | 0.71181 | 8.7595 | 7.2889 | 0.83212 | 8.7595 | 0.9989%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 80 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 26.1371 | 28.4725 | 0.91798 | 26.1371 | 28.4725 | 0.91798 | 30.5546 | 33.2847 | 0.91798 | 0.9527%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 151 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 14.5896 | 53.7419 | 0.27148 | 14.5896 | 53.7419 | 0.27148 | 17.0554 | 62.8249 | 0.27148 | 0.8154%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 15.4015 | 18.8631 | 0.81649 | 15.4015 | 18.8631 | 0.81649 | 18.0045 | 22.0511 | 0.81649 | 0.9501%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 205 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 157.884 | 72.9609 | 2.164 | 157.884 | 72.9609 | 2.164 | 184.5682 | 85.2921 | 2.164 | 0.97%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 19 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 34.6605 | 6.7622 | 5.1256 | 34.6605 | 6.7622 | 5.1256 | 40.5185 | 7.9051 | 5.1256 | 0.991%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 6 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 16.261 | 2.1354 | 7.6148 | 16.261 | 2.1354 | 7.6148 | 19.0093 | 2.4964 | 7.6148 | 0.7065%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 37.1254 | 22.4221 | 1.6557 | 37.1254 | 22.4221 | 1.6557 | 43.4 | 26.2117 | 1.6557 | 0.9752%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 113 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 48.2755 | 40.2175 | 1.2004 | 48.2755 | 40.2175 | 1.2004 | 56.4346 | 47.0147 | 1.2004 | 0.9686%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 9 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 5.7898 | 3.2032 | 1.8075 | 5.7898 | 3.2032 | 1.8075 | 6.7683 | 3.7445 | 1.8075 | 0.7976%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 98.7984 | 22.0662 | 4.4774 | 98.7984 | 22.0662 | 4.4774 | 115.4964 | 25.7957 | 4.4774 | 0.9877%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 55 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 35.6347 | 19.5749 | 1.8204 | 35.6347 | 19.5749 | 1.8204 | 41.6574 | 22.8832 | 1.8204 | 0.981%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 32 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 84.8927 | 11.389 | 7.4539 | 84.8927 | 11.389 | 7.4539 | 99.2405 | 13.3139 | 7.4539 | 0.9713%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 51 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 28.8558 | 18.1512 | 1.5897 | 28.8558 | 18.1512 | 1.5897 | 33.7328 | 21.219 | 1.5897 | 0.9774%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 44 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 41.8474 | 15.6599 | 2.6723 | 41.8474 | 15.6599 | 2.6723 | 48.9201 | 18.3066 | 2.6723 | 0.977%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 115 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 110.6943 | 40.9293 | 2.7045 | 110.6943 | 40.9293 | 2.7045 | 129.4029 | 47.8468 | 2.7045 | 0.968%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 12.6728 | 1.7795 | 7.1214 | 12.6728 | 1.7795 | 7.1214 | 14.8146 | 2.0803 | 7.1214 | 0.8924%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 3 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 20.1239 | 1.0677 | 18.8475 | 20.1239 | 1.0677 | 18.8475 | 23.5251 | 1.2482 | 18.8475 | 0.7823%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 40 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 97.543 | 14.2363 | 6.8517 | 97.543 | 14.2363 | 6.8517 | 114.0289 | 16.6424 | 6.8517 | 0.9429%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 4 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 16.79 | 1.4236 | 11.7938 | 16.79 | 1.4236 | 11.7938 | 19.6277 | 1.6642 | 11.7938 | 0.9974%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 17 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 36.4306 | 6.0504 | 6.0212 | 36.4306 | 6.0504 | 6.0212 | 42.5878 | 7.073 | 6.0212 | 0.9922%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 8 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 13.757 | 2.8473 | 4.8317 | 13.757 | 2.8473 | 4.8317 | 16.082 | 3.3285 | 4.8317 | 0.9193%
2028 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 4 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.5826 | 1.4236 | 1.1117 | 1.5826 | 1.4236 | 1.1117 | 1.8501 | 1.6642 | 1.1117 | 0.9934%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 1 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.055376 | 0.35591 | 0.15559 | 0.055376 | 0.35591 | 0.15559 | 0.064736 | 0.41606 | 0.15559 | 0.9638%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 8 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 25.774 | 2.8473 | 9.0522 | 25.774 | 2.8473 | 9.0522 | 30.13 | 3.3285 | 9.0522 | 0.9975%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 51 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 73.2722 | 18.1512 | 4.0368 | 73.2722 | 18.1512 | 4.0368 | 85.656 | 21.219 | 4.0368 | 0.9974%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 19 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 3.8961 | 6.7622 | 0.57616 | 3.8961 | 6.7622 | 0.57616 | 4.5546 | 7.9051 | 0.57616 | 0.901%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 60 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 7.7241 | 21.3544 | 0.36171 | 7.7241 | 21.3544 | 0.36171 | 9.0296 | 24.9635 | 0.36171 | 0.8573%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 18 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.0436 | 6.4063 | 0.1629 | 1.0436 | 6.4063 | 0.1629 | 1.22 | 7.4891 | 0.1629 | 0.7047%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 38 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.402 | 13.5245 | 0.10366 | 1.402 | 13.5245 | 0.10366 | 1.6389 | 15.8102 | 0.10366 | 0.5082%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 65 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.3188 | 23.1339 | 0.40282 | 9.3188 | 23.1339 | 0.40282 | 10.8938 | 27.0438 | 0.40282 | 0.8949%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 145 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.2361 | 51.6065 | 0.25648 | 13.2361 | 51.6065 | 0.25648 | 15.4732 | 60.3286 | 0.25648 | 0.8426%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 14.9453 | 23.4898 | 0.63624 | 14.9453 | 23.4898 | 0.63624 | 17.4712 | 27.4599 | 0.63624 | 0.9106%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 79 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 14.4047 | 28.1166 | 0.51232 | 14.4047 | 28.1166 | 0.51232 | 16.8392 | 32.8687 | 0.51232 | 0.9543%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 12.9466 | 24.9135 | 0.51966 | 12.9466 | 24.9135 | 0.51966 | 15.1347 | 29.1241 | 0.51966 | 0.9497%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 4 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.2439 | 1.4236 | 3.6835 | 5.2439 | 1.4236 | 3.6835 | 6.1302 | 1.6642 | 3.6835 | 0.9907%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 46 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 42.0693 | 16.3717 | 2.5696 | 42.0693 | 16.3717 | 2.5696 | 49.1795 | 19.1387 | 2.5696 | 0.9915%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 42 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 10.7606 | 14.9481 | 0.71987 | 10.7606 | 14.9481 | 0.71987 | 12.5793 | 17.4745 | 0.71987 | 0.9792%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 39 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.3773 | 13.8804 | 0.60354 | 8.3773 | 13.8804 | 0.60354 | 9.7932 | 16.2263 | 0.60354 | 0.9662%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 6 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.2025 | 2.1354 | 1.0314 | 2.2025 | 2.1354 | 1.0314 | 2.5748 | 2.4964 | 1.0314 | 0.9706%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 68 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 12.5177 | 24.2017 | 0.51723 | 12.5177 | 24.2017 | 0.51723 | 14.6334 | 28.292 | 0.51723 | 0.9727%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 103 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 22.9349 | 36.6584 | 0.62564 | 22.9349 | 36.6584 | 0.62564 | 26.8111 | 42.8541 | 0.62564 | 0.9578%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 39 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 8.7577 | 13.8804 | 0.63094 | 8.7577 | 13.8804 | 0.63094 | 10.2379 | 16.2263 | 0.63094 | 0.9712%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 3 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.89078 | 1.0677 | 0.83428 | 0.89078 | 1.0677 | 0.83428 | 1.0413 | 1.2482 | 0.83428 | 0.9778%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 17 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 18.5404 | 6.0504 | 3.0643 | 18.5404 | 6.0504 | 3.0643 | 21.6739 | 7.073 | 3.0643 | 0.9872%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 45 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 12.4912 | 16.0158 | 0.77993 | 12.4912 | 16.0158 | 0.77993 | 14.6024 | 18.7227 | 0.77993 | 0.9782%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 127 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 225.6415 | 45.2002 | 4.9921 | 225.6415 | 45.2002 | 4.9921 | 263.7775 | 52.8395 | 4.9921 | 0.9891%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 75 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 57.5299 | 26.693 | 2.1552 | 57.5299 | 26.693 | 2.1552 | 67.2531 | 31.2044 | 2.1552 | 0.9941%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 30 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.0925 | 10.6772 | 0.38329 | 4.0925 | 10.6772 | 0.38329 | 4.7842 | 12.4818 | 0.38329 | 0.974%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 22 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.3996 | 7.8299 | 0.43417 | 3.3996 | 7.8299 | 0.43417 | 3.9741 | 9.1533 | 0.43417 | 0.9786%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 9 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.3988 | 3.2032 | 1.3733 | 4.3988 | 3.2032 | 1.3733 | 5.1422 | 3.7445 | 1.3733 | 0.9871%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 32 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 18.9959 | 11.389 | 1.6679 | 18.9959 | 11.389 | 1.6679 | 22.2065 | 13.3139 | 1.6679 | 0.9909%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 50 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 12.8069 | 17.7953 | 0.71968 | 12.8069 | 17.7953 | 0.71968 | 14.9714 | 20.803 | 0.71968 | 0.8569%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 73 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 192.5809 | 25.9812 | 7.4123 | 192.5809 | 25.9812 | 7.4123 | 225.1293 | 30.3723 | 7.4123 | 0.9924%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 72 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 108.2961 | 25.6253 | 4.2261 | 108.2961 | 25.6253 | 4.2261 | 126.5994 | 29.9562 | 4.2261 | 0.9821%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 167.486 | 20.6426 | 8.1136 | 167.486 | 20.6426 | 8.1136 | 195.793 | 24.1314 | 8.1136 | 0.99%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 16 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.027 | 5.6945 | 2.112 | 12.027 | 5.6945 | 2.112 | 14.0597 | 6.6569 | 2.112 | 0.9809%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 26 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 46.6667 | 9.2536 | 5.0431 | 46.6667 | 9.2536 | 5.0431 | 54.5539 | 10.8175 | 5.0431 | 0.9892%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 67 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 120.8944 | 23.8458 | 5.0699 | 120.8944 | 23.8458 | 5.0699 | 141.3269 | 27.876 | 5.0699 | 0.9919%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 126 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 15.5959 | 44.8442 | 0.34778 | 15.5959 | 44.8442 | 0.34778 | 18.2318 | 52.4234 | 0.34778 | 0.8922%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 84 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 20.8004 | 29.8962 | 0.69575 | 20.8004 | 29.8962 | 0.69575 | 24.3159 | 34.949 | 0.69575 | 0.8785%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 71 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 91.5481 | 25.2694 | 3.6229 | 91.5481 | 25.2694 | 3.6229 | 107.0208 | 29.5402 | 3.6229 | 0.9868%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 68 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 30.0512 | 24.2017 | 1.2417 | 30.0512 | 24.2017 | 1.2417 | 35.1302 | 28.292 | 1.2417 | 0.9466%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.3491 | 24.9135 | 0.45554 | 11.3491 | 24.9135 | 0.45554 | 13.2672 | 29.1241 | 0.45554 | 0.9088%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 48 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 86.9871 | 17.0835 | 5.0919 | 86.9871 | 17.0835 | 5.0919 | 101.6889 | 19.9708 | 5.0919 | 0.9905%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 29 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 18.3868 | 10.3213 | 1.7814 | 18.3868 | 10.3213 | 1.7814 | 21.4944 | 12.0657 | 1.7814 | 0.9634%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 81 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.0917 | 28.8284 | 0.48881 | 14.0917 | 28.8284 | 0.48881 | 16.4734 | 33.7008 | 0.48881 | 0.8429%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 155 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 27.8169 | 55.1655 | 0.50424 | 27.8169 | 55.1655 | 0.50424 | 32.5183 | 64.4891 | 0.50424 | 0.8937%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 32.0105 | 6.0504 | 5.2906 | 32.0105 | 6.0504 | 5.2906 | 37.4207 | 7.073 | 5.2906 | 0.9991%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 77 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 26.1629 | 27.4048 | 0.95468 | 26.1629 | 27.4048 | 0.95468 | 30.5847 | 32.0365 | 0.95468 | 0.9216%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 93 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 22.8253 | 33.0993 | 0.6896 | 22.8253 | 33.0993 | 0.6896 | 26.6831 | 38.6935 | 0.6896 | 0.9611%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.1327 | 1.0677 | 5.7437 | 6.1327 | 1.0677 | 5.7437 | 7.1692 | 1.2482 | 5.7437 | 0.9946%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 72 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 33.1406 | 25.6253 | 1.2933 | 33.1406 | 25.6253 | 1.2933 | 38.7417 | 29.9562 | 1.2933 | 0.9703%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 9 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.92221 | 3.2032 | 0.28791 | 0.92221 | 3.2032 | 0.28791 | 1.0781 | 3.7445 | 0.28791 | 0.334%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 4 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 17.7549 | 1.4236 | 12.4716 | 17.7549 | 1.4236 | 12.4716 | 20.7557 | 1.6642 | 12.4716 | 0.9951%
2028 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 1 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 33.8502 | 0.35591 | 95.1098 | 33.8502 | 0.35591 | 95.1098 | 39.5713 | 0.41606 | 95.1098 | 0.9988%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 5 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.2941 | 1.7795 | 2.975 | 5.2941 | 1.7795 | 2.975 | 6.1889 | 2.0803 | 2.975 | 0.9868%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 12 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 38.6908 | 4.2709 | 9.0592 | 38.6908 | 4.2709 | 9.0592 | 45.23 | 4.9927 | 9.0592 | 0.9945%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 31 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 19.5428 | 11.0331 | 1.7713 | 19.5428 | 11.0331 | 1.7713 | 22.8458 | 12.8978 | 1.7713 | 0.9686%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 18 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 83.1497 | 6.4063 | 12.9793 | 83.1497 | 6.4063 | 12.9793 | 97.203 | 7.4891 | 12.9793 | 0.9959%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.2286 | 8.1859 | 1.3717 | 11.2286 | 8.1859 | 1.3717 | 13.1263 | 9.5694 | 1.3717 | 0.9515%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 137 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 62.1241 | 48.7592 | 1.2741 | 62.1241 | 48.7592 | 1.2741 | 72.6237 | 57.0001 | 1.2741 | 0.9662%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 212 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 682.3181 | 75.4522 | 9.043 | 682.3181 | 75.4522 | 9.043 | 797.6376 | 88.2045 | 9.043 | 0.9925%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 31.189 | 4.6268 | 6.741 | 31.189 | 4.6268 | 6.741 | 36.4603 | 5.4088 | 6.741 | 0.9927%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 81 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 390.1034 | 28.8284 | 13.5319 | 390.1034 | 28.8284 | 13.5319 | 456.0353 | 33.7008 | 13.5319 | 0.9963%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.1697 | 1.0677 | 2.0321 | 2.1697 | 1.0677 | 2.0321 | 2.5364 | 1.2482 | 2.0321 | 0.8656%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 132 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 61.9237 | 46.9797 | 1.3181 | 61.9237 | 46.9797 | 1.3181 | 72.3895 | 54.9198 | 1.3181 | 0.9605%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 1 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 42.123 | 0.35591 | 118.3541 | 42.123 | 0.35591 | 118.3541 | 49.2423 | 0.41606 | 118.3541 | 0.9985%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 1220 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 140.7833 | 434.2062 | 0.32423 | 140.7833 | 434.2062 | 0.32423 | 164.5773 | 507.592 | 0.32423 | 0.967%
2028 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.4801 | 0.35591 | 4.1586 | 1.4801 | 0.35591 | 4.1586 | 1.7302 | 0.41606 | 4.1586 | 0.9937%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 52 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 16.4943 | 18.5071 | 0.89124 | 16.4943 | 18.5071 | 0.89124 | 19.282 | 21.6351 | 0.89124 | 0.9498%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 84 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 54.4945 | 29.8962 | 1.8228 | 54.4945 | 29.8962 | 1.8228 | 63.7047 | 34.949 | 1.8228 | 0.9826%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 57 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 16.3862 | 20.2867 | 0.80773 | 16.3862 | 20.2867 | 0.80773 | 19.1556 | 23.7154 | 0.80773 | 0.9106%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 17 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.6769 | 6.0504 | 0.60771 | 3.6769 | 6.0504 | 0.60771 | 4.2983 | 7.073 | 0.60771 | 0.7897%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 6 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 6.7227 | 2.1354 | 3.1481 | 6.7227 | 2.1354 | 3.1481 | 7.8589 | 2.4964 | 3.1481 | 0.9819%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 52 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 29.4513 | 18.5071 | 1.5913 | 29.4513 | 18.5071 | 1.5913 | 34.429 | 21.6351 | 1.5913 | 0.9768%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 0.98148 | 0.35591 | 2.7577 | 0.98148 | 0.35591 | 2.7577 | 1.1474 | 0.41606 | 2.7577 | 0.9298%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 8 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.3883 | 2.8473 | 0.48761 | 1.3883 | 2.8473 | 0.48761 | 1.623 | 3.3285 | 0.48761 | 0.8171%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 23.3036 | 8.5418 | 2.7282 | 23.3036 | 8.5418 | 2.7282 | 27.2421 | 9.9854 | 2.7282 | 0.983%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 151 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 44.0479 | 53.7419 | 0.81962 | 44.0479 | 53.7419 | 0.81962 | 51.4925 | 62.8249 | 0.81962 | 0.9868%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 57 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 26.0468 | 20.2867 | 1.2839 | 26.0468 | 20.2867 | 1.2839 | 30.449 | 23.7154 | 1.2839 | 0.9884%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 47 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.0897 | 16.7276 | 0.36405 | 6.0897 | 16.7276 | 0.36405 | 7.1189 | 19.5548 | 0.36405 | 0.9757%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 32 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.691 | 11.389 | 0.32408 | 3.691 | 11.389 | 0.32408 | 4.3148 | 13.3139 | 0.32408 | 0.9496%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 79 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 17.4616 | 28.1166 | 0.62104 | 17.4616 | 28.1166 | 0.62104 | 20.4128 | 32.8687 | 0.62104 | 0.859%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 40 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 42.644 | 14.2363 | 2.9955 | 42.644 | 14.2363 | 2.9955 | 49.8514 | 16.6424 | 2.9955 | 0.9946%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 14 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 33.6588 | 4.9827 | 6.7551 | 33.6588 | 4.9827 | 6.7551 | 39.3475 | 5.8248 | 6.7551 | 0.8863%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 48 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 202.1881 | 17.0835 | 11.8353 | 202.1881 | 17.0835 | 11.8353 | 236.3602 | 19.9708 | 11.8353 | 0.9837%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 48 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 83.2984 | 17.0835 | 4.876 | 83.2984 | 17.0835 | 4.876 | 97.3768 | 19.9708 | 4.876 | 0.9873%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 37 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 23.8394 | 13.1685 | 1.8103 | 23.8394 | 13.1685 | 1.8103 | 27.8686 | 15.3942 | 1.8103 | 0.9726%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 25 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 19.3507 | 8.8977 | 2.1748 | 19.3507 | 8.8977 | 2.1748 | 22.6212 | 10.4015 | 2.1748 | 0.9861%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 51 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 45.394 | 18.1512 | 2.5009 | 45.394 | 18.1512 | 2.5009 | 53.0661 | 21.219 | 2.5009 | 0.9807%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 124 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 181.2145 | 44.1324 | 4.1062 | 181.2145 | 44.1324 | 4.1062 | 211.8418 | 51.5913 | 4.1062 | 0.9836%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 56 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 58.842 | 19.9308 | 2.9523 | 58.842 | 19.9308 | 2.9523 | 68.7869 | 23.2993 | 2.9523 | 0.9784%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 16 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 31.3562 | 5.6945 | 5.5064 | 31.3562 | 5.6945 | 5.5064 | 36.6558 | 6.6569 | 5.5064 | 0.994%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 62 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 243.6142 | 22.0662 | 11.0401 | 243.6142 | 22.0662 | 11.0401 | 284.7877 | 25.7957 | 11.0401 | 0.9934%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 71 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 232.4738 | 25.2694 | 9.1998 | 232.4738 | 25.2694 | 9.1998 | 271.7645 | 29.5402 | 9.1998 | 0.9889%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 13 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 21.7062 | 4.6268 | 4.6914 | 21.7062 | 4.6268 | 4.6914 | 25.3748 | 5.4088 | 4.6914 | 0.9883%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 165 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 265.7992 | 58.7246 | 4.5262 | 265.7992 | 58.7246 | 4.5262 | 310.7223 | 68.6497 | 4.5262 | 0.9911%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 182 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 562.6422 | 64.775 | 8.6861 | 562.6422 | 64.775 | 8.6861 | 657.7351 | 75.7227 | 8.6861 | 0.9893%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 21 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.3249 | 7.474 | 0.98004 | 7.3249 | 7.474 | 0.98004 | 8.5629 | 8.7372 | 0.98004 | 0.9808%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 19 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 13.5774 | 6.7622 | 2.0078 | 13.5774 | 6.7622 | 2.0078 | 15.8721 | 7.9051 | 2.0078 | 0.9867%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.3484 | 8.1859 | 1.142 | 9.3484 | 8.1859 | 1.142 | 10.9284 | 9.5694 | 1.142 | 0.9646%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 72 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 53.4582 | 25.6253 | 2.0862 | 53.4582 | 25.6253 | 2.0862 | 62.4933 | 29.9562 | 2.0862 | 0.9824%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 17 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.1911 | 6.0504 | 1.0232 | 6.1911 | 6.0504 | 1.0232 | 7.2374 | 7.073 | 1.0232 | 0.6927%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 18 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.227 | 6.4063 | 0.50372 | 3.227 | 6.4063 | 0.50372 | 3.7724 | 7.4891 | 0.50372 | 0.9876%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 15 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.0908 | 5.3386 | 1.8902 | 10.0908 | 5.3386 | 1.8902 | 11.7962 | 6.2409 | 1.8902 | 0.9838%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 6 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 6.7803 | 2.1354 | 3.1751 | 6.7803 | 2.1354 | 3.1751 | 7.9263 | 2.4964 | 3.1751 | 0.987%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 17 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.1681 | 6.0504 | 0.52361 | 3.1681 | 6.0504 | 0.52361 | 3.7035 | 7.073 | 0.52361 | 0.9688%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 73 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 37.7167 | 25.9812 | 1.4517 | 37.7167 | 25.9812 | 1.4517 | 44.0912 | 30.3723 | 1.4517 | 0.9791%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 50 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 32.1844 | 17.7953 | 1.8086 | 32.1844 | 17.7953 | 1.8086 | 37.624 | 20.803 | 1.8086 | 0.9907%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 104 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 30.8081 | 37.0143 | 0.83233 | 30.8081 | 37.0143 | 0.83233 | 36.015 | 43.2701 | 0.83233 | 0.9682%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 15 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.4986 | 5.3386 | 1.03 | 5.4986 | 5.3386 | 1.03 | 6.428 | 6.2409 | 1.03 | 0.6596%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 71 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 27.7975 | 25.2694 | 1.1 | 27.7975 | 25.2694 | 1.1 | 32.4956 | 29.5402 | 1.1 | 0.9454%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 33 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 10.9245 | 11.7449 | 0.93015 | 10.9245 | 11.7449 | 0.93015 | 12.7709 | 13.7299 | 0.93015 | 0.9251%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 2 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.89663 | 0.71181 | 1.2596 | 0.89663 | 0.71181 | 1.2596 | 1.0482 | 0.83212 | 1.2596 | 0.9818%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 99 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 31.2287 | 35.2348 | 0.8863 | 31.2287 | 35.2348 | 0.8863 | 36.5068 | 41.1898 | 0.8863 | 0.9585%
2028 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 3 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.37228 | 1.0677 | 0.34867 | 0.37228 | 1.0677 | 0.34867 | 0.4352 | 1.2482 | 0.34867 | 0.8666%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 29 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 45.3392 | 10.3213 | 4.3928 | 45.3392 | 10.3213 | 4.3928 | 53.0021 | 12.0657 | 4.3928 | 0.9855%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 40 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 15.347 | 14.2363 | 1.078 | 15.347 | 14.2363 | 1.078 | 17.9408 | 16.6424 | 1.078 | 0.878%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 3 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.0495 | 1.0677 | 5.6658 | 6.0495 | 1.0677 | 5.6658 | 7.072 | 1.2482 | 5.6658 | 0.9241%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.0305 | 2.4913 | 7.6386 | 19.0305 | 2.4913 | 7.6386 | 22.2468 | 2.9124 | 7.6386 | 0.9107%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 26 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 39.503 | 9.2536 | 4.2689 | 39.503 | 9.2536 | 4.2689 | 46.1795 | 10.8175 | 4.2689 | 0.9555%
2028 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 2 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.33962 | 0.71181 | 0.47712 | 0.33962 | 0.71181 | 0.47712 | 0.39702 | 0.83212 | 0.47712 | 0.8469%
2028 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 4 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.39379 | 1.4236 | 0.27661 | 0.39379 | 1.4236 | 0.27661 | 0.46034 | 1.6642 | 0.27661 | 0.1628%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 1 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.6061 | 0.35591 | 7.3224 | 2.6061 | 0.35591 | 7.3224 | 3.0466 | 0.41606 | 7.3224 | 0.9927%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 138 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 29.856 | 49.1151 | 0.60788 | 29.856 | 49.1151 | 0.60788 | 34.902 | 57.4161 | 0.60788 | 0.9548%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 245 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 118.1718 | 87.1971 | 1.3552 | 118.1718 | 87.1971 | 1.3552 | 138.1442 | 101.9345 | 1.3552 | 0.9814%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 229 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 46.9005 | 81.5026 | 0.57545 | 46.9005 | 81.5026 | 0.57545 | 54.8272 | 95.2775 | 0.57545 | 0.9699%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 116.5375 | 32.7434 | 3.5591 | 116.5375 | 32.7434 | 3.5591 | 136.2336 | 38.2774 | 3.5591 | 0.9928%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 107 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 96.1417 | 38.082 | 2.5246 | 96.1417 | 38.082 | 2.5246 | 112.3908 | 44.5183 | 2.5246 | 0.9888%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 202.6155 | 20.6426 | 9.8154 | 202.6155 | 20.6426 | 9.8154 | 236.8598 | 24.1314 | 9.8154 | 0.9925%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 22 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 79.1645 | 7.8299 | 10.1105 | 79.1645 | 7.8299 | 10.1105 | 92.5442 | 9.1533 | 10.1105 | 0.9973%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 76 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 160.5499 | 27.0489 | 5.9355 | 160.5499 | 27.0489 | 5.9355 | 187.6847 | 31.6205 | 5.9355 | 0.9936%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 40 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 78.0402 | 14.2363 | 5.4818 | 78.0402 | 14.2363 | 5.4818 | 91.2299 | 16.6424 | 5.4818 | 0.9749%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 21.6881 | 2.4913 | 8.7054 | 21.6881 | 2.4913 | 8.7054 | 25.3536 | 2.9124 | 8.7054 | 0.9918%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 1 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 19.2203 | 0.35591 | 54.0037 | 19.2203 | 0.35591 | 54.0037 | 22.4687 | 0.41606 | 54.0037 | 0.9993%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 7 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 15.3319 | 2.4913 | 6.1541 | 15.3319 | 2.4913 | 6.1541 | 17.9232 | 2.9124 | 6.1541 | 0.8869%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 23 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 37.2925 | 8.1859 | 4.5557 | 37.2925 | 8.1859 | 4.5557 | 43.5954 | 9.5694 | 4.5557 | 0.943%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 1 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.5371 | 0.35591 | 7.1285 | 2.5371 | 0.35591 | 7.1285 | 2.9659 | 0.41606 | 7.1285 | 0.6284%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 42 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 116.8208 | 14.9481 | 7.8151 | 116.8208 | 14.9481 | 7.8151 | 136.5648 | 17.4745 | 7.8151 | 0.9943%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 121 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 176.5588 | 43.0647 | 4.0998 | 176.5588 | 43.0647 | 4.0998 | 206.3992 | 50.3431 | 4.0998 | 0.9917%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 15 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 28.0801 | 5.3386 | 5.2598 | 28.0801 | 5.3386 | 5.2598 | 32.826 | 6.2409 | 5.2598 | 0.8854%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 64 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 64.1338 | 22.778 | 2.8156 | 64.1338 | 22.778 | 2.8156 | 74.9732 | 26.6278 | 2.8156 | 0.985%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 11.7877 | 5.6945 | 2.07 | 11.7877 | 5.6945 | 2.07 | 13.78 | 6.6569 | 2.07 | 0.7994%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 50 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 46.3232 | 17.7953 | 2.6031 | 46.3232 | 17.7953 | 2.6031 | 54.1523 | 20.803 | 2.6031 | 0.9814%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 140 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 135.8918 | 49.8269 | 2.7273 | 135.8918 | 49.8269 | 2.7273 | 158.859 | 58.2483 | 2.7273 | 0.9776%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 76.9818 | 32.7434 | 2.3511 | 76.9818 | 32.7434 | 2.3511 | 89.9926 | 38.2774 | 2.3511 | 0.9541%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 5 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 10.7592 | 1.7795 | 6.0461 | 10.7592 | 1.7795 | 6.0461 | 12.5776 | 2.0803 | 6.0461 | 0.9906%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 11 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 44.119 | 3.915 | 11.2693 | 44.119 | 3.915 | 11.2693 | 51.5757 | 4.5766 | 11.2693 | 0.9968%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 3 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.2852 | 1.0677 | 6.8232 | 7.2852 | 1.0677 | 6.8232 | 8.5165 | 1.2482 | 6.8232 | 0.9549%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 84 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 144.6629 | 29.8962 | 4.8388 | 144.6629 | 29.8962 | 4.8388 | 169.1126 | 34.949 | 4.8388 | 0.9879%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 116 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 149.7393 | 41.2852 | 3.6269 | 149.7393 | 41.2852 | 3.6269 | 175.0469 | 48.2628 | 3.6269 | 0.9747%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 116 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 87.8785 | 41.2852 | 2.1286 | 87.8785 | 41.2852 | 2.1286 | 102.731 | 48.2628 | 2.1286 | 0.9704%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 94 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 99.8244 | 33.4552 | 2.9838 | 99.8244 | 33.4552 | 2.9838 | 116.6959 | 39.1095 | 2.9838 | 0.9781%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 4 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.0594 | 1.4236 | 3.5539 | 5.0594 | 1.4236 | 3.5539 | 5.9144 | 1.6642 | 3.5539 | 0.9721%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 3 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 11.6327 | 1.0677 | 10.8949 | 11.6327 | 1.0677 | 10.8949 | 13.5988 | 1.2482 | 10.8949 | 0.9966%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 99 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 321.8183 | 35.2348 | 9.1335 | 321.8183 | 35.2348 | 9.1335 | 376.2093 | 41.1898 | 9.1335 | 0.9859%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 4 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.2433 | 1.4236 | 7.8976 | 11.2433 | 1.4236 | 7.8976 | 13.1435 | 1.6642 | 7.8976 | 0.8901%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 2 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5082 | 0.71181 | 2.1189 | 1.5082 | 0.71181 | 2.1189 | 1.7631 | 0.83212 | 2.1189 | 0.1879%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 65 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 24.0122 | 23.1339 | 1.038 | 24.0122 | 23.1339 | 1.038 | 28.0706 | 27.0438 | 1.038 | 0.8818%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 21 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 15.7753 | 7.474 | 2.1107 | 15.7753 | 7.474 | 2.1107 | 18.4415 | 8.7372 | 2.1107 | 0.9783%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 90 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 54.4478 | 32.0316 | 1.6998 | 54.4478 | 32.0316 | 1.6998 | 63.6501 | 37.4453 | 1.6998 | 0.9847%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 2 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.2505 | 0.71181 | 15.8054 | 11.2505 | 0.71181 | 15.8054 | 13.1519 | 0.83212 | 15.8054 | 0.9597%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 15 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 29.7608 | 5.3386 | 5.5746 | 29.7608 | 5.3386 | 5.5746 | 34.7907 | 6.2409 | 5.5746 | 0.9745%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 6 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.6157 | 2.1354 | 2.1615 | 4.6157 | 2.1354 | 2.1615 | 5.3958 | 2.4964 | 2.1615 | 0.9134%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 27 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 40.4105 | 9.6095 | 4.2053 | 40.4105 | 9.6095 | 4.2053 | 47.2404 | 11.2336 | 4.2053 | 0.98%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 26 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 45.7689 | 9.2536 | 4.9461 | 45.7689 | 9.2536 | 4.9461 | 53.5043 | 10.8175 | 4.9461 | 0.9857%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 26 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 15.3052 | 9.2536 | 1.654 | 15.3052 | 9.2536 | 1.654 | 17.8919 | 10.8175 | 1.654 | 0.9609%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 1 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.01335 | 0.35591 | 0.037511 | 0.01335 | 0.35591 | 0.037511 | 0.015607 | 0.41606 | 0.037511 | 0.01745%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 31 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.2878 | 11.0331 | 0.5699 | 6.2878 | 11.0331 | 0.5699 | 7.3505 | 12.8978 | 0.5699 | 0.8492%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 22 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.6468 | 7.8299 | 0.33803 | 2.6468 | 7.8299 | 0.33803 | 3.0941 | 9.1533 | 0.33803 | 0.5795%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 161 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 88.8783 | 57.301 | 1.5511 | 88.8783 | 57.301 | 1.5511 | 103.8998 | 66.9855 | 1.5511 | 0.8848%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 14 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 5.9095 | 4.9827 | 1.186 | 5.9095 | 4.9827 | 1.186 | 6.9083 | 5.8248 | 1.186 | 0.9662%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 1 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.7229 | 0.35591 | 13.2701 | 4.7229 | 0.35591 | 13.2701 | 5.5211 | 0.41606 | 13.2701 | 0.9893%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 12 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.7629 | 4.2709 | 0.88106 | 3.7629 | 4.2709 | 0.88106 | 4.3989 | 4.9927 | 0.88106 | 0.9131%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 16 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.62594 | 5.6945 | 0.10992 | 0.62594 | 5.6945 | 0.10992 | 0.73173 | 6.6569 | 0.10992 | 0.51%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 13 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 2.8 | 4.6268 | 0.60517 | 2.8 | 4.6268 | 0.60517 | 3.2732 | 5.4088 | 0.60517 | 0.9662%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 102 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 28.9437 | 36.3025 | 0.79729 | 28.9437 | 36.3025 | 0.79729 | 33.8355 | 42.438 | 0.79729 | 0.9767%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 90 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.5062 | 32.0316 | 0.10946 | 3.5062 | 32.0316 | 0.10946 | 4.0988 | 37.4453 | 0.10946 | 0.7071%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 85 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 79.4005 | 30.2521 | 2.6246 | 79.4005 | 30.2521 | 2.6246 | 92.8201 | 35.365 | 2.6246 | 0.9496%
2028 | 445 | 445-1315 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 0.26142 | 0 | 0 | 0.26142 | 0 | 0.22693 | 0.35591 | 0.63762 | 0.22693 | 0.35591 | 0.63762 | 0.26529 | 0.41606 | 0.63762 | 0.9959%
2028 | 445 | 445-1323 | Tier-2 | Tier-2---18 | Tier-2---12 | 1 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 0.77964 | 0 | 0 | 0.77964 | 0 | 0.67678 | 0.35591 | 1.9016 | 0.67678 | 0.35591 | 1.9016 | 0.79116 | 0.41606 | 1.9016 | 0.9926%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 76 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 60.4896 | 27.0489 | 2.2363 | 60.4896 | 27.0489 | 2.2363 | 70.713 | 31.6205 | 2.2363 | 0.9611%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 43 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.3499 | 15.304 | 0.80697 | 12.3499 | 15.304 | 0.80697 | 14.4371 | 17.8905 | 0.80697 | 0.8872%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 116 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 88.2116 | 41.2852 | 2.1366 | 88.2116 | 41.2852 | 2.1366 | 103.1203 | 48.2628 | 2.1366 | 0.9569%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 65 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 12.9938 | 23.1339 | 0.56168 | 12.9938 | 23.1339 | 0.56168 | 15.1899 | 27.0438 | 0.56168 | 0.8473%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 91 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 27.954 | 32.3875 | 0.86311 | 27.954 | 32.3875 | 0.86311 | 32.6785 | 37.8614 | 0.86311 | 0.8754%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 156 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 33.8185 | 55.5214 | 0.60911 | 33.8185 | 55.5214 | 0.60911 | 39.5342 | 64.9052 | 0.60911 | 0.8812%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 9 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.4107 | 3.2032 | 3.5623 | 11.4107 | 3.2032 | 3.5623 | 13.3393 | 3.7445 | 3.5623 | 0.9724%
2028 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.16597 | 0 | 0 | 0.16597 | 0 | 0.14408 | 0.35591 | 0.40481 | 0.14408 | 0.35591 | 0.40481 | 0.16843 | 0.41606 | 0.40481 | 0.9941%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 9 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.2431 | 3.2032 | 3.1978 | 10.2431 | 3.2032 | 3.1978 | 11.9743 | 3.7445 | 3.1978 | 0.9739%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 43 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 20.8414 | 15.304 | 1.3618 | 20.8414 | 15.304 | 1.3618 | 24.3638 | 17.8905 | 1.3618 | 0.9191%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 85 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.2489 | 30.2521 | 0.33878 | 10.2489 | 30.2521 | 0.33878 | 11.9811 | 35.365 | 0.33878 | 0.557%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.4431 | 17.4394 | 0.19743 | 3.4431 | 17.4394 | 0.19743 | 4.0251 | 20.3869 | 0.19743 | 0.7618%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 45 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.3323 | 16.0158 | 0.2705 | 4.3323 | 16.0158 | 0.2705 | 5.0645 | 18.7227 | 0.2705 | 0.7912%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 224 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 72.4591 | 79.7231 | 0.90888 | 72.4591 | 79.7231 | 0.90888 | 84.7056 | 93.1972 | 0.90888 | 0.9168%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 106 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 45.779 | 37.7261 | 1.2135 | 45.779 | 37.7261 | 1.2135 | 53.5162 | 44.1023 | 1.2135 | 0.9343%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 147 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 52.8654 | 52.3183 | 1.0105 | 52.8654 | 52.3183 | 1.0105 | 61.8002 | 61.1607 | 1.0105 | 0.9049%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 22 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 12.5889 | 7.8299 | 1.6078 | 12.5889 | 7.8299 | 1.6078 | 14.7166 | 9.1533 | 1.6078 | 0.9697%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 7 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.2488 | 2.4913 | 2.1068 | 5.2488 | 2.4913 | 2.1068 | 6.1359 | 2.9124 | 2.1068 | 0.967%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 34 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 45.1059 | 12.1008 | 3.7275 | 45.1059 | 12.1008 | 3.7275 | 52.7293 | 14.146 | 3.7275 | 0.9877%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 45 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 19.2425 | 16.0158 | 1.2015 | 19.2425 | 16.0158 | 1.2015 | 22.4947 | 18.7227 | 1.2015 | 0.9555%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 26 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 71.2723 | 9.2536 | 7.7021 | 71.2723 | 9.2536 | 7.7021 | 83.3182 | 10.8175 | 7.7021 | 0.9923%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 5 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.3795 | 1.7795 | 3.5849 | 6.3795 | 1.7795 | 3.5849 | 7.4577 | 2.0803 | 3.5849 | 0.9277%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 2 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.3622 | 0.71181 | 13.1526 | 9.3622 | 0.71181 | 13.1526 | 10.9446 | 0.83212 | 13.1526 | 0.9525%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 2 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 24.4958 | 0.71181 | 34.4132 | 24.4958 | 0.71181 | 34.4132 | 28.6359 | 0.83212 | 34.4132 | 0.9993%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 1 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 29.7816 | 0.35591 | 83.678 | 29.7816 | 0.35591 | 83.678 | 34.815 | 0.41606 | 83.678 | 0.997%
2028 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.74379 | 0.71181 | 1.0449 | 0.74379 | 0.71181 | 1.0449 | 0.8695 | 0.83212 | 1.0449 | 0.9735%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 20 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 11.8471 | 7.1181 | 1.6644 | 11.8471 | 7.1181 | 1.6644 | 13.8494 | 8.3212 | 1.6644 | 0.9902%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 20 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 44.9395 | 7.1181 | 6.3134 | 44.9395 | 7.1181 | 6.3134 | 52.5347 | 8.3212 | 6.3134 | 0.9833%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 53 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 144.4024 | 18.8631 | 7.6553 | 144.4024 | 18.8631 | 7.6553 | 168.8081 | 22.0511 | 7.6553 | 0.9937%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 6 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 35.0626 | 2.1354 | 16.4194 | 35.0626 | 2.1354 | 16.4194 | 40.9886 | 2.4964 | 16.4194 | 0.9496%
2028 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 3 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.5011 | 1.0677 | 1.4059 | 1.5011 | 1.0677 | 1.4059 | 1.7549 | 1.2482 | 1.4059 | 0.216%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 1 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.7651 | 0.35591 | 4.9593 | 1.7651 | 0.35591 | 4.9593 | 2.0634 | 0.41606 | 4.9593 | 0.9963%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 2 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.3375 | 0.71181 | 8.9034 | 6.3375 | 0.71181 | 8.9034 | 7.4087 | 0.83212 | 8.9034 | 0.9951%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 47 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 25.1714 | 16.7276 | 1.5048 | 25.1714 | 16.7276 | 1.5048 | 29.4257 | 19.5548 | 1.5048 | 0.9734%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 27 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 12.5764 | 9.6095 | 1.3088 | 12.5764 | 9.6095 | 1.3088 | 14.702 | 11.2336 | 1.3088 | 0.9797%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 129 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 22.1562 | 45.912 | 0.48258 | 22.1562 | 45.912 | 0.48258 | 25.9009 | 53.6716 | 0.48258 | 0.9676%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 84 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 27.4777 | 29.8962 | 0.9191 | 27.4777 | 29.8962 | 0.9191 | 32.1217 | 34.949 | 0.9191 | 0.9272%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 31 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 13.9309 | 11.0331 | 1.2626 | 13.9309 | 11.0331 | 1.2626 | 16.2854 | 12.8978 | 1.2626 | 0.9829%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 53 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 56.7803 | 18.8631 | 3.0101 | 56.7803 | 18.8631 | 3.0101 | 66.3768 | 22.0511 | 3.0101 | 0.9672%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.0238 | 1.0677 | 4.7052 | 5.0238 | 1.0677 | 4.7052 | 5.8729 | 1.2482 | 4.7052 | 0.7734%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 19 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 17.4587 | 6.7622 | 2.5818 | 17.4587 | 6.7622 | 2.5818 | 20.4094 | 7.9051 | 2.5818 | 0.9648%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 89 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 41.8632 | 31.6757 | 1.3216 | 41.8632 | 31.6757 | 1.3216 | 48.9386 | 37.0293 | 1.3216 | 0.9649%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 74 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 17.3179 | 26.3371 | 0.65755 | 17.3179 | 26.3371 | 0.65755 | 20.2448 | 30.7884 | 0.65755 | 0.9757%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 49 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 95.2678 | 17.4394 | 5.4628 | 95.2678 | 17.4394 | 5.4628 | 111.3691 | 20.3869 | 5.4628 | 0.9669%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 87 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 71.9681 | 30.9639 | 2.3243 | 71.9681 | 30.9639 | 2.3243 | 84.1316 | 36.1971 | 2.3243 | 0.9779%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 73 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 75.1519 | 25.9812 | 2.8926 | 75.1519 | 25.9812 | 2.8926 | 87.8535 | 30.3723 | 2.8926 | 0.9936%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 25 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 48.1778 | 8.8977 | 5.4147 | 48.1778 | 8.8977 | 5.4147 | 56.3204 | 10.4015 | 5.4147 | 0.9878%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 42 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 105.606 | 14.9481 | 7.0649 | 105.606 | 14.9481 | 7.0649 | 123.4547 | 17.4745 | 7.0649 | 0.9938%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 37 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 77.4933 | 13.1685 | 5.8847 | 77.4933 | 13.1685 | 5.8847 | 90.5906 | 15.3942 | 5.8847 | 0.9905%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 47.2153 | 0.35591 | 132.6619 | 47.2153 | 0.35591 | 132.6619 | 55.1952 | 0.41606 | 132.6619 | 0.9644%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 46 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 47.3605 | 16.3717 | 2.8928 | 47.3605 | 16.3717 | 2.8928 | 55.365 | 19.1387 | 2.8928 | 0.9978%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 114 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 98.0181 | 40.5734 | 2.4158 | 98.0181 | 40.5734 | 2.4158 | 114.5843 | 47.4307 | 2.4158 | 0.9977%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 89 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 117.8145 | 31.6757 | 3.7194 | 117.8145 | 31.6757 | 3.7194 | 137.7264 | 37.0293 | 3.7194 | 0.9899%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 75.0312 | 29.8962 | 2.5097 | 75.0312 | 29.8962 | 2.5097 | 87.7123 | 34.949 | 2.5097 | 0.982%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 283 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 347.0961 | 100.7216 | 3.4461 | 347.0961 | 100.7216 | 3.4461 | 405.7593 | 117.7447 | 3.4461 | 0.9903%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 92 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 155.7203 | 32.7434 | 4.7558 | 155.7203 | 32.7434 | 4.7558 | 182.0388 | 38.2774 | 4.7558 | 0.9555%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 124 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 222.1206 | 44.1324 | 5.033 | 222.1206 | 44.1324 | 5.033 | 259.6615 | 51.5913 | 5.033 | 0.994%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 112 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 21.2119 | 39.8616 | 0.53214 | 21.2119 | 39.8616 | 0.53214 | 24.797 | 46.5986 | 0.53214 | 0.936%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 188 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 34.0376 | 66.9105 | 0.5087 | 34.0376 | 66.9105 | 0.5087 | 39.7903 | 78.2191 | 0.5087 | 0.938%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 55 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.7095 | 19.5749 | 0.24059 | 4.7095 | 19.5749 | 0.24059 | 5.5054 | 22.8832 | 0.24059 | 0.8718%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 78 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.1122 | 27.7607 | 0.47233 | 13.1122 | 27.7607 | 0.47233 | 15.3283 | 32.4526 | 0.47233 | 0.9279%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 84 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 52.3744 | 29.8962 | 1.7519 | 52.3744 | 29.8962 | 1.7519 | 61.2263 | 34.949 | 1.7519 | 0.9729%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 90 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 131.2209 | 32.0316 | 4.0966 | 131.2209 | 32.0316 | 4.0966 | 153.3987 | 37.4453 | 4.0966 | 0.9856%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 21 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 20.9682 | 7.474 | 2.8055 | 20.9682 | 7.474 | 2.8055 | 24.5121 | 8.7372 | 2.8055 | 0.9864%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 56 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 48.9805 | 19.9308 | 2.4575 | 48.9805 | 19.9308 | 2.4575 | 57.2588 | 23.2993 | 2.4575 | 0.9841%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 93 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 90.3866 | 33.0993 | 2.7308 | 90.3866 | 33.0993 | 2.7308 | 105.663 | 38.6935 | 2.7308 | 0.9831%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 79.3589 | 29.8962 | 2.6545 | 79.3589 | 29.8962 | 2.6545 | 92.7715 | 34.949 | 2.6545 | 0.9843%
2028 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.15347 | 0.71181 | 0.2156 | 0.15347 | 0.71181 | 0.2156 | 0.1794 | 0.83212 | 0.2156 | 0.9934%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 32 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 27.1554 | 11.389 | 2.3844 | 27.1554 | 11.389 | 2.3844 | 31.745 | 13.3139 | 2.3844 | 0.9977%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 15 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 14.7668 | 5.3386 | 2.766 | 14.7668 | 5.3386 | 2.766 | 17.2626 | 6.2409 | 2.766 | 0.9957%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 4 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 16.7956 | 1.4236 | 11.7978 | 16.7956 | 1.4236 | 11.7978 | 19.6343 | 1.6642 | 11.7978 | 0.9986%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 46 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.0458 | 16.3717 | 1.1633 | 19.0458 | 16.3717 | 1.1633 | 22.2647 | 19.1387 | 1.1633 | 0.9923%
2028 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 1 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 0.41445 | 0 | 0 | 0.41445 | 0 | 0.35977 | 0.35591 | 1.0109 | 0.35977 | 0.35591 | 1.0109 | 0.42058 | 0.41606 | 1.0109 | 0.9749%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 60 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 124.2819 | 21.3544 | 5.82 | 124.2819 | 21.3544 | 5.82 | 145.2869 | 24.9635 | 5.82 | 0.9856%
2028 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 1 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 56.9533 | 0 | 0 | 56.9533 | 0 | 49.4391 | 0.35591 | 138.9104 | 49.4391 | 0.35591 | 138.9104 | 57.7949 | 0.41606 | 138.9104 | 0.9998%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 13 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 62.2159 | 4.6268 | 13.4469 | 62.2159 | 4.6268 | 13.4469 | 72.7311 | 5.4088 | 13.4469 | 0.9951%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 37 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 74.781 | 13.1685 | 5.6788 | 74.781 | 13.1685 | 5.6788 | 87.4199 | 15.3942 | 5.6788 | 0.9433%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 5 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 26.9206 | 1.7795 | 15.1279 | 26.9206 | 1.7795 | 15.1279 | 31.4705 | 2.0803 | 15.1279 | 0.9258%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 34 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 106.1678 | 12.1008 | 8.7736 | 106.1678 | 12.1008 | 8.7736 | 124.1113 | 14.146 | 8.7736 | 0.9926%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 20 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 17.6579 | 7.1181 | 2.4807 | 17.6579 | 7.1181 | 2.4807 | 20.6423 | 8.3212 | 2.4807 | 0.9747%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 77 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 9.8935 | 27.4048 | 0.36101 | 9.8935 | 27.4048 | 0.36101 | 11.5656 | 32.0365 | 0.36101 | 0.7093%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 28 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 82.8796 | 9.9654 | 8.3167 | 82.8796 | 9.9654 | 8.3167 | 96.8872 | 11.6497 | 8.3167 | 0.9829%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 59 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 158.3796 | 20.9985 | 7.5424 | 158.3796 | 20.9985 | 7.5424 | 185.1476 | 24.5475 | 7.5424 | 0.989%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 2 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 22.1244 | 0.71181 | 31.0817 | 22.1244 | 0.71181 | 31.0817 | 25.8637 | 0.83212 | 31.0817 | 0.9937%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 50 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 46.29 | 17.7953 | 2.6012 | 46.29 | 17.7953 | 2.6012 | 54.1136 | 20.803 | 2.6012 | 0.9631%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 107 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 158.374 | 38.082 | 4.1588 | 158.374 | 38.082 | 4.1588 | 185.1411 | 44.5183 | 4.1588 | 0.9714%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 15 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 25.5856 | 5.3386 | 4.7926 | 25.5856 | 5.3386 | 4.7926 | 29.9099 | 6.2409 | 4.7926 | 0.9712%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 56 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 172.0911 | 19.9308 | 8.6344 | 172.0911 | 19.9308 | 8.6344 | 201.1764 | 23.2993 | 8.6344 | 0.9923%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.098 | 0.71181 | 1.5426 | 1.098 | 0.71181 | 1.5426 | 1.2836 | 0.83212 | 1.5426 | 0.9928%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.057723 | 0.35591 | 0.16219 | 0.057723 | 0.35591 | 0.16219 | 0.067479 | 0.41606 | 0.16219 | 0.9902%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 2 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.8502 | 0.71181 | 4.0041 | 2.8502 | 0.71181 | 4.0041 | 3.3319 | 0.83212 | 4.0041 | 0.9939%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 12 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 1.9514 | 4.2709 | 0.4569 | 1.9514 | 4.2709 | 0.4569 | 2.2812 | 4.9927 | 0.4569 | 0.9666%
2028 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 1.8833 | 0 | 0 | 1.8833 | 0 | 1.6348 | 0.71181 | 2.2967 | 1.6348 | 0.71181 | 2.2967 | 1.9112 | 0.83212 | 2.2967 | 0.9988%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 41 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 74.6087 | 14.5922 | 5.1129 | 74.6087 | 14.5922 | 5.1129 | 87.2184 | 17.0584 | 5.1129 | 0.9986%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 37 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 71.5161 | 13.1685 | 5.4308 | 71.5161 | 13.1685 | 5.4308 | 83.6031 | 15.3942 | 5.4308 | 0.9762%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.2032 | 0.35591 | 6.1905 | 2.2032 | 0.35591 | 6.1905 | 2.5756 | 0.41606 | 6.1905 | 0.9867%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 35 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 78.7826 | 12.4567 | 6.3245 | 78.7826 | 12.4567 | 6.3245 | 92.0977 | 14.5621 | 6.3245 | 0.9973%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 74 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 233.0596 | 26.3371 | 8.8491 | 233.0596 | 26.3371 | 8.8491 | 272.4494 | 30.7884 | 8.8491 | 0.9919%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 2 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 55.0956 | 0.71181 | 77.4018 | 55.0956 | 0.71181 | 77.4018 | 64.4074 | 0.83212 | 77.4018 | 0.9998%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 76 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 134.5725 | 27.0489 | 4.9752 | 134.5725 | 27.0489 | 4.9752 | 157.3168 | 31.6205 | 4.9752 | 0.9833%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 28 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 100.8952 | 9.9654 | 10.1246 | 100.8952 | 9.9654 | 10.1246 | 117.9476 | 11.6497 | 10.1246 | 0.988%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 109 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 46.544 | 38.7938 | 1.1998 | 46.544 | 38.7938 | 1.1998 | 54.4105 | 45.3504 | 1.1998 | 0.9625%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 40 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 11.6853 | 14.2363 | 0.82081 | 11.6853 | 14.2363 | 0.82081 | 13.6602 | 16.6424 | 0.82081 | 0.9181%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 21 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 67.9586 | 7.474 | 9.0926 | 67.9586 | 7.474 | 9.0926 | 79.4443 | 8.7372 | 9.0926 | 0.9835%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 146 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 354.179 | 51.9624 | 6.8161 | 354.179 | 51.9624 | 6.8161 | 414.0392 | 60.7446 | 6.8161 | 0.9889%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 46 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 29.0956 | 16.3717 | 1.7772 | 29.0956 | 16.3717 | 1.7772 | 34.0131 | 19.1387 | 1.7772 | 0.9191%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 194.0772 | 33.8111 | 5.74 | 194.0772 | 33.8111 | 5.74 | 226.8785 | 39.5256 | 5.74 | 0.9908%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 1 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3119 | 0.35591 | 3.6861 | 1.3119 | 0.35591 | 3.6861 | 1.5336 | 0.41606 | 3.6861 | 0.9858%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 10 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.1012 | 3.5591 | 1.9952 | 7.1012 | 3.5591 | 1.9952 | 8.3014 | 4.1606 | 1.9952 | 0.9652%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 126 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 476.1404 | 44.8442 | 10.6176 | 476.1404 | 44.8442 | 10.6176 | 556.6136 | 52.4234 | 10.6176 | 0.9927%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 99 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 278.4341 | 35.2348 | 7.9023 | 278.4341 | 35.2348 | 7.9023 | 325.4926 | 41.1898 | 7.9023 | 0.9926%
2028 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 0.62909 | 0 | 0 | 0.62909 | 0 | 0.54609 | 0.35591 | 1.5344 | 0.54609 | 0.35591 | 1.5344 | 0.63839 | 0.41606 | 1.5344 | 0.9988%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 28 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 10.7977 | 9.9654 | 1.0835 | 10.7977 | 9.9654 | 1.0835 | 12.6227 | 11.6497 | 1.0835 | 0.9598%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 12 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 29.3766 | 4.2709 | 6.8783 | 29.3766 | 4.2709 | 6.8783 | 34.3416 | 4.9927 | 6.8783 | 0.9934%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.3128 | 1.0677 | 8.7221 | 9.3128 | 1.0677 | 8.7221 | 10.8867 | 1.2482 | 8.7221 | 0.6902%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 2 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.2447 | 0.71181 | 18.607 | 13.2447 | 0.71181 | 18.607 | 15.4832 | 0.83212 | 18.607 | 0.7661%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.7551 | 0.71181 | 5.2754 | 3.7551 | 0.71181 | 5.2754 | 4.3897 | 0.83212 | 5.2754 | 0.9947%
2028 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 5 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.52569 | 1.7795 | 0.29541 | 0.52569 | 1.7795 | 0.29541 | 0.61454 | 2.0803 | 0.29541 | 0.9691%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 11 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 112.1303 | 3.915 | 28.6414 | 112.1303 | 3.915 | 28.6414 | 131.0816 | 4.5766 | 28.6414 | 0.9966%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 100 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 130.2558 | 35.5907 | 3.6598 | 130.2558 | 35.5907 | 3.6598 | 152.2705 | 41.6059 | 3.6598 | 0.9905%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 189 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 244.5755 | 67.2664 | 3.6359 | 244.5755 | 67.2664 | 3.6359 | 285.9116 | 78.6352 | 3.6359 | 0.9891%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 28 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 69.2066 | 9.9654 | 6.9447 | 69.2066 | 9.9654 | 6.9447 | 80.9033 | 11.6497 | 6.9447 | 0.9946%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 11 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 37.5911 | 3.915 | 9.6019 | 37.5911 | 3.915 | 9.6019 | 43.9444 | 4.5766 | 9.6019 | 0.9952%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 45 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 126.2079 | 16.0158 | 7.8802 | 126.2079 | 16.0158 | 7.8802 | 147.5385 | 18.7227 | 7.8802 | 0.9843%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 103 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 96.8131 | 36.6584 | 2.641 | 96.8131 | 36.6584 | 2.641 | 113.1756 | 42.8541 | 2.641 | 0.9898%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 81 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 68.5917 | 28.8284 | 2.3793 | 68.5917 | 28.8284 | 2.3793 | 80.1845 | 33.7008 | 2.3793 | 0.9853%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 106 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 199.9405 | 37.7261 | 5.2998 | 199.9405 | 37.7261 | 5.2998 | 233.7327 | 44.1023 | 5.2998 | 0.9839%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 54 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 193.8953 | 19.219 | 10.0887 | 193.8953 | 19.219 | 10.0887 | 226.6658 | 22.4672 | 10.0887 | 0.9748%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 78.7234 | 20.9985 | 3.749 | 78.7234 | 20.9985 | 3.749 | 92.0286 | 24.5475 | 3.749 | 0.9912%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 50 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 43.7441 | 17.7953 | 2.4582 | 43.7441 | 17.7953 | 2.4582 | 51.1373 | 20.803 | 2.4582 | 0.9732%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 19 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 74.4785 | 6.7622 | 11.0139 | 74.4785 | 6.7622 | 11.0139 | 87.0662 | 7.9051 | 11.0139 | 0.9953%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 82 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 55.4979 | 29.1844 | 1.9016 | 55.4979 | 29.1844 | 1.9016 | 64.8777 | 34.1168 | 1.9016 | 0.9803%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 104 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 28.408 | 37.0143 | 0.76749 | 28.408 | 37.0143 | 0.76749 | 33.2093 | 43.2701 | 0.76749 | 0.9369%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 29 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 61.4159 | 10.3213 | 5.9504 | 61.4159 | 10.3213 | 5.9504 | 71.7958 | 12.0657 | 5.9504 | 0.9955%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 1 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 44.7288 | 0.35591 | 125.6757 | 44.7288 | 0.35591 | 125.6757 | 52.2885 | 0.41606 | 125.6757 | 0.803%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 11 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.5843 | 3.915 | 0.91553 | 3.5843 | 3.915 | 0.91553 | 4.1901 | 4.5766 | 0.91553 | 0.6587%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 17 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 39.6418 | 6.0504 | 6.5519 | 39.6418 | 6.0504 | 6.5519 | 46.3417 | 7.073 | 6.5519 | 0.9978%
2028 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 1 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 28.8759 | 0.35591 | 81.1333 | 28.8759 | 0.35591 | 81.1333 | 33.7562 | 0.41606 | 81.1333 | 0.9981%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 24 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.2323 | 8.5418 | 1.4321 | 12.2323 | 8.5418 | 1.4321 | 14.2997 | 9.9854 | 1.4321 | 0.9962%
2028 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 1 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 9.81 | 0.35591 | 27.5635 | 9.81 | 0.35591 | 27.5635 | 11.4681 | 0.41606 | 27.5635 | 0.9972%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 4 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 4.9377 | 1.4236 | 3.4684 | 4.9377 | 1.4236 | 3.4684 | 5.7722 | 1.6642 | 3.4684 | 0.3454%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 4.9835 | 6.7622 | 0.73696 | 4.9835 | 6.7622 | 0.73696 | 5.8257 | 7.9051 | 0.73696 | 0.75%
2028 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | Tier-2---20 | 2 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.030773 | 0 | 0 | 0.030773 | 0 | 0.026713 | 0.71181 | 0.037528 | 0.026713 | 0.71181 | 0.037528 | 0.031228 | 0.83212 | 0.037528 | 0.1687%
2028 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 3 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.6309 | 1.0677 | 0.59089 | 0.6309 | 1.0677 | 0.59089 | 0.73753 | 1.2482 | 0.59089 | 0.9665%
2028 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 0.21747 | 0 | 0 | 0.21747 | 0 | 0.18878 | 0.35591 | 0.53042 | 0.18878 | 0.35591 | 0.53042 | 0.22069 | 0.41606 | 0.53042 | 0.9966%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 79 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 46.1797 | 28.1166 | 1.6424 | 46.1797 | 28.1166 | 1.6424 | 53.9845 | 32.8687 | 1.6424 | 0.8429%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 92 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 57.164 | 32.7434 | 1.7458 | 57.164 | 32.7434 | 1.7458 | 66.8254 | 38.2774 | 1.7458 | 0.9909%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 30 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 12.4546 | 10.6772 | 1.1665 | 12.4546 | 10.6772 | 1.1665 | 14.5596 | 12.4818 | 1.1665 | 0.9975%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.93603 | 0.71181 | 1.315 | 0.93603 | 0.71181 | 1.315 | 1.0942 | 0.83212 | 1.315 | 0.9975%
2028 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 2 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 35.3525 | 0.71181 | 49.6654 | 35.3525 | 0.71181 | 49.6654 | 41.3275 | 0.83212 | 49.6654 | 0.9993%
2028 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | Non-HFTD---22 | 1 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.037296 | 0 | 0 | 0.037296 | 0 | 0.032375 | 0.35591 | 0.090965 | 0.032375 | 0.35591 | 0.090965 | 0.037847 | 0.41606 | 0.090965 | 0.8877%
2028 | 157 | CB 157 | Tier-3 | Tier-3---21 | Tier-3---11 | 1 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.06043 | 0 | 0 | 0.06043 | 0 | 0.052457 | 0.35591 | 0.14739 | 0.052457 | 0.35591 | 0.14739 | 0.061323 | 0.41606 | 0.14739 | 0.9943%
2028 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 5 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.4844 | 1.7795 | 1.9581 | 3.4844 | 1.7795 | 1.9581 | 4.0733 | 2.0803 | 1.9581 | 0.299%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 1 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.4336 | 0.35591 | 20.8863 | 7.4336 | 0.35591 | 20.8863 | 8.6899 | 0.41606 | 20.8863 | 0.8082%
2028 | 212 | CB 212 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 0.22772 | 0 | 0 | 0.22772 | 0 | 0.19768 | 0.35591 | 0.55543 | 0.19768 | 0.35591 | 0.55543 | 0.23109 | 0.41606 | 0.55543 | 0.9909%
2028 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 1 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.844 | 0.35591 | 5.1812 | 1.844 | 0.35591 | 5.1812 | 2.1557 | 0.41606 | 5.1812 | 0.9981%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 50 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 21.5465 | 17.7953 | 1.2108 | 21.5465 | 17.7953 | 1.2108 | 25.1881 | 20.803 | 1.2108 | 0.9929%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 23 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 13.8844 | 8.1859 | 1.6961 | 13.8844 | 8.1859 | 1.6961 | 16.231 | 9.5694 | 1.6961 | 0.9737%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 35.3788 | 36.3025 | 0.97456 | 35.3788 | 36.3025 | 0.97456 | 41.3582 | 42.438 | 0.97456 | 0.9874%
2028 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 17 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 28.2802 | 6.0504 | 4.6741 | 28.2802 | 6.0504 | 4.6741 | 33.0599 | 7.073 | 4.6741 | 0.9888%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 32 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 107.7148 | 11.389 | 9.4578 | 107.7148 | 11.389 | 9.4578 | 125.9198 | 13.3139 | 9.4578 | 0.9762%
2028 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 4 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 18.2459 | 1.4236 | 12.8165 | 18.2459 | 1.4236 | 12.8165 | 21.3297 | 1.6642 | 12.8165 | 0.9954%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 23 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 10.7092 | 8.1859 | 1.3083 | 10.7092 | 8.1859 | 1.3083 | 12.5192 | 9.5694 | 1.3083 | 0.9768%
2028 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 9 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.273 | 3.2032 | 0.7096 | 2.273 | 3.2032 | 0.7096 | 2.6571 | 3.7445 | 0.7096 | 0.6436%
2028 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 5 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 0.96218 | 1.7795 | 0.54069 | 0.96218 | 1.7795 | 0.54069 | 1.1248 | 2.0803 | 0.54069 | 0.375%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.2383 | 8.5418 | 1.3157 | 11.2383 | 8.5418 | 1.3157 | 13.1378 | 9.9854 | 1.3157 | 0.9%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 1 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.3167 | 0.35591 | 6.5093 | 2.3167 | 0.35591 | 6.5093 | 2.7083 | 0.41606 | 6.5093 | 0.7028%
2028 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 30 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.3104 | 10.6772 | 0.77833 | 8.3104 | 10.6772 | 0.77833 | 9.715 | 12.4818 | 0.77833 | 0.995%
2028 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 24 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 6.9657 | 8.5418 | 0.81549 | 6.9657 | 8.5418 | 0.81549 | 8.143 | 9.9854 | 0.81549 | 0.9704%
2028 | 283 | CB 283 | Tier-3 | Tier-3---21 | Tier-3---11 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.060097 | 0 | 0 | 0.060097 | 0 | 0.052168 | 0.35591 | 0.14658 | 0.052168 | 0.35591 | 0.14658 | 0.060986 | 0.41606 | 0.14658 | 0.9941%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 12.619 | 0.35591 | 35.4558 | 12.619 | 0.35591 | 35.4558 | 14.7517 | 0.41606 | 35.4558 | 0.9979%
2028 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 5 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.2534 | 1.7795 | 1.2663 | 2.2534 | 1.7795 | 1.2663 | 2.6343 | 2.0803 | 1.2663 | 0.9938%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 28 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 126.3066 | 9.9654 | 12.6745 | 126.3066 | 9.9654 | 12.6745 | 147.6539 | 11.6497 | 12.6745 | 0.9966%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 83 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 96.8504 | 29.5403 | 3.2786 | 96.8504 | 29.5403 | 3.2786 | 113.2192 | 34.5329 | 3.2786 | 0.9884%
2028 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 53 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 50.9281 | 18.8631 | 2.6999 | 50.9281 | 18.8631 | 2.6999 | 59.5355 | 22.0511 | 2.6999 | 0.9601%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 2 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4116 | 0.71181 | 1.9831 | 1.4116 | 0.71181 | 1.9831 | 1.6502 | 0.83212 | 1.9831 | 0.1888%
2028 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 7 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.2532 | 2.4913 | 3.7141 | 9.2532 | 2.4913 | 3.7141 | 10.8171 | 2.9124 | 3.7141 | 0.9408%
2028 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 1 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 0.65999 | 0 | 0 | 0.65999 | 0 | 0.57291 | 0.35591 | 1.6097 | 0.57291 | 0.35591 | 1.6097 | 0.66974 | 0.41606 | 1.6097 | 0.9829%
2028 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 3 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 0.99585 | 1.0677 | 0.93269 | 0.99585 | 1.0677 | 0.93269 | 1.1642 | 1.2482 | 0.93269 | 0.9768%
2028 | 461 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 1 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 1.005 | 0 | 0 | 1.005 | 0 | 0.87239 | 0.35591 | 2.4512 | 0.87239 | 0.35591 | 2.4512 | 1.0198 | 0.41606 | 2.4512 | 0.9865%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 5 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 57.3752 | 1.7795 | 32.2417 | 57.3752 | 1.7795 | 32.2417 | 67.0723 | 2.0803 | 32.2417 | 0.9549%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 3 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 3.938 | 1.0677 | 3.6883 | 3.938 | 1.0677 | 3.6883 | 4.6036 | 1.2482 | 3.6883 | 0.9425%
2028 | 533 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0035677 | 0 | 0 | 0.0035677 | 0 | 0.003097 | 0.35591 | 0.0087017 | 0.003097 | 0.35591 | 0.0087017 | 0.0036204 | 0.41606 | 0.0087017 | 0.03364%
2028 | 534 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.022693 | 0 | 0 | 0.022693 | 0 | 0.019699 | 0.71181 | 0.027675 | 0.019699 | 0.71181 | 0.027675 | 0.023029 | 0.83212 | 0.027675 | 0.3599%
2028 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 1 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.051127 | 0 | 0 | 0.051127 | 0 | 0.044381 | 0.35591 | 0.1247 | 0.044381 | 0.35591 | 0.1247 | 0.051882 | 0.41606 | 0.1247 | 0.04585%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 5 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.35788 | 1.7795 | 0.20111 | 0.35788 | 1.7795 | 0.20111 | 0.41837 | 2.0803 | 0.20111 | 0.7619%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 4 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.57931 | 1.4236 | 0.40692 | 0.57931 | 1.4236 | 0.40692 | 0.67722 | 1.6642 | 0.40692 | 0.9924%
2028 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 8 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 7.8674 | 2.8473 | 2.7632 | 7.8674 | 2.8473 | 2.7632 | 9.1971 | 3.3285 | 2.7632 | 0.9545%
2028 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 3 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.8415 | 1.0677 | 2.6613 | 2.8415 | 1.0677 | 2.6613 | 3.3218 | 1.2482 | 2.6613 | 0.7837%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 22 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 37.4572 | 7.8299 | 4.7838 | 37.4572 | 7.8299 | 4.7838 | 43.7878 | 9.1533 | 4.7838 | 0.9981%
2028 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 4 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.44294 | 1.4236 | 0.31113 | 0.44294 | 1.4236 | 0.31113 | 0.5178 | 1.6642 | 0.31113 | 0.9266%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 12 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 70.7198 | 4.2709 | 16.5586 | 70.7198 | 4.2709 | 16.5586 | 82.6722 | 4.9927 | 16.5586 | 0.9507%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 8 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 23.7653 | 2.8473 | 8.3468 | 23.7653 | 2.8473 | 8.3468 | 27.7819 | 3.3285 | 8.3468 | 0.9983%
2028 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.739 | 1.4236 | 1.924 | 2.739 | 1.4236 | 1.924 | 3.2019 | 1.6642 | 1.924 | 0.9343%
2028 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 7 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 11.4584 | 2.4913 | 4.5993 | 11.4584 | 2.4913 | 4.5993 | 13.395 | 2.9124 | 4.5993 | 0.7976%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 27 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 98.9626 | 9.6095 | 10.2984 | 98.9626 | 9.6095 | 10.2984 | 115.6885 | 11.2336 | 10.2984 | 0.9951%
2028 | 974 | CB 974 | Tier-2 | Tier-2---12 | Tier-2---11 | 4 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 3.3409 | 0 | 0 | 3.3409 | 0 | 2.9001 | 1.4236 | 2.0371 | 2.9001 | 1.4236 | 2.0371 | 3.3902 | 1.6642 | 2.0371 | 0.9993%
2028 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 3 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.2677 | 1.0677 | 10.553 | 11.2677 | 1.0677 | 10.553 | 13.172 | 1.2482 | 10.553 | 0.9951%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 9 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.3565 | 3.2032 | 1.0479 | 3.3565 | 3.2032 | 1.0479 | 3.9238 | 3.7445 | 1.0479 | 0.997%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.21519 | 0.71181 | 0.30231 | 0.21519 | 0.71181 | 0.30231 | 0.25156 | 0.83212 | 0.30231 | 0.9021%
2028 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.15462 | 0 | 0 | 0.15462 | 0 | 0.13422 | 0.35591 | 0.37713 | 0.13422 | 0.35591 | 0.37713 | 0.15691 | 0.41606 | 0.37713 | 0.9981%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 29 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.0101 | 10.3213 | 1.2605 | 13.0101 | 10.3213 | 1.2605 | 15.2089 | 12.0657 | 1.2605 | 0.9785%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 32 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 43.8007 | 11.389 | 3.8459 | 43.8007 | 11.389 | 3.8459 | 51.2036 | 13.3139 | 3.8459 | 0.9856%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 109 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 59.4325 | 38.7938 | 1.532 | 59.4325 | 38.7938 | 1.532 | 69.4773 | 45.3504 | 1.532 | 0.99%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 66 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 24.8952 | 23.4898 | 1.0598 | 24.8952 | 23.4898 | 1.0598 | 29.1028 | 27.4599 | 1.0598 | 0.9473%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 65 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 89.7491 | 23.1339 | 3.8795 | 89.7491 | 23.1339 | 3.8795 | 104.9177 | 27.0438 | 3.8795 | 0.9831%
2028 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 17 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 44.5423 | 6.0504 | 7.3619 | 44.5423 | 6.0504 | 7.3619 | 52.0704 | 7.073 | 7.3619 | 0.9811%
2028 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 5 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.5273 | 1.7795 | 3.106 | 5.5273 | 1.7795 | 3.106 | 6.4615 | 2.0803 | 3.106 | 0.695%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 19 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 32.1846 | 6.7622 | 4.7595 | 32.1846 | 6.7622 | 4.7595 | 37.6241 | 7.9051 | 4.7595 | 0.9914%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 128 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 27.3464 | 45.5561 | 0.60028 | 27.3464 | 45.5561 | 0.60028 | 31.9682 | 53.2556 | 0.60028 | 0.9371%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.1367 | 18.8631 | 0.74944 | 14.1367 | 18.8631 | 0.74944 | 16.5259 | 22.0511 | 0.74944 | 0.789%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 90 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 30.7262 | 32.0316 | 0.95925 | 30.7262 | 32.0316 | 0.95925 | 35.9193 | 37.4453 | 0.95925 | 0.9517%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 30 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 80.525 | 10.6772 | 7.5418 | 80.525 | 10.6772 | 7.5418 | 94.1347 | 12.4818 | 7.5418 | 0.9933%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 58.6141 | 30.2521 | 1.9375 | 58.6141 | 30.2521 | 1.9375 | 68.5205 | 35.365 | 1.9375 | 0.9757%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 27 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 51.2664 | 9.6095 | 5.335 | 51.2664 | 9.6095 | 5.335 | 59.931 | 11.2336 | 5.335 | 0.9932%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 20 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 32.667 | 7.1181 | 4.5893 | 32.667 | 7.1181 | 4.5893 | 38.1881 | 8.3212 | 4.5893 | 0.9948%

## Fuel Management
Fuel Management - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 500 | 2126959.604 | 655.4565 | 0.03082% | 625.261 | 5194.1601 | 0.12038 | 625.261 | 5194.1601 | 0.12038 | 658.6696 | 5471.6912 | 0.12038
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 500 | 2028961.4705 | 679.4071 | 0.03349% | 618.2512 | 4954.8758 | 0.12478 | 618.2512 | 4954.8758 | 0.12478 | 686.0842 | 5498.5132 | 0.12478
[9 empty] | Capital Cost only in Year 0 | 10.89 | K$/structure | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 500 | 2106114.899 | 660.6891 | 0.03137% | 573.5212 | 4726.6149 | 0.12134 | 573.5212 | 4726.6149 | 0.12134 | 670.4528 | 5525.4667 | 0.12134
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 1500 | 6262035.9734 | 1995.5527 | 0.03187% | 1817.0334 | 14875.6508 | 0.12215 | 1817.0334 | 14875.6508 | 0.12215 | 2015.2066 | 16495.6711 | 0.12217
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 1% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] |  | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total HFTD Poles | Poles in Scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 112 | 2 | 2610.8 | 93.6% | 6.065% | 0.3401% | 0.43635 | 0 | 0 | 0.43635 | 0 | 0.41625 | 20.7766 | 0.020035 | 0.41625 | 20.7766 | 0.020035 | 0.43849 | 21.8868 | 0.020035 | 0.01671%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 188 | 4 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 0.83427 | 0 | 0 | 0.83427 | 0 | 0.79584 | 41.5533 | 0.019152 | 0.79584 | 41.5533 | 0.019152 | 0.83836 | 43.7735 | 0.019152 | 0.01996%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 55 | 1 | 622.3042 | 87.18% | 11.98% | 0.8373% | 0.098641 | 0 | 0 | 0.098641 | 0 | 0.094096 | 10.3883 | 0.0090579 | 0.094096 | 10.3883 | 0.0090579 | 0.099124 | 10.9434 | 0.0090579 | 0.01585%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 78 | 2 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 0.38731 | 0 | 0 | 0.38731 | 0 | 0.36947 | 20.7766 | 0.017783 | 0.36947 | 20.7766 | 0.017783 | 0.38921 | 21.8868 | 0.017783 | 0.02379%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 84 | 4 | 6201.607 | 97.29% | 2.601% | 0.1104% | 2.8731 | 0 | 0 | 2.8731 | 0 | 2.7407 | 41.5533 | 0.065957 | 2.7407 | 41.5533 | 0.065957 | 2.8872 | 43.7735 | 0.065957 | 0.04633%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 90 | 3 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 5.0388 | 0 | 0 | 5.0388 | 0 | 4.8067 | 31.165 | 0.15423 | 4.8067 | 31.165 | 0.15423 | 5.0635 | 32.8301 | 0.15423 | 0.03285%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 56 | 1 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 1.0076 | 0 | 0 | 1.0076 | 0 | 0.96117 | 10.3883 | 0.092524 | 0.96117 | 10.3883 | 0.092524 | 1.0125 | 10.9434 | 0.092524 | 0.01757%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 93 | 2 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 2.2392 | 0 | 0 | 2.2392 | 0 | 2.1361 | 20.7766 | 0.10281 | 2.1361 | 20.7766 | 0.10281 | 2.2502 | 21.8868 | 0.10281 | 0.02114%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 5 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 5.4417 | 0 | 0 | 5.4417 | 0 | 5.191 | 51.9416 | 0.099939 | 5.191 | 51.9416 | 0.099939 | 5.4684 | 54.7169 | 0.099939 | 0.05859%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 60 | 1 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 2.3862 | 0 | 0 | 2.3862 | 0 | 2.2763 | 10.3883 | 0.21912 | 2.2763 | 10.3883 | 0.21912 | 2.3979 | 10.9434 | 0.21912 | 0.01643%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 34 | 1 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 3.5972 | 0 | 0 | 3.5972 | 0 | 3.4315 | 10.3883 | 0.33032 | 3.4315 | 10.3883 | 0.33032 | 3.6148 | 10.9434 | 0.33032 | 0.0292%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 77 | 1 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 0.14802 | 0 | 0 | 0.14802 | 0 | 0.1412 | 10.3883 | 0.013592 | 0.1412 | 10.3883 | 0.013592 | 0.14874 | 10.9434 | 0.013592 | 0.009211%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 28 | 1 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 3.4099 | 0 | 0 | 3.4099 | 0 | 3.2528 | 10.3883 | 0.31312 | 3.2528 | 10.3883 | 0.31312 | 3.4266 | 10.9434 | 0.31312 | 0.0351%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 59 | 2 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 6.1848 | 0 | 0 | 6.1848 | 0 | 5.8999 | 20.7766 | 0.28397 | 5.8999 | 20.7766 | 0.28397 | 6.2151 | 21.8868 | 0.28397 | 0.03352%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 50 | 1 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 1.0665 | 0 | 0 | 1.0665 | 0 | 1.0174 | 10.3883 | 0.097935 | 1.0174 | 10.3883 | 0.097935 | 1.0717 | 10.9434 | 0.097935 | 0.01926%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 107 | 3 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 5.1153 | 0 | 0 | 5.1153 | 0 | 4.8796 | 31.165 | 0.15657 | 4.8796 | 31.165 | 0.15657 | 5.1404 | 32.8301 | 0.15657 | 0.02724%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 15 | 1 | 3034.8235 | 97.12% | 2.752% | 0.1275% | 1.965 | 0 | 0 | 1.965 | 0 | 1.8744 | 10.3883 | 0.18044 | 1.8744 | 10.3883 | 0.18044 | 1.9746 | 10.9434 | 0.18044 | 0.06475%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 56 | 2 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 7.0802 | 0 | 0 | 7.0802 | 0 | 6.7541 | 20.7766 | 0.32508 | 6.7541 | 20.7766 | 0.32508 | 7.1149 | 21.8868 | 0.32508 | 0.03544%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 28 | 1 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 0.44424 | 0 | 0 | 0.44424 | 0 | 0.42378 | 10.3883 | 0.040794 | 0.42378 | 10.3883 | 0.040794 | 0.44642 | 10.9434 | 0.040794 | 0.03428%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 20 | 3 | 418.5676 | 87.71% | 11.66% | 0.6303% | 0.55066 | 0 | 0 | 0.55066 | 0 | 0.52529 | 31.165 | 0.016855 | 0.52529 | 31.165 | 0.016855 | 0.55336 | 32.8301 | 0.016855 | 0.1316%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 177 | 2 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 0.57535 | 0 | 0 | 0.57535 | 0 | 0.54885 | 20.7766 | 0.026417 | 0.54885 | 20.7766 | 0.026417 | 0.57817 | 21.8868 | 0.026417 | 0.01045%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 20 | 1 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 1.9184 | 0 | 0 | 1.9184 | 0 | 1.83 | 10.3883 | 0.17616 | 1.83 | 10.3883 | 0.17616 | 1.9278 | 10.9434 | 0.17616 | 0.04949%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 151 | 5 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 0.55652 | 0 | 0 | 0.55652 | 0 | 0.53089 | 51.9416 | 0.010221 | 0.53089 | 51.9416 | 0.010221 | 0.55925 | 54.7169 | 0.010221 | 0.027%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 1 | 1867.403 | 95.01% | 4.712% | 0.2778% | 0.33476 | 0 | 0 | 0.33476 | 0 | 0.31934 | 10.3883 | 0.03074 | 0.31934 | 10.3883 | 0.03074 | 0.3364 | 10.9434 | 0.03074 | 0.01793%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 205 | 7 | 18749.5963 | 97% | 2.901% | 0.09453% | 6.2105 | 0 | 0 | 6.2105 | 0 | 5.9244 | 72.7182 | 0.081471 | 5.9244 | 72.7182 | 0.081471 | 6.241 | 76.6037 | 0.081471 | 0.03312%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 19 | 1 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 2.1015 | 0 | 0 | 2.1015 | 0 | 2.0047 | 10.3883 | 0.19297 | 2.0047 | 10.3883 | 0.19297 | 2.1118 | 10.9434 | 0.19297 | 0.05216%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 1 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 0.67886 | 0 | 0 | 0.67886 | 0 | 0.64758 | 10.3883 | 0.062338 | 0.64758 | 10.3883 | 0.062338 | 0.68218 | 10.9434 | 0.062338 | 0.01548%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 113 | 4 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 1.9686 | 0 | 0 | 1.9686 | 0 | 1.8779 | 41.5533 | 0.045193 | 1.8779 | 41.5533 | 0.045193 | 1.9782 | 43.7735 | 0.045193 | 0.03429%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 2 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 3.6714 | 0 | 0 | 3.6714 | 0 | 3.5023 | 20.7766 | 0.16857 | 3.5023 | 20.7766 | 0.16857 | 3.6894 | 21.8868 | 0.16857 | 0.03186%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 51 | 1 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 0.65179 | 0 | 0 | 0.65179 | 0 | 0.62177 | 10.3883 | 0.059853 | 0.62177 | 10.3883 | 0.059853 | 0.65499 | 10.9434 | 0.059853 | 0.01916%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 44 | 3 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 3.2869 | 0 | 0 | 3.2869 | 0 | 3.1355 | 31.165 | 0.10061 | 3.1355 | 31.165 | 0.10061 | 3.303 | 32.8301 | 0.10061 | 0.06661%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 115 | 1 | 13172.958 | 96.8% | 3.124% | 0.0728% | 1.1089 | 0 | 0 | 1.1089 | 0 | 1.0578 | 10.3883 | 0.10182 | 1.0578 | 10.3883 | 0.10182 | 1.1143 | 10.9434 | 0.10182 | 0.008418%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 40 | 1 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 2.8092 | 0 | 0 | 2.8092 | 0 | 2.6798 | 10.3883 | 0.25796 | 2.6798 | 10.3883 | 0.25796 | 2.823 | 10.9434 | 0.25796 | 0.02357%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 8 | 1 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 1.981 | 0 | 0 | 1.981 | 0 | 1.8897 | 10.3883 | 0.18191 | 1.8897 | 10.3883 | 0.18191 | 1.9907 | 10.9434 | 0.18191 | 0.1149%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 1 | 1 | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 12.1749 | 10.3883 | 1.172 | 12.1749 | 10.3883 | 1.172 | 12.8254 | 10.9434 | 1.172 | 0.9978%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 19 | 1 | 498.1496 | 90.1% | 9.186% | 0.7154% | 0.23622 | 0 | 0 | 0.23622 | 0 | 0.22534 | 10.3883 | 0.021692 | 0.22534 | 10.3883 | 0.021692 | 0.23738 | 10.9434 | 0.021692 | 0.04742%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 60 | 3 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 0.44491 | 0 | 0 | 0.44491 | 0 | 0.42441 | 31.165 | 0.013618 | 0.42441 | 31.165 | 0.013618 | 0.44709 | 32.8301 | 0.013618 | 0.04287%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 38 | 1 | 317.7725 | 50.82% | 48.53% | 0.6462% | 0.042501 | 0 | 0 | 0.042501 | 0 | 0.040543 | 10.3883 | 0.0039028 | 0.040543 | 10.3883 | 0.0039028 | 0.04271 | 10.9434 | 0.0039028 | 0.01337%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 145 | 2 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 0.21032 | 0 | 0 | 0.21032 | 0 | 0.20063 | 20.7766 | 0.0096564 | 0.20063 | 20.7766 | 0.0096564 | 0.21135 | 21.8868 | 0.0096564 | 0.01162%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 2 | 1890.633 | 91.06% | 8.49% | 0.4466% | 0.52172 | 0 | 0 | 0.52172 | 0 | 0.49769 | 20.7766 | 0.023954 | 0.49769 | 20.7766 | 0.023954 | 0.52428 | 21.8868 | 0.023954 | 0.0276%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 1 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 0.21306 | 0 | 0 | 0.21306 | 0 | 0.20325 | 10.3883 | 0.019565 | 0.20325 | 10.3883 | 0.019565 | 0.21411 | 10.9434 | 0.019565 | 0.01357%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 46 | 3 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 3.1606 | 0 | 0 | 3.1606 | 0 | 3.015 | 31.165 | 0.096745 | 3.015 | 31.165 | 0.096745 | 3.1761 | 32.8301 | 0.096745 | 0.06466%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 68 | 3 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 0.63619 | 0 | 0 | 0.63619 | 0 | 0.60688 | 31.165 | 0.019473 | 0.60688 | 31.165 | 0.019473 | 0.63931 | 32.8301 | 0.019473 | 0.04291%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 103 | 2 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 0.51302 | 0 | 0 | 0.51302 | 0 | 0.48939 | 20.7766 | 0.023555 | 0.48939 | 20.7766 | 0.023555 | 0.51554 | 21.8868 | 0.023555 | 0.0186%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 39 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 0.25869 | 0 | 0 | 0.25869 | 0 | 0.24677 | 10.3883 | 0.023755 | 0.24677 | 10.3883 | 0.023755 | 0.25995 | 10.9434 | 0.023755 | 0.0249%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 45 | 1 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 0.31977 | 0 | 0 | 0.31977 | 0 | 0.30504 | 10.3883 | 0.029364 | 0.30504 | 10.3883 | 0.029364 | 0.32134 | 10.9434 | 0.029364 | 0.02174%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 127 | 6 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 12.2804 | 0 | 0 | 12.2804 | 0 | 11.7147 | 62.3299 | 0.18795 | 11.7147 | 62.3299 | 0.18795 | 12.3406 | 65.6603 | 0.18795 | 0.04673%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 75 | 2 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 1.7673 | 0 | 0 | 1.7673 | 0 | 1.6859 | 20.7766 | 0.081143 | 1.6859 | 20.7766 | 0.081143 | 1.776 | 21.8868 | 0.081143 | 0.02651%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 30 | 1 | 484.0355 | 97.4% | 1.48% | 1.12% | 0.15715 | 0 | 0 | 0.15715 | 0 | 0.14991 | 10.3883 | 0.014431 | 0.14991 | 10.3883 | 0.014431 | 0.15792 | 10.9434 | 0.014431 | 0.03247%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 22 | 1 | 400.1895 | 97.86% | 1.359% | 0.7809% | 0.17801 | 0 | 0 | 0.17801 | 0 | 0.16981 | 10.3883 | 0.016346 | 0.16981 | 10.3883 | 0.016346 | 0.17888 | 10.9434 | 0.016346 | 0.04448%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 32 | 1 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 0.68385 | 0 | 0 | 0.68385 | 0 | 0.65234 | 10.3883 | 0.062796 | 0.65234 | 10.3883 | 0.062796 | 0.6872 | 10.9434 | 0.062796 | 0.03097%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 1 | 19489.7064 | 99% | 0.9737% | 0.02962% | 3.3266 | 0 | 0 | 3.3266 | 0 | 3.1733 | 10.3883 | 0.30547 | 3.1733 | 10.3883 | 0.30547 | 3.3429 | 10.9434 | 0.30547 | 0.01707%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 26 | 1 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 2.0677 | 0 | 0 | 2.0677 | 0 | 1.9724 | 10.3883 | 0.18987 | 1.9724 | 10.3883 | 0.18987 | 2.0778 | 10.9434 | 0.18987 | 0.03804%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 67 | 4 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 8.3146 | 0 | 0 | 8.3146 | 0 | 7.9315 | 41.5533 | 0.19088 | 7.9315 | 41.5533 | 0.19088 | 8.3553 | 43.7735 | 0.19088 | 0.05922%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 126 | 1 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 0.14259 | 0 | 0 | 0.14259 | 0 | 0.13602 | 10.3883 | 0.013094 | 0.13602 | 10.3883 | 0.013094 | 0.14329 | 10.9434 | 0.013094 | 0.007081%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 84 | 3 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 0.85578 | 0 | 0 | 0.85578 | 0 | 0.81635 | 31.165 | 0.026195 | 0.81635 | 31.165 | 0.026195 | 0.85997 | 32.8301 | 0.026195 | 0.03137%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 71 | 1 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 1.4854 | 0 | 0 | 1.4854 | 0 | 1.417 | 10.3883 | 0.1364 | 1.417 | 10.3883 | 0.1364 | 1.4927 | 10.9434 | 0.1364 | 0.0139%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 68 | 4 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 2.0364 | 0 | 0 | 2.0364 | 0 | 1.9426 | 41.5533 | 0.046749 | 1.9426 | 41.5533 | 0.046749 | 2.0464 | 43.7735 | 0.046749 | 0.05568%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 1 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 0.18677 | 0 | 0 | 0.18677 | 0 | 0.17817 | 10.3883 | 0.017151 | 0.17817 | 10.3883 | 0.017151 | 0.18769 | 10.9434 | 0.017151 | 0.01298%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 48 | 1 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 2.0877 | 0 | 0 | 2.0877 | 0 | 1.9915 | 10.3883 | 0.1917 | 1.9915 | 10.3883 | 0.1917 | 2.0979 | 10.9434 | 0.1917 | 0.02064%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 155 | 7 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 1.4472 | 0 | 0 | 1.4472 | 0 | 1.3805 | 72.7182 | 0.018984 | 1.3805 | 72.7182 | 0.018984 | 1.4543 | 76.6037 | 0.018984 | 0.04036%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 2.1692 | 0 | 0 | 2.1692 | 0 | 2.0692 | 10.3883 | 0.19919 | 2.0692 | 10.3883 | 0.19919 | 2.1798 | 10.9434 | 0.19919 | 0.05877%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 77 | 3 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 1.1743 | 0 | 0 | 1.1743 | 0 | 1.1202 | 31.165 | 0.035943 | 1.1202 | 31.165 | 0.035943 | 1.18 | 32.8301 | 0.035943 | 0.03591%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 93 | 4 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 1.1309 | 0 | 0 | 1.1309 | 0 | 1.0788 | 41.5533 | 0.025963 | 1.0788 | 41.5533 | 0.025963 | 1.1365 | 43.7735 | 0.025963 | 0.04134%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 72 | 1 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 0.53024 | 0 | 0 | 0.53024 | 0 | 0.50582 | 10.3883 | 0.048691 | 0.50582 | 10.3883 | 0.048691 | 0.53284 | 10.9434 | 0.048691 | 0.01348%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 18 | 1 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 5.3215 | 0 | 0 | 5.3215 | 0 | 5.0764 | 10.3883 | 0.48866 | 5.0764 | 10.3883 | 0.48866 | 5.3476 | 10.9434 | 0.48866 | 0.05533%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 1 | 1359.3953 | 95.15% | 4.696% | 0.1502% | 0.5624 | 0 | 0 | 0.5624 | 0 | 0.53649 | 10.3883 | 0.051644 | 0.53649 | 10.3883 | 0.051644 | 0.56516 | 10.9434 | 0.051644 | 0.04137%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 137 | 9 | 7406.689 | 96.62% | 3.25% | 0.1263% | 4.7014 | 0 | 0 | 4.7014 | 0 | 4.4848 | 93.4949 | 0.047969 | 4.4848 | 93.4949 | 0.047969 | 4.7245 | 98.4904 | 0.047969 | 0.06348%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 212 | 4 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 14.8306 | 0 | 0 | 14.8306 | 0 | 14.1474 | 41.5533 | 0.34046 | 14.1474 | 41.5533 | 0.34046 | 14.9033 | 43.7735 | 0.34046 | 0.01873%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 81 | 2 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 11.0962 | 0 | 0 | 11.0962 | 0 | 10.585 | 20.7766 | 0.50947 | 10.585 | 20.7766 | 0.50947 | 11.1505 | 21.8868 | 0.50947 | 0.0246%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 132 | 2 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 1.0808 | 0 | 0 | 1.0808 | 0 | 1.031 | 20.7766 | 0.049625 | 1.031 | 20.7766 | 0.049625 | 1.0861 | 21.8868 | 0.049625 | 0.01455%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 1220 | 8 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 1.0635 | 0 | 0 | 1.0635 | 0 | 1.0145 | 83.1066 | 0.012207 | 1.0145 | 83.1066 | 0.012207 | 1.0687 | 87.5471 | 0.012207 | 0.006341%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 52 | 1 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 0.36541 | 0 | 0 | 0.36541 | 0 | 0.34857 | 10.3883 | 0.033554 | 0.34857 | 10.3883 | 0.033554 | 0.3672 | 10.9434 | 0.033554 | 0.01827%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 84 | 3 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 2.242 | 0 | 0 | 2.242 | 0 | 2.1387 | 31.165 | 0.068627 | 2.1387 | 31.165 | 0.068627 | 2.253 | 32.8301 | 0.068627 | 0.03509%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 57 | 3 | 2072.8837 | 91.06% | 8.635% | 0.3% | 0.99351 | 0 | 0 | 0.99351 | 0 | 0.94774 | 31.165 | 0.03041 | 0.94774 | 31.165 | 0.03041 | 0.99838 | 32.8301 | 0.03041 | 0.04793%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 17 | 2 | 536.3838 | 78.97% | 20.71% | 0.32% | 0.49832 | 0 | 0 | 0.49832 | 0 | 0.47536 | 20.7766 | 0.02288 | 0.47536 | 20.7766 | 0.02288 | 0.50076 | 21.8868 | 0.02288 | 0.0929%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 151 | 9 | 5142.095 | 98.68% | 0.901% | 0.4182% | 3.0244 | 0 | 0 | 3.0244 | 0 | 2.8851 | 93.4949 | 0.030858 | 2.8851 | 93.4949 | 0.030858 | 3.0392 | 98.4904 | 0.030858 | 0.05882%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 50 | 1 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 0.49643 | 0 | 0 | 0.49643 | 0 | 0.47356 | 10.3883 | 0.045585 | 0.47356 | 10.3883 | 0.045585 | 0.49886 | 10.9434 | 0.045585 | 0.01986%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 57 | 2 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 1.0528 | 0 | 0 | 1.0528 | 0 | 1.0043 | 20.7766 | 0.048339 | 1.0043 | 20.7766 | 0.048339 | 1.058 | 21.8868 | 0.048339 | 0.03468%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 47 | 2 | 718.991 | 97.57% | 1.357% | 1.072% | 0.29852 | 0 | 0 | 0.29852 | 0 | 0.28477 | 20.7766 | 0.013706 | 0.28477 | 20.7766 | 0.013706 | 0.29998 | 21.8868 | 0.013706 | 0.04152%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 79 | 1 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 0.25463 | 0 | 0 | 0.25463 | 0 | 0.2429 | 10.3883 | 0.023382 | 0.2429 | 10.3883 | 0.023382 | 0.25588 | 10.9434 | 0.023382 | 0.01087%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 5 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 1.9978 | 0 | 0 | 1.9978 | 0 | 1.9058 | 51.9416 | 0.036691 | 1.9058 | 51.9416 | 0.036691 | 2.0076 | 54.7169 | 0.036691 | 0.0484%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 17 | 1 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 1.9164 | 0 | 0 | 1.9164 | 0 | 1.8281 | 10.3883 | 0.17598 | 1.8281 | 10.3883 | 0.17598 | 1.9258 | 10.9434 | 0.17598 | 0.05816%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 14 | 1 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 2.7696 | 0 | 0 | 2.7696 | 0 | 2.642 | 10.3883 | 0.25433 | 2.642 | 10.3883 | 0.25433 | 2.7832 | 10.9434 | 0.25433 | 0.0633%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 37 | 1 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 0.74224 | 0 | 0 | 0.74224 | 0 | 0.70804 | 10.3883 | 0.068158 | 0.70804 | 10.3883 | 0.068158 | 0.74587 | 10.9434 | 0.068158 | 0.02629%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 25 | 1 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 0.89167 | 0 | 0 | 0.89167 | 0 | 0.85059 | 10.3883 | 0.08188 | 0.85059 | 10.3883 | 0.08188 | 0.89604 | 10.9434 | 0.08188 | 0.03944%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 51 | 2 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 2.0507 | 0 | 0 | 2.0507 | 0 | 1.9562 | 20.7766 | 0.094156 | 1.9562 | 20.7766 | 0.094156 | 2.0608 | 21.8868 | 0.094156 | 0.03846%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 124 | 4 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 6.7341 | 0 | 0 | 6.7341 | 0 | 6.4239 | 41.5533 | 0.15459 | 6.4239 | 41.5533 | 0.15459 | 6.7671 | 43.7735 | 0.15459 | 0.03173%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 56 | 1 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 1.2104 | 0 | 0 | 1.2104 | 0 | 1.1547 | 10.3883 | 0.11115 | 1.1547 | 10.3883 | 0.11115 | 1.2164 | 10.9434 | 0.11115 | 0.01747%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 32 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 3.8777 | 0 | 0 | 3.8777 | 0 | 3.6991 | 10.3883 | 0.35608 | 3.6991 | 10.3883 | 0.35608 | 3.8967 | 10.9434 | 0.35608 | 0.03051%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 16 | 1 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 2.2576 | 0 | 0 | 2.2576 | 0 | 2.1536 | 10.3883 | 0.20731 | 2.1536 | 10.3883 | 0.20731 | 2.2687 | 10.9434 | 0.20731 | 0.06212%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 62 | 2 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 9.0529 | 0 | 0 | 9.0529 | 0 | 8.6359 | 20.7766 | 0.41565 | 8.6359 | 20.7766 | 0.41565 | 9.0973 | 21.8868 | 0.41565 | 0.03205%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 71 | 2 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 7.5439 | 0 | 0 | 7.5439 | 0 | 7.1963 | 20.7766 | 0.34637 | 7.1963 | 20.7766 | 0.34637 | 7.5808 | 21.8868 | 0.34637 | 0.02786%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 13 | 1 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 1.9235 | 0 | 0 | 1.9235 | 0 | 1.8349 | 10.3883 | 0.17663 | 1.8349 | 10.3883 | 0.17663 | 1.9329 | 10.9434 | 0.17663 | 0.07602%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 165 | 1 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1.8557 | 0 | 0 | 1.8557 | 0 | 1.7703 | 10.3883 | 0.17041 | 1.7703 | 10.3883 | 0.17041 | 1.8648 | 10.9434 | 0.17041 | 0.006007%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 182 | 6 | 65515.492 | 98.93% | 1.038% | 0.03019% | 21.3678 | 0 | 0 | 21.3678 | 0 | 20.3834 | 62.3299 | 0.32702 | 20.3834 | 62.3299 | 0.32702 | 21.4725 | 65.6603 | 0.32702 | 0.03261%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 1 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 0.46823 | 0 | 0 | 0.46823 | 0 | 0.44666 | 10.3883 | 0.042996 | 0.44666 | 10.3883 | 0.042996 | 0.47052 | 10.9434 | 0.042996 | 0.04194%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 72 | 1 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 0.85532 | 0 | 0 | 0.85532 | 0 | 0.81592 | 10.3883 | 0.078542 | 0.81592 | 10.3883 | 0.078542 | 0.85952 | 10.9434 | 0.078542 | 0.01364%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 17 | 1 | 376.72 | 96.88% | 2.523% | 0.5996% | 0.21468 | 0 | 0 | 0.21468 | 0 | 0.20479 | 10.3883 | 0.019714 | 0.20479 | 10.3883 | 0.019714 | 0.21573 | 10.9434 | 0.019714 | 0.05699%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 73 | 1 | 4437.6588 | 97.91% | 1.769% | 0.321% | 0.59519 | 0 | 0 | 0.59519 | 0 | 0.56777 | 10.3883 | 0.054655 | 0.56777 | 10.3883 | 0.054655 | 0.59811 | 10.9434 | 0.054655 | 0.01341%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 50 | 1 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 0.74152 | 0 | 0 | 0.74152 | 0 | 0.70736 | 10.3883 | 0.068092 | 0.70736 | 10.3883 | 0.068092 | 0.74516 | 10.9434 | 0.068092 | 0.01981%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 104 | 3 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 1.0238 | 0 | 0 | 1.0238 | 0 | 0.9766 | 31.165 | 0.031337 | 0.9766 | 31.165 | 0.031337 | 1.0288 | 32.8301 | 0.031337 | 0.02793%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 9 | 1 | 406.8184 | 64.36% | 35.02% | 0.6193% | 0.29093 | 0 | 0 | 0.29093 | 0 | 0.27753 | 10.3883 | 0.026716 | 0.27753 | 10.3883 | 0.026716 | 0.29236 | 10.9434 | 0.026716 | 0.07151%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 71 | 1 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 0.45102 | 0 | 0 | 0.45102 | 0 | 0.43024 | 10.3883 | 0.041416 | 0.43024 | 10.3883 | 0.041416 | 0.45323 | 10.9434 | 0.041416 | 0.01332%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 1 | 1438.4419 | 90% | 9.47% | 0.5268% | 0.53943 | 0 | 0 | 0.53943 | 0 | 0.51458 | 10.3883 | 0.049535 | 0.51458 | 10.3883 | 0.049535 | 0.54208 | 10.9434 | 0.049535 | 0.0375%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 33 | 1 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 0.38136 | 0 | 0 | 0.38136 | 0 | 0.36379 | 10.3883 | 0.035019 | 0.36379 | 10.3883 | 0.035019 | 0.38323 | 10.9434 | 0.035019 | 0.02803%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 30 | 1 | 962.1527 | 99.5% | 0% | 0.4991% | 0.31912 | 0 | 0 | 0.31912 | 0 | 0.30442 | 10.3883 | 0.029304 | 0.30442 | 10.3883 | 0.029304 | 0.32068 | 10.9434 | 0.029304 | 0.03317%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 99 | 1 | 3753.23 | 95.85% | 3.876% | 0.273% | 0.36338 | 0 | 0 | 0.36338 | 0 | 0.34664 | 10.3883 | 0.033369 | 0.34664 | 10.3883 | 0.033369 | 0.36517 | 10.9434 | 0.033369 | 0.009682%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 29 | 1 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 1.801 | 0 | 0 | 1.801 | 0 | 1.7181 | 10.3883 | 0.16538 | 1.7181 | 10.3883 | 0.16538 | 1.8099 | 10.9434 | 0.16538 | 0.03398%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 40 | 3 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 1.326 | 0 | 0 | 1.326 | 0 | 1.2649 | 31.165 | 0.040587 | 1.2649 | 31.165 | 0.040587 | 1.3325 | 32.8301 | 0.040587 | 0.06585%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 1 | 1 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.8672 | 10.3883 | 1.3349 | 13.8672 | 10.3883 | 1.3349 | 14.6082 | 10.9434 | 1.3349 | 0.9979%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 138 | 3 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 0.74769 | 0 | 0 | 0.74769 | 0 | 0.71324 | 31.165 | 0.022886 | 0.71324 | 31.165 | 0.022886 | 0.75135 | 32.8301 | 0.022886 | 0.02076%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 245 | 6 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 3.3339 | 0 | 0 | 3.3339 | 0 | 3.1803 | 62.3299 | 0.051023 | 3.1803 | 62.3299 | 0.051023 | 3.3502 | 65.6603 | 0.051023 | 0.02403%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 229 | 5 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 1.1797 | 0 | 0 | 1.1797 | 0 | 1.1253 | 51.9416 | 0.021665 | 1.1253 | 51.9416 | 0.021665 | 1.1854 | 54.7169 | 0.021665 | 0.02118%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 2 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 2.9185 | 0 | 0 | 2.9185 | 0 | 2.784 | 20.7766 | 0.134 | 2.784 | 20.7766 | 0.134 | 2.9328 | 21.8868 | 0.134 | 0.02158%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 107 | 3 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 3.1053 | 0 | 0 | 3.1053 | 0 | 2.9622 | 31.165 | 0.095049 | 2.9622 | 31.165 | 0.095049 | 3.1205 | 32.8301 | 0.095049 | 0.02772%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 1 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 3.5692 | 0 | 0 | 3.5692 | 0 | 3.4048 | 10.3883 | 0.32775 | 3.4048 | 10.3883 | 0.32775 | 3.5867 | 10.9434 | 0.32775 | 0.1417%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 7 | 1 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 2.5232 | 0 | 0 | 2.5232 | 0 | 2.4069 | 10.3883 | 0.2317 | 2.4069 | 10.3883 | 0.2317 | 2.5355 | 10.9434 | 0.2317 | 0.1267%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 42 | 1 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 3.2042 | 0 | 0 | 3.2042 | 0 | 3.0566 | 10.3883 | 0.29423 | 3.0566 | 10.3883 | 0.29423 | 3.2199 | 10.9434 | 0.29423 | 0.02367%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 121 | 2 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 3.3619 | 0 | 0 | 3.3619 | 0 | 3.207 | 20.7766 | 0.15436 | 3.207 | 20.7766 | 0.15436 | 3.3784 | 21.8868 | 0.15436 | 0.01639%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 83 | 1 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 1.3442 | 0 | 0 | 1.3442 | 0 | 1.2823 | 10.3883 | 0.12344 | 1.2823 | 10.3883 | 0.12344 | 1.3508 | 10.9434 | 0.12344 | 0.01191%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 50 | 1 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 1.0673 | 0 | 0 | 1.0673 | 0 | 1.0181 | 10.3883 | 0.098005 | 1.0181 | 10.3883 | 0.098005 | 1.0725 | 10.9434 | 0.098005 | 0.01963%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 140 | 2 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 2.2364 | 0 | 0 | 2.2364 | 0 | 2.1333 | 20.7766 | 0.10268 | 2.1333 | 20.7766 | 0.10268 | 2.2473 | 21.8868 | 0.10268 | 0.01397%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 2 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 1.9279 | 0 | 0 | 1.9279 | 0 | 1.8391 | 20.7766 | 0.088516 | 1.8391 | 20.7766 | 0.088516 | 1.9373 | 21.8868 | 0.088516 | 0.02074%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 84 | 1 | 16869.708 | 98.79% | 1.184% | 0.02933% | 1.9839 | 0 | 0 | 1.9839 | 0 | 1.8925 | 10.3883 | 0.18218 | 1.8925 | 10.3883 | 0.18218 | 1.9937 | 10.9434 | 0.18218 | 0.01176%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 116 | 3 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 4.4611 | 0 | 0 | 4.4611 | 0 | 4.2556 | 31.165 | 0.13655 | 4.2556 | 31.165 | 0.13655 | 4.483 | 32.8301 | 0.13655 | 0.02521%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 116 | 4 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 3.4909 | 0 | 0 | 3.4909 | 0 | 3.33 | 41.5533 | 0.080139 | 3.33 | 41.5533 | 0.080139 | 3.508 | 43.7735 | 0.080139 | 0.03346%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 94 | 3 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 3.6701 | 0 | 0 | 3.6701 | 0 | 3.501 | 31.165 | 0.11234 | 3.501 | 31.165 | 0.11234 | 3.6881 | 32.8301 | 0.11234 | 0.03121%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 53 | 1 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 1.107 | 0 | 0 | 1.107 | 0 | 1.056 | 10.3883 | 0.10165 | 1.056 | 10.3883 | 0.10165 | 1.1124 | 10.9434 | 0.10165 | 0.01811%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 99 | 7 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 26.2133 | 0 | 0 | 26.2133 | 0 | 25.0057 | 72.7182 | 0.34387 | 25.0057 | 72.7182 | 0.34387 | 26.3418 | 76.6037 | 0.34387 | 0.06971%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 2 | 1 | 924.8041 | 18.79% | 81.02% | 0.1888% | 0.86873 | 0 | 0 | 0.86873 | 0 | 0.82871 | 10.3883 | 0.079773 | 0.82871 | 10.3883 | 0.079773 | 0.87299 | 10.9434 | 0.079773 | 0.09394%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 65 | 2 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 0.85113 | 0 | 0 | 0.85113 | 0 | 0.81192 | 20.7766 | 0.039079 | 0.81192 | 20.7766 | 0.039079 | 0.8553 | 21.8868 | 0.039079 | 0.02713%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 90 | 2 | 6370.0414 | 98.47% | 1.262% | 0.272% | 1.3938 | 0 | 0 | 1.3938 | 0 | 1.3296 | 20.7766 | 0.063997 | 1.3296 | 20.7766 | 0.063997 | 1.4007 | 21.8868 | 0.063997 | 0.02188%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 27 | 1 | 4750.1268 | 98% | 1.916% | 0.08125% | 1.7242 | 0 | 0 | 1.7242 | 0 | 1.6447 | 10.3883 | 0.15833 | 1.6447 | 10.3883 | 0.15833 | 1.7326 | 10.9434 | 0.15833 | 0.0363%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 31 | 1 | 852.9261 | 84.92% | 14.72% | 0.3553% | 0.23366 | 0 | 0 | 0.23366 | 0 | 0.2229 | 10.3883 | 0.021456 | 0.2229 | 10.3883 | 0.021456 | 0.2348 | 10.9434 | 0.021456 | 0.0274%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 22 | 1 | 526.1263 | 57.95% | 41.57% | 0.4783% | 0.13859 | 0 | 0 | 0.13859 | 0 | 0.13221 | 10.3883 | 0.012727 | 0.13221 | 10.3883 | 0.012727 | 0.13927 | 10.9434 | 0.012727 | 0.02634%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 161 | 4 | 11572.221 | 88.48% | 11.4% | 0.1243% | 2.5438 | 0 | 0 | 2.5438 | 0 | 2.4266 | 41.5533 | 0.058397 | 2.4266 | 41.5533 | 0.058397 | 2.5562 | 43.7735 | 0.058397 | 0.02198%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 16 | 3 | 141.3846 | 51% | 48.51% | 0.49% | 0.1352 | 0 | 0 | 0.1352 | 0 | 0.12897 | 31.165 | 0.0041384 | 0.12897 | 31.165 | 0.0041384 | 0.13586 | 32.8301 | 0.0041384 | 0.09563%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 13 | 1 | 333.8465 | 96.62% | 2.31% | 1.072% | 0.24812 | 0 | 0 | 0.24812 | 0 | 0.23669 | 10.3883 | 0.022784 | 0.23669 | 10.3883 | 0.022784 | 0.24933 | 10.9434 | 0.022784 | 0.07432%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 102 | 1 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 0.32689 | 0 | 0 | 0.32689 | 0 | 0.31183 | 10.3883 | 0.030017 | 0.31183 | 10.3883 | 0.030017 | 0.32849 | 10.9434 | 0.030017 | 0.009575%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 85 | 1 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 1.0761 | 0 | 0 | 1.0761 | 0 | 1.0265 | 10.3883 | 0.098815 | 1.0265 | 10.3883 | 0.098815 | 1.0814 | 10.9434 | 0.098815 | 0.01117%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 76 | 1 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 0.91689 | 0 | 0 | 0.91689 | 0 | 0.87465 | 10.3883 | 0.084195 | 0.87465 | 10.3883 | 0.084195 | 0.92138 | 10.9434 | 0.084195 | 0.01265%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 116 | 3 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 2.6281 | 0 | 0 | 2.6281 | 0 | 2.507 | 31.165 | 0.080443 | 2.507 | 31.165 | 0.080443 | 2.641 | 32.8301 | 0.080443 | 0.02475%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 65 | 1 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 0.23029 | 0 | 0 | 0.23029 | 0 | 0.21968 | 10.3883 | 0.021147 | 0.21968 | 10.3883 | 0.021147 | 0.23142 | 10.9434 | 0.021147 | 0.01303%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 9 | 1 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 1.4606 | 0 | 0 | 1.4606 | 0 | 1.3933 | 10.3883 | 0.13412 | 1.3933 | 10.3883 | 0.13412 | 1.4677 | 10.9434 | 0.13412 | 0.108%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 85 | 2 | 2119.752 | 55.7% | 43.96% | 0.3458% | 0.2778 | 0 | 0 | 0.2778 | 0 | 0.26501 | 20.7766 | 0.012755 | 0.26501 | 20.7766 | 0.012755 | 0.27916 | 21.8868 | 0.012755 | 0.01311%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 2 | 520.639 | 76.18% | 22.78% | 1.038% | 0.1619 | 0 | 0 | 0.1619 | 0 | 0.15444 | 20.7766 | 0.0074333 | 0.15444 | 20.7766 | 0.0074333 | 0.16269 | 21.8868 | 0.0074333 | 0.0311%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 224 | 9 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 3.3538 | 0 | 0 | 3.3538 | 0 | 3.1993 | 93.4949 | 0.034219 | 3.1993 | 93.4949 | 0.034219 | 3.3702 | 98.4904 | 0.034219 | 0.03684%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 147 | 8 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 3.3143 | 0 | 0 | 3.3143 | 0 | 3.1616 | 83.1066 | 0.038043 | 3.1616 | 83.1066 | 0.038043 | 3.3305 | 87.5471 | 0.038043 | 0.04925%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 34 | 1 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 1.5283 | 0 | 0 | 1.5283 | 0 | 1.4579 | 10.3883 | 0.14034 | 1.4579 | 10.3883 | 0.14034 | 1.5358 | 10.9434 | 0.14034 | 0.02905%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 45 | 4 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 1.9704 | 0 | 0 | 1.9704 | 0 | 1.8796 | 41.5533 | 0.045234 | 1.8796 | 41.5533 | 0.045234 | 1.9801 | 43.7735 | 0.045234 | 0.08493%
2026 | 461 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 1 | 2 | 101.8709 | 98.65% | 0% | 1.347% | 2.01 | 0 | 0 | 2.01 | 0 | 1.9174 | 20.7766 | 0.092285 | 1.9174 | 20.7766 | 0.092285 | 2.0198 | 21.8868 | 0.092285 | 1.973%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 20 | 1 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 0.68239 | 0 | 0 | 0.68239 | 0 | 0.65095 | 10.3883 | 0.062662 | 0.65095 | 10.3883 | 0.062662 | 0.68573 | 10.9434 | 0.062662 | 0.04951%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 20 | 3 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 7.7655 | 0 | 0 | 7.7655 | 0 | 7.4077 | 31.165 | 0.23769 | 7.4077 | 31.165 | 0.23769 | 7.8035 | 32.8301 | 0.23769 | 0.1475%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 6 | 1 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 6.7319 | 0 | 0 | 6.7319 | 0 | 6.4218 | 10.3883 | 0.61818 | 6.4218 | 10.3883 | 0.61818 | 6.7649 | 10.9434 | 0.61818 | 0.1583%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 1 | 1 | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.9397 | 10.3883 | 0.18671 | 1.9397 | 10.3883 | 0.18671 | 2.0433 | 10.9434 | 0.18671 | 0.9963%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 27 | 1 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 0.53659 | 0 | 0 | 0.53659 | 0 | 0.51187 | 10.3883 | 0.049273 | 0.51187 | 10.3883 | 0.049273 | 0.53922 | 10.9434 | 0.049273 | 0.03629%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 129 | 2 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 0.39572 | 0 | 0 | 0.39572 | 0 | 0.37749 | 20.7766 | 0.018169 | 0.37749 | 20.7766 | 0.018169 | 0.39766 | 21.8868 | 0.018169 | 0.015%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 53 | 1 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 1.2342 | 0 | 0 | 1.2342 | 0 | 1.1773 | 10.3883 | 0.11333 | 1.1773 | 10.3883 | 0.11333 | 1.2402 | 10.9434 | 0.11333 | 0.01825%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 19 | 1 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 1.0585 | 0 | 0 | 1.0585 | 0 | 1.0098 | 10.3883 | 0.097202 | 1.0098 | 10.3883 | 0.097202 | 1.0637 | 10.9434 | 0.097202 | 0.05078%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 89 | 1 | 4997.7942 | 96.49% | 3.313% | 0.193% | 0.54186 | 0 | 0 | 0.54186 | 0 | 0.5169 | 10.3883 | 0.049758 | 0.5169 | 10.3883 | 0.049758 | 0.54452 | 10.9434 | 0.049758 | 0.01084%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 74 | 3 | 2044.6463 | 97.57% | 2.13% | 0.298% | 0.80878 | 0 | 0 | 0.80878 | 0 | 0.77152 | 31.165 | 0.024756 | 0.77152 | 31.165 | 0.024756 | 0.81275 | 32.8301 | 0.024756 | 0.03956%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 49 | 1 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 2.2397 | 0 | 0 | 2.2397 | 0 | 2.1366 | 10.3883 | 0.20567 | 2.1366 | 10.3883 | 0.20567 | 2.2507 | 10.9434 | 0.20567 | 0.01973%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 87 | 3 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 2.8588 | 0 | 0 | 2.8588 | 0 | 2.7271 | 31.165 | 0.087507 | 2.7271 | 31.165 | 0.087507 | 2.8729 | 32.8301 | 0.087507 | 0.03372%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 73 | 2 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 2.3719 | 0 | 0 | 2.3719 | 0 | 2.2626 | 20.7766 | 0.1089 | 2.2626 | 20.7766 | 0.1089 | 2.3835 | 21.8868 | 0.1089 | 0.02722%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 42 | 1 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 2.8966 | 0 | 0 | 2.8966 | 0 | 2.7632 | 10.3883 | 0.26599 | 2.7632 | 10.3883 | 0.26599 | 2.9108 | 10.9434 | 0.26599 | 0.02366%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 37 | 1 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 2.4127 | 0 | 0 | 2.4127 | 0 | 2.3016 | 10.3883 | 0.22156 | 2.3016 | 10.3883 | 0.22156 | 2.4246 | 10.9434 | 0.22156 | 0.02677%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 46 | 1 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 1.1861 | 0 | 0 | 1.1861 | 0 | 1.1314 | 10.3883 | 0.10891 | 1.1314 | 10.3883 | 0.10891 | 1.1919 | 10.9434 | 0.10891 | 0.02169%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 114 | 2 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 1.981 | 0 | 0 | 1.981 | 0 | 1.8897 | 20.7766 | 0.090954 | 1.8897 | 20.7766 | 0.090954 | 1.9907 | 21.8868 | 0.090954 | 0.0175%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 89 | 3 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 4.5749 | 0 | 0 | 4.5749 | 0 | 4.3641 | 31.165 | 0.14003 | 4.3641 | 31.165 | 0.14003 | 4.5973 | 32.8301 | 0.14003 | 0.03337%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 1 | 8801.877 | 98.2% | 1.718% | 0.0819% | 1.029 | 0 | 0 | 1.029 | 0 | 0.98158 | 10.3883 | 0.094489 | 0.98158 | 10.3883 | 0.094489 | 1.034 | 10.9434 | 0.094489 | 0.01169%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 283 | 5 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 7.0645 | 0 | 0 | 7.0645 | 0 | 6.739 | 51.9416 | 0.12974 | 6.739 | 51.9416 | 0.12974 | 7.0991 | 54.7169 | 0.12974 | 0.0175%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 92 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 1.9499 | 0 | 0 | 1.9499 | 0 | 1.86 | 10.3883 | 0.17905 | 1.86 | 10.3883 | 0.17905 | 1.9594 | 10.9434 | 0.17905 | 0.01039%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 124 | 1 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 2.0635 | 0 | 0 | 2.0635 | 0 | 1.9685 | 10.3883 | 0.18949 | 1.9685 | 10.3883 | 0.18949 | 2.0737 | 10.9434 | 0.18949 | 0.008016%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 22 | 1 | 4323.2442 | 99.81% | 0% | 0.1903% | 1.9614 | 0 | 0 | 1.9614 | 0 | 1.871 | 10.3883 | 0.18011 | 1.871 | 10.3883 | 0.18011 | 1.971 | 10.9434 | 0.18011 | 0.04537%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 37 | 3 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 6.9849 | 0 | 0 | 6.9849 | 0 | 6.6631 | 31.165 | 0.2138 | 6.6631 | 31.165 | 0.2138 | 7.0191 | 32.8301 | 0.2138 | 0.07649%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 41 | 2 | 8606.9717 | 99.86% | 0% | 0.1411% | 4.1926 | 0 | 0 | 4.1926 | 0 | 3.9995 | 20.7766 | 0.1925 | 3.9995 | 20.7766 | 0.1925 | 4.2131 | 21.8868 | 0.1925 | 0.04871%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 37 | 1 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 2.2266 | 0 | 0 | 2.2266 | 0 | 2.1241 | 10.3883 | 0.20447 | 2.1241 | 10.3883 | 0.20447 | 2.2376 | 10.9434 | 0.20447 | 0.02638%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 35 | 2 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 5.1861 | 0 | 0 | 5.1861 | 0 | 4.9472 | 20.7766 | 0.23811 | 4.9472 | 20.7766 | 0.23811 | 5.2115 | 21.8868 | 0.23811 | 0.05699%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 8 | 1 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 3.4222 | 0 | 0 | 3.4222 | 0 | 3.2645 | 10.3883 | 0.31425 | 3.2645 | 10.3883 | 0.31425 | 3.4389 | 10.9434 | 0.31425 | 0.1248%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 76 | 1 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 2.0398 | 0 | 0 | 2.0398 | 0 | 1.9458 | 10.3883 | 0.18731 | 1.9458 | 10.3883 | 0.18731 | 2.0498 | 10.9434 | 0.18731 | 0.01294%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 109 | 1 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 0.49191 | 0 | 0 | 0.49191 | 0 | 0.46925 | 10.3883 | 0.045171 | 0.46925 | 10.3883 | 0.045171 | 0.49432 | 10.9434 | 0.045171 | 0.00883%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 40 | 1 | 1466.2762 | 91.81% | 7.905% | 0.289% | 0.33653 | 0 | 0 | 0.33653 | 0 | 0.32103 | 10.3883 | 0.030903 | 0.32103 | 10.3883 | 0.030903 | 0.33818 | 10.9434 | 0.030903 | 0.02295%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 146 | 3 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 8.3838 | 0 | 0 | 8.3838 | 0 | 7.9975 | 31.165 | 0.25662 | 7.9975 | 31.165 | 0.25662 | 8.4249 | 32.8301 | 0.25662 | 0.02032%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 1 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 2.3534 | 0 | 0 | 2.3534 | 0 | 2.245 | 10.3883 | 0.21611 | 2.245 | 10.3883 | 0.21611 | 2.365 | 10.9434 | 0.21611 | 0.01043%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 1 | 1 | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.4417 | 10.3883 | 0.13878 | 1.4417 | 10.3883 | 0.13878 | 1.5187 | 10.9434 | 0.13878 | 0.9858%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 126 | 2 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 8.7065 | 0 | 0 | 8.7065 | 0 | 8.3054 | 20.7766 | 0.39975 | 8.3054 | 20.7766 | 0.39975 | 8.7491 | 21.8868 | 0.39975 | 0.01576%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 99 | 1 | 32313.161 | 99.26% | 0.708% | 0.02831% | 3.2399 | 0 | 0 | 3.2399 | 0 | 3.0907 | 10.3883 | 0.29751 | 3.0907 | 10.3883 | 0.29751 | 3.2558 | 10.9434 | 0.29751 | 0.01003%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 1 | 1554.328 | 69.02% | 30.62% | 0.3611% | 3.5761 | 0 | 0 | 3.5761 | 0 | 3.4113 | 10.3883 | 0.32838 | 3.4113 | 10.3883 | 0.32838 | 3.5936 | 10.9434 | 0.32838 | 0.2301%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 189 | 7 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 10.4351 | 0 | 0 | 10.4351 | 0 | 9.9544 | 72.7182 | 0.13689 | 9.9544 | 72.7182 | 0.13689 | 10.4863 | 76.6037 | 0.13689 | 0.03663%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 28 | 2 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 5.6947 | 0 | 0 | 5.6947 | 0 | 5.4323 | 20.7766 | 0.26146 | 5.4323 | 20.7766 | 0.26146 | 5.7226 | 21.8868 | 0.26146 | 0.07105%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 45 | 1 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 3.2309 | 0 | 0 | 3.2309 | 0 | 3.082 | 10.3883 | 0.29668 | 3.082 | 10.3883 | 0.29668 | 3.2467 | 10.9434 | 0.29668 | 0.02187%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 103 | 2 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 2.1656 | 0 | 0 | 2.1656 | 0 | 2.0658 | 20.7766 | 0.09943 | 2.0658 | 20.7766 | 0.09943 | 2.1762 | 21.8868 | 0.09943 | 0.01922%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 27 | 1 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 4.2224 | 0 | 0 | 4.2224 | 0 | 4.0278 | 10.3883 | 0.38773 | 4.0278 | 10.3883 | 0.38773 | 4.2431 | 10.9434 | 0.38773 | 0.03685%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 81 | 2 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 1.951 | 0 | 0 | 1.951 | 0 | 1.8612 | 20.7766 | 0.089579 | 1.8612 | 20.7766 | 0.089579 | 1.9606 | 21.8868 | 0.089579 | 0.02433%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 106 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 2.1729 | 0 | 0 | 2.1729 | 0 | 2.0728 | 10.3883 | 0.19953 | 2.0728 | 10.3883 | 0.19953 | 2.1836 | 10.9434 | 0.19953 | 0.009282%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 54 | 1 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 4.1364 | 0 | 0 | 4.1364 | 0 | 3.9458 | 10.3883 | 0.37983 | 3.9458 | 10.3883 | 0.37983 | 4.1567 | 10.9434 | 0.37983 | 0.01805%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 2 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 3.0742 | 0 | 0 | 3.0742 | 0 | 2.9326 | 20.7766 | 0.14115 | 2.9326 | 20.7766 | 0.14115 | 3.0893 | 21.8868 | 0.14115 | 0.0336%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 50 | 2 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 2.0157 | 0 | 0 | 2.0157 | 0 | 1.9228 | 20.7766 | 0.092548 | 1.9228 | 20.7766 | 0.092548 | 2.0256 | 21.8868 | 0.092548 | 0.03893%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 82 | 3 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 2.339 | 0 | 0 | 2.339 | 0 | 2.2313 | 31.165 | 0.071595 | 2.2313 | 31.165 | 0.071595 | 2.3505 | 32.8301 | 0.071595 | 0.03586%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 104 | 3 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 0.94401 | 0 | 0 | 0.94401 | 0 | 0.90052 | 31.165 | 0.028895 | 0.90052 | 31.165 | 0.028895 | 0.94864 | 32.8301 | 0.028895 | 0.02703%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 29 | 1 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 2.4397 | 0 | 0 | 2.4397 | 0 | 2.3273 | 10.3883 | 0.22403 | 2.3273 | 10.3883 | 0.22403 | 2.4516 | 10.9434 | 0.22403 | 0.03433%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 1 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 3.6644 | 0 | 0 | 3.6644 | 0 | 3.4956 | 10.3883 | 0.33649 | 3.4956 | 10.3883 | 0.33649 | 3.6823 | 10.9434 | 0.33649 | 0.01042%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 17 | 1 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 4.0747 | 0 | 0 | 4.0747 | 0 | 3.887 | 10.3883 | 0.37417 | 3.887 | 10.3883 | 0.37417 | 4.0947 | 10.9434 | 0.37417 | 0.05775%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 43 | 1 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 4.3649 | 0 | 0 | 4.3649 | 0 | 4.1638 | 10.3883 | 0.40082 | 4.1638 | 10.3883 | 0.40082 | 4.3863 | 10.9434 | 0.40082 | 0.02319%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 11 | 1 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 4.5541 | 0 | 0 | 4.5541 | 0 | 4.3443 | 10.3883 | 0.41819 | 4.3443 | 10.3883 | 0.41819 | 4.5764 | 10.9434 | 0.41819 | 0.09046%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 33 | 2 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 5.9173 | 0 | 0 | 5.9173 | 0 | 5.6447 | 20.7766 | 0.27168 | 5.6447 | 20.7766 | 0.27168 | 5.9463 | 21.8868 | 0.27168 | 0.06038%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 80 | 2 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 2.2723 | 0 | 0 | 2.2723 | 0 | 2.1676 | 20.7766 | 0.10433 | 2.1676 | 20.7766 | 0.10433 | 2.2834 | 21.8868 | 0.10433 | 0.02399%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 19 | 1 | 585.5086 | 87.68% | 11.85% | 0.4758% | 0.27019 | 0 | 0 | 0.27019 | 0 | 0.25774 | 10.3883 | 0.024811 | 0.25774 | 10.3883 | 0.024811 | 0.27152 | 10.9434 | 0.024811 | 0.04615%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 22 | 3 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 2.9169 | 0 | 0 | 2.9169 | 0 | 2.7825 | 31.165 | 0.089284 | 2.7825 | 31.165 | 0.089284 | 2.9312 | 32.8301 | 0.089284 | 0.1356%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 1 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 0.76848 | 0 | 0 | 0.76848 | 0 | 0.73308 | 10.3883 | 0.070568 | 0.73308 | 10.3883 | 0.070568 | 0.77225 | 10.9434 | 0.070568 | 0.01161%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 124 | 3 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 6.0729 | 0 | 0 | 6.0729 | 0 | 5.7931 | 31.165 | 0.18589 | 5.7931 | 31.165 | 0.18589 | 6.1027 | 32.8301 | 0.18589 | 0.02399%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 119 | 1 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 2.3505 | 0 | 0 | 2.3505 | 0 | 2.2422 | 10.3883 | 0.21584 | 2.2422 | 10.3883 | 0.21584 | 2.362 | 10.9434 | 0.21584 | 0.008277%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 103 | 3 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 7.7102 | 0 | 0 | 7.7102 | 0 | 7.355 | 31.165 | 0.236 | 7.355 | 31.165 | 0.236 | 7.748 | 32.8301 | 0.236 | 0.02888%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 68 | 4 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 9.1476 | 0 | 0 | 9.1476 | 0 | 8.7262 | 41.5533 | 0.21 | 8.7262 | 41.5533 | 0.21 | 9.1924 | 43.7735 | 0.21 | 0.05733%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 81 | 3 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 2.1765 | 0 | 0 | 2.1765 | 0 | 2.0763 | 31.165 | 0.066622 | 2.0763 | 31.165 | 0.066622 | 2.1872 | 32.8301 | 0.066622 | 0.0369%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 63 | 2 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 1.5785 | 0 | 0 | 1.5785 | 0 | 1.5057 | 20.7766 | 0.072472 | 1.5057 | 20.7766 | 0.072472 | 1.5862 | 21.8868 | 0.072472 | 0.03163%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 93 | 2 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 0.91394 | 0 | 0 | 0.91394 | 0 | 0.87184 | 20.7766 | 0.041963 | 0.87184 | 20.7766 | 0.041963 | 0.91842 | 21.8868 | 0.041963 | 0.0196%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 9 | 1 | 240.2897 | 88.19% | 10.99% | 0.8202% | 0.23545 | 0 | 0 | 0.23545 | 0 | 0.2246 | 10.3883 | 0.021621 | 0.2246 | 10.3883 | 0.021621 | 0.2366 | 10.9434 | 0.021621 | 0.09799%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 16 | 1 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 6.3033 | 0 | 0 | 6.3033 | 0 | 6.0129 | 10.3883 | 0.57881 | 6.0129 | 10.3883 | 0.57881 | 6.3342 | 10.9434 | 0.57881 | 0.06236%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 73 | 4 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 5.6042 | 0 | 0 | 5.6042 | 0 | 5.3461 | 41.5533 | 0.12866 | 5.3461 | 41.5533 | 0.12866 | 5.6317 | 43.7735 | 0.12866 | 0.05429%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 43 | 2 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 2.7986 | 0 | 0 | 2.7986 | 0 | 2.6697 | 20.7766 | 0.1285 | 2.6697 | 20.7766 | 0.1285 | 2.8124 | 21.8868 | 0.1285 | 0.04553%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 64 | 2 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 2.6219 | 0 | 0 | 2.6219 | 0 | 2.5011 | 20.7766 | 0.12038 | 2.5011 | 20.7766 | 0.12038 | 2.6347 | 21.8868 | 0.12038 | 0.03015%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 39 | 1 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 0.74901 | 0 | 0 | 0.74901 | 0 | 0.7145 | 10.3883 | 0.068779 | 0.7145 | 10.3883 | 0.068779 | 0.75268 | 10.9434 | 0.068779 | 0.0251%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 12 | 1 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 1.1429 | 0 | 0 | 1.1429 | 0 | 1.0902 | 10.3883 | 0.10495 | 1.0902 | 10.3883 | 0.10495 | 1.1485 | 10.9434 | 0.10495 | 0.08243%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 79 | 3 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 2.0202 | 0 | 0 | 2.0202 | 0 | 1.9271 | 31.165 | 0.061836 | 1.9271 | 31.165 | 0.061836 | 2.0301 | 32.8301 | 0.061836 | 0.03201%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 92 | 2 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 1.4316 | 0 | 0 | 1.4316 | 0 | 1.3656 | 20.7766 | 0.065729 | 1.3656 | 20.7766 | 0.065729 | 1.4386 | 21.8868 | 0.065729 | 0.02154%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 14 | 2 | 456.1931 | 99.77% | 0% | 0.2285% | 0.65022 | 0 | 0 | 0.65022 | 0 | 0.62026 | 20.7766 | 0.029854 | 0.62026 | 20.7766 | 0.029854 | 0.6534 | 21.8868 | 0.029854 | 0.1425%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 13 | 1 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 2.7823 | 0 | 0 | 2.7823 | 0 | 2.6541 | 10.3883 | 0.25549 | 2.6541 | 10.3883 | 0.25549 | 2.7959 | 10.9434 | 0.25549 | 0.0755%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 16 | 1 | 427.4478 | 90.46% | 9.431% | 0.1062% | 0.24168 | 0 | 0 | 0.24168 | 0 | 0.23054 | 10.3883 | 0.022192 | 0.23054 | 10.3883 | 0.022192 | 0.24286 | 10.9434 | 0.022192 | 0.05654%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 51 | 1 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 3.1063 | 0 | 0 | 3.1063 | 0 | 2.9632 | 10.3883 | 0.28525 | 2.9632 | 10.3883 | 0.28525 | 3.1216 | 10.9434 | 0.28525 | 0.01943%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 127 | 4 | 37077.302 | 99.36% | 0.615% | 0.02874% | 11.6027 | 0 | 0 | 11.6027 | 0 | 11.0682 | 41.5533 | 0.26636 | 11.0682 | 41.5533 | 0.26636 | 11.6596 | 43.7735 | 0.26636 | 0.03129%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 1 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 0.30727 | 0 | 0 | 0.30727 | 0 | 0.29311 | 10.3883 | 0.028216 | 0.29311 | 10.3883 | 0.028216 | 0.30878 | 10.9434 | 0.028216 | 0.01489%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 90 | 2 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 0.78658 | 0 | 0 | 0.78658 | 0 | 0.75035 | 20.7766 | 0.036115 | 0.75035 | 20.7766 | 0.036115 | 0.79044 | 21.8868 | 0.036115 | 0.02115%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 32 | 1 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 1.5768 | 0 | 0 | 1.5768 | 0 | 1.5042 | 10.3883 | 0.14479 | 1.5042 | 10.3883 | 0.14479 | 1.5845 | 10.9434 | 0.14479 | 0.0308%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 109 | 1 | 6915.6819 | 99% | 0.9206% | 0.07911% | 0.62812 | 0 | 0 | 0.62812 | 0 | 0.59919 | 10.3883 | 0.057679 | 0.59919 | 10.3883 | 0.057679 | 0.6312 | 10.9434 | 0.057679 | 0.009083%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 66 | 3 | 3027.5479 | 94.73% | 5.109% | 0.164% | 1.3036 | 0 | 0 | 1.3036 | 0 | 1.2435 | 31.165 | 0.039902 | 1.2435 | 31.165 | 0.039902 | 1.31 | 32.8301 | 0.039902 | 0.04306%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 30 | 2 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 6.1843 | 0 | 0 | 6.1843 | 0 | 5.8994 | 20.7766 | 0.28394 | 5.8994 | 20.7766 | 0.28394 | 6.2146 | 21.8868 | 0.28394 | 0.06622%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 17 | 1 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 3.0184 | 0 | 0 | 3.0184 | 0 | 2.8793 | 10.3883 | 0.27717 | 2.8793 | 10.3883 | 0.27717 | 3.0332 | 10.9434 | 0.27717 | 0.05771%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 1 | 6920.124 | 97.57% | 2.306% | 0.1195% | 0.79438 | 0 | 0 | 0.79438 | 0 | 0.75779 | 10.3883 | 0.072946 | 0.75779 | 10.3883 | 0.072946 | 0.79828 | 10.9434 | 0.072946 | 0.01148%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 27 | 3 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 6.562 | 0 | 0 | 6.562 | 0 | 6.2597 | 31.165 | 0.20086 | 6.2597 | 31.165 | 0.20086 | 6.5942 | 32.8301 | 0.20086 | 0.1104%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 19 | 1 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 1.9514 | 0 | 0 | 1.9514 | 0 | 1.8615 | 10.3883 | 0.17919 | 1.8615 | 10.3883 | 0.17919 | 1.9609 | 10.9434 | 0.17919 | 0.05218%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 128 | 1 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 0.24611 | 0 | 0 | 0.24611 | 0 | 0.23478 | 10.3883 | 0.0226 | 0.23478 | 10.3883 | 0.0226 | 0.24732 | 10.9434 | 0.0226 | 0.007321%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 20 | 1 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 1.8816 | 0 | 0 | 1.8816 | 0 | 1.7949 | 10.3883 | 0.17278 | 1.7949 | 10.3883 | 0.17278 | 1.8908 | 10.9434 | 0.17278 | 0.04974%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 112 | 2 | 2610.8 | 93.6% | 6.065% | 0.3401% | 0.43635 | 0 | 0 | 0.43635 | 0 | 0.39708 | 19.8195 | 0.020035 | 0.39708 | 19.8195 | 0.020035 | 0.44064 | 21.9941 | 0.020035 | 0.01671%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 188 | 2 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 0.41714 | 0 | 0 | 0.41714 | 0 | 0.37959 | 19.8195 | 0.019152 | 0.37959 | 19.8195 | 0.019152 | 0.42124 | 21.9941 | 0.019152 | 0.009979%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 78 | 1 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 0.19365 | 0 | 0 | 0.19365 | 0 | 0.17622 | 9.9098 | 0.017783 | 0.17622 | 9.9098 | 0.017783 | 0.19556 | 10.997 | 0.017783 | 0.0119%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 84 | 3 | 6201.607 | 97.29% | 2.601% | 0.1104% | 2.1548 | 0 | 0 | 2.1548 | 0 | 1.9608 | 29.7293 | 0.065957 | 1.9608 | 29.7293 | 0.065957 | 2.176 | 32.9911 | 0.065957 | 0.03475%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 90 | 3 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 5.0388 | 0 | 0 | 5.0388 | 0 | 4.5853 | 29.7293 | 0.15423 | 4.5853 | 29.7293 | 0.15423 | 5.0883 | 32.9911 | 0.15423 | 0.03285%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 93 | 2 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 2.2392 | 0 | 0 | 2.2392 | 0 | 2.0377 | 19.8195 | 0.10281 | 2.0377 | 19.8195 | 0.10281 | 2.2612 | 21.9941 | 0.10281 | 0.02114%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 1 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 1.0883 | 0 | 0 | 1.0883 | 0 | 0.99037 | 9.9098 | 0.099939 | 0.99037 | 9.9098 | 0.099939 | 1.099 | 10.997 | 0.099939 | 0.01172%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 32 | 1 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 0.97758 | 0 | 0 | 0.97758 | 0 | 0.88959 | 9.9098 | 0.089769 | 0.88959 | 9.9098 | 0.089769 | 0.98719 | 10.997 | 0.089769 | 0.03118%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 4 | 1 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 4.8371 | 0 | 0 | 4.8371 | 0 | 4.4017 | 9.9098 | 0.44418 | 4.4017 | 9.9098 | 0.44418 | 4.8846 | 10.997 | 0.44418 | 0.2496%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 60 | 2 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 4.7724 | 0 | 0 | 4.7724 | 0 | 4.3428 | 19.8195 | 0.21912 | 4.3428 | 19.8195 | 0.21912 | 4.8193 | 21.9941 | 0.21912 | 0.03285%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 77 | 3 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 0.44405 | 0 | 0 | 0.44405 | 0 | 0.40408 | 29.7293 | 0.013592 | 0.40408 | 29.7293 | 0.013592 | 0.44841 | 32.9911 | 0.013592 | 0.02763%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 28 | 2 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 6.8197 | 0 | 0 | 6.8197 | 0 | 6.2059 | 19.8195 | 0.31312 | 6.2059 | 19.8195 | 0.31312 | 6.8868 | 21.9941 | 0.31312 | 0.0702%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 50 | 1 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 1.0665 | 0 | 0 | 1.0665 | 0 | 0.97051 | 9.9098 | 0.097935 | 0.97051 | 9.9098 | 0.097935 | 1.077 | 10.997 | 0.097935 | 0.01926%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 107 | 1 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 1.7051 | 0 | 0 | 1.7051 | 0 | 1.5516 | 9.9098 | 0.15657 | 1.5516 | 9.9098 | 0.15657 | 1.7218 | 10.997 | 0.15657 | 0.009079%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 56 | 2 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 7.0802 | 0 | 0 | 7.0802 | 0 | 6.4429 | 19.8195 | 0.32508 | 6.4429 | 19.8195 | 0.32508 | 7.1498 | 21.9941 | 0.32508 | 0.03544%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 20 | 1 | 418.5676 | 87.71% | 11.66% | 0.6303% | 0.18355 | 0 | 0 | 0.18355 | 0 | 0.16703 | 9.9098 | 0.016855 | 0.16703 | 9.9098 | 0.016855 | 0.18536 | 10.997 | 0.016855 | 0.04385%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 177 | 6 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 1.7261 | 0 | 0 | 1.7261 | 0 | 1.5707 | 59.4585 | 0.026417 | 1.5707 | 59.4585 | 0.026417 | 1.743 | 65.9822 | 0.026417 | 0.03134%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 10 | 1 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 3.0242 | 0 | 0 | 3.0242 | 0 | 2.752 | 9.9098 | 0.27771 | 2.752 | 9.9098 | 0.27771 | 3.0539 | 10.997 | 0.27771 | 0.09907%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 80 | 1 | 3160.5079 | 95.27% | 4.501% | 0.231% | 0.37637 | 0 | 0 | 0.37637 | 0 | 0.34249 | 9.9098 | 0.034561 | 0.34249 | 9.9098 | 0.034561 | 0.38007 | 10.997 | 0.034561 | 0.01191%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 151 | 5 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 0.55652 | 0 | 0 | 0.55652 | 0 | 0.50643 | 49.5488 | 0.010221 | 0.50643 | 49.5488 | 0.010221 | 0.56199 | 54.9851 | 0.010221 | 0.027%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 3 | 1867.403 | 95.01% | 4.712% | 0.2778% | 1.0043 | 0 | 0 | 1.0043 | 0 | 0.91388 | 29.7293 | 0.03074 | 0.91388 | 29.7293 | 0.03074 | 1.0142 | 32.9911 | 0.03074 | 0.05378%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 205 | 7 | 18749.5963 | 97% | 2.901% | 0.09453% | 6.2105 | 0 | 0 | 6.2105 | 0 | 5.6515 | 69.3683 | 0.081471 | 5.6515 | 69.3683 | 0.081471 | 6.2716 | 76.9792 | 0.081471 | 0.03312%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 2 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 1.3577 | 0 | 0 | 1.3577 | 0 | 1.2355 | 19.8195 | 0.062338 | 1.2355 | 19.8195 | 0.062338 | 1.3711 | 21.9941 | 0.062338 | 0.03096%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 113 | 2 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 0.9843 | 0 | 0 | 0.9843 | 0 | 0.8957 | 19.8195 | 0.045193 | 0.8957 | 19.8195 | 0.045193 | 0.99397 | 21.9941 | 0.045193 | 0.01714%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 2 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 3.6714 | 0 | 0 | 3.6714 | 0 | 3.341 | 19.8195 | 0.16857 | 3.341 | 19.8195 | 0.16857 | 3.7075 | 21.9941 | 0.16857 | 0.03186%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 32 | 1 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 3.0561 | 0 | 0 | 3.0561 | 0 | 2.781 | 9.9098 | 0.28063 | 2.781 | 9.9098 | 0.28063 | 3.0861 | 10.997 | 0.28063 | 0.03035%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 51 | 1 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 0.65179 | 0 | 0 | 0.65179 | 0 | 0.59312 | 9.9098 | 0.059853 | 0.59312 | 9.9098 | 0.059853 | 0.6582 | 10.997 | 0.059853 | 0.01916%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 115 | 3 | 13172.958 | 96.8% | 3.124% | 0.0728% | 3.3266 | 0 | 0 | 3.3266 | 0 | 3.0271 | 29.7293 | 0.10182 | 3.0271 | 29.7293 | 0.10182 | 3.3593 | 32.9911 | 0.10182 | 0.02525%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 1 | 1635.841 | 89.24% | 10.7% | 0.05535% | 2.9198 | 0 | 0 | 2.9198 | 0 | 2.657 | 9.9098 | 0.26812 | 2.657 | 9.9098 | 0.26812 | 2.9485 | 10.997 | 0.26812 | 0.1785%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 40 | 2 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 5.6184 | 0 | 0 | 5.6184 | 0 | 5.1127 | 19.8195 | 0.25796 | 5.1127 | 19.8195 | 0.25796 | 5.6736 | 21.9941 | 0.25796 | 0.04715%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 51 | 1 | 8462.8018 | 99.74% | 0% | 0.2593% | 1.6551 | 0 | 0 | 1.6551 | 0 | 1.5061 | 9.9098 | 0.15198 | 1.5061 | 9.9098 | 0.15198 | 1.6713 | 10.997 | 0.15198 | 0.01956%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 19 | 1 | 498.1496 | 90.1% | 9.186% | 0.7154% | 0.23622 | 0 | 0 | 0.23622 | 0 | 0.21496 | 9.9098 | 0.021692 | 0.21496 | 9.9098 | 0.021692 | 0.23855 | 10.997 | 0.021692 | 0.04742%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 18 | 1 | 170.5929 | 70.47% | 28.1% | 1.432% | 0.066789 | 0 | 0 | 0.066789 | 0 | 0.060777 | 9.9098 | 0.0061331 | 0.060777 | 9.9098 | 0.0061331 | 0.067446 | 10.997 | 0.0061331 | 0.03915%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 38 | 1 | 317.7725 | 50.82% | 48.53% | 0.6462% | 0.042501 | 0 | 0 | 0.042501 | 0 | 0.038676 | 9.9098 | 0.0039028 | 0.038676 | 9.9098 | 0.0039028 | 0.042919 | 10.997 | 0.0039028 | 0.01337%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 65 | 1 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 0.16516 | 0 | 0 | 0.16516 | 0 | 0.15029 | 9.9098 | 0.015166 | 0.15029 | 9.9098 | 0.015166 | 0.16678 | 10.997 | 0.015166 | 0.01377%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 145 | 3 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 0.31547 | 0 | 0 | 0.31547 | 0 | 0.28708 | 29.7293 | 0.0096564 | 0.28708 | 29.7293 | 0.0096564 | 0.31857 | 32.9911 | 0.0096564 | 0.01743%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 1 | 1890.633 | 91.06% | 8.49% | 0.4466% | 0.26086 | 0 | 0 | 0.26086 | 0 | 0.23738 | 9.9098 | 0.023954 | 0.23738 | 9.9098 | 0.023954 | 0.26342 | 10.997 | 0.023954 | 0.0138%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 79 | 1 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 0.21005 | 0 | 0 | 0.21005 | 0 | 0.19114 | 9.9098 | 0.019288 | 0.19114 | 9.9098 | 0.019288 | 0.21211 | 10.997 | 0.019288 | 0.01208%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 2 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 0.42612 | 0 | 0 | 0.42612 | 0 | 0.38777 | 19.8195 | 0.019565 | 0.38777 | 19.8195 | 0.019565 | 0.43031 | 21.9941 | 0.019565 | 0.02714%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 46 | 2 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 2.1071 | 0 | 0 | 2.1071 | 0 | 1.9174 | 19.8195 | 0.096745 | 1.9174 | 19.8195 | 0.096745 | 2.1278 | 21.9941 | 0.096745 | 0.04311%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 42 | 1 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 0.29514 | 0 | 0 | 0.29514 | 0 | 0.26858 | 9.9098 | 0.027102 | 0.26858 | 9.9098 | 0.027102 | 0.29805 | 10.997 | 0.027102 | 0.02331%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 68 | 3 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 0.63619 | 0 | 0 | 0.63619 | 0 | 0.57892 | 29.7293 | 0.019473 | 0.57892 | 29.7293 | 0.019473 | 0.64244 | 32.9911 | 0.019473 | 0.04291%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 103 | 4 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 1.026 | 0 | 0 | 1.026 | 0 | 0.93369 | 39.639 | 0.023555 | 0.93369 | 39.639 | 0.023555 | 1.0361 | 43.9881 | 0.023555 | 0.03719%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 39 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 0.25869 | 0 | 0 | 0.25869 | 0 | 0.2354 | 9.9098 | 0.023755 | 0.2354 | 9.9098 | 0.023755 | 0.26123 | 10.997 | 0.023755 | 0.0249%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 45 | 1 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 0.31977 | 0 | 0 | 0.31977 | 0 | 0.29099 | 9.9098 | 0.029364 | 0.29099 | 9.9098 | 0.029364 | 0.32291 | 10.997 | 0.029364 | 0.02174%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 127 | 5 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 10.2337 | 0 | 0 | 10.2337 | 0 | 9.3125 | 49.5488 | 0.18795 | 9.3125 | 49.5488 | 0.18795 | 10.3343 | 54.9851 | 0.18795 | 0.03894%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 75 | 1 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 0.88365 | 0 | 0 | 0.88365 | 0 | 0.80411 | 9.9098 | 0.081143 | 0.80411 | 9.9098 | 0.081143 | 0.89233 | 10.997 | 0.081143 | 0.01325%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 22 | 2 | 400.1895 | 97.86% | 1.359% | 0.7809% | 0.35602 | 0 | 0 | 0.35602 | 0 | 0.32398 | 19.8195 | 0.016346 | 0.32398 | 19.8195 | 0.016346 | 0.35952 | 21.9941 | 0.016346 | 0.08896%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 9 | 1 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 0.56304 | 0 | 0 | 0.56304 | 0 | 0.51236 | 9.9098 | 0.051702 | 0.51236 | 9.9098 | 0.051702 | 0.56857 | 10.997 | 0.051702 | 0.1097%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 73 | 3 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 9.1172 | 0 | 0 | 9.1172 | 0 | 8.2965 | 29.7293 | 0.27907 | 8.2965 | 29.7293 | 0.27907 | 9.2068 | 32.9911 | 0.27907 | 0.04078%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 72 | 2 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 3.4654 | 0 | 0 | 3.4654 | 0 | 3.1535 | 19.8195 | 0.15911 | 3.1535 | 19.8195 | 0.15911 | 3.4995 | 21.9941 | 0.15911 | 0.02728%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 26 | 1 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 2.0677 | 0 | 0 | 2.0677 | 0 | 1.8816 | 9.9098 | 0.18987 | 1.8816 | 9.9098 | 0.18987 | 2.088 | 10.997 | 0.18987 | 0.03804%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 67 | 1 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 2.0786 | 0 | 0 | 2.0786 | 0 | 1.8915 | 9.9098 | 0.19088 | 1.8915 | 9.9098 | 0.19088 | 2.0991 | 10.997 | 0.19088 | 0.0148%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 126 | 1 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 0.14259 | 0 | 0 | 0.14259 | 0 | 0.12975 | 9.9098 | 0.013094 | 0.12975 | 9.9098 | 0.013094 | 0.14399 | 10.997 | 0.013094 | 0.007081%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 84 | 1 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 0.28526 | 0 | 0 | 0.28526 | 0 | 0.25958 | 9.9098 | 0.026195 | 0.25958 | 9.9098 | 0.026195 | 0.28806 | 10.997 | 0.026195 | 0.01046%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 71 | 1 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 1.4854 | 0 | 0 | 1.4854 | 0 | 1.3517 | 9.9098 | 0.1364 | 1.3517 | 9.9098 | 0.1364 | 1.5 | 10.997 | 0.1364 | 0.0139%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 68 | 2 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 1.0182 | 0 | 0 | 1.0182 | 0 | 0.92654 | 19.8195 | 0.046749 | 0.92654 | 19.8195 | 0.046749 | 1.0282 | 21.9941 | 0.046749 | 0.02784%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 1 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 0.18677 | 0 | 0 | 0.18677 | 0 | 0.16996 | 9.9098 | 0.017151 | 0.16996 | 9.9098 | 0.017151 | 0.18861 | 10.997 | 0.017151 | 0.01298%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 48 | 2 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 4.1753 | 0 | 0 | 4.1753 | 0 | 3.7995 | 19.8195 | 0.1917 | 3.7995 | 19.8195 | 0.1917 | 4.2164 | 21.9941 | 0.1917 | 0.04127%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 29 | 1 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 0.73039 | 0 | 0 | 0.73039 | 0 | 0.66465 | 9.9098 | 0.06707 | 0.66465 | 9.9098 | 0.06707 | 0.73757 | 10.997 | 0.06707 | 0.03322%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 81 | 4 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 0.80165 | 0 | 0 | 0.80165 | 0 | 0.72949 | 39.639 | 0.018403 | 0.72949 | 39.639 | 0.018403 | 0.80953 | 43.9881 | 0.018403 | 0.04163%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 155 | 3 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 0.62022 | 0 | 0 | 0.62022 | 0 | 0.56439 | 29.7293 | 0.018984 | 0.56439 | 29.7293 | 0.018984 | 0.62632 | 32.9911 | 0.018984 | 0.0173%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 2.1692 | 0 | 0 | 2.1692 | 0 | 1.9739 | 9.9098 | 0.19919 | 1.9739 | 9.9098 | 0.19919 | 2.1905 | 10.997 | 0.19919 | 0.05877%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 77 | 2 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 0.78284 | 0 | 0 | 0.78284 | 0 | 0.71237 | 19.8195 | 0.035943 | 0.71237 | 19.8195 | 0.035943 | 0.79053 | 21.9941 | 0.035943 | 0.02394%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 93 | 2 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 0.56547 | 0 | 0 | 0.56547 | 0 | 0.51457 | 19.8195 | 0.025963 | 0.51457 | 19.8195 | 0.025963 | 0.57103 | 21.9941 | 0.025963 | 0.02067%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 72 | 2 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 1.0605 | 0 | 0 | 1.0605 | 0 | 0.96503 | 19.8195 | 0.048691 | 0.96503 | 19.8195 | 0.048691 | 1.0709 | 21.9941 | 0.048691 | 0.02695%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 137 | 4 | 7406.689 | 96.62% | 3.25% | 0.1263% | 2.0895 | 0 | 0 | 2.0895 | 0 | 1.9014 | 39.639 | 0.047969 | 1.9014 | 39.639 | 0.047969 | 2.1101 | 43.9881 | 0.047969 | 0.02821%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 212 | 2 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 7.4153 | 0 | 0 | 7.4153 | 0 | 6.7478 | 19.8195 | 0.34046 | 6.7478 | 19.8195 | 0.34046 | 7.4882 | 21.9941 | 0.34046 | 0.009363%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 81 | 4 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 22.1923 | 0 | 0 | 22.1923 | 0 | 20.1947 | 39.639 | 0.50947 | 20.1947 | 39.639 | 0.50947 | 22.4104 | 43.9881 | 0.50947 | 0.0492%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 132 | 2 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 1.0808 | 0 | 0 | 1.0808 | 0 | 0.98355 | 19.8195 | 0.049625 | 0.98355 | 19.8195 | 0.049625 | 1.0915 | 21.9941 | 0.049625 | 0.01455%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 1220 | 8 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 1.0635 | 0 | 0 | 1.0635 | 0 | 0.96775 | 79.278 | 0.012207 | 0.96775 | 79.278 | 0.012207 | 1.0739 | 87.9762 | 0.012207 | 0.006341%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 52 | 3 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 1.0962 | 0 | 0 | 1.0962 | 0 | 0.99755 | 29.7293 | 0.033554 | 0.99755 | 29.7293 | 0.033554 | 1.107 | 32.9911 | 0.033554 | 0.0548%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 1 | 2730.9177 | 98.3% | 1.373% | 0.325% | 1.1186 | 0 | 0 | 1.1186 | 0 | 1.0179 | 9.9098 | 0.10271 | 1.0179 | 9.9098 | 0.10271 | 1.1296 | 10.997 | 0.10271 | 0.04096%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 151 | 6 | 5142.095 | 98.68% | 0.901% | 0.4182% | 2.0163 | 0 | 0 | 2.0163 | 0 | 1.8348 | 59.4585 | 0.030858 | 1.8348 | 59.4585 | 0.030858 | 2.0361 | 65.9822 | 0.030858 | 0.03921%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 50 | 2 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 0.99285 | 0 | 0 | 0.99285 | 0 | 0.90348 | 19.8195 | 0.045585 | 0.90348 | 19.8195 | 0.045585 | 1.0026 | 21.9941 | 0.045585 | 0.03971%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 32 | 1 | 447.7794 | 94.96% | 4.349% | 0.694% | 0.13287 | 0 | 0 | 0.13287 | 0 | 0.12091 | 9.9098 | 0.012202 | 0.12091 | 9.9098 | 0.012202 | 0.13418 | 10.997 | 0.012202 | 0.02967%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 79 | 2 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 0.50925 | 0 | 0 | 0.50925 | 0 | 0.46341 | 19.8195 | 0.023382 | 0.46341 | 19.8195 | 0.023382 | 0.51426 | 21.9941 | 0.023382 | 0.02175%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 4 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 1.5983 | 0 | 0 | 1.5983 | 0 | 1.4544 | 39.639 | 0.036691 | 1.4544 | 39.639 | 0.036691 | 1.614 | 43.9881 | 0.036691 | 0.03872%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 40 | 1 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 1.2281 | 0 | 0 | 1.2281 | 0 | 1.1176 | 9.9098 | 0.11278 | 1.1176 | 9.9098 | 0.11278 | 1.2402 | 10.997 | 0.11278 | 0.02486%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 48 | 1 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 4.8525 | 0 | 0 | 4.8525 | 0 | 4.4157 | 9.9098 | 0.44559 | 4.4157 | 9.9098 | 0.44559 | 4.9002 | 10.997 | 0.44559 | 0.02049%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 48 | 1 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 1.9991 | 0 | 0 | 1.9991 | 0 | 1.8192 | 9.9098 | 0.18358 | 1.8192 | 9.9098 | 0.18358 | 2.0188 | 10.997 | 0.18358 | 0.02057%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 51 | 1 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 1.0254 | 0 | 0 | 1.0254 | 0 | 0.93306 | 9.9098 | 0.094156 | 0.93306 | 9.9098 | 0.094156 | 1.0354 | 10.997 | 0.094156 | 0.01923%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 124 | 1 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1.6835 | 0 | 0 | 1.6835 | 0 | 1.532 | 9.9098 | 0.15459 | 1.532 | 9.9098 | 0.15459 | 1.7001 | 10.997 | 0.15459 | 0.007933%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 56 | 1 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 1.2104 | 0 | 0 | 1.2104 | 0 | 1.1015 | 9.9098 | 0.11115 | 1.1015 | 9.9098 | 0.11115 | 1.2223 | 10.997 | 0.11115 | 0.01747%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 71 | 1 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 3.7719 | 0 | 0 | 3.7719 | 0 | 3.4324 | 9.9098 | 0.34637 | 3.4324 | 9.9098 | 0.34637 | 3.809 | 10.997 | 0.34637 | 0.01393%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 165 | 4 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 7.423 | 0 | 0 | 7.423 | 0 | 6.7548 | 39.639 | 0.17041 | 6.7548 | 39.639 | 0.17041 | 7.4959 | 43.9881 | 0.17041 | 0.02403%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 182 | 9 | 65515.492 | 98.93% | 1.038% | 0.03019% | 32.0517 | 0 | 0 | 32.0517 | 0 | 29.1666 | 89.1878 | 0.32702 | 29.1666 | 89.1878 | 0.32702 | 32.3667 | 98.9732 | 0.32702 | 0.04892%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 19 | 2 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 1.6464 | 0 | 0 | 1.6464 | 0 | 1.4982 | 19.8195 | 0.075593 | 1.4982 | 19.8195 | 0.075593 | 1.6626 | 21.9941 | 0.075593 | 0.1039%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 1 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 0.46823 | 0 | 0 | 0.46823 | 0 | 0.42608 | 9.9098 | 0.042996 | 0.42608 | 9.9098 | 0.042996 | 0.47283 | 10.997 | 0.042996 | 0.04194%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 72 | 3 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 2.566 | 0 | 0 | 2.566 | 0 | 2.335 | 29.7293 | 0.078542 | 2.335 | 29.7293 | 0.078542 | 2.5912 | 32.9911 | 0.078542 | 0.04093%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 17 | 1 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 0.41953 | 0 | 0 | 0.41953 | 0 | 0.38177 | 9.9098 | 0.038524 | 0.38177 | 9.9098 | 0.038524 | 0.42365 | 10.997 | 0.038524 | 0.04075%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 73 | 2 | 4437.6588 | 97.91% | 1.769% | 0.321% | 1.1904 | 0 | 0 | 1.1904 | 0 | 1.0832 | 19.8195 | 0.054655 | 1.0832 | 19.8195 | 0.054655 | 1.2021 | 21.9941 | 0.054655 | 0.02682%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 50 | 1 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 0.74152 | 0 | 0 | 0.74152 | 0 | 0.67477 | 9.9098 | 0.068092 | 0.67477 | 9.9098 | 0.068092 | 0.74881 | 10.997 | 0.068092 | 0.01981%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 104 | 5 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 1.7063 | 0 | 0 | 1.7063 | 0 | 1.5527 | 49.5488 | 0.031337 | 1.5527 | 49.5488 | 0.031337 | 1.723 | 54.9851 | 0.031337 | 0.04655%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 71 | 3 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 1.3531 | 0 | 0 | 1.3531 | 0 | 1.2313 | 29.7293 | 0.041416 | 1.2313 | 29.7293 | 0.041416 | 1.3664 | 32.9911 | 0.041416 | 0.03995%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 2 | 1438.4419 | 90% | 9.47% | 0.5268% | 1.0789 | 0 | 0 | 1.0789 | 0 | 0.98176 | 19.8195 | 0.049535 | 0.98176 | 19.8195 | 0.049535 | 1.0895 | 21.9941 | 0.049535 | 0.075%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 99 | 5 | 3753.23 | 95.85% | 3.876% | 0.273% | 1.8169 | 0 | 0 | 1.8169 | 0 | 1.6534 | 49.5488 | 0.033369 | 1.6534 | 49.5488 | 0.033369 | 1.8348 | 54.9851 | 0.033369 | 0.04841%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 24 | 4 | 826.9208 | 97.04% | 2.672% | 0.2884% | 1.3374 | 0 | 0 | 1.3374 | 0 | 1.217 | 39.639 | 0.030702 | 1.217 | 39.639 | 0.030702 | 1.3505 | 43.9881 | 0.030702 | 0.1617%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 40 | 1 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 0.44199 | 0 | 0 | 0.44199 | 0 | 0.4022 | 9.9098 | 0.040587 | 0.4022 | 9.9098 | 0.040587 | 0.44633 | 10.997 | 0.040587 | 0.02195%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 7 | 1 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 3.1318 | 0 | 0 | 3.1318 | 0 | 2.8499 | 9.9098 | 0.28759 | 2.8499 | 9.9098 | 0.28759 | 3.1626 | 10.997 | 0.28759 | 0.1301%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 2 | 1 | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.19562 | 0 | 0 | 0.19562 | 0 | 0.17801 | 9.9098 | 0.017963 | 0.17801 | 9.9098 | 0.017963 | 0.19754 | 10.997 | 0.017963 | 0.4235%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 4 | 1 | 278.652 | 16.28% | 83.57% | 0.1501% | 0.11341 | 0 | 0 | 0.11341 | 0 | 0.1032 | 9.9098 | 0.010414 | 0.1032 | 9.9098 | 0.010414 | 0.11452 | 10.997 | 0.010414 | 0.0407%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 138 | 1 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 0.24923 | 0 | 0 | 0.24923 | 0 | 0.2268 | 9.9098 | 0.022886 | 0.2268 | 9.9098 | 0.022886 | 0.25168 | 10.997 | 0.022886 | 0.006919%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 245 | 5 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 2.7782 | 0 | 0 | 2.7782 | 0 | 2.5281 | 49.5488 | 0.051023 | 2.5281 | 49.5488 | 0.051023 | 2.8055 | 54.9851 | 0.051023 | 0.02003%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 229 | 7 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 1.6515 | 0 | 0 | 1.6515 | 0 | 1.5029 | 69.3683 | 0.021665 | 1.5029 | 69.3683 | 0.021665 | 1.6678 | 76.9792 | 0.021665 | 0.02965%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 1 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 1.4592 | 0 | 0 | 1.4592 | 0 | 1.3279 | 9.9098 | 0.134 | 1.3279 | 9.9098 | 0.134 | 1.4736 | 10.997 | 0.134 | 0.01079%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 107 | 2 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 2.0702 | 0 | 0 | 2.0702 | 0 | 1.8838 | 19.8195 | 0.095049 | 1.8838 | 19.8195 | 0.095049 | 2.0905 | 21.9941 | 0.095049 | 0.01848%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 121 | 1 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1.6809 | 0 | 0 | 1.6809 | 0 | 1.5296 | 9.9098 | 0.15436 | 1.5296 | 9.9098 | 0.15436 | 1.6975 | 10.997 | 0.15436 | 0.008196%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 64 | 1 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 1.1544 | 0 | 0 | 1.1544 | 0 | 1.0505 | 9.9098 | 0.10601 | 1.0505 | 9.9098 | 0.10601 | 1.1657 | 10.997 | 0.10601 | 0.01539%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 1 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 0.84871 | 0 | 0 | 0.84871 | 0 | 0.77231 | 9.9098 | 0.077935 | 0.77231 | 9.9098 | 0.077935 | 0.85705 | 10.997 | 0.077935 | 0.04996%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 83 | 1 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 1.3442 | 0 | 0 | 1.3442 | 0 | 1.2232 | 9.9098 | 0.12344 | 1.2232 | 9.9098 | 0.12344 | 1.3574 | 10.997 | 0.12344 | 0.01191%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 50 | 1 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 1.0673 | 0 | 0 | 1.0673 | 0 | 0.97121 | 9.9098 | 0.098005 | 0.97121 | 9.9098 | 0.098005 | 1.0778 | 10.997 | 0.098005 | 0.01963%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 140 | 2 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 2.2364 | 0 | 0 | 2.2364 | 0 | 2.0351 | 19.8195 | 0.10268 | 2.0351 | 19.8195 | 0.10268 | 2.2583 | 21.9941 | 0.10268 | 0.01397%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 1 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 0.96394 | 0 | 0 | 0.96394 | 0 | 0.87717 | 9.9098 | 0.088516 | 0.87717 | 9.9098 | 0.088516 | 0.97341 | 10.997 | 0.088516 | 0.01037%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 11 | 1 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 4.6204 | 0 | 0 | 4.6204 | 0 | 4.2045 | 9.9098 | 0.42428 | 4.2045 | 9.9098 | 0.42428 | 4.6658 | 10.997 | 0.42428 | 0.09062%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 116 | 3 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 4.4611 | 0 | 0 | 4.4611 | 0 | 4.0596 | 29.7293 | 0.13655 | 4.0596 | 29.7293 | 0.13655 | 4.505 | 32.9911 | 0.13655 | 0.02521%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 116 | 1 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 0.87272 | 0 | 0 | 0.87272 | 0 | 0.79416 | 9.9098 | 0.080139 | 0.79416 | 9.9098 | 0.080139 | 0.88129 | 10.997 | 0.080139 | 0.008365%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 94 | 3 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 3.6701 | 0 | 0 | 3.6701 | 0 | 3.3397 | 29.7293 | 0.11234 | 3.3397 | 29.7293 | 0.11234 | 3.7062 | 32.9911 | 0.11234 | 0.03121%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 53 | 1 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 1.107 | 0 | 0 | 1.107 | 0 | 1.0073 | 9.9098 | 0.10165 | 1.0073 | 9.9098 | 0.10165 | 1.1178 | 10.997 | 0.10165 | 0.01811%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 99 | 2 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 7.4895 | 0 | 0 | 7.4895 | 0 | 6.8153 | 19.8195 | 0.34387 | 6.8153 | 19.8195 | 0.34387 | 7.5631 | 21.9941 | 0.34387 | 0.01992%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 90 | 2 | 6370.0414 | 98.47% | 1.262% | 0.272% | 1.3938 | 0 | 0 | 1.3938 | 0 | 1.2684 | 19.8195 | 0.063997 | 1.2684 | 19.8195 | 0.063997 | 1.4075 | 21.9941 | 0.063997 | 0.02188%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 26 | 1 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 0.67813 | 0 | 0 | 0.67813 | 0 | 0.61709 | 9.9098 | 0.062271 | 0.61709 | 9.9098 | 0.062271 | 0.68479 | 10.997 | 0.062271 | 0.03696%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 1 | 1 | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.013995 | 9.9098 | 0.0014123 | 0.013995 | 9.9098 | 0.0014123 | 0.015531 | 10.997 | 0.0014123 | 0.01745%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 161 | 6 | 11572.221 | 88.48% | 11.4% | 0.1243% | 3.8157 | 0 | 0 | 3.8157 | 0 | 3.4722 | 59.4585 | 0.058397 | 3.4722 | 59.4585 | 0.058397 | 3.8532 | 65.9822 | 0.058397 | 0.03297%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 102 | 2 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 0.65378 | 0 | 0 | 0.65378 | 0 | 0.59493 | 19.8195 | 0.030017 | 0.59493 | 19.8195 | 0.030017 | 0.6602 | 21.9941 | 0.030017 | 0.01915%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 90 | 2 | 571.2373 | 70.71% | 27.93% | 1.361% | 0.089758 | 0 | 0 | 0.089758 | 0 | 0.081679 | 19.8195 | 0.0041211 | 0.081679 | 19.8195 | 0.0041211 | 0.09064 | 21.9941 | 0.0041211 | 0.01571%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 3 | 1 | 117.4434 | 97.68% | 1.947% | 0.3705% | 0.3824 | 0 | 0 | 0.3824 | 0 | 0.34798 | 9.9098 | 0.035115 | 0.34798 | 9.9098 | 0.035115 | 0.38616 | 10.997 | 0.035115 | 0.3256%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 85 | 1 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 1.0761 | 0 | 0 | 1.0761 | 0 | 0.97924 | 9.9098 | 0.098815 | 0.97924 | 9.9098 | 0.098815 | 1.0867 | 10.997 | 0.098815 | 0.01117%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 43 | 4 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 1.3234 | 0 | 0 | 1.3234 | 0 | 1.2043 | 39.639 | 0.030382 | 1.2043 | 39.639 | 0.030382 | 1.3364 | 43.9881 | 0.030382 | 0.08253%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 116 | 2 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 1.752 | 0 | 0 | 1.752 | 0 | 1.5943 | 19.8195 | 0.080443 | 1.5943 | 19.8195 | 0.080443 | 1.7693 | 21.9941 | 0.080443 | 0.0165%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 65 | 1 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 0.23029 | 0 | 0 | 0.23029 | 0 | 0.20956 | 9.9098 | 0.021147 | 0.20956 | 9.9098 | 0.021147 | 0.23255 | 10.997 | 0.021147 | 0.01303%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 91 | 2 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 0.70775 | 0 | 0 | 0.70775 | 0 | 0.64404 | 19.8195 | 0.032495 | 0.64404 | 19.8195 | 0.032495 | 0.71471 | 21.9941 | 0.032495 | 0.01924%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 9 | 1 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 1.4606 | 0 | 0 | 1.4606 | 0 | 1.3291 | 9.9098 | 0.13412 | 1.3291 | 9.9098 | 0.13412 | 1.4749 | 10.997 | 0.13412 | 0.108%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 9 | 1 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 1.3111 | 0 | 0 | 1.3111 | 0 | 1.1931 | 9.9098 | 0.1204 | 1.1931 | 9.9098 | 0.1204 | 1.324 | 10.997 | 0.1204 | 0.1082%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 43 | 1 | 2612.2711 | 91.91% | 7.885% | 0.2065% | 0.55835 | 0 | 0 | 0.55835 | 0 | 0.50809 | 9.9098 | 0.051272 | 0.50809 | 9.9098 | 0.051272 | 0.56384 | 10.997 | 0.051272 | 0.02137%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 85 | 1 | 2119.752 | 55.7% | 43.96% | 0.3458% | 0.1389 | 0 | 0 | 0.1389 | 0 | 0.1264 | 9.9098 | 0.012755 | 0.1264 | 9.9098 | 0.012755 | 0.14027 | 10.997 | 0.012755 | 0.006553%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 45 | 1 | 630.7627 | 79.12% | 20.09% | 0.7869% | 0.11091 | 0 | 0 | 0.11091 | 0 | 0.10092 | 9.9098 | 0.010184 | 0.10092 | 9.9098 | 0.010184 | 0.112 | 10.997 | 0.010184 | 0.01758%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 224 | 10 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 3.7264 | 0 | 0 | 3.7264 | 0 | 3.391 | 99.0975 | 0.034219 | 3.391 | 99.0975 | 0.034219 | 3.7631 | 109.9703 | 0.034219 | 0.04093%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 106 | 3 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 1.4926 | 0 | 0 | 1.4926 | 0 | 1.3582 | 29.7293 | 0.045686 | 1.3582 | 29.7293 | 0.045686 | 1.5072 | 32.9911 | 0.045686 | 0.02644%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 22 | 1 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 0.65919 | 0 | 0 | 0.65919 | 0 | 0.59986 | 9.9098 | 0.060532 | 0.59986 | 9.9098 | 0.060532 | 0.66567 | 10.997 | 0.060532 | 0.04408%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 45 | 2 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 0.9852 | 0 | 0 | 0.9852 | 0 | 0.89652 | 19.8195 | 0.045234 | 0.89652 | 19.8195 | 0.045234 | 0.99489 | 21.9941 | 0.045234 | 0.04247%
2027 | 449 | CB 449 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 1 | 7.8127 | 98.22% | 0% | 1.784% | 0.076733 | 0 | 0 | 0.076733 | 0 | 0.069826 | 9.9098 | 0.0070462 | 0.069826 | 9.9098 | 0.0070462 | 0.077488 | 10.997 | 0.0070462 | 0.9822%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 1 | 1 | 625.5425 | 99.9% | 0% | 0.09615% | 6.2494 | 0 | 0 | 6.2494 | 0 | 5.6869 | 9.9098 | 0.57387 | 5.6869 | 9.9098 | 0.57387 | 6.3108 | 10.997 | 0.57387 | 0.999%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 20 | 1 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 2.5885 | 0 | 0 | 2.5885 | 0 | 2.3555 | 9.9098 | 0.23769 | 2.3555 | 9.9098 | 0.23769 | 2.6139 | 10.997 | 0.23769 | 0.04916%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 53 | 4 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 12.5547 | 0 | 0 | 12.5547 | 0 | 11.4246 | 39.639 | 0.28822 | 11.4246 | 39.639 | 0.28822 | 12.6781 | 43.9881 | 0.28822 | 0.075%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 47 | 1 | 2978.814 | 97.34% | 2.471% | 0.184% | 0.61696 | 0 | 0 | 0.61696 | 0 | 0.56143 | 9.9098 | 0.056654 | 0.56143 | 9.9098 | 0.056654 | 0.62302 | 10.997 | 0.056654 | 0.02071%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 129 | 2 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 0.39572 | 0 | 0 | 0.39572 | 0 | 0.3601 | 19.8195 | 0.018169 | 0.3601 | 19.8195 | 0.018169 | 0.3996 | 21.9941 | 0.018169 | 0.015%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 84 | 1 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 0.37683 | 0 | 0 | 0.37683 | 0 | 0.34291 | 9.9098 | 0.034604 | 0.34291 | 9.9098 | 0.034604 | 0.38054 | 10.997 | 0.034604 | 0.01104%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 53 | 1 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 1.2342 | 0 | 0 | 1.2342 | 0 | 1.1231 | 9.9098 | 0.11333 | 1.1231 | 9.9098 | 0.11333 | 1.2463 | 10.997 | 0.11333 | 0.01825%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 74 | 1 | 2044.6463 | 97.57% | 2.13% | 0.298% | 0.26959 | 0 | 0 | 0.26959 | 0 | 0.24533 | 9.9098 | 0.024756 | 0.24533 | 9.9098 | 0.024756 | 0.27224 | 10.997 | 0.024756 | 0.01319%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 49 | 2 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 4.4795 | 0 | 0 | 4.4795 | 0 | 4.0763 | 19.8195 | 0.20567 | 4.0763 | 19.8195 | 0.20567 | 4.5235 | 21.9941 | 0.20567 | 0.03947%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 87 | 2 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 1.9059 | 0 | 0 | 1.9059 | 0 | 1.7343 | 19.8195 | 0.087507 | 1.7343 | 19.8195 | 0.087507 | 1.9246 | 21.9941 | 0.087507 | 0.02248%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 73 | 4 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 4.7438 | 0 | 0 | 4.7438 | 0 | 4.3168 | 39.639 | 0.1089 | 4.3168 | 39.639 | 0.1089 | 4.7904 | 43.9881 | 0.1089 | 0.05444%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 25 | 2 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 4.44 | 0 | 0 | 4.44 | 0 | 4.0404 | 19.8195 | 0.20386 | 4.0404 | 19.8195 | 0.20386 | 4.4837 | 21.9941 | 0.20386 | 0.07902%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 37 | 1 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 2.4127 | 0 | 0 | 2.4127 | 0 | 2.1956 | 9.9098 | 0.22156 | 2.1956 | 9.9098 | 0.22156 | 2.4365 | 10.997 | 0.22156 | 0.02677%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1 | 1 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 49.4954 | 9.9098 | 4.9946 | 49.4954 | 9.9098 | 4.9946 | 54.926 | 10.997 | 4.9946 | 0.9644%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 46 | 2 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 2.3721 | 0 | 0 | 2.3721 | 0 | 2.1586 | 19.8195 | 0.10891 | 2.1586 | 19.8195 | 0.10891 | 2.3954 | 21.9941 | 0.10891 | 0.04338%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 114 | 4 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 3.962 | 0 | 0 | 3.962 | 0 | 3.6053 | 39.639 | 0.090954 | 3.6053 | 39.639 | 0.090954 | 4.0009 | 43.9881 | 0.090954 | 0.03501%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 89 | 3 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 4.5749 | 0 | 0 | 4.5749 | 0 | 4.1631 | 29.7293 | 0.14003 | 4.1631 | 29.7293 | 0.14003 | 4.6198 | 32.9911 | 0.14003 | 0.03337%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 1 | 8801.877 | 98.2% | 1.718% | 0.0819% | 1.029 | 0 | 0 | 1.029 | 0 | 0.93636 | 9.9098 | 0.094489 | 0.93636 | 9.9098 | 0.094489 | 1.0391 | 10.997 | 0.094489 | 0.01169%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 283 | 7 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 9.8903 | 0 | 0 | 9.8903 | 0 | 9 | 69.3683 | 0.12974 | 9 | 69.3683 | 0.12974 | 9.9875 | 76.9792 | 0.12974 | 0.0245%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 92 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 1.9499 | 0 | 0 | 1.9499 | 0 | 1.7744 | 9.9098 | 0.17905 | 1.7744 | 9.9098 | 0.17905 | 1.969 | 10.997 | 0.17905 | 0.01039%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 124 | 4 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 8.2542 | 0 | 0 | 8.2542 | 0 | 7.5112 | 39.639 | 0.18949 | 7.5112 | 39.639 | 0.18949 | 8.3353 | 43.9881 | 0.18949 | 0.03206%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 4 | 1 | 55.0677 | 92.66% | 4.028% | 3.312% | 0.12756 | 0 | 0 | 0.12756 | 0 | 0.11608 | 9.9098 | 0.011714 | 0.11608 | 9.9098 | 0.011714 | 0.12882 | 10.997 | 0.011714 | 0.2317%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 1 | 1 | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.2688 | 9.9098 | 0.12804 | 1.2688 | 9.9098 | 0.12804 | 1.4081 | 10.997 | 0.12804 | 0.9963%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 41 | 2 | 8606.9717 | 99.86% | 0% | 0.1411% | 4.1926 | 0 | 0 | 4.1926 | 0 | 3.8152 | 19.8195 | 0.1925 | 3.8152 | 19.8195 | 0.1925 | 4.2338 | 21.9941 | 0.1925 | 0.04871%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 37 | 2 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 4.4533 | 0 | 0 | 4.4533 | 0 | 4.0524 | 19.8195 | 0.20447 | 4.0524 | 19.8195 | 0.20447 | 4.497 | 21.9941 | 0.20447 | 0.05277%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 74 | 2 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 7.2563 | 0 | 0 | 7.2563 | 0 | 6.6031 | 19.8195 | 0.33316 | 6.6031 | 19.8195 | 0.33316 | 7.3276 | 21.9941 | 0.33316 | 0.02681%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 76 | 1 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 2.0398 | 0 | 0 | 2.0398 | 0 | 1.8562 | 9.9098 | 0.18731 | 1.8562 | 9.9098 | 0.18731 | 2.0599 | 10.997 | 0.18731 | 0.01294%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 109 | 3 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 1.4757 | 0 | 0 | 1.4757 | 0 | 1.3429 | 29.7293 | 0.045171 | 1.3429 | 29.7293 | 0.045171 | 1.4902 | 32.9911 | 0.045171 | 0.02649%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 40 | 1 | 1466.2762 | 91.81% | 7.905% | 0.289% | 0.33653 | 0 | 0 | 0.33653 | 0 | 0.30624 | 9.9098 | 0.030903 | 0.30624 | 9.9098 | 0.030903 | 0.33984 | 10.997 | 0.030903 | 0.02295%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 146 | 2 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 5.5892 | 0 | 0 | 5.5892 | 0 | 5.0861 | 19.8195 | 0.25662 | 5.0861 | 19.8195 | 0.25662 | 5.6441 | 21.9941 | 0.25662 | 0.01355%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 46 | 1 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 0.72865 | 0 | 0 | 0.72865 | 0 | 0.66306 | 9.9098 | 0.06691 | 0.66306 | 9.9098 | 0.06691 | 0.73581 | 10.997 | 0.06691 | 0.01998%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 1 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 2.3534 | 0 | 0 | 2.3534 | 0 | 2.1416 | 9.9098 | 0.21611 | 2.1416 | 9.9098 | 0.21611 | 2.3765 | 10.997 | 0.21611 | 0.01043%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 10 | 1 | 847.524 | 96.52% | 3.329% | 0.1488% | 0.81805 | 0 | 0 | 0.81805 | 0 | 0.74441 | 9.9098 | 0.075119 | 0.74441 | 9.9098 | 0.075119 | 0.82609 | 10.997 | 0.075119 | 0.09652%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 126 | 3 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 13.0597 | 0 | 0 | 13.0597 | 0 | 11.8842 | 29.7293 | 0.39975 | 11.8842 | 29.7293 | 0.39975 | 13.1881 | 32.9911 | 0.39975 | 0.02364%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 2 | 1 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 7.6289 | 0 | 0 | 7.6289 | 0 | 6.9422 | 9.9098 | 0.70054 | 6.9422 | 9.9098 | 0.70054 | 7.7038 | 10.997 | 0.70054 | 0.383%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 100 | 3 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 4.5016 | 0 | 0 | 4.5016 | 0 | 4.0964 | 29.7293 | 0.13779 | 4.0964 | 29.7293 | 0.13779 | 4.5458 | 32.9911 | 0.13779 | 0.02972%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 189 | 6 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 8.9444 | 0 | 0 | 8.9444 | 0 | 8.1393 | 59.4585 | 0.13689 | 8.1393 | 59.4585 | 0.13689 | 9.0323 | 65.9822 | 0.13689 | 0.0314%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 45 | 2 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 6.4618 | 0 | 0 | 6.4618 | 0 | 5.8801 | 19.8195 | 0.29668 | 5.8801 | 19.8195 | 0.29668 | 6.5253 | 21.9941 | 0.29668 | 0.04375%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 103 | 2 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 2.1656 | 0 | 0 | 2.1656 | 0 | 1.9706 | 19.8195 | 0.09943 | 1.9706 | 19.8195 | 0.09943 | 2.1869 | 21.9941 | 0.09943 | 0.01922%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 27 | 2 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 8.4447 | 0 | 0 | 8.4447 | 0 | 7.6846 | 19.8195 | 0.38773 | 7.6846 | 19.8195 | 0.38773 | 8.5277 | 21.9941 | 0.38773 | 0.07371%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 81 | 2 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 1.951 | 0 | 0 | 1.951 | 0 | 1.7754 | 19.8195 | 0.089579 | 1.7754 | 19.8195 | 0.089579 | 1.9702 | 21.9941 | 0.089579 | 0.02433%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 106 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 2.1729 | 0 | 0 | 2.1729 | 0 | 1.9773 | 9.9098 | 0.19953 | 1.9773 | 9.9098 | 0.19953 | 2.1943 | 10.997 | 0.19953 | 0.009282%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 54 | 1 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 4.1364 | 0 | 0 | 4.1364 | 0 | 3.7641 | 9.9098 | 0.37983 | 3.7641 | 9.9098 | 0.37983 | 4.177 | 10.997 | 0.37983 | 0.01805%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 2 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 3.0742 | 0 | 0 | 3.0742 | 0 | 2.7975 | 19.8195 | 0.14115 | 2.7975 | 19.8195 | 0.14115 | 3.1044 | 21.9941 | 0.14115 | 0.0336%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 82 | 1 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 0.77967 | 0 | 0 | 0.77967 | 0 | 0.70949 | 9.9098 | 0.071595 | 0.70949 | 9.9098 | 0.071595 | 0.78733 | 10.997 | 0.071595 | 0.01195%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 104 | 2 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 0.62934 | 0 | 0 | 0.62934 | 0 | 0.57269 | 19.8195 | 0.028895 | 0.57269 | 19.8195 | 0.028895 | 0.63553 | 21.9941 | 0.028895 | 0.01802%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 29 | 2 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 4.8793 | 0 | 0 | 4.8793 | 0 | 4.4401 | 19.8195 | 0.22403 | 4.4401 | 19.8195 | 0.22403 | 4.9273 | 21.9941 | 0.22403 | 0.06865%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 2 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 7.3287 | 0 | 0 | 7.3287 | 0 | 6.6691 | 19.8195 | 0.33649 | 6.6691 | 19.8195 | 0.33649 | 7.4008 | 21.9941 | 0.33649 | 0.02085%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 17 | 1 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 4.0747 | 0 | 0 | 4.0747 | 0 | 3.7079 | 9.9098 | 0.37417 | 3.7079 | 9.9098 | 0.37417 | 4.1147 | 10.997 | 0.37417 | 0.05775%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 43 | 3 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 13.0946 | 0 | 0 | 13.0946 | 0 | 11.9159 | 29.7293 | 0.40082 | 11.9159 | 29.7293 | 0.40082 | 13.2233 | 32.9911 | 0.40082 | 0.06956%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 11 | 1 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 4.5541 | 0 | 0 | 4.5541 | 0 | 4.1441 | 9.9098 | 0.41819 | 4.1441 | 9.9098 | 0.41819 | 4.5988 | 10.997 | 0.41819 | 0.09046%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 32 | 1 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 1.5717 | 0 | 0 | 1.5717 | 0 | 1.4303 | 9.9098 | 0.14433 | 1.4303 | 9.9098 | 0.14433 | 1.5872 | 10.997 | 0.14433 | 0.03099%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 80 | 3 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 3.4084 | 0 | 0 | 3.4084 | 0 | 3.1016 | 29.7293 | 0.10433 | 3.1016 | 29.7293 | 0.10433 | 3.4419 | 32.9911 | 0.10433 | 0.03599%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 19 | 1 | 585.5086 | 87.68% | 11.85% | 0.4758% | 0.27019 | 0 | 0 | 0.27019 | 0 | 0.24587 | 9.9098 | 0.024811 | 0.24587 | 9.9098 | 0.024811 | 0.27285 | 10.997 | 0.024811 | 0.04615%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 22 | 1 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 0.9723 | 0 | 0 | 0.9723 | 0 | 0.88478 | 9.9098 | 0.089284 | 0.88478 | 9.9098 | 0.089284 | 0.98186 | 10.997 | 0.089284 | 0.0452%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 2 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 1.537 | 0 | 0 | 1.537 | 0 | 1.3986 | 19.8195 | 0.070568 | 1.3986 | 19.8195 | 0.070568 | 1.5521 | 21.9941 | 0.070568 | 0.02321%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 124 | 6 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 12.1458 | 0 | 0 | 12.1458 | 0 | 11.0525 | 59.4585 | 0.18589 | 11.0525 | 59.4585 | 0.18589 | 12.2652 | 65.9822 | 0.18589 | 0.04797%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 119 | 5 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 11.7526 | 0 | 0 | 11.7526 | 0 | 10.6947 | 49.5488 | 0.21584 | 10.6947 | 49.5488 | 0.21584 | 11.8681 | 54.9851 | 0.21584 | 0.04138%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 103 | 4 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 10.2802 | 0 | 0 | 10.2802 | 0 | 9.3549 | 39.639 | 0.236 | 9.3549 | 39.639 | 0.236 | 10.3813 | 43.9881 | 0.236 | 0.03851%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 68 | 2 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 4.5738 | 0 | 0 | 4.5738 | 0 | 4.1621 | 19.8195 | 0.21 | 4.1621 | 19.8195 | 0.21 | 4.6187 | 21.9941 | 0.21 | 0.02866%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 24 | 4 | 919.3728 | 93.93% | 5.62% | 0.4487% | 1.4393 | 0 | 0 | 1.4393 | 0 | 1.3097 | 39.639 | 0.033042 | 1.3097 | 39.639 | 0.033042 | 1.4534 | 43.9881 | 0.033042 | 0.1566%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 81 | 3 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 2.1765 | 0 | 0 | 2.1765 | 0 | 1.9806 | 29.7293 | 0.066622 | 1.9806 | 29.7293 | 0.066622 | 2.1979 | 32.9911 | 0.066622 | 0.0369%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 63 | 1 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 0.78923 | 0 | 0 | 0.78923 | 0 | 0.71818 | 9.9098 | 0.072472 | 0.71818 | 9.9098 | 0.072472 | 0.79698 | 10.997 | 0.072472 | 0.01581%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 16 | 1 | 2514.2831 | 99.84% | 0% | 0.1648% | 1.5688 | 0 | 0 | 1.5688 | 0 | 1.4276 | 9.9098 | 0.14406 | 1.4276 | 9.9098 | 0.14406 | 1.5843 | 10.997 | 0.14406 | 0.0624%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 93 | 2 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 0.91394 | 0 | 0 | 0.91394 | 0 | 0.83168 | 19.8195 | 0.041963 | 0.83168 | 19.8195 | 0.041963 | 0.92293 | 21.9941 | 0.041963 | 0.0196%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 1 | 765.4961 | 75% | 24.28% | 0.7274% | 0.30215 | 0 | 0 | 0.30215 | 0 | 0.27495 | 9.9098 | 0.027746 | 0.27495 | 9.9098 | 0.027746 | 0.30512 | 10.997 | 0.027746 | 0.03947%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 8 | 1 | 247.9994 | 97.75% | 1.792% | 0.4608% | 0.30301 | 0 | 0 | 0.30301 | 0 | 0.27574 | 9.9098 | 0.027825 | 0.27574 | 9.9098 | 0.027825 | 0.30599 | 10.997 | 0.027825 | 0.1222%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 3 | 1 | 75.2008 | 96.65% | 1.975% | 1.378% | 0.24226 | 0 | 0 | 0.24226 | 0 | 0.22046 | 9.9098 | 0.022246 | 0.22046 | 9.9098 | 0.022246 | 0.24464 | 10.997 | 0.022246 | 0.3222%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 23 | 1 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 1.6941 | 0 | 0 | 1.6941 | 0 | 1.5416 | 9.9098 | 0.15556 | 1.5416 | 9.9098 | 0.15556 | 1.7107 | 10.997 | 0.15556 | 0.04272%
2027 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | Tier-3---19 | 2 | 1 | 157.8878 | 78.49% | 21.24% | 0.2654% | 0.61966 | 0 | 0 | 0.61966 | 0 | 0.56389 | 9.9098 | 0.056902 | 0.56389 | 9.9098 | 0.056902 | 0.62575 | 10.997 | 0.056902 | 0.3925%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 64 | 1 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 1.3109 | 0 | 0 | 1.3109 | 0 | 1.1929 | 9.9098 | 0.12038 | 1.1929 | 9.9098 | 0.12038 | 1.3238 | 10.997 | 0.12038 | 0.01507%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 33 | 2 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 2.1246 | 0 | 0 | 2.1246 | 0 | 1.9334 | 19.8195 | 0.09755 | 1.9334 | 19.8195 | 0.09755 | 2.1455 | 21.9941 | 0.09755 | 0.05965%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 39 | 1 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 0.74901 | 0 | 0 | 0.74901 | 0 | 0.68159 | 9.9098 | 0.068779 | 0.68159 | 9.9098 | 0.068779 | 0.75637 | 10.997 | 0.068779 | 0.0251%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 30 | 2 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 2.8284 | 0 | 0 | 2.8284 | 0 | 2.5738 | 19.8195 | 0.12986 | 2.5738 | 19.8195 | 0.12986 | 2.8562 | 21.9941 | 0.12986 | 0.06577%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 79 | 3 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 2.0202 | 0 | 0 | 2.0202 | 0 | 1.8383 | 29.7293 | 0.061836 | 1.8383 | 29.7293 | 0.061836 | 2.04 | 32.9911 | 0.061836 | 0.03201%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 92 | 2 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 1.4316 | 0 | 0 | 1.4316 | 0 | 1.3027 | 19.8195 | 0.065729 | 1.3027 | 19.8195 | 0.065729 | 1.4456 | 21.9941 | 0.065729 | 0.02154%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 30 | 1 | 1438.3629 | 99.75% | 0% | 0.2509% | 0.47825 | 0 | 0 | 0.47825 | 0 | 0.4352 | 9.9098 | 0.043917 | 0.4352 | 9.9098 | 0.043917 | 0.48295 | 10.997 | 0.043917 | 0.03325%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 28 | 1 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 4.1651 | 0 | 0 | 4.1651 | 0 | 3.7902 | 9.9098 | 0.38247 | 3.7902 | 9.9098 | 0.38247 | 4.206 | 10.997 | 0.38247 | 0.03545%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 13 | 1 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 2.7823 | 0 | 0 | 2.7823 | 0 | 2.5318 | 9.9098 | 0.25549 | 2.5318 | 9.9098 | 0.25549 | 2.8096 | 10.997 | 0.25549 | 0.0755%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 16 | 1 | 427.4478 | 90.46% | 9.431% | 0.1062% | 0.24168 | 0 | 0 | 0.24168 | 0 | 0.21992 | 9.9098 | 0.022192 | 0.21992 | 9.9098 | 0.022192 | 0.24405 | 10.997 | 0.022192 | 0.05654%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 51 | 1 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 3.1063 | 0 | 0 | 3.1063 | 0 | 2.8267 | 9.9098 | 0.28525 | 2.8267 | 9.9098 | 0.28525 | 3.1369 | 10.997 | 0.28525 | 0.01943%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 38 | 3 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 6.3935 | 0 | 0 | 6.3935 | 0 | 5.818 | 29.7293 | 0.1957 | 5.818 | 29.7293 | 0.1957 | 6.4563 | 32.9911 | 0.1957 | 0.07835%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 127 | 3 | 37077.302 | 99.36% | 0.615% | 0.02874% | 8.702 | 0 | 0 | 8.702 | 0 | 7.9187 | 29.7293 | 0.26636 | 7.9187 | 29.7293 | 0.26636 | 8.7876 | 32.9911 | 0.26636 | 0.02347%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 1 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 0.30727 | 0 | 0 | 0.30727 | 0 | 0.27961 | 9.9098 | 0.028216 | 0.27961 | 9.9098 | 0.028216 | 0.31029 | 10.997 | 0.028216 | 0.01489%
2027 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 1 | 1 | 15.4911 | 99.81% | 0% | 0.1868% | 0.15462 | 0 | 0 | 0.15462 | 0 | 0.1407 | 9.9098 | 0.014199 | 0.1407 | 9.9098 | 0.014199 | 0.15614 | 10.997 | 0.014199 | 0.9981%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 90 | 6 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 2.3597 | 0 | 0 | 2.3597 | 0 | 2.1473 | 59.4585 | 0.036115 | 2.1473 | 59.4585 | 0.036115 | 2.3829 | 65.9822 | 0.036115 | 0.06344%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 29 | 1 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 0.51681 | 0 | 0 | 0.51681 | 0 | 0.47029 | 9.9098 | 0.047457 | 0.47029 | 9.9098 | 0.047457 | 0.52189 | 10.997 | 0.047457 | 0.03374%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 32 | 1 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 1.5768 | 0 | 0 | 1.5768 | 0 | 1.4349 | 9.9098 | 0.14479 | 1.4349 | 9.9098 | 0.14479 | 1.5923 | 10.997 | 0.14479 | 0.0308%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 109 | 7 | 6915.6819 | 99% | 0.9206% | 0.07911% | 4.3969 | 0 | 0 | 4.3969 | 0 | 4.0011 | 69.3683 | 0.057679 | 4.0011 | 69.3683 | 0.057679 | 4.4401 | 76.9792 | 0.057679 | 0.06358%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 66 | 2 | 3027.5479 | 94.73% | 5.109% | 0.164% | 0.86906 | 0 | 0 | 0.86906 | 0 | 0.79083 | 19.8195 | 0.039902 | 0.79083 | 19.8195 | 0.039902 | 0.8776 | 21.9941 | 0.039902 | 0.02871%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 65 | 3 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 4.7718 | 0 | 0 | 4.7718 | 0 | 4.3423 | 29.7293 | 0.14606 | 4.3423 | 29.7293 | 0.14606 | 4.8187 | 32.9911 | 0.14606 | 0.04537%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 17 | 1 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 3.0184 | 0 | 0 | 3.0184 | 0 | 2.7467 | 9.9098 | 0.27717 | 2.7467 | 9.9098 | 0.27717 | 3.048 | 10.997 | 0.27717 | 0.05771%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 5 | 6920.124 | 97.57% | 2.306% | 0.1195% | 3.9719 | 0 | 0 | 3.9719 | 0 | 3.6144 | 49.5488 | 0.072946 | 3.6144 | 49.5488 | 0.072946 | 4.011 | 54.9851 | 0.072946 | 0.0574%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 27 | 2 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 4.3747 | 0 | 0 | 4.3747 | 0 | 3.9809 | 19.8195 | 0.20086 | 3.9809 | 19.8195 | 0.20086 | 4.4177 | 21.9941 | 0.20086 | 0.07357%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 128 | 4 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 0.98446 | 0 | 0 | 0.98446 | 0 | 0.89584 | 39.639 | 0.0226 | 0.89584 | 39.639 | 0.0226 | 0.99413 | 43.9881 | 0.0226 | 0.02929%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 112 | 3 | 2610.8 | 93.6% | 6.065% | 0.3401% | 0.65453 | 0 | 0 | 0.65453 | 0 | 0.56818 | 28.3597 | 0.020035 | 0.56818 | 28.3597 | 0.020035 | 0.6642 | 33.1528 | 0.020035 | 0.02507%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 188 | 5 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 1.0428 | 0 | 0 | 1.0428 | 0 | 0.90525 | 47.2661 | 0.019152 | 0.90525 | 47.2661 | 0.019152 | 1.0583 | 55.2547 | 0.019152 | 0.02495%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 78 | 2 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 0.38731 | 0 | 0 | 0.38731 | 0 | 0.33621 | 18.9065 | 0.017783 | 0.33621 | 18.9065 | 0.017783 | 0.39303 | 22.1019 | 0.017783 | 0.02379%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 84 | 2 | 6201.607 | 97.29% | 2.601% | 0.1104% | 1.4365 | 0 | 0 | 1.4365 | 0 | 1.247 | 18.9065 | 0.065957 | 1.247 | 18.9065 | 0.065957 | 1.4578 | 22.1019 | 0.065957 | 0.02316%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 21 | 2 | 2448.8293 | 98.64% | 1.317% | 0.04316% | 2.3005 | 0 | 0 | 2.3005 | 0 | 1.997 | 18.9065 | 0.10562 | 1.997 | 18.9065 | 0.10562 | 2.3345 | 22.1019 | 0.10562 | 0.09394%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 56 | 1 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 1.0076 | 0 | 0 | 1.0076 | 0 | 0.87465 | 9.4532 | 0.092524 | 0.87465 | 9.4532 | 0.092524 | 1.0225 | 11.0509 | 0.092524 | 0.01757%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 93 | 4 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 4.4785 | 0 | 0 | 4.4785 | 0 | 3.8876 | 37.8129 | 0.10281 | 3.8876 | 37.8129 | 0.10281 | 4.5446 | 44.2037 | 0.10281 | 0.04228%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 1 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 1.0883 | 0 | 0 | 1.0883 | 0 | 0.94475 | 9.4532 | 0.099939 | 0.94475 | 9.4532 | 0.099939 | 1.1044 | 11.0509 | 0.099939 | 0.01172%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 60 | 2 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 4.7724 | 0 | 0 | 4.7724 | 0 | 4.1427 | 18.9065 | 0.21912 | 4.1427 | 18.9065 | 0.21912 | 4.8429 | 22.1019 | 0.21912 | 0.03285%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 13 | 1 | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 5.5132 | 0 | 0 | 5.5132 | 0 | 4.7858 | 9.4532 | 0.50627 | 4.7858 | 9.4532 | 0.50627 | 5.5947 | 11.0509 | 0.50627 | 0.07655%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 34 | 1 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 3.5972 | 0 | 0 | 3.5972 | 0 | 3.1226 | 9.4532 | 0.33032 | 3.1226 | 9.4532 | 0.33032 | 3.6503 | 11.0509 | 0.33032 | 0.0292%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 77 | 3 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 0.44405 | 0 | 0 | 0.44405 | 0 | 0.38546 | 28.3597 | 0.013592 | 0.38546 | 28.3597 | 0.013592 | 0.45061 | 33.1528 | 0.013592 | 0.02763%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 59 | 2 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 6.1848 | 0 | 0 | 6.1848 | 0 | 5.3688 | 18.9065 | 0.28397 | 5.3688 | 18.9065 | 0.28397 | 6.2762 | 22.1019 | 0.28397 | 0.03352%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 50 | 1 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 1.0665 | 0 | 0 | 1.0665 | 0 | 0.9258 | 9.4532 | 0.097935 | 0.9258 | 9.4532 | 0.097935 | 1.0823 | 11.0509 | 0.097935 | 0.01926%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 107 | 4 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 6.8204 | 0 | 0 | 6.8204 | 0 | 5.9205 | 37.8129 | 0.15657 | 5.9205 | 37.8129 | 0.15657 | 6.9212 | 44.2037 | 0.15657 | 0.03632%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 56 | 1 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 3.5401 | 0 | 0 | 3.5401 | 0 | 3.0731 | 9.4532 | 0.32508 | 3.0731 | 9.4532 | 0.32508 | 3.5924 | 11.0509 | 0.32508 | 0.01772%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 20 | 1 | 418.5676 | 87.71% | 11.66% | 0.6303% | 0.18355 | 0 | 0 | 0.18355 | 0 | 0.15934 | 9.4532 | 0.016855 | 0.15934 | 9.4532 | 0.016855 | 0.18627 | 11.0509 | 0.016855 | 0.04385%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 177 | 1 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 0.28768 | 0 | 0 | 0.28768 | 0 | 0.24972 | 9.4532 | 0.026417 | 0.24972 | 9.4532 | 0.026417 | 0.29193 | 11.0509 | 0.026417 | 0.005224%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 20 | 1 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 1.9184 | 0 | 0 | 1.9184 | 0 | 1.6653 | 9.4532 | 0.17616 | 1.6653 | 9.4532 | 0.17616 | 1.9468 | 11.0509 | 0.17616 | 0.04949%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 80 | 1 | 3160.5079 | 95.27% | 4.501% | 0.231% | 0.37637 | 0 | 0 | 0.37637 | 0 | 0.32671 | 9.4532 | 0.034561 | 0.32671 | 9.4532 | 0.034561 | 0.38193 | 11.0509 | 0.034561 | 0.01191%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 151 | 1 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 0.1113 | 0 | 0 | 0.1113 | 0 | 0.09662 | 9.4532 | 0.010221 | 0.09662 | 9.4532 | 0.010221 | 0.11295 | 11.0509 | 0.010221 | 0.0054%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 2 | 1867.403 | 95.01% | 4.712% | 0.2778% | 0.66952 | 0 | 0 | 0.66952 | 0 | 0.58119 | 18.9065 | 0.03074 | 0.58119 | 18.9065 | 0.03074 | 0.67941 | 22.1019 | 0.03074 | 0.03585%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 205 | 8 | 18749.5963 | 97% | 2.901% | 0.09453% | 7.0978 | 0 | 0 | 7.0978 | 0 | 6.1613 | 75.6258 | 0.081471 | 6.1613 | 75.6258 | 0.081471 | 7.2027 | 88.4075 | 0.081471 | 0.03786%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 19 | 1 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 2.1015 | 0 | 0 | 2.1015 | 0 | 1.8242 | 9.4532 | 0.19297 | 1.8242 | 9.4532 | 0.19297 | 2.1326 | 11.0509 | 0.19297 | 0.05216%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 1 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 0.67886 | 0 | 0 | 0.67886 | 0 | 0.58929 | 9.4532 | 0.062338 | 0.58929 | 9.4532 | 0.062338 | 0.68889 | 11.0509 | 0.062338 | 0.01548%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 113 | 1 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 0.49215 | 0 | 0 | 0.49215 | 0 | 0.42722 | 9.4532 | 0.045193 | 0.42722 | 9.4532 | 0.045193 | 0.49942 | 11.0509 | 0.045193 | 0.008572%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 1 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 1.8357 | 0 | 0 | 1.8357 | 0 | 1.5935 | 9.4532 | 0.16857 | 1.5935 | 9.4532 | 0.16857 | 1.8628 | 11.0509 | 0.16857 | 0.01593%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 55 | 2 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 1.4928 | 0 | 0 | 1.4928 | 0 | 1.2958 | 18.9065 | 0.068538 | 1.2958 | 18.9065 | 0.068538 | 1.5148 | 22.1019 | 0.068538 | 0.03567%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 51 | 2 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 1.3036 | 0 | 0 | 1.3036 | 0 | 1.1316 | 18.9065 | 0.059853 | 1.1316 | 18.9065 | 0.059853 | 1.3229 | 22.1019 | 0.059853 | 0.03833%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 44 | 2 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 2.1913 | 0 | 0 | 2.1913 | 0 | 1.9022 | 18.9065 | 0.10061 | 1.9022 | 18.9065 | 0.10061 | 2.2236 | 22.1019 | 0.10061 | 0.04441%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 115 | 3 | 13172.958 | 96.8% | 3.124% | 0.0728% | 3.3266 | 0 | 0 | 3.3266 | 0 | 2.8877 | 28.3597 | 0.10182 | 2.8877 | 28.3597 | 0.10182 | 3.3757 | 33.1528 | 0.10182 | 0.02525%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 1 | 1635.841 | 89.24% | 10.7% | 0.05535% | 2.9198 | 0 | 0 | 2.9198 | 0 | 2.5346 | 9.4532 | 0.26812 | 2.5346 | 9.4532 | 0.26812 | 2.9629 | 11.0509 | 0.26812 | 0.1785%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 17 | 1 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 2.4687 | 0 | 0 | 2.4687 | 0 | 2.143 | 9.4532 | 0.22669 | 2.143 | 9.4532 | 0.22669 | 2.5052 | 11.0509 | 0.22669 | 0.05836%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 19 | 1 | 498.1496 | 90.1% | 9.186% | 0.7154% | 0.23622 | 0 | 0 | 0.23622 | 0 | 0.20506 | 9.4532 | 0.021692 | 0.20506 | 9.4532 | 0.021692 | 0.23971 | 11.0509 | 0.021692 | 0.04742%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 60 | 1 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 0.1483 | 0 | 0 | 0.1483 | 0 | 0.12874 | 9.4532 | 0.013618 | 0.12874 | 9.4532 | 0.013618 | 0.15049 | 11.0509 | 0.013618 | 0.01429%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 38 | 1 | 317.7725 | 50.82% | 48.53% | 0.6462% | 0.042501 | 0 | 0 | 0.042501 | 0 | 0.036894 | 9.4532 | 0.0039028 | 0.036894 | 9.4532 | 0.0039028 | 0.04313 | 11.0509 | 0.0039028 | 0.01337%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 145 | 2 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 0.21032 | 0 | 0 | 0.21032 | 0 | 0.18257 | 18.9065 | 0.0096564 | 0.18257 | 18.9065 | 0.0096564 | 0.21342 | 22.1019 | 0.0096564 | 0.01162%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 2 | 1890.633 | 91.06% | 8.49% | 0.4466% | 0.52172 | 0 | 0 | 0.52172 | 0 | 0.45289 | 18.9065 | 0.023954 | 0.45289 | 18.9065 | 0.023954 | 0.52943 | 22.1019 | 0.023954 | 0.0276%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 79 | 3 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 0.63015 | 0 | 0 | 0.63015 | 0 | 0.54701 | 28.3597 | 0.019288 | 0.54701 | 28.3597 | 0.019288 | 0.63946 | 33.1528 | 0.019288 | 0.03624%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 1 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 0.21306 | 0 | 0 | 0.21306 | 0 | 0.18495 | 9.4532 | 0.019565 | 0.18495 | 9.4532 | 0.019565 | 0.21621 | 11.0509 | 0.019565 | 0.01357%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 39 | 2 | 998.7912 | 96.62% | 2.787% | 0.5903% | 0.4949 | 0 | 0 | 0.4949 | 0 | 0.42961 | 18.9065 | 0.022723 | 0.42961 | 18.9065 | 0.022723 | 0.50221 | 22.1019 | 0.022723 | 0.04955%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 6 | 1 | 261.4279 | 97.06% | 2.12% | 0.8249% | 0.42288 | 0 | 0 | 0.42288 | 0 | 0.36709 | 9.4532 | 0.038832 | 0.36709 | 9.4532 | 0.038832 | 0.42913 | 11.0509 | 0.038832 | 0.1618%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 68 | 1 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 0.21206 | 0 | 0 | 0.21206 | 0 | 0.18408 | 9.4532 | 0.019473 | 0.18408 | 9.4532 | 0.019473 | 0.2152 | 11.0509 | 0.019473 | 0.0143%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 103 | 3 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 0.76953 | 0 | 0 | 0.76953 | 0 | 0.66801 | 28.3597 | 0.023555 | 0.66801 | 28.3597 | 0.023555 | 0.78091 | 33.1528 | 0.023555 | 0.0279%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 39 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 0.25869 | 0 | 0 | 0.25869 | 0 | 0.22456 | 9.4532 | 0.023755 | 0.22456 | 9.4532 | 0.023755 | 0.26251 | 11.0509 | 0.023755 | 0.0249%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 17 | 1 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 1.2564 | 0 | 0 | 1.2564 | 0 | 1.0906 | 9.4532 | 0.11537 | 1.0906 | 9.4532 | 0.11537 | 1.2749 | 11.0509 | 0.11537 | 0.05807%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 45 | 1 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 0.31977 | 0 | 0 | 0.31977 | 0 | 0.27758 | 9.4532 | 0.029364 | 0.27758 | 9.4532 | 0.029364 | 0.3245 | 11.0509 | 0.029364 | 0.02174%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 127 | 2 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 4.0935 | 0 | 0 | 4.0935 | 0 | 3.5534 | 18.9065 | 0.18795 | 3.5534 | 18.9065 | 0.18795 | 4.154 | 22.1019 | 0.18795 | 0.01558%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 75 | 4 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 3.5346 | 0 | 0 | 3.5346 | 0 | 3.0683 | 37.8129 | 0.081143 | 3.0683 | 37.8129 | 0.081143 | 3.5868 | 44.2037 | 0.081143 | 0.05302%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 30 | 3 | 484.0355 | 97.4% | 1.48% | 1.12% | 0.47145 | 0 | 0 | 0.47145 | 0 | 0.40925 | 28.3597 | 0.014431 | 0.40925 | 28.3597 | 0.014431 | 0.47842 | 33.1528 | 0.014431 | 0.0974%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 9 | 1 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 0.56304 | 0 | 0 | 0.56304 | 0 | 0.48875 | 9.4532 | 0.051702 | 0.48875 | 9.4532 | 0.051702 | 0.57136 | 11.0509 | 0.051702 | 0.1097%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 32 | 1 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 0.68385 | 0 | 0 | 0.68385 | 0 | 0.59362 | 9.4532 | 0.062796 | 0.59362 | 9.4532 | 0.062796 | 0.69395 | 11.0509 | 0.062796 | 0.03097%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 50 | 1 | 1721.769 | 85.69% | 14.07% | 0.2459% | 0.29507 | 0 | 0 | 0.29507 | 0 | 0.25614 | 9.4532 | 0.027095 | 0.25614 | 9.4532 | 0.027095 | 0.29943 | 11.0509 | 0.027095 | 0.01714%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 73 | 1 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 3.0391 | 0 | 0 | 3.0391 | 0 | 2.6381 | 9.4532 | 0.27907 | 2.6381 | 9.4532 | 0.27907 | 3.084 | 11.0509 | 0.27907 | 0.01359%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 72 | 1 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 1.7327 | 0 | 0 | 1.7327 | 0 | 1.5041 | 9.4532 | 0.15911 | 1.5041 | 9.4532 | 0.15911 | 1.7583 | 11.0509 | 0.15911 | 0.01364%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 1 | 19489.7064 | 99% | 0.9737% | 0.02962% | 3.3266 | 0 | 0 | 3.3266 | 0 | 2.8877 | 9.4532 | 0.30547 | 2.8877 | 9.4532 | 0.30547 | 3.3757 | 11.0509 | 0.30547 | 0.01707%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 67 | 2 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 4.1573 | 0 | 0 | 4.1573 | 0 | 3.6088 | 18.9065 | 0.19088 | 3.6088 | 18.9065 | 0.19088 | 4.2187 | 22.1019 | 0.19088 | 0.02961%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 126 | 2 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 0.28518 | 0 | 0 | 0.28518 | 0 | 0.24755 | 18.9065 | 0.013094 | 0.24755 | 18.9065 | 0.013094 | 0.28939 | 22.1019 | 0.013094 | 0.01416%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 84 | 1 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 0.28526 | 0 | 0 | 0.28526 | 0 | 0.24762 | 9.4532 | 0.026195 | 0.24762 | 9.4532 | 0.026195 | 0.28947 | 11.0509 | 0.026195 | 0.01046%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 71 | 2 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 2.9708 | 0 | 0 | 2.9708 | 0 | 2.5788 | 18.9065 | 0.1364 | 2.5788 | 18.9065 | 0.1364 | 3.0147 | 22.1019 | 0.1364 | 0.0278%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 68 | 3 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 1.5273 | 0 | 0 | 1.5273 | 0 | 1.3258 | 28.3597 | 0.046749 | 1.3258 | 28.3597 | 0.046749 | 1.5499 | 33.1528 | 0.046749 | 0.04176%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 70 | 3 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 0.56031 | 0 | 0 | 0.56031 | 0 | 0.48639 | 28.3597 | 0.017151 | 0.48639 | 28.3597 | 0.017151 | 0.56859 | 33.1528 | 0.017151 | 0.03895%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 48 | 1 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 2.0877 | 0 | 0 | 2.0877 | 0 | 1.8122 | 9.4532 | 0.1917 | 1.8122 | 9.4532 | 0.1917 | 2.1185 | 11.0509 | 0.1917 | 0.02064%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 29 | 3 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 2.1912 | 0 | 0 | 2.1912 | 0 | 1.9021 | 28.3597 | 0.06707 | 1.9021 | 28.3597 | 0.06707 | 2.2236 | 33.1528 | 0.06707 | 0.09966%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 81 | 1 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 0.20041 | 0 | 0 | 0.20041 | 0 | 0.17397 | 9.4532 | 0.018403 | 0.17397 | 9.4532 | 0.018403 | 0.20337 | 11.0509 | 0.018403 | 0.01041%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 155 | 7 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 1.4472 | 0 | 0 | 1.4472 | 0 | 1.2562 | 66.1726 | 0.018984 | 1.2562 | 66.1726 | 0.018984 | 1.4686 | 77.3565 | 0.018984 | 0.04036%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 2.1692 | 0 | 0 | 2.1692 | 0 | 1.883 | 9.4532 | 0.19919 | 1.883 | 9.4532 | 0.19919 | 2.2012 | 11.0509 | 0.19919 | 0.05877%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 77 | 1 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 0.39142 | 0 | 0 | 0.39142 | 0 | 0.33978 | 9.4532 | 0.035943 | 0.33978 | 9.4532 | 0.035943 | 0.3972 | 11.0509 | 0.035943 | 0.01197%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 93 | 3 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 0.84821 | 0 | 0 | 0.84821 | 0 | 0.7363 | 28.3597 | 0.025963 | 0.7363 | 28.3597 | 0.025963 | 0.86074 | 33.1528 | 0.025963 | 0.031%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 72 | 1 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 0.53024 | 0 | 0 | 0.53024 | 0 | 0.46029 | 9.4532 | 0.048691 | 0.46029 | 9.4532 | 0.048691 | 0.53808 | 11.0509 | 0.048691 | 0.01348%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 4 | 1 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 5.1134 | 0 | 0 | 5.1134 | 0 | 4.4387 | 9.4532 | 0.46955 | 4.4387 | 9.4532 | 0.46955 | 5.1889 | 11.0509 | 0.46955 | 0.2488%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 31 | 4 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 2.9049 | 0 | 0 | 2.9049 | 0 | 2.5217 | 37.8129 | 0.066688 | 2.5217 | 37.8129 | 0.066688 | 2.9478 | 44.2037 | 0.066688 | 0.125%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 137 | 3 | 7406.689 | 96.62% | 3.25% | 0.1263% | 1.5671 | 0 | 0 | 1.5671 | 0 | 1.3604 | 28.3597 | 0.047969 | 1.3604 | 28.3597 | 0.047969 | 1.5903 | 33.1528 | 0.047969 | 0.02116%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 212 | 4 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 14.8306 | 0 | 0 | 14.8306 | 0 | 12.8739 | 37.8129 | 0.34046 | 12.8739 | 37.8129 | 0.34046 | 15.0498 | 44.2037 | 0.34046 | 0.01873%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 13 | 1 | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 2.7638 | 0 | 0 | 2.7638 | 0 | 2.3992 | 9.4532 | 0.25379 | 2.3992 | 9.4532 | 0.25379 | 2.8046 | 11.0509 | 0.25379 | 0.07636%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 81 | 3 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 16.6442 | 0 | 0 | 16.6442 | 0 | 14.4483 | 28.3597 | 0.50947 | 14.4483 | 28.3597 | 0.50947 | 16.8902 | 33.1528 | 0.50947 | 0.0369%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 132 | 5 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 2.7021 | 0 | 0 | 2.7021 | 0 | 2.3456 | 47.2661 | 0.049625 | 2.3456 | 47.2661 | 0.049625 | 2.742 | 55.2547 | 0.049625 | 0.03638%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 1220 | 9 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 1.1964 | 0 | 0 | 1.1964 | 0 | 1.0386 | 85.0791 | 0.012207 | 1.0386 | 85.0791 | 0.012207 | 1.2141 | 99.4584 | 0.012207 | 0.007133%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 52 | 1 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 0.36541 | 0 | 0 | 0.36541 | 0 | 0.3172 | 9.4532 | 0.033554 | 0.3172 | 9.4532 | 0.033554 | 0.37081 | 11.0509 | 0.033554 | 0.01827%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 84 | 1 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 0.74734 | 0 | 0 | 0.74734 | 0 | 0.64874 | 9.4532 | 0.068627 | 0.64874 | 9.4532 | 0.068627 | 0.75839 | 11.0509 | 0.068627 | 0.0117%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 52 | 1 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 0.65245 | 0 | 0 | 0.65245 | 0 | 0.56637 | 9.4532 | 0.059913 | 0.56637 | 9.4532 | 0.059913 | 0.6621 | 11.0509 | 0.059913 | 0.01878%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 1 | 2730.9177 | 98.3% | 1.373% | 0.325% | 1.1186 | 0 | 0 | 1.1186 | 0 | 0.97098 | 9.4532 | 0.10271 | 0.97098 | 9.4532 | 0.10271 | 1.1351 | 11.0509 | 0.10271 | 0.04096%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 151 | 3 | 5142.095 | 98.68% | 0.901% | 0.4182% | 1.0081 | 0 | 0 | 1.0081 | 0 | 0.87512 | 28.3597 | 0.030858 | 0.87512 | 28.3597 | 0.030858 | 1.023 | 33.1528 | 0.030858 | 0.01961%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 50 | 1 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 0.49643 | 0 | 0 | 0.49643 | 0 | 0.43093 | 9.4532 | 0.045585 | 0.43093 | 9.4532 | 0.045585 | 0.50376 | 11.0509 | 0.045585 | 0.01986%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 23 | 1 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 0.69542 | 0 | 0 | 0.69542 | 0 | 0.60367 | 9.4532 | 0.063859 | 0.60367 | 9.4532 | 0.063859 | 0.7057 | 11.0509 | 0.063859 | 0.04234%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 57 | 6 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 3.1585 | 0 | 0 | 3.1585 | 0 | 2.7418 | 56.7194 | 0.048339 | 2.7418 | 56.7194 | 0.048339 | 3.2052 | 66.3056 | 0.048339 | 0.104%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 32 | 1 | 447.7794 | 94.96% | 4.349% | 0.694% | 0.13287 | 0 | 0 | 0.13287 | 0 | 0.11534 | 9.4532 | 0.012202 | 0.11534 | 9.4532 | 0.012202 | 0.13484 | 11.0509 | 0.012202 | 0.02967%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 79 | 2 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 0.50925 | 0 | 0 | 0.50925 | 0 | 0.44207 | 18.9065 | 0.023382 | 0.44207 | 18.9065 | 0.023382 | 0.51678 | 22.1019 | 0.023382 | 0.02175%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 3 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 1.1987 | 0 | 0 | 1.1987 | 0 | 1.0406 | 28.3597 | 0.036691 | 1.0406 | 28.3597 | 0.036691 | 1.2164 | 33.1528 | 0.036691 | 0.02904%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 40 | 3 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 3.6844 | 0 | 0 | 3.6844 | 0 | 3.1983 | 28.3597 | 0.11278 | 3.1983 | 28.3597 | 0.11278 | 3.7389 | 33.1528 | 0.11278 | 0.07459%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 14 | 1 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 2.7696 | 0 | 0 | 2.7696 | 0 | 2.4042 | 9.4532 | 0.25433 | 2.4042 | 9.4532 | 0.25433 | 2.8105 | 11.0509 | 0.25433 | 0.0633%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 48 | 1 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 4.8525 | 0 | 0 | 4.8525 | 0 | 4.2123 | 9.4532 | 0.44559 | 4.2123 | 9.4532 | 0.44559 | 4.9242 | 11.0509 | 0.44559 | 0.02049%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 48 | 2 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 3.9983 | 0 | 0 | 3.9983 | 0 | 3.4708 | 18.9065 | 0.18358 | 3.4708 | 18.9065 | 0.18358 | 4.0574 | 22.1019 | 0.18358 | 0.04114%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 37 | 1 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 0.74224 | 0 | 0 | 0.74224 | 0 | 0.64431 | 9.4532 | 0.068158 | 0.64431 | 9.4532 | 0.068158 | 0.7532 | 11.0509 | 0.068158 | 0.02629%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 25 | 1 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 0.89167 | 0 | 0 | 0.89167 | 0 | 0.77403 | 9.4532 | 0.08188 | 0.77403 | 9.4532 | 0.08188 | 0.90485 | 11.0509 | 0.08188 | 0.03944%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 51 | 4 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 4.1014 | 0 | 0 | 4.1014 | 0 | 3.5603 | 37.8129 | 0.094156 | 3.5603 | 37.8129 | 0.094156 | 4.162 | 44.2037 | 0.094156 | 0.07692%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 124 | 3 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 5.0506 | 0 | 0 | 5.0506 | 0 | 4.3842 | 28.3597 | 0.15459 | 4.3842 | 28.3597 | 0.15459 | 5.1252 | 33.1528 | 0.15459 | 0.0238%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 56 | 2 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 2.4209 | 0 | 0 | 2.4209 | 0 | 2.1015 | 18.9065 | 0.11115 | 2.1015 | 18.9065 | 0.11115 | 2.4567 | 22.1019 | 0.11115 | 0.03494%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 32 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 3.8777 | 0 | 0 | 3.8777 | 0 | 3.3661 | 9.4532 | 0.35608 | 3.3661 | 9.4532 | 0.35608 | 3.935 | 11.0509 | 0.35608 | 0.03051%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 62 | 1 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 4.5265 | 0 | 0 | 4.5265 | 0 | 3.9293 | 9.4532 | 0.41565 | 3.9293 | 9.4532 | 0.41565 | 4.5934 | 11.0509 | 0.41565 | 0.01602%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 165 | 2 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 3.7115 | 0 | 0 | 3.7115 | 0 | 3.2218 | 18.9065 | 0.17041 | 3.2218 | 18.9065 | 0.17041 | 3.7663 | 22.1019 | 0.17041 | 0.01201%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 182 | 8 | 65515.492 | 98.93% | 1.038% | 0.03019% | 28.4904 | 0 | 0 | 28.4904 | 0 | 24.7315 | 75.6258 | 0.32702 | 24.7315 | 75.6258 | 0.32702 | 28.9114 | 88.4075 | 0.32702 | 0.04349%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 23 | 1 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 0.46823 | 0 | 0 | 0.46823 | 0 | 0.40645 | 9.4532 | 0.042996 | 0.40645 | 9.4532 | 0.042996 | 0.47515 | 11.0509 | 0.042996 | 0.04194%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 72 | 2 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 1.7106 | 0 | 0 | 1.7106 | 0 | 1.485 | 18.9065 | 0.078542 | 1.485 | 18.9065 | 0.078542 | 1.7359 | 22.1019 | 0.078542 | 0.02729%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 18 | 2 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 0.41305 | 0 | 0 | 0.41305 | 0 | 0.35855 | 18.9065 | 0.018965 | 0.35855 | 18.9065 | 0.018965 | 0.41915 | 22.1019 | 0.018965 | 0.1097%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 73 | 2 | 4437.6588 | 97.91% | 1.769% | 0.321% | 1.1904 | 0 | 0 | 1.1904 | 0 | 1.0333 | 18.9065 | 0.054655 | 1.0333 | 18.9065 | 0.054655 | 1.208 | 22.1019 | 0.054655 | 0.02682%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 104 | 4 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 1.365 | 0 | 0 | 1.365 | 0 | 1.1849 | 37.8129 | 0.031337 | 1.1849 | 37.8129 | 0.031337 | 1.3852 | 44.2037 | 0.031337 | 0.03724%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 71 | 2 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 0.90204 | 0 | 0 | 0.90204 | 0 | 0.78303 | 18.9065 | 0.041416 | 0.78303 | 18.9065 | 0.041416 | 0.91537 | 22.1019 | 0.041416 | 0.02663%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 2 | 1438.4419 | 90% | 9.47% | 0.5268% | 1.0789 | 0 | 0 | 1.0789 | 0 | 0.93653 | 18.9065 | 0.049535 | 0.93653 | 18.9065 | 0.049535 | 1.0948 | 22.1019 | 0.049535 | 0.075%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 33 | 3 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 1.1441 | 0 | 0 | 1.1441 | 0 | 0.99314 | 28.3597 | 0.035019 | 0.99314 | 28.3597 | 0.035019 | 1.161 | 33.1528 | 0.035019 | 0.0841%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 99 | 4 | 3753.23 | 95.85% | 3.876% | 0.273% | 1.4535 | 0 | 0 | 1.4535 | 0 | 1.2618 | 37.8129 | 0.033369 | 1.2618 | 37.8129 | 0.033369 | 1.475 | 44.2037 | 0.033369 | 0.03873%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 40 | 3 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 1.326 | 0 | 0 | 1.326 | 0 | 1.151 | 28.3597 | 0.040587 | 1.151 | 28.3597 | 0.040587 | 1.3456 | 33.1528 | 0.040587 | 0.06585%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 26 | 1 | 4762.848 | 95.55% | 4.384% | 0.07015% | 1.7503 | 0 | 0 | 1.7503 | 0 | 1.5193 | 9.4532 | 0.16072 | 1.5193 | 9.4532 | 0.16072 | 1.7761 | 11.0509 | 0.16072 | 0.03675%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 138 | 1 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 0.24923 | 0 | 0 | 0.24923 | 0 | 0.21635 | 9.4532 | 0.022886 | 0.21635 | 9.4532 | 0.022886 | 0.25291 | 11.0509 | 0.022886 | 0.006919%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 245 | 6 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 3.3339 | 0 | 0 | 3.3339 | 0 | 2.894 | 56.7194 | 0.051023 | 2.894 | 56.7194 | 0.051023 | 3.3831 | 66.3056 | 0.051023 | 0.02403%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 229 | 6 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 1.4156 | 0 | 0 | 1.4156 | 0 | 1.2288 | 56.7194 | 0.021665 | 1.2288 | 56.7194 | 0.021665 | 1.4365 | 66.3056 | 0.021665 | 0.02541%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 3 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 4.3777 | 0 | 0 | 4.3777 | 0 | 3.8001 | 28.3597 | 0.134 | 3.8001 | 28.3597 | 0.134 | 4.4424 | 33.1528 | 0.134 | 0.03238%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 58 | 1 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 4.0243 | 0 | 0 | 4.0243 | 0 | 3.4934 | 9.4532 | 0.36954 | 3.4934 | 9.4532 | 0.36954 | 4.0838 | 11.0509 | 0.36954 | 0.01711%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 76 | 2 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 4.8671 | 0 | 0 | 4.8671 | 0 | 4.225 | 18.9065 | 0.22347 | 4.225 | 18.9065 | 0.22347 | 4.9391 | 22.1019 | 0.22347 | 0.02615%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 7 | 1 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 2.5232 | 0 | 0 | 2.5232 | 0 | 2.1903 | 9.4532 | 0.2317 | 2.1903 | 9.4532 | 0.2317 | 2.5605 | 11.0509 | 0.2317 | 0.1267%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 42 | 2 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 6.4084 | 0 | 0 | 6.4084 | 0 | 5.5629 | 18.9065 | 0.29423 | 5.5629 | 18.9065 | 0.29423 | 6.5031 | 22.1019 | 0.29423 | 0.04735%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 121 | 4 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 6.7238 | 0 | 0 | 6.7238 | 0 | 5.8367 | 37.8129 | 0.15436 | 5.8367 | 37.8129 | 0.15436 | 6.8231 | 44.2037 | 0.15436 | 0.03278%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 15 | 1 | 3653.654 | 88.54% | 11.39% | 0.07412% | 2.1565 | 0 | 0 | 2.1565 | 0 | 1.872 | 9.4532 | 0.19803 | 1.872 | 9.4532 | 0.19803 | 2.1884 | 11.0509 | 0.19803 | 0.05902%
2028 | 354 | CB 354 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 1 | 12.0695 | 99.46% | 0% | 0.538% | 0.12005 | 0 | 0 | 0.12005 | 0 | 0.10421 | 9.4532 | 0.011023 | 0.10421 | 9.4532 | 0.011023 | 0.12182 | 11.0509 | 0.011023 | 0.9946%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 64 | 2 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 2.3088 | 0 | 0 | 2.3088 | 0 | 2.0042 | 18.9065 | 0.10601 | 2.0042 | 18.9065 | 0.10601 | 2.3429 | 22.1019 | 0.10601 | 0.03078%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 1 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 0.84871 | 0 | 0 | 0.84871 | 0 | 0.73673 | 9.4532 | 0.077935 | 0.73673 | 9.4532 | 0.077935 | 0.86125 | 11.0509 | 0.077935 | 0.04996%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 83 | 6 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 8.0653 | 0 | 0 | 8.0653 | 0 | 7.0012 | 56.7194 | 0.12344 | 7.0012 | 56.7194 | 0.12344 | 8.1845 | 66.3056 | 0.12344 | 0.07145%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 140 | 4 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 4.4727 | 0 | 0 | 4.4727 | 0 | 3.8826 | 37.8129 | 0.10268 | 3.8826 | 37.8129 | 0.10268 | 4.5388 | 44.2037 | 0.10268 | 0.02793%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 4 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 3.8557 | 0 | 0 | 3.8557 | 0 | 3.347 | 37.8129 | 0.088516 | 3.347 | 37.8129 | 0.088516 | 3.9127 | 44.2037 | 0.088516 | 0.04148%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 11 | 2 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 9.2408 | 0 | 0 | 9.2408 | 0 | 8.0216 | 18.9065 | 0.42428 | 8.0216 | 18.9065 | 0.42428 | 9.3774 | 22.1019 | 0.42428 | 0.1812%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 3 | 1 | 878.9304 | 95.49% | 4.482% | 0.03213% | 2.7975 | 0 | 0 | 2.7975 | 0 | 2.4284 | 9.4532 | 0.25689 | 2.4284 | 9.4532 | 0.25689 | 2.8388 | 11.0509 | 0.25689 | 0.3183%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 84 | 2 | 16869.708 | 98.79% | 1.184% | 0.02933% | 3.9679 | 0 | 0 | 3.9679 | 0 | 3.4444 | 18.9065 | 0.18218 | 3.4444 | 18.9065 | 0.18218 | 4.0265 | 22.1019 | 0.18218 | 0.02352%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 116 | 2 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 2.9741 | 0 | 0 | 2.9741 | 0 | 2.5817 | 18.9065 | 0.13655 | 2.5817 | 18.9065 | 0.13655 | 3.0181 | 22.1019 | 0.13655 | 0.01681%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 116 | 2 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 1.7454 | 0 | 0 | 1.7454 | 0 | 1.5151 | 18.9065 | 0.080139 | 1.5151 | 18.9065 | 0.080139 | 1.7712 | 22.1019 | 0.080139 | 0.01673%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 99 | 1 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 3.7448 | 0 | 0 | 3.7448 | 0 | 3.2507 | 9.4532 | 0.34387 | 3.2507 | 9.4532 | 0.34387 | 3.8001 | 11.0509 | 0.34387 | 0.009959%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 65 | 2 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 0.85113 | 0 | 0 | 0.85113 | 0 | 0.73884 | 18.9065 | 0.039079 | 0.73884 | 18.9065 | 0.039079 | 0.86371 | 22.1019 | 0.039079 | 0.02713%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 90 | 1 | 6370.0414 | 98.47% | 1.262% | 0.272% | 0.69692 | 0 | 0 | 0.69692 | 0 | 0.60498 | 9.4532 | 0.063997 | 0.60498 | 9.4532 | 0.063997 | 0.70722 | 11.0509 | 0.063997 | 0.01094%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 15 | 1 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 2.2856 | 0 | 0 | 2.2856 | 0 | 1.9841 | 9.4532 | 0.20988 | 1.9841 | 9.4532 | 0.20988 | 2.3194 | 11.0509 | 0.20988 | 0.06497%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 6 | 1 | 582.1633 | 91.34% | 8.391% | 0.2732% | 0.8862 | 0 | 0 | 0.8862 | 0 | 0.76928 | 9.4532 | 0.081378 | 0.76928 | 9.4532 | 0.081378 | 0.8993 | 11.0509 | 0.081378 | 0.1522%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 27 | 1 | 4750.1268 | 98% | 1.916% | 0.08125% | 1.7242 | 0 | 0 | 1.7242 | 0 | 1.4967 | 9.4532 | 0.15833 | 1.4967 | 9.4532 | 0.15833 | 1.7496 | 11.0509 | 0.15833 | 0.0363%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 26 | 1 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 2.0279 | 0 | 0 | 2.0279 | 0 | 1.7603 | 9.4532 | 0.18622 | 1.7603 | 9.4532 | 0.18622 | 2.0579 | 11.0509 | 0.18622 | 0.03791%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 31 | 1 | 852.9261 | 84.92% | 14.72% | 0.3553% | 0.23366 | 0 | 0 | 0.23366 | 0 | 0.20283 | 9.4532 | 0.021456 | 0.20283 | 9.4532 | 0.021456 | 0.23711 | 11.0509 | 0.021456 | 0.0274%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 161 | 3 | 11572.221 | 88.48% | 11.4% | 0.1243% | 1.9078 | 0 | 0 | 1.9078 | 0 | 1.6561 | 28.3597 | 0.058397 | 1.6561 | 28.3597 | 0.058397 | 1.936 | 33.1528 | 0.058397 | 0.01649%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 14 | 1 | 704.6091 | 96.62% | 3.132% | 0.2514% | 0.48626 | 0 | 0 | 0.48626 | 0 | 0.42211 | 9.4532 | 0.044652 | 0.42211 | 9.4532 | 0.044652 | 0.49345 | 11.0509 | 0.044652 | 0.06901%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 102 | 1 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 0.32689 | 0 | 0 | 0.32689 | 0 | 0.28376 | 9.4532 | 0.030017 | 0.28376 | 9.4532 | 0.030017 | 0.33172 | 11.0509 | 0.030017 | 0.009575%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 90 | 2 | 571.2373 | 70.71% | 27.93% | 1.361% | 0.089758 | 0 | 0 | 0.089758 | 0 | 0.077916 | 18.9065 | 0.0041211 | 0.077916 | 18.9065 | 0.0041211 | 0.091085 | 22.1019 | 0.0041211 | 0.01571%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 43 | 1 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 0.33086 | 0 | 0 | 0.33086 | 0 | 0.28721 | 9.4532 | 0.030382 | 0.28721 | 9.4532 | 0.030382 | 0.33575 | 11.0509 | 0.030382 | 0.02063%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 116 | 4 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 3.5041 | 0 | 0 | 3.5041 | 0 | 3.0418 | 37.8129 | 0.080443 | 3.0418 | 37.8129 | 0.080443 | 3.5559 | 44.2037 | 0.080443 | 0.033%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 65 | 2 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 0.46058 | 0 | 0 | 0.46058 | 0 | 0.39981 | 18.9065 | 0.021147 | 0.39981 | 18.9065 | 0.021147 | 0.46738 | 22.1019 | 0.021147 | 0.02607%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 91 | 3 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 1.0616 | 0 | 0 | 1.0616 | 0 | 0.92156 | 28.3597 | 0.032495 | 0.92156 | 28.3597 | 0.032495 | 1.0773 | 33.1528 | 0.032495 | 0.02886%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 156 | 2 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 0.49947 | 0 | 0 | 0.49947 | 0 | 0.43357 | 18.9065 | 0.022932 | 0.43357 | 18.9065 | 0.022932 | 0.50685 | 22.1019 | 0.022932 | 0.0113%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 5 | 520.639 | 76.18% | 22.78% | 1.038% | 0.40474 | 0 | 0 | 0.40474 | 0 | 0.35134 | 47.2661 | 0.0074333 | 0.35134 | 47.2661 | 0.0074333 | 0.41072 | 55.2547 | 0.0074333 | 0.07774%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 224 | 7 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 2.6085 | 0 | 0 | 2.6085 | 0 | 2.2643 | 66.1726 | 0.034219 | 2.2643 | 66.1726 | 0.034219 | 2.647 | 77.3565 | 0.034219 | 0.02865%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 106 | 3 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 1.4926 | 0 | 0 | 1.4926 | 0 | 1.2956 | 28.3597 | 0.045686 | 1.2956 | 28.3597 | 0.045686 | 1.5146 | 33.1528 | 0.045686 | 0.02644%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 147 | 7 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 2.9 | 0 | 0 | 2.9 | 0 | 2.5174 | 66.1726 | 0.038043 | 2.5174 | 66.1726 | 0.038043 | 2.9429 | 77.3565 | 0.038043 | 0.04309%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 22 | 3 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 1.9776 | 0 | 0 | 1.9776 | 0 | 1.7167 | 28.3597 | 0.060532 | 1.7167 | 28.3597 | 0.060532 | 2.0068 | 33.1528 | 0.060532 | 0.1322%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 34 | 1 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 1.5283 | 0 | 0 | 1.5283 | 0 | 1.3266 | 9.4532 | 0.14034 | 1.3266 | 9.4532 | 0.14034 | 1.5509 | 11.0509 | 0.14034 | 0.02905%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 53 | 2 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 6.2773 | 0 | 0 | 6.2773 | 0 | 5.4491 | 18.9065 | 0.28822 | 5.4491 | 18.9065 | 0.28822 | 6.3701 | 22.1019 | 0.28822 | 0.0375%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 47 | 1 | 2978.814 | 97.34% | 2.471% | 0.184% | 0.61696 | 0 | 0 | 0.61696 | 0 | 0.53556 | 9.4532 | 0.056654 | 0.53556 | 9.4532 | 0.056654 | 0.62608 | 11.0509 | 0.056654 | 0.02071%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 129 | 5 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 0.98929 | 0 | 0 | 0.98929 | 0 | 0.85877 | 47.2661 | 0.018169 | 0.85877 | 47.2661 | 0.018169 | 1.0039 | 55.2547 | 0.018169 | 0.0375%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 84 | 1 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 0.37683 | 0 | 0 | 0.37683 | 0 | 0.32711 | 9.4532 | 0.034604 | 0.32711 | 9.4532 | 0.034604 | 0.3824 | 11.0509 | 0.034604 | 0.01104%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 53 | 1 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 1.2342 | 0 | 0 | 1.2342 | 0 | 1.0713 | 9.4532 | 0.11333 | 1.0713 | 9.4532 | 0.11333 | 1.2524 | 11.0509 | 0.11333 | 0.01825%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 49 | 2 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 4.4795 | 0 | 0 | 4.4795 | 0 | 3.8885 | 18.9065 | 0.20567 | 3.8885 | 18.9065 | 0.20567 | 4.5457 | 22.1019 | 0.20567 | 0.03947%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 87 | 3 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 2.8588 | 0 | 0 | 2.8588 | 0 | 2.4817 | 28.3597 | 0.087507 | 2.4817 | 28.3597 | 0.087507 | 2.9011 | 33.1528 | 0.087507 | 0.03372%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 25 | 1 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 2.22 | 0 | 0 | 2.22 | 0 | 1.9271 | 9.4532 | 0.20386 | 1.9271 | 9.4532 | 0.20386 | 2.2528 | 11.0509 | 0.20386 | 0.03951%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 42 | 1 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 2.8966 | 0 | 0 | 2.8966 | 0 | 2.5144 | 9.4532 | 0.26599 | 2.5144 | 9.4532 | 0.26599 | 2.9394 | 11.0509 | 0.26599 | 0.02366%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 37 | 1 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 2.4127 | 0 | 0 | 2.4127 | 0 | 2.0944 | 9.4532 | 0.22156 | 2.0944 | 9.4532 | 0.22156 | 2.4484 | 11.0509 | 0.22156 | 0.02677%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 46 | 1 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 1.1861 | 0 | 0 | 1.1861 | 0 | 1.0296 | 9.4532 | 0.10891 | 1.0296 | 9.4532 | 0.10891 | 1.2036 | 11.0509 | 0.10891 | 0.02169%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 114 | 5 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 4.9524 | 0 | 0 | 4.9524 | 0 | 4.299 | 47.2661 | 0.090954 | 4.299 | 47.2661 | 0.090954 | 5.0256 | 55.2547 | 0.090954 | 0.04376%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 89 | 3 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 4.5749 | 0 | 0 | 4.5749 | 0 | 3.9713 | 28.3597 | 0.14003 | 3.9713 | 28.3597 | 0.14003 | 4.6425 | 33.1528 | 0.14003 | 0.03337%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 84 | 2 | 8801.877 | 98.2% | 1.718% | 0.0819% | 2.058 | 0 | 0 | 2.058 | 0 | 1.7865 | 18.9065 | 0.094489 | 1.7865 | 18.9065 | 0.094489 | 2.0884 | 22.1019 | 0.094489 | 0.02338%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 283 | 4 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 5.6516 | 0 | 0 | 5.6516 | 0 | 4.906 | 37.8129 | 0.12974 | 4.906 | 37.8129 | 0.12974 | 5.7351 | 44.2037 | 0.12974 | 0.014%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 4 | 1 | 67.245 | 99.24% | 0% | 0.7576% | 0.16684 | 0 | 0 | 0.16684 | 0 | 0.14483 | 9.4532 | 0.01532 | 0.14483 | 9.4532 | 0.01532 | 0.1693 | 11.0509 | 0.01532 | 0.2481%
2028 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 3 | 1 | 417.7025 | 78.37% | 21.49% | 0.1463% | 1.0911 | 0 | 0 | 1.0911 | 0 | 0.94718 | 9.4532 | 0.1002 | 0.94718 | 9.4532 | 0.1002 | 1.1073 | 11.0509 | 0.1002 | 0.2612%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 92 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 1.9499 | 0 | 0 | 1.9499 | 0 | 1.6926 | 9.4532 | 0.17905 | 1.6926 | 9.4532 | 0.17905 | 1.9787 | 11.0509 | 0.17905 | 0.01039%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 124 | 2 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 4.1271 | 0 | 0 | 4.1271 | 0 | 3.5826 | 18.9065 | 0.18949 | 3.5826 | 18.9065 | 0.18949 | 4.1881 | 22.1019 | 0.18949 | 0.01603%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 74 | 1 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 3.6281 | 0 | 0 | 3.6281 | 0 | 3.1495 | 9.4532 | 0.33316 | 3.1495 | 9.4532 | 0.33316 | 3.6817 | 11.0509 | 0.33316 | 0.0134%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 2 | 1 | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 31.7347 | 0 | 0 | 31.7347 | 0 | 27.5478 | 9.4532 | 2.9141 | 27.5478 | 9.4532 | 2.9141 | 32.2037 | 11.0509 | 2.9141 | 0.4999%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 76 | 1 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 2.0398 | 0 | 0 | 2.0398 | 0 | 1.7707 | 9.4532 | 0.18731 | 1.7707 | 9.4532 | 0.18731 | 2.07 | 11.0509 | 0.18731 | 0.01294%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 28 | 1 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 4.1511 | 0 | 0 | 4.1511 | 0 | 3.6034 | 9.4532 | 0.38118 | 3.6034 | 9.4532 | 0.38118 | 4.2124 | 11.0509 | 0.38118 | 0.03529%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 109 | 1 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 0.49191 | 0 | 0 | 0.49191 | 0 | 0.42701 | 9.4532 | 0.045171 | 0.42701 | 9.4532 | 0.045171 | 0.49918 | 11.0509 | 0.045171 | 0.00883%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 146 | 1 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2.7946 | 0 | 0 | 2.7946 | 0 | 2.4259 | 9.4532 | 0.25662 | 2.4259 | 9.4532 | 0.25662 | 2.8359 | 11.0509 | 0.25662 | 0.006773%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 3 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 7.0602 | 0 | 0 | 7.0602 | 0 | 6.1288 | 28.3597 | 0.21611 | 6.1288 | 28.3597 | 0.21611 | 7.1646 | 33.1528 | 0.21611 | 0.03129%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 126 | 3 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 13.0597 | 0 | 0 | 13.0597 | 0 | 11.3367 | 28.3597 | 0.39975 | 11.3367 | 28.3597 | 0.39975 | 13.2527 | 33.1528 | 0.39975 | 0.02364%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 11 | 2 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 23.4859 | 0 | 0 | 23.4859 | 0 | 20.3873 | 18.9065 | 1.0783 | 20.3873 | 18.9065 | 1.0783 | 23.833 | 22.1019 | 1.0783 | 0.1812%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 100 | 2 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 3.0011 | 0 | 0 | 3.0011 | 0 | 2.6051 | 18.9065 | 0.13779 | 2.6051 | 18.9065 | 0.13779 | 3.0454 | 22.1019 | 0.13779 | 0.01981%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 189 | 4 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 5.9629 | 0 | 0 | 5.9629 | 0 | 5.1762 | 37.8129 | 0.13689 | 5.1762 | 37.8129 | 0.13689 | 6.051 | 44.2037 | 0.13689 | 0.02093%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 28 | 1 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 2.8473 | 0 | 0 | 2.8473 | 0 | 2.4717 | 9.4532 | 0.26146 | 2.4717 | 9.4532 | 0.26146 | 2.8894 | 11.0509 | 0.26146 | 0.03552%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 11 | 1 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 3.9368 | 0 | 0 | 3.9368 | 0 | 3.4174 | 9.4532 | 0.3615 | 3.4174 | 9.4532 | 0.3615 | 3.9949 | 11.0509 | 0.3615 | 0.09047%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 103 | 2 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 2.1656 | 0 | 0 | 2.1656 | 0 | 1.8799 | 18.9065 | 0.09943 | 1.8799 | 18.9065 | 0.09943 | 2.1976 | 22.1019 | 0.09943 | 0.01922%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 27 | 1 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 4.2224 | 0 | 0 | 4.2224 | 0 | 3.6653 | 9.4532 | 0.38773 | 3.6653 | 9.4532 | 0.38773 | 4.2848 | 11.0509 | 0.38773 | 0.03685%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 106 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 2.1729 | 0 | 0 | 2.1729 | 0 | 1.8862 | 9.4532 | 0.19953 | 1.8862 | 9.4532 | 0.19953 | 2.205 | 11.0509 | 0.19953 | 0.009282%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 1 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 1.5371 | 0 | 0 | 1.5371 | 0 | 1.3343 | 9.4532 | 0.14115 | 1.3343 | 9.4532 | 0.14115 | 1.5598 | 11.0509 | 0.14115 | 0.0168%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 104 | 3 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 0.94401 | 0 | 0 | 0.94401 | 0 | 0.81946 | 28.3597 | 0.028895 | 0.81946 | 28.3597 | 0.028895 | 0.95796 | 33.1528 | 0.028895 | 0.02703%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 29 | 1 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 2.4397 | 0 | 0 | 2.4397 | 0 | 2.1178 | 9.4532 | 0.22403 | 2.1178 | 9.4532 | 0.22403 | 2.4757 | 11.0509 | 0.22403 | 0.03433%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 9 | 1 | 387.8494 | 99.7% | 0% | 0.3041% | 0.42963 | 0 | 0 | 0.42963 | 0 | 0.37295 | 9.4532 | 0.039452 | 0.37295 | 9.4532 | 0.039452 | 0.43598 | 11.0509 | 0.039452 | 0.1108%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 95 | 2 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 7.3287 | 0 | 0 | 7.3287 | 0 | 6.3618 | 18.9065 | 0.33649 | 6.3618 | 18.9065 | 0.33649 | 7.437 | 22.1019 | 0.33649 | 0.02085%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 43 | 3 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 13.0946 | 0 | 0 | 13.0946 | 0 | 11.367 | 28.3597 | 0.40082 | 11.367 | 28.3597 | 0.40082 | 13.2882 | 33.1528 | 0.40082 | 0.06956%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 32 | 1 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 1.5717 | 0 | 0 | 1.5717 | 0 | 1.3644 | 9.4532 | 0.14433 | 1.3644 | 9.4532 | 0.14433 | 1.595 | 11.0509 | 0.14433 | 0.03099%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 80 | 1 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 1.1361 | 0 | 0 | 1.1361 | 0 | 0.98623 | 9.4532 | 0.10433 | 0.98623 | 9.4532 | 0.10433 | 1.1529 | 11.0509 | 0.10433 | 0.012%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 64 | 1 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 0.57427 | 0 | 0 | 0.57427 | 0 | 0.49851 | 9.4532 | 0.052734 | 0.49851 | 9.4532 | 0.052734 | 0.58276 | 11.0509 | 0.052734 | 0.01522%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 21 | 1 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 2.3976 | 0 | 0 | 2.3976 | 0 | 2.0813 | 9.4532 | 0.22017 | 2.0813 | 9.4532 | 0.22017 | 2.4331 | 11.0509 | 0.22017 | 0.04679%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 46 | 4 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 10.1307 | 0 | 0 | 10.1307 | 0 | 8.7941 | 37.8129 | 0.23257 | 8.7941 | 37.8129 | 0.23257 | 10.2804 | 44.2037 | 0.23257 | 0.08573%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 5 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 3.8424 | 0 | 0 | 3.8424 | 0 | 3.3355 | 47.2661 | 0.070568 | 3.3355 | 47.2661 | 0.070568 | 3.8992 | 55.2547 | 0.070568 | 0.05803%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 124 | 3 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 6.0729 | 0 | 0 | 6.0729 | 0 | 5.2717 | 28.3597 | 0.18589 | 5.2717 | 28.3597 | 0.18589 | 6.1626 | 33.1528 | 0.18589 | 0.02399%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 119 | 2 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 4.7011 | 0 | 0 | 4.7011 | 0 | 4.0808 | 18.9065 | 0.21584 | 4.0808 | 18.9065 | 0.21584 | 4.7705 | 22.1019 | 0.21584 | 0.01655%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 103 | 4 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 10.2802 | 0 | 0 | 10.2802 | 0 | 8.9239 | 37.8129 | 0.236 | 8.9239 | 37.8129 | 0.236 | 10.4322 | 44.2037 | 0.236 | 0.03851%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 68 | 1 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 2.2869 | 0 | 0 | 2.2869 | 0 | 1.9852 | 9.4532 | 0.21 | 1.9852 | 9.4532 | 0.21 | 2.3207 | 11.0509 | 0.21 | 0.01433%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 24 | 1 | 919.3728 | 93.93% | 5.62% | 0.4487% | 0.35982 | 0 | 0 | 0.35982 | 0 | 0.31235 | 9.4532 | 0.033042 | 0.31235 | 9.4532 | 0.033042 | 0.36514 | 11.0509 | 0.033042 | 0.03914%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 4 | 1 | 140.8367 | 88.02% | 11.68% | 0.2956% | 0.30991 | 0 | 0 | 0.30991 | 0 | 0.26902 | 9.4532 | 0.028458 | 0.26902 | 9.4532 | 0.028458 | 0.31449 | 11.0509 | 0.028458 | 0.22%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 81 | 4 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 2.902 | 0 | 0 | 2.902 | 0 | 2.5192 | 37.8129 | 0.066622 | 2.5192 | 37.8129 | 0.066622 | 2.9449 | 44.2037 | 0.066622 | 0.0492%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 63 | 1 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 0.78923 | 0 | 0 | 0.78923 | 0 | 0.6851 | 9.4532 | 0.072472 | 0.6851 | 9.4532 | 0.072472 | 0.80089 | 11.0509 | 0.072472 | 0.01581%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 93 | 1 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 0.45697 | 0 | 0 | 0.45697 | 0 | 0.39668 | 9.4532 | 0.041963 | 0.39668 | 9.4532 | 0.041963 | 0.46373 | 11.0509 | 0.041963 | 0.009798%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 16 | 1 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 6.3033 | 0 | 0 | 6.3033 | 0 | 5.4717 | 9.4532 | 0.57881 | 5.4717 | 9.4532 | 0.57881 | 6.3964 | 11.0509 | 0.57881 | 0.06236%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 43 | 1 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 1.3993 | 0 | 0 | 1.3993 | 0 | 1.2147 | 9.4532 | 0.1285 | 1.2147 | 9.4532 | 0.1285 | 1.42 | 11.0509 | 0.1285 | 0.02276%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 64 | 3 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 3.9328 | 0 | 0 | 3.9328 | 0 | 3.4139 | 28.3597 | 0.12038 | 3.4139 | 28.3597 | 0.12038 | 3.9909 | 33.1528 | 0.12038 | 0.04522%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 39 | 1 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 0.74901 | 0 | 0 | 0.74901 | 0 | 0.65019 | 9.4532 | 0.068779 | 0.65019 | 9.4532 | 0.068779 | 0.76008 | 11.0509 | 0.068779 | 0.0251%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 79 | 2 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 1.3468 | 0 | 0 | 1.3468 | 0 | 1.1691 | 18.9065 | 0.061836 | 1.1691 | 18.9065 | 0.061836 | 1.3667 | 22.1019 | 0.061836 | 0.02134%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 92 | 3 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 2.1474 | 0 | 0 | 2.1474 | 0 | 1.864 | 28.3597 | 0.065729 | 1.864 | 28.3597 | 0.065729 | 2.1791 | 33.1528 | 0.065729 | 0.03231%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 16 | 1 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 1.1628 | 0 | 0 | 1.1628 | 0 | 1.0094 | 9.4532 | 0.10678 | 1.0094 | 9.4532 | 0.10678 | 1.18 | 11.0509 | 0.10678 | 0.0619%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 30 | 1 | 1438.3629 | 99.75% | 0% | 0.2509% | 0.47825 | 0 | 0 | 0.47825 | 0 | 0.41515 | 9.4532 | 0.043917 | 0.41515 | 9.4532 | 0.043917 | 0.48532 | 11.0509 | 0.043917 | 0.03325%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 51 | 1 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 3.1063 | 0 | 0 | 3.1063 | 0 | 2.6965 | 9.4532 | 0.28525 | 2.6965 | 9.4532 | 0.28525 | 3.1522 | 11.0509 | 0.28525 | 0.01943%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 38 | 2 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 4.2623 | 0 | 0 | 4.2623 | 0 | 3.7 | 18.9065 | 0.1957 | 3.7 | 18.9065 | 0.1957 | 4.3253 | 22.1019 | 0.1957 | 0.05223%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 127 | 4 | 37077.302 | 99.36% | 0.615% | 0.02874% | 11.6027 | 0 | 0 | 11.6027 | 0 | 10.0719 | 37.8129 | 0.26636 | 10.0719 | 37.8129 | 0.26636 | 11.7742 | 44.2037 | 0.26636 | 0.03129%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 53 | 2 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 0.61454 | 0 | 0 | 0.61454 | 0 | 0.53346 | 18.9065 | 0.028216 | 0.53346 | 18.9065 | 0.028216 | 0.62362 | 22.1019 | 0.028216 | 0.02977%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 90 | 4 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 1.5732 | 0 | 0 | 1.5732 | 0 | 1.3656 | 37.8129 | 0.036115 | 1.3656 | 37.8129 | 0.036115 | 1.5964 | 44.2037 | 0.036115 | 0.0423%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 29 | 1 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 0.51681 | 0 | 0 | 0.51681 | 0 | 0.44862 | 9.4532 | 0.047457 | 0.44862 | 9.4532 | 0.047457 | 0.52445 | 11.0509 | 0.047457 | 0.03374%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 32 | 1 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 1.5768 | 0 | 0 | 1.5768 | 0 | 1.3688 | 9.4532 | 0.14479 | 1.3688 | 9.4532 | 0.14479 | 1.6001 | 11.0509 | 0.14479 | 0.0308%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 109 | 1 | 6915.6819 | 99% | 0.9206% | 0.07911% | 0.62812 | 0 | 0 | 0.62812 | 0 | 0.54525 | 9.4532 | 0.057679 | 0.54525 | 9.4532 | 0.057679 | 0.63741 | 11.0509 | 0.057679 | 0.009083%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 66 | 3 | 3027.5479 | 94.73% | 5.109% | 0.164% | 1.3036 | 0 | 0 | 1.3036 | 0 | 1.1316 | 28.3597 | 0.039902 | 1.1316 | 28.3597 | 0.039902 | 1.3229 | 33.1528 | 0.039902 | 0.04306%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 65 | 1 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 1.5906 | 0 | 0 | 1.5906 | 0 | 1.3808 | 9.4532 | 0.14606 | 1.3808 | 9.4532 | 0.14606 | 1.6141 | 11.0509 | 0.14606 | 0.01512%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 30 | 1 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 3.0921 | 0 | 0 | 3.0921 | 0 | 2.6842 | 9.4532 | 0.28394 | 2.6842 | 9.4532 | 0.28394 | 3.1378 | 11.0509 | 0.28394 | 0.03311%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 85 | 3 | 6920.124 | 97.57% | 2.306% | 0.1195% | 2.3832 | 0 | 0 | 2.3832 | 0 | 2.0687 | 28.3597 | 0.072946 | 2.0687 | 28.3597 | 0.072946 | 2.4184 | 33.1528 | 0.072946 | 0.03444%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 27 | 1 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 2.1873 | 0 | 0 | 2.1873 | 0 | 1.8988 | 9.4532 | 0.20086 | 1.8988 | 9.4532 | 0.20086 | 2.2197 | 11.0509 | 0.20086 | 0.03678%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 128 | 6 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 1.4767 | 0 | 0 | 1.4767 | 0 | 1.2819 | 56.7194 | 0.0226 | 1.2819 | 56.7194 | 0.0226 | 1.4985 | 66.3056 | 0.0226 | 0.04393%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 20 | 3 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 5.6448 | 0 | 0 | 5.6448 | 0 | 4.9001 | 28.3597 | 0.17278 | 4.9001 | 28.3597 | 0.17278 | 5.7282 | 33.1528 | 0.17278 | 0.1492%

## Trim and Removal
Prune and Removel - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 91336 | 2834578.5099 | 27614.6575 | 0.9742% | 26342.5072 | 30054.5835 | 0.87649 | 26342.5072 | 30054.5835 | 0.87649 | 27750.0235 | 31660.4412 | 0.87649
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 91336 | 2834578.5099 | 27614.6575 | 0.9742% | 25128.9622 | 28670.0308 | 0.87649 | 25128.9622 | 28670.0308 | 0.87649 | 27886.053 | 31815.6394 | 0.87649
[9 empty] | Capital Cost only in Year 0 | 0.34495 | K$/tree | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [8 empty] | 60.0114 | 2028 | 91336 | 2834578.5099 | 27614.6575 | 0.9742% | 23971.3227 | 27349.2616 | 0.87649 | 23971.3227 | 27349.2616 | 0.87649 | 28022.7493 | 31971.5984 | 0.87649
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 274008 | 8503735.5297 | 82843.9725 | 0.9742% | 75442.792 | 86073.8759 | 0.87649 | 75442.792 | 86073.8759 | 0.87649 | 83658.8258 | 95447.679 | 0.87649
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 1% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 5 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.1068 | 1.6453 | 0.67272 | 1.1068 | 1.6453 | 0.67272 | 1.1659 | 1.7332 | 0.67272 | 0.9903%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 34 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.869 | 11.1879 | 0.34582 | 3.869 | 11.1879 | 0.34582 | 4.0757 | 11.7857 | 0.34582 | 0.9915%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 620 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 36.8178 | 204.0142 | 0.18047 | 36.8178 | 204.0142 | 0.18047 | 38.785 | 214.915 | 0.18047 | 0.9141%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 510 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 332.0782 | 167.8181 | 1.9788 | 332.0782 | 167.8181 | 1.9788 | 349.8216 | 176.7849 | 1.9788 | 0.9902%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 72 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 66.0788 | 23.692 | 2.7891 | 66.0788 | 23.692 | 2.7891 | 69.6095 | 24.9579 | 2.7891 | 0.9818%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 230 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 179.0433 | 75.6827 | 2.3657 | 179.0433 | 75.6827 | 2.3657 | 188.6098 | 79.7265 | 2.3657 | 0.997%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 99 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 47.787 | 32.5765 | 1.4669 | 47.787 | 32.5765 | 1.4669 | 50.3403 | 34.3171 | 1.4669 | 0.9951%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 32 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 13.1718 | 10.5298 | 1.2509 | 13.1718 | 10.5298 | 1.2509 | 13.8756 | 11.0924 | 1.2509 | 0.9958%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 20 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 7.5473 | 6.5811 | 1.1468 | 7.5473 | 6.5811 | 1.1468 | 7.9506 | 6.9327 | 1.1468 | 0.996%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 145 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 93.1374 | 47.713 | 1.952 | 93.1374 | 47.713 | 1.952 | 98.1139 | 50.2624 | 1.952 | 0.9962%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 5 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.5753 | 1.6453 | 3.9965 | 6.5753 | 1.6453 | 3.9965 | 6.9266 | 1.7332 | 3.9965 | 0.9922%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 57 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 47.9789 | 18.7561 | 2.558 | 47.9789 | 18.7561 | 2.558 | 50.5425 | 19.7583 | 2.558 | 0.9916%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 198 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 27.3593 | 65.1529 | 0.41992 | 27.3593 | 65.1529 | 0.41992 | 28.8211 | 68.6341 | 0.41992 | 0.9924%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 886 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 86.7029 | 291.5429 | 0.29739 | 86.7029 | 291.5429 | 0.29739 | 91.3356 | 307.1204 | 0.29739 | 0.9598%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 587 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 35.0604 | 193.1554 | 0.18151 | 35.0604 | 193.1554 | 0.18151 | 36.9337 | 203.4759 | 0.18151 | 0.9739%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 101 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.8971 | 33.2346 | 0.14735 | 4.8971 | 33.2346 | 0.14735 | 5.1588 | 35.0103 | 0.14735 | 0.8768%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 14 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 48.0307 | 4.6068 | 10.4261 | 48.0307 | 4.6068 | 10.4261 | 50.597 | 4.8529 | 10.4261 | 0.9826%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 117 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 111.1363 | 38.4995 | 2.8867 | 111.1363 | 38.4995 | 2.8867 | 117.0745 | 40.5565 | 2.8867 | 0.9858%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 50 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 20.4052 | 16.4528 | 1.2402 | 20.4052 | 16.4528 | 1.2402 | 21.4955 | 17.3319 | 1.2402 | 0.9945%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 307 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 62.3119 | 101.0199 | 0.61683 | 62.3119 | 101.0199 | 0.61683 | 65.6414 | 106.4176 | 0.61683 | 0.9866%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 298 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 239.4495 | 98.0584 | 2.4419 | 239.4495 | 98.0584 | 2.4419 | 252.2436 | 103.2978 | 2.4419 | 0.9914%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 474 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 266.8268 | 155.9722 | 1.7107 | 266.8268 | 155.9722 | 1.7107 | 281.0837 | 164.306 | 1.7107 | 0.9849%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 159 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 252.5213 | 52.3198 | 4.8265 | 252.5213 | 52.3198 | 4.8265 | 266.0138 | 55.1153 | 4.8265 | 0.9916%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 740 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 148.3449 | 243.5008 | 0.60922 | 148.3449 | 243.5008 | 0.60922 | 156.2711 | 256.5114 | 0.60922 | 0.9745%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 49 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14883 | 16.1237 | 0.0092306 | 0.14883 | 16.1237 | 0.0092306 | 0.15678 | 16.9852 | 0.0092306 | 0.8684%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 18 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.032939 | 5.923 | 0.0055612 | 0.032939 | 5.923 | 0.0055612 | 0.034699 | 6.2395 | 0.0055612 | 0.1275%
2026 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 2 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.020949 | 0.65811 | 0.031832 | 0.020949 | 0.65811 | 0.031832 | 0.022068 | 0.69327 | 0.031832 | 0.3435%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 5 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.9161 | 1.6453 | 4.2036 | 6.9161 | 1.6453 | 4.2036 | 7.2856 | 1.7332 | 4.2036 | 0.9924%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 72 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 8.238 | 23.692 | 0.34771 | 8.238 | 23.692 | 0.34771 | 8.6781 | 24.9579 | 0.34771 | 0.9393%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 2 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1825 | 0.65811 | 1.7969 | 1.1825 | 0.65811 | 1.7969 | 1.2457 | 0.69327 | 1.7969 | 0.8802%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 252 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 56.0593 | 82.9219 | 0.67605 | 56.0593 | 82.9219 | 0.67605 | 59.0546 | 87.3525 | 0.67605 | 0.9962%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 260 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 47.4306 | 85.5543 | 0.55439 | 47.4306 | 85.5543 | 0.55439 | 49.9649 | 90.1256 | 0.55439 | 0.9962%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 214 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 23.945 | 70.4178 | 0.34004 | 23.945 | 70.4178 | 0.34004 | 25.2244 | 74.1803 | 0.34004 | 0.9984%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 47 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.89815 | 15.4656 | 0.058074 | 0.89815 | 15.4656 | 0.058074 | 0.94614 | 16.2919 | 0.058074 | 0.9877%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 4 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 20.3953 | 1.3162 | 15.4953 | 20.3953 | 1.3162 | 15.4953 | 21.485 | 1.3865 | 15.4953 | 0.9968%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 24 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 40.3024 | 7.8973 | 5.1033 | 40.3024 | 7.8973 | 5.1033 | 42.4558 | 8.3193 | 5.1033 | 0.9992%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 17 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.759 | 5.5939 | 0.67197 | 3.759 | 5.5939 | 0.67197 | 3.9598 | 5.8928 | 0.67197 | 0.945%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 60 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.4758 | 19.7433 | 0.37865 | 7.4758 | 19.7433 | 0.37865 | 7.8752 | 20.7982 | 0.37865 | 0.994%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 840 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 40.5406 | 276.4063 | 0.14667 | 40.5406 | 276.4063 | 0.14667 | 42.7067 | 291.1751 | 0.14667 | 0.9112%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 10 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.9041 | 3.2906 | 0.57866 | 1.9041 | 3.2906 | 0.57866 | 2.0059 | 3.4664 | 0.57866 | 0.9662%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 2 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.3124 | 0.65811 | 3.5138 | 2.3124 | 0.65811 | 3.5138 | 2.436 | 0.69327 | 3.5138 | 0.9775%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 45 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 37.1689 | 14.8075 | 2.5101 | 37.1689 | 14.8075 | 2.5101 | 39.1549 | 15.5987 | 2.5101 | 0.9826%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 53 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 96.2066 | 17.4399 | 5.5165 | 96.2066 | 17.4399 | 5.5165 | 101.3471 | 18.3718 | 5.5165 | 0.9977%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 215 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 97.5658 | 70.7469 | 1.3791 | 97.5658 | 70.7469 | 1.3791 | 102.7789 | 74.527 | 1.3791 | 0.9908%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 28 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 57.3987 | 9.2135 | 6.2298 | 57.3987 | 9.2135 | 6.2298 | 60.4656 | 9.7058 | 6.2298 | 0.9788%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 21 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 20.009 | 6.9102 | 2.8956 | 20.009 | 6.9102 | 2.8956 | 21.0782 | 7.2794 | 2.8956 | 0.9469%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 186 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 80.0347 | 61.2043 | 1.3077 | 80.0347 | 61.2043 | 1.3077 | 84.311 | 64.4745 | 1.3077 | 0.9648%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 75 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 14.6539 | 24.6791 | 0.59377 | 14.6539 | 24.6791 | 0.59377 | 15.4368 | 25.9978 | 0.59377 | 0.9856%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 117 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 33.4415 | 38.4995 | 0.86862 | 33.4415 | 38.4995 | 0.86862 | 35.2284 | 40.5565 | 0.86862 | 0.9842%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 246 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 27.8656 | 80.9476 | 0.34424 | 27.8656 | 80.9476 | 0.34424 | 29.3545 | 85.2727 | 0.34424 | 0.979%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 35 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 13.083 | 11.5169 | 1.136 | 13.083 | 11.5169 | 1.136 | 13.782 | 12.1323 | 1.136 | 0.9892%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 94 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 40.471 | 30.9312 | 1.3084 | 40.471 | 30.9312 | 1.3084 | 42.6334 | 32.5839 | 1.3084 | 0.9866%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 2 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.9122 | 0.65811 | 5.9446 | 3.9122 | 0.65811 | 5.9446 | 4.1212 | 0.69327 | 5.9446 | 0.9965%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 17 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.3418 | 5.5939 | 0.77617 | 4.3418 | 5.5939 | 0.77617 | 4.5738 | 5.8928 | 0.77617 | 0.9977%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 55 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 11.1645 | 18.098 | 0.61689 | 11.1645 | 18.098 | 0.61689 | 11.761 | 19.065 | 0.61689 | 0.9935%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 9 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.5017 | 2.9615 | 0.50708 | 1.5017 | 2.9615 | 0.50708 | 1.582 | 3.1197 | 0.50708 | 0.9948%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 33 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 17.7477 | 10.8588 | 1.6344 | 17.7477 | 10.8588 | 1.6344 | 18.696 | 11.439 | 1.6344 | 0.9905%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 63 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 56.9641 | 20.7305 | 2.7478 | 56.9641 | 20.7305 | 2.7478 | 60.0078 | 21.8381 | 2.7478 | 0.9304%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 25 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 61.4624 | 8.2264 | 7.4714 | 61.4624 | 8.2264 | 7.4714 | 64.7464 | 8.6659 | 7.4714 | 0.9454%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 335 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 111.2495 | 110.2335 | 1.0092 | 111.2495 | 110.2335 | 1.0092 | 117.1938 | 116.1234 | 1.0092 | 0.9926%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 91 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 34.5034 | 29.944 | 1.1523 | 34.5034 | 29.944 | 1.1523 | 36.3469 | 31.544 | 1.1523 | 0.9815%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 35 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.6887 | 11.5169 | 0.32028 | 3.6887 | 11.5169 | 0.32028 | 3.8858 | 12.1323 | 0.32028 | 0.9046%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 8 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 19.3034 | 2.6324 | 7.3329 | 19.3034 | 2.6324 | 7.3329 | 20.3348 | 2.7731 | 7.3329 | 0.8554%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 101 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 41.1347 | 33.2346 | 1.2377 | 41.1347 | 33.2346 | 1.2377 | 43.3326 | 35.0103 | 1.2377 | 0.9867%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.55516 | 1.3162 | 0.42179 | 0.55516 | 1.3162 | 0.42179 | 0.58483 | 1.3865 | 0.42179 | 0.9994%
2026 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 14 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 4.6068 | 0 | 0 | 4.6068 | 0 | 0 | 4.8529 | 0 | 0%
2026 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 8 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2.6324 | 0 | 0 | 2.6324 | 0 | 0 | 2.7731 | 0 | 0%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 58 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 151.1246 | 19.0852 | 7.9184 | 151.1246 | 19.0852 | 7.9184 | 159.1994 | 20.1049 | 7.9184 | 0.9909%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.47647 | 2.3034 | 0.20686 | 0.47647 | 2.3034 | 0.20686 | 0.50193 | 2.4265 | 0.20686 | 0.2981%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.77236 | 0.32906 | 2.3472 | 0.77236 | 0.32906 | 2.3472 | 0.81363 | 0.34664 | 2.3472 | 0.9995%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 151 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 77.2532 | 49.6873 | 1.5548 | 77.2532 | 49.6873 | 1.5548 | 81.381 | 52.3422 | 1.5548 | 0.9925%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 444 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 351.4153 | 146.1005 | 2.4053 | 351.4153 | 146.1005 | 2.4053 | 370.1919 | 153.9068 | 2.4053 | 0.9936%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 4 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.070593 | 1.3162 | 0.053633 | 0.070593 | 1.3162 | 0.053633 | 0.074365 | 1.3865 | 0.053633 | 0.895%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 42 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.502 | 13.8203 | 0.25339 | 3.502 | 13.8203 | 0.25339 | 3.6891 | 14.5588 | 0.25339 | 0.8771%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 319 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 48.5729 | 104.9686 | 0.46274 | 48.5729 | 104.9686 | 0.46274 | 51.1682 | 110.5772 | 0.46274 | 0.9246%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 26 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 28.8489 | 8.5554 | 3.372 | 28.8489 | 8.5554 | 3.372 | 30.3904 | 9.0126 | 3.372 | 0.9907%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 61 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 36.6006 | 20.0724 | 1.8234 | 36.6006 | 20.0724 | 1.8234 | 38.5562 | 21.1449 | 1.8234 | 0.9899%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 124 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 28.7225 | 40.8028 | 0.70393 | 28.7225 | 40.8028 | 0.70393 | 30.2572 | 42.983 | 0.70393 | 0.9527%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 208 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 16.0328 | 68.4435 | 0.23425 | 16.0328 | 68.4435 | 0.23425 | 16.8894 | 72.1005 | 0.23425 | 0.8154%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 114 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.9249 | 37.5123 | 0.45118 | 16.9249 | 37.5123 | 0.45118 | 17.8293 | 39.5166 | 0.45118 | 0.9501%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 323 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 173.5015 | 106.2848 | 1.6324 | 173.5015 | 106.2848 | 1.6324 | 182.772 | 111.9638 | 1.6324 | 0.97%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 419 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 38.089 | 137.8741 | 0.27626 | 38.089 | 137.8741 | 0.27626 | 40.1242 | 145.2409 | 0.27626 | 0.991%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.8695 | 17.4399 | 1.0246 | 17.8695 | 17.4399 | 1.0246 | 18.8243 | 18.3718 | 1.0246 | 0.7065%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 166 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 40.7977 | 54.6232 | 0.74689 | 40.7977 | 54.6232 | 0.74689 | 42.9776 | 57.5417 | 0.74689 | 0.9752%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 248 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 53.0508 | 81.6057 | 0.65009 | 53.0508 | 81.6057 | 0.65009 | 55.8853 | 85.966 | 0.65009 | 0.9686%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 143 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.3625 | 47.0549 | 0.13521 | 6.3625 | 47.0549 | 0.13521 | 6.7025 | 49.5691 | 0.13521 | 0.7976%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 96 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 108.5713 | 31.5893 | 3.437 | 108.5713 | 31.5893 | 3.437 | 114.3724 | 33.2772 | 3.437 | 0.9877%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 39.1596 | 20.7305 | 1.889 | 39.1596 | 20.7305 | 1.889 | 41.252 | 21.8381 | 1.889 | 0.981%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 234 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 93.29 | 76.9989 | 1.2116 | 93.29 | 76.9989 | 1.2116 | 98.2747 | 81.1131 | 1.2116 | 0.9713%
2026 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 19 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.6098 | 6.252 | 0.41743 | 2.6098 | 6.252 | 0.41743 | 2.7492 | 6.5861 | 0.41743 | 0.6764%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 62 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 31.7101 | 20.4014 | 1.5543 | 31.7101 | 20.4014 | 1.5543 | 33.4045 | 21.4915 | 1.5543 | 0.9774%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 95 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 45.9869 | 31.2602 | 1.4711 | 45.9869 | 31.2602 | 1.4711 | 48.444 | 32.9305 | 1.4711 | 0.977%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 299 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 121.6439 | 98.3875 | 1.2364 | 121.6439 | 98.3875 | 1.2364 | 128.1435 | 103.6445 | 1.2364 | 0.968%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.9263 | 1.6453 | 8.4644 | 13.9263 | 1.6453 | 8.4644 | 14.6704 | 1.7332 | 8.4644 | 0.8924%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 11 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 22.1145 | 3.6196 | 6.1096 | 22.1145 | 3.6196 | 6.1096 | 23.2961 | 3.813 | 6.1096 | 0.7823%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 1 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.41426 | 0.32906 | 1.2589 | 0.41426 | 0.32906 | 1.2589 | 0.43639 | 0.34664 | 1.2589 | 0.9121%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 357 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 107.1917 | 117.4727 | 0.91248 | 107.1917 | 117.4727 | 0.91248 | 112.9191 | 123.7494 | 0.91248 | 0.9429%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 5 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 18.4509 | 1.6453 | 11.2144 | 18.4509 | 1.6453 | 11.2144 | 19.4367 | 1.7332 | 11.2144 | 0.9974%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 208 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 40.0342 | 68.4435 | 0.58492 | 40.0342 | 68.4435 | 0.58492 | 42.1733 | 72.1005 | 0.58492 | 0.9922%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 4 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 6.2019 | 1.3162 | 4.7119 | 6.2019 | 1.3162 | 4.7119 | 6.5333 | 1.3865 | 4.7119 | 0.9914%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 26 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.9995 | 8.5554 | 0.23371 | 1.9995 | 8.5554 | 0.23371 | 2.1063 | 9.0126 | 0.23371 | 0.6623%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 87 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.3429 | 28.6278 | 0.11677 | 3.3429 | 28.6278 | 0.11677 | 3.5215 | 30.1574 | 0.11677 | 0.7437%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 254 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 15.1178 | 83.58 | 0.18088 | 15.1178 | 83.58 | 0.18088 | 15.9255 | 88.0458 | 0.18088 | 0.9193%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 14 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.060854 | 4.6068 | 0.01321 | 0.060854 | 4.6068 | 0.01321 | 0.064106 | 4.8529 | 0.01321 | 0.9638%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 21 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.8681 | 6.9102 | 1.2833 | 8.8681 | 6.9102 | 1.2833 | 9.3419 | 7.2794 | 1.2833 | 0.9553%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 38 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.5085 | 12.5041 | 0.36056 | 4.5085 | 12.5041 | 0.36056 | 4.7494 | 13.1722 | 0.36056 | 0.9636%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 35 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 12.1749 | 11.5169 | 1.0571 | 12.1749 | 11.5169 | 1.0571 | 12.8254 | 12.1323 | 1.0571 | 0.9978%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 180 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 28.3235 | 59.2299 | 0.47819 | 28.3235 | 59.2299 | 0.47819 | 29.8368 | 62.3947 | 0.47819 | 0.9975%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 515 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 80.5201 | 169.4634 | 0.47515 | 80.5201 | 169.4634 | 0.47515 | 84.8224 | 178.5181 | 0.47515 | 0.9974%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 55 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.2815 | 18.098 | 0.23657 | 4.2815 | 18.098 | 0.23657 | 4.5103 | 19.065 | 0.23657 | 0.901%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 44 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.4882 | 14.4784 | 0.58627 | 8.4882 | 14.4784 | 0.58627 | 8.9417 | 15.252 | 0.58627 | 0.8573%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 67 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.1468 | 22.0467 | 0.052018 | 1.1468 | 22.0467 | 0.052018 | 1.2081 | 23.2247 | 0.052018 | 0.7047%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 15 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.5407 | 4.9358 | 0.31214 | 1.5407 | 4.9358 | 0.31214 | 1.623 | 5.1996 | 0.31214 | 0.5082%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 70 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 10.2406 | 23.0339 | 0.44459 | 10.2406 | 23.0339 | 0.44459 | 10.7877 | 24.2646 | 0.44459 | 0.8949%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 129 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 14.5454 | 42.4481 | 0.34266 | 14.5454 | 42.4481 | 0.34266 | 15.3226 | 44.7162 | 0.34266 | 0.8426%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 264 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 16.4236 | 86.8706 | 0.18906 | 16.4236 | 86.8706 | 0.18906 | 17.3012 | 91.5122 | 0.18906 | 0.9106%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 63 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.8295 | 20.7305 | 0.76359 | 15.8295 | 20.7305 | 0.76359 | 16.6753 | 21.8381 | 0.76359 | 0.9543%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 51 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 14.2272 | 16.7818 | 0.84778 | 14.2272 | 16.7818 | 0.84778 | 14.9874 | 17.6785 | 0.84778 | 0.9497%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 5 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.7626 | 1.6453 | 3.5025 | 5.7626 | 1.6453 | 3.5025 | 6.0705 | 1.7332 | 3.5025 | 0.9907%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 291 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 46.2307 | 95.7551 | 0.4828 | 46.2307 | 95.7551 | 0.4828 | 48.7009 | 100.8714 | 0.4828 | 0.9915%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 1 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.825 | 0.32906 | 35.9363 | 11.825 | 0.32906 | 35.9363 | 12.4568 | 0.34664 | 35.9363 | 0.9792%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 68 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 9.206 | 22.3758 | 0.41143 | 9.206 | 22.3758 | 0.41143 | 9.6979 | 23.5713 | 0.41143 | 0.9662%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 10 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.4204 | 3.2906 | 0.73556 | 2.4204 | 3.2906 | 0.73556 | 2.5497 | 3.4664 | 0.73556 | 0.9706%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 50 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.756 | 16.4528 | 0.83609 | 13.756 | 16.4528 | 0.83609 | 14.491 | 17.3319 | 0.83609 | 0.9727%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 81 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 25.2035 | 26.6535 | 0.9456 | 25.2035 | 26.6535 | 0.9456 | 26.5502 | 28.0776 | 0.9456 | 0.9578%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.624 | 6.252 | 1.5393 | 9.624 | 6.252 | 1.5393 | 10.1382 | 6.5861 | 1.5393 | 0.9712%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 7 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.97889 | 2.3034 | 0.42498 | 0.97889 | 2.3034 | 0.42498 | 1.0312 | 2.4265 | 0.42498 | 0.9778%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 42 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 20.3743 | 13.8203 | 1.4742 | 20.3743 | 13.8203 | 1.4742 | 21.463 | 14.5588 | 1.4742 | 0.9872%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 59 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.7268 | 19.4143 | 0.70705 | 13.7268 | 19.4143 | 0.70705 | 14.4603 | 20.4516 | 0.70705 | 0.9782%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 270 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 247.9614 | 88.8449 | 2.7909 | 247.9614 | 88.8449 | 2.7909 | 261.2103 | 93.592 | 2.7909 | 0.9891%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 487 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 63.2206 | 160.2499 | 0.39451 | 63.2206 | 160.2499 | 0.39451 | 66.5986 | 168.8122 | 0.39451 | 0.9941%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 158 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.4973 | 51.9907 | 0.086503 | 4.4973 | 51.9907 | 0.086503 | 4.7376 | 54.7687 | 0.086503 | 0.974%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 69 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.7358 | 22.7048 | 0.16454 | 3.7358 | 22.7048 | 0.16454 | 3.9354 | 23.918 | 0.16454 | 0.9786%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 105 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.8339 | 34.5508 | 0.13991 | 4.8339 | 34.5508 | 0.13991 | 5.0922 | 36.3969 | 0.13991 | 0.9871%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 154 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 20.875 | 50.6745 | 0.41194 | 20.875 | 50.6745 | 0.41194 | 21.9903 | 53.3821 | 0.41194 | 0.9909%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 534 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 14.0738 | 175.7155 | 0.080094 | 14.0738 | 175.7155 | 0.080094 | 14.8257 | 185.1042 | 0.080094 | 0.8569%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 96 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 211.6306 | 31.5893 | 6.6994 | 211.6306 | 31.5893 | 6.6994 | 222.9383 | 33.2772 | 6.6994 | 0.9924%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 169 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 119.0085 | 55.6103 | 2.14 | 119.0085 | 55.6103 | 2.14 | 125.3673 | 58.5817 | 2.14 | 0.9821%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 153 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 184.0533 | 50.3454 | 3.6558 | 184.0533 | 50.3454 | 3.6558 | 193.8875 | 53.0355 | 3.6558 | 0.99%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 46 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 13.2167 | 15.1365 | 0.87316 | 13.2167 | 15.1365 | 0.87316 | 13.9229 | 15.9453 | 0.87316 | 0.9809%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 150 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 51.2828 | 49.3583 | 1.039 | 51.2828 | 49.3583 | 1.039 | 54.0229 | 51.9956 | 1.039 | 0.9892%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 111 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 132.853 | 36.5251 | 3.6373 | 132.853 | 36.5251 | 3.6373 | 139.9515 | 38.4767 | 3.6373 | 0.9919%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 6 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.6793 | 1.9743 | 0.34407 | 0.6793 | 1.9743 | 0.34407 | 0.71559 | 2.0798 | 0.34407 | 0.999%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 502 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 17.1386 | 165.1857 | 0.10375 | 17.1386 | 165.1857 | 0.10375 | 18.0544 | 174.0118 | 0.10375 | 0.8922%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 383 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 22.8579 | 126.0281 | 0.18137 | 22.8579 | 126.0281 | 0.18137 | 24.0792 | 132.762 | 0.18137 | 0.8785%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 367 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 100.6039 | 120.7632 | 0.83307 | 100.6039 | 120.7632 | 0.83307 | 105.9793 | 127.2158 | 0.83307 | 0.9868%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 406 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 33.0238 | 133.5964 | 0.24719 | 33.0238 | 133.5964 | 0.24719 | 34.7883 | 140.7346 | 0.24719 | 0.9466%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 493 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 12.4717 | 162.2242 | 0.076879 | 12.4717 | 162.2242 | 0.076879 | 13.1381 | 170.8921 | 0.076879 | 0.9088%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 69 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 95.5917 | 22.7048 | 4.2102 | 95.5917 | 22.7048 | 4.2102 | 100.6993 | 23.918 | 4.2102 | 0.9905%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 57 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 20.2056 | 18.7561 | 1.0773 | 20.2056 | 18.7561 | 1.0773 | 21.2852 | 19.7583 | 1.0773 | 0.9634%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 218 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 15.4856 | 71.734 | 0.21588 | 15.4856 | 71.734 | 0.21588 | 16.313 | 75.5669 | 0.21588 | 0.8429%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 620 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 30.5685 | 204.0142 | 0.14984 | 30.5685 | 204.0142 | 0.14984 | 32.2018 | 214.915 | 0.14984 | 0.8937%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 35.1769 | 5.5939 | 6.2884 | 35.1769 | 5.5939 | 6.2884 | 37.0565 | 5.8928 | 6.2884 | 0.9991%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 227 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 28.7509 | 74.6955 | 0.38491 | 28.7509 | 74.6955 | 0.38491 | 30.2871 | 78.6866 | 0.38491 | 0.9216%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 357 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 25.0832 | 117.4727 | 0.21352 | 25.0832 | 117.4727 | 0.21352 | 26.4234 | 123.7494 | 0.21352 | 0.9611%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.7393 | 0.98717 | 6.827 | 6.7393 | 0.98717 | 6.827 | 7.0994 | 1.0399 | 6.827 | 0.9946%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 384 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 36.4187 | 126.3572 | 0.28822 | 36.4187 | 126.3572 | 0.28822 | 38.3646 | 133.1086 | 0.28822 | 0.9703%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 29 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 1.0134 | 9.5426 | 0.1062 | 1.0134 | 9.5426 | 0.1062 | 1.0676 | 10.0525 | 0.1062 | 0.334%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 30 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 19.5112 | 9.8717 | 1.9765 | 19.5112 | 9.8717 | 1.9765 | 20.5537 | 10.3991 | 1.9765 | 0.9951%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 27 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.8178 | 8.8845 | 0.65483 | 5.8178 | 8.8845 | 0.65483 | 6.1286 | 9.3592 | 0.65483 | 0.9868%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 56 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 42.518 | 18.4271 | 2.3074 | 42.518 | 18.4271 | 2.3074 | 44.7898 | 19.4117 | 2.3074 | 0.9945%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 34 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 21.4759 | 11.1879 | 1.9196 | 21.4759 | 11.1879 | 1.9196 | 22.6234 | 11.7857 | 1.9196 | 0.9686%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 17 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 91.3747 | 5.5939 | 16.3346 | 91.3747 | 5.5939 | 16.3346 | 96.257 | 5.8928 | 16.3346 | 0.9959%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 120 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 12.3393 | 39.4866 | 0.31249 | 12.3393 | 39.4866 | 0.31249 | 12.9986 | 41.5964 | 0.31249 | 0.9515%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 822 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 68.2692 | 270.4834 | 0.2524 | 68.2692 | 270.4834 | 0.2524 | 71.9169 | 284.9357 | 0.2524 | 0.9662%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 245 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 749.8113 | 80.6185 | 9.3007 | 749.8113 | 80.6185 | 9.3007 | 789.8747 | 84.9261 | 9.3007 | 0.9925%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 34.2741 | 2.9615 | 11.5733 | 34.2741 | 2.9615 | 11.5733 | 36.1055 | 3.1197 | 11.5733 | 0.9927%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 107 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 428.6915 | 35.2089 | 12.1757 | 428.6915 | 35.2089 | 12.1757 | 451.5971 | 37.0902 | 12.1757 | 0.9963%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.3843 | 0.65811 | 3.623 | 2.3843 | 0.65811 | 3.623 | 2.5117 | 0.69327 | 3.623 | 0.8656%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 511 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 68.0491 | 168.1472 | 0.4047 | 68.0491 | 168.1472 | 0.4047 | 71.685 | 177.1315 | 0.4047 | 0.9605%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 14 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 46.2897 | 4.6068 | 10.0482 | 46.2897 | 4.6068 | 10.0482 | 48.763 | 4.8529 | 10.0482 | 0.9985%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 600 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 154.7093 | 197.4331 | 0.7836 | 154.7093 | 197.4331 | 0.7836 | 162.9756 | 207.9822 | 0.7836 | 0.967%
2026 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 3 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.16292 | 0.98717 | 0.16504 | 0.16292 | 0.98717 | 0.16504 | 0.17163 | 1.0399 | 0.16504 | 0.9833%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 349 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 18.1259 | 114.8403 | 0.15784 | 18.1259 | 114.8403 | 0.15784 | 19.0944 | 120.9763 | 0.15784 | 0.9498%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 470 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 59.885 | 154.6559 | 0.38721 | 59.885 | 154.6559 | 0.38721 | 63.0847 | 162.9194 | 0.38721 | 0.9826%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 585 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 18.007 | 192.4973 | 0.093544 | 18.007 | 192.4973 | 0.093544 | 18.9692 | 202.7827 | 0.093544 | 0.9106%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 226 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 4.0406 | 74.3665 | 0.054334 | 4.0406 | 74.3665 | 0.054334 | 4.2565 | 78.34 | 0.054334 | 0.7897%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.3877 | 23.0339 | 0.32073 | 7.3877 | 23.0339 | 0.32073 | 7.7824 | 24.2646 | 0.32073 | 0.9819%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 328 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 32.3646 | 107.9301 | 0.29987 | 32.3646 | 107.9301 | 0.29987 | 34.0939 | 113.697 | 0.29987 | 0.9768%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 3 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0786 | 0.98717 | 1.0926 | 1.0786 | 0.98717 | 1.0926 | 1.1362 | 1.0399 | 1.0926 | 0.9298%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 32 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.5257 | 10.5298 | 0.14489 | 1.5257 | 10.5298 | 0.14489 | 1.6072 | 11.0924 | 0.14489 | 0.8171%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 364 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 25.6087 | 119.7761 | 0.2138 | 25.6087 | 119.7761 | 0.2138 | 26.977 | 126.1759 | 0.2138 | 0.983%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 1452 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 48.405 | 477.7881 | 0.10131 | 48.405 | 477.7881 | 0.10131 | 50.9914 | 503.317 | 0.10131 | 0.9868%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 4 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.0004932 | 1.3162 | 0.00037471 | 0.0004932 | 1.3162 | 0.00037471 | 0.00051955 | 1.3865 | 0.00037471 | 0.004523%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 743 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 28.6233 | 244.488 | 0.11707 | 28.6233 | 244.488 | 0.11707 | 30.1527 | 257.5513 | 0.11707 | 0.9884%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 182 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.692 | 59.888 | 0.11174 | 6.692 | 59.888 | 0.11174 | 7.0496 | 63.0879 | 0.11174 | 0.9757%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 279 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 4.0561 | 91.8064 | 0.044181 | 4.0561 | 91.8064 | 0.044181 | 4.2728 | 96.7117 | 0.044181 | 0.9496%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 309 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 19.1889 | 101.678 | 0.18872 | 19.1889 | 101.678 | 0.18872 | 20.2142 | 107.1108 | 0.18872 | 0.859%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 875 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 46.8623 | 287.9233 | 0.16276 | 46.8623 | 287.9233 | 0.16276 | 49.3662 | 303.3074 | 0.16276 | 0.9946%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 106 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 36.9882 | 34.8798 | 1.0604 | 36.9882 | 34.8798 | 1.0604 | 38.9646 | 36.7435 | 1.0604 | 0.8863%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 399 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 222.188 | 131.293 | 1.6923 | 222.188 | 131.293 | 1.6923 | 234.0599 | 138.3082 | 1.6923 | 0.9837%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 390 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 91.5381 | 128.3315 | 0.71329 | 91.5381 | 128.3315 | 0.71329 | 96.4291 | 135.1884 | 0.71329 | 0.9873%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 104 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 26.1976 | 34.2217 | 0.76552 | 26.1976 | 34.2217 | 0.76552 | 27.5973 | 36.0503 | 0.76552 | 0.9726%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 19 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 21.2648 | 6.252 | 3.4013 | 21.2648 | 6.252 | 3.4013 | 22.401 | 6.5861 | 3.4013 | 0.9861%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 249 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 49.8843 | 81.9347 | 0.60883 | 49.8843 | 81.9347 | 0.60883 | 52.5497 | 86.3126 | 0.60883 | 0.9807%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 365 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 199.1398 | 120.1051 | 1.658 | 199.1398 | 120.1051 | 1.658 | 209.7801 | 126.5225 | 1.658 | 0.9836%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 129 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 64.6625 | 42.4481 | 1.5233 | 64.6625 | 42.4481 | 1.5233 | 68.1175 | 44.7162 | 1.5233 | 0.9784%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 48 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 34.4579 | 15.7946 | 2.1816 | 34.4579 | 15.7946 | 2.1816 | 36.299 | 16.6386 | 2.1816 | 0.994%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 135 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 267.7119 | 44.4224 | 6.0265 | 267.7119 | 44.4224 | 6.0265 | 282.0161 | 46.796 | 6.0265 | 0.9934%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 345 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 255.4695 | 113.524 | 2.2504 | 255.4695 | 113.524 | 2.2504 | 269.1196 | 119.5898 | 2.2504 | 0.9889%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 37 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.4846 | 12.175 | 0.36835 | 4.4846 | 12.175 | 0.36835 | 4.7243 | 12.8256 | 0.36835 | 0.7089%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 23 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 23.8534 | 7.5683 | 3.1518 | 23.8534 | 7.5683 | 3.1518 | 25.1279 | 7.9727 | 3.1518 | 0.9883%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 479 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 292.0914 | 157.6174 | 1.8532 | 292.0914 | 157.6174 | 1.8532 | 307.6982 | 166.0391 | 1.8532 | 0.9911%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 422 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 618.2973 | 138.8613 | 4.4526 | 618.2973 | 138.8613 | 4.4526 | 651.3338 | 146.2808 | 4.4526 | 0.9893%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 399 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 8.0494 | 131.293 | 0.061309 | 8.0494 | 131.293 | 0.061309 | 8.4795 | 138.3082 | 0.061309 | 0.9808%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.9204 | 18.098 | 0.82442 | 14.9204 | 18.098 | 0.82442 | 15.7176 | 19.065 | 0.82442 | 0.9867%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 10.2731 | 76.6699 | 0.13399 | 10.2731 | 76.6699 | 0.13399 | 10.822 | 80.7664 | 0.13399 | 0.9646%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 327 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 58.7462 | 107.601 | 0.54596 | 58.7462 | 107.601 | 0.54596 | 61.8851 | 113.3503 | 0.54596 | 0.9824%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 303 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.8035 | 99.7037 | 0.068237 | 6.8035 | 99.7037 | 0.068237 | 7.167 | 105.031 | 0.068237 | 0.6927%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 31 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.5462 | 10.2007 | 0.34764 | 3.5462 | 10.2007 | 0.34764 | 3.7357 | 10.7457 | 0.34764 | 0.9876%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 123 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 11.0889 | 40.4738 | 0.27398 | 11.0889 | 40.4738 | 0.27398 | 11.6814 | 42.6364 | 0.27398 | 0.9838%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 24 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.451 | 7.8973 | 0.94349 | 7.451 | 7.8973 | 0.94349 | 7.8491 | 8.3193 | 0.94349 | 0.987%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 21 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.4814 | 6.9102 | 0.50381 | 3.4814 | 6.9102 | 0.50381 | 3.6675 | 7.2794 | 0.50381 | 0.9688%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 485 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 41.4475 | 159.5918 | 0.25971 | 41.4475 | 159.5918 | 0.25971 | 43.6621 | 168.119 | 0.25971 | 0.9791%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 263 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 35.3681 | 86.5415 | 0.40868 | 35.3681 | 86.5415 | 0.40868 | 37.2578 | 91.1655 | 0.40868 | 0.9907%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 164 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 33.8556 | 53.965 | 0.62736 | 33.8556 | 53.965 | 0.62736 | 35.6645 | 56.8485 | 0.62736 | 0.9682%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 101 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 6.0425 | 33.2346 | 0.18182 | 6.0425 | 33.2346 | 0.18182 | 6.3654 | 35.0103 | 0.18182 | 0.6596%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 389 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 30.5472 | 128.0025 | 0.23865 | 30.5472 | 128.0025 | 0.23865 | 32.1793 | 134.8418 | 0.23865 | 0.9454%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 74 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 12.0051 | 24.3501 | 0.49302 | 12.0051 | 24.3501 | 0.49302 | 12.6466 | 25.6511 | 0.49302 | 0.9251%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 6 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.98533 | 1.9743 | 0.49907 | 0.98533 | 1.9743 | 0.49907 | 1.038 | 2.0798 | 0.49907 | 0.9818%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 299 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 34.3178 | 98.3875 | 0.3488 | 34.3178 | 98.3875 | 0.3488 | 36.1515 | 103.6445 | 0.3488 | 0.9585%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 47 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 49.8241 | 15.4656 | 3.2216 | 49.8241 | 15.4656 | 3.2216 | 52.4863 | 16.2919 | 3.2216 | 0.9855%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 101 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.865 | 33.2346 | 0.50745 | 16.865 | 33.2346 | 0.50745 | 17.7662 | 35.0103 | 0.50745 | 0.878%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 4.3298 | 0.32906 | 13.1583 | 4.3298 | 0.32906 | 13.1583 | 4.5612 | 0.34664 | 13.1583 | 0.9431%
2026 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 2 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.39171 | 0.65811 | 0.5952 | 0.39171 | 0.65811 | 0.5952 | 0.41263 | 0.69327 | 0.5952 | 0.9823%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 215 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.8786 | 70.7469 | 0.068958 | 4.8786 | 70.7469 | 0.068958 | 5.1393 | 74.527 | 0.068958 | 0.9288%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 22 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.024332 | 7.2392 | 0.0033611 | 0.024332 | 7.2392 | 0.0033611 | 0.025632 | 7.626 | 0.0033611 | 0.7897%
2026 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 2 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 4.3537 | 0.65811 | 6.6155 | 4.3537 | 0.65811 | 6.6155 | 4.5864 | 0.69327 | 6.6155 | 0.9948%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 169 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.6479 | 55.6103 | 0.11955 | 6.6479 | 55.6103 | 0.11955 | 7.0031 | 58.5817 | 0.11955 | 0.9241%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 110 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 20.9129 | 36.1961 | 0.57777 | 20.9129 | 36.1961 | 0.57777 | 22.0303 | 38.1301 | 0.57777 | 0.9107%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 294 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 43.4106 | 96.7422 | 0.44872 | 43.4106 | 96.7422 | 0.44872 | 45.7301 | 101.9113 | 0.44872 | 0.9555%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 5 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.17655 | 1.6453 | 0.10731 | 0.17655 | 1.6453 | 0.10731 | 0.18598 | 1.7332 | 0.10731 | 0.1937%
2026 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 13 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.073515 | 4.2777 | 0.017186 | 0.073515 | 4.2777 | 0.017186 | 0.077443 | 4.5063 | 0.017186 | 0.4938%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 201 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.035668 | 66.1401 | 0.00053928 | 0.035668 | 66.1401 | 0.00053928 | 0.037574 | 69.674 | 0.00053928 | 0.02339%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 10 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0029183 | 3.2906 | 0.00088687 | 0.0029183 | 3.2906 | 0.00088687 | 0.0030742 | 3.4664 | 0.00088687 | 0.001514%
2026 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 149 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.9919 | 49.0292 | 0.040627 | 1.9919 | 49.0292 | 0.040627 | 2.0983 | 51.6489 | 0.040627 | 0.995%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 2 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.8639 | 0.65811 | 4.3517 | 2.8639 | 0.65811 | 4.3517 | 3.0169 | 0.69327 | 4.3517 | 0.9927%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 975 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 32.8093 | 320.8288 | 0.10226 | 32.8093 | 320.8288 | 0.10226 | 34.5623 | 337.9711 | 0.10226 | 0.9548%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 827 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 129.861 | 272.1286 | 0.4772 | 129.861 | 272.1286 | 0.4772 | 136.7997 | 286.6688 | 0.4772 | 0.9814%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 961 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 51.5398 | 316.222 | 0.16299 | 51.5398 | 316.222 | 0.16299 | 54.2936 | 333.1182 | 0.16299 | 0.9699%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 397 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 128.0651 | 130.6349 | 0.98033 | 128.0651 | 130.6349 | 0.98033 | 134.9078 | 137.6149 | 0.98033 | 0.9928%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 538 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 105.6518 | 177.0317 | 0.5968 | 105.6518 | 177.0317 | 0.5968 | 111.297 | 186.4907 | 0.5968 | 0.9888%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 546 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 222.6577 | 179.6641 | 1.2393 | 222.6577 | 179.6641 | 1.2393 | 234.5546 | 189.2638 | 1.2393 | 0.9925%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 86.9953 | 30.2731 | 2.8737 | 86.9953 | 30.2731 | 2.8737 | 91.6436 | 31.8906 | 2.8737 | 0.9973%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 488 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 176.4312 | 160.5789 | 1.0987 | 176.4312 | 160.5789 | 1.0987 | 185.8581 | 169.1589 | 1.0987 | 0.9936%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 319 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 85.7598 | 104.9686 | 0.817 | 85.7598 | 104.9686 | 0.817 | 90.342 | 110.5772 | 0.817 | 0.9749%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 106 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 23.8334 | 34.8798 | 0.6833 | 23.8334 | 34.8798 | 0.6833 | 25.1069 | 36.7435 | 0.6833 | 0.9918%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 24 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 21.1215 | 7.8973 | 2.6745 | 21.1215 | 7.8973 | 2.6745 | 22.2501 | 8.3193 | 2.6745 | 0.9993%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 55 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.8485 | 18.098 | 0.93096 | 16.8485 | 18.098 | 0.93096 | 17.7488 | 19.065 | 0.93096 | 0.8869%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 46 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 40.9814 | 15.1365 | 2.7074 | 40.9814 | 15.1365 | 2.7074 | 43.1711 | 15.9453 | 2.7074 | 0.943%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 13 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.788 | 4.2777 | 0.65176 | 2.788 | 4.2777 | 0.65176 | 2.937 | 4.5063 | 0.65176 | 0.6284%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 139 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 128.3764 | 45.7387 | 2.8067 | 128.3764 | 45.7387 | 2.8067 | 135.2357 | 48.1825 | 2.8067 | 0.9943%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 465 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 194.0236 | 153.0107 | 1.268 | 194.0236 | 153.0107 | 1.268 | 204.3905 | 161.1862 | 1.268 | 0.9917%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 30.8577 | 33.5636 | 0.91938 | 30.8577 | 33.5636 | 0.91938 | 32.5065 | 35.357 | 0.91938 | 0.8854%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 276 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 70.4778 | 90.8192 | 0.77602 | 70.4778 | 90.8192 | 0.77602 | 74.2435 | 95.6718 | 0.77602 | 0.985%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 139 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.9537 | 45.7387 | 0.28321 | 12.9537 | 45.7387 | 0.28321 | 13.6459 | 48.1825 | 0.28321 | 0.7994%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 131 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 50.9054 | 43.1062 | 1.1809 | 50.9054 | 43.1062 | 1.1809 | 53.6253 | 45.4095 | 1.1809 | 0.9814%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 704 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 149.3338 | 231.6548 | 0.64464 | 149.3338 | 231.6548 | 0.64464 | 157.313 | 244.0325 | 0.64464 | 0.9776%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 561 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 84.5967 | 184.6 | 0.45827 | 84.5967 | 184.6 | 0.45827 | 89.1168 | 194.4634 | 0.45827 | 0.9541%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 14 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.8235 | 4.6068 | 2.5665 | 11.8235 | 4.6068 | 2.5665 | 12.4552 | 4.8529 | 2.5665 | 0.9906%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 7 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 48.4832 | 2.3034 | 21.0487 | 48.4832 | 2.3034 | 21.0487 | 51.0737 | 2.4265 | 21.0487 | 0.9968%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 1 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 8.0059 | 0.32906 | 24.3299 | 8.0059 | 0.32906 | 24.3299 | 8.4336 | 0.34664 | 24.3299 | 0.9549%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 194 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 158.9726 | 63.8367 | 2.4903 | 158.9726 | 63.8367 | 2.4903 | 167.4668 | 67.2476 | 2.4903 | 0.9879%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 329 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 164.5511 | 108.2592 | 1.52 | 164.5511 | 108.2592 | 1.52 | 173.3433 | 114.0436 | 1.52 | 0.9747%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 435 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 96.5713 | 143.139 | 0.67467 | 96.5713 | 143.139 | 0.67467 | 101.7312 | 150.7871 | 0.67467 | 0.9704%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 248 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 109.6988 | 81.6057 | 1.3443 | 109.6988 | 81.6057 | 1.3443 | 115.5602 | 85.966 | 1.3443 | 0.9781%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.5598 | 3.6196 | 1.536 | 5.5598 | 3.6196 | 1.536 | 5.8569 | 3.813 | 1.536 | 0.9721%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 36 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.7834 | 11.846 | 1.0791 | 12.7834 | 11.846 | 1.0791 | 13.4665 | 12.4789 | 1.0791 | 0.9966%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 252 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 353.6518 | 82.9219 | 4.2649 | 353.6518 | 82.9219 | 4.2649 | 372.5479 | 87.3525 | 4.2649 | 0.9859%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 14 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 12.3554 | 4.6068 | 2.682 | 12.3554 | 4.6068 | 2.682 | 13.0156 | 4.8529 | 2.682 | 0.8901%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 22 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.6574 | 7.2392 | 0.22895 | 1.6574 | 7.2392 | 0.22895 | 1.746 | 7.626 | 0.22895 | 0.1879%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 590 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 26.3874 | 194.1426 | 0.13592 | 26.3874 | 194.1426 | 0.13592 | 27.7974 | 204.5159 | 0.13592 | 0.8818%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 455 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 17.3358 | 149.7201 | 0.11579 | 17.3358 | 149.7201 | 0.11579 | 18.2621 | 157.7199 | 0.11579 | 0.9783%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 839 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 59.8337 | 276.0773 | 0.21673 | 59.8337 | 276.0773 | 0.21673 | 63.0306 | 290.8285 | 0.21673 | 0.9847%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 3 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 12.3633 | 0.98717 | 12.5241 | 12.3633 | 0.98717 | 12.5241 | 13.0239 | 1.0399 | 12.5241 | 0.9597%
2026 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.67081 | 0.32906 | 2.0386 | 0.67081 | 0.32906 | 2.0386 | 0.70665 | 0.34664 | 2.0386 | 0.9953%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 91 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 32.7047 | 29.944 | 1.0922 | 32.7047 | 29.944 | 1.0922 | 34.4521 | 31.544 | 1.0922 | 0.9745%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 5.0723 | 0.98717 | 5.1382 | 5.0723 | 0.98717 | 5.1382 | 5.3433 | 1.0399 | 5.1382 | 0.9134%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 68 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 44.4079 | 22.3758 | 1.9846 | 44.4079 | 22.3758 | 1.9846 | 46.7806 | 23.5713 | 1.9846 | 0.98%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 20 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 50.2962 | 6.5811 | 7.6425 | 50.2962 | 6.5811 | 7.6425 | 52.9836 | 6.9327 | 7.6425 | 0.9857%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 358 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.8191 | 117.8018 | 0.14277 | 16.8191 | 117.8018 | 0.14277 | 17.7178 | 124.0961 | 0.14277 | 0.9609%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 28 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.014671 | 9.2135 | 0.0015923 | 0.014671 | 9.2135 | 0.0015923 | 0.015455 | 9.7058 | 0.0015923 | 0.01745%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 37 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.9098 | 12.175 | 0.56753 | 6.9098 | 12.175 | 0.56753 | 7.2789 | 12.8256 | 0.56753 | 0.8492%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 17 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.9086 | 5.5939 | 0.51995 | 2.9086 | 5.5939 | 0.51995 | 3.064 | 5.8928 | 0.51995 | 0.5795%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 558 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 97.67 | 183.6128 | 0.53193 | 97.67 | 183.6128 | 0.53193 | 102.8886 | 193.4235 | 0.53193 | 0.8848%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 9 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 5.1901 | 2.9615 | 1.7525 | 5.1901 | 2.9615 | 1.7525 | 5.4674 | 3.1197 | 1.7525 | 0.9893%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 29 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 4.1351 | 9.5426 | 0.43333 | 4.1351 | 9.5426 | 0.43333 | 4.3561 | 10.0525 | 0.43333 | 0.9131%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 7 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.68786 | 2.3034 | 0.29863 | 0.68786 | 2.3034 | 0.29863 | 0.72461 | 2.4265 | 0.29863 | 0.51%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 16 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 31.8067 | 5.2649 | 6.0413 | 31.8067 | 5.2649 | 6.0413 | 33.5062 | 5.5462 | 6.0413 | 0.9767%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 219 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.853 | 72.0631 | 0.053468 | 3.853 | 72.0631 | 0.053468 | 4.0589 | 75.9135 | 0.053468 | 0.7071%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 202 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 87.2546 | 66.4691 | 1.3127 | 87.2546 | 66.4691 | 1.3127 | 91.9168 | 70.0207 | 1.3127 | 0.9496%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 55 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 66.4731 | 18.098 | 3.6729 | 66.4731 | 18.098 | 3.6729 | 70.0248 | 19.065 | 3.6729 | 0.9611%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 33 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 13.5715 | 10.8588 | 1.2498 | 13.5715 | 10.8588 | 1.2498 | 14.2966 | 11.439 | 1.2498 | 0.8872%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 211 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 96.9373 | 69.4306 | 1.3962 | 96.9373 | 69.4306 | 1.3962 | 102.1167 | 73.1404 | 1.3962 | 0.9569%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 16 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 14.2791 | 5.2649 | 2.7121 | 14.2791 | 5.2649 | 2.7121 | 15.0421 | 5.5462 | 2.7121 | 0.8473%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 52 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 30.7191 | 17.1109 | 1.7953 | 30.7191 | 17.1109 | 1.7953 | 32.3605 | 18.0251 | 1.7953 | 0.8754%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 29 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 37.1637 | 9.5426 | 3.8945 | 37.1637 | 9.5426 | 3.8945 | 39.1494 | 10.0525 | 3.8945 | 0.8812%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 2 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 12.5395 | 0.65811 | 19.0537 | 12.5395 | 0.65811 | 19.0537 | 13.2095 | 0.69327 | 19.0537 | 0.9724%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 1 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 11.2563 | 0.32906 | 34.2081 | 11.2563 | 0.32906 | 34.2081 | 11.8578 | 0.34664 | 34.2081 | 0.9739%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 56 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 22.903 | 18.4271 | 1.2429 | 22.903 | 18.4271 | 1.2429 | 24.1267 | 19.4117 | 1.2429 | 0.9191%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 60 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 11.2627 | 19.7433 | 0.57046 | 11.2627 | 19.7433 | 0.57046 | 11.8645 | 20.7982 | 0.57046 | 0.557%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 73 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.7837 | 24.021 | 0.15752 | 3.7837 | 24.021 | 0.15752 | 3.9859 | 25.3045 | 0.15752 | 0.7618%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 79 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.7608 | 25.9954 | 0.18314 | 4.7608 | 25.9954 | 0.18314 | 5.0152 | 27.3843 | 0.18314 | 0.7912%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 243 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 79.6266 | 79.9604 | 0.99583 | 79.6266 | 79.9604 | 0.99583 | 83.8812 | 84.2328 | 0.99583 | 0.9168%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 119 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 50.3074 | 39.1576 | 1.2847 | 50.3074 | 39.1576 | 1.2847 | 52.9954 | 41.2498 | 1.2847 | 0.9343%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 495 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 58.0947 | 162.8823 | 0.35667 | 58.0947 | 162.8823 | 0.35667 | 61.1988 | 171.5853 | 0.35667 | 0.9049%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.8342 | 4.6068 | 3.003 | 13.8342 | 4.6068 | 3.003 | 14.5734 | 4.8529 | 3.003 | 0.9697%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 10 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.768 | 3.2906 | 1.7529 | 5.768 | 3.2906 | 1.7529 | 6.0762 | 3.4664 | 1.7529 | 0.967%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 61 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 49.5677 | 20.0724 | 2.4694 | 49.5677 | 20.0724 | 2.4694 | 52.2162 | 21.1449 | 2.4694 | 0.9877%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 125 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 21.1459 | 41.1319 | 0.5141 | 21.1459 | 41.1319 | 0.5141 | 22.2758 | 43.3296 | 0.5141 | 0.9555%
2026 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.7488 | 16.1237 | 0.17048 | 2.7488 | 16.1237 | 0.17048 | 2.8957 | 16.9852 | 0.17048 | 0.9711%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 257 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 78.3224 | 84.5672 | 0.92616 | 78.3224 | 84.5672 | 0.92616 | 82.5073 | 89.0857 | 0.92616 | 0.9923%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 62 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 7.0106 | 20.4014 | 0.34363 | 7.0106 | 20.4014 | 0.34363 | 7.3851 | 21.4915 | 0.34363 | 0.9277%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 61 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 10.2883 | 20.0724 | 0.51256 | 10.2883 | 20.0724 | 0.51256 | 10.838 | 21.1449 | 0.51256 | 0.9525%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 27 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.3077 | 8.8845 | 0.14719 | 1.3077 | 8.8845 | 0.14719 | 1.3776 | 9.3592 | 0.14719 | 0.999%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.7259 | 1.3162 | 1.3113 | 1.7259 | 1.3162 | 1.3113 | 1.8181 | 1.3865 | 1.3113 | 0.9984%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 175 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 26.9189 | 57.5847 | 0.46747 | 26.9189 | 57.5847 | 0.46747 | 28.3572 | 60.6615 | 0.46747 | 0.9993%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 14 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.36197 | 4.6068 | 0.078574 | 0.36197 | 4.6068 | 0.078574 | 0.38131 | 4.8529 | 0.078574 | 0.9723%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 287 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 32.7275 | 94.4388 | 0.34655 | 32.7275 | 94.4388 | 0.34655 | 34.4762 | 99.4848 | 0.34655 | 0.997%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 15 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 13.019 | 4.9358 | 2.6377 | 13.019 | 4.9358 | 2.6377 | 13.7146 | 5.1996 | 2.6377 | 0.9902%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 213 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 49.3848 | 70.0888 | 0.7046 | 49.3848 | 70.0888 | 0.7046 | 52.0235 | 73.8337 | 0.7046 | 0.9833%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 471 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 158.6864 | 154.985 | 1.0239 | 158.6864 | 154.985 | 1.0239 | 167.1652 | 163.266 | 1.0239 | 0.9937%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 15 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 38.5309 | 4.9358 | 7.8064 | 38.5309 | 4.9358 | 7.8064 | 40.5897 | 5.1996 | 7.8064 | 0.9496%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 90 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.9397 | 29.615 | 0.065496 | 1.9397 | 29.615 | 0.065496 | 2.0433 | 31.1973 | 0.065496 | 0.9963%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 31 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.9644 | 10.2007 | 0.68274 | 6.9644 | 10.2007 | 0.68274 | 7.3365 | 10.7457 | 0.68274 | 0.9951%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 779 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 27.6613 | 256.334 | 0.10791 | 27.6613 | 256.334 | 0.10791 | 29.1393 | 270.0303 | 0.10791 | 0.9734%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 148 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.8205 | 48.7002 | 0.28379 | 13.8205 | 48.7002 | 0.28379 | 14.5589 | 51.3023 | 0.28379 | 0.9797%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 400 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 24.3479 | 131.6221 | 0.18498 | 24.3479 | 131.6221 | 0.18498 | 25.6488 | 138.6548 | 0.18498 | 0.9676%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 745 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 30.1957 | 245.1461 | 0.12317 | 30.1957 | 245.1461 | 0.12317 | 31.8091 | 258.2446 | 0.12317 | 0.9272%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 290 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 15.3089 | 95.426 | 0.16043 | 15.3089 | 95.426 | 0.16043 | 16.1269 | 100.5247 | 0.16043 | 0.9829%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 504 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 62.3968 | 165.8438 | 0.37624 | 62.3968 | 165.8438 | 0.37624 | 65.7308 | 174.7051 | 0.37624 | 0.9672%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 258 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.5208 | 84.8962 | 0.06503 | 5.5208 | 84.8962 | 0.06503 | 5.8158 | 89.4324 | 0.06503 | 0.7734%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 221 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 19.1856 | 72.7212 | 0.26382 | 19.1856 | 72.7212 | 0.26382 | 20.2108 | 76.6068 | 0.26382 | 0.9648%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 63 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.8412 | 20.7305 | 0.088814 | 1.8412 | 20.7305 | 0.088814 | 1.9395 | 21.8381 | 0.088814 | 0.7472%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 657 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 46.0042 | 216.1893 | 0.2128 | 46.0042 | 216.1893 | 0.2128 | 48.4623 | 227.7405 | 0.2128 | 0.9649%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 231 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 19.0309 | 76.0117 | 0.25037 | 19.0309 | 76.0117 | 0.25037 | 20.0478 | 80.0732 | 0.25037 | 0.9757%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 427 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 104.6914 | 140.5066 | 0.7451 | 104.6914 | 140.5066 | 0.7451 | 110.2852 | 148.014 | 0.7451 | 0.9669%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 152 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.9096 | 50.0164 | 0.13815 | 6.9096 | 50.0164 | 0.13815 | 7.2788 | 52.6888 | 0.13815 | 0.8931%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 356 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 79.0871 | 117.1436 | 0.67513 | 79.0871 | 117.1436 | 0.67513 | 83.3128 | 123.4028 | 0.67513 | 0.9779%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 268 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 82.5858 | 88.1868 | 0.93649 | 82.5858 | 88.1868 | 0.93649 | 86.9984 | 92.8987 | 0.93649 | 0.9936%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 378 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 52.9434 | 124.3829 | 0.42565 | 52.9434 | 124.3829 | 0.42565 | 55.7723 | 131.0288 | 0.42565 | 0.9878%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 262 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 116.0523 | 86.2125 | 1.3461 | 116.0523 | 86.2125 | 1.3461 | 122.2532 | 90.8189 | 1.3461 | 0.9938%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 549 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 85.1588 | 180.6513 | 0.4714 | 85.1588 | 180.6513 | 0.4714 | 89.7089 | 190.3037 | 0.4714 | 0.9905%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 29 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.4626 | 9.5426 | 0.048477 | 0.4626 | 9.5426 | 0.048477 | 0.48731 | 10.0525 | 0.048477 | 0.4302%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 39 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.25141 | 12.8332 | 0.01959 | 0.25141 | 12.8332 | 0.01959 | 0.26484 | 13.5188 | 0.01959 | 0.2253%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 897 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 51.8857 | 295.1625 | 0.17579 | 51.8857 | 295.1625 | 0.17579 | 54.658 | 310.9334 | 0.17579 | 0.9644%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 111 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.34053 | 36.5251 | 0.0093232 | 0.34053 | 36.5251 | 0.0093232 | 0.35872 | 38.4767 | 0.0093232 | 0.117%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 119 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 52.0453 | 39.1576 | 1.3291 | 52.0453 | 39.1576 | 1.3291 | 54.8261 | 41.2498 | 1.3291 | 0.9978%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 253 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 107.7138 | 83.251 | 1.2938 | 107.7138 | 83.251 | 1.2938 | 113.4691 | 87.6992 | 1.2938 | 0.9977%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 241 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 129.4684 | 79.3023 | 1.6326 | 129.4684 | 79.3023 | 1.6326 | 136.386 | 83.5395 | 1.6326 | 0.9899%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 136 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 82.4531 | 44.7515 | 1.8425 | 82.4531 | 44.7515 | 1.8425 | 86.8586 | 47.1426 | 1.8425 | 0.982%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 592 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 381.43 | 194.8007 | 1.9581 | 381.43 | 194.8007 | 1.9581 | 401.8103 | 205.2091 | 1.9581 | 0.9903%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 30 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 5.3877 | 9.8717 | 0.54578 | 5.3877 | 9.8717 | 0.54578 | 5.6756 | 10.3991 | 0.54578 | 0.6775%
2026 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 1 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.4566 | 0.32906 | 4.4266 | 1.4566 | 0.32906 | 4.4266 | 1.5344 | 0.34664 | 4.4266 | 0.9944%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 4 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.7778 | 1.3162 | 3.6299 | 4.7778 | 1.3162 | 3.6299 | 5.033 | 1.3865 | 3.6299 | 0.9632%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.46874 | 5.2649 | 0.089032 | 0.46874 | 5.2649 | 0.089032 | 0.49379 | 5.5462 | 0.089032 | 0.9941%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 685 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 171.1238 | 225.4028 | 0.75919 | 171.1238 | 225.4028 | 0.75919 | 180.2671 | 237.4464 | 0.75919 | 0.9555%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 899 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 244.0922 | 295.8206 | 0.82514 | 244.0922 | 295.8206 | 0.82514 | 257.1344 | 311.6267 | 0.82514 | 0.994%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 188 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 23.3101 | 61.8624 | 0.37681 | 23.3101 | 61.8624 | 0.37681 | 24.5556 | 65.1678 | 0.37681 | 0.936%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 406 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 37.4045 | 133.5964 | 0.27998 | 37.4045 | 133.5964 | 0.27998 | 39.403 | 140.7346 | 0.27998 | 0.938%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 88 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 5.1753 | 28.9569 | 0.17872 | 5.1753 | 28.9569 | 0.17872 | 5.4518 | 30.5041 | 0.17872 | 0.8718%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 132 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 14.4092 | 43.4353 | 0.33174 | 14.4092 | 43.4353 | 0.33174 | 15.1791 | 45.7561 | 0.33174 | 0.9279%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 54 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 57.5552 | 17.769 | 3.2391 | 57.5552 | 17.769 | 3.2391 | 60.6304 | 18.7184 | 3.2391 | 0.9729%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 293 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 144.2009 | 96.4132 | 1.4957 | 144.2009 | 96.4132 | 1.4957 | 151.9058 | 101.5647 | 1.4957 | 0.9856%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 134 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 23.0424 | 44.0934 | 0.52258 | 23.0424 | 44.0934 | 0.52258 | 24.2735 | 46.4494 | 0.52258 | 0.9864%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 32 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 53.8256 | 10.5298 | 5.1118 | 53.8256 | 10.5298 | 5.1118 | 56.7015 | 11.0924 | 5.1118 | 0.9841%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 150 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 99.3275 | 49.3583 | 2.0124 | 99.3275 | 49.3583 | 2.0124 | 104.6347 | 51.9956 | 2.0124 | 0.9831%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 119 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 87.2089 | 39.1576 | 2.2271 | 87.2089 | 39.1576 | 2.2271 | 91.8686 | 41.2498 | 2.2271 | 0.9843%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.16865 | 0.65811 | 0.25626 | 0.16865 | 0.65811 | 0.25626 | 0.17766 | 0.69327 | 0.25626 | 0.9934%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 157 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 29.8416 | 51.6617 | 0.57763 | 29.8416 | 51.6617 | 0.57763 | 31.436 | 54.422 | 0.57763 | 0.9977%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 53 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 16.2275 | 17.4399 | 0.93048 | 16.2275 | 17.4399 | 0.93048 | 17.0946 | 18.3718 | 0.93048 | 0.9957%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 25 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 18.457 | 8.2264 | 2.2436 | 18.457 | 8.2264 | 2.2436 | 19.4432 | 8.6659 | 2.2436 | 0.9986%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 300 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 20.9297 | 98.7166 | 0.21202 | 20.9297 | 98.7166 | 0.21202 | 22.048 | 103.9911 | 0.21202 | 0.9923%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 133 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 136.5755 | 43.7643 | 3.1207 | 136.5755 | 43.7643 | 3.1207 | 143.873 | 46.1027 | 3.1207 | 0.9856%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 9 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 68.3702 | 2.9615 | 23.0864 | 68.3702 | 2.9615 | 23.0864 | 72.0233 | 3.1197 | 23.0864 | 0.9951%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 236 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 82.1782 | 77.657 | 1.0582 | 82.1782 | 77.657 | 1.0582 | 86.5691 | 81.8063 | 1.0582 | 0.9433%
2026 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 3 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 3.0791 | 0.98717 | 3.1191 | 3.0791 | 0.98717 | 3.1191 | 3.2436 | 1.0399 | 3.1191 | 0.9958%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 43 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 29.5835 | 14.1494 | 2.0908 | 29.5835 | 14.1494 | 2.0908 | 31.1642 | 14.9054 | 2.0908 | 0.9258%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 109 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 116.6696 | 35.867 | 3.2528 | 116.6696 | 35.867 | 3.2528 | 122.9034 | 37.7834 | 3.2528 | 0.9926%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 129 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 19.4046 | 42.4481 | 0.45714 | 19.4046 | 42.4481 | 0.45714 | 20.4414 | 44.7162 | 0.45714 | 0.9747%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 99 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.8721 | 32.5765 | 0.33374 | 10.8721 | 32.5765 | 0.33374 | 11.453 | 34.3171 | 0.33374 | 0.7093%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 91.0778 | 20.4014 | 4.4643 | 91.0778 | 20.4014 | 4.4643 | 95.9442 | 21.4915 | 4.4643 | 0.9829%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 47 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 174.0462 | 15.4656 | 11.2538 | 174.0462 | 15.4656 | 11.2538 | 183.3457 | 16.2919 | 11.2538 | 0.989%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 9 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 24.3129 | 2.9615 | 8.2097 | 24.3129 | 2.9615 | 8.2097 | 25.612 | 3.1197 | 8.2097 | 0.9937%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 103 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 50.8689 | 33.8927 | 1.5009 | 50.8689 | 33.8927 | 1.5009 | 53.5869 | 35.7036 | 1.5009 | 0.9631%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 226 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 174.04 | 74.3665 | 2.3403 | 174.04 | 74.3665 | 2.3403 | 183.3392 | 78.34 | 2.3403 | 0.9714%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 5 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 28.1165 | 1.6453 | 17.0892 | 28.1165 | 1.6453 | 17.0892 | 29.6188 | 1.7332 | 17.0892 | 0.9712%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 210 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 189.1139 | 69.1016 | 2.7368 | 189.1139 | 69.1016 | 2.7368 | 199.2185 | 72.7938 | 2.7368 | 0.9923%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 6 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.2067 | 1.9743 | 0.61118 | 1.2067 | 1.9743 | 0.61118 | 1.2711 | 2.0798 | 0.61118 | 0.9928%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 27 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.11704 | 8.8845 | 0.013173 | 0.11704 | 8.8845 | 0.013173 | 0.12329 | 9.3592 | 0.013173 | 0.9883%
2026 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 20 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.3301 | 6.5811 | 0.20211 | 1.3301 | 6.5811 | 0.20211 | 1.4012 | 6.9327 | 0.20211 | 0.9963%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 7 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.063433 | 2.3034 | 0.027539 | 0.063433 | 2.3034 | 0.027539 | 0.066823 | 2.4265 | 0.027539 | 0.9902%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 4 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 3.1321 | 1.3162 | 2.3796 | 3.1321 | 1.3162 | 2.3796 | 3.2994 | 1.3865 | 2.3796 | 0.9939%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 95 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.1444 | 31.2602 | 0.068598 | 2.1444 | 31.2602 | 0.068598 | 2.259 | 32.9305 | 0.068598 | 0.9666%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 381 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 81.9888 | 125.37 | 0.65397 | 81.9888 | 125.37 | 0.65397 | 86.3696 | 132.0687 | 0.65397 | 0.9986%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 124 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 78.5903 | 40.8028 | 1.9261 | 78.5903 | 40.8028 | 1.9261 | 82.7895 | 42.983 | 1.9261 | 0.9762%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.4212 | 0.32906 | 7.3579 | 2.4212 | 0.32906 | 7.3579 | 2.5505 | 0.34664 | 7.3579 | 0.9867%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 115 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 86.5756 | 37.8413 | 2.2879 | 86.5756 | 37.8413 | 2.2879 | 91.2014 | 39.8633 | 2.2879 | 0.9973%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 618 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 256.1133 | 203.3561 | 1.2594 | 256.1133 | 203.3561 | 1.2594 | 269.7978 | 214.2217 | 1.2594 | 0.9919%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 53 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 60.5455 | 17.4399 | 3.4717 | 60.5455 | 17.4399 | 3.4717 | 63.7806 | 18.3718 | 3.4717 | 0.9998%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 451 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 147.8841 | 148.4039 | 0.9965 | 147.8841 | 148.4039 | 0.9965 | 155.7857 | 156.3333 | 0.9965 | 0.9833%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 350 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 110.8755 | 115.1693 | 0.96272 | 110.8755 | 115.1693 | 0.96272 | 116.7997 | 121.323 | 0.96272 | 0.988%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 479 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 51.148 | 157.6174 | 0.32451 | 51.148 | 157.6174 | 0.32451 | 53.8809 | 166.0391 | 0.32451 | 0.9625%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 302 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.8412 | 99.3747 | 0.12922 | 12.8412 | 99.3747 | 0.12922 | 13.5273 | 104.6844 | 0.12922 | 0.9181%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 118 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 74.6808 | 38.8285 | 1.9234 | 74.6808 | 38.8285 | 1.9234 | 78.6711 | 40.9032 | 1.9234 | 0.9835%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 313 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 389.2135 | 102.9943 | 3.779 | 389.2135 | 102.9943 | 3.779 | 410.0097 | 108.4974 | 3.779 | 0.9889%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 226 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 31.9736 | 74.3665 | 0.42995 | 31.9736 | 74.3665 | 0.42995 | 33.682 | 78.34 | 0.42995 | 0.9191%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 273 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 213.2749 | 89.8321 | 2.3742 | 213.2749 | 89.8321 | 2.3742 | 224.6704 | 94.6319 | 2.3742 | 0.9908%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 2 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.4417 | 0.65811 | 2.1906 | 1.4417 | 0.65811 | 2.1906 | 1.5187 | 0.69327 | 2.1906 | 0.9858%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 71 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.8036 | 23.3629 | 0.33402 | 7.8036 | 23.3629 | 0.33402 | 8.2206 | 24.6112 | 0.33402 | 0.9652%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 434 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 523.2391 | 142.8099 | 3.6639 | 523.2391 | 142.8099 | 3.6639 | 551.1964 | 150.4405 | 3.6639 | 0.9927%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 1 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 54.3851 | 0.32906 | 165.2766 | 54.3851 | 0.32906 | 165.2766 | 57.291 | 0.34664 | 165.2766 | 0.9997%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 458 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 305.9761 | 150.7073 | 2.0303 | 305.9761 | 150.7073 | 2.0303 | 322.3248 | 158.7598 | 2.0303 | 0.9926%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 136 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.8658 | 44.7515 | 0.26515 | 11.8658 | 44.7515 | 0.26515 | 12.4998 | 47.1426 | 0.26515 | 0.9598%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 74 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 32.2825 | 24.3501 | 1.3258 | 32.2825 | 24.3501 | 1.3258 | 34.0074 | 25.6511 | 1.3258 | 0.9934%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 41 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 10.234 | 13.4913 | 0.75856 | 10.234 | 13.4913 | 0.75856 | 10.7808 | 14.2121 | 0.75856 | 0.6902%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 93 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 14.5549 | 30.6021 | 0.47562 | 14.5549 | 30.6021 | 0.47562 | 15.3325 | 32.2372 | 0.47562 | 0.7661%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 4.1265 | 0.65811 | 6.2702 | 4.1265 | 0.65811 | 6.2702 | 4.347 | 0.69327 | 6.2702 | 0.9947%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 34 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 123.222 | 11.1879 | 11.0139 | 123.222 | 11.1879 | 11.0139 | 129.8059 | 11.7857 | 11.0139 | 0.9966%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 309 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 143.1403 | 101.678 | 1.4078 | 143.1403 | 101.678 | 1.4078 | 150.7885 | 107.1108 | 1.4078 | 0.9905%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 657 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 268.7684 | 216.1893 | 1.2432 | 268.7684 | 216.1893 | 1.2432 | 283.129 | 227.7405 | 1.2432 | 0.9891%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 75 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 76.0524 | 24.6791 | 3.0816 | 76.0524 | 24.6791 | 3.0816 | 80.116 | 25.9978 | 3.0816 | 0.9946%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 25 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 41.3095 | 8.2264 | 5.0216 | 41.3095 | 8.2264 | 5.0216 | 43.5167 | 8.6659 | 5.0216 | 0.9952%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 123 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 138.6921 | 40.4738 | 3.4267 | 138.6921 | 40.4738 | 3.4267 | 146.1026 | 42.6364 | 3.4267 | 0.9843%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 319 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 106.3896 | 104.9686 | 1.0135 | 106.3896 | 104.9686 | 1.0135 | 112.0742 | 110.5772 | 1.0135 | 0.9898%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 88 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 75.3766 | 28.9569 | 2.6031 | 75.3766 | 28.9569 | 2.6031 | 79.4041 | 30.5041 | 2.6031 | 0.9853%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 704 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 219.7181 | 231.6548 | 0.94847 | 219.7181 | 231.6548 | 0.94847 | 231.4579 | 244.0325 | 0.94847 | 0.9839%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 407 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 213.075 | 133.9255 | 1.591 | 213.075 | 133.9255 | 1.591 | 224.4598 | 141.0813 | 1.591 | 0.9748%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 137 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 86.5106 | 45.0806 | 1.919 | 86.5106 | 45.0806 | 1.919 | 91.1329 | 47.4893 | 1.919 | 0.9912%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 80 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 48.0711 | 26.3244 | 1.8261 | 48.0711 | 26.3244 | 1.8261 | 50.6396 | 27.731 | 1.8261 | 0.9732%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 48 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 81.8457 | 15.7946 | 5.1819 | 81.8457 | 15.7946 | 5.1819 | 86.2189 | 16.6386 | 5.1819 | 0.9953%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 42 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 60.9876 | 13.8203 | 4.4129 | 60.9876 | 13.8203 | 4.4129 | 64.2463 | 14.5588 | 4.4129 | 0.9803%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 138 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 31.2181 | 45.4096 | 0.68748 | 31.2181 | 45.4096 | 0.68748 | 32.8861 | 47.8359 | 0.68748 | 0.9369%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 12 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 67.491 | 3.9487 | 17.0921 | 67.491 | 3.9487 | 17.0921 | 71.0971 | 4.1596 | 17.0921 | 0.9955%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 5 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 49.1533 | 1.6453 | 29.8754 | 49.1533 | 1.6453 | 29.8754 | 51.7796 | 1.7332 | 29.8754 | 0.803%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 17 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.9388 | 5.5939 | 0.70413 | 3.9388 | 5.5939 | 0.70413 | 4.1493 | 5.8928 | 0.70413 | 0.6587%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 107 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 43.563 | 35.2089 | 1.2373 | 43.563 | 35.2089 | 1.2373 | 45.8907 | 37.0902 | 1.2373 | 0.9978%
2026 | CB 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 82 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 31.7322 | 26.9825 | 1.176 | 31.7322 | 26.9825 | 1.176 | 33.4277 | 28.4242 | 1.176 | 0.9981%
2026 | CB 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 19 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 13.4423 | 6.252 | 2.1501 | 13.4423 | 6.252 | 2.1501 | 14.1606 | 6.5861 | 2.1501 | 0.9962%
2026 | CB 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.7804 | 0.98717 | 10.9206 | 10.7804 | 0.98717 | 10.9206 | 11.3564 | 1.0399 | 10.9206 | 0.9972%
2026 | CB 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 56 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.4261 | 18.4271 | 0.29446 | 5.4261 | 18.4271 | 0.29446 | 5.716 | 19.4117 | 0.29446 | 0.3454%
2026 | CB 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 80 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.4764 | 26.3244 | 0.20804 | 5.4764 | 26.3244 | 0.20804 | 5.769 | 27.731 | 0.20804 | 0.75%
2026 | CB 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 571 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 50.7476 | 187.8905 | 0.27009 | 50.7476 | 187.8905 | 0.27009 | 53.4591 | 197.9298 | 0.27009 | 0.8429%
2026 | CB 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 1192 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 62.8186 | 392.2338 | 0.16016 | 62.8186 | 392.2338 | 0.16016 | 66.175 | 413.1914 | 0.16016 | 0.9909%
2026 | CB 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 132 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.6866 | 43.4353 | 0.3151 | 13.6866 | 43.4353 | 0.3151 | 14.4179 | 45.7561 | 0.3151 | 0.9975%
2026 | CB 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 1.0286 | 1.3162 | 0.7815 | 1.0286 | 1.3162 | 0.7815 | 1.0836 | 1.3865 | 0.7815 | 0.9975%
2026 | CB 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 38 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 38.8495 | 12.5041 | 3.1069 | 38.8495 | 12.5041 | 3.1069 | 40.9253 | 13.1722 | 3.1069 | 0.9993%
2026 | CB 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 3 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.37491 | 0.98717 | 0.37978 | 0.37491 | 0.98717 | 0.37978 | 0.39494 | 1.0399 | 0.37978 | 0.9408%
2026 | CB 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 1 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.87925 | 0.32906 | 2.672 | 0.87925 | 0.32906 | 2.672 | 0.92622 | 0.34664 | 2.672 | 0.3549%
2026 | CB 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 1 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 3.0261 | 0.32906 | 9.1963 | 3.0261 | 0.32906 | 9.1963 | 3.1878 | 0.34664 | 9.1963 | 0.7993%
2026 | CB 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 58 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.8291 | 19.0852 | 0.20063 | 3.8291 | 19.0852 | 0.20063 | 4.0337 | 20.1049 | 0.20063 | 0.299%
2026 | CB 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 22 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.2158 | 7.2392 | 0.16795 | 1.2158 | 7.2392 | 0.16795 | 1.2808 | 7.626 | 0.16795 | 0.9512%
2026 | CB 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 248 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.17895 | 81.6057 | 0.0021929 | 0.17895 | 81.6057 | 0.0021929 | 0.18852 | 85.966 | 0.0021929 | 0.09583%
2026 | CB 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 89 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 8.1689 | 29.2859 | 0.27894 | 8.1689 | 29.2859 | 0.27894 | 8.6054 | 30.8507 | 0.27894 | 0.8082%
2026 | CB 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 36 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 2.0264 | 11.846 | 0.17107 | 2.0264 | 11.846 | 0.17107 | 2.1347 | 12.4789 | 0.17107 | 0.9981%
2026 | CB 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 209 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 23.6778 | 68.7725 | 0.34429 | 23.6778 | 68.7725 | 0.34429 | 24.9429 | 72.4471 | 0.34429 | 0.9929%
2026 | CB 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 277 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 15.2578 | 91.1483 | 0.1674 | 15.2578 | 91.1483 | 0.1674 | 16.0731 | 96.0185 | 0.1674 | 0.9737%
2026 | CB 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 730 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 38.8784 | 240.2103 | 0.16185 | 38.8784 | 240.2103 | 0.16185 | 40.9557 | 253.045 | 0.16185 | 0.9874%
2026 | CB 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 485 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 31.0776 | 159.5918 | 0.19473 | 31.0776 | 159.5918 | 0.19473 | 32.7382 | 168.119 | 0.19473 | 0.9888%
2026 | CB 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 236 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 118.3696 | 77.657 | 1.5243 | 118.3696 | 77.657 | 1.5243 | 124.6943 | 81.8063 | 1.5243 | 0.9762%
2026 | CB 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 2 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 20.0507 | 0.65811 | 30.4671 | 20.0507 | 0.65811 | 30.4671 | 21.1221 | 0.69327 | 30.4671 | 0.9954%
2026 | CB 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 134 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.7686 | 44.0934 | 0.2669 | 11.7686 | 44.0934 | 0.2669 | 12.3974 | 46.4494 | 0.2669 | 0.9768%
2026 | CB 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 18 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.4978 | 5.923 | 0.42171 | 2.4978 | 5.923 | 0.42171 | 2.6312 | 6.2395 | 0.42171 | 0.6436%
2026 | CB 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 10 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0574 | 3.2906 | 0.32133 | 1.0574 | 3.2906 | 0.32133 | 1.1139 | 3.4664 | 0.32133 | 0.375%
2026 | CB 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 167 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 12.35 | 54.9522 | 0.22474 | 12.35 | 54.9522 | 0.22474 | 13.0099 | 57.8884 | 0.22474 | 0.9%
2026 | CB 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 45 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.5459 | 14.8075 | 0.17193 | 2.5459 | 14.8075 | 0.17193 | 2.6819 | 15.5987 | 0.17193 | 0.7028%
2026 | CB 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 46 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 9.1325 | 15.1365 | 0.60334 | 9.1325 | 15.1365 | 0.60334 | 9.6204 | 15.9453 | 0.60334 | 0.995%
2026 | CB 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 79 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.6547 | 25.9954 | 0.29447 | 7.6547 | 25.9954 | 0.29447 | 8.0637 | 27.3843 | 0.29447 | 0.9704%
2026 | CB 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 82 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.60029 | 26.9825 | 0.022247 | 0.60029 | 26.9825 | 0.022247 | 0.63237 | 28.4242 | 0.022247 | 0.6647%
2026 | CB 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.099934 | 4.2777 | 0.023361 | 0.099934 | 4.2777 | 0.023361 | 0.10527 | 4.5063 | 0.023361 | 0.9726%
2026 | CB 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.8672 | 0.32906 | 42.1425 | 13.8672 | 0.32906 | 42.1425 | 14.6082 | 0.34664 | 42.1425 | 0.9979%
2026 | CB 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.9885 | 4.6068 | 0.43166 | 1.9885 | 4.6068 | 0.43166 | 2.0948 | 4.8529 | 0.43166 | 0.9683%
2026 | CB 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 96 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.39533 | 31.5893 | 0.012515 | 0.39533 | 31.5893 | 0.012515 | 0.41646 | 33.2772 | 0.012515 | 0.3335%
2026 | CB 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 211 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 138.8006 | 69.4306 | 1.9991 | 138.8006 | 69.4306 | 1.9991 | 146.2169 | 73.1404 | 1.9991 | 0.9966%
2026 | CB 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 22 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.83174 | 7.2392 | 0.11489 | 0.83174 | 7.2392 | 0.11489 | 0.87618 | 7.626 | 0.11489 | 0.9922%
2026 | CB 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.071388 | 0.32906 | 0.21695 | 0.071388 | 0.32906 | 0.21695 | 0.075203 | 0.34664 | 0.21695 | 0.986%
2026 | CB 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 376 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 106.4306 | 123.7247 | 0.86022 | 106.4306 | 123.7247 | 0.86022 | 112.1173 | 130.3355 | 0.86022 | 0.9884%
2026 | CB 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.064342 | 0.32906 | 0.19554 | 0.064342 | 0.32906 | 0.19554 | 0.06778 | 0.34664 | 0.19554 | 0.991%
2026 | CB 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 184 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 55.9658 | 60.5462 | 0.92435 | 55.9658 | 60.5462 | 0.92435 | 58.9561 | 63.7812 | 0.92435 | 0.9601%
2026 | CB 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.5513 | 4.6068 | 0.33673 | 1.5513 | 4.6068 | 0.33673 | 1.6341 | 4.8529 | 0.33673 | 0.1888%
2026 | CB 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 2 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.91644 | 0.65811 | 1.3925 | 0.91644 | 0.65811 | 1.3925 | 0.9654 | 0.69327 | 1.3925 | 0.1434%
2026 | CB 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 40 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 10.1685 | 13.1622 | 0.77255 | 10.1685 | 13.1622 | 0.77255 | 10.7118 | 13.8655 | 0.77255 | 0.9408%
2026 | CB 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 56 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 63.0506 | 18.4271 | 3.4216 | 63.0506 | 18.4271 | 3.4216 | 66.4195 | 19.4117 | 3.4216 | 0.9549%
2026 | CB 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.17532 | 0.98717 | 0.1776 | 0.17532 | 0.98717 | 0.1776 | 0.18468 | 1.0399 | 0.1776 | 0.9464%
2026 | CB 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 1 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.016493 | 0.32906 | 0.050124 | 0.016493 | 0.32906 | 0.050124 | 0.017375 | 0.34664 | 0.050124 | 0.9786%
2026 | CB 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 11 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.019677 | 3.6196 | 0.0054362 | 0.019677 | 3.6196 | 0.0054362 | 0.020728 | 3.813 | 0.0054362 | 0.1679%
2026 | CB 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 277 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 9.1717 | 91.1483 | 0.10062 | 9.1717 | 91.1483 | 0.10062 | 9.6618 | 96.0185 | 0.10062 | 0.8949%
2026 | CB 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 87 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 1.0843 | 28.6278 | 0.037875 | 1.0843 | 28.6278 | 0.037875 | 1.1422 | 30.1574 | 0.037875 | 0.372%
2026 | CB 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 12 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.3276 | 3.9487 | 1.096 | 4.3276 | 3.9487 | 1.096 | 4.5588 | 4.1596 | 1.096 | 0.9425%
2026 | CB 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 8 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.39328 | 2.6324 | 0.1494 | 0.39328 | 2.6324 | 0.1494 | 0.4143 | 2.7731 | 0.1494 | 0.7619%
2026 | CB 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 56 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.63661 | 18.4271 | 0.034548 | 0.63661 | 18.4271 | 0.034548 | 0.67063 | 19.4117 | 0.034548 | 0.9924%
2026 | CB 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 45 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.6457 | 14.8075 | 0.58387 | 8.6457 | 14.8075 | 0.58387 | 9.1076 | 15.5987 | 0.58387 | 0.9545%
2026 | CB 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 20 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 3.1226 | 6.5811 | 0.47448 | 3.1226 | 6.5811 | 0.47448 | 3.2895 | 6.9327 | 0.47448 | 0.7837%
2026 | CB 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 375 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 41.1623 | 123.3957 | 0.33358 | 41.1623 | 123.3957 | 0.33358 | 43.3617 | 129.9889 | 0.33358 | 0.9981%
2026 | CB 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 47 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.48675 | 15.4656 | 0.031473 | 0.48675 | 15.4656 | 0.031473 | 0.51276 | 16.2919 | 0.031473 | 0.9266%
2026 | CB 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 23 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 77.7152 | 7.5683 | 10.2686 | 77.7152 | 7.5683 | 10.2686 | 81.8676 | 7.9727 | 10.2686 | 0.9507%
2026 | CB 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 104 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.40449 | 34.2217 | 0.01182 | 0.40449 | 34.2217 | 0.01182 | 0.4261 | 36.0503 | 0.01182 | 0.9943%
2026 | CB 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 26 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 26.1161 | 8.5554 | 3.0526 | 26.1161 | 8.5554 | 3.0526 | 27.5116 | 9.0126 | 3.0526 | 0.9983%
2026 | CB 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 89 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 3.01 | 29.2859 | 0.10278 | 3.01 | 29.2859 | 0.10278 | 3.1708 | 30.8507 | 0.10278 | 0.9343%
2026 | CB 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 2 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.3936 | 0.65811 | 3.6371 | 2.3936 | 0.65811 | 3.6371 | 2.5215 | 0.69327 | 3.6371 | 0.9997%
2026 | CB 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 34 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 108.7518 | 11.1879 | 9.7205 | 108.7518 | 11.1879 | 9.7205 | 114.5625 | 11.7857 | 9.7205 | 0.9951%
2026 | CB 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 36 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 12.3822 | 11.846 | 1.0453 | 12.3822 | 11.846 | 1.0453 | 13.0438 | 12.4789 | 1.0453 | 0.9951%
2026 | CB 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 341 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.6886 | 112.2078 | 0.032873 | 3.6886 | 112.2078 | 0.032873 | 3.8857 | 118.2032 | 0.032873 | 0.997%
2026 | CB 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 23 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.2619 | 7.5683 | 0.16674 | 1.2619 | 7.5683 | 0.16674 | 1.3294 | 7.9727 | 0.16674 | 0.9965%
2026 | CB CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.23647 | 0.65811 | 0.35932 | 0.23647 | 0.65811 | 0.35932 | 0.24911 | 0.69327 | 0.35932 | 0.9021%
2026 | CB FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 161 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.2209 | 52.9779 | 0.023046 | 1.2209 | 52.9779 | 0.023046 | 1.2862 | 55.8086 | 0.023046 | 0.3693%
2026 | CB FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 154 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 9.2645 | 50.6745 | 0.18282 | 9.2645 | 50.6745 | 0.18282 | 9.7595 | 53.3821 | 0.18282 | 0.9433%
2026 | CB JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 126 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 14.297 | 41.461 | 0.34483 | 14.297 | 41.461 | 0.34483 | 15.0609 | 43.6763 | 0.34483 | 0.9785%
2026 | CB MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 97 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 48.1334 | 31.9184 | 1.508 | 48.1334 | 31.9184 | 1.508 | 50.7052 | 33.6238 | 1.508 | 0.9856%
2026 | CB NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 10 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 6.027 | 3.2906 | 1.8316 | 6.027 | 3.2906 | 1.8316 | 6.349 | 3.4664 | 1.8316 | 0.9902%
2026 | CB OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 593 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 65.3114 | 195.1297 | 0.33471 | 65.3114 | 195.1297 | 0.33471 | 68.8011 | 205.5558 | 0.33471 | 0.99%
2026 | CB PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 510 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 27.3578 | 167.8181 | 0.16302 | 27.3578 | 167.8181 | 0.16302 | 28.8196 | 176.7849 | 0.16302 | 0.9473%
2026 | CB RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 214 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 98.6268 | 70.4178 | 1.4006 | 98.6268 | 70.4178 | 1.4006 | 103.8966 | 74.1803 | 1.4006 | 0.9831%
2026 | CB RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 170 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 48.9483 | 55.9394 | 0.87502 | 48.9483 | 55.9394 | 0.87502 | 51.5636 | 58.9283 | 0.87502 | 0.9811%
2026 | CB RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 44 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 6.074 | 14.4784 | 0.41952 | 6.074 | 14.4784 | 0.41952 | 6.3986 | 15.252 | 0.41952 | 0.695%
2026 | CB RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.28348 | 0.98717 | 0.28717 | 0.28348 | 0.98717 | 0.28717 | 0.29863 | 1.0399 | 0.28717 | 0.9988%
2026 | CB RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 182 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 35.3682 | 59.888 | 0.59057 | 35.3682 | 59.888 | 0.59057 | 37.258 | 63.0879 | 0.59057 | 0.9914%
2026 | CB SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 316 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 30.0514 | 103.9814 | 0.28901 | 30.0514 | 103.9814 | 0.28901 | 31.6571 | 109.5373 | 0.28901 | 0.9371%
2026 | CB SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 22 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.017997 | 7.2392 | 0.0024861 | 0.017997 | 7.2392 | 0.0024861 | 0.018959 | 7.626 | 0.0024861 | 0.02003%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 375 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 15.535 | 123.3957 | 0.1259 | 15.535 | 123.3957 | 0.1259 | 16.3651 | 129.9889 | 0.1259 | 0.789%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 113 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 33.7655 | 37.1832 | 0.90808 | 33.7655 | 37.1832 | 0.90808 | 35.5697 | 39.17 | 0.90808 | 0.9517%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 254 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 88.4904 | 83.58 | 1.0588 | 88.4904 | 83.58 | 1.0588 | 93.2185 | 88.0458 | 1.0588 | 0.9933%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 570 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 64.412 | 187.5615 | 0.34342 | 64.412 | 187.5615 | 0.34342 | 67.8536 | 197.5831 | 0.34342 | 0.9757%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 73 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 56.3376 | 24.021 | 2.3453 | 56.3376 | 24.021 | 2.3453 | 59.3477 | 25.3045 | 2.3453 | 0.9932%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 239 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 35.8983 | 78.6442 | 0.45647 | 35.8983 | 78.6442 | 0.45647 | 37.8164 | 82.8463 | 0.45647 | 0.9948%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 5 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.0558 | 1.5695 | 0.67272 | 1.0558 | 1.5695 | 0.67272 | 1.1717 | 1.7417 | 0.67272 | 0.9903%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 34 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.6908 | 10.6725 | 0.34582 | 3.6908 | 10.6725 | 0.34582 | 4.0957 | 11.8434 | 0.34582 | 0.9915%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 620 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 35.1217 | 194.6157 | 0.18047 | 35.1217 | 194.6157 | 0.18047 | 38.9752 | 215.9685 | 0.18047 | 0.9141%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 510 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 316.78 | 160.0871 | 1.9788 | 316.78 | 160.0871 | 1.9788 | 351.5364 | 177.6515 | 1.9788 | 0.9902%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 72 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 63.0347 | 22.6005 | 2.7891 | 63.0347 | 22.6005 | 2.7891 | 69.9507 | 25.0802 | 2.7891 | 0.9818%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 230 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 170.7952 | 72.1961 | 2.3657 | 170.7952 | 72.1961 | 2.3657 | 189.5344 | 80.1173 | 2.3657 | 0.997%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 99 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 45.5855 | 31.0757 | 1.4669 | 45.5855 | 31.0757 | 1.4669 | 50.5871 | 34.4853 | 1.4669 | 0.9951%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 32 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 12.565 | 10.0447 | 1.2509 | 12.565 | 10.0447 | 1.2509 | 13.9437 | 11.1468 | 1.2509 | 0.9958%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 20 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 7.1996 | 6.2779 | 1.1468 | 7.1996 | 6.2779 | 1.1468 | 7.9895 | 6.9667 | 1.1468 | 0.996%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 145 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 88.8468 | 45.515 | 1.952 | 88.8468 | 45.515 | 1.952 | 98.5948 | 50.5088 | 1.952 | 0.9962%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 5 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.2724 | 1.5695 | 3.9965 | 6.2724 | 1.5695 | 3.9965 | 6.9606 | 1.7417 | 3.9965 | 0.9922%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 57 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 45.7686 | 17.8921 | 2.558 | 45.7686 | 17.8921 | 2.558 | 50.7903 | 19.8552 | 2.558 | 0.9916%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 198 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 26.0989 | 62.1515 | 0.41992 | 26.0989 | 62.1515 | 0.41992 | 28.9624 | 68.9706 | 0.41992 | 0.9924%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 886 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 82.7087 | 278.1121 | 0.29739 | 82.7087 | 278.1121 | 0.29739 | 91.7833 | 308.6259 | 0.29739 | 0.9598%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 587 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 33.4452 | 184.2571 | 0.18151 | 33.4452 | 184.2571 | 0.18151 | 37.1147 | 204.4734 | 0.18151 | 0.9739%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 101 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.6715 | 31.7035 | 0.14735 | 4.6715 | 31.7035 | 0.14735 | 5.1841 | 35.182 | 0.14735 | 0.8768%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 14 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 45.818 | 4.3945 | 10.4261 | 45.818 | 4.3945 | 10.4261 | 50.845 | 4.8767 | 10.4261 | 0.9826%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 117 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 106.0165 | 36.7259 | 2.8867 | 106.0165 | 36.7259 | 2.8867 | 117.6484 | 40.7553 | 2.8867 | 0.9858%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 50 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 19.4652 | 15.6948 | 1.2402 | 19.4652 | 15.6948 | 1.2402 | 21.6009 | 17.4168 | 1.2402 | 0.9945%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 307 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 59.4414 | 96.3662 | 0.61683 | 59.4414 | 96.3662 | 0.61683 | 65.9631 | 106.9392 | 0.61683 | 0.9866%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 298 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 228.4185 | 93.5411 | 2.4419 | 228.4185 | 93.5411 | 2.4419 | 253.4801 | 103.8042 | 2.4419 | 0.9914%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 474 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 254.5346 | 148.7868 | 1.7107 | 254.5346 | 148.7868 | 1.7107 | 282.4616 | 165.1114 | 1.7107 | 0.9849%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 159 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 240.8882 | 49.9095 | 4.8265 | 240.8882 | 49.9095 | 4.8265 | 267.3178 | 55.3855 | 4.8265 | 0.9916%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 740 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 141.5109 | 232.2832 | 0.60922 | 141.5109 | 232.2832 | 0.60922 | 157.0372 | 257.7688 | 0.60922 | 0.9745%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 49 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14198 | 15.3809 | 0.0092306 | 0.14198 | 15.3809 | 0.0092306 | 0.15755 | 17.0685 | 0.0092306 | 0.8684%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 18 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.031422 | 5.6501 | 0.0055612 | 0.031422 | 5.6501 | 0.0055612 | 0.034869 | 6.2701 | 0.0055612 | 0.1275%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 2 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.019984 | 0.62779 | 0.031832 | 0.019984 | 0.62779 | 0.031832 | 0.022176 | 0.69667 | 0.031832 | 0.3435%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 5 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.5975 | 1.5695 | 4.2036 | 6.5975 | 1.5695 | 4.2036 | 7.3213 | 1.7417 | 4.2036 | 0.9924%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 72 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.8584 | 22.6005 | 0.34771 | 7.8584 | 22.6005 | 0.34771 | 8.7207 | 25.0802 | 0.34771 | 0.9393%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 2 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1281 | 0.62779 | 1.7969 | 1.1281 | 0.62779 | 1.7969 | 1.2518 | 0.69667 | 1.7969 | 0.8802%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 252 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 53.4767 | 79.1019 | 0.67605 | 53.4767 | 79.1019 | 0.67605 | 59.3441 | 87.7807 | 0.67605 | 0.9962%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 260 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 45.2456 | 81.613 | 0.55439 | 45.2456 | 81.613 | 0.55439 | 50.2098 | 90.5674 | 0.55439 | 0.9962%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 214 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 22.8419 | 67.1738 | 0.34004 | 22.8419 | 67.1738 | 0.34004 | 25.3481 | 74.544 | 0.34004 | 0.9984%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 47 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.85678 | 14.7531 | 0.058074 | 0.85678 | 14.7531 | 0.058074 | 0.95078 | 16.3718 | 0.058074 | 0.9877%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 4 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 19.4557 | 1.2556 | 15.4953 | 19.4557 | 1.2556 | 15.4953 | 21.5904 | 1.3933 | 15.4953 | 0.9968%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 24 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 38.4457 | 7.5335 | 5.1033 | 38.4457 | 7.5335 | 5.1033 | 42.6639 | 8.3601 | 5.1033 | 0.9992%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 17 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.5858 | 5.3362 | 0.67197 | 3.5858 | 5.3362 | 0.67197 | 3.9792 | 5.9217 | 0.67197 | 0.945%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 60 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.1314 | 18.8338 | 0.37865 | 7.1314 | 18.8338 | 0.37865 | 7.9138 | 20.9002 | 0.37865 | 0.994%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 840 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 38.673 | 263.6729 | 0.14667 | 38.673 | 263.6729 | 0.14667 | 42.9161 | 292.6024 | 0.14667 | 0.9112%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 10 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.8164 | 3.139 | 0.57866 | 1.8164 | 3.139 | 0.57866 | 2.0157 | 3.4834 | 0.57866 | 0.9662%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 2 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.2059 | 0.62779 | 3.5138 | 2.2059 | 0.62779 | 3.5138 | 2.4479 | 0.69667 | 3.5138 | 0.9775%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 45 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 35.4566 | 14.1253 | 2.5101 | 35.4566 | 14.1253 | 2.5101 | 39.3468 | 15.6751 | 2.5101 | 0.9826%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 53 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 91.7746 | 16.6365 | 5.5165 | 91.7746 | 16.6365 | 5.5165 | 101.8439 | 18.4618 | 5.5165 | 0.9977%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 215 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 93.0711 | 67.4877 | 1.3791 | 93.0711 | 67.4877 | 1.3791 | 103.2827 | 74.8923 | 1.3791 | 0.9908%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 28 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 54.7545 | 8.7891 | 6.2298 | 54.7545 | 8.7891 | 6.2298 | 60.762 | 9.7534 | 6.2298 | 0.9788%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 21 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 19.0873 | 6.5918 | 2.8956 | 19.0873 | 6.5918 | 2.8956 | 21.1815 | 7.3151 | 2.8956 | 0.9469%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 186 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 76.3476 | 58.3847 | 1.3077 | 76.3476 | 58.3847 | 1.3077 | 84.7243 | 64.7905 | 1.3077 | 0.9648%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 75 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.9788 | 23.5422 | 0.59377 | 13.9788 | 23.5422 | 0.59377 | 15.5125 | 26.1252 | 0.59377 | 0.9856%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 117 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 31.901 | 36.7259 | 0.86862 | 31.901 | 36.7259 | 0.86862 | 35.4011 | 40.7553 | 0.86862 | 0.9842%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 246 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 26.5819 | 77.2185 | 0.34424 | 26.5819 | 77.2185 | 0.34424 | 29.4984 | 85.6907 | 0.34424 | 0.979%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 35 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 12.4803 | 10.9864 | 1.136 | 12.4803 | 10.9864 | 1.136 | 13.8496 | 12.1918 | 1.136 | 0.9892%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 94 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 38.6065 | 29.5063 | 1.3084 | 38.6065 | 29.5063 | 1.3084 | 42.8424 | 32.7436 | 1.3084 | 0.9866%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 2 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.732 | 0.62779 | 5.9446 | 3.732 | 0.62779 | 5.9446 | 4.1414 | 0.69667 | 5.9446 | 0.9965%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 17 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.1418 | 5.3362 | 0.77617 | 4.1418 | 5.3362 | 0.77617 | 4.5962 | 5.9217 | 0.77617 | 0.9977%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 55 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.6502 | 17.2643 | 0.61689 | 10.6502 | 17.2643 | 0.61689 | 11.8187 | 19.1585 | 0.61689 | 0.9935%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 9 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.4325 | 2.8251 | 0.50708 | 1.4325 | 2.8251 | 0.50708 | 1.5897 | 3.135 | 0.50708 | 0.9948%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 33 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.9301 | 10.3586 | 1.6344 | 16.9301 | 10.3586 | 1.6344 | 18.7877 | 11.4951 | 1.6344 | 0.9905%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 63 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 54.3399 | 19.7755 | 2.7478 | 54.3399 | 19.7755 | 2.7478 | 60.302 | 21.9452 | 2.7478 | 0.9304%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 25 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 58.631 | 7.8474 | 7.4714 | 58.631 | 7.8474 | 7.4714 | 65.0638 | 8.7084 | 7.4714 | 0.9454%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 335 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 106.1245 | 105.1553 | 1.0092 | 106.1245 | 105.1553 | 1.0092 | 117.7682 | 116.6926 | 1.0092 | 0.9926%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 91 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 32.9139 | 28.5646 | 1.1523 | 32.9139 | 28.5646 | 1.1523 | 36.5251 | 31.6986 | 1.1523 | 0.9815%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 35 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.5188 | 10.9864 | 0.32028 | 3.5188 | 10.9864 | 0.32028 | 3.9048 | 12.1918 | 0.32028 | 0.9046%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 8 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 18.4141 | 2.5112 | 7.3329 | 18.4141 | 2.5112 | 7.3329 | 20.4345 | 2.7867 | 7.3329 | 0.8554%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 101 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 39.2397 | 31.7035 | 1.2377 | 39.2397 | 31.7035 | 1.2377 | 43.545 | 35.182 | 1.2377 | 0.9867%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.52959 | 1.2556 | 0.42179 | 0.52959 | 1.2556 | 0.42179 | 0.58769 | 1.3933 | 0.42179 | 0.9994%
2027 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 14 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 4.3945 | 0 | 0 | 4.3945 | 0 | 0 | 4.8767 | 0 | 0%
2027 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 8 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2.5112 | 0 | 0 | 2.5112 | 0 | 0 | 2.7867 | 0 | 0%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 58 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 144.1626 | 18.206 | 7.9184 | 144.1626 | 18.206 | 7.9184 | 159.9798 | 20.2035 | 7.9184 | 0.9909%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.45452 | 2.1973 | 0.20686 | 0.45452 | 2.1973 | 0.20686 | 0.50439 | 2.4384 | 0.20686 | 0.2981%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.73678 | 0.3139 | 2.3472 | 0.73678 | 0.3139 | 2.3472 | 0.81761 | 0.34834 | 2.3472 | 0.9995%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 151 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 73.6943 | 47.3983 | 1.5548 | 73.6943 | 47.3983 | 1.5548 | 81.7799 | 52.5988 | 1.5548 | 0.9925%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 444 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 335.2263 | 139.3699 | 2.4053 | 335.2263 | 139.3699 | 2.4053 | 372.0065 | 154.6613 | 2.4053 | 0.9936%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 4 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.067341 | 1.2556 | 0.053633 | 0.067341 | 1.2556 | 0.053633 | 0.07473 | 1.3933 | 0.053633 | 0.895%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 42 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.3406 | 13.1836 | 0.25339 | 3.3406 | 13.1836 | 0.25339 | 3.7072 | 14.6301 | 0.25339 | 0.8771%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 319 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 46.3352 | 100.1329 | 0.46274 | 46.3352 | 100.1329 | 0.46274 | 51.419 | 111.1193 | 0.46274 | 0.9246%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 26 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 27.5199 | 8.1613 | 3.372 | 27.5199 | 8.1613 | 3.372 | 30.5393 | 9.0567 | 3.372 | 0.9907%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 61 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 34.9145 | 19.1477 | 1.8234 | 34.9145 | 19.1477 | 1.8234 | 38.7452 | 21.2485 | 1.8234 | 0.9899%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 124 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 27.3993 | 38.9231 | 0.70393 | 27.3993 | 38.9231 | 0.70393 | 30.4055 | 43.1937 | 0.70393 | 0.9527%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 208 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 15.2942 | 65.2904 | 0.23425 | 15.2942 | 65.2904 | 0.23425 | 16.9722 | 72.4539 | 0.23425 | 0.8154%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 114 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.1452 | 35.7842 | 0.45118 | 16.1452 | 35.7842 | 0.45118 | 17.9167 | 39.7103 | 0.45118 | 0.9501%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 323 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 165.5087 | 101.3885 | 1.6324 | 165.5087 | 101.3885 | 1.6324 | 183.6679 | 112.5126 | 1.6324 | 0.97%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 419 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 36.3343 | 131.5225 | 0.27626 | 36.3343 | 131.5225 | 0.27626 | 40.3209 | 145.9529 | 0.27626 | 0.991%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.0463 | 16.6365 | 1.0246 | 17.0463 | 16.6365 | 1.0246 | 18.9166 | 18.4618 | 1.0246 | 0.7065%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 166 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 38.9182 | 52.1068 | 0.74689 | 38.9182 | 52.1068 | 0.74689 | 43.1883 | 57.8238 | 0.74689 | 0.9752%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 248 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 50.6068 | 77.8463 | 0.65009 | 50.6068 | 77.8463 | 0.65009 | 56.1593 | 86.3874 | 0.65009 | 0.9686%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 143 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.0694 | 44.8872 | 0.13521 | 6.0694 | 44.8872 | 0.13521 | 6.7353 | 49.8121 | 0.13521 | 0.7976%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 96 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 103.5696 | 30.134 | 3.437 | 103.5696 | 30.134 | 3.437 | 114.9331 | 33.4403 | 3.437 | 0.9877%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 37.3556 | 19.7755 | 1.889 | 37.3556 | 19.7755 | 1.889 | 41.4542 | 21.9452 | 1.889 | 0.981%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 234 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 88.9924 | 73.4517 | 1.2116 | 88.9924 | 73.4517 | 1.2116 | 98.7564 | 81.5107 | 1.2116 | 0.9713%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 19 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.4896 | 5.964 | 0.41743 | 2.4896 | 5.964 | 0.41743 | 2.7627 | 6.6184 | 0.41743 | 0.6764%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 62 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 30.2493 | 19.4616 | 1.5543 | 30.2493 | 19.4616 | 1.5543 | 33.5682 | 21.5968 | 1.5543 | 0.9774%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 95 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 43.8683 | 29.8201 | 1.4711 | 43.8683 | 29.8201 | 1.4711 | 48.6815 | 33.0919 | 1.4711 | 0.977%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 299 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 116.04 | 93.855 | 1.2364 | 116.04 | 93.855 | 1.2364 | 128.7717 | 104.1525 | 1.2364 | 0.968%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.2848 | 1.5695 | 8.4644 | 13.2848 | 1.5695 | 8.4644 | 14.7424 | 1.7417 | 8.4644 | 0.8924%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 11 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 21.0957 | 3.4529 | 6.1096 | 21.0957 | 3.4529 | 6.1096 | 23.4103 | 3.8317 | 6.1096 | 0.7823%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 1 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.39517 | 0.3139 | 1.2589 | 0.39517 | 0.3139 | 1.2589 | 0.43853 | 0.34834 | 1.2589 | 0.9121%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 357 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 102.2536 | 112.061 | 0.91248 | 102.2536 | 112.061 | 0.91248 | 113.4727 | 124.356 | 0.91248 | 0.9429%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 5 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 17.6009 | 1.5695 | 11.2144 | 17.6009 | 1.5695 | 11.2144 | 19.532 | 1.7417 | 11.2144 | 0.9974%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 208 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 38.1899 | 65.2904 | 0.58492 | 38.1899 | 65.2904 | 0.58492 | 42.38 | 72.4539 | 0.58492 | 0.9922%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 4 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 5.9162 | 1.2556 | 4.7119 | 5.9162 | 1.2556 | 4.7119 | 6.5653 | 1.3933 | 4.7119 | 0.9914%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 26 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.9074 | 8.1613 | 0.23371 | 1.9074 | 8.1613 | 0.23371 | 2.1166 | 9.0567 | 0.23371 | 0.6623%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 87 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.1889 | 27.309 | 0.11677 | 3.1889 | 27.309 | 0.11677 | 3.5387 | 30.3053 | 0.11677 | 0.7437%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 254 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 14.4213 | 79.7297 | 0.18088 | 14.4213 | 79.7297 | 0.18088 | 16.0036 | 88.4774 | 0.18088 | 0.9193%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 14 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.058051 | 4.3945 | 0.01321 | 0.058051 | 4.3945 | 0.01321 | 0.06442 | 4.8767 | 0.01321 | 0.9638%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 21 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.4596 | 6.5918 | 1.2833 | 8.4596 | 6.5918 | 1.2833 | 9.3877 | 7.3151 | 1.2833 | 0.9553%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 38 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.3008 | 11.9281 | 0.36056 | 4.3008 | 11.9281 | 0.36056 | 4.7727 | 13.2368 | 0.36056 | 0.9636%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 35 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 11.614 | 10.9864 | 1.0571 | 11.614 | 10.9864 | 1.0571 | 12.8883 | 12.1918 | 1.0571 | 0.9978%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 180 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 27.0186 | 56.5013 | 0.47819 | 27.0186 | 56.5013 | 0.47819 | 29.9831 | 62.7005 | 0.47819 | 0.9975%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 515 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 76.8107 | 161.6566 | 0.47515 | 76.8107 | 161.6566 | 0.47515 | 85.2382 | 179.3932 | 0.47515 | 0.9974%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 55 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.0842 | 17.2643 | 0.23657 | 4.0842 | 17.2643 | 0.23657 | 4.5324 | 19.1585 | 0.23657 | 0.901%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 44 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.0972 | 13.8114 | 0.58627 | 8.0972 | 13.8114 | 0.58627 | 8.9856 | 15.3268 | 0.58627 | 0.8573%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 67 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.094 | 21.0311 | 0.052018 | 1.094 | 21.0311 | 0.052018 | 1.214 | 23.3385 | 0.052018 | 0.7047%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 15 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.4697 | 4.7084 | 0.31214 | 1.4697 | 4.7084 | 0.31214 | 1.6309 | 5.225 | 0.31214 | 0.5082%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 70 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.7688 | 21.9727 | 0.44459 | 9.7688 | 21.9727 | 0.44459 | 10.8406 | 24.3835 | 0.44459 | 0.8949%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 129 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.8754 | 40.4926 | 0.34266 | 13.8754 | 40.4926 | 0.34266 | 15.3977 | 44.9354 | 0.34266 | 0.8426%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 264 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 15.667 | 82.8686 | 0.18906 | 15.667 | 82.8686 | 0.18906 | 17.386 | 91.9608 | 0.18906 | 0.9106%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 63 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.1003 | 19.7755 | 0.76359 | 15.1003 | 19.7755 | 0.76359 | 16.7571 | 21.9452 | 0.76359 | 0.9543%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 51 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 13.5718 | 16.0087 | 0.84778 | 13.5718 | 16.0087 | 0.84778 | 15.0609 | 17.7651 | 0.84778 | 0.9497%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 5 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.4971 | 1.5695 | 3.5025 | 5.4971 | 1.5695 | 3.5025 | 6.1003 | 1.7417 | 3.5025 | 0.9907%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 291 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 44.1009 | 91.3438 | 0.4828 | 44.1009 | 91.3438 | 0.4828 | 48.9396 | 101.3658 | 0.4828 | 0.9915%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 1 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.2803 | 0.3139 | 35.9363 | 11.2803 | 0.3139 | 35.9363 | 12.5179 | 0.34834 | 35.9363 | 0.9792%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 68 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.7819 | 21.3449 | 0.41143 | 8.7819 | 21.3449 | 0.41143 | 9.7454 | 23.6869 | 0.41143 | 0.9662%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 10 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.3089 | 3.139 | 0.73556 | 2.3089 | 3.139 | 0.73556 | 2.5622 | 3.4834 | 0.73556 | 0.9706%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 50 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.1223 | 15.6948 | 0.83609 | 13.1223 | 15.6948 | 0.83609 | 14.562 | 17.4168 | 0.83609 | 0.9727%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 81 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 24.0425 | 25.4256 | 0.9456 | 24.0425 | 25.4256 | 0.9456 | 26.6803 | 28.2152 | 0.9456 | 0.9578%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.1807 | 5.964 | 1.5393 | 9.1807 | 5.964 | 1.5393 | 10.1879 | 6.6184 | 1.5393 | 0.9712%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 7 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.9338 | 2.1973 | 0.42498 | 0.9338 | 2.1973 | 0.42498 | 1.0363 | 2.4384 | 0.42498 | 0.9778%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 42 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 19.4357 | 13.1836 | 1.4742 | 19.4357 | 13.1836 | 1.4742 | 21.5682 | 14.6301 | 1.4742 | 0.9872%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 59 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.0944 | 18.5199 | 0.70705 | 13.0944 | 18.5199 | 0.70705 | 14.5311 | 20.5518 | 0.70705 | 0.9782%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 270 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 236.5383 | 84.752 | 2.7909 | 236.5383 | 84.752 | 2.7909 | 262.4908 | 94.0508 | 2.7909 | 0.9891%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 487 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 60.3082 | 152.8675 | 0.39451 | 60.3082 | 152.8675 | 0.39451 | 66.9251 | 169.6398 | 0.39451 | 0.9941%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 158 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.2902 | 49.5956 | 0.086503 | 4.2902 | 49.5956 | 0.086503 | 4.7609 | 55.0371 | 0.086503 | 0.974%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 69 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.5637 | 21.6588 | 0.16454 | 3.5637 | 21.6588 | 0.16454 | 3.9547 | 24.0352 | 0.16454 | 0.9786%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 105 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.6112 | 32.9591 | 0.13991 | 4.6112 | 32.9591 | 0.13991 | 5.1171 | 36.5753 | 0.13991 | 0.9871%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 154 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 19.9133 | 48.34 | 0.41194 | 19.9133 | 48.34 | 0.41194 | 22.0981 | 53.6438 | 0.41194 | 0.9909%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 534 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 13.4254 | 167.6206 | 0.080094 | 13.4254 | 167.6206 | 0.080094 | 14.8984 | 186.0116 | 0.080094 | 0.8569%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 96 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 201.8812 | 30.134 | 6.6994 | 201.8812 | 30.134 | 6.6994 | 224.0311 | 33.4403 | 6.6994 | 0.9924%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 169 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 113.526 | 53.0485 | 2.14 | 113.526 | 53.0485 | 2.14 | 125.9818 | 58.8688 | 2.14 | 0.9821%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 153 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 175.5743 | 48.0261 | 3.6558 | 175.5743 | 48.0261 | 3.6558 | 194.8379 | 53.2954 | 3.6558 | 0.99%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 46 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.6078 | 14.4392 | 0.87316 | 12.6078 | 14.4392 | 0.87316 | 13.9911 | 16.0235 | 0.87316 | 0.9809%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 150 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 48.9203 | 47.0844 | 1.039 | 48.9203 | 47.0844 | 1.039 | 54.2878 | 52.2504 | 1.039 | 0.9892%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 111 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 126.7327 | 34.8425 | 3.6373 | 126.7327 | 34.8425 | 3.6373 | 140.6375 | 38.6653 | 3.6373 | 0.9919%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 6 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.648 | 1.8834 | 0.34407 | 0.648 | 1.8834 | 0.34407 | 0.7191 | 2.09 | 0.34407 | 0.999%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 502 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 16.3491 | 157.5759 | 0.10375 | 16.3491 | 157.5759 | 0.10375 | 18.1429 | 174.8648 | 0.10375 | 0.8922%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 383 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 21.8049 | 120.2223 | 0.18137 | 21.8049 | 120.2223 | 0.18137 | 24.1973 | 133.4128 | 0.18137 | 0.8785%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 367 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 95.9693 | 115.1999 | 0.83307 | 95.9693 | 115.1999 | 0.83307 | 106.4988 | 127.8394 | 0.83307 | 0.9868%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 406 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 31.5024 | 127.4419 | 0.24719 | 31.5024 | 127.4419 | 0.24719 | 34.9588 | 141.4245 | 0.24719 | 0.9466%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 493 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.8972 | 154.7509 | 0.076879 | 11.8972 | 154.7509 | 0.076879 | 13.2025 | 171.7298 | 0.076879 | 0.9088%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 69 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 91.1879 | 21.6588 | 4.2102 | 91.1879 | 21.6588 | 4.2102 | 101.1929 | 24.0352 | 4.2102 | 0.9905%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 57 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 19.2748 | 17.8921 | 1.0773 | 19.2748 | 17.8921 | 1.0773 | 21.3895 | 19.8552 | 1.0773 | 0.9634%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 218 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.7722 | 68.4294 | 0.21588 | 14.7722 | 68.4294 | 0.21588 | 16.393 | 75.9373 | 0.21588 | 0.8429%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 620 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 29.1603 | 194.6157 | 0.14984 | 29.1603 | 194.6157 | 0.14984 | 32.3597 | 215.9685 | 0.14984 | 0.8937%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 33.5564 | 5.3362 | 6.2884 | 33.5564 | 5.3362 | 6.2884 | 37.2381 | 5.9217 | 6.2884 | 0.9991%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 227 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 27.4264 | 71.2545 | 0.38491 | 27.4264 | 71.2545 | 0.38491 | 30.4355 | 79.0723 | 0.38491 | 0.9216%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 357 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 23.9276 | 112.061 | 0.21352 | 23.9276 | 112.061 | 0.21352 | 26.5529 | 124.356 | 0.21352 | 0.9611%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.4289 | 0.94169 | 6.827 | 6.4289 | 0.94169 | 6.827 | 7.1342 | 1.045 | 6.827 | 0.9946%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 384 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 34.741 | 120.5362 | 0.28822 | 34.741 | 120.5362 | 0.28822 | 38.5527 | 133.7611 | 0.28822 | 0.9703%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 29 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.96674 | 9.103 | 0.1062 | 0.96674 | 9.103 | 0.1062 | 1.0728 | 10.1018 | 0.1062 | 0.334%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 30 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 18.6124 | 9.4169 | 1.9765 | 18.6124 | 9.4169 | 1.9765 | 20.6545 | 10.4501 | 1.9765 | 0.9951%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 27 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.5498 | 8.4752 | 0.65483 | 5.5498 | 8.4752 | 0.65483 | 6.1587 | 9.4051 | 0.65483 | 0.9868%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 56 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 40.5593 | 17.5782 | 2.3074 | 40.5593 | 17.5782 | 2.3074 | 45.0094 | 19.5068 | 2.3074 | 0.9945%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 34 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 20.4866 | 10.6725 | 1.9196 | 20.4866 | 10.6725 | 1.9196 | 22.7343 | 11.8434 | 1.9196 | 0.9686%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 17 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 87.1653 | 5.3362 | 16.3346 | 87.1653 | 5.3362 | 16.3346 | 96.7288 | 5.9217 | 16.3346 | 0.9959%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 120 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.7708 | 37.6676 | 0.31249 | 11.7708 | 37.6676 | 0.31249 | 13.0623 | 41.8003 | 0.31249 | 0.9515%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 822 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 65.1242 | 258.0227 | 0.2524 | 65.1242 | 258.0227 | 0.2524 | 72.2695 | 286.3324 | 0.2524 | 0.9662%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 245 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 715.269 | 76.9046 | 9.3007 | 715.269 | 76.9046 | 9.3007 | 793.7467 | 85.3424 | 9.3007 | 0.9925%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 32.6952 | 2.8251 | 11.5733 | 32.6952 | 2.8251 | 11.5733 | 36.2824 | 3.135 | 11.5733 | 0.9927%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 107 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 408.9425 | 33.5869 | 12.1757 | 408.9425 | 33.5869 | 12.1757 | 453.8108 | 37.272 | 12.1757 | 0.9963%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.2745 | 0.62779 | 3.623 | 2.2745 | 0.62779 | 3.623 | 2.5241 | 0.69667 | 3.623 | 0.8656%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 511 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 64.9142 | 160.401 | 0.4047 | 64.9142 | 160.401 | 0.4047 | 72.0364 | 177.9998 | 0.4047 | 0.9605%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 14 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 44.1572 | 4.3945 | 10.0482 | 44.1572 | 4.3945 | 10.0482 | 49.0021 | 4.8767 | 10.0482 | 0.9985%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 600 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 147.5821 | 188.3378 | 0.7836 | 147.5821 | 188.3378 | 0.7836 | 163.7745 | 209.0017 | 0.7836 | 0.967%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 3 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.15542 | 0.94169 | 0.16504 | 0.15542 | 0.94169 | 0.16504 | 0.17247 | 1.045 | 0.16504 | 0.9833%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 349 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 17.2908 | 109.5498 | 0.15784 | 17.2908 | 109.5498 | 0.15784 | 19.188 | 121.5694 | 0.15784 | 0.9498%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 470 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 57.1262 | 147.5313 | 0.38721 | 57.1262 | 147.5313 | 0.38721 | 63.3939 | 163.718 | 0.38721 | 0.9826%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 585 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 17.1775 | 183.6293 | 0.093544 | 17.1775 | 183.6293 | 0.093544 | 19.0622 | 203.7767 | 0.093544 | 0.9106%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 226 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.8545 | 70.9406 | 0.054334 | 3.8545 | 70.9406 | 0.054334 | 4.2774 | 78.724 | 0.054334 | 0.7897%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.0473 | 21.9727 | 0.32073 | 7.0473 | 21.9727 | 0.32073 | 7.8205 | 24.3835 | 0.32073 | 0.9819%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 328 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 30.8736 | 102.958 | 0.29987 | 30.8736 | 102.958 | 0.29987 | 34.261 | 114.2543 | 0.29987 | 0.9768%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 3 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0289 | 0.94169 | 1.0926 | 1.0289 | 0.94169 | 1.0926 | 1.1418 | 1.045 | 1.0926 | 0.9298%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 32 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.4554 | 10.0447 | 0.14489 | 1.4554 | 10.0447 | 0.14489 | 1.6151 | 11.1468 | 0.14489 | 0.8171%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 364 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 24.429 | 114.2582 | 0.2138 | 24.429 | 114.2582 | 0.2138 | 27.1093 | 126.7944 | 0.2138 | 0.983%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 1452 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 46.1751 | 455.7774 | 0.10131 | 46.1751 | 455.7774 | 0.10131 | 51.2413 | 505.7842 | 0.10131 | 0.9868%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 4 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.00047048 | 1.2556 | 0.00037471 | 0.00047048 | 1.2556 | 0.00037471 | 0.0005221 | 1.3933 | 0.00037471 | 0.004523%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 743 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 27.3047 | 233.2249 | 0.11707 | 27.3047 | 233.2249 | 0.11707 | 30.3005 | 258.8138 | 0.11707 | 0.9884%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 182 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.3838 | 57.1291 | 0.11174 | 6.3838 | 57.1291 | 0.11174 | 7.0842 | 63.3972 | 0.11174 | 0.9757%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 279 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.8693 | 87.5771 | 0.044181 | 3.8693 | 87.5771 | 0.044181 | 4.2938 | 97.1858 | 0.044181 | 0.9496%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 309 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 18.3049 | 96.994 | 0.18872 | 18.3049 | 96.994 | 0.18872 | 20.3133 | 107.6359 | 0.18872 | 0.859%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 875 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 44.7034 | 274.6592 | 0.16276 | 44.7034 | 274.6592 | 0.16276 | 49.6082 | 304.7942 | 0.16276 | 0.9946%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 106 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 35.2843 | 33.273 | 1.0604 | 35.2843 | 33.273 | 1.0604 | 39.1556 | 36.9236 | 1.0604 | 0.8863%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 399 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 211.9523 | 125.2446 | 1.6923 | 211.9523 | 125.2446 | 1.6923 | 235.2072 | 138.9862 | 1.6923 | 0.9837%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 390 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 87.3211 | 122.4196 | 0.71329 | 87.3211 | 122.4196 | 0.71329 | 96.9018 | 135.8511 | 0.71329 | 0.9873%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 104 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 24.9907 | 32.6452 | 0.76552 | 24.9907 | 32.6452 | 0.76552 | 27.7326 | 36.227 | 0.76552 | 0.9726%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 19 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 20.2852 | 5.964 | 3.4013 | 20.2852 | 5.964 | 3.4013 | 22.5108 | 6.6184 | 3.4013 | 0.9861%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 249 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 47.5862 | 78.1602 | 0.60883 | 47.5862 | 78.1602 | 0.60883 | 52.8073 | 86.7357 | 0.60883 | 0.9807%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 365 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 189.9659 | 114.5721 | 1.658 | 189.9659 | 114.5721 | 1.658 | 210.8085 | 127.1427 | 1.658 | 0.9836%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 129 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 61.6836 | 40.4926 | 1.5233 | 61.6836 | 40.4926 | 1.5233 | 68.4514 | 44.9354 | 1.5233 | 0.9784%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 48 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 32.8705 | 15.067 | 2.1816 | 32.8705 | 15.067 | 2.1816 | 36.477 | 16.7201 | 2.1816 | 0.994%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 135 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 255.3789 | 42.376 | 6.0265 | 255.3789 | 42.376 | 6.0265 | 283.3985 | 47.0254 | 6.0265 | 0.9934%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 345 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 243.7006 | 108.2942 | 2.2504 | 243.7006 | 108.2942 | 2.2504 | 270.4388 | 120.176 | 2.2504 | 0.9889%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 37 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.278 | 11.6142 | 0.36835 | 4.278 | 11.6142 | 0.36835 | 4.7474 | 12.8884 | 0.36835 | 0.7089%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 23 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 22.7545 | 7.2196 | 3.1518 | 22.7545 | 7.2196 | 3.1518 | 25.251 | 8.0117 | 3.1518 | 0.9883%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 479 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 278.6354 | 150.3563 | 1.8532 | 278.6354 | 150.3563 | 1.8532 | 309.2066 | 166.8531 | 1.8532 | 0.9911%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 422 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 589.8137 | 132.4642 | 4.4526 | 589.8137 | 132.4642 | 4.4526 | 654.5266 | 146.9979 | 4.4526 | 0.9893%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 399 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.6786 | 125.2446 | 0.061309 | 7.6786 | 125.2446 | 0.061309 | 8.5211 | 138.9862 | 0.061309 | 0.9808%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.233 | 17.2643 | 0.82442 | 14.233 | 17.2643 | 0.82442 | 15.7947 | 19.1585 | 0.82442 | 0.9867%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.7998 | 73.1378 | 0.13399 | 9.7998 | 73.1378 | 0.13399 | 10.875 | 81.1623 | 0.13399 | 0.9646%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 327 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 56.0399 | 102.6441 | 0.54596 | 56.0399 | 102.6441 | 0.54596 | 62.1884 | 113.906 | 0.54596 | 0.9824%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 303 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.49 | 95.1106 | 0.068237 | 6.49 | 95.1106 | 0.068237 | 7.2021 | 105.5459 | 0.068237 | 0.6927%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 31 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.3828 | 9.7308 | 0.34764 | 3.3828 | 9.7308 | 0.34764 | 3.754 | 10.7984 | 0.34764 | 0.9876%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 123 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.5781 | 38.6092 | 0.27398 | 10.5781 | 38.6092 | 0.27398 | 11.7387 | 42.8454 | 0.27398 | 0.9838%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 24 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.1078 | 7.5335 | 0.94349 | 7.1078 | 7.5335 | 0.94349 | 7.8876 | 8.3601 | 0.94349 | 0.987%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 21 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.3211 | 6.5918 | 0.50381 | 3.3211 | 6.5918 | 0.50381 | 3.6854 | 7.3151 | 0.50381 | 0.9688%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 485 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 39.5381 | 152.2397 | 0.25971 | 39.5381 | 152.2397 | 0.25971 | 43.8761 | 168.9431 | 0.25971 | 0.9791%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 263 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 33.7387 | 82.5547 | 0.40868 | 33.7387 | 82.5547 | 0.40868 | 37.4405 | 91.6124 | 0.40868 | 0.9907%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 164 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 32.2959 | 51.479 | 0.62736 | 32.2959 | 51.479 | 0.62736 | 35.8393 | 57.1271 | 0.62736 | 0.9682%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 101 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.7642 | 31.7035 | 0.18182 | 5.7642 | 31.7035 | 0.18182 | 6.3966 | 35.182 | 0.18182 | 0.6596%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 389 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 29.1399 | 122.1057 | 0.23865 | 29.1399 | 122.1057 | 0.23865 | 32.3371 | 135.5028 | 0.23865 | 0.9454%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 74 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 11.4521 | 23.2283 | 0.49302 | 11.4521 | 23.2283 | 0.49302 | 12.7086 | 25.7769 | 0.49302 | 0.9251%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 6 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.93993 | 1.8834 | 0.49907 | 0.93993 | 1.8834 | 0.49907 | 1.0431 | 2.09 | 0.49907 | 0.9818%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 299 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 32.7369 | 93.855 | 0.3488 | 32.7369 | 93.855 | 0.3488 | 36.3287 | 104.1525 | 0.3488 | 0.9585%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 47 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 47.5288 | 14.7531 | 3.2216 | 47.5288 | 14.7531 | 3.2216 | 52.7435 | 16.3718 | 3.2216 | 0.9855%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 101 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.0881 | 31.7035 | 0.50745 | 16.0881 | 31.7035 | 0.50745 | 17.8533 | 35.182 | 0.50745 | 0.878%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 4.1304 | 0.3139 | 13.1583 | 4.1304 | 0.3139 | 13.1583 | 4.5835 | 0.34834 | 13.1583 | 0.9431%
2027 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 2 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.37366 | 0.62779 | 0.5952 | 0.37366 | 0.62779 | 0.5952 | 0.41466 | 0.69667 | 0.5952 | 0.9823%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 215 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.6538 | 67.4877 | 0.068958 | 4.6538 | 67.4877 | 0.068958 | 5.1645 | 74.8923 | 0.068958 | 0.9288%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 22 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.023211 | 6.9057 | 0.0033611 | 0.023211 | 6.9057 | 0.0033611 | 0.025758 | 7.6634 | 0.0033611 | 0.7897%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 2 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 4.1532 | 0.62779 | 6.6155 | 4.1532 | 0.62779 | 6.6155 | 4.6088 | 0.69667 | 6.6155 | 0.9948%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 169 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.3417 | 53.0485 | 0.11955 | 6.3417 | 53.0485 | 0.11955 | 7.0375 | 58.8688 | 0.11955 | 0.9241%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 110 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.9495 | 34.5286 | 0.57777 | 19.9495 | 34.5286 | 0.57777 | 22.1383 | 38.317 | 0.57777 | 0.9107%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 294 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 41.4107 | 92.2855 | 0.44872 | 41.4107 | 92.2855 | 0.44872 | 45.9542 | 102.4109 | 0.44872 | 0.9555%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 5 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16842 | 1.5695 | 0.10731 | 0.16842 | 1.5695 | 0.10731 | 0.1869 | 1.7417 | 0.10731 | 0.1937%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 13 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.070129 | 4.0807 | 0.017186 | 0.070129 | 4.0807 | 0.017186 | 0.077823 | 4.5284 | 0.017186 | 0.4938%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 201 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.034025 | 63.0932 | 0.00053928 | 0.034025 | 63.0932 | 0.00053928 | 0.037758 | 70.0156 | 0.00053928 | 0.02339%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 10 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0027839 | 3.139 | 0.00088687 | 0.0027839 | 3.139 | 0.00088687 | 0.0030893 | 3.4834 | 0.00088687 | 0.001514%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 149 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.9002 | 46.7705 | 0.040627 | 1.9002 | 46.7705 | 0.040627 | 2.1086 | 51.9021 | 0.040627 | 0.995%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 2 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.732 | 0.62779 | 4.3517 | 2.732 | 0.62779 | 4.3517 | 3.0317 | 0.69667 | 4.3517 | 0.9927%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 975 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 31.2978 | 306.0489 | 0.10226 | 31.2978 | 306.0489 | 0.10226 | 34.7317 | 339.6278 | 0.10226 | 0.9548%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 827 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 123.8786 | 259.5922 | 0.4772 | 123.8786 | 259.5922 | 0.4772 | 137.4703 | 288.0741 | 0.4772 | 0.9814%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 961 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 49.1654 | 301.6543 | 0.16299 | 49.1654 | 301.6543 | 0.16299 | 54.5597 | 334.7511 | 0.16299 | 0.9699%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 397 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 122.1654 | 124.6168 | 0.98033 | 122.1654 | 124.6168 | 0.98033 | 135.5691 | 138.2895 | 0.98033 | 0.9928%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 538 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 100.7847 | 168.8762 | 0.5968 | 100.7847 | 168.8762 | 0.5968 | 111.8425 | 187.4049 | 0.5968 | 0.9888%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 546 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 212.4003 | 171.3874 | 1.2393 | 212.4003 | 171.3874 | 1.2393 | 235.7044 | 190.1916 | 1.2393 | 0.9925%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 82.9876 | 28.8785 | 2.8737 | 82.9876 | 28.8785 | 2.8737 | 92.0928 | 32.0469 | 2.8737 | 0.9973%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 488 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 168.3033 | 153.1814 | 1.0987 | 168.3033 | 153.1814 | 1.0987 | 186.7692 | 169.9881 | 1.0987 | 0.9936%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 319 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 81.809 | 100.1329 | 0.817 | 81.809 | 100.1329 | 0.817 | 90.7849 | 111.1193 | 0.817 | 0.9749%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 106 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 22.7355 | 33.273 | 0.6833 | 22.7355 | 33.273 | 0.6833 | 25.2299 | 36.9236 | 0.6833 | 0.9918%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 24 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 20.1485 | 7.5335 | 2.6745 | 20.1485 | 7.5335 | 2.6745 | 22.3591 | 8.3601 | 2.6745 | 0.9993%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 55 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.0724 | 17.2643 | 0.93096 | 16.0724 | 17.2643 | 0.93096 | 17.8358 | 19.1585 | 0.93096 | 0.8869%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 46 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 39.0935 | 14.4392 | 2.7074 | 39.0935 | 14.4392 | 2.7074 | 43.3827 | 16.0235 | 2.7074 | 0.943%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 13 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.6596 | 4.0807 | 0.65176 | 2.6596 | 4.0807 | 0.65176 | 2.9514 | 4.5284 | 0.65176 | 0.6284%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 139 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 122.4623 | 43.6316 | 2.8067 | 122.4623 | 43.6316 | 2.8067 | 135.8986 | 48.4187 | 2.8067 | 0.9943%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 465 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 185.0853 | 145.9618 | 1.268 | 185.0853 | 145.9618 | 1.268 | 205.3924 | 161.9764 | 1.268 | 0.9917%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 29.4362 | 32.0174 | 0.91938 | 29.4362 | 32.0174 | 0.91938 | 32.6658 | 35.5303 | 0.91938 | 0.8854%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 276 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 67.231 | 86.6354 | 0.77602 | 67.231 | 86.6354 | 0.77602 | 74.6075 | 96.1408 | 0.77602 | 0.985%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 139 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.357 | 43.6316 | 0.28321 | 12.357 | 43.6316 | 0.28321 | 13.7128 | 48.4187 | 0.28321 | 0.7994%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 131 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 48.5603 | 41.1204 | 1.1809 | 48.5603 | 41.1204 | 1.1809 | 53.8882 | 45.632 | 1.1809 | 0.9814%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 704 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 142.4543 | 220.983 | 0.64464 | 142.4543 | 220.983 | 0.64464 | 158.0841 | 245.2287 | 0.64464 | 0.9776%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 561 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 80.6995 | 176.0958 | 0.45827 | 80.6995 | 176.0958 | 0.45827 | 89.5536 | 195.4166 | 0.45827 | 0.9541%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 14 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.2788 | 4.3945 | 2.5665 | 11.2788 | 4.3945 | 2.5665 | 12.5163 | 4.8767 | 2.5665 | 0.9906%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 7 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 46.2497 | 2.1973 | 21.0487 | 46.2497 | 2.1973 | 21.0487 | 51.3241 | 2.4384 | 21.0487 | 0.9968%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 1 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.6371 | 0.3139 | 24.3299 | 7.6371 | 0.3139 | 24.3299 | 8.475 | 0.34834 | 24.3299 | 0.9549%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 194 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 151.6491 | 60.8959 | 2.4903 | 151.6491 | 60.8959 | 2.4903 | 168.2877 | 67.5772 | 2.4903 | 0.9879%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 329 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 156.9706 | 103.2719 | 1.52 | 156.9706 | 103.2719 | 1.52 | 174.193 | 114.6026 | 1.52 | 0.9747%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 435 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 92.1224 | 136.5449 | 0.67467 | 92.1224 | 136.5449 | 0.67467 | 102.2299 | 151.5263 | 0.67467 | 0.9704%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 248 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 104.6452 | 77.8463 | 1.3443 | 104.6452 | 77.8463 | 1.3443 | 116.1267 | 86.3874 | 1.3443 | 0.9781%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.3037 | 3.4529 | 1.536 | 5.3037 | 3.4529 | 1.536 | 5.8856 | 3.8317 | 1.536 | 0.9721%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 36 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.1945 | 11.3003 | 1.0791 | 12.1945 | 11.3003 | 1.0791 | 13.5325 | 12.5401 | 1.0791 | 0.9966%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 252 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 337.3598 | 79.1019 | 4.2649 | 337.3598 | 79.1019 | 4.2649 | 374.3741 | 87.7807 | 4.2649 | 0.9859%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 14 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.7862 | 4.3945 | 2.682 | 11.7862 | 4.3945 | 2.682 | 13.0794 | 4.8767 | 2.682 | 0.8901%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 22 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5811 | 6.9057 | 0.22895 | 1.5811 | 6.9057 | 0.22895 | 1.7545 | 7.6634 | 0.22895 | 0.1879%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 590 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 25.1718 | 185.1988 | 0.13592 | 25.1718 | 185.1988 | 0.13592 | 27.9336 | 205.5184 | 0.13592 | 0.8818%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 455 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 16.5372 | 142.8228 | 0.11579 | 16.5372 | 142.8228 | 0.11579 | 18.3516 | 158.493 | 0.11579 | 0.9783%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 839 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 57.0772 | 263.359 | 0.21673 | 57.0772 | 263.359 | 0.21673 | 63.3396 | 292.2541 | 0.21673 | 0.9847%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 3 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.7938 | 0.94169 | 12.5241 | 11.7938 | 0.94169 | 12.5241 | 13.0878 | 1.045 | 12.5241 | 0.9597%
2027 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.63991 | 0.3139 | 2.0386 | 0.63991 | 0.3139 | 2.0386 | 0.71012 | 0.34834 | 2.0386 | 0.9953%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 91 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 31.198 | 28.5646 | 1.0922 | 31.198 | 28.5646 | 1.0922 | 34.621 | 31.6986 | 1.0922 | 0.9745%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.8386 | 0.94169 | 5.1382 | 4.8386 | 0.94169 | 5.1382 | 5.3695 | 1.045 | 5.1382 | 0.9134%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 68 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 42.3621 | 21.3449 | 1.9846 | 42.3621 | 21.3449 | 1.9846 | 47.01 | 23.6869 | 1.9846 | 0.98%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 20 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 47.9792 | 6.2779 | 7.6425 | 47.9792 | 6.2779 | 7.6425 | 53.2434 | 6.9667 | 7.6425 | 0.9857%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 358 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.0443 | 112.3749 | 0.14277 | 16.0443 | 112.3749 | 0.14277 | 17.8046 | 124.7044 | 0.14277 | 0.9609%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 28 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.013995 | 8.7891 | 0.0015923 | 0.013995 | 8.7891 | 0.0015923 | 0.015531 | 9.7534 | 0.0015923 | 0.01745%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 37 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.5914 | 11.6142 | 0.56753 | 6.5914 | 11.6142 | 0.56753 | 7.3146 | 12.8884 | 0.56753 | 0.8492%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 17 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.7746 | 5.3362 | 0.51995 | 2.7746 | 5.3362 | 0.51995 | 3.079 | 5.9217 | 0.51995 | 0.5795%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 558 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 93.1705 | 175.1541 | 0.53193 | 93.1705 | 175.1541 | 0.53193 | 103.393 | 194.3716 | 0.53193 | 0.8848%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 9 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.951 | 2.8251 | 1.7525 | 4.951 | 2.8251 | 1.7525 | 5.4942 | 3.135 | 1.7525 | 0.9893%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 29 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.9446 | 9.103 | 0.43333 | 3.9446 | 9.103 | 0.43333 | 4.3774 | 10.1018 | 0.43333 | 0.9131%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 7 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.65617 | 2.1973 | 0.29863 | 0.65617 | 2.1973 | 0.29863 | 0.72816 | 2.4384 | 0.29863 | 0.51%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 16 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 30.3414 | 5.0223 | 6.0413 | 30.3414 | 5.0223 | 6.0413 | 33.6704 | 5.5734 | 6.0413 | 0.9767%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 219 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.6755 | 68.7433 | 0.053468 | 3.6755 | 68.7433 | 0.053468 | 4.0788 | 76.2856 | 0.053468 | 0.7071%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 202 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 83.235 | 63.407 | 1.3127 | 83.235 | 63.407 | 1.3127 | 92.3673 | 70.3639 | 1.3127 | 0.9496%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 55 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 63.4108 | 17.2643 | 3.6729 | 63.4108 | 17.2643 | 3.6729 | 70.3681 | 19.1585 | 3.6729 | 0.9611%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 33 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.9463 | 10.3586 | 1.2498 | 12.9463 | 10.3586 | 1.2498 | 14.3667 | 11.4951 | 1.2498 | 0.8872%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 211 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 92.4716 | 66.2321 | 1.3962 | 92.4716 | 66.2321 | 1.3962 | 102.6173 | 73.4989 | 1.3962 | 0.9569%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 16 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 13.6213 | 5.0223 | 2.7121 | 13.6213 | 5.0223 | 2.7121 | 15.1158 | 5.5734 | 2.7121 | 0.8473%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 52 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 29.3039 | 16.3226 | 1.7953 | 29.3039 | 16.3226 | 1.7953 | 32.5191 | 18.1135 | 1.7953 | 0.8754%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 29 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 35.4517 | 9.103 | 3.8945 | 35.4517 | 9.103 | 3.8945 | 39.3413 | 10.1018 | 3.8945 | 0.8812%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 2 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.9618 | 0.62779 | 19.0537 | 11.9618 | 0.62779 | 19.0537 | 13.2742 | 0.69667 | 19.0537 | 0.9724%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 1 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.7378 | 0.3139 | 34.2081 | 10.7378 | 0.3139 | 34.2081 | 11.9159 | 0.34834 | 34.2081 | 0.9739%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 56 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 21.8479 | 17.5782 | 1.2429 | 21.8479 | 17.5782 | 1.2429 | 24.245 | 19.5068 | 1.2429 | 0.9191%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 60 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.7439 | 18.8338 | 0.57046 | 10.7439 | 18.8338 | 0.57046 | 11.9227 | 20.9002 | 0.57046 | 0.557%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 73 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.6094 | 22.9144 | 0.15752 | 3.6094 | 22.9144 | 0.15752 | 4.0054 | 25.4285 | 0.15752 | 0.7618%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 79 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.5415 | 24.7978 | 0.18314 | 4.5415 | 24.7978 | 0.18314 | 5.0398 | 27.5186 | 0.18314 | 0.7912%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 243 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 75.9584 | 76.2768 | 0.99583 | 75.9584 | 76.2768 | 0.99583 | 84.2924 | 84.6457 | 0.99583 | 0.9168%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 119 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 47.9898 | 37.3537 | 1.2847 | 47.9898 | 37.3537 | 1.2847 | 53.2551 | 41.452 | 1.2847 | 0.9343%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 495 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 55.4184 | 155.3787 | 0.35667 | 55.4184 | 155.3787 | 0.35667 | 61.4988 | 172.4264 | 0.35667 | 0.9049%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.1969 | 4.3945 | 3.003 | 13.1969 | 4.3945 | 3.003 | 14.6448 | 4.8767 | 3.003 | 0.9697%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 10 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.5023 | 3.139 | 1.7529 | 5.5023 | 3.139 | 1.7529 | 6.106 | 3.4834 | 1.7529 | 0.967%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 61 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 47.2842 | 19.1477 | 2.4694 | 47.2842 | 19.1477 | 2.4694 | 52.4721 | 21.2485 | 2.4694 | 0.9877%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 125 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 20.1718 | 39.237 | 0.5141 | 20.1718 | 39.237 | 0.5141 | 22.385 | 43.542 | 0.5141 | 0.9555%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.6222 | 15.3809 | 0.17048 | 2.6222 | 15.3809 | 0.17048 | 2.9098 | 17.0685 | 0.17048 | 0.9711%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 257 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 74.7143 | 80.6713 | 0.92616 | 74.7143 | 80.6713 | 0.92616 | 82.9117 | 89.5224 | 0.92616 | 0.9923%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 62 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.6876 | 19.4616 | 0.34363 | 6.6876 | 19.4616 | 0.34363 | 7.4213 | 21.5968 | 0.34363 | 0.9277%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 61 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.8144 | 19.1477 | 0.51256 | 9.8144 | 19.1477 | 0.51256 | 10.8912 | 21.2485 | 0.51256 | 0.9525%
2027 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 27 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.2474 | 8.4752 | 0.14719 | 1.2474 | 8.4752 | 0.14719 | 1.3843 | 9.4051 | 0.14719 | 0.999%
2027 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.6464 | 1.2556 | 1.3113 | 1.6464 | 1.2556 | 1.3113 | 1.827 | 1.3933 | 1.3113 | 0.9984%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 175 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 25.6788 | 54.9318 | 0.46747 | 25.6788 | 54.9318 | 0.46747 | 28.4962 | 60.9588 | 0.46747 | 0.9993%
2027 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 14 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.3453 | 4.3945 | 0.078574 | 0.3453 | 4.3945 | 0.078574 | 0.38318 | 4.8767 | 0.078574 | 0.9723%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 287 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 31.2198 | 90.0882 | 0.34655 | 31.2198 | 90.0882 | 0.34655 | 34.6452 | 99.9725 | 0.34655 | 0.997%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 15 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 12.4192 | 4.7084 | 2.6377 | 12.4192 | 4.7084 | 2.6377 | 13.7819 | 5.225 | 2.6377 | 0.9902%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 213 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 47.1097 | 66.8599 | 0.7046 | 47.1097 | 66.8599 | 0.7046 | 52.2785 | 74.1956 | 0.7046 | 0.9833%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 471 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 151.376 | 147.8451 | 1.0239 | 151.376 | 147.8451 | 1.0239 | 167.9846 | 164.0664 | 1.0239 | 0.9937%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 15 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 36.7559 | 4.7084 | 7.8064 | 36.7559 | 4.7084 | 7.8064 | 40.7887 | 5.225 | 7.8064 | 0.9496%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 90 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.8503 | 28.2507 | 0.065496 | 1.8503 | 28.2507 | 0.065496 | 2.0533 | 31.3503 | 0.065496 | 0.9963%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 31 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.6436 | 9.7308 | 0.68274 | 6.6436 | 9.7308 | 0.68274 | 7.3725 | 10.7984 | 0.68274 | 0.9951%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 779 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 26.387 | 244.5252 | 0.10791 | 26.387 | 244.5252 | 0.10791 | 29.2822 | 271.3539 | 0.10791 | 0.9734%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 148 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.1838 | 46.4566 | 0.28379 | 13.1838 | 46.4566 | 0.28379 | 14.6303 | 51.5538 | 0.28379 | 0.9797%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 400 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 23.2262 | 125.5585 | 0.18498 | 23.2262 | 125.5585 | 0.18498 | 25.7745 | 139.3345 | 0.18498 | 0.9676%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 745 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 28.8046 | 233.8527 | 0.12317 | 28.8046 | 233.8527 | 0.12317 | 31.965 | 259.5105 | 0.12317 | 0.9272%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 290 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 14.6037 | 91.0299 | 0.16043 | 14.6037 | 91.0299 | 0.16043 | 16.206 | 101.0175 | 0.16043 | 0.9829%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 504 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 59.5224 | 158.2037 | 0.37624 | 59.5224 | 158.2037 | 0.37624 | 66.053 | 175.5615 | 0.37624 | 0.9672%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 258 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.2665 | 80.9852 | 0.06503 | 5.2665 | 80.9852 | 0.06503 | 5.8443 | 89.8708 | 0.06503 | 0.7734%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 221 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 18.3018 | 69.3711 | 0.26382 | 18.3018 | 69.3711 | 0.26382 | 20.3098 | 76.9823 | 0.26382 | 0.9648%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 63 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.7563 | 19.7755 | 0.088814 | 1.7563 | 19.7755 | 0.088814 | 1.949 | 21.9452 | 0.088814 | 0.7472%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 657 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 43.8849 | 206.2299 | 0.2128 | 43.8849 | 206.2299 | 0.2128 | 48.6999 | 228.8569 | 0.2128 | 0.9649%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 231 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 18.1542 | 72.51 | 0.25037 | 18.1542 | 72.51 | 0.25037 | 20.1461 | 80.4657 | 0.25037 | 0.9757%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 427 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 99.8685 | 134.0337 | 0.7451 | 99.8685 | 134.0337 | 0.7451 | 110.8258 | 148.7396 | 0.7451 | 0.9669%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 152 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.5913 | 47.7122 | 0.13815 | 6.5913 | 47.7122 | 0.13815 | 7.3145 | 52.9471 | 0.13815 | 0.8931%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 356 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 75.4437 | 111.7471 | 0.67513 | 75.4437 | 111.7471 | 0.67513 | 83.7212 | 124.0077 | 0.67513 | 0.9779%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 268 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 78.7812 | 84.1242 | 0.93649 | 78.7812 | 84.1242 | 0.93649 | 87.4249 | 93.3541 | 0.93649 | 0.9936%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 378 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 50.5044 | 118.6528 | 0.42565 | 50.5044 | 118.6528 | 0.42565 | 56.0457 | 131.6711 | 0.42565 | 0.9878%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 262 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 110.706 | 82.2408 | 1.3461 | 110.706 | 82.2408 | 1.3461 | 122.8524 | 91.2641 | 1.3461 | 0.9938%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 549 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 81.2357 | 172.3291 | 0.4714 | 81.2357 | 172.3291 | 0.4714 | 90.1487 | 191.2366 | 0.4714 | 0.9905%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 29 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.44129 | 9.103 | 0.048477 | 0.44129 | 9.103 | 0.048477 | 0.4897 | 10.1018 | 0.048477 | 0.4302%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 39 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.23982 | 12.242 | 0.01959 | 0.23982 | 12.242 | 0.01959 | 0.26614 | 13.5851 | 0.01959 | 0.2253%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 897 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 49.4954 | 281.565 | 0.17579 | 49.4954 | 281.565 | 0.17579 | 54.926 | 312.4576 | 0.17579 | 0.9644%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 111 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.32484 | 34.8425 | 0.0093232 | 0.32484 | 34.8425 | 0.0093232 | 0.36048 | 38.6653 | 0.0093232 | 0.117%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 119 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 49.6477 | 37.3537 | 1.3291 | 49.6477 | 37.3537 | 1.3291 | 55.0949 | 41.452 | 1.3291 | 0.9978%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 253 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 102.7516 | 79.4158 | 1.2938 | 102.7516 | 79.4158 | 1.2938 | 114.0253 | 88.1291 | 1.2938 | 0.9977%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 241 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 123.504 | 75.649 | 1.6326 | 123.504 | 75.649 | 1.6326 | 137.0546 | 83.949 | 1.6326 | 0.9899%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 136 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 78.6546 | 42.6899 | 1.8425 | 78.6546 | 42.6899 | 1.8425 | 87.2844 | 47.3737 | 1.8425 | 0.982%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 592 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 363.8583 | 185.8266 | 1.9581 | 363.8583 | 185.8266 | 1.9581 | 403.78 | 206.2151 | 1.9581 | 0.9903%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 30 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 5.1395 | 9.4169 | 0.54578 | 5.1395 | 9.4169 | 0.54578 | 5.7034 | 10.4501 | 0.54578 | 0.6775%
2027 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 1 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.3895 | 0.3139 | 4.4266 | 1.3895 | 0.3139 | 4.4266 | 1.5419 | 0.34834 | 4.4266 | 0.9944%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 4 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.5576 | 1.2556 | 3.6299 | 4.5576 | 1.2556 | 3.6299 | 5.0577 | 1.3933 | 3.6299 | 0.9632%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.44715 | 5.0223 | 0.089032 | 0.44715 | 5.0223 | 0.089032 | 0.49621 | 5.5734 | 0.089032 | 0.9941%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 685 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 163.2404 | 215.019 | 0.75919 | 163.2404 | 215.019 | 0.75919 | 181.1508 | 238.6103 | 0.75919 | 0.9555%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 899 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 232.8474 | 282.1928 | 0.82514 | 232.8474 | 282.1928 | 0.82514 | 258.3948 | 313.1543 | 0.82514 | 0.994%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 188 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 22.2363 | 59.0125 | 0.37681 | 22.2363 | 59.0125 | 0.37681 | 24.676 | 65.4872 | 0.37681 | 0.936%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 406 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 35.6813 | 127.4419 | 0.27998 | 35.6813 | 127.4419 | 0.27998 | 39.5962 | 141.4245 | 0.27998 | 0.938%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 88 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.9369 | 27.6229 | 0.17872 | 4.9369 | 27.6229 | 0.17872 | 5.4786 | 30.6536 | 0.17872 | 0.8718%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 132 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.7454 | 41.4343 | 0.33174 | 13.7454 | 41.4343 | 0.33174 | 15.2535 | 45.9804 | 0.33174 | 0.9279%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 54 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 54.9037 | 16.9504 | 3.2391 | 54.9037 | 16.9504 | 3.2391 | 60.9276 | 18.8102 | 3.2391 | 0.9729%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 293 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 137.5579 | 91.9716 | 1.4957 | 137.5579 | 91.9716 | 1.4957 | 152.6504 | 102.0625 | 1.4957 | 0.9856%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 134 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 21.9808 | 42.0621 | 0.52258 | 21.9808 | 42.0621 | 0.52258 | 24.3925 | 46.6771 | 0.52258 | 0.9864%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 32 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 51.3459 | 10.0447 | 5.1118 | 51.3459 | 10.0447 | 5.1118 | 56.9795 | 11.1468 | 5.1118 | 0.9841%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 150 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 94.7516 | 47.0844 | 2.0124 | 94.7516 | 47.0844 | 2.0124 | 105.1476 | 52.2504 | 2.0124 | 0.9831%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 119 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 83.1913 | 37.3537 | 2.2271 | 83.1913 | 37.3537 | 2.2271 | 92.3189 | 41.452 | 2.2271 | 0.9843%
2027 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.16088 | 0.62779 | 0.25626 | 0.16088 | 0.62779 | 0.25626 | 0.17853 | 0.69667 | 0.25626 | 0.9934%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 157 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 28.4668 | 49.2817 | 0.57763 | 28.4668 | 49.2817 | 0.57763 | 31.5901 | 54.6888 | 0.57763 | 0.9977%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 53 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 15.48 | 16.6365 | 0.93048 | 15.48 | 16.6365 | 0.93048 | 17.1784 | 18.4618 | 0.93048 | 0.9957%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 25 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 17.6067 | 7.8474 | 2.2436 | 17.6067 | 7.8474 | 2.2436 | 19.5385 | 8.7084 | 2.2436 | 0.9986%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 300 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.9656 | 94.1689 | 0.21202 | 19.9656 | 94.1689 | 0.21202 | 22.1561 | 104.5009 | 0.21202 | 0.9923%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 133 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 130.2838 | 41.7482 | 3.1207 | 130.2838 | 41.7482 | 3.1207 | 144.5782 | 46.3287 | 3.1207 | 0.9856%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 9 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 65.2205 | 2.8251 | 23.0864 | 65.2205 | 2.8251 | 23.0864 | 72.3764 | 3.135 | 23.0864 | 0.9951%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 236 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 78.3924 | 74.0795 | 1.0582 | 78.3924 | 74.0795 | 1.0582 | 86.9934 | 82.2074 | 1.0582 | 0.9433%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 3 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 2.9372 | 0.94169 | 3.1191 | 2.9372 | 0.94169 | 3.1191 | 3.2595 | 1.045 | 3.1191 | 0.9958%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 43 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 28.2206 | 13.4975 | 2.0908 | 28.2206 | 13.4975 | 2.0908 | 31.317 | 14.9785 | 2.0908 | 0.9258%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 109 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 111.2949 | 34.2147 | 3.2528 | 111.2949 | 34.2147 | 3.2528 | 123.5059 | 37.9687 | 3.2528 | 0.9926%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 129 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 18.5106 | 40.4926 | 0.45714 | 18.5106 | 40.4926 | 0.45714 | 20.5416 | 44.9354 | 0.45714 | 0.9747%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 99 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.3713 | 31.0757 | 0.33374 | 10.3713 | 31.0757 | 0.33374 | 11.5092 | 34.4853 | 0.33374 | 0.7093%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 86.8821 | 19.4616 | 4.4643 | 86.8821 | 19.4616 | 4.4643 | 96.4146 | 21.5968 | 4.4643 | 0.9829%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 47 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 166.0282 | 14.7531 | 11.2538 | 166.0282 | 14.7531 | 11.2538 | 184.2444 | 16.3718 | 11.2538 | 0.989%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 9 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 23.1929 | 2.8251 | 8.2097 | 23.1929 | 2.8251 | 8.2097 | 25.7375 | 3.135 | 8.2097 | 0.9937%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 103 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 48.5255 | 32.3313 | 1.5009 | 48.5255 | 32.3313 | 1.5009 | 53.8496 | 35.8786 | 1.5009 | 0.9631%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 226 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 166.0224 | 70.9406 | 2.3403 | 166.0224 | 70.9406 | 2.3403 | 184.2379 | 78.724 | 2.3403 | 0.9714%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 5 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 26.8212 | 1.5695 | 17.0892 | 26.8212 | 1.5695 | 17.0892 | 29.764 | 1.7417 | 17.0892 | 0.9712%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 210 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 180.4018 | 65.9182 | 2.7368 | 180.4018 | 65.9182 | 2.7368 | 200.1951 | 73.1506 | 2.7368 | 0.9923%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 6 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.1511 | 1.8834 | 0.61118 | 1.1511 | 1.8834 | 0.61118 | 1.2774 | 2.09 | 0.61118 | 0.9928%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 27 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.11165 | 8.4752 | 0.013173 | 0.11165 | 8.4752 | 0.013173 | 0.1239 | 9.4051 | 0.013173 | 0.9883%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 20 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.2688 | 6.2779 | 0.20211 | 1.2688 | 6.2779 | 0.20211 | 1.4081 | 6.9667 | 0.20211 | 0.9963%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 7 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.060511 | 2.1973 | 0.027539 | 0.060511 | 2.1973 | 0.027539 | 0.06715 | 2.4384 | 0.027539 | 0.9902%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 4 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.9878 | 1.2556 | 2.3796 | 2.9878 | 1.2556 | 2.3796 | 3.3156 | 1.3933 | 2.3796 | 0.9939%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 95 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.0456 | 29.8201 | 0.068598 | 2.0456 | 29.8201 | 0.068598 | 2.27 | 33.0919 | 0.068598 | 0.9666%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 381 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 78.2117 | 119.5945 | 0.65397 | 78.2117 | 119.5945 | 0.65397 | 86.793 | 132.7161 | 0.65397 | 0.9986%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 124 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 74.9698 | 38.9231 | 1.9261 | 74.9698 | 38.9231 | 1.9261 | 83.1953 | 43.1937 | 1.9261 | 0.9762%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.3096 | 0.3139 | 7.3579 | 2.3096 | 0.3139 | 7.3579 | 2.563 | 0.34834 | 7.3579 | 0.9867%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 115 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 82.5872 | 36.0981 | 2.2879 | 82.5872 | 36.0981 | 2.2879 | 91.6485 | 40.0587 | 2.2879 | 0.9973%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 618 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 244.3147 | 193.9879 | 1.2594 | 244.3147 | 193.9879 | 1.2594 | 271.1204 | 215.2718 | 1.2594 | 0.9919%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 53 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 57.7563 | 16.6365 | 3.4717 | 57.7563 | 16.6365 | 3.4717 | 64.0932 | 18.4618 | 3.4717 | 0.9998%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 451 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 141.0713 | 141.5672 | 0.9965 | 141.0713 | 141.5672 | 0.9965 | 156.5494 | 157.0996 | 0.9965 | 0.9833%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 350 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 105.7677 | 109.8637 | 0.96272 | 105.7677 | 109.8637 | 0.96272 | 117.3723 | 121.9177 | 0.96272 | 0.988%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 479 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 48.7918 | 150.3563 | 0.32451 | 48.7918 | 150.3563 | 0.32451 | 54.1451 | 166.8531 | 0.32451 | 0.9625%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 302 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.2496 | 94.7967 | 0.12922 | 12.2496 | 94.7967 | 0.12922 | 13.5936 | 105.1975 | 0.12922 | 0.9181%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 118 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 71.2405 | 37.0398 | 1.9234 | 71.2405 | 37.0398 | 1.9234 | 79.0568 | 41.1037 | 1.9234 | 0.9835%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 313 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 371.2832 | 98.2495 | 3.779 | 371.2832 | 98.2495 | 3.779 | 412.0195 | 109.0292 | 3.779 | 0.9889%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 226 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 30.5007 | 70.9406 | 0.42995 | 30.5007 | 70.9406 | 0.42995 | 33.8472 | 78.724 | 0.42995 | 0.9191%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 273 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 203.4497 | 85.6937 | 2.3742 | 203.4497 | 85.6937 | 2.3742 | 225.7718 | 95.0958 | 2.3742 | 0.9908%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 2 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3753 | 0.62779 | 2.1906 | 1.3753 | 0.62779 | 2.1906 | 1.5261 | 0.69667 | 2.1906 | 0.9858%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 71 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.4441 | 22.2866 | 0.33402 | 7.4441 | 22.2866 | 0.33402 | 8.2609 | 24.7319 | 0.33402 | 0.9652%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 434 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 499.1345 | 136.231 | 3.6639 | 499.1345 | 136.231 | 3.6639 | 553.8984 | 151.1779 | 3.6639 | 0.9927%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 1 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 51.8797 | 0.3139 | 165.2766 | 51.8797 | 0.3139 | 165.2766 | 57.5718 | 0.34834 | 165.2766 | 0.9997%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 458 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 291.8804 | 143.7645 | 2.0303 | 291.8804 | 143.7645 | 2.0303 | 323.9049 | 159.538 | 2.0303 | 0.9926%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 136 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.3192 | 42.6899 | 0.26515 | 11.3192 | 42.6899 | 0.26515 | 12.5611 | 47.3737 | 0.26515 | 0.9598%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 74 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 30.7953 | 23.2283 | 1.3258 | 30.7953 | 23.2283 | 1.3258 | 34.1741 | 25.7769 | 1.3258 | 0.9934%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 41 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.7625 | 12.8697 | 0.75856 | 9.7625 | 12.8697 | 0.75856 | 10.8336 | 14.2818 | 0.75856 | 0.6902%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 93 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.8843 | 29.1924 | 0.47562 | 13.8843 | 29.1924 | 0.47562 | 15.4077 | 32.3953 | 0.47562 | 0.7661%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.9364 | 0.62779 | 6.2702 | 3.9364 | 0.62779 | 6.2702 | 4.3683 | 0.69667 | 6.2702 | 0.9947%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 34 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 117.5454 | 10.6725 | 11.0139 | 117.5454 | 10.6725 | 11.0139 | 130.4422 | 11.8434 | 11.0139 | 0.9966%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 309 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 136.5462 | 96.994 | 1.4078 | 136.5462 | 96.994 | 1.4078 | 151.5277 | 107.6359 | 1.4078 | 0.9905%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 657 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 256.3868 | 206.2299 | 1.2432 | 256.3868 | 206.2299 | 1.2432 | 284.5169 | 228.8569 | 1.2432 | 0.9891%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 75 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 72.5488 | 23.5422 | 3.0816 | 72.5488 | 23.5422 | 3.0816 | 80.5087 | 26.1252 | 3.0816 | 0.9946%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 25 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 39.4065 | 7.8474 | 5.0216 | 39.4065 | 7.8474 | 5.0216 | 43.7301 | 8.7084 | 5.0216 | 0.9952%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 123 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 132.3028 | 38.6092 | 3.4267 | 132.3028 | 38.6092 | 3.4267 | 146.8188 | 42.8454 | 3.4267 | 0.9843%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 319 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 101.4885 | 100.1329 | 1.0135 | 101.4885 | 100.1329 | 1.0135 | 112.6235 | 111.1193 | 1.0135 | 0.9898%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 88 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 71.9042 | 27.6229 | 2.6031 | 71.9042 | 27.6229 | 2.6031 | 79.7933 | 30.6536 | 2.6031 | 0.9853%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 704 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 209.5961 | 220.983 | 0.94847 | 209.5961 | 220.983 | 0.94847 | 232.5925 | 245.2287 | 0.94847 | 0.9839%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 407 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 203.259 | 127.7558 | 1.591 | 203.259 | 127.7558 | 1.591 | 225.5601 | 141.7729 | 1.591 | 0.9748%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 137 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 82.5252 | 43.0038 | 1.919 | 82.5252 | 43.0038 | 1.919 | 91.5797 | 47.7221 | 1.919 | 0.9912%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 80 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 45.8566 | 25.1117 | 1.8261 | 45.8566 | 25.1117 | 1.8261 | 50.8879 | 27.8669 | 1.8261 | 0.9732%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 48 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 78.0753 | 15.067 | 5.1819 | 78.0753 | 15.067 | 5.1819 | 86.6415 | 16.7201 | 5.1819 | 0.9953%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 42 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 58.178 | 13.1836 | 4.4129 | 58.178 | 13.1836 | 4.4129 | 64.5612 | 14.6301 | 4.4129 | 0.9803%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 138 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 29.7799 | 43.3177 | 0.68748 | 29.7799 | 43.3177 | 0.68748 | 33.0473 | 48.0704 | 0.68748 | 0.9369%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 12 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 64.3818 | 3.7668 | 17.0921 | 64.3818 | 3.7668 | 17.0921 | 71.4456 | 4.18 | 17.0921 | 0.9955%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 5 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 46.8889 | 1.5695 | 29.8754 | 46.8889 | 1.5695 | 29.8754 | 52.0335 | 1.7417 | 29.8754 | 0.803%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 17 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.7574 | 5.3362 | 0.70413 | 3.7574 | 5.3362 | 0.70413 | 4.1696 | 5.9217 | 0.70413 | 0.6587%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 107 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 41.5562 | 33.5869 | 1.2373 | 41.5562 | 33.5869 | 1.2373 | 46.1156 | 37.272 | 1.2373 | 0.9978%
2027 | CB 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 82 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 30.2704 | 25.7395 | 1.176 | 30.2704 | 25.7395 | 1.176 | 33.5916 | 28.5636 | 1.176 | 0.9981%
2027 | CB 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 19 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.8231 | 5.964 | 2.1501 | 12.8231 | 5.964 | 2.1501 | 14.23 | 6.6184 | 2.1501 | 0.9962%
2027 | CB 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.2838 | 0.94169 | 10.9206 | 10.2838 | 0.94169 | 10.9206 | 11.4121 | 1.045 | 10.9206 | 0.9972%
2027 | CB 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 56 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.1761 | 17.5782 | 0.29446 | 5.1761 | 17.5782 | 0.29446 | 5.7441 | 19.5068 | 0.29446 | 0.3454%
2027 | CB 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 80 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.2241 | 25.1117 | 0.20804 | 5.2241 | 25.1117 | 0.20804 | 5.7973 | 27.8669 | 0.20804 | 0.75%
2027 | CB 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 571 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 48.4098 | 179.2348 | 0.27009 | 48.4098 | 179.2348 | 0.27009 | 53.7212 | 198.9 | 0.27009 | 0.8429%
2027 | CB 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 1192 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 59.9246 | 374.1644 | 0.16016 | 59.9246 | 374.1644 | 0.16016 | 66.4994 | 415.2168 | 0.16016 | 0.9909%
2027 | CB 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 132 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.0561 | 41.4343 | 0.3151 | 13.0561 | 41.4343 | 0.3151 | 14.4885 | 45.9804 | 0.3151 | 0.9975%
2027 | CB 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.98124 | 1.2556 | 0.7815 | 0.98124 | 1.2556 | 0.7815 | 1.0889 | 1.3933 | 0.7815 | 0.9975%
2027 | CB 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 38 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 37.0598 | 11.9281 | 3.1069 | 37.0598 | 11.9281 | 3.1069 | 41.1259 | 13.2368 | 3.1069 | 0.9993%
2027 | CB 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 3 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.35763 | 0.94169 | 0.37978 | 0.35763 | 0.94169 | 0.37978 | 0.39687 | 1.045 | 0.37978 | 0.9408%
2027 | CB 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 1 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.83874 | 0.3139 | 2.672 | 0.83874 | 0.3139 | 2.672 | 0.93076 | 0.34834 | 2.672 | 0.3549%
2027 | CB 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 1 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 2.8867 | 0.3139 | 9.1963 | 2.8867 | 0.3139 | 9.1963 | 3.2034 | 0.34834 | 9.1963 | 0.7993%
2027 | CB 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 58 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.6527 | 18.206 | 0.20063 | 3.6527 | 18.206 | 0.20063 | 4.0535 | 20.2035 | 0.20063 | 0.299%
2027 | CB 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 22 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.1598 | 6.9057 | 0.16795 | 1.1598 | 6.9057 | 0.16795 | 1.287 | 7.6634 | 0.16795 | 0.9512%
2027 | CB 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 248 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.17071 | 77.8463 | 0.0021929 | 0.17071 | 77.8463 | 0.0021929 | 0.18944 | 86.3874 | 0.0021929 | 0.09583%
2027 | CB 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 89 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.7926 | 27.9368 | 0.27894 | 7.7926 | 27.9368 | 0.27894 | 8.6476 | 31.0019 | 0.27894 | 0.8082%
2027 | CB 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 36 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.9331 | 11.3003 | 0.17107 | 1.9331 | 11.3003 | 0.17107 | 2.1452 | 12.5401 | 0.17107 | 0.9981%
2027 | CB 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 209 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 22.587 | 65.6043 | 0.34429 | 22.587 | 65.6043 | 0.34429 | 25.0652 | 72.8023 | 0.34429 | 0.9929%
2027 | CB 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 277 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 14.5549 | 86.9493 | 0.1674 | 14.5549 | 86.9493 | 0.1674 | 16.1519 | 96.4891 | 0.1674 | 0.9737%
2027 | CB 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 730 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 37.0873 | 229.1443 | 0.16185 | 37.0873 | 229.1443 | 0.16185 | 41.1564 | 254.2855 | 0.16185 | 0.9874%
2027 | CB 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 485 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 29.646 | 152.2397 | 0.19473 | 29.646 | 152.2397 | 0.19473 | 32.8986 | 168.9431 | 0.19473 | 0.9888%
2027 | CB 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 236 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 112.9166 | 74.0795 | 1.5243 | 112.9166 | 74.0795 | 1.5243 | 125.3055 | 82.2074 | 1.5243 | 0.9762%
2027 | CB 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 2 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 19.127 | 0.62779 | 30.4671 | 19.127 | 0.62779 | 30.4671 | 21.2256 | 0.69667 | 30.4671 | 0.9954%
2027 | CB 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 134 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.2264 | 42.0621 | 0.2669 | 11.2264 | 42.0621 | 0.2669 | 12.4582 | 46.6771 | 0.2669 | 0.9768%
2027 | CB 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 18 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.3827 | 5.6501 | 0.42171 | 2.3827 | 5.6501 | 0.42171 | 2.6441 | 6.2701 | 0.42171 | 0.6436%
2027 | CB 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 10 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0086 | 3.139 | 0.32133 | 1.0086 | 3.139 | 0.32133 | 1.1193 | 3.4834 | 0.32133 | 0.375%
2027 | CB 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 167 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.7811 | 52.4207 | 0.22474 | 11.7811 | 52.4207 | 0.22474 | 13.0737 | 58.1722 | 0.22474 | 0.9%
2027 | CB 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 45 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.4286 | 14.1253 | 0.17193 | 2.4286 | 14.1253 | 0.17193 | 2.695 | 15.6751 | 0.17193 | 0.7028%
2027 | CB 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 46 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.7118 | 14.4392 | 0.60334 | 8.7118 | 14.4392 | 0.60334 | 9.6676 | 16.0235 | 0.60334 | 0.995%
2027 | CB 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 79 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.3021 | 24.7978 | 0.29447 | 7.3021 | 24.7978 | 0.29447 | 8.1033 | 27.5186 | 0.29447 | 0.9704%
2027 | CB 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 82 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.57264 | 25.7395 | 0.022247 | 0.57264 | 25.7395 | 0.022247 | 0.63547 | 28.5636 | 0.022247 | 0.6647%
2027 | CB 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.09533 | 4.0807 | 0.023361 | 0.09533 | 4.0807 | 0.023361 | 0.10579 | 4.5284 | 0.023361 | 0.9726%
2027 | CB 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.2284 | 0.3139 | 42.1425 | 13.2284 | 0.3139 | 42.1425 | 14.6798 | 0.34834 | 42.1425 | 0.9979%
2027 | CB 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.8969 | 4.3945 | 0.43166 | 1.8969 | 4.3945 | 0.43166 | 2.1051 | 4.8767 | 0.43166 | 0.9683%
2027 | CB 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 96 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.37712 | 30.134 | 0.012515 | 0.37712 | 30.134 | 0.012515 | 0.4185 | 33.4403 | 0.012515 | 0.3335%
2027 | CB 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 211 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 132.4063 | 66.2321 | 1.9991 | 132.4063 | 66.2321 | 1.9991 | 146.9336 | 73.4989 | 1.9991 | 0.9966%
2027 | CB 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 22 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.79342 | 6.9057 | 0.11489 | 0.79342 | 6.9057 | 0.11489 | 0.88048 | 7.6634 | 0.11489 | 0.9922%
2027 | CB 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.068099 | 0.3139 | 0.21695 | 0.068099 | 0.3139 | 0.21695 | 0.075571 | 0.34834 | 0.21695 | 0.986%
2027 | CB 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 376 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 101.5275 | 118.025 | 0.86022 | 101.5275 | 118.025 | 0.86022 | 112.6669 | 130.9744 | 0.86022 | 0.9884%
2027 | CB 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.061378 | 0.3139 | 0.19554 | 0.061378 | 0.3139 | 0.19554 | 0.068112 | 0.34834 | 0.19554 | 0.991%
2027 | CB 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 184 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 53.3875 | 57.7569 | 0.92435 | 53.3875 | 57.7569 | 0.92435 | 59.2451 | 64.0939 | 0.92435 | 0.9601%
2027 | CB 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4798 | 4.3945 | 0.33673 | 1.4798 | 4.3945 | 0.33673 | 1.6422 | 4.8767 | 0.33673 | 0.1888%
2027 | CB 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 2 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.87422 | 0.62779 | 1.3925 | 0.87422 | 0.62779 | 1.3925 | 0.97014 | 0.69667 | 1.3925 | 0.1434%
2027 | CB 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 40 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.7001 | 12.5559 | 0.77255 | 9.7001 | 12.5559 | 0.77255 | 10.7643 | 13.9334 | 0.77255 | 0.9408%
2027 | CB 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 56 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 60.146 | 17.5782 | 3.4216 | 60.146 | 17.5782 | 3.4216 | 66.7451 | 19.5068 | 3.4216 | 0.9549%
2027 | CB 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.16724 | 0.94169 | 0.1776 | 0.16724 | 0.94169 | 0.1776 | 0.18559 | 1.045 | 0.1776 | 0.9464%
2027 | CB 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 1 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.015734 | 0.3139 | 0.050124 | 0.015734 | 0.3139 | 0.050124 | 0.01746 | 0.34834 | 0.050124 | 0.9786%
2027 | CB 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 11 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.01877 | 3.4529 | 0.0054362 | 0.01877 | 3.4529 | 0.0054362 | 0.02083 | 3.8317 | 0.0054362 | 0.1679%
2027 | CB 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 277 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 8.7492 | 86.9493 | 0.10062 | 8.7492 | 86.9493 | 0.10062 | 9.7091 | 96.4891 | 0.10062 | 0.8949%
2027 | CB 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 87 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 1.0343 | 27.309 | 0.037875 | 1.0343 | 27.309 | 0.037875 | 1.1478 | 30.3053 | 0.037875 | 0.372%
2027 | CB 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 12 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.1282 | 3.7668 | 1.096 | 4.1282 | 3.7668 | 1.096 | 4.5811 | 4.18 | 1.096 | 0.9425%
2027 | CB 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 8 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.37517 | 2.5112 | 0.1494 | 0.37517 | 2.5112 | 0.1494 | 0.41633 | 2.7867 | 0.1494 | 0.7619%
2027 | CB 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 56 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.60728 | 17.5782 | 0.034548 | 0.60728 | 17.5782 | 0.034548 | 0.67391 | 19.5068 | 0.034548 | 0.9924%
2027 | CB 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 45 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.2474 | 14.1253 | 0.58387 | 8.2474 | 14.1253 | 0.58387 | 9.1523 | 15.6751 | 0.58387 | 0.9545%
2027 | CB 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 20 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.9788 | 6.2779 | 0.47448 | 2.9788 | 6.2779 | 0.47448 | 3.3056 | 6.9667 | 0.47448 | 0.7837%
2027 | CB 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 375 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 39.2661 | 117.7111 | 0.33358 | 39.2661 | 117.7111 | 0.33358 | 43.5742 | 130.6261 | 0.33358 | 0.9981%
2027 | CB 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 47 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.46433 | 14.7531 | 0.031473 | 0.46433 | 14.7531 | 0.031473 | 0.51527 | 16.3718 | 0.031473 | 0.9266%
2027 | CB 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 23 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 74.135 | 7.2196 | 10.2686 | 74.135 | 7.2196 | 10.2686 | 82.2689 | 8.0117 | 10.2686 | 0.9507%
2027 | CB 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 104 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.38586 | 32.6452 | 0.01182 | 0.38586 | 32.6452 | 0.01182 | 0.42819 | 36.227 | 0.01182 | 0.9943%
2027 | CB 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 26 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 24.913 | 8.1613 | 3.0526 | 24.913 | 8.1613 | 3.0526 | 27.6464 | 9.0567 | 3.0526 | 0.9983%
2027 | CB 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 89 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.8713 | 27.9368 | 0.10278 | 2.8713 | 27.9368 | 0.10278 | 3.1863 | 31.0019 | 0.10278 | 0.9343%
2027 | CB 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 2 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.2834 | 0.62779 | 3.6371 | 2.2834 | 0.62779 | 3.6371 | 2.5339 | 0.69667 | 3.6371 | 0.9997%
2027 | CB 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 34 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 103.7418 | 10.6725 | 9.7205 | 103.7418 | 10.6725 | 9.7205 | 115.1241 | 11.8434 | 9.7205 | 0.9951%
2027 | CB 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 36 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.8118 | 11.3003 | 1.0453 | 11.8118 | 11.3003 | 1.0453 | 13.1078 | 12.5401 | 1.0453 | 0.9951%
2027 | CB 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 341 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.5186 | 107.0386 | 0.032873 | 3.5186 | 107.0386 | 0.032873 | 3.9047 | 118.7827 | 0.032873 | 0.997%
2027 | CB 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 23 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.2038 | 7.2196 | 0.16674 | 1.2038 | 7.2196 | 0.16674 | 1.3359 | 8.0117 | 0.16674 | 0.9965%
2027 | CB CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.22558 | 0.62779 | 0.35932 | 0.22558 | 0.62779 | 0.35932 | 0.25033 | 0.69667 | 0.35932 | 0.9021%
2027 | CB FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 161 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.1647 | 50.5373 | 0.023046 | 1.1647 | 50.5373 | 0.023046 | 1.2925 | 56.0821 | 0.023046 | 0.3693%
2027 | CB FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 154 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 8.8377 | 48.34 | 0.18282 | 8.8377 | 48.34 | 0.18282 | 9.8074 | 53.6438 | 0.18282 | 0.9433%
2027 | CB JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 126 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.6384 | 39.5509 | 0.34483 | 13.6384 | 39.5509 | 0.34483 | 15.1347 | 43.8904 | 0.34483 | 0.9785%
2027 | CB MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 97 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 45.916 | 30.4479 | 1.508 | 45.916 | 30.4479 | 1.508 | 50.9538 | 33.7886 | 1.508 | 0.9856%
2027 | CB NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 10 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 5.7493 | 3.139 | 1.8316 | 5.7493 | 3.139 | 1.8316 | 6.3801 | 3.4834 | 1.8316 | 0.9902%
2027 | CB OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 593 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 62.3027 | 186.1405 | 0.33471 | 62.3027 | 186.1405 | 0.33471 | 69.1384 | 206.5634 | 0.33471 | 0.99%
2027 | CB PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 510 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 26.0975 | 160.0871 | 0.16302 | 26.0975 | 160.0871 | 0.16302 | 28.9608 | 177.6515 | 0.16302 | 0.9473%
2027 | CB RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 214 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 94.0833 | 67.1738 | 1.4006 | 94.0833 | 67.1738 | 1.4006 | 104.4059 | 74.544 | 1.4006 | 0.9831%
2027 | CB RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 170 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 46.6933 | 53.3624 | 0.87502 | 46.6933 | 53.3624 | 0.87502 | 51.8164 | 59.2172 | 0.87502 | 0.9811%
2027 | CB RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 44 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.7942 | 13.8114 | 0.41952 | 5.7942 | 13.8114 | 0.41952 | 6.4299 | 15.3268 | 0.41952 | 0.695%
2027 | CB RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.27042 | 0.94169 | 0.28717 | 0.27042 | 0.94169 | 0.28717 | 0.30009 | 1.045 | 0.28717 | 0.9988%
2027 | CB RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 182 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 33.7388 | 57.1291 | 0.59057 | 33.7388 | 57.1291 | 0.59057 | 37.4406 | 63.3972 | 0.59057 | 0.9914%
2027 | CB SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 316 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 28.667 | 99.1912 | 0.28901 | 28.667 | 99.1912 | 0.28901 | 31.8123 | 110.0743 | 0.28901 | 0.9371%
2027 | CB SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 22 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.017168 | 6.9057 | 0.0024861 | 0.017168 | 6.9057 | 0.0024861 | 0.019052 | 7.6634 | 0.0024861 | 0.02003%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 375 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.8194 | 117.7111 | 0.1259 | 14.8194 | 117.7111 | 0.1259 | 16.4453 | 130.6261 | 0.1259 | 0.789%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 113 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 32.21 | 35.4703 | 0.90808 | 32.21 | 35.4703 | 0.90808 | 35.744 | 39.362 | 0.90808 | 0.9517%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 254 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 84.4138 | 79.7297 | 1.0588 | 84.4138 | 79.7297 | 1.0588 | 93.6755 | 88.4774 | 1.0588 | 0.9933%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 570 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 61.4447 | 178.9209 | 0.34342 | 61.4447 | 178.9209 | 0.34342 | 68.1863 | 198.5517 | 0.34342 | 0.9757%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 73 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 53.7422 | 22.9144 | 2.3453 | 53.7422 | 22.9144 | 2.3453 | 59.6387 | 25.4285 | 2.3453 | 0.9932%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 239 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 34.2446 | 75.0212 | 0.45647 | 34.2446 | 75.0212 | 0.45647 | 38.0018 | 83.2524 | 0.45647 | 0.9948%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 5 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.0072 | 1.4972 | 0.67272 | 1.0072 | 1.4972 | 0.67272 | 1.1774 | 1.7502 | 0.67272 | 0.9903%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 34 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.5207 | 10.1808 | 0.34582 | 3.5207 | 10.1808 | 0.34582 | 4.1158 | 11.9015 | 0.34582 | 0.9915%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 620 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 33.5037 | 185.6502 | 0.18047 | 33.5037 | 185.6502 | 0.18047 | 39.1662 | 217.0271 | 0.18047 | 0.9141%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 510 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 302.1866 | 152.7122 | 1.9788 | 302.1866 | 152.7122 | 1.9788 | 353.2596 | 178.5223 | 1.9788 | 0.9902%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 72 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 60.1308 | 21.5594 | 2.7891 | 60.1308 | 21.5594 | 2.7891 | 70.2936 | 25.2032 | 2.7891 | 0.9818%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 230 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 162.927 | 68.8702 | 2.3657 | 162.927 | 68.8702 | 2.3657 | 190.4635 | 80.5101 | 2.3657 | 0.997%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 99 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 43.4855 | 29.6441 | 1.4669 | 43.4855 | 29.6441 | 1.4669 | 50.835 | 34.6543 | 1.4669 | 0.9951%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 32 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 11.9862 | 9.5819 | 1.2509 | 11.9862 | 9.5819 | 1.2509 | 14.012 | 11.2014 | 1.2509 | 0.9958%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 20 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 6.8679 | 5.9887 | 1.1468 | 6.8679 | 5.9887 | 1.1468 | 8.0287 | 7.0009 | 1.1468 | 0.996%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 145 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 84.7538 | 43.4182 | 1.952 | 84.7538 | 43.4182 | 1.952 | 99.0781 | 50.7563 | 1.952 | 0.9962%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 5 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 5.9834 | 1.4972 | 3.9965 | 5.9834 | 1.4972 | 3.9965 | 6.9947 | 1.7502 | 3.9965 | 0.9922%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 57 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 43.6602 | 17.0678 | 2.558 | 43.6602 | 17.0678 | 2.558 | 51.0392 | 19.9525 | 2.558 | 0.9916%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 198 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 24.8966 | 59.2883 | 0.41992 | 24.8966 | 59.2883 | 0.41992 | 29.1044 | 69.3087 | 0.41992 | 0.9924%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 886 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 78.8985 | 265.3001 | 0.29739 | 78.8985 | 265.3001 | 0.29739 | 92.2332 | 310.1388 | 0.29739 | 0.9598%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 587 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 31.9045 | 175.7688 | 0.18151 | 31.9045 | 175.7688 | 0.18151 | 37.2967 | 205.4757 | 0.18151 | 0.9739%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 101 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.4563 | 30.243 | 0.14735 | 4.4563 | 30.243 | 0.14735 | 5.2095 | 35.3544 | 0.14735 | 0.8768%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 14 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 43.7073 | 4.1921 | 10.4261 | 43.7073 | 4.1921 | 10.4261 | 51.0943 | 4.9006 | 10.4261 | 0.9826%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 117 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 101.1325 | 35.034 | 2.8867 | 101.1325 | 35.034 | 2.8867 | 118.2251 | 40.9551 | 2.8867 | 0.9858%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 50 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 18.5685 | 14.9718 | 1.2402 | 18.5685 | 14.9718 | 1.2402 | 21.7068 | 17.5022 | 1.2402 | 0.9945%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 307 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 56.703 | 91.9268 | 0.61683 | 56.703 | 91.9268 | 0.61683 | 66.2865 | 107.4634 | 0.61683 | 0.9866%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 298 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 217.8957 | 89.2318 | 2.4419 | 217.8957 | 89.2318 | 2.4419 | 254.7226 | 104.313 | 2.4419 | 0.9914%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 474 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 242.8087 | 141.9325 | 1.7107 | 242.8087 | 141.9325 | 1.7107 | 283.8462 | 165.9208 | 1.7107 | 0.9849%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 159 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 229.7909 | 47.6103 | 4.8265 | 229.7909 | 47.6103 | 4.8265 | 268.6282 | 55.657 | 4.8265 | 0.9916%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 740 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 134.9918 | 221.5824 | 0.60922 | 134.9918 | 221.5824 | 0.60922 | 157.807 | 259.0324 | 0.60922 | 0.9745%
2028 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 49 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.13544 | 14.6724 | 0.0092306 | 0.13544 | 14.6724 | 0.0092306 | 0.15833 | 17.1521 | 0.0092306 | 0.8684%
2028 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 18 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.029974 | 5.3898 | 0.0055612 | 0.029974 | 5.3898 | 0.0055612 | 0.03504 | 6.3008 | 0.0055612 | 0.1275%
2028 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 2 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.019063 | 0.59887 | 0.031832 | 0.019063 | 0.59887 | 0.031832 | 0.022285 | 0.70009 | 0.031832 | 0.3435%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 5 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.2935 | 1.4972 | 4.2036 | 6.2935 | 1.4972 | 4.2036 | 7.3572 | 1.7502 | 4.2036 | 0.9924%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 72 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.4964 | 21.5594 | 0.34771 | 7.4964 | 21.5594 | 0.34771 | 8.7634 | 25.2032 | 0.34771 | 0.9393%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 2 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.0761 | 0.59887 | 1.7969 | 1.0761 | 0.59887 | 1.7969 | 1.258 | 0.70009 | 1.7969 | 0.8802%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 252 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 51.0132 | 75.4578 | 0.67605 | 51.0132 | 75.4578 | 0.67605 | 59.635 | 88.211 | 0.67605 | 0.9962%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 260 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 43.1612 | 77.8533 | 0.55439 | 43.1612 | 77.8533 | 0.55439 | 50.456 | 91.0114 | 0.55439 | 0.9962%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 214 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 21.7896 | 64.0792 | 0.34004 | 21.7896 | 64.0792 | 0.34004 | 25.4723 | 74.9094 | 0.34004 | 0.9984%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 47 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.81731 | 14.0735 | 0.058074 | 0.81731 | 14.0735 | 0.058074 | 0.95544 | 16.4521 | 0.058074 | 0.9877%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 4 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 18.5594 | 1.1977 | 15.4953 | 18.5594 | 1.1977 | 15.4953 | 21.6962 | 1.4002 | 15.4953 | 0.9968%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 24 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 36.6746 | 7.1865 | 5.1033 | 36.6746 | 7.1865 | 5.1033 | 42.8731 | 8.4011 | 5.1033 | 0.9992%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 17 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.4206 | 5.0904 | 0.67197 | 3.4206 | 5.0904 | 0.67197 | 3.9987 | 5.9507 | 0.67197 | 0.945%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 60 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 6.8028 | 17.9661 | 0.37865 | 6.8028 | 17.9661 | 0.37865 | 7.9526 | 21.0026 | 0.37865 | 0.994%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 840 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 36.8914 | 251.526 | 0.14667 | 36.8914 | 251.526 | 0.14667 | 43.1264 | 294.0368 | 0.14667 | 0.9112%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 10 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.7327 | 2.9944 | 0.57866 | 1.7327 | 2.9944 | 0.57866 | 2.0256 | 3.5004 | 0.57866 | 0.9662%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 2 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.1043 | 0.59887 | 3.5138 | 2.1043 | 0.59887 | 3.5138 | 2.4599 | 0.70009 | 3.5138 | 0.9775%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 45 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 33.8232 | 13.4746 | 2.5101 | 33.8232 | 13.4746 | 2.5101 | 39.5397 | 15.752 | 2.5101 | 0.9826%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 53 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 87.5467 | 15.8701 | 5.5165 | 87.5467 | 15.8701 | 5.5165 | 102.3431 | 18.5523 | 5.5165 | 0.9977%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 215 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 88.7835 | 64.3787 | 1.3791 | 88.7835 | 64.3787 | 1.3791 | 103.789 | 75.2594 | 1.3791 | 0.9908%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 28 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 52.232 | 8.3842 | 6.2298 | 52.232 | 8.3842 | 6.2298 | 61.0598 | 9.8012 | 6.2298 | 0.9788%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 21 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 18.208 | 6.2882 | 2.8956 | 18.208 | 6.2882 | 2.8956 | 21.2853 | 7.3509 | 2.8956 | 0.9469%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 186 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 72.8304 | 55.695 | 1.3077 | 72.8304 | 55.695 | 1.3077 | 85.1396 | 65.1081 | 1.3077 | 0.9648%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 75 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.3348 | 22.4577 | 0.59377 | 13.3348 | 22.4577 | 0.59377 | 15.5885 | 26.2533 | 0.59377 | 0.9856%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 117 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 30.4313 | 35.034 | 0.86862 | 30.4313 | 35.034 | 0.86862 | 35.5746 | 40.9551 | 0.86862 | 0.9842%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 246 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 25.3573 | 73.6612 | 0.34424 | 25.3573 | 73.6612 | 0.34424 | 29.643 | 86.1108 | 0.34424 | 0.979%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 35 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 11.9053 | 10.4803 | 1.136 | 11.9053 | 10.4803 | 1.136 | 13.9174 | 12.2515 | 1.136 | 0.9892%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 94 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 36.828 | 28.147 | 1.3084 | 36.828 | 28.147 | 1.3084 | 43.0524 | 32.9041 | 1.3084 | 0.9866%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 2 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.5601 | 0.59887 | 5.9446 | 3.5601 | 0.59887 | 5.9446 | 4.1617 | 0.70009 | 5.9446 | 0.9965%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 17 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 3.951 | 5.0904 | 0.77617 | 3.951 | 5.0904 | 0.77617 | 4.6188 | 5.9507 | 0.77617 | 0.9977%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 55 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.1595 | 16.469 | 0.61689 | 10.1595 | 16.469 | 0.61689 | 11.8766 | 19.2524 | 0.61689 | 0.9935%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 9 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.3665 | 2.6949 | 0.50708 | 1.3665 | 2.6949 | 0.50708 | 1.5975 | 3.1504 | 0.50708 | 0.9948%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 33 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.1502 | 9.8814 | 1.6344 | 16.1502 | 9.8814 | 1.6344 | 18.8798 | 11.5514 | 1.6344 | 0.9905%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 63 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 51.8366 | 18.8645 | 2.7478 | 51.8366 | 18.8645 | 2.7478 | 60.5976 | 22.0528 | 2.7478 | 0.9304%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 25 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 55.93 | 7.4859 | 7.4714 | 55.93 | 7.4859 | 7.4714 | 65.3828 | 8.7511 | 7.4714 | 0.9454%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 335 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 101.2356 | 100.311 | 1.0092 | 101.2356 | 100.311 | 1.0092 | 118.3455 | 117.2647 | 1.0092 | 0.9926%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 91 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 31.3976 | 27.2487 | 1.1523 | 31.3976 | 27.2487 | 1.1523 | 36.7042 | 31.854 | 1.1523 | 0.9815%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 35 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.3566 | 10.4803 | 0.32028 | 3.3566 | 10.4803 | 0.32028 | 3.924 | 12.2515 | 0.32028 | 0.9046%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 8 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 17.5658 | 2.3955 | 7.3329 | 17.5658 | 2.3955 | 7.3329 | 20.5346 | 2.8004 | 7.3329 | 0.8554%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 101 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 37.432 | 30.243 | 1.2377 | 37.432 | 30.243 | 1.2377 | 43.7585 | 35.3544 | 1.2377 | 0.9867%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.50519 | 1.1977 | 0.42179 | 0.50519 | 1.1977 | 0.42179 | 0.59057 | 1.4002 | 0.42179 | 0.9994%
2028 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 14 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 4.1921 | 0 | 0 | 4.1921 | 0 | 0 | 4.9006 | 0 | 0%
2028 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 8 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2.3955 | 0 | 0 | 2.3955 | 0 | 0 | 2.8004 | 0 | 0%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 58 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 137.5213 | 17.3673 | 7.9184 | 137.5213 | 17.3673 | 7.9184 | 160.764 | 20.3025 | 7.9184 | 0.9909%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.43358 | 2.0961 | 0.20686 | 0.43358 | 2.0961 | 0.20686 | 0.50686 | 2.4503 | 0.20686 | 0.2981%
2028 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.70284 | 0.29944 | 2.3472 | 0.70284 | 0.29944 | 2.3472 | 0.82162 | 0.35004 | 2.3472 | 0.9995%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 151 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 70.2994 | 45.2148 | 1.5548 | 70.2994 | 45.2148 | 1.5548 | 82.1808 | 52.8566 | 1.5548 | 0.9925%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 444 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 319.7831 | 132.9495 | 2.4053 | 319.7831 | 132.9495 | 2.4053 | 373.8301 | 155.4194 | 2.4053 | 0.9936%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 4 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.064239 | 1.1977 | 0.053633 | 0.064239 | 1.1977 | 0.053633 | 0.075096 | 1.4002 | 0.053633 | 0.895%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 42 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.1867 | 12.5763 | 0.25339 | 3.1867 | 12.5763 | 0.25339 | 3.7253 | 14.7018 | 0.25339 | 0.8771%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 319 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 44.2007 | 95.52 | 0.46274 | 44.2007 | 95.52 | 0.46274 | 51.6711 | 111.664 | 0.46274 | 0.9246%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 26 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 26.2521 | 7.7853 | 3.372 | 26.2521 | 7.7853 | 3.372 | 30.689 | 9.1011 | 3.372 | 0.9907%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 61 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 33.306 | 18.2656 | 1.8234 | 33.306 | 18.2656 | 1.8234 | 38.9351 | 21.3527 | 1.8234 | 0.9899%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 124 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 26.1371 | 37.13 | 0.70393 | 26.1371 | 37.13 | 0.70393 | 30.5546 | 43.4054 | 0.70393 | 0.9527%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 208 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 14.5896 | 62.2826 | 0.23425 | 14.5896 | 62.2826 | 0.23425 | 17.0554 | 72.8091 | 0.23425 | 0.8154%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 114 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 15.4015 | 34.1357 | 0.45118 | 15.4015 | 34.1357 | 0.45118 | 18.0045 | 39.905 | 0.45118 | 0.9501%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 323 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 157.884 | 96.7177 | 1.6324 | 157.884 | 96.7177 | 1.6324 | 184.5682 | 113.0641 | 1.6324 | 0.97%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 419 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 34.6605 | 125.4636 | 0.27626 | 34.6605 | 125.4636 | 0.27626 | 40.5185 | 146.6683 | 0.27626 | 0.991%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 16.261 | 15.8701 | 1.0246 | 16.261 | 15.8701 | 1.0246 | 19.0093 | 18.5523 | 1.0246 | 0.7065%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 166 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 37.1254 | 49.7063 | 0.74689 | 37.1254 | 49.7063 | 0.74689 | 43.4 | 58.1073 | 0.74689 | 0.9752%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 248 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 48.2755 | 74.2601 | 0.65009 | 48.2755 | 74.2601 | 0.65009 | 56.4346 | 86.8109 | 0.65009 | 0.9686%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 143 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 5.7898 | 42.8193 | 0.13521 | 5.7898 | 42.8193 | 0.13521 | 6.7683 | 50.0563 | 0.13521 | 0.7976%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 96 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 98.7984 | 28.7458 | 3.437 | 98.7984 | 28.7458 | 3.437 | 115.4964 | 33.6042 | 3.437 | 0.9877%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 63 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 35.6347 | 18.8645 | 1.889 | 35.6347 | 18.8645 | 1.889 | 41.6574 | 22.0528 | 1.889 | 0.981%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 234 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 84.8927 | 70.068 | 1.2116 | 84.8927 | 70.068 | 1.2116 | 99.2405 | 81.9102 | 1.2116 | 0.9713%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 19 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.3749 | 5.6893 | 0.41743 | 2.3749 | 5.6893 | 0.41743 | 2.7763 | 6.6508 | 0.41743 | 0.6764%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 62 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 28.8558 | 18.565 | 1.5543 | 28.8558 | 18.565 | 1.5543 | 33.7328 | 21.7027 | 1.5543 | 0.9774%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 95 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 41.8474 | 28.4464 | 1.4711 | 41.8474 | 28.4464 | 1.4711 | 48.9201 | 33.2542 | 1.4711 | 0.977%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 299 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 110.6943 | 89.5313 | 1.2364 | 110.6943 | 89.5313 | 1.2364 | 129.4029 | 104.6631 | 1.2364 | 0.968%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 12.6728 | 1.4972 | 8.4644 | 12.6728 | 1.4972 | 8.4644 | 14.8146 | 1.7502 | 8.4644 | 0.8924%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 11 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 20.1239 | 3.2938 | 6.1096 | 20.1239 | 3.2938 | 6.1096 | 23.5251 | 3.8505 | 6.1096 | 0.7823%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 1 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.37697 | 0.29944 | 1.2589 | 0.37697 | 0.29944 | 1.2589 | 0.44068 | 0.35004 | 1.2589 | 0.9121%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 357 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 97.543 | 106.8986 | 0.91248 | 97.543 | 106.8986 | 0.91248 | 114.0289 | 124.9656 | 0.91248 | 0.9429%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 5 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 16.79 | 1.4972 | 11.2144 | 16.79 | 1.4972 | 11.2144 | 19.6277 | 1.7502 | 11.2144 | 0.9974%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 208 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 36.4306 | 62.2826 | 0.58492 | 36.4306 | 62.2826 | 0.58492 | 42.5878 | 72.8091 | 0.58492 | 0.9922%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 4 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 5.6436 | 1.1977 | 4.7119 | 5.6436 | 1.1977 | 4.7119 | 6.5975 | 1.4002 | 4.7119 | 0.9914%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 26 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.8195 | 7.7853 | 0.23371 | 1.8195 | 7.7853 | 0.23371 | 2.127 | 9.1011 | 0.23371 | 0.6623%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 87 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.042 | 26.0509 | 0.11677 | 3.042 | 26.0509 | 0.11677 | 3.5561 | 30.4538 | 0.11677 | 0.7437%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 254 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 13.757 | 76.0567 | 0.18088 | 13.757 | 76.0567 | 0.18088 | 16.082 | 88.9111 | 0.18088 | 0.9193%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 14 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.055376 | 4.1921 | 0.01321 | 0.055376 | 4.1921 | 0.01321 | 0.064736 | 4.9006 | 0.01321 | 0.9638%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 21 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.0699 | 6.2882 | 1.2833 | 8.0699 | 6.2882 | 1.2833 | 9.4338 | 7.3509 | 1.2833 | 0.9553%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 38 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.1027 | 11.3786 | 0.36056 | 4.1027 | 11.3786 | 0.36056 | 4.7961 | 13.3017 | 0.36056 | 0.9636%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 35 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 11.079 | 10.4803 | 1.0571 | 11.079 | 10.4803 | 1.0571 | 12.9514 | 12.2515 | 1.0571 | 0.9978%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 180 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 25.774 | 53.8984 | 0.47819 | 25.774 | 53.8984 | 0.47819 | 30.13 | 63.0079 | 0.47819 | 0.9975%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 515 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 73.2722 | 154.2094 | 0.47515 | 73.2722 | 154.2094 | 0.47515 | 85.656 | 180.2725 | 0.47515 | 0.9974%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 55 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 3.8961 | 16.469 | 0.23657 | 3.8961 | 16.469 | 0.23657 | 4.5546 | 19.2524 | 0.23657 | 0.901%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 44 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 7.7241 | 13.1752 | 0.58627 | 7.7241 | 13.1752 | 0.58627 | 9.0296 | 15.4019 | 0.58627 | 0.8573%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 67 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.0436 | 20.0622 | 0.052018 | 1.0436 | 20.0622 | 0.052018 | 1.22 | 23.4529 | 0.052018 | 0.7047%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 15 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.402 | 4.4915 | 0.31214 | 1.402 | 4.4915 | 0.31214 | 1.6389 | 5.2507 | 0.31214 | 0.5082%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 70 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.3188 | 20.9605 | 0.44459 | 9.3188 | 20.9605 | 0.44459 | 10.8938 | 24.5031 | 0.44459 | 0.8949%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 129 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.2361 | 38.6272 | 0.34266 | 13.2361 | 38.6272 | 0.34266 | 15.4732 | 45.1556 | 0.34266 | 0.8426%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 264 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 14.9453 | 79.051 | 0.18906 | 14.9453 | 79.051 | 0.18906 | 17.4712 | 92.4116 | 0.18906 | 0.9106%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 63 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 14.4047 | 18.8645 | 0.76359 | 14.4047 | 18.8645 | 0.76359 | 16.8392 | 22.0528 | 0.76359 | 0.9543%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 51 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 12.9466 | 15.2712 | 0.84778 | 12.9466 | 15.2712 | 0.84778 | 15.1347 | 17.8522 | 0.84778 | 0.9497%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 5 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.2439 | 1.4972 | 3.5025 | 5.2439 | 1.4972 | 3.5025 | 6.1302 | 1.7502 | 3.5025 | 0.9907%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 291 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 42.0693 | 87.1358 | 0.4828 | 42.0693 | 87.1358 | 0.4828 | 49.1795 | 101.8627 | 0.4828 | 0.9915%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 1 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 10.7606 | 0.29944 | 35.9363 | 10.7606 | 0.29944 | 35.9363 | 12.5793 | 0.35004 | 35.9363 | 0.9792%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 68 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.3773 | 20.3616 | 0.41143 | 8.3773 | 20.3616 | 0.41143 | 9.7932 | 23.803 | 0.41143 | 0.9662%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 10 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.2025 | 2.9944 | 0.73556 | 2.2025 | 2.9944 | 0.73556 | 2.5748 | 3.5004 | 0.73556 | 0.9706%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 50 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 12.5177 | 14.9718 | 0.83609 | 12.5177 | 14.9718 | 0.83609 | 14.6334 | 17.5022 | 0.83609 | 0.9727%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 81 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 22.9349 | 24.2543 | 0.9456 | 22.9349 | 24.2543 | 0.9456 | 26.8111 | 28.3535 | 0.9456 | 0.9578%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 8.7577 | 5.6893 | 1.5393 | 8.7577 | 5.6893 | 1.5393 | 10.2379 | 6.6508 | 1.5393 | 0.9712%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 7 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.89078 | 2.0961 | 0.42498 | 0.89078 | 2.0961 | 0.42498 | 1.0413 | 2.4503 | 0.42498 | 0.9778%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 42 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 18.5404 | 12.5763 | 1.4742 | 18.5404 | 12.5763 | 1.4742 | 21.6739 | 14.7018 | 1.4742 | 0.9872%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 59 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 12.4912 | 17.6667 | 0.70705 | 12.4912 | 17.6667 | 0.70705 | 14.6024 | 20.6526 | 0.70705 | 0.9782%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 270 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 225.6415 | 80.8476 | 2.7909 | 225.6415 | 80.8476 | 2.7909 | 263.7775 | 94.5118 | 2.7909 | 0.9891%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 487 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 57.5299 | 145.8252 | 0.39451 | 57.5299 | 145.8252 | 0.39451 | 67.2531 | 170.4713 | 0.39451 | 0.9941%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 158 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.0925 | 47.3108 | 0.086503 | 4.0925 | 47.3108 | 0.086503 | 4.7842 | 55.3069 | 0.086503 | 0.974%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 69 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.3996 | 20.6611 | 0.16454 | 3.3996 | 20.6611 | 0.16454 | 3.9741 | 24.153 | 0.16454 | 0.9786%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 105 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.3988 | 31.4408 | 0.13991 | 4.3988 | 31.4408 | 0.13991 | 5.1422 | 36.7546 | 0.13991 | 0.9871%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 154 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 18.9959 | 46.1131 | 0.41194 | 18.9959 | 46.1131 | 0.41194 | 22.2065 | 53.9067 | 0.41194 | 0.9909%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 534 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 12.8069 | 159.8987 | 0.080094 | 12.8069 | 159.8987 | 0.080094 | 14.9714 | 186.9234 | 0.080094 | 0.8569%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 96 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 192.5809 | 28.7458 | 6.6994 | 192.5809 | 28.7458 | 6.6994 | 225.1293 | 33.6042 | 6.6994 | 0.9924%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 169 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 108.2961 | 50.6046 | 2.14 | 108.2961 | 50.6046 | 2.14 | 126.5994 | 59.1574 | 2.14 | 0.9821%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 153 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 167.486 | 45.8137 | 3.6558 | 167.486 | 45.8137 | 3.6558 | 195.793 | 53.5567 | 3.6558 | 0.99%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 46 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.027 | 13.774 | 0.87316 | 12.027 | 13.774 | 0.87316 | 14.0597 | 16.102 | 0.87316 | 0.9809%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 150 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 46.6667 | 44.9154 | 1.039 | 46.6667 | 44.9154 | 1.039 | 54.5539 | 52.5066 | 1.039 | 0.9892%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 111 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 120.8944 | 33.2374 | 3.6373 | 120.8944 | 33.2374 | 3.6373 | 141.3269 | 38.8549 | 3.6373 | 0.9919%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 6 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.61815 | 1.7966 | 0.34407 | 0.61815 | 1.7966 | 0.34407 | 0.72263 | 2.1003 | 0.34407 | 0.999%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 502 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 15.5959 | 150.3167 | 0.10375 | 15.5959 | 150.3167 | 0.10375 | 18.2318 | 175.722 | 0.10375 | 0.8922%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 383 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 20.8004 | 114.6839 | 0.18137 | 20.8004 | 114.6839 | 0.18137 | 24.3159 | 134.0668 | 0.18137 | 0.8785%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 367 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 91.5481 | 109.8929 | 0.83307 | 91.5481 | 109.8929 | 0.83307 | 107.0208 | 128.4661 | 0.83307 | 0.9868%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 406 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 30.0512 | 121.5709 | 0.24719 | 30.0512 | 121.5709 | 0.24719 | 35.1302 | 142.1178 | 0.24719 | 0.9466%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 493 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.3491 | 147.6218 | 0.076879 | 11.3491 | 147.6218 | 0.076879 | 13.2672 | 172.5716 | 0.076879 | 0.9088%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 69 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 86.9871 | 20.6611 | 4.2102 | 86.9871 | 20.6611 | 4.2102 | 101.6889 | 24.153 | 4.2102 | 0.9905%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 57 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 18.3868 | 17.0678 | 1.0773 | 18.3868 | 17.0678 | 1.0773 | 21.4944 | 19.9525 | 1.0773 | 0.9634%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 218 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.0917 | 65.277 | 0.21588 | 14.0917 | 65.277 | 0.21588 | 16.4734 | 76.3095 | 0.21588 | 0.8429%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 620 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 27.8169 | 185.6502 | 0.14984 | 27.8169 | 185.6502 | 0.14984 | 32.5183 | 217.0271 | 0.14984 | 0.8937%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 32.0105 | 5.0904 | 6.2884 | 32.0105 | 5.0904 | 6.2884 | 37.4207 | 5.9507 | 6.2884 | 0.9991%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 227 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 26.1629 | 67.9719 | 0.38491 | 26.1629 | 67.9719 | 0.38491 | 30.5847 | 79.4599 | 0.38491 | 0.9216%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 357 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 22.8253 | 106.8986 | 0.21352 | 22.8253 | 106.8986 | 0.21352 | 26.6831 | 124.9656 | 0.21352 | 0.9611%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.1327 | 0.89831 | 6.827 | 6.1327 | 0.89831 | 6.827 | 7.1692 | 1.0501 | 6.827 | 0.9946%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 384 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 33.1406 | 114.9833 | 0.28822 | 33.1406 | 114.9833 | 0.28822 | 38.7417 | 134.4168 | 0.28822 | 0.9703%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 29 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.92221 | 8.6836 | 0.1062 | 0.92221 | 8.6836 | 0.1062 | 1.0781 | 10.1513 | 0.1062 | 0.334%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 30 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 17.7549 | 8.9831 | 1.9765 | 17.7549 | 8.9831 | 1.9765 | 20.7557 | 10.5013 | 1.9765 | 0.9951%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 27 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.2941 | 8.0848 | 0.65483 | 5.2941 | 8.0848 | 0.65483 | 6.1889 | 9.4512 | 0.65483 | 0.9868%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 56 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 38.6908 | 16.7684 | 2.3074 | 38.6908 | 16.7684 | 2.3074 | 45.23 | 19.6025 | 2.3074 | 0.9945%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 34 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 19.5428 | 10.1808 | 1.9196 | 19.5428 | 10.1808 | 1.9196 | 22.8458 | 11.9015 | 1.9196 | 0.9686%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 17 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 83.1497 | 5.0904 | 16.3346 | 83.1497 | 5.0904 | 16.3346 | 97.203 | 5.9507 | 16.3346 | 0.9959%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 120 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.2286 | 35.9323 | 0.31249 | 11.2286 | 35.9323 | 0.31249 | 13.1263 | 42.0053 | 0.31249 | 0.9515%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 822 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 62.1241 | 246.1362 | 0.2524 | 62.1241 | 246.1362 | 0.2524 | 72.6237 | 287.736 | 0.2524 | 0.9662%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 245 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 682.3181 | 73.3618 | 9.3007 | 682.3181 | 73.3618 | 9.3007 | 797.6376 | 85.7607 | 9.3007 | 0.9925%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 31.189 | 2.6949 | 11.5733 | 31.189 | 2.6949 | 11.5733 | 36.4603 | 3.1504 | 11.5733 | 0.9927%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 107 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 390.1034 | 32.0396 | 12.1757 | 390.1034 | 32.0396 | 12.1757 | 456.0353 | 37.4547 | 12.1757 | 0.9963%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.1697 | 0.59887 | 3.623 | 2.1697 | 0.59887 | 3.623 | 2.5364 | 0.70009 | 3.623 | 0.8656%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 511 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 61.9237 | 153.0117 | 0.4047 | 61.9237 | 153.0117 | 0.4047 | 72.3895 | 178.8724 | 0.4047 | 0.9605%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 14 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 42.123 | 4.1921 | 10.0482 | 42.123 | 4.1921 | 10.0482 | 49.2423 | 4.9006 | 10.0482 | 0.9985%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 600 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 140.7833 | 179.6614 | 0.7836 | 140.7833 | 179.6614 | 0.7836 | 164.5773 | 210.0263 | 0.7836 | 0.967%
2028 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 3 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.14826 | 0.89831 | 0.16504 | 0.14826 | 0.89831 | 0.16504 | 0.17332 | 1.0501 | 0.16504 | 0.9833%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 349 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 16.4943 | 104.5031 | 0.15784 | 16.4943 | 104.5031 | 0.15784 | 19.282 | 122.1653 | 0.15784 | 0.9498%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 470 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 54.4945 | 140.7348 | 0.38721 | 54.4945 | 140.7348 | 0.38721 | 63.7047 | 164.5206 | 0.38721 | 0.9826%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 585 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 16.3862 | 175.1699 | 0.093544 | 16.3862 | 175.1699 | 0.093544 | 19.1556 | 204.7756 | 0.093544 | 0.9106%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 226 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.6769 | 67.6725 | 0.054334 | 3.6769 | 67.6725 | 0.054334 | 4.2983 | 79.1099 | 0.054334 | 0.7897%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 6.7227 | 20.9605 | 0.32073 | 6.7227 | 20.9605 | 0.32073 | 7.8589 | 24.5031 | 0.32073 | 0.9819%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 328 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 29.4513 | 98.2149 | 0.29987 | 29.4513 | 98.2149 | 0.29987 | 34.429 | 114.8144 | 0.29987 | 0.9768%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 3 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 0.98148 | 0.89831 | 1.0926 | 0.98148 | 0.89831 | 1.0926 | 1.1474 | 1.0501 | 1.0926 | 0.9298%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 32 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.3883 | 9.5819 | 0.14489 | 1.3883 | 9.5819 | 0.14489 | 1.623 | 11.2014 | 0.14489 | 0.8171%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 364 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 23.3036 | 108.9946 | 0.2138 | 23.3036 | 108.9946 | 0.2138 | 27.2421 | 127.4159 | 0.2138 | 0.983%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 1452 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 44.0479 | 434.7807 | 0.10131 | 44.0479 | 434.7807 | 0.10131 | 51.4925 | 508.2636 | 0.10131 | 0.9868%
2028 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 4 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.0004488 | 1.1977 | 0.00037471 | 0.0004488 | 1.1977 | 0.00037471 | 0.00052465 | 1.4002 | 0.00037471 | 0.004523%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 743 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 26.0468 | 222.4807 | 0.11707 | 26.0468 | 222.4807 | 0.11707 | 30.449 | 260.0825 | 0.11707 | 0.9884%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 182 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.0897 | 54.4973 | 0.11174 | 6.0897 | 54.4973 | 0.11174 | 7.1189 | 63.708 | 0.11174 | 0.9757%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 279 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.691 | 83.5426 | 0.044181 | 3.691 | 83.5426 | 0.044181 | 4.3148 | 97.6622 | 0.044181 | 0.9496%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 309 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 17.4616 | 92.5256 | 0.18872 | 17.4616 | 92.5256 | 0.18872 | 20.4128 | 108.1635 | 0.18872 | 0.859%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 875 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 42.644 | 262.0063 | 0.16276 | 42.644 | 262.0063 | 0.16276 | 49.8514 | 306.2883 | 0.16276 | 0.9946%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 106 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 33.6588 | 31.7402 | 1.0604 | 33.6588 | 31.7402 | 1.0604 | 39.3475 | 37.1046 | 1.0604 | 0.8863%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 399 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 202.1881 | 119.4749 | 1.6923 | 202.1881 | 119.4749 | 1.6923 | 236.3602 | 139.6675 | 1.6923 | 0.9837%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 390 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 83.2984 | 116.7799 | 0.71329 | 83.2984 | 116.7799 | 0.71329 | 97.3768 | 136.5171 | 0.71329 | 0.9873%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 104 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 23.8394 | 31.1413 | 0.76552 | 23.8394 | 31.1413 | 0.76552 | 27.8686 | 36.4046 | 0.76552 | 0.9726%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 19 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 19.3507 | 5.6893 | 3.4013 | 19.3507 | 5.6893 | 3.4013 | 22.6212 | 6.6508 | 3.4013 | 0.9861%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 249 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 45.394 | 74.5595 | 0.60883 | 45.394 | 74.5595 | 0.60883 | 53.0661 | 87.1609 | 0.60883 | 0.9807%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 365 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 181.2145 | 109.294 | 1.658 | 181.2145 | 109.294 | 1.658 | 211.8418 | 127.766 | 1.658 | 0.9836%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 129 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 58.842 | 38.6272 | 1.5233 | 58.842 | 38.6272 | 1.5233 | 68.7869 | 45.1556 | 1.5233 | 0.9784%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 48 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 31.3562 | 14.3729 | 2.1816 | 31.3562 | 14.3729 | 2.1816 | 36.6558 | 16.8021 | 2.1816 | 0.994%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 135 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 243.6142 | 40.4238 | 6.0265 | 243.6142 | 40.4238 | 6.0265 | 284.7877 | 47.2559 | 6.0265 | 0.9934%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 345 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 232.4738 | 103.3053 | 2.2504 | 232.4738 | 103.3053 | 2.2504 | 271.7645 | 120.7651 | 2.2504 | 0.9889%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 37 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.081 | 11.0791 | 0.36835 | 4.081 | 11.0791 | 0.36835 | 4.7707 | 12.9516 | 0.36835 | 0.7089%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 23 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 21.7062 | 6.887 | 3.1518 | 21.7062 | 6.887 | 3.1518 | 25.3748 | 8.051 | 3.1518 | 0.9883%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 479 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 265.7992 | 143.4297 | 1.8532 | 265.7992 | 143.4297 | 1.8532 | 310.7223 | 167.671 | 1.8532 | 0.9911%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 422 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 562.6422 | 126.3619 | 4.4526 | 562.6422 | 126.3619 | 4.4526 | 657.7351 | 147.7185 | 4.4526 | 0.9893%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 399 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.3249 | 119.4749 | 0.061309 | 7.3249 | 119.4749 | 0.061309 | 8.5629 | 139.6675 | 0.061309 | 0.9808%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 13.5774 | 16.469 | 0.82442 | 13.5774 | 16.469 | 0.82442 | 15.8721 | 19.2524 | 0.82442 | 0.9867%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.3484 | 69.7685 | 0.13399 | 9.3484 | 69.7685 | 0.13399 | 10.9284 | 81.5602 | 0.13399 | 0.9646%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 327 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 53.4582 | 97.9155 | 0.54596 | 53.4582 | 97.9155 | 0.54596 | 62.4933 | 114.4643 | 0.54596 | 0.9824%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 303 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.1911 | 90.729 | 0.068237 | 6.1911 | 90.729 | 0.068237 | 7.2374 | 106.0633 | 0.068237 | 0.6927%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 31 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.227 | 9.2825 | 0.34764 | 3.227 | 9.2825 | 0.34764 | 3.7724 | 10.8514 | 0.34764 | 0.9876%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 123 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.0908 | 36.8306 | 0.27398 | 10.0908 | 36.8306 | 0.27398 | 11.7962 | 43.0554 | 0.27398 | 0.9838%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 24 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 6.7803 | 7.1865 | 0.94349 | 6.7803 | 7.1865 | 0.94349 | 7.9263 | 8.4011 | 0.94349 | 0.987%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 21 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.1681 | 6.2882 | 0.50381 | 3.1681 | 6.2882 | 0.50381 | 3.7035 | 7.3509 | 0.50381 | 0.9688%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 485 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 37.7167 | 145.2263 | 0.25971 | 37.7167 | 145.2263 | 0.25971 | 44.0912 | 169.7712 | 0.25971 | 0.9791%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 263 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 32.1844 | 78.7516 | 0.40868 | 32.1844 | 78.7516 | 0.40868 | 37.624 | 92.0615 | 0.40868 | 0.9907%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 164 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 30.8081 | 49.1075 | 0.62736 | 30.8081 | 49.1075 | 0.62736 | 36.015 | 57.4072 | 0.62736 | 0.9682%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 101 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.4986 | 30.243 | 0.18182 | 5.4986 | 30.243 | 0.18182 | 6.428 | 35.3544 | 0.18182 | 0.6596%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 389 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 27.7975 | 116.4805 | 0.23865 | 27.7975 | 116.4805 | 0.23865 | 32.4956 | 136.167 | 0.23865 | 0.9454%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 74 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 10.9245 | 22.1582 | 0.49302 | 10.9245 | 22.1582 | 0.49302 | 12.7709 | 25.9032 | 0.49302 | 0.9251%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 6 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.89663 | 1.7966 | 0.49907 | 0.89663 | 1.7966 | 0.49907 | 1.0482 | 2.1003 | 0.49907 | 0.9818%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 299 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 31.2287 | 89.5313 | 0.3488 | 31.2287 | 89.5313 | 0.3488 | 36.5068 | 104.6631 | 0.3488 | 0.9585%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 47 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 45.3392 | 14.0735 | 3.2216 | 45.3392 | 14.0735 | 3.2216 | 53.0021 | 16.4521 | 3.2216 | 0.9855%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 101 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 15.347 | 30.243 | 0.50745 | 15.347 | 30.243 | 0.50745 | 17.9408 | 35.3544 | 0.50745 | 0.878%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 3.9401 | 0.29944 | 13.1583 | 3.9401 | 0.29944 | 13.1583 | 4.606 | 0.35004 | 13.1583 | 0.9431%
2028 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 2 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.35645 | 0.59887 | 0.5952 | 0.35645 | 0.59887 | 0.5952 | 0.41669 | 0.70009 | 0.5952 | 0.9823%
2028 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 215 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.4395 | 64.3787 | 0.068958 | 4.4395 | 64.3787 | 0.068958 | 5.1898 | 75.2594 | 0.068958 | 0.9288%
2028 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 22 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.022142 | 6.5876 | 0.0033611 | 0.022142 | 6.5876 | 0.0033611 | 0.025884 | 7.701 | 0.0033611 | 0.7897%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 2 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 3.9618 | 0.59887 | 6.6155 | 3.9618 | 0.59887 | 6.6155 | 4.6314 | 0.70009 | 6.6155 | 0.9948%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 169 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.0495 | 50.6046 | 0.11955 | 6.0495 | 50.6046 | 0.11955 | 7.072 | 59.1574 | 0.11955 | 0.9241%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 110 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.0305 | 32.9379 | 0.57777 | 19.0305 | 32.9379 | 0.57777 | 22.2468 | 38.5048 | 0.57777 | 0.9107%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 294 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 39.503 | 88.0341 | 0.44872 | 39.503 | 88.0341 | 0.44872 | 46.1795 | 102.9129 | 0.44872 | 0.9555%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 5 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16066 | 1.4972 | 0.10731 | 0.16066 | 1.4972 | 0.10731 | 0.18781 | 1.7502 | 0.10731 | 0.1937%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 13 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.066898 | 3.8927 | 0.017186 | 0.066898 | 3.8927 | 0.017186 | 0.078204 | 4.5506 | 0.017186 | 0.4938%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 201 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.032458 | 60.1866 | 0.00053928 | 0.032458 | 60.1866 | 0.00053928 | 0.037943 | 70.3588 | 0.00053928 | 0.02339%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 10 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0026556 | 2.9944 | 0.00088687 | 0.0026556 | 2.9944 | 0.00088687 | 0.0031044 | 3.5004 | 0.00088687 | 0.001514%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 149 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.8126 | 44.6159 | 0.040627 | 1.8126 | 44.6159 | 0.040627 | 2.119 | 52.1565 | 0.040627 | 0.995%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 2 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.6061 | 0.59887 | 4.3517 | 2.6061 | 0.59887 | 4.3517 | 3.0466 | 0.70009 | 4.3517 | 0.9927%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 975 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 29.856 | 291.9498 | 0.10226 | 29.856 | 291.9498 | 0.10226 | 34.902 | 341.2927 | 0.10226 | 0.9548%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 827 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 118.1718 | 247.6333 | 0.4772 | 118.1718 | 247.6333 | 0.4772 | 138.1442 | 289.4862 | 0.4772 | 0.9814%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 961 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 46.9005 | 287.7577 | 0.16299 | 46.9005 | 287.7577 | 0.16299 | 54.8272 | 336.3921 | 0.16299 | 0.9699%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 397 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 116.5375 | 118.876 | 0.98033 | 116.5375 | 118.876 | 0.98033 | 136.2336 | 138.9674 | 0.98033 | 0.9928%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 538 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 96.1417 | 161.0964 | 0.5968 | 96.1417 | 161.0964 | 0.5968 | 112.3908 | 188.3236 | 0.5968 | 0.9888%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 546 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 202.6155 | 163.4919 | 1.2393 | 202.6155 | 163.4919 | 1.2393 | 236.8598 | 191.1239 | 1.2393 | 0.9925%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 92 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 79.1645 | 27.5481 | 2.8737 | 79.1645 | 27.5481 | 2.8737 | 92.5442 | 32.204 | 2.8737 | 0.9973%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 488 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 160.5499 | 146.1246 | 1.0987 | 160.5499 | 146.1246 | 1.0987 | 187.6847 | 170.8214 | 1.0987 | 0.9936%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 319 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 78.0402 | 95.52 | 0.817 | 78.0402 | 95.52 | 0.817 | 91.2299 | 111.664 | 0.817 | 0.9749%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 106 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 21.6881 | 31.7402 | 0.6833 | 21.6881 | 31.7402 | 0.6833 | 25.3536 | 37.1046 | 0.6833 | 0.9918%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 24 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 19.2203 | 7.1865 | 2.6745 | 19.2203 | 7.1865 | 2.6745 | 22.4687 | 8.4011 | 2.6745 | 0.9993%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 55 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 15.3319 | 16.469 | 0.93096 | 15.3319 | 16.469 | 0.93096 | 17.9232 | 19.2524 | 0.93096 | 0.8869%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 46 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 37.2925 | 13.774 | 2.7074 | 37.2925 | 13.774 | 2.7074 | 43.5954 | 16.102 | 2.7074 | 0.943%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 13 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.5371 | 3.8927 | 0.65176 | 2.5371 | 3.8927 | 0.65176 | 2.9659 | 4.5506 | 0.65176 | 0.6284%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 139 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 116.8208 | 41.6216 | 2.8067 | 116.8208 | 41.6216 | 2.8067 | 136.5648 | 48.6561 | 2.8067 | 0.9943%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 465 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 176.5588 | 139.2376 | 1.268 | 176.5588 | 139.2376 | 1.268 | 206.3992 | 162.7704 | 1.268 | 0.9917%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 102 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 28.0801 | 30.5424 | 0.91938 | 28.0801 | 30.5424 | 0.91938 | 32.826 | 35.7045 | 0.91938 | 0.8854%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 276 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 64.1338 | 82.6443 | 0.77602 | 64.1338 | 82.6443 | 0.77602 | 74.9732 | 96.6121 | 0.77602 | 0.985%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 139 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 11.7877 | 41.6216 | 0.28321 | 11.7877 | 41.6216 | 0.28321 | 13.78 | 48.6561 | 0.28321 | 0.7994%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 131 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 46.3232 | 39.2261 | 1.1809 | 46.3232 | 39.2261 | 1.1809 | 54.1523 | 45.8557 | 1.1809 | 0.9814%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 704 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 135.8918 | 210.8028 | 0.64464 | 135.8918 | 210.8028 | 0.64464 | 158.859 | 246.4308 | 0.64464 | 0.9776%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 561 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 76.9818 | 167.9834 | 0.45827 | 76.9818 | 167.9834 | 0.45827 | 89.9926 | 196.3746 | 0.45827 | 0.9541%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 14 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 10.7592 | 4.1921 | 2.5665 | 10.7592 | 4.1921 | 2.5665 | 12.5776 | 4.9006 | 2.5665 | 0.9906%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 7 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 44.119 | 2.0961 | 21.0487 | 44.119 | 2.0961 | 21.0487 | 51.5757 | 2.4503 | 21.0487 | 0.9968%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 1 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.2852 | 0.29944 | 24.3299 | 7.2852 | 0.29944 | 24.3299 | 8.5165 | 0.35004 | 24.3299 | 0.9549%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 194 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 144.6629 | 58.0905 | 2.4903 | 144.6629 | 58.0905 | 2.4903 | 169.1126 | 67.9085 | 2.4903 | 0.9879%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 329 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 149.7393 | 98.5144 | 1.52 | 149.7393 | 98.5144 | 1.52 | 175.0469 | 115.1644 | 1.52 | 0.9747%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 435 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 87.8785 | 130.2545 | 0.67467 | 87.8785 | 130.2545 | 0.67467 | 102.731 | 152.269 | 0.67467 | 0.9704%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 248 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 99.8244 | 74.2601 | 1.3443 | 99.8244 | 74.2601 | 1.3443 | 116.6959 | 86.8109 | 1.3443 | 0.9781%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.0594 | 3.2938 | 1.536 | 5.0594 | 3.2938 | 1.536 | 5.9144 | 3.8505 | 1.536 | 0.9721%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 36 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 11.6327 | 10.7797 | 1.0791 | 11.6327 | 10.7797 | 1.0791 | 13.5988 | 12.6016 | 1.0791 | 0.9966%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 252 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 321.8183 | 75.4578 | 4.2649 | 321.8183 | 75.4578 | 4.2649 | 376.2093 | 88.211 | 4.2649 | 0.9859%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 14 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.2433 | 4.1921 | 2.682 | 11.2433 | 4.1921 | 2.682 | 13.1435 | 4.9006 | 2.682 | 0.8901%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 22 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5082 | 6.5876 | 0.22895 | 1.5082 | 6.5876 | 0.22895 | 1.7631 | 7.701 | 0.22895 | 0.1879%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 590 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 24.0122 | 176.6671 | 0.13592 | 24.0122 | 176.6671 | 0.13592 | 28.0706 | 206.5258 | 0.13592 | 0.8818%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 455 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 15.7753 | 136.2433 | 0.11579 | 15.7753 | 136.2433 | 0.11579 | 18.4415 | 159.2699 | 0.11579 | 0.9783%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 839 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 54.4478 | 251.2266 | 0.21673 | 54.4478 | 251.2266 | 0.21673 | 63.6501 | 293.6867 | 0.21673 | 0.9847%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 3 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.2505 | 0.89831 | 12.5241 | 11.2505 | 0.89831 | 12.5241 | 13.1519 | 1.0501 | 12.5241 | 0.9597%
2028 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.61043 | 0.29944 | 2.0386 | 0.61043 | 0.29944 | 2.0386 | 0.7136 | 0.35004 | 2.0386 | 0.9953%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 91 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 29.7608 | 27.2487 | 1.0922 | 29.7608 | 27.2487 | 1.0922 | 34.7907 | 31.854 | 1.0922 | 0.9745%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.6157 | 0.89831 | 5.1382 | 4.6157 | 0.89831 | 5.1382 | 5.3958 | 1.0501 | 5.1382 | 0.9134%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 68 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 40.4105 | 20.3616 | 1.9846 | 40.4105 | 20.3616 | 1.9846 | 47.2404 | 23.803 | 1.9846 | 0.98%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 20 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 45.7689 | 5.9887 | 7.6425 | 45.7689 | 5.9887 | 7.6425 | 53.5043 | 7.0009 | 7.6425 | 0.9857%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 358 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 15.3052 | 107.198 | 0.14277 | 15.3052 | 107.198 | 0.14277 | 17.8919 | 125.3157 | 0.14277 | 0.9609%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 28 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.01335 | 8.3842 | 0.0015923 | 0.01335 | 8.3842 | 0.0015923 | 0.015607 | 9.8012 | 0.0015923 | 0.01745%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 37 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.2878 | 11.0791 | 0.56753 | 6.2878 | 11.0791 | 0.56753 | 7.3505 | 12.9516 | 0.56753 | 0.8492%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 17 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.6468 | 5.0904 | 0.51995 | 2.6468 | 5.0904 | 0.51995 | 3.0941 | 5.9507 | 0.51995 | 0.5795%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 558 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 88.8783 | 167.0851 | 0.53193 | 88.8783 | 167.0851 | 0.53193 | 103.8998 | 195.3244 | 0.53193 | 0.8848%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 9 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.7229 | 2.6949 | 1.7525 | 4.7229 | 2.6949 | 1.7525 | 5.5211 | 3.1504 | 1.7525 | 0.9893%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 29 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.7629 | 8.6836 | 0.43333 | 3.7629 | 8.6836 | 0.43333 | 4.3989 | 10.1513 | 0.43333 | 0.9131%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 7 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.62594 | 2.0961 | 0.29863 | 0.62594 | 2.0961 | 0.29863 | 0.73173 | 2.4503 | 0.29863 | 0.51%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 16 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 28.9437 | 4.791 | 6.0413 | 28.9437 | 4.791 | 6.0413 | 33.8355 | 5.6007 | 6.0413 | 0.9767%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 219 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.5062 | 65.5764 | 0.053468 | 3.5062 | 65.5764 | 0.053468 | 4.0988 | 76.6596 | 0.053468 | 0.7071%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 202 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 79.4005 | 60.486 | 1.3127 | 79.4005 | 60.486 | 1.3127 | 92.8201 | 70.7088 | 1.3127 | 0.9496%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 55 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 60.4896 | 16.469 | 3.6729 | 60.4896 | 16.469 | 3.6729 | 70.713 | 19.2524 | 3.6729 | 0.9611%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 33 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.3499 | 9.8814 | 1.2498 | 12.3499 | 9.8814 | 1.2498 | 14.4371 | 11.5514 | 1.2498 | 0.8872%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 211 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 88.2116 | 63.1809 | 1.3962 | 88.2116 | 63.1809 | 1.3962 | 103.1203 | 73.8592 | 1.3962 | 0.9569%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 16 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 12.9938 | 4.791 | 2.7121 | 12.9938 | 4.791 | 2.7121 | 15.1899 | 5.6007 | 2.7121 | 0.8473%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 52 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 27.954 | 15.5707 | 1.7953 | 27.954 | 15.5707 | 1.7953 | 32.6785 | 18.2023 | 1.7953 | 0.8754%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 29 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 33.8185 | 8.6836 | 3.8945 | 33.8185 | 8.6836 | 3.8945 | 39.5342 | 10.1513 | 3.8945 | 0.8812%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 2 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.4107 | 0.59887 | 19.0537 | 11.4107 | 0.59887 | 19.0537 | 13.3393 | 0.70009 | 19.0537 | 0.9724%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 1 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.2431 | 0.29944 | 34.2081 | 10.2431 | 0.29944 | 34.2081 | 11.9743 | 0.35004 | 34.2081 | 0.9739%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 56 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 20.8414 | 16.7684 | 1.2429 | 20.8414 | 16.7684 | 1.2429 | 24.3638 | 19.6025 | 1.2429 | 0.9191%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 60 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.2489 | 17.9661 | 0.57046 | 10.2489 | 17.9661 | 0.57046 | 11.9811 | 21.0026 | 0.57046 | 0.557%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 73 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.4431 | 21.8588 | 0.15752 | 3.4431 | 21.8588 | 0.15752 | 4.0251 | 25.5532 | 0.15752 | 0.7618%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 79 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.3323 | 23.6554 | 0.18314 | 4.3323 | 23.6554 | 0.18314 | 5.0645 | 27.6535 | 0.18314 | 0.7912%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 243 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 72.4591 | 72.7629 | 0.99583 | 72.4591 | 72.7629 | 0.99583 | 84.7056 | 85.0606 | 0.99583 | 0.9168%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 119 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 45.779 | 35.6329 | 1.2847 | 45.779 | 35.6329 | 1.2847 | 53.5162 | 41.6552 | 1.2847 | 0.9343%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 495 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 52.8654 | 148.2207 | 0.35667 | 52.8654 | 148.2207 | 0.35667 | 61.8002 | 173.2717 | 0.35667 | 0.9049%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 12.5889 | 4.1921 | 3.003 | 12.5889 | 4.1921 | 3.003 | 14.7166 | 4.9006 | 3.003 | 0.9697%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 10 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.2488 | 2.9944 | 1.7529 | 5.2488 | 2.9944 | 1.7529 | 6.1359 | 3.5004 | 1.7529 | 0.967%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 61 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 45.1059 | 18.2656 | 2.4694 | 45.1059 | 18.2656 | 2.4694 | 52.7293 | 21.3527 | 2.4694 | 0.9877%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 125 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 19.2425 | 37.4295 | 0.5141 | 19.2425 | 37.4295 | 0.5141 | 22.4947 | 43.7555 | 0.5141 | 0.9555%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.5014 | 14.6724 | 0.17048 | 2.5014 | 14.6724 | 0.17048 | 2.9241 | 17.1521 | 0.17048 | 0.9711%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 257 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 71.2723 | 76.955 | 0.92616 | 71.2723 | 76.955 | 0.92616 | 83.3182 | 89.9613 | 0.92616 | 0.9923%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 62 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.3795 | 18.565 | 0.34363 | 6.3795 | 18.565 | 0.34363 | 7.4577 | 21.7027 | 0.34363 | 0.9277%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 61 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.3622 | 18.2656 | 0.51256 | 9.3622 | 18.2656 | 0.51256 | 10.9446 | 21.3527 | 0.51256 | 0.9525%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 27 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.19 | 8.0848 | 0.14719 | 1.19 | 8.0848 | 0.14719 | 1.3911 | 9.4512 | 0.14719 | 0.999%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.5706 | 1.1977 | 1.3113 | 1.5706 | 1.1977 | 1.3113 | 1.836 | 1.4002 | 1.3113 | 0.9984%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 175 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 24.4958 | 52.4013 | 0.46747 | 24.4958 | 52.4013 | 0.46747 | 28.6359 | 61.2577 | 0.46747 | 0.9993%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 14 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.32939 | 4.1921 | 0.078574 | 0.32939 | 4.1921 | 0.078574 | 0.38506 | 4.9006 | 0.078574 | 0.9723%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 287 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 29.7816 | 85.9381 | 0.34655 | 29.7816 | 85.9381 | 0.34655 | 34.815 | 100.4626 | 0.34655 | 0.997%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 15 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 11.8471 | 4.4915 | 2.6377 | 11.8471 | 4.4915 | 2.6377 | 13.8494 | 5.2507 | 2.6377 | 0.9902%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 213 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 44.9395 | 63.7798 | 0.7046 | 44.9395 | 63.7798 | 0.7046 | 52.5347 | 74.5593 | 0.7046 | 0.9833%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 471 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 144.4024 | 141.0342 | 1.0239 | 144.4024 | 141.0342 | 1.0239 | 168.8081 | 164.8706 | 1.0239 | 0.9937%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 15 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 35.0626 | 4.4915 | 7.8064 | 35.0626 | 4.4915 | 7.8064 | 40.9886 | 5.2507 | 7.8064 | 0.9496%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 90 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.7651 | 26.9492 | 0.065496 | 1.7651 | 26.9492 | 0.065496 | 2.0634 | 31.5039 | 0.065496 | 0.9963%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 31 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.3375 | 9.2825 | 0.68274 | 6.3375 | 9.2825 | 0.68274 | 7.4087 | 10.8514 | 0.68274 | 0.9951%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 779 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 25.1714 | 233.2604 | 0.10791 | 25.1714 | 233.2604 | 0.10791 | 29.4257 | 272.6841 | 0.10791 | 0.9734%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 148 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 12.5764 | 44.3165 | 0.28379 | 12.5764 | 44.3165 | 0.28379 | 14.702 | 51.8065 | 0.28379 | 0.9797%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 400 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 22.1562 | 119.7743 | 0.18498 | 22.1562 | 119.7743 | 0.18498 | 25.9009 | 140.0175 | 0.18498 | 0.9676%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 745 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 27.4777 | 223.0796 | 0.12317 | 27.4777 | 223.0796 | 0.12317 | 32.1217 | 260.7826 | 0.12317 | 0.9272%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 290 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 13.9309 | 86.8364 | 0.16043 | 13.9309 | 86.8364 | 0.16043 | 16.2854 | 101.5127 | 0.16043 | 0.9829%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 504 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 56.7803 | 150.9156 | 0.37624 | 56.7803 | 150.9156 | 0.37624 | 66.3768 | 176.4221 | 0.37624 | 0.9672%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 258 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.0238 | 77.2544 | 0.06503 | 5.0238 | 77.2544 | 0.06503 | 5.8729 | 90.3113 | 0.06503 | 0.7734%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 221 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 17.4587 | 66.1753 | 0.26382 | 17.4587 | 66.1753 | 0.26382 | 20.4094 | 77.3597 | 0.26382 | 0.9648%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 63 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.6754 | 18.8645 | 0.088814 | 1.6754 | 18.8645 | 0.088814 | 1.9586 | 22.0528 | 0.088814 | 0.7472%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 657 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 41.8632 | 196.7293 | 0.2128 | 41.8632 | 196.7293 | 0.2128 | 48.9386 | 229.9788 | 0.2128 | 0.9649%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 231 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 17.3179 | 69.1697 | 0.25037 | 17.3179 | 69.1697 | 0.25037 | 20.2448 | 80.8601 | 0.25037 | 0.9757%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 427 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 95.2678 | 127.8591 | 0.7451 | 95.2678 | 127.8591 | 0.7451 | 111.3691 | 149.4687 | 0.7451 | 0.9669%
2028 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 152 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.2877 | 45.5142 | 0.13815 | 6.2877 | 45.5142 | 0.13815 | 7.3504 | 53.2067 | 0.13815 | 0.8931%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 356 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 71.9681 | 106.5991 | 0.67513 | 71.9681 | 106.5991 | 0.67513 | 84.1316 | 124.6156 | 0.67513 | 0.9779%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 268 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 75.1519 | 80.2488 | 0.93649 | 75.1519 | 80.2488 | 0.93649 | 87.8535 | 93.8117 | 0.93649 | 0.9936%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 378 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 48.1778 | 113.1867 | 0.42565 | 48.1778 | 113.1867 | 0.42565 | 56.3204 | 132.3165 | 0.42565 | 0.9878%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 262 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 105.606 | 78.4522 | 1.3461 | 105.606 | 78.4522 | 1.3461 | 123.4547 | 91.7115 | 1.3461 | 0.9938%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 549 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 77.4933 | 164.3902 | 0.4714 | 77.4933 | 164.3902 | 0.4714 | 90.5906 | 192.174 | 0.4714 | 0.9905%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 29 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.42096 | 8.6836 | 0.048477 | 0.42096 | 8.6836 | 0.048477 | 0.4921 | 10.1513 | 0.048477 | 0.4302%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 39 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.22878 | 11.678 | 0.01959 | 0.22878 | 11.678 | 0.01959 | 0.26744 | 13.6517 | 0.01959 | 0.2253%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 897 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 47.2153 | 268.5938 | 0.17579 | 47.2153 | 268.5938 | 0.17579 | 55.1952 | 313.9893 | 0.17579 | 0.9644%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 111 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.30988 | 33.2374 | 0.0093232 | 0.30988 | 33.2374 | 0.0093232 | 0.36225 | 38.8549 | 0.0093232 | 0.117%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 119 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 47.3605 | 35.6329 | 1.3291 | 47.3605 | 35.6329 | 1.3291 | 55.365 | 41.6552 | 1.3291 | 0.9978%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 253 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 98.0181 | 75.7572 | 1.2938 | 98.0181 | 75.7572 | 1.2938 | 114.5843 | 88.5611 | 1.2938 | 0.9977%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 241 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 117.8145 | 72.164 | 1.6326 | 117.8145 | 72.164 | 1.6326 | 137.7264 | 84.3606 | 1.6326 | 0.9899%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 136 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 75.0312 | 40.7233 | 1.8425 | 75.0312 | 40.7233 | 1.8425 | 87.7123 | 47.606 | 1.8425 | 0.982%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 592 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 347.0961 | 177.266 | 1.9581 | 347.0961 | 177.266 | 1.9581 | 405.7593 | 207.2259 | 1.9581 | 0.9903%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 30 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 4.9027 | 8.9831 | 0.54578 | 4.9027 | 8.9831 | 0.54578 | 5.7314 | 10.5013 | 0.54578 | 0.6775%
2028 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 1 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.3255 | 0.29944 | 4.4266 | 1.3255 | 0.29944 | 4.4266 | 1.5495 | 0.35004 | 4.4266 | 0.9944%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 4 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.3477 | 1.1977 | 3.6299 | 4.3477 | 1.1977 | 3.6299 | 5.0825 | 1.4002 | 3.6299 | 0.9632%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.42655 | 4.791 | 0.089032 | 0.42655 | 4.791 | 0.089032 | 0.49864 | 5.6007 | 0.089032 | 0.9941%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 685 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 155.7203 | 205.1135 | 0.75919 | 155.7203 | 205.1135 | 0.75919 | 182.0388 | 239.78 | 0.75919 | 0.9555%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 899 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 222.1206 | 269.1927 | 0.82514 | 222.1206 | 269.1927 | 0.82514 | 259.6615 | 314.6894 | 0.82514 | 0.994%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 188 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 21.2119 | 56.2939 | 0.37681 | 21.2119 | 56.2939 | 0.37681 | 24.797 | 65.8082 | 0.37681 | 0.936%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 406 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 34.0376 | 121.5709 | 0.27998 | 34.0376 | 121.5709 | 0.27998 | 39.7903 | 142.1178 | 0.27998 | 0.938%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 88 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.7095 | 26.3503 | 0.17872 | 4.7095 | 26.3503 | 0.17872 | 5.5054 | 30.8039 | 0.17872 | 0.8718%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 132 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.1122 | 39.5255 | 0.33174 | 13.1122 | 39.5255 | 0.33174 | 15.3283 | 46.2058 | 0.33174 | 0.9279%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 54 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 52.3744 | 16.1695 | 3.2391 | 52.3744 | 16.1695 | 3.2391 | 61.2263 | 18.9024 | 3.2391 | 0.9729%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 293 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 131.2209 | 87.7347 | 1.4957 | 131.2209 | 87.7347 | 1.4957 | 153.3987 | 102.5628 | 1.4957 | 0.9856%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 134 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 20.9682 | 40.1244 | 0.52258 | 20.9682 | 40.1244 | 0.52258 | 24.5121 | 46.9059 | 0.52258 | 0.9864%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 32 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 48.9805 | 9.5819 | 5.1118 | 48.9805 | 9.5819 | 5.1118 | 57.2588 | 11.2014 | 5.1118 | 0.9841%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 150 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 90.3866 | 44.9154 | 2.0124 | 90.3866 | 44.9154 | 2.0124 | 105.663 | 52.5066 | 2.0124 | 0.9831%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 119 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 79.3589 | 35.6329 | 2.2271 | 79.3589 | 35.6329 | 2.2271 | 92.7715 | 41.6552 | 2.2271 | 0.9843%
2028 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.15347 | 0.59887 | 0.25626 | 0.15347 | 0.59887 | 0.25626 | 0.1794 | 0.70009 | 0.25626 | 0.9934%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 157 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 27.1554 | 47.0114 | 0.57763 | 27.1554 | 47.0114 | 0.57763 | 31.745 | 54.9569 | 0.57763 | 0.9977%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 53 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 14.7668 | 15.8701 | 0.93048 | 14.7668 | 15.8701 | 0.93048 | 17.2626 | 18.5523 | 0.93048 | 0.9957%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 25 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 16.7956 | 7.4859 | 2.2436 | 16.7956 | 7.4859 | 2.2436 | 19.6343 | 8.7511 | 2.2436 | 0.9986%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 300 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.0458 | 89.8307 | 0.21202 | 19.0458 | 89.8307 | 0.21202 | 22.2647 | 105.0131 | 0.21202 | 0.9923%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 133 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 124.2819 | 39.825 | 3.1207 | 124.2819 | 39.825 | 3.1207 | 145.2869 | 46.5558 | 3.1207 | 0.9856%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 9 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 62.2159 | 2.6949 | 23.0864 | 62.2159 | 2.6949 | 23.0864 | 72.7311 | 3.1504 | 23.0864 | 0.9951%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 236 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 74.781 | 70.6668 | 1.0582 | 74.781 | 70.6668 | 1.0582 | 87.4199 | 82.6103 | 1.0582 | 0.9433%
2028 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 3 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 2.8019 | 0.89831 | 3.1191 | 2.8019 | 0.89831 | 3.1191 | 3.2755 | 1.0501 | 3.1191 | 0.9958%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 43 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 26.9206 | 12.8757 | 2.0908 | 26.9206 | 12.8757 | 2.0908 | 31.4705 | 15.0519 | 2.0908 | 0.9258%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 109 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 106.1678 | 32.6385 | 3.2528 | 106.1678 | 32.6385 | 3.2528 | 124.1113 | 38.1548 | 3.2528 | 0.9926%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 129 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 17.6579 | 38.6272 | 0.45714 | 17.6579 | 38.6272 | 0.45714 | 20.6423 | 45.1556 | 0.45714 | 0.9747%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 99 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 9.8935 | 29.6441 | 0.33374 | 9.8935 | 29.6441 | 0.33374 | 11.5656 | 34.6543 | 0.33374 | 0.7093%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 62 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 82.8796 | 18.565 | 4.4643 | 82.8796 | 18.565 | 4.4643 | 96.8872 | 21.7027 | 4.4643 | 0.9829%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 47 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 158.3796 | 14.0735 | 11.2538 | 158.3796 | 14.0735 | 11.2538 | 185.1476 | 16.4521 | 11.2538 | 0.989%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 9 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 22.1244 | 2.6949 | 8.2097 | 22.1244 | 2.6949 | 8.2097 | 25.8637 | 3.1504 | 8.2097 | 0.9937%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 103 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 46.29 | 30.8419 | 1.5009 | 46.29 | 30.8419 | 1.5009 | 54.1136 | 36.0545 | 1.5009 | 0.9631%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 226 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 158.374 | 67.6725 | 2.3403 | 158.374 | 67.6725 | 2.3403 | 185.1411 | 79.1099 | 2.3403 | 0.9714%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 5 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 25.5856 | 1.4972 | 17.0892 | 25.5856 | 1.4972 | 17.0892 | 29.9099 | 1.7502 | 17.0892 | 0.9712%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 210 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 172.0911 | 62.8815 | 2.7368 | 172.0911 | 62.8815 | 2.7368 | 201.1764 | 73.5092 | 2.7368 | 0.9923%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 6 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.098 | 1.7966 | 0.61118 | 1.098 | 1.7966 | 0.61118 | 1.2836 | 2.1003 | 0.61118 | 0.9928%
2028 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 27 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.1065 | 8.0848 | 0.013173 | 0.1065 | 8.0848 | 0.013173 | 0.1245 | 9.4512 | 0.013173 | 0.9883%
2028 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 20 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.2104 | 5.9887 | 0.20211 | 1.2104 | 5.9887 | 0.20211 | 1.415 | 7.0009 | 0.20211 | 0.9963%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 7 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.057723 | 2.0961 | 0.027539 | 0.057723 | 2.0961 | 0.027539 | 0.067479 | 2.4503 | 0.027539 | 0.9902%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 4 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.8502 | 1.1977 | 2.3796 | 2.8502 | 1.1977 | 2.3796 | 3.3319 | 1.4002 | 2.3796 | 0.9939%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 95 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 1.9514 | 28.4464 | 0.068598 | 1.9514 | 28.4464 | 0.068598 | 2.2812 | 33.2542 | 0.068598 | 0.9666%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 381 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 74.6087 | 114.085 | 0.65397 | 74.6087 | 114.085 | 0.65397 | 87.2184 | 133.3667 | 0.65397 | 0.9986%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 124 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 71.5161 | 37.13 | 1.9261 | 71.5161 | 37.13 | 1.9261 | 83.6031 | 43.4054 | 1.9261 | 0.9762%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.2032 | 0.29944 | 7.3579 | 2.2032 | 0.29944 | 7.3579 | 2.5756 | 0.35004 | 7.3579 | 0.9867%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 115 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 78.7826 | 34.4351 | 2.2879 | 78.7826 | 34.4351 | 2.2879 | 92.0977 | 40.255 | 2.2879 | 0.9973%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 618 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 233.0596 | 185.0513 | 1.2594 | 233.0596 | 185.0513 | 1.2594 | 272.4494 | 216.3271 | 1.2594 | 0.9919%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 53 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 55.0956 | 15.8701 | 3.4717 | 55.0956 | 15.8701 | 3.4717 | 64.4074 | 18.5523 | 3.4717 | 0.9998%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 451 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 134.5725 | 135.0455 | 0.9965 | 134.5725 | 135.0455 | 0.9965 | 157.3168 | 157.8697 | 0.9965 | 0.9833%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 350 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 100.8952 | 104.8025 | 0.96272 | 100.8952 | 104.8025 | 0.96272 | 117.9476 | 122.5153 | 0.96272 | 0.988%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 479 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 46.544 | 143.4297 | 0.32451 | 46.544 | 143.4297 | 0.32451 | 54.4105 | 167.671 | 0.32451 | 0.9625%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 302 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 11.6853 | 90.4296 | 0.12922 | 11.6853 | 90.4296 | 0.12922 | 13.6602 | 105.7132 | 0.12922 | 0.9181%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 118 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 67.9586 | 35.3334 | 1.9234 | 67.9586 | 35.3334 | 1.9234 | 79.4443 | 41.3052 | 1.9234 | 0.9835%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 313 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 354.179 | 93.7234 | 3.779 | 354.179 | 93.7234 | 3.779 | 414.0392 | 109.5637 | 3.779 | 0.9889%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 226 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 29.0956 | 67.6725 | 0.42995 | 29.0956 | 67.6725 | 0.42995 | 34.0131 | 79.1099 | 0.42995 | 0.9191%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 273 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 194.0772 | 81.746 | 2.3742 | 194.0772 | 81.746 | 2.3742 | 226.8785 | 95.562 | 2.3742 | 0.9908%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 2 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3119 | 0.59887 | 2.1906 | 1.3119 | 0.59887 | 2.1906 | 1.5336 | 0.70009 | 2.1906 | 0.9858%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 71 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.1012 | 21.2599 | 0.33402 | 7.1012 | 21.2599 | 0.33402 | 8.3014 | 24.8531 | 0.33402 | 0.9652%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 434 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 476.1404 | 129.9551 | 3.6639 | 476.1404 | 129.9551 | 3.6639 | 556.6136 | 151.919 | 3.6639 | 0.9927%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 1 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 49.4897 | 0.29944 | 165.2766 | 49.4897 | 0.29944 | 165.2766 | 57.8541 | 0.35004 | 165.2766 | 0.9997%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 458 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 278.4341 | 137.1416 | 2.0303 | 278.4341 | 137.1416 | 2.0303 | 325.4926 | 160.32 | 2.0303 | 0.9926%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 136 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 10.7977 | 40.7233 | 0.26515 | 10.7977 | 40.7233 | 0.26515 | 12.6227 | 47.606 | 0.26515 | 0.9598%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 74 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 29.3766 | 22.1582 | 1.3258 | 29.3766 | 22.1582 | 1.3258 | 34.3416 | 25.9032 | 1.3258 | 0.9934%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 41 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.3128 | 12.2769 | 0.75856 | 9.3128 | 12.2769 | 0.75856 | 10.8867 | 14.3518 | 0.75856 | 0.6902%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 93 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.2447 | 27.8475 | 0.47562 | 13.2447 | 27.8475 | 0.47562 | 15.4832 | 32.5541 | 0.47562 | 0.7661%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.7551 | 0.59887 | 6.2702 | 3.7551 | 0.59887 | 6.2702 | 4.3897 | 0.70009 | 6.2702 | 0.9947%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 34 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 112.1303 | 10.1808 | 11.0139 | 112.1303 | 10.1808 | 11.0139 | 131.0816 | 11.9015 | 11.0139 | 0.9966%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 309 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 130.2558 | 92.5256 | 1.4078 | 130.2558 | 92.5256 | 1.4078 | 152.2705 | 108.1635 | 1.4078 | 0.9905%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 657 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 244.5755 | 196.7293 | 1.2432 | 244.5755 | 196.7293 | 1.2432 | 285.9116 | 229.9788 | 1.2432 | 0.9891%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 75 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 69.2066 | 22.4577 | 3.0816 | 69.2066 | 22.4577 | 3.0816 | 80.9033 | 26.2533 | 3.0816 | 0.9946%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 25 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 37.5911 | 7.4859 | 5.0216 | 37.5911 | 7.4859 | 5.0216 | 43.9444 | 8.7511 | 5.0216 | 0.9952%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 123 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 126.2079 | 36.8306 | 3.4267 | 126.2079 | 36.8306 | 3.4267 | 147.5385 | 43.0554 | 3.4267 | 0.9843%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 319 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 96.8131 | 95.52 | 1.0135 | 96.8131 | 95.52 | 1.0135 | 113.1756 | 111.664 | 1.0135 | 0.9898%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 88 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 68.5917 | 26.3503 | 2.6031 | 68.5917 | 26.3503 | 2.6031 | 80.1845 | 30.8039 | 2.6031 | 0.9853%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 704 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 199.9405 | 210.8028 | 0.94847 | 199.9405 | 210.8028 | 0.94847 | 233.7327 | 246.4308 | 0.94847 | 0.9839%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 407 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 193.8953 | 121.8703 | 1.591 | 193.8953 | 121.8703 | 1.591 | 226.6658 | 142.4678 | 1.591 | 0.9748%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 137 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 78.7234 | 41.0227 | 1.919 | 78.7234 | 41.0227 | 1.919 | 92.0286 | 47.956 | 1.919 | 0.9912%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 80 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 43.7441 | 23.9549 | 1.8261 | 43.7441 | 23.9549 | 1.8261 | 51.1373 | 28.0035 | 1.8261 | 0.9732%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 48 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 74.4785 | 14.3729 | 5.1819 | 74.4785 | 14.3729 | 5.1819 | 87.0662 | 16.8021 | 5.1819 | 0.9953%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 42 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 55.4979 | 12.5763 | 4.4129 | 55.4979 | 12.5763 | 4.4129 | 64.8777 | 14.7018 | 4.4129 | 0.9803%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 138 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 28.408 | 41.3221 | 0.68748 | 28.408 | 41.3221 | 0.68748 | 33.2093 | 48.306 | 0.68748 | 0.9369%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 12 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 61.4159 | 3.5932 | 17.0921 | 61.4159 | 3.5932 | 17.0921 | 71.7958 | 4.2005 | 17.0921 | 0.9955%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 5 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 44.7288 | 1.4972 | 29.8754 | 44.7288 | 1.4972 | 29.8754 | 52.2885 | 1.7502 | 29.8754 | 0.803%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 17 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.5843 | 5.0904 | 0.70413 | 3.5843 | 5.0904 | 0.70413 | 4.1901 | 5.9507 | 0.70413 | 0.6587%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 107 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 39.6418 | 32.0396 | 1.2373 | 39.6418 | 32.0396 | 1.2373 | 46.3417 | 37.4547 | 1.2373 | 0.9978%
2028 | CB 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 82 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 28.8759 | 24.5537 | 1.176 | 28.8759 | 24.5537 | 1.176 | 33.7562 | 28.7036 | 1.176 | 0.9981%
2028 | CB 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 19 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.2323 | 5.6893 | 2.1501 | 12.2323 | 5.6893 | 2.1501 | 14.2997 | 6.6508 | 2.1501 | 0.9962%
2028 | CB 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 3 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 9.81 | 0.89831 | 10.9206 | 9.81 | 0.89831 | 10.9206 | 11.4681 | 1.0501 | 10.9206 | 0.9972%
2028 | CB 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 56 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 4.9377 | 16.7684 | 0.29446 | 4.9377 | 16.7684 | 0.29446 | 5.7722 | 19.6025 | 0.29446 | 0.3454%
2028 | CB 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 80 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 4.9835 | 23.9549 | 0.20804 | 4.9835 | 23.9549 | 0.20804 | 5.8257 | 28.0035 | 0.20804 | 0.75%
2028 | CB 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 571 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 46.1797 | 170.9778 | 0.27009 | 46.1797 | 170.9778 | 0.27009 | 53.9845 | 199.875 | 0.27009 | 0.8429%
2028 | CB 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 1192 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 57.164 | 356.9274 | 0.16016 | 57.164 | 356.9274 | 0.16016 | 66.8254 | 417.2522 | 0.16016 | 0.9909%
2028 | CB 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 132 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 12.4546 | 39.5255 | 0.3151 | 12.4546 | 39.5255 | 0.3151 | 14.5596 | 46.2058 | 0.3151 | 0.9975%
2028 | CB 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.93603 | 1.1977 | 0.7815 | 0.93603 | 1.1977 | 0.7815 | 1.0942 | 1.4002 | 0.7815 | 0.9975%
2028 | CB 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 38 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 35.3525 | 11.3786 | 3.1069 | 35.3525 | 11.3786 | 3.1069 | 41.3275 | 13.3017 | 3.1069 | 0.9993%
2028 | CB 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 3 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.34116 | 0.89831 | 0.37978 | 0.34116 | 0.89831 | 0.37978 | 0.39882 | 1.0501 | 0.37978 | 0.9408%
2028 | CB 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 1 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.8001 | 0.29944 | 2.672 | 0.8001 | 0.29944 | 2.672 | 0.93533 | 0.35004 | 2.672 | 0.3549%
2028 | CB 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 1 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 2.7537 | 0.29944 | 9.1963 | 2.7537 | 0.29944 | 9.1963 | 3.2191 | 0.35004 | 9.1963 | 0.7993%
2028 | CB 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 58 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.4844 | 17.3673 | 0.20063 | 3.4844 | 17.3673 | 0.20063 | 4.0733 | 20.3025 | 0.20063 | 0.299%
2028 | CB 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 22 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.1064 | 6.5876 | 0.16795 | 1.1064 | 6.5876 | 0.16795 | 1.2933 | 7.701 | 0.16795 | 0.9512%
2028 | CB 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 248 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.16285 | 74.2601 | 0.0021929 | 0.16285 | 74.2601 | 0.0021929 | 0.19037 | 86.8109 | 0.0021929 | 0.09583%
2028 | CB 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 89 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.4336 | 26.6498 | 0.27894 | 7.4336 | 26.6498 | 0.27894 | 8.6899 | 31.1539 | 0.27894 | 0.8082%
2028 | CB 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 36 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.844 | 10.7797 | 0.17107 | 1.844 | 10.7797 | 0.17107 | 2.1557 | 12.6016 | 0.17107 | 0.9981%
2028 | CB 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 209 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 21.5465 | 62.5821 | 0.34429 | 21.5465 | 62.5821 | 0.34429 | 25.1881 | 73.1591 | 0.34429 | 0.9929%
2028 | CB 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 277 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 13.8844 | 82.9437 | 0.1674 | 13.8844 | 82.9437 | 0.1674 | 16.231 | 96.9621 | 0.1674 | 0.9737%
2028 | CB 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 730 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 35.3788 | 218.5881 | 0.16185 | 35.3788 | 218.5881 | 0.16185 | 41.3582 | 255.532 | 0.16185 | 0.9874%
2028 | CB 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 485 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 28.2802 | 145.2263 | 0.19473 | 28.2802 | 145.2263 | 0.19473 | 33.0599 | 169.7712 | 0.19473 | 0.9888%
2028 | CB 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 236 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 107.7148 | 70.6668 | 1.5243 | 107.7148 | 70.6668 | 1.5243 | 125.9198 | 82.6103 | 1.5243 | 0.9762%
2028 | CB 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 2 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 18.2459 | 0.59887 | 30.4671 | 18.2459 | 0.59887 | 30.4671 | 21.3297 | 0.70009 | 30.4671 | 0.9954%
2028 | CB 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 134 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 10.7092 | 40.1244 | 0.2669 | 10.7092 | 40.1244 | 0.2669 | 12.5192 | 46.9059 | 0.2669 | 0.9768%
2028 | CB 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 18 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.273 | 5.3898 | 0.42171 | 2.273 | 5.3898 | 0.42171 | 2.6571 | 6.3008 | 0.42171 | 0.6436%
2028 | CB 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 10 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 0.96218 | 2.9944 | 0.32133 | 0.96218 | 2.9944 | 0.32133 | 1.1248 | 3.5004 | 0.32133 | 0.375%
2028 | CB 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 167 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.2383 | 50.0058 | 0.22474 | 11.2383 | 50.0058 | 0.22474 | 13.1378 | 58.4573 | 0.22474 | 0.9%
2028 | CB 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 45 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.3167 | 13.4746 | 0.17193 | 2.3167 | 13.4746 | 0.17193 | 2.7083 | 15.752 | 0.17193 | 0.7028%
2028 | CB 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 46 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.3104 | 13.774 | 0.60334 | 8.3104 | 13.774 | 0.60334 | 9.715 | 16.102 | 0.60334 | 0.995%
2028 | CB 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 79 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 6.9657 | 23.6554 | 0.29447 | 6.9657 | 23.6554 | 0.29447 | 8.143 | 27.6535 | 0.29447 | 0.9704%
2028 | CB 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 82 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.54626 | 24.5537 | 0.022247 | 0.54626 | 24.5537 | 0.022247 | 0.63858 | 28.7036 | 0.022247 | 0.6647%
2028 | CB 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.090938 | 3.8927 | 0.023361 | 0.090938 | 3.8927 | 0.023361 | 0.10631 | 4.5506 | 0.023361 | 0.9726%
2028 | CB 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 12.619 | 0.29944 | 42.1425 | 12.619 | 0.29944 | 42.1425 | 14.7517 | 0.35004 | 42.1425 | 0.9979%
2028 | CB 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.8095 | 4.1921 | 0.43166 | 1.8095 | 4.1921 | 0.43166 | 2.1154 | 4.9006 | 0.43166 | 0.9683%
2028 | CB 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 96 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.35975 | 28.7458 | 0.012515 | 0.35975 | 28.7458 | 0.012515 | 0.42055 | 33.6042 | 0.012515 | 0.3335%
2028 | CB 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 211 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 126.3066 | 63.1809 | 1.9991 | 126.3066 | 63.1809 | 1.9991 | 147.6539 | 73.8592 | 1.9991 | 0.9966%
2028 | CB 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 22 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.75687 | 6.5876 | 0.11489 | 0.75687 | 6.5876 | 0.11489 | 0.88479 | 7.701 | 0.11489 | 0.9922%
2028 | CB 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.064962 | 0.29944 | 0.21695 | 0.064962 | 0.29944 | 0.21695 | 0.075942 | 0.35004 | 0.21695 | 0.986%
2028 | CB 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 376 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 96.8504 | 112.5878 | 0.86022 | 96.8504 | 112.5878 | 0.86022 | 113.2192 | 131.6165 | 0.86022 | 0.9884%
2028 | CB 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.05855 | 0.29944 | 0.19554 | 0.05855 | 0.29944 | 0.19554 | 0.068446 | 0.35004 | 0.19554 | 0.991%
2028 | CB 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 184 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 50.9281 | 55.0962 | 0.92435 | 50.9281 | 55.0962 | 0.92435 | 59.5355 | 64.4081 | 0.92435 | 0.9601%
2028 | CB 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4116 | 4.1921 | 0.33673 | 1.4116 | 4.1921 | 0.33673 | 1.6502 | 4.9006 | 0.33673 | 0.1888%
2028 | CB 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 2 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.83395 | 0.59887 | 1.3925 | 0.83395 | 0.59887 | 1.3925 | 0.97489 | 0.70009 | 1.3925 | 0.1434%
2028 | CB 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 40 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.2532 | 11.9774 | 0.77255 | 9.2532 | 11.9774 | 0.77255 | 10.8171 | 14.0018 | 0.77255 | 0.9408%
2028 | CB 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 56 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 57.3752 | 16.7684 | 3.4216 | 57.3752 | 16.7684 | 3.4216 | 67.0723 | 19.6025 | 3.4216 | 0.9549%
2028 | CB 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.15954 | 0.89831 | 0.1776 | 0.15954 | 0.89831 | 0.1776 | 0.1865 | 1.0501 | 0.1776 | 0.9464%
2028 | CB 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 1 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.015009 | 0.29944 | 0.050124 | 0.015009 | 0.29944 | 0.050124 | 0.017546 | 0.35004 | 0.050124 | 0.9786%
2028 | CB 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 11 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.017906 | 3.2938 | 0.0054362 | 0.017906 | 3.2938 | 0.0054362 | 0.020932 | 3.8505 | 0.0054362 | 0.1679%
2028 | CB 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 277 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 8.3461 | 82.9437 | 0.10062 | 8.3461 | 82.9437 | 0.10062 | 9.7567 | 96.9621 | 0.10062 | 0.8949%
2028 | CB 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 87 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 0.98668 | 26.0509 | 0.037875 | 0.98668 | 26.0509 | 0.037875 | 1.1534 | 30.4538 | 0.037875 | 0.372%
2028 | CB 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 12 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 3.938 | 3.5932 | 1.096 | 3.938 | 3.5932 | 1.096 | 4.6036 | 4.2005 | 1.096 | 0.9425%
2028 | CB 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 8 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.35788 | 2.3955 | 0.1494 | 0.35788 | 2.3955 | 0.1494 | 0.41837 | 2.8004 | 0.1494 | 0.7619%
2028 | CB 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 56 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.57931 | 16.7684 | 0.034548 | 0.57931 | 16.7684 | 0.034548 | 0.67722 | 19.6025 | 0.034548 | 0.9924%
2028 | CB 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 45 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 7.8674 | 13.4746 | 0.58387 | 7.8674 | 13.4746 | 0.58387 | 9.1971 | 15.752 | 0.58387 | 0.9545%
2028 | CB 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 20 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.8415 | 5.9887 | 0.47448 | 2.8415 | 5.9887 | 0.47448 | 3.3218 | 7.0009 | 0.47448 | 0.7837%
2028 | CB 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 375 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 37.4572 | 112.2884 | 0.33358 | 37.4572 | 112.2884 | 0.33358 | 43.7878 | 131.2664 | 0.33358 | 0.9981%
2028 | CB 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 47 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.44294 | 14.0735 | 0.031473 | 0.44294 | 14.0735 | 0.031473 | 0.5178 | 16.4521 | 0.031473 | 0.9266%
2028 | CB 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 23 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 70.7198 | 6.887 | 10.2686 | 70.7198 | 6.887 | 10.2686 | 82.6722 | 8.051 | 10.2686 | 0.9507%
2028 | CB 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 104 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.36808 | 31.1413 | 0.01182 | 0.36808 | 31.1413 | 0.01182 | 0.43029 | 36.4046 | 0.01182 | 0.9943%
2028 | CB 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 26 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 23.7653 | 7.7853 | 3.0526 | 23.7653 | 7.7853 | 3.0526 | 27.7819 | 9.1011 | 3.0526 | 0.9983%
2028 | CB 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 89 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.739 | 26.6498 | 0.10278 | 2.739 | 26.6498 | 0.10278 | 3.2019 | 31.1539 | 0.10278 | 0.9343%
2028 | CB 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 2 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.1782 | 0.59887 | 3.6371 | 2.1782 | 0.59887 | 3.6371 | 2.5463 | 0.70009 | 3.6371 | 0.9997%
2028 | CB 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 34 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 98.9626 | 10.1808 | 9.7205 | 98.9626 | 10.1808 | 9.7205 | 115.6885 | 11.9015 | 9.7205 | 0.9951%
2028 | CB 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 36 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.2677 | 10.7797 | 1.0453 | 11.2677 | 10.7797 | 1.0453 | 13.172 | 12.6016 | 1.0453 | 0.9951%
2028 | CB 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 341 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.3565 | 102.1076 | 0.032873 | 3.3565 | 102.1076 | 0.032873 | 3.9238 | 119.3649 | 0.032873 | 0.997%
2028 | CB 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 23 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.1483 | 6.887 | 0.16674 | 1.1483 | 6.887 | 0.16674 | 1.3424 | 8.051 | 0.16674 | 0.9965%
2028 | CB CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.21519 | 0.59887 | 0.35932 | 0.21519 | 0.59887 | 0.35932 | 0.25156 | 0.70009 | 0.35932 | 0.9021%
2028 | CB FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 161 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.111 | 48.2092 | 0.023046 | 1.111 | 48.2092 | 0.023046 | 1.2988 | 56.357 | 0.023046 | 0.3693%
2028 | CB FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 154 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 8.4306 | 46.1131 | 0.18282 | 8.4306 | 46.1131 | 0.18282 | 9.8554 | 53.9067 | 0.18282 | 0.9433%
2028 | CB JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 126 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.0101 | 37.7289 | 0.34483 | 13.0101 | 37.7289 | 0.34483 | 15.2089 | 44.1055 | 0.34483 | 0.9785%
2028 | CB MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 97 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 43.8007 | 29.0453 | 1.508 | 43.8007 | 29.0453 | 1.508 | 51.2036 | 33.9542 | 1.508 | 0.9856%
2028 | CB NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 10 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 5.4844 | 2.9944 | 1.8316 | 5.4844 | 2.9944 | 1.8316 | 6.4114 | 3.5004 | 1.8316 | 0.9902%
2028 | CB OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 593 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 59.4325 | 177.5654 | 0.33471 | 59.4325 | 177.5654 | 0.33471 | 69.4773 | 207.576 | 0.33471 | 0.99%
2028 | CB PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 510 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 24.8952 | 152.7122 | 0.16302 | 24.8952 | 152.7122 | 0.16302 | 29.1028 | 178.5223 | 0.16302 | 0.9473%
2028 | CB RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 214 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 89.7491 | 64.0792 | 1.4006 | 89.7491 | 64.0792 | 1.4006 | 104.9177 | 74.9094 | 1.4006 | 0.9831%
2028 | CB RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 170 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 44.5423 | 50.9041 | 0.87502 | 44.5423 | 50.9041 | 0.87502 | 52.0704 | 59.5074 | 0.87502 | 0.9811%
2028 | CB RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 44 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.5273 | 13.1752 | 0.41952 | 5.5273 | 13.1752 | 0.41952 | 6.4615 | 15.4019 | 0.41952 | 0.695%
2028 | CB RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.25797 | 0.89831 | 0.28717 | 0.25797 | 0.89831 | 0.28717 | 0.30156 | 1.0501 | 0.28717 | 0.9988%
2028 | CB RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 182 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 32.1846 | 54.4973 | 0.59057 | 32.1846 | 54.4973 | 0.59057 | 37.6241 | 63.708 | 0.59057 | 0.9914%
2028 | CB SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 316 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 27.3464 | 94.6217 | 0.28901 | 27.3464 | 94.6217 | 0.28901 | 31.9682 | 110.6138 | 0.28901 | 0.9371%
2028 | CB SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 22 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.016377 | 6.5876 | 0.0024861 | 0.016377 | 6.5876 | 0.0024861 | 0.019145 | 7.701 | 0.0024861 | 0.02003%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 375 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.1367 | 112.2884 | 0.1259 | 14.1367 | 112.2884 | 0.1259 | 16.5259 | 131.2664 | 0.1259 | 0.789%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 113 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 30.7262 | 33.8362 | 0.90808 | 30.7262 | 33.8362 | 0.90808 | 35.9193 | 39.5549 | 0.90808 | 0.9517%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 254 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 80.525 | 76.0567 | 1.0588 | 80.525 | 76.0567 | 1.0588 | 94.1347 | 88.9111 | 1.0588 | 0.9933%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 570 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 58.6141 | 170.6784 | 0.34342 | 58.6141 | 170.6784 | 0.34342 | 68.5205 | 199.525 | 0.34342 | 0.9757%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 73 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 51.2664 | 21.8588 | 2.3453 | 51.2664 | 21.8588 | 2.3453 | 59.931 | 25.5532 | 2.3453 | 0.9932%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 239 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 32.667 | 71.5651 | 0.45647 | 32.667 | 71.5651 | 0.45647 | 38.1881 | 83.6605 | 0.45647 | 0.9948%

## Off Cycle Patrol
Off Cycle Patrol - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 246834 | 2845627.9812 | 27705.3336 | 0.9736% | 26429.006 | 2007.6433 | 13.1642 | 26429.006 | 2007.6433 | 13.1642 | 27841.144 | 2114.9144 | 13.1642
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 246834 | 2845627.9812 | 27705.3336 | 0.9736% | 25211.4761 | 1915.1553 | 13.1642 | 25211.4761 | 1915.1553 | 13.1642 | 27977.6202 | 2125.2817 | 13.1642
[9 empty] | Capital Cost only in Year 0 | 0.0085264 | K$/inspection | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 246834 | 2845627.9812 | 27705.3336 | 0.9736% | 24050.0354 | 1826.9281 | 13.1642 | 24050.0354 | 1826.9281 | 13.1642 | 28114.7654 | 2135.6997 | 13.1642
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 740502 | 8536883.9436 | 83116.0007 | 0.9736% | 75690.5175 | 5749.7267 | 13.1642 | 75690.5175 | 5749.7267 | 13.1642 | 83933.5296 | 6375.8959 | 13.1642
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 1% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | %Trees in the Scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.1068 | 0.048801 | 22.6798 | 1.1068 | 0.048801 | 22.6798 | 1.1659 | 0.051409 | 22.6798 | 0.9903%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 86 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.869 | 0.69949 | 5.5312 | 3.869 | 0.69949 | 5.5312 | 4.0757 | 0.73686 | 5.5312 | 0.9915%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 1144 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 36.8178 | 9.3048 | 3.9569 | 36.8178 | 9.3048 | 3.9569 | 38.785 | 9.802 | 3.9569 | 0.9141%
2026 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 1.0899 | 0.032534 | 33.5007 | 1.0899 | 0.032534 | 33.5007 | 1.1482 | 0.034273 | 33.5007 | 0.9976%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 1369 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 332.0782 | 11.1349 | 29.8233 | 332.0782 | 11.1349 | 29.8233 | 349.8216 | 11.7298 | 29.8233 | 0.9902%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 234 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 66.0788 | 1.9033 | 34.7188 | 66.0788 | 1.9033 | 34.7188 | 69.6095 | 2.005 | 34.7188 | 0.9818%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 633 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 179.0433 | 5.1486 | 34.7755 | 179.0433 | 5.1486 | 34.7755 | 188.6098 | 5.4236 | 34.7755 | 0.997%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 269 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 47.787 | 2.1879 | 21.8412 | 47.787 | 2.1879 | 21.8412 | 50.3403 | 2.3048 | 21.8412 | 0.9951%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 53 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 13.1718 | 0.43108 | 30.5555 | 13.1718 | 0.43108 | 30.5555 | 13.8756 | 0.45411 | 30.5555 | 0.9958%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 7.5473 | 0.24401 | 30.9306 | 7.5473 | 0.24401 | 30.9306 | 7.9506 | 0.25704 | 30.9306 | 0.996%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 392 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 93.1374 | 3.1884 | 29.2117 | 93.1374 | 3.1884 | 29.2117 | 98.1139 | 3.3587 | 29.2117 | 0.9962%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 14 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.5753 | 0.11387 | 57.744 | 6.5753 | 0.11387 | 57.744 | 6.9266 | 0.11995 | 57.744 | 0.9922%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 221 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 47.9789 | 1.7975 | 26.6917 | 47.9789 | 1.7975 | 26.6917 | 50.5425 | 1.8936 | 26.6917 | 0.9916%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 209 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 27.3593 | 1.6999 | 16.0945 | 27.3593 | 1.6999 | 16.0945 | 28.8211 | 1.7907 | 16.0945 | 0.9924%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 1740 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 86.7029 | 14.1524 | 6.1264 | 86.7029 | 14.1524 | 6.1264 | 91.3356 | 14.9086 | 6.1264 | 0.9598%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 1132 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 35.0604 | 9.2072 | 3.8079 | 35.0604 | 9.2072 | 3.8079 | 36.9337 | 9.6992 | 3.8079 | 0.9739%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 220 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.8971 | 1.7894 | 2.7368 | 4.8971 | 1.7894 | 2.7368 | 5.1588 | 1.885 | 2.7368 | 0.8768%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 48.0307 | 0.85403 | 56.2403 | 48.0307 | 0.85403 | 56.2403 | 50.597 | 0.89966 | 56.2403 | 0.9826%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 269 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 111.1363 | 2.1879 | 50.7951 | 111.1363 | 2.1879 | 50.7951 | 117.0745 | 2.3048 | 50.7951 | 0.9858%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 107 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 20.4052 | 0.87029 | 23.4464 | 20.4052 | 0.87029 | 23.4464 | 21.4955 | 0.91679 | 23.4464 | 0.9945%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 209 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 62.3119 | 1.6999 | 36.6559 | 62.3119 | 1.6999 | 36.6559 | 65.6414 | 1.7907 | 36.6559 | 0.9866%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 1458 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 239.4495 | 11.8588 | 20.1918 | 239.4495 | 11.8588 | 20.1918 | 252.2436 | 12.4924 | 20.1918 | 0.9914%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 1503 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 266.8268 | 12.2248 | 21.8267 | 266.8268 | 12.2248 | 21.8267 | 281.0837 | 12.878 | 21.8267 | 0.9849%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 1232 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 252.5213 | 10.0206 | 25.2003 | 252.5213 | 10.0206 | 25.2003 | 266.0138 | 10.556 | 25.2003 | 0.9916%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 1991 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 148.3449 | 16.194 | 9.1605 | 148.3449 | 16.194 | 9.1605 | 156.2711 | 17.0592 | 9.1605 | 0.9745%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 43 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14883 | 0.34974 | 0.42555 | 0.14883 | 0.34974 | 0.42555 | 0.15678 | 0.36843 | 0.42555 | 0.8684%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.032939 | 0.20334 | 0.16199 | 0.032939 | 0.20334 | 0.16199 | 0.034699 | 0.2142 | 0.16199 | 0.1275%
2026 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.020949 | 0.032534 | 0.6439 | 0.020949 | 0.032534 | 0.6439 | 0.022068 | 0.034273 | 0.6439 | 0.3435%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 19 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.9161 | 0.15454 | 44.7533 | 6.9161 | 0.15454 | 44.7533 | 7.2856 | 0.1628 | 44.7533 | 0.9924%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 140 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 8.238 | 1.1387 | 7.2345 | 8.238 | 1.1387 | 7.2345 | 8.6781 | 1.1995 | 7.2345 | 0.9393%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 37 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1825 | 0.30094 | 3.9294 | 1.1825 | 0.30094 | 3.9294 | 1.2457 | 0.31702 | 3.9294 | 0.8802%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 600 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 56.0593 | 4.8801 | 11.4872 | 56.0593 | 4.8801 | 11.4872 | 59.0546 | 5.1409 | 11.4872 | 0.9962%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 661 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 47.4306 | 5.3763 | 8.8222 | 47.4306 | 5.3763 | 8.8222 | 49.9649 | 5.6636 | 8.8222 | 0.9962%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 315 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 23.945 | 2.5621 | 9.3459 | 23.945 | 2.5621 | 9.3459 | 25.2244 | 2.699 | 9.3459 | 0.9984%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 124 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.89815 | 1.0086 | 0.89053 | 0.89815 | 1.0086 | 0.89053 | 0.94614 | 1.0625 | 0.89053 | 0.9877%
2026 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 0.54035 | 0 | 0 | 0.54035 | 0 | 0.51545 | 0.0081336 | 63.3734 | 0.51545 | 0.0081336 | 63.3734 | 0.54299 | 0.0085682 | 63.3734 | 0.9875%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 22 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 20.3953 | 0.17894 | 113.9792 | 20.3953 | 0.17894 | 113.9792 | 21.485 | 0.1885 | 113.9792 | 0.9968%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 102 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 40.3024 | 0.82962 | 48.5791 | 40.3024 | 0.82962 | 48.5791 | 42.4558 | 0.87395 | 48.5791 | 0.9992%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 57 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.759 | 0.46361 | 8.1079 | 3.759 | 0.46361 | 8.1079 | 3.9598 | 0.48839 | 8.1079 | 0.945%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 53 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.4758 | 0.43108 | 17.3419 | 7.4758 | 0.43108 | 17.3419 | 7.8752 | 0.45411 | 17.3419 | 0.994%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 1839 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 40.5406 | 14.9576 | 2.7104 | 40.5406 | 14.9576 | 2.7104 | 42.7067 | 15.7569 | 2.7104 | 0.9112%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 21 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 2.0214 | 0.17081 | 11.8347 | 2.0214 | 0.17081 | 11.8347 | 2.1294 | 0.17993 | 11.8347 | 0.8819%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 23 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.9041 | 0.18707 | 10.1785 | 1.9041 | 0.18707 | 10.1785 | 2.0059 | 0.19707 | 10.1785 | 0.9662%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 9 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.3124 | 0.073202 | 31.5898 | 2.3124 | 0.073202 | 31.5898 | 2.436 | 0.077113 | 31.5898 | 0.9775%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 149 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 37.1689 | 1.2119 | 30.6699 | 37.1689 | 1.2119 | 30.6699 | 39.1549 | 1.2767 | 30.6699 | 0.9826%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 224 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 96.2066 | 1.8219 | 52.805 | 96.2066 | 1.8219 | 52.805 | 101.3471 | 1.9193 | 52.805 | 0.9977%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 469 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 97.5658 | 3.8146 | 25.5766 | 97.5658 | 3.8146 | 25.5766 | 102.7789 | 4.0185 | 25.5766 | 0.9908%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 78 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 57.3987 | 0.63442 | 90.4744 | 57.3987 | 0.63442 | 90.4744 | 60.4656 | 0.66832 | 90.4744 | 0.9788%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 54 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 20.009 | 0.43921 | 45.5566 | 20.009 | 0.43921 | 45.5566 | 21.0782 | 0.46268 | 45.5566 | 0.9469%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 327 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 80.0347 | 2.6597 | 30.0918 | 80.0347 | 2.6597 | 30.0918 | 84.311 | 2.8018 | 30.0918 | 0.9648%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 133 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 14.6539 | 1.0818 | 13.5462 | 14.6539 | 1.0818 | 13.5462 | 15.4368 | 1.1396 | 13.5462 | 0.9856%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 440 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 33.4415 | 3.5788 | 9.3444 | 33.4415 | 3.5788 | 9.3444 | 35.2284 | 3.77 | 9.3444 | 0.9842%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 759 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 27.8656 | 6.1734 | 4.5138 | 27.8656 | 6.1734 | 4.5138 | 29.3545 | 6.5032 | 4.5138 | 0.979%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 13.083 | 0.74829 | 17.4838 | 13.083 | 0.74829 | 17.4838 | 13.782 | 0.78827 | 17.4838 | 0.9892%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 550 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 40.471 | 4.4735 | 9.0469 | 40.471 | 4.4735 | 9.0469 | 42.6334 | 4.7125 | 9.0469 | 0.9866%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 6 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.9122 | 0.048801 | 80.1659 | 3.9122 | 0.048801 | 80.1659 | 4.1212 | 0.051409 | 80.1659 | 0.9965%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 63 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.3418 | 0.51242 | 8.4733 | 4.3418 | 0.51242 | 8.4733 | 4.5738 | 0.53979 | 8.4733 | 0.9977%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 115 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 11.1645 | 0.93536 | 11.936 | 11.1645 | 0.93536 | 11.936 | 11.761 | 0.98534 | 11.936 | 0.9935%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 18 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.5017 | 0.1464 | 10.2573 | 1.5017 | 0.1464 | 10.2573 | 1.582 | 0.15423 | 10.2573 | 0.9948%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 150 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 17.7477 | 1.22 | 14.5469 | 17.7477 | 1.22 | 14.5469 | 18.696 | 1.2852 | 14.5469 | 0.9905%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 104 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 56.9641 | 0.84589 | 67.3421 | 56.9641 | 0.84589 | 67.3421 | 60.0078 | 0.89109 | 67.3421 | 0.9304%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 164 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 61.4624 | 1.3339 | 46.077 | 61.4624 | 1.3339 | 46.077 | 64.7464 | 1.4052 | 46.077 | 0.9454%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 908 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 111.2495 | 7.3853 | 15.0637 | 111.2495 | 7.3853 | 15.0637 | 117.1938 | 7.7799 | 15.0637 | 0.9926%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 355 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 34.5034 | 2.8874 | 11.9496 | 34.5034 | 2.8874 | 11.9496 | 36.3469 | 3.0417 | 11.9496 | 0.9815%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.6887 | 0.40668 | 9.0703 | 3.6887 | 0.40668 | 9.0703 | 3.8858 | 0.42841 | 9.0703 | 0.9046%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 14 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 19.3034 | 0.11387 | 169.521 | 19.3034 | 0.11387 | 169.521 | 20.3348 | 0.11995 | 169.521 | 0.8554%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 217 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 41.1347 | 1.765 | 23.306 | 41.1347 | 1.765 | 23.306 | 43.3326 | 1.8593 | 23.306 | 0.9867%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.55516 | 0.032534 | 17.064 | 0.55516 | 0.032534 | 17.064 | 0.58483 | 0.034273 | 17.064 | 0.9994%
2026 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.016267 | 0 | 0 | 0.016267 | 0 | 0 | 0.017136 | 0 | 0%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 153 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 151.1246 | 1.2444 | 121.4401 | 151.1246 | 1.2444 | 121.4401 | 159.1994 | 1.3109 | 121.4401 | 0.9909%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 315 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 77.2532 | 2.5621 | 30.1526 | 77.2532 | 2.5621 | 30.1526 | 81.381 | 2.699 | 30.1526 | 0.9925%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 756 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 351.4153 | 6.149 | 57.1501 | 351.4153 | 6.149 | 57.1501 | 370.1919 | 6.4775 | 57.1501 | 0.9936%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 10 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.070593 | 0.081336 | 0.86792 | 0.070593 | 0.081336 | 0.86792 | 0.074365 | 0.085682 | 0.86792 | 0.895%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 121 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.502 | 0.98416 | 3.5583 | 3.502 | 0.98416 | 3.5583 | 3.6891 | 1.0367 | 3.5583 | 0.8771%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 985 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 48.5729 | 8.0116 | 6.0628 | 48.5729 | 8.0116 | 6.0628 | 51.1682 | 8.4396 | 6.0628 | 0.9246%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 107 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 28.8489 | 0.87029 | 33.1485 | 28.8489 | 0.87029 | 33.1485 | 30.3904 | 0.91679 | 33.1485 | 0.9907%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 308 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 36.6006 | 2.5051 | 14.6102 | 36.6006 | 2.5051 | 14.6102 | 38.5562 | 2.639 | 14.6102 | 0.9899%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 354 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 28.7225 | 2.8793 | 9.9756 | 28.7225 | 2.8793 | 9.9756 | 30.2572 | 3.0331 | 9.9756 | 0.9527%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 890 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 16.0328 | 7.2389 | 2.2148 | 16.0328 | 7.2389 | 2.2148 | 16.8894 | 7.6257 | 2.2148 | 0.8154%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 325 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.9249 | 2.6434 | 6.4027 | 16.9249 | 2.6434 | 6.4027 | 17.8293 | 2.7847 | 6.4027 | 0.9501%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 1376 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 173.5015 | 11.1918 | 15.5026 | 173.5015 | 11.1918 | 15.5026 | 182.772 | 11.7898 | 15.5026 | 0.97%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 675 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 38.089 | 5.4902 | 6.9377 | 38.089 | 5.4902 | 6.9377 | 40.1242 | 5.7835 | 6.9377 | 0.991%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 215 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.8695 | 1.7487 | 10.2186 | 17.8695 | 1.7487 | 10.2186 | 18.8243 | 1.8422 | 10.2186 | 0.7065%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 778 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 40.7977 | 6.3279 | 6.4473 | 40.7977 | 6.3279 | 6.4473 | 42.9776 | 6.666 | 6.4473 | 0.9752%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 973 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 53.0508 | 7.914 | 6.7034 | 53.0508 | 7.914 | 6.7034 | 55.8853 | 8.3368 | 6.7034 | 0.9686%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 237 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.3625 | 1.9277 | 3.3006 | 6.3625 | 1.9277 | 3.3006 | 6.7025 | 2.0307 | 3.3006 | 0.7976%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 689 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 108.5713 | 5.604 | 19.3738 | 108.5713 | 5.604 | 19.3738 | 114.3724 | 5.9035 | 19.3738 | 0.9877%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 39.1596 | 2.9037 | 13.4862 | 39.1596 | 2.9037 | 13.4862 | 41.252 | 3.0588 | 13.4862 | 0.981%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 832 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 93.29 | 6.7671 | 13.7857 | 93.29 | 6.7671 | 13.7857 | 98.2747 | 7.1287 | 13.7857 | 0.9713%
2026 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 33 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.6098 | 0.26841 | 9.7233 | 2.6098 | 0.26841 | 9.7233 | 2.7492 | 0.28275 | 9.7233 | 0.6764%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 285 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 31.7101 | 2.3181 | 13.6795 | 31.7101 | 2.3181 | 13.6795 | 33.4045 | 2.4419 | 13.6795 | 0.9774%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 475 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 45.9869 | 3.8634 | 11.9031 | 45.9869 | 3.8634 | 11.9031 | 48.444 | 4.0699 | 11.9031 | 0.977%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 1095 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 121.6439 | 8.9063 | 13.6582 | 121.6439 | 8.9063 | 13.6582 | 128.1435 | 9.3821 | 13.6582 | 0.968%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.9263 | 0.65882 | 21.1383 | 13.9263 | 0.65882 | 21.1383 | 14.6704 | 0.69402 | 21.1383 | 0.8924%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 37 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 22.1145 | 0.30094 | 73.4842 | 22.1145 | 0.30094 | 73.4842 | 23.2961 | 0.31702 | 73.4842 | 0.7823%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 8 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.41426 | 0.065069 | 6.3665 | 0.41426 | 0.065069 | 6.3665 | 0.43639 | 0.068545 | 6.3665 | 0.9121%
2026 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 9 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0012779 | 0 | 0 | 0.0012779 | 0 | 0.001219 | 0.073202 | 0.016652 | 0.001219 | 0.073202 | 0.016652 | 0.0012841 | 0.077113 | 0.016652 | 0.1338%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 606 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 107.1917 | 4.9289 | 21.7474 | 107.1917 | 4.9289 | 21.7474 | 112.9191 | 5.1923 | 21.7474 | 0.9429%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 22 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 18.4509 | 0.17894 | 103.1128 | 18.4509 | 0.17894 | 103.1128 | 19.4367 | 0.1885 | 103.1128 | 0.9974%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 424 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 40.0342 | 3.4486 | 11.6087 | 40.0342 | 3.4486 | 11.6087 | 42.1733 | 3.6329 | 11.6087 | 0.9922%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 24 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 6.2019 | 0.19521 | 31.771 | 6.2019 | 0.19521 | 31.771 | 6.5333 | 0.20564 | 31.771 | 0.9914%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 101 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.9995 | 0.82149 | 2.434 | 1.9995 | 0.82149 | 2.434 | 2.1063 | 0.86538 | 2.434 | 0.6623%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 185 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.3429 | 1.5047 | 2.2216 | 3.3429 | 1.5047 | 2.2216 | 3.5215 | 1.5851 | 2.2216 | 0.7437%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 536 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 15.1178 | 4.3596 | 3.4677 | 15.1178 | 4.3596 | 3.4677 | 15.9255 | 4.5925 | 3.4677 | 0.9193%
2026 | 196 | 196-43F | Tier-2 | Tier-2---17 | Tier-2---9 | 5 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.048193 | 0 | 0 | 0.048193 | 0 | 0.045972 | 0.040668 | 1.1304 | 0.045972 | 0.040668 | 1.1304 | 0.048429 | 0.042841 | 1.1304 | 0.0514%
2026 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 3 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.7392 | 0.024401 | 71.2765 | 1.7392 | 0.024401 | 71.2765 | 1.8321 | 0.025704 | 71.2765 | 0.9934%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 19 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.060854 | 0.15454 | 0.39378 | 0.060854 | 0.15454 | 0.39378 | 0.064106 | 0.1628 | 0.39378 | 0.9638%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 85 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.8681 | 0.69135 | 12.8272 | 8.8681 | 0.69135 | 12.8272 | 9.3419 | 0.72829 | 12.8272 | 0.9553%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 266 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.5085 | 2.1635 | 2.0839 | 4.5085 | 2.1635 | 2.0839 | 4.7494 | 2.2791 | 2.0839 | 0.9636%
2026 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 11 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 1.2217 | 0 | 0 | 1.2217 | 0 | 1.1655 | 0.089469 | 13.0263 | 1.1655 | 0.089469 | 13.0263 | 1.2277 | 0.09425 | 13.0263 | 0.9852%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 85 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 12.1749 | 0.69135 | 17.6102 | 12.1749 | 0.69135 | 17.6102 | 12.8254 | 0.72829 | 17.6102 | 0.9978%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 346 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 28.3235 | 2.8142 | 10.0644 | 28.3235 | 2.8142 | 10.0644 | 29.8368 | 2.9646 | 10.0644 | 0.9975%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1409 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 80.5201 | 11.4602 | 7.0261 | 80.5201 | 11.4602 | 7.0261 | 84.8224 | 12.0725 | 7.0261 | 0.9974%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 205 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.2815 | 1.6674 | 2.5678 | 4.2815 | 1.6674 | 2.5678 | 4.5103 | 1.7565 | 2.5678 | 0.901%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 361 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.4882 | 2.9362 | 2.8909 | 8.4882 | 2.9362 | 2.8909 | 8.9417 | 3.0931 | 2.8909 | 0.8573%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 238 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.1468 | 1.9358 | 0.59243 | 1.1468 | 1.9358 | 0.59243 | 1.2081 | 2.0392 | 0.59243 | 0.7047%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 182 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.5407 | 1.4803 | 1.0408 | 1.5407 | 1.4803 | 1.0408 | 1.623 | 1.5594 | 1.0408 | 0.5082%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 427 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 10.2406 | 3.473 | 2.9486 | 10.2406 | 3.473 | 2.9486 | 10.7877 | 3.6586 | 2.9486 | 0.8949%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 305 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 14.5454 | 2.4807 | 5.8633 | 14.5454 | 2.4807 | 5.8633 | 15.3226 | 2.6133 | 5.8633 | 0.8426%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 1226 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 16.4236 | 9.9718 | 1.647 | 16.4236 | 9.9718 | 1.647 | 17.3012 | 10.5046 | 1.647 | 0.9106%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 384 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.8295 | 3.1233 | 5.0682 | 15.8295 | 3.1233 | 5.0682 | 16.6753 | 3.2902 | 5.0682 | 0.9543%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 260 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 14.2272 | 2.1147 | 6.7277 | 14.2272 | 2.1147 | 6.7277 | 14.9874 | 2.2277 | 6.7277 | 0.9497%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 43 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.7626 | 0.34974 | 16.4767 | 5.7626 | 0.34974 | 16.4767 | 6.0705 | 0.36843 | 16.4767 | 0.9907%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 1745 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 46.2307 | 14.1931 | 3.2573 | 46.2307 | 14.1931 | 3.2573 | 48.7009 | 14.9514 | 3.2573 | 0.9915%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 25 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.825 | 0.20334 | 58.1541 | 11.825 | 0.20334 | 58.1541 | 12.4568 | 0.2142 | 58.1541 | 0.9792%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 678 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 9.206 | 5.5146 | 1.6694 | 9.206 | 5.5146 | 1.6694 | 9.6979 | 5.8092 | 1.6694 | 0.9662%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 66 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.4204 | 0.53682 | 4.5088 | 2.4204 | 0.53682 | 4.5088 | 2.5497 | 0.5655 | 4.5088 | 0.9706%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 209 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.756 | 1.6999 | 8.0921 | 13.756 | 1.6999 | 8.0921 | 14.491 | 1.7907 | 8.0921 | 0.9727%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 425 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 25.2035 | 3.4568 | 7.2911 | 25.2035 | 3.4568 | 7.2911 | 26.5502 | 3.6415 | 7.2911 | 0.9578%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 108 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.624 | 0.87843 | 10.956 | 9.624 | 0.87843 | 10.956 | 10.1382 | 0.92536 | 10.956 | 0.9712%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 113 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.97889 | 0.91909 | 1.0651 | 0.97889 | 0.91909 | 1.0651 | 1.0312 | 0.9682 | 1.0651 | 0.9778%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 164 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 20.3743 | 1.3339 | 15.2742 | 20.3743 | 1.3339 | 15.2742 | 21.463 | 1.4052 | 15.2742 | 0.9872%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 120 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.7268 | 0.97603 | 14.0639 | 13.7268 | 0.97603 | 14.0639 | 14.4603 | 1.0282 | 14.0639 | 0.9782%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 1826 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 247.9614 | 14.8519 | 16.6956 | 247.9614 | 14.8519 | 16.6956 | 261.2103 | 15.6455 | 16.6956 | 0.9891%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 979 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 63.2206 | 7.9628 | 7.9395 | 63.2206 | 7.9628 | 7.9395 | 66.5986 | 8.3882 | 7.9395 | 0.9941%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 1960 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.4973 | 15.9418 | 0.28211 | 4.4973 | 15.9418 | 0.28211 | 4.7376 | 16.7936 | 0.28211 | 0.974%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 966 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.7358 | 7.857 | 0.47548 | 3.7358 | 7.857 | 0.47548 | 3.9354 | 8.2768 | 0.47548 | 0.9786%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 515 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.8339 | 4.1888 | 1.154 | 4.8339 | 4.1888 | 1.154 | 5.0922 | 4.4126 | 1.154 | 0.9871%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 20.875 | 2.5865 | 8.0708 | 20.875 | 2.5865 | 8.0708 | 21.9903 | 2.7247 | 8.0708 | 0.9909%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 1448 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 14.0738 | 11.7774 | 1.195 | 14.0738 | 11.7774 | 1.195 | 14.8257 | 12.4067 | 1.195 | 0.8569%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 654 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 211.6306 | 5.3194 | 39.785 | 211.6306 | 5.3194 | 39.785 | 222.9383 | 5.6036 | 39.785 | 0.9924%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 757 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 119.0085 | 6.1571 | 19.3286 | 119.0085 | 6.1571 | 19.3286 | 125.3673 | 6.4861 | 19.3286 | 0.9821%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 414 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 184.0533 | 3.3673 | 54.659 | 184.0533 | 3.3673 | 54.659 | 193.8875 | 3.5472 | 54.659 | 0.99%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 153 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 13.2167 | 1.2444 | 10.6206 | 13.2167 | 1.2444 | 10.6206 | 13.9229 | 1.3109 | 10.6206 | 0.9809%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 308 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 51.2828 | 2.5051 | 20.471 | 51.2828 | 2.5051 | 20.471 | 54.0229 | 2.639 | 20.471 | 0.9892%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 489 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 132.853 | 3.9773 | 33.4026 | 132.853 | 3.9773 | 33.4026 | 139.9515 | 4.1898 | 33.4026 | 0.9919%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 10 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.6793 | 0.081336 | 8.3518 | 0.6793 | 0.081336 | 8.3518 | 0.71559 | 0.085682 | 8.3518 | 0.999%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 951 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 17.1386 | 7.735 | 2.2157 | 17.1386 | 7.735 | 2.2157 | 18.0544 | 8.1483 | 2.2157 | 0.8922%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 793 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 22.8579 | 6.4499 | 3.5439 | 22.8579 | 6.4499 | 3.5439 | 24.0792 | 6.7946 | 3.5439 | 0.8785%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 1095 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 100.6039 | 8.9063 | 11.2959 | 100.6039 | 8.9063 | 11.2959 | 105.9793 | 9.3821 | 11.2959 | 0.9868%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 874 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 33.0238 | 7.1087 | 4.6455 | 33.0238 | 7.1087 | 4.6455 | 34.7883 | 7.4886 | 4.6455 | 0.9466%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 976 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 12.4717 | 7.9384 | 1.5711 | 12.4717 | 7.9384 | 1.5711 | 13.1381 | 8.3625 | 1.5711 | 0.9088%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 282 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 95.5917 | 2.2937 | 41.6763 | 95.5917 | 2.2937 | 41.6763 | 100.6993 | 2.4162 | 41.6763 | 0.9905%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 169 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 20.2056 | 1.3746 | 14.6995 | 20.2056 | 1.3746 | 14.6995 | 21.2852 | 1.448 | 14.6995 | 0.9634%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 992 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 15.4856 | 8.0685 | 1.9193 | 15.4856 | 8.0685 | 1.9193 | 16.313 | 8.4996 | 1.9193 | 0.8429%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 3231 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 30.5685 | 26.2796 | 1.1632 | 30.5685 | 26.2796 | 1.1632 | 32.2018 | 27.6837 | 1.1632 | 0.8937%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 155 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 35.1769 | 1.2607 | 27.9026 | 35.1769 | 1.2607 | 27.9026 | 37.0565 | 1.3281 | 27.9026 | 0.9991%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 1090 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 28.7509 | 8.8656 | 3.243 | 28.7509 | 8.8656 | 3.243 | 30.2871 | 9.3393 | 3.243 | 0.9216%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 1687 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 25.0832 | 13.7213 | 1.828 | 25.0832 | 13.7213 | 1.828 | 26.4234 | 14.4545 | 1.828 | 0.9611%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 17 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.7393 | 0.13827 | 48.7401 | 6.7393 | 0.13827 | 48.7401 | 7.0994 | 0.14566 | 48.7401 | 0.9946%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 1158 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 36.4187 | 9.4187 | 3.8666 | 36.4187 | 9.4187 | 3.8666 | 38.3646 | 9.9219 | 3.8666 | 0.9703%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 157 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 1.0134 | 1.277 | 0.79362 | 1.0134 | 1.277 | 0.79362 | 1.0676 | 1.3452 | 0.79362 | 0.334%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 19.5112 | 0.91909 | 21.2287 | 19.5112 | 0.91909 | 21.2287 | 20.5537 | 0.9682 | 21.2287 | 0.9951%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 7 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 37.1986 | 0.056935 | 653.3518 | 37.1986 | 0.056935 | 653.3518 | 39.1862 | 0.059977 | 653.3518 | 0.9988%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 353 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.8178 | 2.8712 | 2.0263 | 5.8178 | 2.8712 | 2.0263 | 6.1286 | 3.0246 | 2.0263 | 0.9868%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 367 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 42.518 | 2.985 | 14.2438 | 42.518 | 2.985 | 14.2438 | 44.7898 | 3.1445 | 14.2438 | 0.9945%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 163 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 21.4759 | 1.3258 | 16.1988 | 21.4759 | 1.3258 | 16.1988 | 22.6234 | 1.3966 | 16.1988 | 0.9686%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 169 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 91.3747 | 1.3746 | 66.4749 | 91.3747 | 1.3746 | 66.4749 | 96.257 | 1.448 | 66.4749 | 0.9959%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 514 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 12.3393 | 4.1807 | 2.9515 | 12.3393 | 4.1807 | 2.9515 | 12.9986 | 4.404 | 2.9515 | 0.9515%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 2343 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 68.2692 | 19.057 | 3.5824 | 68.2692 | 19.057 | 3.5824 | 71.9169 | 20.0752 | 3.5824 | 0.9662%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 676 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 749.8113 | 5.4983 | 136.3715 | 749.8113 | 5.4983 | 136.3715 | 789.8747 | 5.7921 | 136.3715 | 0.9925%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 34.2741 | 0.10574 | 324.1468 | 34.2741 | 0.10574 | 324.1468 | 36.1055 | 0.11139 | 324.1468 | 0.9927%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 375 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 428.6915 | 3.0501 | 140.5504 | 428.6915 | 3.0501 | 140.5504 | 451.5971 | 3.2131 | 140.5504 | 0.9963%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 36 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.3843 | 0.29281 | 8.143 | 2.3843 | 0.29281 | 8.143 | 2.5117 | 0.30845 | 8.143 | 0.8656%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 1345 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 68.0491 | 10.9397 | 6.2204 | 68.0491 | 10.9397 | 6.2204 | 71.685 | 11.5242 | 6.2204 | 0.9605%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 192 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 46.2897 | 1.5616 | 29.6416 | 46.2897 | 1.5616 | 29.6416 | 48.763 | 1.6451 | 29.6416 | 0.9985%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 3380 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 154.7093 | 27.4915 | 5.6275 | 154.7093 | 27.4915 | 5.6275 | 162.9756 | 28.9604 | 5.6275 | 0.967%
2026 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.16292 | 0.040668 | 4.0062 | 0.16292 | 0.040668 | 4.0062 | 0.17163 | 0.042841 | 4.0062 | 0.9833%
2026 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.6265 | 0.048801 | 33.3285 | 1.6265 | 0.048801 | 33.3285 | 1.7134 | 0.051409 | 33.3285 | 0.9937%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 997 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 18.1259 | 8.1092 | 2.2352 | 18.1259 | 8.1092 | 2.2352 | 19.0944 | 8.5425 | 2.2352 | 0.9498%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 1487 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 59.885 | 12.0946 | 4.9514 | 59.885 | 12.0946 | 4.9514 | 63.0847 | 12.7409 | 4.9514 | 0.9826%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 942 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 18.007 | 7.6618 | 2.3502 | 18.007 | 7.6618 | 2.3502 | 18.9692 | 8.0712 | 2.3502 | 0.9106%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 284 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 4.0406 | 2.3099 | 1.7492 | 4.0406 | 2.3099 | 1.7492 | 4.2565 | 2.4334 | 1.7492 | 0.7897%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 133 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.3877 | 1.0818 | 6.8293 | 7.3877 | 1.0818 | 6.8293 | 7.7824 | 1.1396 | 6.8293 | 0.9819%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 791 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 32.3646 | 6.4337 | 5.0305 | 32.3646 | 6.4337 | 5.0305 | 34.0939 | 6.7774 | 5.0305 | 0.9768%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 14 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0786 | 0.11387 | 9.4719 | 1.0786 | 0.11387 | 9.4719 | 1.1362 | 0.11995 | 9.4719 | 0.9298%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 110 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.5257 | 0.89469 | 1.7052 | 1.5257 | 0.89469 | 1.7052 | 1.6072 | 0.9425 | 1.7052 | 0.8171%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 1015 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 25.6087 | 8.2556 | 3.102 | 25.6087 | 8.2556 | 3.102 | 26.977 | 8.6967 | 3.102 | 0.983%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 3357 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 48.405 | 27.3044 | 1.7728 | 48.405 | 27.3044 | 1.7728 | 50.9914 | 28.7633 | 1.7728 | 0.9868%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.0004932 | 0.048801 | 0.010106 | 0.0004932 | 0.048801 | 0.010106 | 0.00051955 | 0.051409 | 0.010106 | 0.004523%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 1436 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 28.6233 | 11.6798 | 2.4507 | 28.6233 | 11.6798 | 2.4507 | 30.1527 | 12.3039 | 2.4507 | 0.9884%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 475 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.692 | 3.8634 | 1.7321 | 6.692 | 3.8634 | 1.7321 | 7.0496 | 4.0699 | 1.7321 | 0.9757%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 392 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 4.0561 | 3.1884 | 1.2722 | 4.0561 | 3.1884 | 1.2722 | 4.2728 | 3.3587 | 1.2722 | 0.9496%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 870 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 19.1889 | 7.0762 | 2.7117 | 19.1889 | 7.0762 | 2.7117 | 20.2142 | 7.4543 | 2.7117 | 0.859%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 1397 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 46.8623 | 11.3626 | 4.1243 | 46.8623 | 11.3626 | 4.1243 | 49.3662 | 11.9697 | 4.1243 | 0.9946%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 250 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 36.9882 | 2.0334 | 18.1904 | 36.9882 | 2.0334 | 18.1904 | 38.9646 | 2.142 | 18.1904 | 0.8863%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 738 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 222.188 | 6.0026 | 37.0154 | 222.188 | 6.0026 | 37.0154 | 234.0599 | 6.3233 | 37.0154 | 0.9837%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 814 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 91.5381 | 6.6207 | 13.826 | 91.5381 | 6.6207 | 13.826 | 96.4291 | 6.9745 | 13.826 | 0.9873%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 270 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 26.1976 | 2.1961 | 11.9293 | 26.1976 | 2.1961 | 11.9293 | 27.5973 | 2.3134 | 11.9293 | 0.9726%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 156 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 21.2648 | 1.2688 | 16.7593 | 21.2648 | 1.2688 | 16.7593 | 22.401 | 1.3366 | 16.7593 | 0.9861%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 513 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 49.8843 | 4.1725 | 11.9554 | 49.8843 | 4.1725 | 11.9554 | 52.5497 | 4.3955 | 11.9554 | 0.9807%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 985 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 199.1398 | 8.0116 | 24.8565 | 199.1398 | 8.0116 | 24.8565 | 209.7801 | 8.4396 | 24.8565 | 0.9836%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 252 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 64.6625 | 2.0497 | 31.5479 | 64.6625 | 2.0497 | 31.5479 | 68.1175 | 2.1592 | 31.5479 | 0.9784%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 34.4579 | 0.91096 | 37.8259 | 34.4579 | 0.91096 | 37.8259 | 36.299 | 0.95963 | 37.8259 | 0.994%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 316 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 267.7119 | 2.5702 | 104.1595 | 267.7119 | 2.5702 | 104.1595 | 282.0161 | 2.7075 | 104.1595 | 0.9934%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 996 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 255.4695 | 8.101 | 31.5354 | 255.4695 | 8.101 | 31.5354 | 269.1196 | 8.5339 | 31.5354 | 0.9889%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 81 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.4846 | 0.65882 | 6.8071 | 4.4846 | 0.65882 | 6.8071 | 4.7243 | 0.69402 | 6.8071 | 0.7089%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 23.8534 | 0.28468 | 83.7915 | 23.8534 | 0.28468 | 83.7915 | 25.1279 | 0.29989 | 83.7915 | 0.9883%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 1029 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 292.0914 | 8.3695 | 34.8997 | 292.0914 | 8.3695 | 34.8997 | 307.6982 | 8.8166 | 34.8997 | 0.9911%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 1238 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 618.2973 | 10.0694 | 61.4038 | 618.2973 | 10.0694 | 61.4038 | 651.3338 | 10.6074 | 61.4038 | 0.9893%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 725 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 8.0494 | 5.8968 | 1.365 | 8.0494 | 5.8968 | 1.365 | 8.4795 | 6.2119 | 1.365 | 0.9808%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 131 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.9204 | 1.0655 | 14.0032 | 14.9204 | 1.0655 | 14.0032 | 15.7176 | 1.1224 | 14.0032 | 0.9867%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 504 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 10.2731 | 4.0993 | 2.506 | 10.2731 | 4.0993 | 2.506 | 10.822 | 4.3184 | 2.506 | 0.9646%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 918 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 58.7462 | 7.4666 | 7.8678 | 58.7462 | 7.4666 | 7.8678 | 61.8851 | 7.8656 | 7.8678 | 0.9824%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 635 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.8035 | 5.1648 | 1.3173 | 6.8035 | 5.1648 | 1.3173 | 7.167 | 5.4408 | 1.3173 | 0.6927%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 65 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.5462 | 0.52868 | 6.7076 | 3.5462 | 0.52868 | 6.7076 | 3.7357 | 0.55693 | 6.7076 | 0.9876%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 257 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 11.0889 | 2.0903 | 5.3049 | 11.0889 | 2.0903 | 5.3049 | 11.6814 | 2.202 | 5.3049 | 0.9838%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 110 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.451 | 0.89469 | 8.328 | 7.451 | 0.89469 | 8.328 | 7.8491 | 0.9425 | 8.328 | 0.987%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 98 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.4814 | 0.79709 | 4.3677 | 3.4814 | 0.79709 | 4.3677 | 3.6675 | 0.83968 | 4.3677 | 0.9688%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 971 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 41.4475 | 7.8977 | 5.248 | 41.4475 | 7.8977 | 5.248 | 43.6621 | 8.3197 | 5.248 | 0.9791%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 530 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 35.3681 | 4.3108 | 8.2045 | 35.3681 | 4.3108 | 8.2045 | 37.2578 | 4.5411 | 8.2045 | 0.9907%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 549 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 33.8556 | 4.4653 | 7.5819 | 33.8556 | 4.4653 | 7.5819 | 35.6645 | 4.7039 | 7.5819 | 0.9682%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 164 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 6.0425 | 1.3339 | 4.53 | 6.0425 | 1.3339 | 4.53 | 6.3654 | 1.4052 | 4.53 | 0.6596%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 921 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 30.5472 | 7.491 | 4.0778 | 30.5472 | 7.491 | 4.0778 | 32.1793 | 7.8913 | 4.0778 | 0.9454%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 333 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 12.0051 | 2.7085 | 4.4324 | 12.0051 | 2.7085 | 4.4324 | 12.6466 | 2.8532 | 4.4324 | 0.9251%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 19 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.98533 | 0.15454 | 6.3759 | 0.98533 | 0.15454 | 6.3759 | 1.038 | 0.1628 | 6.3759 | 0.9818%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 34.3178 | 5.2136 | 6.5823 | 34.3178 | 5.2136 | 6.5823 | 36.1515 | 5.4922 | 6.5823 | 0.9585%
2026 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.4091 | 0.073202 | 5.5887 | 0.4091 | 0.073202 | 5.5887 | 0.43096 | 0.077113 | 5.5887 | 0.8666%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 81 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 49.8241 | 0.65882 | 75.6263 | 49.8241 | 0.65882 | 75.6263 | 52.4863 | 0.69402 | 75.6263 | 0.9855%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 245 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.865 | 1.9927 | 8.4633 | 16.865 | 1.9927 | 8.4633 | 17.7662 | 2.0992 | 8.4633 | 0.878%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 4.3298 | 0.032534 | 133.0848 | 4.3298 | 0.032534 | 133.0848 | 4.5612 | 0.034273 | 133.0848 | 0.9431%
2026 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 9 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.39171 | 0.073202 | 5.351 | 0.39171 | 0.073202 | 5.351 | 0.41263 | 0.077113 | 5.351 | 0.9823%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 329 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.8786 | 2.6759 | 1.8231 | 4.8786 | 2.6759 | 1.8231 | 5.1393 | 2.8189 | 1.8231 | 0.9288%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 44 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.024332 | 0.35788 | 0.06799 | 0.024332 | 0.35788 | 0.06799 | 0.025632 | 0.377 | 0.06799 | 0.7897%
2026 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 4.3537 | 0.032534 | 133.82 | 4.3537 | 0.032534 | 133.82 | 4.5864 | 0.034273 | 133.82 | 0.9948%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 129 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.6479 | 1.0492 | 6.336 | 6.6479 | 1.0492 | 6.336 | 7.0031 | 1.1053 | 6.336 | 0.9241%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 249 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 20.9129 | 2.0253 | 10.326 | 20.9129 | 2.0253 | 10.326 | 22.0303 | 2.1335 | 10.326 | 0.9107%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 590 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 43.4106 | 4.7988 | 9.0461 | 43.4106 | 4.7988 | 9.0461 | 45.7301 | 5.0552 | 9.0461 | 0.9555%
2026 | 308 | 308-485AE | Tier-2 | Tier-2---15 | Tier-2---8 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.043838 | 0 | 0 | 0.043838 | 0 | 0.041818 | 0.040668 | 1.0283 | 0.041818 | 0.040668 | 1.0283 | 0.044052 | 0.042841 | 1.0283 | 0.02775%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 20 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.17655 | 0.16267 | 1.0853 | 0.17655 | 0.16267 | 1.0853 | 0.18598 | 0.17136 | 1.0853 | 0.1937%
2026 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 4 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.37322 | 0.032534 | 11.4715 | 0.37322 | 0.032534 | 11.4715 | 0.39316 | 0.034273 | 11.4715 | 0.8469%
2026 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 32 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.073515 | 0.26027 | 0.28245 | 0.073515 | 0.26027 | 0.28245 | 0.077443 | 0.27418 | 0.28245 | 0.4938%
2026 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 26 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.43274 | 0.21147 | 2.0463 | 0.43274 | 0.21147 | 2.0463 | 0.45586 | 0.22277 | 2.0463 | 0.1628%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 262 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.035668 | 2.131 | 0.016738 | 0.035668 | 2.131 | 0.016738 | 0.037574 | 2.2449 | 0.016738 | 0.02339%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 38 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0029183 | 0.30908 | 0.009442 | 0.0029183 | 0.30908 | 0.009442 | 0.0030742 | 0.32559 | 0.009442 | 0.001514%
2026 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 323 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.9919 | 2.6271 | 0.7582 | 1.9919 | 2.6271 | 0.7582 | 2.0983 | 2.7675 | 0.7582 | 0.995%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.8639 | 0.1464 | 19.5615 | 2.8639 | 0.1464 | 19.5615 | 3.0169 | 0.15423 | 19.5615 | 0.9927%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 1796 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 32.8093 | 14.6079 | 2.246 | 32.8093 | 14.6079 | 2.246 | 34.5623 | 15.3884 | 2.246 | 0.9548%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 2181 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 129.861 | 17.7393 | 7.3205 | 129.861 | 17.7393 | 7.3205 | 136.7997 | 18.6872 | 7.3205 | 0.9814%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 2656 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 51.5398 | 21.6028 | 2.3858 | 51.5398 | 21.6028 | 2.3858 | 54.2936 | 22.757 | 2.3858 | 0.9699%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 1091 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 128.0651 | 8.8737 | 14.4319 | 128.0651 | 8.8737 | 14.4319 | 134.9078 | 9.3479 | 14.4319 | 0.9928%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 1620 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 105.6518 | 13.1764 | 8.0183 | 105.6518 | 13.1764 | 8.0183 | 111.297 | 13.8804 | 8.0183 | 0.9888%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 1027 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 222.6577 | 8.3532 | 26.6554 | 222.6577 | 8.3532 | 26.6554 | 234.5546 | 8.7995 | 26.6554 | 0.9925%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 222 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 86.9953 | 1.8057 | 48.1794 | 86.9953 | 1.8057 | 48.1794 | 91.6436 | 1.9021 | 48.1794 | 0.9973%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 1531 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 176.4312 | 12.4525 | 14.1683 | 176.4312 | 12.4525 | 14.1683 | 185.8581 | 13.1179 | 14.1683 | 0.9936%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 1034 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 85.7598 | 8.4101 | 10.1972 | 85.7598 | 8.4101 | 10.1972 | 90.342 | 8.8595 | 10.1972 | 0.9749%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 340 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 23.8334 | 2.7654 | 8.6184 | 23.8334 | 2.7654 | 8.6184 | 25.1069 | 2.9132 | 8.6184 | 0.9918%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 60 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 21.1215 | 0.48801 | 43.2805 | 21.1215 | 0.48801 | 43.2805 | 22.2501 | 0.51409 | 43.2805 | 0.9993%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 143 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.8485 | 1.1631 | 14.4859 | 16.8485 | 1.1631 | 14.4859 | 17.7488 | 1.2252 | 14.4859 | 0.8869%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 150 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 40.9814 | 1.22 | 33.5903 | 40.9814 | 1.22 | 33.5903 | 43.1711 | 1.2852 | 33.5903 | 0.943%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 30 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.788 | 0.24401 | 11.426 | 2.788 | 0.24401 | 11.426 | 2.937 | 0.25704 | 11.426 | 0.6284%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 484 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 128.3764 | 3.9367 | 32.6106 | 128.3764 | 3.9367 | 32.6106 | 135.2357 | 4.147 | 32.6106 | 0.9943%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 1235 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 194.0236 | 10.045 | 19.3155 | 194.0236 | 10.045 | 19.3155 | 204.3905 | 10.5817 | 19.3155 | 0.9917%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 30.8577 | 1.9195 | 16.0757 | 30.8577 | 1.9195 | 16.0757 | 32.5065 | 2.0221 | 16.0757 | 0.8854%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 587 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 70.4778 | 4.7744 | 14.7616 | 70.4778 | 4.7744 | 14.7616 | 74.2435 | 5.0295 | 14.7616 | 0.985%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 253 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.9537 | 2.0578 | 6.295 | 12.9537 | 2.0578 | 6.295 | 13.6459 | 2.1677 | 6.295 | 0.7994%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 403 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 50.9054 | 3.2778 | 15.5302 | 50.9054 | 3.2778 | 15.5302 | 53.6253 | 3.453 | 15.5302 | 0.9814%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 1342 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 149.3338 | 10.9153 | 13.6812 | 149.3338 | 10.9153 | 13.6812 | 157.313 | 11.4985 | 13.6812 | 0.9776%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 1273 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 84.5967 | 10.354 | 8.1704 | 84.5967 | 10.354 | 8.1704 | 89.1168 | 10.9073 | 8.1704 | 0.9541%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.8235 | 0.39855 | 29.6666 | 11.8235 | 0.39855 | 29.6666 | 12.4552 | 0.41984 | 29.6666 | 0.9906%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 47 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 48.4832 | 0.38228 | 126.827 | 48.4832 | 0.38228 | 126.827 | 51.0737 | 0.4027 | 126.827 | 0.9968%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 11 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 8.0059 | 0.089469 | 89.4818 | 8.0059 | 0.089469 | 89.4818 | 8.4336 | 0.09425 | 89.4818 | 0.9549%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 484 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 158.9726 | 3.9367 | 40.3827 | 158.9726 | 3.9367 | 40.3827 | 167.4668 | 4.147 | 40.3827 | 0.9879%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 901 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 164.5511 | 7.3284 | 22.454 | 164.5511 | 7.3284 | 22.454 | 173.3433 | 7.7199 | 22.454 | 0.9747%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 1047 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 96.5713 | 8.5159 | 11.3402 | 96.5713 | 8.5159 | 11.3402 | 101.7312 | 8.9709 | 11.3402 | 0.9704%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 712 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 109.6988 | 5.7911 | 18.9426 | 109.6988 | 5.7911 | 18.9426 | 115.5602 | 6.1005 | 18.9426 | 0.9781%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 18 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.5598 | 0.1464 | 37.9758 | 5.5598 | 0.1464 | 37.9758 | 5.8569 | 0.15423 | 37.9758 | 0.9721%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.7834 | 0.47175 | 27.098 | 12.7834 | 0.47175 | 27.098 | 13.4665 | 0.49695 | 27.098 | 0.9966%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 404 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 353.6518 | 3.286 | 107.6249 | 353.6518 | 3.286 | 107.6249 | 372.5479 | 3.4615 | 107.6249 | 0.9859%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 66 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 12.3554 | 0.53682 | 23.0161 | 12.3554 | 0.53682 | 23.0161 | 13.0156 | 0.5655 | 23.0161 | 0.8901%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 79 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.6574 | 0.64255 | 2.5794 | 1.6574 | 0.64255 | 2.5794 | 1.746 | 0.67689 | 2.5794 | 0.1879%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 1637 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 26.3874 | 13.3147 | 1.9818 | 26.3874 | 13.3147 | 1.9818 | 27.7974 | 14.0261 | 1.9818 | 0.8818%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 699 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 17.3358 | 5.6854 | 3.0492 | 17.3358 | 5.6854 | 3.0492 | 18.2621 | 5.9891 | 3.0492 | 0.9783%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 1562 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 59.8337 | 12.7046 | 4.7096 | 59.8337 | 12.7046 | 4.7096 | 63.0306 | 13.3835 | 4.7096 | 0.9847%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 30 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 12.3633 | 0.24401 | 50.6679 | 12.3633 | 0.24401 | 50.6679 | 13.0239 | 0.25704 | 50.6679 | 0.9597%
2026 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.67081 | 0.0081336 | 82.4741 | 0.67081 | 0.0081336 | 82.4741 | 0.70665 | 0.0085682 | 82.4741 | 0.9953%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 334 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 32.7047 | 2.7166 | 12.0388 | 32.7047 | 2.7166 | 12.0388 | 34.4521 | 2.8618 | 12.0388 | 0.9745%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 5.0723 | 0.39855 | 12.7269 | 5.0723 | 0.39855 | 12.7269 | 5.3433 | 0.41984 | 12.7269 | 0.9134%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 121 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 44.4079 | 0.98416 | 45.1225 | 44.4079 | 0.98416 | 45.1225 | 46.7806 | 1.0367 | 45.1225 | 0.98%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 50.2962 | 0.51242 | 98.1552 | 50.2962 | 0.51242 | 98.1552 | 52.9836 | 0.53979 | 98.1552 | 0.9857%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 889 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.8191 | 7.2307 | 2.3261 | 16.8191 | 7.2307 | 2.3261 | 17.7178 | 7.6171 | 2.3261 | 0.9609%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 34 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.014671 | 0.27654 | 0.053051 | 0.014671 | 0.27654 | 0.053051 | 0.015455 | 0.29132 | 0.053051 | 0.01745%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 637 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.9098 | 5.1811 | 1.3336 | 6.9098 | 5.1811 | 1.3336 | 7.2789 | 5.4579 | 1.3336 | 0.8492%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 642 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.9086 | 5.2218 | 0.55701 | 2.9086 | 5.2218 | 0.55701 | 3.064 | 5.5008 | 0.55701 | 0.5795%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 1846 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 97.67 | 15.0146 | 6.505 | 97.67 | 15.0146 | 6.505 | 102.8886 | 15.8168 | 6.505 | 0.8848%
2026 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 38 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 6.494 | 0.30908 | 21.0112 | 6.494 | 0.30908 | 21.0112 | 6.841 | 0.32559 | 21.0112 | 0.9662%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 44 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 5.1901 | 0.35788 | 14.5024 | 5.1901 | 0.35788 | 14.5024 | 5.4674 | 0.377 | 14.5024 | 0.9893%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 297 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 4.1351 | 2.4157 | 1.7118 | 4.1351 | 2.4157 | 1.7118 | 4.3561 | 2.5447 | 1.7118 | 0.9131%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 189 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.68786 | 1.5372 | 0.44746 | 0.68786 | 1.5372 | 0.44746 | 0.72461 | 1.6194 | 0.44746 | 0.51%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 9 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 3.0769 | 0.073202 | 42.0335 | 3.0769 | 0.073202 | 42.0335 | 3.2414 | 0.077113 | 42.0335 | 0.9662%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 31.8067 | 1.0574 | 30.0811 | 31.8067 | 1.0574 | 30.0811 | 33.5062 | 1.1139 | 30.0811 | 0.9767%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 529 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.853 | 4.3027 | 0.8955 | 3.853 | 4.3027 | 0.8955 | 4.0589 | 4.5326 | 0.8955 | 0.7071%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 353 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 87.2546 | 2.8712 | 30.3901 | 87.2546 | 2.8712 | 30.3901 | 91.9168 | 3.0246 | 30.3901 | 0.9496%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 203 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 66.4731 | 1.6511 | 40.2595 | 66.4731 | 1.6511 | 40.2595 | 70.0248 | 1.7393 | 40.2595 | 0.9611%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 107 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 13.5715 | 0.87029 | 15.5942 | 13.5715 | 0.87029 | 15.5942 | 14.2966 | 0.91679 | 15.5942 | 0.8872%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 448 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 96.9373 | 3.6438 | 26.603 | 96.9373 | 3.6438 | 26.603 | 102.1167 | 3.8385 | 26.603 | 0.9569%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 175 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 14.2791 | 1.4234 | 10.0319 | 14.2791 | 1.4234 | 10.0319 | 15.0421 | 1.4994 | 10.0319 | 0.8473%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 216 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 30.7191 | 1.7569 | 17.4853 | 30.7191 | 1.7569 | 17.4853 | 32.3605 | 1.8507 | 17.4853 | 0.8754%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 296 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 37.1637 | 2.4075 | 15.4364 | 37.1637 | 2.4075 | 15.4364 | 39.1494 | 2.5362 | 15.4364 | 0.8812%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 12.5395 | 0.22774 | 55.0603 | 12.5395 | 0.22774 | 55.0603 | 13.2095 | 0.23991 | 55.0603 | 0.9724%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 20 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 11.2563 | 0.16267 | 69.1968 | 11.2563 | 0.16267 | 69.1968 | 11.8578 | 0.17136 | 69.1968 | 0.9739%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 139 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 22.903 | 1.1306 | 20.258 | 22.903 | 1.1306 | 20.258 | 24.1267 | 1.191 | 20.258 | 0.9191%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 245 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 11.2627 | 1.9927 | 5.6519 | 11.2627 | 1.9927 | 5.6519 | 11.8645 | 2.0992 | 5.6519 | 0.557%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 225 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.7837 | 1.8301 | 2.0676 | 3.7837 | 1.8301 | 2.0676 | 3.9859 | 1.9278 | 2.0676 | 0.7618%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 164 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.7608 | 1.3339 | 3.5691 | 4.7608 | 1.3339 | 3.5691 | 5.0152 | 1.4052 | 3.5691 | 0.7912%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 713 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 79.6266 | 5.7992 | 13.7305 | 79.6266 | 5.7992 | 13.7305 | 83.8812 | 6.1091 | 13.7305 | 0.9168%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 336 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 50.3074 | 2.7329 | 18.4082 | 50.3074 | 2.7329 | 18.4082 | 52.9954 | 2.8789 | 18.4082 | 0.9343%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 1001 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 58.0947 | 8.1417 | 7.1354 | 58.0947 | 8.1417 | 7.1354 | 61.1988 | 8.5767 | 7.1354 | 0.9049%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 61 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.8342 | 0.49615 | 27.8831 | 13.8342 | 0.49615 | 27.8831 | 14.5734 | 0.52266 | 27.8831 | 0.9697%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 37 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.768 | 0.30094 | 19.1665 | 5.768 | 0.30094 | 19.1665 | 6.0762 | 0.31702 | 19.1665 | 0.967%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 115 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 49.5677 | 0.93536 | 52.9931 | 49.5677 | 0.93536 | 52.9931 | 52.2162 | 0.98534 | 52.9931 | 0.9877%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 265 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 21.1459 | 2.1554 | 9.8107 | 21.1459 | 2.1554 | 9.8107 | 22.2758 | 2.2706 | 9.8107 | 0.9555%
2026 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 80 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.7488 | 0.65069 | 4.2244 | 2.7488 | 0.65069 | 4.2244 | 2.8957 | 0.68545 | 4.2244 | 0.9711%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 586 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 78.3224 | 4.7663 | 16.4326 | 78.3224 | 4.7663 | 16.4326 | 82.5073 | 5.0209 | 16.4326 | 0.9923%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 132 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 7.0106 | 1.0736 | 6.5298 | 7.0106 | 1.0736 | 6.5298 | 7.3851 | 1.131 | 6.5298 | 0.9277%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 171 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 10.2883 | 1.3908 | 7.3972 | 10.2883 | 1.3908 | 7.3972 | 10.838 | 1.4652 | 7.3972 | 0.9525%
2026 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 6 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 1.7471 | 0 | 0 | 1.7471 | 0 | 1.6666 | 0.048801 | 34.1501 | 1.6666 | 0.048801 | 34.1501 | 1.7556 | 0.051409 | 34.1501 | 0.3253%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 11 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.3077 | 0.089469 | 14.616 | 1.3077 | 0.089469 | 14.616 | 1.3776 | 0.09425 | 14.616 | 0.999%
2026 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 5 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 6.2494 | 0 | 0 | 6.2494 | 0 | 5.9615 | 0.040668 | 146.5902 | 5.9615 | 0.040668 | 146.5902 | 6.28 | 0.042841 | 146.5902 | 0.999%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 15 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.7259 | 0.122 | 14.1464 | 1.7259 | 0.122 | 14.1464 | 1.8181 | 0.12852 | 14.1464 | 0.9984%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 373 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 26.9189 | 3.0338 | 8.8729 | 26.9189 | 3.0338 | 8.8729 | 28.3572 | 3.1959 | 8.8729 | 0.9993%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 52 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.36197 | 0.42295 | 0.85584 | 0.36197 | 0.42295 | 0.85584 | 0.38131 | 0.44554 | 0.85584 | 0.9723%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 277 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 32.7275 | 2.253 | 14.5262 | 32.7275 | 2.253 | 14.5262 | 34.4762 | 2.3734 | 14.5262 | 0.997%
2026 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.81736 | 0.0081336 | 100.4925 | 0.81736 | 0.0081336 | 100.4925 | 0.86104 | 0.0085682 | 100.4925 | 0.9735%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 49 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 13.019 | 0.39855 | 32.6663 | 13.019 | 0.39855 | 32.6663 | 13.7146 | 0.41984 | 32.6663 | 0.9902%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 443 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 49.3848 | 3.6032 | 13.7059 | 49.3848 | 3.6032 | 13.7059 | 52.0235 | 3.7957 | 13.7059 | 0.9833%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 878 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 158.6864 | 7.1413 | 22.221 | 158.6864 | 7.1413 | 22.221 | 167.1652 | 7.5228 | 22.221 | 0.9937%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 108 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 38.5309 | 0.87843 | 43.8636 | 38.5309 | 0.87843 | 43.8636 | 40.5897 | 0.92536 | 43.8636 | 0.9496%
2026 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 14 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.6496 | 0.11387 | 14.487 | 1.6496 | 0.11387 | 14.487 | 1.7378 | 0.11995 | 14.487 | 0.216%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 192 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.9397 | 1.5616 | 1.2421 | 1.9397 | 1.5616 | 1.2421 | 2.0433 | 1.6451 | 1.2421 | 0.9963%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 82 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.9644 | 0.66695 | 10.4422 | 6.9644 | 0.66695 | 10.4422 | 7.3365 | 0.70259 | 10.4422 | 0.9951%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 1001 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 27.6613 | 8.1417 | 3.3975 | 27.6613 | 8.1417 | 3.3975 | 29.1393 | 8.5767 | 3.3975 | 0.9734%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 437 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.8205 | 3.5544 | 3.8883 | 13.8205 | 3.5544 | 3.8883 | 14.5589 | 3.7443 | 3.8883 | 0.9797%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 1143 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 24.3479 | 9.2967 | 2.619 | 24.3479 | 9.2967 | 2.619 | 25.6488 | 9.7934 | 2.619 | 0.9676%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 1286 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 30.1957 | 10.4598 | 2.8868 | 30.1957 | 10.4598 | 2.8868 | 31.8091 | 11.0187 | 2.8868 | 0.9272%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 482 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 15.3089 | 3.9204 | 3.905 | 15.3089 | 3.9204 | 3.905 | 16.1269 | 4.1299 | 3.905 | 0.9829%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 848 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 62.3968 | 6.8973 | 9.0466 | 62.3968 | 6.8973 | 9.0466 | 65.7308 | 7.2658 | 9.0466 | 0.9672%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 593 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.5208 | 4.8232 | 1.1446 | 5.5208 | 4.8232 | 1.1446 | 5.8158 | 5.0809 | 1.1446 | 0.7734%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 496 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 19.1856 | 4.0343 | 4.7557 | 19.1856 | 4.0343 | 4.7557 | 20.2108 | 4.2498 | 4.7557 | 0.9648%
2026 | 520 | 520-1936 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 0.63566 | 0 | 0 | 0.63566 | 0 | 0.60638 | 0.016267 | 37.2761 | 0.60638 | 0.016267 | 37.2761 | 0.63878 | 0.017136 | 37.2761 | 0.9977%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 188 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.8412 | 1.5291 | 1.2041 | 1.8412 | 1.5291 | 1.2041 | 1.9395 | 1.6108 | 1.2041 | 0.7472%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 1385 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 46.0042 | 11.265 | 4.0838 | 46.0042 | 11.265 | 4.0838 | 48.4623 | 11.8669 | 4.0838 | 0.9649%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 640 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 19.0309 | 5.2055 | 3.6559 | 19.0309 | 5.2055 | 3.6559 | 20.0478 | 5.4836 | 3.6559 | 0.9757%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 932 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 104.6914 | 7.5805 | 13.8106 | 104.6914 | 7.5805 | 13.8106 | 110.2852 | 7.9855 | 13.8106 | 0.9669%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 448 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.9096 | 3.6438 | 1.8963 | 6.9096 | 3.6438 | 1.8963 | 7.2788 | 3.8385 | 1.8963 | 0.8931%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 973 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 79.0871 | 7.914 | 9.9933 | 79.0871 | 7.914 | 9.9933 | 83.3128 | 8.3368 | 9.9933 | 0.9779%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 734 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 82.5858 | 5.97 | 13.8334 | 82.5858 | 5.97 | 13.8334 | 86.9984 | 6.289 | 13.8334 | 0.9936%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 900 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 52.9434 | 7.3202 | 7.2325 | 52.9434 | 7.3202 | 7.2325 | 55.7723 | 7.7113 | 7.2325 | 0.9878%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 673 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 116.0523 | 5.4739 | 21.201 | 116.0523 | 5.4739 | 21.201 | 122.2532 | 5.7664 | 21.201 | 0.9938%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 1600 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 85.1588 | 13.0137 | 6.5438 | 85.1588 | 13.0137 | 6.5438 | 89.7089 | 13.7091 | 6.5438 | 0.9905%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.4626 | 0.75642 | 0.61156 | 0.4626 | 0.75642 | 0.61156 | 0.48731 | 0.79684 | 0.61156 | 0.4302%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 79 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.25141 | 0.64255 | 0.39126 | 0.25141 | 0.64255 | 0.39126 | 0.26484 | 0.67689 | 0.39126 | 0.2253%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1898 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 51.8857 | 15.4375 | 3.361 | 51.8857 | 15.4375 | 3.361 | 54.658 | 16.2624 | 3.361 | 0.9644%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 230 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.34053 | 1.8707 | 0.18203 | 0.34053 | 1.8707 | 0.18203 | 0.35872 | 1.9707 | 0.18203 | 0.117%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 486 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 52.0453 | 3.9529 | 13.1663 | 52.0453 | 3.9529 | 13.1663 | 54.8261 | 4.1641 | 13.1663 | 0.9978%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 935 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 107.7138 | 7.6049 | 14.1637 | 107.7138 | 7.6049 | 14.1637 | 113.4691 | 8.0112 | 14.1637 | 0.9977%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 638 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 129.4684 | 5.1892 | 24.9495 | 129.4684 | 5.1892 | 24.9495 | 136.386 | 5.4665 | 24.9495 | 0.9899%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 82.4531 | 4.2701 | 19.3093 | 82.4531 | 4.2701 | 19.3093 | 86.8586 | 4.4983 | 19.3093 | 0.982%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 1862 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 381.43 | 15.1447 | 25.1857 | 381.43 | 15.1447 | 25.1857 | 401.8103 | 15.9539 | 25.1857 | 0.9903%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 61 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 5.3877 | 0.49615 | 10.8591 | 5.3877 | 0.49615 | 10.8591 | 5.6756 | 0.52266 | 10.8591 | 0.6775%
2026 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 3 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.4566 | 0.024401 | 59.6948 | 1.4566 | 0.024401 | 59.6948 | 1.5344 | 0.025704 | 59.6948 | 0.9944%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 14 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.7778 | 0.11387 | 41.9579 | 4.7778 | 0.11387 | 41.9579 | 5.033 | 0.11995 | 41.9579 | 0.9632%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.46874 | 0.31721 | 1.4777 | 0.46874 | 0.31721 | 1.4777 | 0.49379 | 0.33416 | 1.4777 | 0.9941%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 1930 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 171.1238 | 15.6978 | 10.9011 | 171.1238 | 15.6978 | 10.9011 | 180.2671 | 16.5366 | 10.9011 | 0.9555%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 2562 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 244.0922 | 20.8382 | 11.7137 | 244.0922 | 20.8382 | 11.7137 | 257.1344 | 21.9516 | 11.7137 | 0.994%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 587 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 23.3101 | 4.7744 | 4.8823 | 23.3101 | 4.7744 | 4.8823 | 24.5556 | 5.0295 | 4.8823 | 0.936%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 1265 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 37.4045 | 10.289 | 3.6354 | 37.4045 | 10.289 | 3.6354 | 39.403 | 10.8387 | 3.6354 | 0.938%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 212 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 5.1753 | 1.7243 | 3.0014 | 5.1753 | 1.7243 | 3.0014 | 5.4518 | 1.8165 | 3.0014 | 0.8718%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 319 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 14.4092 | 2.5946 | 5.5535 | 14.4092 | 2.5946 | 5.5535 | 15.1791 | 2.7332 | 5.5535 | 0.9279%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 273 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 57.5552 | 2.2205 | 25.9203 | 57.5552 | 2.2205 | 25.9203 | 60.6304 | 2.3391 | 25.9203 | 0.9729%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 800 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 144.2009 | 6.5069 | 22.1614 | 144.2009 | 6.5069 | 22.1614 | 151.9058 | 6.8545 | 22.1614 | 0.9856%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 258 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 23.0424 | 2.0985 | 10.9806 | 23.0424 | 2.0985 | 10.9806 | 24.2735 | 2.2106 | 10.9806 | 0.9864%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 243 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 53.8256 | 1.9765 | 27.2333 | 53.8256 | 1.9765 | 27.2333 | 56.7015 | 2.0821 | 27.2333 | 0.9841%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 537 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 99.3275 | 4.3677 | 22.7412 | 99.3275 | 4.3677 | 22.7412 | 104.6347 | 4.6011 | 22.7412 | 0.9831%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 483 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 87.2089 | 3.9285 | 22.1989 | 87.2089 | 3.9285 | 22.1989 | 91.8686 | 4.1384 | 22.1989 | 0.9843%
2026 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 1 | 100% | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081336 | 0 | 0 | 0.0081336 | 0 | 0 | 0.0085682 | 0 | 0%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 410 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 29.8416 | 3.3348 | 8.9486 | 29.8416 | 3.3348 | 8.9486 | 31.436 | 3.5129 | 8.9486 | 0.9977%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 206 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 16.2275 | 1.6755 | 9.6851 | 16.2275 | 1.6755 | 9.6851 | 17.0946 | 1.765 | 9.6851 | 0.9957%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 93 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 18.457 | 0.75642 | 24.4004 | 18.457 | 0.75642 | 24.4004 | 19.4432 | 0.79684 | 24.4004 | 0.9986%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 730 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 20.9297 | 5.9375 | 3.525 | 20.9297 | 5.9375 | 3.525 | 22.048 | 6.2548 | 3.525 | 0.9923%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 486 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 136.5755 | 3.9529 | 34.5506 | 136.5755 | 3.9529 | 34.5506 | 143.873 | 4.1641 | 34.5506 | 0.9856%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 34 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 68.3702 | 0.27654 | 247.2329 | 68.3702 | 0.27654 | 247.2329 | 72.0233 | 0.29132 | 247.2329 | 0.9951%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 551 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 82.1782 | 4.4816 | 18.3368 | 82.1782 | 4.4816 | 18.3368 | 86.5691 | 4.7211 | 18.3368 | 0.9433%
2026 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 17 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 3.0791 | 0.13827 | 22.2685 | 3.0791 | 0.13827 | 22.2685 | 3.2436 | 0.14566 | 22.2685 | 0.9958%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 153 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 29.5835 | 1.2444 | 23.7726 | 29.5835 | 1.2444 | 23.7726 | 31.1642 | 1.3109 | 23.7726 | 0.9258%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 558 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 116.6696 | 4.5385 | 25.7064 | 116.6696 | 4.5385 | 25.7064 | 122.9034 | 4.781 | 25.7064 | 0.9926%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 846 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 19.4046 | 6.881 | 2.82 | 19.4046 | 6.881 | 2.82 | 20.4414 | 7.2487 | 2.82 | 0.9747%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 565 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.8721 | 4.5955 | 2.3658 | 10.8721 | 4.5955 | 2.3658 | 11.453 | 4.841 | 2.3658 | 0.7093%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 91.0778 | 3.0338 | 30.0208 | 91.0778 | 3.0338 | 30.0208 | 95.9442 | 3.1959 | 30.0208 | 0.9829%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 412 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 174.0462 | 3.351 | 51.9381 | 174.0462 | 3.351 | 51.9381 | 183.3457 | 3.5301 | 51.9381 | 0.989%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 24.3129 | 0.53682 | 45.2909 | 24.3129 | 0.53682 | 45.2909 | 25.612 | 0.5655 | 45.2909 | 0.9937%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 433 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 50.8689 | 3.5218 | 14.4438 | 50.8689 | 3.5218 | 14.4438 | 53.5869 | 3.71 | 14.4438 | 0.9631%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 933 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 174.04 | 7.5886 | 22.9343 | 174.04 | 7.5886 | 22.9343 | 183.3392 | 7.9941 | 22.9343 | 0.9714%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 34 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 28.1165 | 0.27654 | 101.6719 | 28.1165 | 0.27654 | 101.6719 | 29.6188 | 0.29132 | 101.6719 | 0.9712%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 415 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 189.1139 | 3.3754 | 56.0265 | 189.1139 | 3.3754 | 56.0265 | 199.2185 | 3.5558 | 56.0265 | 0.9923%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 24 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.2067 | 0.19521 | 6.1815 | 1.2067 | 0.19521 | 6.1815 | 1.2711 | 0.20564 | 6.1815 | 0.9928%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 62 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.11704 | 0.50428 | 0.23209 | 0.11704 | 0.50428 | 0.23209 | 0.12329 | 0.53123 | 0.23209 | 0.9883%
2026 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 36 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.3301 | 0.29281 | 4.5426 | 1.3301 | 0.29281 | 4.5426 | 1.4012 | 0.30845 | 4.5426 | 0.9963%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 9 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.063433 | 0.073202 | 0.86655 | 0.063433 | 0.073202 | 0.86655 | 0.066823 | 0.077113 | 0.86655 | 0.9902%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 13 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 3.1321 | 0.10574 | 29.6217 | 3.1321 | 0.10574 | 29.6217 | 3.2994 | 0.11139 | 29.6217 | 0.9939%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 241 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.1444 | 1.9602 | 1.094 | 2.1444 | 1.9602 | 1.094 | 2.259 | 2.0649 | 1.094 | 0.9666%
2026 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 1 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 1.8833 | 0 | 0 | 1.8833 | 0 | 1.7966 | 0.0081336 | 220.8819 | 1.7966 | 0.0081336 | 220.8819 | 1.8926 | 0.0085682 | 220.8819 | 0.9988%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 793 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 81.9888 | 6.4499 | 12.7116 | 81.9888 | 6.4499 | 12.7116 | 86.3696 | 6.7946 | 12.7116 | 0.9986%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 503 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 78.5903 | 4.0912 | 19.2096 | 78.5903 | 4.0912 | 19.2096 | 82.7895 | 4.3098 | 19.2096 | 0.9762%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 8 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.4212 | 0.065069 | 37.2094 | 2.4212 | 0.065069 | 37.2094 | 2.5505 | 0.068545 | 37.2094 | 0.9867%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 781 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 86.5756 | 6.3523 | 13.629 | 86.5756 | 6.3523 | 13.629 | 91.2014 | 6.6917 | 13.629 | 0.9973%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 1809 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 256.1133 | 14.7136 | 17.4065 | 256.1133 | 14.7136 | 17.4065 | 269.7978 | 15.4998 | 17.4065 | 0.9919%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 130 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 60.5455 | 1.0574 | 57.2608 | 60.5455 | 1.0574 | 57.2608 | 63.7806 | 1.1139 | 57.2608 | 0.9998%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 1320 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 147.8841 | 10.7363 | 13.7742 | 147.8841 | 10.7363 | 13.7742 | 155.7857 | 11.31 | 13.7742 | 0.9833%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 741 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 110.8755 | 6.027 | 18.3965 | 110.8755 | 6.027 | 18.3965 | 116.7997 | 6.349 | 18.3965 | 0.988%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 1020 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 51.148 | 8.2962 | 6.1652 | 51.148 | 8.2962 | 6.1652 | 53.8809 | 8.7395 | 6.1652 | 0.9625%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 585 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.8412 | 4.7581 | 2.6988 | 12.8412 | 4.7581 | 2.6988 | 13.5273 | 5.0124 | 2.6988 | 0.9181%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 352 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 74.6808 | 2.863 | 26.0846 | 74.6808 | 2.863 | 26.0846 | 78.6711 | 3.016 | 26.0846 | 0.9835%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 1150 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 389.2135 | 9.3536 | 41.611 | 389.2135 | 9.3536 | 41.611 | 410.0097 | 9.8534 | 41.611 | 0.9889%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 577 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 31.9736 | 4.6931 | 6.8129 | 31.9736 | 4.6931 | 6.8129 | 33.682 | 4.9438 | 6.8129 | 0.9191%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 762 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 213.2749 | 6.1978 | 34.4115 | 213.2749 | 6.1978 | 34.4115 | 224.6704 | 6.5289 | 34.4115 | 0.9908%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.4417 | 0.073202 | 19.6944 | 1.4417 | 0.073202 | 19.6944 | 1.5187 | 0.077113 | 19.6944 | 0.9858%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 211 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.8036 | 1.7162 | 4.5471 | 7.8036 | 1.7162 | 4.5471 | 8.2206 | 1.8079 | 4.5471 | 0.9652%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 1555 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 523.2391 | 12.6477 | 41.3703 | 523.2391 | 12.6477 | 41.3703 | 551.1964 | 13.3235 | 41.3703 | 0.9927%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 16 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 54.3851 | 0.13014 | 417.906 | 54.3851 | 0.13014 | 417.906 | 57.291 | 0.13709 | 417.906 | 0.9997%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 1096 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 305.9761 | 8.9144 | 34.3238 | 305.9761 | 8.9144 | 34.3238 | 322.3248 | 9.3907 | 34.3238 | 0.9926%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 309 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.8658 | 2.5133 | 4.7213 | 11.8658 | 2.5133 | 4.7213 | 12.4998 | 2.6476 | 4.7213 | 0.9598%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 318 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 32.2825 | 2.5865 | 12.4812 | 32.2825 | 2.5865 | 12.4812 | 34.0074 | 2.7247 | 12.4812 | 0.9934%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 84 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 10.234 | 0.68322 | 14.979 | 10.234 | 0.68322 | 14.979 | 10.7808 | 0.71973 | 14.979 | 0.6902%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 116 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 14.5549 | 0.94349 | 15.4265 | 14.5549 | 0.94349 | 15.4265 | 15.3325 | 0.99391 | 15.4265 | 0.7661%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 3 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 4.1265 | 0.024401 | 169.1142 | 4.1265 | 0.024401 | 169.1142 | 4.347 | 0.025704 | 169.1142 | 0.9947%
2026 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.5777 | 0.10574 | 5.4635 | 0.5777 | 0.10574 | 5.4635 | 0.60856 | 0.11139 | 5.4635 | 0.9691%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 75 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 123.222 | 0.61002 | 201.9972 | 123.222 | 0.61002 | 201.9972 | 129.8059 | 0.64261 | 201.9972 | 0.9966%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 913 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 143.1403 | 7.426 | 19.2757 | 143.1403 | 7.426 | 19.2757 | 150.7885 | 7.8227 | 19.2757 | 0.9905%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 1693 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 268.7684 | 13.7701 | 19.5182 | 268.7684 | 13.7701 | 19.5182 | 283.129 | 14.5059 | 19.5182 | 0.9891%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 169 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 76.0524 | 1.3746 | 55.328 | 76.0524 | 1.3746 | 55.328 | 80.116 | 1.448 | 55.328 | 0.9946%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 109 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 41.3095 | 0.88656 | 46.5953 | 41.3095 | 0.88656 | 46.5953 | 43.5167 | 0.93393 | 46.5953 | 0.9952%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 442 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 138.6921 | 3.595 | 38.5787 | 138.6921 | 3.595 | 38.5787 | 146.1026 | 3.7871 | 38.5787 | 0.9843%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 1149 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 106.3896 | 9.3455 | 11.3841 | 106.3896 | 9.3455 | 11.3841 | 112.0742 | 9.8448 | 11.3841 | 0.9898%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 320 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 75.3766 | 2.6027 | 28.9604 | 75.3766 | 2.6027 | 28.9604 | 79.4041 | 2.7418 | 28.9604 | 0.9853%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 1391 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 219.7181 | 11.3138 | 19.4204 | 219.7181 | 11.3138 | 19.4204 | 231.4579 | 11.9183 | 19.4204 | 0.9839%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 943 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 213.075 | 7.67 | 27.7804 | 213.075 | 7.67 | 27.7804 | 224.4598 | 8.0798 | 27.7804 | 0.9748%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 373 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 86.5106 | 3.0338 | 28.5154 | 86.5106 | 3.0338 | 28.5154 | 91.1329 | 3.1959 | 28.5154 | 0.9912%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 264 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 48.0711 | 2.1473 | 22.3872 | 48.0711 | 2.1473 | 22.3872 | 50.6396 | 2.262 | 22.3872 | 0.9732%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 149 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 81.8457 | 1.2119 | 67.5349 | 81.8457 | 1.2119 | 67.5349 | 86.2189 | 1.2767 | 67.5349 | 0.9953%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 246 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 60.9876 | 2.0009 | 30.4807 | 60.9876 | 2.0009 | 30.4807 | 64.2463 | 2.1078 | 30.4807 | 0.9803%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 603 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 31.2181 | 4.9045 | 6.3651 | 31.2181 | 4.9045 | 6.3651 | 32.8861 | 5.1666 | 6.3651 | 0.9369%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 67.491 | 0.59375 | 113.6688 | 67.491 | 0.59375 | 113.6688 | 71.0971 | 0.62548 | 113.6688 | 0.9955%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 24 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 49.1533 | 0.19521 | 251.8024 | 49.1533 | 0.19521 | 251.8024 | 51.7796 | 0.20564 | 251.8024 | 0.803%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 41 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.9388 | 0.33348 | 11.8115 | 3.9388 | 0.33348 | 11.8115 | 4.1493 | 0.35129 | 11.8115 | 0.6587%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 303 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 43.563 | 2.4645 | 17.6764 | 43.563 | 2.4645 | 17.6764 | 45.8907 | 2.5962 | 17.6764 | 0.9978%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 150 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 31.7322 | 1.22 | 26.0092 | 31.7322 | 1.22 | 26.0092 | 33.4277 | 1.2852 | 26.0092 | 0.9981%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 159 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 13.4423 | 1.2932 | 10.3943 | 13.4423 | 1.2932 | 10.3943 | 14.1606 | 1.3623 | 10.3943 | 0.9962%
2026 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 18 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.7804 | 0.1464 | 73.6346 | 10.7804 | 0.1464 | 73.6346 | 11.3564 | 0.15423 | 73.6346 | 0.9972%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 46 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.4261 | 0.37414 | 14.5027 | 5.4261 | 0.37414 | 14.5027 | 5.716 | 0.39414 | 14.5027 | 0.3454%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 192 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.4764 | 1.5616 | 3.5068 | 5.4764 | 1.5616 | 3.5068 | 5.769 | 1.6451 | 3.5068 | 0.75%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 12 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.69331 | 0.097603 | 7.1034 | 0.69331 | 0.097603 | 7.1034 | 0.73035 | 0.10282 | 7.1034 | 0.9665%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 1218 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 50.7476 | 9.9067 | 5.1226 | 50.7476 | 9.9067 | 5.1226 | 53.4591 | 10.436 | 5.1226 | 0.8429%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 2353 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 62.8186 | 19.1383 | 3.2823 | 62.8186 | 19.1383 | 3.2823 | 66.175 | 20.1609 | 3.2823 | 0.9909%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 259 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.6866 | 2.1066 | 6.497 | 13.6866 | 2.1066 | 6.497 | 14.4179 | 2.2192 | 6.497 | 0.9975%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 1.0286 | 0.032534 | 31.6166 | 1.0286 | 0.032534 | 31.6166 | 1.0836 | 0.034273 | 31.6166 | 0.9975%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 85 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 38.8495 | 0.69135 | 56.1933 | 38.8495 | 0.69135 | 56.1933 | 40.9253 | 0.72829 | 56.1933 | 0.9993%
2026 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 17 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.37491 | 0.13827 | 2.7114 | 0.37491 | 0.13827 | 2.7114 | 0.39494 | 0.14566 | 2.7114 | 0.9408%
2026 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 3 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.87925 | 0.024401 | 36.0336 | 0.87925 | 0.024401 | 36.0336 | 0.92622 | 0.025704 | 36.0336 | 0.3549%
2026 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 3.0261 | 0.040668 | 74.4097 | 3.0261 | 0.040668 | 74.4097 | 3.1878 | 0.042841 | 74.4097 | 0.7993%
2026 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 137 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.8291 | 1.1143 | 3.4363 | 3.8291 | 1.1143 | 3.4363 | 4.0337 | 1.1738 | 3.4363 | 0.299%
2026 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 312 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.2158 | 2.5377 | 0.4791 | 1.2158 | 2.5377 | 0.4791 | 1.2808 | 2.6733 | 0.4791 | 0.9512%
2026 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 504 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.17895 | 4.0993 | 0.043655 | 0.17895 | 4.0993 | 0.043655 | 0.18852 | 4.3184 | 0.043655 | 0.09583%
2026 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 358 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 8.1689 | 2.9118 | 2.8054 | 8.1689 | 2.9118 | 2.8054 | 8.6054 | 3.0674 | 2.8054 | 0.8082%
2026 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 1.3377 | 0 | 0 | 1.3377 | 0 | 1.2761 | 0.056935 | 22.4131 | 1.2761 | 0.056935 | 22.4131 | 1.3443 | 0.059977 | 22.4131 | 0.9989%
2026 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 68 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 2.0264 | 0.55308 | 3.6639 | 2.0264 | 0.55308 | 3.6639 | 2.1347 | 0.58264 | 3.6639 | 0.9981%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 696 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 23.6778 | 5.661 | 4.1826 | 23.6778 | 5.661 | 4.1826 | 24.9429 | 5.9634 | 4.1826 | 0.9929%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 645 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 15.2578 | 5.2462 | 2.9084 | 15.2578 | 5.2462 | 2.9084 | 16.0731 | 5.5265 | 2.9084 | 0.9737%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 1826 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 38.8784 | 14.8519 | 2.6177 | 38.8784 | 14.8519 | 2.6177 | 40.9557 | 15.6455 | 2.6177 | 0.9874%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 1032 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 31.0776 | 8.3939 | 3.7024 | 31.0776 | 8.3939 | 3.7024 | 32.7382 | 8.8423 | 3.7024 | 0.9888%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 504 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 118.3696 | 4.0993 | 28.8754 | 118.3696 | 4.0993 | 28.8754 | 124.6943 | 4.3184 | 28.8754 | 0.9762%
2026 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 35 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 20.0507 | 0.28468 | 70.4337 | 20.0507 | 0.28468 | 70.4337 | 21.1221 | 0.29989 | 70.4337 | 0.9954%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 222 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.7686 | 1.8057 | 6.5176 | 11.7686 | 1.8057 | 6.5176 | 12.3974 | 1.9021 | 6.5176 | 0.9768%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 44 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.4978 | 0.35788 | 6.9795 | 2.4978 | 0.35788 | 6.9795 | 2.6312 | 0.377 | 6.9795 | 0.6436%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0574 | 0.16267 | 6.5 | 1.0574 | 0.16267 | 6.5 | 1.1139 | 0.17136 | 6.5 | 0.375%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 519 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 12.35 | 4.2213 | 2.9256 | 12.35 | 4.2213 | 2.9256 | 13.0099 | 4.4469 | 2.9256 | 0.9%
2026 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 109 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.5459 | 0.88656 | 2.8716 | 2.5459 | 0.88656 | 2.8716 | 2.6819 | 0.93393 | 2.8716 | 0.7028%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 263 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 9.1325 | 2.1391 | 4.2692 | 9.1325 | 2.1391 | 4.2692 | 9.6204 | 2.2534 | 4.2692 | 0.995%
2026 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 195 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.6547 | 1.586 | 4.8263 | 7.6547 | 1.586 | 4.8263 | 8.0637 | 1.6708 | 4.8263 | 0.9704%
2026 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 17 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 0.50007 | 0 | 0 | 0.50007 | 0 | 0.47703 | 0.13827 | 3.45 | 0.47703 | 0.13827 | 3.45 | 0.50252 | 0.14566 | 3.45 | 0.1609%
2026 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 160 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.60029 | 1.3014 | 0.46128 | 0.60029 | 1.3014 | 0.46128 | 0.63237 | 1.3709 | 0.46128 | 0.6647%
2026 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 23 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.099934 | 0.18707 | 0.5342 | 0.099934 | 0.18707 | 0.5342 | 0.10527 | 0.19707 | 0.5342 | 0.9726%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.8672 | 0.1464 | 94.7185 | 13.8672 | 0.1464 | 94.7185 | 14.6082 | 0.15423 | 94.7185 | 0.9979%
2026 | 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 29 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.9885 | 0.23587 | 8.4305 | 1.9885 | 0.23587 | 8.4305 | 2.0948 | 0.24848 | 8.4305 | 0.9683%
2026 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 233 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.39533 | 1.8951 | 0.20861 | 0.39533 | 1.8951 | 0.20861 | 0.41646 | 1.9964 | 0.20861 | 0.3335%
2026 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 2 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.4763 | 0.016267 | 152.229 | 2.4763 | 0.016267 | 152.229 | 2.6086 | 0.017136 | 152.229 | 0.9938%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 641 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 138.8006 | 5.2136 | 26.6227 | 138.8006 | 5.2136 | 26.6227 | 146.2169 | 5.4922 | 26.6227 | 0.9966%
2026 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 26 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.83174 | 0.21147 | 3.9331 | 0.83174 | 0.21147 | 3.9331 | 0.87618 | 0.22277 | 3.9331 | 0.9922%
2026 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.071388 | 0.0081336 | 8.777 | 0.071388 | 0.0081336 | 8.777 | 0.075203 | 0.0085682 | 8.777 | 0.986%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 875 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 106.4306 | 7.1169 | 14.9547 | 106.4306 | 7.1169 | 14.9547 | 112.1173 | 7.4971 | 14.9547 | 0.9884%
2026 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.064342 | 0.040668 | 1.5821 | 0.064342 | 0.040668 | 1.5821 | 0.06778 | 0.042841 | 1.5821 | 0.991%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 495 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 55.9658 | 4.0261 | 13.9007 | 55.9658 | 4.0261 | 13.9007 | 58.9561 | 4.2412 | 13.9007 | 0.9601%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 9 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.5513 | 0.073202 | 21.1915 | 1.5513 | 0.073202 | 21.1915 | 1.6341 | 0.077113 | 21.1915 | 0.1888%
2026 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 1 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.91644 | 0.0081336 | 112.6733 | 0.91644 | 0.0081336 | 112.6733 | 0.9654 | 0.0085682 | 112.6733 | 0.1434%
2026 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 134 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 10.1685 | 1.0899 | 9.3298 | 10.1685 | 1.0899 | 9.3298 | 10.7118 | 1.1481 | 9.3298 | 0.9408%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 1.0944 | 0.040668 | 26.9097 | 1.0944 | 0.040668 | 26.9097 | 1.1528 | 0.042841 | 26.9097 | 0.9768%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 174 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 63.0506 | 1.4152 | 44.5511 | 63.0506 | 1.4152 | 44.5511 | 66.4195 | 1.4909 | 44.5511 | 0.9549%
2026 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.17532 | 0.024401 | 7.1849 | 0.17532 | 0.024401 | 7.1849 | 0.18468 | 0.025704 | 7.1849 | 0.9464%
2026 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 7 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.016493 | 0.056935 | 0.28969 | 0.016493 | 0.056935 | 0.28969 | 0.017375 | 0.059977 | 0.28969 | 0.9786%
2026 | 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 16 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.019677 | 0.13014 | 0.1512 | 0.019677 | 0.13014 | 0.1512 | 0.020728 | 0.13709 | 0.1512 | 0.1679%
2026 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 531 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 9.1717 | 4.3189 | 2.1236 | 9.1717 | 4.3189 | 2.1236 | 9.6618 | 4.5497 | 2.1236 | 0.8949%
2026 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 318 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 1.0843 | 2.5865 | 0.41921 | 1.0843 | 2.5865 | 0.41921 | 1.1422 | 2.7247 | 0.41921 | 0.372%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 31 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.3276 | 0.25214 | 17.1633 | 4.3276 | 0.25214 | 17.1633 | 4.5588 | 0.26561 | 17.1633 | 0.9425%
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 10 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.39328 | 0.081336 | 4.8353 | 0.39328 | 0.081336 | 4.8353 | 0.4143 | 0.085682 | 4.8353 | 0.7619%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 186 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.63661 | 1.5128 | 0.4208 | 0.63661 | 1.5128 | 0.4208 | 0.67063 | 1.5937 | 0.4208 | 0.9924%
2026 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 47 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.6457 | 0.38228 | 22.6162 | 8.6457 | 0.38228 | 22.6162 | 9.1076 | 0.4027 | 22.6162 | 0.9545%
2026 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 21 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 3.1226 | 0.17081 | 18.2817 | 3.1226 | 0.17081 | 18.2817 | 3.2895 | 0.17993 | 18.2817 | 0.7837%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 892 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 41.1623 | 7.2552 | 5.6735 | 41.1623 | 7.2552 | 5.6735 | 43.3617 | 7.6428 | 5.6735 | 0.9981%
2026 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 70 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.48675 | 0.56935 | 0.85492 | 0.48675 | 0.56935 | 0.85492 | 0.51276 | 0.59977 | 0.85492 | 0.9266%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 102 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 77.7152 | 0.82962 | 93.6751 | 77.7152 | 0.82962 | 93.6751 | 81.8676 | 0.87395 | 93.6751 | 0.9507%
2026 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 169 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.40449 | 1.3746 | 0.29427 | 0.40449 | 1.3746 | 0.29427 | 0.4261 | 1.448 | 0.29427 | 0.9943%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 58 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 26.1161 | 0.47175 | 55.3604 | 26.1161 | 0.47175 | 55.3604 | 27.5116 | 0.49695 | 55.3604 | 0.9983%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 108 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 3.01 | 0.87843 | 3.4265 | 3.01 | 0.87843 | 3.4265 | 3.1708 | 0.92536 | 3.4265 | 0.9343%
2026 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 12.5918 | 0.024401 | 516.0423 | 12.5918 | 0.024401 | 516.0423 | 13.2646 | 0.025704 | 516.0423 | 0.7976%
2026 | 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 7 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.3936 | 0.056935 | 42.0413 | 2.3936 | 0.056935 | 42.0413 | 2.5215 | 0.059977 | 42.0413 | 0.9997%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 161 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 108.7518 | 1.3095 | 83.048 | 108.7518 | 1.3095 | 83.048 | 114.5625 | 1.3795 | 83.048 | 0.9951%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 12.3822 | 0.40668 | 30.4472 | 12.3822 | 0.40668 | 30.4472 | 13.0438 | 0.42841 | 30.4472 | 0.9951%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 423 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.6886 | 3.4405 | 1.0721 | 3.6886 | 3.4405 | 1.0721 | 3.8857 | 3.6243 | 1.0721 | 0.997%
2026 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 106 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.2619 | 0.86216 | 1.4637 | 1.2619 | 0.86216 | 1.4637 | 1.3294 | 0.90823 | 1.4637 | 0.9965%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.23647 | 0.032534 | 7.2684 | 0.23647 | 0.032534 | 7.2684 | 0.24911 | 0.034273 | 7.2684 | 0.9021%
2026 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 463 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.2209 | 3.7658 | 0.32421 | 1.2209 | 3.7658 | 0.32421 | 1.2862 | 3.9671 | 0.32421 | 0.3693%
2026 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 343 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 9.2645 | 2.7898 | 3.3208 | 9.2645 | 2.7898 | 3.3208 | 9.7595 | 2.9389 | 3.3208 | 0.9433%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 417 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 14.297 | 3.3917 | 4.2153 | 14.297 | 3.3917 | 4.2153 | 15.0609 | 3.5729 | 4.2153 | 0.9785%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 286 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 48.1334 | 2.3262 | 20.6918 | 48.1334 | 2.3262 | 20.6918 | 50.7052 | 2.4505 | 20.6918 | 0.9856%
2026 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 6.027 | 0.15454 | 38.9998 | 6.027 | 0.15454 | 38.9998 | 6.349 | 0.1628 | 38.9998 | 0.9902%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 786 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 65.3114 | 6.393 | 10.2161 | 65.3114 | 6.393 | 10.2161 | 68.8011 | 6.7346 | 10.2161 | 0.99%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 1534 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 27.3578 | 12.4769 | 2.1927 | 27.3578 | 12.4769 | 2.1927 | 28.8196 | 13.1436 | 2.1927 | 0.9473%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 454 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 98.6268 | 3.6926 | 26.709 | 98.6268 | 3.6926 | 26.709 | 103.8966 | 3.8899 | 26.709 | 0.9831%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 283 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 48.9483 | 2.3018 | 21.2652 | 48.9483 | 2.3018 | 21.2652 | 51.5636 | 2.4248 | 21.2652 | 0.9811%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 200 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 6.074 | 1.6267 | 3.7339 | 6.074 | 1.6267 | 3.7339 | 6.3986 | 1.7136 | 3.7339 | 0.695%
2026 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.28348 | 0.032534 | 8.7134 | 0.28348 | 0.032534 | 8.7134 | 0.29863 | 0.034273 | 8.7134 | 0.9988%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 330 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 35.3682 | 2.6841 | 13.177 | 35.3682 | 2.6841 | 13.177 | 37.258 | 2.8275 | 13.177 | 0.9914%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 793 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 30.0514 | 6.4499 | 4.6592 | 30.0514 | 6.4499 | 4.6592 | 31.6571 | 6.7946 | 4.6592 | 0.9371%
2026 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 52 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.017997 | 0.42295 | 0.042552 | 0.017997 | 0.42295 | 0.042552 | 0.018959 | 0.44554 | 0.042552 | 0.02003%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 1644 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 15.535 | 13.3716 | 1.1618 | 15.535 | 13.3716 | 1.1618 | 16.3651 | 14.0861 | 1.1618 | 0.789%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 433 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 33.7655 | 3.5218 | 9.5875 | 33.7655 | 3.5218 | 9.5875 | 35.5697 | 3.71 | 9.5875 | 0.9517%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 341 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 88.4904 | 2.7735 | 31.9051 | 88.4904 | 2.7735 | 31.9051 | 93.2185 | 2.9217 | 31.9051 | 0.9933%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 1098 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 64.412 | 8.9307 | 7.2125 | 64.412 | 8.9307 | 7.2125 | 67.8536 | 9.4078 | 7.2125 | 0.9757%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 329 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 56.3376 | 2.6759 | 21.0533 | 56.3376 | 2.6759 | 21.0533 | 59.3477 | 2.8189 | 21.0533 | 0.9932%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 505 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 35.8983 | 4.1075 | 8.7398 | 35.8983 | 4.1075 | 8.7398 | 37.8164 | 4.3269 | 8.7398 | 0.9948%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.0558 | 0.046553 | 22.6798 | 1.0558 | 0.046553 | 22.6798 | 1.1717 | 0.051661 | 22.6798 | 0.9903%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 86 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.6908 | 0.66726 | 5.5312 | 3.6908 | 0.66726 | 5.5312 | 4.0957 | 0.74047 | 5.5312 | 0.9915%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 1144 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 35.1217 | 8.8762 | 3.9569 | 35.1217 | 8.8762 | 3.9569 | 38.9752 | 9.85 | 3.9569 | 0.9141%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 1.0397 | 0.031036 | 33.5007 | 1.0397 | 0.031036 | 33.5007 | 1.1538 | 0.034441 | 33.5007 | 0.9976%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 1369 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 316.78 | 10.6219 | 29.8233 | 316.78 | 10.6219 | 29.8233 | 351.5364 | 11.7873 | 29.8233 | 0.9902%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 234 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 63.0347 | 1.8156 | 34.7188 | 63.0347 | 1.8156 | 34.7188 | 69.9507 | 2.0148 | 34.7188 | 0.9818%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 633 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 170.7952 | 4.9114 | 34.7755 | 170.7952 | 4.9114 | 34.7755 | 189.5344 | 5.4502 | 34.7755 | 0.997%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 269 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 45.5855 | 2.0871 | 21.8412 | 45.5855 | 2.0871 | 21.8412 | 50.5871 | 2.3161 | 21.8412 | 0.9951%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 53 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 12.565 | 0.41122 | 30.5555 | 12.565 | 0.41122 | 30.5555 | 13.9437 | 0.45634 | 30.5555 | 0.9958%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 7.1996 | 0.23277 | 30.9306 | 7.1996 | 0.23277 | 30.9306 | 7.9895 | 0.2583 | 30.9306 | 0.996%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 392 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 88.8468 | 3.0415 | 29.2117 | 88.8468 | 3.0415 | 29.2117 | 98.5948 | 3.3752 | 29.2117 | 0.9962%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 14 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.2724 | 0.10862 | 57.744 | 6.2724 | 0.10862 | 57.744 | 6.9606 | 0.12054 | 57.744 | 0.9922%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 221 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 45.7686 | 1.7147 | 26.6917 | 45.7686 | 1.7147 | 26.6917 | 50.7903 | 1.9028 | 26.6917 | 0.9916%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 209 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 26.0989 | 1.6216 | 16.0945 | 26.0989 | 1.6216 | 16.0945 | 28.9624 | 1.7995 | 16.0945 | 0.9924%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 1740 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 82.7087 | 13.5005 | 6.1264 | 82.7087 | 13.5005 | 6.1264 | 91.7833 | 14.9817 | 6.1264 | 0.9598%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 1132 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 33.4452 | 8.7831 | 3.8079 | 33.4452 | 8.7831 | 3.8079 | 37.1147 | 9.7467 | 3.8079 | 0.9739%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 220 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.6715 | 1.707 | 2.7368 | 4.6715 | 1.707 | 2.7368 | 5.1841 | 1.8942 | 2.7368 | 0.8768%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 45.818 | 0.81468 | 56.2403 | 45.818 | 0.81468 | 56.2403 | 50.845 | 0.90407 | 56.2403 | 0.9826%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 269 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 106.0165 | 2.0871 | 50.7951 | 106.0165 | 2.0871 | 50.7951 | 117.6484 | 2.3161 | 50.7951 | 0.9858%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 107 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 19.4652 | 0.8302 | 23.4464 | 19.4652 | 0.8302 | 23.4464 | 21.6009 | 0.92129 | 23.4464 | 0.9945%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 209 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 59.4414 | 1.6216 | 36.6559 | 59.4414 | 1.6216 | 36.6559 | 65.9631 | 1.7995 | 36.6559 | 0.9866%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 1458 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 228.4185 | 11.3124 | 20.1918 | 228.4185 | 11.3124 | 20.1918 | 253.4801 | 12.5536 | 20.1918 | 0.9914%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 1503 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 254.5346 | 11.6616 | 21.8267 | 254.5346 | 11.6616 | 21.8267 | 282.4616 | 12.9411 | 21.8267 | 0.9849%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 1232 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 240.8882 | 9.5589 | 25.2003 | 240.8882 | 9.5589 | 25.2003 | 267.3178 | 10.6077 | 25.2003 | 0.9916%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 1991 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 141.5109 | 15.4479 | 9.1605 | 141.5109 | 15.4479 | 9.1605 | 157.0372 | 17.1428 | 9.1605 | 0.9745%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 43 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14198 | 0.33363 | 0.42555 | 0.14198 | 0.33363 | 0.42555 | 0.15755 | 0.37024 | 0.42555 | 0.8684%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.031422 | 0.19397 | 0.16199 | 0.031422 | 0.19397 | 0.16199 | 0.034869 | 0.21525 | 0.16199 | 0.1275%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.019984 | 0.031036 | 0.6439 | 0.019984 | 0.031036 | 0.6439 | 0.022176 | 0.034441 | 0.6439 | 0.3435%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 19 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.5975 | 0.14742 | 44.7533 | 6.5975 | 0.14742 | 44.7533 | 7.3213 | 0.16359 | 44.7533 | 0.9924%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 140 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.8584 | 1.0862 | 7.2345 | 7.8584 | 1.0862 | 7.2345 | 8.7207 | 1.2054 | 7.2345 | 0.9393%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 37 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1281 | 0.28708 | 3.9294 | 1.1281 | 0.28708 | 3.9294 | 1.2518 | 0.31858 | 3.9294 | 0.8802%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 600 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 53.4767 | 4.6553 | 11.4872 | 53.4767 | 4.6553 | 11.4872 | 59.3441 | 5.1661 | 11.4872 | 0.9962%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 661 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 45.2456 | 5.1286 | 8.8222 | 45.2456 | 5.1286 | 8.8222 | 50.2098 | 5.6913 | 8.8222 | 0.9962%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 315 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 22.8419 | 2.444 | 9.3459 | 22.8419 | 2.444 | 9.3459 | 25.3481 | 2.7122 | 9.3459 | 0.9984%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 124 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.85678 | 0.9621 | 0.89053 | 0.85678 | 0.9621 | 0.89053 | 0.95078 | 1.0677 | 0.89053 | 0.9877%
2027 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 0.54035 | 0 | 0 | 0.54035 | 0 | 0.49171 | 0.0077589 | 63.3734 | 0.49171 | 0.0077589 | 63.3734 | 0.54566 | 0.0086102 | 63.3734 | 0.9875%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 22 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 19.4557 | 0.1707 | 113.9792 | 19.4557 | 0.1707 | 113.9792 | 21.5904 | 0.18942 | 113.9792 | 0.9968%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 102 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 38.4457 | 0.79141 | 48.5791 | 38.4457 | 0.79141 | 48.5791 | 42.6639 | 0.87824 | 48.5791 | 0.9992%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 57 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.5858 | 0.44226 | 8.1079 | 3.5858 | 0.44226 | 8.1079 | 3.9792 | 0.49078 | 8.1079 | 0.945%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 53 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.1314 | 0.41122 | 17.3419 | 7.1314 | 0.41122 | 17.3419 | 7.9138 | 0.45634 | 17.3419 | 0.994%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 1839 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 38.673 | 14.2686 | 2.7104 | 38.673 | 14.2686 | 2.7104 | 42.9161 | 15.8341 | 2.7104 | 0.9112%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 21 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 1.9283 | 0.16294 | 11.8347 | 1.9283 | 0.16294 | 11.8347 | 2.1399 | 0.18081 | 11.8347 | 0.8819%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 23 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.8164 | 0.17845 | 10.1785 | 1.8164 | 0.17845 | 10.1785 | 2.0157 | 0.19803 | 10.1785 | 0.9662%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 9 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.2059 | 0.06983 | 31.5898 | 2.2059 | 0.06983 | 31.5898 | 2.4479 | 0.077491 | 31.5898 | 0.9775%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 149 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 35.4566 | 1.1561 | 30.6699 | 35.4566 | 1.1561 | 30.6699 | 39.3468 | 1.2829 | 30.6699 | 0.9826%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 224 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 91.7746 | 1.738 | 52.805 | 91.7746 | 1.738 | 52.805 | 101.8439 | 1.9287 | 52.805 | 0.9977%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 469 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 93.0711 | 3.6389 | 25.5766 | 93.0711 | 3.6389 | 25.5766 | 103.2827 | 4.0382 | 25.5766 | 0.9908%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 78 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 54.7545 | 0.60519 | 90.4744 | 54.7545 | 0.60519 | 90.4744 | 60.762 | 0.67159 | 90.4744 | 0.9788%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 54 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 19.0873 | 0.41898 | 45.5566 | 19.0873 | 0.41898 | 45.5566 | 21.1815 | 0.46495 | 45.5566 | 0.9469%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 327 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 76.3476 | 2.5372 | 30.0918 | 76.3476 | 2.5372 | 30.0918 | 84.7243 | 2.8155 | 30.0918 | 0.9648%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 133 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.9788 | 1.0319 | 13.5462 | 13.9788 | 1.0319 | 13.5462 | 15.5125 | 1.1452 | 13.5462 | 0.9856%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 440 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 31.901 | 3.4139 | 9.3444 | 31.901 | 3.4139 | 9.3444 | 35.4011 | 3.7885 | 9.3444 | 0.9842%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 759 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 26.5819 | 5.889 | 4.5138 | 26.5819 | 5.889 | 4.5138 | 29.4984 | 6.5351 | 4.5138 | 0.979%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 12.4803 | 0.71382 | 17.4838 | 12.4803 | 0.71382 | 17.4838 | 13.8496 | 0.79214 | 17.4838 | 0.9892%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 550 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 38.6065 | 4.2674 | 9.0469 | 38.6065 | 4.2674 | 9.0469 | 42.8424 | 4.7356 | 9.0469 | 0.9866%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 6 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.732 | 0.046553 | 80.1659 | 3.732 | 0.046553 | 80.1659 | 4.1414 | 0.051661 | 80.1659 | 0.9965%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 63 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.1418 | 0.48881 | 8.4733 | 4.1418 | 0.48881 | 8.4733 | 4.5962 | 0.54244 | 8.4733 | 0.9977%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 115 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.6502 | 0.89227 | 11.936 | 10.6502 | 0.89227 | 11.936 | 11.8187 | 0.99017 | 11.936 | 0.9935%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 18 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.4325 | 0.13966 | 10.2573 | 1.4325 | 0.13966 | 10.2573 | 1.5897 | 0.15498 | 10.2573 | 0.9948%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 150 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.9301 | 1.1638 | 14.5469 | 16.9301 | 1.1638 | 14.5469 | 18.7877 | 1.2915 | 14.5469 | 0.9905%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 104 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 54.3399 | 0.80692 | 67.3421 | 54.3399 | 0.80692 | 67.3421 | 60.302 | 0.89546 | 67.3421 | 0.9304%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 164 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 58.631 | 1.2725 | 46.077 | 58.631 | 1.2725 | 46.077 | 65.0638 | 1.4121 | 46.077 | 0.9454%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 908 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 106.1245 | 7.0451 | 15.0637 | 106.1245 | 7.0451 | 15.0637 | 117.7682 | 7.818 | 15.0637 | 0.9926%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 355 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 32.9139 | 2.7544 | 11.9496 | 32.9139 | 2.7544 | 11.9496 | 36.5251 | 3.0566 | 11.9496 | 0.9815%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.5188 | 0.38794 | 9.0703 | 3.5188 | 0.38794 | 9.0703 | 3.9048 | 0.43051 | 9.0703 | 0.9046%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 14 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 18.4141 | 0.10862 | 169.521 | 18.4141 | 0.10862 | 169.521 | 20.4345 | 0.12054 | 169.521 | 0.8554%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 217 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 39.2397 | 1.6837 | 23.306 | 39.2397 | 1.6837 | 23.306 | 43.545 | 1.8684 | 23.306 | 0.9867%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.52959 | 0.031036 | 17.064 | 0.52959 | 0.031036 | 17.064 | 0.58769 | 0.034441 | 17.064 | 0.9994%
2027 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.015518 | 0 | 0 | 0.015518 | 0 | 0 | 0.01722 | 0 | 0%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 153 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 144.1626 | 1.1871 | 121.4401 | 144.1626 | 1.1871 | 121.4401 | 159.9798 | 1.3174 | 121.4401 | 0.9909%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 315 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 73.6943 | 2.444 | 30.1526 | 73.6943 | 2.444 | 30.1526 | 81.7799 | 2.7122 | 30.1526 | 0.9925%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 756 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 335.2263 | 5.8657 | 57.1501 | 335.2263 | 5.8657 | 57.1501 | 372.0065 | 6.5093 | 57.1501 | 0.9936%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 10 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.067341 | 0.077589 | 0.86792 | 0.067341 | 0.077589 | 0.86792 | 0.07473 | 0.086102 | 0.86792 | 0.895%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 121 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.3406 | 0.93882 | 3.5583 | 3.3406 | 0.93882 | 3.5583 | 3.7072 | 1.0418 | 3.5583 | 0.8771%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 985 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 46.3352 | 7.6425 | 6.0628 | 46.3352 | 7.6425 | 6.0628 | 51.419 | 8.481 | 6.0628 | 0.9246%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 107 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 27.5199 | 0.8302 | 33.1485 | 27.5199 | 0.8302 | 33.1485 | 30.5393 | 0.92129 | 33.1485 | 0.9907%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 308 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 34.9145 | 2.3897 | 14.6102 | 34.9145 | 2.3897 | 14.6102 | 38.7452 | 2.6519 | 14.6102 | 0.9899%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 354 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 27.3993 | 2.7466 | 9.9756 | 27.3993 | 2.7466 | 9.9756 | 30.4055 | 3.048 | 9.9756 | 0.9527%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 890 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 15.2942 | 6.9054 | 2.2148 | 15.2942 | 6.9054 | 2.2148 | 16.9722 | 7.663 | 2.2148 | 0.8154%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 325 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.1452 | 2.5216 | 6.4027 | 16.1452 | 2.5216 | 6.4027 | 17.9167 | 2.7983 | 6.4027 | 0.9501%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 1376 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 165.5087 | 10.6762 | 15.5026 | 165.5087 | 10.6762 | 15.5026 | 183.6679 | 11.8476 | 15.5026 | 0.97%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 675 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 36.3343 | 5.2372 | 6.9377 | 36.3343 | 5.2372 | 6.9377 | 40.3209 | 5.8119 | 6.9377 | 0.991%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 215 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.0463 | 1.6682 | 10.2186 | 17.0463 | 1.6682 | 10.2186 | 18.9166 | 1.8512 | 10.2186 | 0.7065%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 778 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 38.9182 | 6.0364 | 6.4473 | 38.9182 | 6.0364 | 6.4473 | 43.1883 | 6.6987 | 6.4473 | 0.9752%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 973 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 50.6068 | 7.5494 | 6.7034 | 50.6068 | 7.5494 | 6.7034 | 56.1593 | 8.3777 | 6.7034 | 0.9686%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 237 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.0694 | 1.8389 | 3.3006 | 6.0694 | 1.8389 | 3.3006 | 6.7353 | 2.0406 | 3.3006 | 0.7976%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 689 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 103.5696 | 5.3459 | 19.3738 | 103.5696 | 5.3459 | 19.3738 | 114.9331 | 5.9324 | 19.3738 | 0.9877%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 37.3556 | 2.7699 | 13.4862 | 37.3556 | 2.7699 | 13.4862 | 41.4542 | 3.0738 | 13.4862 | 0.981%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 832 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 88.9924 | 6.4554 | 13.7857 | 88.9924 | 6.4554 | 13.7857 | 98.7564 | 7.1637 | 13.7857 | 0.9713%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 33 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.4896 | 0.25604 | 9.7233 | 2.4896 | 0.25604 | 9.7233 | 2.7627 | 0.28414 | 9.7233 | 0.6764%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 285 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 30.2493 | 2.2113 | 13.6795 | 30.2493 | 2.2113 | 13.6795 | 33.5682 | 2.4539 | 13.6795 | 0.9774%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 475 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 43.8683 | 3.6855 | 11.9031 | 43.8683 | 3.6855 | 11.9031 | 48.6815 | 4.0898 | 11.9031 | 0.977%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 1095 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 116.04 | 8.496 | 13.6582 | 116.04 | 8.496 | 13.6582 | 128.7717 | 9.4281 | 13.6582 | 0.968%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.2848 | 0.62847 | 21.1383 | 13.2848 | 0.62847 | 21.1383 | 14.7424 | 0.69742 | 21.1383 | 0.8924%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 37 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 21.0957 | 0.28708 | 73.4842 | 21.0957 | 0.28708 | 73.4842 | 23.4103 | 0.31858 | 73.4842 | 0.7823%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 8 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.39517 | 0.062071 | 6.3665 | 0.39517 | 0.062071 | 6.3665 | 0.43853 | 0.068881 | 6.3665 | 0.9121%
2027 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 9 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0012779 | 0 | 0 | 0.0012779 | 0 | 0.0011628 | 0.06983 | 0.016652 | 0.0011628 | 0.06983 | 0.016652 | 0.0012904 | 0.077491 | 0.016652 | 0.1338%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 606 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 102.2536 | 4.7019 | 21.7474 | 102.2536 | 4.7019 | 21.7474 | 113.4727 | 5.2178 | 21.7474 | 0.9429%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 22 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 17.6009 | 0.1707 | 103.1128 | 17.6009 | 0.1707 | 103.1128 | 19.532 | 0.18942 | 103.1128 | 0.9974%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 424 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 38.1899 | 3.2898 | 11.6087 | 38.1899 | 3.2898 | 11.6087 | 42.38 | 3.6507 | 11.6087 | 0.9922%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 24 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 5.9162 | 0.18621 | 31.771 | 5.9162 | 0.18621 | 31.771 | 6.5653 | 0.20664 | 31.771 | 0.9914%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 101 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.9074 | 0.78365 | 2.434 | 1.9074 | 0.78365 | 2.434 | 2.1166 | 0.86963 | 2.434 | 0.6623%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 185 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.1889 | 1.4354 | 2.2216 | 3.1889 | 1.4354 | 2.2216 | 3.5387 | 1.5929 | 2.2216 | 0.7437%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 536 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 14.4213 | 4.1588 | 3.4677 | 14.4213 | 4.1588 | 3.4677 | 16.0036 | 4.615 | 3.4677 | 0.9193%
2027 | 196 | 196-43F | Tier-2 | Tier-2---17 | Tier-2---9 | 5 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.048193 | 0 | 0 | 0.048193 | 0 | 0.043855 | 0.038794 | 1.1304 | 0.043855 | 0.038794 | 1.1304 | 0.048666 | 0.043051 | 1.1304 | 0.0514%
2027 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 3 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.6591 | 0.023277 | 71.2765 | 1.6591 | 0.023277 | 71.2765 | 1.8411 | 0.02583 | 71.2765 | 0.9934%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 19 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.058051 | 0.14742 | 0.39378 | 0.058051 | 0.14742 | 0.39378 | 0.06442 | 0.16359 | 0.39378 | 0.9638%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 85 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.4596 | 0.6595 | 12.8272 | 8.4596 | 0.6595 | 12.8272 | 9.3877 | 0.73186 | 12.8272 | 0.9553%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 266 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.3008 | 2.0639 | 2.0839 | 4.3008 | 2.0639 | 2.0839 | 4.7727 | 2.2903 | 2.0839 | 0.9636%
2027 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 11 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 1.2217 | 0 | 0 | 1.2217 | 0 | 1.1118 | 0.085348 | 13.0263 | 1.1118 | 0.085348 | 13.0263 | 1.2337 | 0.094712 | 13.0263 | 0.9852%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 85 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 11.614 | 0.6595 | 17.6102 | 11.614 | 0.6595 | 17.6102 | 12.8883 | 0.73186 | 17.6102 | 0.9978%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 346 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 27.0186 | 2.6846 | 10.0644 | 27.0186 | 2.6846 | 10.0644 | 29.9831 | 2.9791 | 10.0644 | 0.9975%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1409 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 76.8107 | 10.9323 | 7.0261 | 76.8107 | 10.9323 | 7.0261 | 85.2382 | 12.1317 | 7.0261 | 0.9974%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 205 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.0842 | 1.5906 | 2.5678 | 4.0842 | 1.5906 | 2.5678 | 4.5324 | 1.7651 | 2.5678 | 0.901%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 361 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.0972 | 2.801 | 2.8909 | 8.0972 | 2.801 | 2.8909 | 8.9856 | 3.1083 | 2.8909 | 0.8573%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 238 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.094 | 1.8466 | 0.59243 | 1.094 | 1.8466 | 0.59243 | 1.214 | 2.0492 | 0.59243 | 0.7047%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 182 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.4697 | 1.4121 | 1.0408 | 1.4697 | 1.4121 | 1.0408 | 1.6309 | 1.5671 | 1.0408 | 0.5082%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 427 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.7688 | 3.313 | 2.9486 | 9.7688 | 3.313 | 2.9486 | 10.8406 | 3.6765 | 2.9486 | 0.8949%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 305 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.8754 | 2.3665 | 5.8633 | 13.8754 | 2.3665 | 5.8633 | 15.3977 | 2.6261 | 5.8633 | 0.8426%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 1226 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 15.667 | 9.5124 | 1.647 | 15.667 | 9.5124 | 1.647 | 17.386 | 10.5561 | 1.647 | 0.9106%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 384 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.1003 | 2.9794 | 5.0682 | 15.1003 | 2.9794 | 5.0682 | 16.7571 | 3.3063 | 5.0682 | 0.9543%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 260 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 13.5718 | 2.0173 | 6.7277 | 13.5718 | 2.0173 | 6.7277 | 15.0609 | 2.2386 | 6.7277 | 0.9497%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 43 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.4971 | 0.33363 | 16.4767 | 5.4971 | 0.33363 | 16.4767 | 6.1003 | 0.37024 | 16.4767 | 0.9907%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 1745 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 44.1009 | 13.5392 | 3.2573 | 44.1009 | 13.5392 | 3.2573 | 48.9396 | 15.0247 | 3.2573 | 0.9915%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 25 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.2803 | 0.19397 | 58.1541 | 11.2803 | 0.19397 | 58.1541 | 12.5179 | 0.21525 | 58.1541 | 0.9792%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 678 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.7819 | 5.2605 | 1.6694 | 8.7819 | 5.2605 | 1.6694 | 9.7454 | 5.8377 | 1.6694 | 0.9662%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 66 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.3089 | 0.51209 | 4.5088 | 2.3089 | 0.51209 | 4.5088 | 2.5622 | 0.56827 | 4.5088 | 0.9706%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 209 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.1223 | 1.6216 | 8.0921 | 13.1223 | 1.6216 | 8.0921 | 14.562 | 1.7995 | 8.0921 | 0.9727%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 425 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 24.0425 | 3.2975 | 7.2911 | 24.0425 | 3.2975 | 7.2911 | 26.6803 | 3.6593 | 7.2911 | 0.9578%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 108 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.1807 | 0.83796 | 10.956 | 9.1807 | 0.83796 | 10.956 | 10.1879 | 0.9299 | 10.956 | 0.9712%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 113 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.9338 | 0.87675 | 1.0651 | 0.9338 | 0.87675 | 1.0651 | 1.0363 | 0.97295 | 1.0651 | 0.9778%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 164 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 19.4357 | 1.2725 | 15.2742 | 19.4357 | 1.2725 | 15.2742 | 21.5682 | 1.4121 | 15.2742 | 0.9872%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 120 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.0944 | 0.93107 | 14.0639 | 13.0944 | 0.93107 | 14.0639 | 14.5311 | 1.0332 | 14.0639 | 0.9782%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 1826 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 236.5383 | 14.1677 | 16.6956 | 236.5383 | 14.1677 | 16.6956 | 262.4908 | 15.7222 | 16.6956 | 0.9891%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 979 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 60.3082 | 7.5959 | 7.9395 | 60.3082 | 7.5959 | 7.9395 | 66.9251 | 8.4294 | 7.9395 | 0.9941%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 1960 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.2902 | 15.2074 | 0.28211 | 4.2902 | 15.2074 | 0.28211 | 4.7609 | 16.8759 | 0.28211 | 0.974%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 966 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.5637 | 7.4951 | 0.47548 | 3.5637 | 7.4951 | 0.47548 | 3.9547 | 8.3174 | 0.47548 | 0.9786%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 515 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.6112 | 3.9958 | 1.154 | 4.6112 | 3.9958 | 1.154 | 5.1171 | 4.4342 | 1.154 | 0.9871%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 19.9133 | 2.4673 | 8.0708 | 19.9133 | 2.4673 | 8.0708 | 22.0981 | 2.738 | 8.0708 | 0.9909%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 1448 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 13.4254 | 11.2349 | 1.195 | 13.4254 | 11.2349 | 1.195 | 14.8984 | 12.4675 | 1.195 | 0.8569%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 654 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 201.8812 | 5.0743 | 39.785 | 201.8812 | 5.0743 | 39.785 | 224.0311 | 5.631 | 39.785 | 0.9924%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 757 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 113.526 | 5.8735 | 19.3286 | 113.526 | 5.8735 | 19.3286 | 125.9818 | 6.5179 | 19.3286 | 0.9821%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 414 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 175.5743 | 3.2122 | 54.659 | 175.5743 | 3.2122 | 54.659 | 194.8379 | 3.5646 | 54.659 | 0.99%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 153 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.6078 | 1.1871 | 10.6206 | 12.6078 | 1.1871 | 10.6206 | 13.9911 | 1.3174 | 10.6206 | 0.9809%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 308 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 48.9203 | 2.3897 | 20.471 | 48.9203 | 2.3897 | 20.471 | 54.2878 | 2.6519 | 20.471 | 0.9892%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 489 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 126.7327 | 3.7941 | 33.4026 | 126.7327 | 3.7941 | 33.4026 | 140.6375 | 4.2104 | 33.4026 | 0.9919%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 10 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.648 | 0.077589 | 8.3518 | 0.648 | 0.077589 | 8.3518 | 0.7191 | 0.086102 | 8.3518 | 0.999%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 951 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 16.3491 | 7.3787 | 2.2157 | 16.3491 | 7.3787 | 2.2157 | 18.1429 | 8.1883 | 2.2157 | 0.8922%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 793 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 21.8049 | 6.1528 | 3.5439 | 21.8049 | 6.1528 | 3.5439 | 24.1973 | 6.8279 | 3.5439 | 0.8785%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 1095 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 95.9693 | 8.496 | 11.2959 | 95.9693 | 8.496 | 11.2959 | 106.4988 | 9.4281 | 11.2959 | 0.9868%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 874 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 31.5024 | 6.7813 | 4.6455 | 31.5024 | 6.7813 | 4.6455 | 34.9588 | 7.5253 | 4.6455 | 0.9466%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 976 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.8972 | 7.5727 | 1.5711 | 11.8972 | 7.5727 | 1.5711 | 13.2025 | 8.4035 | 1.5711 | 0.9088%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 282 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 91.1879 | 2.188 | 41.6763 | 91.1879 | 2.188 | 41.6763 | 101.1929 | 2.4281 | 41.6763 | 0.9905%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 169 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 19.2748 | 1.3113 | 14.6995 | 19.2748 | 1.3113 | 14.6995 | 21.3895 | 1.4551 | 14.6995 | 0.9634%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 992 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.7722 | 7.6968 | 1.9193 | 14.7722 | 7.6968 | 1.9193 | 16.393 | 8.5413 | 1.9193 | 0.8429%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 3231 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 29.1603 | 25.0689 | 1.1632 | 29.1603 | 25.0689 | 1.1632 | 32.3597 | 27.8194 | 1.1632 | 0.8937%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 155 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 33.5564 | 1.2026 | 27.9026 | 33.5564 | 1.2026 | 27.9026 | 37.2381 | 1.3346 | 27.9026 | 0.9991%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 1090 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 27.4264 | 8.4572 | 3.243 | 27.4264 | 8.4572 | 3.243 | 30.4355 | 9.3851 | 3.243 | 0.9216%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 1687 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 23.9276 | 13.0892 | 1.828 | 23.9276 | 13.0892 | 1.828 | 26.5529 | 14.5253 | 1.828 | 0.9611%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 17 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.4289 | 0.1319 | 48.7401 | 6.4289 | 0.1319 | 48.7401 | 7.1342 | 0.14637 | 48.7401 | 0.9946%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 1158 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 34.741 | 8.9848 | 3.8666 | 34.741 | 8.9848 | 3.8666 | 38.5527 | 9.9706 | 3.8666 | 0.9703%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 157 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.96674 | 1.2181 | 0.79362 | 0.96674 | 1.2181 | 0.79362 | 1.0728 | 1.3518 | 0.79362 | 0.334%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 18.6124 | 0.87675 | 21.2287 | 18.6124 | 0.87675 | 21.2287 | 20.6545 | 0.97295 | 21.2287 | 0.9951%
2027 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 7 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 35.4849 | 0.054312 | 653.3518 | 35.4849 | 0.054312 | 653.3518 | 39.3783 | 0.060271 | 653.3518 | 0.9988%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 353 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.5498 | 2.7389 | 2.0263 | 5.5498 | 2.7389 | 2.0263 | 6.1587 | 3.0394 | 2.0263 | 0.9868%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 367 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 40.5593 | 2.8475 | 14.2438 | 40.5593 | 2.8475 | 14.2438 | 45.0094 | 3.1599 | 14.2438 | 0.9945%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 163 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 20.4866 | 1.2647 | 16.1988 | 20.4866 | 1.2647 | 16.1988 | 22.7343 | 1.4035 | 16.1988 | 0.9686%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 169 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 87.1653 | 1.3113 | 66.4749 | 87.1653 | 1.3113 | 66.4749 | 96.7288 | 1.4551 | 66.4749 | 0.9959%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 514 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.7708 | 3.9881 | 2.9515 | 11.7708 | 3.9881 | 2.9515 | 13.0623 | 4.4256 | 2.9515 | 0.9515%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 2343 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 65.1242 | 18.1791 | 3.5824 | 65.1242 | 18.1791 | 3.5824 | 72.2695 | 20.1736 | 3.5824 | 0.9662%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 676 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 715.269 | 5.245 | 136.3715 | 715.269 | 5.245 | 136.3715 | 793.7467 | 5.8205 | 136.3715 | 0.9925%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 32.6952 | 0.10087 | 324.1468 | 32.6952 | 0.10087 | 324.1468 | 36.2824 | 0.11193 | 324.1468 | 0.9927%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 375 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 408.9425 | 2.9096 | 140.5504 | 408.9425 | 2.9096 | 140.5504 | 453.8108 | 3.2288 | 140.5504 | 0.9963%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 36 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.2745 | 0.27932 | 8.143 | 2.2745 | 0.27932 | 8.143 | 2.5241 | 0.30997 | 8.143 | 0.8656%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 1345 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 64.9142 | 10.4357 | 6.2204 | 64.9142 | 10.4357 | 6.2204 | 72.0364 | 11.5807 | 6.2204 | 0.9605%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 192 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 44.1572 | 1.4897 | 29.6416 | 44.1572 | 1.4897 | 29.6416 | 49.0021 | 1.6532 | 29.6416 | 0.9985%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 3380 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 147.5821 | 26.225 | 5.6275 | 147.5821 | 26.225 | 5.6275 | 163.7745 | 29.1024 | 5.6275 | 0.967%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.15542 | 0.038794 | 4.0062 | 0.15542 | 0.038794 | 4.0062 | 0.17247 | 0.043051 | 4.0062 | 0.9833%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.5515 | 0.046553 | 33.3285 | 1.5515 | 0.046553 | 33.3285 | 1.7218 | 0.051661 | 33.3285 | 0.9937%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 997 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 17.2908 | 7.7356 | 2.2352 | 17.2908 | 7.7356 | 2.2352 | 19.188 | 8.5843 | 2.2352 | 0.9498%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 1487 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 57.1262 | 11.5375 | 4.9514 | 57.1262 | 11.5375 | 4.9514 | 63.3939 | 12.8033 | 4.9514 | 0.9826%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 942 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 17.1775 | 7.3089 | 2.3502 | 17.1775 | 7.3089 | 2.3502 | 19.0622 | 8.1108 | 2.3502 | 0.9106%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 284 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.8545 | 2.2035 | 1.7492 | 3.8545 | 2.2035 | 1.7492 | 4.2774 | 2.4453 | 1.7492 | 0.7897%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 133 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.0473 | 1.0319 | 6.8293 | 7.0473 | 1.0319 | 6.8293 | 7.8205 | 1.1452 | 6.8293 | 0.9819%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 791 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 30.8736 | 6.1373 | 5.0305 | 30.8736 | 6.1373 | 5.0305 | 34.261 | 6.8106 | 5.0305 | 0.9768%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 14 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0289 | 0.10862 | 9.4719 | 1.0289 | 0.10862 | 9.4719 | 1.1418 | 0.12054 | 9.4719 | 0.9298%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 110 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.4554 | 0.85348 | 1.7052 | 1.4554 | 0.85348 | 1.7052 | 1.6151 | 0.94712 | 1.7052 | 0.8171%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 1015 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 24.429 | 7.8753 | 3.102 | 24.429 | 7.8753 | 3.102 | 27.1093 | 8.7393 | 3.102 | 0.983%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 3357 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 46.1751 | 26.0466 | 1.7728 | 46.1751 | 26.0466 | 1.7728 | 51.2413 | 28.9043 | 1.7728 | 0.9868%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.00047048 | 0.046553 | 0.010106 | 0.00047048 | 0.046553 | 0.010106 | 0.0005221 | 0.051661 | 0.010106 | 0.004523%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 1436 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 27.3047 | 11.1418 | 2.4507 | 27.3047 | 11.1418 | 2.4507 | 30.3005 | 12.3642 | 2.4507 | 0.9884%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 475 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.3838 | 3.6855 | 1.7321 | 6.3838 | 3.6855 | 1.7321 | 7.0842 | 4.0898 | 1.7321 | 0.9757%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 392 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.8693 | 3.0415 | 1.2722 | 3.8693 | 3.0415 | 1.2722 | 4.2938 | 3.3752 | 1.2722 | 0.9496%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 870 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 18.3049 | 6.7502 | 2.7117 | 18.3049 | 6.7502 | 2.7117 | 20.3133 | 7.4908 | 2.7117 | 0.859%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 1397 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 44.7034 | 10.8392 | 4.1243 | 44.7034 | 10.8392 | 4.1243 | 49.6082 | 12.0284 | 4.1243 | 0.9946%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 250 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 35.2843 | 1.9397 | 18.1904 | 35.2843 | 1.9397 | 18.1904 | 39.1556 | 2.1525 | 18.1904 | 0.8863%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 738 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 211.9523 | 5.7261 | 37.0154 | 211.9523 | 5.7261 | 37.0154 | 235.2072 | 6.3543 | 37.0154 | 0.9837%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 814 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 87.3211 | 6.3157 | 13.826 | 87.3211 | 6.3157 | 13.826 | 96.9018 | 7.0087 | 13.826 | 0.9873%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 270 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 24.9907 | 2.0949 | 11.9293 | 24.9907 | 2.0949 | 11.9293 | 27.7326 | 2.3247 | 11.9293 | 0.9726%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 156 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 20.2852 | 1.2104 | 16.7593 | 20.2852 | 1.2104 | 16.7593 | 22.5108 | 1.3432 | 16.7593 | 0.9861%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 513 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 47.5862 | 3.9803 | 11.9554 | 47.5862 | 3.9803 | 11.9554 | 52.8073 | 4.417 | 11.9554 | 0.9807%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 985 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 189.9659 | 7.6425 | 24.8565 | 189.9659 | 7.6425 | 24.8565 | 210.8085 | 8.481 | 24.8565 | 0.9836%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 252 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 61.6836 | 1.9552 | 31.5479 | 61.6836 | 1.9552 | 31.5479 | 68.4514 | 2.1698 | 31.5479 | 0.9784%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 32.8705 | 0.86899 | 37.8259 | 32.8705 | 0.86899 | 37.8259 | 36.477 | 0.96434 | 37.8259 | 0.994%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 316 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 255.3789 | 2.4518 | 104.1595 | 255.3789 | 2.4518 | 104.1595 | 283.3985 | 2.7208 | 104.1595 | 0.9934%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 996 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 243.7006 | 7.7278 | 31.5354 | 243.7006 | 7.7278 | 31.5354 | 270.4388 | 8.5757 | 31.5354 | 0.9889%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 81 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.278 | 0.62847 | 6.8071 | 4.278 | 0.62847 | 6.8071 | 4.7474 | 0.69742 | 6.8071 | 0.7089%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 22.7545 | 0.27156 | 83.7915 | 22.7545 | 0.27156 | 83.7915 | 25.251 | 0.30136 | 83.7915 | 0.9883%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 1029 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 278.6354 | 7.9839 | 34.8997 | 278.6354 | 7.9839 | 34.8997 | 309.2066 | 8.8599 | 34.8997 | 0.9911%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 1238 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 589.8137 | 9.6055 | 61.4038 | 589.8137 | 9.6055 | 61.4038 | 654.5266 | 10.6594 | 61.4038 | 0.9893%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 725 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.6786 | 5.6252 | 1.365 | 7.6786 | 5.6252 | 1.365 | 8.5211 | 6.2424 | 1.365 | 0.9808%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 131 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.233 | 1.0164 | 14.0032 | 14.233 | 1.0164 | 14.0032 | 15.7947 | 1.1279 | 14.0032 | 0.9867%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 504 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.7998 | 3.9105 | 2.506 | 9.7998 | 3.9105 | 2.506 | 10.875 | 4.3395 | 2.506 | 0.9646%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 918 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 56.0399 | 7.1227 | 7.8678 | 56.0399 | 7.1227 | 7.8678 | 62.1884 | 7.9041 | 7.8678 | 0.9824%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 635 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.49 | 4.9269 | 1.3173 | 6.49 | 4.9269 | 1.3173 | 7.2021 | 5.4675 | 1.3173 | 0.6927%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 65 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.3828 | 0.50433 | 6.7076 | 3.3828 | 0.50433 | 6.7076 | 3.754 | 0.55966 | 6.7076 | 0.9876%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 257 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.5781 | 1.994 | 5.3049 | 10.5781 | 1.994 | 5.3049 | 11.7387 | 2.2128 | 5.3049 | 0.9838%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 110 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.1078 | 0.85348 | 8.328 | 7.1078 | 0.85348 | 8.328 | 7.8876 | 0.94712 | 8.328 | 0.987%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 98 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.3211 | 0.76037 | 4.3677 | 3.3211 | 0.76037 | 4.3677 | 3.6854 | 0.8438 | 4.3677 | 0.9688%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 971 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 39.5381 | 7.5339 | 5.248 | 39.5381 | 7.5339 | 5.248 | 43.8761 | 8.3605 | 5.248 | 0.9791%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 530 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 33.7387 | 4.1122 | 8.2045 | 33.7387 | 4.1122 | 8.2045 | 37.4405 | 4.5634 | 8.2045 | 0.9907%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 549 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 32.2959 | 4.2596 | 7.5819 | 32.2959 | 4.2596 | 7.5819 | 35.8393 | 4.727 | 7.5819 | 0.9682%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 164 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.7642 | 1.2725 | 4.53 | 5.7642 | 1.2725 | 4.53 | 6.3966 | 1.4121 | 4.53 | 0.6596%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 921 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 29.1399 | 7.1459 | 4.0778 | 29.1399 | 7.1459 | 4.0778 | 32.3371 | 7.93 | 4.0778 | 0.9454%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 333 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 11.4521 | 2.5837 | 4.4324 | 11.4521 | 2.5837 | 4.4324 | 12.7086 | 2.8672 | 4.4324 | 0.9251%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 19 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.93993 | 0.14742 | 6.3759 | 0.93993 | 0.14742 | 6.3759 | 1.0431 | 0.16359 | 6.3759 | 0.9818%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 32.7369 | 4.9734 | 6.5823 | 32.7369 | 4.9734 | 6.5823 | 36.3287 | 5.5191 | 6.5823 | 0.9585%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.39026 | 0.06983 | 5.5887 | 0.39026 | 0.06983 | 5.5887 | 0.43308 | 0.077491 | 5.5887 | 0.8666%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 81 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 47.5288 | 0.62847 | 75.6263 | 47.5288 | 0.62847 | 75.6263 | 52.7435 | 0.69742 | 75.6263 | 0.9855%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 245 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.0881 | 1.9009 | 8.4633 | 16.0881 | 1.9009 | 8.4633 | 17.8533 | 2.1095 | 8.4633 | 0.878%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 4.1304 | 0.031036 | 133.0848 | 4.1304 | 0.031036 | 133.0848 | 4.5835 | 0.034441 | 133.0848 | 0.9431%
2027 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 9 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.37366 | 0.06983 | 5.351 | 0.37366 | 0.06983 | 5.351 | 0.41466 | 0.077491 | 5.351 | 0.9823%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 329 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.6538 | 2.5527 | 1.8231 | 4.6538 | 2.5527 | 1.8231 | 5.1645 | 2.8327 | 1.8231 | 0.9288%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 44 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.023211 | 0.34139 | 0.06799 | 0.023211 | 0.34139 | 0.06799 | 0.025758 | 0.37885 | 0.06799 | 0.7897%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 4.1532 | 0.031036 | 133.82 | 4.1532 | 0.031036 | 133.82 | 4.6088 | 0.034441 | 133.82 | 0.9948%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 129 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.3417 | 1.0009 | 6.336 | 6.3417 | 1.0009 | 6.336 | 7.0375 | 1.1107 | 6.336 | 0.9241%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 249 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.9495 | 1.932 | 10.326 | 19.9495 | 1.932 | 10.326 | 22.1383 | 2.1439 | 10.326 | 0.9107%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 590 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 41.4107 | 4.5777 | 9.0461 | 41.4107 | 4.5777 | 9.0461 | 45.9542 | 5.08 | 9.0461 | 0.9555%
2027 | 308 | 308-485AE | Tier-2 | Tier-2---15 | Tier-2---8 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.043838 | 0 | 0 | 0.043838 | 0 | 0.039892 | 0.038794 | 1.0283 | 0.039892 | 0.038794 | 1.0283 | 0.044268 | 0.043051 | 1.0283 | 0.02775%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 20 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16842 | 0.15518 | 1.0853 | 0.16842 | 0.15518 | 1.0853 | 0.1869 | 0.1722 | 1.0853 | 0.1937%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 4 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.35602 | 0.031036 | 11.4715 | 0.35602 | 0.031036 | 11.4715 | 0.39508 | 0.034441 | 11.4715 | 0.8469%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 32 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.070129 | 0.24828 | 0.28245 | 0.070129 | 0.24828 | 0.28245 | 0.077823 | 0.27553 | 0.28245 | 0.4938%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 26 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.4128 | 0.20173 | 2.0463 | 0.4128 | 0.20173 | 2.0463 | 0.4581 | 0.22386 | 2.0463 | 0.1628%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 262 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.034025 | 2.0328 | 0.016738 | 0.034025 | 2.0328 | 0.016738 | 0.037758 | 2.2559 | 0.016738 | 0.02339%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 38 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0027839 | 0.29484 | 0.009442 | 0.0027839 | 0.29484 | 0.009442 | 0.0030893 | 0.32719 | 0.009442 | 0.001514%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 323 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.9002 | 2.5061 | 0.7582 | 1.9002 | 2.5061 | 0.7582 | 2.1086 | 2.7811 | 0.7582 | 0.995%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.732 | 0.13966 | 19.5615 | 2.732 | 0.13966 | 19.5615 | 3.0317 | 0.15498 | 19.5615 | 0.9927%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 1796 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 31.2978 | 13.9349 | 2.246 | 31.2978 | 13.9349 | 2.246 | 34.7317 | 15.4639 | 2.246 | 0.9548%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 2181 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 123.8786 | 16.9221 | 7.3205 | 123.8786 | 16.9221 | 7.3205 | 137.4703 | 18.7788 | 7.3205 | 0.9814%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 2656 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 49.1654 | 20.6076 | 2.3858 | 49.1654 | 20.6076 | 2.3858 | 54.5597 | 22.8686 | 2.3858 | 0.9699%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 1091 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 122.1654 | 8.4649 | 14.4319 | 122.1654 | 8.4649 | 14.4319 | 135.5691 | 9.3937 | 14.4319 | 0.9928%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 1620 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 100.7847 | 12.5694 | 8.0183 | 100.7847 | 12.5694 | 8.0183 | 111.8425 | 13.9485 | 8.0183 | 0.9888%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 1027 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 212.4003 | 7.9684 | 26.6554 | 212.4003 | 7.9684 | 26.6554 | 235.7044 | 8.8426 | 26.6554 | 0.9925%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 222 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 82.9876 | 1.7225 | 48.1794 | 82.9876 | 1.7225 | 48.1794 | 92.0928 | 1.9115 | 48.1794 | 0.9973%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 1531 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 168.3033 | 11.8788 | 14.1683 | 168.3033 | 11.8788 | 14.1683 | 186.7692 | 13.1822 | 14.1683 | 0.9936%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 1034 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 81.809 | 8.0227 | 10.1972 | 81.809 | 8.0227 | 10.1972 | 90.7849 | 8.9029 | 10.1972 | 0.9749%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 340 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 22.7355 | 2.638 | 8.6184 | 22.7355 | 2.638 | 8.6184 | 25.2299 | 2.9275 | 8.6184 | 0.9918%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 60 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 20.1485 | 0.46553 | 43.2805 | 20.1485 | 0.46553 | 43.2805 | 22.3591 | 0.51661 | 43.2805 | 0.9993%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 143 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.0724 | 1.1095 | 14.4859 | 16.0724 | 1.1095 | 14.4859 | 17.8358 | 1.2313 | 14.4859 | 0.8869%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 150 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 39.0935 | 1.1638 | 33.5903 | 39.0935 | 1.1638 | 33.5903 | 43.3827 | 1.2915 | 33.5903 | 0.943%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 30 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.6596 | 0.23277 | 11.426 | 2.6596 | 0.23277 | 11.426 | 2.9514 | 0.2583 | 11.426 | 0.6284%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 484 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 122.4623 | 3.7553 | 32.6106 | 122.4623 | 3.7553 | 32.6106 | 135.8986 | 4.1673 | 32.6106 | 0.9943%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 1235 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 185.0853 | 9.5822 | 19.3155 | 185.0853 | 9.5822 | 19.3155 | 205.3924 | 10.6336 | 19.3155 | 0.9917%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 29.4362 | 1.8311 | 16.0757 | 29.4362 | 1.8311 | 16.0757 | 32.6658 | 2.032 | 16.0757 | 0.8854%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 587 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 67.231 | 4.5545 | 14.7616 | 67.231 | 4.5545 | 14.7616 | 74.6075 | 5.0542 | 14.7616 | 0.985%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 253 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.357 | 1.963 | 6.295 | 12.357 | 1.963 | 6.295 | 13.7128 | 2.1784 | 6.295 | 0.7994%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 403 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 48.5603 | 3.1268 | 15.5302 | 48.5603 | 3.1268 | 15.5302 | 53.8882 | 3.4699 | 15.5302 | 0.9814%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 1342 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 142.4543 | 10.4124 | 13.6812 | 142.4543 | 10.4124 | 13.6812 | 158.0841 | 11.5548 | 13.6812 | 0.9776%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 1273 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 80.6995 | 9.8771 | 8.1704 | 80.6995 | 9.8771 | 8.1704 | 89.5536 | 10.9607 | 8.1704 | 0.9541%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.2788 | 0.38019 | 29.6666 | 11.2788 | 0.38019 | 29.6666 | 12.5163 | 0.4219 | 29.6666 | 0.9906%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 47 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 46.2497 | 0.36467 | 126.827 | 46.2497 | 0.36467 | 126.827 | 51.3241 | 0.40468 | 126.827 | 0.9968%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 11 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.6371 | 0.085348 | 89.4818 | 7.6371 | 0.085348 | 89.4818 | 8.475 | 0.094712 | 89.4818 | 0.9549%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 484 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 151.6491 | 3.7553 | 40.3827 | 151.6491 | 3.7553 | 40.3827 | 168.2877 | 4.1673 | 40.3827 | 0.9879%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 901 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 156.9706 | 6.9908 | 22.454 | 156.9706 | 6.9908 | 22.454 | 174.193 | 7.7578 | 22.454 | 0.9747%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 1047 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 92.1224 | 8.1235 | 11.3402 | 92.1224 | 8.1235 | 11.3402 | 102.2299 | 9.0148 | 11.3402 | 0.9704%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 712 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 104.6452 | 5.5243 | 18.9426 | 104.6452 | 5.5243 | 18.9426 | 116.1267 | 6.1304 | 18.9426 | 0.9781%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 18 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.3037 | 0.13966 | 37.9758 | 5.3037 | 0.13966 | 37.9758 | 5.8856 | 0.15498 | 37.9758 | 0.9721%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.1945 | 0.45002 | 27.098 | 12.1945 | 0.45002 | 27.098 | 13.5325 | 0.49939 | 27.098 | 0.9966%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 404 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 337.3598 | 3.1346 | 107.6249 | 337.3598 | 3.1346 | 107.6249 | 374.3741 | 3.4785 | 107.6249 | 0.9859%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 66 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.7862 | 0.51209 | 23.0161 | 11.7862 | 0.51209 | 23.0161 | 13.0794 | 0.56827 | 23.0161 | 0.8901%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 79 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5811 | 0.61295 | 2.5794 | 1.5811 | 0.61295 | 2.5794 | 1.7545 | 0.6802 | 2.5794 | 0.1879%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 1637 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 25.1718 | 12.7013 | 1.9818 | 25.1718 | 12.7013 | 1.9818 | 27.9336 | 14.0948 | 1.9818 | 0.8818%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 699 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 16.5372 | 5.4235 | 3.0492 | 16.5372 | 5.4235 | 3.0492 | 18.3516 | 6.0185 | 3.0492 | 0.9783%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 1562 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 57.0772 | 12.1194 | 4.7096 | 57.0772 | 12.1194 | 4.7096 | 63.3396 | 13.4491 | 4.7096 | 0.9847%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 30 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.7938 | 0.23277 | 50.6679 | 11.7938 | 0.23277 | 50.6679 | 13.0878 | 0.2583 | 50.6679 | 0.9597%
2027 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.63991 | 0.0077589 | 82.4741 | 0.63991 | 0.0077589 | 82.4741 | 0.71012 | 0.0086102 | 82.4741 | 0.9953%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 334 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 31.198 | 2.5915 | 12.0388 | 31.198 | 2.5915 | 12.0388 | 34.621 | 2.8758 | 12.0388 | 0.9745%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.8386 | 0.38019 | 12.7269 | 4.8386 | 0.38019 | 12.7269 | 5.3695 | 0.4219 | 12.7269 | 0.9134%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 121 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 42.3621 | 0.93882 | 45.1225 | 42.3621 | 0.93882 | 45.1225 | 47.01 | 1.0418 | 45.1225 | 0.98%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 47.9792 | 0.48881 | 98.1552 | 47.9792 | 0.48881 | 98.1552 | 53.2434 | 0.54244 | 98.1552 | 0.9857%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 889 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.0443 | 6.8976 | 2.3261 | 16.0443 | 6.8976 | 2.3261 | 17.8046 | 7.6544 | 2.3261 | 0.9609%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 34 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.013995 | 0.2638 | 0.053051 | 0.013995 | 0.2638 | 0.053051 | 0.015531 | 0.29275 | 0.053051 | 0.01745%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 637 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.5914 | 4.9424 | 1.3336 | 6.5914 | 4.9424 | 1.3336 | 7.3146 | 5.4847 | 1.3336 | 0.8492%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 642 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.7746 | 4.9812 | 0.55701 | 2.7746 | 4.9812 | 0.55701 | 3.079 | 5.5277 | 0.55701 | 0.5795%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 1846 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 93.1705 | 14.3229 | 6.505 | 93.1705 | 14.3229 | 6.505 | 103.393 | 15.8944 | 6.505 | 0.8848%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 38 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 6.1949 | 0.29484 | 21.0112 | 6.1949 | 0.29484 | 21.0112 | 6.8746 | 0.32719 | 21.0112 | 0.9662%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 44 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.951 | 0.34139 | 14.5024 | 4.951 | 0.34139 | 14.5024 | 5.4942 | 0.37885 | 14.5024 | 0.9893%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 297 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.9446 | 2.3044 | 1.7118 | 3.9446 | 2.3044 | 1.7118 | 4.3774 | 2.5572 | 1.7118 | 0.9131%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 189 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.65617 | 1.4664 | 0.44746 | 0.65617 | 1.4664 | 0.44746 | 0.72816 | 1.6273 | 0.44746 | 0.51%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 9 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 2.9352 | 0.06983 | 42.0335 | 2.9352 | 0.06983 | 42.0335 | 3.2572 | 0.077491 | 42.0335 | 0.9662%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 30.3414 | 1.0087 | 30.0811 | 30.3414 | 1.0087 | 30.0811 | 33.6704 | 1.1193 | 30.0811 | 0.9767%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 529 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.6755 | 4.1044 | 0.8955 | 3.6755 | 4.1044 | 0.8955 | 4.0788 | 4.5548 | 0.8955 | 0.7071%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 353 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 83.235 | 2.7389 | 30.3901 | 83.235 | 2.7389 | 30.3901 | 92.3673 | 3.0394 | 30.3901 | 0.9496%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 203 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 63.4108 | 1.5751 | 40.2595 | 63.4108 | 1.5751 | 40.2595 | 70.3681 | 1.7479 | 40.2595 | 0.9611%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 107 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.9463 | 0.8302 | 15.5942 | 12.9463 | 0.8302 | 15.5942 | 14.3667 | 0.92129 | 15.5942 | 0.8872%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 448 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 92.4716 | 3.476 | 26.603 | 92.4716 | 3.476 | 26.603 | 102.6173 | 3.8574 | 26.603 | 0.9569%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 175 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 13.6213 | 1.3578 | 10.0319 | 13.6213 | 1.3578 | 10.0319 | 15.1158 | 1.5068 | 10.0319 | 0.8473%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 216 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 29.3039 | 1.6759 | 17.4853 | 29.3039 | 1.6759 | 17.4853 | 32.5191 | 1.8598 | 17.4853 | 0.8754%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 296 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 35.4517 | 2.2966 | 15.4364 | 35.4517 | 2.2966 | 15.4364 | 39.3413 | 2.5486 | 15.4364 | 0.8812%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.9618 | 0.21725 | 55.0603 | 11.9618 | 0.21725 | 55.0603 | 13.2742 | 0.24108 | 55.0603 | 0.9724%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 20 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.7378 | 0.15518 | 69.1968 | 10.7378 | 0.15518 | 69.1968 | 11.9159 | 0.1722 | 69.1968 | 0.9739%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 139 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 21.8479 | 1.0785 | 20.258 | 21.8479 | 1.0785 | 20.258 | 24.245 | 1.1968 | 20.258 | 0.9191%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 245 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.7439 | 1.9009 | 5.6519 | 10.7439 | 1.9009 | 5.6519 | 11.9227 | 2.1095 | 5.6519 | 0.557%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 225 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.6094 | 1.7457 | 2.0676 | 3.6094 | 1.7457 | 2.0676 | 4.0054 | 1.9373 | 2.0676 | 0.7618%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 164 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.5415 | 1.2725 | 3.5691 | 4.5415 | 1.2725 | 3.5691 | 5.0398 | 1.4121 | 3.5691 | 0.7912%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 713 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 75.9584 | 5.5321 | 13.7305 | 75.9584 | 5.5321 | 13.7305 | 84.2924 | 6.139 | 13.7305 | 0.9168%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 336 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 47.9898 | 2.607 | 18.4082 | 47.9898 | 2.607 | 18.4082 | 53.2551 | 2.893 | 18.4082 | 0.9343%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 1001 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 55.4184 | 7.7666 | 7.1354 | 55.4184 | 7.7666 | 7.1354 | 61.4988 | 8.6188 | 7.1354 | 0.9049%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 61 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.1969 | 0.47329 | 27.8831 | 13.1969 | 0.47329 | 27.8831 | 14.6448 | 0.52522 | 27.8831 | 0.9697%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 37 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.5023 | 0.28708 | 19.1665 | 5.5023 | 0.28708 | 19.1665 | 6.106 | 0.31858 | 19.1665 | 0.967%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 115 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 47.2842 | 0.89227 | 52.9931 | 47.2842 | 0.89227 | 52.9931 | 52.4721 | 0.99017 | 52.9931 | 0.9877%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 265 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 20.1718 | 2.0561 | 9.8107 | 20.1718 | 2.0561 | 9.8107 | 22.385 | 2.2817 | 9.8107 | 0.9555%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 80 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.6222 | 0.62071 | 4.2244 | 2.6222 | 0.62071 | 4.2244 | 2.9098 | 0.68881 | 4.2244 | 0.9711%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 586 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 74.7143 | 4.5467 | 16.4326 | 74.7143 | 4.5467 | 16.4326 | 82.9117 | 5.0456 | 16.4326 | 0.9923%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 132 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.6876 | 1.0242 | 6.5298 | 6.6876 | 1.0242 | 6.5298 | 7.4213 | 1.1365 | 6.5298 | 0.9277%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 171 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.8144 | 1.3268 | 7.3972 | 9.8144 | 1.3268 | 7.3972 | 10.8912 | 1.4723 | 7.3972 | 0.9525%
2027 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 6 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 1.7471 | 0 | 0 | 1.7471 | 0 | 1.5898 | 0.046553 | 34.1501 | 1.5898 | 0.046553 | 34.1501 | 1.7642 | 0.051661 | 34.1501 | 0.3253%
2027 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 11 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.2474 | 0.085348 | 14.616 | 1.2474 | 0.085348 | 14.616 | 1.3843 | 0.094712 | 14.616 | 0.999%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 5 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 6.2494 | 0 | 0 | 6.2494 | 0 | 5.6869 | 0.038794 | 146.5902 | 5.6869 | 0.038794 | 146.5902 | 6.3108 | 0.043051 | 146.5902 | 0.999%
2027 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 15 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.6464 | 0.11638 | 14.1464 | 1.6464 | 0.11638 | 14.1464 | 1.827 | 0.12915 | 14.1464 | 0.9984%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 373 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 25.6788 | 2.8941 | 8.8729 | 25.6788 | 2.8941 | 8.8729 | 28.4962 | 3.2116 | 8.8729 | 0.9993%
2027 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 52 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.3453 | 0.40346 | 0.85584 | 0.3453 | 0.40346 | 0.85584 | 0.38318 | 0.44773 | 0.85584 | 0.9723%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 277 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 31.2198 | 2.1492 | 14.5262 | 31.2198 | 2.1492 | 14.5262 | 34.6452 | 2.385 | 14.5262 | 0.997%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.77971 | 0.0077589 | 100.4925 | 0.77971 | 0.0077589 | 100.4925 | 0.86526 | 0.0086102 | 100.4925 | 0.9735%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 49 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 12.4192 | 0.38019 | 32.6663 | 12.4192 | 0.38019 | 32.6663 | 13.7819 | 0.4219 | 32.6663 | 0.9902%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 443 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 47.1097 | 3.4372 | 13.7059 | 47.1097 | 3.4372 | 13.7059 | 52.2785 | 3.8143 | 13.7059 | 0.9833%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 878 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 151.376 | 6.8123 | 22.221 | 151.376 | 6.8123 | 22.221 | 167.9846 | 7.5597 | 22.221 | 0.9937%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 108 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 36.7559 | 0.83796 | 43.8636 | 36.7559 | 0.83796 | 43.8636 | 40.7887 | 0.9299 | 43.8636 | 0.9496%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 14 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.5736 | 0.10862 | 14.487 | 1.5736 | 0.10862 | 14.487 | 1.7463 | 0.12054 | 14.487 | 0.216%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 192 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.8503 | 1.4897 | 1.2421 | 1.8503 | 1.4897 | 1.2421 | 2.0533 | 1.6532 | 1.2421 | 0.9963%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 82 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.6436 | 0.63623 | 10.4422 | 6.6436 | 0.63623 | 10.4422 | 7.3725 | 0.70603 | 10.4422 | 0.9951%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 1001 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 26.387 | 7.7666 | 3.3975 | 26.387 | 7.7666 | 3.3975 | 29.2822 | 8.6188 | 3.3975 | 0.9734%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 437 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.1838 | 3.3906 | 3.8883 | 13.1838 | 3.3906 | 3.8883 | 14.6303 | 3.7626 | 3.8883 | 0.9797%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 1143 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 23.2262 | 8.8684 | 2.619 | 23.2262 | 8.8684 | 2.619 | 25.7745 | 9.8414 | 2.619 | 0.9676%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 1286 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 28.8046 | 9.9779 | 2.8868 | 28.8046 | 9.9779 | 2.8868 | 31.965 | 11.0727 | 2.8868 | 0.9272%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 482 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 14.6037 | 3.7398 | 3.905 | 14.6037 | 3.7398 | 3.905 | 16.206 | 4.1501 | 3.905 | 0.9829%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 848 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 59.5224 | 6.5795 | 9.0466 | 59.5224 | 6.5795 | 9.0466 | 66.053 | 7.3014 | 9.0466 | 0.9672%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 593 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.2665 | 4.601 | 1.1446 | 5.2665 | 4.601 | 1.1446 | 5.8443 | 5.1058 | 1.1446 | 0.7734%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 496 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 18.3018 | 3.8484 | 4.7557 | 18.3018 | 3.8484 | 4.7557 | 20.3098 | 4.2706 | 4.7557 | 0.9648%
2027 | 520 | 520-1936 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 0.63566 | 0 | 0 | 0.63566 | 0 | 0.57844 | 0.015518 | 37.2761 | 0.57844 | 0.015518 | 37.2761 | 0.64191 | 0.01722 | 37.2761 | 0.9977%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 188 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.7563 | 1.4587 | 1.2041 | 1.7563 | 1.4587 | 1.2041 | 1.949 | 1.6187 | 1.2041 | 0.7472%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 1385 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 43.8849 | 10.746 | 4.0838 | 43.8849 | 10.746 | 4.0838 | 48.6999 | 11.9251 | 4.0838 | 0.9649%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 640 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 18.1542 | 4.9657 | 3.6559 | 18.1542 | 4.9657 | 3.6559 | 20.1461 | 5.5105 | 3.6559 | 0.9757%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 932 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 99.8685 | 7.2313 | 13.8106 | 99.8685 | 7.2313 | 13.8106 | 110.8258 | 8.0247 | 13.8106 | 0.9669%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 448 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.5913 | 3.476 | 1.8963 | 6.5913 | 3.476 | 1.8963 | 7.3145 | 3.8574 | 1.8963 | 0.8931%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 973 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 75.4437 | 7.5494 | 9.9933 | 75.4437 | 7.5494 | 9.9933 | 83.7212 | 8.3777 | 9.9933 | 0.9779%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 734 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 78.7812 | 5.695 | 13.8334 | 78.7812 | 5.695 | 13.8334 | 87.4249 | 6.3199 | 13.8334 | 0.9936%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 900 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 50.5044 | 6.983 | 7.2325 | 50.5044 | 6.983 | 7.2325 | 56.0457 | 7.7491 | 7.2325 | 0.9878%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 673 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 110.706 | 5.2217 | 21.201 | 110.706 | 5.2217 | 21.201 | 122.8524 | 5.7946 | 21.201 | 0.9938%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 1600 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 81.2357 | 12.4142 | 6.5438 | 81.2357 | 12.4142 | 6.5438 | 90.1487 | 13.7763 | 6.5438 | 0.9905%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.44129 | 0.72158 | 0.61156 | 0.44129 | 0.72158 | 0.61156 | 0.4897 | 0.80075 | 0.61156 | 0.4302%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 79 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.23982 | 0.61295 | 0.39126 | 0.23982 | 0.61295 | 0.39126 | 0.26614 | 0.6802 | 0.39126 | 0.2253%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1898 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 49.4954 | 14.7264 | 3.361 | 49.4954 | 14.7264 | 3.361 | 54.926 | 16.3421 | 3.361 | 0.9644%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 230 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.32484 | 1.7845 | 0.18203 | 0.32484 | 1.7845 | 0.18203 | 0.36048 | 1.9803 | 0.18203 | 0.117%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 486 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 49.6477 | 3.7708 | 13.1663 | 49.6477 | 3.7708 | 13.1663 | 55.0949 | 4.1845 | 13.1663 | 0.9978%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 935 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 102.7516 | 7.2546 | 14.1637 | 102.7516 | 7.2546 | 14.1637 | 114.0253 | 8.0505 | 14.1637 | 0.9977%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 638 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 123.504 | 4.9502 | 24.9495 | 123.504 | 4.9502 | 24.9495 | 137.0546 | 5.4933 | 24.9495 | 0.9899%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 78.6546 | 4.0734 | 19.3093 | 78.6546 | 4.0734 | 19.3093 | 87.2844 | 4.5203 | 19.3093 | 0.982%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 1862 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 363.8583 | 14.447 | 25.1857 | 363.8583 | 14.447 | 25.1857 | 403.78 | 16.0321 | 25.1857 | 0.9903%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 61 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 5.1395 | 0.47329 | 10.8591 | 5.1395 | 0.47329 | 10.8591 | 5.7034 | 0.52522 | 10.8591 | 0.6775%
2027 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 3 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.3895 | 0.023277 | 59.6948 | 1.3895 | 0.023277 | 59.6948 | 1.5419 | 0.02583 | 59.6948 | 0.9944%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 14 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.5576 | 0.10862 | 41.9579 | 4.5576 | 0.10862 | 41.9579 | 5.0577 | 0.12054 | 41.9579 | 0.9632%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.44715 | 0.3026 | 1.4777 | 0.44715 | 0.3026 | 1.4777 | 0.49621 | 0.3358 | 1.4777 | 0.9941%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 1930 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 163.2404 | 14.9746 | 10.9011 | 163.2404 | 14.9746 | 10.9011 | 181.1508 | 16.6176 | 10.9011 | 0.9555%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 2562 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 232.8474 | 19.8782 | 11.7137 | 232.8474 | 19.8782 | 11.7137 | 258.3948 | 22.0592 | 11.7137 | 0.994%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 587 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 22.2363 | 4.5545 | 4.8823 | 22.2363 | 4.5545 | 4.8823 | 24.676 | 5.0542 | 4.8823 | 0.936%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 1265 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 35.6813 | 9.815 | 3.6354 | 35.6813 | 9.815 | 3.6354 | 39.5962 | 10.8919 | 3.6354 | 0.938%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 212 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.9369 | 1.6449 | 3.0014 | 4.9369 | 1.6449 | 3.0014 | 5.4786 | 1.8254 | 3.0014 | 0.8718%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 319 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.7454 | 2.4751 | 5.5535 | 13.7454 | 2.4751 | 5.5535 | 15.2535 | 2.7466 | 5.5535 | 0.9279%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 273 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 54.9037 | 2.1182 | 25.9203 | 54.9037 | 2.1182 | 25.9203 | 60.9276 | 2.3506 | 25.9203 | 0.9729%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 800 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 137.5579 | 6.2071 | 22.1614 | 137.5579 | 6.2071 | 22.1614 | 152.6504 | 6.8881 | 22.1614 | 0.9856%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 258 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 21.9808 | 2.0018 | 10.9806 | 21.9808 | 2.0018 | 10.9806 | 24.3925 | 2.2214 | 10.9806 | 0.9864%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 243 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 51.3459 | 1.8854 | 27.2333 | 51.3459 | 1.8854 | 27.2333 | 56.9795 | 2.0923 | 27.2333 | 0.9841%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 537 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 94.7516 | 4.1665 | 22.7412 | 94.7516 | 4.1665 | 22.7412 | 105.1476 | 4.6237 | 22.7412 | 0.9831%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 483 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 83.1913 | 3.7475 | 22.1989 | 83.1913 | 3.7475 | 22.1989 | 92.3189 | 4.1587 | 22.1989 | 0.9843%
2027 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 1 | 100% | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077589 | 0 | 0 | 0.0077589 | 0 | 0 | 0.0086102 | 0 | 0%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 410 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 28.4668 | 3.1811 | 8.9486 | 28.4668 | 3.1811 | 8.9486 | 31.5901 | 3.5302 | 8.9486 | 0.9977%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 206 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 15.48 | 1.5983 | 9.6851 | 15.48 | 1.5983 | 9.6851 | 17.1784 | 1.7737 | 9.6851 | 0.9957%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 93 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 17.6067 | 0.72158 | 24.4004 | 17.6067 | 0.72158 | 24.4004 | 19.5385 | 0.80075 | 24.4004 | 0.9986%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 730 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.9656 | 5.664 | 3.525 | 19.9656 | 5.664 | 3.525 | 22.1561 | 6.2854 | 3.525 | 0.9923%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 486 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 130.2838 | 3.7708 | 34.5506 | 130.2838 | 3.7708 | 34.5506 | 144.5782 | 4.1845 | 34.5506 | 0.9856%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 34 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 65.2205 | 0.2638 | 247.2329 | 65.2205 | 0.2638 | 247.2329 | 72.3764 | 0.29275 | 247.2329 | 0.9951%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 551 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 78.3924 | 4.2751 | 18.3368 | 78.3924 | 4.2751 | 18.3368 | 86.9934 | 4.7442 | 18.3368 | 0.9433%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 17 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 2.9372 | 0.1319 | 22.2685 | 2.9372 | 0.1319 | 22.2685 | 3.2595 | 0.14637 | 22.2685 | 0.9958%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 153 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 28.2206 | 1.1871 | 23.7726 | 28.2206 | 1.1871 | 23.7726 | 31.317 | 1.3174 | 23.7726 | 0.9258%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 558 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 111.2949 | 4.3295 | 25.7064 | 111.2949 | 4.3295 | 25.7064 | 123.5059 | 4.8045 | 25.7064 | 0.9926%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 846 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 18.5106 | 6.564 | 2.82 | 18.5106 | 6.564 | 2.82 | 20.5416 | 7.2842 | 2.82 | 0.9747%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 565 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.3713 | 4.3838 | 2.3658 | 10.3713 | 4.3838 | 2.3658 | 11.5092 | 4.8647 | 2.3658 | 0.7093%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 86.8821 | 2.8941 | 30.0208 | 86.8821 | 2.8941 | 30.0208 | 96.4146 | 3.2116 | 30.0208 | 0.9829%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 412 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 166.0282 | 3.1967 | 51.9381 | 166.0282 | 3.1967 | 51.9381 | 184.2444 | 3.5474 | 51.9381 | 0.989%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 23.1929 | 0.51209 | 45.2909 | 23.1929 | 0.51209 | 45.2909 | 25.7375 | 0.56827 | 45.2909 | 0.9937%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 433 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 48.5255 | 3.3596 | 14.4438 | 48.5255 | 3.3596 | 14.4438 | 53.8496 | 3.7282 | 14.4438 | 0.9631%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 933 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 166.0224 | 7.239 | 22.9343 | 166.0224 | 7.239 | 22.9343 | 184.2379 | 8.0333 | 22.9343 | 0.9714%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 34 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 26.8212 | 0.2638 | 101.6719 | 26.8212 | 0.2638 | 101.6719 | 29.764 | 0.29275 | 101.6719 | 0.9712%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 415 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 180.4018 | 3.2199 | 56.0265 | 180.4018 | 3.2199 | 56.0265 | 200.1951 | 3.5732 | 56.0265 | 0.9923%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 24 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.1511 | 0.18621 | 6.1815 | 1.1511 | 0.18621 | 6.1815 | 1.2774 | 0.20664 | 6.1815 | 0.9928%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 62 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.11165 | 0.48105 | 0.23209 | 0.11165 | 0.48105 | 0.23209 | 0.1239 | 0.53383 | 0.23209 | 0.9883%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 36 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.2688 | 0.27932 | 4.5426 | 1.2688 | 0.27932 | 4.5426 | 1.4081 | 0.30997 | 4.5426 | 0.9963%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 9 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.060511 | 0.06983 | 0.86655 | 0.060511 | 0.06983 | 0.86655 | 0.06715 | 0.077491 | 0.86655 | 0.9902%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 13 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.9878 | 0.10087 | 29.6217 | 2.9878 | 0.10087 | 29.6217 | 3.3156 | 0.11193 | 29.6217 | 0.9939%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 241 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.0456 | 1.8699 | 1.094 | 2.0456 | 1.8699 | 1.094 | 2.27 | 2.075 | 1.094 | 0.9666%
2027 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 1 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 1.8833 | 0 | 0 | 1.8833 | 0 | 1.7138 | 0.0077589 | 220.8819 | 1.7138 | 0.0077589 | 220.8819 | 1.9018 | 0.0086102 | 220.8819 | 0.9988%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 793 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 78.2117 | 6.1528 | 12.7116 | 78.2117 | 6.1528 | 12.7116 | 86.793 | 6.8279 | 12.7116 | 0.9986%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 503 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 74.9698 | 3.9027 | 19.2096 | 74.9698 | 3.9027 | 19.2096 | 83.1953 | 4.3309 | 19.2096 | 0.9762%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 8 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.3096 | 0.062071 | 37.2094 | 2.3096 | 0.062071 | 37.2094 | 2.563 | 0.068881 | 37.2094 | 0.9867%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 781 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 82.5872 | 6.0597 | 13.629 | 82.5872 | 6.0597 | 13.629 | 91.6485 | 6.7245 | 13.629 | 0.9973%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 1809 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 244.3147 | 14.0358 | 17.4065 | 244.3147 | 14.0358 | 17.4065 | 271.1204 | 15.5758 | 17.4065 | 0.9919%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 130 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 57.7563 | 1.0087 | 57.2608 | 57.7563 | 1.0087 | 57.2608 | 64.0932 | 1.1193 | 57.2608 | 0.9998%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 1320 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 141.0713 | 10.2417 | 13.7742 | 141.0713 | 10.2417 | 13.7742 | 156.5494 | 11.3654 | 13.7742 | 0.9833%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 741 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 105.7677 | 5.7493 | 18.3965 | 105.7677 | 5.7493 | 18.3965 | 117.3723 | 6.3801 | 18.3965 | 0.988%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 1020 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 48.7918 | 7.9141 | 6.1652 | 48.7918 | 7.9141 | 6.1652 | 54.1451 | 8.7824 | 6.1652 | 0.9625%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 585 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.2496 | 4.5389 | 2.6988 | 12.2496 | 4.5389 | 2.6988 | 13.5936 | 5.0369 | 2.6988 | 0.9181%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 352 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 71.2405 | 2.7311 | 26.0846 | 71.2405 | 2.7311 | 26.0846 | 79.0568 | 3.0308 | 26.0846 | 0.9835%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 1150 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 371.2832 | 8.9227 | 41.611 | 371.2832 | 8.9227 | 41.611 | 412.0195 | 9.9017 | 41.611 | 0.9889%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 577 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 30.5007 | 4.4769 | 6.8129 | 30.5007 | 4.4769 | 6.8129 | 33.8472 | 4.9681 | 6.8129 | 0.9191%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 762 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 203.4497 | 5.9123 | 34.4115 | 203.4497 | 5.9123 | 34.4115 | 225.7718 | 6.5609 | 34.4115 | 0.9908%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3753 | 0.06983 | 19.6944 | 1.3753 | 0.06983 | 19.6944 | 1.5261 | 0.077491 | 19.6944 | 0.9858%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 211 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.4441 | 1.6371 | 4.5471 | 7.4441 | 1.6371 | 4.5471 | 8.2609 | 1.8167 | 4.5471 | 0.9652%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 1555 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 499.1345 | 12.0651 | 41.3703 | 499.1345 | 12.0651 | 41.3703 | 553.8984 | 13.3888 | 41.3703 | 0.9927%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 16 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 51.8797 | 0.12414 | 417.906 | 51.8797 | 0.12414 | 417.906 | 57.5718 | 0.13776 | 417.906 | 0.9997%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 1096 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 291.8804 | 8.5037 | 34.3238 | 291.8804 | 8.5037 | 34.3238 | 323.9049 | 9.4367 | 34.3238 | 0.9926%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 309 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.3192 | 2.3975 | 4.7213 | 11.3192 | 2.3975 | 4.7213 | 12.5611 | 2.6605 | 4.7213 | 0.9598%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 318 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 30.7953 | 2.4673 | 12.4812 | 30.7953 | 2.4673 | 12.4812 | 34.1741 | 2.738 | 12.4812 | 0.9934%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 84 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.7625 | 0.65175 | 14.979 | 9.7625 | 0.65175 | 14.979 | 10.8336 | 0.72325 | 14.979 | 0.6902%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 116 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.8843 | 0.90003 | 15.4265 | 13.8843 | 0.90003 | 15.4265 | 15.4077 | 0.99878 | 15.4265 | 0.7661%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 3 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.9364 | 0.023277 | 169.1142 | 3.9364 | 0.023277 | 169.1142 | 4.3683 | 0.02583 | 169.1142 | 0.9947%
2027 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.55108 | 0.10087 | 5.4635 | 0.55108 | 0.10087 | 5.4635 | 0.61155 | 0.11193 | 5.4635 | 0.9691%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 75 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 117.5454 | 0.58192 | 201.9972 | 117.5454 | 0.58192 | 201.9972 | 130.4422 | 0.64576 | 201.9972 | 0.9966%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 913 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 136.5462 | 7.0839 | 19.2757 | 136.5462 | 7.0839 | 19.2757 | 151.5277 | 7.8611 | 19.2757 | 0.9905%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 1693 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 256.3868 | 13.1358 | 19.5182 | 256.3868 | 13.1358 | 19.5182 | 284.5169 | 14.577 | 19.5182 | 0.9891%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 169 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 72.5488 | 1.3113 | 55.328 | 72.5488 | 1.3113 | 55.328 | 80.5087 | 1.4551 | 55.328 | 0.9946%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 109 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 39.4065 | 0.84572 | 46.5953 | 39.4065 | 0.84572 | 46.5953 | 43.7301 | 0.93851 | 46.5953 | 0.9952%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 442 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 132.3028 | 3.4294 | 38.5787 | 132.3028 | 3.4294 | 38.5787 | 146.8188 | 3.8057 | 38.5787 | 0.9843%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 1149 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 101.4885 | 8.915 | 11.3841 | 101.4885 | 8.915 | 11.3841 | 112.6235 | 9.8931 | 11.3841 | 0.9898%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 320 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 71.9042 | 2.4828 | 28.9604 | 71.9042 | 2.4828 | 28.9604 | 79.7933 | 2.7553 | 28.9604 | 0.9853%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 1391 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 209.5961 | 10.7926 | 19.4204 | 209.5961 | 10.7926 | 19.4204 | 232.5925 | 11.9767 | 19.4204 | 0.9839%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 943 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 203.259 | 7.3166 | 27.7804 | 203.259 | 7.3166 | 27.7804 | 225.5601 | 8.1194 | 27.7804 | 0.9748%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 373 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 82.5252 | 2.8941 | 28.5154 | 82.5252 | 2.8941 | 28.5154 | 91.5797 | 3.2116 | 28.5154 | 0.9912%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 264 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 45.8566 | 2.0483 | 22.3872 | 45.8566 | 2.0483 | 22.3872 | 50.8879 | 2.2731 | 22.3872 | 0.9732%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 149 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 78.0753 | 1.1561 | 67.5349 | 78.0753 | 1.1561 | 67.5349 | 86.6415 | 1.2829 | 67.5349 | 0.9953%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 246 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 58.178 | 1.9087 | 30.4807 | 58.178 | 1.9087 | 30.4807 | 64.5612 | 2.1181 | 30.4807 | 0.9803%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 603 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 29.7799 | 4.6786 | 6.3651 | 29.7799 | 4.6786 | 6.3651 | 33.0473 | 5.1919 | 6.3651 | 0.9369%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 64.3818 | 0.5664 | 113.6688 | 64.3818 | 0.5664 | 113.6688 | 71.4456 | 0.62854 | 113.6688 | 0.9955%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 24 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 46.8889 | 0.18621 | 251.8024 | 46.8889 | 0.18621 | 251.8024 | 52.0335 | 0.20664 | 251.8024 | 0.803%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 41 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.7574 | 0.31811 | 11.8115 | 3.7574 | 0.31811 | 11.8115 | 4.1696 | 0.35302 | 11.8115 | 0.6587%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 303 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 41.5562 | 2.3509 | 17.6764 | 41.5562 | 2.3509 | 17.6764 | 46.1156 | 2.6089 | 17.6764 | 0.9978%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 150 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 30.2704 | 1.1638 | 26.0092 | 30.2704 | 1.1638 | 26.0092 | 33.5916 | 1.2915 | 26.0092 | 0.9981%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 159 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.8231 | 1.2337 | 10.3943 | 12.8231 | 1.2337 | 10.3943 | 14.23 | 1.369 | 10.3943 | 0.9962%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 18 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.2838 | 0.13966 | 73.6346 | 10.2838 | 0.13966 | 73.6346 | 11.4121 | 0.15498 | 73.6346 | 0.9972%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 46 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.1761 | 0.35691 | 14.5027 | 5.1761 | 0.35691 | 14.5027 | 5.7441 | 0.39607 | 14.5027 | 0.3454%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 192 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.2241 | 1.4897 | 3.5068 | 5.2241 | 1.4897 | 3.5068 | 5.7973 | 1.6532 | 3.5068 | 0.75%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 12 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.66137 | 0.093107 | 7.1034 | 0.66137 | 0.093107 | 7.1034 | 0.73393 | 0.10332 | 7.1034 | 0.9665%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 1218 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 48.4098 | 9.4503 | 5.1226 | 48.4098 | 9.4503 | 5.1226 | 53.7212 | 10.4872 | 5.1226 | 0.8429%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 2353 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 59.9246 | 18.2566 | 3.2823 | 59.9246 | 18.2566 | 3.2823 | 66.4994 | 20.2597 | 3.2823 | 0.9909%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 259 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.0561 | 2.0095 | 6.497 | 13.0561 | 2.0095 | 6.497 | 14.4885 | 2.23 | 6.497 | 0.9975%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.98124 | 0.031036 | 31.6166 | 0.98124 | 0.031036 | 31.6166 | 1.0889 | 0.034441 | 31.6166 | 0.9975%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 85 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 37.0598 | 0.6595 | 56.1933 | 37.0598 | 0.6595 | 56.1933 | 41.1259 | 0.73186 | 56.1933 | 0.9993%
2027 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 17 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.35763 | 0.1319 | 2.7114 | 0.35763 | 0.1319 | 2.7114 | 0.39687 | 0.14637 | 2.7114 | 0.9408%
2027 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 3 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.83874 | 0.023277 | 36.0336 | 0.83874 | 0.023277 | 36.0336 | 0.93076 | 0.02583 | 36.0336 | 0.3549%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 2.8867 | 0.038794 | 74.4097 | 2.8867 | 0.038794 | 74.4097 | 3.2034 | 0.043051 | 74.4097 | 0.7993%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 137 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.6527 | 1.063 | 3.4363 | 3.6527 | 1.063 | 3.4363 | 4.0535 | 1.1796 | 3.4363 | 0.299%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 312 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.1598 | 2.4208 | 0.4791 | 1.1598 | 2.4208 | 0.4791 | 1.287 | 2.6864 | 0.4791 | 0.9512%
2027 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 504 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.17071 | 3.9105 | 0.043655 | 0.17071 | 3.9105 | 0.043655 | 0.18944 | 4.3395 | 0.043655 | 0.09583%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 358 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.7926 | 2.7777 | 2.8054 | 7.7926 | 2.7777 | 2.8054 | 8.6476 | 3.0824 | 2.8054 | 0.8082%
2027 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 1.3377 | 0 | 0 | 1.3377 | 0 | 1.2173 | 0.054312 | 22.4131 | 1.2173 | 0.054312 | 22.4131 | 1.3509 | 0.060271 | 22.4131 | 0.9989%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 68 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.9331 | 0.5276 | 3.6639 | 1.9331 | 0.5276 | 3.6639 | 2.1452 | 0.58549 | 3.6639 | 0.9981%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 696 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 22.587 | 5.4002 | 4.1826 | 22.587 | 5.4002 | 4.1826 | 25.0652 | 5.9927 | 4.1826 | 0.9929%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 645 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 14.5549 | 5.0045 | 2.9084 | 14.5549 | 5.0045 | 2.9084 | 16.1519 | 5.5536 | 2.9084 | 0.9737%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 1826 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 37.0873 | 14.1677 | 2.6177 | 37.0873 | 14.1677 | 2.6177 | 41.1564 | 15.7222 | 2.6177 | 0.9874%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 1032 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 29.646 | 8.0072 | 3.7024 | 29.646 | 8.0072 | 3.7024 | 32.8986 | 8.8857 | 3.7024 | 0.9888%
2027 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 504 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 112.9166 | 3.9105 | 28.8754 | 112.9166 | 3.9105 | 28.8754 | 125.3055 | 4.3395 | 28.8754 | 0.9762%
2027 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 35 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 19.127 | 0.27156 | 70.4337 | 19.127 | 0.27156 | 70.4337 | 21.2256 | 0.30136 | 70.4337 | 0.9954%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 222 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.2264 | 1.7225 | 6.5176 | 11.2264 | 1.7225 | 6.5176 | 12.4582 | 1.9115 | 6.5176 | 0.9768%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 44 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.3827 | 0.34139 | 6.9795 | 2.3827 | 0.34139 | 6.9795 | 2.6441 | 0.37885 | 6.9795 | 0.6436%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0086 | 0.15518 | 6.5 | 1.0086 | 0.15518 | 6.5 | 1.1193 | 0.1722 | 6.5 | 0.375%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 519 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.7811 | 4.0269 | 2.9256 | 11.7811 | 4.0269 | 2.9256 | 13.0737 | 4.4687 | 2.9256 | 0.9%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 109 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.4286 | 0.84572 | 2.8716 | 2.4286 | 0.84572 | 2.8716 | 2.695 | 0.93851 | 2.8716 | 0.7028%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 263 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.7118 | 2.0406 | 4.2692 | 8.7118 | 2.0406 | 4.2692 | 9.6676 | 2.2645 | 4.2692 | 0.995%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 195 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.3021 | 1.513 | 4.8263 | 7.3021 | 1.513 | 4.8263 | 8.1033 | 1.679 | 4.8263 | 0.9704%
2027 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 17 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 0.50007 | 0 | 0 | 0.50007 | 0 | 0.45506 | 0.1319 | 3.45 | 0.45506 | 0.1319 | 3.45 | 0.50498 | 0.14637 | 3.45 | 0.1609%
2027 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 160 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.57264 | 1.2414 | 0.46128 | 0.57264 | 1.2414 | 0.46128 | 0.63547 | 1.3776 | 0.46128 | 0.6647%
2027 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 23 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.09533 | 0.17845 | 0.5342 | 0.09533 | 0.17845 | 0.5342 | 0.10579 | 0.19803 | 0.5342 | 0.9726%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.2284 | 0.13966 | 94.7185 | 13.2284 | 0.13966 | 94.7185 | 14.6798 | 0.15498 | 94.7185 | 0.9979%
2027 | 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 29 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.8969 | 0.22501 | 8.4305 | 1.8969 | 0.22501 | 8.4305 | 2.1051 | 0.24969 | 8.4305 | 0.9683%
2027 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 233 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.37712 | 1.8078 | 0.20861 | 0.37712 | 1.8078 | 0.20861 | 0.4185 | 2.0062 | 0.20861 | 0.3335%
2027 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 2 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.3623 | 0.015518 | 152.229 | 2.3623 | 0.015518 | 152.229 | 2.6214 | 0.01722 | 152.229 | 0.9938%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 641 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 132.4063 | 4.9734 | 26.6227 | 132.4063 | 4.9734 | 26.6227 | 146.9336 | 5.5191 | 26.6227 | 0.9966%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 26 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.79342 | 0.20173 | 3.9331 | 0.79342 | 0.20173 | 3.9331 | 0.88048 | 0.22386 | 3.9331 | 0.9922%
2027 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.068099 | 0.0077589 | 8.777 | 0.068099 | 0.0077589 | 8.777 | 0.075571 | 0.0086102 | 8.777 | 0.986%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 875 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 101.5275 | 6.789 | 14.9547 | 101.5275 | 6.789 | 14.9547 | 112.6669 | 7.5339 | 14.9547 | 0.9884%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.061378 | 0.038794 | 1.5821 | 0.061378 | 0.038794 | 1.5821 | 0.068112 | 0.043051 | 1.5821 | 0.991%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 495 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 53.3875 | 3.8406 | 13.9007 | 53.3875 | 3.8406 | 13.9007 | 59.2451 | 4.262 | 13.9007 | 0.9601%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 9 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4798 | 0.06983 | 21.1915 | 1.4798 | 0.06983 | 21.1915 | 1.6422 | 0.077491 | 21.1915 | 0.1888%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 1 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.87422 | 0.0077589 | 112.6733 | 0.87422 | 0.0077589 | 112.6733 | 0.97014 | 0.0086102 | 112.6733 | 0.1434%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 134 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.7001 | 1.0397 | 9.3298 | 9.7001 | 1.0397 | 9.3298 | 10.7643 | 1.1538 | 9.3298 | 0.9408%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 1.0439 | 0.038794 | 26.9097 | 1.0439 | 0.038794 | 26.9097 | 1.1585 | 0.043051 | 26.9097 | 0.9768%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 174 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 60.146 | 1.35 | 44.5511 | 60.146 | 1.35 | 44.5511 | 66.7451 | 1.4982 | 44.5511 | 0.9549%
2027 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.16724 | 0.023277 | 7.1849 | 0.16724 | 0.023277 | 7.1849 | 0.18559 | 0.02583 | 7.1849 | 0.9464%
2027 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 7 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.015734 | 0.054312 | 0.28969 | 0.015734 | 0.054312 | 0.28969 | 0.01746 | 0.060271 | 0.28969 | 0.9786%
2027 | 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 16 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.01877 | 0.12414 | 0.1512 | 0.01877 | 0.12414 | 0.1512 | 0.02083 | 0.13776 | 0.1512 | 0.1679%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 531 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 8.7492 | 4.12 | 2.1236 | 8.7492 | 4.12 | 2.1236 | 9.7091 | 4.572 | 2.1236 | 0.8949%
2027 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 318 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 1.0343 | 2.4673 | 0.41921 | 1.0343 | 2.4673 | 0.41921 | 1.1478 | 2.738 | 0.41921 | 0.372%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 31 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.1282 | 0.24053 | 17.1633 | 4.1282 | 0.24053 | 17.1633 | 4.5811 | 0.26692 | 17.1633 | 0.9425%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 10 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.37517 | 0.077589 | 4.8353 | 0.37517 | 0.077589 | 4.8353 | 0.41633 | 0.086102 | 4.8353 | 0.7619%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 186 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.60728 | 1.4432 | 0.4208 | 0.60728 | 1.4432 | 0.4208 | 0.67391 | 1.6015 | 0.4208 | 0.9924%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 47 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.2474 | 0.36467 | 22.6162 | 8.2474 | 0.36467 | 22.6162 | 9.1523 | 0.40468 | 22.6162 | 0.9545%
2027 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 21 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.9788 | 0.16294 | 18.2817 | 2.9788 | 0.16294 | 18.2817 | 3.3056 | 0.18081 | 18.2817 | 0.7837%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 892 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 39.2661 | 6.9209 | 5.6735 | 39.2661 | 6.9209 | 5.6735 | 43.5742 | 7.6803 | 5.6735 | 0.9981%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 70 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.46433 | 0.54312 | 0.85492 | 0.46433 | 0.54312 | 0.85492 | 0.51527 | 0.60271 | 0.85492 | 0.9266%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 102 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 74.135 | 0.79141 | 93.6751 | 74.135 | 0.79141 | 93.6751 | 82.2689 | 0.87824 | 93.6751 | 0.9507%
2027 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 169 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.38586 | 1.3113 | 0.29427 | 0.38586 | 1.3113 | 0.29427 | 0.42819 | 1.4551 | 0.29427 | 0.9943%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 58 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 24.913 | 0.45002 | 55.3604 | 24.913 | 0.45002 | 55.3604 | 27.6464 | 0.49939 | 55.3604 | 0.9983%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 108 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.8713 | 0.83796 | 3.4265 | 2.8713 | 0.83796 | 3.4265 | 3.1863 | 0.9299 | 3.4265 | 0.9343%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 12.0117 | 0.023277 | 516.0423 | 12.0117 | 0.023277 | 516.0423 | 13.3296 | 0.02583 | 516.0423 | 0.7976%
2027 | 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 7 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.2834 | 0.054312 | 42.0413 | 2.2834 | 0.054312 | 42.0413 | 2.5339 | 0.060271 | 42.0413 | 0.9997%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 161 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 103.7418 | 1.2492 | 83.048 | 103.7418 | 1.2492 | 83.048 | 115.1241 | 1.3862 | 83.048 | 0.9951%
2027 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.8118 | 0.38794 | 30.4472 | 11.8118 | 0.38794 | 30.4472 | 13.1078 | 0.43051 | 30.4472 | 0.9951%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 423 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.5186 | 3.282 | 1.0721 | 3.5186 | 3.282 | 1.0721 | 3.9047 | 3.6421 | 1.0721 | 0.997%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 106 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.2038 | 0.82244 | 1.4637 | 1.2038 | 0.82244 | 1.4637 | 1.3359 | 0.91268 | 1.4637 | 0.9965%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.22558 | 0.031036 | 7.2684 | 0.22558 | 0.031036 | 7.2684 | 0.25033 | 0.034441 | 7.2684 | 0.9021%
2027 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 463 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.1647 | 3.5924 | 0.32421 | 1.1647 | 3.5924 | 0.32421 | 1.2925 | 3.9865 | 0.32421 | 0.3693%
2027 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 343 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 8.8377 | 2.6613 | 3.3208 | 8.8377 | 2.6613 | 3.3208 | 9.8074 | 2.9533 | 3.3208 | 0.9433%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 417 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.6384 | 3.2355 | 4.2153 | 13.6384 | 3.2355 | 4.2153 | 15.1347 | 3.5904 | 4.2153 | 0.9785%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 286 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 45.916 | 2.219 | 20.6918 | 45.916 | 2.219 | 20.6918 | 50.9538 | 2.4625 | 20.6918 | 0.9856%
2027 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 5.7493 | 0.14742 | 38.9998 | 5.7493 | 0.14742 | 38.9998 | 6.3801 | 0.16359 | 38.9998 | 0.9902%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 786 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 62.3027 | 6.0985 | 10.2161 | 62.3027 | 6.0985 | 10.2161 | 69.1384 | 6.7676 | 10.2161 | 0.99%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 1534 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 26.0975 | 11.9021 | 2.1927 | 26.0975 | 11.9021 | 2.1927 | 28.9608 | 13.208 | 2.1927 | 0.9473%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 454 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 94.0833 | 3.5225 | 26.709 | 94.0833 | 3.5225 | 26.709 | 104.4059 | 3.909 | 26.709 | 0.9831%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 283 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 46.6933 | 2.1958 | 21.2652 | 46.6933 | 2.1958 | 21.2652 | 51.8164 | 2.4367 | 21.2652 | 0.9811%
2027 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 200 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.7942 | 1.5518 | 3.7339 | 5.7942 | 1.5518 | 3.7339 | 6.4299 | 1.722 | 3.7339 | 0.695%
2027 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.27042 | 0.031036 | 8.7134 | 0.27042 | 0.031036 | 8.7134 | 0.30009 | 0.034441 | 8.7134 | 0.9988%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 330 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 33.7388 | 2.5604 | 13.177 | 33.7388 | 2.5604 | 13.177 | 37.4406 | 2.8414 | 13.177 | 0.9914%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 793 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 28.667 | 6.1528 | 4.6592 | 28.667 | 6.1528 | 4.6592 | 31.8123 | 6.8279 | 4.6592 | 0.9371%
2027 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 52 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.017168 | 0.40346 | 0.042552 | 0.017168 | 0.40346 | 0.042552 | 0.019052 | 0.44773 | 0.042552 | 0.02003%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 1644 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.8194 | 12.7556 | 1.1618 | 14.8194 | 12.7556 | 1.1618 | 16.4453 | 14.1551 | 1.1618 | 0.789%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 433 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 32.21 | 3.3596 | 9.5875 | 32.21 | 3.3596 | 9.5875 | 35.744 | 3.7282 | 9.5875 | 0.9517%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 341 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 84.4138 | 2.6458 | 31.9051 | 84.4138 | 2.6458 | 31.9051 | 93.6755 | 2.9361 | 31.9051 | 0.9933%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 1098 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 61.4447 | 8.5192 | 7.2125 | 61.4447 | 8.5192 | 7.2125 | 68.1863 | 9.454 | 7.2125 | 0.9757%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 329 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 53.7422 | 2.5527 | 21.0533 | 53.7422 | 2.5527 | 21.0533 | 59.6387 | 2.8327 | 21.0533 | 0.9932%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 505 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 34.2446 | 3.9182 | 8.7398 | 34.2446 | 3.9182 | 8.7398 | 38.0018 | 4.3481 | 8.7398 | 0.9948%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.0072 | 0.044409 | 22.6798 | 1.0072 | 0.044409 | 22.6798 | 1.1774 | 0.051914 | 22.6798 | 0.9903%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 86 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.5207 | 0.63652 | 5.5312 | 3.5207 | 0.63652 | 5.5312 | 4.1158 | 0.7441 | 5.5312 | 0.9915%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 1144 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 33.5037 | 8.4673 | 3.9569 | 33.5037 | 8.4673 | 3.9569 | 39.1662 | 9.8983 | 3.9569 | 0.9141%
2028 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 0.99181 | 0.029606 | 33.5007 | 0.99181 | 0.029606 | 33.5007 | 1.1594 | 0.034609 | 33.5007 | 0.9976%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 1369 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 302.1866 | 10.1326 | 29.8233 | 302.1866 | 10.1326 | 29.8233 | 353.2596 | 11.8451 | 29.8233 | 0.9902%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 234 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 60.1308 | 1.7319 | 34.7188 | 60.1308 | 1.7319 | 34.7188 | 70.2936 | 2.0247 | 34.7188 | 0.9818%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 633 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 162.927 | 4.6851 | 34.7755 | 162.927 | 4.6851 | 34.7755 | 190.4635 | 5.477 | 34.7755 | 0.997%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 269 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 43.4855 | 1.991 | 21.8412 | 43.4855 | 1.991 | 21.8412 | 50.835 | 2.3275 | 21.8412 | 0.9951%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 53 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 11.9862 | 0.39228 | 30.5555 | 11.9862 | 0.39228 | 30.5555 | 14.012 | 0.45858 | 30.5555 | 0.9958%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 6.8679 | 0.22204 | 30.9306 | 6.8679 | 0.22204 | 30.9306 | 8.0287 | 0.25957 | 30.9306 | 0.996%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 392 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 84.7538 | 2.9014 | 29.2117 | 84.7538 | 2.9014 | 29.2117 | 99.0781 | 3.3917 | 29.2117 | 0.9962%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 14 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 5.9834 | 0.10362 | 57.744 | 5.9834 | 0.10362 | 57.744 | 6.9947 | 0.12113 | 57.744 | 0.9922%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 221 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 43.6602 | 1.6357 | 26.6917 | 43.6602 | 1.6357 | 26.6917 | 51.0392 | 1.9122 | 26.6917 | 0.9916%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 209 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 24.8966 | 1.5469 | 16.0945 | 24.8966 | 1.5469 | 16.0945 | 29.1044 | 1.8083 | 16.0945 | 0.9924%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 1740 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 78.8985 | 12.8785 | 6.1264 | 78.8985 | 12.8785 | 6.1264 | 92.2332 | 15.0551 | 6.1264 | 0.9598%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 1132 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 31.9045 | 8.3784 | 3.8079 | 31.9045 | 8.3784 | 3.8079 | 37.2967 | 9.7945 | 3.8079 | 0.9739%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 220 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.4563 | 1.6283 | 2.7368 | 4.4563 | 1.6283 | 2.7368 | 5.2095 | 1.9035 | 2.7368 | 0.8768%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 43.7073 | 0.77715 | 56.2403 | 43.7073 | 0.77715 | 56.2403 | 51.0943 | 0.9085 | 56.2403 | 0.9826%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 269 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 101.1325 | 1.991 | 50.7951 | 101.1325 | 1.991 | 50.7951 | 118.2251 | 2.3275 | 50.7951 | 0.9858%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 107 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 18.5685 | 0.79195 | 23.4464 | 18.5685 | 0.79195 | 23.4464 | 21.7068 | 0.9258 | 23.4464 | 0.9945%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 209 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 56.703 | 1.5469 | 36.6559 | 56.703 | 1.5469 | 36.6559 | 66.2865 | 1.8083 | 36.6559 | 0.9866%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 1458 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 217.8957 | 10.7913 | 20.1918 | 217.8957 | 10.7913 | 20.1918 | 254.7226 | 12.6152 | 20.1918 | 0.9914%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 1503 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 242.8087 | 11.1244 | 21.8267 | 242.8087 | 11.1244 | 21.8267 | 283.8462 | 13.0045 | 21.8267 | 0.9849%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 1232 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 229.7909 | 9.1186 | 25.2003 | 229.7909 | 9.1186 | 25.2003 | 268.6282 | 10.6597 | 25.2003 | 0.9916%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 1991 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 134.9918 | 14.7363 | 9.1605 | 134.9918 | 14.7363 | 9.1605 | 157.807 | 17.2269 | 9.1605 | 0.9745%
2028 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 43 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.13544 | 0.31826 | 0.42555 | 0.13544 | 0.31826 | 0.42555 | 0.15833 | 0.37205 | 0.42555 | 0.8684%
2028 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.029974 | 0.18504 | 0.16199 | 0.029974 | 0.18504 | 0.16199 | 0.03504 | 0.21631 | 0.16199 | 0.1275%
2028 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.019063 | 0.029606 | 0.6439 | 0.019063 | 0.029606 | 0.6439 | 0.022285 | 0.034609 | 0.6439 | 0.3435%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 19 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.2935 | 0.14063 | 44.7533 | 6.2935 | 0.14063 | 44.7533 | 7.3572 | 0.1644 | 44.7533 | 0.9924%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 140 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.4964 | 1.0362 | 7.2345 | 7.4964 | 1.0362 | 7.2345 | 8.7634 | 1.2113 | 7.2345 | 0.9393%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 37 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.0761 | 0.27385 | 3.9294 | 1.0761 | 0.27385 | 3.9294 | 1.258 | 0.32014 | 3.9294 | 0.8802%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 600 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 51.0132 | 4.4409 | 11.4872 | 51.0132 | 4.4409 | 11.4872 | 59.635 | 5.1914 | 11.4872 | 0.9962%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 661 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 43.1612 | 4.8924 | 8.8222 | 43.1612 | 4.8924 | 8.8222 | 50.456 | 5.7192 | 8.8222 | 0.9962%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 315 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 21.7896 | 2.3315 | 9.3459 | 21.7896 | 2.3315 | 9.3459 | 25.4723 | 2.7255 | 9.3459 | 0.9984%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 124 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.81731 | 0.91778 | 0.89053 | 0.81731 | 0.91778 | 0.89053 | 0.95544 | 1.0729 | 0.89053 | 0.9877%
2028 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 0.54035 | 0 | 0 | 0.54035 | 0 | 0.46905 | 0.0074014 | 63.3734 | 0.46905 | 0.0074014 | 63.3734 | 0.54833 | 0.0086524 | 63.3734 | 0.9875%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 22 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 18.5594 | 0.16283 | 113.9792 | 18.5594 | 0.16283 | 113.9792 | 21.6962 | 0.19035 | 113.9792 | 0.9968%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 102 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 36.6746 | 0.75495 | 48.5791 | 36.6746 | 0.75495 | 48.5791 | 42.8731 | 0.88254 | 48.5791 | 0.9992%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 57 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.4206 | 0.42188 | 8.1079 | 3.4206 | 0.42188 | 8.1079 | 3.9987 | 0.49319 | 8.1079 | 0.945%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 53 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 6.8028 | 0.39228 | 17.3419 | 6.8028 | 0.39228 | 17.3419 | 7.9526 | 0.45858 | 17.3419 | 0.994%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 1839 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 36.8914 | 13.6113 | 2.7104 | 36.8914 | 13.6113 | 2.7104 | 43.1264 | 15.9117 | 2.7104 | 0.9112%
2028 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 21 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 1.8395 | 0.15543 | 11.8347 | 1.8395 | 0.15543 | 11.8347 | 2.1504 | 0.1817 | 11.8347 | 0.8819%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 23 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.7327 | 0.17023 | 10.1785 | 1.7327 | 0.17023 | 10.1785 | 2.0256 | 0.199 | 10.1785 | 0.9662%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 9 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.1043 | 0.066613 | 31.5898 | 2.1043 | 0.066613 | 31.5898 | 2.4599 | 0.077871 | 31.5898 | 0.9775%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 149 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 33.8232 | 1.1028 | 30.6699 | 33.8232 | 1.1028 | 30.6699 | 39.5397 | 1.2892 | 30.6699 | 0.9826%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 224 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 87.5467 | 1.6579 | 52.805 | 87.5467 | 1.6579 | 52.805 | 102.3431 | 1.9381 | 52.805 | 0.9977%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 469 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 88.7835 | 3.4713 | 25.5766 | 88.7835 | 3.4713 | 25.5766 | 103.789 | 4.058 | 25.5766 | 0.9908%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 78 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 52.232 | 0.57731 | 90.4744 | 52.232 | 0.57731 | 90.4744 | 61.0598 | 0.67489 | 90.4744 | 0.9788%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 54 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 18.208 | 0.39968 | 45.5566 | 18.208 | 0.39968 | 45.5566 | 21.2853 | 0.46723 | 45.5566 | 0.9469%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 327 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 72.8304 | 2.4203 | 30.0918 | 72.8304 | 2.4203 | 30.0918 | 85.1396 | 2.8293 | 30.0918 | 0.9648%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 133 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.3348 | 0.98439 | 13.5462 | 13.3348 | 0.98439 | 13.5462 | 15.5885 | 1.1508 | 13.5462 | 0.9856%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 440 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 30.4313 | 3.2566 | 9.3444 | 30.4313 | 3.2566 | 9.3444 | 35.5746 | 3.807 | 9.3444 | 0.9842%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 759 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 25.3573 | 5.6177 | 4.5138 | 25.3573 | 5.6177 | 4.5138 | 29.643 | 6.5672 | 4.5138 | 0.979%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 11.9053 | 0.68093 | 17.4838 | 11.9053 | 0.68093 | 17.4838 | 13.9174 | 0.79602 | 17.4838 | 0.9892%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 550 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 36.828 | 4.0708 | 9.0469 | 36.828 | 4.0708 | 9.0469 | 43.0524 | 4.7588 | 9.0469 | 0.9866%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 6 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.5601 | 0.044409 | 80.1659 | 3.5601 | 0.044409 | 80.1659 | 4.1617 | 0.051914 | 80.1659 | 0.9965%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 63 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 3.951 | 0.46629 | 8.4733 | 3.951 | 0.46629 | 8.4733 | 4.6188 | 0.5451 | 8.4733 | 0.9977%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 115 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.1595 | 0.85117 | 11.936 | 10.1595 | 0.85117 | 11.936 | 11.8766 | 0.99502 | 11.936 | 0.9935%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 18 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.3665 | 0.13323 | 10.2573 | 1.3665 | 0.13323 | 10.2573 | 1.5975 | 0.15574 | 10.2573 | 0.9948%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 150 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.1502 | 1.1102 | 14.5469 | 16.1502 | 1.1102 | 14.5469 | 18.8798 | 1.2979 | 14.5469 | 0.9905%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 104 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 51.8366 | 0.76975 | 67.3421 | 51.8366 | 0.76975 | 67.3421 | 60.5976 | 0.89985 | 67.3421 | 0.9304%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 164 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 55.93 | 1.2138 | 46.077 | 55.93 | 1.2138 | 46.077 | 65.3828 | 1.419 | 46.077 | 0.9454%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 908 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 101.2356 | 6.7205 | 15.0637 | 101.2356 | 6.7205 | 15.0637 | 118.3455 | 7.8564 | 15.0637 | 0.9926%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 355 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 31.3976 | 2.6275 | 11.9496 | 31.3976 | 2.6275 | 11.9496 | 36.7042 | 3.0716 | 11.9496 | 0.9815%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.3566 | 0.37007 | 9.0703 | 3.3566 | 0.37007 | 9.0703 | 3.924 | 0.43262 | 9.0703 | 0.9046%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 14 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 17.5658 | 0.10362 | 169.521 | 17.5658 | 0.10362 | 169.521 | 20.5346 | 0.12113 | 169.521 | 0.8554%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 217 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 37.432 | 1.6061 | 23.306 | 37.432 | 1.6061 | 23.306 | 43.7585 | 1.8776 | 23.306 | 0.9867%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.50519 | 0.029606 | 17.064 | 0.50519 | 0.029606 | 17.064 | 0.59057 | 0.034609 | 17.064 | 0.9994%
2028 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.014803 | 0 | 0 | 0.014803 | 0 | 0 | 0.017305 | 0 | 0%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 153 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 137.5213 | 1.1324 | 121.4401 | 137.5213 | 1.1324 | 121.4401 | 160.764 | 1.3238 | 121.4401 | 0.9909%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 315 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 70.2994 | 2.3315 | 30.1526 | 70.2994 | 2.3315 | 30.1526 | 82.1808 | 2.7255 | 30.1526 | 0.9925%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 756 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 319.7831 | 5.5955 | 57.1501 | 319.7831 | 5.5955 | 57.1501 | 373.8301 | 6.5412 | 57.1501 | 0.9936%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 10 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.064239 | 0.074014 | 0.86792 | 0.064239 | 0.074014 | 0.86792 | 0.075096 | 0.086524 | 0.86792 | 0.895%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 121 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.1867 | 0.89557 | 3.5583 | 3.1867 | 0.89557 | 3.5583 | 3.7253 | 1.0469 | 3.5583 | 0.8771%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 985 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 44.2007 | 7.2904 | 6.0628 | 44.2007 | 7.2904 | 6.0628 | 51.6711 | 8.5226 | 6.0628 | 0.9246%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 107 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 26.2521 | 0.79195 | 33.1485 | 26.2521 | 0.79195 | 33.1485 | 30.689 | 0.9258 | 33.1485 | 0.9907%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 308 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 33.306 | 2.2796 | 14.6102 | 33.306 | 2.2796 | 14.6102 | 38.9351 | 2.6649 | 14.6102 | 0.9899%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 354 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 26.1371 | 2.6201 | 9.9756 | 26.1371 | 2.6201 | 9.9756 | 30.5546 | 3.0629 | 9.9756 | 0.9527%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 890 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 14.5896 | 6.5873 | 2.2148 | 14.5896 | 6.5873 | 2.2148 | 17.0554 | 7.7006 | 2.2148 | 0.8154%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 325 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 15.4015 | 2.4055 | 6.4027 | 15.4015 | 2.4055 | 6.4027 | 18.0045 | 2.812 | 6.4027 | 0.9501%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 1376 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 157.884 | 10.1844 | 15.5026 | 157.884 | 10.1844 | 15.5026 | 184.5682 | 11.9057 | 15.5026 | 0.97%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 675 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 34.6605 | 4.996 | 6.9377 | 34.6605 | 4.996 | 6.9377 | 40.5185 | 5.8404 | 6.9377 | 0.991%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 215 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 16.261 | 1.5913 | 10.2186 | 16.261 | 1.5913 | 10.2186 | 19.0093 | 1.8603 | 10.2186 | 0.7065%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 778 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 37.1254 | 5.7583 | 6.4473 | 37.1254 | 5.7583 | 6.4473 | 43.4 | 6.7315 | 6.4473 | 0.9752%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 973 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 48.2755 | 7.2016 | 6.7034 | 48.2755 | 7.2016 | 6.7034 | 56.4346 | 8.4188 | 6.7034 | 0.9686%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 237 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 5.7898 | 1.7541 | 3.3006 | 5.7898 | 1.7541 | 3.3006 | 6.7683 | 2.0506 | 3.3006 | 0.7976%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 689 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 98.7984 | 5.0996 | 19.3738 | 98.7984 | 5.0996 | 19.3738 | 115.4964 | 5.9615 | 19.3738 | 0.9877%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 35.6347 | 2.6423 | 13.4862 | 35.6347 | 2.6423 | 13.4862 | 41.6574 | 3.0889 | 13.4862 | 0.981%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 832 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 84.8927 | 6.158 | 13.7857 | 84.8927 | 6.158 | 13.7857 | 99.2405 | 7.1988 | 13.7857 | 0.9713%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 33 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.3749 | 0.24425 | 9.7233 | 2.3749 | 0.24425 | 9.7233 | 2.7763 | 0.28553 | 9.7233 | 0.6764%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 285 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 28.8558 | 2.1094 | 13.6795 | 28.8558 | 2.1094 | 13.6795 | 33.7328 | 2.4659 | 13.6795 | 0.9774%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 475 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 41.8474 | 3.5157 | 11.9031 | 41.8474 | 3.5157 | 11.9031 | 48.9201 | 4.1099 | 11.9031 | 0.977%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 1095 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 110.6943 | 8.1046 | 13.6582 | 110.6943 | 8.1046 | 13.6582 | 129.4029 | 9.4743 | 13.6582 | 0.968%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 12.6728 | 0.59952 | 21.1383 | 12.6728 | 0.59952 | 21.1383 | 14.8146 | 0.70084 | 21.1383 | 0.8924%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 37 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 20.1239 | 0.27385 | 73.4842 | 20.1239 | 0.27385 | 73.4842 | 23.5251 | 0.32014 | 73.4842 | 0.7823%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 8 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.37697 | 0.059212 | 6.3665 | 0.37697 | 0.059212 | 6.3665 | 0.44068 | 0.069219 | 6.3665 | 0.9121%
2028 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 9 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0012779 | 0 | 0 | 0.0012779 | 0 | 0.0011093 | 0.066613 | 0.016652 | 0.0011093 | 0.066613 | 0.016652 | 0.0012967 | 0.077871 | 0.016652 | 0.1338%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 606 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 97.543 | 4.4853 | 21.7474 | 97.543 | 4.4853 | 21.7474 | 114.0289 | 5.2433 | 21.7474 | 0.9429%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 22 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 16.79 | 0.16283 | 103.1128 | 16.79 | 0.16283 | 103.1128 | 19.6277 | 0.19035 | 103.1128 | 0.9974%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 424 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 36.4306 | 3.1382 | 11.6087 | 36.4306 | 3.1382 | 11.6087 | 42.5878 | 3.6686 | 11.6087 | 0.9922%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 24 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 5.6436 | 0.17763 | 31.771 | 5.6436 | 0.17763 | 31.771 | 6.5975 | 0.20766 | 31.771 | 0.9914%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 101 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.8195 | 0.74755 | 2.434 | 1.8195 | 0.74755 | 2.434 | 2.127 | 0.87389 | 2.434 | 0.6623%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 185 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.042 | 1.3693 | 2.2216 | 3.042 | 1.3693 | 2.2216 | 3.5561 | 1.6007 | 2.2216 | 0.7437%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 536 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 13.757 | 3.9672 | 3.4677 | 13.757 | 3.9672 | 3.4677 | 16.082 | 4.6377 | 3.4677 | 0.9193%
2028 | 196 | 196-43F | Tier-2 | Tier-2---17 | Tier-2---9 | 5 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.048193 | 0 | 0 | 0.048193 | 0 | 0.041834 | 0.037007 | 1.1304 | 0.041834 | 0.037007 | 1.1304 | 0.048905 | 0.043262 | 1.1304 | 0.0514%
2028 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 3 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.5826 | 0.022204 | 71.2765 | 1.5826 | 0.022204 | 71.2765 | 1.8501 | 0.025957 | 71.2765 | 0.9934%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 19 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.055376 | 0.14063 | 0.39378 | 0.055376 | 0.14063 | 0.39378 | 0.064736 | 0.1644 | 0.39378 | 0.9638%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 85 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.0699 | 0.62912 | 12.8272 | 8.0699 | 0.62912 | 12.8272 | 9.4338 | 0.73545 | 12.8272 | 0.9553%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 266 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.1027 | 1.9688 | 2.0839 | 4.1027 | 1.9688 | 2.0839 | 4.7961 | 2.3015 | 2.0839 | 0.9636%
2028 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 11 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 1.2217 | 0 | 0 | 1.2217 | 0 | 1.0605 | 0.081416 | 13.0263 | 1.0605 | 0.081416 | 13.0263 | 1.2398 | 0.095176 | 13.0263 | 0.9852%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 85 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 11.079 | 0.62912 | 17.6102 | 11.079 | 0.62912 | 17.6102 | 12.9514 | 0.73545 | 17.6102 | 0.9978%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 346 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 25.774 | 2.5609 | 10.0644 | 25.774 | 2.5609 | 10.0644 | 30.13 | 2.9937 | 10.0644 | 0.9975%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1409 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 73.2722 | 10.4286 | 7.0261 | 73.2722 | 10.4286 | 7.0261 | 85.656 | 12.1912 | 7.0261 | 0.9974%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 205 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 3.8961 | 1.5173 | 2.5678 | 3.8961 | 1.5173 | 2.5678 | 4.5546 | 1.7737 | 2.5678 | 0.901%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 361 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 7.7241 | 2.6719 | 2.8909 | 7.7241 | 2.6719 | 2.8909 | 9.0296 | 3.1235 | 2.8909 | 0.8573%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 238 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.0436 | 1.7615 | 0.59243 | 1.0436 | 1.7615 | 0.59243 | 1.22 | 2.0593 | 0.59243 | 0.7047%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 182 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.402 | 1.3471 | 1.0408 | 1.402 | 1.3471 | 1.0408 | 1.6389 | 1.5747 | 1.0408 | 0.5082%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 427 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.3188 | 3.1604 | 2.9486 | 9.3188 | 3.1604 | 2.9486 | 10.8938 | 3.6946 | 2.9486 | 0.8949%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 305 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.2361 | 2.2574 | 5.8633 | 13.2361 | 2.2574 | 5.8633 | 15.4732 | 2.639 | 5.8633 | 0.8426%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 1226 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 14.9453 | 9.0742 | 1.647 | 14.9453 | 9.0742 | 1.647 | 17.4712 | 10.6078 | 1.647 | 0.9106%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 384 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 14.4047 | 2.8422 | 5.0682 | 14.4047 | 2.8422 | 5.0682 | 16.8392 | 3.3225 | 5.0682 | 0.9543%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 260 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 12.9466 | 1.9244 | 6.7277 | 12.9466 | 1.9244 | 6.7277 | 15.1347 | 2.2496 | 6.7277 | 0.9497%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 43 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.2439 | 0.31826 | 16.4767 | 5.2439 | 0.31826 | 16.4767 | 6.1302 | 0.37205 | 16.4767 | 0.9907%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 1745 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 42.0693 | 12.9155 | 3.2573 | 42.0693 | 12.9155 | 3.2573 | 49.1795 | 15.0984 | 3.2573 | 0.9915%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 25 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 10.7606 | 0.18504 | 58.1541 | 10.7606 | 0.18504 | 58.1541 | 12.5793 | 0.21631 | 58.1541 | 0.9792%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 678 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.3773 | 5.0182 | 1.6694 | 8.3773 | 5.0182 | 1.6694 | 9.7932 | 5.8663 | 1.6694 | 0.9662%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 66 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.2025 | 0.4885 | 4.5088 | 2.2025 | 0.4885 | 4.5088 | 2.5748 | 0.57106 | 4.5088 | 0.9706%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 209 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 12.5177 | 1.5469 | 8.0921 | 12.5177 | 1.5469 | 8.0921 | 14.6334 | 1.8083 | 8.0921 | 0.9727%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 425 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 22.9349 | 3.1456 | 7.2911 | 22.9349 | 3.1456 | 7.2911 | 26.8111 | 3.6773 | 7.2911 | 0.9578%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 108 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 8.7577 | 0.79936 | 10.956 | 8.7577 | 0.79936 | 10.956 | 10.2379 | 0.93446 | 10.956 | 0.9712%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 113 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.89078 | 0.83636 | 1.0651 | 0.89078 | 0.83636 | 1.0651 | 1.0413 | 0.97772 | 1.0651 | 0.9778%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 164 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 18.5404 | 1.2138 | 15.2742 | 18.5404 | 1.2138 | 15.2742 | 21.6739 | 1.419 | 15.2742 | 0.9872%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 120 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 12.4912 | 0.88817 | 14.0639 | 12.4912 | 0.88817 | 14.0639 | 14.6024 | 1.0383 | 14.0639 | 0.9782%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 1826 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 225.6415 | 13.515 | 16.6956 | 225.6415 | 13.515 | 16.6956 | 263.7775 | 15.7992 | 16.6956 | 0.9891%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 979 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 57.5299 | 7.246 | 7.9395 | 57.5299 | 7.246 | 7.9395 | 67.2531 | 8.4707 | 7.9395 | 0.9941%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 1960 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.0925 | 14.5068 | 0.28211 | 4.0925 | 14.5068 | 0.28211 | 4.7842 | 16.9587 | 0.28211 | 0.974%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 966 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.3996 | 7.1498 | 0.47548 | 3.3996 | 7.1498 | 0.47548 | 3.9741 | 8.3582 | 0.47548 | 0.9786%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 515 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.3988 | 3.8117 | 1.154 | 4.3988 | 3.8117 | 1.154 | 5.1422 | 4.456 | 1.154 | 0.9871%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 18.9959 | 2.3537 | 8.0708 | 18.9959 | 2.3537 | 8.0708 | 22.2065 | 2.7515 | 8.0708 | 0.9909%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 1448 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 12.8069 | 10.7173 | 1.195 | 12.8069 | 10.7173 | 1.195 | 14.9714 | 12.5286 | 1.195 | 0.8569%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 654 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 192.5809 | 4.8405 | 39.785 | 192.5809 | 4.8405 | 39.785 | 225.1293 | 5.6587 | 39.785 | 0.9924%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 757 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 108.2961 | 5.6029 | 19.3286 | 108.2961 | 5.6029 | 19.3286 | 126.5994 | 6.5498 | 19.3286 | 0.9821%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 414 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 167.486 | 3.0642 | 54.659 | 167.486 | 3.0642 | 54.659 | 195.793 | 3.5821 | 54.659 | 0.99%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 153 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.027 | 1.1324 | 10.6206 | 12.027 | 1.1324 | 10.6206 | 14.0597 | 1.3238 | 10.6206 | 0.9809%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 308 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 46.6667 | 2.2796 | 20.471 | 46.6667 | 2.2796 | 20.471 | 54.5539 | 2.6649 | 20.471 | 0.9892%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 489 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 120.8944 | 3.6193 | 33.4026 | 120.8944 | 3.6193 | 33.4026 | 141.3269 | 4.231 | 33.4026 | 0.9919%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 10 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.61815 | 0.074014 | 8.3518 | 0.61815 | 0.074014 | 8.3518 | 0.72263 | 0.086524 | 8.3518 | 0.999%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 951 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 15.5959 | 7.0388 | 2.2157 | 15.5959 | 7.0388 | 2.2157 | 18.2318 | 8.2284 | 2.2157 | 0.8922%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 793 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 20.8004 | 5.8693 | 3.5439 | 20.8004 | 5.8693 | 3.5439 | 24.3159 | 6.8613 | 3.5439 | 0.8785%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 1095 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 91.5481 | 8.1046 | 11.2959 | 91.5481 | 8.1046 | 11.2959 | 107.0208 | 9.4743 | 11.2959 | 0.9868%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 874 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 30.0512 | 6.4689 | 4.6455 | 30.0512 | 6.4689 | 4.6455 | 35.1302 | 7.5622 | 4.6455 | 0.9466%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 976 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.3491 | 7.2238 | 1.5711 | 11.3491 | 7.2238 | 1.5711 | 13.2672 | 8.4447 | 1.5711 | 0.9088%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 282 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 86.9871 | 2.0872 | 41.6763 | 86.9871 | 2.0872 | 41.6763 | 101.6889 | 2.44 | 41.6763 | 0.9905%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 169 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 18.3868 | 1.2508 | 14.6995 | 18.3868 | 1.2508 | 14.6995 | 21.4944 | 1.4623 | 14.6995 | 0.9634%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 992 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.0917 | 7.3422 | 1.9193 | 14.0917 | 7.3422 | 1.9193 | 16.4734 | 8.5832 | 1.9193 | 0.8429%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 3231 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 27.8169 | 23.9141 | 1.1632 | 27.8169 | 23.9141 | 1.1632 | 32.5183 | 27.9558 | 1.1632 | 0.8937%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 155 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 32.0105 | 1.1472 | 27.9026 | 32.0105 | 1.1472 | 27.9026 | 37.4207 | 1.3411 | 27.9026 | 0.9991%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 1090 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 26.1629 | 8.0676 | 3.243 | 26.1629 | 8.0676 | 3.243 | 30.5847 | 9.4311 | 3.243 | 0.9216%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 1687 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 22.8253 | 12.4862 | 1.828 | 22.8253 | 12.4862 | 1.828 | 26.6831 | 14.5966 | 1.828 | 0.9611%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 17 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.1327 | 0.12582 | 48.7401 | 6.1327 | 0.12582 | 48.7401 | 7.1692 | 0.14709 | 48.7401 | 0.9946%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 1158 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 33.1406 | 8.5709 | 3.8666 | 33.1406 | 8.5709 | 3.8666 | 38.7417 | 10.0194 | 3.8666 | 0.9703%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 157 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.92221 | 1.162 | 0.79362 | 0.92221 | 1.162 | 0.79362 | 1.0781 | 1.3584 | 0.79362 | 0.334%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 17.7549 | 0.83636 | 21.2287 | 17.7549 | 0.83636 | 21.2287 | 20.7557 | 0.97772 | 21.2287 | 0.9951%
2028 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 7 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 33.8502 | 0.05181 | 653.3518 | 33.8502 | 0.05181 | 653.3518 | 39.5713 | 0.060567 | 653.3518 | 0.9988%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 353 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.2941 | 2.6127 | 2.0263 | 5.2941 | 2.6127 | 2.0263 | 6.1889 | 3.0543 | 2.0263 | 0.9868%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 367 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 38.6908 | 2.7163 | 14.2438 | 38.6908 | 2.7163 | 14.2438 | 45.23 | 3.1754 | 14.2438 | 0.9945%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 163 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 19.5428 | 1.2064 | 16.1988 | 19.5428 | 1.2064 | 16.1988 | 22.8458 | 1.4103 | 16.1988 | 0.9686%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 169 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 83.1497 | 1.2508 | 66.4749 | 83.1497 | 1.2508 | 66.4749 | 97.203 | 1.4623 | 66.4749 | 0.9959%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 514 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.2286 | 3.8043 | 2.9515 | 11.2286 | 3.8043 | 2.9515 | 13.1263 | 4.4473 | 2.9515 | 0.9515%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 2343 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 62.1241 | 17.3416 | 3.5824 | 62.1241 | 17.3416 | 3.5824 | 72.6237 | 20.2725 | 3.5824 | 0.9662%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 676 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 682.3181 | 5.0034 | 136.3715 | 682.3181 | 5.0034 | 136.3715 | 797.6376 | 5.849 | 136.3715 | 0.9925%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 31.189 | 0.096219 | 324.1468 | 31.189 | 0.096219 | 324.1468 | 36.4603 | 0.11248 | 324.1468 | 0.9927%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 375 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 390.1034 | 2.7755 | 140.5504 | 390.1034 | 2.7755 | 140.5504 | 456.0353 | 3.2446 | 140.5504 | 0.9963%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 36 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.1697 | 0.26645 | 8.143 | 2.1697 | 0.26645 | 8.143 | 2.5364 | 0.31149 | 8.143 | 0.8656%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 1345 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 61.9237 | 9.9549 | 6.2204 | 61.9237 | 9.9549 | 6.2204 | 72.3895 | 11.6374 | 6.2204 | 0.9605%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 192 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 42.123 | 1.4211 | 29.6416 | 42.123 | 1.4211 | 29.6416 | 49.2423 | 1.6613 | 29.6416 | 0.9985%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 3380 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 140.7833 | 25.0169 | 5.6275 | 140.7833 | 25.0169 | 5.6275 | 164.5773 | 29.245 | 5.6275 | 0.967%
2028 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.14826 | 0.037007 | 4.0062 | 0.14826 | 0.037007 | 4.0062 | 0.17332 | 0.043262 | 4.0062 | 0.9833%
2028 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.4801 | 0.044409 | 33.3285 | 1.4801 | 0.044409 | 33.3285 | 1.7302 | 0.051914 | 33.3285 | 0.9937%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 997 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 16.4943 | 7.3792 | 2.2352 | 16.4943 | 7.3792 | 2.2352 | 19.282 | 8.6264 | 2.2352 | 0.9498%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 1487 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 54.4945 | 11.0059 | 4.9514 | 54.4945 | 11.0059 | 4.9514 | 63.7047 | 12.8661 | 4.9514 | 0.9826%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 942 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 16.3862 | 6.9722 | 2.3502 | 16.3862 | 6.9722 | 2.3502 | 19.1556 | 8.1505 | 2.3502 | 0.9106%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 284 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.6769 | 2.102 | 1.7492 | 3.6769 | 2.102 | 1.7492 | 4.2983 | 2.4573 | 1.7492 | 0.7897%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 133 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 6.7227 | 0.98439 | 6.8293 | 6.7227 | 0.98439 | 6.8293 | 7.8589 | 1.1508 | 6.8293 | 0.9819%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 791 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 29.4513 | 5.8545 | 5.0305 | 29.4513 | 5.8545 | 5.0305 | 34.429 | 6.844 | 5.0305 | 0.9768%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 14 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 0.98148 | 0.10362 | 9.4719 | 0.98148 | 0.10362 | 9.4719 | 1.1474 | 0.12113 | 9.4719 | 0.9298%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 110 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.3883 | 0.81416 | 1.7052 | 1.3883 | 0.81416 | 1.7052 | 1.623 | 0.95176 | 1.7052 | 0.8171%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 1015 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 23.3036 | 7.5125 | 3.102 | 23.3036 | 7.5125 | 3.102 | 27.2421 | 8.7822 | 3.102 | 0.983%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 3357 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 44.0479 | 24.8466 | 1.7728 | 44.0479 | 24.8466 | 1.7728 | 51.4925 | 29.046 | 1.7728 | 0.9868%
2028 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.0004488 | 0.044409 | 0.010106 | 0.0004488 | 0.044409 | 0.010106 | 0.00052465 | 0.051914 | 0.010106 | 0.004523%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 1436 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 26.0468 | 10.6285 | 2.4507 | 26.0468 | 10.6285 | 2.4507 | 30.449 | 12.4248 | 2.4507 | 0.9884%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 475 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.0897 | 3.5157 | 1.7321 | 6.0897 | 3.5157 | 1.7321 | 7.1189 | 4.1099 | 1.7321 | 0.9757%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 392 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.691 | 2.9014 | 1.2722 | 3.691 | 2.9014 | 1.2722 | 4.3148 | 3.3917 | 1.2722 | 0.9496%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 870 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 17.4616 | 6.4393 | 2.7117 | 17.4616 | 6.4393 | 2.7117 | 20.4128 | 7.5276 | 2.7117 | 0.859%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 1397 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 42.644 | 10.3398 | 4.1243 | 42.644 | 10.3398 | 4.1243 | 49.8514 | 12.0874 | 4.1243 | 0.9946%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 250 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 33.6588 | 1.8504 | 18.1904 | 33.6588 | 1.8504 | 18.1904 | 39.3475 | 2.1631 | 18.1904 | 0.8863%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 738 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 202.1881 | 5.4623 | 37.0154 | 202.1881 | 5.4623 | 37.0154 | 236.3602 | 6.3855 | 37.0154 | 0.9837%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 814 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 83.2984 | 6.0248 | 13.826 | 83.2984 | 6.0248 | 13.826 | 97.3768 | 7.043 | 13.826 | 0.9873%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 270 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 23.8394 | 1.9984 | 11.9293 | 23.8394 | 1.9984 | 11.9293 | 27.8686 | 2.3361 | 11.9293 | 0.9726%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 156 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 19.3507 | 1.1546 | 16.7593 | 19.3507 | 1.1546 | 16.7593 | 22.6212 | 1.3498 | 16.7593 | 0.9861%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 513 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 45.394 | 3.7969 | 11.9554 | 45.394 | 3.7969 | 11.9554 | 53.0661 | 4.4387 | 11.9554 | 0.9807%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 985 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 181.2145 | 7.2904 | 24.8565 | 181.2145 | 7.2904 | 24.8565 | 211.8418 | 8.5226 | 24.8565 | 0.9836%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 252 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 58.842 | 1.8652 | 31.5479 | 58.842 | 1.8652 | 31.5479 | 68.7869 | 2.1804 | 31.5479 | 0.9784%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 31.3562 | 0.82896 | 37.8259 | 31.3562 | 0.82896 | 37.8259 | 36.6558 | 0.96907 | 37.8259 | 0.994%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 316 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 243.6142 | 2.3389 | 104.1595 | 243.6142 | 2.3389 | 104.1595 | 284.7877 | 2.7341 | 104.1595 | 0.9934%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 996 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 232.4738 | 7.3718 | 31.5354 | 232.4738 | 7.3718 | 31.5354 | 271.7645 | 8.6178 | 31.5354 | 0.9889%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 81 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.081 | 0.59952 | 6.8071 | 4.081 | 0.59952 | 6.8071 | 4.7707 | 0.70084 | 6.8071 | 0.7089%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 21.7062 | 0.25905 | 83.7915 | 21.7062 | 0.25905 | 83.7915 | 25.3748 | 0.30283 | 83.7915 | 0.9883%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 1029 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 265.7992 | 7.6161 | 34.8997 | 265.7992 | 7.6161 | 34.8997 | 310.7223 | 8.9033 | 34.8997 | 0.9911%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 1238 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 562.6422 | 9.163 | 61.4038 | 562.6422 | 9.163 | 61.4038 | 657.7351 | 10.7116 | 61.4038 | 0.9893%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 725 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.3249 | 5.366 | 1.365 | 7.3249 | 5.366 | 1.365 | 8.5629 | 6.273 | 1.365 | 0.9808%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 131 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 13.5774 | 0.96959 | 14.0032 | 13.5774 | 0.96959 | 14.0032 | 15.8721 | 1.1335 | 14.0032 | 0.9867%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 504 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.3484 | 3.7303 | 2.506 | 9.3484 | 3.7303 | 2.506 | 10.9284 | 4.3608 | 2.506 | 0.9646%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 918 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 53.4582 | 6.7945 | 7.8678 | 53.4582 | 6.7945 | 7.8678 | 62.4933 | 7.9429 | 7.8678 | 0.9824%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 635 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.1911 | 4.6999 | 1.3173 | 6.1911 | 4.6999 | 1.3173 | 7.2374 | 5.4943 | 1.3173 | 0.6927%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 65 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.227 | 0.48109 | 6.7076 | 3.227 | 0.48109 | 6.7076 | 3.7724 | 0.5624 | 6.7076 | 0.9876%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 257 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.0908 | 1.9022 | 5.3049 | 10.0908 | 1.9022 | 5.3049 | 11.7962 | 2.2237 | 5.3049 | 0.9838%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 110 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 6.7803 | 0.81416 | 8.328 | 6.7803 | 0.81416 | 8.328 | 7.9263 | 0.95176 | 8.328 | 0.987%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 98 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.1681 | 0.72534 | 4.3677 | 3.1681 | 0.72534 | 4.3677 | 3.7035 | 0.84793 | 4.3677 | 0.9688%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 971 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 37.7167 | 7.1868 | 5.248 | 37.7167 | 7.1868 | 5.248 | 44.0912 | 8.4015 | 5.248 | 0.9791%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 530 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 32.1844 | 3.9228 | 8.2045 | 32.1844 | 3.9228 | 8.2045 | 37.624 | 4.5858 | 8.2045 | 0.9907%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 549 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 30.8081 | 4.0634 | 7.5819 | 30.8081 | 4.0634 | 7.5819 | 36.015 | 4.7502 | 7.5819 | 0.9682%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 164 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.4986 | 1.2138 | 4.53 | 5.4986 | 1.2138 | 4.53 | 6.428 | 1.419 | 4.53 | 0.6596%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 921 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 27.7975 | 6.8167 | 4.0778 | 27.7975 | 6.8167 | 4.0778 | 32.4956 | 7.9688 | 4.0778 | 0.9454%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 333 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 10.9245 | 2.4647 | 4.4324 | 10.9245 | 2.4647 | 4.4324 | 12.7709 | 2.8812 | 4.4324 | 0.9251%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 19 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.89663 | 0.14063 | 6.3759 | 0.89663 | 0.14063 | 6.3759 | 1.0482 | 0.1644 | 6.3759 | 0.9818%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 31.2287 | 4.7443 | 6.5823 | 31.2287 | 4.7443 | 6.5823 | 36.5068 | 5.5462 | 6.5823 | 0.9585%
2028 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.37228 | 0.066613 | 5.5887 | 0.37228 | 0.066613 | 5.5887 | 0.4352 | 0.077871 | 5.5887 | 0.8666%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 81 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 45.3392 | 0.59952 | 75.6263 | 45.3392 | 0.59952 | 75.6263 | 53.0021 | 0.70084 | 75.6263 | 0.9855%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 245 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 15.347 | 1.8134 | 8.4633 | 15.347 | 1.8134 | 8.4633 | 17.9408 | 2.1198 | 8.4633 | 0.878%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 3.9401 | 0.029606 | 133.0848 | 3.9401 | 0.029606 | 133.0848 | 4.606 | 0.034609 | 133.0848 | 0.9431%
2028 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 9 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.35645 | 0.066613 | 5.351 | 0.35645 | 0.066613 | 5.351 | 0.41669 | 0.077871 | 5.351 | 0.9823%
2028 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 329 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.4395 | 2.4351 | 1.8231 | 4.4395 | 2.4351 | 1.8231 | 5.1898 | 2.8466 | 1.8231 | 0.9288%
2028 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 44 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.022142 | 0.32566 | 0.06799 | 0.022142 | 0.32566 | 0.06799 | 0.025884 | 0.3807 | 0.06799 | 0.7897%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 4 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 3.9618 | 0.029606 | 133.82 | 3.9618 | 0.029606 | 133.82 | 4.6314 | 0.034609 | 133.82 | 0.9948%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 129 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.0495 | 0.95479 | 6.336 | 6.0495 | 0.95479 | 6.336 | 7.072 | 1.1162 | 6.336 | 0.9241%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 249 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.0305 | 1.843 | 10.326 | 19.0305 | 1.843 | 10.326 | 22.2468 | 2.1544 | 10.326 | 0.9107%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 590 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 39.503 | 4.3669 | 9.0461 | 39.503 | 4.3669 | 9.0461 | 46.1795 | 5.1049 | 9.0461 | 0.9555%
2028 | 308 | 308-485AE | Tier-2 | Tier-2---15 | Tier-2---8 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.043838 | 0 | 0 | 0.043838 | 0 | 0.038054 | 0.037007 | 1.0283 | 0.038054 | 0.037007 | 1.0283 | 0.044485 | 0.043262 | 1.0283 | 0.02775%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 20 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16066 | 0.14803 | 1.0853 | 0.16066 | 0.14803 | 1.0853 | 0.18781 | 0.17305 | 1.0853 | 0.1937%
2028 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 4 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.33962 | 0.029606 | 11.4715 | 0.33962 | 0.029606 | 11.4715 | 0.39702 | 0.034609 | 11.4715 | 0.8469%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 32 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.066898 | 0.23685 | 0.28245 | 0.066898 | 0.23685 | 0.28245 | 0.078204 | 0.27688 | 0.28245 | 0.4938%
2028 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 26 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.39379 | 0.19244 | 2.0463 | 0.39379 | 0.19244 | 2.0463 | 0.46034 | 0.22496 | 2.0463 | 0.1628%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 262 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.032458 | 1.9392 | 0.016738 | 0.032458 | 1.9392 | 0.016738 | 0.037943 | 2.2669 | 0.016738 | 0.02339%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 38 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0026556 | 0.28125 | 0.009442 | 0.0026556 | 0.28125 | 0.009442 | 0.0031044 | 0.32879 | 0.009442 | 0.001514%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 323 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.8126 | 2.3907 | 0.7582 | 1.8126 | 2.3907 | 0.7582 | 2.119 | 2.7947 | 0.7582 | 0.995%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.6061 | 0.13323 | 19.5615 | 2.6061 | 0.13323 | 19.5615 | 3.0466 | 0.15574 | 19.5615 | 0.9927%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 1796 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 29.856 | 13.293 | 2.246 | 29.856 | 13.293 | 2.246 | 34.902 | 15.5397 | 2.246 | 0.9548%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 2181 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 118.1718 | 16.1425 | 7.3205 | 118.1718 | 16.1425 | 7.3205 | 138.1442 | 18.8708 | 7.3205 | 0.9814%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 2656 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 46.9005 | 19.6582 | 2.3858 | 46.9005 | 19.6582 | 2.3858 | 54.8272 | 22.9807 | 2.3858 | 0.9699%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 1091 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 116.5375 | 8.075 | 14.4319 | 116.5375 | 8.075 | 14.4319 | 136.2336 | 9.4397 | 14.4319 | 0.9928%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 1620 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 96.1417 | 11.9903 | 8.0183 | 96.1417 | 11.9903 | 8.0183 | 112.3908 | 14.0168 | 8.0183 | 0.9888%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 1027 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 202.6155 | 7.6013 | 26.6554 | 202.6155 | 7.6013 | 26.6554 | 236.8598 | 8.886 | 26.6554 | 0.9925%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 222 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 79.1645 | 1.6431 | 48.1794 | 79.1645 | 1.6431 | 48.1794 | 92.5442 | 1.9208 | 48.1794 | 0.9973%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 1531 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 160.5499 | 11.3316 | 14.1683 | 160.5499 | 11.3316 | 14.1683 | 187.6847 | 13.2468 | 14.1683 | 0.9936%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 1034 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 78.0402 | 7.6531 | 10.1972 | 78.0402 | 7.6531 | 10.1972 | 91.2299 | 8.9466 | 10.1972 | 0.9749%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 340 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 21.6881 | 2.5165 | 8.6184 | 21.6881 | 2.5165 | 8.6184 | 25.3536 | 2.9418 | 8.6184 | 0.9918%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 60 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 19.2203 | 0.44409 | 43.2805 | 19.2203 | 0.44409 | 43.2805 | 22.4687 | 0.51914 | 43.2805 | 0.9993%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 143 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 15.3319 | 1.0584 | 14.4859 | 15.3319 | 1.0584 | 14.4859 | 17.9232 | 1.2373 | 14.4859 | 0.8869%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 150 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 37.2925 | 1.1102 | 33.5903 | 37.2925 | 1.1102 | 33.5903 | 43.5954 | 1.2979 | 33.5903 | 0.943%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 30 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.5371 | 0.22204 | 11.426 | 2.5371 | 0.22204 | 11.426 | 2.9659 | 0.25957 | 11.426 | 0.6284%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 484 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 116.8208 | 3.5823 | 32.6106 | 116.8208 | 3.5823 | 32.6106 | 136.5648 | 4.1877 | 32.6106 | 0.9943%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 1235 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 176.5588 | 9.1408 | 19.3155 | 176.5588 | 9.1408 | 19.3155 | 206.3992 | 10.6857 | 19.3155 | 0.9917%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 28.0801 | 1.7467 | 16.0757 | 28.0801 | 1.7467 | 16.0757 | 32.826 | 2.042 | 16.0757 | 0.8854%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 587 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 64.1338 | 4.3446 | 14.7616 | 64.1338 | 4.3446 | 14.7616 | 74.9732 | 5.0789 | 14.7616 | 0.985%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 253 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 11.7877 | 1.8726 | 6.295 | 11.7877 | 1.8726 | 6.295 | 13.78 | 2.1891 | 6.295 | 0.7994%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 403 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 46.3232 | 2.9828 | 15.5302 | 46.3232 | 2.9828 | 15.5302 | 54.1523 | 3.4869 | 15.5302 | 0.9814%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 1342 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 135.8918 | 9.9327 | 13.6812 | 135.8918 | 9.9327 | 13.6812 | 158.859 | 11.6115 | 13.6812 | 0.9776%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 1273 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 76.9818 | 9.422 | 8.1704 | 76.9818 | 9.422 | 8.1704 | 89.9926 | 11.0145 | 8.1704 | 0.9541%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 10.7592 | 0.36267 | 29.6666 | 10.7592 | 0.36267 | 29.6666 | 12.5776 | 0.42397 | 29.6666 | 0.9906%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 47 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 44.119 | 0.34787 | 126.827 | 44.119 | 0.34787 | 126.827 | 51.5757 | 0.40666 | 126.827 | 0.9968%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 11 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.2852 | 0.081416 | 89.4818 | 7.2852 | 0.081416 | 89.4818 | 8.5165 | 0.095176 | 89.4818 | 0.9549%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 484 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 144.6629 | 3.5823 | 40.3827 | 144.6629 | 3.5823 | 40.3827 | 169.1126 | 4.1877 | 40.3827 | 0.9879%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 901 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 149.7393 | 6.6687 | 22.454 | 149.7393 | 6.6687 | 22.454 | 175.0469 | 7.7958 | 22.454 | 0.9747%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 1047 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 87.8785 | 7.7493 | 11.3402 | 87.8785 | 7.7493 | 11.3402 | 102.731 | 9.059 | 11.3402 | 0.9704%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 712 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 99.8244 | 5.2698 | 18.9426 | 99.8244 | 5.2698 | 18.9426 | 116.6959 | 6.1605 | 18.9426 | 0.9781%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 18 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.0594 | 0.13323 | 37.9758 | 5.0594 | 0.13323 | 37.9758 | 5.9144 | 0.15574 | 37.9758 | 0.9721%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 11.6327 | 0.42928 | 27.098 | 11.6327 | 0.42928 | 27.098 | 13.5988 | 0.50184 | 27.098 | 0.9966%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 404 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 321.8183 | 2.9902 | 107.6249 | 321.8183 | 2.9902 | 107.6249 | 376.2093 | 3.4956 | 107.6249 | 0.9859%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 66 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.2433 | 0.4885 | 23.0161 | 11.2433 | 0.4885 | 23.0161 | 13.1435 | 0.57106 | 23.0161 | 0.8901%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 79 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5082 | 0.58471 | 2.5794 | 1.5082 | 0.58471 | 2.5794 | 1.7631 | 0.68354 | 2.5794 | 0.1879%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 1637 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 24.0122 | 12.1162 | 1.9818 | 24.0122 | 12.1162 | 1.9818 | 28.0706 | 14.1639 | 1.9818 | 0.8818%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 699 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 15.7753 | 5.1736 | 3.0492 | 15.7753 | 5.1736 | 3.0492 | 18.4415 | 6.048 | 3.0492 | 0.9783%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 1562 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 54.4478 | 11.5611 | 4.7096 | 54.4478 | 11.5611 | 4.7096 | 63.6501 | 13.515 | 4.7096 | 0.9847%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 30 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.2505 | 0.22204 | 50.6679 | 11.2505 | 0.22204 | 50.6679 | 13.1519 | 0.25957 | 50.6679 | 0.9597%
2028 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.61043 | 0.0074014 | 82.4741 | 0.61043 | 0.0074014 | 82.4741 | 0.7136 | 0.0086524 | 82.4741 | 0.9953%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 334 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 29.7608 | 2.4721 | 12.0388 | 29.7608 | 2.4721 | 12.0388 | 34.7907 | 2.8899 | 12.0388 | 0.9745%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 49 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.6157 | 0.36267 | 12.7269 | 4.6157 | 0.36267 | 12.7269 | 5.3958 | 0.42397 | 12.7269 | 0.9134%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 121 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 40.4105 | 0.89557 | 45.1225 | 40.4105 | 0.89557 | 45.1225 | 47.2404 | 1.0469 | 45.1225 | 0.98%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 45.7689 | 0.46629 | 98.1552 | 45.7689 | 0.46629 | 98.1552 | 53.5043 | 0.5451 | 98.1552 | 0.9857%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 889 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 15.3052 | 6.5799 | 2.3261 | 15.3052 | 6.5799 | 2.3261 | 17.8919 | 7.692 | 2.3261 | 0.9609%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 34 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.01335 | 0.25165 | 0.053051 | 0.01335 | 0.25165 | 0.053051 | 0.015607 | 0.29418 | 0.053051 | 0.01745%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 637 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.2878 | 4.7147 | 1.3336 | 6.2878 | 4.7147 | 1.3336 | 7.3505 | 5.5116 | 1.3336 | 0.8492%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 642 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.6468 | 4.7517 | 0.55701 | 2.6468 | 4.7517 | 0.55701 | 3.0941 | 5.5548 | 0.55701 | 0.5795%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 1846 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 88.8783 | 13.6631 | 6.505 | 88.8783 | 13.6631 | 6.505 | 103.8998 | 15.9723 | 6.505 | 0.8848%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 38 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 5.9095 | 0.28125 | 21.0112 | 5.9095 | 0.28125 | 21.0112 | 6.9083 | 0.32879 | 21.0112 | 0.9662%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 44 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.7229 | 0.32566 | 14.5024 | 4.7229 | 0.32566 | 14.5024 | 5.5211 | 0.3807 | 14.5024 | 0.9893%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 297 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.7629 | 2.1982 | 1.7118 | 3.7629 | 2.1982 | 1.7118 | 4.3989 | 2.5698 | 1.7118 | 0.9131%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 189 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.62594 | 1.3989 | 0.44746 | 0.62594 | 1.3989 | 0.44746 | 0.73173 | 1.6353 | 0.44746 | 0.51%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 9 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 2.8 | 0.066613 | 42.0335 | 2.8 | 0.066613 | 42.0335 | 3.2732 | 0.077871 | 42.0335 | 0.9662%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 28.9437 | 0.96219 | 30.0811 | 28.9437 | 0.96219 | 30.0811 | 33.8355 | 1.1248 | 30.0811 | 0.9767%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 529 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.5062 | 3.9154 | 0.8955 | 3.5062 | 3.9154 | 0.8955 | 4.0988 | 4.5771 | 0.8955 | 0.7071%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 353 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 79.4005 | 2.6127 | 30.3901 | 79.4005 | 2.6127 | 30.3901 | 92.8201 | 3.0543 | 30.3901 | 0.9496%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 203 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 60.4896 | 1.5025 | 40.2595 | 60.4896 | 1.5025 | 40.2595 | 70.713 | 1.7564 | 40.2595 | 0.9611%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 107 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.3499 | 0.79195 | 15.5942 | 12.3499 | 0.79195 | 15.5942 | 14.4371 | 0.9258 | 15.5942 | 0.8872%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 448 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 88.2116 | 3.3158 | 26.603 | 88.2116 | 3.3158 | 26.603 | 103.1203 | 3.8763 | 26.603 | 0.9569%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 175 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 12.9938 | 1.2953 | 10.0319 | 12.9938 | 1.2953 | 10.0319 | 15.1899 | 1.5142 | 10.0319 | 0.8473%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 216 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 27.954 | 1.5987 | 17.4853 | 27.954 | 1.5987 | 17.4853 | 32.6785 | 1.8689 | 17.4853 | 0.8754%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 296 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 33.8185 | 2.1908 | 15.4364 | 33.8185 | 2.1908 | 15.4364 | 39.5342 | 2.5611 | 15.4364 | 0.8812%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.4107 | 0.20724 | 55.0603 | 11.4107 | 0.20724 | 55.0603 | 13.3393 | 0.24227 | 55.0603 | 0.9724%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 20 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.2431 | 0.14803 | 69.1968 | 10.2431 | 0.14803 | 69.1968 | 11.9743 | 0.17305 | 69.1968 | 0.9739%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 139 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 20.8414 | 1.0288 | 20.258 | 20.8414 | 1.0288 | 20.258 | 24.3638 | 1.2027 | 20.258 | 0.9191%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 245 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.2489 | 1.8134 | 5.6519 | 10.2489 | 1.8134 | 5.6519 | 11.9811 | 2.1198 | 5.6519 | 0.557%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 225 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.4431 | 1.6653 | 2.0676 | 3.4431 | 1.6653 | 2.0676 | 4.0251 | 1.9468 | 2.0676 | 0.7618%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 164 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.3323 | 1.2138 | 3.5691 | 4.3323 | 1.2138 | 3.5691 | 5.0645 | 1.419 | 3.5691 | 0.7912%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 713 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 72.4591 | 5.2772 | 13.7305 | 72.4591 | 5.2772 | 13.7305 | 84.7056 | 6.1691 | 13.7305 | 0.9168%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 336 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 45.779 | 2.4869 | 18.4082 | 45.779 | 2.4869 | 18.4082 | 53.5162 | 2.9072 | 18.4082 | 0.9343%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 1001 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 52.8654 | 7.4088 | 7.1354 | 52.8654 | 7.4088 | 7.1354 | 61.8002 | 8.661 | 7.1354 | 0.9049%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 61 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 12.5889 | 0.45149 | 27.8831 | 12.5889 | 0.45149 | 27.8831 | 14.7166 | 0.52779 | 27.8831 | 0.9697%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 37 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.2488 | 0.27385 | 19.1665 | 5.2488 | 0.27385 | 19.1665 | 6.1359 | 0.32014 | 19.1665 | 0.967%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 115 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 45.1059 | 0.85117 | 52.9931 | 45.1059 | 0.85117 | 52.9931 | 52.7293 | 0.99502 | 52.9931 | 0.9877%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 265 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 19.2425 | 1.9614 | 9.8107 | 19.2425 | 1.9614 | 9.8107 | 22.4947 | 2.2929 | 9.8107 | 0.9555%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 80 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.5014 | 0.59212 | 4.2244 | 2.5014 | 0.59212 | 4.2244 | 2.9241 | 0.69219 | 4.2244 | 0.9711%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 586 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 71.2723 | 4.3372 | 16.4326 | 71.2723 | 4.3372 | 16.4326 | 83.3182 | 5.0703 | 16.4326 | 0.9923%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 132 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.3795 | 0.97699 | 6.5298 | 6.3795 | 0.97699 | 6.5298 | 7.4577 | 1.1421 | 6.5298 | 0.9277%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 171 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.3622 | 1.2656 | 7.3972 | 9.3622 | 1.2656 | 7.3972 | 10.9446 | 1.4796 | 7.3972 | 0.9525%
2028 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 6 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 1.7471 | 0 | 0 | 1.7471 | 0 | 1.5166 | 0.044409 | 34.1501 | 1.5166 | 0.044409 | 34.1501 | 1.7729 | 0.051914 | 34.1501 | 0.3253%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 11 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.19 | 0.081416 | 14.616 | 1.19 | 0.081416 | 14.616 | 1.3911 | 0.095176 | 14.616 | 0.999%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 5 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 6.2494 | 0 | 0 | 6.2494 | 0 | 5.4249 | 0.037007 | 146.5902 | 5.4249 | 0.037007 | 146.5902 | 6.3418 | 0.043262 | 146.5902 | 0.999%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 15 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.5706 | 0.11102 | 14.1464 | 1.5706 | 0.11102 | 14.1464 | 1.836 | 0.12979 | 14.1464 | 0.9984%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 373 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 24.4958 | 2.7607 | 8.8729 | 24.4958 | 2.7607 | 8.8729 | 28.6359 | 3.2273 | 8.8729 | 0.9993%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 52 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.32939 | 0.38488 | 0.85584 | 0.32939 | 0.38488 | 0.85584 | 0.38506 | 0.44992 | 0.85584 | 0.9723%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 277 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 29.7816 | 2.0502 | 14.5262 | 29.7816 | 2.0502 | 14.5262 | 34.815 | 2.3967 | 14.5262 | 0.997%
2028 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.74379 | 0.0074014 | 100.4925 | 0.74379 | 0.0074014 | 100.4925 | 0.8695 | 0.0086524 | 100.4925 | 0.9735%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 49 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 11.8471 | 0.36267 | 32.6663 | 11.8471 | 0.36267 | 32.6663 | 13.8494 | 0.42397 | 32.6663 | 0.9902%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 443 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 44.9395 | 3.2788 | 13.7059 | 44.9395 | 3.2788 | 13.7059 | 52.5347 | 3.833 | 13.7059 | 0.9833%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 878 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 144.4024 | 6.4985 | 22.221 | 144.4024 | 6.4985 | 22.221 | 168.8081 | 7.5968 | 22.221 | 0.9937%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 108 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 35.0626 | 0.79936 | 43.8636 | 35.0626 | 0.79936 | 43.8636 | 40.9886 | 0.93446 | 43.8636 | 0.9496%
2028 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 14 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.5011 | 0.10362 | 14.487 | 1.5011 | 0.10362 | 14.487 | 1.7549 | 0.12113 | 14.487 | 0.216%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 192 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.7651 | 1.4211 | 1.2421 | 1.7651 | 1.4211 | 1.2421 | 2.0634 | 1.6613 | 1.2421 | 0.9963%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 82 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.3375 | 0.60692 | 10.4422 | 6.3375 | 0.60692 | 10.4422 | 7.4087 | 0.70949 | 10.4422 | 0.9951%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 1001 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 25.1714 | 7.4088 | 3.3975 | 25.1714 | 7.4088 | 3.3975 | 29.4257 | 8.661 | 3.3975 | 0.9734%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 437 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 12.5764 | 3.2344 | 3.8883 | 12.5764 | 3.2344 | 3.8883 | 14.702 | 3.7811 | 3.8883 | 0.9797%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 1143 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 22.1562 | 8.4599 | 2.619 | 22.1562 | 8.4599 | 2.619 | 25.9009 | 9.8897 | 2.619 | 0.9676%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 1286 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 27.4777 | 9.5183 | 2.8868 | 27.4777 | 9.5183 | 2.8868 | 32.1217 | 11.127 | 2.8868 | 0.9272%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 482 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 13.9309 | 3.5675 | 3.905 | 13.9309 | 3.5675 | 3.905 | 16.2854 | 4.1704 | 3.905 | 0.9829%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 848 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 56.7803 | 6.2764 | 9.0466 | 56.7803 | 6.2764 | 9.0466 | 66.3768 | 7.3372 | 9.0466 | 0.9672%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 593 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.0238 | 4.3891 | 1.1446 | 5.0238 | 4.3891 | 1.1446 | 5.8729 | 5.1309 | 1.1446 | 0.7734%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 496 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 17.4587 | 3.6711 | 4.7557 | 17.4587 | 3.6711 | 4.7557 | 20.4094 | 4.2916 | 4.7557 | 0.9648%
2028 | 520 | 520-1936 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 0.63566 | 0 | 0 | 0.63566 | 0 | 0.55179 | 0.014803 | 37.2761 | 0.55179 | 0.014803 | 37.2761 | 0.64505 | 0.017305 | 37.2761 | 0.9977%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 188 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.6754 | 1.3915 | 1.2041 | 1.6754 | 1.3915 | 1.2041 | 1.9586 | 1.6266 | 1.2041 | 0.7472%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 1385 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 41.8632 | 10.251 | 4.0838 | 41.8632 | 10.251 | 4.0838 | 48.9386 | 11.9835 | 4.0838 | 0.9649%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 640 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 17.3179 | 4.7369 | 3.6559 | 17.3179 | 4.7369 | 3.6559 | 20.2448 | 5.5375 | 3.6559 | 0.9757%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 932 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 95.2678 | 6.8981 | 13.8106 | 95.2678 | 6.8981 | 13.8106 | 111.3691 | 8.064 | 13.8106 | 0.9669%
2028 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 448 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.2877 | 3.3158 | 1.8963 | 6.2877 | 3.3158 | 1.8963 | 7.3504 | 3.8763 | 1.8963 | 0.8931%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 973 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 71.9681 | 7.2016 | 9.9933 | 71.9681 | 7.2016 | 9.9933 | 84.1316 | 8.4188 | 9.9933 | 0.9779%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 734 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 75.1519 | 5.4327 | 13.8334 | 75.1519 | 5.4327 | 13.8334 | 87.8535 | 6.3508 | 13.8334 | 0.9936%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 900 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 48.1778 | 6.6613 | 7.2325 | 48.1778 | 6.6613 | 7.2325 | 56.3204 | 7.7871 | 7.2325 | 0.9878%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 673 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 105.606 | 4.9812 | 21.201 | 105.606 | 4.9812 | 21.201 | 123.4547 | 5.823 | 21.201 | 0.9938%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 1600 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 77.4933 | 11.8423 | 6.5438 | 77.4933 | 11.8423 | 6.5438 | 90.5906 | 13.8438 | 6.5438 | 0.9905%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.42096 | 0.68833 | 0.61156 | 0.42096 | 0.68833 | 0.61156 | 0.4921 | 0.80467 | 0.61156 | 0.4302%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 79 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.22878 | 0.58471 | 0.39126 | 0.22878 | 0.58471 | 0.39126 | 0.26744 | 0.68354 | 0.39126 | 0.2253%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1898 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 47.2153 | 14.0479 | 3.361 | 47.2153 | 14.0479 | 3.361 | 55.1952 | 16.4222 | 3.361 | 0.9644%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 230 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.30988 | 1.7023 | 0.18203 | 0.30988 | 1.7023 | 0.18203 | 0.36225 | 1.99 | 0.18203 | 0.117%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 486 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 47.3605 | 3.5971 | 13.1663 | 47.3605 | 3.5971 | 13.1663 | 55.365 | 4.2051 | 13.1663 | 0.9978%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 935 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 98.0181 | 6.9204 | 14.1637 | 98.0181 | 6.9204 | 14.1637 | 114.5843 | 8.09 | 14.1637 | 0.9977%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 638 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 117.8145 | 4.7221 | 24.9495 | 117.8145 | 4.7221 | 24.9495 | 137.7264 | 5.5202 | 24.9495 | 0.9899%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 75.0312 | 3.8858 | 19.3093 | 75.0312 | 3.8858 | 19.3093 | 87.7123 | 4.5425 | 19.3093 | 0.982%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 1862 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 347.0961 | 13.7815 | 25.1857 | 347.0961 | 13.7815 | 25.1857 | 405.7593 | 16.1107 | 25.1857 | 0.9903%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 61 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 4.9027 | 0.45149 | 10.8591 | 4.9027 | 0.45149 | 10.8591 | 5.7314 | 0.52779 | 10.8591 | 0.6775%
2028 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 3 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.3255 | 0.022204 | 59.6948 | 1.3255 | 0.022204 | 59.6948 | 1.5495 | 0.025957 | 59.6948 | 0.9944%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 14 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.3477 | 0.10362 | 41.9579 | 4.3477 | 0.10362 | 41.9579 | 5.0825 | 0.12113 | 41.9579 | 0.9632%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.42655 | 0.28866 | 1.4777 | 0.42655 | 0.28866 | 1.4777 | 0.49864 | 0.33744 | 1.4777 | 0.9941%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 1930 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 155.7203 | 14.2848 | 10.9011 | 155.7203 | 14.2848 | 10.9011 | 182.0388 | 16.6991 | 10.9011 | 0.9555%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 2562 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 222.1206 | 18.9625 | 11.7137 | 222.1206 | 18.9625 | 11.7137 | 259.6615 | 22.1674 | 11.7137 | 0.994%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 587 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 21.2119 | 4.3446 | 4.8823 | 21.2119 | 4.3446 | 4.8823 | 24.797 | 5.0789 | 4.8823 | 0.936%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 1265 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 34.0376 | 9.3628 | 3.6354 | 34.0376 | 9.3628 | 3.6354 | 39.7903 | 10.9453 | 3.6354 | 0.938%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 212 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.7095 | 1.5691 | 3.0014 | 4.7095 | 1.5691 | 3.0014 | 5.5054 | 1.8343 | 3.0014 | 0.8718%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 319 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.1122 | 2.3611 | 5.5535 | 13.1122 | 2.3611 | 5.5535 | 15.3283 | 2.7601 | 5.5535 | 0.9279%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 273 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 52.3744 | 2.0206 | 25.9203 | 52.3744 | 2.0206 | 25.9203 | 61.2263 | 2.3621 | 25.9203 | 0.9729%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 800 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 131.2209 | 5.9212 | 22.1614 | 131.2209 | 5.9212 | 22.1614 | 153.3987 | 6.9219 | 22.1614 | 0.9856%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 258 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 20.9682 | 1.9096 | 10.9806 | 20.9682 | 1.9096 | 10.9806 | 24.5121 | 2.2323 | 10.9806 | 0.9864%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 243 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 48.9805 | 1.7986 | 27.2333 | 48.9805 | 1.7986 | 27.2333 | 57.2588 | 2.1025 | 27.2333 | 0.9841%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 537 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 90.3866 | 3.9746 | 22.7412 | 90.3866 | 3.9746 | 22.7412 | 105.663 | 4.6463 | 22.7412 | 0.9831%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 483 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 79.3589 | 3.5749 | 22.1989 | 79.3589 | 3.5749 | 22.1989 | 92.7715 | 4.1791 | 22.1989 | 0.9843%
2028 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 1 | 100% | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074014 | 0 | 0 | 0.0074014 | 0 | 0 | 0.0086524 | 0 | 0%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 410 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 27.1554 | 3.0346 | 8.9486 | 27.1554 | 3.0346 | 8.9486 | 31.745 | 3.5475 | 8.9486 | 0.9977%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 206 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 14.7668 | 1.5247 | 9.6851 | 14.7668 | 1.5247 | 9.6851 | 17.2626 | 1.7824 | 9.6851 | 0.9957%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 93 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 16.7956 | 0.68833 | 24.4004 | 16.7956 | 0.68833 | 24.4004 | 19.6343 | 0.80467 | 24.4004 | 0.9986%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 730 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.0458 | 5.4031 | 3.525 | 19.0458 | 5.4031 | 3.525 | 22.2647 | 6.3162 | 3.525 | 0.9923%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 486 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 124.2819 | 3.5971 | 34.5506 | 124.2819 | 3.5971 | 34.5506 | 145.2869 | 4.2051 | 34.5506 | 0.9856%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 34 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 62.2159 | 0.25165 | 247.2329 | 62.2159 | 0.25165 | 247.2329 | 72.7311 | 0.29418 | 247.2329 | 0.9951%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 551 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 74.781 | 4.0782 | 18.3368 | 74.781 | 4.0782 | 18.3368 | 87.4199 | 4.7675 | 18.3368 | 0.9433%
2028 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 17 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 2.8019 | 0.12582 | 22.2685 | 2.8019 | 0.12582 | 22.2685 | 3.2755 | 0.14709 | 22.2685 | 0.9958%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 153 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 26.9206 | 1.1324 | 23.7726 | 26.9206 | 1.1324 | 23.7726 | 31.4705 | 1.3238 | 23.7726 | 0.9258%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 558 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 106.1678 | 4.13 | 25.7064 | 106.1678 | 4.13 | 25.7064 | 124.1113 | 4.828 | 25.7064 | 0.9926%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 846 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 17.6579 | 6.2616 | 2.82 | 17.6579 | 6.2616 | 2.82 | 20.6423 | 7.3199 | 2.82 | 0.9747%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 565 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 9.8935 | 4.1818 | 2.3658 | 9.8935 | 4.1818 | 2.3658 | 11.5656 | 4.8886 | 2.3658 | 0.7093%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 82.8796 | 2.7607 | 30.0208 | 82.8796 | 2.7607 | 30.0208 | 96.8872 | 3.2273 | 30.0208 | 0.9829%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 412 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 158.3796 | 3.0494 | 51.9381 | 158.3796 | 3.0494 | 51.9381 | 185.1476 | 3.5648 | 51.9381 | 0.989%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 66 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 22.1244 | 0.4885 | 45.2909 | 22.1244 | 0.4885 | 45.2909 | 25.8637 | 0.57106 | 45.2909 | 0.9937%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 433 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 46.29 | 3.2048 | 14.4438 | 46.29 | 3.2048 | 14.4438 | 54.1136 | 3.7465 | 14.4438 | 0.9631%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 933 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 158.374 | 6.9055 | 22.9343 | 158.374 | 6.9055 | 22.9343 | 185.1411 | 8.0727 | 22.9343 | 0.9714%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 34 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 25.5856 | 0.25165 | 101.6719 | 25.5856 | 0.25165 | 101.6719 | 29.9099 | 0.29418 | 101.6719 | 0.9712%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 415 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 172.0911 | 3.0716 | 56.0265 | 172.0911 | 3.0716 | 56.0265 | 201.1764 | 3.5907 | 56.0265 | 0.9923%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 24 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.098 | 0.17763 | 6.1815 | 1.098 | 0.17763 | 6.1815 | 1.2836 | 0.20766 | 6.1815 | 0.9928%
2028 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 62 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.1065 | 0.45889 | 0.23209 | 0.1065 | 0.45889 | 0.23209 | 0.1245 | 0.53645 | 0.23209 | 0.9883%
2028 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 36 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.2104 | 0.26645 | 4.5426 | 1.2104 | 0.26645 | 4.5426 | 1.415 | 0.31149 | 4.5426 | 0.9963%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 9 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.057723 | 0.066613 | 0.86655 | 0.057723 | 0.066613 | 0.86655 | 0.067479 | 0.077871 | 0.86655 | 0.9902%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 13 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.8502 | 0.096219 | 29.6217 | 2.8502 | 0.096219 | 29.6217 | 3.3319 | 0.11248 | 29.6217 | 0.9939%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 241 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 1.9514 | 1.7837 | 1.094 | 1.9514 | 1.7837 | 1.094 | 2.2812 | 2.0852 | 1.094 | 0.9666%
2028 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 1 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 1.8833 | 0 | 0 | 1.8833 | 0 | 1.6348 | 0.0074014 | 220.8819 | 1.6348 | 0.0074014 | 220.8819 | 1.9112 | 0.0086524 | 220.8819 | 0.9988%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 793 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 74.6087 | 5.8693 | 12.7116 | 74.6087 | 5.8693 | 12.7116 | 87.2184 | 6.8613 | 12.7116 | 0.9986%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 503 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 71.5161 | 3.7229 | 19.2096 | 71.5161 | 3.7229 | 19.2096 | 83.6031 | 4.3521 | 19.2096 | 0.9762%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 8 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.2032 | 0.059212 | 37.2094 | 2.2032 | 0.059212 | 37.2094 | 2.5756 | 0.069219 | 37.2094 | 0.9867%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 781 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 78.7826 | 5.7805 | 13.629 | 78.7826 | 5.7805 | 13.629 | 92.0977 | 6.7575 | 13.629 | 0.9973%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 1809 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 233.0596 | 13.3892 | 17.4065 | 233.0596 | 13.3892 | 17.4065 | 272.4494 | 15.6521 | 17.4065 | 0.9919%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 130 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 55.0956 | 0.96219 | 57.2608 | 55.0956 | 0.96219 | 57.2608 | 64.4074 | 1.1248 | 57.2608 | 0.9998%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 1320 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 134.5725 | 9.7699 | 13.7742 | 134.5725 | 9.7699 | 13.7742 | 157.3168 | 11.4211 | 13.7742 | 0.9833%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 741 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 100.8952 | 5.4845 | 18.3965 | 100.8952 | 5.4845 | 18.3965 | 117.9476 | 6.4114 | 18.3965 | 0.988%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 1020 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 46.544 | 7.5495 | 6.1652 | 46.544 | 7.5495 | 6.1652 | 54.4105 | 8.8254 | 6.1652 | 0.9625%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 585 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 11.6853 | 4.3298 | 2.6988 | 11.6853 | 4.3298 | 2.6988 | 13.6602 | 5.0616 | 2.6988 | 0.9181%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 352 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 67.9586 | 2.6053 | 26.0846 | 67.9586 | 2.6053 | 26.0846 | 79.4443 | 3.0456 | 26.0846 | 0.9835%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 1150 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 354.179 | 8.5117 | 41.611 | 354.179 | 8.5117 | 41.611 | 414.0392 | 9.9502 | 41.611 | 0.9889%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 577 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 29.0956 | 4.2706 | 6.8129 | 29.0956 | 4.2706 | 6.8129 | 34.0131 | 4.9924 | 6.8129 | 0.9191%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 762 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 194.0772 | 5.6399 | 34.4115 | 194.0772 | 5.6399 | 34.4115 | 226.8785 | 6.5931 | 34.4115 | 0.9908%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3119 | 0.066613 | 19.6944 | 1.3119 | 0.066613 | 19.6944 | 1.5336 | 0.077871 | 19.6944 | 0.9858%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 211 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.1012 | 1.5617 | 4.5471 | 7.1012 | 1.5617 | 4.5471 | 8.3014 | 1.8257 | 4.5471 | 0.9652%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 1555 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 476.1404 | 11.5092 | 41.3703 | 476.1404 | 11.5092 | 41.3703 | 556.6136 | 13.4544 | 41.3703 | 0.9927%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 16 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 49.4897 | 0.11842 | 417.906 | 49.4897 | 0.11842 | 417.906 | 57.8541 | 0.13844 | 417.906 | 0.9997%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 1096 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 278.4341 | 8.112 | 34.3238 | 278.4341 | 8.112 | 34.3238 | 325.4926 | 9.483 | 34.3238 | 0.9926%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 309 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 10.7977 | 2.287 | 4.7213 | 10.7977 | 2.287 | 4.7213 | 12.6227 | 2.6736 | 4.7213 | 0.9598%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 318 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 29.3766 | 2.3537 | 12.4812 | 29.3766 | 2.3537 | 12.4812 | 34.3416 | 2.7515 | 12.4812 | 0.9934%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 84 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.3128 | 0.62172 | 14.979 | 9.3128 | 0.62172 | 14.979 | 10.8867 | 0.7268 | 14.979 | 0.6902%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 116 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.2447 | 0.85857 | 15.4265 | 13.2447 | 0.85857 | 15.4265 | 15.4832 | 1.0037 | 15.4265 | 0.7661%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 3 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.7551 | 0.022204 | 169.1142 | 3.7551 | 0.022204 | 169.1142 | 4.3897 | 0.025957 | 169.1142 | 0.9947%
2028 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.52569 | 0.096219 | 5.4635 | 0.52569 | 0.096219 | 5.4635 | 0.61454 | 0.11248 | 5.4635 | 0.9691%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 75 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 112.1303 | 0.55511 | 201.9972 | 112.1303 | 0.55511 | 201.9972 | 131.0816 | 0.64893 | 201.9972 | 0.9966%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 913 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 130.2558 | 6.7575 | 19.2757 | 130.2558 | 6.7575 | 19.2757 | 152.2705 | 7.8996 | 19.2757 | 0.9905%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 1693 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 244.5755 | 12.5306 | 19.5182 | 244.5755 | 12.5306 | 19.5182 | 285.9116 | 14.6485 | 19.5182 | 0.9891%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 169 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 69.2066 | 1.2508 | 55.328 | 69.2066 | 1.2508 | 55.328 | 80.9033 | 1.4623 | 55.328 | 0.9946%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 109 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 37.5911 | 0.80676 | 46.5953 | 37.5911 | 0.80676 | 46.5953 | 43.9444 | 0.94311 | 46.5953 | 0.9952%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 442 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 126.2079 | 3.2714 | 38.5787 | 126.2079 | 3.2714 | 38.5787 | 147.5385 | 3.8243 | 38.5787 | 0.9843%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 1149 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 96.8131 | 8.5043 | 11.3841 | 96.8131 | 8.5043 | 11.3841 | 113.1756 | 9.9416 | 11.3841 | 0.9898%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 320 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 68.5917 | 2.3685 | 28.9604 | 68.5917 | 2.3685 | 28.9604 | 80.1845 | 2.7688 | 28.9604 | 0.9853%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 1391 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 199.9405 | 10.2954 | 19.4204 | 199.9405 | 10.2954 | 19.4204 | 233.7327 | 12.0355 | 19.4204 | 0.9839%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 943 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 193.8953 | 6.9796 | 27.7804 | 193.8953 | 6.9796 | 27.7804 | 226.6658 | 8.1592 | 27.7804 | 0.9748%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 373 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 78.7234 | 2.7607 | 28.5154 | 78.7234 | 2.7607 | 28.5154 | 92.0286 | 3.2273 | 28.5154 | 0.9912%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 264 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 43.7441 | 1.954 | 22.3872 | 43.7441 | 1.954 | 22.3872 | 51.1373 | 2.2842 | 22.3872 | 0.9732%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 149 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 74.4785 | 1.1028 | 67.5349 | 74.4785 | 1.1028 | 67.5349 | 87.0662 | 1.2892 | 67.5349 | 0.9953%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 246 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 55.4979 | 1.8208 | 30.4807 | 55.4979 | 1.8208 | 30.4807 | 64.8777 | 2.1285 | 30.4807 | 0.9803%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 603 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 28.408 | 4.4631 | 6.3651 | 28.408 | 4.4631 | 6.3651 | 33.2093 | 5.2174 | 6.3651 | 0.9369%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 61.4159 | 0.54031 | 113.6688 | 61.4159 | 0.54031 | 113.6688 | 71.7958 | 0.63162 | 113.6688 | 0.9955%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 24 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 44.7288 | 0.17763 | 251.8024 | 44.7288 | 0.17763 | 251.8024 | 52.2885 | 0.20766 | 251.8024 | 0.803%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 41 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.5843 | 0.30346 | 11.8115 | 3.5843 | 0.30346 | 11.8115 | 4.1901 | 0.35475 | 11.8115 | 0.6587%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 303 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 39.6418 | 2.2426 | 17.6764 | 39.6418 | 2.2426 | 17.6764 | 46.3417 | 2.6217 | 17.6764 | 0.9978%
2028 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 150 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 28.8759 | 1.1102 | 26.0092 | 28.8759 | 1.1102 | 26.0092 | 33.7562 | 1.2979 | 26.0092 | 0.9981%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 159 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.2323 | 1.1768 | 10.3943 | 12.2323 | 1.1768 | 10.3943 | 14.2997 | 1.3757 | 10.3943 | 0.9962%
2028 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 18 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 9.81 | 0.13323 | 73.6346 | 9.81 | 0.13323 | 73.6346 | 11.4681 | 0.15574 | 73.6346 | 0.9972%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 46 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 4.9377 | 0.34047 | 14.5027 | 4.9377 | 0.34047 | 14.5027 | 5.7722 | 0.39801 | 14.5027 | 0.3454%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 192 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 4.9835 | 1.4211 | 3.5068 | 4.9835 | 1.4211 | 3.5068 | 5.8257 | 1.6613 | 3.5068 | 0.75%
2028 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 12 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.6309 | 0.088817 | 7.1034 | 0.6309 | 0.088817 | 7.1034 | 0.73753 | 0.10383 | 7.1034 | 0.9665%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 1218 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 46.1797 | 9.015 | 5.1226 | 46.1797 | 9.015 | 5.1226 | 53.9845 | 10.5386 | 5.1226 | 0.8429%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 2353 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 57.164 | 17.4156 | 3.2823 | 57.164 | 17.4156 | 3.2823 | 66.8254 | 20.359 | 3.2823 | 0.9909%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 259 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 12.4546 | 1.917 | 6.497 | 12.4546 | 1.917 | 6.497 | 14.5596 | 2.241 | 6.497 | 0.9975%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.93603 | 0.029606 | 31.6166 | 0.93603 | 0.029606 | 31.6166 | 1.0942 | 0.034609 | 31.6166 | 0.9975%
2028 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 85 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 35.3525 | 0.62912 | 56.1933 | 35.3525 | 0.62912 | 56.1933 | 41.3275 | 0.73545 | 56.1933 | 0.9993%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 17 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.34116 | 0.12582 | 2.7114 | 0.34116 | 0.12582 | 2.7114 | 0.39882 | 0.14709 | 2.7114 | 0.9408%
2028 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 3 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.8001 | 0.022204 | 36.0336 | 0.8001 | 0.022204 | 36.0336 | 0.93533 | 0.025957 | 36.0336 | 0.3549%
2028 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 2.7537 | 0.037007 | 74.4097 | 2.7537 | 0.037007 | 74.4097 | 3.2191 | 0.043262 | 74.4097 | 0.7993%
2028 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 137 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.4844 | 1.014 | 3.4363 | 3.4844 | 1.014 | 3.4363 | 4.0733 | 1.1854 | 3.4363 | 0.299%
2028 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 312 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.1064 | 2.3093 | 0.4791 | 1.1064 | 2.3093 | 0.4791 | 1.2933 | 2.6995 | 0.4791 | 0.9512%
2028 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 504 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.16285 | 3.7303 | 0.043655 | 0.16285 | 3.7303 | 0.043655 | 0.19037 | 4.3608 | 0.043655 | 0.09583%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 358 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.4336 | 2.6497 | 2.8054 | 7.4336 | 2.6497 | 2.8054 | 8.6899 | 3.0975 | 2.8054 | 0.8082%
2028 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 1.3377 | 0 | 0 | 1.3377 | 0 | 1.1612 | 0.05181 | 22.4131 | 1.1612 | 0.05181 | 22.4131 | 1.3575 | 0.060567 | 22.4131 | 0.9989%
2028 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 68 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.844 | 0.5033 | 3.6639 | 1.844 | 0.5033 | 3.6639 | 2.1557 | 0.58836 | 3.6639 | 0.9981%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 696 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 21.5465 | 5.1514 | 4.1826 | 21.5465 | 5.1514 | 4.1826 | 25.1881 | 6.0221 | 4.1826 | 0.9929%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 645 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 13.8844 | 4.7739 | 2.9084 | 13.8844 | 4.7739 | 2.9084 | 16.231 | 5.5808 | 2.9084 | 0.9737%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 1826 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 35.3788 | 13.515 | 2.6177 | 35.3788 | 13.515 | 2.6177 | 41.3582 | 15.7992 | 2.6177 | 0.9874%
2028 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 1032 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 28.2802 | 7.6383 | 3.7024 | 28.2802 | 7.6383 | 3.7024 | 33.0599 | 8.9292 | 3.7024 | 0.9888%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 504 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 107.7148 | 3.7303 | 28.8754 | 107.7148 | 3.7303 | 28.8754 | 125.9198 | 4.3608 | 28.8754 | 0.9762%
2028 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 35 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 18.2459 | 0.25905 | 70.4337 | 18.2459 | 0.25905 | 70.4337 | 21.3297 | 0.30283 | 70.4337 | 0.9954%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 222 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 10.7092 | 1.6431 | 6.5176 | 10.7092 | 1.6431 | 6.5176 | 12.5192 | 1.9208 | 6.5176 | 0.9768%
2028 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 44 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.273 | 0.32566 | 6.9795 | 2.273 | 0.32566 | 6.9795 | 2.6571 | 0.3807 | 6.9795 | 0.6436%
2028 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 0.96218 | 0.14803 | 6.5 | 0.96218 | 0.14803 | 6.5 | 1.1248 | 0.17305 | 6.5 | 0.375%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 519 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.2383 | 3.8413 | 2.9256 | 11.2383 | 3.8413 | 2.9256 | 13.1378 | 4.4906 | 2.9256 | 0.9%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 109 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.3167 | 0.80676 | 2.8716 | 2.3167 | 0.80676 | 2.8716 | 2.7083 | 0.94311 | 2.8716 | 0.7028%
2028 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 263 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.3104 | 1.9466 | 4.2692 | 8.3104 | 1.9466 | 4.2692 | 9.715 | 2.2756 | 4.2692 | 0.995%
2028 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 195 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 6.9657 | 1.4433 | 4.8263 | 6.9657 | 1.4433 | 4.8263 | 8.143 | 1.6872 | 4.8263 | 0.9704%
2028 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 17 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 0.50007 | 0 | 0 | 0.50007 | 0 | 0.43409 | 0.12582 | 3.45 | 0.43409 | 0.12582 | 3.45 | 0.50746 | 0.14709 | 3.45 | 0.1609%
2028 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 160 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.54626 | 1.1842 | 0.46128 | 0.54626 | 1.1842 | 0.46128 | 0.63858 | 1.3844 | 0.46128 | 0.6647%
2028 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 23 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.090938 | 0.17023 | 0.5342 | 0.090938 | 0.17023 | 0.5342 | 0.10631 | 0.199 | 0.5342 | 0.9726%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 12.619 | 0.13323 | 94.7185 | 12.619 | 0.13323 | 94.7185 | 14.7517 | 0.15574 | 94.7185 | 0.9979%
2028 | 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 29 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.8095 | 0.21464 | 8.4305 | 1.8095 | 0.21464 | 8.4305 | 2.1154 | 0.25092 | 8.4305 | 0.9683%
2028 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 233 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.35975 | 1.7245 | 0.20861 | 0.35975 | 1.7245 | 0.20861 | 0.42055 | 2.016 | 0.20861 | 0.3335%
2028 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 2 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.2534 | 0.014803 | 152.229 | 2.2534 | 0.014803 | 152.229 | 2.6343 | 0.017305 | 152.229 | 0.9938%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 641 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 126.3066 | 4.7443 | 26.6227 | 126.3066 | 4.7443 | 26.6227 | 147.6539 | 5.5462 | 26.6227 | 0.9966%
2028 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 26 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.75687 | 0.19244 | 3.9331 | 0.75687 | 0.19244 | 3.9331 | 0.88479 | 0.22496 | 3.9331 | 0.9922%
2028 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.064962 | 0.0074014 | 8.777 | 0.064962 | 0.0074014 | 8.777 | 0.075942 | 0.0086524 | 8.777 | 0.986%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 875 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 96.8504 | 6.4763 | 14.9547 | 96.8504 | 6.4763 | 14.9547 | 113.2192 | 7.5708 | 14.9547 | 0.9884%
2028 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.05855 | 0.037007 | 1.5821 | 0.05855 | 0.037007 | 1.5821 | 0.068446 | 0.043262 | 1.5821 | 0.991%
2028 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 495 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 50.9281 | 3.6637 | 13.9007 | 50.9281 | 3.6637 | 13.9007 | 59.5355 | 4.2829 | 13.9007 | 0.9601%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 9 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4116 | 0.066613 | 21.1915 | 1.4116 | 0.066613 | 21.1915 | 1.6502 | 0.077871 | 21.1915 | 0.1888%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 1 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.83395 | 0.0074014 | 112.6733 | 0.83395 | 0.0074014 | 112.6733 | 0.97489 | 0.0086524 | 112.6733 | 0.1434%
2028 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 134 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.2532 | 0.99179 | 9.3298 | 9.2532 | 0.99179 | 9.3298 | 10.8171 | 1.1594 | 9.3298 | 0.9408%
2028 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 0.99585 | 0.037007 | 26.9097 | 0.99585 | 0.037007 | 26.9097 | 1.1642 | 0.043262 | 26.9097 | 0.9768%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 174 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 57.3752 | 1.2879 | 44.5511 | 57.3752 | 1.2879 | 44.5511 | 67.0723 | 1.5055 | 44.5511 | 0.9549%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.15954 | 0.022204 | 7.1849 | 0.15954 | 0.022204 | 7.1849 | 0.1865 | 0.025957 | 7.1849 | 0.9464%
2028 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 7 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.015009 | 0.05181 | 0.28969 | 0.015009 | 0.05181 | 0.28969 | 0.017546 | 0.060567 | 0.28969 | 0.9786%
2028 | 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 16 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.017906 | 0.11842 | 0.1512 | 0.017906 | 0.11842 | 0.1512 | 0.020932 | 0.13844 | 0.1512 | 0.1679%
2028 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 531 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 8.3461 | 3.9302 | 2.1236 | 8.3461 | 3.9302 | 2.1236 | 9.7567 | 4.5944 | 2.1236 | 0.8949%
2028 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 318 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 0.98668 | 2.3537 | 0.41921 | 0.98668 | 2.3537 | 0.41921 | 1.1534 | 2.7515 | 0.41921 | 0.372%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 31 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 3.938 | 0.22944 | 17.1633 | 3.938 | 0.22944 | 17.1633 | 4.6036 | 0.26822 | 17.1633 | 0.9425%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 10 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.35788 | 0.074014 | 4.8353 | 0.35788 | 0.074014 | 4.8353 | 0.41837 | 0.086524 | 4.8353 | 0.7619%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 186 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.57931 | 1.3767 | 0.4208 | 0.57931 | 1.3767 | 0.4208 | 0.67722 | 1.6093 | 0.4208 | 0.9924%
2028 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 47 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 7.8674 | 0.34787 | 22.6162 | 7.8674 | 0.34787 | 22.6162 | 9.1971 | 0.40666 | 22.6162 | 0.9545%
2028 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 21 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.8415 | 0.15543 | 18.2817 | 2.8415 | 0.15543 | 18.2817 | 3.3218 | 0.1817 | 18.2817 | 0.7837%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 892 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 37.4572 | 6.6021 | 5.6735 | 37.4572 | 6.6021 | 5.6735 | 43.7878 | 7.7179 | 5.6735 | 0.9981%
2028 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 70 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.44294 | 0.5181 | 0.85492 | 0.44294 | 0.5181 | 0.85492 | 0.5178 | 0.60567 | 0.85492 | 0.9266%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 102 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 70.7198 | 0.75495 | 93.6751 | 70.7198 | 0.75495 | 93.6751 | 82.6722 | 0.88254 | 93.6751 | 0.9507%
2028 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 169 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.36808 | 1.2508 | 0.29427 | 0.36808 | 1.2508 | 0.29427 | 0.43029 | 1.4623 | 0.29427 | 0.9943%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 58 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 23.7653 | 0.42928 | 55.3604 | 23.7653 | 0.42928 | 55.3604 | 27.7819 | 0.50184 | 55.3604 | 0.9983%
2028 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 108 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.739 | 0.79936 | 3.4265 | 2.739 | 0.79936 | 3.4265 | 3.2019 | 0.93446 | 3.4265 | 0.9343%
2028 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 3 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 11.4584 | 0.022204 | 516.0423 | 11.4584 | 0.022204 | 516.0423 | 13.395 | 0.025957 | 516.0423 | 0.7976%
2028 | 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 7 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.1782 | 0.05181 | 42.0413 | 2.1782 | 0.05181 | 42.0413 | 2.5463 | 0.060567 | 42.0413 | 0.9997%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 161 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 98.9626 | 1.1916 | 83.048 | 98.9626 | 1.1916 | 83.048 | 115.6885 | 1.393 | 83.048 | 0.9951%
2028 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.2677 | 0.37007 | 30.4472 | 11.2677 | 0.37007 | 30.4472 | 13.172 | 0.43262 | 30.4472 | 0.9951%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 423 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.3565 | 3.1308 | 1.0721 | 3.3565 | 3.1308 | 1.0721 | 3.9238 | 3.66 | 1.0721 | 0.997%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 106 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.1483 | 0.78455 | 1.4637 | 1.1483 | 0.78455 | 1.4637 | 1.3424 | 0.91715 | 1.4637 | 0.9965%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.21519 | 0.029606 | 7.2684 | 0.21519 | 0.029606 | 7.2684 | 0.25156 | 0.034609 | 7.2684 | 0.9021%
2028 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 463 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.111 | 3.4269 | 0.32421 | 1.111 | 3.4269 | 0.32421 | 1.2988 | 4.006 | 0.32421 | 0.3693%
2028 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 343 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 8.4306 | 2.5387 | 3.3208 | 8.4306 | 2.5387 | 3.3208 | 9.8554 | 2.9678 | 3.3208 | 0.9433%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 417 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.0101 | 3.0864 | 4.2153 | 13.0101 | 3.0864 | 4.2153 | 15.2089 | 3.608 | 4.2153 | 0.9785%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 286 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 43.8007 | 2.1168 | 20.6918 | 43.8007 | 2.1168 | 20.6918 | 51.2036 | 2.4746 | 20.6918 | 0.9856%
2028 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 5.4844 | 0.14063 | 38.9998 | 5.4844 | 0.14063 | 38.9998 | 6.4114 | 0.1644 | 38.9998 | 0.9902%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 786 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 59.4325 | 5.8175 | 10.2161 | 59.4325 | 5.8175 | 10.2161 | 69.4773 | 6.8008 | 10.2161 | 0.99%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 1534 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 24.8952 | 11.3538 | 2.1927 | 24.8952 | 11.3538 | 2.1927 | 29.1028 | 13.2727 | 2.1927 | 0.9473%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 454 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 89.7491 | 3.3603 | 26.709 | 89.7491 | 3.3603 | 26.709 | 104.9177 | 3.9282 | 26.709 | 0.9831%
2028 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 283 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 44.5423 | 2.0946 | 21.2652 | 44.5423 | 2.0946 | 21.2652 | 52.0704 | 2.4486 | 21.2652 | 0.9811%
2028 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 200 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.5273 | 1.4803 | 3.7339 | 5.5273 | 1.4803 | 3.7339 | 6.4615 | 1.7305 | 3.7339 | 0.695%
2028 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.25797 | 0.029606 | 8.7134 | 0.25797 | 0.029606 | 8.7134 | 0.30156 | 0.034609 | 8.7134 | 0.9988%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 330 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 32.1846 | 2.4425 | 13.177 | 32.1846 | 2.4425 | 13.177 | 37.6241 | 2.8553 | 13.177 | 0.9914%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 793 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 27.3464 | 5.8693 | 4.6592 | 27.3464 | 5.8693 | 4.6592 | 31.9682 | 6.8613 | 4.6592 | 0.9371%
2028 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 52 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.016377 | 0.38488 | 0.042552 | 0.016377 | 0.38488 | 0.042552 | 0.019145 | 0.44992 | 0.042552 | 0.02003%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 1644 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.1367 | 12.168 | 1.1618 | 14.1367 | 12.168 | 1.1618 | 16.5259 | 14.2245 | 1.1618 | 0.789%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 433 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 30.7262 | 3.2048 | 9.5875 | 30.7262 | 3.2048 | 9.5875 | 35.9193 | 3.7465 | 9.5875 | 0.9517%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 341 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 80.525 | 2.5239 | 31.9051 | 80.525 | 2.5239 | 31.9051 | 94.1347 | 2.9505 | 31.9051 | 0.9933%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 1098 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 58.6141 | 8.1268 | 7.2125 | 58.6141 | 8.1268 | 7.2125 | 68.5205 | 9.5003 | 7.2125 | 0.9757%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 329 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 51.2664 | 2.4351 | 21.0533 | 51.2664 | 2.4351 | 21.0533 | 59.931 | 2.8466 | 21.0533 | 0.9932%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 505 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 32.667 | 3.7377 | 8.7398 | 32.667 | 3.7377 | 8.7398 | 38.1881 | 4.3694 | 8.7398 | 0.9948%

## Veg Detail Inspection
Veg Detail Inspection - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 255000 | 2849951.0757 | 27730.1327 | 0.973% | 26452.6627 | 4648.9198 | 5.6901 | 26452.6627 | 4648.9198 | 5.6901 | 27866.0648 | 4897.3179 | 5.6901
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 255000 | 2849951.0757 | 27730.1327 | 0.973% | 25234.0431 | 4434.7536 | 5.6901 | 25234.0431 | 4434.7536 | 5.6901 | 28002.6631 | 4921.3244 | 5.6901
[9 empty] | Capital Cost only in Year 0 | 0.019111 | K$/inspection | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 255000 | 2849951.0757 | 27730.1327 | 0.973% | 24071.5627 | 4230.4537 | 5.6901 | 24071.5627 | 4230.4537 | 5.6901 | 28139.9311 | 4945.4485 | 5.6901
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 765000 | 8549853.2272 | 83190.3982 | 0.973% | 75758.2685 | 13314.127 | 5.6901 | 75758.2685 | 13314.127 | 5.6901 | 84008.659 | 14764.0908 | 5.6901
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 1% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.1068 | 0.10939 | 10.1183 | 1.1068 | 0.10939 | 10.1183 | 1.1659 | 0.11523 | 10.1183 | 0.9903%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 79 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.869 | 1.4403 | 2.6863 | 3.869 | 1.4403 | 2.6863 | 4.0757 | 1.5172 | 2.6863 | 0.9915%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 1219 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 36.8178 | 22.2237 | 1.6567 | 36.8178 | 22.2237 | 1.6567 | 38.785 | 23.4111 | 1.6567 | 0.9141%
2026 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 20 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 1.0899 | 0.36462 | 2.9892 | 1.0899 | 0.36462 | 2.9892 | 1.1482 | 0.3841 | 2.9892 | 0.9976%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 1445 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 332.0782 | 26.3439 | 12.6055 | 332.0782 | 26.3439 | 12.6055 | 349.8216 | 27.7515 | 12.6055 | 0.9902%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 194 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 66.0788 | 3.5368 | 18.6831 | 66.0788 | 3.5368 | 18.6831 | 69.6095 | 3.7258 | 18.6831 | 0.9818%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 618 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 179.0433 | 11.2668 | 15.8912 | 179.0433 | 11.2668 | 15.8912 | 188.6098 | 11.8688 | 15.8912 | 0.997%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 334 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 47.787 | 6.0892 | 7.8479 | 47.787 | 6.0892 | 7.8479 | 50.3403 | 6.4145 | 7.8479 | 0.9951%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 70 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 13.1718 | 1.2762 | 10.3214 | 13.1718 | 1.2762 | 10.3214 | 13.8756 | 1.3444 | 10.3214 | 0.9958%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 28 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 7.5473 | 0.51047 | 14.785 | 7.5473 | 0.51047 | 14.785 | 7.9506 | 0.53774 | 14.785 | 0.996%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 473 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 93.1374 | 8.6233 | 10.8007 | 93.1374 | 8.6233 | 10.8007 | 98.1139 | 9.084 | 10.8007 | 0.9962%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 18 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.5753 | 0.32816 | 20.037 | 6.5753 | 0.32816 | 20.037 | 6.9266 | 0.34569 | 20.037 | 0.9922%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 262 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 47.9789 | 4.7765 | 10.0447 | 47.9789 | 4.7765 | 10.0447 | 50.5425 | 5.0318 | 10.0447 | 0.9916%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 428 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 27.3593 | 7.8029 | 3.5063 | 27.3593 | 7.8029 | 3.5063 | 28.8211 | 8.2198 | 3.5063 | 0.9924%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 1949 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 86.7029 | 35.5323 | 2.4401 | 86.7029 | 35.5323 | 2.4401 | 91.3356 | 37.4309 | 2.4401 | 0.9598%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 1169 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 35.0604 | 21.3121 | 1.6451 | 35.0604 | 21.3121 | 1.6451 | 36.9337 | 22.4508 | 1.6451 | 0.9739%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 235 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.8971 | 4.2843 | 1.143 | 4.8971 | 4.2843 | 1.143 | 5.1588 | 4.5132 | 1.143 | 0.8768%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 100 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 48.0307 | 1.8231 | 26.3455 | 48.0307 | 1.8231 | 26.3455 | 50.597 | 1.9205 | 26.3455 | 0.9826%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 240 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 111.1363 | 4.3755 | 25.3999 | 111.1363 | 4.3755 | 25.3999 | 117.0745 | 4.6092 | 25.3999 | 0.9858%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 288 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 20.4052 | 5.2505 | 3.8863 | 20.4052 | 5.2505 | 3.8863 | 21.4955 | 5.5311 | 3.8863 | 0.9945%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 762 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 62.3119 | 13.8921 | 4.4854 | 62.3119 | 13.8921 | 4.4854 | 65.6414 | 14.6343 | 4.4854 | 0.9866%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 1434 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 239.4495 | 26.1433 | 9.1591 | 239.4495 | 26.1433 | 9.1591 | 252.2436 | 27.5402 | 9.1591 | 0.9914%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 1366 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 266.8268 | 24.9036 | 10.7144 | 266.8268 | 24.9036 | 10.7144 | 281.0837 | 26.2343 | 10.7144 | 0.9849%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 1131 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 252.5213 | 20.6193 | 12.2468 | 252.5213 | 20.6193 | 12.2468 | 266.0138 | 21.721 | 12.2468 | 0.9916%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 1778 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 148.3449 | 32.4148 | 4.5765 | 148.3449 | 32.4148 | 4.5765 | 156.2711 | 34.1468 | 4.5765 | 0.9745%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 92 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14883 | 1.6773 | 0.088735 | 0.14883 | 1.6773 | 0.088735 | 0.15678 | 1.7669 | 0.088735 | 0.8684%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.032939 | 0.45578 | 0.07227 | 0.032939 | 0.45578 | 0.07227 | 0.034699 | 0.48013 | 0.07227 | 0.1275%
2026 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.020949 | 0.072924 | 0.28727 | 0.020949 | 0.072924 | 0.28727 | 0.022068 | 0.076821 | 0.28727 | 0.3435%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 21 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.9161 | 0.38285 | 18.0646 | 6.9161 | 0.38285 | 18.0646 | 7.2856 | 0.40331 | 18.0646 | 0.9924%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 183 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 8.238 | 3.3363 | 2.4692 | 8.238 | 3.3363 | 2.4692 | 8.6781 | 3.5145 | 2.4692 | 0.9393%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 39 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1825 | 0.71101 | 1.6632 | 1.1825 | 0.71101 | 1.6632 | 1.2457 | 0.749 | 1.6632 | 0.8802%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 564 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 56.0593 | 10.2823 | 5.452 | 56.0593 | 10.2823 | 5.452 | 59.0546 | 10.8317 | 5.452 | 0.9962%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 628 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 47.4306 | 11.4491 | 4.1427 | 47.4306 | 11.4491 | 4.1427 | 49.9649 | 12.0608 | 4.1427 | 0.9962%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 414 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 23.945 | 7.5477 | 3.1725 | 23.945 | 7.5477 | 3.1725 | 25.2244 | 7.9509 | 3.1725 | 0.9984%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 100 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.89815 | 1.8231 | 0.49265 | 0.89815 | 1.8231 | 0.49265 | 0.94614 | 1.9205 | 0.49265 | 0.9877%
2026 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 0.54035 | 0 | 0 | 0.54035 | 0 | 0.51545 | 0.018231 | 28.2733 | 0.51545 | 0.018231 | 28.2733 | 0.54299 | 0.019205 | 28.2733 | 0.9875%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 43 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 20.3953 | 0.78394 | 26.0165 | 20.3953 | 0.78394 | 26.0165 | 21.485 | 0.82582 | 26.0165 | 0.9968%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 120 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 40.3024 | 2.1877 | 18.422 | 40.3024 | 2.1877 | 18.422 | 42.4558 | 2.3046 | 18.422 | 0.9992%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 113 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.759 | 2.0601 | 1.8246 | 3.759 | 2.0601 | 1.8246 | 3.9598 | 2.1702 | 1.8246 | 0.945%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 69 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.4758 | 1.2579 | 5.9428 | 7.4758 | 1.2579 | 5.9428 | 7.8752 | 1.3252 | 5.9428 | 0.994%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 2029 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 40.5406 | 36.9908 | 1.096 | 40.5406 | 36.9908 | 1.096 | 42.7067 | 38.9673 | 1.096 | 0.9112%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 24 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 2.0214 | 0.43755 | 4.6199 | 2.0214 | 0.43755 | 4.6199 | 2.1294 | 0.46092 | 4.6199 | 0.8819%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 25 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.9041 | 0.45578 | 4.1777 | 1.9041 | 0.45578 | 4.1777 | 2.0059 | 0.48013 | 4.1777 | 0.9662%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 7 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.3124 | 0.12762 | 18.1201 | 2.3124 | 0.12762 | 18.1201 | 2.436 | 0.13444 | 18.1201 | 0.9775%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 151 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 37.1689 | 2.7529 | 13.5018 | 37.1689 | 2.7529 | 13.5018 | 39.1549 | 2.9 | 13.5018 | 0.9826%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 214 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 96.2066 | 3.9014 | 24.6592 | 96.2066 | 3.9014 | 24.6592 | 101.3471 | 4.1099 | 24.6592 | 0.9977%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 457 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 97.5658 | 8.3316 | 11.7103 | 97.5658 | 8.3316 | 11.7103 | 102.7789 | 8.7768 | 11.7103 | 0.9908%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 85 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 57.3987 | 1.5496 | 37.04 | 57.3987 | 1.5496 | 37.04 | 60.4656 | 1.6324 | 37.04 | 0.9788%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 52 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 20.009 | 0.94802 | 21.1063 | 20.009 | 0.94802 | 21.1063 | 21.0782 | 0.99867 | 21.1063 | 0.9469%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 334 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 80.0347 | 6.0892 | 13.1438 | 80.0347 | 6.0892 | 13.1438 | 84.311 | 6.4145 | 13.1438 | 0.9648%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 166 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 14.6539 | 3.0264 | 4.8421 | 14.6539 | 3.0264 | 4.8421 | 15.4368 | 3.1881 | 4.8421 | 0.9856%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 452 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 33.4415 | 8.2404 | 4.0582 | 33.4415 | 8.2404 | 4.0582 | 35.2284 | 8.6807 | 4.0582 | 0.9842%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 766 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 27.8656 | 13.965 | 1.9954 | 27.8656 | 13.965 | 1.9954 | 29.3545 | 14.7112 | 1.9954 | 0.979%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 112 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 13.083 | 2.0419 | 6.4073 | 13.083 | 2.0419 | 6.4073 | 13.782 | 2.151 | 6.4073 | 0.9892%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 544 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 40.471 | 9.9177 | 4.0807 | 40.471 | 9.9177 | 4.0807 | 42.6334 | 10.4476 | 4.0807 | 0.9866%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 27 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.9122 | 0.49224 | 7.9478 | 3.9122 | 0.49224 | 7.9478 | 4.1212 | 0.51854 | 7.9478 | 0.9965%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 77 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.3418 | 1.4038 | 3.0929 | 4.3418 | 1.4038 | 3.0929 | 4.5738 | 1.4788 | 3.0929 | 0.9977%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 129 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 11.1645 | 2.3518 | 4.7472 | 11.1645 | 2.3518 | 4.7472 | 11.761 | 2.4775 | 4.7472 | 0.9935%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 20 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.5017 | 0.36462 | 4.1186 | 1.5017 | 0.36462 | 4.1186 | 1.582 | 0.3841 | 4.1186 | 0.9948%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 173 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 17.7477 | 3.154 | 5.6271 | 17.7477 | 3.154 | 5.6271 | 18.696 | 3.3225 | 5.6271 | 0.9905%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 137 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 56.9641 | 2.4977 | 22.807 | 56.9641 | 2.4977 | 22.807 | 60.0078 | 2.6311 | 22.807 | 0.9304%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 121 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 61.4624 | 2.206 | 27.862 | 61.4624 | 2.206 | 27.862 | 64.7464 | 2.3238 | 27.862 | 0.9454%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 740 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 111.2495 | 13.491 | 8.2462 | 111.2495 | 13.491 | 8.2462 | 117.1938 | 14.2118 | 8.2462 | 0.9926%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 333 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 34.5034 | 6.0709 | 5.6834 | 34.5034 | 6.0709 | 5.6834 | 36.3469 | 6.3953 | 5.6834 | 0.9815%
2026 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | Non-HFTD---15 | 123 | 100% | 14.0801 | 87.11% | 0% | 12.89% | 0.12265 | 0 | 0 | 0.12265 | 0 | 0.117 | 2.2424 | 0.052176 | 0.117 | 2.2424 | 0.052176 | 0.12325 | 2.3622 | 0.052176 | 0.8711%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 76 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.6887 | 1.3856 | 2.6622 | 3.6887 | 1.3856 | 2.6622 | 3.8858 | 1.4596 | 2.6622 | 0.9046%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 17 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 19.3034 | 0.30993 | 62.2834 | 19.3034 | 0.30993 | 62.2834 | 20.3348 | 0.32649 | 62.2834 | 0.8554%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 221 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 41.1347 | 4.0291 | 10.2095 | 41.1347 | 4.0291 | 10.2095 | 43.3326 | 4.2443 | 10.2095 | 0.9867%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.55516 | 0.072924 | 7.6129 | 0.55516 | 0.072924 | 7.6129 | 0.58483 | 0.076821 | 7.6129 | 0.9994%
2026 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 15 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.27347 | 0 | 0 | 0.27347 | 0 | 0 | 0.28808 | 0 | 0%
2026 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 23 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.41931 | 0 | 0 | 0.41931 | 0 | 0 | 0.44172 | 0 | 0%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 149 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 151.1246 | 2.7164 | 55.6336 | 151.1246 | 2.7164 | 55.6336 | 159.1994 | 2.8616 | 55.6336 | 0.9909%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 19 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.47647 | 0.34639 | 1.3755 | 0.47647 | 0.34639 | 1.3755 | 0.50193 | 0.3649 | 1.3755 | 0.2981%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.77236 | 0.018231 | 42.365 | 0.77236 | 0.018231 | 42.365 | 0.81363 | 0.019205 | 42.365 | 0.9995%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 334 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 77.2532 | 6.0892 | 12.687 | 77.2532 | 6.0892 | 12.687 | 81.381 | 6.4145 | 12.687 | 0.9925%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 831 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 351.4153 | 15.15 | 23.1957 | 351.4153 | 15.15 | 23.1957 | 370.1919 | 15.9595 | 23.1957 | 0.9936%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.070593 | 0.16408 | 0.43024 | 0.070593 | 0.16408 | 0.43024 | 0.074365 | 0.17285 | 0.43024 | 0.895%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 124 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.502 | 2.2607 | 1.5491 | 3.502 | 2.2607 | 1.5491 | 3.6891 | 2.3814 | 1.5491 | 0.8771%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 1030 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 48.5729 | 18.778 | 2.5867 | 48.5729 | 18.778 | 2.5867 | 51.1682 | 19.7813 | 2.5867 | 0.9246%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 96 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 28.8489 | 1.7502 | 16.4834 | 28.8489 | 1.7502 | 16.4834 | 30.3904 | 1.8437 | 16.4834 | 0.9907%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 316 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 36.6006 | 5.761 | 6.3532 | 36.6006 | 5.761 | 6.3532 | 38.5562 | 6.0688 | 6.3532 | 0.9899%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 356 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 28.7225 | 6.4903 | 4.4255 | 28.7225 | 6.4903 | 4.4255 | 30.2572 | 6.837 | 4.4255 | 0.9527%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 882 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 16.0328 | 16.0798 | 0.99708 | 16.0328 | 16.0798 | 0.99708 | 16.8894 | 16.939 | 0.99708 | 0.8154%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 441 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.9249 | 8.0399 | 2.1051 | 16.9249 | 8.0399 | 2.1051 | 17.8293 | 8.4695 | 2.1051 | 0.9501%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 1391 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 173.5015 | 25.3594 | 6.8417 | 173.5015 | 25.3594 | 6.8417 | 182.772 | 26.7144 | 6.8417 | 0.97%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 593 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 38.089 | 10.811 | 3.5232 | 38.089 | 10.811 | 3.5232 | 40.1242 | 11.3887 | 3.5232 | 0.991%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 236 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.8695 | 4.3025 | 4.1533 | 17.8695 | 4.3025 | 4.1533 | 18.8243 | 4.5324 | 4.1533 | 0.7065%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 756 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 40.7977 | 13.7827 | 2.9601 | 40.7977 | 13.7827 | 2.9601 | 42.9776 | 14.5191 | 2.9601 | 0.9752%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 864 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 53.0508 | 15.7516 | 3.368 | 53.0508 | 15.7516 | 3.368 | 55.8853 | 16.5933 | 3.368 | 0.9686%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 245 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.3625 | 4.4666 | 1.4245 | 6.3625 | 4.4666 | 1.4245 | 6.7025 | 4.7053 | 1.4245 | 0.7976%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 575 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 108.5713 | 10.4829 | 10.357 | 108.5713 | 10.4829 | 10.357 | 114.3724 | 11.043 | 10.357 | 0.9877%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 39.1596 | 6.5085 | 6.0167 | 39.1596 | 6.5085 | 6.0167 | 41.252 | 6.8562 | 6.0167 | 0.981%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 870 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 93.29 | 15.861 | 5.8817 | 93.29 | 15.861 | 5.8817 | 98.2747 | 16.7085 | 5.8817 | 0.9713%
2026 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 30 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.6098 | 0.54693 | 4.7717 | 2.6098 | 0.54693 | 4.7717 | 2.7492 | 0.57616 | 4.7717 | 0.6764%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 270 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 31.7101 | 4.9224 | 6.442 | 31.7101 | 4.9224 | 6.442 | 33.4045 | 5.1854 | 6.442 | 0.9774%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 451 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 45.9869 | 8.2222 | 5.593 | 45.9869 | 8.2222 | 5.593 | 48.444 | 8.6615 | 5.593 | 0.977%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 1054 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 121.6439 | 19.2155 | 6.3305 | 121.6439 | 19.2155 | 6.3305 | 128.1435 | 20.2422 | 6.3305 | 0.968%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 77 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.9263 | 1.4038 | 9.9205 | 13.9263 | 1.4038 | 9.9205 | 14.6704 | 1.4788 | 9.9205 | 0.8924%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 36 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 22.1145 | 0.65632 | 33.6948 | 22.1145 | 0.65632 | 33.6948 | 23.2961 | 0.69139 | 33.6948 | 0.7823%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.41426 | 0.16408 | 2.5247 | 0.41426 | 0.16408 | 2.5247 | 0.43639 | 0.17285 | 2.5247 | 0.9121%
2026 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 3 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0012779 | 0 | 0 | 0.0012779 | 0 | 0.001219 | 0.054693 | 0.022288 | 0.001219 | 0.054693 | 0.022288 | 0.0012841 | 0.057616 | 0.022288 | 0.1338%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 1311 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 107.1917 | 23.9009 | 4.4848 | 107.1917 | 23.9009 | 4.4848 | 112.9191 | 25.178 | 4.4848 | 0.9429%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 11 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 18.4509 | 0.20054 | 92.0051 | 18.4509 | 0.20054 | 92.0051 | 19.4367 | 0.21126 | 92.0051 | 0.9974%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 338 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 40.0342 | 6.1621 | 6.4968 | 40.0342 | 6.1621 | 6.4968 | 42.1733 | 6.4913 | 6.4968 | 0.9922%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 17 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 6.2019 | 0.30993 | 20.0107 | 6.2019 | 0.30993 | 20.0107 | 6.5333 | 0.32649 | 20.0107 | 0.9914%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 85 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.9995 | 1.5496 | 1.2903 | 1.9995 | 1.5496 | 1.2903 | 2.1063 | 1.6324 | 1.2903 | 0.6623%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 180 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.3429 | 3.2816 | 1.0187 | 3.3429 | 3.2816 | 1.0187 | 3.5215 | 3.4569 | 1.0187 | 0.7437%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 481 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 15.1178 | 8.7691 | 1.724 | 15.1178 | 8.7691 | 1.724 | 15.9255 | 9.2377 | 1.724 | 0.9193%
2026 | 196 | 196-43F | Tier-2 | Tier-2---17 | Tier-2---9 | 138 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.048193 | 0 | 0 | 0.048193 | 0 | 0.045972 | 2.5159 | 0.018273 | 0.045972 | 2.5159 | 0.018273 | 0.048429 | 2.6503 | 0.018273 | 0.0514%
2026 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 2 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.7392 | 0.036462 | 47.6988 | 1.7392 | 0.036462 | 47.6988 | 1.8321 | 0.03841 | 47.6988 | 0.9934%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 27 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.060854 | 0.49224 | 0.12363 | 0.060854 | 0.49224 | 0.12363 | 0.064106 | 0.51854 | 0.12363 | 0.9638%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 103 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.8681 | 1.8778 | 4.7226 | 8.8681 | 1.8778 | 4.7226 | 9.3419 | 1.9781 | 4.7226 | 0.9553%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 301 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.5085 | 5.4875 | 0.82158 | 4.5085 | 5.4875 | 0.82158 | 4.7494 | 5.7808 | 0.82158 | 0.9636%
2026 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 9 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 1.2217 | 0 | 0 | 1.2217 | 0 | 1.1655 | 0.16408 | 7.103 | 1.1655 | 0.16408 | 7.103 | 1.2277 | 0.17285 | 7.103 | 0.9852%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 66 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 12.1749 | 1.2032 | 10.1183 | 12.1749 | 1.2032 | 10.1183 | 12.8254 | 1.2675 | 10.1183 | 0.9978%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 385 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 28.3235 | 7.019 | 4.0353 | 28.3235 | 7.019 | 4.0353 | 29.8368 | 7.394 | 4.0353 | 0.9975%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1294 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 80.5201 | 23.591 | 3.4132 | 80.5201 | 23.591 | 3.4132 | 84.8224 | 24.8515 | 3.4132 | 0.9974%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 202 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.2815 | 3.6827 | 1.1626 | 4.2815 | 3.6827 | 1.1626 | 4.5103 | 3.8794 | 1.1626 | 0.901%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 360 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.4882 | 6.5632 | 1.2933 | 8.4882 | 6.5632 | 1.2933 | 8.9417 | 6.9139 | 1.2933 | 0.8573%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 240 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.1468 | 4.3755 | 0.2621 | 1.1468 | 4.3755 | 0.2621 | 1.2081 | 4.6092 | 0.2621 | 0.7047%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 183 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.5407 | 3.3363 | 0.46179 | 1.5407 | 3.3363 | 0.46179 | 1.623 | 3.5145 | 0.46179 | 0.5082%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 410 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 10.2406 | 7.4747 | 1.37 | 10.2406 | 7.4747 | 1.37 | 10.7877 | 7.8741 | 1.37 | 0.8949%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 321 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 14.5454 | 5.8522 | 2.4855 | 14.5454 | 5.8522 | 2.4855 | 15.3226 | 6.1649 | 2.4855 | 0.8426%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 1148 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 16.4236 | 20.9293 | 0.78472 | 16.4236 | 20.9293 | 0.78472 | 17.3012 | 22.0475 | 0.78472 | 0.9106%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 386 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.8295 | 7.0372 | 2.2494 | 15.8295 | 7.0372 | 2.2494 | 16.6753 | 7.4132 | 2.2494 | 0.9543%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 267 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 14.2272 | 4.8677 | 2.9228 | 14.2272 | 4.8677 | 2.9228 | 14.9874 | 5.1278 | 2.9228 | 0.9497%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 39 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.7626 | 0.71101 | 8.1048 | 5.7626 | 0.71101 | 8.1048 | 6.0705 | 0.749 | 8.1048 | 0.9907%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 1799 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 46.2307 | 32.7977 | 1.4096 | 46.2307 | 32.7977 | 1.4096 | 48.7009 | 34.5501 | 1.4096 | 0.9915%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 23 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.825 | 0.41931 | 28.2008 | 11.825 | 0.41931 | 28.2008 | 12.4568 | 0.44172 | 28.2008 | 0.9792%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 658 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 9.206 | 11.996 | 0.76742 | 9.206 | 11.996 | 0.76742 | 9.6979 | 12.637 | 0.76742 | 0.9662%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 63 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.4204 | 1.1486 | 2.1073 | 2.4204 | 1.1486 | 2.1073 | 2.5497 | 1.2099 | 2.1073 | 0.9706%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 268 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.756 | 4.8859 | 2.8154 | 13.756 | 4.8859 | 2.8154 | 14.491 | 5.147 | 2.8154 | 0.9727%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 413 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 25.2035 | 7.5294 | 3.3473 | 25.2035 | 7.5294 | 3.3473 | 26.5502 | 7.9317 | 3.3473 | 0.9578%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 105 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.624 | 1.9143 | 5.0275 | 9.624 | 1.9143 | 5.0275 | 10.1382 | 2.0165 | 5.0275 | 0.9712%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 94 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.97889 | 1.7137 | 0.57121 | 0.97889 | 1.7137 | 0.57121 | 1.0312 | 1.8053 | 0.57121 | 0.9778%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 160 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 20.3743 | 2.917 | 6.9848 | 20.3743 | 2.917 | 6.9848 | 21.463 | 3.0728 | 6.9848 | 0.9872%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 125 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.7268 | 2.2789 | 6.0235 | 13.7268 | 2.2789 | 6.0235 | 14.4603 | 2.4006 | 6.0235 | 0.9782%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 1694 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 247.9614 | 30.8834 | 8.029 | 247.9614 | 30.8834 | 8.029 | 261.2103 | 32.5336 | 8.029 | 0.9891%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 980 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 63.2206 | 17.8664 | 3.5385 | 63.2206 | 17.8664 | 3.5385 | 66.5986 | 18.8211 | 3.5385 | 0.9941%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 1791 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.4973 | 32.6518 | 0.13774 | 4.4973 | 32.6518 | 0.13774 | 4.7376 | 34.3965 | 0.13774 | 0.974%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 892 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.7358 | 16.2621 | 0.22973 | 3.7358 | 16.2621 | 0.22973 | 3.9354 | 17.131 | 0.22973 | 0.9786%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 433 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.8339 | 7.894 | 0.61235 | 4.8339 | 7.894 | 0.61235 | 5.0922 | 8.3158 | 0.61235 | 0.9871%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 20.875 | 5.7975 | 3.6007 | 20.875 | 5.7975 | 3.6007 | 21.9903 | 6.1072 | 3.6007 | 0.9909%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 1357 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 14.0738 | 24.7395 | 0.56888 | 14.0738 | 24.7395 | 0.56888 | 14.8257 | 26.0614 | 0.56888 | 0.8569%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 617 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 211.6306 | 11.2486 | 18.814 | 211.6306 | 11.2486 | 18.814 | 222.9383 | 11.8496 | 18.814 | 0.9924%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 729 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 119.0085 | 13.2904 | 8.9544 | 119.0085 | 13.2904 | 8.9544 | 125.3673 | 14.0006 | 8.9544 | 0.9821%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 471 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 184.0533 | 8.5868 | 21.4344 | 184.0533 | 8.5868 | 21.4344 | 193.8875 | 9.0456 | 21.4344 | 0.99%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 156 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 13.2167 | 2.844 | 4.6471 | 13.2167 | 2.844 | 4.6471 | 13.9229 | 2.996 | 4.6471 | 0.9809%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 354 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 51.2828 | 6.4538 | 7.9462 | 51.2828 | 6.4538 | 7.9462 | 54.0229 | 6.7986 | 7.9462 | 0.9892%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 445 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 132.853 | 8.1128 | 16.3757 | 132.853 | 8.1128 | 16.3757 | 139.9515 | 8.5463 | 16.3757 | 0.9919%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.6793 | 0.12762 | 5.3229 | 0.6793 | 0.12762 | 5.3229 | 0.71559 | 0.13444 | 5.3229 | 0.999%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 997 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 17.1386 | 18.1764 | 0.94291 | 17.1386 | 18.1764 | 0.94291 | 18.0544 | 19.1476 | 0.94291 | 0.8922%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 790 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 22.8579 | 14.4025 | 1.5871 | 22.8579 | 14.4025 | 1.5871 | 24.0792 | 15.1721 | 1.5871 | 0.8785%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 1010 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 100.6039 | 18.4134 | 5.4636 | 100.6039 | 18.4134 | 5.4636 | 105.9793 | 19.3972 | 5.4636 | 0.9868%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 866 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 33.0238 | 15.7881 | 2.0917 | 33.0238 | 15.7881 | 2.0917 | 34.7883 | 16.6317 | 2.0917 | 0.9466%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 923 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 12.4717 | 16.8273 | 0.74116 | 12.4717 | 16.8273 | 0.74116 | 13.1381 | 17.7264 | 0.74116 | 0.9088%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 249 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 95.5917 | 4.5395 | 21.0576 | 95.5917 | 4.5395 | 21.0576 | 100.6993 | 4.7821 | 21.0576 | 0.9905%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 187 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 20.2056 | 3.4092 | 5.9268 | 20.2056 | 3.4092 | 5.9268 | 21.2852 | 3.5914 | 5.9268 | 0.9634%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 978 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 15.4856 | 17.83 | 0.86852 | 15.4856 | 17.83 | 0.86852 | 16.313 | 18.7827 | 0.86852 | 0.8429%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 2947 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 30.5685 | 53.7269 | 0.56896 | 30.5685 | 53.7269 | 0.56896 | 32.2018 | 56.5976 | 0.56896 | 0.8937%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 161 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 35.1769 | 2.9352 | 11.9845 | 35.1769 | 2.9352 | 11.9845 | 37.0565 | 3.092 | 11.9845 | 0.9991%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 1068 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 28.7509 | 19.4708 | 1.4766 | 28.7509 | 19.4708 | 1.4766 | 30.2871 | 20.5111 | 1.4766 | 0.9216%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 1386 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 25.0832 | 25.2682 | 0.99268 | 25.0832 | 25.2682 | 0.99268 | 26.4234 | 26.6184 | 0.99268 | 0.9611%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 16 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.7393 | 0.2917 | 23.1039 | 6.7393 | 0.2917 | 23.1039 | 7.0994 | 0.30728 | 23.1039 | 0.9946%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 1029 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 36.4187 | 18.7598 | 1.9413 | 36.4187 | 18.7598 | 1.9413 | 38.3646 | 19.7621 | 1.9413 | 0.9703%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 144 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 1.0134 | 2.6253 | 0.38603 | 1.0134 | 2.6253 | 0.38603 | 1.0676 | 2.7655 | 0.38603 | 0.334%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 19.5112 | 2.0601 | 9.471 | 19.5112 | 2.0601 | 9.471 | 20.5537 | 2.1702 | 9.471 | 0.9951%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 6 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 37.1986 | 0.10939 | 340.0663 | 37.1986 | 0.10939 | 340.0663 | 39.1862 | 0.11523 | 340.0663 | 0.9988%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 333 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.8178 | 6.0709 | 0.9583 | 5.8178 | 6.0709 | 0.9583 | 6.1286 | 6.3953 | 0.9583 | 0.9868%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 365 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 42.518 | 6.6543 | 6.3895 | 42.518 | 6.6543 | 6.3895 | 44.7898 | 7.0099 | 6.3895 | 0.9945%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 172 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 21.4759 | 3.1357 | 6.8488 | 21.4759 | 3.1357 | 6.8488 | 22.6234 | 3.3033 | 6.8488 | 0.9686%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 173 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 91.3747 | 3.154 | 28.9713 | 91.3747 | 3.154 | 28.9713 | 96.257 | 3.3225 | 28.9713 | 0.9959%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 573 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 12.3393 | 10.4464 | 1.1812 | 12.3393 | 10.4464 | 1.1812 | 12.9986 | 11.0046 | 1.1812 | 0.9515%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 2453 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 68.2692 | 44.7208 | 1.5266 | 68.2692 | 44.7208 | 1.5266 | 71.9169 | 47.1103 | 1.5266 | 0.9662%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 895 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 749.8113 | 16.3168 | 45.9533 | 749.8113 | 16.3168 | 45.9533 | 789.8747 | 17.1886 | 45.9533 | 0.9925%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 47 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 34.2741 | 0.85686 | 39.9997 | 34.2741 | 0.85686 | 39.9997 | 36.1055 | 0.90264 | 39.9997 | 0.9927%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 409 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 428.6915 | 7.4565 | 57.4923 | 428.6915 | 7.4565 | 57.4923 | 451.5971 | 7.8549 | 57.4923 | 0.9963%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 40 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.3843 | 0.72924 | 3.2696 | 2.3843 | 0.72924 | 3.2696 | 2.5117 | 0.76821 | 3.2696 | 0.8656%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 1410 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 68.0491 | 25.7058 | 2.6472 | 68.0491 | 25.7058 | 2.6472 | 71.685 | 27.0793 | 2.6472 | 0.9605%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 237 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 46.2897 | 4.3208 | 10.7133 | 46.2897 | 4.3208 | 10.7133 | 48.763 | 4.5516 | 10.7133 | 0.9985%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 3377 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 154.7093 | 61.5663 | 2.5129 | 154.7093 | 61.5663 | 2.5129 | 162.9756 | 64.8559 | 2.5129 | 0.967%
2026 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 4 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.16292 | 0.072924 | 2.2342 | 0.16292 | 0.072924 | 2.2342 | 0.17163 | 0.076821 | 2.2342 | 0.9833%
2026 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 10 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.6265 | 0.18231 | 8.9215 | 1.6265 | 0.18231 | 8.9215 | 1.7134 | 0.19205 | 8.9215 | 0.9937%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 1039 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 18.1259 | 18.9421 | 0.95691 | 18.1259 | 18.9421 | 0.95691 | 19.0944 | 19.9542 | 0.95691 | 0.9498%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 1418 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 59.885 | 25.8516 | 2.3165 | 59.885 | 25.8516 | 2.3165 | 63.0847 | 27.2329 | 2.3165 | 0.9826%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 1039 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 18.007 | 18.9421 | 0.95064 | 18.007 | 18.9421 | 0.95064 | 18.9692 | 19.9542 | 0.95064 | 0.9106%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 329 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 4.0406 | 5.998 | 0.67365 | 4.0406 | 5.998 | 0.67365 | 4.2565 | 6.3185 | 0.67365 | 0.7897%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 165 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.3877 | 3.0081 | 2.4559 | 7.3877 | 3.0081 | 2.4559 | 7.7824 | 3.1689 | 2.4559 | 0.9819%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 865 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 32.3646 | 15.7699 | 2.0523 | 32.3646 | 15.7699 | 2.0523 | 34.0939 | 16.6125 | 2.0523 | 0.9768%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 13 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0786 | 0.237 | 4.5509 | 1.0786 | 0.237 | 4.5509 | 1.1362 | 0.24967 | 4.5509 | 0.9298%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 106 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.5257 | 1.9325 | 0.78948 | 1.5257 | 1.9325 | 0.78948 | 1.6072 | 2.0357 | 0.78948 | 0.8171%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 1011 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 25.6087 | 18.4316 | 1.3894 | 25.6087 | 18.4316 | 1.3894 | 26.977 | 19.4164 | 1.3894 | 0.983%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 3541 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 48.405 | 64.5562 | 0.74981 | 48.405 | 64.5562 | 0.74981 | 50.9914 | 68.0055 | 0.74981 | 0.9868%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.0004932 | 0.10939 | 0.0045088 | 0.0004932 | 0.10939 | 0.0045088 | 0.00051955 | 0.11523 | 0.0045088 | 0.004523%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 1420 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 28.6233 | 25.8881 | 1.1057 | 28.6233 | 25.8881 | 1.1057 | 30.1527 | 27.2713 | 1.1057 | 0.9884%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 548 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.692 | 9.9906 | 0.66983 | 6.692 | 9.9906 | 0.66983 | 7.0496 | 10.5244 | 0.66983 | 0.9757%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 453 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 4.0561 | 8.2587 | 0.49113 | 4.0561 | 8.2587 | 0.49113 | 4.2728 | 8.6999 | 0.49113 | 0.9496%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 875 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 19.1889 | 15.9522 | 1.2029 | 19.1889 | 15.9522 | 1.2029 | 20.2142 | 16.8045 | 1.2029 | 0.859%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 1371 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 46.8623 | 24.9948 | 1.8749 | 46.8623 | 24.9948 | 1.8749 | 49.3662 | 26.3303 | 1.8749 | 0.9946%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 275 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 36.9882 | 5.0135 | 7.3777 | 36.9882 | 5.0135 | 7.3777 | 38.9646 | 5.2814 | 7.3777 | 0.8863%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 897 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 222.188 | 16.3533 | 13.5868 | 222.188 | 16.3533 | 13.5868 | 234.0599 | 17.227 | 13.5868 | 0.9837%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 800 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 91.5381 | 14.5848 | 6.2762 | 91.5381 | 14.5848 | 6.2762 | 96.4291 | 15.3641 | 6.2762 | 0.9873%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 260 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 26.1976 | 4.7401 | 5.5268 | 26.1976 | 4.7401 | 5.5268 | 27.5973 | 4.9933 | 5.5268 | 0.9726%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 177 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 21.2648 | 3.2269 | 6.5899 | 21.2648 | 3.2269 | 6.5899 | 22.401 | 3.3993 | 6.5899 | 0.9861%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 530 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 49.8843 | 9.6625 | 5.1627 | 49.8843 | 9.6625 | 5.1627 | 52.5497 | 10.1787 | 5.1627 | 0.9807%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 954 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 199.1398 | 17.3924 | 11.4498 | 199.1398 | 17.3924 | 11.4498 | 209.7801 | 18.3217 | 11.4498 | 0.9836%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 256 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 64.6625 | 4.6672 | 13.8548 | 64.6625 | 4.6672 | 13.8548 | 68.1175 | 4.9165 | 13.8548 | 0.9784%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 34.4579 | 2.0419 | 16.8756 | 34.4579 | 2.0419 | 16.8756 | 36.299 | 2.151 | 16.8756 | 0.994%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 398 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 267.7119 | 7.256 | 36.8954 | 267.7119 | 7.256 | 36.8954 | 282.0161 | 7.6437 | 36.8954 | 0.9934%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 1107 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 255.4695 | 20.1818 | 12.6584 | 255.4695 | 20.1818 | 12.6584 | 269.1196 | 21.2601 | 12.6584 | 0.9889%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 88 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.4846 | 1.6043 | 2.7953 | 4.4846 | 1.6043 | 2.7953 | 4.7243 | 1.6901 | 2.7953 | 0.7089%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 23.8534 | 0.63809 | 37.3826 | 23.8534 | 0.63809 | 37.3826 | 25.1279 | 0.67218 | 37.3826 | 0.9883%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 1011 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 292.0914 | 18.4316 | 15.8473 | 292.0914 | 18.4316 | 15.8473 | 307.6982 | 19.4164 | 15.8473 | 0.9911%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 1263 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 618.2973 | 23.0258 | 26.8523 | 618.2973 | 23.0258 | 26.8523 | 651.3338 | 24.2561 | 26.8523 | 0.9893%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 689 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 8.0494 | 12.5612 | 0.64082 | 8.0494 | 12.5612 | 0.64082 | 8.4795 | 13.2324 | 0.64082 | 0.9808%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 111 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.9204 | 2.0236 | 7.373 | 14.9204 | 2.0236 | 7.373 | 15.7176 | 2.1318 | 7.373 | 0.9867%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 480 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 10.2731 | 8.7509 | 1.1739 | 10.2731 | 8.7509 | 1.1739 | 10.822 | 9.2185 | 1.1739 | 0.9646%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 909 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 58.7462 | 16.572 | 3.5449 | 58.7462 | 16.572 | 3.5449 | 61.8851 | 17.4575 | 3.5449 | 0.9824%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 674 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.8035 | 12.2877 | 0.55368 | 6.8035 | 12.2877 | 0.55368 | 7.167 | 12.9443 | 0.55368 | 0.6927%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 61 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.5462 | 1.1121 | 3.1888 | 3.5462 | 1.1121 | 3.1888 | 3.7357 | 1.1715 | 3.1888 | 0.9876%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 261 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 11.0889 | 4.7583 | 2.3304 | 11.0889 | 4.7583 | 2.3304 | 11.6814 | 5.0125 | 2.3304 | 0.9838%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 103 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.451 | 1.8778 | 3.968 | 7.451 | 1.8778 | 3.968 | 7.8491 | 1.9781 | 3.968 | 0.987%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 102 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.4814 | 1.8596 | 1.8722 | 3.4814 | 1.8596 | 1.8722 | 3.6675 | 1.9589 | 1.8722 | 0.9688%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 1050 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 41.4475 | 19.1426 | 2.1652 | 41.4475 | 19.1426 | 2.1652 | 43.6621 | 20.1654 | 2.1652 | 0.9791%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 538 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 35.3681 | 9.8083 | 3.6059 | 35.3681 | 9.8083 | 3.6059 | 37.2578 | 10.3324 | 3.6059 | 0.9907%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 555 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 33.8556 | 10.1182 | 3.346 | 33.8556 | 10.1182 | 3.346 | 35.6645 | 10.6589 | 3.346 | 0.9682%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 301 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 6.0425 | 5.4875 | 1.1011 | 6.0425 | 5.4875 | 1.1011 | 6.3654 | 5.7808 | 1.1011 | 0.6596%
2026 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 1 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 1.1925 | 0 | 0 | 1.1925 | 0 | 1.1376 | 0.018231 | 62.3973 | 1.1376 | 0.018231 | 62.3973 | 1.1983 | 0.019205 | 62.3973 | 0.295%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 883 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 30.5472 | 16.098 | 1.8976 | 30.5472 | 16.098 | 1.8976 | 32.1793 | 16.9582 | 1.8976 | 0.9454%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 296 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 12.0051 | 5.3964 | 2.2247 | 12.0051 | 5.3964 | 2.2247 | 12.6466 | 5.6847 | 2.2247 | 0.9251%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 20 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.98533 | 0.36462 | 2.7023 | 0.98533 | 0.36462 | 2.7023 | 1.038 | 0.3841 | 2.7023 | 0.9818%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 34.3178 | 11.6861 | 2.9366 | 34.3178 | 11.6861 | 2.9366 | 36.1515 | 12.3105 | 2.9366 | 0.9585%
2026 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.4091 | 0.16408 | 2.4933 | 0.4091 | 0.16408 | 2.4933 | 0.43096 | 0.17285 | 2.4933 | 0.8666%
2026 | 280 | 280-24AE | Tier-2 | Tier-2---12 | Tier-2---4 | 6 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.11503 | 0 | 0 | 0.11503 | 0 | 0.10973 | 0.10939 | 1.0032 | 0.10973 | 0.10939 | 1.0032 | 0.1156 | 0.11523 | 1.0032 | 0.03145%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 49.8241 | 1.9872 | 25.0727 | 49.8241 | 1.9872 | 25.0727 | 52.4863 | 2.0934 | 25.0727 | 0.9855%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 284 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.865 | 5.1776 | 3.2573 | 16.865 | 5.1776 | 3.2573 | 17.7662 | 5.4543 | 3.2573 | 0.878%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 4.3298 | 0.018231 | 237.4971 | 4.3298 | 0.018231 | 237.4971 | 4.5612 | 0.019205 | 237.4971 | 0.9431%
2026 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 18 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.39171 | 0.32816 | 1.1936 | 0.39171 | 0.32816 | 1.1936 | 0.41263 | 0.34569 | 1.1936 | 0.9823%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 375 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.8786 | 6.8366 | 0.71359 | 4.8786 | 6.8366 | 0.71359 | 5.1393 | 7.2019 | 0.71359 | 0.9288%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 62 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.024332 | 1.1303 | 0.021527 | 0.024332 | 1.1303 | 0.021527 | 0.025632 | 1.1907 | 0.021527 | 0.7897%
2026 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 63 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 4.3537 | 1.1486 | 3.7906 | 4.3537 | 1.1486 | 3.7906 | 4.5864 | 1.2099 | 3.7906 | 0.9948%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 269 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.6479 | 4.9042 | 1.3556 | 6.6479 | 4.9042 | 1.3556 | 7.0031 | 5.1662 | 1.3556 | 0.9241%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 521 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 20.9129 | 9.4984 | 2.2017 | 20.9129 | 9.4984 | 2.2017 | 22.0303 | 10.0059 | 2.2017 | 0.9107%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 1014 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 43.4106 | 18.4863 | 2.3483 | 43.4106 | 18.4863 | 2.3483 | 45.7301 | 19.474 | 2.3483 | 0.9555%
2026 | 308 | 308-485AE | Tier-2 | Tier-2---15 | Tier-2---8 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.043838 | 0 | 0 | 0.043838 | 0 | 0.041818 | 0.091155 | 0.45876 | 0.041818 | 0.091155 | 0.45876 | 0.044052 | 0.096026 | 0.45876 | 0.02775%
2026 | 308 | 308-486AE | Tier-2 | Tier-2---16 | Tier-2---8 | 2 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.039249 | 0 | 0 | 0.039249 | 0 | 0.037441 | 0.036462 | 1.0268 | 0.037441 | 0.036462 | 1.0268 | 0.039442 | 0.03841 | 1.0268 | 0.02383%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 16 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.17655 | 0.2917 | 0.60525 | 0.17655 | 0.2917 | 0.60525 | 0.18598 | 0.30728 | 0.60525 | 0.1937%
2026 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 5 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.37322 | 0.091155 | 4.0943 | 0.37322 | 0.091155 | 4.0943 | 0.39316 | 0.096026 | 4.0943 | 0.8469%
2026 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 34 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.073515 | 0.61986 | 0.1186 | 0.073515 | 0.61986 | 0.1186 | 0.077443 | 0.65298 | 0.1186 | 0.4938%
2026 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 22 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.43274 | 0.40108 | 1.0789 | 0.43274 | 0.40108 | 1.0789 | 0.45586 | 0.42251 | 1.0789 | 0.1628%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 347 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.035668 | 6.3262 | 0.0056382 | 0.035668 | 6.3262 | 0.0056382 | 0.037574 | 6.6642 | 0.0056382 | 0.02339%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 50 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0029183 | 0.91155 | 0.0032015 | 0.0029183 | 0.91155 | 0.0032015 | 0.0030742 | 0.96026 | 0.0032015 | 0.001514%
2026 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.1439 | 0 | 0 | 0.1439 | 0 | 0.13727 | 0.14585 | 0.94116 | 0.13727 | 0.14585 | 0.94116 | 0.1446 | 0.15364 | 0.94116 | 0.981%
2026 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 424 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.9919 | 7.73 | 0.25769 | 1.9919 | 7.73 | 0.25769 | 2.0983 | 8.143 | 0.25769 | 0.995%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 17 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.8639 | 0.30993 | 9.2405 | 2.8639 | 0.30993 | 9.2405 | 3.0169 | 0.32649 | 9.2405 | 0.9927%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 2015 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 32.8093 | 36.7356 | 0.89312 | 32.8093 | 36.7356 | 0.89312 | 34.5623 | 38.6984 | 0.89312 | 0.9548%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 2337 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 129.861 | 42.606 | 3.048 | 129.861 | 42.606 | 3.048 | 136.7997 | 44.8825 | 3.048 | 0.9814%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 2775 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 51.5398 | 50.5912 | 1.0187 | 51.5398 | 50.5912 | 1.0187 | 54.2936 | 53.2943 | 1.0187 | 0.9699%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 1107 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 128.0651 | 20.1818 | 6.3456 | 128.0651 | 20.1818 | 6.3456 | 134.9078 | 21.2601 | 6.3456 | 0.9928%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 1576 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 105.6518 | 28.7321 | 3.6771 | 105.6518 | 28.7321 | 3.6771 | 111.297 | 30.2673 | 3.6771 | 0.9888%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 1026 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 222.6577 | 18.7051 | 11.9036 | 222.6577 | 18.7051 | 11.9036 | 234.5546 | 19.7045 | 11.9036 | 0.9925%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 243 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 86.9953 | 4.4301 | 19.6371 | 86.9953 | 4.4301 | 19.6371 | 91.6436 | 4.6669 | 19.6371 | 0.9973%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 1556 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 176.4312 | 28.3675 | 6.2195 | 176.4312 | 28.3675 | 6.2195 | 185.8581 | 29.8832 | 6.2195 | 0.9936%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 951 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 85.7598 | 17.3377 | 4.9464 | 85.7598 | 17.3377 | 4.9464 | 90.342 | 18.2641 | 4.9464 | 0.9749%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 266 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 23.8334 | 4.8495 | 4.9147 | 23.8334 | 4.8495 | 4.9147 | 25.1069 | 5.1086 | 4.9147 | 0.9918%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 93 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 21.1215 | 1.6955 | 12.4575 | 21.1215 | 1.6955 | 12.4575 | 22.2501 | 1.7861 | 12.4575 | 0.9993%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 172 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.8485 | 3.1357 | 5.3731 | 16.8485 | 3.1357 | 5.3731 | 17.7488 | 3.3033 | 5.3731 | 0.8869%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 138 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 40.9814 | 2.5159 | 16.289 | 40.9814 | 2.5159 | 16.289 | 43.1711 | 2.6503 | 16.289 | 0.943%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.788 | 0.91155 | 3.0586 | 2.788 | 0.91155 | 3.0586 | 2.937 | 0.96026 | 3.0586 | 0.6284%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 379 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 128.3764 | 6.9096 | 18.5795 | 128.3764 | 6.9096 | 18.5795 | 135.2357 | 7.2788 | 18.5795 | 0.9943%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 1602 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 194.0236 | 29.2062 | 6.6432 | 194.0236 | 29.2062 | 6.6432 | 204.3905 | 30.7667 | 6.6432 | 0.9917%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 226 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 30.8577 | 4.1202 | 7.4893 | 30.8577 | 4.1202 | 7.4893 | 32.5065 | 4.3404 | 7.4893 | 0.8854%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 580 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 70.4778 | 10.574 | 6.6652 | 70.4778 | 10.574 | 6.6652 | 74.2435 | 11.139 | 6.6652 | 0.985%
2026 | 355 | 355-65R | Tier-2 | Tier-2---21 | Tier-2---24 | 2 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.00030886 | 0 | 0 | 0.00030886 | 0 | 0.00029463 | 0.036462 | 0.0080805 | 0.00029463 | 0.036462 | 0.0080805 | 0.00031038 | 0.03841 | 0.0080805 | 0.4611%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 248 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.9537 | 4.5213 | 2.865 | 12.9537 | 4.5213 | 2.865 | 13.6459 | 4.7629 | 2.865 | 0.7994%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 346 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 50.9054 | 6.3079 | 8.07 | 50.9054 | 6.3079 | 8.07 | 53.6253 | 6.645 | 8.07 | 0.9814%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 1320 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 149.3338 | 24.065 | 6.2054 | 149.3338 | 24.065 | 6.2054 | 157.313 | 25.3508 | 6.2054 | 0.9776%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 1086 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 84.5967 | 19.7989 | 4.2728 | 84.5967 | 19.7989 | 4.2728 | 89.1168 | 20.8568 | 4.2728 | 0.9541%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 47 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.8235 | 0.85686 | 13.7986 | 11.8235 | 0.85686 | 13.7986 | 12.4552 | 0.90264 | 13.7986 | 0.9906%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 50 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 48.4832 | 0.91155 | 53.1875 | 48.4832 | 0.91155 | 53.1875 | 51.0737 | 0.96026 | 53.1875 | 0.9968%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 10 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 8.0059 | 0.18231 | 43.9134 | 8.0059 | 0.18231 | 43.9134 | 8.4336 | 0.19205 | 43.9134 | 0.9549%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 489 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 158.9726 | 8.915 | 17.8321 | 158.9726 | 8.915 | 17.8321 | 167.4668 | 9.3913 | 17.8321 | 0.9879%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 938 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 164.5511 | 17.1007 | 9.6225 | 164.5511 | 17.1007 | 9.6225 | 173.3433 | 18.0144 | 9.6225 | 0.9747%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 1053 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 96.5713 | 19.1973 | 5.0305 | 96.5713 | 19.1973 | 5.0305 | 101.7312 | 20.223 | 5.0305 | 0.9704%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 650 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 109.6988 | 11.8502 | 9.2571 | 109.6988 | 11.8502 | 9.2571 | 115.5602 | 12.4834 | 9.2571 | 0.9781%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 29 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.5598 | 0.5287 | 10.516 | 5.5598 | 0.5287 | 10.516 | 5.8569 | 0.55695 | 10.516 | 0.9721%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 56 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.7834 | 1.0209 | 12.5212 | 12.7834 | 1.0209 | 12.5212 | 13.4665 | 1.0755 | 12.5212 | 0.9966%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 437 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 353.6518 | 7.967 | 44.3897 | 353.6518 | 7.967 | 44.3897 | 372.5479 | 8.3927 | 44.3897 | 0.9859%
2026 | 386 | 386-25R | Tier-2 | Tier-2---15 | Tier-2---9 | 3 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 0.50797 | 0 | 0 | 0.50797 | 0 | 0.48456 | 0.054693 | 8.8597 | 0.48456 | 0.054693 | 8.8597 | 0.51046 | 0.057616 | 8.8597 | 0.3536%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 79 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 12.3554 | 1.4403 | 8.5786 | 12.3554 | 1.4403 | 8.5786 | 13.0156 | 1.5172 | 8.5786 | 0.8901%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 87 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.6574 | 1.5861 | 1.045 | 1.6574 | 1.5861 | 1.045 | 1.746 | 1.6708 | 1.045 | 0.1879%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 1753 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 26.3874 | 31.959 | 0.82566 | 26.3874 | 31.959 | 0.82566 | 27.7974 | 33.6667 | 0.82566 | 0.8818%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 728 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 17.3358 | 13.2722 | 1.3062 | 17.3358 | 13.2722 | 1.3062 | 18.2621 | 13.9814 | 1.3062 | 0.9783%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 1526 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 59.8337 | 27.8206 | 2.1507 | 59.8337 | 27.8206 | 2.1507 | 63.0306 | 29.3071 | 2.1507 | 0.9847%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 68 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 12.3633 | 1.2397 | 9.9727 | 12.3633 | 1.2397 | 9.9727 | 13.0239 | 1.306 | 9.9727 | 0.9597%
2026 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 115 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.67081 | 2.0966 | 0.31996 | 0.67081 | 2.0966 | 0.31996 | 0.70665 | 2.2086 | 0.31996 | 0.9953%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 376 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 32.7047 | 6.8549 | 4.771 | 32.7047 | 6.8549 | 4.771 | 34.4521 | 7.2211 | 4.771 | 0.9745%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 5.0723 | 0.87509 | 5.7963 | 5.0723 | 0.87509 | 5.7963 | 5.3433 | 0.92185 | 5.7963 | 0.9134%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 115 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 44.4079 | 2.0966 | 21.1812 | 44.4079 | 2.0966 | 21.1812 | 46.7806 | 2.2086 | 21.1812 | 0.98%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 50.2962 | 1.1486 | 43.7908 | 50.2962 | 1.1486 | 43.7908 | 52.9836 | 1.2099 | 43.7908 | 0.9857%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 909 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.8191 | 16.572 | 1.0149 | 16.8191 | 16.572 | 1.0149 | 17.7178 | 17.4575 | 1.0149 | 0.9609%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 31 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.014671 | 0.56516 | 0.025959 | 0.014671 | 0.56516 | 0.025959 | 0.015455 | 0.59536 | 0.025959 | 0.01745%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 866 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.9098 | 15.7881 | 0.43766 | 6.9098 | 15.7881 | 0.43766 | 7.2789 | 16.6317 | 0.43766 | 0.8492%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 664 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.9086 | 12.1054 | 0.24027 | 2.9086 | 12.1054 | 0.24027 | 3.064 | 12.7522 | 0.24027 | 0.5795%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 1856 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 97.67 | 33.8368 | 2.8865 | 97.67 | 33.8368 | 2.8865 | 102.8886 | 35.6448 | 2.8865 | 0.8848%
2026 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 38 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 6.494 | 0.69278 | 9.3739 | 6.494 | 0.69278 | 9.3739 | 6.841 | 0.7298 | 9.3739 | 0.9662%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 41 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 5.1901 | 0.74747 | 6.9435 | 5.1901 | 0.74747 | 6.9435 | 5.4674 | 0.78741 | 6.9435 | 0.9893%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 289 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 4.1351 | 5.2688 | 0.78483 | 4.1351 | 5.2688 | 0.78483 | 4.3561 | 5.5503 | 0.78483 | 0.9131%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 204 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.68786 | 3.7191 | 0.18495 | 0.68786 | 3.7191 | 0.18495 | 0.72461 | 3.9179 | 0.18495 | 0.51%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 6 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 3.0769 | 0.10939 | 28.1292 | 3.0769 | 0.10939 | 28.1292 | 3.2414 | 0.11523 | 28.1292 | 0.9662%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 31.8067 | 2.5706 | 12.3734 | 31.8067 | 2.5706 | 12.3734 | 33.5062 | 2.7079 | 12.3734 | 0.9767%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 594 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.853 | 10.8292 | 0.3558 | 3.853 | 10.8292 | 0.3558 | 4.0589 | 11.4079 | 0.3558 | 0.7071%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 390 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 87.2546 | 7.1101 | 12.2719 | 87.2546 | 7.1101 | 12.2719 | 91.9168 | 7.49 | 12.2719 | 0.9496%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 252 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 66.4731 | 4.5942 | 14.4688 | 66.4731 | 4.5942 | 14.4688 | 70.0248 | 4.8397 | 14.4688 | 0.9611%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 171 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 13.5715 | 3.1175 | 4.3533 | 13.5715 | 3.1175 | 4.3533 | 14.2966 | 3.2841 | 4.3533 | 0.8872%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 454 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 96.9373 | 8.2769 | 11.7118 | 96.9373 | 8.2769 | 11.7118 | 102.1167 | 8.7191 | 11.7118 | 0.9569%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 208 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 14.2791 | 3.7921 | 3.7655 | 14.2791 | 3.7921 | 3.7655 | 15.0421 | 3.9947 | 3.7655 | 0.8473%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 235 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 30.7191 | 4.2843 | 7.1702 | 30.7191 | 4.2843 | 7.1702 | 32.3605 | 4.5132 | 7.1702 | 0.8754%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 381 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 37.1637 | 6.946 | 5.3504 | 37.1637 | 6.946 | 5.3504 | 39.1494 | 7.3172 | 5.3504 | 0.8812%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 12.5395 | 0.51047 | 24.5645 | 12.5395 | 0.51047 | 24.5645 | 13.2095 | 0.53774 | 24.5645 | 0.9724%
2026 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.16597 | 0 | 0 | 0.16597 | 0 | 0.15833 | 0.12762 | 1.2406 | 0.15833 | 0.12762 | 1.2406 | 0.16679 | 0.13444 | 1.2406 | 0.9941%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 27 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 11.2563 | 0.49224 | 22.8677 | 11.2563 | 0.49224 | 22.8677 | 11.8578 | 0.51854 | 22.8677 | 0.9739%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 154 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 22.903 | 2.8076 | 8.1575 | 22.903 | 2.8076 | 8.1575 | 24.1267 | 2.9576 | 8.1575 | 0.9191%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 269 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 11.2627 | 4.9042 | 2.2966 | 11.2627 | 4.9042 | 2.2966 | 11.8645 | 5.1662 | 2.2966 | 0.557%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 267 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.7837 | 4.8677 | 0.77732 | 3.7837 | 4.8677 | 0.77732 | 3.9859 | 5.1278 | 0.77732 | 0.7618%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 191 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.7608 | 3.4821 | 1.3672 | 4.7608 | 3.4821 | 1.3672 | 5.0152 | 3.6682 | 1.3672 | 0.7912%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 744 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 79.6266 | 13.5639 | 5.8705 | 79.6266 | 13.5639 | 5.8705 | 83.8812 | 14.2886 | 5.8705 | 0.9168%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 525 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 50.3074 | 9.5713 | 5.2561 | 50.3074 | 9.5713 | 5.2561 | 52.9954 | 10.0827 | 5.2561 | 0.9343%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 964 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 58.0947 | 17.5747 | 3.3056 | 58.0947 | 17.5747 | 3.3056 | 61.1988 | 18.5138 | 3.3056 | 0.9049%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 62 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.8342 | 1.1303 | 12.2391 | 13.8342 | 1.1303 | 12.2391 | 14.5734 | 1.1907 | 12.2391 | 0.9697%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 36 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.768 | 0.65632 | 8.7884 | 5.768 | 0.65632 | 8.7884 | 6.0762 | 0.69139 | 8.7884 | 0.967%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 197 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 49.5677 | 3.5915 | 13.8013 | 49.5677 | 3.5915 | 13.8013 | 52.2162 | 3.7834 | 13.8013 | 0.9877%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 250 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 21.1459 | 4.5578 | 4.6395 | 21.1459 | 4.5578 | 4.6395 | 22.2758 | 4.8013 | 4.6395 | 0.9555%
2026 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 78 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.7488 | 1.422 | 1.933 | 2.7488 | 1.422 | 1.933 | 2.8957 | 1.498 | 1.933 | 0.9711%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 633 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 78.3224 | 11.5403 | 6.7869 | 78.3224 | 11.5403 | 6.7869 | 82.5073 | 12.1569 | 6.7869 | 0.9923%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 138 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 7.0106 | 2.5159 | 2.7865 | 7.0106 | 2.5159 | 2.7865 | 7.3851 | 2.6503 | 2.7865 | 0.9277%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 158 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 10.2883 | 2.8805 | 3.5717 | 10.2883 | 2.8805 | 3.5717 | 10.838 | 3.0344 | 3.5717 | 0.9525%
2026 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 7 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 1.7471 | 0 | 0 | 1.7471 | 0 | 1.6666 | 0.12762 | 13.0591 | 1.6666 | 0.12762 | 13.0591 | 1.7556 | 0.13444 | 13.0591 | 0.3253%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 26 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.3077 | 0.47401 | 2.7588 | 1.3077 | 0.47401 | 2.7588 | 1.3776 | 0.49933 | 2.7588 | 0.999%
2026 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 3 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 6.2494 | 0 | 0 | 6.2494 | 0 | 5.9615 | 0.054693 | 108.9992 | 5.9615 | 0.054693 | 108.9992 | 6.28 | 0.057616 | 108.9992 | 0.999%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.7259 | 0.21877 | 7.889 | 1.7259 | 0.21877 | 7.889 | 1.8181 | 0.23046 | 7.889 | 0.9984%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 354 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 26.9189 | 6.4538 | 4.171 | 26.9189 | 6.4538 | 4.171 | 28.3572 | 6.7986 | 4.171 | 0.9993%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 36 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.36197 | 0.65632 | 0.55152 | 0.36197 | 0.65632 | 0.55152 | 0.38131 | 0.69139 | 0.55152 | 0.9723%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 363 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 32.7275 | 6.6179 | 4.9453 | 32.7275 | 6.6179 | 4.9453 | 34.4762 | 6.9715 | 4.9453 | 0.997%
2026 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.81736 | 0.018231 | 44.8336 | 0.81736 | 0.018231 | 44.8336 | 0.86104 | 0.019205 | 44.8336 | 0.9735%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 69 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 13.019 | 1.2579 | 10.3494 | 13.019 | 1.2579 | 10.3494 | 13.7146 | 1.3252 | 10.3494 | 0.9902%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 415 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 49.3848 | 7.5659 | 6.5273 | 49.3848 | 7.5659 | 6.5273 | 52.0235 | 7.9701 | 6.5273 | 0.9833%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 887 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 158.6864 | 16.1709 | 9.8131 | 158.6864 | 16.1709 | 9.8131 | 167.1652 | 17.035 | 9.8131 | 0.9937%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 127 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 38.5309 | 2.3153 | 16.6416 | 38.5309 | 2.3153 | 16.6416 | 40.5897 | 2.4391 | 16.6416 | 0.9496%
2026 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 58 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.6496 | 1.0574 | 1.5601 | 1.6496 | 1.0574 | 1.5601 | 1.7378 | 1.1139 | 1.5601 | 0.216%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 163 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.9397 | 2.9717 | 0.65272 | 1.9397 | 2.9717 | 0.65272 | 2.0433 | 3.1304 | 0.65272 | 0.9963%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 78 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.9644 | 1.422 | 4.8976 | 6.9644 | 1.422 | 4.8976 | 7.3365 | 1.498 | 4.8976 | 0.9951%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 1241 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 27.6613 | 22.6247 | 1.2226 | 27.6613 | 22.6247 | 1.2226 | 29.1393 | 23.8336 | 1.2226 | 0.9734%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 524 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.8205 | 9.5531 | 1.4467 | 13.8205 | 9.5531 | 1.4467 | 14.5589 | 10.0635 | 1.4467 | 0.9797%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 1235 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 24.3479 | 22.5154 | 1.0814 | 24.3479 | 22.5154 | 1.0814 | 25.6488 | 23.7184 | 1.0814 | 0.9676%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 1467 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 30.1957 | 26.745 | 1.129 | 30.1957 | 26.745 | 1.129 | 31.8091 | 28.174 | 1.129 | 0.9272%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 521 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 15.3089 | 9.4984 | 1.6117 | 15.3089 | 9.4984 | 1.6117 | 16.1269 | 10.0059 | 1.6117 | 0.9829%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 969 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 62.3968 | 17.6659 | 3.5321 | 62.3968 | 17.6659 | 3.5321 | 65.7308 | 18.6098 | 3.5321 | 0.9672%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 556 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.5208 | 10.1365 | 0.54465 | 5.5208 | 10.1365 | 0.54465 | 5.8158 | 10.6781 | 0.54465 | 0.7734%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 511 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 19.1856 | 9.3161 | 2.0594 | 19.1856 | 9.3161 | 2.0594 | 20.2108 | 9.8138 | 2.0594 | 0.9648%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 171 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.8412 | 3.1175 | 0.59058 | 1.8412 | 3.1175 | 0.59058 | 1.9395 | 3.2841 | 0.59058 | 0.7472%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 1723 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 46.0042 | 31.4121 | 1.4645 | 46.0042 | 31.4121 | 1.4645 | 48.4623 | 33.0905 | 1.4645 | 0.9649%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 616 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 19.0309 | 11.2303 | 1.6946 | 19.0309 | 11.2303 | 1.6946 | 20.0478 | 11.8304 | 1.6946 | 0.9757%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 944 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 104.6914 | 17.2101 | 6.0831 | 104.6914 | 17.2101 | 6.0831 | 110.2852 | 18.1297 | 6.0831 | 0.9669%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 417 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.9096 | 7.6024 | 0.90888 | 6.9096 | 7.6024 | 0.90888 | 7.2788 | 8.0086 | 0.90888 | 0.8931%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 1063 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 79.0871 | 19.3796 | 4.0809 | 79.0871 | 19.3796 | 4.0809 | 83.3128 | 20.4151 | 4.0809 | 0.9779%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 830 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 82.5858 | 15.1318 | 5.4578 | 82.5858 | 15.1318 | 5.4578 | 86.9984 | 15.9403 | 5.4578 | 0.9936%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 820 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 52.9434 | 14.9495 | 3.5415 | 52.9434 | 14.9495 | 3.5415 | 55.7723 | 15.7482 | 3.5415 | 0.9878%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 582 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 116.0523 | 10.6105 | 10.9375 | 116.0523 | 10.6105 | 10.9375 | 122.2532 | 11.1774 | 10.9375 | 0.9938%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 1580 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 85.1588 | 28.8051 | 2.9564 | 85.1588 | 28.8051 | 2.9564 | 89.7089 | 30.3442 | 2.9564 | 0.9905%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 100 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.4626 | 1.8231 | 0.25374 | 0.4626 | 1.8231 | 0.25374 | 0.48731 | 1.9205 | 0.25374 | 0.4302%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 89 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.25141 | 1.6226 | 0.15494 | 0.25141 | 1.6226 | 0.15494 | 0.26484 | 1.7093 | 0.15494 | 0.2253%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1782 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 51.8857 | 32.4877 | 1.5971 | 51.8857 | 32.4877 | 1.5971 | 54.658 | 34.2236 | 1.5971 | 0.9644%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 214 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.34053 | 3.9014 | 0.087283 | 0.34053 | 3.9014 | 0.087283 | 0.35872 | 4.1099 | 0.087283 | 0.117%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 525 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 52.0453 | 9.5713 | 5.4376 | 52.0453 | 9.5713 | 5.4376 | 54.8261 | 10.0827 | 5.4376 | 0.9978%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 928 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 107.7138 | 16.9184 | 6.3667 | 107.7138 | 16.9184 | 6.3667 | 113.4691 | 17.8224 | 6.3667 | 0.9977%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 622 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 129.4684 | 11.3397 | 11.4172 | 129.4684 | 11.3397 | 11.4172 | 136.386 | 11.9456 | 11.4172 | 0.9899%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 500 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 82.4531 | 9.1155 | 9.0453 | 82.4531 | 9.1155 | 9.0453 | 86.8586 | 9.6026 | 9.0453 | 0.982%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 1778 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 381.43 | 32.4148 | 11.7671 | 381.43 | 32.4148 | 11.7671 | 401.8103 | 34.1468 | 11.7671 | 0.9903%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 86 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 5.3877 | 1.5679 | 3.4363 | 5.3877 | 1.5679 | 3.4363 | 5.6756 | 1.6516 | 3.4363 | 0.6775%
2026 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 30 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.4566 | 0.54693 | 2.6632 | 1.4566 | 0.54693 | 2.6632 | 1.5344 | 0.57616 | 2.6632 | 0.9944%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 33 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.7778 | 0.60162 | 7.9414 | 4.7778 | 0.60162 | 7.9414 | 5.033 | 0.63377 | 7.9414 | 0.9632%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 37 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.46874 | 0.67455 | 0.6949 | 0.46874 | 0.67455 | 0.6949 | 0.49379 | 0.71059 | 0.6949 | 0.9941%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 1675 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 171.1238 | 30.537 | 5.6038 | 171.1238 | 30.537 | 5.6038 | 180.2671 | 32.1687 | 5.6038 | 0.9555%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 2456 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 244.0922 | 44.7755 | 5.4515 | 244.0922 | 44.7755 | 5.4515 | 257.1344 | 47.1679 | 5.4515 | 0.994%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 612 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 23.3101 | 11.1574 | 2.0892 | 23.3101 | 11.1574 | 2.0892 | 24.5556 | 11.7536 | 2.0892 | 0.936%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 1200 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 37.4045 | 21.8773 | 1.7097 | 37.4045 | 21.8773 | 1.7097 | 39.403 | 23.0462 | 1.7097 | 0.938%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 229 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 5.1753 | 4.1749 | 1.2396 | 5.1753 | 4.1749 | 1.2396 | 5.4518 | 4.398 | 1.2396 | 0.8718%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 341 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 14.4092 | 6.2168 | 2.3178 | 14.4092 | 6.2168 | 2.3178 | 15.1791 | 6.549 | 2.3178 | 0.9279%
2026 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 24 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 2.66 | 0 | 0 | 2.66 | 0 | 2.5374 | 0.43755 | 5.7992 | 2.5374 | 0.43755 | 5.7992 | 2.673 | 0.46092 | 5.7992 | 0.8123%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 264 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 57.5552 | 4.813 | 11.9583 | 57.5552 | 4.813 | 11.9583 | 60.6304 | 5.0702 | 11.9583 | 0.9729%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 753 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 144.2009 | 13.728 | 10.5042 | 144.2009 | 13.728 | 10.5042 | 151.9058 | 14.4615 | 10.5042 | 0.9856%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 265 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 23.0424 | 4.8312 | 4.7695 | 23.0424 | 4.8312 | 4.7695 | 24.2735 | 5.0894 | 4.7695 | 0.9864%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 248 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 53.8256 | 4.5213 | 11.9049 | 53.8256 | 4.5213 | 11.9049 | 56.7015 | 4.7629 | 11.9049 | 0.9841%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 528 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 99.3275 | 9.626 | 10.3187 | 99.3275 | 9.626 | 10.3187 | 104.6347 | 10.1403 | 10.3187 | 0.9831%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 469 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 87.2089 | 8.5504 | 10.1994 | 87.2089 | 8.5504 | 10.1994 | 91.8686 | 9.0072 | 10.1994 | 0.9843%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 16 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.16865 | 0.2917 | 0.57816 | 0.16865 | 0.2917 | 0.57816 | 0.17766 | 0.30728 | 0.57816 | 0.9934%
2026 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 1 | 100% | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.018231 | 0 | 0 | 0.018231 | 0 | 0 | 0.019205 | 0 | 0%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 392 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 29.8416 | 7.1466 | 4.1756 | 29.8416 | 7.1466 | 4.1756 | 31.436 | 7.5284 | 4.1756 | 0.9977%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 230 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 16.2275 | 4.1931 | 3.87 | 16.2275 | 4.1931 | 3.87 | 17.0946 | 4.4172 | 3.87 | 0.9957%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 98 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 18.457 | 1.7866 | 10.3305 | 18.457 | 1.7866 | 10.3305 | 19.4432 | 1.8821 | 10.3305 | 0.9986%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 843 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 20.9297 | 15.3688 | 1.3618 | 20.9297 | 15.3688 | 1.3618 | 22.048 | 16.19 | 1.3618 | 0.9923%
2026 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 39 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 0.41445 | 0 | 0 | 0.41445 | 0 | 0.39536 | 0.71101 | 0.55605 | 0.39536 | 0.71101 | 0.55605 | 0.41648 | 0.749 | 0.55605 | 0.9749%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 493 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 136.5755 | 8.9879 | 15.1955 | 136.5755 | 8.9879 | 15.1955 | 143.873 | 9.4681 | 15.1955 | 0.9856%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 33 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 68.3702 | 0.60162 | 113.6425 | 68.3702 | 0.60162 | 113.6425 | 72.0233 | 0.63377 | 113.6425 | 0.9951%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 580 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 82.1782 | 10.574 | 7.7717 | 82.1782 | 10.574 | 7.7717 | 86.5691 | 11.139 | 7.7717 | 0.9433%
2026 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 18 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 3.0791 | 0.32816 | 9.3829 | 3.0791 | 0.32816 | 9.3829 | 3.2436 | 0.34569 | 9.3829 | 0.9958%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 101 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 29.5835 | 1.8413 | 16.0663 | 29.5835 | 1.8413 | 16.0663 | 31.1642 | 1.9397 | 16.0663 | 0.9258%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 484 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 116.6696 | 8.8238 | 13.2221 | 116.6696 | 8.8238 | 13.2221 | 122.9034 | 9.2953 | 13.2221 | 0.9926%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 773 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 19.4046 | 14.0926 | 1.3769 | 19.4046 | 14.0926 | 1.3769 | 20.4414 | 14.8456 | 1.3769 | 0.9747%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 543 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.8721 | 9.8995 | 1.0983 | 10.8721 | 9.8995 | 1.0983 | 11.453 | 10.4284 | 1.0983 | 0.7093%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 371 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 91.0778 | 6.7637 | 13.4656 | 91.0778 | 6.7637 | 13.4656 | 95.9442 | 7.1251 | 13.4656 | 0.9829%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 414 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 174.0462 | 7.5477 | 23.0596 | 174.0462 | 7.5477 | 23.0596 | 183.3457 | 7.9509 | 23.0596 | 0.989%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 54 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 24.3129 | 0.98448 | 24.6963 | 24.3129 | 0.98448 | 24.6963 | 25.612 | 1.0371 | 24.6963 | 0.9937%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 446 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 50.8689 | 8.1311 | 6.2561 | 50.8689 | 8.1311 | 6.2561 | 53.5869 | 8.5655 | 6.2561 | 0.9631%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 868 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 174.04 | 15.8246 | 10.9981 | 174.04 | 15.8246 | 10.9981 | 183.3392 | 16.6701 | 10.9981 | 0.9714%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 82 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 28.1165 | 1.4949 | 18.8077 | 28.1165 | 1.4949 | 18.8077 | 29.6188 | 1.5748 | 18.8077 | 0.9712%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 410 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 189.1139 | 7.4747 | 25.3004 | 189.1139 | 7.4747 | 25.3004 | 199.2185 | 7.8741 | 25.3004 | 0.9923%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 23 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.2067 | 0.41931 | 2.8777 | 1.2067 | 0.41931 | 2.8777 | 1.2711 | 0.44172 | 2.8777 | 0.9928%
2026 | 834 | 834-887AE | Tier-2 | Tier-2---17 | Tier-2---13 | 2 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 0.69393 | 0 | 0 | 0.69393 | 0 | 0.66196 | 0.036462 | 18.1548 | 0.66196 | 0.036462 | 18.1548 | 0.69733 | 0.03841 | 18.1548 | 0.9864%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 59 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.11704 | 1.0756 | 0.10881 | 0.11704 | 1.0756 | 0.10881 | 0.12329 | 1.1331 | 0.10881 | 0.9883%
2026 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 131 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.3301 | 2.3883 | 0.55694 | 1.3301 | 2.3883 | 0.55694 | 1.4012 | 2.5159 | 0.55694 | 0.9963%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 8 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.063433 | 0.14585 | 0.43493 | 0.063433 | 0.14585 | 0.43493 | 0.066823 | 0.15364 | 0.43493 | 0.9902%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 15 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 3.1321 | 0.27347 | 11.4533 | 3.1321 | 0.27347 | 11.4533 | 3.2994 | 0.28808 | 11.4533 | 0.9939%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 231 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.1444 | 4.2114 | 0.50919 | 2.1444 | 4.2114 | 0.50919 | 2.259 | 4.4364 | 0.50919 | 0.9666%
2026 | 858 | 858-14 | Tier-2 | Tier-2---12 | Tier-2---7 | 10 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 4.0968 | 0 | 0 | 4.0968 | 0 | 3.9081 | 0.18231 | 21.4364 | 3.9081 | 0.18231 | 21.4364 | 4.1169 | 0.19205 | 21.4364 | 0.9951%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 856 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 81.9888 | 15.6058 | 5.2537 | 81.9888 | 15.6058 | 5.2537 | 86.3696 | 16.4396 | 5.2537 | 0.9986%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 438 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 78.5903 | 7.9852 | 9.842 | 78.5903 | 7.9852 | 9.842 | 82.7895 | 8.4119 | 9.842 | 0.9762%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 4 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.4212 | 0.072924 | 33.2011 | 2.4212 | 0.072924 | 33.2011 | 2.5505 | 0.076821 | 33.2011 | 0.9867%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 703 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 86.5756 | 12.8164 | 6.755 | 86.5756 | 12.8164 | 6.755 | 91.2014 | 13.5012 | 6.755 | 0.9973%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 1553 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 256.1133 | 28.3128 | 9.0458 | 256.1133 | 28.3128 | 9.0458 | 269.7978 | 29.8256 | 9.0458 | 0.9919%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 110 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 60.5455 | 2.0054 | 30.191 | 60.5455 | 2.0054 | 30.191 | 63.7806 | 2.1126 | 30.191 | 0.9998%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 1316 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 147.8841 | 23.9921 | 6.1639 | 147.8841 | 23.9921 | 6.1639 | 155.7857 | 25.274 | 6.1639 | 0.9833%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 759 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 110.8755 | 13.8374 | 8.0128 | 110.8755 | 13.8374 | 8.0128 | 116.7997 | 14.5767 | 8.0128 | 0.988%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 1095 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 51.148 | 19.963 | 2.5621 | 51.148 | 19.963 | 2.5621 | 53.8809 | 21.0297 | 2.5621 | 0.9625%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 563 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.8412 | 10.2641 | 1.2511 | 12.8412 | 10.2641 | 1.2511 | 13.5273 | 10.8125 | 1.2511 | 0.9181%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 319 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 74.6808 | 5.8157 | 12.8412 | 74.6808 | 5.8157 | 12.8412 | 78.6711 | 6.1264 | 12.8412 | 0.9835%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 1307 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 389.2135 | 23.828 | 16.3343 | 389.2135 | 23.828 | 16.3343 | 410.0097 | 25.1012 | 16.3343 | 0.9889%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 559 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 31.9736 | 10.1912 | 3.1374 | 31.9736 | 10.1912 | 3.1374 | 33.682 | 10.7357 | 3.1374 | 0.9191%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 876 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 213.2749 | 15.9704 | 13.3544 | 213.2749 | 15.9704 | 13.3544 | 224.6704 | 16.8237 | 13.3544 | 0.9908%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.4417 | 0.16408 | 8.7864 | 1.4417 | 0.16408 | 8.7864 | 1.5187 | 0.17285 | 8.7864 | 0.9858%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 221 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.8036 | 4.0291 | 1.9368 | 7.8036 | 4.0291 | 1.9368 | 8.2206 | 4.2443 | 1.9368 | 0.9652%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 1430 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 523.2391 | 26.0704 | 20.0702 | 523.2391 | 26.0704 | 20.0702 | 551.1964 | 27.4634 | 20.0702 | 0.9927%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 10 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 54.3851 | 0.18231 | 298.3103 | 54.3851 | 0.18231 | 298.3103 | 57.291 | 0.19205 | 298.3103 | 0.9997%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 988 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 305.9761 | 18.0123 | 16.9871 | 305.9761 | 18.0123 | 16.9871 | 322.3248 | 18.9747 | 16.9871 | 0.9926%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 319 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.8658 | 5.8157 | 2.0403 | 11.8658 | 5.8157 | 2.0403 | 12.4998 | 6.1264 | 2.0403 | 0.9598%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 310 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 32.2825 | 5.6516 | 5.7121 | 32.2825 | 5.6516 | 5.7121 | 34.0074 | 5.9536 | 5.7121 | 0.9934%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 87 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 10.234 | 1.5861 | 6.4523 | 10.234 | 1.5861 | 6.4523 | 10.7808 | 1.6708 | 6.4523 | 0.6902%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 126 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 14.5549 | 2.2971 | 6.3361 | 14.5549 | 2.2971 | 6.3361 | 15.3325 | 2.4199 | 6.3361 | 0.7661%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 53 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 4.1265 | 0.96625 | 4.2707 | 4.1265 | 0.96625 | 4.2707 | 4.347 | 1.0179 | 4.2707 | 0.9947%
2026 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 42 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.5777 | 0.7657 | 0.75446 | 0.5777 | 0.7657 | 0.75446 | 0.60856 | 0.80662 | 0.75446 | 0.9691%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 70 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 123.222 | 1.2762 | 96.5558 | 123.222 | 1.2762 | 96.5558 | 129.8059 | 1.3444 | 96.5558 | 0.9966%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 945 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 143.1403 | 17.2283 | 8.3084 | 143.1403 | 17.2283 | 8.3084 | 150.7885 | 18.1489 | 8.3084 | 0.9905%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 1604 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 268.7684 | 29.2426 | 9.191 | 268.7684 | 29.2426 | 9.191 | 283.129 | 30.8051 | 9.191 | 0.9891%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 200 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 76.0524 | 3.6462 | 20.8579 | 76.0524 | 3.6462 | 20.8579 | 80.116 | 3.841 | 20.8579 | 0.9946%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 118 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 41.3095 | 2.1513 | 19.2024 | 41.3095 | 2.1513 | 19.2024 | 43.5167 | 2.2662 | 19.2024 | 0.9952%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 11 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 1.9177 | 0 | 0 | 1.9177 | 0 | 1.8294 | 0.20054 | 9.1223 | 1.8294 | 0.20054 | 9.1223 | 1.9271 | 0.21126 | 9.1223 | 0.9994%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 427 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 138.6921 | 7.7847 | 17.8161 | 138.6921 | 7.7847 | 17.8161 | 146.1026 | 8.2006 | 17.8161 | 0.9843%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 1117 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 106.3896 | 20.3641 | 5.2244 | 106.3896 | 20.3641 | 5.2244 | 112.0742 | 21.4522 | 5.2244 | 0.9898%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 361 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 75.3766 | 6.5814 | 11.453 | 75.3766 | 6.5814 | 11.453 | 79.4041 | 6.9331 | 11.453 | 0.9853%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 1464 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 219.7181 | 26.6903 | 8.2321 | 219.7181 | 26.6903 | 8.2321 | 231.4579 | 28.1164 | 8.2321 | 0.9839%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 958 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 213.075 | 17.4654 | 12.1999 | 213.075 | 17.4654 | 12.1999 | 224.4598 | 18.3986 | 12.1999 | 0.9748%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 360 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 86.5106 | 6.5632 | 13.1812 | 86.5106 | 6.5632 | 13.1812 | 91.1329 | 6.9139 | 13.1812 | 0.9912%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 249 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 48.0711 | 4.5395 | 10.5894 | 48.0711 | 4.5395 | 10.5894 | 50.6396 | 4.7821 | 10.5894 | 0.9732%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 144 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 81.8457 | 2.6253 | 31.1761 | 81.8457 | 2.6253 | 31.1761 | 86.2189 | 2.7655 | 31.1761 | 0.9953%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 198 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 60.9876 | 3.6097 | 16.8952 | 60.9876 | 3.6097 | 16.8952 | 64.2463 | 3.8026 | 16.8952 | 0.9803%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 611 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 31.2181 | 11.1392 | 2.8025 | 31.2181 | 11.1392 | 2.8025 | 32.8861 | 11.7344 | 2.8025 | 0.9369%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 67.491 | 1.3309 | 50.712 | 67.491 | 1.3309 | 50.712 | 71.0971 | 1.402 | 50.712 | 0.9955%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 25 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 49.1533 | 0.45578 | 107.8452 | 49.1533 | 0.45578 | 107.8452 | 51.7796 | 0.48013 | 107.8452 | 0.803%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 189 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.9388 | 3.4457 | 1.1431 | 3.9388 | 3.4457 | 1.1431 | 4.1493 | 3.6298 | 1.1431 | 0.6587%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 392 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 43.563 | 7.1466 | 6.0957 | 43.563 | 7.1466 | 6.0957 | 45.8907 | 7.5284 | 6.0957 | 0.9978%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 184 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 31.7322 | 3.3545 | 9.4596 | 31.7322 | 3.3545 | 9.4596 | 33.4277 | 3.5338 | 9.4596 | 0.9981%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 149 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 13.4423 | 2.7164 | 4.9485 | 13.4423 | 2.7164 | 4.9485 | 14.1606 | 2.8616 | 4.9485 | 0.9962%
2026 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.7804 | 0.74747 | 14.4225 | 10.7804 | 0.74747 | 14.4225 | 11.3564 | 0.78741 | 14.4225 | 0.9972%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 242 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.4261 | 4.4119 | 1.2299 | 5.4261 | 4.4119 | 1.2299 | 5.716 | 4.6477 | 1.2299 | 0.3454%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.4764 | 4.3937 | 1.2464 | 5.4764 | 4.3937 | 1.2464 | 5.769 | 4.6284 | 1.2464 | 0.75%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 13 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.69331 | 0.237 | 2.9253 | 0.69331 | 0.237 | 2.9253 | 0.73035 | 0.24967 | 2.9253 | 0.9665%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 1271 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 50.7476 | 23.1717 | 2.1901 | 50.7476 | 23.1717 | 2.1901 | 53.4591 | 24.4098 | 2.1901 | 0.8429%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 2262 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 62.8186 | 41.2387 | 1.5233 | 62.8186 | 41.2387 | 1.5233 | 66.175 | 43.4421 | 1.5233 | 0.9909%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 367 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.6866 | 6.6908 | 2.0456 | 13.6866 | 6.6908 | 2.0456 | 14.4179 | 7.0483 | 2.0456 | 0.9975%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 15 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 1.0286 | 0.27347 | 3.7614 | 1.0286 | 0.27347 | 3.7614 | 1.0836 | 0.28808 | 3.7614 | 0.9975%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 74 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 38.8495 | 1.3491 | 28.7966 | 38.8495 | 1.3491 | 28.7966 | 40.9253 | 1.4212 | 28.7966 | 0.9993%
2026 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 14 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.37491 | 0.25523 | 1.4689 | 0.37491 | 0.25523 | 1.4689 | 0.39494 | 0.26887 | 1.4689 | 0.9408%
2026 | 1446 | CB 1446 | Tier-1 | Non-HFTD---17 | Non-HFTD---24 | 13 | 100% | 1.7782 | 79.62% | 0% | 20.38% | 0.014159 | 0 | 0 | 0.014159 | 0 | 0.013507 | 0.237 | 0.05699 | 0.013507 | 0.237 | 0.05699 | 0.014229 | 0.24967 | 0.05699 | 0.7962%
2026 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | Non-HFTD---22 | 26 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.037296 | 0 | 0 | 0.037296 | 0 | 0.035578 | 0.47401 | 0.075057 | 0.035578 | 0.47401 | 0.075057 | 0.037479 | 0.49933 | 0.075057 | 0.8877%
2026 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 24 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.87925 | 0.43755 | 2.0095 | 0.87925 | 0.43755 | 2.0095 | 0.92622 | 0.46092 | 2.0095 | 0.3549%
2026 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 3.0261 | 0.091155 | 33.197 | 3.0261 | 0.091155 | 33.197 | 3.1878 | 0.096026 | 33.197 | 0.7993%
2026 | 196 | CB 196 | Tier-2 | Tier-2---15 | Tier-2---9 | 14 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.042252 | 0 | 0 | 0.042252 | 0 | 0.040305 | 0.25523 | 0.15792 | 0.040305 | 0.25523 | 0.15792 | 0.042459 | 0.26887 | 0.15792 | 0.03142%
2026 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 168 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.8291 | 3.0628 | 1.2502 | 3.8291 | 3.0628 | 1.2502 | 4.0337 | 3.2265 | 1.2502 | 0.299%
2026 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 321 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.2158 | 5.8522 | 0.20775 | 1.2158 | 5.8522 | 0.20775 | 1.2808 | 6.1649 | 0.20775 | 0.9512%
2026 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 554 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.17895 | 10.1 | 0.017718 | 0.17895 | 10.1 | 0.017718 | 0.18852 | 10.6397 | 0.017718 | 0.09583%
2026 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 463 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 8.1689 | 8.441 | 0.96777 | 8.1689 | 8.441 | 0.96777 | 8.6054 | 8.892 | 0.96777 | 0.8082%
2026 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 8 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 1.3377 | 0 | 0 | 1.3377 | 0 | 1.2761 | 0.14585 | 8.7494 | 1.2761 | 0.14585 | 8.7494 | 1.3443 | 0.15364 | 8.7494 | 0.9989%
2026 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 77 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 2.0264 | 1.4038 | 1.4435 | 2.0264 | 1.4038 | 1.4435 | 2.1347 | 1.4788 | 1.4435 | 0.9981%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 688 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 23.6778 | 12.543 | 1.8877 | 23.6778 | 12.543 | 1.8877 | 24.9429 | 13.2132 | 1.8877 | 0.9929%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 605 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 15.2578 | 11.0298 | 1.3833 | 15.2578 | 11.0298 | 1.3833 | 16.0731 | 11.6191 | 1.3833 | 0.9737%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 1834 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 38.8784 | 33.4358 | 1.1628 | 38.8784 | 33.4358 | 1.1628 | 40.9557 | 35.2223 | 1.1628 | 0.9874%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 1006 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 31.0776 | 18.3404 | 1.6945 | 31.0776 | 18.3404 | 1.6945 | 32.7382 | 19.3204 | 1.6945 | 0.9888%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 678 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 118.3696 | 12.3607 | 9.5763 | 118.3696 | 12.3607 | 9.5763 | 124.6943 | 13.0211 | 9.5763 | 0.9762%
2026 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 34 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 20.0507 | 0.61986 | 32.3474 | 20.0507 | 0.61986 | 32.3474 | 21.1221 | 0.65298 | 32.3474 | 0.9954%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 241 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.7686 | 4.3937 | 2.6785 | 11.7686 | 4.3937 | 2.6785 | 12.3974 | 4.6284 | 2.6785 | 0.9768%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 55 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.4978 | 1.0027 | 2.491 | 2.4978 | 1.0027 | 2.491 | 2.6312 | 1.0563 | 2.491 | 0.6436%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0574 | 0.36462 | 2.8999 | 1.0574 | 0.36462 | 2.8999 | 1.1139 | 0.3841 | 2.8999 | 0.375%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 577 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 12.35 | 10.5193 | 1.174 | 12.35 | 10.5193 | 1.174 | 13.0099 | 11.0814 | 1.174 | 0.9%
2026 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 119 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.5459 | 2.1695 | 1.1735 | 2.5459 | 2.1695 | 1.1735 | 2.6819 | 2.2854 | 1.1735 | 0.7028%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 276 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 9.1325 | 5.0318 | 1.815 | 9.1325 | 5.0318 | 1.815 | 9.6204 | 5.3006 | 1.815 | 0.995%
2026 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 167 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.6547 | 3.0446 | 2.5142 | 7.6547 | 3.0446 | 2.5142 | 8.0637 | 3.2073 | 2.5142 | 0.9704%
2026 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 8 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 0.50007 | 0 | 0 | 0.50007 | 0 | 0.47703 | 0.14585 | 3.2707 | 0.47703 | 0.14585 | 3.2707 | 0.50252 | 0.15364 | 3.2707 | 0.1609%
2026 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 385 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.60029 | 7.019 | 0.085525 | 0.60029 | 7.019 | 0.085525 | 0.63237 | 7.394 | 0.085525 | 0.6647%
2026 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 151 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.099934 | 2.7529 | 0.036301 | 0.099934 | 2.7529 | 0.036301 | 0.10527 | 2.9 | 0.036301 | 0.9726%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.8672 | 0.40108 | 34.5744 | 13.8672 | 0.40108 | 34.5744 | 14.6082 | 0.42251 | 34.5744 | 0.9979%
2026 | 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 37 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.9885 | 0.67455 | 2.948 | 1.9885 | 0.67455 | 2.948 | 2.0948 | 0.71059 | 2.948 | 0.9683%
2026 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 228 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.39533 | 4.1567 | 0.095108 | 0.39533 | 4.1567 | 0.095108 | 0.41646 | 4.3788 | 0.095108 | 0.3335%
2026 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 3 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.4763 | 0.054693 | 45.2768 | 2.4763 | 0.054693 | 45.2768 | 2.6086 | 0.057616 | 45.2768 | 0.9938%
2026 | 350 | CB 350 | Tier-2 | Tier-2---15 | Tier-2---11 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 1.3347 | 0 | 0 | 1.3347 | 0 | 1.2732 | 0.018231 | 69.8371 | 1.2732 | 0.018231 | 69.8371 | 1.3412 | 0.019205 | 69.8371 | 0.9992%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 542 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 138.8006 | 9.8812 | 14.0469 | 138.8006 | 9.8812 | 14.0469 | 146.2169 | 10.4092 | 14.0469 | 0.9966%
2026 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 27 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.83174 | 0.49224 | 1.6897 | 0.83174 | 0.49224 | 1.6897 | 0.87618 | 0.51854 | 1.6897 | 0.9922%
2026 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 2 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.071388 | 0.036462 | 1.9579 | 0.071388 | 0.036462 | 1.9579 | 0.075203 | 0.03841 | 1.9579 | 0.986%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 836 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 106.4306 | 15.2412 | 6.9831 | 106.4306 | 15.2412 | 6.9831 | 112.1173 | 16.0555 | 6.9831 | 0.9884%
2026 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.064342 | 0.091155 | 0.70585 | 0.064342 | 0.091155 | 0.70585 | 0.06778 | 0.096026 | 0.70585 | 0.991%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 372 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 55.9658 | 6.782 | 8.2522 | 55.9658 | 6.782 | 8.2522 | 58.9561 | 7.1443 | 8.2522 | 0.9601%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 35 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.5513 | 0.63809 | 2.4311 | 1.5513 | 0.63809 | 2.4311 | 1.6341 | 0.67218 | 2.4311 | 0.1888%
2026 | 381 | CB 381 | Tier-1 | Non-HFTD---5 | Non-HFTD---17 | 10 | 100% | 47.7165 | 98.4% | 0% | 1.604% | 0.46951 | 0 | 0 | 0.46951 | 0 | 0.44788 | 0.18231 | 2.4567 | 0.44788 | 0.18231 | 2.4567 | 0.47181 | 0.19205 | 2.4567 | 0.984%
2026 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 3 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.91644 | 0.054693 | 16.756 | 0.91644 | 0.054693 | 16.756 | 0.9654 | 0.057616 | 16.756 | 0.1434%
2026 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 152 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 10.1685 | 2.7711 | 3.6695 | 10.1685 | 2.7711 | 3.6695 | 10.7118 | 2.9192 | 3.6695 | 0.9408%
2026 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 9 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 0.65999 | 0 | 0 | 0.65999 | 0 | 0.62958 | 0.16408 | 3.8371 | 0.62958 | 0.16408 | 3.8371 | 0.66322 | 0.17285 | 3.8371 | 0.9829%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 4 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 1.0944 | 0.072924 | 15.0068 | 1.0944 | 0.072924 | 15.0068 | 1.1528 | 0.076821 | 15.0068 | 0.9768%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 183 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 63.0506 | 3.3363 | 18.8985 | 63.0506 | 3.3363 | 18.8985 | 66.4195 | 3.5145 | 18.8985 | 0.9549%
2026 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.17532 | 0.054693 | 3.2055 | 0.17532 | 0.054693 | 3.2055 | 0.18468 | 0.057616 | 3.2055 | 0.9464%
2026 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 6 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.016493 | 0.10939 | 0.15078 | 0.016493 | 0.10939 | 0.15078 | 0.017375 | 0.11523 | 0.15078 | 0.9786%
2026 | 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 19 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.019677 | 0.34639 | 0.056806 | 0.019677 | 0.34639 | 0.056806 | 0.020728 | 0.3649 | 0.056806 | 0.1679%
2026 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 553 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 9.1717 | 10.0818 | 0.90973 | 9.1717 | 10.0818 | 0.90973 | 9.6618 | 10.6205 | 0.90973 | 0.8949%
2026 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 301 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 1.0843 | 5.4875 | 0.19759 | 1.0843 | 5.4875 | 0.19759 | 1.1422 | 5.7808 | 0.19759 | 0.372%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 34 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.3276 | 0.61986 | 6.9816 | 4.3276 | 0.61986 | 6.9816 | 4.5588 | 0.65298 | 6.9816 | 0.9425%
2026 | 533 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0035677 | 0 | 0 | 0.0035677 | 0 | 0.0034033 | 0.018231 | 0.18668 | 0.0034033 | 0.018231 | 0.18668 | 0.0035852 | 0.019205 | 0.18668 | 0.03364%
2026 | 534 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 3 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.022693 | 0 | 0 | 0.022693 | 0 | 0.021648 | 0.054693 | 0.3958 | 0.021648 | 0.054693 | 0.3958 | 0.022804 | 0.057616 | 0.3958 | 0.3599%
2026 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 3 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.051127 | 0 | 0 | 0.051127 | 0 | 0.048771 | 0.054693 | 0.89172 | 0.048771 | 0.054693 | 0.89172 | 0.051377 | 0.057616 | 0.89172 | 0.04585%
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 51 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.39328 | 0.92978 | 0.42298 | 0.39328 | 0.92978 | 0.42298 | 0.4143 | 0.97946 | 0.42298 | 0.7619%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 189 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.63661 | 3.4457 | 0.18476 | 0.63661 | 3.4457 | 0.18476 | 0.67063 | 3.6298 | 0.18476 | 0.9924%
2026 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 54 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.6457 | 0.98448 | 8.782 | 8.6457 | 0.98448 | 8.782 | 9.1076 | 1.0371 | 8.782 | 0.9545%
2026 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 26 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 3.1226 | 0.47401 | 6.5877 | 3.1226 | 0.47401 | 6.5877 | 3.2895 | 0.49933 | 6.5877 | 0.7837%
2026 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 19 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 7.5828 | 0 | 0 | 7.5828 | 0 | 7.2335 | 0.34639 | 20.8825 | 7.2335 | 0.34639 | 20.8825 | 7.62 | 0.3649 | 20.8825 | 0.6312%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 752 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 41.1623 | 13.7098 | 3.0024 | 41.1623 | 13.7098 | 3.0024 | 43.3617 | 14.4423 | 3.0024 | 0.9981%
2026 | 750 | CB 750 | Tier-1 | Non-HFTD---4 | Non-HFTD---11 | 7 | 100% | 147.1702 | 99.68% | 0% | 0.3223% | 1.467 | 0 | 0 | 1.467 | 0 | 1.3994 | 0.12762 | 10.9654 | 1.3994 | 0.12762 | 10.9654 | 1.4741 | 0.13444 | 10.9654 | 0.9968%
2026 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 50 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.48675 | 0.91155 | 0.53398 | 0.48675 | 0.91155 | 0.53398 | 0.51276 | 0.96026 | 0.53398 | 0.9266%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 107 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 77.7152 | 1.9507 | 39.8392 | 77.7152 | 1.9507 | 39.8392 | 81.8676 | 2.055 | 39.8392 | 0.9507%
2026 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 189 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.40449 | 3.4457 | 0.11739 | 0.40449 | 3.4457 | 0.11739 | 0.4261 | 3.6298 | 0.11739 | 0.9943%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 62 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 26.1161 | 1.1303 | 23.105 | 26.1161 | 1.1303 | 23.105 | 27.5116 | 1.1907 | 23.105 | 0.9983%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 173 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 3.01 | 3.154 | 0.95434 | 3.01 | 3.154 | 0.95434 | 3.1708 | 3.3225 | 0.95434 | 0.9343%
2026 | 911 | CB 911 | Tier-2 | Tier-2---14 | Tier-2---11 | 14 | 100% | 193.6033 | 99.75% | 0% | 0.253% | 1.9311 | 0 | 0 | 1.9311 | 0 | 1.8422 | 0.25523 | 7.2176 | 1.8422 | 0.25523 | 7.2176 | 1.9406 | 0.26887 | 7.2176 | 0.9975%
2026 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 42 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 12.5918 | 0.7657 | 16.4447 | 12.5918 | 0.7657 | 16.4447 | 13.2646 | 0.80662 | 16.4447 | 0.7976%
2026 | 955 | CB 955 | Tier-1 | Non-HFTD---9 | Non-HFTD---22 | 60 | 100% | 15.216 | 95.67% | 0% | 4.328% | 0.14557 | 0 | 0 | 0.14557 | 0 | 0.13887 | 1.0939 | 0.12695 | 0.13887 | 1.0939 | 0.12695 | 0.14629 | 1.1523 | 0.12695 | 0.9567%
2026 | 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 6 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.3936 | 0.10939 | 21.8823 | 2.3936 | 0.10939 | 21.8823 | 2.5215 | 0.11523 | 21.8823 | 0.9997%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 162 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 108.7518 | 2.9534 | 36.8222 | 108.7518 | 2.9534 | 36.8222 | 114.5625 | 3.1112 | 36.8222 | 0.9951%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 12.3822 | 0.91155 | 13.5837 | 12.3822 | 0.91155 | 13.5837 | 13.0438 | 0.96026 | 13.5837 | 0.9951%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 450 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.6886 | 8.204 | 0.44961 | 3.6886 | 8.204 | 0.44961 | 3.8857 | 8.6423 | 0.44961 | 0.997%
2026 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 104 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.2619 | 1.896 | 0.66556 | 1.2619 | 1.896 | 0.66556 | 1.3294 | 1.9973 | 0.66556 | 0.9965%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.23647 | 0.072924 | 3.2427 | 0.23647 | 0.072924 | 3.2427 | 0.24911 | 0.076821 | 3.2427 | 0.9021%
2026 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 414 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.2209 | 7.5477 | 0.16176 | 1.2209 | 7.5477 | 0.16176 | 1.2862 | 7.9509 | 0.16176 | 0.3693%
2026 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 320 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 9.2645 | 5.8339 | 1.588 | 9.2645 | 5.8339 | 1.588 | 9.7595 | 6.1457 | 1.588 | 0.9433%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 436 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 14.297 | 7.9487 | 1.7986 | 14.297 | 7.9487 | 1.7986 | 15.0609 | 8.3735 | 1.7986 | 0.9785%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 288 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 48.1334 | 5.2505 | 9.1673 | 48.1334 | 5.2505 | 9.1673 | 50.7052 | 5.5311 | 9.1673 | 0.9856%
2026 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 6.027 | 0.34639 | 17.3993 | 6.027 | 0.34639 | 17.3993 | 6.349 | 0.3649 | 17.3993 | 0.9902%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 1446 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 65.3114 | 26.3621 | 2.4775 | 65.3114 | 26.3621 | 2.4775 | 68.8011 | 27.7707 | 2.4775 | 0.99%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 1505 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 27.3578 | 27.4377 | 0.99709 | 27.3578 | 27.4377 | 0.99709 | 28.8196 | 28.9038 | 0.99709 | 0.9473%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 474 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 98.6268 | 8.6415 | 11.4131 | 98.6268 | 8.6415 | 11.4131 | 103.8966 | 9.1032 | 11.4131 | 0.9831%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 306 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 48.9483 | 5.5787 | 8.7741 | 48.9483 | 5.5787 | 8.7741 | 51.5636 | 5.8768 | 8.7741 | 0.9811%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 312 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 6.074 | 5.6881 | 1.0679 | 6.074 | 5.6881 | 1.0679 | 6.3986 | 5.992 | 1.0679 | 0.695%
2026 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.28348 | 0.072924 | 3.8874 | 0.28348 | 0.072924 | 3.8874 | 0.29863 | 0.076821 | 3.8874 | 0.9988%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 309 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 35.3682 | 5.6334 | 6.2783 | 35.3682 | 5.6334 | 6.2783 | 37.258 | 5.9344 | 6.2783 | 0.9914%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 1052 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 30.0514 | 19.1791 | 1.5669 | 30.0514 | 19.1791 | 1.5669 | 31.6571 | 20.2038 | 1.5669 | 0.9371%
2026 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 38 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.017997 | 0.69278 | 0.025978 | 0.017997 | 0.69278 | 0.025978 | 0.018959 | 0.7298 | 0.025978 | 0.02003%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 1615 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 15.535 | 29.4432 | 0.52763 | 15.535 | 29.4432 | 0.52763 | 16.3651 | 31.0163 | 0.52763 | 0.789%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 419 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 33.7655 | 7.6388 | 4.4203 | 33.7655 | 7.6388 | 4.4203 | 35.5697 | 8.047 | 4.4203 | 0.9517%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 483 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 88.4904 | 8.8056 | 10.0493 | 88.4904 | 8.8056 | 10.0493 | 93.2185 | 9.2761 | 10.0493 | 0.9933%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 1102 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 64.412 | 20.0906 | 3.2061 | 64.412 | 20.0906 | 3.2061 | 67.8536 | 21.1641 | 3.2061 | 0.9757%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 440 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 56.3376 | 8.0217 | 7.0232 | 56.3376 | 8.0217 | 7.0232 | 59.3477 | 8.4503 | 7.0232 | 0.9932%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 454 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 35.8983 | 8.2769 | 4.3372 | 35.8983 | 8.2769 | 4.3372 | 37.8164 | 8.7191 | 4.3372 | 0.9948%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.0558 | 0.10435 | 10.1183 | 1.0558 | 0.10435 | 10.1183 | 1.1717 | 0.1158 | 10.1183 | 0.9903%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 79 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.6908 | 1.3739 | 2.6863 | 3.6908 | 1.3739 | 2.6863 | 4.0957 | 1.5246 | 2.6863 | 0.9915%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 1219 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 35.1217 | 21.1999 | 1.6567 | 35.1217 | 21.1999 | 1.6567 | 38.9752 | 23.5259 | 1.6567 | 0.9141%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 20 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 1.0397 | 0.34782 | 2.9892 | 1.0397 | 0.34782 | 2.9892 | 1.1538 | 0.38599 | 2.9892 | 0.9976%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 1445 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 316.78 | 25.1303 | 12.6055 | 316.78 | 25.1303 | 12.6055 | 351.5364 | 27.8875 | 12.6055 | 0.9902%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 194 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 63.0347 | 3.3739 | 18.6831 | 63.0347 | 3.3739 | 18.6831 | 69.9507 | 3.7441 | 18.6831 | 0.9818%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 618 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 170.7952 | 10.7478 | 15.8912 | 170.7952 | 10.7478 | 15.8912 | 189.5344 | 11.927 | 15.8912 | 0.997%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 334 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 45.5855 | 5.8087 | 7.8479 | 45.5855 | 5.8087 | 7.8479 | 50.5871 | 6.446 | 7.8479 | 0.9951%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 70 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 12.565 | 1.2174 | 10.3214 | 12.565 | 1.2174 | 10.3214 | 13.9437 | 1.351 | 10.3214 | 0.9958%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 28 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 7.1996 | 0.48695 | 14.785 | 7.1996 | 0.48695 | 14.785 | 7.9895 | 0.54038 | 14.785 | 0.996%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 473 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 88.8468 | 8.226 | 10.8007 | 88.8468 | 8.226 | 10.8007 | 98.5948 | 9.1286 | 10.8007 | 0.9962%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 18 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 6.2724 | 0.31304 | 20.037 | 6.2724 | 0.31304 | 20.037 | 6.9606 | 0.34739 | 20.037 | 0.9922%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 262 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 45.7686 | 4.5565 | 10.0447 | 45.7686 | 4.5565 | 10.0447 | 50.7903 | 5.0564 | 10.0447 | 0.9916%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 428 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 26.0989 | 7.4434 | 3.5063 | 26.0989 | 7.4434 | 3.5063 | 28.9624 | 8.2601 | 3.5063 | 0.9924%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 1949 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 82.7087 | 33.8954 | 2.4401 | 82.7087 | 33.8954 | 2.4401 | 91.7833 | 37.6144 | 2.4401 | 0.9598%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 1169 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 33.4452 | 20.3303 | 1.6451 | 33.4452 | 20.3303 | 1.6451 | 37.1147 | 22.5609 | 1.6451 | 0.9739%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 235 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.6715 | 4.0869 | 1.143 | 4.6715 | 4.0869 | 1.143 | 5.1841 | 4.5353 | 1.143 | 0.8768%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 100 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 45.818 | 1.7391 | 26.3455 | 45.818 | 1.7391 | 26.3455 | 50.845 | 1.9299 | 26.3455 | 0.9826%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 240 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 106.0165 | 4.1739 | 25.3999 | 106.0165 | 4.1739 | 25.3999 | 117.6484 | 4.6318 | 25.3999 | 0.9858%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 288 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 19.4652 | 5.0087 | 3.8863 | 19.4652 | 5.0087 | 3.8863 | 21.6009 | 5.5582 | 3.8863 | 0.9945%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 762 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 59.4414 | 13.2521 | 4.4854 | 59.4414 | 13.2521 | 4.4854 | 65.9631 | 14.7061 | 4.4854 | 0.9866%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 1434 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 228.4185 | 24.939 | 9.1591 | 228.4185 | 24.939 | 9.1591 | 253.4801 | 27.6752 | 9.1591 | 0.9914%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 1366 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 254.5346 | 23.7564 | 10.7144 | 254.5346 | 23.7564 | 10.7144 | 282.4616 | 26.3629 | 10.7144 | 0.9849%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 1131 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 240.8882 | 19.6694 | 12.2468 | 240.8882 | 19.6694 | 12.2468 | 267.3178 | 21.8275 | 12.2468 | 0.9916%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 1778 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 141.5109 | 30.9215 | 4.5765 | 141.5109 | 30.9215 | 4.5765 | 157.0372 | 34.3142 | 4.5765 | 0.9745%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 92 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.14198 | 1.6 | 0.088735 | 0.14198 | 1.6 | 0.088735 | 0.15755 | 1.7755 | 0.088735 | 0.8684%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.031422 | 0.43478 | 0.07227 | 0.031422 | 0.43478 | 0.07227 | 0.034869 | 0.48248 | 0.07227 | 0.1275%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.019984 | 0.069565 | 0.28727 | 0.019984 | 0.069565 | 0.28727 | 0.022176 | 0.077197 | 0.28727 | 0.3435%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 21 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.5975 | 0.36522 | 18.0646 | 6.5975 | 0.36522 | 18.0646 | 7.3213 | 0.40529 | 18.0646 | 0.9924%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 183 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.8584 | 3.1826 | 2.4692 | 7.8584 | 3.1826 | 2.4692 | 8.7207 | 3.5318 | 2.4692 | 0.9393%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 39 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1281 | 0.67826 | 1.6632 | 1.1281 | 0.67826 | 1.6632 | 1.2518 | 0.75267 | 1.6632 | 0.8802%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 564 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 53.4767 | 9.8086 | 5.452 | 53.4767 | 9.8086 | 5.452 | 59.3441 | 10.8848 | 5.452 | 0.9962%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 628 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 45.2456 | 10.9217 | 4.1427 | 45.2456 | 10.9217 | 4.1427 | 50.2098 | 12.12 | 4.1427 | 0.9962%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 414 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 22.8419 | 7.2 | 3.1725 | 22.8419 | 7.2 | 3.1725 | 25.3481 | 7.9899 | 3.1725 | 0.9984%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 100 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.85678 | 1.7391 | 0.49265 | 0.85678 | 1.7391 | 0.49265 | 0.95078 | 1.9299 | 0.49265 | 0.9877%
2027 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 0.54035 | 0 | 0 | 0.54035 | 0 | 0.49171 | 0.017391 | 28.2733 | 0.49171 | 0.017391 | 28.2733 | 0.54566 | 0.019299 | 28.2733 | 0.9875%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 43 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 19.4557 | 0.74782 | 26.0165 | 19.4557 | 0.74782 | 26.0165 | 21.5904 | 0.82987 | 26.0165 | 0.9968%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 120 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 38.4457 | 2.0869 | 18.422 | 38.4457 | 2.0869 | 18.422 | 42.6639 | 2.3159 | 18.422 | 0.9992%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 113 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.5858 | 1.9652 | 1.8246 | 3.5858 | 1.9652 | 1.8246 | 3.9792 | 2.1808 | 1.8246 | 0.945%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 69 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 7.1314 | 1.2 | 5.9428 | 7.1314 | 1.2 | 5.9428 | 7.9138 | 1.3317 | 5.9428 | 0.994%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 2029 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 38.673 | 35.2867 | 1.096 | 38.673 | 35.2867 | 1.096 | 42.9161 | 39.1583 | 1.096 | 0.9112%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 24 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 1.9283 | 0.41739 | 4.6199 | 1.9283 | 0.41739 | 4.6199 | 2.1399 | 0.46318 | 4.6199 | 0.8819%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 25 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.8164 | 0.43478 | 4.1777 | 1.8164 | 0.43478 | 4.1777 | 2.0157 | 0.48248 | 4.1777 | 0.9662%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 7 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.2059 | 0.12174 | 18.1201 | 2.2059 | 0.12174 | 18.1201 | 2.4479 | 0.1351 | 18.1201 | 0.9775%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 151 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 35.4566 | 2.6261 | 13.5018 | 35.4566 | 2.6261 | 13.5018 | 39.3468 | 2.9142 | 13.5018 | 0.9826%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 214 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 91.7746 | 3.7217 | 24.6592 | 91.7746 | 3.7217 | 24.6592 | 101.8439 | 4.1301 | 24.6592 | 0.9977%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 457 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 93.0711 | 7.9478 | 11.7103 | 93.0711 | 7.9478 | 11.7103 | 103.2827 | 8.8198 | 11.7103 | 0.9908%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 85 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 54.7545 | 1.4783 | 37.04 | 54.7545 | 1.4783 | 37.04 | 60.762 | 1.6404 | 37.04 | 0.9788%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 52 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 19.0873 | 0.90434 | 21.1063 | 19.0873 | 0.90434 | 21.1063 | 21.1815 | 1.0036 | 21.1063 | 0.9469%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 334 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 76.3476 | 5.8087 | 13.1438 | 76.3476 | 5.8087 | 13.1438 | 84.7243 | 6.446 | 13.1438 | 0.9648%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 166 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.9788 | 2.8869 | 4.8421 | 13.9788 | 2.8869 | 4.8421 | 15.5125 | 3.2037 | 4.8421 | 0.9856%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 452 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 31.901 | 7.8608 | 4.0582 | 31.901 | 7.8608 | 4.0582 | 35.4011 | 8.7233 | 4.0582 | 0.9842%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 766 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 26.5819 | 13.3217 | 1.9954 | 26.5819 | 13.3217 | 1.9954 | 29.4984 | 14.7833 | 1.9954 | 0.979%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 112 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 12.4803 | 1.9478 | 6.4073 | 12.4803 | 1.9478 | 6.4073 | 13.8496 | 2.1615 | 6.4073 | 0.9892%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 544 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 38.6065 | 9.4608 | 4.0807 | 38.6065 | 9.4608 | 4.0807 | 42.8424 | 10.4988 | 4.0807 | 0.9866%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 27 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.732 | 0.46956 | 7.9478 | 3.732 | 0.46956 | 7.9478 | 4.1414 | 0.52108 | 7.9478 | 0.9965%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 77 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 4.1418 | 1.3391 | 3.0929 | 4.1418 | 1.3391 | 3.0929 | 4.5962 | 1.486 | 3.0929 | 0.9977%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 129 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.6502 | 2.2435 | 4.7472 | 10.6502 | 2.2435 | 4.7472 | 11.8187 | 2.4896 | 4.7472 | 0.9935%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 20 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.4325 | 0.34782 | 4.1186 | 1.4325 | 0.34782 | 4.1186 | 1.5897 | 0.38599 | 4.1186 | 0.9948%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 173 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.9301 | 3.0087 | 5.6271 | 16.9301 | 3.0087 | 5.6271 | 18.7877 | 3.3388 | 5.6271 | 0.9905%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 137 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 54.3399 | 2.3826 | 22.807 | 54.3399 | 2.3826 | 22.807 | 60.302 | 2.644 | 22.807 | 0.9304%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 121 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 58.631 | 2.1043 | 27.862 | 58.631 | 2.1043 | 27.862 | 65.0638 | 2.3352 | 27.862 | 0.9454%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 740 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 106.1245 | 12.8695 | 8.2462 | 106.1245 | 12.8695 | 8.2462 | 117.7682 | 14.2815 | 8.2462 | 0.9926%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 333 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 32.9139 | 5.7913 | 5.6834 | 32.9139 | 5.7913 | 5.6834 | 36.5251 | 6.4267 | 5.6834 | 0.9815%
2027 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | Non-HFTD---15 | 123 | 100% | 14.0801 | 87.11% | 0% | 12.89% | 0.12265 | 0 | 0 | 0.12265 | 0 | 0.11161 | 2.1391 | 0.052176 | 0.11161 | 2.1391 | 0.052176 | 0.12386 | 2.3738 | 0.052176 | 0.8711%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 76 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.5188 | 1.3217 | 2.6622 | 3.5188 | 1.3217 | 2.6622 | 3.9048 | 1.4667 | 2.6622 | 0.9046%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 17 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 18.4141 | 0.29565 | 62.2834 | 18.4141 | 0.29565 | 62.2834 | 20.4345 | 0.32809 | 62.2834 | 0.8554%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 221 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 39.2397 | 3.8435 | 10.2095 | 39.2397 | 3.8435 | 10.2095 | 43.545 | 4.2651 | 10.2095 | 0.9867%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.52959 | 0.069565 | 7.6129 | 0.52959 | 0.069565 | 7.6129 | 0.58769 | 0.077197 | 7.6129 | 0.9994%
2027 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 15 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.26087 | 0 | 0 | 0.26087 | 0 | 0 | 0.28949 | 0 | 0%
2027 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 23 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0.4 | 0 | 0 | 0.44388 | 0 | 0%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 149 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 144.1626 | 2.5913 | 55.6336 | 144.1626 | 2.5913 | 55.6336 | 159.9798 | 2.8756 | 55.6336 | 0.9909%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 19 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.45452 | 0.33043 | 1.3755 | 0.45452 | 0.33043 | 1.3755 | 0.50439 | 0.36669 | 1.3755 | 0.2981%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.73678 | 0.017391 | 42.365 | 0.73678 | 0.017391 | 42.365 | 0.81761 | 0.019299 | 42.365 | 0.9995%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 334 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 73.6943 | 5.8087 | 12.687 | 73.6943 | 5.8087 | 12.687 | 81.7799 | 6.446 | 12.687 | 0.9925%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 831 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 335.2263 | 14.4521 | 23.1957 | 335.2263 | 14.4521 | 23.1957 | 372.0065 | 16.0377 | 23.1957 | 0.9936%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.067341 | 0.15652 | 0.43024 | 0.067341 | 0.15652 | 0.43024 | 0.07473 | 0.17369 | 0.43024 | 0.895%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 124 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.3406 | 2.1565 | 1.5491 | 3.3406 | 2.1565 | 1.5491 | 3.7072 | 2.3931 | 1.5491 | 0.8771%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 1030 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 46.3352 | 17.9129 | 2.5867 | 46.3352 | 17.9129 | 2.5867 | 51.419 | 19.8783 | 2.5867 | 0.9246%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 96 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 27.5199 | 1.6696 | 16.4834 | 27.5199 | 1.6696 | 16.4834 | 30.5393 | 1.8527 | 16.4834 | 0.9907%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 316 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 34.9145 | 5.4956 | 6.3532 | 34.9145 | 5.4956 | 6.3532 | 38.7452 | 6.0986 | 6.3532 | 0.9899%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 356 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 27.3993 | 6.1913 | 4.4255 | 27.3993 | 6.1913 | 4.4255 | 30.4055 | 6.8706 | 4.4255 | 0.9527%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 882 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 15.2942 | 15.339 | 0.99708 | 15.2942 | 15.339 | 0.99708 | 16.9722 | 17.022 | 0.99708 | 0.8154%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 441 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 16.1452 | 7.6695 | 2.1051 | 16.1452 | 7.6695 | 2.1051 | 17.9167 | 8.511 | 2.1051 | 0.9501%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 1391 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 165.5087 | 24.1911 | 6.8417 | 165.5087 | 24.1911 | 6.8417 | 183.6679 | 26.8453 | 6.8417 | 0.97%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 593 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 36.3343 | 10.313 | 3.5232 | 36.3343 | 10.313 | 3.5232 | 40.3209 | 11.4445 | 3.5232 | 0.991%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 236 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 17.0463 | 4.1043 | 4.1533 | 17.0463 | 4.1043 | 4.1533 | 18.9166 | 4.5546 | 4.1533 | 0.7065%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 756 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 38.9182 | 13.1477 | 2.9601 | 38.9182 | 13.1477 | 2.9601 | 43.1883 | 14.5903 | 2.9601 | 0.9752%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 864 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 50.6068 | 15.026 | 3.368 | 50.6068 | 15.026 | 3.368 | 56.1593 | 16.6746 | 3.368 | 0.9686%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 245 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 6.0694 | 4.2608 | 1.4245 | 6.0694 | 4.2608 | 1.4245 | 6.7353 | 4.7283 | 1.4245 | 0.7976%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 575 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 103.5696 | 9.9999 | 10.357 | 103.5696 | 9.9999 | 10.357 | 114.9331 | 11.0971 | 10.357 | 0.9877%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 37.3556 | 6.2087 | 6.0167 | 37.3556 | 6.2087 | 6.0167 | 41.4542 | 6.8899 | 6.0167 | 0.981%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 870 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 88.9924 | 15.1303 | 5.8817 | 88.9924 | 15.1303 | 5.8817 | 98.7564 | 16.7904 | 5.8817 | 0.9713%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 30 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.4896 | 0.52174 | 4.7717 | 2.4896 | 0.52174 | 4.7717 | 2.7627 | 0.57898 | 4.7717 | 0.6764%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 270 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 30.2493 | 4.6956 | 6.442 | 30.2493 | 4.6956 | 6.442 | 33.5682 | 5.2108 | 6.442 | 0.9774%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 451 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 43.8683 | 7.8434 | 5.593 | 43.8683 | 7.8434 | 5.593 | 48.6815 | 8.704 | 5.593 | 0.977%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 1054 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 116.04 | 18.3303 | 6.3305 | 116.04 | 18.3303 | 6.3305 | 128.7717 | 20.3415 | 6.3305 | 0.968%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 77 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 13.2848 | 1.3391 | 9.9205 | 13.2848 | 1.3391 | 9.9205 | 14.7424 | 1.486 | 9.9205 | 0.8924%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 36 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 21.0957 | 0.62608 | 33.6948 | 21.0957 | 0.62608 | 33.6948 | 23.4103 | 0.69478 | 33.6948 | 0.7823%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.39517 | 0.15652 | 2.5247 | 0.39517 | 0.15652 | 2.5247 | 0.43853 | 0.17369 | 2.5247 | 0.9121%
2027 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 3 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0012779 | 0 | 0 | 0.0012779 | 0 | 0.0011628 | 0.052174 | 0.022288 | 0.0011628 | 0.052174 | 0.022288 | 0.0012904 | 0.057898 | 0.022288 | 0.1338%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 1311 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 102.2536 | 22.7999 | 4.4848 | 102.2536 | 22.7999 | 4.4848 | 113.4727 | 25.3014 | 4.4848 | 0.9429%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 11 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 17.6009 | 0.1913 | 92.0051 | 17.6009 | 0.1913 | 92.0051 | 19.532 | 0.21229 | 92.0051 | 0.9974%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 338 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 38.1899 | 5.8782 | 6.4968 | 38.1899 | 5.8782 | 6.4968 | 42.38 | 6.5232 | 6.4968 | 0.9922%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 17 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 5.9162 | 0.29565 | 20.0107 | 5.9162 | 0.29565 | 20.0107 | 6.5653 | 0.32809 | 20.0107 | 0.9914%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 85 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.9074 | 1.4783 | 1.2903 | 1.9074 | 1.4783 | 1.2903 | 2.1166 | 1.6404 | 1.2903 | 0.6623%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 180 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.1889 | 3.1304 | 1.0187 | 3.1889 | 3.1304 | 1.0187 | 3.5387 | 3.4739 | 1.0187 | 0.7437%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 481 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 14.4213 | 8.3652 | 1.724 | 14.4213 | 8.3652 | 1.724 | 16.0036 | 9.283 | 1.724 | 0.9193%
2027 | 196 | 196-43F | Tier-2 | Tier-2---17 | Tier-2---9 | 138 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.048193 | 0 | 0 | 0.048193 | 0 | 0.043855 | 2.4 | 0.018273 | 0.043855 | 2.4 | 0.018273 | 0.048666 | 2.6633 | 0.018273 | 0.0514%
2027 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 2 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.6591 | 0.034782 | 47.6988 | 1.6591 | 0.034782 | 47.6988 | 1.8411 | 0.038599 | 47.6988 | 0.9934%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 27 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.058051 | 0.46956 | 0.12363 | 0.058051 | 0.46956 | 0.12363 | 0.06442 | 0.52108 | 0.12363 | 0.9638%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 103 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.4596 | 1.7913 | 4.7226 | 8.4596 | 1.7913 | 4.7226 | 9.3877 | 1.9878 | 4.7226 | 0.9553%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 301 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.3008 | 5.2347 | 0.82158 | 4.3008 | 5.2347 | 0.82158 | 4.7727 | 5.8091 | 0.82158 | 0.9636%
2027 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 9 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 1.2217 | 0 | 0 | 1.2217 | 0 | 1.1118 | 0.15652 | 7.103 | 1.1118 | 0.15652 | 7.103 | 1.2337 | 0.17369 | 7.103 | 0.9852%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 66 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 11.614 | 1.1478 | 10.1183 | 11.614 | 1.1478 | 10.1183 | 12.8883 | 1.2738 | 10.1183 | 0.9978%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 385 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 27.0186 | 6.6956 | 4.0353 | 27.0186 | 6.6956 | 4.0353 | 29.9831 | 7.4302 | 4.0353 | 0.9975%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1294 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 76.8107 | 22.5042 | 3.4132 | 76.8107 | 22.5042 | 3.4132 | 85.2382 | 24.9733 | 3.4132 | 0.9974%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 202 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 4.0842 | 3.513 | 1.1626 | 4.0842 | 3.513 | 1.1626 | 4.5324 | 3.8985 | 1.1626 | 0.901%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 360 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 8.0972 | 6.2608 | 1.2933 | 8.0972 | 6.2608 | 1.2933 | 8.9856 | 6.9478 | 1.2933 | 0.8573%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 240 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.094 | 4.1739 | 0.2621 | 1.094 | 4.1739 | 0.2621 | 1.214 | 4.6318 | 0.2621 | 0.7047%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 183 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.4697 | 3.1826 | 0.46179 | 1.4697 | 3.1826 | 0.46179 | 1.6309 | 3.5318 | 0.46179 | 0.5082%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 410 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.7688 | 7.1304 | 1.37 | 9.7688 | 7.1304 | 1.37 | 10.8406 | 7.9127 | 1.37 | 0.8949%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 321 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.8754 | 5.5826 | 2.4855 | 13.8754 | 5.5826 | 2.4855 | 15.3977 | 6.1951 | 2.4855 | 0.8426%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 1148 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 15.667 | 19.9651 | 0.78472 | 15.667 | 19.9651 | 0.78472 | 17.386 | 22.1556 | 0.78472 | 0.9106%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 386 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 15.1003 | 6.713 | 2.2494 | 15.1003 | 6.713 | 2.2494 | 16.7571 | 7.4495 | 2.2494 | 0.9543%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 267 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 13.5718 | 4.6434 | 2.9228 | 13.5718 | 4.6434 | 2.9228 | 15.0609 | 5.1529 | 2.9228 | 0.9497%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 39 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.4971 | 0.67826 | 8.1048 | 5.4971 | 0.67826 | 8.1048 | 6.1003 | 0.75267 | 8.1048 | 0.9907%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 1799 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 44.1009 | 31.2868 | 1.4096 | 44.1009 | 31.2868 | 1.4096 | 48.9396 | 34.7195 | 1.4096 | 0.9915%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 23 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 11.2803 | 0.4 | 28.2008 | 11.2803 | 0.4 | 28.2008 | 12.5179 | 0.44388 | 28.2008 | 0.9792%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 658 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.7819 | 11.4434 | 0.76742 | 8.7819 | 11.4434 | 0.76742 | 9.7454 | 12.6989 | 0.76742 | 0.9662%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 63 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.3089 | 1.0956 | 2.1073 | 2.3089 | 1.0956 | 2.1073 | 2.5622 | 1.2159 | 2.1073 | 0.9706%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 268 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 13.1223 | 4.6608 | 2.8154 | 13.1223 | 4.6608 | 2.8154 | 14.562 | 5.1722 | 2.8154 | 0.9727%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 413 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 24.0425 | 7.1826 | 3.3473 | 24.0425 | 7.1826 | 3.3473 | 26.6803 | 7.9706 | 3.3473 | 0.9578%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 105 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 9.1807 | 1.8261 | 5.0275 | 9.1807 | 1.8261 | 5.0275 | 10.1879 | 2.0264 | 5.0275 | 0.9712%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 94 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.9338 | 1.6348 | 0.57121 | 0.9338 | 1.6348 | 0.57121 | 1.0363 | 1.8141 | 0.57121 | 0.9778%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 160 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 19.4357 | 2.7826 | 6.9848 | 19.4357 | 2.7826 | 6.9848 | 21.5682 | 3.0879 | 6.9848 | 0.9872%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 125 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 13.0944 | 2.1739 | 6.0235 | 13.0944 | 2.1739 | 6.0235 | 14.5311 | 2.4124 | 6.0235 | 0.9782%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 1694 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 236.5383 | 29.4607 | 8.029 | 236.5383 | 29.4607 | 8.029 | 262.4908 | 32.693 | 8.029 | 0.9891%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 980 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 60.3082 | 17.0434 | 3.5385 | 60.3082 | 17.0434 | 3.5385 | 66.9251 | 18.9133 | 3.5385 | 0.9941%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 1791 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.2902 | 31.1476 | 0.13774 | 4.2902 | 31.1476 | 0.13774 | 4.7609 | 34.5651 | 0.13774 | 0.974%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 892 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.5637 | 15.5129 | 0.22973 | 3.5637 | 15.5129 | 0.22973 | 3.9547 | 17.215 | 0.22973 | 0.9786%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 433 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.6112 | 7.5304 | 0.61235 | 4.6112 | 7.5304 | 0.61235 | 5.1171 | 8.3566 | 0.61235 | 0.9871%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 19.9133 | 5.5304 | 3.6007 | 19.9133 | 5.5304 | 3.6007 | 22.0981 | 6.1372 | 3.6007 | 0.9909%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 1357 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 13.4254 | 23.5998 | 0.56888 | 13.4254 | 23.5998 | 0.56888 | 14.8984 | 26.1892 | 0.56888 | 0.8569%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 617 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 201.8812 | 10.7304 | 18.814 | 201.8812 | 10.7304 | 18.814 | 224.0311 | 11.9077 | 18.814 | 0.9924%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 729 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 113.526 | 12.6782 | 8.9544 | 113.526 | 12.6782 | 8.9544 | 125.9818 | 14.0692 | 8.9544 | 0.9821%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 471 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 175.5743 | 8.1913 | 21.4344 | 175.5743 | 8.1913 | 21.4344 | 194.8379 | 9.09 | 21.4344 | 0.99%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 156 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.6078 | 2.713 | 4.6471 | 12.6078 | 2.713 | 4.6471 | 13.9911 | 3.0107 | 4.6471 | 0.9809%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 354 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 48.9203 | 6.1565 | 7.9462 | 48.9203 | 6.1565 | 7.9462 | 54.2878 | 6.832 | 7.9462 | 0.9892%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 445 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 126.7327 | 7.7391 | 16.3757 | 126.7327 | 7.7391 | 16.3757 | 140.6375 | 8.5882 | 16.3757 | 0.9919%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.648 | 0.12174 | 5.3229 | 0.648 | 0.12174 | 5.3229 | 0.7191 | 0.1351 | 5.3229 | 0.999%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 997 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 16.3491 | 17.339 | 0.94291 | 16.3491 | 17.339 | 0.94291 | 18.1429 | 19.2414 | 0.94291 | 0.8922%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 790 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 21.8049 | 13.739 | 1.5871 | 21.8049 | 13.739 | 1.5871 | 24.1973 | 15.2465 | 1.5871 | 0.8785%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 1010 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 95.9693 | 17.5651 | 5.4636 | 95.9693 | 17.5651 | 5.4636 | 106.4988 | 19.4923 | 5.4636 | 0.9868%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 866 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 31.5024 | 15.0608 | 2.0917 | 31.5024 | 15.0608 | 2.0917 | 34.9588 | 16.7132 | 2.0917 | 0.9466%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 923 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.8972 | 16.0521 | 0.74116 | 11.8972 | 16.0521 | 0.74116 | 13.2025 | 17.8133 | 0.74116 | 0.9088%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 249 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 91.1879 | 4.3304 | 21.0576 | 91.1879 | 4.3304 | 21.0576 | 101.1929 | 4.8055 | 21.0576 | 0.9905%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 187 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 19.2748 | 3.2522 | 5.9268 | 19.2748 | 3.2522 | 5.9268 | 21.3895 | 3.609 | 5.9268 | 0.9634%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 978 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.7722 | 17.0086 | 0.86852 | 14.7722 | 17.0086 | 0.86852 | 16.393 | 18.8747 | 0.86852 | 0.8429%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 2947 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 29.1603 | 51.2518 | 0.56896 | 29.1603 | 51.2518 | 0.56896 | 32.3597 | 56.8751 | 0.56896 | 0.8937%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 161 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 33.5564 | 2.8 | 11.9845 | 33.5564 | 2.8 | 11.9845 | 37.2381 | 3.1072 | 11.9845 | 0.9991%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 1068 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 27.4264 | 18.5738 | 1.4766 | 27.4264 | 18.5738 | 1.4766 | 30.4355 | 20.6117 | 1.4766 | 0.9216%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 1386 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 23.9276 | 24.1042 | 0.99268 | 23.9276 | 24.1042 | 0.99268 | 26.5529 | 26.7488 | 0.99268 | 0.9611%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 16 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.4289 | 0.27826 | 23.1039 | 6.4289 | 0.27826 | 23.1039 | 7.1342 | 0.30879 | 23.1039 | 0.9946%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 1029 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 34.741 | 17.8955 | 1.9413 | 34.741 | 17.8955 | 1.9413 | 38.5527 | 19.859 | 1.9413 | 0.9703%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 144 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.96674 | 2.5043 | 0.38603 | 0.96674 | 2.5043 | 0.38603 | 1.0728 | 2.7791 | 0.38603 | 0.334%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 18.6124 | 1.9652 | 9.471 | 18.6124 | 1.9652 | 9.471 | 20.6545 | 2.1808 | 9.471 | 0.9951%
2027 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 6 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 35.4849 | 0.10435 | 340.0663 | 35.4849 | 0.10435 | 340.0663 | 39.3783 | 0.1158 | 340.0663 | 0.9988%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 333 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.5498 | 5.7913 | 0.9583 | 5.5498 | 5.7913 | 0.9583 | 6.1587 | 6.4267 | 0.9583 | 0.9868%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 365 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 40.5593 | 6.3478 | 6.3895 | 40.5593 | 6.3478 | 6.3895 | 45.0094 | 7.0442 | 6.3895 | 0.9945%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 172 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 20.4866 | 2.9913 | 6.8488 | 20.4866 | 2.9913 | 6.8488 | 22.7343 | 3.3195 | 6.8488 | 0.9686%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 173 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 87.1653 | 3.0087 | 28.9713 | 87.1653 | 3.0087 | 28.9713 | 96.7288 | 3.3388 | 28.9713 | 0.9959%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 573 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.7708 | 9.9652 | 1.1812 | 11.7708 | 9.9652 | 1.1812 | 13.0623 | 11.0585 | 1.1812 | 0.9515%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 2453 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 65.1242 | 42.6606 | 1.5266 | 65.1242 | 42.6606 | 1.5266 | 72.2695 | 47.3412 | 1.5266 | 0.9662%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 895 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 715.269 | 15.5651 | 45.9533 | 715.269 | 15.5651 | 45.9533 | 793.7467 | 17.2729 | 45.9533 | 0.9925%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 47 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 32.6952 | 0.81739 | 39.9997 | 32.6952 | 0.81739 | 39.9997 | 36.2824 | 0.90707 | 39.9997 | 0.9927%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 409 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 408.9425 | 7.113 | 57.4923 | 408.9425 | 7.113 | 57.4923 | 453.8108 | 7.8934 | 57.4923 | 0.9963%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 40 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.2745 | 0.69565 | 3.2696 | 2.2745 | 0.69565 | 3.2696 | 2.5241 | 0.77197 | 3.2696 | 0.8656%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 1410 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 64.9142 | 24.5216 | 2.6472 | 64.9142 | 24.5216 | 2.6472 | 72.0364 | 27.212 | 2.6472 | 0.9605%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 237 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 44.1572 | 4.1217 | 10.7133 | 44.1572 | 4.1217 | 10.7133 | 49.0021 | 4.5739 | 10.7133 | 0.9985%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 3377 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 147.5821 | 58.7301 | 2.5129 | 147.5821 | 58.7301 | 2.5129 | 163.7745 | 65.1738 | 2.5129 | 0.967%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 4 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.15542 | 0.069565 | 2.2342 | 0.15542 | 0.069565 | 2.2342 | 0.17247 | 0.077197 | 2.2342 | 0.9833%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 10 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.5515 | 0.17391 | 8.9215 | 1.5515 | 0.17391 | 8.9215 | 1.7218 | 0.19299 | 8.9215 | 0.9937%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 1039 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 17.2908 | 18.0694 | 0.95691 | 17.2908 | 18.0694 | 0.95691 | 19.188 | 20.052 | 0.95691 | 0.9498%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 1418 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 57.1262 | 24.6607 | 2.3165 | 57.1262 | 24.6607 | 2.3165 | 63.3939 | 27.3664 | 2.3165 | 0.9826%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 1039 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 17.1775 | 18.0694 | 0.95064 | 17.1775 | 18.0694 | 0.95064 | 19.0622 | 20.052 | 0.95064 | 0.9106%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 329 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.8545 | 5.7217 | 0.67365 | 3.8545 | 5.7217 | 0.67365 | 4.2774 | 6.3495 | 0.67365 | 0.7897%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 165 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 7.0473 | 2.8695 | 2.4559 | 7.0473 | 2.8695 | 2.4559 | 7.8205 | 3.1844 | 2.4559 | 0.9819%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 865 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 30.8736 | 15.0434 | 2.0523 | 30.8736 | 15.0434 | 2.0523 | 34.261 | 16.6939 | 2.0523 | 0.9768%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 13 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 1.0289 | 0.22609 | 4.5509 | 1.0289 | 0.22609 | 4.5509 | 1.1418 | 0.25089 | 4.5509 | 0.9298%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 106 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.4554 | 1.8435 | 0.78948 | 1.4554 | 1.8435 | 0.78948 | 1.6151 | 2.0457 | 0.78948 | 0.8171%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 1011 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 24.429 | 17.5825 | 1.3894 | 24.429 | 17.5825 | 1.3894 | 27.1093 | 19.5116 | 1.3894 | 0.983%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 3541 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 46.1751 | 61.5822 | 0.74981 | 46.1751 | 61.5822 | 0.74981 | 51.2413 | 68.3389 | 0.74981 | 0.9868%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.00047048 | 0.10435 | 0.0045088 | 0.00047048 | 0.10435 | 0.0045088 | 0.0005221 | 0.1158 | 0.0045088 | 0.004523%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 1420 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 27.3047 | 24.6955 | 1.1057 | 27.3047 | 24.6955 | 1.1057 | 30.3005 | 27.405 | 1.1057 | 0.9884%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 548 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.3838 | 9.5304 | 0.66983 | 6.3838 | 9.5304 | 0.66983 | 7.0842 | 10.576 | 0.66983 | 0.9757%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 453 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.8693 | 7.8782 | 0.49113 | 3.8693 | 7.8782 | 0.49113 | 4.2938 | 8.7426 | 0.49113 | 0.9496%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 875 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 18.3049 | 15.2173 | 1.2029 | 18.3049 | 15.2173 | 1.2029 | 20.3133 | 16.8869 | 1.2029 | 0.859%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 1371 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 44.7034 | 23.8433 | 1.8749 | 44.7034 | 23.8433 | 1.8749 | 49.6082 | 26.4594 | 1.8749 | 0.9946%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 275 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 35.2843 | 4.7826 | 7.3777 | 35.2843 | 4.7826 | 7.3777 | 39.1556 | 5.3073 | 7.3777 | 0.8863%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 897 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 211.9523 | 15.5999 | 13.5868 | 211.9523 | 15.5999 | 13.5868 | 235.2072 | 17.3115 | 13.5868 | 0.9837%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 800 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 87.3211 | 13.913 | 6.2762 | 87.3211 | 13.913 | 6.2762 | 96.9018 | 15.4394 | 6.2762 | 0.9873%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 260 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 24.9907 | 4.5217 | 5.5268 | 24.9907 | 4.5217 | 5.5268 | 27.7326 | 5.0178 | 5.5268 | 0.9726%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 177 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 20.2852 | 3.0782 | 6.5899 | 20.2852 | 3.0782 | 6.5899 | 22.5108 | 3.416 | 6.5899 | 0.9861%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 530 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 47.5862 | 9.2173 | 5.1627 | 47.5862 | 9.2173 | 5.1627 | 52.8073 | 10.2286 | 5.1627 | 0.9807%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 954 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 189.9659 | 16.5912 | 11.4498 | 189.9659 | 16.5912 | 11.4498 | 210.8085 | 18.4115 | 11.4498 | 0.9836%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 256 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 61.6836 | 4.4521 | 13.8548 | 61.6836 | 4.4521 | 13.8548 | 68.4514 | 4.9406 | 13.8548 | 0.9784%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 32.8705 | 1.9478 | 16.8756 | 32.8705 | 1.9478 | 16.8756 | 36.477 | 2.1615 | 16.8756 | 0.994%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 398 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 255.3789 | 6.9217 | 36.8954 | 255.3789 | 6.9217 | 36.8954 | 283.3985 | 7.6811 | 36.8954 | 0.9934%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 1107 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 243.7006 | 19.252 | 12.6584 | 243.7006 | 19.252 | 12.6584 | 270.4388 | 21.3643 | 12.6584 | 0.9889%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 88 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.278 | 1.5304 | 2.7953 | 4.278 | 1.5304 | 2.7953 | 4.7474 | 1.6983 | 2.7953 | 0.7089%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 22.7545 | 0.60869 | 37.3826 | 22.7545 | 0.60869 | 37.3826 | 25.251 | 0.67548 | 37.3826 | 0.9883%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 1011 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 278.6354 | 17.5825 | 15.8473 | 278.6354 | 17.5825 | 15.8473 | 309.2066 | 19.5116 | 15.8473 | 0.9911%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 1263 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 589.8137 | 21.9651 | 26.8523 | 589.8137 | 21.9651 | 26.8523 | 654.5266 | 24.375 | 26.8523 | 0.9893%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 689 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.6786 | 11.9825 | 0.64082 | 7.6786 | 11.9825 | 0.64082 | 8.5211 | 13.2972 | 0.64082 | 0.9808%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 111 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 14.233 | 1.9304 | 7.373 | 14.233 | 1.9304 | 7.373 | 15.7947 | 2.1422 | 7.373 | 0.9867%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 480 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.7998 | 8.3478 | 1.1739 | 9.7998 | 8.3478 | 1.1739 | 10.875 | 9.2637 | 1.1739 | 0.9646%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 909 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 56.0399 | 15.8086 | 3.5449 | 56.0399 | 15.8086 | 3.5449 | 62.1884 | 17.5431 | 3.5449 | 0.9824%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 674 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.49 | 11.7217 | 0.55368 | 6.49 | 11.7217 | 0.55368 | 7.2021 | 13.0077 | 0.55368 | 0.6927%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 61 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.3828 | 1.0609 | 3.1888 | 3.3828 | 1.0609 | 3.1888 | 3.754 | 1.1773 | 3.1888 | 0.9876%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 261 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.5781 | 4.5391 | 2.3304 | 10.5781 | 4.5391 | 2.3304 | 11.7387 | 5.0371 | 2.3304 | 0.9838%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 103 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 7.1078 | 1.7913 | 3.968 | 7.1078 | 1.7913 | 3.968 | 7.8876 | 1.9878 | 3.968 | 0.987%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 102 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.3211 | 1.7739 | 1.8722 | 3.3211 | 1.7739 | 1.8722 | 3.6854 | 1.9685 | 1.8722 | 0.9688%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 1050 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 39.5381 | 18.2608 | 2.1652 | 39.5381 | 18.2608 | 2.1652 | 43.8761 | 20.2643 | 2.1652 | 0.9791%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 538 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 33.7387 | 9.3565 | 3.6059 | 33.7387 | 9.3565 | 3.6059 | 37.4405 | 10.383 | 3.6059 | 0.9907%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 555 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 32.2959 | 9.6521 | 3.346 | 32.2959 | 9.6521 | 3.346 | 35.8393 | 10.7111 | 3.346 | 0.9682%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 301 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.7642 | 5.2347 | 1.1011 | 5.7642 | 5.2347 | 1.1011 | 6.3966 | 5.8091 | 1.1011 | 0.6596%
2027 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 1 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 1.1925 | 0 | 0 | 1.1925 | 0 | 1.0852 | 0.017391 | 62.3973 | 1.0852 | 0.017391 | 62.3973 | 1.2042 | 0.019299 | 62.3973 | 0.295%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 883 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 29.1399 | 15.3564 | 1.8976 | 29.1399 | 15.3564 | 1.8976 | 32.3371 | 17.0413 | 1.8976 | 0.9454%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 296 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 11.4521 | 5.1478 | 2.2247 | 11.4521 | 5.1478 | 2.2247 | 12.7086 | 5.7126 | 2.2247 | 0.9251%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 20 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.93993 | 0.34782 | 2.7023 | 0.93993 | 0.34782 | 2.7023 | 1.0431 | 0.38599 | 2.7023 | 0.9818%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 32.7369 | 11.1478 | 2.9366 | 32.7369 | 11.1478 | 2.9366 | 36.3287 | 12.3709 | 2.9366 | 0.9585%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.39026 | 0.15652 | 2.4933 | 0.39026 | 0.15652 | 2.4933 | 0.43308 | 0.17369 | 2.4933 | 0.8666%
2027 | 280 | 280-24AE | Tier-2 | Tier-2---12 | Tier-2---4 | 6 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.11503 | 0 | 0 | 0.11503 | 0 | 0.10468 | 0.10435 | 1.0032 | 0.10468 | 0.10435 | 1.0032 | 0.11616 | 0.1158 | 1.0032 | 0.03145%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 47.5288 | 1.8956 | 25.0727 | 47.5288 | 1.8956 | 25.0727 | 52.7435 | 2.1036 | 25.0727 | 0.9855%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 284 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 16.0881 | 4.9391 | 3.2573 | 16.0881 | 4.9391 | 3.2573 | 17.8533 | 5.481 | 3.2573 | 0.878%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 4.1304 | 0.017391 | 237.4971 | 4.1304 | 0.017391 | 237.4971 | 4.5835 | 0.019299 | 237.4971 | 0.9431%
2027 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 18 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.37366 | 0.31304 | 1.1936 | 0.37366 | 0.31304 | 1.1936 | 0.41466 | 0.34739 | 1.1936 | 0.9823%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 375 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.6538 | 6.5217 | 0.71359 | 4.6538 | 6.5217 | 0.71359 | 5.1645 | 7.2372 | 0.71359 | 0.9288%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 62 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.023211 | 1.0783 | 0.021527 | 0.023211 | 1.0783 | 0.021527 | 0.025758 | 1.1966 | 0.021527 | 0.7897%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 63 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 4.1532 | 1.0956 | 3.7906 | 4.1532 | 1.0956 | 3.7906 | 4.6088 | 1.2159 | 3.7906 | 0.9948%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 269 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.3417 | 4.6782 | 1.3556 | 6.3417 | 4.6782 | 1.3556 | 7.0375 | 5.1915 | 1.3556 | 0.9241%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 521 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.9495 | 9.0608 | 2.2017 | 19.9495 | 9.0608 | 2.2017 | 22.1383 | 10.0549 | 2.2017 | 0.9107%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 1014 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 41.4107 | 17.6347 | 2.3483 | 41.4107 | 17.6347 | 2.3483 | 45.9542 | 19.5695 | 2.3483 | 0.9555%
2027 | 308 | 308-485AE | Tier-2 | Tier-2---15 | Tier-2---8 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.043838 | 0 | 0 | 0.043838 | 0 | 0.039892 | 0.086956 | 0.45876 | 0.039892 | 0.086956 | 0.45876 | 0.044268 | 0.096497 | 0.45876 | 0.02775%
2027 | 308 | 308-486AE | Tier-2 | Tier-2---16 | Tier-2---8 | 2 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.039249 | 0 | 0 | 0.039249 | 0 | 0.035716 | 0.034782 | 1.0268 | 0.035716 | 0.034782 | 1.0268 | 0.039635 | 0.038599 | 1.0268 | 0.02383%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 16 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16842 | 0.27826 | 0.60525 | 0.16842 | 0.27826 | 0.60525 | 0.1869 | 0.30879 | 0.60525 | 0.1937%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 5 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.35602 | 0.086956 | 4.0943 | 0.35602 | 0.086956 | 4.0943 | 0.39508 | 0.096497 | 4.0943 | 0.8469%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 34 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.070129 | 0.5913 | 0.1186 | 0.070129 | 0.5913 | 0.1186 | 0.077823 | 0.65618 | 0.1186 | 0.4938%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 22 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.4128 | 0.38261 | 1.0789 | 0.4128 | 0.38261 | 1.0789 | 0.4581 | 0.42458 | 1.0789 | 0.1628%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 347 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.034025 | 6.0347 | 0.0056382 | 0.034025 | 6.0347 | 0.0056382 | 0.037758 | 6.6969 | 0.0056382 | 0.02339%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 50 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0027839 | 0.86956 | 0.0032015 | 0.0027839 | 0.86956 | 0.0032015 | 0.0030893 | 0.96497 | 0.0032015 | 0.001514%
2027 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.1439 | 0 | 0 | 0.1439 | 0 | 0.13094 | 0.13913 | 0.94116 | 0.13094 | 0.13913 | 0.94116 | 0.14531 | 0.15439 | 0.94116 | 0.981%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 424 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.9002 | 7.3739 | 0.25769 | 1.9002 | 7.3739 | 0.25769 | 2.1086 | 8.1829 | 0.25769 | 0.995%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 17 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.732 | 0.29565 | 9.2405 | 2.732 | 0.29565 | 9.2405 | 3.0317 | 0.32809 | 9.2405 | 0.9927%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 2015 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 31.2978 | 35.0432 | 0.89312 | 31.2978 | 35.0432 | 0.89312 | 34.7317 | 38.8881 | 0.89312 | 0.9548%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 2337 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 123.8786 | 40.6432 | 3.048 | 123.8786 | 40.6432 | 3.048 | 137.4703 | 45.1025 | 3.048 | 0.9814%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 2775 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 49.1654 | 48.2606 | 1.0187 | 49.1654 | 48.2606 | 1.0187 | 54.5597 | 53.5556 | 1.0187 | 0.9699%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 1107 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 122.1654 | 19.252 | 6.3456 | 122.1654 | 19.252 | 6.3456 | 135.5691 | 21.3643 | 6.3456 | 0.9928%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 1576 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 100.7847 | 27.4085 | 3.6771 | 100.7847 | 27.4085 | 3.6771 | 111.8425 | 30.4157 | 3.6771 | 0.9888%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 1026 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 212.4003 | 17.8434 | 11.9036 | 212.4003 | 17.8434 | 11.9036 | 235.7044 | 19.8011 | 11.9036 | 0.9925%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 243 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 82.9876 | 4.2261 | 19.6371 | 82.9876 | 4.2261 | 19.6371 | 92.0928 | 4.6897 | 19.6371 | 0.9973%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 1556 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 168.3033 | 27.0607 | 6.2195 | 168.3033 | 27.0607 | 6.2195 | 186.7692 | 30.0297 | 6.2195 | 0.9936%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 951 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 81.809 | 16.539 | 4.9464 | 81.809 | 16.539 | 4.9464 | 90.7849 | 18.3536 | 4.9464 | 0.9749%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 266 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 22.7355 | 4.6261 | 4.9147 | 22.7355 | 4.6261 | 4.9147 | 25.2299 | 5.1336 | 4.9147 | 0.9918%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 93 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 20.1485 | 1.6174 | 12.4575 | 20.1485 | 1.6174 | 12.4575 | 22.3591 | 1.7948 | 12.4575 | 0.9993%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 172 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 16.0724 | 2.9913 | 5.3731 | 16.0724 | 2.9913 | 5.3731 | 17.8358 | 3.3195 | 5.3731 | 0.8869%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 138 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 39.0935 | 2.4 | 16.289 | 39.0935 | 2.4 | 16.289 | 43.3827 | 2.6633 | 16.289 | 0.943%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.6596 | 0.86956 | 3.0586 | 2.6596 | 0.86956 | 3.0586 | 2.9514 | 0.96497 | 3.0586 | 0.6284%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 379 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 122.4623 | 6.5913 | 18.5795 | 122.4623 | 6.5913 | 18.5795 | 135.8986 | 7.3144 | 18.5795 | 0.9943%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 1602 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 185.0853 | 27.8607 | 6.6432 | 185.0853 | 27.8607 | 6.6432 | 205.3924 | 30.9175 | 6.6432 | 0.9917%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 226 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 29.4362 | 3.9304 | 7.4893 | 29.4362 | 3.9304 | 7.4893 | 32.6658 | 4.3616 | 7.4893 | 0.8854%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 580 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 67.231 | 10.0869 | 6.6652 | 67.231 | 10.0869 | 6.6652 | 74.6075 | 11.1936 | 6.6652 | 0.985%
2027 | 355 | 355-65R | Tier-2 | Tier-2---21 | Tier-2---24 | 2 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.00030886 | 0 | 0 | 0.00030886 | 0 | 0.00028106 | 0.034782 | 0.0080805 | 0.00028106 | 0.034782 | 0.0080805 | 0.0003119 | 0.038599 | 0.0080805 | 0.4611%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 248 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 12.357 | 4.313 | 2.865 | 12.357 | 4.313 | 2.865 | 13.7128 | 4.7862 | 2.865 | 0.7994%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 346 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 48.5603 | 6.0174 | 8.07 | 48.5603 | 6.0174 | 8.07 | 53.8882 | 6.6776 | 8.07 | 0.9814%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 1320 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 142.4543 | 22.9564 | 6.2054 | 142.4543 | 22.9564 | 6.2054 | 158.0841 | 25.4751 | 6.2054 | 0.9776%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 1086 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 80.6995 | 18.8868 | 4.2728 | 80.6995 | 18.8868 | 4.2728 | 89.5536 | 20.9591 | 4.2728 | 0.9541%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 47 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 11.2788 | 0.81739 | 13.7986 | 11.2788 | 0.81739 | 13.7986 | 12.5163 | 0.90707 | 13.7986 | 0.9906%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 50 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 46.2497 | 0.86956 | 53.1875 | 46.2497 | 0.86956 | 53.1875 | 51.3241 | 0.96497 | 53.1875 | 0.9968%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 10 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.6371 | 0.17391 | 43.9134 | 7.6371 | 0.17391 | 43.9134 | 8.475 | 0.19299 | 43.9134 | 0.9549%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 489 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 151.6491 | 8.5043 | 17.8321 | 151.6491 | 8.5043 | 17.8321 | 168.2877 | 9.4374 | 17.8321 | 0.9879%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 938 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 156.9706 | 16.3129 | 9.6225 | 156.9706 | 16.3129 | 9.6225 | 174.193 | 18.1028 | 9.6225 | 0.9747%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 1053 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 92.1224 | 18.3129 | 5.0305 | 92.1224 | 18.3129 | 5.0305 | 102.2299 | 20.3222 | 5.0305 | 0.9704%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 650 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 104.6452 | 11.3043 | 9.2571 | 104.6452 | 11.3043 | 9.2571 | 116.1267 | 12.5446 | 9.2571 | 0.9781%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 29 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.3037 | 0.50434 | 10.516 | 5.3037 | 0.50434 | 10.516 | 5.8856 | 0.55968 | 10.516 | 0.9721%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 56 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 12.1945 | 0.97391 | 12.5212 | 12.1945 | 0.97391 | 12.5212 | 13.5325 | 1.0808 | 12.5212 | 0.9966%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 437 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 337.3598 | 7.6 | 44.3897 | 337.3598 | 7.6 | 44.3897 | 374.3741 | 8.4338 | 44.3897 | 0.9859%
2027 | 386 | 386-25R | Tier-2 | Tier-2---15 | Tier-2---9 | 3 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 0.50797 | 0 | 0 | 0.50797 | 0 | 0.46224 | 0.052174 | 8.8597 | 0.46224 | 0.052174 | 8.8597 | 0.51296 | 0.057898 | 8.8597 | 0.3536%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 79 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.7862 | 1.3739 | 8.5786 | 11.7862 | 1.3739 | 8.5786 | 13.0794 | 1.5246 | 8.5786 | 0.8901%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 87 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5811 | 1.513 | 1.045 | 1.5811 | 1.513 | 1.045 | 1.7545 | 1.679 | 1.045 | 0.1879%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 1753 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 25.1718 | 30.4868 | 0.82566 | 25.1718 | 30.4868 | 0.82566 | 27.9336 | 33.8317 | 0.82566 | 0.8818%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 728 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 16.5372 | 12.6608 | 1.3062 | 16.5372 | 12.6608 | 1.3062 | 18.3516 | 14.0499 | 1.3062 | 0.9783%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 1526 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 57.0772 | 26.539 | 2.1507 | 57.0772 | 26.539 | 2.1507 | 63.3396 | 29.4507 | 2.1507 | 0.9847%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 68 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.7938 | 1.1826 | 9.9727 | 11.7938 | 1.1826 | 9.9727 | 13.0878 | 1.3124 | 9.9727 | 0.9597%
2027 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 115 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.63991 | 2 | 0.31996 | 0.63991 | 2 | 0.31996 | 0.71012 | 2.2194 | 0.31996 | 0.9953%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 376 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 31.198 | 6.5391 | 4.771 | 31.198 | 6.5391 | 4.771 | 34.621 | 7.2565 | 4.771 | 0.9745%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.8386 | 0.83478 | 5.7963 | 4.8386 | 0.83478 | 5.7963 | 5.3695 | 0.92637 | 5.7963 | 0.9134%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 115 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 42.3621 | 2 | 21.1812 | 42.3621 | 2 | 21.1812 | 47.01 | 2.2194 | 21.1812 | 0.98%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 47.9792 | 1.0956 | 43.7908 | 47.9792 | 1.0956 | 43.7908 | 53.2434 | 1.2159 | 43.7908 | 0.9857%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 909 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 16.0443 | 15.8086 | 1.0149 | 16.0443 | 15.8086 | 1.0149 | 17.8046 | 17.5431 | 1.0149 | 0.9609%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 31 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.013995 | 0.53913 | 0.025959 | 0.013995 | 0.53913 | 0.025959 | 0.015531 | 0.59828 | 0.025959 | 0.01745%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 866 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.5914 | 15.0608 | 0.43766 | 6.5914 | 15.0608 | 0.43766 | 7.3146 | 16.7132 | 0.43766 | 0.8492%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 664 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.7746 | 11.5478 | 0.24027 | 2.7746 | 11.5478 | 0.24027 | 3.079 | 12.8147 | 0.24027 | 0.5795%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 1856 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 93.1705 | 32.278 | 2.8865 | 93.1705 | 32.278 | 2.8865 | 103.393 | 35.8195 | 2.8865 | 0.8848%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 38 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 6.1949 | 0.66087 | 9.3739 | 6.1949 | 0.66087 | 9.3739 | 6.8746 | 0.73337 | 9.3739 | 0.9662%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 41 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.951 | 0.71304 | 6.9435 | 4.951 | 0.71304 | 6.9435 | 5.4942 | 0.79127 | 6.9435 | 0.9893%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 289 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.9446 | 5.0261 | 0.78483 | 3.9446 | 5.0261 | 0.78483 | 4.3774 | 5.5775 | 0.78483 | 0.9131%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 204 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.65617 | 3.5478 | 0.18495 | 0.65617 | 3.5478 | 0.18495 | 0.72816 | 3.9371 | 0.18495 | 0.51%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 6 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 2.9352 | 0.10435 | 28.1292 | 2.9352 | 0.10435 | 28.1292 | 3.2572 | 0.1158 | 28.1292 | 0.9662%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 30.3414 | 2.4522 | 12.3734 | 30.3414 | 2.4522 | 12.3734 | 33.6704 | 2.7212 | 12.3734 | 0.9767%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 594 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.6755 | 10.3304 | 0.3558 | 3.6755 | 10.3304 | 0.3558 | 4.0788 | 11.4638 | 0.3558 | 0.7071%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 390 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 83.235 | 6.7826 | 12.2719 | 83.235 | 6.7826 | 12.2719 | 92.3673 | 7.5267 | 12.2719 | 0.9496%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 252 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 63.4108 | 4.3826 | 14.4688 | 63.4108 | 4.3826 | 14.4688 | 70.3681 | 4.8634 | 14.4688 | 0.9611%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 171 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.9463 | 2.9739 | 4.3533 | 12.9463 | 2.9739 | 4.3533 | 14.3667 | 3.3002 | 4.3533 | 0.8872%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 454 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 92.4716 | 7.8956 | 11.7118 | 92.4716 | 7.8956 | 11.7118 | 102.6173 | 8.7619 | 11.7118 | 0.9569%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 208 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 13.6213 | 3.6174 | 3.7655 | 13.6213 | 3.6174 | 3.7655 | 15.1158 | 4.0143 | 3.7655 | 0.8473%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 235 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 29.3039 | 4.0869 | 7.1702 | 29.3039 | 4.0869 | 7.1702 | 32.5191 | 4.5353 | 7.1702 | 0.8754%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 381 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 35.4517 | 6.626 | 5.3504 | 35.4517 | 6.626 | 5.3504 | 39.3413 | 7.353 | 5.3504 | 0.8812%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.9618 | 0.48695 | 24.5645 | 11.9618 | 0.48695 | 24.5645 | 13.2742 | 0.54038 | 24.5645 | 0.9724%
2027 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.16597 | 0 | 0 | 0.16597 | 0 | 0.15103 | 0.12174 | 1.2406 | 0.15103 | 0.12174 | 1.2406 | 0.1676 | 0.1351 | 1.2406 | 0.9941%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 27 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.7378 | 0.46956 | 22.8677 | 10.7378 | 0.46956 | 22.8677 | 11.9159 | 0.52108 | 22.8677 | 0.9739%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 154 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 21.8479 | 2.6782 | 8.1575 | 21.8479 | 2.6782 | 8.1575 | 24.245 | 2.9721 | 8.1575 | 0.9191%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 269 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.7439 | 4.6782 | 2.2966 | 10.7439 | 4.6782 | 2.2966 | 11.9227 | 5.1915 | 2.2966 | 0.557%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 267 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.6094 | 4.6434 | 0.77732 | 3.6094 | 4.6434 | 0.77732 | 4.0054 | 5.1529 | 0.77732 | 0.7618%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 191 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.5415 | 3.3217 | 1.3672 | 4.5415 | 3.3217 | 1.3672 | 5.0398 | 3.6862 | 1.3672 | 0.7912%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 744 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 75.9584 | 12.939 | 5.8705 | 75.9584 | 12.939 | 5.8705 | 84.2924 | 14.3587 | 5.8705 | 0.9168%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 525 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 47.9898 | 9.1304 | 5.2561 | 47.9898 | 9.1304 | 5.2561 | 53.2551 | 10.1321 | 5.2561 | 0.9343%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 964 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 55.4184 | 16.7651 | 3.3056 | 55.4184 | 16.7651 | 3.3056 | 61.4988 | 18.6045 | 3.3056 | 0.9049%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 62 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 13.1969 | 1.0783 | 12.2391 | 13.1969 | 1.0783 | 12.2391 | 14.6448 | 1.1966 | 12.2391 | 0.9697%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 36 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.5023 | 0.62608 | 8.7884 | 5.5023 | 0.62608 | 8.7884 | 6.106 | 0.69478 | 8.7884 | 0.967%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 197 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 47.2842 | 3.4261 | 13.8013 | 47.2842 | 3.4261 | 13.8013 | 52.4721 | 3.802 | 13.8013 | 0.9877%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 250 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 20.1718 | 4.3478 | 4.6395 | 20.1718 | 4.3478 | 4.6395 | 22.385 | 4.8248 | 4.6395 | 0.9555%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 78 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.6222 | 1.3565 | 1.933 | 2.6222 | 1.3565 | 1.933 | 2.9098 | 1.5053 | 1.933 | 0.9711%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 633 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 74.7143 | 11.0086 | 6.7869 | 74.7143 | 11.0086 | 6.7869 | 82.9117 | 12.2165 | 6.7869 | 0.9923%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 138 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.6876 | 2.4 | 2.7865 | 6.6876 | 2.4 | 2.7865 | 7.4213 | 2.6633 | 2.7865 | 0.9277%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 158 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.8144 | 2.7478 | 3.5717 | 9.8144 | 2.7478 | 3.5717 | 10.8912 | 3.0493 | 3.5717 | 0.9525%
2027 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 7 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 1.7471 | 0 | 0 | 1.7471 | 0 | 1.5898 | 0.12174 | 13.0591 | 1.5898 | 0.12174 | 13.0591 | 1.7642 | 0.1351 | 13.0591 | 0.3253%
2027 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 26 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.2474 | 0.45217 | 2.7588 | 1.2474 | 0.45217 | 2.7588 | 1.3843 | 0.50178 | 2.7588 | 0.999%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 3 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 6.2494 | 0 | 0 | 6.2494 | 0 | 5.6869 | 0.052174 | 108.9992 | 5.6869 | 0.052174 | 108.9992 | 6.3108 | 0.057898 | 108.9992 | 0.999%
2027 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.6464 | 0.20869 | 7.889 | 1.6464 | 0.20869 | 7.889 | 1.827 | 0.23159 | 7.889 | 0.9984%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 354 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 25.6788 | 6.1565 | 4.171 | 25.6788 | 6.1565 | 4.171 | 28.4962 | 6.832 | 4.171 | 0.9993%
2027 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 36 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.3453 | 0.62608 | 0.55152 | 0.3453 | 0.62608 | 0.55152 | 0.38318 | 0.69478 | 0.55152 | 0.9723%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 363 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 31.2198 | 6.313 | 4.9453 | 31.2198 | 6.313 | 4.9453 | 34.6452 | 7.0057 | 4.9453 | 0.997%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.77971 | 0.017391 | 44.8336 | 0.77971 | 0.017391 | 44.8336 | 0.86526 | 0.019299 | 44.8336 | 0.9735%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 69 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 12.4192 | 1.2 | 10.3494 | 12.4192 | 1.2 | 10.3494 | 13.7819 | 1.3317 | 10.3494 | 0.9902%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 415 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 47.1097 | 7.2173 | 6.5273 | 47.1097 | 7.2173 | 6.5273 | 52.2785 | 8.0092 | 6.5273 | 0.9833%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 887 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 151.376 | 15.426 | 9.8131 | 151.376 | 15.426 | 9.8131 | 167.9846 | 17.1185 | 9.8131 | 0.9937%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 127 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 36.7559 | 2.2087 | 16.6416 | 36.7559 | 2.2087 | 16.6416 | 40.7887 | 2.451 | 16.6416 | 0.9496%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 58 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.5736 | 1.0087 | 1.5601 | 1.5736 | 1.0087 | 1.5601 | 1.7463 | 1.1194 | 1.5601 | 0.216%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 163 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.8503 | 2.8348 | 0.65272 | 1.8503 | 2.8348 | 0.65272 | 2.0533 | 3.1458 | 0.65272 | 0.9963%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 78 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.6436 | 1.3565 | 4.8976 | 6.6436 | 1.3565 | 4.8976 | 7.3725 | 1.5053 | 4.8976 | 0.9951%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 1241 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 26.387 | 21.5825 | 1.2226 | 26.387 | 21.5825 | 1.2226 | 29.2822 | 23.9504 | 1.2226 | 0.9734%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 524 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 13.1838 | 9.113 | 1.4467 | 13.1838 | 9.113 | 1.4467 | 14.6303 | 10.1128 | 1.4467 | 0.9797%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 1235 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 23.2262 | 21.4781 | 1.0814 | 23.2262 | 21.4781 | 1.0814 | 25.7745 | 23.8346 | 1.0814 | 0.9676%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 1467 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 28.8046 | 25.5129 | 1.129 | 28.8046 | 25.5129 | 1.129 | 31.965 | 28.3121 | 1.129 | 0.9272%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 521 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 14.6037 | 9.0608 | 1.6117 | 14.6037 | 9.0608 | 1.6117 | 16.206 | 10.0549 | 1.6117 | 0.9829%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 969 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 59.5224 | 16.8521 | 3.5321 | 59.5224 | 16.8521 | 3.5321 | 66.053 | 18.701 | 3.5321 | 0.9672%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 556 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.2665 | 9.6695 | 0.54465 | 5.2665 | 9.6695 | 0.54465 | 5.8443 | 10.7304 | 0.54465 | 0.7734%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 511 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 18.3018 | 8.8869 | 2.0594 | 18.3018 | 8.8869 | 2.0594 | 20.3098 | 9.8619 | 2.0594 | 0.9648%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 171 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.7563 | 2.9739 | 0.59058 | 1.7563 | 2.9739 | 0.59058 | 1.949 | 3.3002 | 0.59058 | 0.7472%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 1723 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 43.8849 | 29.965 | 1.4645 | 43.8849 | 29.965 | 1.4645 | 48.6999 | 33.2527 | 1.4645 | 0.9649%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 616 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 18.1542 | 10.713 | 1.6946 | 18.1542 | 10.713 | 1.6946 | 20.1461 | 11.8884 | 1.6946 | 0.9757%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 944 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 99.8685 | 16.4173 | 6.0831 | 99.8685 | 16.4173 | 6.0831 | 110.8258 | 18.2185 | 6.0831 | 0.9669%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 417 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.5913 | 7.2521 | 0.90888 | 6.5913 | 7.2521 | 0.90888 | 7.3145 | 8.0478 | 0.90888 | 0.8931%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 1063 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 75.4437 | 18.4868 | 4.0809 | 75.4437 | 18.4868 | 4.0809 | 83.7212 | 20.5152 | 4.0809 | 0.9779%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 830 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 78.7812 | 14.4347 | 5.4578 | 78.7812 | 14.4347 | 5.4578 | 87.4249 | 16.0184 | 5.4578 | 0.9936%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 820 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 50.5044 | 14.2608 | 3.5415 | 50.5044 | 14.2608 | 3.5415 | 56.0457 | 15.8254 | 3.5415 | 0.9878%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 582 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 110.706 | 10.1217 | 10.9375 | 110.706 | 10.1217 | 10.9375 | 122.8524 | 11.2322 | 10.9375 | 0.9938%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 1580 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 81.2357 | 27.4781 | 2.9564 | 81.2357 | 27.4781 | 2.9564 | 90.1487 | 30.4929 | 2.9564 | 0.9905%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 100 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.44129 | 1.7391 | 0.25374 | 0.44129 | 1.7391 | 0.25374 | 0.4897 | 1.9299 | 0.25374 | 0.4302%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 89 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.23982 | 1.5478 | 0.15494 | 0.23982 | 1.5478 | 0.15494 | 0.26614 | 1.7176 | 0.15494 | 0.2253%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1782 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 49.4954 | 30.9911 | 1.5971 | 49.4954 | 30.9911 | 1.5971 | 54.926 | 34.3914 | 1.5971 | 0.9644%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 214 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.32484 | 3.7217 | 0.087283 | 0.32484 | 3.7217 | 0.087283 | 0.36048 | 4.1301 | 0.087283 | 0.117%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 525 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 49.6477 | 9.1304 | 5.4376 | 49.6477 | 9.1304 | 5.4376 | 55.0949 | 10.1321 | 5.4376 | 0.9978%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 928 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 102.7516 | 16.139 | 6.3667 | 102.7516 | 16.139 | 6.3667 | 114.0253 | 17.9098 | 6.3667 | 0.9977%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 622 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 123.504 | 10.8173 | 11.4172 | 123.504 | 10.8173 | 11.4172 | 137.0546 | 12.0042 | 11.4172 | 0.9899%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 500 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 78.6546 | 8.6956 | 9.0453 | 78.6546 | 8.6956 | 9.0453 | 87.2844 | 9.6497 | 9.0453 | 0.982%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 1778 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 363.8583 | 30.9215 | 11.7671 | 363.8583 | 30.9215 | 11.7671 | 403.78 | 34.3142 | 11.7671 | 0.9903%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 86 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 5.1395 | 1.4956 | 3.4363 | 5.1395 | 1.4956 | 3.4363 | 5.7034 | 1.6597 | 3.4363 | 0.6775%
2027 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 30 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.3895 | 0.52174 | 2.6632 | 1.3895 | 0.52174 | 2.6632 | 1.5419 | 0.57898 | 2.6632 | 0.9944%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 33 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.5576 | 0.57391 | 7.9414 | 4.5576 | 0.57391 | 7.9414 | 5.0577 | 0.63688 | 7.9414 | 0.9632%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 37 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.44715 | 0.64347 | 0.6949 | 0.44715 | 0.64347 | 0.6949 | 0.49621 | 0.71407 | 0.6949 | 0.9941%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 1675 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 163.2404 | 29.1302 | 5.6038 | 163.2404 | 29.1302 | 5.6038 | 181.1508 | 32.3263 | 5.6038 | 0.9555%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 2456 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 232.8474 | 42.7128 | 5.4515 | 232.8474 | 42.7128 | 5.4515 | 258.3948 | 47.3991 | 5.4515 | 0.994%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 612 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 22.2363 | 10.6434 | 2.0892 | 22.2363 | 10.6434 | 2.0892 | 24.676 | 11.8112 | 2.0892 | 0.936%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 1200 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 35.6813 | 20.8694 | 1.7097 | 35.6813 | 20.8694 | 1.7097 | 39.5962 | 23.1592 | 1.7097 | 0.938%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 229 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.9369 | 3.9826 | 1.2396 | 4.9369 | 3.9826 | 1.2396 | 5.4786 | 4.4195 | 1.2396 | 0.8718%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 341 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.7454 | 5.9304 | 2.3178 | 13.7454 | 5.9304 | 2.3178 | 15.2535 | 6.5811 | 2.3178 | 0.9279%
2027 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 24 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 2.66 | 0 | 0 | 2.66 | 0 | 2.4205 | 0.41739 | 5.7992 | 2.4205 | 0.41739 | 5.7992 | 2.6861 | 0.46318 | 5.7992 | 0.8123%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 264 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 54.9037 | 4.5913 | 11.9583 | 54.9037 | 4.5913 | 11.9583 | 60.9276 | 5.095 | 11.9583 | 0.9729%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 753 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 137.5579 | 13.0956 | 10.5042 | 137.5579 | 13.0956 | 10.5042 | 152.6504 | 14.5324 | 10.5042 | 0.9856%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 265 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 21.9808 | 4.6087 | 4.7695 | 21.9808 | 4.6087 | 4.7695 | 24.3925 | 5.1143 | 4.7695 | 0.9864%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 248 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 51.3459 | 4.313 | 11.9049 | 51.3459 | 4.313 | 11.9049 | 56.9795 | 4.7862 | 11.9049 | 0.9841%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 528 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 94.7516 | 9.1825 | 10.3187 | 94.7516 | 9.1825 | 10.3187 | 105.1476 | 10.19 | 10.3187 | 0.9831%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 469 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 83.1913 | 8.1565 | 10.1994 | 83.1913 | 8.1565 | 10.1994 | 92.3189 | 9.0514 | 10.1994 | 0.9843%
2027 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 16 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.16088 | 0.27826 | 0.57816 | 0.16088 | 0.27826 | 0.57816 | 0.17853 | 0.30879 | 0.57816 | 0.9934%
2027 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 1 | 100% | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.017391 | 0 | 0 | 0.017391 | 0 | 0 | 0.019299 | 0 | 0%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 392 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 28.4668 | 6.8173 | 4.1756 | 28.4668 | 6.8173 | 4.1756 | 31.5901 | 7.5653 | 4.1756 | 0.9977%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 230 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 15.48 | 4 | 3.87 | 15.48 | 4 | 3.87 | 17.1784 | 4.4388 | 3.87 | 0.9957%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 98 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 17.6067 | 1.7043 | 10.3305 | 17.6067 | 1.7043 | 10.3305 | 19.5385 | 1.8913 | 10.3305 | 0.9986%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 843 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.9656 | 14.6608 | 1.3618 | 19.9656 | 14.6608 | 1.3618 | 22.1561 | 16.2693 | 1.3618 | 0.9923%
2027 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 39 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 0.41445 | 0 | 0 | 0.41445 | 0 | 0.37715 | 0.67826 | 0.55605 | 0.37715 | 0.67826 | 0.55605 | 0.41852 | 0.75267 | 0.55605 | 0.9749%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 493 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 130.2838 | 8.5739 | 15.1955 | 130.2838 | 8.5739 | 15.1955 | 144.5782 | 9.5146 | 15.1955 | 0.9856%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 33 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 65.2205 | 0.57391 | 113.6425 | 65.2205 | 0.57391 | 113.6425 | 72.3764 | 0.63688 | 113.6425 | 0.9951%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 580 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 78.3924 | 10.0869 | 7.7717 | 78.3924 | 10.0869 | 7.7717 | 86.9934 | 11.1936 | 7.7717 | 0.9433%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 18 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 2.9372 | 0.31304 | 9.3829 | 2.9372 | 0.31304 | 9.3829 | 3.2595 | 0.34739 | 9.3829 | 0.9958%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 101 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 28.2206 | 1.7565 | 16.0663 | 28.2206 | 1.7565 | 16.0663 | 31.317 | 1.9492 | 16.0663 | 0.9258%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 484 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 111.2949 | 8.4173 | 13.2221 | 111.2949 | 8.4173 | 13.2221 | 123.5059 | 9.3409 | 13.2221 | 0.9926%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 773 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 18.5106 | 13.4434 | 1.3769 | 18.5106 | 13.4434 | 1.3769 | 20.5416 | 14.9184 | 1.3769 | 0.9747%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 543 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 10.3713 | 9.4434 | 1.0983 | 10.3713 | 9.4434 | 1.0983 | 11.5092 | 10.4795 | 1.0983 | 0.7093%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 371 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 86.8821 | 6.4521 | 13.4656 | 86.8821 | 6.4521 | 13.4656 | 96.4146 | 7.16 | 13.4656 | 0.9829%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 414 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 166.0282 | 7.2 | 23.0596 | 166.0282 | 7.2 | 23.0596 | 184.2444 | 7.9899 | 23.0596 | 0.989%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 54 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 23.1929 | 0.93912 | 24.6963 | 23.1929 | 0.93912 | 24.6963 | 25.7375 | 1.0422 | 24.6963 | 0.9937%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 446 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 48.5255 | 7.7565 | 6.2561 | 48.5255 | 7.7565 | 6.2561 | 53.8496 | 8.6075 | 6.2561 | 0.9631%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 868 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 166.0224 | 15.0956 | 10.9981 | 166.0224 | 15.0956 | 10.9981 | 184.2379 | 16.7518 | 10.9981 | 0.9714%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 82 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 26.8212 | 1.4261 | 18.8077 | 26.8212 | 1.4261 | 18.8077 | 29.764 | 1.5825 | 18.8077 | 0.9712%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 410 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 180.4018 | 7.1304 | 25.3004 | 180.4018 | 7.1304 | 25.3004 | 200.1951 | 7.9127 | 25.3004 | 0.9923%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 23 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.1511 | 0.4 | 2.8777 | 1.1511 | 0.4 | 2.8777 | 1.2774 | 0.44388 | 2.8777 | 0.9928%
2027 | 834 | 834-887AE | Tier-2 | Tier-2---17 | Tier-2---13 | 2 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 0.69393 | 0 | 0 | 0.69393 | 0 | 0.63147 | 0.034782 | 18.1548 | 0.63147 | 0.034782 | 18.1548 | 0.70075 | 0.038599 | 18.1548 | 0.9864%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 59 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.11165 | 1.0261 | 0.10881 | 0.11165 | 1.0261 | 0.10881 | 0.1239 | 1.1387 | 0.10881 | 0.9883%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 131 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.2688 | 2.2782 | 0.55694 | 1.2688 | 2.2782 | 0.55694 | 1.4081 | 2.5282 | 0.55694 | 0.9963%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 8 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.060511 | 0.13913 | 0.43493 | 0.060511 | 0.13913 | 0.43493 | 0.06715 | 0.15439 | 0.43493 | 0.9902%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 15 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.9878 | 0.26087 | 11.4533 | 2.9878 | 0.26087 | 11.4533 | 3.3156 | 0.28949 | 11.4533 | 0.9939%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 231 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 2.0456 | 4.0174 | 0.50919 | 2.0456 | 4.0174 | 0.50919 | 2.27 | 4.4581 | 0.50919 | 0.9666%
2027 | 858 | 858-14 | Tier-2 | Tier-2---12 | Tier-2---7 | 10 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 4.0968 | 0 | 0 | 4.0968 | 0 | 3.728 | 0.17391 | 21.4364 | 3.728 | 0.17391 | 21.4364 | 4.1371 | 0.19299 | 21.4364 | 0.9951%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 856 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 78.2117 | 14.8869 | 5.2537 | 78.2117 | 14.8869 | 5.2537 | 86.793 | 16.5202 | 5.2537 | 0.9986%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 438 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 74.9698 | 7.6173 | 9.842 | 74.9698 | 7.6173 | 9.842 | 83.1953 | 8.4531 | 9.842 | 0.9762%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 4 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.3096 | 0.069565 | 33.2011 | 2.3096 | 0.069565 | 33.2011 | 2.563 | 0.077197 | 33.2011 | 0.9867%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 703 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 82.5872 | 12.226 | 6.755 | 82.5872 | 12.226 | 6.755 | 91.6485 | 13.5674 | 6.755 | 0.9973%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 1553 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 244.3147 | 27.0085 | 9.0458 | 244.3147 | 27.0085 | 9.0458 | 271.1204 | 29.9718 | 9.0458 | 0.9919%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 110 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 57.7563 | 1.913 | 30.191 | 57.7563 | 1.913 | 30.191 | 64.0932 | 2.1229 | 30.191 | 0.9998%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 1316 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 141.0713 | 22.8868 | 6.1639 | 141.0713 | 22.8868 | 6.1639 | 156.5494 | 25.3979 | 6.1639 | 0.9833%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 759 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 105.7677 | 13.1999 | 8.0128 | 105.7677 | 13.1999 | 8.0128 | 117.3723 | 14.6482 | 8.0128 | 0.988%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 1095 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 48.7918 | 19.0434 | 2.5621 | 48.7918 | 19.0434 | 2.5621 | 54.1451 | 21.1327 | 2.5621 | 0.9625%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 563 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 12.2496 | 9.7912 | 1.2511 | 12.2496 | 9.7912 | 1.2511 | 13.5936 | 10.8655 | 1.2511 | 0.9181%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 319 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 71.2405 | 5.5478 | 12.8412 | 71.2405 | 5.5478 | 12.8412 | 79.0568 | 6.1565 | 12.8412 | 0.9835%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 1307 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 371.2832 | 22.7303 | 16.3343 | 371.2832 | 22.7303 | 16.3343 | 412.0195 | 25.2242 | 16.3343 | 0.9889%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 559 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 30.5007 | 9.7217 | 3.1374 | 30.5007 | 9.7217 | 3.1374 | 33.8472 | 10.7883 | 3.1374 | 0.9191%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 876 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 203.4497 | 15.2347 | 13.3544 | 203.4497 | 15.2347 | 13.3544 | 225.7718 | 16.9062 | 13.3544 | 0.9908%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3753 | 0.15652 | 8.7864 | 1.3753 | 0.15652 | 8.7864 | 1.5261 | 0.17369 | 8.7864 | 0.9858%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 221 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.4441 | 3.8435 | 1.9368 | 7.4441 | 3.8435 | 1.9368 | 8.2609 | 4.2651 | 1.9368 | 0.9652%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 1430 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 499.1345 | 24.8694 | 20.0702 | 499.1345 | 24.8694 | 20.0702 | 553.8984 | 27.598 | 20.0702 | 0.9927%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 10 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 51.8797 | 0.17391 | 298.3103 | 51.8797 | 0.17391 | 298.3103 | 57.5718 | 0.19299 | 298.3103 | 0.9997%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 988 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 291.8804 | 17.1825 | 16.9871 | 291.8804 | 17.1825 | 16.9871 | 323.9049 | 19.0677 | 16.9871 | 0.9926%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 319 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 11.3192 | 5.5478 | 2.0403 | 11.3192 | 5.5478 | 2.0403 | 12.5611 | 6.1565 | 2.0403 | 0.9598%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 310 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 30.7953 | 5.3913 | 5.7121 | 30.7953 | 5.3913 | 5.7121 | 34.1741 | 5.9828 | 5.7121 | 0.9934%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 87 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.7625 | 1.513 | 6.4523 | 9.7625 | 1.513 | 6.4523 | 10.8336 | 1.679 | 6.4523 | 0.6902%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 126 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.8843 | 2.1913 | 6.3361 | 13.8843 | 2.1913 | 6.3361 | 15.4077 | 2.4317 | 6.3361 | 0.7661%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 53 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.9364 | 0.92173 | 4.2707 | 3.9364 | 0.92173 | 4.2707 | 4.3683 | 1.0229 | 4.2707 | 0.9947%
2027 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 42 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.55108 | 0.73043 | 0.75446 | 0.55108 | 0.73043 | 0.75446 | 0.61155 | 0.81057 | 0.75446 | 0.9691%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 70 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 117.5454 | 1.2174 | 96.5558 | 117.5454 | 1.2174 | 96.5558 | 130.4422 | 1.351 | 96.5558 | 0.9966%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 945 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 136.5462 | 16.4347 | 8.3084 | 136.5462 | 16.4347 | 8.3084 | 151.5277 | 18.2378 | 8.3084 | 0.9905%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 1604 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 256.3868 | 27.8955 | 9.191 | 256.3868 | 27.8955 | 9.191 | 284.5169 | 30.9561 | 9.191 | 0.9891%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 200 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 72.5488 | 3.4782 | 20.8579 | 72.5488 | 3.4782 | 20.8579 | 80.5087 | 3.8599 | 20.8579 | 0.9946%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 118 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 39.4065 | 2.0522 | 19.2024 | 39.4065 | 2.0522 | 19.2024 | 43.7301 | 2.2773 | 19.2024 | 0.9952%
2027 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 11 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 1.9177 | 0 | 0 | 1.9177 | 0 | 1.7451 | 0.1913 | 9.1223 | 1.7451 | 0.1913 | 9.1223 | 1.9366 | 0.21229 | 9.1223 | 0.9994%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 427 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 132.3028 | 7.426 | 17.8161 | 132.3028 | 7.426 | 17.8161 | 146.8188 | 8.2408 | 17.8161 | 0.9843%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 1117 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 101.4885 | 19.426 | 5.2244 | 101.4885 | 19.426 | 5.2244 | 112.6235 | 21.5573 | 5.2244 | 0.9898%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 361 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 71.9042 | 6.2782 | 11.453 | 71.9042 | 6.2782 | 11.453 | 79.7933 | 6.9671 | 11.453 | 0.9853%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 1464 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 209.5961 | 25.4607 | 8.2321 | 209.5961 | 25.4607 | 8.2321 | 232.5925 | 28.2542 | 8.2321 | 0.9839%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 958 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 203.259 | 16.6608 | 12.1999 | 203.259 | 16.6608 | 12.1999 | 225.5601 | 18.4887 | 12.1999 | 0.9748%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 360 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 82.5252 | 6.2608 | 13.1812 | 82.5252 | 6.2608 | 13.1812 | 91.5797 | 6.9478 | 13.1812 | 0.9912%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 249 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 45.8566 | 4.3304 | 10.5894 | 45.8566 | 4.3304 | 10.5894 | 50.8879 | 4.8055 | 10.5894 | 0.9732%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 144 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 78.0753 | 2.5043 | 31.1761 | 78.0753 | 2.5043 | 31.1761 | 86.6415 | 2.7791 | 31.1761 | 0.9953%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 198 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 58.178 | 3.4435 | 16.8952 | 58.178 | 3.4435 | 16.8952 | 64.5612 | 3.8213 | 16.8952 | 0.9803%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 611 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 29.7799 | 10.626 | 2.8025 | 29.7799 | 10.626 | 2.8025 | 33.0473 | 11.7919 | 2.8025 | 0.9369%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 64.3818 | 1.2696 | 50.712 | 64.3818 | 1.2696 | 50.712 | 71.4456 | 1.4088 | 50.712 | 0.9955%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 25 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 46.8889 | 0.43478 | 107.8452 | 46.8889 | 0.43478 | 107.8452 | 52.0335 | 0.48248 | 107.8452 | 0.803%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 189 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.7574 | 3.2869 | 1.1431 | 3.7574 | 3.2869 | 1.1431 | 4.1696 | 3.6476 | 1.1431 | 0.6587%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 392 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 41.5562 | 6.8173 | 6.0957 | 41.5562 | 6.8173 | 6.0957 | 46.1156 | 7.5653 | 6.0957 | 0.9978%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 184 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 30.2704 | 3.2 | 9.4596 | 30.2704 | 3.2 | 9.4596 | 33.5916 | 3.5511 | 9.4596 | 0.9981%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 149 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.8231 | 2.5913 | 4.9485 | 12.8231 | 2.5913 | 4.9485 | 14.23 | 2.8756 | 4.9485 | 0.9962%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 10.2838 | 0.71304 | 14.4225 | 10.2838 | 0.71304 | 14.4225 | 11.4121 | 0.79127 | 14.4225 | 0.9972%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 242 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 5.1761 | 4.2087 | 1.2299 | 5.1761 | 4.2087 | 1.2299 | 5.7441 | 4.6704 | 1.2299 | 0.3454%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 5.2241 | 4.1913 | 1.2464 | 5.2241 | 4.1913 | 1.2464 | 5.7973 | 4.6511 | 1.2464 | 0.75%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 13 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.66137 | 0.22609 | 2.9253 | 0.66137 | 0.22609 | 2.9253 | 0.73393 | 0.25089 | 2.9253 | 0.9665%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 1271 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 48.4098 | 22.1042 | 2.1901 | 48.4098 | 22.1042 | 2.1901 | 53.7212 | 24.5294 | 2.1901 | 0.8429%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 2262 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 59.9246 | 39.3389 | 1.5233 | 59.9246 | 39.3389 | 1.5233 | 66.4994 | 43.655 | 1.5233 | 0.9909%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 367 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 13.0561 | 6.3826 | 2.0456 | 13.0561 | 6.3826 | 2.0456 | 14.4885 | 7.0828 | 2.0456 | 0.9975%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 15 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.98124 | 0.26087 | 3.7614 | 0.98124 | 0.26087 | 3.7614 | 1.0889 | 0.28949 | 3.7614 | 0.9975%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 74 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 37.0598 | 1.2869 | 28.7966 | 37.0598 | 1.2869 | 28.7966 | 41.1259 | 1.4281 | 28.7966 | 0.9993%
2027 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 14 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.35763 | 0.24348 | 1.4689 | 0.35763 | 0.24348 | 1.4689 | 0.39687 | 0.27019 | 1.4689 | 0.9408%
2027 | 1446 | CB 1446 | Tier-1 | Non-HFTD---17 | Non-HFTD---24 | 13 | 100% | 1.7782 | 79.62% | 0% | 20.38% | 0.014159 | 0 | 0 | 0.014159 | 0 | 0.012885 | 0.22609 | 0.05699 | 0.012885 | 0.22609 | 0.05699 | 0.014298 | 0.25089 | 0.05699 | 0.7962%
2027 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | Non-HFTD---22 | 26 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.037296 | 0 | 0 | 0.037296 | 0 | 0.033939 | 0.45217 | 0.075057 | 0.033939 | 0.45217 | 0.075057 | 0.037662 | 0.50178 | 0.075057 | 0.8877%
2027 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 24 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.83874 | 0.41739 | 2.0095 | 0.83874 | 0.41739 | 2.0095 | 0.93076 | 0.46318 | 2.0095 | 0.3549%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 2.8867 | 0.086956 | 33.197 | 2.8867 | 0.086956 | 33.197 | 3.2034 | 0.096497 | 33.197 | 0.7993%
2027 | 196 | CB 196 | Tier-2 | Tier-2---15 | Tier-2---9 | 14 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.042252 | 0 | 0 | 0.042252 | 0 | 0.038449 | 0.24348 | 0.15792 | 0.038449 | 0.24348 | 0.15792 | 0.042667 | 0.27019 | 0.15792 | 0.03142%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 168 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.6527 | 2.9217 | 1.2502 | 3.6527 | 2.9217 | 1.2502 | 4.0535 | 3.2423 | 1.2502 | 0.299%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 321 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.1598 | 5.5826 | 0.20775 | 1.1598 | 5.5826 | 0.20775 | 1.287 | 6.1951 | 0.20775 | 0.9512%
2027 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 554 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.17071 | 9.6347 | 0.017718 | 0.17071 | 9.6347 | 0.017718 | 0.18944 | 10.6918 | 0.017718 | 0.09583%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 463 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.7926 | 8.0521 | 0.96777 | 7.7926 | 8.0521 | 0.96777 | 8.6476 | 8.9356 | 0.96777 | 0.8082%
2027 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 8 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 1.3377 | 0 | 0 | 1.3377 | 0 | 1.2173 | 0.13913 | 8.7494 | 1.2173 | 0.13913 | 8.7494 | 1.3509 | 0.15439 | 8.7494 | 0.9989%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 77 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.9331 | 1.3391 | 1.4435 | 1.9331 | 1.3391 | 1.4435 | 2.1452 | 1.486 | 1.4435 | 0.9981%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 688 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 22.587 | 11.9651 | 1.8877 | 22.587 | 11.9651 | 1.8877 | 25.0652 | 13.2779 | 1.8877 | 0.9929%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 605 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 14.5549 | 10.5217 | 1.3833 | 14.5549 | 10.5217 | 1.3833 | 16.1519 | 11.6761 | 1.3833 | 0.9737%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 1834 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 37.0873 | 31.8954 | 1.1628 | 37.0873 | 31.8954 | 1.1628 | 41.1564 | 35.3949 | 1.1628 | 0.9874%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 1006 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 29.646 | 17.4955 | 1.6945 | 29.646 | 17.4955 | 1.6945 | 32.8986 | 19.4151 | 1.6945 | 0.9888%
2027 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 678 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 112.9166 | 11.7912 | 9.5763 | 112.9166 | 11.7912 | 9.5763 | 125.3055 | 13.0849 | 9.5763 | 0.9762%
2027 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 34 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 19.127 | 0.5913 | 32.3474 | 19.127 | 0.5913 | 32.3474 | 21.2256 | 0.65618 | 32.3474 | 0.9954%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 241 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 11.2264 | 4.1913 | 2.6785 | 11.2264 | 4.1913 | 2.6785 | 12.4582 | 4.6511 | 2.6785 | 0.9768%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 55 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.3827 | 0.95652 | 2.491 | 2.3827 | 0.95652 | 2.491 | 2.6441 | 1.0615 | 2.491 | 0.6436%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 1.0086 | 0.34782 | 2.8999 | 1.0086 | 0.34782 | 2.8999 | 1.1193 | 0.38599 | 2.8999 | 0.375%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 577 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.7811 | 10.0347 | 1.174 | 11.7811 | 10.0347 | 1.174 | 13.0737 | 11.1357 | 1.174 | 0.9%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 119 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.4286 | 2.0696 | 1.1735 | 2.4286 | 2.0696 | 1.1735 | 2.695 | 2.2966 | 1.1735 | 0.7028%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 276 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.7118 | 4.8 | 1.815 | 8.7118 | 4.8 | 1.815 | 9.6676 | 5.3266 | 1.815 | 0.995%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 167 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 7.3021 | 2.9043 | 2.5142 | 7.3021 | 2.9043 | 2.5142 | 8.1033 | 3.223 | 2.5142 | 0.9704%
2027 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 8 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 0.50007 | 0 | 0 | 0.50007 | 0 | 0.45506 | 0.13913 | 3.2707 | 0.45506 | 0.13913 | 3.2707 | 0.50498 | 0.15439 | 3.2707 | 0.1609%
2027 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 385 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.57264 | 6.6956 | 0.085525 | 0.57264 | 6.6956 | 0.085525 | 0.63547 | 7.4302 | 0.085525 | 0.6647%
2027 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 151 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.09533 | 2.6261 | 0.036301 | 0.09533 | 2.6261 | 0.036301 | 0.10579 | 2.9142 | 0.036301 | 0.9726%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 13.2284 | 0.38261 | 34.5744 | 13.2284 | 0.38261 | 34.5744 | 14.6798 | 0.42458 | 34.5744 | 0.9979%
2027 | 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 37 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.8969 | 0.64347 | 2.948 | 1.8969 | 0.64347 | 2.948 | 2.1051 | 0.71407 | 2.948 | 0.9683%
2027 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 228 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.37712 | 3.9652 | 0.095108 | 0.37712 | 3.9652 | 0.095108 | 0.4185 | 4.4002 | 0.095108 | 0.3335%
2027 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 3 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.3623 | 0.052174 | 45.2768 | 2.3623 | 0.052174 | 45.2768 | 2.6214 | 0.057898 | 45.2768 | 0.9938%
2027 | 350 | CB 350 | Tier-2 | Tier-2---15 | Tier-2---11 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 1.3347 | 0 | 0 | 1.3347 | 0 | 1.2146 | 0.017391 | 69.8371 | 1.2146 | 0.017391 | 69.8371 | 1.3478 | 0.019299 | 69.8371 | 0.9992%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 542 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 132.4063 | 9.426 | 14.0469 | 132.4063 | 9.426 | 14.0469 | 146.9336 | 10.4602 | 14.0469 | 0.9966%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 27 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.79342 | 0.46956 | 1.6897 | 0.79342 | 0.46956 | 1.6897 | 0.88048 | 0.52108 | 1.6897 | 0.9922%
2027 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 2 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.068099 | 0.034782 | 1.9579 | 0.068099 | 0.034782 | 1.9579 | 0.075571 | 0.038599 | 1.9579 | 0.986%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 836 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 101.5275 | 14.539 | 6.9831 | 101.5275 | 14.539 | 6.9831 | 112.6669 | 16.1342 | 6.9831 | 0.9884%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.061378 | 0.086956 | 0.70585 | 0.061378 | 0.086956 | 0.70585 | 0.068112 | 0.096497 | 0.70585 | 0.991%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 372 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 53.3875 | 6.4695 | 8.2522 | 53.3875 | 6.4695 | 8.2522 | 59.2451 | 7.1793 | 8.2522 | 0.9601%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 35 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4798 | 0.60869 | 2.4311 | 1.4798 | 0.60869 | 2.4311 | 1.6422 | 0.67548 | 2.4311 | 0.1888%
2027 | 381 | CB 381 | Tier-1 | Non-HFTD---5 | Non-HFTD---17 | 10 | 100% | 47.7165 | 98.4% | 0% | 1.604% | 0.46951 | 0 | 0 | 0.46951 | 0 | 0.42725 | 0.17391 | 2.4567 | 0.42725 | 0.17391 | 2.4567 | 0.47413 | 0.19299 | 2.4567 | 0.984%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 3 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.87422 | 0.052174 | 16.756 | 0.87422 | 0.052174 | 16.756 | 0.97014 | 0.057898 | 16.756 | 0.1434%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 152 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.7001 | 2.6435 | 3.6695 | 9.7001 | 2.6435 | 3.6695 | 10.7643 | 2.9335 | 3.6695 | 0.9408%
2027 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 9 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 0.65999 | 0 | 0 | 0.65999 | 0 | 0.60058 | 0.15652 | 3.8371 | 0.60058 | 0.15652 | 3.8371 | 0.66647 | 0.17369 | 3.8371 | 0.9829%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 4 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 1.0439 | 0.069565 | 15.0068 | 1.0439 | 0.069565 | 15.0068 | 1.1585 | 0.077197 | 15.0068 | 0.9768%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 183 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 60.146 | 3.1826 | 18.8985 | 60.146 | 3.1826 | 18.8985 | 66.7451 | 3.5318 | 18.8985 | 0.9549%
2027 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.16724 | 0.052174 | 3.2055 | 0.16724 | 0.052174 | 3.2055 | 0.18559 | 0.057898 | 3.2055 | 0.9464%
2027 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 6 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.015734 | 0.10435 | 0.15078 | 0.015734 | 0.10435 | 0.15078 | 0.01746 | 0.1158 | 0.15078 | 0.9786%
2027 | 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 19 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.01877 | 0.33043 | 0.056806 | 0.01877 | 0.33043 | 0.056806 | 0.02083 | 0.36669 | 0.056806 | 0.1679%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 553 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 8.7492 | 9.6173 | 0.90973 | 8.7492 | 9.6173 | 0.90973 | 9.7091 | 10.6725 | 0.90973 | 0.8949%
2027 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 301 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 1.0343 | 5.2347 | 0.19759 | 1.0343 | 5.2347 | 0.19759 | 1.1478 | 5.8091 | 0.19759 | 0.372%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 34 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 4.1282 | 0.5913 | 6.9816 | 4.1282 | 0.5913 | 6.9816 | 4.5811 | 0.65618 | 6.9816 | 0.9425%
2027 | 533 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0035677 | 0 | 0 | 0.0035677 | 0 | 0.0032465 | 0.017391 | 0.18668 | 0.0032465 | 0.017391 | 0.18668 | 0.0036028 | 0.019299 | 0.18668 | 0.03364%
2027 | 534 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 3 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.022693 | 0 | 0 | 0.022693 | 0 | 0.020651 | 0.052174 | 0.3958 | 0.020651 | 0.052174 | 0.3958 | 0.022916 | 0.057898 | 0.3958 | 0.3599%
2027 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 3 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.051127 | 0 | 0 | 0.051127 | 0 | 0.046524 | 0.052174 | 0.89172 | 0.046524 | 0.052174 | 0.89172 | 0.051629 | 0.057898 | 0.89172 | 0.04585%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 51 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.37517 | 0.88695 | 0.42298 | 0.37517 | 0.88695 | 0.42298 | 0.41633 | 0.98426 | 0.42298 | 0.7619%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 189 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.60728 | 3.2869 | 0.18476 | 0.60728 | 3.2869 | 0.18476 | 0.67391 | 3.6476 | 0.18476 | 0.9924%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 54 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 8.2474 | 0.93912 | 8.782 | 8.2474 | 0.93912 | 8.782 | 9.1523 | 1.0422 | 8.782 | 0.9545%
2027 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 26 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.9788 | 0.45217 | 6.5877 | 2.9788 | 0.45217 | 6.5877 | 3.3056 | 0.50178 | 6.5877 | 0.7837%
2027 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 19 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 7.5828 | 0 | 0 | 7.5828 | 0 | 6.9003 | 0.33043 | 20.8825 | 6.9003 | 0.33043 | 20.8825 | 7.6573 | 0.36669 | 20.8825 | 0.6312%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 752 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 39.2661 | 13.0782 | 3.0024 | 39.2661 | 13.0782 | 3.0024 | 43.5742 | 14.5131 | 3.0024 | 0.9981%
2027 | 750 | CB 750 | Tier-1 | Non-HFTD---4 | Non-HFTD---11 | 7 | 100% | 147.1702 | 99.68% | 0% | 0.3223% | 1.467 | 0 | 0 | 1.467 | 0 | 1.3349 | 0.12174 | 10.9654 | 1.3349 | 0.12174 | 10.9654 | 1.4814 | 0.1351 | 10.9654 | 0.9968%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 50 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.46433 | 0.86956 | 0.53398 | 0.46433 | 0.86956 | 0.53398 | 0.51527 | 0.96497 | 0.53398 | 0.9266%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 107 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 74.135 | 1.8609 | 39.8392 | 74.135 | 1.8609 | 39.8392 | 82.2689 | 2.065 | 39.8392 | 0.9507%
2027 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 189 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.38586 | 3.2869 | 0.11739 | 0.38586 | 3.2869 | 0.11739 | 0.42819 | 3.6476 | 0.11739 | 0.9943%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 62 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 24.913 | 1.0783 | 23.105 | 24.913 | 1.0783 | 23.105 | 27.6464 | 1.1966 | 23.105 | 0.9983%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 173 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.8713 | 3.0087 | 0.95434 | 2.8713 | 3.0087 | 0.95434 | 3.1863 | 3.3388 | 0.95434 | 0.9343%
2027 | 911 | CB 911 | Tier-2 | Tier-2---14 | Tier-2---11 | 14 | 100% | 193.6033 | 99.75% | 0% | 0.253% | 1.9311 | 0 | 0 | 1.9311 | 0 | 1.7573 | 0.24348 | 7.2176 | 1.7573 | 0.24348 | 7.2176 | 1.9501 | 0.27019 | 7.2176 | 0.9975%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 42 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 12.0117 | 0.73043 | 16.4447 | 12.0117 | 0.73043 | 16.4447 | 13.3296 | 0.81057 | 16.4447 | 0.7976%
2027 | 955 | CB 955 | Tier-1 | Non-HFTD---9 | Non-HFTD---22 | 60 | 100% | 15.216 | 95.67% | 0% | 4.328% | 0.14557 | 0 | 0 | 0.14557 | 0 | 0.13247 | 1.0435 | 0.12695 | 0.13247 | 1.0435 | 0.12695 | 0.14701 | 1.158 | 0.12695 | 0.9567%
2027 | 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 6 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.2834 | 0.10435 | 21.8823 | 2.2834 | 0.10435 | 21.8823 | 2.5339 | 0.1158 | 21.8823 | 0.9997%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 162 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 103.7418 | 2.8174 | 36.8222 | 103.7418 | 2.8174 | 36.8222 | 115.1241 | 3.1265 | 36.8222 | 0.9951%
2027 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.8118 | 0.86956 | 13.5837 | 11.8118 | 0.86956 | 13.5837 | 13.1078 | 0.96497 | 13.5837 | 0.9951%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 450 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.5186 | 7.826 | 0.44961 | 3.5186 | 7.826 | 0.44961 | 3.9047 | 8.6847 | 0.44961 | 0.997%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 104 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.2038 | 1.8087 | 0.66556 | 1.2038 | 1.8087 | 0.66556 | 1.3359 | 2.0071 | 0.66556 | 0.9965%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.22558 | 0.069565 | 3.2427 | 0.22558 | 0.069565 | 3.2427 | 0.25033 | 0.077197 | 3.2427 | 0.9021%
2027 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 414 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.1647 | 7.2 | 0.16176 | 1.1647 | 7.2 | 0.16176 | 1.2925 | 7.9899 | 0.16176 | 0.3693%
2027 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 320 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 8.8377 | 5.5652 | 1.588 | 8.8377 | 5.5652 | 1.588 | 9.8074 | 6.1758 | 1.588 | 0.9433%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 436 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.6384 | 7.5826 | 1.7986 | 13.6384 | 7.5826 | 1.7986 | 15.1347 | 8.4145 | 1.7986 | 0.9785%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 288 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 45.916 | 5.0087 | 9.1673 | 45.916 | 5.0087 | 9.1673 | 50.9538 | 5.5582 | 9.1673 | 0.9856%
2027 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 5.7493 | 0.33043 | 17.3993 | 5.7493 | 0.33043 | 17.3993 | 6.3801 | 0.36669 | 17.3993 | 0.9902%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 1446 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 62.3027 | 25.1477 | 2.4775 | 62.3027 | 25.1477 | 2.4775 | 69.1384 | 27.9068 | 2.4775 | 0.99%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 1505 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 26.0975 | 26.1737 | 0.99709 | 26.0975 | 26.1737 | 0.99709 | 28.9608 | 29.0455 | 0.99709 | 0.9473%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 474 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 94.0833 | 8.2434 | 11.4131 | 94.0833 | 8.2434 | 11.4131 | 104.4059 | 9.1479 | 11.4131 | 0.9831%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 306 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 46.6933 | 5.3217 | 8.7741 | 46.6933 | 5.3217 | 8.7741 | 51.8164 | 5.9056 | 8.7741 | 0.9811%
2027 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 312 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.7942 | 5.4261 | 1.0679 | 5.7942 | 5.4261 | 1.0679 | 6.4299 | 6.0214 | 1.0679 | 0.695%
2027 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.27042 | 0.069565 | 3.8874 | 0.27042 | 0.069565 | 3.8874 | 0.30009 | 0.077197 | 3.8874 | 0.9988%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 309 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 33.7388 | 5.3739 | 6.2783 | 33.7388 | 5.3739 | 6.2783 | 37.4406 | 5.9635 | 6.2783 | 0.9914%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 1052 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 28.667 | 18.2955 | 1.5669 | 28.667 | 18.2955 | 1.5669 | 31.8123 | 20.3029 | 1.5669 | 0.9371%
2027 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 38 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.017168 | 0.66087 | 0.025978 | 0.017168 | 0.66087 | 0.025978 | 0.019052 | 0.73337 | 0.025978 | 0.02003%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 1615 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.8194 | 28.0868 | 0.52763 | 14.8194 | 28.0868 | 0.52763 | 16.4453 | 31.1684 | 0.52763 | 0.789%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 419 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 32.21 | 7.2869 | 4.4203 | 32.21 | 7.2869 | 4.4203 | 35.744 | 8.0864 | 4.4203 | 0.9517%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 483 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 84.4138 | 8.3999 | 10.0493 | 84.4138 | 8.3999 | 10.0493 | 93.6755 | 9.3216 | 10.0493 | 0.9933%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 1102 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 61.4447 | 19.1651 | 3.2061 | 61.4447 | 19.1651 | 3.2061 | 68.1863 | 21.2678 | 3.2061 | 0.9757%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 440 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 53.7422 | 7.6521 | 7.0232 | 53.7422 | 7.6521 | 7.0232 | 59.6387 | 8.4917 | 7.0232 | 0.9932%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 454 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 34.2446 | 7.8956 | 4.3372 | 34.2446 | 7.8956 | 4.3372 | 38.0018 | 8.7619 | 4.3372 | 0.9948%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0 | 1.0072 | 0.09954 | 10.1183 | 1.0072 | 0.09954 | 10.1183 | 1.1774 | 0.11636 | 10.1183 | 0.9903%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 79 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 4.0558 | 0 | 0 | 4.0558 | 0 | 3.5207 | 1.3106 | 2.6863 | 3.5207 | 1.3106 | 2.6863 | 4.1158 | 1.5321 | 2.6863 | 0.9915%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 1219 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 38.5958 | 0 | 0 | 38.5958 | 0 | 33.5037 | 20.2232 | 1.6567 | 33.5037 | 20.2232 | 1.6567 | 39.1662 | 23.6412 | 1.6567 | 0.9141%
2028 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 20 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 1.1426 | 0 | 0 | 1.1426 | 0 | 0.99181 | 0.3318 | 2.9892 | 0.99181 | 0.3318 | 2.9892 | 1.1594 | 0.38788 | 2.9892 | 0.9976%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 1445 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 348.1151 | 0 | 0 | 348.1151 | 0 | 302.1866 | 23.9726 | 12.6055 | 302.1866 | 23.9726 | 12.6055 | 353.2596 | 28.0242 | 12.6055 | 0.9902%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 194 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 69.2699 | 0 | 0 | 69.2699 | 0 | 60.1308 | 3.2185 | 18.6831 | 60.1308 | 3.2185 | 18.6831 | 70.2936 | 3.7624 | 18.6831 | 0.9818%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 618 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 187.6898 | 0 | 0 | 187.6898 | 0 | 162.927 | 10.2526 | 15.8912 | 162.927 | 10.2526 | 15.8912 | 190.4635 | 11.9854 | 15.8912 | 0.997%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 334 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 50.0947 | 0 | 0 | 50.0947 | 0 | 43.4855 | 5.5411 | 7.8479 | 43.4855 | 5.5411 | 7.8479 | 50.835 | 6.4776 | 7.8479 | 0.9951%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 70 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 13.8079 | 0 | 0 | 13.8079 | 0 | 11.9862 | 1.1613 | 10.3214 | 11.9862 | 1.1613 | 10.3214 | 14.012 | 1.3576 | 10.3214 | 0.9958%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 28 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 7.9118 | 0 | 0 | 7.9118 | 0 | 6.8679 | 0.46452 | 14.785 | 6.8679 | 0.46452 | 14.785 | 8.0287 | 0.54303 | 14.785 | 0.996%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 473 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 97.6353 | 0 | 0 | 97.6353 | 0 | 84.7538 | 7.8471 | 10.8007 | 84.7538 | 7.8471 | 10.8007 | 99.0781 | 9.1733 | 10.8007 | 0.9962%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 18 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 6.8928 | 0 | 0 | 6.8928 | 0 | 5.9834 | 0.29862 | 20.037 | 5.9834 | 0.29862 | 20.037 | 6.9947 | 0.34909 | 20.037 | 0.9922%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 262 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 50.2959 | 0 | 0 | 50.2959 | 0 | 43.6602 | 4.3466 | 10.0447 | 43.6602 | 4.3466 | 10.0447 | 51.0392 | 5.0812 | 10.0447 | 0.9916%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 428 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 28.6805 | 0 | 0 | 28.6805 | 0 | 24.8966 | 7.1005 | 3.5063 | 24.8966 | 7.1005 | 3.5063 | 29.1044 | 8.3006 | 3.5063 | 0.9924%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 1949 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 90.8901 | 0 | 0 | 90.8901 | 0 | 78.8985 | 32.3339 | 2.4401 | 78.8985 | 32.3339 | 2.4401 | 92.2332 | 37.7987 | 2.4401 | 0.9598%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 1169 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 36.7535 | 0 | 0 | 36.7535 | 0 | 31.9045 | 19.3937 | 1.6451 | 31.9045 | 19.3937 | 1.6451 | 37.2967 | 22.6715 | 1.6451 | 0.9739%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 235 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.1336 | 0 | 0 | 5.1336 | 0 | 4.4563 | 3.8987 | 1.143 | 4.4563 | 3.8987 | 1.143 | 5.2095 | 4.5576 | 1.143 | 0.8768%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 100 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 50.3502 | 0 | 0 | 50.3502 | 0 | 43.7073 | 1.659 | 26.3455 | 43.7073 | 1.659 | 26.3455 | 51.0943 | 1.9394 | 26.3455 | 0.9826%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 240 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 116.5034 | 0 | 0 | 116.5034 | 0 | 101.1325 | 3.9816 | 25.3999 | 101.1325 | 3.9816 | 25.3999 | 118.2251 | 4.6545 | 25.3999 | 0.9858%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 288 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 21.3907 | 0 | 0 | 21.3907 | 0 | 18.5685 | 4.7779 | 3.8863 | 18.5685 | 4.7779 | 3.8863 | 21.7068 | 5.5854 | 3.8863 | 0.9945%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 762 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 65.3212 | 0 | 0 | 65.3212 | 0 | 56.703 | 12.6416 | 4.4854 | 56.703 | 12.6416 | 4.4854 | 66.2865 | 14.7782 | 4.4854 | 0.9866%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 1434 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 251.0131 | 0 | 0 | 251.0131 | 0 | 217.8957 | 23.7901 | 9.1591 | 217.8957 | 23.7901 | 9.1591 | 254.7226 | 27.8109 | 9.1591 | 0.9914%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 1366 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 279.7126 | 0 | 0 | 279.7126 | 0 | 242.8087 | 22.662 | 10.7144 | 242.8087 | 22.662 | 10.7144 | 283.8462 | 26.4921 | 10.7144 | 0.9849%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 1131 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 264.7162 | 0 | 0 | 264.7162 | 0 | 229.7909 | 18.7633 | 12.2468 | 229.7909 | 18.7633 | 12.2468 | 268.6282 | 21.9345 | 12.2468 | 0.9916%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 1778 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 155.5089 | 0 | 0 | 155.5089 | 0 | 134.9918 | 29.497 | 4.5765 | 134.9918 | 29.497 | 4.5765 | 157.807 | 34.4824 | 4.5765 | 0.9745%
2028 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 92 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.15602 | 0 | 0 | 0.15602 | 0 | 0.13544 | 1.5263 | 0.088735 | 0.13544 | 1.5263 | 0.088735 | 0.15833 | 1.7842 | 0.088735 | 0.8684%
2028 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.03453 | 0 | 0 | 0.03453 | 0 | 0.029974 | 0.41475 | 0.07227 | 0.029974 | 0.41475 | 0.07227 | 0.03504 | 0.48485 | 0.07227 | 0.1275%
2028 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.021961 | 0 | 0 | 0.021961 | 0 | 0.019063 | 0.06636 | 0.28727 | 0.019063 | 0.06636 | 0.28727 | 0.022285 | 0.077576 | 0.28727 | 0.3435%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 21 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 7.2501 | 0 | 0 | 7.2501 | 0 | 6.2935 | 0.34839 | 18.0646 | 6.2935 | 0.34839 | 18.0646 | 7.3572 | 0.40727 | 18.0646 | 0.9924%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 183 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 8.6358 | 0 | 0 | 8.6358 | 0 | 7.4964 | 3.036 | 2.4692 | 7.4964 | 3.036 | 2.4692 | 8.7634 | 3.5491 | 2.4692 | 0.9393%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 39 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.0761 | 0.64701 | 1.6632 | 1.0761 | 0.64701 | 1.6632 | 1.258 | 0.75636 | 1.6632 | 0.8802%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 564 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 58.7665 | 0 | 0 | 58.7665 | 0 | 51.0132 | 9.3568 | 5.452 | 51.0132 | 9.3568 | 5.452 | 59.635 | 10.9382 | 5.452 | 0.9962%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 628 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 49.7212 | 0 | 0 | 49.7212 | 0 | 43.1612 | 10.4185 | 4.1427 | 43.1612 | 10.4185 | 4.1427 | 50.456 | 12.1794 | 4.1427 | 0.9962%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 414 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 25.1014 | 0 | 0 | 25.1014 | 0 | 21.7896 | 6.8683 | 3.1725 | 21.7896 | 6.8683 | 3.1725 | 25.4723 | 8.0291 | 3.1725 | 0.9984%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 100 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 0.94153 | 0 | 0 | 0.94153 | 0 | 0.81731 | 1.659 | 0.49265 | 0.81731 | 1.659 | 0.49265 | 0.95544 | 1.9394 | 0.49265 | 0.9877%
2028 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 0.54035 | 0 | 0 | 0.54035 | 0 | 0.46905 | 0.01659 | 28.2733 | 0.46905 | 0.01659 | 28.2733 | 0.54833 | 0.019394 | 28.2733 | 0.9875%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 43 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 21.3802 | 0 | 0 | 21.3802 | 0 | 18.5594 | 0.71337 | 26.0165 | 18.5594 | 0.71337 | 26.0165 | 21.6962 | 0.83394 | 26.0165 | 0.9968%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 120 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 42.2487 | 0 | 0 | 42.2487 | 0 | 36.6746 | 1.9908 | 18.422 | 36.6746 | 1.9908 | 18.422 | 42.8731 | 2.3273 | 18.422 | 0.9992%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 113 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 3.9405 | 0 | 0 | 3.9405 | 0 | 3.4206 | 1.8747 | 1.8246 | 3.4206 | 1.8747 | 1.8246 | 3.9987 | 2.1915 | 1.8246 | 0.945%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 69 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 7.8368 | 0 | 0 | 7.8368 | 0 | 6.8028 | 1.1447 | 5.9428 | 6.8028 | 1.1447 | 5.9428 | 7.9526 | 1.3382 | 5.9428 | 0.994%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 2029 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 42.4984 | 0 | 0 | 42.4984 | 0 | 36.8914 | 33.6611 | 1.096 | 36.8914 | 33.6611 | 1.096 | 43.1264 | 39.3503 | 1.096 | 0.9112%
2028 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 24 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 2.1191 | 0 | 0 | 2.1191 | 0 | 1.8395 | 0.39816 | 4.6199 | 1.8395 | 0.39816 | 4.6199 | 2.1504 | 0.46545 | 4.6199 | 0.8819%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 25 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.9961 | 0 | 0 | 1.9961 | 0 | 1.7327 | 0.41475 | 4.1777 | 1.7327 | 0.41475 | 4.1777 | 2.0256 | 0.48485 | 4.1777 | 0.9662%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 7 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 2.4241 | 0 | 0 | 2.4241 | 0 | 2.1043 | 0.11613 | 18.1201 | 2.1043 | 0.11613 | 18.1201 | 2.4599 | 0.13576 | 18.1201 | 0.9775%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 151 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 38.9639 | 0 | 0 | 38.9639 | 0 | 33.8232 | 2.5051 | 13.5018 | 33.8232 | 2.5051 | 13.5018 | 39.5397 | 2.9285 | 13.5018 | 0.9826%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 214 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 100.8527 | 0 | 0 | 100.8527 | 0 | 87.5467 | 3.5503 | 24.6592 | 87.5467 | 3.5503 | 24.6592 | 102.3431 | 4.1503 | 24.6592 | 0.9977%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 457 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 102.2775 | 0 | 0 | 102.2775 | 0 | 88.7835 | 7.5816 | 11.7103 | 88.7835 | 7.5816 | 11.7103 | 103.789 | 8.863 | 11.7103 | 0.9908%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 85 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 60.1706 | 0 | 0 | 60.1706 | 0 | 52.232 | 1.4102 | 37.04 | 52.232 | 1.4102 | 37.04 | 61.0598 | 1.6485 | 37.04 | 0.9788%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 52 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 20.9753 | 0 | 0 | 20.9753 | 0 | 18.208 | 0.86268 | 21.1063 | 18.208 | 0.86268 | 21.1063 | 21.2853 | 1.0085 | 21.1063 | 0.9469%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 334 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 83.8997 | 0 | 0 | 83.8997 | 0 | 72.8304 | 5.5411 | 13.1438 | 72.8304 | 5.5411 | 13.1438 | 85.1396 | 6.4776 | 13.1438 | 0.9648%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 166 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 15.3615 | 0 | 0 | 15.3615 | 0 | 13.3348 | 2.7539 | 4.8421 | 13.3348 | 2.7539 | 4.8421 | 15.5885 | 3.2194 | 4.8421 | 0.9856%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 452 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 35.0565 | 0 | 0 | 35.0565 | 0 | 30.4313 | 7.4987 | 4.0582 | 30.4313 | 7.4987 | 4.0582 | 35.5746 | 8.766 | 4.0582 | 0.9842%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 766 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 29.2113 | 0 | 0 | 29.2113 | 0 | 25.3573 | 12.708 | 1.9954 | 25.3573 | 12.708 | 1.9954 | 29.643 | 14.8557 | 1.9954 | 0.979%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 112 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 11.9053 | 1.8581 | 6.4073 | 11.9053 | 1.8581 | 6.4073 | 13.9174 | 2.1721 | 6.4073 | 0.9892%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 544 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 42.4254 | 0 | 0 | 42.4254 | 0 | 36.828 | 9.025 | 4.0807 | 36.828 | 9.025 | 4.0807 | 43.0524 | 10.5503 | 4.0807 | 0.9866%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 27 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 4.1011 | 0 | 0 | 4.1011 | 0 | 3.5601 | 0.44793 | 7.9478 | 3.5601 | 0.44793 | 7.9478 | 4.1617 | 0.52364 | 7.9478 | 0.9965%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 77 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 4.5515 | 0 | 0 | 4.5515 | 0 | 3.951 | 1.2774 | 3.0929 | 3.951 | 1.2774 | 3.0929 | 4.6188 | 1.4933 | 3.0929 | 0.9977%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 129 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 11.7036 | 0 | 0 | 11.7036 | 0 | 10.1595 | 2.1401 | 4.7472 | 10.1595 | 2.1401 | 4.7472 | 11.8766 | 2.5018 | 4.7472 | 0.9935%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 20 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 1.5742 | 0 | 0 | 1.5742 | 0 | 1.3665 | 0.3318 | 4.1186 | 1.3665 | 0.3318 | 4.1186 | 1.5975 | 0.38788 | 4.1186 | 0.9948%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 173 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 18.6048 | 0 | 0 | 18.6048 | 0 | 16.1502 | 2.8701 | 5.6271 | 16.1502 | 2.8701 | 5.6271 | 18.8798 | 3.3551 | 5.6271 | 0.9905%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 137 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 59.7151 | 0 | 0 | 59.7151 | 0 | 51.8366 | 2.2728 | 22.807 | 51.8366 | 2.2728 | 22.807 | 60.5976 | 2.657 | 22.807 | 0.9304%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 121 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 64.4306 | 0 | 0 | 64.4306 | 0 | 55.93 | 2.0074 | 27.862 | 55.93 | 2.0074 | 27.862 | 65.3828 | 2.3467 | 27.862 | 0.9454%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 740 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 116.6221 | 0 | 0 | 116.6221 | 0 | 101.2356 | 12.2766 | 8.2462 | 101.2356 | 12.2766 | 8.2462 | 118.3455 | 14.3515 | 8.2462 | 0.9926%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 333 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 36.1696 | 0 | 0 | 36.1696 | 0 | 31.3976 | 5.5245 | 5.6834 | 31.3976 | 5.5245 | 5.6834 | 36.7042 | 6.4582 | 5.6834 | 0.9815%
2028 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | Non-HFTD---15 | 123 | 100% | 14.0801 | 87.11% | 0% | 12.89% | 0.12265 | 0 | 0 | 0.12265 | 0 | 0.10647 | 2.0406 | 0.052176 | 0.10647 | 2.0406 | 0.052176 | 0.12446 | 2.3855 | 0.052176 | 0.8711%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 76 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 3.8668 | 0 | 0 | 3.8668 | 0 | 3.3566 | 1.2608 | 2.6622 | 3.3566 | 1.2608 | 2.6622 | 3.924 | 1.4739 | 2.6622 | 0.9046%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 17 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 20.2356 | 0 | 0 | 20.2356 | 0 | 17.5658 | 0.28203 | 62.2834 | 17.5658 | 0.28203 | 62.2834 | 20.5346 | 0.3297 | 62.2834 | 0.8554%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 221 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 43.1212 | 0 | 0 | 43.1212 | 0 | 37.432 | 3.6664 | 10.2095 | 37.432 | 3.6664 | 10.2095 | 43.7585 | 4.2861 | 10.2095 | 0.9867%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 0.58197 | 0 | 0 | 0.58197 | 0 | 0.50519 | 0.06636 | 7.6129 | 0.50519 | 0.06636 | 7.6129 | 0.59057 | 0.077576 | 7.6129 | 0.9994%
2028 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 15 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.24885 | 0 | 0 | 0.24885 | 0 | 0 | 0.29091 | 0 | 0%
2028 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 23 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.38157 | 0 | 0 | 0.38157 | 0 | 0 | 0.44606 | 0 | 0%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 149 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 158.4228 | 0 | 0 | 158.4228 | 0 | 137.5213 | 2.4719 | 55.6336 | 137.5213 | 2.4719 | 55.6336 | 160.764 | 2.8897 | 55.6336 | 0.9909%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 19 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 0.49948 | 0 | 0 | 0.49948 | 0 | 0.43358 | 0.31521 | 1.3755 | 0.43358 | 0.31521 | 1.3755 | 0.50686 | 0.36848 | 1.3755 | 0.2981%
2028 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 0.80966 | 0 | 0 | 0.80966 | 0 | 0.70284 | 0.01659 | 42.365 | 0.70284 | 0.01659 | 42.365 | 0.82162 | 0.019394 | 42.365 | 0.9995%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 334 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 80.984 | 0 | 0 | 80.984 | 0 | 70.2994 | 5.5411 | 12.687 | 70.2994 | 5.5411 | 12.687 | 82.1808 | 6.4776 | 12.687 | 0.9925%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 831 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 368.386 | 0 | 0 | 368.386 | 0 | 319.7831 | 13.7863 | 23.1957 | 319.7831 | 13.7863 | 23.1957 | 373.8301 | 16.1163 | 23.1957 | 0.9936%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.074002 | 0 | 0 | 0.074002 | 0 | 0.064239 | 0.14931 | 0.43024 | 0.064239 | 0.14931 | 0.43024 | 0.075096 | 0.17455 | 0.43024 | 0.895%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 124 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.1867 | 2.0572 | 1.5491 | 3.1867 | 2.0572 | 1.5491 | 3.7253 | 2.4048 | 1.5491 | 0.8771%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 1030 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 50.9186 | 0 | 0 | 50.9186 | 0 | 44.2007 | 17.0877 | 2.5867 | 44.2007 | 17.0877 | 2.5867 | 51.6711 | 19.9757 | 2.5867 | 0.9246%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 96 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 30.2421 | 0 | 0 | 30.2421 | 0 | 26.2521 | 1.5926 | 16.4834 | 26.2521 | 1.5926 | 16.4834 | 30.689 | 1.8618 | 16.4834 | 0.9907%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 316 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 38.3681 | 0 | 0 | 38.3681 | 0 | 33.306 | 5.2424 | 6.3532 | 33.306 | 5.2424 | 6.3532 | 38.9351 | 6.1285 | 6.3532 | 0.9899%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 356 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 30.1096 | 0 | 0 | 30.1096 | 0 | 26.1371 | 5.906 | 4.4255 | 26.1371 | 5.906 | 4.4255 | 30.5546 | 6.9042 | 4.4255 | 0.9527%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 882 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.807 | 0 | 0 | 16.807 | 0 | 14.5896 | 14.6324 | 0.99708 | 14.5896 | 14.6324 | 0.99708 | 17.0554 | 17.1054 | 0.99708 | 0.8154%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 441 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 17.7423 | 0 | 0 | 17.7423 | 0 | 15.4015 | 7.3162 | 2.1051 | 15.4015 | 7.3162 | 2.1051 | 18.0045 | 8.5527 | 2.1051 | 0.9501%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 1391 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 181.8804 | 0 | 0 | 181.8804 | 0 | 157.884 | 23.0767 | 6.8417 | 157.884 | 23.0767 | 6.8417 | 184.5682 | 26.9769 | 6.8417 | 0.97%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 593 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 39.9284 | 0 | 0 | 39.9284 | 0 | 34.6605 | 9.8379 | 3.5232 | 34.6605 | 9.8379 | 3.5232 | 40.5185 | 11.5006 | 3.5232 | 0.991%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 236 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 18.7325 | 0 | 0 | 18.7325 | 0 | 16.261 | 3.9152 | 4.1533 | 16.261 | 3.9152 | 4.1533 | 19.0093 | 4.577 | 4.1533 | 0.7065%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 756 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 42.7679 | 0 | 0 | 42.7679 | 0 | 37.1254 | 12.5421 | 2.9601 | 37.1254 | 12.5421 | 2.9601 | 43.4 | 14.6618 | 2.9601 | 0.9752%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 864 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 55.6127 | 0 | 0 | 55.6127 | 0 | 48.2755 | 14.3338 | 3.368 | 48.2755 | 14.3338 | 3.368 | 56.4346 | 16.7563 | 3.368 | 0.9686%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 245 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 6.6698 | 0 | 0 | 6.6698 | 0 | 5.7898 | 4.0646 | 1.4245 | 5.7898 | 4.0646 | 1.4245 | 6.7683 | 4.7515 | 1.4245 | 0.7976%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 575 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 113.8145 | 0 | 0 | 113.8145 | 0 | 98.7984 | 9.5393 | 10.357 | 98.7984 | 9.5393 | 10.357 | 115.4964 | 11.1515 | 10.357 | 0.9877%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 41.0508 | 0 | 0 | 41.0508 | 0 | 35.6347 | 5.9226 | 6.0167 | 35.6347 | 5.9226 | 6.0167 | 41.6574 | 6.9236 | 6.0167 | 0.981%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 870 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 97.7953 | 0 | 0 | 97.7953 | 0 | 84.8927 | 14.4333 | 5.8817 | 84.8927 | 14.4333 | 5.8817 | 99.2405 | 16.8727 | 5.8817 | 0.9713%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 30 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 2.7358 | 0 | 0 | 2.7358 | 0 | 2.3749 | 0.4977 | 4.7717 | 2.3749 | 0.4977 | 4.7717 | 2.7763 | 0.58182 | 4.7717 | 0.6764%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 270 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 33.2415 | 0 | 0 | 33.2415 | 0 | 28.8558 | 4.4793 | 6.442 | 28.8558 | 4.4793 | 6.442 | 33.7328 | 5.2364 | 6.442 | 0.9774%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 451 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 48.2077 | 0 | 0 | 48.2077 | 0 | 41.8474 | 7.4821 | 5.593 | 41.8474 | 7.4821 | 5.593 | 48.9201 | 8.7467 | 5.593 | 0.977%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 1054 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 127.5184 | 0 | 0 | 127.5184 | 0 | 110.6943 | 17.4859 | 6.3305 | 110.6943 | 17.4859 | 6.3305 | 129.4029 | 20.4412 | 6.3305 | 0.968%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 77 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.5989 | 0 | 0 | 14.5989 | 0 | 12.6728 | 1.2774 | 9.9205 | 12.6728 | 1.2774 | 9.9205 | 14.8146 | 1.4933 | 9.9205 | 0.8924%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 36 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 23.1825 | 0 | 0 | 23.1825 | 0 | 20.1239 | 0.59724 | 33.6948 | 20.1239 | 0.59724 | 33.6948 | 23.5251 | 0.69818 | 33.6948 | 0.7823%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 0.43426 | 0 | 0 | 0.43426 | 0 | 0.37697 | 0.14931 | 2.5247 | 0.37697 | 0.14931 | 2.5247 | 0.44068 | 0.17455 | 2.5247 | 0.9121%
2028 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 3 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0012779 | 0 | 0 | 0.0012779 | 0 | 0.0011093 | 0.04977 | 0.022288 | 0.0011093 | 0.04977 | 0.022288 | 0.0012967 | 0.058182 | 0.022288 | 0.1338%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 1311 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 112.3683 | 0 | 0 | 112.3683 | 0 | 97.543 | 21.7495 | 4.4848 | 97.543 | 21.7495 | 4.4848 | 114.0289 | 25.4254 | 4.4848 | 0.9429%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 11 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 19.3419 | 0 | 0 | 19.3419 | 0 | 16.79 | 0.18249 | 92.0051 | 16.79 | 0.18249 | 92.0051 | 19.6277 | 0.21333 | 92.0051 | 0.9974%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 338 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 41.9676 | 0 | 0 | 41.9676 | 0 | 36.4306 | 5.6074 | 6.4968 | 36.4306 | 5.6074 | 6.4968 | 42.5878 | 6.5551 | 6.4968 | 0.9922%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 17 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 6.5014 | 0 | 0 | 6.5014 | 0 | 5.6436 | 0.28203 | 20.0107 | 5.6436 | 0.28203 | 20.0107 | 6.5975 | 0.3297 | 20.0107 | 0.9914%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 85 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.096 | 0 | 0 | 2.096 | 0 | 1.8195 | 1.4102 | 1.2903 | 1.8195 | 1.4102 | 1.2903 | 2.127 | 1.6485 | 1.2903 | 0.6623%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 180 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 3.5043 | 0 | 0 | 3.5043 | 0 | 3.042 | 2.9862 | 1.0187 | 3.042 | 2.9862 | 1.0187 | 3.5561 | 3.4909 | 1.0187 | 0.7437%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 481 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 15.8478 | 0 | 0 | 15.8478 | 0 | 13.757 | 7.9798 | 1.724 | 13.757 | 7.9798 | 1.724 | 16.082 | 9.3285 | 1.724 | 0.9193%
2028 | 196 | 196-43F | Tier-2 | Tier-2---17 | Tier-2---9 | 138 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.048193 | 0 | 0 | 0.048193 | 0 | 0.041834 | 2.2894 | 0.018273 | 0.041834 | 2.2894 | 0.018273 | 0.048905 | 2.6764 | 0.018273 | 0.0514%
2028 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 2 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 1.8232 | 0 | 0 | 1.8232 | 0 | 1.5826 | 0.03318 | 47.6988 | 1.5826 | 0.03318 | 47.6988 | 1.8501 | 0.038788 | 47.6988 | 0.9934%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 27 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.063793 | 0 | 0 | 0.063793 | 0 | 0.055376 | 0.44793 | 0.12363 | 0.055376 | 0.44793 | 0.12363 | 0.064736 | 0.52364 | 0.12363 | 0.9638%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 103 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 9.2964 | 0 | 0 | 9.2964 | 0 | 8.0699 | 1.7088 | 4.7226 | 8.0699 | 1.7088 | 4.7226 | 9.4338 | 1.9976 | 4.7226 | 0.9553%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 301 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 4.7262 | 0 | 0 | 4.7262 | 0 | 4.1027 | 4.9936 | 0.82158 | 4.1027 | 4.9936 | 0.82158 | 4.7961 | 5.8376 | 0.82158 | 0.9636%
2028 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 9 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 1.2217 | 0 | 0 | 1.2217 | 0 | 1.0605 | 0.14931 | 7.103 | 1.0605 | 0.14931 | 7.103 | 1.2398 | 0.17455 | 7.103 | 0.9852%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 66 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 12.7628 | 0 | 0 | 12.7628 | 0 | 11.079 | 1.0949 | 10.1183 | 11.079 | 1.0949 | 10.1183 | 12.9514 | 1.28 | 10.1183 | 0.9978%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 385 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 29.6913 | 0 | 0 | 29.6913 | 0 | 25.774 | 6.3872 | 4.0353 | 25.774 | 6.3872 | 4.0353 | 30.13 | 7.4667 | 4.0353 | 0.9975%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1294 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 84.4086 | 0 | 0 | 84.4086 | 0 | 73.2722 | 21.4675 | 3.4132 | 73.2722 | 21.4675 | 3.4132 | 85.656 | 25.0957 | 3.4132 | 0.9974%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 202 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 4.4883 | 0 | 0 | 4.4883 | 0 | 3.8961 | 3.3512 | 1.1626 | 3.8961 | 3.3512 | 1.1626 | 4.5546 | 3.9176 | 1.1626 | 0.901%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 360 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 8.8981 | 0 | 0 | 8.8981 | 0 | 7.7241 | 5.9724 | 1.2933 | 7.7241 | 5.9724 | 1.2933 | 9.0296 | 6.9818 | 1.2933 | 0.8573%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 240 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 1.2022 | 0 | 0 | 1.2022 | 0 | 1.0436 | 3.9816 | 0.2621 | 1.0436 | 3.9816 | 0.2621 | 1.22 | 4.6545 | 0.2621 | 0.7047%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 183 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.6151 | 0 | 0 | 1.6151 | 0 | 1.402 | 3.036 | 0.46179 | 1.402 | 3.036 | 0.46179 | 1.6389 | 3.5491 | 0.46179 | 0.5082%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 410 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.7351 | 0 | 0 | 10.7351 | 0 | 9.3188 | 6.8019 | 1.37 | 9.3188 | 6.8019 | 1.37 | 10.8938 | 7.9515 | 1.37 | 0.8949%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 321 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.2479 | 0 | 0 | 15.2479 | 0 | 13.2361 | 5.3254 | 2.4855 | 13.2361 | 5.3254 | 2.4855 | 15.4732 | 6.2254 | 2.4855 | 0.8426%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 1148 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 17.2168 | 0 | 0 | 17.2168 | 0 | 14.9453 | 19.0453 | 0.78472 | 14.9453 | 19.0453 | 0.78472 | 17.4712 | 22.2642 | 0.78472 | 0.9106%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 386 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 16.594 | 0 | 0 | 16.594 | 0 | 14.4047 | 6.4037 | 2.2494 | 14.4047 | 6.4037 | 2.2494 | 16.8392 | 7.4861 | 2.2494 | 0.9543%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 267 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 14.9143 | 0 | 0 | 14.9143 | 0 | 12.9466 | 4.4295 | 2.9228 | 12.9466 | 4.4295 | 2.9228 | 15.1347 | 5.1782 | 2.9228 | 0.9497%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 39 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 6.0409 | 0 | 0 | 6.0409 | 0 | 5.2439 | 0.64701 | 8.1048 | 5.2439 | 0.64701 | 8.1048 | 6.1302 | 0.75636 | 8.1048 | 0.9907%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 1799 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 48.4633 | 0 | 0 | 48.4633 | 0 | 42.0693 | 29.8454 | 1.4096 | 42.0693 | 29.8454 | 1.4096 | 49.1795 | 34.8897 | 1.4096 | 0.9915%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 23 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 12.3961 | 0 | 0 | 12.3961 | 0 | 10.7606 | 0.38157 | 28.2008 | 10.7606 | 0.38157 | 28.2008 | 12.5793 | 0.44606 | 28.2008 | 0.9792%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 658 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 9.6505 | 0 | 0 | 9.6505 | 0 | 8.3773 | 10.9162 | 0.76742 | 8.3773 | 10.9162 | 0.76742 | 9.7932 | 12.7612 | 0.76742 | 0.9662%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 63 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.5373 | 0 | 0 | 2.5373 | 0 | 2.2025 | 1.0452 | 2.1073 | 2.2025 | 1.0452 | 2.1073 | 2.5748 | 1.2218 | 2.1073 | 0.9706%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 268 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 14.4203 | 0 | 0 | 14.4203 | 0 | 12.5177 | 4.4461 | 2.8154 | 12.5177 | 4.4461 | 2.8154 | 14.6334 | 5.1976 | 2.8154 | 0.9727%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 413 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 26.4207 | 0 | 0 | 26.4207 | 0 | 22.9349 | 6.8517 | 3.3473 | 22.9349 | 6.8517 | 3.3473 | 26.8111 | 8.0097 | 3.3473 | 0.9578%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 105 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 10.0888 | 0 | 0 | 10.0888 | 0 | 8.7577 | 1.742 | 5.0275 | 8.7577 | 1.742 | 5.0275 | 10.2379 | 2.0364 | 5.0275 | 0.9712%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 94 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 1.0262 | 0 | 0 | 1.0262 | 0 | 0.89078 | 1.5595 | 0.57121 | 0.89078 | 1.5595 | 0.57121 | 1.0413 | 1.823 | 0.57121 | 0.9778%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 160 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 21.3583 | 0 | 0 | 21.3583 | 0 | 18.5404 | 2.6544 | 6.9848 | 18.5404 | 2.6544 | 6.9848 | 21.6739 | 3.103 | 6.9848 | 0.9872%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 125 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 14.3897 | 0 | 0 | 14.3897 | 0 | 12.4912 | 2.0738 | 6.0235 | 12.4912 | 2.0738 | 6.0235 | 14.6024 | 2.4242 | 6.0235 | 0.9782%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 1694 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 259.9361 | 0 | 0 | 259.9361 | 0 | 225.6415 | 28.1035 | 8.029 | 225.6415 | 28.1035 | 8.029 | 263.7775 | 32.8533 | 8.029 | 0.9891%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 980 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 66.2737 | 0 | 0 | 66.2737 | 0 | 57.5299 | 16.2582 | 3.5385 | 57.5299 | 16.2582 | 3.5385 | 67.2531 | 19.006 | 3.5385 | 0.9941%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 1791 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 4.7145 | 0 | 0 | 4.7145 | 0 | 4.0925 | 29.7127 | 0.13774 | 4.0925 | 29.7127 | 0.13774 | 4.7842 | 34.7345 | 0.13774 | 0.974%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 892 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 3.9162 | 0 | 0 | 3.9162 | 0 | 3.3996 | 14.7983 | 0.22973 | 3.3996 | 14.7983 | 0.22973 | 3.9741 | 17.2994 | 0.22973 | 0.9786%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 433 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 5.0673 | 0 | 0 | 5.0673 | 0 | 4.3988 | 7.1835 | 0.61235 | 4.3988 | 7.1835 | 0.61235 | 5.1422 | 8.3976 | 0.61235 | 0.9871%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 21.8831 | 0 | 0 | 21.8831 | 0 | 18.9959 | 5.2756 | 3.6007 | 18.9959 | 5.2756 | 3.6007 | 22.2065 | 6.1673 | 3.6007 | 0.9909%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 1357 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 14.7534 | 0 | 0 | 14.7534 | 0 | 12.8069 | 22.5126 | 0.56888 | 12.8069 | 22.5126 | 0.56888 | 14.9714 | 26.3175 | 0.56888 | 0.8569%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 617 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 221.8508 | 0 | 0 | 221.8508 | 0 | 192.5809 | 10.236 | 18.814 | 192.5809 | 10.236 | 18.814 | 225.1293 | 11.966 | 18.814 | 0.9924%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 729 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 124.7557 | 0 | 0 | 124.7557 | 0 | 108.2961 | 12.0941 | 8.9544 | 108.2961 | 12.0941 | 8.9544 | 126.5994 | 14.1382 | 8.9544 | 0.9821%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 471 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 192.9417 | 0 | 0 | 192.9417 | 0 | 167.486 | 7.8139 | 21.4344 | 167.486 | 7.8139 | 21.4344 | 195.793 | 9.1345 | 21.4344 | 0.99%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 156 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 13.8549 | 0 | 0 | 13.8549 | 0 | 12.027 | 2.588 | 4.6471 | 12.027 | 2.588 | 4.6471 | 14.0597 | 3.0255 | 4.6471 | 0.9809%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 354 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 53.7594 | 0 | 0 | 53.7594 | 0 | 46.6667 | 5.8729 | 7.9462 | 46.6667 | 5.8729 | 7.9462 | 54.5539 | 6.8654 | 7.9462 | 0.9892%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 445 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 139.2688 | 0 | 0 | 139.2688 | 0 | 120.8944 | 7.3826 | 16.3757 | 120.8944 | 7.3826 | 16.3757 | 141.3269 | 8.6303 | 16.3757 | 0.9919%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 0.7121 | 0 | 0 | 0.7121 | 0 | 0.61815 | 0.11613 | 5.3229 | 0.61815 | 0.11613 | 5.3229 | 0.72263 | 0.13576 | 5.3229 | 0.999%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 997 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 17.9663 | 0 | 0 | 17.9663 | 0 | 15.5959 | 16.5402 | 0.94291 | 15.5959 | 16.5402 | 0.94291 | 18.2318 | 19.3357 | 0.94291 | 0.8922%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 790 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 23.9618 | 0 | 0 | 23.9618 | 0 | 20.8004 | 13.1061 | 1.5871 | 20.8004 | 13.1061 | 1.5871 | 24.3159 | 15.3212 | 1.5871 | 0.8785%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 1010 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 105.4623 | 0 | 0 | 105.4623 | 0 | 91.5481 | 16.7559 | 5.4636 | 91.5481 | 16.7559 | 5.4636 | 107.0208 | 19.5879 | 5.4636 | 0.9868%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 866 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 34.6186 | 0 | 0 | 34.6186 | 0 | 30.0512 | 14.367 | 2.0917 | 30.0512 | 14.367 | 2.0917 | 35.1302 | 16.7951 | 2.0917 | 0.9466%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 923 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 13.074 | 0 | 0 | 13.074 | 0 | 11.3491 | 15.3126 | 0.74116 | 11.3491 | 15.3126 | 0.74116 | 13.2672 | 17.9006 | 0.74116 | 0.9088%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 249 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 100.208 | 0 | 0 | 100.208 | 0 | 86.9871 | 4.1309 | 21.0576 | 86.9871 | 4.1309 | 21.0576 | 101.6889 | 4.8291 | 21.0576 | 0.9905%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 187 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 21.1814 | 0 | 0 | 21.1814 | 0 | 18.3868 | 3.1023 | 5.9268 | 18.3868 | 3.1023 | 5.9268 | 21.4944 | 3.6267 | 5.9268 | 0.9634%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 978 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 16.2335 | 0 | 0 | 16.2335 | 0 | 14.0917 | 16.225 | 0.86852 | 14.0917 | 16.225 | 0.86852 | 16.4734 | 18.9672 | 0.86852 | 0.8429%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 2947 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 32.0447 | 0 | 0 | 32.0447 | 0 | 27.8169 | 48.8908 | 0.56896 | 27.8169 | 48.8908 | 0.56896 | 32.5183 | 57.1539 | 0.56896 | 0.8937%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 161 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 36.8757 | 0 | 0 | 36.8757 | 0 | 32.0105 | 2.671 | 11.9845 | 32.0105 | 2.671 | 11.9845 | 37.4207 | 3.1224 | 11.9845 | 0.9991%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 1068 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 30.1393 | 0 | 0 | 30.1393 | 0 | 26.1629 | 17.7181 | 1.4766 | 26.1629 | 17.7181 | 1.4766 | 30.5847 | 20.7127 | 1.4766 | 0.9216%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 1386 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 26.2945 | 0 | 0 | 26.2945 | 0 | 22.8253 | 22.9938 | 0.99268 | 22.8253 | 22.9938 | 0.99268 | 26.6831 | 26.88 | 0.99268 | 0.9611%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 16 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 7.0648 | 0 | 0 | 7.0648 | 0 | 6.1327 | 0.26544 | 23.1039 | 6.1327 | 0.26544 | 23.1039 | 7.1692 | 0.3103 | 23.1039 | 0.9946%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 1029 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 38.1775 | 0 | 0 | 38.1775 | 0 | 33.1406 | 17.0711 | 1.9413 | 33.1406 | 17.0711 | 1.9413 | 38.7417 | 19.9563 | 1.9413 | 0.9703%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 144 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.0624 | 0 | 0 | 1.0624 | 0 | 0.92221 | 2.389 | 0.38603 | 0.92221 | 2.389 | 0.38603 | 1.0781 | 2.7927 | 0.38603 | 0.334%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 20.4535 | 0 | 0 | 20.4535 | 0 | 17.7549 | 1.8747 | 9.471 | 17.7549 | 1.8747 | 9.471 | 20.7557 | 2.1915 | 9.471 | 0.9951%
2028 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 6 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 38.995 | 0 | 0 | 38.995 | 0 | 33.8502 | 0.09954 | 340.0663 | 33.8502 | 0.09954 | 340.0663 | 39.5713 | 0.11636 | 340.0663 | 0.9988%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 333 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 6.0987 | 0 | 0 | 6.0987 | 0 | 5.2941 | 5.5245 | 0.9583 | 5.2941 | 5.5245 | 0.9583 | 6.1889 | 6.4582 | 0.9583 | 0.9868%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 365 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 44.5714 | 0 | 0 | 44.5714 | 0 | 38.6908 | 6.0554 | 6.3895 | 38.6908 | 6.0554 | 6.3895 | 45.23 | 7.0788 | 6.3895 | 0.9945%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 172 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 22.5131 | 0 | 0 | 22.5131 | 0 | 19.5428 | 2.8535 | 6.8488 | 19.5428 | 2.8535 | 6.8488 | 22.8458 | 3.3358 | 6.8488 | 0.9686%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 173 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 95.7874 | 0 | 0 | 95.7874 | 0 | 83.1497 | 2.8701 | 28.9713 | 83.1497 | 2.8701 | 28.9713 | 97.203 | 3.3551 | 28.9713 | 0.9959%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 573 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 12.9352 | 0 | 0 | 12.9352 | 0 | 11.2286 | 9.5061 | 1.1812 | 11.2286 | 9.5061 | 1.1812 | 13.1263 | 11.1127 | 1.1812 | 0.9515%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 2453 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 71.5661 | 0 | 0 | 71.5661 | 0 | 62.1241 | 40.6953 | 1.5266 | 62.1241 | 40.6953 | 1.5266 | 72.6237 | 47.5733 | 1.5266 | 0.9662%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 895 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 786.0217 | 0 | 0 | 786.0217 | 0 | 682.3181 | 14.8481 | 45.9533 | 682.3181 | 14.8481 | 45.9533 | 797.6376 | 17.3576 | 45.9533 | 0.9925%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 47 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 35.9293 | 0 | 0 | 35.9293 | 0 | 31.189 | 0.77973 | 39.9997 | 31.189 | 0.77973 | 39.9997 | 36.4603 | 0.91151 | 39.9997 | 0.9927%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 409 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 449.3941 | 0 | 0 | 449.3941 | 0 | 390.1034 | 6.7853 | 57.4923 | 390.1034 | 6.7853 | 57.4923 | 456.0353 | 7.9321 | 57.4923 | 0.9963%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 40 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 2.4995 | 0 | 0 | 2.4995 | 0 | 2.1697 | 0.6636 | 3.2696 | 2.1697 | 0.6636 | 3.2696 | 2.5364 | 0.77576 | 3.2696 | 0.8656%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 1410 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 71.3353 | 0 | 0 | 71.3353 | 0 | 61.9237 | 23.3919 | 2.6472 | 61.9237 | 23.3919 | 2.6472 | 72.3895 | 27.3454 | 2.6472 | 0.9605%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 237 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 48.5252 | 0 | 0 | 48.5252 | 0 | 42.123 | 3.9318 | 10.7133 | 42.123 | 3.9318 | 10.7133 | 49.2423 | 4.5964 | 10.7133 | 0.9985%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 3377 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 162.1806 | 0 | 0 | 162.1806 | 0 | 140.7833 | 56.0245 | 2.5129 | 140.7833 | 56.0245 | 2.5129 | 164.5773 | 65.4933 | 2.5129 | 0.967%
2028 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 4 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.17079 | 0 | 0 | 0.17079 | 0 | 0.14826 | 0.06636 | 2.2342 | 0.14826 | 0.06636 | 2.2342 | 0.17332 | 0.077576 | 2.2342 | 0.9833%
2028 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 10 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 1.705 | 0 | 0 | 1.705 | 0 | 1.4801 | 0.1659 | 8.9215 | 1.4801 | 0.1659 | 8.9215 | 1.7302 | 0.19394 | 8.9215 | 0.9937%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 1039 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 19.0012 | 0 | 0 | 19.0012 | 0 | 16.4943 | 17.237 | 0.95691 | 16.4943 | 17.237 | 0.95691 | 19.282 | 20.1503 | 0.95691 | 0.9498%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 1418 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 62.777 | 0 | 0 | 62.777 | 0 | 54.4945 | 23.5246 | 2.3165 | 54.4945 | 23.5246 | 2.3165 | 63.7047 | 27.5006 | 2.3165 | 0.9826%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 1039 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 18.8766 | 0 | 0 | 18.8766 | 0 | 16.3862 | 17.237 | 0.95064 | 16.3862 | 17.237 | 0.95064 | 19.1556 | 20.1503 | 0.95064 | 0.9106%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 329 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 4.2357 | 0 | 0 | 4.2357 | 0 | 3.6769 | 5.4581 | 0.67365 | 3.6769 | 5.4581 | 0.67365 | 4.2983 | 6.3806 | 0.67365 | 0.7897%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 165 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 7.7444 | 0 | 0 | 7.7444 | 0 | 6.7227 | 2.7374 | 2.4559 | 6.7227 | 2.7374 | 2.4559 | 7.8589 | 3.2 | 2.4559 | 0.9819%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 865 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 33.9276 | 0 | 0 | 33.9276 | 0 | 29.4513 | 14.3504 | 2.0523 | 29.4513 | 14.3504 | 2.0523 | 34.429 | 16.7757 | 2.0523 | 0.9768%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 13 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 1.1307 | 0 | 0 | 1.1307 | 0 | 0.98148 | 0.21567 | 4.5509 | 0.98148 | 0.21567 | 4.5509 | 1.1474 | 0.25212 | 4.5509 | 0.9298%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 106 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 1.5993 | 0 | 0 | 1.5993 | 0 | 1.3883 | 1.7585 | 0.78948 | 1.3883 | 1.7585 | 0.78948 | 1.623 | 2.0558 | 0.78948 | 0.8171%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 1011 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 26.8454 | 0 | 0 | 26.8454 | 0 | 23.3036 | 16.7725 | 1.3894 | 23.3036 | 16.7725 | 1.3894 | 27.2421 | 19.6072 | 1.3894 | 0.983%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 3541 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 50.7426 | 0 | 0 | 50.7426 | 0 | 44.0479 | 58.7452 | 0.74981 | 44.0479 | 58.7452 | 0.74981 | 51.4925 | 68.6739 | 0.74981 | 0.9868%
2028 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.00051701 | 0 | 0 | 0.00051701 | 0 | 0.0004488 | 0.09954 | 0.0045088 | 0.0004488 | 0.09954 | 0.0045088 | 0.00052465 | 0.11636 | 0.0045088 | 0.004523%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 1420 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 30.0056 | 0 | 0 | 30.0056 | 0 | 26.0468 | 23.5578 | 1.1057 | 26.0468 | 23.5578 | 1.1057 | 30.449 | 27.5394 | 1.1057 | 0.9884%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 548 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 7.0152 | 0 | 0 | 7.0152 | 0 | 6.0897 | 9.0913 | 0.66983 | 6.0897 | 9.0913 | 0.66983 | 7.1189 | 10.6279 | 0.66983 | 0.9757%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 453 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 4.252 | 0 | 0 | 4.252 | 0 | 3.691 | 7.5153 | 0.49113 | 3.691 | 7.5153 | 0.49113 | 4.3148 | 8.7854 | 0.49113 | 0.9496%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 875 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 20.1156 | 0 | 0 | 20.1156 | 0 | 17.4616 | 14.5163 | 1.2029 | 17.4616 | 14.5163 | 1.2029 | 20.4128 | 16.9697 | 1.2029 | 0.859%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 1371 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 49.1254 | 0 | 0 | 49.1254 | 0 | 42.644 | 22.7449 | 1.8749 | 42.644 | 22.7449 | 1.8749 | 49.8514 | 26.5891 | 1.8749 | 0.9946%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 275 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 38.7745 | 0 | 0 | 38.7745 | 0 | 33.6588 | 4.5623 | 7.3777 | 33.6588 | 4.5623 | 7.3777 | 39.3475 | 5.3333 | 7.3777 | 0.8863%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 897 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 232.9181 | 0 | 0 | 232.9181 | 0 | 202.1881 | 14.8812 | 13.5868 | 202.1881 | 14.8812 | 13.5868 | 236.3602 | 17.3963 | 13.5868 | 0.9837%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 800 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 95.9587 | 0 | 0 | 95.9587 | 0 | 83.2984 | 13.272 | 6.2762 | 83.2984 | 13.272 | 6.2762 | 97.3768 | 15.5151 | 6.2762 | 0.9873%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 260 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 27.4627 | 0 | 0 | 27.4627 | 0 | 23.8394 | 4.3134 | 5.5268 | 23.8394 | 4.3134 | 5.5268 | 27.8686 | 5.0424 | 5.5268 | 0.9726%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 177 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 22.2918 | 0 | 0 | 22.2918 | 0 | 19.3507 | 2.9364 | 6.5899 | 19.3507 | 2.9364 | 6.5899 | 22.6212 | 3.4327 | 6.5899 | 0.9861%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 530 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 52.2933 | 0 | 0 | 52.2933 | 0 | 45.394 | 8.7927 | 5.1627 | 45.394 | 8.7927 | 5.1627 | 53.0661 | 10.2788 | 5.1627 | 0.9807%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 954 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 208.7568 | 0 | 0 | 208.7568 | 0 | 181.2145 | 15.8269 | 11.4498 | 181.2145 | 15.8269 | 11.4498 | 211.8418 | 18.5018 | 11.4498 | 0.9836%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 256 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 67.7852 | 0 | 0 | 67.7852 | 0 | 58.842 | 4.247 | 13.8548 | 58.842 | 4.247 | 13.8548 | 68.7869 | 4.9648 | 13.8548 | 0.9784%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 36.122 | 0 | 0 | 36.122 | 0 | 31.3562 | 1.8581 | 16.8756 | 31.3562 | 1.8581 | 16.8756 | 36.6558 | 2.1721 | 16.8756 | 0.994%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 398 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 280.6404 | 0 | 0 | 280.6404 | 0 | 243.6142 | 6.6028 | 36.8954 | 243.6142 | 6.6028 | 36.8954 | 284.7877 | 7.7188 | 36.8954 | 0.9934%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 1107 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 267.8069 | 0 | 0 | 267.8069 | 0 | 232.4738 | 18.3651 | 12.6584 | 232.4738 | 18.3651 | 12.6584 | 271.7645 | 21.4691 | 12.6584 | 0.9889%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 88 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 4.7012 | 0 | 0 | 4.7012 | 0 | 4.081 | 1.4599 | 2.7953 | 4.081 | 1.4599 | 2.7953 | 4.7707 | 1.7067 | 2.7953 | 0.7089%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 25.0053 | 0 | 0 | 25.0053 | 0 | 21.7062 | 0.58065 | 37.3826 | 21.7062 | 0.58065 | 37.3826 | 25.3748 | 0.67879 | 37.3826 | 0.9883%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 1011 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 306.1973 | 0 | 0 | 306.1973 | 0 | 265.7992 | 16.7725 | 15.8473 | 265.7992 | 16.7725 | 15.8473 | 310.7223 | 19.6072 | 15.8473 | 0.9911%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 1263 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 648.1566 | 0 | 0 | 648.1566 | 0 | 562.6422 | 20.9532 | 26.8523 | 562.6422 | 20.9532 | 26.8523 | 657.7351 | 24.4945 | 26.8523 | 0.9893%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 689 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 8.4382 | 0 | 0 | 8.4382 | 0 | 7.3249 | 11.4305 | 0.64082 | 7.3249 | 11.4305 | 0.64082 | 8.5629 | 13.3624 | 0.64082 | 0.9808%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 111 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 15.6409 | 0 | 0 | 15.6409 | 0 | 13.5774 | 1.8415 | 7.373 | 13.5774 | 1.8415 | 7.373 | 15.8721 | 2.1527 | 7.373 | 0.9867%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 480 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 10.7692 | 0 | 0 | 10.7692 | 0 | 9.3484 | 7.9632 | 1.1739 | 9.3484 | 7.9632 | 1.1739 | 10.9284 | 9.3091 | 1.1739 | 0.9646%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 909 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 61.5832 | 0 | 0 | 61.5832 | 0 | 53.4582 | 15.0803 | 3.5449 | 53.4582 | 15.0803 | 3.5449 | 62.4933 | 17.6291 | 3.5449 | 0.9824%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 674 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.132 | 0 | 0 | 7.132 | 0 | 6.1911 | 11.1817 | 0.55368 | 6.1911 | 11.1817 | 0.55368 | 7.2374 | 13.0715 | 0.55368 | 0.6927%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 61 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 3.7175 | 0 | 0 | 3.7175 | 0 | 3.227 | 1.012 | 3.1888 | 3.227 | 1.012 | 3.1888 | 3.7724 | 1.183 | 3.1888 | 0.9876%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 261 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 11.6245 | 0 | 0 | 11.6245 | 0 | 10.0908 | 4.33 | 2.3304 | 10.0908 | 4.33 | 2.3304 | 11.7962 | 5.0618 | 2.3304 | 0.9838%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 103 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 7.8109 | 0 | 0 | 7.8109 | 0 | 6.7803 | 1.7088 | 3.968 | 6.7803 | 1.7088 | 3.968 | 7.9263 | 1.9976 | 3.968 | 0.987%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 102 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 3.6496 | 0 | 0 | 3.6496 | 0 | 3.1681 | 1.6922 | 1.8722 | 3.1681 | 1.6922 | 1.8722 | 3.7035 | 1.9782 | 1.8722 | 0.9688%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 1050 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 43.4491 | 0 | 0 | 43.4491 | 0 | 37.7167 | 17.4195 | 2.1652 | 37.7167 | 17.4195 | 2.1652 | 44.0912 | 20.3636 | 2.1652 | 0.9791%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 538 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 37.0761 | 0 | 0 | 37.0761 | 0 | 32.1844 | 8.9254 | 3.6059 | 32.1844 | 8.9254 | 3.6059 | 37.624 | 10.4339 | 3.6059 | 0.9907%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 555 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 35.4905 | 0 | 0 | 35.4905 | 0 | 30.8081 | 9.2075 | 3.346 | 30.8081 | 9.2075 | 3.346 | 36.015 | 10.7636 | 3.346 | 0.9682%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 301 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 6.3344 | 0 | 0 | 6.3344 | 0 | 5.4986 | 4.9936 | 1.1011 | 5.4986 | 4.9936 | 1.1011 | 6.428 | 5.8376 | 1.1011 | 0.6596%
2028 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 1 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 1.1925 | 0 | 0 | 1.1925 | 0 | 1.0352 | 0.01659 | 62.3973 | 1.0352 | 0.01659 | 62.3973 | 1.2101 | 0.019394 | 62.3973 | 0.295%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 883 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 32.0224 | 0 | 0 | 32.0224 | 0 | 27.7975 | 14.649 | 1.8976 | 27.7975 | 14.649 | 1.8976 | 32.4956 | 17.1248 | 1.8976 | 0.9454%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 296 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 12.5849 | 0 | 0 | 12.5849 | 0 | 10.9245 | 4.9106 | 2.2247 | 10.9245 | 4.9106 | 2.2247 | 12.7709 | 5.7406 | 2.2247 | 0.9251%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 20 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 1.0329 | 0 | 0 | 1.0329 | 0 | 0.89663 | 0.3318 | 2.7023 | 0.89663 | 0.3318 | 2.7023 | 1.0482 | 0.38788 | 2.7023 | 0.9818%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 35.9751 | 0 | 0 | 35.9751 | 0 | 31.2287 | 10.6342 | 2.9366 | 31.2287 | 10.6342 | 2.9366 | 36.5068 | 12.4315 | 2.9366 | 0.9585%
2028 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 0.42886 | 0 | 0 | 0.42886 | 0 | 0.37228 | 0.14931 | 2.4933 | 0.37228 | 0.14931 | 2.4933 | 0.4352 | 0.17455 | 2.4933 | 0.8666%
2028 | 280 | 280-24AE | Tier-2 | Tier-2---12 | Tier-2---4 | 6 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.11503 | 0 | 0 | 0.11503 | 0 | 0.099855 | 0.09954 | 1.0032 | 0.099855 | 0.09954 | 1.0032 | 0.11673 | 0.11636 | 1.0032 | 0.03145%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 52.2302 | 0 | 0 | 52.2302 | 0 | 45.3392 | 1.8083 | 25.0727 | 45.3392 | 1.8083 | 25.0727 | 53.0021 | 2.1139 | 25.0727 | 0.9855%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 284 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 17.6795 | 0 | 0 | 17.6795 | 0 | 15.347 | 4.7116 | 3.2573 | 15.347 | 4.7116 | 3.2573 | 17.9408 | 5.5079 | 3.2573 | 0.878%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 4.5389 | 0 | 0 | 4.5389 | 0 | 3.9401 | 0.01659 | 237.4971 | 3.9401 | 0.01659 | 237.4971 | 4.606 | 0.019394 | 237.4971 | 0.9431%
2028 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 18 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 0.41062 | 0 | 0 | 0.41062 | 0 | 0.35645 | 0.29862 | 1.1936 | 0.35645 | 0.29862 | 1.1936 | 0.41669 | 0.34909 | 1.1936 | 0.9823%
2028 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 375 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 5.1142 | 0 | 0 | 5.1142 | 0 | 4.4395 | 6.2213 | 0.71359 | 4.4395 | 6.2213 | 0.71359 | 5.1898 | 7.2727 | 0.71359 | 0.9288%
2028 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 62 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.025507 | 0 | 0 | 0.025507 | 0 | 0.022142 | 1.0286 | 0.021527 | 0.022142 | 1.0286 | 0.021527 | 0.025884 | 1.2024 | 0.021527 | 0.7897%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 63 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 4.564 | 0 | 0 | 4.564 | 0 | 3.9618 | 1.0452 | 3.7906 | 3.9618 | 1.0452 | 3.7906 | 4.6314 | 1.2218 | 3.7906 | 0.9948%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 269 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 6.969 | 0 | 0 | 6.969 | 0 | 6.0495 | 4.4627 | 1.3556 | 6.0495 | 4.4627 | 1.3556 | 7.072 | 5.217 | 1.3556 | 0.9241%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 521 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 21.9229 | 0 | 0 | 21.9229 | 0 | 19.0305 | 8.6434 | 2.2017 | 19.0305 | 8.6434 | 2.2017 | 22.2468 | 10.1042 | 2.2017 | 0.9107%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 1014 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 45.507 | 0 | 0 | 45.507 | 0 | 39.503 | 16.8223 | 2.3483 | 39.503 | 16.8223 | 2.3483 | 46.1795 | 19.6654 | 2.3483 | 0.9555%
2028 | 308 | 308-485AE | Tier-2 | Tier-2---15 | Tier-2---8 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.043838 | 0 | 0 | 0.043838 | 0 | 0.038054 | 0.08295 | 0.45876 | 0.038054 | 0.08295 | 0.45876 | 0.044485 | 0.09697 | 0.45876 | 0.02775%
2028 | 308 | 308-486AE | Tier-2 | Tier-2---16 | Tier-2---8 | 2 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.039249 | 0 | 0 | 0.039249 | 0 | 0.034071 | 0.03318 | 1.0268 | 0.034071 | 0.03318 | 1.0268 | 0.039829 | 0.038788 | 1.0268 | 0.02383%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 16 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16066 | 0.26544 | 0.60525 | 0.16066 | 0.26544 | 0.60525 | 0.18781 | 0.3103 | 0.60525 | 0.1937%
2028 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 5 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.39124 | 0 | 0 | 0.39124 | 0 | 0.33962 | 0.08295 | 4.0943 | 0.33962 | 0.08295 | 4.0943 | 0.39702 | 0.09697 | 4.0943 | 0.8469%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 34 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.077066 | 0 | 0 | 0.077066 | 0 | 0.066898 | 0.56406 | 0.1186 | 0.066898 | 0.56406 | 0.1186 | 0.078204 | 0.65939 | 0.1186 | 0.4938%
2028 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 22 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 0.45364 | 0 | 0 | 0.45364 | 0 | 0.39379 | 0.36498 | 1.0789 | 0.39379 | 0.36498 | 1.0789 | 0.46034 | 0.42667 | 1.0789 | 0.1628%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 347 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.037391 | 0 | 0 | 0.037391 | 0 | 0.032458 | 5.7567 | 0.0056382 | 0.032458 | 5.7567 | 0.0056382 | 0.037943 | 6.7297 | 0.0056382 | 0.02339%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 50 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0030592 | 0 | 0 | 0.0030592 | 0 | 0.0026556 | 0.8295 | 0.0032015 | 0.0026556 | 0.8295 | 0.0032015 | 0.0031044 | 0.9697 | 0.0032015 | 0.001514%
2028 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.1439 | 0 | 0 | 0.1439 | 0 | 0.12491 | 0.13272 | 0.94116 | 0.12491 | 0.13272 | 0.94116 | 0.14602 | 0.15515 | 0.94116 | 0.981%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 424 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 2.0881 | 0 | 0 | 2.0881 | 0 | 1.8126 | 7.0342 | 0.25769 | 1.8126 | 7.0342 | 0.25769 | 2.119 | 8.223 | 0.25769 | 0.995%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 17 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 3.0022 | 0 | 0 | 3.0022 | 0 | 2.6061 | 0.28203 | 9.2405 | 2.6061 | 0.28203 | 9.2405 | 3.0466 | 0.3297 | 9.2405 | 0.9927%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 2015 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 34.3937 | 0 | 0 | 34.3937 | 0 | 29.856 | 33.4289 | 0.89312 | 29.856 | 33.4289 | 0.89312 | 34.902 | 39.0787 | 0.89312 | 0.9548%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 2337 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 136.1324 | 0 | 0 | 136.1324 | 0 | 118.1718 | 38.7709 | 3.048 | 118.1718 | 38.7709 | 3.048 | 138.1442 | 45.3236 | 3.048 | 0.9814%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 2775 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 54.0287 | 0 | 0 | 54.0287 | 0 | 46.9005 | 46.0373 | 1.0187 | 46.9005 | 46.0373 | 1.0187 | 54.8272 | 53.8181 | 1.0187 | 0.9699%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 1107 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 134.2497 | 0 | 0 | 134.2497 | 0 | 116.5375 | 18.3651 | 6.3456 | 116.5375 | 18.3651 | 6.3456 | 136.2336 | 21.4691 | 6.3456 | 0.9928%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 1576 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 110.754 | 0 | 0 | 110.754 | 0 | 96.1417 | 26.1459 | 3.6771 | 96.1417 | 26.1459 | 3.6771 | 112.3908 | 30.5648 | 3.6771 | 0.9888%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 1026 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 233.4104 | 0 | 0 | 233.4104 | 0 | 202.6155 | 17.0214 | 11.9036 | 202.6155 | 17.0214 | 11.9036 | 236.8598 | 19.8982 | 11.9036 | 0.9925%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 243 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 91.1965 | 0 | 0 | 91.1965 | 0 | 79.1645 | 4.0314 | 19.6371 | 79.1645 | 4.0314 | 19.6371 | 92.5442 | 4.7127 | 19.6371 | 0.9973%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 1556 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 184.9515 | 0 | 0 | 184.9515 | 0 | 160.5499 | 25.8141 | 6.2195 | 160.5499 | 25.8141 | 6.2195 | 187.6847 | 30.1769 | 6.2195 | 0.9936%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 951 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 89.9014 | 0 | 0 | 89.9014 | 0 | 78.0402 | 15.7771 | 4.9464 | 78.0402 | 15.7771 | 4.9464 | 91.2299 | 18.4436 | 4.9464 | 0.9749%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 266 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 24.9844 | 0 | 0 | 24.9844 | 0 | 21.6881 | 4.4129 | 4.9147 | 21.6881 | 4.4129 | 4.9147 | 25.3536 | 5.1588 | 4.9147 | 0.9918%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 93 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 22.1415 | 0 | 0 | 22.1415 | 0 | 19.2203 | 1.5429 | 12.4575 | 19.2203 | 1.5429 | 12.4575 | 22.4687 | 1.8036 | 12.4575 | 0.9993%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 172 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 17.6622 | 0 | 0 | 17.6622 | 0 | 15.3319 | 2.8535 | 5.3731 | 15.3319 | 2.8535 | 5.3731 | 17.9232 | 3.3358 | 5.3731 | 0.8869%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 138 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 42.9605 | 0 | 0 | 42.9605 | 0 | 37.2925 | 2.2894 | 16.289 | 37.2925 | 2.2894 | 16.289 | 43.5954 | 2.6764 | 16.289 | 0.943%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 2.9227 | 0 | 0 | 2.9227 | 0 | 2.5371 | 0.8295 | 3.0586 | 2.5371 | 0.8295 | 3.0586 | 2.9659 | 0.9697 | 3.0586 | 0.6284%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 379 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 134.576 | 0 | 0 | 134.576 | 0 | 116.8208 | 6.2876 | 18.5795 | 116.8208 | 6.2876 | 18.5795 | 136.5648 | 7.3503 | 18.5795 | 0.9943%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 1602 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 203.3935 | 0 | 0 | 203.3935 | 0 | 176.5588 | 26.5772 | 6.6432 | 176.5588 | 26.5772 | 6.6432 | 206.3992 | 31.0691 | 6.6432 | 0.9917%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 226 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 32.3479 | 0 | 0 | 32.3479 | 0 | 28.0801 | 3.7493 | 7.4893 | 28.0801 | 3.7493 | 7.4893 | 32.826 | 4.383 | 7.4893 | 0.8854%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 580 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 73.8814 | 0 | 0 | 73.8814 | 0 | 64.1338 | 9.6222 | 6.6652 | 64.1338 | 9.6222 | 6.6652 | 74.9732 | 11.2485 | 6.6652 | 0.985%
2028 | 355 | 355-65R | Tier-2 | Tier-2---21 | Tier-2---24 | 2 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.00030886 | 0 | 0 | 0.00030886 | 0 | 0.00026811 | 0.03318 | 0.0080805 | 0.00026811 | 0.03318 | 0.0080805 | 0.00031343 | 0.038788 | 0.0080805 | 0.4611%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 248 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 13.5793 | 0 | 0 | 13.5793 | 0 | 11.7877 | 4.1143 | 2.865 | 11.7877 | 4.1143 | 2.865 | 13.78 | 4.8097 | 2.865 | 0.7994%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 346 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 53.3637 | 0 | 0 | 53.3637 | 0 | 46.3232 | 5.7401 | 8.07 | 46.3232 | 5.7401 | 8.07 | 54.1523 | 6.7103 | 8.07 | 0.9814%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 1320 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 156.5456 | 0 | 0 | 156.5456 | 0 | 135.8918 | 21.8988 | 6.2054 | 135.8918 | 21.8988 | 6.2054 | 158.859 | 25.6 | 6.2054 | 0.9776%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 1086 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 88.6821 | 0 | 0 | 88.6821 | 0 | 76.9818 | 18.0168 | 4.2728 | 76.9818 | 18.0168 | 4.2728 | 89.9926 | 21.0618 | 4.2728 | 0.9541%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 47 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 12.3945 | 0 | 0 | 12.3945 | 0 | 10.7592 | 0.77973 | 13.7986 | 10.7592 | 0.77973 | 13.7986 | 12.5776 | 0.91151 | 13.7986 | 0.9906%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 50 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 50.8246 | 0 | 0 | 50.8246 | 0 | 44.119 | 0.8295 | 53.1875 | 44.119 | 0.8295 | 53.1875 | 51.5757 | 0.9697 | 53.1875 | 0.9968%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 10 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 8.3925 | 0 | 0 | 8.3925 | 0 | 7.2852 | 0.1659 | 43.9134 | 7.2852 | 0.1659 | 43.9134 | 8.5165 | 0.19394 | 43.9134 | 0.9549%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 489 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 166.6498 | 0 | 0 | 166.6498 | 0 | 144.6629 | 8.1125 | 17.8321 | 144.6629 | 8.1125 | 17.8321 | 169.1126 | 9.4836 | 17.8321 | 0.9879%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 938 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 172.4977 | 0 | 0 | 172.4977 | 0 | 149.7393 | 15.5614 | 9.6225 | 149.7393 | 15.5614 | 9.6225 | 175.0469 | 18.1915 | 9.6225 | 0.9747%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 1053 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 101.2349 | 0 | 0 | 101.2349 | 0 | 87.8785 | 17.4693 | 5.0305 | 87.8785 | 17.4693 | 5.0305 | 102.731 | 20.4218 | 5.0305 | 0.9704%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 650 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 114.9965 | 0 | 0 | 114.9965 | 0 | 99.8244 | 10.7835 | 9.2571 | 99.8244 | 10.7835 | 9.2571 | 116.6959 | 12.606 | 9.2571 | 0.9781%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 29 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 5.8283 | 0 | 0 | 5.8283 | 0 | 5.0594 | 0.48111 | 10.516 | 5.0594 | 0.48111 | 10.516 | 5.9144 | 0.56242 | 10.516 | 0.9721%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 56 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 13.4008 | 0 | 0 | 13.4008 | 0 | 11.6327 | 0.92904 | 12.5212 | 11.6327 | 0.92904 | 12.5212 | 13.5988 | 1.0861 | 12.5212 | 0.9966%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 437 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 370.7306 | 0 | 0 | 370.7306 | 0 | 321.8183 | 7.2498 | 44.3897 | 321.8183 | 7.2498 | 44.3897 | 376.2093 | 8.4751 | 44.3897 | 0.9859%
2028 | 386 | 386-25R | Tier-2 | Tier-2---15 | Tier-2---9 | 3 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 0.50797 | 0 | 0 | 0.50797 | 0 | 0.44095 | 0.04977 | 8.8597 | 0.44095 | 0.04977 | 8.8597 | 0.51547 | 0.058182 | 8.8597 | 0.3536%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 79 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 12.9521 | 0 | 0 | 12.9521 | 0 | 11.2433 | 1.3106 | 8.5786 | 11.2433 | 1.3106 | 8.5786 | 13.1435 | 1.5321 | 8.5786 | 0.8901%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 87 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.7375 | 0 | 0 | 1.7375 | 0 | 1.5082 | 1.4433 | 1.045 | 1.5082 | 1.4433 | 1.045 | 1.7631 | 1.6873 | 1.045 | 0.1879%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 1753 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 27.6618 | 0 | 0 | 27.6618 | 0 | 24.0122 | 29.0823 | 0.82566 | 24.0122 | 29.0823 | 0.82566 | 28.0706 | 33.9975 | 0.82566 | 0.8818%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 728 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 18.173 | 0 | 0 | 18.173 | 0 | 15.7753 | 12.0775 | 1.3062 | 15.7753 | 12.0775 | 1.3062 | 18.4415 | 14.1188 | 1.3062 | 0.9783%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 1526 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 62.7232 | 0 | 0 | 62.7232 | 0 | 54.4478 | 25.3164 | 2.1507 | 54.4478 | 25.3164 | 2.1507 | 63.6501 | 29.5951 | 2.1507 | 0.9847%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 68 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 12.9604 | 0 | 0 | 12.9604 | 0 | 11.2505 | 1.1281 | 9.9727 | 11.2505 | 1.1281 | 9.9727 | 13.1519 | 1.3188 | 9.9727 | 0.9597%
2028 | 434 | 434-301 | Tier-2 | Tier-2---17 | Tier-2---11 | 115 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 0.7032 | 0 | 0 | 0.7032 | 0 | 0.61043 | 1.9079 | 0.31996 | 0.61043 | 1.9079 | 0.31996 | 0.7136 | 2.2303 | 0.31996 | 0.9953%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 376 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 34.284 | 0 | 0 | 34.284 | 0 | 29.7608 | 6.2378 | 4.771 | 29.7608 | 6.2378 | 4.771 | 34.7907 | 7.2921 | 4.771 | 0.9745%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 5.3172 | 0 | 0 | 5.3172 | 0 | 4.6157 | 0.79632 | 5.7963 | 4.6157 | 0.79632 | 5.7963 | 5.3958 | 0.93091 | 5.7963 | 0.9134%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 115 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 46.5524 | 0 | 0 | 46.5524 | 0 | 40.4105 | 1.9079 | 21.1812 | 40.4105 | 1.9079 | 21.1812 | 47.2404 | 2.2303 | 21.1812 | 0.98%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 52.7252 | 0 | 0 | 52.7252 | 0 | 45.7689 | 1.0452 | 43.7908 | 45.7689 | 1.0452 | 43.7908 | 53.5043 | 1.2218 | 43.7908 | 0.9857%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 909 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 17.6314 | 0 | 0 | 17.6314 | 0 | 15.3052 | 15.0803 | 1.0149 | 15.3052 | 15.0803 | 1.0149 | 17.8919 | 17.6291 | 1.0149 | 0.9609%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 31 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.015379 | 0 | 0 | 0.015379 | 0 | 0.01335 | 0.51429 | 0.025959 | 0.01335 | 0.51429 | 0.025959 | 0.015607 | 0.60121 | 0.025959 | 0.01745%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 866 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.2878 | 14.367 | 0.43766 | 6.2878 | 14.367 | 0.43766 | 7.3505 | 16.7951 | 0.43766 | 0.8492%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 664 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 3.049 | 0 | 0 | 3.049 | 0 | 2.6468 | 11.0158 | 0.24027 | 2.6468 | 11.0158 | 0.24027 | 3.0941 | 12.8776 | 0.24027 | 0.5795%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 1856 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 102.3867 | 0 | 0 | 102.3867 | 0 | 88.8783 | 30.7911 | 2.8865 | 88.8783 | 30.7911 | 2.8865 | 103.8998 | 35.9951 | 2.8865 | 0.8848%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 38 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 6.8077 | 0 | 0 | 6.8077 | 0 | 5.9095 | 0.63042 | 9.3739 | 5.9095 | 0.63042 | 9.3739 | 6.9083 | 0.73697 | 9.3739 | 0.9662%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 41 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 5.4407 | 0 | 0 | 5.4407 | 0 | 4.7229 | 0.68019 | 6.9435 | 4.7229 | 0.68019 | 6.9435 | 5.5211 | 0.79515 | 6.9435 | 0.9893%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 289 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 4.3348 | 0 | 0 | 4.3348 | 0 | 3.7629 | 4.7945 | 0.78483 | 3.7629 | 4.7945 | 0.78483 | 4.3989 | 5.6048 | 0.78483 | 0.9131%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 204 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 0.72107 | 0 | 0 | 0.72107 | 0 | 0.62594 | 3.3844 | 0.18495 | 0.62594 | 3.3844 | 0.18495 | 0.73173 | 3.9564 | 0.18495 | 0.51%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 6 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 3.2255 | 0 | 0 | 3.2255 | 0 | 2.8 | 0.09954 | 28.1292 | 2.8 | 0.09954 | 28.1292 | 3.2732 | 0.11636 | 28.1292 | 0.9662%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 33.3427 | 0 | 0 | 33.3427 | 0 | 28.9437 | 2.3392 | 12.3734 | 28.9437 | 2.3392 | 12.3734 | 33.8355 | 2.7345 | 12.3734 | 0.9767%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 594 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 4.0391 | 0 | 0 | 4.0391 | 0 | 3.5062 | 9.8545 | 0.3558 | 3.5062 | 9.8545 | 0.3558 | 4.0988 | 11.52 | 0.3558 | 0.7071%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 390 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 91.4684 | 0 | 0 | 91.4684 | 0 | 79.4005 | 6.4701 | 12.2719 | 79.4005 | 6.4701 | 12.2719 | 92.8201 | 7.5636 | 12.2719 | 0.9496%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 252 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 69.6833 | 0 | 0 | 69.6833 | 0 | 60.4896 | 4.1807 | 14.4688 | 60.4896 | 4.1807 | 14.4688 | 70.713 | 4.8873 | 14.4688 | 0.9611%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 171 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 14.2269 | 0 | 0 | 14.2269 | 0 | 12.3499 | 2.8369 | 4.3533 | 12.3499 | 2.8369 | 4.3533 | 14.4371 | 3.3164 | 4.3533 | 0.8872%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 454 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 101.6186 | 0 | 0 | 101.6186 | 0 | 88.2116 | 7.5319 | 11.7118 | 88.2116 | 7.5319 | 11.7118 | 103.1203 | 8.8048 | 11.7118 | 0.9569%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 208 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 14.9687 | 0 | 0 | 14.9687 | 0 | 12.9938 | 3.4507 | 3.7655 | 12.9938 | 3.4507 | 3.7655 | 15.1899 | 4.0339 | 3.7655 | 0.8473%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 235 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 32.2026 | 0 | 0 | 32.2026 | 0 | 27.954 | 3.8987 | 7.1702 | 27.954 | 3.8987 | 7.1702 | 32.6785 | 4.5576 | 7.1702 | 0.8754%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 381 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 38.9585 | 0 | 0 | 38.9585 | 0 | 33.8185 | 6.3208 | 5.3504 | 33.8185 | 6.3208 | 5.3504 | 39.5342 | 7.3891 | 5.3504 | 0.8812%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 13.145 | 0 | 0 | 13.145 | 0 | 11.4107 | 0.46452 | 24.5645 | 11.4107 | 0.46452 | 24.5645 | 13.3393 | 0.54303 | 24.5645 | 0.9724%
2028 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 7 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.16597 | 0 | 0 | 0.16597 | 0 | 0.14408 | 0.11613 | 1.2406 | 0.14408 | 0.11613 | 1.2406 | 0.16843 | 0.13576 | 1.2406 | 0.9941%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 27 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 11.7999 | 0 | 0 | 11.7999 | 0 | 10.2431 | 0.44793 | 22.8677 | 10.2431 | 0.44793 | 22.8677 | 11.9743 | 0.52364 | 22.8677 | 0.9739%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 154 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 24.009 | 0 | 0 | 24.009 | 0 | 20.8414 | 2.5549 | 8.1575 | 20.8414 | 2.5549 | 8.1575 | 24.3638 | 2.9867 | 8.1575 | 0.9191%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 269 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 11.8066 | 0 | 0 | 11.8066 | 0 | 10.2489 | 4.4627 | 2.2966 | 10.2489 | 4.4627 | 2.2966 | 11.9811 | 5.217 | 2.2966 | 0.557%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 267 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 3.9665 | 0 | 0 | 3.9665 | 0 | 3.4431 | 4.4295 | 0.77732 | 3.4431 | 4.4295 | 0.77732 | 4.0251 | 5.1782 | 0.77732 | 0.7618%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 191 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 4.9907 | 0 | 0 | 4.9907 | 0 | 4.3323 | 3.1687 | 1.3672 | 4.3323 | 3.1687 | 1.3672 | 5.0645 | 3.7042 | 1.3672 | 0.7912%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 744 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 83.472 | 0 | 0 | 83.472 | 0 | 72.4591 | 12.343 | 5.8705 | 72.4591 | 12.343 | 5.8705 | 84.7056 | 14.4291 | 5.8705 | 0.9168%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 525 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 52.7368 | 0 | 0 | 52.7368 | 0 | 45.779 | 8.7098 | 5.2561 | 45.779 | 8.7098 | 5.2561 | 53.5162 | 10.1818 | 5.2561 | 0.9343%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 964 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 60.9003 | 0 | 0 | 60.9003 | 0 | 52.8654 | 15.9928 | 3.3056 | 52.8654 | 15.9928 | 3.3056 | 61.8002 | 18.6957 | 3.3056 | 0.9049%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 62 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 14.5023 | 0 | 0 | 14.5023 | 0 | 12.5889 | 1.0286 | 12.2391 | 12.5889 | 1.0286 | 12.2391 | 14.7166 | 1.2024 | 12.2391 | 0.9697%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 36 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 6.0466 | 0 | 0 | 6.0466 | 0 | 5.2488 | 0.59724 | 8.7884 | 5.2488 | 0.59724 | 8.7884 | 6.1359 | 0.69818 | 8.7884 | 0.967%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 197 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 51.9614 | 0 | 0 | 51.9614 | 0 | 45.1059 | 3.2682 | 13.8013 | 45.1059 | 3.2682 | 13.8013 | 52.7293 | 3.8206 | 13.8013 | 0.9877%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 250 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 22.1671 | 0 | 0 | 22.1671 | 0 | 19.2425 | 4.1475 | 4.6395 | 19.2425 | 4.1475 | 4.6395 | 22.4947 | 4.8485 | 4.6395 | 0.9555%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 78 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 2.8815 | 0 | 0 | 2.8815 | 0 | 2.5014 | 1.294 | 1.933 | 2.5014 | 1.294 | 1.933 | 2.9241 | 1.5127 | 1.933 | 0.9711%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 633 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 82.1048 | 0 | 0 | 82.1048 | 0 | 71.2723 | 10.5015 | 6.7869 | 71.2723 | 10.5015 | 6.7869 | 83.3182 | 12.2763 | 6.7869 | 0.9923%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 138 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 7.3491 | 0 | 0 | 7.3491 | 0 | 6.3795 | 2.2894 | 2.7865 | 6.3795 | 2.2894 | 2.7865 | 7.4577 | 2.6764 | 2.7865 | 0.9277%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 158 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 10.7852 | 0 | 0 | 10.7852 | 0 | 9.3622 | 2.6212 | 3.5717 | 9.3622 | 2.6212 | 3.5717 | 10.9446 | 3.0642 | 3.5717 | 0.9525%
2028 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 7 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 1.7471 | 0 | 0 | 1.7471 | 0 | 1.5166 | 0.11613 | 13.0591 | 1.5166 | 0.11613 | 13.0591 | 1.7729 | 0.13576 | 13.0591 | 0.3253%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 26 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 1.3708 | 0 | 0 | 1.3708 | 0 | 1.19 | 0.43134 | 2.7588 | 1.19 | 0.43134 | 2.7588 | 1.3911 | 0.50424 | 2.7588 | 0.999%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 3 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 6.2494 | 0 | 0 | 6.2494 | 0 | 5.4249 | 0.04977 | 108.9992 | 5.4249 | 0.04977 | 108.9992 | 6.3418 | 0.058182 | 108.9992 | 0.999%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 1.8093 | 0 | 0 | 1.8093 | 0 | 1.5706 | 0.19908 | 7.889 | 1.5706 | 0.19908 | 7.889 | 1.836 | 0.23273 | 7.889 | 0.9984%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 354 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 28.2188 | 0 | 0 | 28.2188 | 0 | 24.4958 | 5.8729 | 4.171 | 24.4958 | 5.8729 | 4.171 | 28.6359 | 6.8654 | 4.171 | 0.9993%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 36 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 0.37945 | 0 | 0 | 0.37945 | 0 | 0.32939 | 0.59724 | 0.55152 | 0.32939 | 0.59724 | 0.55152 | 0.38506 | 0.69818 | 0.55152 | 0.9723%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 363 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 34.308 | 0 | 0 | 34.308 | 0 | 29.7816 | 6.0222 | 4.9453 | 29.7816 | 6.0222 | 4.9453 | 34.815 | 7.04 | 4.9453 | 0.997%
2028 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 0.85684 | 0 | 0 | 0.85684 | 0 | 0.74379 | 0.01659 | 44.8336 | 0.74379 | 0.01659 | 44.8336 | 0.8695 | 0.019394 | 44.8336 | 0.9735%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 69 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 13.6477 | 0 | 0 | 13.6477 | 0 | 11.8471 | 1.1447 | 10.3494 | 11.8471 | 1.1447 | 10.3494 | 13.8494 | 1.3382 | 10.3494 | 0.9902%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 415 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 51.7697 | 0 | 0 | 51.7697 | 0 | 44.9395 | 6.8849 | 6.5273 | 44.9395 | 6.8849 | 6.5273 | 52.5347 | 8.0485 | 6.5273 | 0.9833%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 887 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 166.3498 | 0 | 0 | 166.3498 | 0 | 144.4024 | 14.7153 | 9.8131 | 144.4024 | 14.7153 | 9.8131 | 168.8081 | 17.2024 | 9.8131 | 0.9937%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 127 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 40.3917 | 0 | 0 | 40.3917 | 0 | 35.0626 | 2.1069 | 16.6416 | 35.0626 | 2.1069 | 16.6416 | 40.9886 | 2.463 | 16.6416 | 0.9496%
2028 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 58 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 1.7293 | 0 | 0 | 1.7293 | 0 | 1.5011 | 0.96222 | 1.5601 | 1.5011 | 0.96222 | 1.5601 | 1.7549 | 1.1248 | 1.5601 | 0.216%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 163 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 2.0333 | 0 | 0 | 2.0333 | 0 | 1.7651 | 2.7042 | 0.65272 | 1.7651 | 2.7042 | 0.65272 | 2.0634 | 3.1612 | 0.65272 | 0.9963%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 78 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 7.3008 | 0 | 0 | 7.3008 | 0 | 6.3375 | 1.294 | 4.8976 | 6.3375 | 1.294 | 4.8976 | 7.4087 | 1.5127 | 4.8976 | 0.9951%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 1241 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 28.9972 | 0 | 0 | 28.9972 | 0 | 25.1714 | 20.5882 | 1.2226 | 25.1714 | 20.5882 | 1.2226 | 29.4257 | 24.0678 | 1.2226 | 0.9734%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 524 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 14.4879 | 0 | 0 | 14.4879 | 0 | 12.5764 | 8.6932 | 1.4467 | 12.5764 | 8.6932 | 1.4467 | 14.702 | 10.1624 | 1.4467 | 0.9797%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 1235 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.5237 | 0 | 0 | 25.5237 | 0 | 22.1562 | 20.4887 | 1.0814 | 22.1562 | 20.4887 | 1.0814 | 25.9009 | 23.9515 | 1.0814 | 0.9676%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 1467 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 31.6539 | 0 | 0 | 31.6539 | 0 | 27.4777 | 24.3376 | 1.129 | 27.4777 | 24.3376 | 1.129 | 32.1217 | 28.4509 | 1.129 | 0.9272%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 521 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 16.0482 | 0 | 0 | 16.0482 | 0 | 13.9309 | 8.6434 | 1.6117 | 13.9309 | 8.6434 | 1.6117 | 16.2854 | 10.1042 | 1.6117 | 0.9829%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 969 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 65.4102 | 0 | 0 | 65.4102 | 0 | 56.7803 | 16.0757 | 3.5321 | 56.7803 | 16.0757 | 3.5321 | 66.3768 | 18.7927 | 3.5321 | 0.9672%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 556 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 5.7874 | 0 | 0 | 5.7874 | 0 | 5.0238 | 9.224 | 0.54465 | 5.0238 | 9.224 | 0.54465 | 5.8729 | 10.783 | 0.54465 | 0.7734%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 511 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 20.1122 | 0 | 0 | 20.1122 | 0 | 17.4587 | 8.4775 | 2.0594 | 17.4587 | 8.4775 | 2.0594 | 20.4094 | 9.9103 | 2.0594 | 0.9648%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 171 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 1.9301 | 0 | 0 | 1.9301 | 0 | 1.6754 | 2.8369 | 0.59058 | 1.6754 | 2.8369 | 0.59058 | 1.9586 | 3.3164 | 0.59058 | 0.7472%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 1723 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 48.2259 | 0 | 0 | 48.2259 | 0 | 41.8632 | 28.5846 | 1.4645 | 41.8632 | 28.5846 | 1.4645 | 48.9386 | 33.4157 | 1.4645 | 0.9649%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 616 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 19.95 | 0 | 0 | 19.95 | 0 | 17.3179 | 10.2194 | 1.6946 | 17.3179 | 10.2194 | 1.6946 | 20.2448 | 11.9467 | 1.6946 | 0.9757%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 944 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 109.7472 | 0 | 0 | 109.7472 | 0 | 95.2678 | 15.661 | 6.0831 | 95.2678 | 15.661 | 6.0831 | 111.3691 | 18.3079 | 6.0831 | 0.9669%
2028 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 417 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 7.2433 | 0 | 0 | 7.2433 | 0 | 6.2877 | 6.918 | 0.90888 | 6.2877 | 6.918 | 0.90888 | 7.3504 | 8.0873 | 0.90888 | 0.8931%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 1063 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 82.9064 | 0 | 0 | 82.9064 | 0 | 71.9681 | 17.6352 | 4.0809 | 71.9681 | 17.6352 | 4.0809 | 84.1316 | 20.6157 | 4.0809 | 0.9779%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 830 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 86.5741 | 0 | 0 | 86.5741 | 0 | 75.1519 | 13.7697 | 5.4578 | 75.1519 | 13.7697 | 5.4578 | 87.8535 | 16.097 | 5.4578 | 0.9936%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 820 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 55.5002 | 0 | 0 | 55.5002 | 0 | 48.1778 | 13.6038 | 3.5415 | 48.1778 | 13.6038 | 3.5415 | 56.3204 | 15.903 | 3.5415 | 0.9878%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 582 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 121.6568 | 0 | 0 | 121.6568 | 0 | 105.606 | 9.6554 | 10.9375 | 105.606 | 9.6554 | 10.9375 | 123.4547 | 11.2873 | 10.9375 | 0.9938%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 1580 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 89.2713 | 0 | 0 | 89.2713 | 0 | 77.4933 | 26.2122 | 2.9564 | 77.4933 | 26.2122 | 2.9564 | 90.5906 | 30.6424 | 2.9564 | 0.9905%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 100 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 0.48494 | 0 | 0 | 0.48494 | 0 | 0.42096 | 1.659 | 0.25374 | 0.42096 | 1.659 | 0.25374 | 0.4921 | 1.9394 | 0.25374 | 0.4302%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 89 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 0.26355 | 0 | 0 | 0.26355 | 0 | 0.22878 | 1.4765 | 0.15494 | 0.22878 | 1.4765 | 0.15494 | 0.26744 | 1.7261 | 0.15494 | 0.2253%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 1782 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 54.3914 | 0 | 0 | 54.3914 | 0 | 47.2153 | 29.5634 | 1.5971 | 47.2153 | 29.5634 | 1.5971 | 55.1952 | 34.56 | 1.5971 | 0.9644%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 214 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 0.35698 | 0 | 0 | 0.35698 | 0 | 0.30988 | 3.5503 | 0.087283 | 0.30988 | 3.5503 | 0.087283 | 0.36225 | 4.1503 | 0.087283 | 0.117%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 525 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 54.5587 | 0 | 0 | 54.5587 | 0 | 47.3605 | 8.7098 | 5.4376 | 47.3605 | 8.7098 | 5.4376 | 55.365 | 10.1818 | 5.4376 | 0.9978%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 928 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 112.9156 | 0 | 0 | 112.9156 | 0 | 98.0181 | 15.3955 | 6.3667 | 98.0181 | 15.3955 | 6.3667 | 114.5843 | 17.9976 | 6.3667 | 0.9977%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 622 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 135.7207 | 0 | 0 | 135.7207 | 0 | 117.8145 | 10.319 | 11.4172 | 117.8145 | 10.319 | 11.4172 | 137.7264 | 12.063 | 11.4172 | 0.9899%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 500 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 86.4349 | 0 | 0 | 86.4349 | 0 | 75.0312 | 8.295 | 9.0453 | 75.0312 | 8.295 | 9.0453 | 87.7123 | 9.697 | 9.0453 | 0.982%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 1778 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 399.8502 | 0 | 0 | 399.8502 | 0 | 347.0961 | 29.497 | 11.7671 | 347.0961 | 29.497 | 11.7671 | 405.7593 | 34.4824 | 11.7671 | 0.9903%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 86 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 5.6479 | 0 | 0 | 5.6479 | 0 | 4.9027 | 1.4267 | 3.4363 | 4.9027 | 1.4267 | 3.4363 | 5.7314 | 1.6679 | 3.4363 | 0.6775%
2028 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 30 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 1.5269 | 0 | 0 | 1.5269 | 0 | 1.3255 | 0.4977 | 2.6632 | 1.3255 | 0.4977 | 2.6632 | 1.5495 | 0.58182 | 2.6632 | 0.9944%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 33 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.0085 | 0 | 0 | 5.0085 | 0 | 4.3477 | 0.54747 | 7.9414 | 4.3477 | 0.54747 | 7.9414 | 5.0825 | 0.64 | 7.9414 | 0.9632%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 37 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 0.49138 | 0 | 0 | 0.49138 | 0 | 0.42655 | 0.61383 | 0.6949 | 0.42655 | 0.61383 | 0.6949 | 0.49864 | 0.71757 | 0.6949 | 0.9941%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 1675 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 179.3878 | 0 | 0 | 179.3878 | 0 | 155.7203 | 27.7883 | 5.6038 | 155.7203 | 27.7883 | 5.6038 | 182.0388 | 32.4848 | 5.6038 | 0.9555%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 2456 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 255.88 | 0 | 0 | 255.88 | 0 | 222.1206 | 40.7451 | 5.4515 | 222.1206 | 40.7451 | 5.4515 | 259.6615 | 47.6315 | 5.4515 | 0.994%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 612 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 24.4359 | 0 | 0 | 24.4359 | 0 | 21.2119 | 10.1531 | 2.0892 | 21.2119 | 10.1531 | 2.0892 | 24.797 | 11.8691 | 2.0892 | 0.936%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 1200 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 39.2108 | 0 | 0 | 39.2108 | 0 | 34.0376 | 19.908 | 1.7097 | 34.0376 | 19.908 | 1.7097 | 39.7903 | 23.2727 | 1.7097 | 0.938%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 229 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 5.4252 | 0 | 0 | 5.4252 | 0 | 4.7095 | 3.7991 | 1.2396 | 4.7095 | 3.7991 | 1.2396 | 5.5054 | 4.4412 | 1.2396 | 0.8718%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 341 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 15.105 | 0 | 0 | 15.105 | 0 | 13.1122 | 5.6572 | 2.3178 | 13.1122 | 5.6572 | 2.3178 | 15.3283 | 6.6133 | 2.3178 | 0.9279%
2028 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 24 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 2.66 | 0 | 0 | 2.66 | 0 | 2.309 | 0.39816 | 5.7992 | 2.309 | 0.39816 | 5.7992 | 2.6993 | 0.46545 | 5.7992 | 0.8123%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 264 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 60.3347 | 0 | 0 | 60.3347 | 0 | 52.3744 | 4.3798 | 11.9583 | 52.3744 | 4.3798 | 11.9583 | 61.2263 | 5.12 | 11.9583 | 0.9729%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 753 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 151.1648 | 0 | 0 | 151.1648 | 0 | 131.2209 | 12.4923 | 10.5042 | 131.2209 | 12.4923 | 10.5042 | 153.3987 | 14.6036 | 10.5042 | 0.9856%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 265 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 24.1551 | 0 | 0 | 24.1551 | 0 | 20.9682 | 4.3964 | 4.7695 | 20.9682 | 4.3964 | 4.7695 | 24.5121 | 5.1394 | 4.7695 | 0.9864%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 248 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 56.425 | 0 | 0 | 56.425 | 0 | 48.9805 | 4.1143 | 11.9049 | 48.9805 | 4.1143 | 11.9049 | 57.2588 | 4.8097 | 11.9049 | 0.9841%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 528 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 104.1242 | 0 | 0 | 104.1242 | 0 | 90.3866 | 8.7595 | 10.3187 | 90.3866 | 8.7595 | 10.3187 | 105.663 | 10.24 | 10.3187 | 0.9831%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 469 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 91.4204 | 0 | 0 | 91.4204 | 0 | 79.3589 | 7.7807 | 10.1994 | 79.3589 | 7.7807 | 10.1994 | 92.7715 | 9.0957 | 10.1994 | 0.9843%
2028 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 16 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.17679 | 0 | 0 | 0.17679 | 0 | 0.15347 | 0.26544 | 0.57816 | 0.15347 | 0.26544 | 0.57816 | 0.1794 | 0.3103 | 0.57816 | 0.9934%
2028 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 1 | 100% | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.01659 | 0 | 0 | 0.01659 | 0 | 0 | 0.019394 | 0 | 0%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 392 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 31.2827 | 0 | 0 | 31.2827 | 0 | 27.1554 | 6.5033 | 4.1756 | 27.1554 | 6.5033 | 4.1756 | 31.745 | 7.6024 | 4.1756 | 0.9977%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 230 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 17.0112 | 0 | 0 | 17.0112 | 0 | 14.7668 | 3.8157 | 3.87 | 14.7668 | 3.8157 | 3.87 | 17.2626 | 4.4606 | 3.87 | 0.9957%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 98 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 19.3483 | 0 | 0 | 19.3483 | 0 | 16.7956 | 1.6258 | 10.3305 | 16.7956 | 1.6258 | 10.3305 | 19.6343 | 1.9006 | 10.3305 | 0.9986%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 843 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 21.9405 | 0 | 0 | 21.9405 | 0 | 19.0458 | 13.9854 | 1.3618 | 19.0458 | 13.9854 | 1.3618 | 22.2647 | 16.3491 | 1.3618 | 0.9923%
2028 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 39 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 0.41445 | 0 | 0 | 0.41445 | 0 | 0.35977 | 0.64701 | 0.55605 | 0.35977 | 0.64701 | 0.55605 | 0.42058 | 0.75636 | 0.55605 | 0.9749%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 493 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 143.1711 | 0 | 0 | 143.1711 | 0 | 124.2819 | 8.1789 | 15.1955 | 124.2819 | 8.1789 | 15.1955 | 145.2869 | 9.5612 | 15.1955 | 0.9856%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 33 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 71.672 | 0 | 0 | 71.672 | 0 | 62.2159 | 0.54747 | 113.6425 | 62.2159 | 0.54747 | 113.6425 | 72.7311 | 0.64 | 113.6425 | 0.9951%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 580 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 86.1468 | 0 | 0 | 86.1468 | 0 | 74.781 | 9.6222 | 7.7717 | 74.781 | 9.6222 | 7.7717 | 87.4199 | 11.2485 | 7.7717 | 0.9433%
2028 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 18 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 3.2278 | 0 | 0 | 3.2278 | 0 | 2.8019 | 0.29862 | 9.3829 | 2.8019 | 0.29862 | 9.3829 | 3.2755 | 0.34909 | 9.3829 | 0.9958%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 101 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.0122 | 0 | 0 | 31.0122 | 0 | 26.9206 | 1.6756 | 16.0663 | 26.9206 | 1.6756 | 16.0663 | 31.4705 | 1.9588 | 16.0663 | 0.9258%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 484 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 122.3039 | 0 | 0 | 122.3039 | 0 | 106.1678 | 8.0296 | 13.2221 | 106.1678 | 8.0296 | 13.2221 | 124.1113 | 9.3867 | 13.2221 | 0.9926%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 773 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 20.3417 | 0 | 0 | 20.3417 | 0 | 17.6579 | 12.8241 | 1.3769 | 17.6579 | 12.8241 | 1.3769 | 20.6423 | 14.9915 | 1.3769 | 0.9747%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 543 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 11.3972 | 0 | 0 | 11.3972 | 0 | 9.8935 | 9.0084 | 1.0983 | 9.8935 | 9.0084 | 1.0983 | 11.5656 | 10.5309 | 1.0983 | 0.7093%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 371 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 95.4762 | 0 | 0 | 95.4762 | 0 | 82.8796 | 6.1549 | 13.4656 | 82.8796 | 6.1549 | 13.4656 | 96.8872 | 7.1951 | 13.4656 | 0.9829%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 414 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 182.4513 | 0 | 0 | 182.4513 | 0 | 158.3796 | 6.8683 | 23.0596 | 158.3796 | 6.8683 | 23.0596 | 185.1476 | 8.0291 | 23.0596 | 0.989%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 54 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 25.487 | 0 | 0 | 25.487 | 0 | 22.1244 | 0.89586 | 24.6963 | 22.1244 | 0.89586 | 24.6963 | 25.8637 | 1.0473 | 24.6963 | 0.9937%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 446 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 53.3255 | 0 | 0 | 53.3255 | 0 | 46.29 | 7.3991 | 6.2561 | 46.29 | 7.3991 | 6.2561 | 54.1136 | 8.6497 | 6.2561 | 0.9631%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 868 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 182.4449 | 0 | 0 | 182.4449 | 0 | 158.374 | 14.4001 | 10.9981 | 158.374 | 14.4001 | 10.9981 | 185.1411 | 16.8339 | 10.9981 | 0.9714%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 82 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 29.4743 | 0 | 0 | 29.4743 | 0 | 25.5856 | 1.3604 | 18.8077 | 25.5856 | 1.3604 | 18.8077 | 29.9099 | 1.5903 | 18.8077 | 0.9712%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 410 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 198.2467 | 0 | 0 | 198.2467 | 0 | 172.0911 | 6.8019 | 25.3004 | 172.0911 | 6.8019 | 25.3004 | 201.1764 | 7.9515 | 25.3004 | 0.9923%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 23 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 1.2649 | 0 | 0 | 1.2649 | 0 | 1.098 | 0.38157 | 2.8777 | 1.098 | 0.38157 | 2.8777 | 1.2836 | 0.44606 | 2.8777 | 0.9928%
2028 | 834 | 834-887AE | Tier-2 | Tier-2---17 | Tier-2---13 | 2 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 0.69393 | 0 | 0 | 0.69393 | 0 | 0.60238 | 0.03318 | 18.1548 | 0.60238 | 0.03318 | 18.1548 | 0.70419 | 0.038788 | 18.1548 | 0.9864%
2028 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 59 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.12269 | 0 | 0 | 0.12269 | 0 | 0.1065 | 0.97881 | 0.10881 | 0.1065 | 0.97881 | 0.10881 | 0.1245 | 1.1442 | 0.10881 | 0.9883%
2028 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 131 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 1.3944 | 0 | 0 | 1.3944 | 0 | 1.2104 | 2.1733 | 0.55694 | 1.2104 | 2.1733 | 0.55694 | 1.415 | 2.5406 | 0.55694 | 0.9963%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 8 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.066497 | 0 | 0 | 0.066497 | 0 | 0.057723 | 0.13272 | 0.43493 | 0.057723 | 0.13272 | 0.43493 | 0.067479 | 0.15515 | 0.43493 | 0.9902%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 15 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.8502 | 0.24885 | 11.4533 | 2.8502 | 0.24885 | 11.4533 | 3.3319 | 0.29091 | 11.4533 | 0.9939%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 231 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 2.248 | 0 | 0 | 2.248 | 0 | 1.9514 | 3.8323 | 0.50919 | 1.9514 | 3.8323 | 0.50919 | 2.2812 | 4.48 | 0.50919 | 0.9666%
2028 | 858 | 858-14 | Tier-2 | Tier-2---12 | Tier-2---7 | 10 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 4.0968 | 0 | 0 | 4.0968 | 0 | 3.5563 | 0.1659 | 21.4364 | 3.5563 | 0.1659 | 21.4364 | 4.1574 | 0.19394 | 21.4364 | 0.9951%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 856 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 85.9483 | 0 | 0 | 85.9483 | 0 | 74.6087 | 14.2011 | 5.2537 | 74.6087 | 14.2011 | 5.2537 | 87.2184 | 16.6012 | 5.2537 | 0.9986%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 438 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 82.3856 | 0 | 0 | 82.3856 | 0 | 71.5161 | 7.2664 | 9.842 | 71.5161 | 7.2664 | 9.842 | 83.6031 | 8.4945 | 9.842 | 0.9762%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 4 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 2.5381 | 0 | 0 | 2.5381 | 0 | 2.2032 | 0.06636 | 33.2011 | 2.2032 | 0.06636 | 33.2011 | 2.5756 | 0.077576 | 33.2011 | 0.9867%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 703 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 90.7565 | 0 | 0 | 90.7565 | 0 | 78.7826 | 11.6628 | 6.755 | 78.7826 | 11.6628 | 6.755 | 92.0977 | 13.6339 | 6.755 | 0.9973%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 1553 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 268.4817 | 0 | 0 | 268.4817 | 0 | 233.0596 | 25.7643 | 9.0458 | 233.0596 | 25.7643 | 9.0458 | 272.4494 | 30.1188 | 9.0458 | 0.9919%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 110 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 63.4695 | 0 | 0 | 63.4695 | 0 | 55.0956 | 1.8249 | 30.191 | 55.0956 | 1.8249 | 30.191 | 64.4074 | 2.1333 | 30.191 | 0.9998%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 1316 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 155.0258 | 0 | 0 | 155.0258 | 0 | 134.5725 | 21.8325 | 6.1639 | 134.5725 | 21.8325 | 6.1639 | 157.3168 | 25.5224 | 6.1639 | 0.9833%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 759 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 116.23 | 0 | 0 | 116.23 | 0 | 100.8952 | 12.5918 | 8.0128 | 100.8952 | 12.5918 | 8.0128 | 117.9476 | 14.72 | 8.0128 | 0.988%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 1095 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 53.6181 | 0 | 0 | 53.6181 | 0 | 46.544 | 18.1661 | 2.5621 | 46.544 | 18.1661 | 2.5621 | 54.4105 | 21.2363 | 2.5621 | 0.9625%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 563 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.4613 | 0 | 0 | 13.4613 | 0 | 11.6853 | 9.3402 | 1.2511 | 11.6853 | 9.3402 | 1.2511 | 13.6602 | 10.9188 | 1.2511 | 0.9181%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 319 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 78.2874 | 0 | 0 | 78.2874 | 0 | 67.9586 | 5.2922 | 12.8412 | 67.9586 | 5.2922 | 12.8412 | 79.4443 | 6.1867 | 12.8412 | 0.9835%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 1307 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 408.0096 | 0 | 0 | 408.0096 | 0 | 354.179 | 21.6831 | 16.3343 | 354.179 | 21.6831 | 16.3343 | 414.0392 | 25.3478 | 16.3343 | 0.9889%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 559 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 33.5177 | 0 | 0 | 33.5177 | 0 | 29.0956 | 9.2738 | 3.1374 | 29.0956 | 9.2738 | 3.1374 | 34.0131 | 10.8412 | 3.1374 | 0.9191%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 876 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 223.5745 | 0 | 0 | 223.5745 | 0 | 194.0772 | 14.5329 | 13.3544 | 194.0772 | 14.5329 | 13.3544 | 226.8785 | 16.9891 | 13.3544 | 0.9908%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 1.5113 | 0 | 0 | 1.5113 | 0 | 1.3119 | 0.14931 | 8.7864 | 1.3119 | 0.14931 | 8.7864 | 1.5336 | 0.17455 | 8.7864 | 0.9858%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 221 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 8.1805 | 0 | 0 | 8.1805 | 0 | 7.1012 | 3.6664 | 1.9368 | 7.1012 | 3.6664 | 1.9368 | 8.3014 | 4.2861 | 1.9368 | 0.9652%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 1430 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 548.5077 | 0 | 0 | 548.5077 | 0 | 476.1404 | 23.7237 | 20.0702 | 476.1404 | 23.7237 | 20.0702 | 556.6136 | 27.7333 | 20.0702 | 0.9927%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 10 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 57.0115 | 0 | 0 | 57.0115 | 0 | 49.4897 | 0.1659 | 298.3103 | 49.4897 | 0.1659 | 298.3103 | 57.8541 | 0.19394 | 298.3103 | 0.9997%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 988 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 320.7525 | 0 | 0 | 320.7525 | 0 | 278.4341 | 16.3909 | 16.9871 | 278.4341 | 16.3909 | 16.9871 | 325.4926 | 19.1612 | 16.9871 | 0.9926%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 319 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 12.4388 | 0 | 0 | 12.4388 | 0 | 10.7977 | 5.2922 | 2.0403 | 10.7977 | 5.2922 | 2.0403 | 12.6227 | 6.1867 | 2.0403 | 0.9598%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 310 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 33.8415 | 0 | 0 | 33.8415 | 0 | 29.3766 | 5.1429 | 5.7121 | 29.3766 | 5.1429 | 5.7121 | 34.3416 | 6.0121 | 5.7121 | 0.9934%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 87 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 10.7282 | 0 | 0 | 10.7282 | 0 | 9.3128 | 1.4433 | 6.4523 | 9.3128 | 1.4433 | 6.4523 | 10.8867 | 1.6873 | 6.4523 | 0.6902%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 126 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 15.2577 | 0 | 0 | 15.2577 | 0 | 13.2447 | 2.0903 | 6.3361 | 13.2447 | 2.0903 | 6.3361 | 15.4832 | 2.4436 | 6.3361 | 0.7661%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 53 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 4.3258 | 0 | 0 | 4.3258 | 0 | 3.7551 | 0.87927 | 4.2707 | 3.7551 | 0.87927 | 4.2707 | 4.3897 | 1.0279 | 4.2707 | 0.9947%
2028 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 42 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 0.60559 | 0 | 0 | 0.60559 | 0 | 0.52569 | 0.69678 | 0.75446 | 0.52569 | 0.69678 | 0.75446 | 0.61454 | 0.81454 | 0.75446 | 0.9691%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 70 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 129.1727 | 0 | 0 | 129.1727 | 0 | 112.1303 | 1.1613 | 96.5558 | 112.1303 | 1.1613 | 96.5558 | 131.0816 | 1.3576 | 96.5558 | 0.9966%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 945 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 150.053 | 0 | 0 | 150.053 | 0 | 130.2558 | 15.6776 | 8.3084 | 130.2558 | 15.6776 | 8.3084 | 152.2705 | 18.3273 | 8.3084 | 0.9905%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 1604 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 281.7479 | 0 | 0 | 281.7479 | 0 | 244.5755 | 26.6104 | 9.191 | 244.5755 | 26.6104 | 9.191 | 285.9116 | 31.1078 | 9.191 | 0.9891%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 200 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 79.7252 | 0 | 0 | 79.7252 | 0 | 69.2066 | 3.318 | 20.8579 | 69.2066 | 3.318 | 20.8579 | 80.9033 | 3.8788 | 20.8579 | 0.9946%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 118 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 37.5911 | 1.9576 | 19.2024 | 37.5911 | 1.9576 | 19.2024 | 43.9444 | 2.2885 | 19.2024 | 0.9952%
2028 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 11 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 1.9177 | 0 | 0 | 1.9177 | 0 | 1.6647 | 0.18249 | 9.1223 | 1.6647 | 0.18249 | 9.1223 | 1.9461 | 0.21333 | 9.1223 | 0.9994%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 427 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 145.3899 | 0 | 0 | 145.3899 | 0 | 126.2079 | 7.0839 | 17.8161 | 126.2079 | 7.0839 | 17.8161 | 147.5385 | 8.2812 | 17.8161 | 0.9843%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 1117 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 111.5275 | 0 | 0 | 111.5275 | 0 | 96.8131 | 18.531 | 5.2244 | 96.8131 | 18.531 | 5.2244 | 113.1756 | 21.663 | 5.2244 | 0.9898%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 361 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 79.0167 | 0 | 0 | 79.0167 | 0 | 68.5917 | 5.989 | 11.453 | 68.5917 | 5.989 | 11.453 | 80.1845 | 7.0012 | 11.453 | 0.9853%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 1464 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 230.3289 | 0 | 0 | 230.3289 | 0 | 199.9405 | 24.2878 | 8.2321 | 199.9405 | 24.2878 | 8.2321 | 233.7327 | 28.3927 | 8.2321 | 0.9839%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 958 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 223.3649 | 0 | 0 | 223.3649 | 0 | 193.8953 | 15.8932 | 12.1999 | 193.8953 | 15.8932 | 12.1999 | 226.6658 | 18.5794 | 12.1999 | 0.9748%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 360 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 90.6884 | 0 | 0 | 90.6884 | 0 | 78.7234 | 5.9724 | 13.1812 | 78.7234 | 5.9724 | 13.1812 | 92.0286 | 6.9818 | 13.1812 | 0.9912%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 249 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 50.3926 | 0 | 0 | 50.3926 | 0 | 43.7441 | 4.1309 | 10.5894 | 43.7441 | 4.1309 | 10.5894 | 51.1373 | 4.8291 | 10.5894 | 0.9732%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 144 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 85.7983 | 0 | 0 | 85.7983 | 0 | 74.4785 | 2.389 | 31.1761 | 74.4785 | 2.389 | 31.1761 | 87.0662 | 2.7927 | 31.1761 | 0.9953%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 198 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 63.9329 | 0 | 0 | 63.9329 | 0 | 55.4979 | 3.2848 | 16.8952 | 55.4979 | 3.2848 | 16.8952 | 64.8777 | 3.84 | 16.8952 | 0.9803%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 611 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 32.7257 | 0 | 0 | 32.7257 | 0 | 28.408 | 10.1365 | 2.8025 | 28.408 | 10.1365 | 2.8025 | 33.2093 | 11.8497 | 2.8025 | 0.9369%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 70.7503 | 0 | 0 | 70.7503 | 0 | 61.4159 | 1.2111 | 50.712 | 61.4159 | 1.2111 | 50.712 | 71.7958 | 1.4158 | 50.712 | 0.9955%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 25 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 51.527 | 0 | 0 | 51.527 | 0 | 44.7288 | 0.41475 | 107.8452 | 44.7288 | 0.41475 | 107.8452 | 52.2885 | 0.48485 | 107.8452 | 0.803%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 189 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.5843 | 3.1355 | 1.1431 | 3.5843 | 3.1355 | 1.1431 | 4.1901 | 3.6655 | 1.1431 | 0.6587%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 392 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 45.6668 | 0 | 0 | 45.6668 | 0 | 39.6418 | 6.5033 | 6.0957 | 39.6418 | 6.5033 | 6.0957 | 46.3417 | 7.6024 | 6.0957 | 0.9978%
2028 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 184 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 33.2646 | 0 | 0 | 33.2646 | 0 | 28.8759 | 3.0526 | 9.4596 | 28.8759 | 3.0526 | 9.4596 | 33.7562 | 3.5685 | 9.4596 | 0.9981%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 149 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 14.0915 | 0 | 0 | 14.0915 | 0 | 12.2323 | 2.4719 | 4.9485 | 12.2323 | 2.4719 | 4.9485 | 14.2997 | 2.8897 | 4.9485 | 0.9962%
2028 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 11.301 | 0 | 0 | 11.301 | 0 | 9.81 | 0.68019 | 14.4225 | 9.81 | 0.68019 | 14.4225 | 11.4681 | 0.79515 | 14.4225 | 0.9972%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 242 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 5.6882 | 0 | 0 | 5.6882 | 0 | 4.9377 | 4.0148 | 1.2299 | 4.9377 | 4.0148 | 1.2299 | 5.7722 | 4.6933 | 1.2299 | 0.3454%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 5.7409 | 0 | 0 | 5.7409 | 0 | 4.9835 | 3.9982 | 1.2464 | 4.9835 | 3.9982 | 1.2464 | 5.8257 | 4.6739 | 1.2464 | 0.75%
2028 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 13 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 0.72679 | 0 | 0 | 0.72679 | 0 | 0.6309 | 0.21567 | 2.9253 | 0.6309 | 0.21567 | 2.9253 | 0.73753 | 0.25212 | 2.9253 | 0.9665%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 1271 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 53.1984 | 0 | 0 | 53.1984 | 0 | 46.1797 | 21.0859 | 2.1901 | 46.1797 | 21.0859 | 2.1901 | 53.9845 | 24.6497 | 2.1901 | 0.8429%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 2262 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 65.8522 | 0 | 0 | 65.8522 | 0 | 57.164 | 37.5266 | 1.5233 | 57.164 | 37.5266 | 1.5233 | 66.8254 | 43.869 | 1.5233 | 0.9909%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 367 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 14.3475 | 0 | 0 | 14.3475 | 0 | 12.4546 | 6.0885 | 2.0456 | 12.4546 | 6.0885 | 2.0456 | 14.5596 | 7.1176 | 2.0456 | 0.9975%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 15 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 1.0783 | 0 | 0 | 1.0783 | 0 | 0.93603 | 0.24885 | 3.7614 | 0.93603 | 0.24885 | 3.7614 | 1.0942 | 0.29091 | 3.7614 | 0.9975%
2028 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 74 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 40.7256 | 0 | 0 | 40.7256 | 0 | 35.3525 | 1.2277 | 28.7966 | 35.3525 | 1.2277 | 28.7966 | 41.3275 | 1.4351 | 28.7966 | 0.9993%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 14 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 0.39301 | 0 | 0 | 0.39301 | 0 | 0.34116 | 0.23226 | 1.4689 | 0.34116 | 0.23226 | 1.4689 | 0.39882 | 0.27151 | 1.4689 | 0.9408%
2028 | 1446 | CB 1446 | Tier-1 | Non-HFTD---17 | Non-HFTD---24 | 13 | 100% | 1.7782 | 79.62% | 0% | 20.38% | 0.014159 | 0 | 0 | 0.014159 | 0 | 0.012291 | 0.21567 | 0.05699 | 0.012291 | 0.21567 | 0.05699 | 0.014368 | 0.25212 | 0.05699 | 0.7962%
2028 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | Non-HFTD---22 | 26 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.037296 | 0 | 0 | 0.037296 | 0 | 0.032375 | 0.43134 | 0.075057 | 0.032375 | 0.43134 | 0.075057 | 0.037847 | 0.50424 | 0.075057 | 0.8877%
2028 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 24 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 0.92171 | 0 | 0 | 0.92171 | 0 | 0.8001 | 0.39816 | 2.0095 | 0.8001 | 0.39816 | 2.0095 | 0.93533 | 0.46545 | 2.0095 | 0.3549%
2028 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 3.1722 | 0 | 0 | 3.1722 | 0 | 2.7537 | 0.08295 | 33.197 | 2.7537 | 0.08295 | 33.197 | 3.2191 | 0.09697 | 33.197 | 0.7993%
2028 | 196 | CB 196 | Tier-2 | Tier-2---15 | Tier-2---9 | 14 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.042252 | 0 | 0 | 0.042252 | 0 | 0.036677 | 0.23226 | 0.15792 | 0.036677 | 0.23226 | 0.15792 | 0.042876 | 0.27151 | 0.15792 | 0.03142%
2028 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 168 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.014 | 0 | 0 | 4.014 | 0 | 3.4844 | 2.7871 | 1.2502 | 3.4844 | 2.7871 | 1.2502 | 4.0733 | 3.2582 | 1.2502 | 0.299%
2028 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 321 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 1.2745 | 0 | 0 | 1.2745 | 0 | 1.1064 | 5.3254 | 0.20775 | 1.1064 | 5.3254 | 0.20775 | 1.2933 | 6.2254 | 0.20775 | 0.9512%
2028 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 554 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.1876 | 0 | 0 | 0.1876 | 0 | 0.16285 | 9.1909 | 0.017718 | 0.16285 | 9.1909 | 0.017718 | 0.19037 | 10.7442 | 0.017718 | 0.09583%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 463 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 8.5634 | 0 | 0 | 8.5634 | 0 | 7.4336 | 7.6812 | 0.96777 | 7.4336 | 7.6812 | 0.96777 | 8.6899 | 8.9794 | 0.96777 | 0.8082%
2028 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 8 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 1.3377 | 0 | 0 | 1.3377 | 0 | 1.1612 | 0.13272 | 8.7494 | 1.1612 | 0.13272 | 8.7494 | 1.3575 | 0.15515 | 8.7494 | 0.9989%
2028 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 77 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 2.1243 | 0 | 0 | 2.1243 | 0 | 1.844 | 1.2774 | 1.4435 | 1.844 | 1.2774 | 1.4435 | 2.1557 | 1.4933 | 1.4435 | 0.9981%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 688 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 24.8213 | 0 | 0 | 24.8213 | 0 | 21.5465 | 11.4139 | 1.8877 | 21.5465 | 11.4139 | 1.8877 | 25.1881 | 13.343 | 1.8877 | 0.9929%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 605 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 15.9947 | 0 | 0 | 15.9947 | 0 | 13.8844 | 10.037 | 1.3833 | 13.8844 | 10.037 | 1.3833 | 16.231 | 11.7333 | 1.3833 | 0.9737%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 1834 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 40.7559 | 0 | 0 | 40.7559 | 0 | 35.3788 | 30.4261 | 1.1628 | 35.3788 | 30.4261 | 1.1628 | 41.3582 | 35.5684 | 1.1628 | 0.9874%
2028 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 1006 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 32.5785 | 0 | 0 | 32.5785 | 0 | 28.2802 | 16.6896 | 1.6945 | 28.2802 | 16.6896 | 1.6945 | 33.0599 | 19.5103 | 1.6945 | 0.9888%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 678 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 124.086 | 0 | 0 | 124.086 | 0 | 107.7148 | 11.248 | 9.5763 | 107.7148 | 11.248 | 9.5763 | 125.9198 | 13.1491 | 9.5763 | 0.9762%
2028 | 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 34 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 21.019 | 0 | 0 | 21.019 | 0 | 18.2459 | 0.56406 | 32.3474 | 18.2459 | 0.56406 | 32.3474 | 21.3297 | 0.65939 | 32.3474 | 0.9954%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 241 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 12.3369 | 0 | 0 | 12.3369 | 0 | 10.7092 | 3.9982 | 2.6785 | 10.7092 | 3.9982 | 2.6785 | 12.5192 | 4.6739 | 2.6785 | 0.9768%
2028 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 55 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 2.6184 | 0 | 0 | 2.6184 | 0 | 2.273 | 0.91245 | 2.491 | 2.273 | 0.91245 | 2.491 | 2.6571 | 1.0667 | 2.491 | 0.6436%
2028 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 1.1084 | 0 | 0 | 1.1084 | 0 | 0.96218 | 0.3318 | 2.8999 | 0.96218 | 0.3318 | 2.8999 | 1.1248 | 0.38788 | 2.8999 | 0.375%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 577 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 12.9464 | 0 | 0 | 12.9464 | 0 | 11.2383 | 9.5724 | 1.174 | 11.2383 | 9.5724 | 1.174 | 13.1378 | 11.1903 | 1.174 | 0.9%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 119 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 2.6688 | 0 | 0 | 2.6688 | 0 | 2.3167 | 1.9742 | 1.1735 | 2.3167 | 1.9742 | 1.1735 | 2.7083 | 2.3079 | 1.1735 | 0.7028%
2028 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 276 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 9.5735 | 0 | 0 | 9.5735 | 0 | 8.3104 | 4.5788 | 1.815 | 8.3104 | 4.5788 | 1.815 | 9.715 | 5.3527 | 1.815 | 0.995%
2028 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 167 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 8.0244 | 0 | 0 | 8.0244 | 0 | 6.9657 | 2.7705 | 2.5142 | 6.9657 | 2.7705 | 2.5142 | 8.143 | 3.2388 | 2.5142 | 0.9704%
2028 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 8 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 0.50007 | 0 | 0 | 0.50007 | 0 | 0.43409 | 0.13272 | 3.2707 | 0.43409 | 0.13272 | 3.2707 | 0.50746 | 0.15515 | 3.2707 | 0.1609%
2028 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 385 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.62928 | 0 | 0 | 0.62928 | 0 | 0.54626 | 6.3872 | 0.085525 | 0.54626 | 6.3872 | 0.085525 | 0.63858 | 7.4667 | 0.085525 | 0.6647%
2028 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 151 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.10476 | 0 | 0 | 0.10476 | 0 | 0.090938 | 2.5051 | 0.036301 | 0.090938 | 2.5051 | 0.036301 | 0.10631 | 2.9285 | 0.036301 | 0.9726%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 14.5369 | 0 | 0 | 14.5369 | 0 | 12.619 | 0.36498 | 34.5744 | 12.619 | 0.36498 | 34.5744 | 14.7517 | 0.42667 | 34.5744 | 0.9979%
2028 | 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 37 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 2.0846 | 0 | 0 | 2.0846 | 0 | 1.8095 | 0.61383 | 2.948 | 1.8095 | 0.61383 | 2.948 | 2.1154 | 0.71757 | 2.948 | 0.9683%
2028 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 228 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 0.41442 | 0 | 0 | 0.41442 | 0 | 0.35975 | 3.7825 | 0.095108 | 0.35975 | 3.7825 | 0.095108 | 0.42055 | 4.4218 | 0.095108 | 0.3335%
2028 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 3 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 2.5959 | 0 | 0 | 2.5959 | 0 | 2.2534 | 0.04977 | 45.2768 | 2.2534 | 0.04977 | 45.2768 | 2.6343 | 0.058182 | 45.2768 | 0.9938%
2028 | 350 | CB 350 | Tier-2 | Tier-2---15 | Tier-2---11 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 1.3347 | 0 | 0 | 1.3347 | 0 | 1.1586 | 0.01659 | 69.8371 | 1.1586 | 0.01659 | 69.8371 | 1.3544 | 0.019394 | 69.8371 | 0.9992%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 542 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 145.5036 | 0 | 0 | 145.5036 | 0 | 126.3066 | 8.9918 | 14.0469 | 126.3066 | 8.9918 | 14.0469 | 147.6539 | 10.5115 | 14.0469 | 0.9966%
2028 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 27 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 0.87191 | 0 | 0 | 0.87191 | 0 | 0.75687 | 0.44793 | 1.6897 | 0.75687 | 0.44793 | 1.6897 | 0.88479 | 0.52364 | 1.6897 | 0.9922%
2028 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 2 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.074836 | 0 | 0 | 0.074836 | 0 | 0.064962 | 0.03318 | 1.9579 | 0.064962 | 0.03318 | 1.9579 | 0.075942 | 0.038788 | 1.9579 | 0.986%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 836 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 111.5704 | 0 | 0 | 111.5704 | 0 | 96.8504 | 13.8693 | 6.9831 | 96.8504 | 13.8693 | 6.9831 | 113.2192 | 16.2133 | 6.9831 | 0.9884%
2028 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.067449 | 0 | 0 | 0.067449 | 0 | 0.05855 | 0.08295 | 0.70585 | 0.05855 | 0.08295 | 0.70585 | 0.068446 | 0.09697 | 0.70585 | 0.991%
2028 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 372 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 58.6685 | 0 | 0 | 58.6685 | 0 | 50.9281 | 6.1715 | 8.2522 | 50.9281 | 6.1715 | 8.2522 | 59.5355 | 7.2145 | 8.2522 | 0.9601%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 35 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 1.6262 | 0 | 0 | 1.6262 | 0 | 1.4116 | 0.58065 | 2.4311 | 1.4116 | 0.58065 | 2.4311 | 1.6502 | 0.67879 | 2.4311 | 0.1888%
2028 | 381 | CB 381 | Tier-1 | Non-HFTD---5 | Non-HFTD---17 | 10 | 100% | 47.7165 | 98.4% | 0% | 1.604% | 0.46951 | 0 | 0 | 0.46951 | 0 | 0.40757 | 0.1659 | 2.4567 | 0.40757 | 0.1659 | 2.4567 | 0.47645 | 0.19394 | 2.4567 | 0.984%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 3 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.83395 | 0.04977 | 16.756 | 0.83395 | 0.04977 | 16.756 | 0.97489 | 0.058182 | 16.756 | 0.1434%
2028 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 152 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 10.6596 | 0 | 0 | 10.6596 | 0 | 9.2532 | 2.5217 | 3.6695 | 9.2532 | 2.5217 | 3.6695 | 10.8171 | 2.9479 | 3.6695 | 0.9408%
2028 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 9 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 0.65999 | 0 | 0 | 0.65999 | 0 | 0.57291 | 0.14931 | 3.8371 | 0.57291 | 0.14931 | 3.8371 | 0.66974 | 0.17455 | 3.8371 | 0.9829%
2028 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 4 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.1472 | 0 | 0 | 1.1472 | 0 | 0.99585 | 0.06636 | 15.0068 | 0.99585 | 0.06636 | 15.0068 | 1.1642 | 0.077576 | 15.0068 | 0.9768%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 183 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 66.0955 | 0 | 0 | 66.0955 | 0 | 57.3752 | 3.036 | 18.8985 | 57.3752 | 3.036 | 18.8985 | 67.0723 | 3.5491 | 18.8985 | 0.9549%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.18378 | 0 | 0 | 0.18378 | 0 | 0.15954 | 0.04977 | 3.2055 | 0.15954 | 0.04977 | 3.2055 | 0.1865 | 0.058182 | 3.2055 | 0.9464%
2028 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 6 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.01729 | 0 | 0 | 0.01729 | 0 | 0.015009 | 0.09954 | 0.15078 | 0.015009 | 0.09954 | 0.15078 | 0.017546 | 0.11636 | 0.15078 | 0.9786%
2028 | 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 19 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.020627 | 0 | 0 | 0.020627 | 0 | 0.017906 | 0.31521 | 0.056806 | 0.017906 | 0.31521 | 0.056806 | 0.020932 | 0.36848 | 0.056806 | 0.1679%
2028 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 553 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 9.6146 | 0 | 0 | 9.6146 | 0 | 8.3461 | 9.1743 | 0.90973 | 8.3461 | 9.1743 | 0.90973 | 9.7567 | 10.7248 | 0.90973 | 0.8949%
2028 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 301 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 1.1366 | 0 | 0 | 1.1366 | 0 | 0.98668 | 4.9936 | 0.19759 | 0.98668 | 4.9936 | 0.19759 | 1.1534 | 5.8376 | 0.19759 | 0.372%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 34 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.5366 | 0 | 0 | 4.5366 | 0 | 3.938 | 0.56406 | 6.9816 | 3.938 | 0.56406 | 6.9816 | 4.6036 | 0.65939 | 6.9816 | 0.9425%
2028 | 533 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 1 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0035677 | 0 | 0 | 0.0035677 | 0 | 0.003097 | 0.01659 | 0.18668 | 0.003097 | 0.01659 | 0.18668 | 0.0036204 | 0.019394 | 0.18668 | 0.03364%
2028 | 534 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 3 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.022693 | 0 | 0 | 0.022693 | 0 | 0.019699 | 0.04977 | 0.3958 | 0.019699 | 0.04977 | 0.3958 | 0.023029 | 0.058182 | 0.3958 | 0.3599%
2028 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 3 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.051127 | 0 | 0 | 0.051127 | 0 | 0.044381 | 0.04977 | 0.89172 | 0.044381 | 0.04977 | 0.89172 | 0.051882 | 0.058182 | 0.89172 | 0.04585%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 51 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 0.41228 | 0 | 0 | 0.41228 | 0 | 0.35788 | 0.84609 | 0.42298 | 0.35788 | 0.84609 | 0.42298 | 0.41837 | 0.98909 | 0.42298 | 0.7619%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 189 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 0.66736 | 0 | 0 | 0.66736 | 0 | 0.57931 | 3.1355 | 0.18476 | 0.57931 | 3.1355 | 0.18476 | 0.67722 | 3.6655 | 0.18476 | 0.9924%
2028 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 54 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 9.0632 | 0 | 0 | 9.0632 | 0 | 7.8674 | 0.89586 | 8.782 | 7.8674 | 0.89586 | 8.782 | 9.1971 | 1.0473 | 8.782 | 0.9545%
2028 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 26 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 3.2734 | 0 | 0 | 3.2734 | 0 | 2.8415 | 0.43134 | 6.5877 | 2.8415 | 0.43134 | 6.5877 | 3.3218 | 0.50424 | 6.5877 | 0.7837%
2028 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 19 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 7.5828 | 0 | 0 | 7.5828 | 0 | 6.5824 | 0.31521 | 20.8825 | 6.5824 | 0.31521 | 20.8825 | 7.6949 | 0.36848 | 20.8825 | 0.6312%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 752 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 43.1502 | 0 | 0 | 43.1502 | 0 | 37.4572 | 12.4757 | 3.0024 | 37.4572 | 12.4757 | 3.0024 | 43.7878 | 14.5842 | 3.0024 | 0.9981%
2028 | 750 | CB 750 | Tier-1 | Non-HFTD---4 | Non-HFTD---11 | 7 | 100% | 147.1702 | 99.68% | 0% | 0.3223% | 1.467 | 0 | 0 | 1.467 | 0 | 1.2734 | 0.11613 | 10.9654 | 1.2734 | 0.11613 | 10.9654 | 1.4886 | 0.13576 | 10.9654 | 0.9968%
2028 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 50 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 0.51026 | 0 | 0 | 0.51026 | 0 | 0.44294 | 0.8295 | 0.53398 | 0.44294 | 0.8295 | 0.53398 | 0.5178 | 0.9697 | 0.53398 | 0.9266%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 107 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 81.4683 | 0 | 0 | 81.4683 | 0 | 70.7198 | 1.7751 | 39.8392 | 70.7198 | 1.7751 | 39.8392 | 82.6722 | 2.0751 | 39.8392 | 0.9507%
2028 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 189 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 0.42402 | 0 | 0 | 0.42402 | 0 | 0.36808 | 3.1355 | 0.11739 | 0.36808 | 3.1355 | 0.11739 | 0.43029 | 3.6655 | 0.11739 | 0.9943%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 62 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 27.3774 | 0 | 0 | 27.3774 | 0 | 23.7653 | 1.0286 | 23.105 | 23.7653 | 1.0286 | 23.105 | 27.7819 | 1.2024 | 23.105 | 0.9983%
2028 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 173 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 3.1553 | 0 | 0 | 3.1553 | 0 | 2.739 | 2.8701 | 0.95434 | 2.739 | 2.8701 | 0.95434 | 3.2019 | 3.3551 | 0.95434 | 0.9343%
2028 | 911 | CB 911 | Tier-2 | Tier-2---14 | Tier-2---11 | 14 | 100% | 193.6033 | 99.75% | 0% | 0.253% | 1.9311 | 0 | 0 | 1.9311 | 0 | 1.6764 | 0.23226 | 7.2176 | 1.6764 | 0.23226 | 7.2176 | 1.9597 | 0.27151 | 7.2176 | 0.9975%
2028 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 42 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 13.1999 | 0 | 0 | 13.1999 | 0 | 11.4584 | 0.69678 | 16.4447 | 11.4584 | 0.69678 | 16.4447 | 13.395 | 0.81454 | 16.4447 | 0.7976%
2028 | 955 | CB 955 | Tier-1 | Non-HFTD---9 | Non-HFTD---22 | 60 | 100% | 15.216 | 95.67% | 0% | 4.328% | 0.14557 | 0 | 0 | 0.14557 | 0 | 0.12637 | 0.9954 | 0.12695 | 0.12637 | 0.9954 | 0.12695 | 0.14773 | 1.1636 | 0.12695 | 0.9567%
2028 | 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 6 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 2.5092 | 0 | 0 | 2.5092 | 0 | 2.1782 | 0.09954 | 21.8823 | 2.1782 | 0.09954 | 21.8823 | 2.5463 | 0.11636 | 21.8823 | 0.9997%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 162 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 114.0037 | 0 | 0 | 114.0037 | 0 | 98.9626 | 2.6876 | 36.8222 | 98.9626 | 2.6876 | 36.8222 | 115.6885 | 3.1418 | 36.8222 | 0.9951%
2028 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 12.9802 | 0 | 0 | 12.9802 | 0 | 11.2677 | 0.8295 | 13.5837 | 11.2677 | 0.8295 | 13.5837 | 13.172 | 0.9697 | 13.5837 | 0.9951%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 450 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 3.8667 | 0 | 0 | 3.8667 | 0 | 3.3565 | 7.4655 | 0.44961 | 3.3565 | 7.4655 | 0.44961 | 3.9238 | 8.7273 | 0.44961 | 0.997%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 104 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 1.3229 | 0 | 0 | 1.3229 | 0 | 1.1483 | 1.7254 | 0.66556 | 1.1483 | 1.7254 | 0.66556 | 1.3424 | 2.017 | 0.66556 | 0.9965%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.24789 | 0 | 0 | 0.24789 | 0 | 0.21519 | 0.06636 | 3.2427 | 0.21519 | 0.06636 | 3.2427 | 0.25156 | 0.077576 | 3.2427 | 0.9021%
2028 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 414 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 1.2799 | 0 | 0 | 1.2799 | 0 | 1.111 | 6.8683 | 0.16176 | 1.111 | 6.8683 | 0.16176 | 1.2988 | 8.0291 | 0.16176 | 0.3693%
2028 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 320 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 9.7119 | 0 | 0 | 9.7119 | 0 | 8.4306 | 5.3088 | 1.588 | 8.4306 | 5.3088 | 1.588 | 9.8554 | 6.2061 | 1.588 | 0.9433%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 436 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 14.9874 | 0 | 0 | 14.9874 | 0 | 13.0101 | 7.2332 | 1.7986 | 13.0101 | 7.2332 | 1.7986 | 15.2089 | 8.4557 | 1.7986 | 0.9785%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 288 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 50.4579 | 0 | 0 | 50.4579 | 0 | 43.8007 | 4.7779 | 9.1673 | 43.8007 | 4.7779 | 9.1673 | 51.2036 | 5.5854 | 9.1673 | 0.9856%
2028 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 6.318 | 0 | 0 | 6.318 | 0 | 5.4844 | 0.31521 | 17.3993 | 5.4844 | 0.31521 | 17.3993 | 6.4114 | 0.36848 | 17.3993 | 0.9902%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 1446 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 68.4655 | 0 | 0 | 68.4655 | 0 | 59.4325 | 23.9892 | 2.4775 | 59.4325 | 23.9892 | 2.4775 | 69.4773 | 28.0436 | 2.4775 | 0.99%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 1505 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 28.679 | 0 | 0 | 28.679 | 0 | 24.8952 | 24.968 | 0.99709 | 24.8952 | 24.968 | 0.99709 | 29.1028 | 29.1878 | 0.99709 | 0.9473%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 474 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 103.3898 | 0 | 0 | 103.3898 | 0 | 89.7491 | 7.8637 | 11.4131 | 89.7491 | 7.8637 | 11.4131 | 104.9177 | 9.1927 | 11.4131 | 0.9831%
2028 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 306 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 51.3121 | 0 | 0 | 51.3121 | 0 | 44.5423 | 5.0765 | 8.7741 | 44.5423 | 5.0765 | 8.7741 | 52.0704 | 5.9345 | 8.7741 | 0.9811%
2028 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 312 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.3674 | 0 | 0 | 6.3674 | 0 | 5.5273 | 5.1761 | 1.0679 | 5.5273 | 5.1761 | 1.0679 | 6.4615 | 6.0509 | 1.0679 | 0.695%
2028 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 0.29717 | 0 | 0 | 0.29717 | 0 | 0.25797 | 0.06636 | 3.8874 | 0.25797 | 0.06636 | 3.8874 | 0.30156 | 0.077576 | 3.8874 | 0.9988%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 309 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 37.0762 | 0 | 0 | 37.0762 | 0 | 32.1846 | 5.1263 | 6.2783 | 32.1846 | 5.1263 | 6.2783 | 37.6241 | 5.9927 | 6.2783 | 0.9914%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 1052 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 31.5027 | 0 | 0 | 31.5027 | 0 | 27.3464 | 17.4527 | 1.5669 | 27.3464 | 17.4527 | 1.5669 | 31.9682 | 20.4024 | 1.5669 | 0.9371%
2028 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 38 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.018866 | 0 | 0 | 0.018866 | 0 | 0.016377 | 0.63042 | 0.025978 | 0.016377 | 0.63042 | 0.025978 | 0.019145 | 0.73697 | 0.025978 | 0.02003%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 1615 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 16.2852 | 0 | 0 | 16.2852 | 0 | 14.1367 | 26.7929 | 0.52763 | 14.1367 | 26.7929 | 0.52763 | 16.5259 | 31.3212 | 0.52763 | 0.789%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 419 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 35.3962 | 0 | 0 | 35.3962 | 0 | 30.7262 | 6.9512 | 4.4203 | 30.7262 | 6.9512 | 4.4203 | 35.9193 | 8.1261 | 4.4203 | 0.9517%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 483 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 92.7638 | 0 | 0 | 92.7638 | 0 | 80.525 | 8.013 | 10.0493 | 80.525 | 8.013 | 10.0493 | 94.1347 | 9.3673 | 10.0493 | 0.9933%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 1102 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 67.5226 | 0 | 0 | 67.5226 | 0 | 58.6141 | 18.2822 | 3.2061 | 58.6141 | 18.2822 | 3.2061 | 68.5205 | 21.3721 | 3.2061 | 0.9757%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 440 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 59.0582 | 0 | 0 | 59.0582 | 0 | 51.2664 | 7.2996 | 7.0232 | 51.2664 | 7.2996 | 7.0232 | 59.931 | 8.5333 | 7.0232 | 0.9932%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 454 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 37.632 | 0 | 0 | 37.632 | 0 | 32.667 | 7.5319 | 4.3372 | 32.667 | 7.5319 | 4.3372 | 38.1881 | 8.8048 | 4.3372 | 0.9948%

## OH Inspections--->
back to index

## OH Patrol
OH Patrol - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 75135 | 2857247.4849 | 209851.6206 | 7.345% | 200184.189 | 1047.5537 | 191.0968 | 200184.189 | 1047.5537 | 191.0968 | 210880.305 | 1103.5259 | 191.0968
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 75135 | 2857247.4849 | 209851.6206 | 7.345% | 190962.1161 | 999.295 | 191.0968 | 190962.1161 | 999.295 | 191.0968 | 211914.032 | 1108.9354 | 191.0968
[9 empty] | Capital Cost only in Year 0 | 0.014616 | K$/inspection | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 75135 | 2857247.4849 | 209851.6206 | 7.345% | 182164.8851 | 953.2596 | 191.0968 | 182164.8851 | 953.2596 | 191.0968 | 212952.8263 | 1114.3713 | 191.0968
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 225405 | 8571742.4547 | 629554.8618 | 7.345% | 573311.1902 | 3000.1083 | 191.0968 | 573311.1902 | 3000.1083 | 191.0968 | 635747.1633 | 3326.8326 | 191.0968
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 10% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units in Scope (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 4 | 1 | 117.1572 | 99.03% | 0.8725% | 0.09309% | 2.9006 | 0 | 0 | 2.9006 | 0 | 2.767 | 0.013942 | 198.4626 | 2.767 | 0.013942 | 198.4626 | 2.9149 | 0.014687 | 198.4626 | 2.476%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 10 | 10 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 40.5584 | 0 | 0 | 40.5584 | 0 | 38.69 | 0.13942 | 277.5011 | 38.69 | 0.13942 | 277.5011 | 40.7573 | 0.14687 | 277.5011 | 9.915%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 117 | 4222.2471 | 91.41% | 8.486% | 0.103% | 309.2954 | 0 | 0 | 309.2954 | 0 | 295.0468 | 1.6312 | 180.8719 | 295.0468 | 1.6312 | 180.8719 | 310.8115 | 1.7184 | 180.8719 | 7.325%
2026 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 10 | 10 | 114.5301 | 99.76% | 0% | 0.2395% | 11.4256 | 0 | 0 | 11.4256 | 0 | 10.8992 | 0.13942 | 78.1739 | 10.8992 | 0.13942 | 78.1739 | 11.4816 | 0.14687 | 78.1739 | 9.976%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 421 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 2840.2415 | 0 | 0 | 2840.2415 | 0 | 2709.3974 | 5.8697 | 461.5902 | 2709.3974 | 5.8697 | 461.5902 | 2854.1642 | 6.1833 | 461.5902 | 8.079%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 70 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 570.4582 | 0 | 0 | 570.4582 | 0 | 544.1784 | 0.97596 | 557.5827 | 544.1784 | 0.97596 | 557.5827 | 573.2546 | 1.0281 | 557.5827 | 8.085%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 139 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 1552.9096 | 0 | 0 | 1552.9096 | 0 | 1481.3702 | 1.938 | 764.3897 | 1481.3702 | 1.938 | 764.3897 | 1560.5219 | 2.0415 | 764.3897 | 8.249%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 69 | 61 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 442.8665 | 0 | 0 | 442.8665 | 0 | 422.4645 | 0.85048 | 496.7369 | 422.4645 | 0.85048 | 496.7369 | 445.0374 | 0.89592 | 496.7369 | 8.797%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 16 | 16 | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 138.0795 | 0 | 0 | 138.0795 | 0 | 131.7185 | 0.22308 | 590.463 | 131.7185 | 0.22308 | 590.463 | 138.7564 | 0.235 | 590.463 | 9.958%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 12 | 10 | 794.3626 | 99.6% | 0.3592% | 0.04176% | 65.9315 | 0 | 0 | 65.9315 | 0 | 62.8941 | 0.13942 | 451.1035 | 62.8941 | 0.13942 | 451.1035 | 66.2547 | 0.14687 | 451.1035 | 8.3%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 107 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 751.5808 | 0 | 0 | 751.5808 | 0 | 716.9571 | 1.4918 | 480.5907 | 716.9571 | 1.4918 | 480.5907 | 755.2651 | 1.5715 | 480.5907 | 7.669%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 9 | 9 | 694.7204 | 99.22% | 0.7469% | 0.03547% | 68.9285 | 0 | 0 | 68.9285 | 0 | 65.7531 | 0.12548 | 524.0101 | 65.7531 | 0.12548 | 524.0101 | 69.2664 | 0.13219 | 524.0101 | 9.922%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 76 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 429.4935 | 0 | 0 | 429.4935 | 0 | 409.7076 | 1.0596 | 386.6575 | 409.7076 | 1.0596 | 386.6575 | 431.5988 | 1.1162 | 386.6575 | 8.468%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 82 | 73 | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 255.3265 | 0 | 0 | 255.3265 | 0 | 243.5641 | 1.0178 | 239.3076 | 243.5641 | 1.0178 | 239.3076 | 256.5781 | 1.0722 | 239.3076 | 8.835%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 376 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 728.6709 | 0 | 0 | 728.6709 | 0 | 695.1025 | 5.2423 | 132.595 | 695.1025 | 5.2423 | 132.595 | 732.2428 | 5.5224 | 132.595 | 7.695%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 290 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 280.4875 | 0 | 0 | 280.4875 | 0 | 267.566 | 4.0433 | 66.1758 | 267.566 | 4.0433 | 66.1758 | 281.8624 | 4.2593 | 66.1758 | 7.432%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 85 | 585.5086 | 87.68% | 11.85% | 0.4758% | 36.6688 | 0 | 0 | 36.6688 | 0 | 34.9795 | 1.1851 | 29.5162 | 34.9795 | 1.1851 | 29.5162 | 36.8485 | 1.2484 | 29.5162 | 6.263%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 85 | 60 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 355.4132 | 0 | 0 | 355.4132 | 0 | 339.0401 | 0.83654 | 405.2899 | 339.0401 | 0.83654 | 405.2899 | 357.1554 | 0.88123 | 405.2899 | 6.936%
2026 | 1030 | 1030-1735F | Tier-3 | missing | missing | 6 | 6 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.083654 | 0 | 0 | 0.083654 | 0 | 0 | 0.088123 | 0 | 0%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 143 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 863.2115 | 0 | 0 | 863.2115 | 0 | 823.4452 | 1.9937 | 413.0139 | 823.4452 | 1.9937 | 413.0139 | 867.443 | 2.1003 | 413.0139 | 7.304%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 20 | 17 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 181.8205 | 0 | 0 | 181.8205 | 0 | 173.4444 | 0.23702 | 731.7748 | 173.4444 | 0.23702 | 731.7748 | 182.7118 | 0.24968 | 731.7748 | 8.453%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 98 | 72 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 479.9105 | 0 | 0 | 479.9105 | 0 | 457.802 | 1.0038 | 456.0487 | 457.802 | 1.0038 | 456.0487 | 482.263 | 1.0575 | 456.0487 | 7.248%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 323 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 2209.1889 | 0 | 0 | 2209.1889 | 0 | 2107.4162 | 4.5034 | 467.9654 | 2107.4162 | 4.5034 | 467.9654 | 2220.0183 | 4.744 | 467.9654 | 8.726%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 375 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 2222.2926 | 0 | 0 | 2222.2926 | 0 | 2119.9161 | 5.2284 | 405.465 | 2119.9161 | 5.2284 | 405.465 | 2233.1862 | 5.5077 | 405.465 | 7.825%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 372 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 2333.5174 | 0 | 0 | 2333.5174 | 0 | 2226.0171 | 5.1865 | 429.1919 | 2226.0171 | 5.1865 | 429.1919 | 2344.9562 | 5.4637 | 429.1919 | 8.741%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 338 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 984.307 | 0 | 0 | 984.307 | 0 | 938.962 | 4.7125 | 199.2495 | 938.962 | 4.7125 | 199.2495 | 989.132 | 4.9643 | 199.2495 | 6.168%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 16 | 12 | 17.9659 | 86.84% | 10.72% | 2.434% | 1.1701 | 0 | 0 | 1.1701 | 0 | 1.1162 | 0.16731 | 6.6718 | 1.1162 | 0.16731 | 6.6718 | 1.1759 | 0.17625 | 6.6718 | 6.513%
2026 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | Tier-2---12 | 40 | 1 | 40.9949 | 23.55% | 73.64% | 2.81% | 0.024132 | 0 | 0 | 0.024132 | 0 | 0.023021 | 0.013942 | 1.6511 | 0.023021 | 0.013942 | 1.6511 | 0.024251 | 0.014687 | 1.6511 | 0.05887%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 4 | 4 | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.3453 | 0 | 0 | 0.3453 | 0 | 0.32939 | 0.055769 | 5.9063 | 0.32939 | 0.055769 | 5.9063 | 0.34699 | 0.058749 | 5.9063 | 1.275%
2026 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 3 | 3 | 6.3934 | 34.35% | 64.55% | 1.103% | 0.21961 | 0 | 0 | 0.21961 | 0 | 0.20949 | 0.041827 | 5.0085 | 0.20949 | 0.041827 | 5.0085 | 0.22068 | 0.044062 | 5.0085 | 3.435%
2026 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | Tier-2---12 | 237 | 1 | 117.3021 | 94.99% | 0% | 5.009% | 0.047015 | 0 | 0 | 0.047015 | 0 | 0.04485 | 0.013942 | 3.2168 | 0.04485 | 0.013942 | 3.2168 | 0.047246 | 0.014687 | 3.2168 | 0.04008%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 44 | 38 | 730.5479 | 99.24% | 0.5863% | 0.172% | 62.6144 | 0 | 0 | 62.6144 | 0 | 59.7298 | 0.52981 | 112.7389 | 59.7298 | 0.52981 | 112.7389 | 62.9213 | 0.55812 | 112.7389 | 8.571%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 122 | 117 | 919.3728 | 93.93% | 5.62% | 0.4487% | 82.8186 | 0 | 0 | 82.8186 | 0 | 79.0033 | 1.6312 | 48.4312 | 79.0033 | 1.6312 | 48.4312 | 83.2246 | 1.7184 | 48.4312 | 9.008%
2026 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 72 | 509.5021 | 91.97% | 7.519% | 0.512% | 42.1724 | 0 | 0 | 42.1724 | 0 | 40.2296 | 1.0038 | 40.0755 | 40.2296 | 1.0038 | 40.0755 | 42.3791 | 1.0575 | 40.0755 | 8.277%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 29 | 14 | 140.8367 | 88.02% | 11.68% | 0.2956% | 5.9845 | 0 | 0 | 5.9845 | 0 | 5.7088 | 0.19519 | 29.2469 | 5.7088 | 0.19519 | 29.2469 | 6.0138 | 0.20562 | 29.2469 | 4.249%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 317 | 215 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 398.5741 | 0 | 0 | 398.5741 | 0 | 380.2126 | 2.9976 | 126.8394 | 380.2126 | 2.9976 | 126.8394 | 400.5279 | 3.1578 | 126.8394 | 6.757%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 225 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 348.513 | 0 | 0 | 348.513 | 0 | 332.4577 | 3.137 | 105.979 | 332.4577 | 3.137 | 105.979 | 350.2214 | 3.3046 | 105.979 | 6.983%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 128 | 2514.2831 | 99.84% | 0% | 0.1648% | 192.3939 | 0 | 0 | 192.3939 | 0 | 183.5307 | 1.7846 | 102.8406 | 183.5307 | 1.7846 | 102.8406 | 193.337 | 1.88 | 102.8406 | 7.652%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 65 | 34 | 95.3301 | 98.77% | 0% | 1.235% | 4.9249 | 0 | 0 | 4.9249 | 0 | 4.698 | 0.47404 | 9.9107 | 4.698 | 0.47404 | 9.9107 | 4.9491 | 0.49937 | 9.9107 | 5.166%
2026 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 4 | 4 | 54.719 | 98.75% | 1.065% | 0.1855% | 5.4035 | 0 | 0 | 5.4035 | 0 | 5.1545 | 0.055769 | 92.4261 | 5.1545 | 0.055769 | 92.4261 | 5.4299 | 0.058749 | 92.4261 | 9.875%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 34 | 32 | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 201.2258 | 0 | 0 | 201.2258 | 0 | 191.9557 | 0.44615 | 430.2462 | 191.9557 | 0.44615 | 430.2462 | 202.2122 | 0.46999 | 430.2462 | 9.381%
2026 | 1100 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 54 | 51 | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 399.0156 | 0 | 0 | 399.0156 | 0 | 380.6337 | 0.71106 | 535.3072 | 380.6337 | 0.71106 | 535.3072 | 400.9715 | 0.74905 | 535.3072 | 9.437%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 12 | 12 | 417.0013 | 94.5% | 5.418% | 0.08666% | 39.4048 | 0 | 0 | 39.4048 | 0 | 37.5895 | 0.16731 | 224.6733 | 37.5895 | 0.16731 | 224.6733 | 39.598 | 0.17625 | 224.6733 | 9.45%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 17 | 788.3757 | 99.4% | 0.5205% | 0.07536% | 70.1185 | 0 | 0 | 70.1185 | 0 | 66.8883 | 0.23702 | 282.2067 | 66.8883 | 0.23702 | 282.2067 | 70.4622 | 0.24968 | 282.2067 | 8.894%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 397 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 209.849 | 0 | 0 | 209.849 | 0 | 200.1817 | 5.5351 | 36.1659 | 200.1817 | 5.5351 | 36.1659 | 210.8777 | 5.8308 | 36.1659 | 4.499%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 65 | 56 | 240.2897 | 88.19% | 10.99% | 0.8202% | 18.2565 | 0 | 0 | 18.2565 | 0 | 17.4154 | 0.78077 | 22.3055 | 17.4154 | 0.78077 | 22.3055 | 18.346 | 0.82249 | 22.3055 | 7.598%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 46 | 206.5878 | 96.62% | 2.592% | 0.7875% | 18.7386 | 0 | 0 | 18.7386 | 0 | 17.8754 | 0.64135 | 27.8717 | 17.8754 | 0.64135 | 27.8717 | 18.8305 | 0.67561 | 27.8717 | 9.071%
2026 | 260 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 37 | 30 | 247.9994 | 97.75% | 1.792% | 0.4608% | 19.655 | 0 | 0 | 19.655 | 0 | 18.7495 | 0.41827 | 44.8265 | 18.7495 | 0.41827 | 44.8265 | 19.7513 | 0.44062 | 44.8265 | 7.925%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 98 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 310.444 | 0 | 0 | 310.444 | 0 | 296.1425 | 1.3663 | 216.7408 | 296.1425 | 1.3663 | 216.7408 | 311.9658 | 1.4393 | 216.7408 | 7.829%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 94 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 948.0153 | 0 | 0 | 948.0153 | 0 | 904.3422 | 1.3106 | 690.0347 | 904.3422 | 1.3106 | 690.0347 | 952.6625 | 1.3806 | 690.0347 | 9.378%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 216 | 186 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 880.7229 | 0 | 0 | 880.7229 | 0 | 840.1498 | 2.5933 | 323.9737 | 840.1498 | 2.5933 | 323.9737 | 885.0401 | 2.7318 | 323.9737 | 8.532%
2026 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | Tier-2---13 | 29 | 15 | 70.6534 | 98.66% | 0% | 1.337% | 3.6056 | 0 | 0 | 3.6056 | 0 | 3.4395 | 0.20913 | 16.4465 | 3.4395 | 0.20913 | 16.4465 | 3.6233 | 0.22031 | 16.4465 | 5.103%
2026 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | Tier-3---19 | 13 | 12 | 157.8878 | 78.49% | 21.24% | 0.2654% | 11.44 | 0 | 0 | 11.44 | 0 | 10.9129 | 0.16731 | 65.2269 | 10.9129 | 0.16731 | 65.2269 | 11.496 | 0.17625 | 65.2269 | 7.246%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 133 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 537.0936 | 0 | 0 | 537.0936 | 0 | 512.3508 | 1.8543 | 276.3006 | 512.3508 | 1.8543 | 276.3006 | 539.7264 | 1.9534 | 276.3006 | 8.737%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 58 | 55 | 2215.156 | 94.69% | 5.226% | 0.08401% | 198.904 | 0 | 0 | 198.904 | 0 | 189.7409 | 0.76683 | 247.4368 | 189.7409 | 0.76683 | 247.4368 | 199.879 | 0.8078 | 247.4368 | 8.979%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 205 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 735.0191 | 0 | 0 | 735.0191 | 0 | 701.1583 | 2.8582 | 245.3173 | 701.1583 | 2.8582 | 245.3173 | 738.6222 | 3.0109 | 245.3173 | 8.452%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 95 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 138.9852 | 0 | 0 | 138.9852 | 0 | 132.5825 | 1.3245 | 100.0987 | 132.5825 | 1.3245 | 100.0987 | 139.6665 | 1.3953 | 100.0987 | 8.918%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 166 | 136 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 287.2101 | 0 | 0 | 287.2101 | 0 | 273.9789 | 1.8962 | 144.4921 | 273.9789 | 1.8962 | 144.4921 | 288.618 | 1.9975 | 144.4921 | 8.063%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 157 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 245.2498 | 0 | 0 | 245.2498 | 0 | 233.9516 | 2.1889 | 106.879 | 233.9516 | 2.1889 | 106.879 | 246.452 | 2.3059 | 106.879 | 8.22%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 56 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 132.4185 | 0 | 0 | 132.4185 | 0 | 126.3182 | 0.78077 | 161.7871 | 126.3182 | 0.78077 | 161.7871 | 133.0676 | 0.82249 | 161.7871 | 9.551%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 167 | 146 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 370.9048 | 0 | 0 | 370.9048 | 0 | 353.818 | 2.0356 | 173.8173 | 353.818 | 2.0356 | 173.8173 | 372.723 | 2.1443 | 173.8173 | 8.625%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 44 | 44 | 411.5414 | 99.65% | 0% | 0.3468% | 41.0114 | 0 | 0 | 41.0114 | 0 | 39.1221 | 0.61346 | 63.7728 | 39.1221 | 0.61346 | 63.7728 | 41.2125 | 0.64624 | 63.7728 | 9.965%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 31 | 456.1931 | 99.77% | 0% | 0.2285% | 41.499 | 0 | 0 | 41.499 | 0 | 39.5873 | 0.43221 | 91.5925 | 39.5873 | 0.43221 | 91.5925 | 41.7025 | 0.4553 | 91.5925 | 9.097%
2026 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 2 | 2 | 2.4589 | 98.62% | 0% | 1.38% | 0.2425 | 0 | 0 | 0.2425 | 0 | 0.23133 | 0.027885 | 8.2959 | 0.23133 | 0.027885 | 8.2959 | 0.24369 | 0.029374 | 8.2959 | 9.862%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 52 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 95.0921 | 0 | 0 | 95.0921 | 0 | 90.7114 | 0.725 | 125.1194 | 90.7114 | 0.725 | 125.1194 | 95.5583 | 0.76374 | 125.1194 | 8.072%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 7 | 158.2514 | 99.48% | 0.3681% | 0.155% | 15.7423 | 0 | 0 | 15.7423 | 0 | 15.0171 | 0.097596 | 153.8703 | 15.0171 | 0.097596 | 153.8703 | 15.8195 | 0.10281 | 153.8703 | 9.948%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 68 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 175.7123 | 0 | 0 | 175.7123 | 0 | 167.6176 | 0.94808 | 176.7977 | 167.6176 | 0.94808 | 176.7977 | 176.5736 | 0.99873 | 176.7977 | 9.354%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 152 | 29 | 6418.5082 | 93.04% | 6.917% | 0.04745% | 113.9301 | 0 | 0 | 113.9301 | 0 | 108.6816 | 0.40433 | 268.7967 | 108.6816 | 0.40433 | 268.7967 | 114.4886 | 0.42593 | 268.7967 | 1.775%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 48 | 28 | 6815.4278 | 94.54% | 5.441% | 0.023% | 375.8452 | 0 | 0 | 375.8452 | 0 | 358.5308 | 0.39038 | 918.4054 | 358.5308 | 0.39038 | 918.4054 | 377.6876 | 0.41124 | 918.4054 | 5.515%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 267 | 209 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 912.8844 | 0 | 0 | 912.8844 | 0 | 870.8297 | 2.9139 | 298.8498 | 870.8297 | 2.9139 | 298.8498 | 917.3593 | 3.0696 | 298.8498 | 7.77%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 146 | 102 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 252.6921 | 0 | 0 | 252.6921 | 0 | 241.0511 | 1.4221 | 169.502 | 241.0511 | 1.4221 | 169.502 | 253.9307 | 1.4981 | 169.502 | 6.857%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 22 | 18 | 427.4478 | 90.46% | 9.431% | 0.1062% | 31.6376 | 0 | 0 | 31.6376 | 0 | 30.1801 | 0.25096 | 120.2581 | 30.1801 | 0.25096 | 120.2581 | 31.7927 | 0.26437 | 120.2581 | 7.402%
2026 | 1458 | 1458-1057F | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 3 | 155.9987 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.041827 | 0 | 0 | 0.041827 | 0 | 0 | 0.044062 | 0 | 0%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 36 | 29 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 163.0089 | 0 | 0 | 163.0089 | 0 | 155.4994 | 0.40433 | 384.5889 | 155.4994 | 0.40433 | 384.5889 | 163.8079 | 0.42593 | 384.5889 | 6.891%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 80 | 52 | 4370.0987 | 98.67% | 1.293% | 0.03403% | 280.288 | 0 | 0 | 280.288 | 0 | 267.3757 | 0.725 | 368.7946 | 267.3757 | 0.725 | 368.7946 | 281.6619 | 0.76374 | 368.7946 | 6.414%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 58.2342 | 99.94% | 0% | 0.06312% | 5.8197 | 0 | 0 | 5.8197 | 0 | 5.5516 | 0.027885 | 199.0936 | 5.5516 | 0.027885 | 199.0936 | 5.8483 | 0.029374 | 199.0936 | 9.994%
2026 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 3 | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.041827 | 0 | 0 | 0.041827 | 0 | 0 | 0.044062 | 0 | 0%
2026 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 5 | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.069711 | 0 | 0 | 0.069711 | 0 | 0 | 0.073436 | 0 | 0%
2026 | 1458 | 1458-1119F | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.013942 | 0 | 0 | 0.013942 | 0 | 0 | 0.014687 | 0 | 0%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 188 | 132 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 1112.3302 | 0 | 0 | 1112.3302 | 0 | 1061.0874 | 1.8404 | 576.5583 | 1061.0874 | 1.8404 | 576.5583 | 1117.7828 | 1.9387 | 576.5583 | 6.958%
2026 | 1458 | 1458-454F | Tier-2 | Tier-2---18 | Tier-2---10 | 2 | 2 | 84.0912 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.027885 | 0 | 0 | 0.027885 | 0 | 0 | 0.029374 | 0 | 0%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 6 | 167.5686 | 29.81% | 70.17% | 0.01889% | 4.2812 | 0 | 0 | 4.2812 | 0 | 4.084 | 0.083654 | 48.8205 | 4.084 | 0.083654 | 48.8205 | 4.3022 | 0.088123 | 48.8205 | 2.555%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 2 | 2 | 81.0039 | 99.95% | 0% | 0.04716% | 8.0966 | 0 | 0 | 8.0966 | 0 | 7.7236 | 0.027885 | 276.9841 | 7.7236 | 0.027885 | 276.9841 | 8.1363 | 0.029374 | 276.9841 | 9.995%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 127 | 108 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 688.6829 | 0 | 0 | 688.6829 | 0 | 656.9567 | 1.5058 | 436.2938 | 656.9567 | 1.5058 | 436.2938 | 692.0588 | 1.5862 | 436.2938 | 8.44%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 353 | 37077.302 | 99.36% | 0.615% | 0.02874% | 2948.759 | 0 | 0 | 2948.759 | 0 | 2812.9158 | 4.9216 | 571.5418 | 2812.9158 | 4.9216 | 571.5418 | 2963.2137 | 5.1846 | 571.5418 | 7.953%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 7 | 8.268 | 89.5% | 6.947% | 3.548% | 0.57557 | 0 | 0 | 0.57557 | 0 | 0.54906 | 0.097596 | 5.6258 | 0.54906 | 0.097596 | 5.6258 | 0.5784 | 0.10281 | 5.6258 | 6.961%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 87 | 81 | 418.5676 | 87.71% | 11.66% | 0.6303% | 34.1791 | 0 | 0 | 34.1791 | 0 | 32.6045 | 1.1293 | 28.8708 | 32.6045 | 1.1293 | 28.8708 | 34.3466 | 1.1897 | 28.8708 | 8.166%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 669 | 544 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 414.0467 | 0 | 0 | 414.0467 | 0 | 394.9725 | 7.5846 | 52.0756 | 394.9725 | 7.5846 | 52.0756 | 416.0764 | 7.9899 | 52.0756 | 7.519%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 60 | 55 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 277.2195 | 0 | 0 | 277.2195 | 0 | 264.4486 | 0.76683 | 344.8613 | 264.4486 | 0.76683 | 344.8613 | 278.5784 | 0.8078 | 344.8613 | 9.081%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 203 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 365.6682 | 0 | 0 | 365.6682 | 0 | 348.8226 | 2.8303 | 123.2465 | 348.8226 | 2.8303 | 123.2465 | 367.4607 | 2.9815 | 123.2465 | 9.434%
2026 | 157 | 157-207R | Tier-3 | Tier-3---16 | Tier-3---7 | 23 | 23 | 719.0865 | 99.89% | 0% | 0.1123% | 71.8279 | 0 | 0 | 71.8279 | 0 | 68.5189 | 0.32067 | 213.6725 | 68.5189 | 0.32067 | 213.6725 | 72.18 | 0.33781 | 213.6725 | 9.989%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 250 | 219 | 3160.5079 | 95.27% | 4.501% | 0.231% | 263.7603 | 0 | 0 | 263.7603 | 0 | 251.6094 | 3.0534 | 82.4041 | 251.6094 | 3.0534 | 82.4041 | 265.0532 | 3.2165 | 82.4041 | 8.346%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 554 | 449 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 136.2159 | 0 | 0 | 136.2159 | 0 | 129.9407 | 6.2601 | 20.757 | 129.9407 | 6.2601 | 20.757 | 136.8836 | 6.5946 | 20.757 | 6.609%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 173 | 154 | 1867.403 | 95.01% | 4.712% | 0.2778% | 157.9371 | 0 | 0 | 157.9371 | 0 | 150.6613 | 2.1471 | 70.1693 | 150.6613 | 2.1471 | 70.1693 | 158.7113 | 2.2618 | 70.1693 | 8.458%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 675 | 562 | 18749.5963 | 97% | 2.901% | 0.09453% | 1514.3227 | 0 | 0 | 1514.3227 | 0 | 1444.5609 | 7.8356 | 184.3595 | 1444.5609 | 7.8356 | 184.3595 | 1521.7458 | 8.2542 | 184.3595 | 8.077%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 99 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 383.7782 | 0 | 0 | 383.7782 | 0 | 366.0983 | 1.3803 | 265.2336 | 366.0983 | 1.3803 | 265.2336 | 385.6594 | 1.454 | 265.2336 | 9.525%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 86 | 62 | 2651.4354 | 70.65% | 29.24% | 0.1064% | 135.0483 | 0 | 0 | 135.0483 | 0 | 128.8269 | 0.86442 | 149.0325 | 128.8269 | 0.86442 | 149.0325 | 135.7103 | 0.91061 | 149.0325 | 5.093%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 239 | 216 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 386.522 | 0 | 0 | 386.522 | 0 | 368.7157 | 3.0115 | 122.4345 | 368.7157 | 3.0115 | 122.4345 | 388.4167 | 3.1724 | 122.4345 | 8.814%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 251 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 465.293 | 0 | 0 | 465.293 | 0 | 443.858 | 3.4995 | 126.8342 | 443.858 | 3.4995 | 126.8342 | 467.5739 | 3.6865 | 126.8342 | 8.104%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 43 | 836.2457 | 79.76% | 20.09% | 0.1547% | 55.1538 | 0 | 0 | 55.1538 | 0 | 52.613 | 0.59952 | 87.7588 | 52.613 | 0.59952 | 87.7588 | 55.4242 | 0.63155 | 87.7588 | 6.595%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 236 | 191 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 921.1257 | 0 | 0 | 921.1257 | 0 | 878.6914 | 2.663 | 329.9658 | 878.6914 | 2.663 | 329.9658 | 925.641 | 2.8053 | 329.9658 | 7.994%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 131 | 126 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 394.8393 | 0 | 0 | 394.8393 | 0 | 376.6499 | 1.7567 | 214.4042 | 376.6499 | 1.7567 | 214.4042 | 396.7748 | 1.8506 | 214.4042 | 9.435%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 250 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 783.6159 | 0 | 0 | 783.6159 | 0 | 747.5164 | 3.4856 | 214.4602 | 747.5164 | 3.4856 | 214.4602 | 787.4572 | 3.6718 | 214.4602 | 7.783%
2026 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 9 | 404.4817 | 67.64% | 32.12% | 0.2398% | 4.9245 | 0 | 0 | 4.9245 | 0 | 4.6976 | 0.12548 | 37.4372 | 4.6976 | 0.12548 | 37.4372 | 4.9486 | 0.13219 | 37.4372 | 1.217%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 172 | 143 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 276.3684 | 0 | 0 | 276.3684 | 0 | 263.6367 | 1.9937 | 132.2318 | 263.6367 | 1.9937 | 132.2318 | 277.7232 | 2.1003 | 132.2318 | 8.126%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 214 | 166 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 373.9475 | 0 | 0 | 373.9475 | 0 | 356.7205 | 2.3144 | 154.1296 | 356.7205 | 2.3144 | 154.1296 | 375.7805 | 2.4381 | 154.1296 | 7.579%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 345 | 270 | 13172.958 | 96.8% | 3.124% | 0.0728% | 997.9703 | 0 | 0 | 997.9703 | 0 | 951.9958 | 3.7644 | 252.8933 | 951.9958 | 3.7644 | 252.8933 | 1002.8623 | 3.9656 | 252.8933 | 7.576%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 27 | 1635.841 | 89.24% | 10.7% | 0.05535% | 131.3899 | 0 | 0 | 131.3899 | 0 | 125.3371 | 0.37644 | 332.9522 | 125.3371 | 0.37644 | 332.9522 | 132.034 | 0.39656 | 332.9522 | 8.032%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 176 | 7 | 2963.4059 | 78.23% | 21.66% | 0.1106% | 9.2203 | 0 | 0 | 9.2203 | 0 | 8.7955 | 0.097596 | 90.1219 | 8.7955 | 0.097596 | 90.1219 | 9.2655 | 0.10281 | 90.1219 | 0.3111%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 7 | 47.6106 | 91.21% | 0% | 8.789% | 0.15199 | 0 | 0 | 0.15199 | 0 | 0.14499 | 0.097596 | 1.4856 | 0.14499 | 0.097596 | 1.4856 | 0.15274 | 0.10281 | 1.4856 | 0.3192%
2026 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 45 | 7 | 0.95479 | 13.38% | 0% | 86.62% | 0.0019878 | 0 | 0 | 0.0019878 | 0 | 0.0018962 | 0.097596 | 0.019429 | 0.0018962 | 0.097596 | 0.019429 | 0.0019975 | 0.10281 | 0.019429 | 0.2082%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 166 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 641.0014 | 0 | 0 | 641.0014 | 0 | 611.4718 | 2.3144 | 264.2009 | 611.4718 | 2.3144 | 264.2009 | 644.1436 | 2.4381 | 264.2009 | 5.379%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 26 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 193.419 | 0 | 0 | 193.419 | 0 | 184.5086 | 0.3625 | 508.9901 | 184.5086 | 0.3625 | 508.9901 | 194.3672 | 0.38187 | 508.9901 | 9.974%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 81 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 326.8629 | 0 | 0 | 326.8629 | 0 | 311.805 | 1.1293 | 276.0985 | 311.805 | 1.1293 | 276.0985 | 328.4652 | 1.1897 | 276.0985 | 7.727%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 19 | 19 | 655.8009 | 99.14% | 0.7615% | 0.1019% | 65.0139 | 0 | 0 | 65.0139 | 0 | 62.0188 | 0.2649 | 234.1186 | 62.0188 | 0.2649 | 234.1186 | 65.3326 | 0.27906 | 234.1186 | 9.914%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 42 | 25 | 316.4778 | 66.23% | 33.5% | 0.2671% | 12.4764 | 0 | 0 | 12.4764 | 0 | 11.9017 | 0.34856 | 34.1456 | 11.9017 | 0.34856 | 34.1456 | 12.5376 | 0.36718 | 34.1456 | 3.942%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 114 | 50 | 471.2015 | 74.37% | 25.17% | 0.4626% | 15.3697 | 0 | 0 | 15.3697 | 0 | 14.6617 | 0.69711 | 21.0319 | 14.6617 | 0.69711 | 21.0319 | 15.4451 | 0.73436 | 21.0319 | 3.262%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 161 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 98.1347 | 0 | 0 | 98.1347 | 0 | 93.6139 | 2.2447 | 41.7042 | 93.6139 | 2.2447 | 41.7042 | 98.6158 | 2.3646 | 41.7042 | 5.692%
2026 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 29 | 29 | 183.5383 | 99.34% | 0.09556% | 0.5689% | 18.2319 | 0 | 0 | 18.2319 | 0 | 17.392 | 0.40433 | 43.0147 | 17.392 | 0.40433 | 43.0147 | 18.3213 | 0.42593 | 43.0147 | 9.934%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 9 | 9 | 6.6189 | 96.38% | 0% | 3.621% | 0.63793 | 0 | 0 | 0.63793 | 0 | 0.60854 | 0.12548 | 4.8497 | 0.60854 | 0.12548 | 4.8497 | 0.64106 | 0.13219 | 4.8497 | 9.638%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 84 | 973.0999 | 95.53% | 4.02% | 0.4464% | 41.537 | 0 | 0 | 41.537 | 0 | 39.6234 | 1.1712 | 33.8329 | 39.6234 | 1.1712 | 33.8329 | 41.7406 | 1.2337 | 33.8329 | 4.269%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 315 | 490.4615 | 96.36% | 1.259% | 2.378% | 44.3083 | 0 | 0 | 44.3083 | 0 | 42.2671 | 4.3918 | 9.624 | 42.2671 | 4.3918 | 9.624 | 44.5255 | 4.6265 | 9.624 | 9.034%
2026 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 102 | 1 | 124.0064 | 98.52% | 0% | 1.478% | 0.11978 | 0 | 0 | 0.11978 | 0 | 0.11426 | 0.013942 | 8.1952 | 0.11426 | 0.013942 | 8.1952 | 0.12037 | 0.014687 | 8.1952 | 0.09659%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 16 | 1279.0443 | 99.78% | 0% | 0.2159% | 15.4701 | 0 | 0 | 15.4701 | 0 | 14.7574 | 0.22308 | 66.1541 | 14.7574 | 0.22308 | 66.1541 | 15.5459 | 0.235 | 66.1541 | 1.21%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 106 | 2976.5734 | 99.75% | 0% | 0.2502% | 76.2052 | 0 | 0 | 76.2052 | 0 | 72.6946 | 1.4779 | 49.1883 | 72.6946 | 1.4779 | 49.1883 | 76.5787 | 1.5568 | 49.1883 | 2.56%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 345 | 8462.8018 | 99.74% | 0% | 0.2593% | 272.4132 | 0 | 0 | 272.4132 | 0 | 259.8637 | 4.8101 | 54.0247 | 259.8637 | 4.8101 | 54.0247 | 273.7486 | 5.0671 | 54.0247 | 3.219%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 111 | 105 | 498.1496 | 90.1% | 9.186% | 0.7154% | 42.4564 | 0 | 0 | 42.4564 | 0 | 40.5005 | 1.4639 | 27.6654 | 40.5005 | 1.4639 | 27.6654 | 42.6645 | 1.5422 | 27.6654 | 8.523%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 221 | 193 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 77.7075 | 0 | 0 | 77.7075 | 0 | 74.1277 | 2.6909 | 27.548 | 74.1277 | 2.6909 | 27.548 | 78.0885 | 2.8346 | 27.548 | 7.487%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 77 | 72 | 170.5929 | 70.47% | 28.1% | 1.432% | 11.2414 | 0 | 0 | 11.2414 | 0 | 10.7236 | 1.0038 | 10.6825 | 10.7236 | 1.0038 | 10.6825 | 11.2965 | 1.0575 | 10.6825 | 6.59%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 95 | 71 | 317.7725 | 50.82% | 48.53% | 0.6462% | 12.0704 | 0 | 0 | 12.0704 | 0 | 11.5143 | 0.9899 | 11.6318 | 11.5143 | 0.9899 | 11.6318 | 12.1296 | 1.0428 | 11.6318 | 3.798%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 293 | 259 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 94.894 | 0 | 0 | 94.894 | 0 | 90.5225 | 3.6111 | 25.0682 | 90.5225 | 3.6111 | 25.0682 | 95.3592 | 3.804 | 25.0682 | 7.91%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 361 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 131.0591 | 0 | 0 | 131.0591 | 0 | 125.0215 | 5.0332 | 24.8395 | 125.0215 | 5.0332 | 24.8395 | 131.7016 | 5.3021 | 24.8395 | 7.243%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 279 | 252 | 1890.633 | 91.06% | 8.49% | 0.4466% | 155.5063 | 0 | 0 | 155.5063 | 0 | 148.3424 | 3.5135 | 42.2212 | 148.3424 | 3.5135 | 42.2212 | 156.2686 | 3.7012 | 42.2212 | 8.225%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 287 | 250 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 144.5469 | 0 | 0 | 144.5469 | 0 | 137.8879 | 3.4856 | 39.5596 | 137.8879 | 3.4856 | 39.5596 | 145.2554 | 3.6718 | 39.5596 | 8.312%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 219 | 185 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 125.9884 | 0 | 0 | 125.9884 | 0 | 120.1844 | 2.5793 | 46.5953 | 120.1844 | 2.5793 | 46.5953 | 126.606 | 2.7171 | 46.5953 | 8.023%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 79 | 77 | 609.7797 | 99.07% | 0.4924% | 0.4406% | 58.8797 | 0 | 0 | 58.8797 | 0 | 56.1673 | 1.0736 | 52.3189 | 56.1673 | 1.0736 | 52.3189 | 59.1684 | 1.1309 | 52.3189 | 9.656%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 218 | 186 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 413.4942 | 0 | 0 | 413.4942 | 0 | 394.4453 | 2.5933 | 152.1037 | 394.4453 | 2.5933 | 152.1037 | 415.5211 | 2.7318 | 152.1037 | 8.46%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 273 | 259 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 117.6038 | 0 | 0 | 117.6038 | 0 | 112.1861 | 3.6111 | 31.0674 | 112.1861 | 3.6111 | 31.0674 | 118.1803 | 3.804 | 31.0674 | 9.29%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 201 | 179 | 998.7912 | 96.62% | 2.787% | 0.5903% | 85.9427 | 0 | 0 | 85.9427 | 0 | 81.9835 | 2.4957 | 32.8503 | 81.9835 | 2.4957 | 32.8503 | 86.364 | 2.629 | 32.8503 | 8.605%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 71 | 66 | 261.4279 | 97.06% | 2.12% | 0.8249% | 23.5861 | 0 | 0 | 23.5861 | 0 | 22.4996 | 0.92019 | 24.451 | 22.4996 | 0.92019 | 24.451 | 23.7017 | 0.96936 | 24.451 | 9.022%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 201 | 183 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 131.2891 | 0 | 0 | 131.2891 | 0 | 125.2409 | 2.5514 | 49.0864 | 125.2409 | 2.5514 | 49.0864 | 131.9327 | 2.6878 | 49.0864 | 8.856%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 234 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 208.1629 | 0 | 0 | 208.1629 | 0 | 198.5732 | 3.2625 | 60.8655 | 198.5732 | 3.2625 | 60.8655 | 209.1833 | 3.4368 | 60.8655 | 7.546%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 115 | 105 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 92.115 | 0 | 0 | 92.115 | 0 | 87.8714 | 1.4639 | 60.0239 | 87.8714 | 1.4639 | 60.0239 | 92.5665 | 1.5422 | 60.0239 | 8.867%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 31 | 29 | 104.9439 | 97.78% | 1.295% | 0.9224% | 9.5996 | 0 | 0 | 9.5996 | 0 | 9.1574 | 0.40433 | 22.6485 | 9.1574 | 0.40433 | 22.6485 | 9.6467 | 0.42593 | 22.6485 | 9.147%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 155 | 151 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 208.0708 | 0 | 0 | 208.0708 | 0 | 198.4854 | 2.1053 | 94.2796 | 198.4854 | 2.1053 | 94.2796 | 209.0907 | 2.2178 | 94.2796 | 9.617%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 147 | 133 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 130.1927 | 0 | 0 | 130.1927 | 0 | 124.195 | 1.8543 | 66.9759 | 124.195 | 1.8543 | 66.9759 | 130.8309 | 1.9534 | 66.9759 | 8.85%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 377 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 2197.2181 | 0 | 0 | 2197.2181 | 0 | 2095.9968 | 5.2562 | 398.7634 | 2095.9968 | 5.2562 | 398.7634 | 2207.9887 | 5.5371 | 398.7634 | 8.36%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 248 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 576.6978 | 0 | 0 | 576.6978 | 0 | 550.1306 | 3.4577 | 159.1036 | 550.1306 | 3.4577 | 159.1036 | 579.5248 | 3.6424 | 159.1036 | 8.65%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 157 | 155 | 484.0355 | 97.4% | 1.48% | 1.12% | 46.5447 | 0 | 0 | 46.5447 | 0 | 44.4005 | 2.1611 | 20.5457 | 44.4005 | 2.1611 | 20.5457 | 46.7729 | 2.2765 | 20.5457 | 9.616%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 94 | 89 | 400.1895 | 97.86% | 1.359% | 0.7809% | 37.0794 | 0 | 0 | 37.0794 | 0 | 35.3712 | 1.2409 | 28.5053 | 35.3712 | 1.2409 | 28.5053 | 37.2611 | 1.3072 | 28.5053 | 9.265%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 70 | 60 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 43.4342 | 0 | 0 | 43.4342 | 0 | 41.4333 | 0.83654 | 49.5295 | 41.4333 | 0.83654 | 49.5295 | 43.6471 | 0.88123 | 49.5295 | 8.461%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 150 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 188.6471 | 0 | 0 | 188.6471 | 0 | 179.9565 | 2.0913 | 86.0483 | 179.9565 | 2.0913 | 86.0483 | 189.5719 | 2.2031 | 86.0483 | 8.543%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 160 | 1721.769 | 85.69% | 14.07% | 0.2459% | 120.4361 | 0 | 0 | 120.4361 | 0 | 114.8878 | 2.2308 | 51.5015 | 114.8878 | 2.2308 | 51.5015 | 121.0265 | 2.35 | 51.5015 | 6.995%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 264 | 206 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1731.1083 | 0 | 0 | 1731.1083 | 0 | 1651.3597 | 2.8721 | 574.9638 | 1651.3597 | 2.8721 | 574.9638 | 1739.5941 | 3.0256 | 574.9638 | 7.744%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 205 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 999.0205 | 0 | 0 | 999.0205 | 0 | 952.9976 | 2.8582 | 333.4295 | 952.9976 | 2.8582 | 333.4295 | 1003.9176 | 3.0109 | 333.4295 | 7.865%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 193 | 19489.7064 | 99% | 0.9737% | 0.02962% | 1532.4175 | 0 | 0 | 1532.4175 | 0 | 1461.8222 | 2.6909 | 543.2544 | 1461.8222 | 2.6909 | 543.2544 | 1539.9294 | 2.8346 | 543.2544 | 7.863%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 50 | 1412.4296 | 98.09% | 1.785% | 0.1216% | 130.7071 | 0 | 0 | 130.7071 | 0 | 124.6857 | 0.69711 | 178.8597 | 124.6857 | 0.69711 | 178.8597 | 131.3478 | 0.73436 | 178.8597 | 9.254%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 117 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 499.1945 | 0 | 0 | 499.1945 | 0 | 476.1976 | 1.6312 | 291.9224 | 476.1976 | 1.6312 | 291.9224 | 501.6415 | 1.7184 | 291.9224 | 9.185%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 195 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 1013.3363 | 0 | 0 | 1013.3363 | 0 | 966.654 | 2.7187 | 355.5514 | 966.654 | 2.7187 | 355.5514 | 1018.3037 | 2.864 | 355.5514 | 7.217%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 71.2816 | 99.9% | 0% | 0.09987% | 7.121 | 0 | 0 | 7.121 | 0 | 6.793 | 0.027885 | 243.6109 | 6.793 | 0.027885 | 243.6109 | 7.1559 | 0.029374 | 243.6109 | 9.99%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 333 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 131.2012 | 0 | 0 | 131.2012 | 0 | 125.157 | 4.6428 | 26.9573 | 125.157 | 4.6428 | 26.9573 | 131.8443 | 4.8909 | 26.9573 | 6.516%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 306 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 213.1484 | 0 | 0 | 213.1484 | 0 | 203.3291 | 4.2663 | 47.6589 | 203.3291 | 4.2663 | 47.6589 | 214.1932 | 4.4943 | 47.6589 | 7.815%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 297 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 981.8904 | 0 | 0 | 981.8904 | 0 | 936.6567 | 4.1409 | 226.1986 | 936.6567 | 4.1409 | 226.1986 | 986.7035 | 4.3621 | 226.1986 | 9.188%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 247 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 291.8358 | 0 | 0 | 291.8358 | 0 | 278.3916 | 3.4437 | 80.8398 | 278.3916 | 3.4437 | 80.8398 | 293.2664 | 3.6277 | 80.8398 | 7.98%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 217 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 110.8226 | 0 | 0 | 110.8226 | 0 | 105.7172 | 3.0255 | 34.9423 | 105.7172 | 3.0255 | 34.9423 | 111.3658 | 3.1871 | 34.9423 | 7.703%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 116 | 114 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 984.8031 | 0 | 0 | 984.8031 | 0 | 939.4353 | 1.5894 | 591.0552 | 939.4353 | 1.5894 | 591.0552 | 989.6306 | 1.6743 | 591.0552 | 9.734%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 132 | 111 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 178.116 | 0 | 0 | 178.116 | 0 | 169.9106 | 1.5476 | 109.7902 | 169.9106 | 1.5476 | 109.7902 | 178.9892 | 1.6303 | 109.7902 | 8.101%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 272 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 134.619 | 0 | 0 | 134.619 | 0 | 128.4174 | 3.7923 | 33.8626 | 128.4174 | 3.7923 | 33.8626 | 135.2789 | 3.9949 | 33.8626 | 6.99%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 614 | 616 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 321.491 | 0 | 0 | 321.491 | 0 | 306.6806 | 8.5884 | 35.7085 | 306.6806 | 8.5884 | 35.7085 | 323.067 | 9.0473 | 35.7085 | 8.966%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 97 | 54 | 3690.9623 | 99.91% | 0% | 0.09183% | 205.2876 | 0 | 0 | 205.2876 | 0 | 195.8304 | 0.75288 | 260.1072 | 195.8304 | 0.75288 | 260.1072 | 206.2939 | 0.79311 | 260.1072 | 5.562%
2026 | 221 | 221-1236F | Tier-3 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.013942 | 0 | 0 | 0.013942 | 0 | 0 | 0.014687 | 0 | 0%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 307 | 168 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 164.9318 | 0 | 0 | 164.9318 | 0 | 157.3338 | 2.3423 | 67.1705 | 157.3338 | 2.3423 | 67.1705 | 165.7403 | 2.4675 | 67.1705 | 5.043%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 293 | 223 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 200.1253 | 0 | 0 | 200.1253 | 0 | 190.906 | 3.1091 | 61.4017 | 190.906 | 3.1091 | 61.4017 | 201.1063 | 3.2753 | 61.4017 | 7.315%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 13 | 13 | 710.3273 | 99.46% | 0.4791% | 0.06249% | 70.648 | 0 | 0 | 70.648 | 0 | 67.3934 | 0.18125 | 371.8262 | 67.3934 | 0.18125 | 371.8262 | 70.9943 | 0.19093 | 371.8262 | 9.946%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 244 | 151 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 236.2624 | 0 | 0 | 236.2624 | 0 | 225.3782 | 2.1053 | 107.0535 | 225.3782 | 2.1053 | 107.0535 | 237.4205 | 2.2178 | 107.0535 | 6.004%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 18 | 26 | 318.0967 | 33.4% | 66.33% | 0.2755% | 15.3453 | 0 | 0 | 15.3453 | 0 | 14.6384 | 0.3625 | 40.3819 | 14.6384 | 0.3625 | 40.3819 | 15.4206 | 0.38187 | 40.3819 | 4.824%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 99 | 76 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 157.0165 | 0 | 0 | 157.0165 | 0 | 149.783 | 1.0596 | 141.3563 | 149.783 | 1.0596 | 141.3563 | 157.7861 | 1.1162 | 141.3563 | 7.639%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 100 | 91 | 3904.259 | 99.88% | 0.03221% | 0.0896% | 354.8548 | 0 | 0 | 354.8548 | 0 | 338.5074 | 1.2687 | 266.8042 | 338.5074 | 1.2687 | 266.8042 | 356.5943 | 1.3365 | 266.8042 | 9.089%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 93 | 93 | 618.0174 | 98.68% | 0.7939% | 0.5237% | 60.9875 | 0 | 0 | 60.9875 | 0 | 58.1779 | 1.2966 | 44.8684 | 58.1779 | 1.2966 | 44.8684 | 61.2864 | 1.3659 | 44.8684 | 9.868%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 67 | 55 | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 365.8842 | 0 | 0 | 365.8842 | 0 | 349.0287 | 0.76683 | 455.1604 | 349.0287 | 0.76683 | 455.1604 | 367.6778 | 0.8078 | 455.1604 | 8.164%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 106 | 68 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 144.4234 | 0 | 0 | 144.4234 | 0 | 137.7702 | 0.94808 | 145.3156 | 137.7702 | 0.94808 | 145.3156 | 145.1314 | 0.99873 | 145.3156 | 6.214%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 123 | 107 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 833.2729 | 0 | 0 | 833.2729 | 0 | 794.8857 | 1.4918 | 532.8279 | 794.8857 | 1.4918 | 532.8279 | 837.3575 | 1.5715 | 532.8279 | 8.664%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 76 | 57 | 1359.3953 | 95.15% | 4.696% | 0.1502% | 97.0139 | 0 | 0 | 97.0139 | 0 | 92.5447 | 0.79471 | 116.4508 | 92.5447 | 0.79471 | 116.4508 | 97.4894 | 0.83717 | 116.4508 | 7.137%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 367 | 257 | 7406.689 | 96.62% | 3.25% | 0.1263% | 501.1579 | 0 | 0 | 501.1579 | 0 | 478.0706 | 3.5832 | 133.4212 | 478.0706 | 3.5832 | 133.4212 | 503.6146 | 3.7746 | 133.4212 | 6.766%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 451 | 389 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 6779.655 | 0 | 0 | 6779.655 | 0 | 6467.3303 | 5.4235 | 1192.4535 | 6467.3303 | 5.4235 | 1192.4535 | 6812.8886 | 5.7133 | 1192.4535 | 8.561%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 18 | 17 | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 339.3326 | 0 | 0 | 339.3326 | 0 | 323.7003 | 0.23702 | 1365.7152 | 323.7003 | 0.23702 | 1365.7152 | 340.996 | 0.24968 | 1365.7152 | 9.375%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 287 | 246 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 3851.9498 | 0 | 0 | 3851.9498 | 0 | 3674.4984 | 3.4298 | 1071.344 | 3674.4984 | 3.4298 | 1071.344 | 3870.8319 | 3.6131 | 1071.344 | 8.54%
2026 | 220 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 43 | 18 | 288.7705 | 86.56% | 13.18% | 0.2657% | 10.463 | 0 | 0 | 10.463 | 0 | 9.981 | 0.25096 | 39.771 | 9.981 | 0.25096 | 39.771 | 10.5143 | 0.26437 | 39.771 | 3.623%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 407 | 288 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 504.7808 | 0 | 0 | 504.7808 | 0 | 481.5266 | 4.0154 | 119.9206 | 481.5266 | 4.0154 | 119.9206 | 507.2552 | 4.2299 | 119.9206 | 6.797%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 79 | 75 | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 460.682 | 0 | 0 | 460.682 | 0 | 439.4593 | 1.0457 | 420.2652 | 439.4593 | 1.0457 | 420.2652 | 462.9403 | 1.1015 | 420.2652 | 9.479%
2026 | 221 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 910 | 544 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 969.5191 | 0 | 0 | 969.5191 | 0 | 924.8554 | 7.5846 | 121.9385 | 924.8554 | 7.5846 | 121.9385 | 974.2717 | 7.9899 | 121.9385 | 5.78%
2026 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 5 | 17.3686 | 98.33% | 0% | 1.666% | 1.0675 | 0 | 0 | 1.0675 | 0 | 1.0183 | 0.069711 | 14.607 | 1.0183 | 0.069711 | 14.607 | 1.0727 | 0.073436 | 14.607 | 6.146%
2026 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 9 | 9 | 171.5883 | 99.37% | 0.4538% | 0.1789% | 17.0503 | 0 | 0 | 17.0503 | 0 | 16.2648 | 0.12548 | 129.6199 | 16.2648 | 0.12548 | 129.6199 | 17.1338 | 0.13219 | 129.6199 | 9.937%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 213 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 150.4557 | 0 | 0 | 150.4557 | 0 | 143.5245 | 2.9697 | 48.3295 | 143.5245 | 2.9697 | 48.3295 | 151.1932 | 3.1284 | 48.3295 | 7.521%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 328 | 221 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 422.9789 | 0 | 0 | 422.9789 | 0 | 403.4931 | 3.0812 | 130.9513 | 403.4931 | 3.0812 | 130.9513 | 425.0523 | 3.2459 | 130.9513 | 6.621%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 245 | 177 | 2072.8837 | 91.06% | 8.635% | 0.3% | 136.3741 | 0 | 0 | 136.3741 | 0 | 130.0917 | 2.4678 | 52.716 | 130.0917 | 2.4678 | 52.716 | 137.0426 | 2.5996 | 52.716 | 6.579%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 71 | 51 | 536.3838 | 78.97% | 20.71% | 0.32% | 30.4256 | 0 | 0 | 30.4256 | 0 | 29.024 | 0.71106 | 40.8181 | 29.024 | 0.71106 | 40.8181 | 30.5748 | 0.74905 | 40.8181 | 5.672%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 52 | 38 | 788.7224 | 98.19% | 1.606% | 0.2041% | 56.5939 | 0 | 0 | 56.5939 | 0 | 53.9868 | 0.52981 | 101.899 | 53.9868 | 0.52981 | 101.899 | 56.8714 | 0.55812 | 101.899 | 7.175%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 183 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 263.0824 | 0 | 0 | 263.0824 | 0 | 250.9628 | 2.5514 | 98.3613 | 250.9628 | 2.5514 | 98.3613 | 264.3721 | 2.6878 | 98.3613 | 7.574%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 6 | 121.6067 | 92.98% | 6.845% | 0.1786% | 11.3066 | 0 | 0 | 11.3066 | 0 | 10.7857 | 0.083654 | 128.9325 | 10.7857 | 0.083654 | 128.9325 | 11.362 | 0.088123 | 128.9325 | 9.298%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 41 | 29 | 195.7251 | 81.71% | 17.81% | 0.4804% | 11.3124 | 0 | 0 | 11.3124 | 0 | 10.7913 | 0.40433 | 26.6896 | 10.7913 | 0.40433 | 26.6896 | 11.3679 | 0.42593 | 26.6896 | 5.78%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 245 | 2730.9177 | 98.3% | 1.373% | 0.325% | 184.2332 | 0 | 0 | 184.2332 | 0 | 175.746 | 3.4159 | 51.45 | 175.746 | 3.4159 | 51.45 | 185.1363 | 3.5984 | 51.45 | 6.746%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 613 | 5142.095 | 98.68% | 0.901% | 0.4182% | 360.8495 | 0 | 0 | 360.8495 | 0 | 344.2259 | 8.5466 | 40.2763 | 344.2259 | 8.5466 | 40.2763 | 362.6183 | 9.0033 | 40.2763 | 7.018%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 5 | 4 | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0041361 | 0 | 0 | 0.0041361 | 0 | 0.0039456 | 0.055769 | 0.070748 | 0.0039456 | 0.055769 | 0.070748 | 0.0041564 | 0.058749 | 0.070748 | 0.03619%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 292 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 212.6612 | 0 | 0 | 212.6612 | 0 | 202.8643 | 4.0711 | 49.8298 | 202.8643 | 4.0711 | 49.8298 | 213.7037 | 4.2887 | 49.8298 | 7.005%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 222 | 718.991 | 97.57% | 1.357% | 1.072% | 57.0469 | 0 | 0 | 57.0469 | 0 | 54.4188 | 3.0952 | 17.5818 | 54.4188 | 3.0952 | 17.5818 | 57.3265 | 3.2606 | 17.5818 | 7.934%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 89 | 447.7794 | 94.96% | 4.349% | 0.694% | 38.225 | 0 | 0 | 38.225 | 0 | 36.464 | 1.2409 | 29.386 | 36.464 | 1.2409 | 29.386 | 38.4124 | 1.3072 | 29.386 | 8.537%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 327 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 159.6551 | 0 | 0 | 159.6551 | 0 | 152.3001 | 4.5591 | 33.4055 | 152.3001 | 4.5591 | 33.4055 | 160.4377 | 4.8027 | 33.4055 | 6.818%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 216 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 317.6971 | 0 | 0 | 317.6971 | 0 | 303.0615 | 3.0115 | 100.6336 | 303.0615 | 3.0115 | 100.6336 | 319.2545 | 3.1724 | 100.6336 | 6.432%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 130 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 209.157 | 0 | 0 | 209.157 | 0 | 199.5216 | 1.8125 | 110.081 | 199.5216 | 1.8125 | 110.081 | 210.1823 | 1.9093 | 110.081 | 4.781%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 270 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1184.3293 | 0 | 0 | 1184.3293 | 0 | 1129.7697 | 3.7644 | 300.1181 | 1129.7697 | 3.7644 | 300.1181 | 1190.1348 | 3.9656 | 300.1181 | 5.002%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 252 | 162 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 616.8774 | 0 | 0 | 616.8774 | 0 | 588.4592 | 2.2587 | 260.5357 | 588.4592 | 2.2587 | 260.5357 | 619.9013 | 2.3793 | 260.5357 | 6.347%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 137 | 97 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 194.444 | 0 | 0 | 194.444 | 0 | 185.4864 | 1.3524 | 137.1533 | 185.4864 | 1.3524 | 137.1533 | 195.3972 | 1.4247 | 137.1533 | 6.886%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 81 | 69 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 189.8927 | 0 | 0 | 189.8927 | 0 | 181.1448 | 0.96202 | 188.2967 | 181.1448 | 0.96202 | 188.2967 | 190.8236 | 1.0134 | 188.2967 | 8.4%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 171 | 127 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 388.3774 | 0 | 0 | 388.3774 | 0 | 370.4857 | 1.7707 | 209.2347 | 370.4857 | 1.7707 | 209.2347 | 390.2812 | 1.8653 | 209.2347 | 7.284%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 498 | 306 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1282.7226 | 0 | 0 | 1282.7226 | 0 | 1223.6302 | 4.2663 | 286.8103 | 1223.6302 | 4.2663 | 286.8103 | 1289.0104 | 4.4943 | 286.8103 | 6.044%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 192 | 130 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 458.9623 | 0 | 0 | 458.9623 | 0 | 437.8188 | 1.8125 | 241.5556 | 437.8188 | 1.8125 | 241.5556 | 461.2121 | 1.9093 | 241.5556 | 6.625%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 126 | 113 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 323.9509 | 0 | 0 | 323.9509 | 0 | 309.0272 | 1.5755 | 196.1482 | 309.0272 | 1.5755 | 196.1482 | 325.5389 | 1.6597 | 196.1482 | 8.914%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 223 | 158 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1988.3938 | 0 | 0 | 1988.3938 | 0 | 1896.7926 | 2.2029 | 861.0508 | 1896.7926 | 2.2029 | 861.0508 | 1998.1408 | 2.3206 | 861.0508 | 7.039%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 275 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1374.0091 | 0 | 0 | 1374.0091 | 0 | 1310.7113 | 3.8341 | 341.8538 | 1310.7113 | 3.8341 | 341.8538 | 1380.7444 | 4.039 | 341.8538 | 5.074%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 46 | 663.2151 | 70.89% | 28.72% | 0.399% | 19.1377 | 0 | 0 | 19.1377 | 0 | 18.256 | 0.64135 | 28.4652 | 18.256 | 0.64135 | 28.4652 | 19.2315 | 0.67561 | 28.4652 | 2.886%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 59 | 29 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 122.9074 | 0 | 0 | 122.9074 | 0 | 117.2453 | 0.40433 | 289.977 | 117.2453 | 0.40433 | 289.977 | 123.5099 | 0.42593 | 289.977 | 4.858%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 499 | 344 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 2110.859 | 0 | 0 | 2110.859 | 0 | 2013.6161 | 4.7961 | 419.8404 | 2013.6161 | 4.7961 | 419.8404 | 2121.2064 | 5.0524 | 419.8404 | 6.833%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 651 | 565 | 65515.492 | 98.93% | 1.038% | 0.03019% | 5625.3221 | 0 | 0 | 5625.3221 | 0 | 5366.1752 | 7.8774 | 681.2122 | 5366.1752 | 7.8774 | 681.2122 | 5652.8973 | 8.2983 | 681.2122 | 8.586%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 110 | 860.3234 | 98.08% | 1.495% | 0.4234% | 73.0864 | 0 | 0 | 73.0864 | 0 | 69.7194 | 1.5337 | 45.4598 | 69.7194 | 1.5337 | 45.4598 | 73.4446 | 1.6156 | 45.4598 | 8.495%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 50 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 142.1904 | 0 | 0 | 142.1904 | 0 | 135.64 | 0.69711 | 194.5735 | 135.64 | 0.69711 | 194.5735 | 142.8874 | 0.73436 | 194.5735 | 8.97%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 134 | 111 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 89.2076 | 0 | 0 | 89.2076 | 0 | 85.098 | 1.5476 | 54.9873 | 85.098 | 1.5476 | 54.9873 | 89.6449 | 1.6303 | 54.9873 | 7.99%
2026 | 1233 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 250 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 504.7804 | 0 | 0 | 504.7804 | 0 | 481.5262 | 3.4856 | 138.1484 | 481.5262 | 3.4856 | 138.1484 | 507.2548 | 3.6718 | 138.1484 | 8.052%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 101 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 66.6975 | 0 | 0 | 66.6975 | 0 | 63.6249 | 1.4082 | 45.1827 | 63.6249 | 1.4082 | 45.1827 | 67.0245 | 1.4834 | 45.1827 | 6.478%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 52 | 38 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 27.166 | 0 | 0 | 27.166 | 0 | 25.9145 | 0.52981 | 48.9131 | 25.9145 | 0.52981 | 48.9131 | 27.2992 | 0.55812 | 48.9131 | 7.217%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 165 | 99 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 69.7467 | 0 | 0 | 69.7467 | 0 | 66.5337 | 1.3803 | 48.2028 | 66.5337 | 1.3803 | 48.2028 | 70.0886 | 1.454 | 48.2028 | 5.903%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 71 | 40 | 791.3356 | 98.7% | 1.112% | 0.1837% | 44.0048 | 0 | 0 | 44.0048 | 0 | 41.9776 | 0.55769 | 75.2703 | 41.9776 | 0.55769 | 75.2703 | 44.2205 | 0.58749 | 75.2703 | 5.561%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 75 | 64 | 376.72 | 96.88% | 2.523% | 0.5996% | 31.143 | 0 | 0 | 31.143 | 0 | 29.7083 | 0.89231 | 33.2938 | 29.7083 | 0.89231 | 33.2938 | 31.2956 | 0.93998 | 33.2938 | 8.267%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 363 | 4437.6588 | 97.91% | 1.769% | 0.321% | 253.1626 | 0 | 0 | 253.1626 | 0 | 241.4999 | 5.061 | 47.7174 | 241.4999 | 5.061 | 47.7174 | 254.4036 | 5.3315 | 47.7174 | 5.705%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 269 | 189 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 260.4973 | 0 | 0 | 260.4973 | 0 | 248.4967 | 2.6351 | 94.3029 | 248.4967 | 2.6351 | 94.3029 | 261.7743 | 2.7759 | 94.3029 | 6.96%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 265 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 273.401 | 0 | 0 | 273.401 | 0 | 260.8059 | 3.6947 | 70.5891 | 260.8059 | 3.6947 | 70.5891 | 274.7412 | 3.8921 | 70.5891 | 7.458%
2026 | 240 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 56 | 960.3446 | 65.96% | 33.81% | 0.2324% | 30.3183 | 0 | 0 | 30.3183 | 0 | 28.9216 | 0.78077 | 37.0425 | 28.9216 | 0.78077 | 37.0425 | 30.4669 | 0.82249 | 37.0425 | 3.157%
2026 | 242 | 242-1427F | Tier-2 | Tier-2---20 | Tier-2---19 | 5 | 3 | 24.991 | 71.07% | 28.66% | 0.2708% | 1.0657 | 0 | 0 | 1.0657 | 0 | 1.0166 | 0.041827 | 24.305 | 1.0166 | 0.041827 | 24.305 | 1.0709 | 0.044062 | 24.305 | 4.264%
2026 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 470 | 1 | 404.2589 | 29.5% | 68.39% | 2.113% | 0.025372 | 0 | 0 | 0.025372 | 0 | 0.024204 | 0.013942 | 1.736 | 0.024204 | 0.013942 | 1.736 | 0.025497 | 0.014687 | 1.736 | 0.006276%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 310 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 227.682 | 0 | 0 | 227.682 | 0 | 217.1931 | 4.3221 | 50.2517 | 217.1931 | 4.3221 | 50.2517 | 228.7981 | 4.553 | 50.2517 | 6.722%
2026 | 246 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 161 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 89.2584 | 0 | 0 | 89.2584 | 0 | 85.1465 | 2.2447 | 37.9321 | 85.1465 | 2.2447 | 37.9321 | 89.696 | 2.3646 | 37.9321 | 6.562%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 9 | 9 | 105.2026 | 98.18% | 1.532% | 0.2854% | 10.3291 | 0 | 0 | 10.3291 | 0 | 9.8533 | 0.12548 | 78.5241 | 9.8533 | 0.12548 | 78.5241 | 10.3797 | 0.13219 | 78.5241 | 9.818%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 292 | 3753.23 | 95.85% | 3.876% | 0.273% | 226.3951 | 0 | 0 | 226.3951 | 0 | 215.9656 | 4.0711 | 53.0478 | 215.9656 | 4.0711 | 53.0478 | 227.5049 | 4.2887 | 53.0478 | 6.032%
2026 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 98 | 86 | 49.4853 | 86.66% | 6.71% | 6.626% | 3.7635 | 0 | 0 | 3.7635 | 0 | 3.5901 | 1.199 | 2.9942 | 3.5901 | 1.199 | 2.9942 | 3.7819 | 1.2631 | 2.9942 | 7.605%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 96 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 460.0093 | 0 | 0 | 460.0093 | 0 | 438.8176 | 1.3385 | 327.8528 | 438.8176 | 1.3385 | 327.8528 | 462.2643 | 1.41 | 327.8528 | 8.68%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 112 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 155.9138 | 0 | 0 | 155.9138 | 0 | 148.7311 | 1.5615 | 95.2467 | 148.7311 | 1.5615 | 95.2467 | 156.6781 | 1.645 | 95.2467 | 7.743%
2026 | 283 | 283-80F | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 2 | 22.6843 | 50.28% | 49.56% | 0.1579% | 1.1406 | 0 | 0 | 1.1406 | 0 | 1.0881 | 0.027885 | 39.0209 | 1.0881 | 0.027885 | 39.0209 | 1.1462 | 0.029374 | 39.0209 | 5.028%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 170 | 2 | 481.2843 | 94.31% | 4.95% | 0.7414% | 0.53399 | 0 | 0 | 0.53399 | 0 | 0.50939 | 0.027885 | 18.2678 | 0.50939 | 0.027885 | 18.2678 | 0.53661 | 0.029374 | 18.2678 | 0.111%
2026 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 7 | 2 | 41.8014 | 98.23% | 1.253% | 0.5152% | 1.1732 | 0 | 0 | 1.1732 | 0 | 1.1192 | 0.027885 | 40.1354 | 1.1192 | 0.027885 | 40.1354 | 1.179 | 0.029374 | 40.1354 | 2.807%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 34 | 550.61 | 92.88% | 6.93% | 0.1872% | 40.4378 | 0 | 0 | 40.4378 | 0 | 38.5749 | 0.47404 | 81.3752 | 38.5749 | 0.47404 | 81.3752 | 40.636 | 0.49937 | 81.3752 | 7.344%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 43 | 29 | 3.2301 | 78.97% | 0% | 21.03% | 0.17202 | 0 | 0 | 0.17202 | 0 | 0.1641 | 0.40433 | 0.40586 | 0.1641 | 0.40433 | 0.40586 | 0.17287 | 0.42593 | 0.40586 | 5.326%
2026 | 198 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 68 | 458.7821 | 99.48% | 0% | 0.5194% | 44.9785 | 0 | 0 | 44.9785 | 0 | 42.9064 | 0.94808 | 45.2563 | 42.9064 | 0.94808 | 45.2563 | 45.199 | 0.99873 | 45.2563 | 9.804%
2026 | 231 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 194 | 754.1323 | 92.41% | 6.882% | 0.7076% | 54.0793 | 0 | 0 | 54.0793 | 0 | 51.588 | 2.7048 | 19.0727 | 51.588 | 2.7048 | 19.0727 | 54.3444 | 2.8493 | 19.0727 | 7.171%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 49 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 202.683 | 0 | 0 | 202.683 | 0 | 193.3458 | 0.68317 | 283.0119 | 193.3458 | 0.68317 | 283.0119 | 203.6765 | 0.71967 | 283.0119 | 8.42%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 86 | 4762.848 | 95.55% | 4.384% | 0.07015% | 359.046 | 0 | 0 | 359.046 | 0 | 342.5054 | 1.199 | 285.6505 | 342.5054 | 1.199 | 285.6505 | 360.806 | 1.2631 | 285.6505 | 7.538%
2026 | 308 | 308-486AE | Tier-2 | Tier-2---16 | Tier-2---8 | 142 | 1 | 164.6778 | 2.383% | 96.2% | 1.419% | 0.002764 | 0 | 0 | 0.002764 | 0 | 0.0026367 | 0.013942 | 0.18911 | 0.0026367 | 0.013942 | 0.18911 | 0.0027776 | 0.014687 | 0.18911 | 0.001678%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 39 | 14 | 95.5263 | 19.37% | 79.9% | 0.729% | 0.66438 | 0 | 0 | 0.66438 | 0 | 0.63377 | 0.19519 | 3.2469 | 0.63377 | 0.19519 | 3.2469 | 0.66763 | 0.20562 | 3.2469 | 0.6955%
2026 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 14 | 7 | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9562 | 0 | 0 | 1.9562 | 0 | 1.8661 | 0.097596 | 19.1204 | 1.8661 | 0.097596 | 19.1204 | 1.9658 | 0.10281 | 19.1204 | 4.235%
2026 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 15 | 12 | 15.6056 | 49.38% | 48.09% | 2.529% | 0.61652 | 0 | 0 | 0.61652 | 0 | 0.58812 | 0.16731 | 3.5152 | 0.58812 | 0.16731 | 3.5152 | 0.61955 | 0.17625 | 3.5152 | 3.951%
2026 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 12 | 278.652 | 16.28% | 83.57% | 0.1501% | 3.8883 | 0 | 0 | 3.8883 | 0 | 3.7092 | 0.16731 | 22.17 | 3.7092 | 0.16731 | 22.17 | 3.9074 | 0.17625 | 22.17 | 1.395%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 79 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.15148 | 0 | 0 | 0.15148 | 0 | 0.1445 | 1.1014 | 0.13119 | 0.1445 | 1.1014 | 0.13119 | 0.15222 | 1.1603 | 0.13119 | 0.09476%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 15 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0086582 | 0 | 0 | 0.0086582 | 0 | 0.0082593 | 0.20913 | 0.039493 | 0.0082593 | 0.20913 | 0.039493 | 0.0087006 | 0.22031 | 0.039493 | 0.004284%
2026 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 9 | 9 | 14.6681 | 98.1% | 0% | 1.899% | 1.439 | 0 | 0 | 1.439 | 0 | 1.3727 | 0.12548 | 10.9393 | 1.3727 | 0.12548 | 10.9393 | 1.446 | 0.13219 | 10.9393 | 9.81%
2026 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 39 | 34 | 209.8559 | 99.5% | 0% | 0.498% | 18.204 | 0 | 0 | 18.204 | 0 | 17.3654 | 0.47404 | 36.633 | 17.3654 | 0.47404 | 36.633 | 18.2933 | 0.49937 | 36.633 | 8.675%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 15 | 8 | 302.428 | 99.27% | 0.6612% | 0.06922% | 16.0117 | 0 | 0 | 16.0117 | 0 | 15.2741 | 0.11154 | 136.9401 | 15.2741 | 0.11154 | 136.9401 | 16.0902 | 0.1175 | 136.9401 | 5.294%
2026 | 233 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 476 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 289.7593 | 0 | 0 | 289.7593 | 0 | 276.4107 | 6.6365 | 41.6499 | 276.4107 | 6.6365 | 41.6499 | 291.1797 | 6.9911 | 41.6499 | 8.044%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 709 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 1168.497 | 0 | 0 | 1168.497 | 0 | 1114.6668 | 9.8851 | 112.7625 | 1114.6668 | 9.8851 | 112.7625 | 1174.225 | 10.4133 | 112.7625 | 8.424%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 711 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 476.0154 | 0 | 0 | 476.0154 | 0 | 454.0863 | 9.913 | 45.8073 | 454.0863 | 9.913 | 45.8073 | 478.3488 | 10.4426 | 45.8073 | 8.545%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 297 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 1104.4919 | 0 | 0 | 1104.4919 | 0 | 1053.6102 | 4.1409 | 254.4424 | 1053.6102 | 4.1409 | 254.4424 | 1109.906 | 4.3621 | 254.4424 | 8.168%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 373 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 869.7107 | 0 | 0 | 869.7107 | 0 | 829.6449 | 5.2005 | 159.5326 | 829.6449 | 5.2005 | 159.5326 | 873.974 | 5.4783 | 159.5326 | 7.764%
2026 | 1039 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 225 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1540.0982 | 0 | 0 | 1540.0982 | 0 | 1469.1491 | 3.137 | 468.3272 | 1469.1491 | 3.137 | 468.3272 | 1547.6477 | 3.3046 | 468.3272 | 6.549%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 83 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 688.1193 | 0 | 0 | 688.1193 | 0 | 656.4191 | 1.1572 | 567.2429 | 656.4191 | 1.1572 | 567.2429 | 691.4924 | 1.219 | 567.2429 | 7.525%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 279 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 1437.3667 | 0 | 0 | 1437.3667 | 0 | 1371.1502 | 3.8899 | 352.49 | 1371.1502 | 3.8899 | 352.49 | 1444.4126 | 4.0977 | 352.49 | 7.722%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 161 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 709.5156 | 0 | 0 | 709.5156 | 0 | 676.8297 | 2.2447 | 301.5224 | 676.8297 | 2.2447 | 301.5224 | 712.9936 | 2.3646 | 301.5224 | 7.694%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 46 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 205.229 | 0 | 0 | 205.229 | 0 | 195.7745 | 0.64135 | 305.2561 | 195.7745 | 0.64135 | 305.2561 | 206.235 | 0.67561 | 305.2561 | 8.147%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 25 | 25 | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 221.4151 | 0 | 0 | 221.4151 | 0 | 211.215 | 0.34856 | 605.9695 | 211.215 | 0.34856 | 605.9695 | 222.5005 | 0.36718 | 605.9695 | 9.993%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 28 | 25 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 157.6982 | 0 | 0 | 157.6982 | 0 | 150.4334 | 0.34856 | 431.5888 | 150.4334 | 0.34856 | 431.5888 | 158.4712 | 0.36718 | 431.5888 | 7.919%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 69 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 361.4968 | 0 | 0 | 361.4968 | 0 | 344.8434 | 0.96202 | 358.4584 | 344.8434 | 0.96202 | 358.4584 | 363.2688 | 1.0134 | 358.4584 | 7.935%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 11 | 465.1006 | 62.84% | 37.09% | 0.07221% | 29.2268 | 0 | 0 | 29.2268 | 0 | 27.8804 | 0.15337 | 181.7909 | 27.8804 | 0.15337 | 181.7909 | 29.3701 | 0.16156 | 181.7909 | 6.284%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 147 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 1092.9655 | 0 | 0 | 1092.9655 | 0 | 1042.6148 | 2.0495 | 508.7127 | 1042.6148 | 2.0495 | 508.7127 | 1098.3232 | 2.159 | 508.7127 | 8.075%
2026 | 350 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 327 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1382.7374 | 0 | 0 | 1382.7374 | 0 | 1319.0375 | 4.5591 | 289.318 | 1319.0375 | 4.5591 | 289.318 | 1389.5155 | 4.8027 | 289.318 | 6.742%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 75 | 3653.654 | 88.54% | 11.39% | 0.07412% | 272.5948 | 0 | 0 | 272.5948 | 0 | 260.0369 | 1.0457 | 248.6794 | 260.0369 | 1.0457 | 248.6794 | 273.9311 | 1.1015 | 248.6794 | 7.461%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 129 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 421.7122 | 0 | 0 | 421.7122 | 0 | 402.2848 | 1.7986 | 223.6711 | 402.2848 | 1.7986 | 223.6711 | 423.7795 | 1.8947 | 223.6711 | 5.622%
2026 | 355 | 355-65R | Tier-2 | Tier-2---21 | Tier-2---24 | 1 | 1 | 0.06699 | 46.11% | 0% | 53.89% | 0.0030886 | 0 | 0 | 0.0030886 | 0 | 0.0029463 | 0.013942 | 0.21132 | 0.0029463 | 0.013942 | 0.21132 | 0.0031038 | 0.014687 | 0.21132 | 4.611%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 58 | 35 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 81.9442 | 0 | 0 | 81.9442 | 0 | 78.1692 | 0.48798 | 160.1893 | 78.1692 | 0.48798 | 160.1893 | 82.3459 | 0.51405 | 160.1893 | 4.824%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 119 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 293.9946 | 0 | 0 | 293.9946 | 0 | 280.4509 | 1.6591 | 169.0347 | 280.4509 | 1.6591 | 169.0347 | 295.4358 | 1.7478 | 169.0347 | 5.407%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 429 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 912.4735 | 0 | 0 | 912.4735 | 0 | 870.4378 | 5.9812 | 145.528 | 870.4378 | 5.9812 | 145.528 | 916.9464 | 6.3008 | 145.528 | 5.698%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 730 | 400 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 485.9291 | 0 | 0 | 485.9291 | 0 | 463.5433 | 5.5769 | 83.1182 | 463.5433 | 5.5769 | 83.1182 | 488.3111 | 5.8749 | 83.1182 | 5.228%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 40 | 22 | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 68.1695 | 0 | 0 | 68.1695 | 0 | 65.0291 | 0.30673 | 212.0073 | 65.0291 | 0.30673 | 212.0073 | 68.5037 | 0.32312 | 212.0073 | 5.448%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 48 | 44 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 465.8919 | 0 | 0 | 465.8919 | 0 | 444.4292 | 0.61346 | 724.4625 | 444.4292 | 0.61346 | 724.4625 | 468.1757 | 0.64624 | 724.4625 | 9.137%
2026 | 1458 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 17 | 10 | 878.9304 | 95.49% | 4.482% | 0.03213% | 49.3677 | 0 | 0 | 49.3677 | 0 | 47.0934 | 0.13942 | 337.7739 | 47.0934 | 0.13942 | 337.7739 | 49.6097 | 0.14687 | 337.7739 | 5.617%
2026 | 1458 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 141 | 16869.708 | 98.79% | 1.184% | 0.02933% | 867.0712 | 0 | 0 | 867.0712 | 0 | 827.127 | 1.9659 | 420.7451 | 827.127 | 1.9659 | 420.7451 | 871.3215 | 2.0709 | 420.7451 | 5.14%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 242 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 1149.9849 | 0 | 0 | 1149.9849 | 0 | 1097.0075 | 3.374 | 325.1324 | 1097.0075 | 3.374 | 325.1324 | 1155.6221 | 3.5543 | 325.1324 | 6.498%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 231 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 610.5815 | 0 | 0 | 610.5815 | 0 | 582.4533 | 3.2207 | 180.8486 | 582.4533 | 3.2207 | 180.8486 | 613.5746 | 3.3928 | 180.8486 | 5.853%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 172 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 727.1836 | 0 | 0 | 727.1836 | 0 | 693.6838 | 2.3981 | 289.2671 | 693.6838 | 2.3981 | 289.2671 | 730.7483 | 2.5262 | 289.2671 | 6.185%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 21 | 9 | 599.5834 | 97.21% | 2.746% | 0.04768% | 24.9785 | 0 | 0 | 24.9785 | 0 | 23.8278 | 0.12548 | 189.8923 | 23.8278 | 0.12548 | 189.8923 | 25.101 | 0.13219 | 189.8923 | 4.166%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 13 | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 124.4356 | 0 | 0 | 124.4356 | 0 | 118.7032 | 0.18125 | 654.9149 | 118.7032 | 0.18125 | 654.9149 | 125.0456 | 0.19093 | 654.9149 | 9.254%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 344 | 227 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 2446.3909 | 0 | 0 | 2446.3909 | 0 | 2333.6907 | 3.1649 | 737.3666 | 2333.6907 | 3.1649 | 737.3666 | 2458.383 | 3.334 | 737.3666 | 6.506%
2026 | 283 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 140 | 38 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 35.1557 | 0 | 0 | 35.1557 | 0 | 33.5361 | 0.52981 | 63.2988 | 33.5361 | 0.52981 | 63.2988 | 35.328 | 0.55812 | 63.2988 | 2.416%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 76 | 41 | 924.8041 | 18.79% | 81.02% | 0.1888% | 9.3732 | 0 | 0 | 9.3732 | 0 | 8.9414 | 0.57163 | 15.6418 | 8.9414 | 0.57163 | 15.6418 | 9.4191 | 0.60218 | 15.6418 | 1.014%
2026 | 1138 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 458 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 169.3729 | 0 | 0 | 169.3729 | 0 | 161.5702 | 6.3856 | 25.3024 | 161.5702 | 6.3856 | 25.3024 | 170.2031 | 6.7268 | 25.3024 | 5.399%
2026 | 401 | 401-684R | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 1 | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049818 | 0 | 0 | 0.049818 | 0 | 0.047523 | 0.013942 | 3.4085 | 0.047523 | 0.013942 | 3.4085 | 0.050062 | 0.014687 | 3.4085 | 3.121%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 193 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 102.5551 | 0 | 0 | 102.5551 | 0 | 97.8306 | 2.6909 | 36.3566 | 97.8306 | 2.6909 | 36.3566 | 103.0579 | 2.8346 | 36.3566 | 5.521%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 494 | 6370.0414 | 98.47% | 1.262% | 0.272% | 361.9772 | 0 | 0 | 361.9772 | 0 | 345.3017 | 6.8875 | 50.1346 | 345.3017 | 6.8875 | 50.1346 | 363.7516 | 7.2555 | 50.1346 | 5.682%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 47 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 13.271 | 0 | 0 | 13.271 | 0 | 12.6596 | 0.65529 | 19.3192 | 12.6596 | 0.65529 | 19.3192 | 13.336 | 0.6903 | 19.3192 | 0.9827%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 84 | 81 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 330.5962 | 0 | 0 | 330.5962 | 0 | 315.3663 | 1.1293 | 279.252 | 315.3663 | 1.1293 | 279.252 | 332.2168 | 1.1897 | 279.252 | 9.397%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 49 | 582.1633 | 91.34% | 8.391% | 0.2732% | 54.2799 | 0 | 0 | 54.2799 | 0 | 51.7793 | 0.68317 | 75.7925 | 51.7793 | 0.68317 | 75.7925 | 54.546 | 0.71967 | 75.7925 | 9.324%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 133 | 119 | 4750.1268 | 98% | 1.916% | 0.08125% | 416.5218 | 0 | 0 | 416.5218 | 0 | 397.3335 | 1.6591 | 239.4827 | 397.3335 | 1.6591 | 239.4827 | 418.5636 | 1.7478 | 239.4827 | 8.769%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 97 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 506.3705 | 0 | 0 | 506.3705 | 0 | 483.043 | 1.3524 | 357.1742 | 483.043 | 1.3524 | 357.1742 | 508.8527 | 1.4247 | 357.1742 | 9.467%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 201 | 196 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 171.9277 | 0 | 0 | 171.9277 | 0 | 164.0074 | 2.7327 | 60.0169 | 164.0074 | 2.7327 | 60.0169 | 172.7705 | 2.8787 | 60.0169 | 9.37%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 3 | 3 | 88.141 | 1.745% | 98.17% | 0.08447% | 0.15379 | 0 | 0 | 0.15379 | 0 | 0.14671 | 0.041827 | 3.5075 | 0.14671 | 0.041827 | 3.5075 | 0.15455 | 0.044062 | 3.5075 | 0.1745%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 89 | 852.9261 | 84.92% | 14.72% | 0.3553% | 44.4597 | 0 | 0 | 44.4597 | 0 | 42.4116 | 1.2409 | 34.1791 | 42.4116 | 1.2409 | 34.1791 | 44.6777 | 1.3072 | 34.1791 | 5.213%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 144 | 71 | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0335 | 0 | 0 | 15.0335 | 0 | 14.3409 | 0.9899 | 14.4872 | 14.3409 | 0.9899 | 14.4872 | 15.1071 | 1.0428 | 14.4872 | 2.857%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 408 | 11572.221 | 88.48% | 11.4% | 0.1243% | 547.4938 | 0 | 0 | 547.4938 | 0 | 522.2719 | 5.6885 | 91.8126 | 522.2719 | 5.6885 | 91.8126 | 550.1776 | 5.9924 | 91.8126 | 4.731%
2026 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 54 | 50 | 704.6091 | 96.62% | 3.132% | 0.2514% | 63.0339 | 0 | 0 | 63.0339 | 0 | 60.1301 | 0.69711 | 86.2557 | 60.1301 | 0.69711 | 86.2557 | 63.3429 | 0.73436 | 86.2557 | 8.946%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 25 | 25 | 549.9829 | 98.93% | 0.9134% | 0.161% | 54.4074 | 0 | 0 | 54.4074 | 0 | 51.901 | 0.34856 | 148.9023 | 51.901 | 0.34856 | 148.9023 | 54.6741 | 0.36718 | 148.9023 | 9.893%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 74 | 50 | 474.7376 | 91.31% | 8.325% | 0.3651% | 29.2893 | 0 | 0 | 29.2893 | 0 | 27.94 | 0.69711 | 40.0795 | 27.94 | 0.69711 | 40.0795 | 29.4329 | 0.73436 | 40.0795 | 6.17%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 73 | 26 | 141.3846 | 51% | 48.51% | 0.49% | 2.5682 | 0 | 0 | 2.5682 | 0 | 2.4499 | 0.3625 | 6.7584 | 2.4499 | 0.3625 | 6.7584 | 2.5808 | 0.38187 | 6.7584 | 1.816%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 122 | 84 | 333.8465 | 96.62% | 2.31% | 1.072% | 22.2086 | 0 | 0 | 22.2086 | 0 | 21.1855 | 1.1712 | 18.0895 | 21.1855 | 1.1712 | 18.0895 | 22.3175 | 1.2337 | 18.0895 | 6.652%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 354 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 292.8867 | 0 | 0 | 292.8867 | 0 | 279.394 | 4.9356 | 56.6083 | 279.394 | 4.9356 | 56.6083 | 294.3224 | 5.1993 | 56.6083 | 8.579%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 465 | 363 | 571.2373 | 70.71% | 27.93% | 1.361% | 31.5311 | 0 | 0 | 31.5311 | 0 | 30.0786 | 5.061 | 5.9431 | 30.0786 | 5.061 | 5.9431 | 31.6857 | 5.3315 | 5.9431 | 5.52%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 275 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 746.4038 | 0 | 0 | 746.4038 | 0 | 712.0185 | 3.8341 | 185.7054 | 712.0185 | 3.8341 | 185.7054 | 750.0626 | 4.039 | 185.7054 | 7.749%
2026 | 445 | 445-1315 | Tier-2 | Tier-2---19 | Tier-2---11 | 4 | 1 | 26.2494 | 99.59% | 0% | 0.4079% | 0.65356 | 0 | 0 | 0.65356 | 0 | 0.62345 | 0.013942 | 44.7164 | 0.62345 | 0.013942 | 44.7164 | 0.65676 | 0.014687 | 44.7164 | 2.49%
2026 | 445 | 445-1323 | Tier-2 | Tier-2---18 | Tier-2---12 | 6 | 8 | 78.5439 | 99.26% | 0.525% | 0.2138% | 10.3952 | 0 | 0 | 10.3952 | 0 | 9.9163 | 0.11154 | 88.9046 | 9.9163 | 0.11154 | 88.9046 | 10.4461 | 0.1175 | 88.9046 | 13.23%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 197 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 623.982 | 0 | 0 | 623.982 | 0 | 595.2364 | 2.7466 | 216.7151 | 595.2364 | 2.7466 | 216.7151 | 627.0407 | 2.8934 | 216.7151 | 8.606%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 73 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 107.0683 | 0 | 0 | 107.0683 | 0 | 102.1359 | 1.0178 | 100.3509 | 102.1359 | 1.0178 | 100.3509 | 107.5931 | 1.0722 | 100.3509 | 6.677%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 439 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 848.1098 | 0 | 0 | 848.1098 | 0 | 809.0391 | 6.1207 | 132.1816 | 809.0391 | 6.1207 | 132.1816 | 852.2672 | 6.4477 | 132.1816 | 7.986%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 220 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 138.3664 | 0 | 0 | 138.3664 | 0 | 131.9921 | 3.0673 | 43.032 | 131.9921 | 3.0673 | 43.032 | 139.0446 | 3.2312 | 43.032 | 7.832%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 197 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 257.8827 | 0 | 0 | 257.8827 | 0 | 246.0026 | 2.7466 | 89.5652 | 246.0026 | 2.7466 | 89.5652 | 259.1468 | 2.8934 | 89.5652 | 7.01%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 511 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 339.1443 | 0 | 0 | 339.1443 | 0 | 323.5206 | 7.1245 | 45.4095 | 323.5206 | 7.1245 | 45.4095 | 340.8067 | 7.5052 | 45.4095 | 7.671%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 25 | 22 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 115.6761 | 0 | 0 | 115.6761 | 0 | 110.3472 | 0.30673 | 359.7531 | 110.3472 | 0.30673 | 359.7531 | 116.2432 | 0.32312 | 359.7531 | 8.557%
2026 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 4 | 16.696 | 99.41% | 0% | 0.5907% | 1.6597 | 0 | 0 | 1.6597 | 0 | 1.5833 | 0.055769 | 28.3898 | 1.5833 | 0.055769 | 28.3898 | 1.6679 | 0.058749 | 28.3898 | 9.941%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 51 | 45 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 104.1172 | 0 | 0 | 104.1172 | 0 | 99.3207 | 0.6274 | 158.3045 | 99.3207 | 0.6274 | 158.3045 | 104.6275 | 0.66093 | 158.3045 | 8.593%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 184 | 154 | 2612.2711 | 91.91% | 7.885% | 0.2065% | 200.9452 | 0 | 0 | 200.9452 | 0 | 191.6881 | 2.1471 | 89.2772 | 191.6881 | 2.1471 | 89.2772 | 201.9302 | 2.2618 | 89.2772 | 7.692%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 314 | 213 | 2119.752 | 55.7% | 43.96% | 0.3458% | 80.0895 | 0 | 0 | 80.0895 | 0 | 76.3999 | 2.9697 | 25.7264 | 76.3999 | 2.9697 | 25.7264 | 80.4821 | 3.1284 | 25.7264 | 3.778%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 151 | 520.639 | 76.18% | 22.78% | 1.038% | 29.6503 | 0 | 0 | 29.6503 | 0 | 28.2843 | 2.1053 | 13.4349 | 28.2843 | 2.1053 | 13.4349 | 29.7956 | 2.2178 | 13.4349 | 5.695%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 170 | 140 | 630.7627 | 79.12% | 20.09% | 0.7869% | 41.1002 | 0 | 0 | 41.1002 | 0 | 39.2068 | 1.9519 | 20.0863 | 39.2068 | 1.9519 | 20.0863 | 41.3016 | 2.0562 | 20.0863 | 6.516%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 493 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 573.9427 | 0 | 0 | 573.9427 | 0 | 547.5024 | 6.8735 | 79.6535 | 547.5024 | 6.8735 | 79.6535 | 576.7562 | 7.2408 | 79.6535 | 6.304%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 303 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 386.9071 | 0 | 0 | 386.9071 | 0 | 369.0831 | 4.2245 | 87.367 | 369.0831 | 4.2245 | 87.367 | 388.8037 | 4.4502 | 87.367 | 6.854%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 418 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 457.0253 | 0 | 0 | 457.0253 | 0 | 435.9711 | 5.8279 | 74.8079 | 435.9711 | 5.8279 | 74.8079 | 459.2656 | 6.1393 | 74.8079 | 6.791%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 72 | 55 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 110.7812 | 0 | 0 | 110.7812 | 0 | 105.6777 | 0.76683 | 137.8119 | 105.6777 | 0.76683 | 137.8119 | 111.3242 | 0.8078 | 137.8119 | 7.408%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 26 | 26 | 625.3129 | 96.7% | 3.156% | 0.1473% | 60.4656 | 0 | 0 | 60.4656 | 0 | 57.6801 | 0.3625 | 159.1178 | 57.6801 | 0.3625 | 159.1178 | 60.762 | 0.38187 | 159.1178 | 9.67%
2026 | 441 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 130 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 409.3932 | 0 | 0 | 409.3932 | 0 | 390.5333 | 1.8125 | 215.467 | 390.5333 | 1.8125 | 215.467 | 411.4 | 1.9093 | 215.467 | 7.782%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 161 | 123 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 169.3511 | 0 | 0 | 169.3511 | 0 | 161.5495 | 1.7149 | 94.2034 | 161.5495 | 1.7149 | 94.2034 | 170.1813 | 1.8065 | 94.2034 | 7.3%
2026 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 15 | 296.7138 | 97.11% | 2.719% | 0.1664% | 24.0127 | 0 | 0 | 24.0127 | 0 | 22.9065 | 0.20913 | 109.5302 | 22.9065 | 0.20913 | 109.5302 | 24.1304 | 0.22031 | 109.5302 | 8.093%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 126 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 494.986 | 0 | 0 | 494.986 | 0 | 472.183 | 1.7567 | 268.7855 | 472.183 | 1.7567 | 268.7855 | 497.4124 | 1.8506 | 268.7855 | 5.982%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 22 | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.7456 | 0 | 0 | 36.7456 | 0 | 35.0528 | 0.30673 | 114.2789 | 35.0528 | 0.30673 | 114.2789 | 36.9257 | 0.32312 | 114.2789 | 4.638%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 41 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 63.1703 | 0 | 0 | 63.1703 | 0 | 60.2602 | 0.57163 | 105.4174 | 60.2602 | 0.57163 | 105.4174 | 63.4799 | 0.60218 | 105.4174 | 5.579%
2026 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 18 | 5 | 537.0702 | 32.53% | 67.41% | 0.0594% | 4.8529 | 0 | 0 | 4.8529 | 0 | 4.6294 | 0.069711 | 66.4076 | 4.6294 | 0.069711 | 66.4076 | 4.8767 | 0.073436 | 66.4076 | 0.9036%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 5 | 5 | 137.227 | 99.9% | 0% | 0.1049% | 13.7083 | 0 | 0 | 13.7083 | 0 | 13.0768 | 0.069711 | 187.5847 | 13.0768 | 0.069711 | 187.5847 | 13.7755 | 0.073436 | 187.5847 | 9.99%
2026 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 19 | 625.5425 | 99.9% | 0% | 0.09615% | 59.3694 | 0 | 0 | 59.3694 | 0 | 56.6344 | 0.2649 | 213.7925 | 56.6344 | 0.2649 | 213.7925 | 59.6604 | 0.27906 | 213.7925 | 9.491%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 10 | 181.2174 | 99.84% | 0% | 0.161% | 15.0771 | 0 | 0 | 15.0771 | 0 | 14.3826 | 0.13942 | 103.1579 | 14.3826 | 0.13942 | 103.1579 | 15.1511 | 0.14687 | 103.1579 | 8.32%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 58 | 2823.7515 | 99.93% | 0% | 0.06613% | 230.5201 | 0 | 0 | 230.5201 | 0 | 219.9005 | 0.80865 | 271.9345 | 219.9005 | 0.80865 | 271.9345 | 231.6501 | 0.85186 | 271.9345 | 8.164%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 2 | 3 | 39.0262 | 97.23% | 2.586% | 0.1833% | 5.6918 | 0 | 0 | 5.6918 | 0 | 5.4296 | 0.041827 | 129.8115 | 5.4296 | 0.041827 | 129.8115 | 5.7197 | 0.044062 | 129.8115 | 14.58%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 53 | 41 | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 265.4015 | 0 | 0 | 265.4015 | 0 | 253.175 | 0.57163 | 442.8972 | 253.175 | 0.57163 | 442.8972 | 266.7025 | 0.60218 | 442.8972 | 7.713%
2026 | 454 | 454-49F | Tier-2 | Tier-2---13 | Tier-2---8 | 52 | 1 | 292.9743 | 76.06% | 23.59% | 0.3558% | 0.42851 | 0 | 0 | 0.42851 | 0 | 0.40877 | 0.013942 | 29.3187 | 0.40877 | 0.013942 | 29.3187 | 0.43061 | 0.014687 | 29.3187 | 0.1463%
2026 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 11 | 10 | 88.0149 | 97.35% | 2.233% | 0.4157% | 7.7894 | 0 | 0 | 7.7894 | 0 | 7.4306 | 0.13942 | 53.2952 | 7.4306 | 0.13942 | 53.2952 | 7.8276 | 0.14687 | 53.2952 | 8.85%
2026 | 260 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 198 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 116.9805 | 0 | 0 | 116.9805 | 0 | 111.5914 | 2.7606 | 40.4233 | 111.5914 | 2.7606 | 40.4233 | 117.5539 | 2.9081 | 40.4233 | 8.487%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 125 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 455.719 | 0 | 0 | 455.719 | 0 | 434.725 | 1.7428 | 249.4426 | 434.725 | 1.7428 | 249.4426 | 457.953 | 1.8359 | 249.4426 | 8.656%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 475 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 1479.703 | 0 | 0 | 1479.703 | 0 | 1411.5361 | 6.6226 | 213.1397 | 1411.5361 | 6.6226 | 213.1397 | 1486.9564 | 6.9764 | 213.1397 | 8.839%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 128 | 21 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 66.2676 | 0 | 0 | 66.2676 | 0 | 63.2148 | 0.29279 | 215.9064 | 63.2148 | 0.29279 | 215.9064 | 66.5924 | 0.30843 | 215.9064 | 1.558%
2026 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 16 | 800.5503 | 21.6% | 78.32% | 0.07823% | 13.8344 | 0 | 0 | 13.8344 | 0 | 13.1971 | 0.22308 | 59.1593 | 13.1971 | 0.22308 | 59.1593 | 13.9022 | 0.235 | 59.1593 | 1.728%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 23 | 22 | 204.0835 | 99.63% | 0% | 0.368% | 19.4492 | 0 | 0 | 19.4492 | 0 | 18.5532 | 0.30673 | 60.487 | 18.5532 | 0.30673 | 60.487 | 19.5445 | 0.32312 | 60.487 | 9.53%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 154 | 23 | 733.6834 | 99.51% | 0% | 0.4917% | 10.9037 | 0 | 0 | 10.9037 | 0 | 10.4014 | 0.32067 | 32.4363 | 10.4014 | 0.32067 | 32.4363 | 10.9572 | 0.33781 | 32.4363 | 1.486%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 180 | 156 | 2978.814 | 97.34% | 2.471% | 0.184% | 251.3089 | 0 | 0 | 251.3089 | 0 | 239.7316 | 2.175 | 110.2216 | 239.7316 | 2.175 | 110.2216 | 252.5408 | 2.2912 | 110.2216 | 8.437%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 155 | 112 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 104.6866 | 0 | 0 | 104.6866 | 0 | 99.8639 | 1.5615 | 63.9524 | 99.8639 | 1.5615 | 63.9524 | 105.1998 | 1.645 | 63.9524 | 7.079%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 408 | 329 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 205.8159 | 0 | 0 | 205.8159 | 0 | 196.3344 | 4.587 | 42.8022 | 196.3344 | 4.587 | 42.8022 | 206.8248 | 4.8321 | 42.8022 | 7.802%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 401 | 276 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 217.8673 | 0 | 0 | 217.8673 | 0 | 207.8306 | 3.8481 | 54.009 | 207.8306 | 3.8481 | 54.009 | 218.9353 | 4.0537 | 54.009 | 6.382%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 129 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 142.774 | 0 | 0 | 142.774 | 0 | 136.1967 | 1.7986 | 75.7256 | 136.1967 | 1.7986 | 75.7256 | 143.4739 | 1.8947 | 75.7256 | 8.744%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 249 | 205 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 538.5174 | 0 | 0 | 538.5174 | 0 | 513.709 | 2.8582 | 179.7336 | 513.709 | 2.8582 | 179.7336 | 541.1572 | 3.0109 | 179.7336 | 7.963%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 201 | 748.333 | 77.34% | 21.7% | 0.962% | 28.5115 | 0 | 0 | 28.5115 | 0 | 27.198 | 2.8024 | 9.7053 | 27.198 | 2.8024 | 9.7053 | 28.6513 | 2.9521 | 9.7053 | 3.81%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 276 | 149 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 108.5766 | 0 | 0 | 108.5766 | 0 | 103.5747 | 2.0774 | 49.8578 | 103.5747 | 2.0774 | 49.8578 | 109.1088 | 2.1884 | 49.8578 | 5.209%
2026 | 520 | 520-1936 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 3 | 63.7111 | 99.77% | 0% | 0.2279% | 4.7674 | 0 | 0 | 4.7674 | 0 | 4.5478 | 0.041827 | 108.7296 | 4.5478 | 0.041827 | 108.7296 | 4.7908 | 0.044062 | 108.7296 | 7.483%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 113 | 54 | 258.296 | 74.72% | 24.53% | 0.7505% | 9.2233 | 0 | 0 | 9.2233 | 0 | 8.7984 | 0.75288 | 11.6863 | 8.7984 | 0.75288 | 11.6863 | 9.2685 | 0.79311 | 11.6863 | 3.571%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 306 | 275 | 4997.7942 | 96.49% | 3.313% | 0.193% | 433.4028 | 0 | 0 | 433.4028 | 0 | 413.4368 | 3.8341 | 107.8307 | 413.4368 | 3.8341 | 107.8307 | 435.5273 | 4.039 | 107.8307 | 8.672%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 219 | 176 | 2044.6463 | 97.57% | 2.13% | 0.298% | 160.3287 | 0 | 0 | 160.3287 | 0 | 152.9427 | 2.4538 | 62.3278 | 152.9427 | 2.4538 | 62.3278 | 161.1146 | 2.585 | 62.3278 | 7.841%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 264 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 919.7864 | 0 | 0 | 919.7864 | 0 | 877.4138 | 3.6808 | 238.3782 | 877.4138 | 3.6808 | 238.3782 | 924.2952 | 3.8774 | 238.3782 | 8.104%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 136 | 810.9996 | 89.31% | 10.24% | 0.4457% | 49.5022 | 0 | 0 | 49.5022 | 0 | 47.2217 | 1.8962 | 24.904 | 47.2217 | 1.8962 | 24.904 | 49.7448 | 1.9975 | 24.904 | 6.104%
2026 | 239 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 276 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 683.0496 | 0 | 0 | 683.0496 | 0 | 651.5829 | 3.8481 | 169.3271 | 651.5829 | 3.8481 | 169.3271 | 686.3978 | 4.0537 | 169.3271 | 8.057%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 264 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 744.4805 | 0 | 0 | 744.4805 | 0 | 710.1838 | 3.6808 | 192.9447 | 710.1838 | 3.6808 | 192.9447 | 748.1299 | 3.8774 | 192.9447 | 8.544%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 247 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 382.9204 | 0 | 0 | 382.9204 | 0 | 365.28 | 3.4437 | 106.0706 | 365.28 | 3.4437 | 106.0706 | 384.7974 | 3.6277 | 106.0706 | 6.815%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 232 | 207 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 1085.4723 | 0 | 0 | 1085.4723 | 0 | 1035.4669 | 2.8861 | 358.783 | 1035.4669 | 2.8861 | 358.783 | 1090.7933 | 3.0403 | 358.783 | 8.867%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 437 | 328 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 670.0457 | 0 | 0 | 670.0457 | 0 | 639.1781 | 4.5731 | 139.77 | 639.1781 | 4.5731 | 139.77 | 673.3303 | 4.8174 | 139.77 | 7.435%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 34 | 112.7117 | 43.02% | 55.81% | 1.165% | 2.5762 | 0 | 0 | 2.5762 | 0 | 2.4575 | 0.47404 | 5.1843 | 2.4575 | 0.47404 | 5.1843 | 2.5889 | 0.49937 | 5.1843 | 2.286%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 42 | 116.9577 | 22.53% | 76.17% | 1.295% | 1.1902 | 0 | 0 | 1.1902 | 0 | 1.1354 | 0.58558 | 1.9389 | 1.1354 | 0.58558 | 1.9389 | 1.196 | 0.61686 | 1.9389 | 1.018%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 354 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 317.7319 | 0 | 0 | 317.7319 | 0 | 303.0947 | 4.9356 | 61.4103 | 303.0947 | 4.9356 | 61.4103 | 319.2894 | 5.1993 | 61.4103 | 5.634%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 99 | 305.199 | 11.7% | 87.21% | 1.095% | 1.7759 | 0 | 0 | 1.7759 | 0 | 1.6941 | 1.3803 | 1.2273 | 1.6941 | 1.3803 | 1.2273 | 1.7846 | 1.454 | 1.2273 | 0.5819%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 231 | 173 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 408.5997 | 0 | 0 | 408.5997 | 0 | 389.7763 | 2.412 | 161.5978 | 389.7763 | 2.412 | 161.5978 | 410.6026 | 2.5409 | 161.5978 | 7.472%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 489 | 289 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 667.3334 | 0 | 0 | 667.3334 | 0 | 636.5907 | 4.0293 | 157.9896 | 636.5907 | 4.0293 | 157.9896 | 670.6046 | 4.2446 | 157.9896 | 5.896%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 283 | 223 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 1069.4603 | 0 | 0 | 1069.4603 | 0 | 1020.1924 | 3.1091 | 328.128 | 1020.1924 | 3.1091 | 328.128 | 1074.7027 | 3.2753 | 328.128 | 7.8%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 204 | 8801.877 | 98.2% | 1.718% | 0.0819% | 623.0646 | 0 | 0 | 623.0646 | 0 | 594.3613 | 2.8442 | 208.9712 | 594.3613 | 2.8442 | 208.9712 | 626.1189 | 2.9962 | 208.9712 | 7.079%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 842 | 634 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 3010.7489 | 0 | 0 | 3010.7489 | 0 | 2872.0499 | 8.8394 | 324.9142 | 2872.0499 | 8.8394 | 324.9142 | 3025.5075 | 9.3117 | 324.9142 | 7.457%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 18 | 18 | 833.6308 | 67.75% | 32.17% | 0.07637% | 56.479 | 0 | 0 | 56.479 | 0 | 53.8771 | 0.25096 | 214.6831 | 53.8771 | 0.25096 | 214.6831 | 56.7559 | 0.26437 | 214.6831 | 6.775%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 92 | 11 | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.9884 | 0 | 0 | 5.9884 | 0 | 5.7125 | 0.15337 | 37.2479 | 5.7125 | 0.15337 | 37.2479 | 6.0178 | 0.16156 | 37.2479 | 1.152%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 9 | 9 | 49.4293 | 99.41% | 0% | 0.5897% | 4.9138 | 0 | 0 | 4.9138 | 0 | 4.6874 | 0.12548 | 37.3557 | 4.6874 | 0.12548 | 37.3557 | 4.9379 | 0.13219 | 37.3557 | 9.941%
2026 | 1118 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 360 | 18774.394 | 95.55% | 4.388% | 0.06321% | 1622.6031 | 0 | 0 | 1622.6031 | 0 | 1547.8531 | 5.0192 | 308.385 | 1547.8531 | 5.0192 | 308.385 | 1630.557 | 5.2874 | 308.385 | 8.643%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 631 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 2144.2272 | 0 | 0 | 2144.2272 | 0 | 2045.4471 | 8.7976 | 232.501 | 2045.4471 | 8.7976 | 232.501 | 2154.7381 | 9.2676 | 232.501 | 8.329%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 344 | 278 | 2610.8 | 93.6% | 6.065% | 0.3401% | 197.4758 | 0 | 0 | 197.4758 | 0 | 188.3785 | 3.876 | 48.6018 | 188.3785 | 3.876 | 48.6018 | 198.4438 | 4.0831 | 48.6018 | 7.564%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 551 | 445 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 316.6756 | 0 | 0 | 316.6756 | 0 | 302.087 | 6.2043 | 48.6898 | 302.087 | 6.2043 | 48.6898 | 318.2279 | 6.5358 | 48.6898 | 7.576%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 159 | 622.3042 | 87.18% | 11.98% | 0.8373% | 45.4006 | 0 | 0 | 45.4006 | 0 | 43.3091 | 2.2168 | 19.5366 | 43.3091 | 2.2168 | 19.5366 | 45.6232 | 2.3353 | 19.5366 | 7.296%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 198 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 128.3604 | 0 | 0 | 128.3604 | 0 | 122.4471 | 2.7606 | 44.3557 | 122.4471 | 2.7606 | 44.3557 | 128.9896 | 2.9081 | 44.3557 | 7.885%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 310 | 229 | 6201.607 | 97.29% | 2.601% | 0.1104% | 445.698 | 0 | 0 | 445.698 | 0 | 425.1656 | 3.1928 | 133.1645 | 425.1656 | 3.1928 | 133.1645 | 447.8828 | 3.3634 | 133.1645 | 7.187%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 242 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 1122.1435 | 0 | 0 | 1122.1435 | 0 | 1070.4487 | 3.374 | 317.2609 | 1070.4487 | 3.374 | 317.2609 | 1127.6442 | 3.5543 | 317.2609 | 7.316%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 46 | 34 | 2448.8293 | 98.64% | 1.317% | 0.04316% | 178.5379 | 0 | 0 | 178.5379 | 0 | 170.3131 | 0.47404 | 359.2817 | 170.3131 | 0.47404 | 359.2817 | 179.4131 | 0.49937 | 359.2817 | 7.291%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 188 | 158 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 474.2097 | 0 | 0 | 474.2097 | 0 | 452.3639 | 2.2029 | 205.351 | 452.3639 | 2.2029 | 205.351 | 476.5343 | 2.3206 | 205.351 | 8.27%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 313 | 270 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 898.1963 | 0 | 0 | 898.1963 | 0 | 856.8183 | 3.7644 | 227.6098 | 856.8183 | 3.7644 | 227.6098 | 902.5992 | 3.9656 | 227.6098 | 8.48%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 273 | 226 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 756.8138 | 0 | 0 | 756.8138 | 0 | 721.949 | 3.151 | 229.1206 | 721.949 | 3.151 | 229.1206 | 760.5237 | 3.3193 | 229.1206 | 8.148%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 4 | 17.7969 | 99.34% | 0% | 0.6614% | 1.7679 | 0 | 0 | 1.7679 | 0 | 1.6865 | 0.055769 | 30.2403 | 1.6865 | 0.055769 | 30.2403 | 1.7766 | 0.058749 | 30.2403 | 9.934%
2026 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 4 | 3 | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.041827 | 0 | 0 | 0.041827 | 0 | 0 | 0.044062 | 0 | 0%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 102 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 227.9168 | 0 | 0 | 227.9168 | 0 | 217.4172 | 1.4221 | 152.8832 | 217.4172 | 1.4221 | 152.8832 | 229.0341 | 1.4981 | 152.8832 | 7.269%
2026 | 75 | 75-2260F | Tier-3 | missing | missing | 2 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.013942 | 0 | 0 | 0.013942 | 0 | 0 | 0.014687 | 0 | 0%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 65 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 131.6342 | 0 | 0 | 131.6342 | 0 | 125.5701 | 0.90625 | 138.5603 | 125.5701 | 0.90625 | 138.5603 | 132.2795 | 0.95467 | 138.5603 | 7.705%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 69 | 58 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 162.6382 | 0 | 0 | 162.6382 | 0 | 155.1458 | 0.80865 | 191.8572 | 155.1458 | 0.80865 | 191.8572 | 163.4355 | 0.85186 | 191.8572 | 8.394%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 241 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 165.7574 | 0 | 0 | 165.7574 | 0 | 158.1213 | 3.3601 | 47.0586 | 158.1213 | 3.3601 | 47.0586 | 166.5699 | 3.5396 | 47.0586 | 7.496%
2026 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 24 | 21 | 42.5113 | 97.49% | 0.5175% | 1.991% | 3.6264 | 0 | 0 | 3.6264 | 0 | 3.4594 | 0.29279 | 11.8153 | 3.4594 | 0.29279 | 11.8153 | 3.6442 | 0.30843 | 11.8153 | 8.531%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 186 | 143 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 1100.7243 | 0 | 0 | 1100.7243 | 0 | 1050.0162 | 1.9937 | 526.6547 | 1050.0162 | 1.9937 | 526.6547 | 1106.12 | 2.1003 | 526.6547 | 7.577%
2026 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 29 | 29 | 5696.3358 | 99.98% | 0% | 0.01771% | 569.5327 | 0 | 0 | 569.5327 | 0 | 543.2955 | 0.40433 | 1343.7055 | 543.2955 | 0.40433 | 1343.7055 | 572.3245 | 0.42593 | 1343.7055 | 9.998%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 33 | 32 | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 695.0009 | 0 | 0 | 695.0009 | 0 | 662.9836 | 0.44615 | 1486 | 662.9836 | 0.44615 | 1486 | 698.4077 | 0.46999 | 1486 | 9.65%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 143 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 236.4489 | 0 | 0 | 236.4489 | 0 | 225.5562 | 1.9937 | 113.1318 | 225.5562 | 1.9937 | 113.1318 | 237.608 | 2.1003 | 113.1318 | 2.589%
2026 | 73 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 9 | 5 | 324.1263 | 99.58% | 0.3619% | 0.05404% | 17.9321 | 0 | 0 | 17.9321 | 0 | 17.106 | 0.069711 | 245.3833 | 17.106 | 0.069711 | 245.3833 | 18.02 | 0.073436 | 245.3833 | 5.532%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 48 | 3349.7594 | 92.58% | 7.304% | 0.116% | 105.5733 | 0 | 0 | 105.5733 | 0 | 100.7098 | 0.66923 | 150.4861 | 100.7098 | 0.66923 | 150.4861 | 106.0908 | 0.70499 | 150.4861 | 3.152%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 198 | 185 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 1142.7385 | 0 | 0 | 1142.7385 | 0 | 1090.0949 | 2.5793 | 422.6283 | 1090.0949 | 2.5793 | 422.6283 | 1148.3402 | 2.7171 | 422.6283 | 9.275%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 159 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 180.6886 | 0 | 0 | 180.6886 | 0 | 172.3646 | 2.2168 | 77.753 | 172.3646 | 2.2168 | 77.753 | 181.5743 | 2.3353 | 77.753 | 8.658%
2026 | 222 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 206 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 75.9811 | 0 | 0 | 75.9811 | 0 | 72.4808 | 2.8721 | 25.2361 | 72.4808 | 2.8721 | 25.2361 | 76.3536 | 3.0256 | 25.2361 | 4.728%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 80 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 553.4853 | 0 | 0 | 553.4853 | 0 | 527.9874 | 1.1154 | 473.3687 | 527.9874 | 1.1154 | 473.3687 | 556.1985 | 1.175 | 473.3687 | 5.698%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 192 | 130 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 1235.3475 | 0 | 0 | 1235.3475 | 0 | 1178.4375 | 1.8125 | 650.1734 | 1178.4375 | 1.8125 | 650.1734 | 1241.4031 | 1.9093 | 650.1734 | 6.696%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 74 | 65 | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 223.8726 | 0 | 0 | 223.8726 | 0 | 213.5592 | 0.90625 | 235.6519 | 213.5592 | 0.90625 | 235.6519 | 224.97 | 0.95467 | 235.6519 | 8.729%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 180 | 106 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 314.028 | 0 | 0 | 314.028 | 0 | 299.5614 | 1.4779 | 202.6964 | 299.5614 | 1.4779 | 202.6964 | 315.5673 | 1.5568 | 202.6964 | 5.672%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 238 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 1016.9059 | 0 | 0 | 1016.9059 | 0 | 970.0591 | 3.3183 | 292.3393 | 970.0591 | 3.3183 | 292.3393 | 1021.8907 | 3.4956 | 292.3393 | 5.415%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 116 | 110 | 3034.8235 | 97.12% | 2.752% | 0.1275% | 279.4979 | 0 | 0 | 279.4979 | 0 | 266.622 | 1.5337 | 173.8479 | 266.622 | 1.5337 | 173.8479 | 280.868 | 1.6156 | 173.8479 | 9.21%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 218 | 192 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 1746.0262 | 0 | 0 | 1746.0262 | 0 | 1665.5904 | 2.6769 | 622.2043 | 1665.5904 | 2.6769 | 622.2043 | 1754.5852 | 2.82 | 622.2043 | 8.74%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 11 | 127.4062 | 99.28% | 0% | 0.716% | 3.6617 | 0 | 0 | 3.6617 | 0 | 3.493 | 0.15337 | 22.7756 | 3.493 | 0.15337 | 22.7756 | 3.6796 | 0.16156 | 22.7756 | 2.874%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 6 | 12.4137 | 98.83% | 0% | 1.166% | 0.56626 | 0 | 0 | 0.56626 | 0 | 0.54017 | 0.083654 | 6.4573 | 0.54017 | 0.083654 | 6.4573 | 0.56904 | 0.088123 | 6.4573 | 4.562%
2026 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 17 | 17 | 139.955 | 99.63% | 0% | 0.3714% | 13.9435 | 0 | 0 | 13.9435 | 0 | 13.3012 | 0.23702 | 56.1186 | 13.3012 | 0.23702 | 56.1186 | 14.0119 | 0.24968 | 56.1186 | 9.963%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 3 | 6.7153 | 99.02% | 0% | 0.9775% | 0.66497 | 0 | 0 | 0.66497 | 0 | 0.63433 | 0.041827 | 15.1657 | 0.63433 | 0.041827 | 15.1657 | 0.66823 | 0.044062 | 15.1657 | 9.902%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 16 | 16 | 330.3488 | 99.39% | 0.4551% | 0.1546% | 32.8335 | 0 | 0 | 32.8335 | 0 | 31.3209 | 0.22308 | 140.4043 | 31.3209 | 0.22308 | 140.4043 | 32.9944 | 0.235 | 140.4043 | 9.939%
2026 | 260 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 40 | 36 | 232.5563 | 96.66% | 2.796% | 0.5416% | 20.2316 | 0 | 0 | 20.2316 | 0 | 19.2996 | 0.50192 | 38.4513 | 19.2996 | 0.50192 | 38.4513 | 20.3308 | 0.52874 | 38.4513 | 8.7%
2026 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 7 | 7 | 188.5529 | 99.88% | 0% | 0.1171% | 18.8332 | 0 | 0 | 18.8332 | 0 | 17.9656 | 0.097596 | 184.0813 | 17.9656 | 0.097596 | 184.0813 | 18.9255 | 0.10281 | 184.0813 | 9.988%
2026 | 599 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 159 | 8606.9717 | 99.86% | 0% | 0.1411% | 245.346 | 0 | 0 | 245.346 | 0 | 234.0434 | 2.2168 | 105.576 | 234.0434 | 2.2168 | 105.576 | 246.5487 | 2.3353 | 105.576 | 2.851%
2026 | 907 | 907-1475 | Tier-3 | Tier-3---21 | Tier-3---21 | 4 | 4 | 4.2814 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.055769 | 0 | 0 | 0.055769 | 0 | 0 | 0.058749 | 0 | 0%
2026 | 1021 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 162 | 123 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 625.5206 | 0 | 0 | 625.5206 | 0 | 596.7041 | 1.7149 | 347.9525 | 596.7041 | 1.7149 | 347.9525 | 628.5869 | 1.8065 | 347.9525 | 7.412%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 5 | 5 | 257.2419 | 98.67% | 1.294% | 0.04048% | 25.3809 | 0 | 0 | 25.3809 | 0 | 24.2117 | 0.069711 | 347.3126 | 24.2117 | 0.069711 | 347.3126 | 25.5053 | 0.073436 | 347.3126 | 9.867%
2026 | 907 | 907-1604 | Tier-3 | Tier-3---19 | Tier-3---16 | 2 | 4 | 17.8439 | 83.33% | 16.48% | 0.1969% | 2.9738 | 0 | 0 | 2.9738 | 0 | 2.8368 | 0.055769 | 50.8662 | 2.8368 | 0.055769 | 50.8662 | 2.9883 | 0.058749 | 50.8662 | 16.67%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 117 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 717.4672 | 0 | 0 | 717.4672 | 0 | 684.415 | 1.6312 | 419.5654 | 684.415 | 1.6312 | 419.5654 | 720.9842 | 1.7184 | 419.5654 | 7.884%
2026 | 1021 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 278 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1923.6578 | 0 | 0 | 1923.6578 | 0 | 1835.0388 | 3.876 | 473.4417 | 1835.0388 | 3.876 | 473.4417 | 1933.0875 | 4.0831 | 473.4417 | 7.107%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 33 | 29 | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 557.7619 | 0 | 0 | 557.7619 | 0 | 532.0669 | 0.40433 | 1315.9345 | 532.0669 | 0.40433 | 1315.9345 | 560.496 | 0.42593 | 1315.9345 | 8.786%
2026 | 350 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 240 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 1227.927 | 0 | 0 | 1227.927 | 0 | 1171.3589 | 3.3461 | 350.0618 | 1171.3589 | 3.3461 | 350.0618 | 1233.9462 | 3.5249 | 350.0618 | 7.788%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 130 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 910.2348 | 0 | 0 | 910.2348 | 0 | 868.3022 | 1.8125 | 479.064 | 868.3022 | 1.8125 | 479.064 | 914.6967 | 1.9093 | 479.064 | 7.738%
2026 | 350 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 471 | 386 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 439.4181 | 0 | 0 | 439.4181 | 0 | 419.175 | 5.3817 | 77.8886 | 419.175 | 5.3817 | 77.8886 | 441.5721 | 5.6693 | 77.8886 | 7.888%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 131 | 1466.2762 | 91.81% | 7.905% | 0.289% | 117.5619 | 0 | 0 | 117.5619 | 0 | 112.1461 | 1.8264 | 61.4015 | 112.1461 | 1.8264 | 61.4015 | 118.1382 | 1.924 | 61.4015 | 8.018%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 89 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 566.4697 | 0 | 0 | 566.4697 | 0 | 540.3736 | 1.2409 | 435.4819 | 540.3736 | 1.2409 | 435.4819 | 569.2465 | 1.3072 | 435.4819 | 7.116%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 423 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 3155.1751 | 0 | 0 | 3155.1751 | 0 | 3009.8227 | 5.8976 | 510.3481 | 3009.8227 | 5.8976 | 510.3481 | 3170.6416 | 6.2127 | 510.3481 | 7.647%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 162 | 124 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 256.5556 | 0 | 0 | 256.5556 | 0 | 244.7366 | 1.7288 | 141.5609 | 244.7366 | 1.7288 | 141.5609 | 257.8132 | 1.8212 | 141.5609 | 7.035%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 282 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1736.8596 | 0 | 0 | 1736.8596 | 0 | 1656.8461 | 3.9317 | 421.4044 | 1656.8461 | 3.9317 | 421.4044 | 1745.3737 | 4.1418 | 421.4044 | 7.697%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 7 | 5 | 153.3115 | 98.58% | 1.358% | 0.06577% | 10.7949 | 0 | 0 | 10.7949 | 0 | 10.2976 | 0.069711 | 147.7182 | 10.2976 | 0.069711 | 147.7182 | 10.8479 | 0.073436 | 147.7182 | 7.041%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 40 | 847.524 | 96.52% | 3.329% | 0.1488% | 62.9267 | 0 | 0 | 62.9267 | 0 | 60.0278 | 0.55769 | 107.6362 | 60.0278 | 0.55769 | 107.6362 | 63.2352 | 0.58749 | 107.6362 | 7.425%
2026 | 216 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 419 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 4541.9905 | 0 | 0 | 4541.9905 | 0 | 4332.7504 | 5.8418 | 741.6784 | 4332.7504 | 5.8418 | 741.6784 | 4564.2552 | 6.154 | 741.6784 | 8.22%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 24 | 5703.0403 | 99.97% | 0% | 0.03309% | 220.6898 | 0 | 0 | 220.6898 | 0 | 210.5231 | 0.33461 | 629.1504 | 210.5231 | 0.33461 | 629.1504 | 221.7716 | 0.35249 | 629.1504 | 3.87%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 271 | 32313.161 | 99.26% | 0.708% | 0.02831% | 2813.0723 | 0 | 0 | 2813.0723 | 0 | 2683.4799 | 3.7784 | 710.2235 | 2683.4799 | 3.7784 | 710.2235 | 2826.8619 | 3.9802 | 710.2235 | 8.706%
2026 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 3 | 3 | 62.9838 | 99.88% | 0% | 0.1185% | 6.2909 | 0 | 0 | 6.2909 | 0 | 6.0011 | 0.041827 | 143.4751 | 6.0011 | 0.041827 | 143.4751 | 6.3218 | 0.044062 | 143.4751 | 9.988%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 194 | 106 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 67.9648 | 0 | 0 | 67.9648 | 0 | 64.8338 | 1.4779 | 43.8694 | 64.8338 | 1.4779 | 43.8694 | 68.298 | 1.5568 | 43.8694 | 5.244%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 111 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 286.7483 | 0 | 0 | 286.7483 | 0 | 273.5384 | 1.5476 | 176.7508 | 273.5384 | 1.5476 | 176.7508 | 288.154 | 1.6303 | 176.7508 | 8.417%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 35 | 1554.328 | 69.02% | 30.62% | 0.3611% | 12.7284 | 0 | 0 | 12.7284 | 0 | 12.142 | 0.48798 | 24.8822 | 12.142 | 0.48798 | 24.8822 | 12.7908 | 0.51405 | 24.8822 | 0.8189%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 252 | 24 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 14.5312 | 0 | 0 | 14.5312 | 0 | 13.8618 | 0.33461 | 41.426 | 13.8618 | 0.33461 | 41.426 | 14.6024 | 0.35249 | 41.426 | 0.7296%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 36 | 33 | 434.8834 | 99.47% | 0.2691% | 0.2608% | 39.6531 | 0 | 0 | 39.6531 | 0 | 37.8263 | 0.4601 | 82.2141 | 37.8263 | 0.4601 | 82.2141 | 39.8475 | 0.48468 | 82.2141 | 9.118%
2026 | 770 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 33 | 62.492 | 96.91% | 0.773% | 2.32% | 4.542 | 0 | 0 | 4.542 | 0 | 4.3327 | 0.4601 | 9.417 | 4.3327 | 0.4601 | 9.417 | 4.5642 | 0.48468 | 9.417 | 7.268%
2026 | 237 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 64 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 898.5928 | 0 | 0 | 898.5928 | 0 | 857.1965 | 0.89231 | 960.6527 | 857.1965 | 0.89231 | 960.6527 | 902.9977 | 0.93998 | 960.6527 | 6.933%
2026 | 176 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 260 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 1134.1213 | 0 | 0 | 1134.1213 | 0 | 1081.8747 | 3.625 | 298.4486 | 1081.8747 | 3.625 | 298.4486 | 1139.6807 | 3.8187 | 298.4486 | 7.487%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 478 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 2255.871 | 0 | 0 | 2255.871 | 0 | 2151.9477 | 6.6644 | 322.9013 | 2151.9477 | 6.6644 | 322.9013 | 2266.9292 | 7.0205 | 322.9013 | 7.92%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 106 | 88 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 661.8693 | 0 | 0 | 661.8693 | 0 | 631.3783 | 1.2269 | 514.6038 | 631.3783 | 1.2269 | 514.6038 | 665.1137 | 1.2925 | 514.6038 | 8.257%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 50 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 373.3143 | 0 | 0 | 373.3143 | 0 | 356.1165 | 0.69711 | 510.8438 | 356.1165 | 0.69711 | 510.8438 | 375.1443 | 0.73436 | 510.8438 | 8.579%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 3 | 191.8954 | 99.94% | 0% | 0.06293% | 28.7662 | 0 | 0 | 28.7662 | 0 | 27.441 | 0.041827 | 656.0617 | 27.441 | 0.041827 | 656.0617 | 28.9072 | 0.044062 | 656.0617 | 14.99%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 212 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 1096.8917 | 0 | 0 | 1096.8917 | 0 | 1046.3602 | 2.9558 | 354.0066 | 1046.3602 | 2.9558 | 354.0066 | 1102.2686 | 3.1137 | 354.0066 | 7.426%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 406 | 346 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 950.4557 | 0 | 0 | 950.4557 | 0 | 906.6701 | 4.824 | 187.9486 | 906.6701 | 4.824 | 187.9486 | 955.1147 | 5.0818 | 187.9486 | 8.435%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 213 | 190 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 704.8442 | 0 | 0 | 704.8442 | 0 | 672.3735 | 2.649 | 253.8183 | 672.3735 | 2.649 | 253.8183 | 708.2993 | 2.7906 | 253.8183 | 8.789%
2026 | 235 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 474 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1566.3686 | 0 | 0 | 1566.3686 | 0 | 1494.2092 | 6.6086 | 226.0992 | 1494.2092 | 6.6086 | 226.0992 | 1574.0468 | 6.9618 | 226.0992 | 6.691%
2026 | 972 | 972-1641 | Tier-2 | Tier-2---13 | Tier-2---5 | 3 | 3 | 295.0839 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.041827 | 0 | 0 | 0.041827 | 0 | 0 | 0.044062 | 0 | 0%
2026 | 972 | 972-1642 | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 9 | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.12548 | 0 | 0 | 0.12548 | 0 | 0 | 0.13219 | 0 | 0%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 543 | 384 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1579.5972 | 0 | 0 | 1579.5972 | 0 | 1506.8284 | 5.3538 | 281.4483 | 1506.8284 | 5.3538 | 281.4483 | 1587.3403 | 5.6399 | 281.4483 | 6.893%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 189 | 155 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 743.7408 | 0 | 0 | 743.7408 | 0 | 709.4782 | 2.1611 | 328.3019 | 709.4782 | 2.1611 | 328.3019 | 747.3866 | 2.2765 | 328.3019 | 8.129%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 161 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 418.2068 | 0 | 0 | 418.2068 | 0 | 398.9409 | 2.2447 | 177.725 | 398.9409 | 2.2447 | 177.725 | 420.2568 | 2.3646 | 177.725 | 8.077%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 53 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 770.7303 | 0 | 0 | 770.7303 | 0 | 735.2243 | 0.73894 | 994.97 | 735.2243 | 0.73894 | 994.97 | 774.5084 | 0.77842 | 994.97 | 8.941%
2026 | 973 | 973-530AE | Tier-3 | Tier-3---17 | Tier-3---5 | 2 | 2 | 388.0062 | 6.476% | 93.52% | 0.007746% | 2.5128 | 0 | 0 | 2.5128 | 0 | 2.397 | 0.027885 | 85.9627 | 2.397 | 0.027885 | 85.9627 | 2.5251 | 0.029374 | 85.9627 | 0.6476%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 199 | 197 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 632.9032 | 0 | 0 | 632.9032 | 0 | 603.7466 | 2.7466 | 219.8136 | 603.7466 | 2.7466 | 219.8136 | 636.0056 | 2.8934 | 219.8136 | 9.705%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 389 | 305 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 256.5895 | 0 | 0 | 256.5895 | 0 | 244.7689 | 4.2524 | 57.5602 | 244.7689 | 4.2524 | 57.5602 | 257.8473 | 4.4796 | 57.5602 | 7.346%
2026 | 973 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 111 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 586.0659 | 0 | 0 | 586.0659 | 0 | 559.067 | 1.5476 | 361.2492 | 559.067 | 1.5476 | 361.2492 | 588.9388 | 1.6303 | 361.2492 | 8.246%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 30 | 13 | 6417.0381 | 80.3% | 19.69% | 0.01691% | 223.2839 | 0 | 0 | 223.2839 | 0 | 212.9976 | 0.18125 | 1175.1612 | 212.9976 | 0.18125 | 1175.1612 | 224.3784 | 0.19093 | 1175.1612 | 3.48%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 29 | 626.8618 | 65.87% | 33.98% | 0.153% | 41.2906 | 0 | 0 | 41.2906 | 0 | 39.3884 | 0.40433 | 97.4174 | 39.3884 | 0.40433 | 97.4174 | 41.493 | 0.42593 | 97.4174 | 6.587%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 158 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 439.9608 | 0 | 0 | 439.9608 | 0 | 419.6927 | 2.2029 | 190.5199 | 419.6927 | 2.2029 | 190.5199 | 442.1175 | 2.3206 | 190.5199 | 9.613%
2026 | 354 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 55 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 234.5584 | 0 | 0 | 234.5584 | 0 | 223.7528 | 0.76683 | 291.7909 | 223.7528 | 0.76683 | 291.7909 | 235.7082 | 0.8078 | 291.7909 | 7.038%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 111 | 85 | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 107.9078 | 0 | 0 | 107.9078 | 0 | 102.9367 | 1.1851 | 86.8595 | 102.9367 | 1.1851 | 86.8595 | 108.4368 | 1.2484 | 86.8595 | 7.629%
2026 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 38 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 104.7414 | 0 | 0 | 104.7414 | 0 | 99.9162 | 0.52981 | 188.5898 | 99.9162 | 0.52981 | 188.5898 | 105.2548 | 0.55812 | 188.5898 | 9.242%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 24 | 1646.9837 | 34.54% | 65.41% | 0.04829% | 56.8815 | 0 | 0 | 56.8815 | 0 | 54.2611 | 0.33461 | 162.1598 | 54.2611 | 0.33461 | 162.1598 | 57.1603 | 0.35249 | 162.1598 | 3.454%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 70 | 765.4961 | 75% | 24.28% | 0.7274% | 13.8097 | 0 | 0 | 13.8097 | 0 | 13.1735 | 0.97596 | 13.498 | 13.1735 | 0.97596 | 13.498 | 13.8774 | 1.0281 | 13.498 | 1.804%
2026 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | Tier-2---20 | 8 | 1 | 2.3826 | 9.042% | 83.57% | 7.391% | 0.0026929 | 0 | 0 | 0.0026929 | 0 | 0.0025688 | 0.013942 | 0.18425 | 0.0025688 | 0.013942 | 0.18425 | 0.0027061 | 0.014687 | 0.18425 | 0.113%
2026 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | Tier-2---20 | 20 | 3 | 18.2465 | 16.87% | 78.76% | 4.376% | 0.046159 | 0 | 0 | 0.046159 | 0 | 0.044033 | 0.041827 | 1.0527 | 0.044033 | 0.041827 | 1.0527 | 0.046386 | 0.044062 | 1.0527 | 0.253%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 34 | 31 | 75.2008 | 96.65% | 1.975% | 1.378% | 6.6266 | 0 | 0 | 6.6266 | 0 | 6.3214 | 0.43221 | 14.6256 | 6.3214 | 0.43221 | 14.6256 | 6.6591 | 0.4553 | 14.6256 | 8.812%
2026 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 4 | 70.8201 | 99.8% | 0% | 0.2033% | 5.6541 | 0 | 0 | 5.6541 | 0 | 5.3936 | 0.055769 | 96.7133 | 5.3936 | 0.055769 | 96.7133 | 5.6818 | 0.058749 | 96.7133 | 7.984%
2026 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 3 | 21.8223 | 99.66% | 0% | 0.344% | 2.1747 | 0 | 0 | 2.1747 | 0 | 2.0745 | 0.041827 | 49.5983 | 2.0745 | 0.041827 | 49.5983 | 2.1854 | 0.044062 | 49.5983 | 9.966%
2026 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | Tier-3---17 | 3 | 2 | 0.76155 | 90.92% | 0% | 9.083% | 0.046158 | 0 | 0 | 0.046158 | 0 | 0.044032 | 0.027885 | 1.5791 | 0.044032 | 0.027885 | 1.5791 | 0.046385 | 0.029374 | 1.5791 | 6.061%
2026 | 239 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 332 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 735.9108 | 0 | 0 | 735.9108 | 0 | 702.0089 | 4.6288 | 151.6598 | 702.0089 | 4.6288 | 151.6598 | 739.5182 | 4.8762 | 151.6598 | 11.66%
2026 | 230 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 402 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 425.6045 | 0 | 0 | 425.6045 | 0 | 405.9978 | 5.6048 | 72.4375 | 405.9978 | 5.6048 | 72.4375 | 427.6908 | 5.9043 | 72.4375 | 6.404%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 106 | 1438.3629 | 99.75% | 0% | 0.2509% | 131.1068 | 0 | 0 | 131.1068 | 0 | 125.067 | 1.4779 | 84.6258 | 125.067 | 1.4779 | 84.6258 | 131.7495 | 1.5568 | 84.6258 | 9.115%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 9 | 9 | 108.0997 | 99.75% | 0% | 0.2497% | 10.783 | 0 | 0 | 10.783 | 0 | 10.2862 | 0.12548 | 81.9747 | 10.2862 | 0.12548 | 81.9747 | 10.8358 | 0.13219 | 81.9747 | 9.975%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 32 | 31 | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 394.5296 | 0 | 0 | 394.5296 | 0 | 376.3544 | 0.43221 | 870.7658 | 376.3544 | 0.43221 | 870.7658 | 396.4636 | 0.4553 | 870.7658 | 9.681%
2026 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 31 | 41.7756 | 94.08% | 0% | 5.924% | 1.6031 | 0 | 0 | 1.6031 | 0 | 1.5292 | 0.43221 | 3.5381 | 1.5292 | 0.43221 | 3.5381 | 1.6109 | 0.4553 | 3.5381 | 3.837%
2026 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 184 | 8 | 259.6903 | 35.49% | 63.12% | 1.387% | 0.40074 | 0 | 0 | 0.40074 | 0 | 0.38228 | 0.11154 | 3.4273 | 0.38228 | 0.11154 | 3.4273 | 0.40271 | 0.1175 | 3.4273 | 0.1543%
2026 | 157 | CB 157 | Tier-3 | Tier-3---21 | Tier-3---11 | 2 | 2 | 6.0775 | 99.43% | 0% | 0.5677% | 0.6043 | 0 | 0 | 0.6043 | 0 | 0.57646 | 0.027885 | 20.673 | 0.57646 | 0.027885 | 20.673 | 0.60726 | 0.029374 | 20.673 | 9.943%
2026 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 154 | 2 | 396.8506 | 79.93% | 19.29% | 0.7702% | 0.41198 | 0 | 0 | 0.41198 | 0 | 0.393 | 0.027885 | 14.0937 | 0.393 | 0.027885 | 14.0937 | 0.414 | 0.029374 | 14.0937 | 0.1038%
2026 | 197 | CB 196 | Tier-2 | Tier-2---15 | Tier-2---9 | 24 | 1 | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.017605 | 0 | 0 | 0.017605 | 0 | 0.016794 | 0.013942 | 1.2045 | 0.016794 | 0.013942 | 1.2045 | 0.017691 | 0.014687 | 1.2045 | 0.01309%
2026 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 478 | 80 | 1342.6559 | 29.9% | 69.37% | 0.7369% | 6.718 | 0 | 0 | 6.718 | 0 | 6.4085 | 1.1154 | 5.7456 | 6.4085 | 1.1154 | 5.7456 | 6.7509 | 1.175 | 5.7456 | 0.5004%
2026 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 188 | 133.9861 | 95.12% | 0% | 4.877% | 12.415 | 0 | 0 | 12.415 | 0 | 11.843 | 2.6211 | 4.5183 | 11.843 | 2.6211 | 4.5183 | 12.4758 | 2.7612 | 4.5183 | 9.266%
2026 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 233 | 109 | 195.752 | 9.583% | 88.23% | 2.187% | 0.8776 | 0 | 0 | 0.8776 | 0 | 0.83717 | 1.5197 | 0.55087 | 0.83717 | 1.5197 | 0.55087 | 0.8819 | 1.6009 | 0.55087 | 0.4483%
2026 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 229 | 220 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 82.2684 | 0 | 0 | 82.2684 | 0 | 78.4785 | 3.0673 | 25.5855 | 78.4785 | 3.0673 | 25.5855 | 82.6717 | 3.2312 | 25.5855 | 7.765%
2026 | 210 | CB 210 | Tier-2 | Tier-2---21 | Tier-2---17 | 3 | 1 | 1.9532 | 96.21% | 0% | 3.789% | 0.062638 | 0 | 0 | 0.062638 | 0 | 0.059753 | 0.013942 | 4.2857 | 0.059753 | 0.013942 | 4.2857 | 0.062945 | 0.014687 | 4.2857 | 3.207%
2026 | 211 | CB 211 | Tier-2 | Tier-2---21 | Tier-2---24 | 2 | 1 | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.013942 | 0 | 0 | 0.013942 | 0 | 0 | 0.014687 | 0 | 0%
2026 | 212 | CB 212 | Tier-2 | Tier-2---19 | Tier-2---11 | 7 | 6 | 22.9809 | 99.09% | 0% | 0.9069% | 1.9519 | 0 | 0 | 1.9519 | 0 | 1.862 | 0.083654 | 22.2585 | 1.862 | 0.083654 | 22.2585 | 1.9615 | 0.088123 | 22.2585 | 8.494%
2026 | 214 | CB 214 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 59.1996 | 99.88% | 0% | 0.1188% | 3.942 | 0 | 0 | 3.942 | 0 | 3.7604 | 0.027885 | 134.8543 | 3.7604 | 0.027885 | 134.8543 | 3.9613 | 0.029374 | 134.8543 | 6.659%
2026 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 133.9133 | 99.89% | 0% | 0.1056% | 8.0263 | 0 | 0 | 8.0263 | 0 | 7.6566 | 0.041827 | 183.0536 | 7.6566 | 0.041827 | 183.0536 | 8.0657 | 0.044062 | 183.0536 | 5.994%
2026 | 217 | CB 217 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 26.6678 | 99.71% | 0% | 0.2895% | 1.7727 | 0 | 0 | 1.7727 | 0 | 1.691 | 0.027885 | 60.6444 | 1.691 | 0.027885 | 60.6444 | 1.7814 | 0.029374 | 60.6444 | 6.647%
2026 | 220 | CB 220 | Tier-3 | Tier-3---21 | Tier-3---24 | 2 | 1 | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.013942 | 0 | 0 | 0.013942 | 0 | 0 | 0.014687 | 0 | 0%
2026 | 1235 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 12 | 10 | 212.8275 | 99.81% | 0% | 0.1866% | 17.7025 | 0 | 0 | 17.7025 | 0 | 16.887 | 0.13942 | 121.1208 | 16.887 | 0.13942 | 121.1208 | 17.7893 | 0.14687 | 121.1208 | 8.318%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 174 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 166.1116 | 0 | 0 | 166.1116 | 0 | 158.4591 | 2.426 | 65.3182 | 158.4591 | 2.426 | 65.3182 | 166.9258 | 2.5556 | 65.3182 | 6.645%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 259 | 144 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 88.9279 | 0 | 0 | 88.9279 | 0 | 84.8312 | 2.0077 | 42.2531 | 84.8312 | 2.0077 | 42.2531 | 89.3638 | 2.115 | 42.2531 | 5.414%
2026 | 230 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 613 | 396 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 263.2844 | 0 | 0 | 263.2844 | 0 | 251.1554 | 5.5211 | 45.4897 | 251.1554 | 5.5211 | 45.4897 | 264.575 | 5.8161 | 45.4897 | 6.378%
2026 | 232 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 201 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 186.0305 | 0 | 0 | 186.0305 | 0 | 177.4604 | 2.8024 | 63.3245 | 177.4604 | 2.8024 | 63.3245 | 186.9424 | 2.9521 | 63.3245 | 5.646%
2026 | 971 | CB 235 | Tier-2 | Tier-2---12 | Tier-2---11 | 6 | 4 | 443.5427 | 99.96% | 0% | 0.03939% | 29.5579 | 0 | 0 | 29.5579 | 0 | 28.1962 | 0.055769 | 505.5878 | 28.1962 | 0.055769 | 505.5878 | 29.7028 | 0.058749 | 505.5878 | 6.664%
2026 | 235 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 161 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 592.8145 | 0 | 0 | 592.8145 | 0 | 565.5048 | 2.2447 | 251.928 | 565.5048 | 2.2447 | 251.928 | 595.7205 | 2.3646 | 251.928 | 4.664%
2026 | 236 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 41 | 14 | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 71.7723 | 0 | 0 | 71.7723 | 0 | 68.4659 | 0.19519 | 350.762 | 68.4659 | 0.19519 | 350.762 | 72.1242 | 0.20562 | 350.762 | 3.399%
2026 | 239 | CB 239 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 1 | 10.6776 | 99.64% | 0% | 0.3633% | 0.53194 | 0 | 0 | 0.53194 | 0 | 0.50744 | 0.013942 | 36.3955 | 0.50744 | 0.013942 | 36.3955 | 0.53455 | 0.014687 | 36.3955 | 4.982%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 114 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 59.0928 | 0 | 0 | 59.0928 | 0 | 56.3705 | 1.5894 | 35.4661 | 56.3705 | 1.5894 | 35.4661 | 59.3824 | 1.6743 | 35.4661 | 4.679%
2026 | 240 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 35 | 406.8184 | 64.36% | 35.02% | 0.6193% | 10.5338 | 0 | 0 | 10.5338 | 0 | 10.0486 | 0.48798 | 20.5922 | 10.0486 | 0.48798 | 20.5922 | 10.5855 | 0.51405 | 20.5922 | 2.589%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 197 | 16 | 295.5508 | 37.5% | 61.39% | 1.106% | 0.90024 | 0 | 0 | 0.90024 | 0 | 0.85877 | 0.22308 | 3.8497 | 0.85877 | 0.22308 | 3.8497 | 0.90465 | 0.235 | 3.8497 | 0.3046%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 180 | 1438.4419 | 90% | 9.47% | 0.5268% | 76.9095 | 0 | 0 | 76.9095 | 0 | 73.3664 | 2.5096 | 29.2342 | 73.3664 | 2.5096 | 29.2342 | 77.2865 | 2.6437 | 29.2342 | 5.347%
2026 | 246 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 29 | 379.7423 | 70.28% | 29.01% | 0.71% | 8.5995 | 0 | 0 | 8.5995 | 0 | 8.2033 | 0.40433 | 20.2889 | 8.2033 | 0.40433 | 20.2889 | 8.6417 | 0.42593 | 20.2889 | 2.265%
2026 | 240 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 136 | 62 | 962.1527 | 99.5% | 0% | 0.4991% | 43.6439 | 0 | 0 | 43.6439 | 0 | 41.6333 | 0.86442 | 48.1632 | 41.6333 | 0.86442 | 48.1632 | 43.8579 | 0.91061 | 48.1632 | 4.536%
2026 | 1233 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 101 | 65 | 826.9208 | 97.04% | 2.672% | 0.2884% | 51.6421 | 0 | 0 | 51.6421 | 0 | 49.2631 | 0.90625 | 54.3593 | 49.2631 | 0.90625 | 54.3593 | 51.8953 | 0.95467 | 54.3593 | 6.245%
2026 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 108 | 32 | 310.7968 | 16.09% | 83.08% | 0.8251% | 1.4817 | 0 | 0 | 1.4817 | 0 | 1.4134 | 0.44615 | 3.168 | 1.4134 | 0.44615 | 3.168 | 1.489 | 0.46999 | 3.168 | 0.4767%
2026 | 283 | CB 283 | Tier-3 | Tier-3---21 | Tier-3---11 | 2 | 2 | 6.0451 | 99.41% | 0% | 0.5857% | 0.60097 | 0 | 0 | 0.60097 | 0 | 0.57329 | 0.027885 | 20.5593 | 0.57329 | 0.027885 | 20.5593 | 0.60392 | 0.029374 | 20.5593 | 9.941%
2026 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 17 | 13 | 94.6686 | 66.47% | 32.93% | 0.6021% | 4.8122 | 0 | 0 | 4.8122 | 0 | 4.5905 | 0.18125 | 25.3268 | 4.5905 | 0.18125 | 25.3268 | 4.8358 | 0.19093 | 25.3268 | 5.083%
2026 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 21 | 1 | 10.7713 | 97.26% | 0% | 2.741% | 0.049886 | 0 | 0 | 0.049886 | 0 | 0.047588 | 0.013942 | 3.4132 | 0.047588 | 0.013942 | 3.4132 | 0.05013 | 0.014687 | 3.4132 | 0.4631%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 21 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 138.7612 | 0 | 0 | 138.7612 | 0 | 132.3688 | 0.29279 | 452.0978 | 132.3688 | 0.29279 | 452.0978 | 139.4414 | 0.30843 | 452.0978 | 9.526%
2026 | 200 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 34 | 8 | 215.2852 | 96.83% | 2.614% | 0.5577% | 4.9049 | 0 | 0 | 4.9049 | 0 | 4.6789 | 0.11154 | 41.949 | 4.6789 | 0.11154 | 41.949 | 4.9289 | 0.1175 | 41.949 | 2.278%
2026 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 156 | 73 | 124.2501 | 33.35% | 64.03% | 2.615% | 1.9393 | 0 | 0 | 1.9393 | 0 | 1.85 | 1.0178 | 1.8176 | 1.85 | 1.0178 | 1.8176 | 1.9488 | 1.0722 | 1.8176 | 1.561%
2026 | 200 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 48 | 25 | 261.2105 | 99.38% | 0% | 0.6196% | 13.5204 | 0 | 0 | 13.5204 | 0 | 12.8976 | 0.34856 | 37.0027 | 12.8976 | 0.34856 | 37.0027 | 13.5867 | 0.36718 | 37.0027 | 5.176%
2026 | 350 | CB 350 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 1 | 133.5736 | 99.92% | 0% | 0.07821% | 3.3367 | 0 | 0 | 3.3367 | 0 | 3.183 | 0.013942 | 228.2991 | 3.183 | 0.013942 | 228.2991 | 3.3531 | 0.014687 | 228.2991 | 2.498%
2026 | 353 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 110 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 1039.3116 | 0 | 0 | 1039.3116 | 0 | 991.4326 | 1.5337 | 646.4524 | 991.4326 | 1.5337 | 646.4524 | 1044.4062 | 1.6156 | 646.4524 | 7.119%
2026 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 5 | 4 | 87.8741 | 99.22% | 0.6237% | 0.1541% | 6.9753 | 0 | 0 | 6.9753 | 0 | 6.6539 | 0.055769 | 119.3118 | 6.6539 | 0.055769 | 119.3118 | 7.0094 | 0.058749 | 119.3118 | 7.938%
2026 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 4 | 1 | 7.5897 | 98.6% | 0% | 1.398% | 0.18709 | 0 | 0 | 0.18709 | 0 | 0.17847 | 0.013942 | 12.8007 | 0.17847 | 0.013942 | 12.8007 | 0.18801 | 0.014687 | 12.8007 | 2.465%
2026 | 354 | CB 354 | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 2 | 12.0695 | 99.46% | 0% | 0.538% | 0.8003 | 0 | 0 | 0.8003 | 0 | 0.76344 | 0.027885 | 27.3784 | 0.76344 | 0.027885 | 27.3784 | 0.80423 | 0.029374 | 27.3784 | 6.631%
2026 | 356 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 168 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 620.6565 | 0 | 0 | 620.6565 | 0 | 592.0641 | 2.3423 | 252.77 | 592.0641 | 2.3423 | 252.77 | 623.6989 | 2.4675 | 252.77 | 5.498%
2026 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 2 | 6.8062 | 99.1% | 0% | 0.8997% | 0.44966 | 0 | 0 | 0.44966 | 0 | 0.42895 | 0.027885 | 15.3829 | 0.42895 | 0.027885 | 15.3829 | 0.45187 | 0.029374 | 15.3829 | 6.607%
2026 | 1166 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 106 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 383.8802 | 0 | 0 | 383.8802 | 0 | 366.1957 | 1.4779 | 247.784 | 366.1957 | 1.4779 | 247.784 | 385.762 | 1.5568 | 247.784 | 6.282%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 21 | 6 | 861.4334 | 18.88% | 81.11% | 0.0161% | 4.6462 | 0 | 0 | 4.6462 | 0 | 4.4322 | 0.083654 | 52.9824 | 4.4322 | 0.083654 | 52.9824 | 4.669 | 0.088123 | 52.9824 | 0.5394%
2026 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 145 | 5 | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.33127 | 0 | 0 | 0.33127 | 0 | 0.31601 | 0.069711 | 4.5332 | 0.31601 | 0.069711 | 4.5332 | 0.3329 | 0.073436 | 4.5332 | 0.04946%
2026 | 442 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 94 | 87 | 1133.0808 | 94.08% | 5.666% | 0.2577% | 98.6577 | 0 | 0 | 98.6577 | 0 | 94.1127 | 1.213 | 77.5881 | 94.1127 | 1.213 | 77.5881 | 99.1413 | 1.2778 | 77.5881 | 8.707%
2026 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 36 | 22 | 67.1473 | 98.29% | 0% | 1.71% | 4.0333 | 0 | 0 | 4.0333 | 0 | 3.8475 | 0.30673 | 12.5435 | 3.8475 | 0.30673 | 12.5435 | 4.053 | 0.32312 | 12.5435 | 6.007%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 17 | 15 | 117.4434 | 97.68% | 1.947% | 0.3705% | 10.1225 | 0 | 0 | 10.1225 | 0 | 9.6561 | 0.20913 | 46.1719 | 9.6561 | 0.20913 | 46.1719 | 10.1721 | 0.22031 | 46.1719 | 8.619%
2026 | 449 | CB 449 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 7.8127 | 98.22% | 0% | 1.784% | 0.4604 | 0 | 0 | 0.4604 | 0 | 0.43919 | 0.041827 | 10.5002 | 0.43919 | 0.041827 | 10.5002 | 0.46266 | 0.044062 | 10.5002 | 5.893%
2026 | 443 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 36 | 27 | 101.8709 | 98.65% | 0% | 1.347% | 7.5374 | 0 | 0 | 7.5374 | 0 | 7.1902 | 0.37644 | 19.1003 | 7.1902 | 0.37644 | 19.1003 | 7.5743 | 0.39656 | 19.1003 | 7.399%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 48 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 83.2699 | 0 | 0 | 83.2699 | 0 | 79.4339 | 0.66923 | 118.6945 | 79.4339 | 0.66923 | 118.6945 | 83.6781 | 0.70499 | 118.6945 | 1.203%
2026 | 1299 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 6 | 19.4193 | 94.64% | 0% | 5.361% | 0.35571 | 0 | 0 | 0.35571 | 0 | 0.33932 | 0.083654 | 4.0563 | 0.33932 | 0.083654 | 4.0563 | 0.35745 | 0.088123 | 4.0563 | 1.832%
2026 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 2 | 2 | 1.7668 | 97.86% | 0% | 2.14% | 0.1729 | 0 | 0 | 0.1729 | 0 | 0.16493 | 0.027885 | 5.9149 | 0.16493 | 0.027885 | 5.9149 | 0.17375 | 0.029374 | 5.9149 | 9.786%
2026 | 520 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 14 | 11 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.16207 | 0 | 0 | 0.16207 | 0 | 0.1546 | 0.15337 | 1.0081 | 0.1546 | 0.15337 | 1.0081 | 0.16287 | 0.16156 | 1.0081 | 1.319%
2026 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 129 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 49.0233 | 0 | 0 | 49.0233 | 0 | 46.7649 | 1.7986 | 26.0014 | 46.7649 | 1.7986 | 26.0014 | 49.2636 | 1.8947 | 26.0014 | 4.563%
2026 | 522 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 126 | 305.5692 | 37.2% | 61.32% | 1.484% | 5.5296 | 0 | 0 | 5.5296 | 0 | 5.2749 | 1.7567 | 3.0027 | 5.2749 | 1.7567 | 3.0027 | 5.5567 | 1.8506 | 3.0027 | 1.81%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 90 | 12 | 481.3309 | 94.25% | 5.298% | 0.4514% | 6.0487 | 0 | 0 | 6.0487 | 0 | 5.7701 | 0.16731 | 34.488 | 5.7701 | 0.16731 | 34.488 | 6.0784 | 0.17625 | 34.488 | 1.257%
2026 | 1160 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 14 | 1 | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0025483 | 0 | 0 | 0.0025483 | 0 | 0.002431 | 0.013942 | 0.17436 | 0.002431 | 0.013942 | 0.17436 | 0.0025608 | 0.014687 | 0.17436 | 0.02403%
2026 | 1161 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 12 | 6 | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11347 | 0 | 0 | 0.11347 | 0 | 0.10824 | 0.083654 | 1.2939 | 0.10824 | 0.083654 | 1.2939 | 0.11402 | 0.088123 | 1.2939 | 1.8%
2026 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 10 | 5 | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25563 | 0 | 0 | 0.25563 | 0 | 0.24386 | 0.069711 | 3.4981 | 0.24386 | 0.069711 | 3.4981 | 0.25689 | 0.073436 | 3.4981 | 0.2293%
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 39 | 33 | 54.1099 | 76.19% | 21.99% | 1.82% | 3.4885 | 0 | 0 | 3.4885 | 0 | 3.3278 | 0.4601 | 7.2328 | 3.3278 | 0.4601 | 7.2328 | 3.5056 | 0.48468 | 7.2328 | 6.447%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 5 | 67.245 | 99.24% | 0% | 0.7576% | 2.0855 | 0 | 0 | 2.0855 | 0 | 1.9894 | 0.069711 | 28.5378 | 1.9894 | 0.069711 | 28.5378 | 2.0957 | 0.073436 | 28.5378 | 3.101%
2026 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 43 | 35 | 949.4775 | 95.45% | 4.414% | 0.1311% | 73.7702 | 0 | 0 | 73.7702 | 0 | 70.3718 | 0.48798 | 144.2104 | 70.3718 | 0.48798 | 144.2104 | 74.1319 | 0.51405 | 144.2104 | 7.77%
2026 | 542 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 19 | 13 | 417.7025 | 78.37% | 21.49% | 0.1463% | 22.397 | 0 | 0 | 22.397 | 0 | 21.3652 | 0.18125 | 117.8773 | 21.3652 | 0.18125 | 117.8773 | 22.5068 | 0.19093 | 117.8773 | 5.362%
2026 | 1094 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 262 | 4323.2442 | 99.81% | 0% | 0.1903% | 306.3779 | 0 | 0 | 306.3779 | 0 | 292.2637 | 3.6529 | 80.0091 | 292.2637 | 3.6529 | 80.0091 | 307.8797 | 3.8481 | 80.0091 | 7.087%
2026 | 67 | CB 67 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 10.8761 | 99.3% | 0% | 0.7025% | 0.71998 | 0 | 0 | 0.71998 | 0 | 0.68681 | 0.027885 | 24.6305 | 0.68681 | 0.027885 | 24.6305 | 0.72351 | 0.029374 | 24.6305 | 6.62%
2026 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 53 | 53 | 55.0677 | 92.66% | 4.028% | 3.312% | 5.1026 | 0 | 0 | 5.1026 | 0 | 4.8675 | 0.73894 | 6.5871 | 4.8675 | 0.73894 | 6.5871 | 5.1276 | 0.77842 | 6.5871 | 9.266%
2026 | 78 | CB 78 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 3 | 25.281 | 99.56% | 0% | 0.4423% | 1.8877 | 0 | 0 | 1.8877 | 0 | 1.8007 | 0.041827 | 43.0519 | 1.8007 | 0.041827 | 43.0519 | 1.8969 | 0.044062 | 43.0519 | 7.467%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 24 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 27.6164 | 0 | 0 | 27.6164 | 0 | 26.3441 | 0.33461 | 78.7297 | 26.3441 | 0.33461 | 78.7297 | 27.7517 | 0.35249 | 78.7297 | 0.3223%
2026 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 12 | 8 | 42.6475 | 99.43% | 0% | 0.5747% | 2.8268 | 0 | 0 | 2.8268 | 0 | 2.6966 | 0.11154 | 24.1765 | 2.6966 | 0.11154 | 24.1765 | 2.8407 | 0.1175 | 24.1765 | 6.628%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 39 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 209.3563 | 0 | 0 | 209.3563 | 0 | 199.7117 | 0.54375 | 367.2864 | 199.7117 | 0.54375 | 367.2864 | 210.3826 | 0.5728 | 367.2864 | 7.634%
2026 | 75 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 30 | 337.7351 | 93.43% | 6.078% | 0.496% | 13.9205 | 0 | 0 | 13.9205 | 0 | 13.2792 | 0.41827 | 31.748 | 13.2792 | 0.41827 | 31.748 | 13.9887 | 0.44062 | 31.748 | 4.122%
2026 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 53 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 112.8379 | 0 | 0 | 112.8379 | 0 | 107.6396 | 0.73894 | 145.6674 | 107.6396 | 0.73894 | 145.6674 | 113.391 | 0.77842 | 145.6674 | 6.818%
2026 | 236 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 4 | 3 | 251.0066 | 99.97% | 0% | 0.03372% | 18.8191 | 0 | 0 | 18.8191 | 0 | 17.9522 | 0.041827 | 429.2023 | 17.9522 | 0.041827 | 429.2023 | 18.9114 | 0.044062 | 429.2023 | 7.497%
2026 | 235 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 114 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 778.2289 | 0 | 0 | 778.2289 | 0 | 742.3775 | 1.5894 | 467.0743 | 742.3775 | 1.5894 | 467.0743 | 782.0437 | 1.6743 | 467.0743 | 6.793%
2026 | 973 | CB 973 | Tier-2 | Tier-2---14 | Tier-2---11 | 7 | 4 | 310.4015 | 99.93% | 0% | 0.0686% | 17.7251 | 0 | 0 | 17.7251 | 0 | 16.9085 | 0.055769 | 303.1874 | 16.9085 | 0.055769 | 303.1874 | 17.8119 | 0.058749 | 303.1874 | 5.71%
2026 | 973 | CB 974 | Tier-2 | Tier-2---12 | Tier-2---11 | 7 | 5 | 334.3039 | 99.93% | 0% | 0.06503% | 23.8633 | 0 | 0 | 23.8633 | 0 | 22.764 | 0.069711 | 326.546 | 22.764 | 0.069711 | 326.546 | 23.9803 | 0.073436 | 326.546 | 7.138%
2026 | 970 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 11 | 8 | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 94.4014 | 0 | 0 | 94.4014 | 0 | 90.0526 | 0.11154 | 807.3691 | 90.0526 | 0.11154 | 807.3691 | 94.8642 | 0.1175 | 807.3691 | 7.237%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 35 | 24 | 387.8494 | 99.7% | 0% | 0.3041% | 26.5145 | 0 | 0 | 26.5145 | 0 | 25.293 | 0.33461 | 75.5885 | 25.293 | 0.33461 | 75.5885 | 26.6445 | 0.35249 | 75.5885 | 6.836%
2026 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 14 | 11 | 132.7571 | 99.65% | 0% | 0.354% | 10.394 | 0 | 0 | 10.394 | 0 | 9.9152 | 0.15337 | 64.6507 | 9.9152 | 0.15337 | 64.6507 | 10.4449 | 0.16156 | 64.6507 | 7.829%
2026 | 982 | CB 982 | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.013942 | 0 | 0 | 0.013942 | 0 | 0 | 0.014687 | 0 | 0%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 6 | 2 | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.82631 | 0 | 0 | 0.82631 | 0 | 0.78824 | 0.027885 | 28.268 | 0.78824 | 0.027885 | 28.268 | 0.83036 | 0.029374 | 28.268 | 3.007%
2026 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 15.4911 | 99.81% | 0% | 0.1868% | 1.5462 | 0 | 0 | 1.5462 | 0 | 1.475 | 0.027885 | 52.8961 | 1.475 | 0.027885 | 52.8961 | 1.5538 | 0.029374 | 52.8961 | 9.981%
2026 | 520 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 161 | 346.5871 | 36.93% | 61.45% | 1.621% | 5.5543 | 0 | 0 | 5.5543 | 0 | 5.2984 | 2.2447 | 2.3604 | 5.2984 | 2.2447 | 2.3604 | 5.5815 | 2.3646 | 2.3604 | 1.603%
2026 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 109 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 61.1907 | 0 | 0 | 61.1907 | 0 | 58.3718 | 1.5197 | 38.4098 | 58.3718 | 1.5197 | 38.4098 | 61.4907 | 1.6009 | 38.4098 | 5.943%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 80 | 67 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 125.5197 | 0 | 0 | 125.5197 | 0 | 119.7372 | 0.93413 | 128.1801 | 119.7372 | 0.93413 | 128.1801 | 126.135 | 0.98405 | 128.1801 | 8.195%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 116 | 86 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 374.0843 | 0 | 0 | 374.0843 | 0 | 356.851 | 1.199 | 297.6148 | 356.851 | 1.199 | 297.6148 | 375.918 | 1.2631 | 297.6148 | 7.307%
2026 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 403 | 5 | 638.0788 | 99.02% | 0% | 0.9838% | 0.78387 | 0 | 0 | 0.78387 | 0 | 0.74776 | 0.069711 | 10.7265 | 0.74776 | 0.069711 | 10.7265 | 0.78772 | 0.073436 | 10.7265 | 0.1228%
2026 | 221 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 190 | 153 | 6915.6819 | 99% | 0.9206% | 0.07911% | 551.3273 | 0 | 0 | 551.3273 | 0 | 525.9288 | 2.1332 | 246.548 | 525.9288 | 2.1332 | 246.548 | 554.0299 | 2.2471 | 246.548 | 7.972%
2026 | 222 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 247 | 132 | 3027.5479 | 94.73% | 5.109% | 0.164% | 153.2642 | 0 | 0 | 153.2642 | 0 | 146.2036 | 1.8404 | 79.442 | 146.2036 | 1.8404 | 79.442 | 154.0155 | 1.9387 | 79.442 | 5.062%
2026 | 237 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 179 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 524.2711 | 0 | 0 | 524.2711 | 0 | 500.119 | 2.4957 | 200.3947 | 500.119 | 2.4957 | 200.3947 | 526.841 | 2.629 | 200.3947 | 4.985%
2026 | 237 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 62 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 269.606 | 0 | 0 | 269.606 | 0 | 257.1858 | 0.86442 | 297.5236 | 257.1858 | 0.86442 | 297.5236 | 270.9276 | 0.91061 | 297.5236 | 5.155%
2026 | 237 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 93 | 916.1972 | 69.5% | 30.07% | 0.4286% | 24.5712 | 0 | 0 | 24.5712 | 0 | 23.4392 | 1.2966 | 18.077 | 23.4392 | 1.2966 | 18.077 | 24.6916 | 1.3659 | 18.077 | 2.682%
2026 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 29.7534 | 99.88% | 0% | 0.1212% | 2.9717 | 0 | 0 | 2.9717 | 0 | 2.8348 | 0.027885 | 101.6631 | 2.8348 | 0.027885 | 101.6631 | 2.9863 | 0.029374 | 101.6631 | 9.988%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 58 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 228.7681 | 0 | 0 | 228.7681 | 0 | 218.2292 | 0.80865 | 269.8677 | 218.2292 | 0.80865 | 269.8677 | 229.8895 | 0.85186 | 269.8677 | 6.117%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 225 | 184 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 257.6221 | 0 | 0 | 257.6221 | 0 | 245.754 | 2.5654 | 95.7963 | 245.754 | 2.5654 | 95.7963 | 258.8849 | 2.7025 | 95.7963 | 7.664%
2026 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 220 | 27 | 94.186 | 2.003% | 94.63% | 3.363% | 0.023154 | 0 | 0 | 0.023154 | 0 | 0.022087 | 0.37644 | 0.058674 | 0.022087 | 0.37644 | 0.058674 | 0.023267 | 0.39656 | 0.058674 | 0.02458%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 138 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 71.5721 | 0 | 0 | 71.5721 | 0 | 68.2749 | 1.924 | 35.4853 | 68.2749 | 1.924 | 35.4853 | 71.923 | 2.0268 | 35.4853 | 3.468%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 235 | 175 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 263.5885 | 0 | 0 | 263.5885 | 0 | 251.4455 | 2.4399 | 103.0556 | 251.4455 | 2.4399 | 103.0556 | 264.8806 | 2.5703 | 103.0556 | 7.087%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 122 | 74 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 562.6656 | 0 | 0 | 562.6656 | 0 | 536.7448 | 1.0317 | 520.238 | 536.7448 | 1.0317 | 520.238 | 565.4238 | 1.0869 | 520.238 | 6.025%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 306 | 6920.124 | 97.57% | 2.306% | 0.1195% | 477.1808 | 0 | 0 | 477.1808 | 0 | 455.1981 | 4.2663 | 106.6952 | 455.1981 | 4.2663 | 106.6952 | 479.5199 | 4.4943 | 106.6952 | 6.896%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 125 | 117 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 552.7852 | 0 | 0 | 552.7852 | 0 | 527.3195 | 1.6312 | 323.2615 | 527.3195 | 1.6312 | 323.2615 | 555.4949 | 1.7184 | 323.2615 | 9.296%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 103 | 81 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 295.9408 | 0 | 0 | 295.9408 | 0 | 282.3074 | 1.1293 | 249.9788 | 282.3074 | 1.1293 | 249.9788 | 297.3915 | 1.1897 | 249.9788 | 7.823%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 4 | 1 | 117.1572 | 99.03% | 0.8725% | 0.09309% | 2.9006 | 0 | 0 | 2.9006 | 0 | 2.6396 | 0.0133 | 198.4626 | 2.6396 | 0.0133 | 198.4626 | 2.9292 | 0.014759 | 198.4626 | 2.476%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 10 | 10 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 40.5584 | 0 | 0 | 40.5584 | 0 | 36.9076 | 0.133 | 277.5011 | 36.9076 | 0.133 | 277.5011 | 40.9571 | 0.14759 | 277.5011 | 9.915%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 117 | 4222.2471 | 91.41% | 8.486% | 0.103% | 309.2954 | 0 | 0 | 309.2954 | 0 | 281.4546 | 1.5561 | 180.8719 | 281.4546 | 1.5561 | 180.8719 | 312.3351 | 1.7268 | 180.8719 | 7.325%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 10 | 10 | 114.5301 | 99.76% | 0% | 0.2395% | 11.4256 | 0 | 0 | 11.4256 | 0 | 10.3971 | 0.133 | 78.1739 | 10.3971 | 0.133 | 78.1739 | 11.5379 | 0.14759 | 78.1739 | 9.976%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 421 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 2840.2415 | 0 | 0 | 2840.2415 | 0 | 2584.5811 | 5.5993 | 461.5902 | 2584.5811 | 5.5993 | 461.5902 | 2868.1552 | 6.2136 | 461.5902 | 8.079%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 70 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 570.4582 | 0 | 0 | 570.4582 | 0 | 519.1092 | 0.931 | 557.5827 | 519.1092 | 0.931 | 557.5827 | 576.0647 | 1.0331 | 557.5827 | 8.085%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 139 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 1552.9096 | 0 | 0 | 1552.9096 | 0 | 1413.1265 | 1.8487 | 764.3897 | 1413.1265 | 1.8487 | 764.3897 | 1568.1715 | 2.0515 | 764.3897 | 8.249%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 69 | 61 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 442.8665 | 0 | 0 | 442.8665 | 0 | 403.0025 | 0.8113 | 496.7369 | 403.0025 | 0.8113 | 496.7369 | 447.219 | 0.90031 | 496.7369 | 8.797%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 16 | 16 | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 138.0795 | 0 | 0 | 138.0795 | 0 | 125.6505 | 0.2128 | 590.463 | 125.6505 | 0.2128 | 590.463 | 139.4365 | 0.23615 | 590.463 | 9.958%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 12 | 10 | 794.3626 | 99.6% | 0.3592% | 0.04176% | 65.9315 | 0 | 0 | 65.9315 | 0 | 59.9967 | 0.133 | 451.1035 | 59.9967 | 0.133 | 451.1035 | 66.5794 | 0.14759 | 451.1035 | 8.3%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 107 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 751.5808 | 0 | 0 | 751.5808 | 0 | 683.9283 | 1.4231 | 480.5907 | 683.9283 | 1.4231 | 480.5907 | 758.9673 | 1.5792 | 480.5907 | 7.669%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 9 | 9 | 694.7204 | 99.22% | 0.7469% | 0.03547% | 68.9285 | 0 | 0 | 68.9285 | 0 | 62.724 | 0.1197 | 524.0101 | 62.724 | 0.1197 | 524.0101 | 69.6059 | 0.13283 | 524.0101 | 9.922%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 76 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 429.4935 | 0 | 0 | 429.4935 | 0 | 390.8332 | 1.0108 | 386.6575 | 390.8332 | 1.0108 | 386.6575 | 433.7145 | 1.1217 | 386.6575 | 8.468%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 82 | 73 | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 255.3265 | 0 | 0 | 255.3265 | 0 | 232.3436 | 0.9709 | 239.3076 | 232.3436 | 0.9709 | 239.3076 | 257.8358 | 1.0774 | 239.3076 | 8.835%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 376 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 728.6709 | 0 | 0 | 728.6709 | 0 | 663.0806 | 5.0008 | 132.595 | 663.0806 | 5.0008 | 132.595 | 735.8322 | 5.5495 | 132.595 | 7.695%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 290 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 280.4875 | 0 | 0 | 280.4875 | 0 | 255.2398 | 3.857 | 66.1758 | 255.2398 | 3.857 | 66.1758 | 283.2441 | 4.2802 | 66.1758 | 7.432%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 85 | 585.5086 | 87.68% | 11.85% | 0.4758% | 36.6688 | 0 | 0 | 36.6688 | 0 | 33.3681 | 1.1305 | 29.5162 | 33.3681 | 1.1305 | 29.5162 | 37.0291 | 1.2545 | 29.5162 | 6.263%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 85 | 60 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 355.4132 | 0 | 0 | 355.4132 | 0 | 323.4212 | 0.798 | 405.2899 | 323.4212 | 0.798 | 405.2899 | 358.9062 | 0.88555 | 405.2899 | 6.936%
2027 | 1030 | 1030-1735F | Tier-3 | missing | missing | 6 | 6 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0798 | 0 | 0 | 0.0798 | 0 | 0 | 0.088555 | 0 | 0%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 143 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 863.2115 | 0 | 0 | 863.2115 | 0 | 785.5107 | 1.9019 | 413.0139 | 785.5107 | 1.9019 | 413.0139 | 871.6951 | 2.1106 | 413.0139 | 7.304%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 20 | 17 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 181.8205 | 0 | 0 | 181.8205 | 0 | 165.4542 | 0.2261 | 731.7748 | 165.4542 | 0.2261 | 731.7748 | 183.6075 | 0.25091 | 731.7748 | 8.453%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 98 | 72 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 479.9105 | 0 | 0 | 479.9105 | 0 | 436.712 | 0.9576 | 456.0487 | 436.712 | 0.9576 | 456.0487 | 484.6271 | 1.0627 | 456.0487 | 7.248%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 323 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 2209.1889 | 0 | 0 | 2209.1889 | 0 | 2010.3318 | 4.2959 | 467.9654 | 2010.3318 | 4.2959 | 467.9654 | 2230.9007 | 4.7672 | 467.9654 | 8.726%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 375 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 2222.2926 | 0 | 0 | 2222.2926 | 0 | 2022.256 | 4.9875 | 405.465 | 2022.256 | 4.9875 | 405.465 | 2244.1332 | 5.5347 | 405.465 | 7.825%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 372 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 2333.5174 | 0 | 0 | 2333.5174 | 0 | 2123.469 | 4.9476 | 429.1919 | 2123.469 | 4.9476 | 429.1919 | 2356.4511 | 5.4904 | 429.1919 | 8.741%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 338 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 984.307 | 0 | 0 | 984.307 | 0 | 895.7059 | 4.4954 | 199.2495 | 895.7059 | 4.4954 | 199.2495 | 993.9807 | 4.9886 | 199.2495 | 6.168%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 16 | 12 | 17.9659 | 86.84% | 10.72% | 2.434% | 1.1701 | 0 | 0 | 1.1701 | 0 | 1.0648 | 0.1596 | 6.6718 | 1.0648 | 0.1596 | 6.6718 | 1.1816 | 0.17711 | 6.6718 | 6.513%
2027 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | Tier-2---12 | 40 | 1 | 40.9949 | 23.55% | 73.64% | 2.81% | 0.024132 | 0 | 0 | 0.024132 | 0 | 0.02196 | 0.0133 | 1.6511 | 0.02196 | 0.0133 | 1.6511 | 0.02437 | 0.014759 | 1.6511 | 0.05887%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 4 | 4 | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.3453 | 0 | 0 | 0.3453 | 0 | 0.31422 | 0.0532 | 5.9063 | 0.31422 | 0.0532 | 5.9063 | 0.34869 | 0.059037 | 5.9063 | 1.275%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 3 | 3 | 6.3934 | 34.35% | 64.55% | 1.103% | 0.21961 | 0 | 0 | 0.21961 | 0 | 0.19984 | 0.0399 | 5.0085 | 0.19984 | 0.0399 | 5.0085 | 0.22176 | 0.044278 | 5.0085 | 3.435%
2027 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | Tier-2---12 | 237 | 1 | 117.3021 | 94.99% | 0% | 5.009% | 0.047015 | 0 | 0 | 0.047015 | 0 | 0.042783 | 0.0133 | 3.2168 | 0.042783 | 0.0133 | 3.2168 | 0.047478 | 0.014759 | 3.2168 | 0.04008%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 44 | 38 | 730.5479 | 99.24% | 0.5863% | 0.172% | 62.6144 | 0 | 0 | 62.6144 | 0 | 56.9782 | 0.5054 | 112.7389 | 56.9782 | 0.5054 | 112.7389 | 63.2297 | 0.56085 | 112.7389 | 8.571%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 122 | 117 | 919.3728 | 93.93% | 5.62% | 0.4487% | 82.8186 | 0 | 0 | 82.8186 | 0 | 75.3638 | 1.5561 | 48.4312 | 75.3638 | 1.5561 | 48.4312 | 83.6325 | 1.7268 | 48.4312 | 9.008%
2027 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 72 | 509.5021 | 91.97% | 7.519% | 0.512% | 42.1724 | 0 | 0 | 42.1724 | 0 | 38.3763 | 0.9576 | 40.0755 | 38.3763 | 0.9576 | 40.0755 | 42.5869 | 1.0627 | 40.0755 | 8.277%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 29 | 14 | 140.8367 | 88.02% | 11.68% | 0.2956% | 5.9845 | 0 | 0 | 5.9845 | 0 | 5.4458 | 0.1862 | 29.2469 | 5.4458 | 0.1862 | 29.2469 | 6.0433 | 0.20663 | 29.2469 | 4.249%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 317 | 215 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 398.5741 | 0 | 0 | 398.5741 | 0 | 362.697 | 2.8595 | 126.8394 | 362.697 | 2.8595 | 126.8394 | 402.4913 | 3.1732 | 126.8394 | 6.757%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 225 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 348.513 | 0 | 0 | 348.513 | 0 | 317.1421 | 2.9925 | 105.979 | 317.1421 | 2.9925 | 105.979 | 351.9382 | 3.3208 | 105.979 | 6.983%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 128 | 2514.2831 | 99.84% | 0% | 0.1648% | 192.3939 | 0 | 0 | 192.3939 | 0 | 175.0758 | 1.7024 | 102.8406 | 175.0758 | 1.7024 | 102.8406 | 194.2847 | 1.8892 | 102.8406 | 7.652%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 65 | 34 | 95.3301 | 98.77% | 0% | 1.235% | 4.9249 | 0 | 0 | 4.9249 | 0 | 4.4816 | 0.4522 | 9.9107 | 4.4816 | 0.4522 | 9.9107 | 4.9733 | 0.50181 | 9.9107 | 5.166%
2027 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 4 | 4 | 54.719 | 98.75% | 1.065% | 0.1855% | 5.4035 | 0 | 0 | 5.4035 | 0 | 4.9171 | 0.0532 | 92.4261 | 4.9171 | 0.0532 | 92.4261 | 5.4566 | 0.059037 | 92.4261 | 9.875%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 34 | 32 | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 201.2258 | 0 | 0 | 201.2258 | 0 | 183.1127 | 0.4256 | 430.2462 | 183.1127 | 0.4256 | 430.2462 | 203.2034 | 0.4723 | 430.2462 | 9.381%
2027 | 1100 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 54 | 51 | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 399.0156 | 0 | 0 | 399.0156 | 0 | 363.0987 | 0.6783 | 535.3072 | 363.0987 | 0.6783 | 535.3072 | 402.9371 | 0.75272 | 535.3072 | 9.437%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 12 | 12 | 417.0013 | 94.5% | 5.418% | 0.08666% | 39.4048 | 0 | 0 | 39.4048 | 0 | 35.8578 | 0.1596 | 224.6733 | 35.8578 | 0.1596 | 224.6733 | 39.7921 | 0.17711 | 224.6733 | 9.45%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 17 | 788.3757 | 99.4% | 0.5205% | 0.07536% | 70.1185 | 0 | 0 | 70.1185 | 0 | 63.8069 | 0.2261 | 282.2067 | 63.8069 | 0.2261 | 282.2067 | 70.8077 | 0.25091 | 282.2067 | 8.894%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 397 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 209.849 | 0 | 0 | 209.849 | 0 | 190.9597 | 5.2801 | 36.1659 | 190.9597 | 5.2801 | 36.1659 | 211.9114 | 5.8594 | 36.1659 | 4.499%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 65 | 56 | 240.2897 | 88.19% | 10.99% | 0.8202% | 18.2565 | 0 | 0 | 18.2565 | 0 | 16.6131 | 0.7448 | 22.3055 | 16.6131 | 0.7448 | 22.3055 | 18.4359 | 0.82652 | 22.3055 | 7.598%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 46 | 206.5878 | 96.62% | 2.592% | 0.7875% | 18.7386 | 0 | 0 | 18.7386 | 0 | 17.0519 | 0.6118 | 27.8717 | 17.0519 | 0.6118 | 27.8717 | 18.9228 | 0.67892 | 27.8717 | 9.071%
2027 | 260 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 37 | 30 | 247.9994 | 97.75% | 1.792% | 0.4608% | 19.655 | 0 | 0 | 19.655 | 0 | 17.8858 | 0.399 | 44.8265 | 17.8858 | 0.399 | 44.8265 | 19.8481 | 0.44278 | 44.8265 | 7.925%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 98 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 310.444 | 0 | 0 | 310.444 | 0 | 282.4998 | 1.3034 | 216.7408 | 282.4998 | 1.3034 | 216.7408 | 313.495 | 1.4464 | 216.7408 | 7.829%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 94 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 948.0153 | 0 | 0 | 948.0153 | 0 | 862.681 | 1.2502 | 690.0347 | 862.681 | 1.2502 | 690.0347 | 957.3324 | 1.3874 | 690.0347 | 9.378%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 216 | 186 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 880.7229 | 0 | 0 | 880.7229 | 0 | 801.4458 | 2.4738 | 323.9737 | 801.4458 | 2.4738 | 323.9737 | 889.3786 | 2.7452 | 323.9737 | 8.532%
2027 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | Tier-2---13 | 29 | 15 | 70.6534 | 98.66% | 0% | 1.337% | 3.6056 | 0 | 0 | 3.6056 | 0 | 3.2811 | 0.1995 | 16.4465 | 3.2811 | 0.1995 | 16.4465 | 3.6411 | 0.22139 | 16.4465 | 5.103%
2027 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | Tier-3---19 | 13 | 12 | 157.8878 | 78.49% | 21.24% | 0.2654% | 11.44 | 0 | 0 | 11.44 | 0 | 10.4102 | 0.1596 | 65.2269 | 10.4102 | 0.1596 | 65.2269 | 11.5524 | 0.17711 | 65.2269 | 7.246%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 133 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 537.0936 | 0 | 0 | 537.0936 | 0 | 488.7479 | 1.7689 | 276.3006 | 488.7479 | 1.7689 | 276.3006 | 542.3721 | 1.963 | 276.3006 | 8.737%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 58 | 55 | 2215.156 | 94.69% | 5.226% | 0.08401% | 198.904 | 0 | 0 | 198.904 | 0 | 180.9999 | 0.7315 | 247.4368 | 180.9999 | 0.7315 | 247.4368 | 200.8588 | 0.81176 | 247.4368 | 8.979%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 205 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 735.0191 | 0 | 0 | 735.0191 | 0 | 668.8574 | 2.7265 | 245.3173 | 668.8574 | 2.7265 | 245.3173 | 742.2428 | 3.0256 | 245.3173 | 8.452%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 95 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 138.9852 | 0 | 0 | 138.9852 | 0 | 126.4747 | 1.2635 | 100.0987 | 126.4747 | 1.2635 | 100.0987 | 140.3512 | 1.4021 | 100.0987 | 8.918%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 166 | 136 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 287.2101 | 0 | 0 | 287.2101 | 0 | 261.3573 | 1.8088 | 144.4921 | 261.3573 | 1.8088 | 144.4921 | 290.0328 | 2.0073 | 144.4921 | 8.063%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 157 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 245.2498 | 0 | 0 | 245.2498 | 0 | 223.174 | 2.0881 | 106.879 | 223.174 | 2.0881 | 106.879 | 247.6601 | 2.3172 | 106.879 | 8.22%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 56 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 132.4185 | 0 | 0 | 132.4185 | 0 | 120.499 | 0.7448 | 161.7871 | 120.499 | 0.7448 | 161.7871 | 133.7199 | 0.82652 | 161.7871 | 9.551%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 167 | 146 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 370.9048 | 0 | 0 | 370.9048 | 0 | 337.5183 | 1.9418 | 173.8173 | 337.5183 | 1.9418 | 173.8173 | 374.5501 | 2.1548 | 173.8173 | 8.625%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 44 | 44 | 411.5414 | 99.65% | 0% | 0.3468% | 41.0114 | 0 | 0 | 41.0114 | 0 | 37.3198 | 0.5852 | 63.7728 | 37.3198 | 0.5852 | 63.7728 | 41.4145 | 0.64941 | 63.7728 | 9.965%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 31 | 456.1931 | 99.77% | 0% | 0.2285% | 41.499 | 0 | 0 | 41.499 | 0 | 37.7636 | 0.4123 | 91.5925 | 37.7636 | 0.4123 | 91.5925 | 41.9069 | 0.45754 | 91.5925 | 9.097%
2027 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 2 | 2 | 2.4589 | 98.62% | 0% | 1.38% | 0.2425 | 0 | 0 | 0.2425 | 0 | 0.22067 | 0.0266 | 8.2959 | 0.22067 | 0.0266 | 8.2959 | 0.24488 | 0.029518 | 8.2959 | 9.862%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 52 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 95.0921 | 0 | 0 | 95.0921 | 0 | 86.5325 | 0.6916 | 125.1194 | 86.5325 | 0.6916 | 125.1194 | 96.0267 | 0.76748 | 125.1194 | 8.072%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 7 | 158.2514 | 99.48% | 0.3681% | 0.155% | 15.7423 | 0 | 0 | 15.7423 | 0 | 14.3253 | 0.0931 | 153.8703 | 14.3253 | 0.0931 | 153.8703 | 15.8971 | 0.10331 | 153.8703 | 9.948%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 68 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 175.7123 | 0 | 0 | 175.7123 | 0 | 159.8958 | 0.9044 | 176.7977 | 159.8958 | 0.9044 | 176.7977 | 177.4392 | 1.0036 | 176.7977 | 9.354%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 152 | 29 | 6418.5082 | 93.04% | 6.917% | 0.04745% | 113.9301 | 0 | 0 | 113.9301 | 0 | 103.6748 | 0.3857 | 268.7967 | 103.6748 | 0.3857 | 268.7967 | 115.0498 | 0.42802 | 268.7967 | 1.775%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 48 | 28 | 6815.4278 | 94.54% | 5.441% | 0.023% | 375.8452 | 0 | 0 | 375.8452 | 0 | 342.014 | 0.3724 | 918.4054 | 342.014 | 0.3724 | 918.4054 | 379.539 | 0.41326 | 918.4054 | 5.515%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 267 | 209 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 912.8844 | 0 | 0 | 912.8844 | 0 | 830.7124 | 2.7797 | 298.8498 | 830.7124 | 2.7797 | 298.8498 | 921.8562 | 3.0847 | 298.8498 | 7.77%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 146 | 102 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 252.6921 | 0 | 0 | 252.6921 | 0 | 229.9463 | 1.3566 | 169.502 | 229.9463 | 1.3566 | 169.502 | 255.1755 | 1.5054 | 169.502 | 6.857%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 22 | 18 | 427.4478 | 90.46% | 9.431% | 0.1062% | 31.6376 | 0 | 0 | 31.6376 | 0 | 28.7898 | 0.2394 | 120.2581 | 28.7898 | 0.2394 | 120.2581 | 31.9485 | 0.26567 | 120.2581 | 7.402%
2027 | 1458 | 1458-1057F | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 3 | 155.9987 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0399 | 0 | 0 | 0.0399 | 0 | 0 | 0.044278 | 0 | 0%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 36 | 29 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 163.0089 | 0 | 0 | 163.0089 | 0 | 148.3359 | 0.3857 | 384.5889 | 148.3359 | 0.3857 | 384.5889 | 164.6109 | 0.42802 | 384.5889 | 6.891%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 80 | 52 | 4370.0987 | 98.67% | 1.293% | 0.03403% | 280.288 | 0 | 0 | 280.288 | 0 | 255.0582 | 0.6916 | 368.7946 | 255.0582 | 0.6916 | 368.7946 | 283.0426 | 0.76748 | 368.7946 | 6.414%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 58.2342 | 99.94% | 0% | 0.06312% | 5.8197 | 0 | 0 | 5.8197 | 0 | 5.2959 | 0.0266 | 199.0936 | 5.2959 | 0.0266 | 199.0936 | 5.8769 | 0.029518 | 199.0936 | 9.994%
2027 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 3 | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0399 | 0 | 0 | 0.0399 | 0 | 0 | 0.044278 | 0 | 0%
2027 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 5 | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0665 | 0 | 0 | 0.0665 | 0 | 0 | 0.073796 | 0 | 0%
2027 | 1458 | 1458-1119F | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0133 | 0 | 0 | 0.0133 | 0 | 0 | 0.014759 | 0 | 0%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 188 | 132 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 1112.3302 | 0 | 0 | 1112.3302 | 0 | 1012.2053 | 1.7556 | 576.5583 | 1012.2053 | 1.7556 | 576.5583 | 1123.2621 | 1.9482 | 576.5583 | 6.958%
2027 | 1458 | 1458-454F | Tier-2 | Tier-2---18 | Tier-2---10 | 2 | 2 | 84.0912 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0266 | 0 | 0 | 0.0266 | 0 | 0 | 0.029518 | 0 | 0%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 6 | 167.5686 | 29.81% | 70.17% | 0.01889% | 4.2812 | 0 | 0 | 4.2812 | 0 | 3.8959 | 0.0798 | 48.8205 | 3.8959 | 0.0798 | 48.8205 | 4.3233 | 0.088555 | 48.8205 | 2.555%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 2 | 2 | 81.0039 | 99.95% | 0% | 0.04716% | 8.0966 | 0 | 0 | 8.0966 | 0 | 7.3678 | 0.0266 | 276.9841 | 7.3678 | 0.0266 | 276.9841 | 8.1761 | 0.029518 | 276.9841 | 9.995%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 127 | 108 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 688.6829 | 0 | 0 | 688.6829 | 0 | 626.6921 | 1.4364 | 436.2938 | 626.6921 | 1.4364 | 436.2938 | 695.4513 | 1.594 | 436.2938 | 8.44%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 353 | 37077.302 | 99.36% | 0.615% | 0.02874% | 2948.759 | 0 | 0 | 2948.759 | 0 | 2683.3305 | 4.6949 | 571.5418 | 2683.3305 | 4.6949 | 571.5418 | 2977.7393 | 5.21 | 571.5418 | 7.953%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 7 | 8.268 | 89.5% | 6.947% | 3.548% | 0.57557 | 0 | 0 | 0.57557 | 0 | 0.52376 | 0.0931 | 5.6258 | 0.52376 | 0.0931 | 5.6258 | 0.58123 | 0.10331 | 5.6258 | 6.961%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 87 | 81 | 418.5676 | 87.71% | 11.66% | 0.6303% | 34.1791 | 0 | 0 | 34.1791 | 0 | 31.1025 | 1.0773 | 28.8708 | 31.1025 | 1.0773 | 28.8708 | 34.515 | 1.1955 | 28.8708 | 8.166%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 669 | 544 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 414.0467 | 0 | 0 | 414.0467 | 0 | 376.7769 | 7.2352 | 52.0756 | 376.7769 | 7.2352 | 52.0756 | 418.116 | 8.029 | 52.0756 | 7.519%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 60 | 55 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 277.2195 | 0 | 0 | 277.2195 | 0 | 252.266 | 0.7315 | 344.8613 | 252.266 | 0.7315 | 344.8613 | 279.944 | 0.81176 | 344.8613 | 9.081%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 203 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 365.6682 | 0 | 0 | 365.6682 | 0 | 332.7531 | 2.6999 | 123.2465 | 332.7531 | 2.6999 | 123.2465 | 369.262 | 2.9961 | 123.2465 | 9.434%
2027 | 157 | 157-207R | Tier-3 | Tier-3---16 | Tier-3---7 | 23 | 23 | 719.0865 | 99.89% | 0% | 0.1123% | 71.8279 | 0 | 0 | 71.8279 | 0 | 65.3624 | 0.3059 | 213.6725 | 65.3624 | 0.3059 | 213.6725 | 72.5338 | 0.33946 | 213.6725 | 9.989%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 250 | 219 | 3160.5079 | 95.27% | 4.501% | 0.231% | 263.7603 | 0 | 0 | 263.7603 | 0 | 240.0183 | 2.9127 | 82.4041 | 240.0183 | 2.9127 | 82.4041 | 266.3525 | 3.2323 | 82.4041 | 8.346%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 554 | 449 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 136.2159 | 0 | 0 | 136.2159 | 0 | 123.9546 | 5.9717 | 20.757 | 123.9546 | 5.9717 | 20.757 | 137.5546 | 6.6269 | 20.757 | 6.609%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 173 | 154 | 1867.403 | 95.01% | 4.712% | 0.2778% | 157.9371 | 0 | 0 | 157.9371 | 0 | 143.7206 | 2.0482 | 70.1693 | 143.7206 | 2.0482 | 70.1693 | 159.4893 | 2.2729 | 70.1693 | 8.458%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 675 | 562 | 18749.5963 | 97% | 2.901% | 0.09453% | 1514.3227 | 0 | 0 | 1514.3227 | 0 | 1378.013 | 7.4746 | 184.3595 | 1378.013 | 7.4746 | 184.3595 | 1529.2054 | 8.2947 | 184.3595 | 8.077%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 99 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 383.7782 | 0 | 0 | 383.7782 | 0 | 349.2329 | 1.3167 | 265.2336 | 349.2329 | 1.3167 | 265.2336 | 387.5499 | 1.4612 | 265.2336 | 9.525%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 86 | 62 | 2651.4354 | 70.65% | 29.24% | 0.1064% | 135.0483 | 0 | 0 | 135.0483 | 0 | 122.8921 | 0.8246 | 149.0325 | 122.8921 | 0.8246 | 149.0325 | 136.3756 | 0.91507 | 149.0325 | 5.093%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 239 | 216 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 386.522 | 0 | 0 | 386.522 | 0 | 351.7297 | 2.8728 | 122.4345 | 351.7297 | 2.8728 | 122.4345 | 390.3207 | 3.188 | 122.4345 | 8.814%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 251 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 465.293 | 0 | 0 | 465.293 | 0 | 423.4103 | 3.3383 | 126.8342 | 423.4103 | 3.3383 | 126.8342 | 469.8659 | 3.7046 | 126.8342 | 8.104%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 43 | 836.2457 | 79.76% | 20.09% | 0.1547% | 55.1538 | 0 | 0 | 55.1538 | 0 | 50.1892 | 0.5719 | 87.7588 | 50.1892 | 0.5719 | 87.7588 | 55.6959 | 0.63465 | 87.7588 | 6.595%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 236 | 191 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 921.1257 | 0 | 0 | 921.1257 | 0 | 838.2119 | 2.5403 | 329.9658 | 838.2119 | 2.5403 | 329.9658 | 930.1785 | 2.819 | 329.9658 | 7.994%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 131 | 126 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 394.8393 | 0 | 0 | 394.8393 | 0 | 359.2984 | 1.6758 | 214.4042 | 359.2984 | 1.6758 | 214.4042 | 398.7198 | 1.8597 | 214.4042 | 9.435%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 250 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 783.6159 | 0 | 0 | 783.6159 | 0 | 713.0798 | 3.325 | 214.4602 | 713.0798 | 3.325 | 214.4602 | 791.3173 | 3.6898 | 214.4602 | 7.783%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 9 | 404.4817 | 67.64% | 32.12% | 0.2398% | 4.9245 | 0 | 0 | 4.9245 | 0 | 4.4812 | 0.1197 | 37.4372 | 4.4812 | 0.1197 | 37.4372 | 4.9729 | 0.13283 | 37.4372 | 1.217%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 172 | 143 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 276.3684 | 0 | 0 | 276.3684 | 0 | 251.4915 | 1.9019 | 132.2318 | 251.4915 | 1.9019 | 132.2318 | 279.0845 | 2.1106 | 132.2318 | 8.126%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 214 | 166 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 373.9475 | 0 | 0 | 373.9475 | 0 | 340.2871 | 2.2078 | 154.1296 | 340.2871 | 2.2078 | 154.1296 | 377.6226 | 2.45 | 154.1296 | 7.579%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 345 | 270 | 13172.958 | 96.8% | 3.124% | 0.0728% | 997.9703 | 0 | 0 | 997.9703 | 0 | 908.1394 | 3.591 | 252.8933 | 908.1394 | 3.591 | 252.8933 | 1007.7783 | 3.985 | 252.8933 | 7.576%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 27 | 1635.841 | 89.24% | 10.7% | 0.05535% | 131.3899 | 0 | 0 | 131.3899 | 0 | 119.5631 | 0.3591 | 332.9522 | 119.5631 | 0.3591 | 332.9522 | 132.6812 | 0.3985 | 332.9522 | 8.032%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 176 | 7 | 2963.4059 | 78.23% | 21.66% | 0.1106% | 9.2203 | 0 | 0 | 9.2203 | 0 | 8.3903 | 0.0931 | 90.1219 | 8.3903 | 0.0931 | 90.1219 | 9.3109 | 0.10331 | 90.1219 | 0.3111%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 7 | 47.6106 | 91.21% | 0% | 8.789% | 0.15199 | 0 | 0 | 0.15199 | 0 | 0.13831 | 0.0931 | 1.4856 | 0.13831 | 0.0931 | 1.4856 | 0.15349 | 0.10331 | 1.4856 | 0.3192%
2027 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 45 | 7 | 0.95479 | 13.38% | 0% | 86.62% | 0.0019878 | 0 | 0 | 0.0019878 | 0 | 0.0018088 | 0.0931 | 0.019429 | 0.0018088 | 0.0931 | 0.019429 | 0.0020073 | 0.10331 | 0.019429 | 0.2082%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 166 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 641.0014 | 0 | 0 | 641.0014 | 0 | 583.3026 | 2.2078 | 264.2009 | 583.3026 | 2.2078 | 264.2009 | 647.3011 | 2.45 | 264.2009 | 5.379%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 26 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 193.419 | 0 | 0 | 193.419 | 0 | 176.0087 | 0.3458 | 508.9901 | 176.0087 | 0.3458 | 508.9901 | 195.32 | 0.38374 | 508.9901 | 9.974%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 81 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 326.8629 | 0 | 0 | 326.8629 | 0 | 297.4408 | 1.0773 | 276.0985 | 297.4408 | 1.0773 | 276.0985 | 330.0753 | 1.1955 | 276.0985 | 7.727%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 19 | 19 | 655.8009 | 99.14% | 0.7615% | 0.1019% | 65.0139 | 0 | 0 | 65.0139 | 0 | 59.1617 | 0.2527 | 234.1186 | 59.1617 | 0.2527 | 234.1186 | 65.6528 | 0.28043 | 234.1186 | 9.914%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 42 | 25 | 316.4778 | 66.23% | 33.5% | 0.2671% | 12.4764 | 0 | 0 | 12.4764 | 0 | 11.3534 | 0.3325 | 34.1456 | 11.3534 | 0.3325 | 34.1456 | 12.5991 | 0.36898 | 34.1456 | 3.942%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 114 | 50 | 471.2015 | 74.37% | 25.17% | 0.4626% | 15.3697 | 0 | 0 | 15.3697 | 0 | 13.9862 | 0.665 | 21.0319 | 13.9862 | 0.665 | 21.0319 | 15.5208 | 0.73796 | 21.0319 | 3.262%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 161 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 98.1347 | 0 | 0 | 98.1347 | 0 | 89.3013 | 2.1413 | 41.7042 | 89.3013 | 2.1413 | 41.7042 | 99.0992 | 2.3762 | 41.7042 | 5.692%
2027 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 29 | 29 | 183.5383 | 99.34% | 0.09556% | 0.5689% | 18.2319 | 0 | 0 | 18.2319 | 0 | 16.5908 | 0.3857 | 43.0147 | 16.5908 | 0.3857 | 43.0147 | 18.4111 | 0.42802 | 43.0147 | 9.934%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 9 | 9 | 6.6189 | 96.38% | 0% | 3.621% | 0.63793 | 0 | 0 | 0.63793 | 0 | 0.58051 | 0.1197 | 4.8497 | 0.58051 | 0.1197 | 4.8497 | 0.6442 | 0.13283 | 4.8497 | 9.638%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 84 | 973.0999 | 95.53% | 4.02% | 0.4464% | 41.537 | 0 | 0 | 41.537 | 0 | 37.7981 | 1.1172 | 33.8329 | 37.7981 | 1.1172 | 33.8329 | 41.9452 | 1.2398 | 33.8329 | 4.269%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 315 | 490.4615 | 96.36% | 1.259% | 2.378% | 44.3083 | 0 | 0 | 44.3083 | 0 | 40.3199 | 4.1895 | 9.624 | 40.3199 | 4.1895 | 9.624 | 44.7437 | 4.6492 | 9.624 | 9.034%
2027 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 102 | 1 | 124.0064 | 98.52% | 0% | 1.478% | 0.11978 | 0 | 0 | 0.11978 | 0 | 0.109 | 0.0133 | 8.1952 | 0.109 | 0.0133 | 8.1952 | 0.12096 | 0.014759 | 8.1952 | 0.09659%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 16 | 1279.0443 | 99.78% | 0% | 0.2159% | 15.4701 | 0 | 0 | 15.4701 | 0 | 14.0776 | 0.2128 | 66.1541 | 14.0776 | 0.2128 | 66.1541 | 15.6221 | 0.23615 | 66.1541 | 1.21%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 106 | 2976.5734 | 99.75% | 0% | 0.2502% | 76.2052 | 0 | 0 | 76.2052 | 0 | 69.3457 | 1.4098 | 49.1883 | 69.3457 | 1.4098 | 49.1883 | 76.9541 | 1.5645 | 49.1883 | 2.56%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 345 | 8462.8018 | 99.74% | 0% | 0.2593% | 272.4132 | 0 | 0 | 272.4132 | 0 | 247.8923 | 4.5885 | 54.0247 | 247.8923 | 4.5885 | 54.0247 | 275.0905 | 5.0919 | 54.0247 | 3.219%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 111 | 105 | 498.1496 | 90.1% | 9.186% | 0.7154% | 42.4564 | 0 | 0 | 42.4564 | 0 | 38.6348 | 1.3965 | 27.6654 | 38.6348 | 1.3965 | 27.6654 | 42.8737 | 1.5497 | 27.6654 | 8.523%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 221 | 193 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 77.7075 | 0 | 0 | 77.7075 | 0 | 70.7128 | 2.5669 | 27.548 | 70.7128 | 2.5669 | 27.548 | 78.4712 | 2.8485 | 27.548 | 7.487%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 77 | 72 | 170.5929 | 70.47% | 28.1% | 1.432% | 11.2414 | 0 | 0 | 11.2414 | 0 | 10.2295 | 0.9576 | 10.6825 | 10.2295 | 0.9576 | 10.6825 | 11.3519 | 1.0627 | 10.6825 | 6.59%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 95 | 71 | 317.7725 | 50.82% | 48.53% | 0.6462% | 12.0704 | 0 | 0 | 12.0704 | 0 | 10.9839 | 0.9443 | 11.6318 | 10.9839 | 0.9443 | 11.6318 | 12.189 | 1.0479 | 11.6318 | 3.798%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 293 | 259 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 94.894 | 0 | 0 | 94.894 | 0 | 86.3523 | 3.4447 | 25.0682 | 86.3523 | 3.4447 | 25.0682 | 95.8266 | 3.8226 | 25.0682 | 7.91%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 361 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 131.0591 | 0 | 0 | 131.0591 | 0 | 119.262 | 4.8013 | 24.8395 | 119.262 | 4.8013 | 24.8395 | 132.3472 | 5.3281 | 24.8395 | 7.243%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 279 | 252 | 1890.633 | 91.06% | 8.49% | 0.4466% | 155.5063 | 0 | 0 | 155.5063 | 0 | 141.5086 | 3.3516 | 42.2212 | 141.5086 | 3.3516 | 42.2212 | 157.0346 | 3.7193 | 42.2212 | 8.225%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 287 | 250 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 144.5469 | 0 | 0 | 144.5469 | 0 | 131.5357 | 3.325 | 39.5596 | 131.5357 | 3.325 | 39.5596 | 145.9675 | 3.6898 | 39.5596 | 8.312%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 219 | 185 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 125.9884 | 0 | 0 | 125.9884 | 0 | 114.6477 | 2.4605 | 46.5953 | 114.6477 | 2.4605 | 46.5953 | 127.2266 | 2.7305 | 46.5953 | 8.023%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 79 | 77 | 609.7797 | 99.07% | 0.4924% | 0.4406% | 58.8797 | 0 | 0 | 58.8797 | 0 | 53.5798 | 1.0241 | 52.3189 | 53.5798 | 1.0241 | 52.3189 | 59.4584 | 1.1365 | 52.3189 | 9.656%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 218 | 186 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 413.4942 | 0 | 0 | 413.4942 | 0 | 376.2741 | 2.4738 | 152.1037 | 376.2741 | 2.4738 | 152.1037 | 417.558 | 2.7452 | 152.1037 | 8.46%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 273 | 259 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 117.6038 | 0 | 0 | 117.6038 | 0 | 107.0179 | 3.4447 | 31.0674 | 107.0179 | 3.4447 | 31.0674 | 118.7596 | 3.8226 | 31.0674 | 9.29%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 201 | 179 | 998.7912 | 96.62% | 2.787% | 0.5903% | 85.9427 | 0 | 0 | 85.9427 | 0 | 78.2067 | 2.3807 | 32.8503 | 78.2067 | 2.3807 | 32.8503 | 86.7873 | 2.6419 | 32.8503 | 8.605%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 71 | 66 | 261.4279 | 97.06% | 2.12% | 0.8249% | 23.5861 | 0 | 0 | 23.5861 | 0 | 21.4631 | 0.8778 | 24.451 | 21.4631 | 0.8778 | 24.451 | 23.8179 | 0.97411 | 24.451 | 9.022%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 201 | 183 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 131.2891 | 0 | 0 | 131.2891 | 0 | 119.4713 | 2.4339 | 49.0864 | 119.4713 | 2.4339 | 49.0864 | 132.5794 | 2.7009 | 49.0864 | 8.856%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 234 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 208.1629 | 0 | 0 | 208.1629 | 0 | 189.4254 | 3.1122 | 60.8655 | 189.4254 | 3.1122 | 60.8655 | 210.2087 | 3.4537 | 60.8655 | 7.546%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 115 | 105 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 92.115 | 0 | 0 | 92.115 | 0 | 83.8234 | 1.3965 | 60.0239 | 83.8234 | 1.3965 | 60.0239 | 93.0203 | 1.5497 | 60.0239 | 8.867%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 31 | 29 | 104.9439 | 97.78% | 1.295% | 0.9224% | 9.5996 | 0 | 0 | 9.5996 | 0 | 8.7355 | 0.3857 | 22.6485 | 8.7355 | 0.3857 | 22.6485 | 9.694 | 0.42802 | 22.6485 | 9.147%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 155 | 151 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 208.0708 | 0 | 0 | 208.0708 | 0 | 189.3416 | 2.0083 | 94.2796 | 189.3416 | 2.0083 | 94.2796 | 210.1157 | 2.2286 | 94.2796 | 9.617%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 147 | 133 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 130.1927 | 0 | 0 | 130.1927 | 0 | 118.4736 | 1.7689 | 66.9759 | 118.4736 | 1.7689 | 66.9759 | 131.4722 | 1.963 | 66.9759 | 8.85%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 377 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 2197.2181 | 0 | 0 | 2197.2181 | 0 | 1999.4385 | 5.0141 | 398.7634 | 1999.4385 | 5.0141 | 398.7634 | 2218.8122 | 5.5642 | 398.7634 | 8.36%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 248 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 576.6978 | 0 | 0 | 576.6978 | 0 | 524.7872 | 3.2984 | 159.1036 | 524.7872 | 3.2984 | 159.1036 | 582.3656 | 3.6603 | 159.1036 | 8.65%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 157 | 155 | 484.0355 | 97.4% | 1.48% | 1.12% | 46.5447 | 0 | 0 | 46.5447 | 0 | 42.355 | 2.0615 | 20.5457 | 42.355 | 2.0615 | 20.5457 | 47.0021 | 2.2877 | 20.5457 | 9.616%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 94 | 89 | 400.1895 | 97.86% | 1.359% | 0.7809% | 37.0794 | 0 | 0 | 37.0794 | 0 | 33.7417 | 1.1837 | 28.5053 | 33.7417 | 1.1837 | 28.5053 | 37.4438 | 1.3136 | 28.5053 | 9.265%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 70 | 60 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 43.4342 | 0 | 0 | 43.4342 | 0 | 39.5246 | 0.798 | 49.5295 | 39.5246 | 0.798 | 49.5295 | 43.8611 | 0.88555 | 49.5295 | 8.461%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 150 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 188.6471 | 0 | 0 | 188.6471 | 0 | 171.6663 | 1.995 | 86.0483 | 171.6663 | 1.995 | 86.0483 | 190.5011 | 2.2139 | 86.0483 | 8.543%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 160 | 1721.769 | 85.69% | 14.07% | 0.2459% | 120.4361 | 0 | 0 | 120.4361 | 0 | 109.5952 | 2.128 | 51.5015 | 109.5952 | 2.128 | 51.5015 | 121.6197 | 2.3615 | 51.5015 | 6.995%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 264 | 206 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1731.1083 | 0 | 0 | 1731.1083 | 0 | 1575.285 | 2.7398 | 574.9638 | 1575.285 | 2.7398 | 574.9638 | 1748.1216 | 3.0404 | 574.9638 | 7.744%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 205 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 999.0205 | 0 | 0 | 999.0205 | 0 | 909.095 | 2.7265 | 333.4295 | 909.095 | 2.7265 | 333.4295 | 1008.8388 | 3.0256 | 333.4295 | 7.865%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 193 | 19489.7064 | 99% | 0.9737% | 0.02962% | 1532.4175 | 0 | 0 | 1532.4175 | 0 | 1394.4791 | 2.5669 | 543.2544 | 1394.4791 | 2.5669 | 543.2544 | 1547.478 | 2.8485 | 543.2544 | 7.863%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 50 | 1412.4296 | 98.09% | 1.785% | 0.1216% | 130.7071 | 0 | 0 | 130.7071 | 0 | 118.9416 | 0.665 | 178.8597 | 118.9416 | 0.665 | 178.8597 | 131.9916 | 0.73796 | 178.8597 | 9.254%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 117 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 499.1945 | 0 | 0 | 499.1945 | 0 | 454.2602 | 1.5561 | 291.9224 | 454.2602 | 1.5561 | 291.9224 | 504.1005 | 1.7268 | 291.9224 | 9.185%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 195 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 1013.3363 | 0 | 0 | 1013.3363 | 0 | 922.1222 | 2.5935 | 355.5514 | 922.1222 | 2.5935 | 355.5514 | 1023.2953 | 2.8781 | 355.5514 | 7.217%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 71.2816 | 99.9% | 0% | 0.09987% | 7.121 | 0 | 0 | 7.121 | 0 | 6.48 | 0.0266 | 243.6109 | 6.48 | 0.0266 | 243.6109 | 7.191 | 0.029518 | 243.6109 | 9.99%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 333 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 131.2012 | 0 | 0 | 131.2012 | 0 | 119.3913 | 4.4289 | 26.9573 | 119.3913 | 4.4289 | 26.9573 | 132.4906 | 4.9148 | 26.9573 | 6.516%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 306 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 213.1484 | 0 | 0 | 213.1484 | 0 | 193.9621 | 4.0698 | 47.6589 | 193.9621 | 4.0698 | 47.6589 | 215.2432 | 4.5163 | 47.6589 | 7.815%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 297 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 981.8904 | 0 | 0 | 981.8904 | 0 | 893.5068 | 3.9501 | 226.1986 | 893.5068 | 3.9501 | 226.1986 | 991.5403 | 4.3835 | 226.1986 | 9.188%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 247 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 291.8358 | 0 | 0 | 291.8358 | 0 | 265.5666 | 3.2851 | 80.8398 | 265.5666 | 3.2851 | 80.8398 | 294.704 | 3.6455 | 80.8398 | 7.98%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 217 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 110.8226 | 0 | 0 | 110.8226 | 0 | 100.8471 | 2.8861 | 34.9423 | 100.8471 | 2.8861 | 34.9423 | 111.9118 | 3.2028 | 34.9423 | 7.703%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 116 | 114 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 984.8031 | 0 | 0 | 984.8031 | 0 | 896.1574 | 1.5162 | 591.0552 | 896.1574 | 1.5162 | 591.0552 | 994.4817 | 1.6826 | 591.0552 | 9.734%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 132 | 111 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 178.116 | 0 | 0 | 178.116 | 0 | 162.0832 | 1.4763 | 109.7902 | 162.0832 | 1.4763 | 109.7902 | 179.8666 | 1.6383 | 109.7902 | 8.101%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 272 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 134.619 | 0 | 0 | 134.619 | 0 | 122.5015 | 3.6176 | 33.8626 | 122.5015 | 3.6176 | 33.8626 | 135.942 | 4.0145 | 33.8626 | 6.99%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 614 | 616 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 321.491 | 0 | 0 | 321.491 | 0 | 292.5525 | 8.1928 | 35.7085 | 292.5525 | 8.1928 | 35.7085 | 324.6506 | 9.0917 | 35.7085 | 8.966%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 97 | 54 | 3690.9623 | 99.91% | 0% | 0.09183% | 205.2876 | 0 | 0 | 205.2876 | 0 | 186.8089 | 0.7182 | 260.1072 | 186.8089 | 0.7182 | 260.1072 | 207.3051 | 0.797 | 260.1072 | 5.562%
2027 | 221 | 221-1236F | Tier-3 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0133 | 0 | 0 | 0.0133 | 0 | 0 | 0.014759 | 0 | 0%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 307 | 168 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 164.9318 | 0 | 0 | 164.9318 | 0 | 150.0857 | 2.2344 | 67.1705 | 150.0857 | 2.2344 | 67.1705 | 166.5528 | 2.4796 | 67.1705 | 5.043%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 293 | 223 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 200.1253 | 0 | 0 | 200.1253 | 0 | 182.1113 | 2.9659 | 61.4017 | 182.1113 | 2.9659 | 61.4017 | 202.0921 | 3.2913 | 61.4017 | 7.315%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 13 | 13 | 710.3273 | 99.46% | 0.4791% | 0.06249% | 70.648 | 0 | 0 | 70.648 | 0 | 64.2887 | 0.1729 | 371.8262 | 64.2887 | 0.1729 | 371.8262 | 71.3423 | 0.19187 | 371.8262 | 9.946%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 244 | 151 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 236.2624 | 0 | 0 | 236.2624 | 0 | 214.9955 | 2.0083 | 107.0535 | 214.9955 | 2.0083 | 107.0535 | 238.5843 | 2.2286 | 107.0535 | 6.004%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 18 | 26 | 318.0967 | 33.4% | 66.33% | 0.2755% | 15.3453 | 0 | 0 | 15.3453 | 0 | 13.9641 | 0.3458 | 40.3819 | 13.9641 | 0.3458 | 40.3819 | 15.4962 | 0.38374 | 40.3819 | 4.824%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 99 | 76 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 157.0165 | 0 | 0 | 157.0165 | 0 | 142.8828 | 1.0108 | 141.3563 | 142.8828 | 1.0108 | 141.3563 | 158.5596 | 1.1217 | 141.3563 | 7.639%
2027 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 100 | 91 | 3904.259 | 99.88% | 0.03221% | 0.0896% | 354.8548 | 0 | 0 | 354.8548 | 0 | 322.913 | 1.2103 | 266.8042 | 322.913 | 1.2103 | 266.8042 | 358.3423 | 1.3431 | 266.8042 | 9.089%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 93 | 93 | 618.0174 | 98.68% | 0.7939% | 0.5237% | 60.9875 | 0 | 0 | 60.9875 | 0 | 55.4977 | 1.2369 | 44.8684 | 55.4977 | 1.2369 | 44.8684 | 61.5868 | 1.3726 | 44.8684 | 9.868%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 67 | 55 | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 365.8842 | 0 | 0 | 365.8842 | 0 | 332.9497 | 0.7315 | 455.1604 | 332.9497 | 0.7315 | 455.1604 | 369.4801 | 0.81176 | 455.1604 | 8.164%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 106 | 68 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 144.4234 | 0 | 0 | 144.4234 | 0 | 131.4234 | 0.9044 | 145.3156 | 131.4234 | 0.9044 | 145.3156 | 145.8428 | 1.0036 | 145.3156 | 6.214%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 123 | 107 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 833.2729 | 0 | 0 | 833.2729 | 0 | 758.267 | 1.4231 | 532.8279 | 758.267 | 1.4231 | 532.8279 | 841.4622 | 1.5792 | 532.8279 | 8.664%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 76 | 57 | 1359.3953 | 95.15% | 4.696% | 0.1502% | 97.0139 | 0 | 0 | 97.0139 | 0 | 88.2813 | 0.7581 | 116.4508 | 88.2813 | 0.7581 | 116.4508 | 97.9673 | 0.84128 | 116.4508 | 7.137%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 367 | 257 | 7406.689 | 96.62% | 3.25% | 0.1263% | 501.1579 | 0 | 0 | 501.1579 | 0 | 456.0469 | 3.4181 | 133.4212 | 456.0469 | 3.4181 | 133.4212 | 506.0833 | 3.7931 | 133.4212 | 6.766%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 451 | 389 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 6779.655 | 0 | 0 | 6779.655 | 0 | 6169.3937 | 5.1737 | 1192.4535 | 6169.3937 | 5.1737 | 1192.4535 | 6846.2851 | 5.7413 | 1192.4535 | 8.561%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 18 | 17 | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 339.3326 | 0 | 0 | 339.3326 | 0 | 308.7881 | 0.2261 | 1365.7152 | 308.7881 | 0.2261 | 1365.7152 | 342.6676 | 0.25091 | 1365.7152 | 9.375%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 287 | 246 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 3851.9498 | 0 | 0 | 3851.9498 | 0 | 3505.2219 | 3.2718 | 1071.344 | 3505.2219 | 3.2718 | 1071.344 | 3889.8066 | 3.6308 | 1071.344 | 8.54%
2027 | 220 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 43 | 18 | 288.7705 | 86.56% | 13.18% | 0.2657% | 10.463 | 0 | 0 | 10.463 | 0 | 9.5212 | 0.2394 | 39.771 | 9.5212 | 0.2394 | 39.771 | 10.5658 | 0.26567 | 39.771 | 3.623%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 407 | 288 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 504.7808 | 0 | 0 | 504.7808 | 0 | 459.3437 | 3.8304 | 119.9206 | 459.3437 | 3.8304 | 119.9206 | 509.7418 | 4.2507 | 119.9206 | 6.797%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 79 | 75 | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 460.682 | 0 | 0 | 460.682 | 0 | 419.2144 | 0.9975 | 420.2652 | 419.2144 | 0.9975 | 420.2652 | 465.2096 | 1.1069 | 420.2652 | 9.479%
2027 | 221 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 910 | 544 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 969.5191 | 0 | 0 | 969.5191 | 0 | 882.2492 | 7.2352 | 121.9385 | 882.2492 | 7.2352 | 121.9385 | 979.0475 | 8.029 | 121.9385 | 5.78%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 5 | 17.3686 | 98.33% | 0% | 1.666% | 1.0675 | 0 | 0 | 1.0675 | 0 | 0.97137 | 0.0665 | 14.607 | 0.97137 | 0.0665 | 14.607 | 1.0779 | 0.073796 | 14.607 | 6.146%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 9 | 9 | 171.5883 | 99.37% | 0.4538% | 0.1789% | 17.0503 | 0 | 0 | 17.0503 | 0 | 15.5155 | 0.1197 | 129.6199 | 15.5155 | 0.1197 | 129.6199 | 17.2178 | 0.13283 | 129.6199 | 9.937%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 213 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 150.4557 | 0 | 0 | 150.4557 | 0 | 136.9126 | 2.8329 | 48.3295 | 136.9126 | 2.8329 | 48.3295 | 151.9343 | 3.1437 | 48.3295 | 7.521%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 328 | 221 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 422.9789 | 0 | 0 | 422.9789 | 0 | 384.905 | 2.9393 | 130.9513 | 384.905 | 2.9393 | 130.9513 | 427.1359 | 3.2618 | 130.9513 | 6.621%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 245 | 177 | 2072.8837 | 91.06% | 8.635% | 0.3% | 136.3741 | 0 | 0 | 136.3741 | 0 | 124.0986 | 2.3541 | 52.716 | 124.0986 | 2.3541 | 52.716 | 137.7144 | 2.6124 | 52.716 | 6.579%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 71 | 51 | 536.3838 | 78.97% | 20.71% | 0.32% | 30.4256 | 0 | 0 | 30.4256 | 0 | 27.6869 | 0.6783 | 40.8181 | 27.6869 | 0.6783 | 40.8181 | 30.7246 | 0.75272 | 40.8181 | 5.672%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 52 | 38 | 788.7224 | 98.19% | 1.606% | 0.2041% | 56.5939 | 0 | 0 | 56.5939 | 0 | 51.4997 | 0.5054 | 101.899 | 51.4997 | 0.5054 | 101.899 | 57.1501 | 0.56085 | 101.899 | 7.175%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 183 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 263.0824 | 0 | 0 | 263.0824 | 0 | 239.4014 | 2.4339 | 98.3613 | 239.4014 | 2.4339 | 98.3613 | 265.668 | 2.7009 | 98.3613 | 7.574%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 6 | 121.6067 | 92.98% | 6.845% | 0.1786% | 11.3066 | 0 | 0 | 11.3066 | 0 | 10.2888 | 0.0798 | 128.9325 | 10.2888 | 0.0798 | 128.9325 | 11.4177 | 0.088555 | 128.9325 | 9.298%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 41 | 29 | 195.7251 | 81.71% | 17.81% | 0.4804% | 11.3124 | 0 | 0 | 11.3124 | 0 | 10.2942 | 0.3857 | 26.6896 | 10.2942 | 0.3857 | 26.6896 | 11.4236 | 0.42802 | 26.6896 | 5.78%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 245 | 2730.9177 | 98.3% | 1.373% | 0.325% | 184.2332 | 0 | 0 | 184.2332 | 0 | 167.6497 | 3.2585 | 51.45 | 167.6497 | 3.2585 | 51.45 | 186.0439 | 3.616 | 51.45 | 6.746%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 613 | 5142.095 | 98.68% | 0.901% | 0.4182% | 360.8495 | 0 | 0 | 360.8495 | 0 | 328.3681 | 8.1529 | 40.2763 | 328.3681 | 8.1529 | 40.2763 | 364.3959 | 9.0474 | 40.2763 | 7.018%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 5 | 4 | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0041361 | 0 | 0 | 0.0041361 | 0 | 0.0037638 | 0.0532 | 0.070748 | 0.0037638 | 0.0532 | 0.070748 | 0.0041768 | 0.059037 | 0.070748 | 0.03619%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 292 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 212.6612 | 0 | 0 | 212.6612 | 0 | 193.5188 | 3.8836 | 49.8298 | 193.5188 | 3.8836 | 49.8298 | 214.7512 | 4.3097 | 49.8298 | 7.005%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 222 | 718.991 | 97.57% | 1.357% | 1.072% | 57.0469 | 0 | 0 | 57.0469 | 0 | 51.9119 | 2.9526 | 17.5818 | 51.9119 | 2.9526 | 17.5818 | 57.6075 | 3.2766 | 17.5818 | 7.934%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 89 | 447.7794 | 94.96% | 4.349% | 0.694% | 38.225 | 0 | 0 | 38.225 | 0 | 34.7842 | 1.1837 | 29.386 | 34.7842 | 1.1837 | 29.386 | 38.6007 | 1.3136 | 29.386 | 8.537%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 327 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 159.6551 | 0 | 0 | 159.6551 | 0 | 145.284 | 4.3491 | 33.4055 | 145.284 | 4.3491 | 33.4055 | 161.2242 | 4.8263 | 33.4055 | 6.818%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 216 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 317.6971 | 0 | 0 | 317.6971 | 0 | 289.1001 | 2.8728 | 100.6336 | 289.1001 | 2.8728 | 100.6336 | 320.8194 | 3.188 | 100.6336 | 6.432%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 130 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 209.157 | 0 | 0 | 209.157 | 0 | 190.33 | 1.729 | 110.081 | 190.33 | 1.729 | 110.081 | 211.2126 | 1.9187 | 110.081 | 4.781%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 270 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1184.3293 | 0 | 0 | 1184.3293 | 0 | 1077.7235 | 3.591 | 300.1181 | 1077.7235 | 3.591 | 300.1181 | 1195.9688 | 3.985 | 300.1181 | 5.002%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 252 | 162 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 616.8774 | 0 | 0 | 616.8774 | 0 | 561.3501 | 2.1546 | 260.5357 | 561.3501 | 2.1546 | 260.5357 | 622.9401 | 2.391 | 260.5357 | 6.347%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 137 | 97 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 194.444 | 0 | 0 | 194.444 | 0 | 176.9414 | 1.2901 | 137.1533 | 176.9414 | 1.2901 | 137.1533 | 196.355 | 1.4316 | 137.1533 | 6.886%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 81 | 69 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 189.8927 | 0 | 0 | 189.8927 | 0 | 172.7998 | 0.9177 | 188.2967 | 172.7998 | 0.9177 | 188.2967 | 191.759 | 1.0184 | 188.2967 | 8.4%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 171 | 127 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 388.3774 | 0 | 0 | 388.3774 | 0 | 353.4182 | 1.6891 | 209.2347 | 353.4182 | 1.6891 | 209.2347 | 392.1944 | 1.8744 | 209.2347 | 7.284%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 498 | 306 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1282.7226 | 0 | 0 | 1282.7226 | 0 | 1167.2601 | 4.0698 | 286.8103 | 1167.2601 | 4.0698 | 286.8103 | 1295.3291 | 4.5163 | 286.8103 | 6.044%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 192 | 130 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 458.9623 | 0 | 0 | 458.9623 | 0 | 417.6494 | 1.729 | 241.5556 | 417.6494 | 1.729 | 241.5556 | 463.4729 | 1.9187 | 241.5556 | 6.625%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 126 | 113 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 323.9509 | 0 | 0 | 323.9509 | 0 | 294.7909 | 1.5029 | 196.1482 | 294.7909 | 1.5029 | 196.1482 | 327.1347 | 1.6678 | 196.1482 | 8.914%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 223 | 158 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1988.3938 | 0 | 0 | 1988.3938 | 0 | 1809.4113 | 2.1014 | 861.0508 | 1809.4113 | 2.1014 | 861.0508 | 2007.9356 | 2.332 | 861.0508 | 7.039%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 275 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1374.0091 | 0 | 0 | 1374.0091 | 0 | 1250.3295 | 3.6575 | 341.8538 | 1250.3295 | 3.6575 | 341.8538 | 1387.5128 | 4.0588 | 341.8538 | 5.074%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 46 | 663.2151 | 70.89% | 28.72% | 0.399% | 19.1377 | 0 | 0 | 19.1377 | 0 | 17.415 | 0.6118 | 28.4652 | 17.415 | 0.6118 | 28.4652 | 19.3258 | 0.67892 | 28.4652 | 2.886%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 59 | 29 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 122.9074 | 0 | 0 | 122.9074 | 0 | 111.8441 | 0.3857 | 289.977 | 111.8441 | 0.3857 | 289.977 | 124.1153 | 0.42802 | 289.977 | 4.858%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 499 | 344 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 2110.859 | 0 | 0 | 2110.859 | 0 | 1920.8529 | 4.5752 | 419.8404 | 1920.8529 | 4.5752 | 419.8404 | 2131.6044 | 5.0772 | 419.8404 | 6.833%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 651 | 565 | 65515.492 | 98.93% | 1.038% | 0.03019% | 5625.3221 | 0 | 0 | 5625.3221 | 0 | 5118.9665 | 7.5145 | 681.2122 | 5118.9665 | 7.5145 | 681.2122 | 5680.6075 | 8.339 | 681.2122 | 8.586%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 110 | 860.3234 | 98.08% | 1.495% | 0.4234% | 73.0864 | 0 | 0 | 73.0864 | 0 | 66.5076 | 1.463 | 45.4598 | 66.5076 | 1.463 | 45.4598 | 73.8046 | 1.6235 | 45.4598 | 8.495%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 50 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 142.1904 | 0 | 0 | 142.1904 | 0 | 129.3913 | 0.665 | 194.5735 | 129.3913 | 0.665 | 194.5735 | 143.5878 | 0.73796 | 194.5735 | 8.97%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 134 | 111 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 89.2076 | 0 | 0 | 89.2076 | 0 | 81.1777 | 1.4763 | 54.9873 | 81.1777 | 1.4763 | 54.9873 | 90.0844 | 1.6383 | 54.9873 | 7.99%
2027 | 1233 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 250 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 504.7804 | 0 | 0 | 504.7804 | 0 | 459.3433 | 3.325 | 138.1484 | 459.3433 | 3.325 | 138.1484 | 509.7413 | 3.6898 | 138.1484 | 8.052%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 101 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 66.6975 | 0 | 0 | 66.6975 | 0 | 60.6938 | 1.3433 | 45.1827 | 60.6938 | 1.3433 | 45.1827 | 67.353 | 1.4907 | 45.1827 | 6.478%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 52 | 38 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 27.166 | 0 | 0 | 27.166 | 0 | 24.7207 | 0.5054 | 48.9131 | 24.7207 | 0.5054 | 48.9131 | 27.433 | 0.56085 | 48.9131 | 7.217%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 165 | 99 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 69.7467 | 0 | 0 | 69.7467 | 0 | 63.4686 | 1.3167 | 48.2028 | 63.4686 | 1.3167 | 48.2028 | 70.4322 | 1.4612 | 48.2028 | 5.903%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 71 | 40 | 791.3356 | 98.7% | 1.112% | 0.1837% | 44.0048 | 0 | 0 | 44.0048 | 0 | 40.0438 | 0.532 | 75.2703 | 40.0438 | 0.532 | 75.2703 | 44.4373 | 0.59037 | 75.2703 | 5.561%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 75 | 64 | 376.72 | 96.88% | 2.523% | 0.5996% | 31.143 | 0 | 0 | 31.143 | 0 | 28.3397 | 0.8512 | 33.2938 | 28.3397 | 0.8512 | 33.2938 | 31.449 | 0.94459 | 33.2938 | 8.267%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 363 | 4437.6588 | 97.91% | 1.769% | 0.321% | 253.1626 | 0 | 0 | 253.1626 | 0 | 230.3745 | 4.8279 | 47.7174 | 230.3745 | 4.8279 | 47.7174 | 255.6507 | 5.3576 | 47.7174 | 5.705%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 269 | 189 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 260.4973 | 0 | 0 | 260.4973 | 0 | 237.049 | 2.5137 | 94.3029 | 237.049 | 2.5137 | 94.3029 | 263.0575 | 2.7895 | 94.3029 | 6.96%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 265 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 273.401 | 0 | 0 | 273.401 | 0 | 248.7911 | 3.5245 | 70.5891 | 248.7911 | 3.5245 | 70.5891 | 276.0879 | 3.9112 | 70.5891 | 7.458%
2027 | 240 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 56 | 960.3446 | 65.96% | 33.81% | 0.2324% | 30.3183 | 0 | 0 | 30.3183 | 0 | 27.5892 | 0.7448 | 37.0425 | 27.5892 | 0.7448 | 37.0425 | 30.6162 | 0.82652 | 37.0425 | 3.157%
2027 | 242 | 242-1427F | Tier-2 | Tier-2---20 | Tier-2---19 | 5 | 3 | 24.991 | 71.07% | 28.66% | 0.2708% | 1.0657 | 0 | 0 | 1.0657 | 0 | 0.96977 | 0.0399 | 24.305 | 0.96977 | 0.0399 | 24.305 | 1.0762 | 0.044278 | 24.305 | 4.264%
2027 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 470 | 1 | 404.2589 | 29.5% | 68.39% | 2.113% | 0.025372 | 0 | 0 | 0.025372 | 0 | 0.023089 | 0.0133 | 1.736 | 0.023089 | 0.0133 | 1.736 | 0.025622 | 0.014759 | 1.736 | 0.006276%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 310 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 227.682 | 0 | 0 | 227.682 | 0 | 207.1875 | 4.123 | 50.2517 | 207.1875 | 4.123 | 50.2517 | 229.9196 | 4.5754 | 50.2517 | 6.722%
2027 | 246 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 161 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 89.2584 | 0 | 0 | 89.2584 | 0 | 81.2239 | 2.1413 | 37.9321 | 81.2239 | 2.1413 | 37.9321 | 90.1356 | 2.3762 | 37.9321 | 6.562%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 9 | 9 | 105.2026 | 98.18% | 1.532% | 0.2854% | 10.3291 | 0 | 0 | 10.3291 | 0 | 9.3993 | 0.1197 | 78.5241 | 9.3993 | 0.1197 | 78.5241 | 10.4306 | 0.13283 | 78.5241 | 9.818%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 292 | 3753.23 | 95.85% | 3.876% | 0.273% | 226.3951 | 0 | 0 | 226.3951 | 0 | 206.0165 | 3.8836 | 53.0478 | 206.0165 | 3.8836 | 53.0478 | 228.6201 | 4.3097 | 53.0478 | 6.032%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 98 | 86 | 49.4853 | 86.66% | 6.71% | 6.626% | 3.7635 | 0 | 0 | 3.7635 | 0 | 3.4247 | 1.1438 | 2.9942 | 3.4247 | 1.1438 | 2.9942 | 3.8005 | 1.2693 | 2.9942 | 7.605%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 96 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 460.0093 | 0 | 0 | 460.0093 | 0 | 418.6022 | 1.2768 | 327.8528 | 418.6022 | 1.2768 | 327.8528 | 464.5303 | 1.4169 | 327.8528 | 8.68%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 112 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 155.9138 | 0 | 0 | 155.9138 | 0 | 141.8794 | 1.4896 | 95.2467 | 141.8794 | 1.4896 | 95.2467 | 157.4461 | 1.653 | 95.2467 | 7.743%
2027 | 283 | 283-80F | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 2 | 22.6843 | 50.28% | 49.56% | 0.1579% | 1.1406 | 0 | 0 | 1.1406 | 0 | 1.038 | 0.0266 | 39.0209 | 1.038 | 0.0266 | 39.0209 | 1.1518 | 0.029518 | 39.0209 | 5.028%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 170 | 2 | 481.2843 | 94.31% | 4.95% | 0.7414% | 0.53399 | 0 | 0 | 0.53399 | 0 | 0.48592 | 0.0266 | 18.2678 | 0.48592 | 0.0266 | 18.2678 | 0.53924 | 0.029518 | 18.2678 | 0.111%
2027 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 7 | 2 | 41.8014 | 98.23% | 1.253% | 0.5152% | 1.1732 | 0 | 0 | 1.1732 | 0 | 1.0676 | 0.0266 | 40.1354 | 1.0676 | 0.0266 | 40.1354 | 1.1847 | 0.029518 | 40.1354 | 2.807%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 34 | 550.61 | 92.88% | 6.93% | 0.1872% | 40.4378 | 0 | 0 | 40.4378 | 0 | 36.7979 | 0.4522 | 81.3752 | 36.7979 | 0.4522 | 81.3752 | 40.8352 | 0.50181 | 81.3752 | 7.344%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 43 | 29 | 3.2301 | 78.97% | 0% | 21.03% | 0.17202 | 0 | 0 | 0.17202 | 0 | 0.15654 | 0.3857 | 0.40586 | 0.15654 | 0.3857 | 0.40586 | 0.17372 | 0.42802 | 0.40586 | 5.326%
2027 | 198 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 68 | 458.7821 | 99.48% | 0% | 0.5194% | 44.9785 | 0 | 0 | 44.9785 | 0 | 40.9298 | 0.9044 | 45.2563 | 40.9298 | 0.9044 | 45.2563 | 45.4205 | 1.0036 | 45.2563 | 9.804%
2027 | 231 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 194 | 754.1323 | 92.41% | 6.882% | 0.7076% | 54.0793 | 0 | 0 | 54.0793 | 0 | 49.2114 | 2.5802 | 19.0727 | 49.2114 | 2.5802 | 19.0727 | 54.6108 | 2.8633 | 19.0727 | 7.171%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 49 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 202.683 | 0 | 0 | 202.683 | 0 | 184.4388 | 0.6517 | 283.0119 | 184.4388 | 0.6517 | 283.0119 | 204.6749 | 0.7232 | 283.0119 | 8.42%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 86 | 4762.848 | 95.55% | 4.384% | 0.07015% | 359.046 | 0 | 0 | 359.046 | 0 | 326.7269 | 1.1438 | 285.6505 | 326.7269 | 1.1438 | 285.6505 | 362.5746 | 1.2693 | 285.6505 | 7.538%
2027 | 308 | 308-486AE | Tier-2 | Tier-2---16 | Tier-2---8 | 142 | 1 | 164.6778 | 2.383% | 96.2% | 1.419% | 0.002764 | 0 | 0 | 0.002764 | 0 | 0.0025152 | 0.0133 | 0.18911 | 0.0025152 | 0.0133 | 0.18911 | 0.0027912 | 0.014759 | 0.18911 | 0.001678%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 39 | 14 | 95.5263 | 19.37% | 79.9% | 0.729% | 0.66438 | 0 | 0 | 0.66438 | 0 | 0.60457 | 0.1862 | 3.2469 | 0.60457 | 0.1862 | 3.2469 | 0.67091 | 0.20663 | 3.2469 | 0.6955%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 14 | 7 | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9562 | 0 | 0 | 1.9562 | 0 | 1.7801 | 0.0931 | 19.1204 | 1.7801 | 0.0931 | 19.1204 | 1.9754 | 0.10331 | 19.1204 | 4.235%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 15 | 12 | 15.6056 | 49.38% | 48.09% | 2.529% | 0.61652 | 0 | 0 | 0.61652 | 0 | 0.56103 | 0.1596 | 3.5152 | 0.56103 | 0.1596 | 3.5152 | 0.62258 | 0.17711 | 3.5152 | 3.951%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 12 | 278.652 | 16.28% | 83.57% | 0.1501% | 3.8883 | 0 | 0 | 3.8883 | 0 | 3.5383 | 0.1596 | 22.17 | 3.5383 | 0.1596 | 22.17 | 3.9265 | 0.17711 | 22.17 | 1.395%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 79 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.15148 | 0 | 0 | 0.15148 | 0 | 0.13785 | 1.0507 | 0.13119 | 0.13785 | 1.0507 | 0.13119 | 0.15297 | 1.166 | 0.13119 | 0.09476%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 15 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0086582 | 0 | 0 | 0.0086582 | 0 | 0.0078788 | 0.1995 | 0.039493 | 0.0078788 | 0.1995 | 0.039493 | 0.0087433 | 0.22139 | 0.039493 | 0.004284%
2027 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 9 | 9 | 14.6681 | 98.1% | 0% | 1.899% | 1.439 | 0 | 0 | 1.439 | 0 | 1.3094 | 0.1197 | 10.9393 | 1.3094 | 0.1197 | 10.9393 | 1.4531 | 0.13283 | 10.9393 | 9.81%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 39 | 34 | 209.8559 | 99.5% | 0% | 0.498% | 18.204 | 0 | 0 | 18.204 | 0 | 16.5654 | 0.4522 | 36.633 | 16.5654 | 0.4522 | 36.633 | 18.3829 | 0.50181 | 36.633 | 8.675%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 15 | 8 | 302.428 | 99.27% | 0.6612% | 0.06922% | 16.0117 | 0 | 0 | 16.0117 | 0 | 14.5704 | 0.1064 | 136.9401 | 14.5704 | 0.1064 | 136.9401 | 16.169 | 0.11807 | 136.9401 | 5.294%
2027 | 233 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 476 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 289.7593 | 0 | 0 | 289.7593 | 0 | 263.677 | 6.3308 | 41.6499 | 263.677 | 6.3308 | 41.6499 | 292.6071 | 7.0254 | 41.6499 | 8.044%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 709 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 1168.497 | 0 | 0 | 1168.497 | 0 | 1063.3164 | 9.4297 | 112.7625 | 1063.3164 | 9.4297 | 112.7625 | 1179.981 | 10.4643 | 112.7625 | 8.424%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 711 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 476.0154 | 0 | 0 | 476.0154 | 0 | 433.1675 | 9.4563 | 45.8073 | 433.1675 | 9.4563 | 45.8073 | 480.6936 | 10.4938 | 45.8073 | 8.545%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 297 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 1104.4919 | 0 | 0 | 1104.4919 | 0 | 1005.0725 | 3.9501 | 254.4424 | 1005.0725 | 3.9501 | 254.4424 | 1115.3468 | 4.3835 | 254.4424 | 8.168%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 373 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 869.7107 | 0 | 0 | 869.7107 | 0 | 791.4249 | 4.9609 | 159.5326 | 791.4249 | 4.9609 | 159.5326 | 878.2581 | 5.5052 | 159.5326 | 7.764%
2027 | 1039 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 225 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1540.0982 | 0 | 0 | 1540.0982 | 0 | 1401.4684 | 2.9925 | 468.3272 | 1401.4684 | 2.9925 | 468.3272 | 1555.2342 | 3.3208 | 468.3272 | 6.549%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 83 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 688.1193 | 0 | 0 | 688.1193 | 0 | 626.1792 | 1.1039 | 567.2429 | 626.1792 | 1.1039 | 567.2429 | 694.8821 | 1.225 | 567.2429 | 7.525%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 279 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 1437.3667 | 0 | 0 | 1437.3667 | 0 | 1307.9841 | 3.7107 | 352.49 | 1307.9841 | 3.7107 | 352.49 | 1451.4931 | 4.1178 | 352.49 | 7.722%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 161 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 709.5156 | 0 | 0 | 709.5156 | 0 | 645.6495 | 2.1413 | 301.5224 | 645.6495 | 2.1413 | 301.5224 | 716.4887 | 2.3762 | 301.5224 | 7.694%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 46 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 205.229 | 0 | 0 | 205.229 | 0 | 186.7556 | 0.6118 | 305.2561 | 186.7556 | 0.6118 | 305.2561 | 207.246 | 0.67892 | 305.2561 | 8.147%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 25 | 25 | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 221.4151 | 0 | 0 | 221.4151 | 0 | 201.4848 | 0.3325 | 605.9695 | 201.4848 | 0.3325 | 605.9695 | 223.5912 | 0.36898 | 605.9695 | 9.993%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 28 | 25 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 157.6982 | 0 | 0 | 157.6982 | 0 | 143.5032 | 0.3325 | 431.5888 | 143.5032 | 0.3325 | 431.5888 | 159.2481 | 0.36898 | 431.5888 | 7.919%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 69 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 361.4968 | 0 | 0 | 361.4968 | 0 | 328.9571 | 0.9177 | 358.4584 | 328.9571 | 0.9177 | 358.4584 | 365.0496 | 1.0184 | 358.4584 | 7.935%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 11 | 465.1006 | 62.84% | 37.09% | 0.07221% | 29.2268 | 0 | 0 | 29.2268 | 0 | 26.596 | 0.1463 | 181.7909 | 26.596 | 0.1463 | 181.7909 | 29.514 | 0.16235 | 181.7909 | 6.284%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 147 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 1092.9655 | 0 | 0 | 1092.9655 | 0 | 994.5837 | 1.9551 | 508.7127 | 994.5837 | 1.9551 | 508.7127 | 1103.7071 | 2.1696 | 508.7127 | 8.075%
2027 | 350 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 327 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1382.7374 | 0 | 0 | 1382.7374 | 0 | 1258.2722 | 4.3491 | 289.318 | 1258.2722 | 4.3491 | 289.318 | 1396.3269 | 4.8263 | 289.318 | 6.742%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 75 | 3653.654 | 88.54% | 11.39% | 0.07412% | 272.5948 | 0 | 0 | 272.5948 | 0 | 248.0576 | 0.9975 | 248.6794 | 248.0576 | 0.9975 | 248.6794 | 275.2739 | 1.1069 | 248.6794 | 7.461%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 129 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 421.7122 | 0 | 0 | 421.7122 | 0 | 383.7524 | 1.7157 | 223.6711 | 383.7524 | 1.7157 | 223.6711 | 425.8568 | 1.9039 | 223.6711 | 5.622%
2027 | 355 | 355-65R | Tier-2 | Tier-2---21 | Tier-2---24 | 1 | 1 | 0.06699 | 46.11% | 0% | 53.89% | 0.0030886 | 0 | 0 | 0.0030886 | 0 | 0.0028106 | 0.0133 | 0.21132 | 0.0028106 | 0.0133 | 0.21132 | 0.003119 | 0.014759 | 0.21132 | 4.611%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 58 | 35 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 81.9442 | 0 | 0 | 81.9442 | 0 | 74.5681 | 0.4655 | 160.1893 | 74.5681 | 0.4655 | 160.1893 | 82.7495 | 0.51657 | 160.1893 | 4.824%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 119 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 293.9946 | 0 | 0 | 293.9946 | 0 | 267.5311 | 1.5827 | 169.0347 | 267.5311 | 1.5827 | 169.0347 | 296.884 | 1.7563 | 169.0347 | 5.407%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 429 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 912.4735 | 0 | 0 | 912.4735 | 0 | 830.3385 | 5.7057 | 145.528 | 830.3385 | 5.7057 | 145.528 | 921.4413 | 6.3317 | 145.528 | 5.698%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 730 | 400 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 485.9291 | 0 | 0 | 485.9291 | 0 | 442.1888 | 5.32 | 83.1182 | 442.1888 | 5.32 | 83.1182 | 490.7048 | 5.9037 | 83.1182 | 5.228%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 40 | 22 | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 68.1695 | 0 | 0 | 68.1695 | 0 | 62.0333 | 0.2926 | 212.0073 | 62.0333 | 0.2926 | 212.0073 | 68.8395 | 0.3247 | 212.0073 | 5.448%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 48 | 44 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 465.8919 | 0 | 0 | 465.8919 | 0 | 423.9553 | 0.5852 | 724.4625 | 423.9553 | 0.5852 | 724.4625 | 470.4706 | 0.64941 | 724.4625 | 9.137%
2027 | 1458 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 17 | 10 | 878.9304 | 95.49% | 4.482% | 0.03213% | 49.3677 | 0 | 0 | 49.3677 | 0 | 44.9239 | 0.133 | 337.7739 | 44.9239 | 0.133 | 337.7739 | 49.8529 | 0.14759 | 337.7739 | 5.617%
2027 | 1458 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 141 | 16869.708 | 98.79% | 1.184% | 0.02933% | 867.0712 | 0 | 0 | 867.0712 | 0 | 789.0229 | 1.8753 | 420.7451 | 789.0229 | 1.8753 | 420.7451 | 875.5927 | 2.0811 | 420.7451 | 5.14%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 242 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 1149.9849 | 0 | 0 | 1149.9849 | 0 | 1046.4706 | 3.2186 | 325.1324 | 1046.4706 | 3.2186 | 325.1324 | 1161.2869 | 3.5717 | 325.1324 | 6.498%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 231 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 610.5815 | 0 | 0 | 610.5815 | 0 | 555.6209 | 3.0723 | 180.8486 | 555.6209 | 3.0723 | 180.8486 | 616.5823 | 3.4094 | 180.8486 | 5.853%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 172 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 727.1836 | 0 | 0 | 727.1836 | 0 | 661.7272 | 2.2876 | 289.2671 | 661.7272 | 2.2876 | 289.2671 | 734.3304 | 2.5386 | 289.2671 | 6.185%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 21 | 9 | 599.5834 | 97.21% | 2.746% | 0.04768% | 24.9785 | 0 | 0 | 24.9785 | 0 | 22.7301 | 0.1197 | 189.8923 | 22.7301 | 0.1197 | 189.8923 | 25.224 | 0.13283 | 189.8923 | 4.166%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 13 | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 124.4356 | 0 | 0 | 124.4356 | 0 | 113.2347 | 0.1729 | 654.9149 | 113.2347 | 0.1729 | 654.9149 | 125.6586 | 0.19187 | 654.9149 | 9.254%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 344 | 227 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 2446.3909 | 0 | 0 | 2446.3909 | 0 | 2226.1824 | 3.0191 | 737.3666 | 2226.1824 | 3.0191 | 737.3666 | 2470.4339 | 3.3503 | 737.3666 | 6.506%
2027 | 283 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 140 | 38 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 35.1557 | 0 | 0 | 35.1557 | 0 | 31.9912 | 0.5054 | 63.2988 | 31.9912 | 0.5054 | 63.2988 | 35.5012 | 0.56085 | 63.2988 | 2.416%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 76 | 41 | 924.8041 | 18.79% | 81.02% | 0.1888% | 9.3732 | 0 | 0 | 9.3732 | 0 | 8.5294 | 0.5453 | 15.6418 | 8.5294 | 0.5453 | 15.6418 | 9.4653 | 0.60513 | 15.6418 | 1.014%
2027 | 1138 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 458 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 169.3729 | 0 | 0 | 169.3729 | 0 | 154.127 | 6.0914 | 25.3024 | 154.127 | 6.0914 | 25.3024 | 171.0374 | 6.7597 | 25.3024 | 5.399%
2027 | 401 | 401-684R | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 1 | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049818 | 0 | 0 | 0.049818 | 0 | 0.045333 | 0.0133 | 3.4085 | 0.045333 | 0.0133 | 3.4085 | 0.050307 | 0.014759 | 3.4085 | 3.121%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 193 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 102.5551 | 0 | 0 | 102.5551 | 0 | 93.3238 | 2.5669 | 36.3566 | 93.3238 | 2.5669 | 36.3566 | 103.563 | 2.8485 | 36.3566 | 5.521%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 494 | 6370.0414 | 98.47% | 1.262% | 0.272% | 361.9772 | 0 | 0 | 361.9772 | 0 | 329.3943 | 6.5702 | 50.1346 | 329.3943 | 6.5702 | 50.1346 | 365.5347 | 7.2911 | 50.1346 | 5.682%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 47 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 13.271 | 0 | 0 | 13.271 | 0 | 12.0764 | 0.6251 | 19.3192 | 12.0764 | 0.6251 | 19.3192 | 13.4014 | 0.69368 | 19.3192 | 0.9827%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 84 | 81 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 330.5962 | 0 | 0 | 330.5962 | 0 | 300.838 | 1.0773 | 279.252 | 300.838 | 1.0773 | 279.252 | 333.8453 | 1.1955 | 279.252 | 9.397%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 49 | 582.1633 | 91.34% | 8.391% | 0.2732% | 54.2799 | 0 | 0 | 54.2799 | 0 | 49.394 | 0.6517 | 75.7925 | 49.394 | 0.6517 | 75.7925 | 54.8134 | 0.7232 | 75.7925 | 9.324%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 133 | 119 | 4750.1268 | 98% | 1.916% | 0.08125% | 416.5218 | 0 | 0 | 416.5218 | 0 | 379.0292 | 1.5827 | 239.4827 | 379.0292 | 1.5827 | 239.4827 | 420.6154 | 1.7563 | 239.4827 | 8.769%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 97 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 506.3705 | 0 | 0 | 506.3705 | 0 | 460.7902 | 1.2901 | 357.1742 | 460.7902 | 1.2901 | 357.1742 | 511.347 | 1.4316 | 357.1742 | 9.467%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 201 | 196 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 171.9277 | 0 | 0 | 171.9277 | 0 | 156.4519 | 2.6068 | 60.0169 | 156.4519 | 2.6068 | 60.0169 | 173.6174 | 2.8928 | 60.0169 | 9.37%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 3 | 3 | 88.141 | 1.745% | 98.17% | 0.08447% | 0.15379 | 0 | 0 | 0.15379 | 0 | 0.13995 | 0.0399 | 3.5075 | 0.13995 | 0.0399 | 3.5075 | 0.15531 | 0.044278 | 3.5075 | 0.1745%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 89 | 852.9261 | 84.92% | 14.72% | 0.3553% | 44.4597 | 0 | 0 | 44.4597 | 0 | 40.4578 | 1.1837 | 34.1791 | 40.4578 | 1.1837 | 34.1791 | 44.8967 | 1.3136 | 34.1791 | 5.213%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 144 | 71 | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0335 | 0 | 0 | 15.0335 | 0 | 13.6802 | 0.9443 | 14.4872 | 13.6802 | 0.9443 | 14.4872 | 15.1812 | 1.0479 | 14.4872 | 2.857%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 408 | 11572.221 | 88.48% | 11.4% | 0.1243% | 547.4938 | 0 | 0 | 547.4938 | 0 | 498.2119 | 5.4264 | 91.8126 | 498.2119 | 5.4264 | 91.8126 | 552.8745 | 6.0218 | 91.8126 | 4.731%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 54 | 50 | 704.6091 | 96.62% | 3.132% | 0.2514% | 63.0339 | 0 | 0 | 63.0339 | 0 | 57.36 | 0.665 | 86.2557 | 57.36 | 0.665 | 86.2557 | 63.6534 | 0.73796 | 86.2557 | 8.946%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 25 | 25 | 549.9829 | 98.93% | 0.9134% | 0.161% | 54.4074 | 0 | 0 | 54.4074 | 0 | 49.51 | 0.3325 | 148.9023 | 49.51 | 0.3325 | 148.9023 | 54.9421 | 0.36898 | 148.9023 | 9.893%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 74 | 50 | 474.7376 | 91.31% | 8.325% | 0.3651% | 29.2893 | 0 | 0 | 29.2893 | 0 | 26.6528 | 0.665 | 40.0795 | 26.6528 | 0.665 | 40.0795 | 29.5771 | 0.73796 | 40.0795 | 6.17%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 73 | 26 | 141.3846 | 51% | 48.51% | 0.49% | 2.5682 | 0 | 0 | 2.5682 | 0 | 2.337 | 0.3458 | 6.7584 | 2.337 | 0.3458 | 6.7584 | 2.5935 | 0.38374 | 6.7584 | 1.816%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 122 | 84 | 333.8465 | 96.62% | 2.31% | 1.072% | 22.2086 | 0 | 0 | 22.2086 | 0 | 20.2096 | 1.1172 | 18.0895 | 20.2096 | 1.1172 | 18.0895 | 22.4269 | 1.2398 | 18.0895 | 6.652%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 354 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 292.8867 | 0 | 0 | 292.8867 | 0 | 266.5229 | 4.7082 | 56.6083 | 266.5229 | 4.7082 | 56.6083 | 295.7652 | 5.2248 | 56.6083 | 8.579%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 465 | 363 | 571.2373 | 70.71% | 27.93% | 1.361% | 31.5311 | 0 | 0 | 31.5311 | 0 | 28.6929 | 4.8279 | 5.9431 | 28.6929 | 4.8279 | 5.9431 | 31.841 | 5.3576 | 5.9431 | 5.52%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 275 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 746.4038 | 0 | 0 | 746.4038 | 0 | 679.2172 | 3.6575 | 185.7054 | 679.2172 | 3.6575 | 185.7054 | 753.7394 | 4.0588 | 185.7054 | 7.749%
2027 | 445 | 445-1315 | Tier-2 | Tier-2---19 | Tier-2---11 | 4 | 1 | 26.2494 | 99.59% | 0% | 0.4079% | 0.65356 | 0 | 0 | 0.65356 | 0 | 0.59473 | 0.0133 | 44.7164 | 0.59473 | 0.0133 | 44.7164 | 0.65998 | 0.014759 | 44.7164 | 2.49%
2027 | 445 | 445-1323 | Tier-2 | Tier-2---18 | Tier-2---12 | 6 | 8 | 78.5439 | 99.26% | 0.525% | 0.2138% | 10.3952 | 0 | 0 | 10.3952 | 0 | 9.4594 | 0.1064 | 88.9046 | 9.4594 | 0.1064 | 88.9046 | 10.4973 | 0.11807 | 88.9046 | 13.23%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 197 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 623.982 | 0 | 0 | 623.982 | 0 | 567.8151 | 2.6201 | 216.7151 | 567.8151 | 2.6201 | 216.7151 | 630.1144 | 2.9076 | 216.7151 | 8.606%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 73 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 107.0683 | 0 | 0 | 107.0683 | 0 | 97.4307 | 0.9709 | 100.3509 | 97.4307 | 0.9709 | 100.3509 | 108.1205 | 1.0774 | 100.3509 | 6.677%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 439 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 848.1098 | 0 | 0 | 848.1098 | 0 | 771.7683 | 5.8387 | 132.1816 | 771.7683 | 5.8387 | 132.1816 | 856.4449 | 6.4793 | 132.1816 | 7.986%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 220 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 138.3664 | 0 | 0 | 138.3664 | 0 | 125.9115 | 2.926 | 43.032 | 125.9115 | 2.926 | 43.032 | 139.7262 | 3.247 | 43.032 | 7.832%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 197 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 257.8827 | 0 | 0 | 257.8827 | 0 | 234.6697 | 2.6201 | 89.5652 | 234.6697 | 2.6201 | 89.5652 | 260.4171 | 2.9076 | 89.5652 | 7.01%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 511 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 339.1443 | 0 | 0 | 339.1443 | 0 | 308.6167 | 6.7963 | 45.4095 | 308.6167 | 6.7963 | 45.4095 | 342.4774 | 7.542 | 45.4095 | 7.671%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 25 | 22 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 115.6761 | 0 | 0 | 115.6761 | 0 | 105.2637 | 0.2926 | 359.7531 | 105.2637 | 0.2926 | 359.7531 | 116.813 | 0.3247 | 359.7531 | 8.557%
2027 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 4 | 16.696 | 99.41% | 0% | 0.5907% | 1.6597 | 0 | 0 | 1.6597 | 0 | 1.5103 | 0.0532 | 28.3898 | 1.5103 | 0.0532 | 28.3898 | 1.676 | 0.059037 | 28.3898 | 9.941%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 51 | 45 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 104.1172 | 0 | 0 | 104.1172 | 0 | 94.7452 | 0.5985 | 158.3045 | 94.7452 | 0.5985 | 158.3045 | 105.1404 | 0.66417 | 158.3045 | 8.593%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 184 | 154 | 2612.2711 | 91.91% | 7.885% | 0.2065% | 200.9452 | 0 | 0 | 200.9452 | 0 | 182.8574 | 2.0482 | 89.2772 | 182.8574 | 2.0482 | 89.2772 | 202.9201 | 2.2729 | 89.2772 | 7.692%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 314 | 213 | 2119.752 | 55.7% | 43.96% | 0.3458% | 80.0895 | 0 | 0 | 80.0895 | 0 | 72.8803 | 2.8329 | 25.7264 | 72.8803 | 2.8329 | 25.7264 | 80.8766 | 3.1437 | 25.7264 | 3.778%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 151 | 520.639 | 76.18% | 22.78% | 1.038% | 29.6503 | 0 | 0 | 29.6503 | 0 | 26.9813 | 2.0083 | 13.4349 | 26.9813 | 2.0083 | 13.4349 | 29.9417 | 2.2286 | 13.4349 | 5.695%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 170 | 140 | 630.7627 | 79.12% | 20.09% | 0.7869% | 41.1002 | 0 | 0 | 41.1002 | 0 | 37.4006 | 1.862 | 20.0863 | 37.4006 | 1.862 | 20.0863 | 41.5041 | 2.0663 | 20.0863 | 6.516%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 493 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 573.9427 | 0 | 0 | 573.9427 | 0 | 522.2801 | 6.5569 | 79.6535 | 522.2801 | 6.5569 | 79.6535 | 579.5834 | 7.2763 | 79.6535 | 6.304%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 303 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 386.9071 | 0 | 0 | 386.9071 | 0 | 352.0802 | 4.0299 | 87.367 | 352.0802 | 4.0299 | 87.367 | 390.7096 | 4.472 | 87.367 | 6.854%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 418 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 457.0253 | 0 | 0 | 457.0253 | 0 | 415.8868 | 5.5594 | 74.8079 | 415.8868 | 5.5594 | 74.8079 | 461.5169 | 6.1694 | 74.8079 | 6.791%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 72 | 55 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 110.7812 | 0 | 0 | 110.7812 | 0 | 100.8093 | 0.7315 | 137.8119 | 100.8093 | 0.7315 | 137.8119 | 111.8699 | 0.81176 | 137.8119 | 7.408%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 26 | 26 | 625.3129 | 96.7% | 3.156% | 0.1473% | 60.4656 | 0 | 0 | 60.4656 | 0 | 55.0229 | 0.3458 | 159.1178 | 55.0229 | 0.3458 | 159.1178 | 61.0599 | 0.38374 | 159.1178 | 9.67%
2027 | 441 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 130 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 409.3932 | 0 | 0 | 409.3932 | 0 | 372.5423 | 1.729 | 215.467 | 372.5423 | 1.729 | 215.467 | 413.4167 | 1.9187 | 215.467 | 7.782%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 161 | 123 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 169.3511 | 0 | 0 | 169.3511 | 0 | 154.1072 | 1.6359 | 94.2034 | 154.1072 | 1.6359 | 94.2034 | 171.0155 | 1.8154 | 94.2034 | 7.3%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 15 | 296.7138 | 97.11% | 2.719% | 0.1664% | 24.0127 | 0 | 0 | 24.0127 | 0 | 21.8513 | 0.1995 | 109.5302 | 21.8513 | 0.1995 | 109.5302 | 24.2487 | 0.22139 | 109.5302 | 8.093%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 126 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 494.986 | 0 | 0 | 494.986 | 0 | 450.4305 | 1.6758 | 268.7855 | 450.4305 | 1.6758 | 268.7855 | 499.8507 | 1.8597 | 268.7855 | 5.982%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 22 | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.7456 | 0 | 0 | 36.7456 | 0 | 33.438 | 0.2926 | 114.2789 | 33.438 | 0.2926 | 114.2789 | 37.1067 | 0.3247 | 114.2789 | 4.638%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 41 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 63.1703 | 0 | 0 | 63.1703 | 0 | 57.4841 | 0.5453 | 105.4174 | 57.4841 | 0.5453 | 105.4174 | 63.7911 | 0.60513 | 105.4174 | 5.579%
2027 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 18 | 5 | 537.0702 | 32.53% | 67.41% | 0.0594% | 4.8529 | 0 | 0 | 4.8529 | 0 | 4.4161 | 0.0665 | 66.4076 | 4.4161 | 0.0665 | 66.4076 | 4.9006 | 0.073796 | 66.4076 | 0.9036%
2027 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 5 | 5 | 137.227 | 99.9% | 0% | 0.1049% | 13.7083 | 0 | 0 | 13.7083 | 0 | 12.4744 | 0.0665 | 187.5847 | 12.4744 | 0.0665 | 187.5847 | 13.843 | 0.073796 | 187.5847 | 9.99%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 19 | 625.5425 | 99.9% | 0% | 0.09615% | 59.3694 | 0 | 0 | 59.3694 | 0 | 54.0253 | 0.2527 | 213.7925 | 54.0253 | 0.2527 | 213.7925 | 59.9529 | 0.28043 | 213.7925 | 9.491%
2027 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 10 | 181.2174 | 99.84% | 0% | 0.161% | 15.0771 | 0 | 0 | 15.0771 | 0 | 13.72 | 0.133 | 103.1579 | 13.72 | 0.133 | 103.1579 | 15.2253 | 0.14759 | 103.1579 | 8.32%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 58 | 2823.7515 | 99.93% | 0% | 0.06613% | 230.5201 | 0 | 0 | 230.5201 | 0 | 209.7702 | 0.7714 | 271.9345 | 209.7702 | 0.7714 | 271.9345 | 232.7857 | 0.85604 | 271.9345 | 8.164%
2027 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 2 | 3 | 39.0262 | 97.23% | 2.586% | 0.1833% | 5.6918 | 0 | 0 | 5.6918 | 0 | 5.1795 | 0.0399 | 129.8115 | 5.1795 | 0.0399 | 129.8115 | 5.7478 | 0.044278 | 129.8115 | 14.58%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 53 | 41 | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 265.4015 | 0 | 0 | 265.4015 | 0 | 241.5117 | 0.5453 | 442.8972 | 241.5117 | 0.5453 | 442.8972 | 268.0098 | 0.60513 | 442.8972 | 7.713%
2027 | 454 | 454-49F | Tier-2 | Tier-2---13 | Tier-2---8 | 52 | 1 | 292.9743 | 76.06% | 23.59% | 0.3558% | 0.42851 | 0 | 0 | 0.42851 | 0 | 0.38994 | 0.0133 | 29.3187 | 0.38994 | 0.0133 | 29.3187 | 0.43272 | 0.014759 | 29.3187 | 0.1463%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 11 | 10 | 88.0149 | 97.35% | 2.233% | 0.4157% | 7.7894 | 0 | 0 | 7.7894 | 0 | 7.0883 | 0.133 | 53.2952 | 7.0883 | 0.133 | 53.2952 | 7.866 | 0.14759 | 53.2952 | 8.85%
2027 | 260 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 198 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 116.9805 | 0 | 0 | 116.9805 | 0 | 106.4506 | 2.6334 | 40.4233 | 106.4506 | 2.6334 | 40.4233 | 118.1302 | 2.9223 | 40.4233 | 8.487%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 125 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 455.719 | 0 | 0 | 455.719 | 0 | 414.6981 | 1.6625 | 249.4426 | 414.6981 | 1.6625 | 249.4426 | 460.1978 | 1.8449 | 249.4426 | 8.656%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 475 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 1479.703 | 0 | 0 | 1479.703 | 0 | 1346.5096 | 6.3175 | 213.1397 | 1346.5096 | 6.3175 | 213.1397 | 1494.2454 | 7.0106 | 213.1397 | 8.839%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 128 | 21 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 66.2676 | 0 | 0 | 66.2676 | 0 | 60.3026 | 0.2793 | 215.9064 | 60.3026 | 0.2793 | 215.9064 | 66.9189 | 0.30994 | 215.9064 | 1.558%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 16 | 800.5503 | 21.6% | 78.32% | 0.07823% | 13.8344 | 0 | 0 | 13.8344 | 0 | 12.5891 | 0.2128 | 59.1593 | 12.5891 | 0.2128 | 59.1593 | 13.9703 | 0.23615 | 59.1593 | 1.728%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 23 | 22 | 204.0835 | 99.63% | 0% | 0.368% | 19.4492 | 0 | 0 | 19.4492 | 0 | 17.6985 | 0.2926 | 60.487 | 17.6985 | 0.2926 | 60.487 | 19.6403 | 0.3247 | 60.487 | 9.53%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 154 | 23 | 733.6834 | 99.51% | 0% | 0.4917% | 10.9037 | 0 | 0 | 10.9037 | 0 | 9.9222 | 0.3059 | 32.4363 | 9.9222 | 0.3059 | 32.4363 | 11.0109 | 0.33946 | 32.4363 | 1.486%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 180 | 156 | 2978.814 | 97.34% | 2.471% | 0.184% | 251.3089 | 0 | 0 | 251.3089 | 0 | 228.6876 | 2.0748 | 110.2216 | 228.6876 | 2.0748 | 110.2216 | 253.7787 | 2.3024 | 110.2216 | 8.437%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 155 | 112 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 104.6866 | 0 | 0 | 104.6866 | 0 | 95.2634 | 1.4896 | 63.9524 | 95.2634 | 1.4896 | 63.9524 | 105.7155 | 1.653 | 63.9524 | 7.079%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 408 | 329 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 205.8159 | 0 | 0 | 205.8159 | 0 | 187.2897 | 4.3757 | 42.8022 | 187.2897 | 4.3757 | 42.8022 | 207.8387 | 4.8558 | 42.8022 | 7.802%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 401 | 276 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 217.8673 | 0 | 0 | 217.8673 | 0 | 198.2563 | 3.6708 | 54.009 | 198.2563 | 3.6708 | 54.009 | 220.0085 | 4.0735 | 54.009 | 6.382%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 129 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 142.774 | 0 | 0 | 142.774 | 0 | 129.9224 | 1.7157 | 75.7256 | 129.9224 | 1.7157 | 75.7256 | 144.1772 | 1.9039 | 75.7256 | 8.744%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 249 | 205 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 538.5174 | 0 | 0 | 538.5174 | 0 | 490.0435 | 2.7265 | 179.7336 | 490.0435 | 2.7265 | 179.7336 | 543.8099 | 3.0256 | 179.7336 | 7.963%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 201 | 748.333 | 77.34% | 21.7% | 0.962% | 28.5115 | 0 | 0 | 28.5115 | 0 | 25.9451 | 2.6733 | 9.7053 | 25.9451 | 2.6733 | 9.7053 | 28.7917 | 2.9666 | 9.7053 | 3.81%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 276 | 149 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 108.5766 | 0 | 0 | 108.5766 | 0 | 98.8032 | 1.9817 | 49.8578 | 98.8032 | 1.9817 | 49.8578 | 109.6436 | 2.1991 | 49.8578 | 5.209%
2027 | 520 | 520-1936 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 3 | 63.7111 | 99.77% | 0% | 0.2279% | 4.7674 | 0 | 0 | 4.7674 | 0 | 4.3383 | 0.0399 | 108.7296 | 4.3383 | 0.0399 | 108.7296 | 4.8143 | 0.044278 | 108.7296 | 7.483%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 113 | 54 | 258.296 | 74.72% | 24.53% | 0.7505% | 9.2233 | 0 | 0 | 9.2233 | 0 | 8.3931 | 0.7182 | 11.6863 | 8.3931 | 0.7182 | 11.6863 | 9.314 | 0.797 | 11.6863 | 3.571%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 306 | 275 | 4997.7942 | 96.49% | 3.313% | 0.193% | 433.4028 | 0 | 0 | 433.4028 | 0 | 394.3906 | 3.6575 | 107.8307 | 394.3906 | 3.6575 | 107.8307 | 437.6622 | 4.0588 | 107.8307 | 8.672%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 219 | 176 | 2044.6463 | 97.57% | 2.13% | 0.298% | 160.3287 | 0 | 0 | 160.3287 | 0 | 145.8969 | 2.3408 | 62.3278 | 145.8969 | 2.3408 | 62.3278 | 161.9044 | 2.5976 | 62.3278 | 7.841%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 264 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 919.7864 | 0 | 0 | 919.7864 | 0 | 836.9931 | 3.5112 | 238.3782 | 836.9931 | 3.5112 | 238.3782 | 928.8261 | 3.8964 | 238.3782 | 8.104%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 136 | 810.9996 | 89.31% | 10.24% | 0.4457% | 49.5022 | 0 | 0 | 49.5022 | 0 | 45.0463 | 1.8088 | 24.904 | 45.0463 | 1.8088 | 24.904 | 49.9887 | 2.0073 | 24.904 | 6.104%
2027 | 239 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 276 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 683.0496 | 0 | 0 | 683.0496 | 0 | 621.5658 | 3.6708 | 169.3271 | 621.5658 | 3.6708 | 169.3271 | 689.7625 | 4.0735 | 169.3271 | 8.057%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 264 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 744.4805 | 0 | 0 | 744.4805 | 0 | 677.4671 | 3.5112 | 192.9447 | 677.4671 | 3.5112 | 192.9447 | 751.7972 | 3.8964 | 192.9447 | 8.544%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 247 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 382.9204 | 0 | 0 | 382.9204 | 0 | 348.4523 | 3.2851 | 106.0706 | 348.4523 | 3.2851 | 106.0706 | 386.6837 | 3.6455 | 106.0706 | 6.815%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 232 | 207 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 1085.4723 | 0 | 0 | 1085.4723 | 0 | 987.765 | 2.7531 | 358.783 | 987.765 | 2.7531 | 358.783 | 1096.1403 | 3.0552 | 358.783 | 8.867%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 437 | 328 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 670.0457 | 0 | 0 | 670.0457 | 0 | 609.7325 | 4.3624 | 139.77 | 609.7325 | 4.3624 | 139.77 | 676.6309 | 4.841 | 139.77 | 7.435%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 34 | 112.7117 | 43.02% | 55.81% | 1.165% | 2.5762 | 0 | 0 | 2.5762 | 0 | 2.3443 | 0.4522 | 5.1843 | 2.3443 | 0.4522 | 5.1843 | 2.6015 | 0.50181 | 5.1843 | 2.286%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 42 | 116.9577 | 22.53% | 76.17% | 1.295% | 1.1902 | 0 | 0 | 1.1902 | 0 | 1.0831 | 0.5586 | 1.9389 | 1.0831 | 0.5586 | 1.9389 | 1.2019 | 0.61989 | 1.9389 | 1.018%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 354 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 317.7319 | 0 | 0 | 317.7319 | 0 | 289.1317 | 4.7082 | 61.4103 | 289.1317 | 4.7082 | 61.4103 | 320.8546 | 5.2248 | 61.4103 | 5.634%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 99 | 305.199 | 11.7% | 87.21% | 1.095% | 1.7759 | 0 | 0 | 1.7759 | 0 | 1.6161 | 1.3167 | 1.2273 | 1.6161 | 1.3167 | 1.2273 | 1.7934 | 1.4612 | 1.2273 | 0.5819%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 231 | 173 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 408.5997 | 0 | 0 | 408.5997 | 0 | 371.8201 | 2.3009 | 161.5978 | 371.8201 | 2.3009 | 161.5978 | 412.6154 | 2.5533 | 161.5978 | 7.472%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 489 | 289 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 667.3334 | 0 | 0 | 667.3334 | 0 | 607.2643 | 3.8437 | 157.9896 | 607.2643 | 3.8437 | 157.9896 | 673.8919 | 4.2654 | 157.9896 | 5.896%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 283 | 223 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 1069.4603 | 0 | 0 | 1069.4603 | 0 | 973.1943 | 2.9659 | 328.128 | 973.1943 | 2.9659 | 328.128 | 1079.9709 | 3.2913 | 328.128 | 7.8%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 204 | 8801.877 | 98.2% | 1.718% | 0.0819% | 623.0646 | 0 | 0 | 623.0646 | 0 | 566.9803 | 2.7132 | 208.9712 | 566.9803 | 2.7132 | 208.9712 | 629.1881 | 3.0109 | 208.9712 | 7.079%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 842 | 634 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 3010.7489 | 0 | 0 | 3010.7489 | 0 | 2739.7405 | 8.4322 | 324.9142 | 2739.7405 | 8.4322 | 324.9142 | 3040.3384 | 9.3574 | 324.9142 | 7.457%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 18 | 18 | 833.6308 | 67.75% | 32.17% | 0.07637% | 56.479 | 0 | 0 | 56.479 | 0 | 51.3951 | 0.2394 | 214.6831 | 51.3951 | 0.2394 | 214.6831 | 57.0341 | 0.26567 | 214.6831 | 6.775%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 92 | 11 | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.9884 | 0 | 0 | 5.9884 | 0 | 5.4494 | 0.1463 | 37.2479 | 5.4494 | 0.1463 | 37.2479 | 6.0473 | 0.16235 | 37.2479 | 1.152%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 9 | 9 | 49.4293 | 99.41% | 0% | 0.5897% | 4.9138 | 0 | 0 | 4.9138 | 0 | 4.4715 | 0.1197 | 37.3557 | 4.4715 | 0.1197 | 37.3557 | 4.9621 | 0.13283 | 37.3557 | 9.941%
2027 | 1118 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 360 | 18774.394 | 95.55% | 4.388% | 0.06321% | 1622.6031 | 0 | 0 | 1622.6031 | 0 | 1476.5467 | 4.788 | 308.385 | 1476.5467 | 4.788 | 308.385 | 1638.55 | 5.3133 | 308.385 | 8.643%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 631 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 2144.2272 | 0 | 0 | 2144.2272 | 0 | 1951.2176 | 8.3923 | 232.501 | 1951.2176 | 8.3923 | 232.501 | 2165.3006 | 9.3131 | 232.501 | 8.329%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 344 | 278 | 2610.8 | 93.6% | 6.065% | 0.3401% | 197.4758 | 0 | 0 | 197.4758 | 0 | 179.7003 | 3.6974 | 48.6018 | 179.7003 | 3.6974 | 48.6018 | 199.4166 | 4.1031 | 48.6018 | 7.564%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 551 | 445 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 316.6756 | 0 | 0 | 316.6756 | 0 | 288.1704 | 5.9185 | 48.6898 | 288.1704 | 5.9185 | 48.6898 | 319.7878 | 6.5679 | 48.6898 | 7.576%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 159 | 622.3042 | 87.18% | 11.98% | 0.8373% | 45.4006 | 0 | 0 | 45.4006 | 0 | 41.314 | 2.1147 | 19.5366 | 41.314 | 2.1147 | 19.5366 | 45.8468 | 2.3467 | 19.5366 | 7.296%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 198 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 128.3604 | 0 | 0 | 128.3604 | 0 | 116.8062 | 2.6334 | 44.3557 | 116.8062 | 2.6334 | 44.3557 | 129.6219 | 2.9223 | 44.3557 | 7.885%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 310 | 229 | 6201.607 | 97.29% | 2.601% | 0.1104% | 445.698 | 0 | 0 | 445.698 | 0 | 405.5791 | 3.0457 | 133.1645 | 405.5791 | 3.0457 | 133.1645 | 450.0783 | 3.3799 | 133.1645 | 7.187%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 242 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 1122.1435 | 0 | 0 | 1122.1435 | 0 | 1021.1353 | 3.2186 | 317.2609 | 1021.1353 | 3.2186 | 317.2609 | 1133.1719 | 3.5717 | 317.2609 | 7.316%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 46 | 34 | 2448.8293 | 98.64% | 1.317% | 0.04316% | 178.5379 | 0 | 0 | 178.5379 | 0 | 162.4671 | 0.4522 | 359.2817 | 162.4671 | 0.4522 | 359.2817 | 180.2926 | 0.50181 | 359.2817 | 7.291%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 188 | 158 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 474.2097 | 0 | 0 | 474.2097 | 0 | 431.5244 | 2.1014 | 205.351 | 431.5244 | 2.1014 | 205.351 | 478.8702 | 2.332 | 205.351 | 8.27%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 313 | 270 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 898.1963 | 0 | 0 | 898.1963 | 0 | 817.3464 | 3.591 | 227.6098 | 817.3464 | 3.591 | 227.6098 | 907.0238 | 3.985 | 227.6098 | 8.48%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 273 | 226 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 756.8138 | 0 | 0 | 756.8138 | 0 | 688.6903 | 3.0058 | 229.1206 | 688.6903 | 3.0058 | 229.1206 | 764.2518 | 3.3356 | 229.1206 | 8.148%
2027 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 4 | 17.7969 | 99.34% | 0% | 0.6614% | 1.7679 | 0 | 0 | 1.7679 | 0 | 1.6088 | 0.0532 | 30.2403 | 1.6088 | 0.0532 | 30.2403 | 1.7853 | 0.059037 | 30.2403 | 9.934%
2027 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 4 | 3 | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0399 | 0 | 0 | 0.0399 | 0 | 0 | 0.044278 | 0 | 0%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 102 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 227.9168 | 0 | 0 | 227.9168 | 0 | 207.4012 | 1.3566 | 152.8832 | 207.4012 | 1.3566 | 152.8832 | 230.1568 | 1.5054 | 152.8832 | 7.269%
2027 | 75 | 75-2260F | Tier-3 | missing | missing | 2 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0133 | 0 | 0 | 0.0133 | 0 | 0 | 0.014759 | 0 | 0%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 65 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 131.6342 | 0 | 0 | 131.6342 | 0 | 119.7853 | 0.8645 | 138.5603 | 119.7853 | 0.8645 | 138.5603 | 132.9279 | 0.95935 | 138.5603 | 7.705%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 69 | 58 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 162.6382 | 0 | 0 | 162.6382 | 0 | 147.9986 | 0.7714 | 191.8572 | 147.9986 | 0.7714 | 191.8572 | 164.2366 | 0.85604 | 191.8572 | 8.394%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 241 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 165.7574 | 0 | 0 | 165.7574 | 0 | 150.8369 | 3.2053 | 47.0586 | 150.8369 | 3.2053 | 47.0586 | 167.3864 | 3.557 | 47.0586 | 7.496%
2027 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 24 | 21 | 42.5113 | 97.49% | 0.5175% | 1.991% | 3.6264 | 0 | 0 | 3.6264 | 0 | 3.3 | 0.2793 | 11.8153 | 3.3 | 0.2793 | 11.8153 | 3.6621 | 0.30994 | 11.8153 | 8.531%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 186 | 143 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 1100.7243 | 0 | 0 | 1100.7243 | 0 | 1001.6441 | 1.9019 | 526.6547 | 1001.6441 | 1.9019 | 526.6547 | 1111.5422 | 2.1106 | 526.6547 | 7.577%
2027 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 29 | 29 | 5696.3358 | 99.98% | 0% | 0.01771% | 569.5327 | 0 | 0 | 569.5327 | 0 | 518.267 | 0.3857 | 1343.7055 | 518.267 | 0.3857 | 1343.7055 | 575.13 | 0.42802 | 1343.7055 | 9.998%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 33 | 32 | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 695.0009 | 0 | 0 | 695.0009 | 0 | 632.4413 | 0.4256 | 1486 | 632.4413 | 0.4256 | 1486 | 701.8313 | 0.4723 | 1486 | 9.65%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 143 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 236.4489 | 0 | 0 | 236.4489 | 0 | 215.1653 | 1.9019 | 113.1318 | 215.1653 | 1.9019 | 113.1318 | 238.7727 | 2.1106 | 113.1318 | 2.589%
2027 | 73 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 9 | 5 | 324.1263 | 99.58% | 0.3619% | 0.05404% | 17.9321 | 0 | 0 | 17.9321 | 0 | 16.318 | 0.0665 | 245.3833 | 16.318 | 0.0665 | 245.3833 | 18.1084 | 0.073796 | 245.3833 | 5.532%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 48 | 3349.7594 | 92.58% | 7.304% | 0.116% | 105.5733 | 0 | 0 | 105.5733 | 0 | 96.0703 | 0.6384 | 150.4861 | 96.0703 | 0.6384 | 150.4861 | 106.6109 | 0.70844 | 150.4861 | 3.152%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 198 | 185 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 1142.7385 | 0 | 0 | 1142.7385 | 0 | 1039.8765 | 2.4605 | 422.6283 | 1039.8765 | 2.4605 | 422.6283 | 1153.9693 | 2.7305 | 422.6283 | 9.275%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 159 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 180.6886 | 0 | 0 | 180.6886 | 0 | 164.4242 | 2.1147 | 77.753 | 164.4242 | 2.1147 | 77.753 | 182.4644 | 2.3467 | 77.753 | 8.658%
2027 | 222 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 206 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 75.9811 | 0 | 0 | 75.9811 | 0 | 69.1418 | 2.7398 | 25.2361 | 69.1418 | 2.7398 | 25.2361 | 76.7278 | 3.0404 | 25.2361 | 4.728%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 80 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 553.4853 | 0 | 0 | 553.4853 | 0 | 503.6641 | 1.064 | 473.3687 | 503.6641 | 1.064 | 473.3687 | 558.925 | 1.1807 | 473.3687 | 5.698%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 192 | 130 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 1235.3475 | 0 | 0 | 1235.3475 | 0 | 1124.1494 | 1.729 | 650.1734 | 1124.1494 | 1.729 | 650.1734 | 1247.4884 | 1.9187 | 650.1734 | 6.696%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 74 | 65 | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 223.8726 | 0 | 0 | 223.8726 | 0 | 203.721 | 0.8645 | 235.6519 | 203.721 | 0.8645 | 235.6519 | 226.0728 | 0.95935 | 235.6519 | 8.729%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 180 | 106 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 314.028 | 0 | 0 | 314.028 | 0 | 285.7612 | 1.4098 | 202.6964 | 285.7612 | 1.4098 | 202.6964 | 317.1142 | 1.5645 | 202.6964 | 5.672%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 238 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 1016.9059 | 0 | 0 | 1016.9059 | 0 | 925.3705 | 3.1654 | 292.3393 | 925.3705 | 3.1654 | 292.3393 | 1026.9 | 3.5127 | 292.3393 | 5.415%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 116 | 110 | 3034.8235 | 97.12% | 2.752% | 0.1275% | 279.4979 | 0 | 0 | 279.4979 | 0 | 254.3393 | 1.463 | 173.8479 | 254.3393 | 1.463 | 173.8479 | 282.2448 | 1.6235 | 173.8479 | 9.21%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 218 | 192 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 1746.0262 | 0 | 0 | 1746.0262 | 0 | 1588.8601 | 2.5536 | 622.2043 | 1588.8601 | 2.5536 | 622.2043 | 1763.1861 | 2.8338 | 622.2043 | 8.74%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 11 | 127.4062 | 99.28% | 0% | 0.716% | 3.6617 | 0 | 0 | 3.6617 | 0 | 3.3321 | 0.1463 | 22.7756 | 3.3321 | 0.1463 | 22.7756 | 3.6977 | 0.16235 | 22.7756 | 2.874%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 6 | 12.4137 | 98.83% | 0% | 1.166% | 0.56626 | 0 | 0 | 0.56626 | 0 | 0.51529 | 0.0798 | 6.4573 | 0.51529 | 0.0798 | 6.4573 | 0.57183 | 0.088555 | 6.4573 | 4.562%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 17 | 17 | 139.955 | 99.63% | 0% | 0.3714% | 13.9435 | 0 | 0 | 13.9435 | 0 | 12.6884 | 0.2261 | 56.1186 | 12.6884 | 0.2261 | 56.1186 | 14.0806 | 0.25091 | 56.1186 | 9.963%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 3 | 6.7153 | 99.02% | 0% | 0.9775% | 0.66497 | 0 | 0 | 0.66497 | 0 | 0.60511 | 0.0399 | 15.1657 | 0.60511 | 0.0399 | 15.1657 | 0.6715 | 0.044278 | 15.1657 | 9.902%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 16 | 16 | 330.3488 | 99.39% | 0.4551% | 0.1546% | 32.8335 | 0 | 0 | 32.8335 | 0 | 29.878 | 0.2128 | 140.4043 | 29.878 | 0.2128 | 140.4043 | 33.1562 | 0.23615 | 140.4043 | 9.939%
2027 | 260 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 40 | 36 | 232.5563 | 96.66% | 2.796% | 0.5416% | 20.2316 | 0 | 0 | 20.2316 | 0 | 18.4105 | 0.4788 | 38.4513 | 18.4105 | 0.4788 | 38.4513 | 20.4304 | 0.53133 | 38.4513 | 8.7%
2027 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 7 | 7 | 188.5529 | 99.88% | 0% | 0.1171% | 18.8332 | 0 | 0 | 18.8332 | 0 | 17.138 | 0.0931 | 184.0813 | 17.138 | 0.0931 | 184.0813 | 19.0183 | 0.10331 | 184.0813 | 9.988%
2027 | 599 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 159 | 8606.9717 | 99.86% | 0% | 0.1411% | 245.346 | 0 | 0 | 245.346 | 0 | 223.2615 | 2.1147 | 105.576 | 223.2615 | 2.1147 | 105.576 | 247.7573 | 2.3467 | 105.576 | 2.851%
2027 | 907 | 907-1475 | Tier-3 | Tier-3---21 | Tier-3---21 | 4 | 4 | 4.2814 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0532 | 0 | 0 | 0.0532 | 0 | 0 | 0.059037 | 0 | 0%
2027 | 1021 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 162 | 123 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 625.5206 | 0 | 0 | 625.5206 | 0 | 569.2152 | 1.6359 | 347.9525 | 569.2152 | 1.6359 | 347.9525 | 631.6682 | 1.8154 | 347.9525 | 7.412%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 5 | 5 | 257.2419 | 98.67% | 1.294% | 0.04048% | 25.3809 | 0 | 0 | 25.3809 | 0 | 23.0963 | 0.0665 | 347.3126 | 23.0963 | 0.0665 | 347.3126 | 25.6303 | 0.073796 | 347.3126 | 9.867%
2027 | 907 | 907-1604 | Tier-3 | Tier-3---19 | Tier-3---16 | 2 | 4 | 17.8439 | 83.33% | 16.48% | 0.1969% | 2.9738 | 0 | 0 | 2.9738 | 0 | 2.7061 | 0.0532 | 50.8662 | 2.7061 | 0.0532 | 50.8662 | 3.003 | 0.059037 | 50.8662 | 16.67%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 117 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 717.4672 | 0 | 0 | 717.4672 | 0 | 652.8854 | 1.5561 | 419.5654 | 652.8854 | 1.5561 | 419.5654 | 724.5185 | 1.7268 | 419.5654 | 7.884%
2027 | 1021 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 278 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1923.6578 | 0 | 0 | 1923.6578 | 0 | 1750.5024 | 3.6974 | 473.4417 | 1750.5024 | 3.6974 | 473.4417 | 1942.5634 | 4.1031 | 473.4417 | 7.107%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 33 | 29 | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 557.7619 | 0 | 0 | 557.7619 | 0 | 507.5557 | 0.3857 | 1315.9345 | 507.5557 | 0.3857 | 1315.9345 | 563.2435 | 0.42802 | 1315.9345 | 8.786%
2027 | 350 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 240 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 1227.927 | 0 | 0 | 1227.927 | 0 | 1117.3968 | 3.192 | 350.0618 | 1117.3968 | 3.192 | 350.0618 | 1239.995 | 3.5422 | 350.0618 | 7.788%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 130 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 910.2348 | 0 | 0 | 910.2348 | 0 | 828.3013 | 1.729 | 479.064 | 828.3013 | 1.729 | 479.064 | 919.1805 | 1.9187 | 479.064 | 7.738%
2027 | 350 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 471 | 386 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 439.4181 | 0 | 0 | 439.4181 | 0 | 399.8645 | 5.1338 | 77.8886 | 399.8645 | 5.1338 | 77.8886 | 443.7366 | 5.6971 | 77.8886 | 7.888%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 131 | 1466.2762 | 91.81% | 7.905% | 0.289% | 117.5619 | 0 | 0 | 117.5619 | 0 | 106.9798 | 1.7423 | 61.4015 | 106.9798 | 1.7423 | 61.4015 | 118.7173 | 1.9335 | 61.4015 | 8.018%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 89 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 566.4697 | 0 | 0 | 566.4697 | 0 | 515.4797 | 1.1837 | 435.4819 | 515.4797 | 1.1837 | 435.4819 | 572.0369 | 1.3136 | 435.4819 | 7.116%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 423 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 3155.1751 | 0 | 0 | 3155.1751 | 0 | 2871.1663 | 5.6259 | 510.3481 | 2871.1663 | 5.6259 | 510.3481 | 3186.184 | 6.2432 | 510.3481 | 7.647%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 162 | 124 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 256.5556 | 0 | 0 | 256.5556 | 0 | 233.4621 | 1.6492 | 141.5609 | 233.4621 | 1.6492 | 141.5609 | 259.077 | 1.8301 | 141.5609 | 7.035%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 282 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1736.8596 | 0 | 0 | 1736.8596 | 0 | 1580.5186 | 3.7506 | 421.4044 | 1580.5186 | 3.7506 | 421.4044 | 1753.9294 | 4.1621 | 421.4044 | 7.697%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 7 | 5 | 153.3115 | 98.58% | 1.358% | 0.06577% | 10.7949 | 0 | 0 | 10.7949 | 0 | 9.8233 | 0.0665 | 147.7182 | 9.8233 | 0.0665 | 147.7182 | 10.901 | 0.073796 | 147.7182 | 7.041%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 40 | 847.524 | 96.52% | 3.329% | 0.1488% | 62.9267 | 0 | 0 | 62.9267 | 0 | 57.2624 | 0.532 | 107.6362 | 57.2624 | 0.532 | 107.6362 | 63.5451 | 0.59037 | 107.6362 | 7.425%
2027 | 216 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 419 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 4541.9905 | 0 | 0 | 4541.9905 | 0 | 4133.1495 | 5.5727 | 741.6784 | 4133.1495 | 5.5727 | 741.6784 | 4586.629 | 6.1841 | 741.6784 | 8.22%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 24 | 5703.0403 | 99.97% | 0% | 0.03309% | 220.6898 | 0 | 0 | 220.6898 | 0 | 200.8247 | 0.3192 | 629.1504 | 200.8247 | 0.3192 | 629.1504 | 222.8587 | 0.35422 | 629.1504 | 3.87%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 271 | 32313.161 | 99.26% | 0.708% | 0.02831% | 2813.0723 | 0 | 0 | 2813.0723 | 0 | 2559.8575 | 3.6043 | 710.2235 | 2559.8575 | 3.6043 | 710.2235 | 2840.7191 | 3.9998 | 710.2235 | 8.706%
2027 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 3 | 3 | 62.9838 | 99.88% | 0% | 0.1185% | 6.2909 | 0 | 0 | 6.2909 | 0 | 5.7247 | 0.0399 | 143.4751 | 5.7247 | 0.0399 | 143.4751 | 6.3527 | 0.044278 | 143.4751 | 9.988%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 194 | 106 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 67.9648 | 0 | 0 | 67.9648 | 0 | 61.847 | 1.4098 | 43.8694 | 61.847 | 1.4098 | 43.8694 | 68.6327 | 1.5645 | 43.8694 | 5.244%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 111 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 286.7483 | 0 | 0 | 286.7483 | 0 | 260.9371 | 1.4763 | 176.7508 | 260.9371 | 1.4763 | 176.7508 | 289.5665 | 1.6383 | 176.7508 | 8.417%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 35 | 1554.328 | 69.02% | 30.62% | 0.3611% | 12.7284 | 0 | 0 | 12.7284 | 0 | 11.5826 | 0.4655 | 24.8822 | 11.5826 | 0.4655 | 24.8822 | 12.8535 | 0.51657 | 24.8822 | 0.8189%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 252 | 24 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 14.5312 | 0 | 0 | 14.5312 | 0 | 13.2232 | 0.3192 | 41.426 | 13.2232 | 0.3192 | 41.426 | 14.674 | 0.35422 | 41.426 | 0.7296%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 36 | 33 | 434.8834 | 99.47% | 0.2691% | 0.2608% | 39.6531 | 0 | 0 | 39.6531 | 0 | 36.0838 | 0.4389 | 82.2141 | 36.0838 | 0.4389 | 82.2141 | 40.0428 | 0.48705 | 82.2141 | 9.118%
2027 | 770 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 33 | 62.492 | 96.91% | 0.773% | 2.32% | 4.542 | 0 | 0 | 4.542 | 0 | 4.1331 | 0.4389 | 9.417 | 4.1331 | 0.4389 | 9.417 | 4.5866 | 0.48705 | 9.417 | 7.268%
2027 | 237 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 64 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 898.5928 | 0 | 0 | 898.5928 | 0 | 817.7072 | 0.8512 | 960.6527 | 817.7072 | 0.8512 | 960.6527 | 907.4242 | 0.94459 | 960.6527 | 6.933%
2027 | 176 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 260 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 1134.1213 | 0 | 0 | 1134.1213 | 0 | 1032.0349 | 3.458 | 298.4486 | 1032.0349 | 3.458 | 298.4486 | 1145.2674 | 3.8374 | 298.4486 | 7.487%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 478 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 2255.871 | 0 | 0 | 2255.871 | 0 | 2052.8119 | 6.3574 | 322.9013 | 2052.8119 | 6.3574 | 322.9013 | 2278.0416 | 7.0549 | 322.9013 | 7.92%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 106 | 88 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 661.8693 | 0 | 0 | 661.8693 | 0 | 602.292 | 1.1704 | 514.6038 | 602.292 | 1.1704 | 514.6038 | 668.3741 | 1.2988 | 514.6038 | 8.257%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 50 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 373.3143 | 0 | 0 | 373.3143 | 0 | 339.7109 | 0.665 | 510.8438 | 339.7109 | 0.665 | 510.8438 | 376.9832 | 0.73796 | 510.8438 | 8.579%
2027 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 3 | 191.8954 | 99.94% | 0% | 0.06293% | 28.7662 | 0 | 0 | 28.7662 | 0 | 26.1768 | 0.0399 | 656.0617 | 26.1768 | 0.0399 | 656.0617 | 29.0489 | 0.044278 | 656.0617 | 14.99%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 212 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 1096.8917 | 0 | 0 | 1096.8917 | 0 | 998.1565 | 2.8196 | 354.0066 | 998.1565 | 2.8196 | 354.0066 | 1107.6719 | 3.129 | 354.0066 | 7.426%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 406 | 346 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 950.4557 | 0 | 0 | 950.4557 | 0 | 864.9017 | 4.6018 | 187.9486 | 864.9017 | 4.6018 | 187.9486 | 959.7967 | 5.1067 | 187.9486 | 8.435%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 213 | 190 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 704.8442 | 0 | 0 | 704.8442 | 0 | 641.3986 | 2.527 | 253.8183 | 641.3986 | 2.527 | 253.8183 | 711.7714 | 2.8043 | 253.8183 | 8.789%
2027 | 235 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 474 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1566.3686 | 0 | 0 | 1566.3686 | 0 | 1425.374 | 6.3042 | 226.0992 | 1425.374 | 6.3042 | 226.0992 | 1581.7627 | 6.9959 | 226.0992 | 6.691%
2027 | 972 | 972-1641 | Tier-2 | Tier-2---13 | Tier-2---5 | 3 | 3 | 295.0839 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0399 | 0 | 0 | 0.0399 | 0 | 0 | 0.044278 | 0 | 0%
2027 | 972 | 972-1642 | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 9 | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.1197 | 0 | 0 | 0.1197 | 0 | 0 | 0.13283 | 0 | 0%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 543 | 384 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1579.5972 | 0 | 0 | 1579.5972 | 0 | 1437.4119 | 5.1072 | 281.4483 | 1437.4119 | 5.1072 | 281.4483 | 1595.1214 | 5.6675 | 281.4483 | 6.893%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 189 | 155 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 743.7408 | 0 | 0 | 743.7408 | 0 | 676.794 | 2.0615 | 328.3019 | 676.794 | 2.0615 | 328.3019 | 751.0502 | 2.2877 | 328.3019 | 8.129%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 161 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 418.2068 | 0 | 0 | 418.2068 | 0 | 380.5625 | 2.1413 | 177.725 | 380.5625 | 2.1413 | 177.725 | 422.3169 | 2.3762 | 177.725 | 8.077%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 53 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 770.7303 | 0 | 0 | 770.7303 | 0 | 701.354 | 0.7049 | 994.97 | 701.354 | 0.7049 | 994.97 | 778.305 | 0.78224 | 994.97 | 8.941%
2027 | 973 | 973-530AE | Tier-3 | Tier-3---17 | Tier-3---5 | 2 | 2 | 388.0062 | 6.476% | 93.52% | 0.007746% | 2.5128 | 0 | 0 | 2.5128 | 0 | 2.2866 | 0.0266 | 85.9627 | 2.2866 | 0.0266 | 85.9627 | 2.5375 | 0.029518 | 85.9627 | 0.6476%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 199 | 197 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 632.9032 | 0 | 0 | 632.9032 | 0 | 575.9333 | 2.6201 | 219.8136 | 575.9333 | 2.6201 | 219.8136 | 639.1233 | 2.9076 | 219.8136 | 9.705%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 389 | 305 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 256.5895 | 0 | 0 | 256.5895 | 0 | 233.4929 | 4.0565 | 57.5602 | 233.4929 | 4.0565 | 57.5602 | 259.1112 | 4.5016 | 57.5602 | 7.346%
2027 | 973 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 111 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 586.0659 | 0 | 0 | 586.0659 | 0 | 533.312 | 1.4763 | 361.2492 | 533.312 | 1.4763 | 361.2492 | 591.8257 | 1.6383 | 361.2492 | 8.246%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 30 | 13 | 6417.0381 | 80.3% | 19.69% | 0.01691% | 223.2839 | 0 | 0 | 223.2839 | 0 | 203.1853 | 0.1729 | 1175.1612 | 203.1853 | 0.1729 | 1175.1612 | 225.4783 | 0.19187 | 1175.1612 | 3.48%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 29 | 626.8618 | 65.87% | 33.98% | 0.153% | 41.2906 | 0 | 0 | 41.2906 | 0 | 37.5739 | 0.3857 | 97.4174 | 37.5739 | 0.3857 | 97.4174 | 41.6964 | 0.42802 | 97.4174 | 6.587%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 158 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 439.9608 | 0 | 0 | 439.9608 | 0 | 400.3583 | 2.1014 | 190.5199 | 400.3583 | 2.1014 | 190.5199 | 444.2847 | 2.332 | 190.5199 | 9.613%
2027 | 354 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 55 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 234.5584 | 0 | 0 | 234.5584 | 0 | 213.445 | 0.7315 | 291.7909 | 213.445 | 0.7315 | 291.7909 | 236.8637 | 0.81176 | 291.7909 | 7.038%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 111 | 85 | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 107.9078 | 0 | 0 | 107.9078 | 0 | 98.1947 | 1.1305 | 86.8595 | 98.1947 | 1.1305 | 86.8595 | 108.9683 | 1.2545 | 86.8595 | 7.629%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 38 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 104.7414 | 0 | 0 | 104.7414 | 0 | 95.3133 | 0.5054 | 188.5898 | 95.3133 | 0.5054 | 188.5898 | 105.7708 | 0.56085 | 188.5898 | 9.242%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 24 | 1646.9837 | 34.54% | 65.41% | 0.04829% | 56.8815 | 0 | 0 | 56.8815 | 0 | 51.7614 | 0.3192 | 162.1598 | 51.7614 | 0.3192 | 162.1598 | 57.4405 | 0.35422 | 162.1598 | 3.454%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 70 | 765.4961 | 75% | 24.28% | 0.7274% | 13.8097 | 0 | 0 | 13.8097 | 0 | 12.5666 | 0.931 | 13.498 | 12.5666 | 0.931 | 13.498 | 13.9454 | 1.0331 | 13.498 | 1.804%
2027 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | Tier-2---20 | 8 | 1 | 2.3826 | 9.042% | 83.57% | 7.391% | 0.0026929 | 0 | 0 | 0.0026929 | 0 | 0.0024505 | 0.0133 | 0.18425 | 0.0024505 | 0.0133 | 0.18425 | 0.0027194 | 0.014759 | 0.18425 | 0.113%
2027 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | Tier-2---20 | 20 | 3 | 18.2465 | 16.87% | 78.76% | 4.376% | 0.046159 | 0 | 0 | 0.046159 | 0 | 0.042004 | 0.0399 | 1.0527 | 0.042004 | 0.0399 | 1.0527 | 0.046613 | 0.044278 | 1.0527 | 0.253%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 34 | 31 | 75.2008 | 96.65% | 1.975% | 1.378% | 6.6266 | 0 | 0 | 6.6266 | 0 | 6.0301 | 0.4123 | 14.6256 | 6.0301 | 0.4123 | 14.6256 | 6.6918 | 0.45754 | 14.6256 | 8.812%
2027 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 4 | 70.8201 | 99.8% | 0% | 0.2033% | 5.6541 | 0 | 0 | 5.6541 | 0 | 5.1451 | 0.0532 | 96.7133 | 5.1451 | 0.0532 | 96.7133 | 5.7097 | 0.059037 | 96.7133 | 7.984%
2027 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 3 | 21.8223 | 99.66% | 0% | 0.344% | 2.1747 | 0 | 0 | 2.1747 | 0 | 1.979 | 0.0399 | 49.5983 | 1.979 | 0.0399 | 49.5983 | 2.1961 | 0.044278 | 49.5983 | 9.966%
2027 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | Tier-3---17 | 3 | 2 | 0.76155 | 90.92% | 0% | 9.083% | 0.046158 | 0 | 0 | 0.046158 | 0 | 0.042003 | 0.0266 | 1.5791 | 0.042003 | 0.0266 | 1.5791 | 0.046612 | 0.029518 | 1.5791 | 6.061%
2027 | 239 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 332 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 735.9108 | 0 | 0 | 735.9108 | 0 | 669.6688 | 4.4156 | 151.6598 | 669.6688 | 4.4156 | 151.6598 | 743.1433 | 4.9001 | 151.6598 | 11.66%
2027 | 230 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 402 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 425.6045 | 0 | 0 | 425.6045 | 0 | 387.2943 | 5.3466 | 72.4375 | 387.2943 | 5.3466 | 72.4375 | 429.7873 | 5.9332 | 72.4375 | 6.404%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 106 | 1438.3629 | 99.75% | 0% | 0.2509% | 131.1068 | 0 | 0 | 131.1068 | 0 | 119.3054 | 1.4098 | 84.6258 | 119.3054 | 1.4098 | 84.6258 | 132.3953 | 1.5645 | 84.6258 | 9.115%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 9 | 9 | 108.0997 | 99.75% | 0% | 0.2497% | 10.783 | 0 | 0 | 10.783 | 0 | 9.8124 | 0.1197 | 81.9747 | 9.8124 | 0.1197 | 81.9747 | 10.889 | 0.13283 | 81.9747 | 9.975%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 32 | 31 | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 394.5296 | 0 | 0 | 394.5296 | 0 | 359.0166 | 0.4123 | 870.7658 | 359.0166 | 0.4123 | 870.7658 | 398.407 | 0.45754 | 870.7658 | 9.681%
2027 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 31 | 41.7756 | 94.08% | 0% | 5.924% | 1.6031 | 0 | 0 | 1.6031 | 0 | 1.4588 | 0.4123 | 3.5381 | 1.4588 | 0.4123 | 3.5381 | 1.6188 | 0.45754 | 3.5381 | 3.837%
2027 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 184 | 8 | 259.6903 | 35.49% | 63.12% | 1.387% | 0.40074 | 0 | 0 | 0.40074 | 0 | 0.36467 | 0.1064 | 3.4273 | 0.36467 | 0.1064 | 3.4273 | 0.40468 | 0.11807 | 3.4273 | 0.1543%
2027 | 157 | CB 157 | Tier-3 | Tier-3---21 | Tier-3---11 | 2 | 2 | 6.0775 | 99.43% | 0% | 0.5677% | 0.6043 | 0 | 0 | 0.6043 | 0 | 0.5499 | 0.0266 | 20.673 | 0.5499 | 0.0266 | 20.673 | 0.61023 | 0.029518 | 20.673 | 9.943%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 154 | 2 | 396.8506 | 79.93% | 19.29% | 0.7702% | 0.41198 | 0 | 0 | 0.41198 | 0 | 0.37489 | 0.0266 | 14.0937 | 0.37489 | 0.0266 | 14.0937 | 0.41603 | 0.029518 | 14.0937 | 0.1038%
2027 | 197 | CB 196 | Tier-2 | Tier-2---15 | Tier-2---9 | 24 | 1 | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.017605 | 0 | 0 | 0.017605 | 0 | 0.01602 | 0.0133 | 1.2045 | 0.01602 | 0.0133 | 1.2045 | 0.017778 | 0.014759 | 1.2045 | 0.01309%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 478 | 80 | 1342.6559 | 29.9% | 69.37% | 0.7369% | 6.718 | 0 | 0 | 6.718 | 0 | 6.1133 | 1.064 | 5.7456 | 6.1133 | 1.064 | 5.7456 | 6.784 | 1.1807 | 5.7456 | 0.5004%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 188 | 133.9861 | 95.12% | 0% | 4.877% | 12.415 | 0 | 0 | 12.415 | 0 | 11.2974 | 2.5004 | 4.5183 | 11.2974 | 2.5004 | 4.5183 | 12.537 | 2.7747 | 4.5183 | 9.266%
2027 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 233 | 109 | 195.752 | 9.583% | 88.23% | 2.187% | 0.8776 | 0 | 0 | 0.8776 | 0 | 0.7986 | 1.4497 | 0.55087 | 0.7986 | 1.4497 | 0.55087 | 0.88622 | 1.6088 | 0.55087 | 0.4483%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 229 | 220 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 82.2684 | 0 | 0 | 82.2684 | 0 | 74.8631 | 2.926 | 25.5855 | 74.8631 | 2.926 | 25.5855 | 83.0769 | 3.247 | 25.5855 | 7.765%
2027 | 210 | CB 210 | Tier-2 | Tier-2---21 | Tier-2---17 | 3 | 1 | 1.9532 | 96.21% | 0% | 3.789% | 0.062638 | 0 | 0 | 0.062638 | 0 | 0.057 | 0.0133 | 4.2857 | 0.057 | 0.0133 | 4.2857 | 0.063254 | 0.014759 | 4.2857 | 3.207%
2027 | 211 | CB 211 | Tier-2 | Tier-2---21 | Tier-2---24 | 2 | 1 | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0133 | 0 | 0 | 0.0133 | 0 | 0 | 0.014759 | 0 | 0%
2027 | 212 | CB 212 | Tier-2 | Tier-2---19 | Tier-2---11 | 7 | 6 | 22.9809 | 99.09% | 0% | 0.9069% | 1.9519 | 0 | 0 | 1.9519 | 0 | 1.7762 | 0.0798 | 22.2585 | 1.7762 | 0.0798 | 22.2585 | 1.9711 | 0.088555 | 22.2585 | 8.494%
2027 | 214 | CB 214 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 59.1996 | 99.88% | 0% | 0.1188% | 3.942 | 0 | 0 | 3.942 | 0 | 3.5871 | 0.0266 | 134.8543 | 3.5871 | 0.0266 | 134.8543 | 3.9807 | 0.029518 | 134.8543 | 6.659%
2027 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 133.9133 | 99.89% | 0% | 0.1056% | 8.0263 | 0 | 0 | 8.0263 | 0 | 7.3038 | 0.0399 | 183.0536 | 7.3038 | 0.0399 | 183.0536 | 8.1052 | 0.044278 | 183.0536 | 5.994%
2027 | 217 | CB 217 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 26.6678 | 99.71% | 0% | 0.2895% | 1.7727 | 0 | 0 | 1.7727 | 0 | 1.6131 | 0.0266 | 60.6444 | 1.6131 | 0.0266 | 60.6444 | 1.7901 | 0.029518 | 60.6444 | 6.647%
2027 | 220 | CB 220 | Tier-3 | Tier-3---21 | Tier-3---24 | 2 | 1 | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0133 | 0 | 0 | 0.0133 | 0 | 0 | 0.014759 | 0 | 0%
2027 | 1235 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 12 | 10 | 212.8275 | 99.81% | 0% | 0.1866% | 17.7025 | 0 | 0 | 17.7025 | 0 | 16.1091 | 0.133 | 121.1208 | 16.1091 | 0.133 | 121.1208 | 17.8765 | 0.14759 | 121.1208 | 8.318%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 174 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 166.1116 | 0 | 0 | 166.1116 | 0 | 151.1593 | 2.3142 | 65.3182 | 151.1593 | 2.3142 | 65.3182 | 167.7441 | 2.5681 | 65.3182 | 6.645%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 259 | 144 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 88.9279 | 0 | 0 | 88.9279 | 0 | 80.9232 | 1.9152 | 42.2531 | 80.9232 | 1.9152 | 42.2531 | 89.8019 | 2.1253 | 42.2531 | 5.414%
2027 | 230 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 613 | 396 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 263.2844 | 0 | 0 | 263.2844 | 0 | 239.5852 | 5.2668 | 45.4897 | 239.5852 | 5.2668 | 45.4897 | 265.8719 | 5.8447 | 45.4897 | 6.378%
2027 | 232 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 201 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 186.0305 | 0 | 0 | 186.0305 | 0 | 169.2852 | 2.6733 | 63.3245 | 169.2852 | 2.6733 | 63.3245 | 187.8588 | 2.9666 | 63.3245 | 5.646%
2027 | 971 | CB 235 | Tier-2 | Tier-2---12 | Tier-2---11 | 6 | 4 | 443.5427 | 99.96% | 0% | 0.03939% | 29.5579 | 0 | 0 | 29.5579 | 0 | 26.8973 | 0.0532 | 505.5878 | 26.8973 | 0.0532 | 505.5878 | 29.8484 | 0.059037 | 505.5878 | 6.664%
2027 | 235 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 161 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 592.8145 | 0 | 0 | 592.8145 | 0 | 539.4531 | 2.1413 | 251.928 | 539.4531 | 2.1413 | 251.928 | 598.6407 | 2.3762 | 251.928 | 4.664%
2027 | 236 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 41 | 14 | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 71.7723 | 0 | 0 | 71.7723 | 0 | 65.3119 | 0.1862 | 350.762 | 65.3119 | 0.1862 | 350.762 | 72.4777 | 0.20663 | 350.762 | 3.399%
2027 | 239 | CB 239 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 1 | 10.6776 | 99.64% | 0% | 0.3633% | 0.53194 | 0 | 0 | 0.53194 | 0 | 0.48406 | 0.0133 | 36.3955 | 0.48406 | 0.0133 | 36.3955 | 0.53717 | 0.014759 | 36.3955 | 4.982%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 114 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 59.0928 | 0 | 0 | 59.0928 | 0 | 53.7736 | 1.5162 | 35.4661 | 53.7736 | 1.5162 | 35.4661 | 59.6735 | 1.6826 | 35.4661 | 4.679%
2027 | 240 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 35 | 406.8184 | 64.36% | 35.02% | 0.6193% | 10.5338 | 0 | 0 | 10.5338 | 0 | 9.5857 | 0.4655 | 20.5922 | 9.5857 | 0.4655 | 20.5922 | 10.6374 | 0.51657 | 20.5922 | 2.589%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 197 | 16 | 295.5508 | 37.5% | 61.39% | 1.106% | 0.90024 | 0 | 0 | 0.90024 | 0 | 0.81921 | 0.2128 | 3.8497 | 0.81921 | 0.2128 | 3.8497 | 0.90909 | 0.23615 | 3.8497 | 0.3046%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 180 | 1438.4419 | 90% | 9.47% | 0.5268% | 76.9095 | 0 | 0 | 76.9095 | 0 | 69.9866 | 2.394 | 29.2342 | 69.9866 | 2.394 | 29.2342 | 77.6654 | 2.6567 | 29.2342 | 5.347%
2027 | 246 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 29 | 379.7423 | 70.28% | 29.01% | 0.71% | 8.5995 | 0 | 0 | 8.5995 | 0 | 7.8254 | 0.3857 | 20.2889 | 7.8254 | 0.3857 | 20.2889 | 8.684 | 0.42802 | 20.2889 | 2.265%
2027 | 240 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 136 | 62 | 962.1527 | 99.5% | 0% | 0.4991% | 43.6439 | 0 | 0 | 43.6439 | 0 | 39.7154 | 0.8246 | 48.1632 | 39.7154 | 0.8246 | 48.1632 | 44.0729 | 0.91507 | 48.1632 | 4.536%
2027 | 1233 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 101 | 65 | 826.9208 | 97.04% | 2.672% | 0.2884% | 51.6421 | 0 | 0 | 51.6421 | 0 | 46.9936 | 0.8645 | 54.3593 | 46.9936 | 0.8645 | 54.3593 | 52.1497 | 0.95935 | 54.3593 | 6.245%
2027 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 108 | 32 | 310.7968 | 16.09% | 83.08% | 0.8251% | 1.4817 | 0 | 0 | 1.4817 | 0 | 1.3483 | 0.4256 | 3.168 | 1.3483 | 0.4256 | 3.168 | 1.4963 | 0.4723 | 3.168 | 0.4767%
2027 | 283 | CB 283 | Tier-3 | Tier-3---21 | Tier-3---11 | 2 | 2 | 6.0451 | 99.41% | 0% | 0.5857% | 0.60097 | 0 | 0 | 0.60097 | 0 | 0.54688 | 0.0266 | 20.5593 | 0.54688 | 0.0266 | 20.5593 | 0.60688 | 0.029518 | 20.5593 | 9.941%
2027 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 17 | 13 | 94.6686 | 66.47% | 32.93% | 0.6021% | 4.8122 | 0 | 0 | 4.8122 | 0 | 4.379 | 0.1729 | 25.3268 | 4.379 | 0.1729 | 25.3268 | 4.8595 | 0.19187 | 25.3268 | 5.083%
2027 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 21 | 1 | 10.7713 | 97.26% | 0% | 2.741% | 0.049886 | 0 | 0 | 0.049886 | 0 | 0.045395 | 0.0133 | 3.4132 | 0.045395 | 0.0133 | 3.4132 | 0.050376 | 0.014759 | 3.4132 | 0.4631%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 21 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 138.7612 | 0 | 0 | 138.7612 | 0 | 126.2708 | 0.2793 | 452.0978 | 126.2708 | 0.2793 | 452.0978 | 140.125 | 0.30994 | 452.0978 | 9.526%
2027 | 200 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 34 | 8 | 215.2852 | 96.83% | 2.614% | 0.5577% | 4.9049 | 0 | 0 | 4.9049 | 0 | 4.4634 | 0.1064 | 41.949 | 4.4634 | 0.1064 | 41.949 | 4.9531 | 0.11807 | 41.949 | 2.278%
2027 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 156 | 73 | 124.2501 | 33.35% | 64.03% | 2.615% | 1.9393 | 0 | 0 | 1.9393 | 0 | 1.7647 | 0.9709 | 1.8176 | 1.7647 | 0.9709 | 1.8176 | 1.9584 | 1.0774 | 1.8176 | 1.561%
2027 | 200 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 48 | 25 | 261.2105 | 99.38% | 0% | 0.6196% | 13.5204 | 0 | 0 | 13.5204 | 0 | 12.3034 | 0.3325 | 37.0027 | 12.3034 | 0.3325 | 37.0027 | 13.6533 | 0.36898 | 37.0027 | 5.176%
2027 | 350 | CB 350 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 1 | 133.5736 | 99.92% | 0% | 0.07821% | 3.3367 | 0 | 0 | 3.3367 | 0 | 3.0364 | 0.0133 | 228.2991 | 3.0364 | 0.0133 | 228.2991 | 3.3695 | 0.014759 | 228.2991 | 2.498%
2027 | 353 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 110 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 1039.3116 | 0 | 0 | 1039.3116 | 0 | 945.7594 | 1.463 | 646.4524 | 945.7594 | 1.463 | 646.4524 | 1049.5259 | 1.6235 | 646.4524 | 7.119%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 5 | 4 | 87.8741 | 99.22% | 0.6237% | 0.1541% | 6.9753 | 0 | 0 | 6.9753 | 0 | 6.3474 | 0.0532 | 119.3118 | 6.3474 | 0.0532 | 119.3118 | 7.0438 | 0.059037 | 119.3118 | 7.938%
2027 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 4 | 1 | 7.5897 | 98.6% | 0% | 1.398% | 0.18709 | 0 | 0 | 0.18709 | 0 | 0.17025 | 0.0133 | 12.8007 | 0.17025 | 0.0133 | 12.8007 | 0.18893 | 0.014759 | 12.8007 | 2.465%
2027 | 354 | CB 354 | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 2 | 12.0695 | 99.46% | 0% | 0.538% | 0.8003 | 0 | 0 | 0.8003 | 0 | 0.72827 | 0.0266 | 27.3784 | 0.72827 | 0.0266 | 27.3784 | 0.80817 | 0.029518 | 27.3784 | 6.631%
2027 | 356 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 168 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 620.6565 | 0 | 0 | 620.6565 | 0 | 564.7889 | 2.2344 | 252.77 | 564.7889 | 2.2344 | 252.77 | 626.7563 | 2.4796 | 252.77 | 5.498%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 2 | 6.8062 | 99.1% | 0% | 0.8997% | 0.44966 | 0 | 0 | 0.44966 | 0 | 0.40919 | 0.0266 | 15.3829 | 0.40919 | 0.0266 | 15.3829 | 0.45408 | 0.029518 | 15.3829 | 6.607%
2027 | 1166 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 106 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 383.8802 | 0 | 0 | 383.8802 | 0 | 349.3258 | 1.4098 | 247.784 | 349.3258 | 1.4098 | 247.784 | 387.653 | 1.5645 | 247.784 | 6.282%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 21 | 6 | 861.4334 | 18.88% | 81.11% | 0.0161% | 4.6462 | 0 | 0 | 4.6462 | 0 | 4.228 | 0.0798 | 52.9824 | 4.228 | 0.0798 | 52.9824 | 4.6919 | 0.088555 | 52.9824 | 0.5394%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 145 | 5 | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.33127 | 0 | 0 | 0.33127 | 0 | 0.30145 | 0.0665 | 4.5332 | 0.30145 | 0.0665 | 4.5332 | 0.33453 | 0.073796 | 4.5332 | 0.04946%
2027 | 442 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 94 | 87 | 1133.0808 | 94.08% | 5.666% | 0.2577% | 98.6577 | 0 | 0 | 98.6577 | 0 | 89.7771 | 1.1571 | 77.5881 | 89.7771 | 1.1571 | 77.5881 | 99.6273 | 1.2841 | 77.5881 | 8.707%
2027 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 36 | 22 | 67.1473 | 98.29% | 0% | 1.71% | 4.0333 | 0 | 0 | 4.0333 | 0 | 3.6702 | 0.2926 | 12.5435 | 3.6702 | 0.2926 | 12.5435 | 4.0729 | 0.3247 | 12.5435 | 6.007%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 17 | 15 | 117.4434 | 97.68% | 1.947% | 0.3705% | 10.1225 | 0 | 0 | 10.1225 | 0 | 9.2113 | 0.1995 | 46.1719 | 9.2113 | 0.1995 | 46.1719 | 10.2219 | 0.22139 | 46.1719 | 8.619%
2027 | 449 | CB 449 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 7.8127 | 98.22% | 0% | 1.784% | 0.4604 | 0 | 0 | 0.4604 | 0 | 0.41896 | 0.0399 | 10.5002 | 0.41896 | 0.0399 | 10.5002 | 0.46493 | 0.044278 | 10.5002 | 5.893%
2027 | 443 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 36 | 27 | 101.8709 | 98.65% | 0% | 1.347% | 7.5374 | 0 | 0 | 7.5374 | 0 | 6.8589 | 0.3591 | 19.1003 | 6.8589 | 0.3591 | 19.1003 | 7.6115 | 0.3985 | 19.1003 | 7.399%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 48 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 83.2699 | 0 | 0 | 83.2699 | 0 | 75.7745 | 0.6384 | 118.6945 | 75.7745 | 0.6384 | 118.6945 | 84.0883 | 0.70844 | 118.6945 | 1.203%
2027 | 1299 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 6 | 19.4193 | 94.64% | 0% | 5.361% | 0.35571 | 0 | 0 | 0.35571 | 0 | 0.32369 | 0.0798 | 4.0563 | 0.32369 | 0.0798 | 4.0563 | 0.35921 | 0.088555 | 4.0563 | 1.832%
2027 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 2 | 2 | 1.7668 | 97.86% | 0% | 2.14% | 0.1729 | 0 | 0 | 0.1729 | 0 | 0.15734 | 0.0266 | 5.9149 | 0.15734 | 0.0266 | 5.9149 | 0.1746 | 0.029518 | 5.9149 | 9.786%
2027 | 520 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 14 | 11 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.16207 | 0 | 0 | 0.16207 | 0 | 0.14748 | 0.1463 | 1.0081 | 0.14748 | 0.1463 | 1.0081 | 0.16366 | 0.16235 | 1.0081 | 1.319%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 129 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 49.0233 | 0 | 0 | 49.0233 | 0 | 44.6105 | 1.7157 | 26.0014 | 44.6105 | 1.7157 | 26.0014 | 49.5051 | 1.9039 | 26.0014 | 4.563%
2027 | 522 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 126 | 305.5692 | 37.2% | 61.32% | 1.484% | 5.5296 | 0 | 0 | 5.5296 | 0 | 5.0319 | 1.6758 | 3.0027 | 5.0319 | 1.6758 | 3.0027 | 5.584 | 1.8597 | 3.0027 | 1.81%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 90 | 12 | 481.3309 | 94.25% | 5.298% | 0.4514% | 6.0487 | 0 | 0 | 6.0487 | 0 | 5.5043 | 0.1596 | 34.488 | 5.5043 | 0.1596 | 34.488 | 6.1082 | 0.17711 | 34.488 | 1.257%
2027 | 1160 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 14 | 1 | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0025483 | 0 | 0 | 0.0025483 | 0 | 0.002319 | 0.0133 | 0.17436 | 0.002319 | 0.0133 | 0.17436 | 0.0025734 | 0.014759 | 0.17436 | 0.02403%
2027 | 1161 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 12 | 6 | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11347 | 0 | 0 | 0.11347 | 0 | 0.10325 | 0.0798 | 1.2939 | 0.10325 | 0.0798 | 1.2939 | 0.11458 | 0.088555 | 1.2939 | 1.8%
2027 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 10 | 5 | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25563 | 0 | 0 | 0.25563 | 0 | 0.23262 | 0.0665 | 3.4981 | 0.23262 | 0.0665 | 3.4981 | 0.25815 | 0.073796 | 3.4981 | 0.2293%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 39 | 33 | 54.1099 | 76.19% | 21.99% | 1.82% | 3.4885 | 0 | 0 | 3.4885 | 0 | 3.1745 | 0.4389 | 7.2328 | 3.1745 | 0.4389 | 7.2328 | 3.5228 | 0.48705 | 7.2328 | 6.447%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 5 | 67.245 | 99.24% | 0% | 0.7576% | 2.0855 | 0 | 0 | 2.0855 | 0 | 1.8978 | 0.0665 | 28.5378 | 1.8978 | 0.0665 | 28.5378 | 2.106 | 0.073796 | 28.5378 | 3.101%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 43 | 35 | 949.4775 | 95.45% | 4.414% | 0.1311% | 73.7702 | 0 | 0 | 73.7702 | 0 | 67.1299 | 0.4655 | 144.2104 | 67.1299 | 0.4655 | 144.2104 | 74.4953 | 0.51657 | 144.2104 | 7.77%
2027 | 542 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 19 | 13 | 417.7025 | 78.37% | 21.49% | 0.1463% | 22.397 | 0 | 0 | 22.397 | 0 | 20.381 | 0.1729 | 117.8773 | 20.381 | 0.1729 | 117.8773 | 22.6171 | 0.19187 | 117.8773 | 5.362%
2027 | 1094 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 262 | 4323.2442 | 99.81% | 0% | 0.1903% | 306.3779 | 0 | 0 | 306.3779 | 0 | 278.7997 | 3.4846 | 80.0091 | 278.7997 | 3.4846 | 80.0091 | 309.3889 | 3.8669 | 80.0091 | 7.087%
2027 | 67 | CB 67 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 10.8761 | 99.3% | 0% | 0.7025% | 0.71998 | 0 | 0 | 0.71998 | 0 | 0.65517 | 0.0266 | 24.6305 | 0.65517 | 0.0266 | 24.6305 | 0.72705 | 0.029518 | 24.6305 | 6.62%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 53 | 53 | 55.0677 | 92.66% | 4.028% | 3.312% | 5.1026 | 0 | 0 | 5.1026 | 0 | 4.6433 | 0.7049 | 6.5871 | 4.6433 | 0.7049 | 6.5871 | 5.1527 | 0.78224 | 6.5871 | 9.266%
2027 | 78 | CB 78 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 3 | 25.281 | 99.56% | 0% | 0.4423% | 1.8877 | 0 | 0 | 1.8877 | 0 | 1.7178 | 0.0399 | 43.0519 | 1.7178 | 0.0399 | 43.0519 | 1.9062 | 0.044278 | 43.0519 | 7.467%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 24 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 27.6164 | 0 | 0 | 27.6164 | 0 | 25.1305 | 0.3192 | 78.7297 | 25.1305 | 0.3192 | 78.7297 | 27.8878 | 0.35422 | 78.7297 | 0.3223%
2027 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 12 | 8 | 42.6475 | 99.43% | 0% | 0.5747% | 2.8268 | 0 | 0 | 2.8268 | 0 | 2.5724 | 0.1064 | 24.1765 | 2.5724 | 0.1064 | 24.1765 | 2.8546 | 0.11807 | 24.1765 | 6.628%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 39 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 209.3563 | 0 | 0 | 209.3563 | 0 | 190.5114 | 0.5187 | 367.2864 | 190.5114 | 0.5187 | 367.2864 | 211.4138 | 0.57561 | 367.2864 | 7.634%
2027 | 75 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 30 | 337.7351 | 93.43% | 6.078% | 0.496% | 13.9205 | 0 | 0 | 13.9205 | 0 | 12.6675 | 0.399 | 31.748 | 12.6675 | 0.399 | 31.748 | 14.0573 | 0.44278 | 31.748 | 4.122%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 53 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 112.8379 | 0 | 0 | 112.8379 | 0 | 102.6809 | 0.7049 | 145.6674 | 102.6809 | 0.7049 | 145.6674 | 113.9468 | 0.78224 | 145.6674 | 6.818%
2027 | 236 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 4 | 3 | 251.0066 | 99.97% | 0% | 0.03372% | 18.8191 | 0 | 0 | 18.8191 | 0 | 17.1252 | 0.0399 | 429.2023 | 17.1252 | 0.0399 | 429.2023 | 19.0041 | 0.044278 | 429.2023 | 7.497%
2027 | 235 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 114 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 778.2289 | 0 | 0 | 778.2289 | 0 | 708.1777 | 1.5162 | 467.0743 | 708.1777 | 1.5162 | 467.0743 | 785.8773 | 1.6826 | 467.0743 | 6.793%
2027 | 973 | CB 973 | Tier-2 | Tier-2---14 | Tier-2---11 | 7 | 4 | 310.4015 | 99.93% | 0% | 0.0686% | 17.7251 | 0 | 0 | 17.7251 | 0 | 16.1296 | 0.0532 | 303.1874 | 16.1296 | 0.0532 | 303.1874 | 17.8993 | 0.059037 | 303.1874 | 5.71%
2027 | 973 | CB 974 | Tier-2 | Tier-2---12 | Tier-2---11 | 7 | 5 | 334.3039 | 99.93% | 0% | 0.06503% | 23.8633 | 0 | 0 | 23.8633 | 0 | 21.7153 | 0.0665 | 326.546 | 21.7153 | 0.0665 | 326.546 | 24.0979 | 0.073796 | 326.546 | 7.138%
2027 | 970 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 11 | 8 | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 94.4014 | 0 | 0 | 94.4014 | 0 | 85.904 | 0.1064 | 807.3691 | 85.904 | 0.1064 | 807.3691 | 95.3292 | 0.11807 | 807.3691 | 7.237%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 35 | 24 | 387.8494 | 99.7% | 0% | 0.3041% | 26.5145 | 0 | 0 | 26.5145 | 0 | 24.1278 | 0.3192 | 75.5885 | 24.1278 | 0.3192 | 75.5885 | 26.7751 | 0.35422 | 75.5885 | 6.836%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 14 | 11 | 132.7571 | 99.65% | 0% | 0.354% | 10.394 | 0 | 0 | 10.394 | 0 | 9.4584 | 0.1463 | 64.6507 | 9.4584 | 0.1463 | 64.6507 | 10.4961 | 0.16235 | 64.6507 | 7.829%
2027 | 982 | CB 982 | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0133 | 0 | 0 | 0.0133 | 0 | 0 | 0.014759 | 0 | 0%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 6 | 2 | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.82631 | 0 | 0 | 0.82631 | 0 | 0.75193 | 0.0266 | 28.268 | 0.75193 | 0.0266 | 28.268 | 0.83443 | 0.029518 | 28.268 | 3.007%
2027 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 15.4911 | 99.81% | 0% | 0.1868% | 1.5462 | 0 | 0 | 1.5462 | 0 | 1.407 | 0.0266 | 52.8961 | 1.407 | 0.0266 | 52.8961 | 1.5614 | 0.029518 | 52.8961 | 9.981%
2027 | 520 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 161 | 346.5871 | 36.93% | 61.45% | 1.621% | 5.5543 | 0 | 0 | 5.5543 | 0 | 5.0543 | 2.1413 | 2.3604 | 5.0543 | 2.1413 | 2.3604 | 5.6089 | 2.3762 | 2.3604 | 1.603%
2027 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 109 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 61.1907 | 0 | 0 | 61.1907 | 0 | 55.6827 | 1.4497 | 38.4098 | 55.6827 | 1.4497 | 38.4098 | 61.7921 | 1.6088 | 38.4098 | 5.943%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 80 | 67 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 125.5197 | 0 | 0 | 125.5197 | 0 | 114.2212 | 0.8911 | 128.1801 | 114.2212 | 0.8911 | 128.1801 | 126.7533 | 0.98887 | 128.1801 | 8.195%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 116 | 86 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 374.0843 | 0 | 0 | 374.0843 | 0 | 340.4116 | 1.1438 | 297.6148 | 340.4116 | 1.1438 | 297.6148 | 377.7608 | 1.2693 | 297.6148 | 7.307%
2027 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 403 | 5 | 638.0788 | 99.02% | 0% | 0.9838% | 0.78387 | 0 | 0 | 0.78387 | 0 | 0.71331 | 0.0665 | 10.7265 | 0.71331 | 0.0665 | 10.7265 | 0.79158 | 0.073796 | 10.7265 | 0.1228%
2027 | 221 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 190 | 153 | 6915.6819 | 99% | 0.9206% | 0.07911% | 551.3273 | 0 | 0 | 551.3273 | 0 | 501.7004 | 2.0349 | 246.548 | 501.7004 | 2.0349 | 246.548 | 556.7457 | 2.2582 | 246.548 | 7.972%
2027 | 222 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 247 | 132 | 3027.5479 | 94.73% | 5.109% | 0.164% | 153.2642 | 0 | 0 | 153.2642 | 0 | 139.4683 | 1.7556 | 79.442 | 139.4683 | 1.7556 | 79.442 | 154.7705 | 1.9482 | 79.442 | 5.062%
2027 | 237 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 179 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 524.2711 | 0 | 0 | 524.2711 | 0 | 477.0795 | 2.3807 | 200.3947 | 477.0795 | 2.3807 | 200.3947 | 529.4236 | 2.6419 | 200.3947 | 4.985%
2027 | 237 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 62 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 269.606 | 0 | 0 | 269.606 | 0 | 245.3378 | 0.8246 | 297.5236 | 245.3378 | 0.8246 | 297.5236 | 272.2557 | 0.91507 | 297.5236 | 5.155%
2027 | 237 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 93 | 916.1972 | 69.5% | 30.07% | 0.4286% | 24.5712 | 0 | 0 | 24.5712 | 0 | 22.3594 | 1.2369 | 18.077 | 22.3594 | 1.2369 | 18.077 | 24.8126 | 1.3726 | 18.077 | 2.682%
2027 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 29.7534 | 99.88% | 0% | 0.1212% | 2.9717 | 0 | 0 | 2.9717 | 0 | 2.7042 | 0.0266 | 101.6631 | 2.7042 | 0.0266 | 101.6631 | 3.0009 | 0.029518 | 101.6631 | 9.988%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 58 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 228.7681 | 0 | 0 | 228.7681 | 0 | 208.1758 | 0.7714 | 269.8677 | 208.1758 | 0.7714 | 269.8677 | 231.0164 | 0.85604 | 269.8677 | 6.117%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 225 | 184 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 257.6221 | 0 | 0 | 257.6221 | 0 | 234.4326 | 2.4472 | 95.7963 | 234.4326 | 2.4472 | 95.7963 | 260.154 | 2.7157 | 95.7963 | 7.664%
2027 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 220 | 27 | 94.186 | 2.003% | 94.63% | 3.363% | 0.023154 | 0 | 0 | 0.023154 | 0 | 0.02107 | 0.3591 | 0.058674 | 0.02107 | 0.3591 | 0.058674 | 0.023382 | 0.3985 | 0.058674 | 0.02458%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 138 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 71.5721 | 0 | 0 | 71.5721 | 0 | 65.1297 | 1.8354 | 35.4853 | 65.1297 | 1.8354 | 35.4853 | 72.2755 | 2.0368 | 35.4853 | 3.468%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 235 | 175 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 263.5885 | 0 | 0 | 263.5885 | 0 | 239.8619 | 2.3275 | 103.0556 | 239.8619 | 2.3275 | 103.0556 | 266.179 | 2.5829 | 103.0556 | 7.087%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 122 | 74 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 562.6656 | 0 | 0 | 562.6656 | 0 | 512.018 | 0.9842 | 520.238 | 512.018 | 0.9842 | 520.238 | 568.1955 | 1.0922 | 520.238 | 6.025%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 306 | 6920.124 | 97.57% | 2.306% | 0.1195% | 477.1808 | 0 | 0 | 477.1808 | 0 | 434.228 | 4.0698 | 106.6952 | 434.228 | 4.0698 | 106.6952 | 481.8705 | 4.5163 | 106.6952 | 6.896%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 125 | 117 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 552.7852 | 0 | 0 | 552.7852 | 0 | 503.027 | 1.5561 | 323.2615 | 503.027 | 1.5561 | 323.2615 | 558.2179 | 1.7268 | 323.2615 | 9.296%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 103 | 81 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 295.9408 | 0 | 0 | 295.9408 | 0 | 269.3021 | 1.0773 | 249.9788 | 269.3021 | 1.0773 | 249.9788 | 298.8493 | 1.1955 | 249.9788 | 7.823%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 4 | 1 | 117.1572 | 99.03% | 0.8725% | 0.09309% | 2.9006 | 0 | 0 | 2.9006 | 0 | 2.518 | 0.012687 | 198.4626 | 2.518 | 0.012687 | 198.4626 | 2.9435 | 0.014832 | 198.4626 | 2.476%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 10 | 10 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 40.5584 | 0 | 0 | 40.5584 | 0 | 35.2074 | 0.12687 | 277.5011 | 35.2074 | 0.12687 | 277.5011 | 41.1578 | 0.14832 | 277.5011 | 9.915%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 117 | 4222.2471 | 91.41% | 8.486% | 0.103% | 309.2954 | 0 | 0 | 309.2954 | 0 | 268.4885 | 1.4844 | 180.8719 | 268.4885 | 1.4844 | 180.8719 | 313.8662 | 1.7353 | 180.8719 | 7.325%
2028 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 10 | 10 | 114.5301 | 99.76% | 0% | 0.2395% | 11.4256 | 0 | 0 | 11.4256 | 0 | 9.9181 | 0.12687 | 78.1739 | 9.9181 | 0.12687 | 78.1739 | 11.5944 | 0.14832 | 78.1739 | 9.976%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 421 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 2840.2415 | 0 | 0 | 2840.2415 | 0 | 2465.5147 | 5.3413 | 461.5902 | 2465.5147 | 5.3413 | 461.5902 | 2882.2148 | 6.2441 | 461.5902 | 8.079%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 70 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 570.4582 | 0 | 0 | 570.4582 | 0 | 495.1949 | 0.88811 | 557.5827 | 495.1949 | 0.88811 | 557.5827 | 578.8885 | 1.0382 | 557.5827 | 8.085%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 139 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 1552.9096 | 0 | 0 | 1552.9096 | 0 | 1348.0267 | 1.7635 | 764.3897 | 1348.0267 | 1.7635 | 764.3897 | 1575.8586 | 2.0616 | 764.3897 | 8.249%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 69 | 61 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 442.8665 | 0 | 0 | 442.8665 | 0 | 384.437 | 0.77392 | 496.7369 | 384.437 | 0.77392 | 496.7369 | 449.4112 | 0.90473 | 496.7369 | 8.797%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 16 | 16 | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 138.0795 | 0 | 0 | 138.0795 | 0 | 119.862 | 0.203 | 590.463 | 119.862 | 0.203 | 590.463 | 140.1201 | 0.23731 | 590.463 | 9.958%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 12 | 10 | 794.3626 | 99.6% | 0.3592% | 0.04176% | 65.9315 | 0 | 0 | 65.9315 | 0 | 57.2328 | 0.12687 | 451.1035 | 57.2328 | 0.12687 | 451.1035 | 66.9058 | 0.14832 | 451.1035 | 8.3%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 107 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 751.5808 | 0 | 0 | 751.5808 | 0 | 652.4212 | 1.3575 | 480.5907 | 652.4212 | 1.3575 | 480.5907 | 762.6878 | 1.587 | 480.5907 | 7.669%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 9 | 9 | 694.7204 | 99.22% | 0.7469% | 0.03547% | 68.9285 | 0 | 0 | 68.9285 | 0 | 59.8344 | 0.11419 | 524.0101 | 59.8344 | 0.11419 | 524.0101 | 69.9471 | 0.13348 | 524.0101 | 9.922%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 76 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 429.4935 | 0 | 0 | 429.4935 | 0 | 372.8283 | 0.96423 | 386.6575 | 372.8283 | 0.96423 | 386.6575 | 435.8405 | 1.1272 | 386.6575 | 8.468%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 82 | 73 | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 255.3265 | 0 | 0 | 255.3265 | 0 | 221.64 | 0.92617 | 239.3076 | 221.64 | 0.92617 | 239.3076 | 259.0997 | 1.0827 | 239.3076 | 8.835%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 376 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 728.6709 | 0 | 0 | 728.6709 | 0 | 632.5338 | 4.7704 | 132.595 | 632.5338 | 4.7704 | 132.595 | 739.4392 | 5.5767 | 132.595 | 7.695%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 290 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 280.4875 | 0 | 0 | 280.4875 | 0 | 243.4814 | 3.6793 | 66.1758 | 243.4814 | 3.6793 | 66.1758 | 284.6326 | 4.3012 | 66.1758 | 7.432%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 85 | 585.5086 | 87.68% | 11.85% | 0.4758% | 36.6688 | 0 | 0 | 36.6688 | 0 | 31.8309 | 1.0784 | 29.5162 | 31.8309 | 1.0784 | 29.5162 | 37.2106 | 1.2607 | 29.5162 | 6.263%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 85 | 60 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 355.4132 | 0 | 0 | 355.4132 | 0 | 308.5218 | 0.76124 | 405.2899 | 308.5218 | 0.76124 | 405.2899 | 360.6656 | 0.8899 | 405.2899 | 6.936%
2028 | 1030 | 1030-1735F | Tier-3 | missing | missing | 6 | 6 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.076124 | 0 | 0 | 0.076124 | 0 | 0 | 0.08899 | 0 | 0%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 143 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 863.2115 | 0 | 0 | 863.2115 | 0 | 749.3239 | 1.8143 | 413.0139 | 749.3239 | 1.8143 | 413.0139 | 875.9682 | 2.1209 | 413.0139 | 7.304%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 20 | 17 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 181.8205 | 0 | 0 | 181.8205 | 0 | 157.8321 | 0.21568 | 731.7748 | 157.8321 | 0.21568 | 731.7748 | 184.5075 | 0.25214 | 731.7748 | 8.453%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 98 | 72 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 479.9105 | 0 | 0 | 479.9105 | 0 | 416.5936 | 0.91348 | 456.0487 | 416.5936 | 0.91348 | 456.0487 | 487.0027 | 1.0679 | 456.0487 | 7.248%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 323 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 2209.1889 | 0 | 0 | 2209.1889 | 0 | 1917.72 | 4.098 | 467.9654 | 1917.72 | 4.098 | 467.9654 | 2241.8365 | 4.7906 | 467.9654 | 8.726%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 375 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 2222.2926 | 0 | 0 | 2222.2926 | 0 | 1929.0948 | 4.7577 | 405.465 | 1929.0948 | 4.7577 | 405.465 | 2255.1338 | 5.5618 | 405.465 | 7.825%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 372 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 2333.5174 | 0 | 0 | 2333.5174 | 0 | 2025.6452 | 4.7197 | 429.1919 | 2025.6452 | 4.7197 | 429.1919 | 2368.0023 | 5.5174 | 429.1919 | 8.741%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 338 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 984.307 | 0 | 0 | 984.307 | 0 | 854.4426 | 4.2883 | 199.2495 | 854.4426 | 4.2883 | 199.2495 | 998.8531 | 5.0131 | 199.2495 | 6.168%
2028 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 16 | 12 | 17.9659 | 86.84% | 10.72% | 2.434% | 1.1701 | 0 | 0 | 1.1701 | 0 | 1.0158 | 0.15225 | 6.6718 | 1.0158 | 0.15225 | 6.6718 | 1.1874 | 0.17798 | 6.6718 | 6.513%
2028 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | Tier-2---12 | 40 | 1 | 40.9949 | 23.55% | 73.64% | 2.81% | 0.024132 | 0 | 0 | 0.024132 | 0 | 0.020949 | 0.012687 | 1.6511 | 0.020949 | 0.012687 | 1.6511 | 0.024489 | 0.014832 | 1.6511 | 0.05887%
2028 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 4 | 4 | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.3453 | 0 | 0 | 0.3453 | 0 | 0.29974 | 0.050749 | 5.9063 | 0.29974 | 0.050749 | 5.9063 | 0.3504 | 0.059326 | 5.9063 | 1.275%
2028 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 3 | 3 | 6.3934 | 34.35% | 64.55% | 1.103% | 0.21961 | 0 | 0 | 0.21961 | 0 | 0.19063 | 0.038062 | 5.0085 | 0.19063 | 0.038062 | 5.0085 | 0.22285 | 0.044495 | 5.0085 | 3.435%
2028 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | Tier-2---12 | 237 | 1 | 117.3021 | 94.99% | 0% | 5.009% | 0.047015 | 0 | 0 | 0.047015 | 0 | 0.040812 | 0.012687 | 3.2168 | 0.040812 | 0.012687 | 3.2168 | 0.04771 | 0.014832 | 3.2168 | 0.04008%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 44 | 38 | 730.5479 | 99.24% | 0.5863% | 0.172% | 62.6144 | 0 | 0 | 62.6144 | 0 | 54.3533 | 0.48212 | 112.7389 | 54.3533 | 0.48212 | 112.7389 | 63.5397 | 0.5636 | 112.7389 | 8.571%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 122 | 117 | 919.3728 | 93.93% | 5.62% | 0.4487% | 82.8186 | 0 | 0 | 82.8186 | 0 | 71.8919 | 1.4844 | 48.4312 | 71.8919 | 1.4844 | 48.4312 | 84.0425 | 1.7353 | 48.4312 | 9.008%
2028 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 72 | 509.5021 | 91.97% | 7.519% | 0.512% | 42.1724 | 0 | 0 | 42.1724 | 0 | 36.6084 | 0.91348 | 40.0755 | 36.6084 | 0.91348 | 40.0755 | 42.7956 | 1.0679 | 40.0755 | 8.277%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 29 | 14 | 140.8367 | 88.02% | 11.68% | 0.2956% | 5.9845 | 0 | 0 | 5.9845 | 0 | 5.1949 | 0.17762 | 29.2469 | 5.1949 | 0.17762 | 29.2469 | 6.0729 | 0.20764 | 29.2469 | 4.249%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 317 | 215 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 398.5741 | 0 | 0 | 398.5741 | 0 | 345.9883 | 2.7278 | 126.8394 | 345.9883 | 2.7278 | 126.8394 | 404.4643 | 3.1888 | 126.8394 | 6.757%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 225 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 348.513 | 0 | 0 | 348.513 | 0 | 302.532 | 2.8546 | 105.979 | 302.532 | 2.8546 | 105.979 | 353.6634 | 3.3371 | 105.979 | 6.983%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 128 | 2514.2831 | 99.84% | 0% | 0.1648% | 192.3939 | 0 | 0 | 192.3939 | 0 | 167.0105 | 1.624 | 102.8406 | 167.0105 | 1.624 | 102.8406 | 195.2371 | 1.8984 | 102.8406 | 7.652%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 65 | 34 | 95.3301 | 98.77% | 0% | 1.235% | 4.9249 | 0 | 0 | 4.9249 | 0 | 4.2752 | 0.43137 | 9.9107 | 4.2752 | 0.43137 | 9.9107 | 4.9977 | 0.50427 | 9.9107 | 5.166%
2028 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 4 | 4 | 54.719 | 98.75% | 1.065% | 0.1855% | 5.4035 | 0 | 0 | 5.4035 | 0 | 4.6905 | 0.050749 | 92.4261 | 4.6905 | 0.050749 | 92.4261 | 5.4833 | 0.059326 | 92.4261 | 9.875%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 34 | 32 | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 201.2258 | 0 | 0 | 201.2258 | 0 | 174.6771 | 0.40599 | 430.2462 | 174.6771 | 0.40599 | 430.2462 | 204.1995 | 0.47461 | 430.2462 | 9.381%
2028 | 1100 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 54 | 51 | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 399.0156 | 0 | 0 | 399.0156 | 0 | 346.3715 | 0.64705 | 535.3072 | 346.3715 | 0.64705 | 535.3072 | 404.9123 | 0.75641 | 535.3072 | 9.437%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 12 | 12 | 417.0013 | 94.5% | 5.418% | 0.08666% | 39.4048 | 0 | 0 | 39.4048 | 0 | 34.2059 | 0.15225 | 224.6733 | 34.2059 | 0.15225 | 224.6733 | 39.9871 | 0.17798 | 224.6733 | 9.45%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 17 | 788.3757 | 99.4% | 0.5205% | 0.07536% | 70.1185 | 0 | 0 | 70.1185 | 0 | 60.8675 | 0.21568 | 282.2067 | 60.8675 | 0.21568 | 282.2067 | 71.1547 | 0.25214 | 282.2067 | 8.894%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 397 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 209.849 | 0 | 0 | 209.849 | 0 | 182.1626 | 5.0369 | 36.1659 | 182.1626 | 5.0369 | 36.1659 | 212.9502 | 5.8881 | 36.1659 | 4.499%
2028 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 65 | 56 | 240.2897 | 88.19% | 10.99% | 0.8202% | 18.2565 | 0 | 0 | 18.2565 | 0 | 15.8478 | 0.71049 | 22.3055 | 15.8478 | 0.71049 | 22.3055 | 18.5263 | 0.83057 | 22.3055 | 7.598%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 46 | 206.5878 | 96.62% | 2.592% | 0.7875% | 18.7386 | 0 | 0 | 18.7386 | 0 | 16.2663 | 0.58362 | 27.8717 | 16.2663 | 0.58362 | 27.8717 | 19.0155 | 0.68225 | 27.8717 | 9.071%
2028 | 260 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 37 | 30 | 247.9994 | 97.75% | 1.792% | 0.4608% | 19.655 | 0 | 0 | 19.655 | 0 | 17.0618 | 0.38062 | 44.8265 | 17.0618 | 0.38062 | 44.8265 | 19.9454 | 0.44495 | 44.8265 | 7.925%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 98 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 310.444 | 0 | 0 | 310.444 | 0 | 269.4856 | 1.2434 | 216.7408 | 269.4856 | 1.2434 | 216.7408 | 315.0317 | 1.4535 | 216.7408 | 7.829%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 94 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 948.0153 | 0 | 0 | 948.0153 | 0 | 822.9391 | 1.1926 | 690.0347 | 822.9391 | 1.1926 | 690.0347 | 962.0252 | 1.3942 | 690.0347 | 9.378%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 216 | 186 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 880.7229 | 0 | 0 | 880.7229 | 0 | 764.5249 | 2.3598 | 323.9737 | 764.5249 | 2.3598 | 323.9737 | 893.7383 | 2.7587 | 323.9737 | 8.532%
2028 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | Tier-2---13 | 29 | 15 | 70.6534 | 98.66% | 0% | 1.337% | 3.6056 | 0 | 0 | 3.6056 | 0 | 3.1299 | 0.19031 | 16.4465 | 3.1299 | 0.19031 | 16.4465 | 3.6589 | 0.22247 | 16.4465 | 5.103%
2028 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | Tier-3---19 | 13 | 12 | 157.8878 | 78.49% | 21.24% | 0.2654% | 11.44 | 0 | 0 | 11.44 | 0 | 9.9306 | 0.15225 | 65.2269 | 9.9306 | 0.15225 | 65.2269 | 11.609 | 0.17798 | 65.2269 | 7.246%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 133 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 537.0936 | 0 | 0 | 537.0936 | 0 | 466.2323 | 1.6874 | 276.3006 | 466.2323 | 1.6874 | 276.3006 | 545.0308 | 1.9726 | 276.3006 | 8.737%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 58 | 55 | 2215.156 | 94.69% | 5.226% | 0.08401% | 198.904 | 0 | 0 | 198.904 | 0 | 172.6616 | 0.6978 | 247.4368 | 172.6616 | 0.6978 | 247.4368 | 201.8434 | 0.81574 | 247.4368 | 8.979%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 205 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 735.0191 | 0 | 0 | 735.0191 | 0 | 638.0445 | 2.6009 | 245.3173 | 638.0445 | 2.6009 | 245.3173 | 745.8813 | 3.0405 | 245.3173 | 8.452%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 95 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 138.9852 | 0 | 0 | 138.9852 | 0 | 120.6482 | 1.2053 | 100.0987 | 120.6482 | 1.2053 | 100.0987 | 141.0392 | 1.409 | 100.0987 | 8.918%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 166 | 136 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 287.2101 | 0 | 0 | 287.2101 | 0 | 249.3171 | 1.7255 | 144.4921 | 249.3171 | 1.7255 | 144.4921 | 291.4545 | 2.0171 | 144.4921 | 8.063%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 157 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 245.2498 | 0 | 0 | 245.2498 | 0 | 212.8928 | 1.9919 | 106.879 | 212.8928 | 1.9919 | 106.879 | 248.8741 | 2.3286 | 106.879 | 8.22%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 56 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 132.4185 | 0 | 0 | 132.4185 | 0 | 114.9479 | 0.71049 | 161.7871 | 114.9479 | 0.71049 | 161.7871 | 134.3754 | 0.83057 | 161.7871 | 9.551%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 167 | 146 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 370.9048 | 0 | 0 | 370.9048 | 0 | 321.9696 | 1.8523 | 173.8173 | 321.9696 | 1.8523 | 173.8173 | 376.3861 | 2.1654 | 173.8173 | 8.625%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 44 | 44 | 411.5414 | 99.65% | 0% | 0.3468% | 41.0114 | 0 | 0 | 41.0114 | 0 | 35.6006 | 0.55824 | 63.7728 | 35.6006 | 0.55824 | 63.7728 | 41.6175 | 0.65259 | 63.7728 | 9.965%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 31 | 456.1931 | 99.77% | 0% | 0.2285% | 41.499 | 0 | 0 | 41.499 | 0 | 36.0239 | 0.39331 | 91.5925 | 36.0239 | 0.39331 | 91.5925 | 42.1123 | 0.45978 | 91.5925 | 9.097%
2028 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 2 | 2 | 2.4589 | 98.62% | 0% | 1.38% | 0.2425 | 0 | 0 | 0.2425 | 0 | 0.21051 | 0.025375 | 8.2959 | 0.21051 | 0.025375 | 8.2959 | 0.24608 | 0.029663 | 8.2959 | 9.862%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 52 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 95.0921 | 0 | 0 | 95.0921 | 0 | 82.5462 | 0.65974 | 125.1194 | 82.5462 | 0.65974 | 125.1194 | 96.4974 | 0.77124 | 125.1194 | 8.072%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 7 | 158.2514 | 99.48% | 0.3681% | 0.155% | 15.7423 | 0 | 0 | 15.7423 | 0 | 13.6654 | 0.088811 | 153.8703 | 13.6654 | 0.088811 | 153.8703 | 15.975 | 0.10382 | 153.8703 | 9.948%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 68 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 175.7123 | 0 | 0 | 175.7123 | 0 | 152.5297 | 0.86274 | 176.7977 | 152.5297 | 0.86274 | 176.7977 | 178.309 | 1.0085 | 176.7977 | 9.354%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 152 | 29 | 6418.5082 | 93.04% | 6.917% | 0.04745% | 113.9301 | 0 | 0 | 113.9301 | 0 | 98.8988 | 0.36793 | 268.7967 | 98.8988 | 0.36793 | 268.7967 | 115.6138 | 0.43012 | 268.7967 | 1.775%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 48 | 28 | 6815.4278 | 94.54% | 5.441% | 0.023% | 375.8452 | 0 | 0 | 375.8452 | 0 | 326.2581 | 0.35524 | 918.4054 | 326.2581 | 0.35524 | 918.4054 | 381.3995 | 0.41528 | 918.4054 | 5.515%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 267 | 209 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 912.8844 | 0 | 0 | 912.8844 | 0 | 792.4432 | 2.6516 | 298.8498 | 792.4432 | 2.6516 | 298.8498 | 926.3751 | 3.0998 | 298.8498 | 7.77%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 146 | 102 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 252.6921 | 0 | 0 | 252.6921 | 0 | 219.3532 | 1.2941 | 169.502 | 219.3532 | 1.2941 | 169.502 | 256.4264 | 1.5128 | 169.502 | 6.857%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 22 | 18 | 427.4478 | 90.46% | 9.431% | 0.1062% | 31.6376 | 0 | 0 | 31.6376 | 0 | 27.4635 | 0.22837 | 120.2581 | 27.4635 | 0.22837 | 120.2581 | 32.1051 | 0.26697 | 120.2581 | 7.402%
2028 | 1458 | 1458-1057F | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 3 | 155.9987 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.038062 | 0 | 0 | 0.038062 | 0 | 0 | 0.044495 | 0 | 0%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 36 | 29 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 163.0089 | 0 | 0 | 163.0089 | 0 | 141.5023 | 0.36793 | 384.5889 | 141.5023 | 0.36793 | 384.5889 | 165.4178 | 0.43012 | 384.5889 | 6.891%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 80 | 52 | 4370.0987 | 98.67% | 1.293% | 0.03403% | 280.288 | 0 | 0 | 280.288 | 0 | 243.3082 | 0.65974 | 368.7946 | 243.3082 | 0.65974 | 368.7946 | 284.4301 | 0.77124 | 368.7946 | 6.414%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 58.2342 | 99.94% | 0% | 0.06312% | 5.8197 | 0 | 0 | 5.8197 | 0 | 5.0519 | 0.025375 | 199.0936 | 5.0519 | 0.025375 | 199.0936 | 5.9057 | 0.029663 | 199.0936 | 9.994%
2028 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 3 | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.038062 | 0 | 0 | 0.038062 | 0 | 0 | 0.044495 | 0 | 0%
2028 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 5 | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.063436 | 0 | 0 | 0.063436 | 0 | 0 | 0.074158 | 0 | 0%
2028 | 1458 | 1458-1119F | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.012687 | 0 | 0 | 0.012687 | 0 | 0 | 0.014832 | 0 | 0%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 188 | 132 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 1112.3302 | 0 | 0 | 1112.3302 | 0 | 965.5751 | 1.6747 | 576.5583 | 965.5751 | 1.6747 | 576.5583 | 1128.7683 | 1.9578 | 576.5583 | 6.958%
2028 | 1458 | 1458-454F | Tier-2 | Tier-2---18 | Tier-2---10 | 2 | 2 | 84.0912 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.025375 | 0 | 0 | 0.025375 | 0 | 0 | 0.029663 | 0 | 0%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 6 | 167.5686 | 29.81% | 70.17% | 0.01889% | 4.2812 | 0 | 0 | 4.2812 | 0 | 3.7164 | 0.076124 | 48.8205 | 3.7164 | 0.076124 | 48.8205 | 4.3445 | 0.08899 | 48.8205 | 2.555%
2028 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 2 | 2 | 81.0039 | 99.95% | 0% | 0.04716% | 8.0966 | 0 | 0 | 8.0966 | 0 | 7.0284 | 0.025375 | 276.9841 | 7.0284 | 0.025375 | 276.9841 | 8.2162 | 0.029663 | 276.9841 | 9.995%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 127 | 108 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 688.6829 | 0 | 0 | 688.6829 | 0 | 597.8217 | 1.3702 | 436.2938 | 597.8217 | 1.3702 | 436.2938 | 698.8603 | 1.6018 | 436.2938 | 8.44%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 353 | 37077.302 | 99.36% | 0.615% | 0.02874% | 2948.759 | 0 | 0 | 2948.759 | 0 | 2559.715 | 4.4786 | 571.5418 | 2559.715 | 4.4786 | 571.5418 | 2992.336 | 5.2356 | 571.5418 | 7.953%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 7 | 8.268 | 89.5% | 6.947% | 3.548% | 0.57557 | 0 | 0 | 0.57557 | 0 | 0.49964 | 0.088811 | 5.6258 | 0.49964 | 0.088811 | 5.6258 | 0.58408 | 0.10382 | 5.6258 | 6.961%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 87 | 81 | 418.5676 | 87.71% | 11.66% | 0.6303% | 34.1791 | 0 | 0 | 34.1791 | 0 | 29.6697 | 1.0277 | 28.8708 | 29.6697 | 1.0277 | 28.8708 | 34.6842 | 1.2014 | 28.8708 | 8.166%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 669 | 544 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 414.0467 | 0 | 0 | 414.0467 | 0 | 359.4196 | 6.9019 | 52.0756 | 359.4196 | 6.9019 | 52.0756 | 420.1656 | 8.0684 | 52.0756 | 7.519%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 60 | 55 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 277.2195 | 0 | 0 | 277.2195 | 0 | 240.6446 | 0.6978 | 344.8613 | 240.6446 | 0.6978 | 344.8613 | 281.3163 | 0.81574 | 344.8613 | 9.081%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 203 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 365.6682 | 0 | 0 | 365.6682 | 0 | 317.4238 | 2.5755 | 123.2465 | 317.4238 | 2.5755 | 123.2465 | 371.0721 | 3.0108 | 123.2465 | 9.434%
2028 | 157 | 157-207R | Tier-3 | Tier-3---16 | Tier-3---7 | 23 | 23 | 719.0865 | 99.89% | 0% | 0.1123% | 71.8279 | 0 | 0 | 71.8279 | 0 | 62.3513 | 0.29181 | 213.6725 | 62.3513 | 0.29181 | 213.6725 | 72.8894 | 0.34113 | 213.6725 | 9.989%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 250 | 219 | 3160.5079 | 95.27% | 4.501% | 0.231% | 263.7603 | 0 | 0 | 263.7603 | 0 | 228.9611 | 2.7785 | 82.4041 | 228.9611 | 2.7785 | 82.4041 | 267.6582 | 3.2481 | 82.4041 | 8.346%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 554 | 449 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 136.2159 | 0 | 0 | 136.2159 | 0 | 118.2443 | 5.6966 | 20.757 | 118.2443 | 5.6966 | 20.757 | 138.2289 | 6.6594 | 20.757 | 6.609%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 173 | 154 | 1867.403 | 95.01% | 4.712% | 0.2778% | 157.9371 | 0 | 0 | 157.9371 | 0 | 137.0997 | 1.9538 | 70.1693 | 137.0997 | 1.9538 | 70.1693 | 160.2711 | 2.2841 | 70.1693 | 8.458%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 675 | 562 | 18749.5963 | 97% | 2.901% | 0.09453% | 1514.3227 | 0 | 0 | 1514.3227 | 0 | 1314.5308 | 7.1303 | 184.3595 | 1314.5308 | 7.1303 | 184.3595 | 1536.7015 | 8.3354 | 184.3595 | 8.077%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 99 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 383.7782 | 0 | 0 | 383.7782 | 0 | 333.1445 | 1.256 | 265.2336 | 333.1445 | 1.256 | 265.2336 | 389.4497 | 1.4683 | 265.2336 | 9.525%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 86 | 62 | 2651.4354 | 70.65% | 29.24% | 0.1064% | 135.0483 | 0 | 0 | 135.0483 | 0 | 117.2307 | 0.78661 | 149.0325 | 117.2307 | 0.78661 | 149.0325 | 137.0441 | 0.91956 | 149.0325 | 5.093%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 239 | 216 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 386.522 | 0 | 0 | 386.522 | 0 | 335.5263 | 2.7405 | 122.4345 | 335.5263 | 2.7405 | 122.4345 | 392.234 | 3.2036 | 122.4345 | 8.814%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 251 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 465.293 | 0 | 0 | 465.293 | 0 | 403.9047 | 3.1845 | 126.8342 | 403.9047 | 3.1845 | 126.8342 | 472.1692 | 3.7227 | 126.8342 | 8.104%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 43 | 836.2457 | 79.76% | 20.09% | 0.1547% | 55.1538 | 0 | 0 | 55.1538 | 0 | 47.8771 | 0.54555 | 87.7588 | 47.8771 | 0.54555 | 87.7588 | 55.9689 | 0.63776 | 87.7588 | 6.595%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 236 | 191 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 921.1257 | 0 | 0 | 921.1257 | 0 | 799.5972 | 2.4233 | 329.9658 | 799.5972 | 2.4233 | 329.9658 | 934.7382 | 2.8328 | 329.9658 | 7.994%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 131 | 126 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 394.8393 | 0 | 0 | 394.8393 | 0 | 342.7463 | 1.5986 | 214.4042 | 342.7463 | 1.5986 | 214.4042 | 400.6743 | 1.8688 | 214.4042 | 9.435%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 250 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 783.6159 | 0 | 0 | 783.6159 | 0 | 680.2297 | 3.1718 | 214.4602 | 680.2297 | 3.1718 | 214.4602 | 795.1963 | 3.7079 | 214.4602 | 7.783%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 9 | 404.4817 | 67.64% | 32.12% | 0.2398% | 4.9245 | 0 | 0 | 4.9245 | 0 | 4.2748 | 0.11419 | 37.4372 | 4.2748 | 0.11419 | 37.4372 | 4.9973 | 0.13348 | 37.4372 | 1.217%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 172 | 143 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 276.3684 | 0 | 0 | 276.3684 | 0 | 239.9058 | 1.8143 | 132.2318 | 239.9058 | 1.8143 | 132.2318 | 280.4526 | 2.1209 | 132.2318 | 8.126%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 214 | 166 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 373.9475 | 0 | 0 | 373.9475 | 0 | 324.6108 | 2.1061 | 154.1296 | 324.6108 | 2.1061 | 154.1296 | 379.4737 | 2.462 | 154.1296 | 7.579%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 345 | 270 | 13172.958 | 96.8% | 3.124% | 0.0728% | 997.9703 | 0 | 0 | 997.9703 | 0 | 866.3033 | 3.4256 | 252.8933 | 866.3033 | 3.4256 | 252.8933 | 1012.7184 | 4.0045 | 252.8933 | 7.576%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 27 | 1635.841 | 89.24% | 10.7% | 0.05535% | 131.3899 | 0 | 0 | 131.3899 | 0 | 114.055 | 0.34256 | 332.9522 | 114.055 | 0.34256 | 332.9522 | 133.3316 | 0.40045 | 332.9522 | 8.032%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 176 | 7 | 2963.4059 | 78.23% | 21.66% | 0.1106% | 9.2203 | 0 | 0 | 9.2203 | 0 | 8.0038 | 0.088811 | 90.1219 | 8.0038 | 0.088811 | 90.1219 | 9.3566 | 0.10382 | 90.1219 | 0.3111%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 7 | 47.6106 | 91.21% | 0% | 8.789% | 0.15199 | 0 | 0 | 0.15199 | 0 | 0.13194 | 0.088811 | 1.4856 | 0.13194 | 0.088811 | 1.4856 | 0.15424 | 0.10382 | 1.4856 | 0.3192%
2028 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 45 | 7 | 0.95479 | 13.38% | 0% | 86.62% | 0.0019878 | 0 | 0 | 0.0019878 | 0 | 0.0017255 | 0.088811 | 0.019429 | 0.0017255 | 0.088811 | 0.019429 | 0.0020171 | 0.10382 | 0.019429 | 0.2082%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 166 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 641.0014 | 0 | 0 | 641.0014 | 0 | 556.431 | 2.1061 | 264.2009 | 556.431 | 2.1061 | 264.2009 | 650.4742 | 2.462 | 264.2009 | 5.379%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 26 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 193.419 | 0 | 0 | 193.419 | 0 | 167.9003 | 0.32987 | 508.9901 | 167.9003 | 0.32987 | 508.9901 | 196.2774 | 0.38562 | 508.9901 | 9.974%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 81 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 326.8629 | 0 | 0 | 326.8629 | 0 | 283.7383 | 1.0277 | 276.0985 | 283.7383 | 1.0277 | 276.0985 | 331.6933 | 1.2014 | 276.0985 | 7.727%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 19 | 19 | 655.8009 | 99.14% | 0.7615% | 0.1019% | 65.0139 | 0 | 0 | 65.0139 | 0 | 56.4363 | 0.24106 | 234.1186 | 56.4363 | 0.24106 | 234.1186 | 65.9747 | 0.2818 | 234.1186 | 9.914%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 42 | 25 | 316.4778 | 66.23% | 33.5% | 0.2671% | 12.4764 | 0 | 0 | 12.4764 | 0 | 10.8304 | 0.31718 | 34.1456 | 10.8304 | 0.31718 | 34.1456 | 12.6608 | 0.37079 | 34.1456 | 3.942%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 114 | 50 | 471.2015 | 74.37% | 25.17% | 0.4626% | 15.3697 | 0 | 0 | 15.3697 | 0 | 13.3419 | 0.63436 | 21.0319 | 13.3419 | 0.63436 | 21.0319 | 15.5969 | 0.74158 | 21.0319 | 3.262%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 161 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 98.1347 | 0 | 0 | 98.1347 | 0 | 85.1873 | 2.0427 | 41.7042 | 85.1873 | 2.0427 | 41.7042 | 99.585 | 2.3879 | 41.7042 | 5.692%
2028 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 29 | 29 | 183.5383 | 99.34% | 0.09556% | 0.5689% | 18.2319 | 0 | 0 | 18.2319 | 0 | 15.8265 | 0.36793 | 43.0147 | 15.8265 | 0.36793 | 43.0147 | 18.5013 | 0.43012 | 43.0147 | 9.934%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 9 | 9 | 6.6189 | 96.38% | 0% | 3.621% | 0.63793 | 0 | 0 | 0.63793 | 0 | 0.55376 | 0.11419 | 4.8497 | 0.55376 | 0.11419 | 4.8497 | 0.64736 | 0.13348 | 4.8497 | 9.638%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 84 | 973.0999 | 95.53% | 4.02% | 0.4464% | 41.537 | 0 | 0 | 41.537 | 0 | 36.0568 | 1.0657 | 33.8329 | 36.0568 | 1.0657 | 33.8329 | 42.1508 | 1.2459 | 33.8329 | 4.269%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 315 | 490.4615 | 96.36% | 1.259% | 2.378% | 44.3083 | 0 | 0 | 44.3083 | 0 | 38.4625 | 3.9965 | 9.624 | 38.4625 | 3.9965 | 9.624 | 44.963 | 4.6719 | 9.624 | 9.034%
2028 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 102 | 1 | 124.0064 | 98.52% | 0% | 1.478% | 0.11978 | 0 | 0 | 0.11978 | 0 | 0.10398 | 0.012687 | 8.1952 | 0.10398 | 0.012687 | 8.1952 | 0.12155 | 0.014832 | 8.1952 | 0.09659%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 16 | 1279.0443 | 99.78% | 0% | 0.2159% | 15.4701 | 0 | 0 | 15.4701 | 0 | 13.4291 | 0.203 | 66.1541 | 13.4291 | 0.203 | 66.1541 | 15.6987 | 0.23731 | 66.1541 | 1.21%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 106 | 2976.5734 | 99.75% | 0% | 0.2502% | 76.2052 | 0 | 0 | 76.2052 | 0 | 66.1511 | 1.3449 | 49.1883 | 66.1511 | 1.3449 | 49.1883 | 77.3314 | 1.5721 | 49.1883 | 2.56%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 345 | 8462.8018 | 99.74% | 0% | 0.2593% | 272.4132 | 0 | 0 | 272.4132 | 0 | 236.4724 | 4.3771 | 54.0247 | 236.4724 | 4.3771 | 54.0247 | 276.439 | 5.1169 | 54.0247 | 3.219%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 111 | 105 | 498.1496 | 90.1% | 9.186% | 0.7154% | 42.4564 | 0 | 0 | 42.4564 | 0 | 36.8549 | 1.3322 | 27.6654 | 36.8549 | 1.3322 | 27.6654 | 43.0839 | 1.5573 | 27.6654 | 8.523%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 221 | 193 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 77.7075 | 0 | 0 | 77.7075 | 0 | 67.4552 | 2.4486 | 27.548 | 67.4552 | 2.4486 | 27.548 | 78.8559 | 2.8625 | 27.548 | 7.487%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 77 | 72 | 170.5929 | 70.47% | 28.1% | 1.432% | 11.2414 | 0 | 0 | 11.2414 | 0 | 9.7583 | 0.91348 | 10.6825 | 9.7583 | 0.91348 | 10.6825 | 11.4076 | 1.0679 | 10.6825 | 6.59%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 95 | 71 | 317.7725 | 50.82% | 48.53% | 0.6462% | 12.0704 | 0 | 0 | 12.0704 | 0 | 10.4779 | 0.9008 | 11.6318 | 10.4779 | 0.9008 | 11.6318 | 12.2488 | 1.053 | 11.6318 | 3.798%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 293 | 259 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 94.894 | 0 | 0 | 94.894 | 0 | 82.3742 | 3.286 | 25.0682 | 82.3742 | 3.286 | 25.0682 | 96.2964 | 3.8414 | 25.0682 | 7.91%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 361 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 131.0591 | 0 | 0 | 131.0591 | 0 | 113.7678 | 4.5801 | 24.8395 | 113.7678 | 4.5801 | 24.8395 | 132.9959 | 5.3542 | 24.8395 | 7.243%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 279 | 252 | 1890.633 | 91.06% | 8.49% | 0.4466% | 155.5063 | 0 | 0 | 155.5063 | 0 | 134.9896 | 3.1972 | 42.2212 | 134.9896 | 3.1972 | 42.2212 | 157.8044 | 3.7376 | 42.2212 | 8.225%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 287 | 250 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 144.5469 | 0 | 0 | 144.5469 | 0 | 125.4761 | 3.1718 | 39.5596 | 125.4761 | 3.1718 | 39.5596 | 146.683 | 3.7079 | 39.5596 | 8.312%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 219 | 185 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 125.9884 | 0 | 0 | 125.9884 | 0 | 109.3662 | 2.3471 | 46.5953 | 109.3662 | 2.3471 | 46.5953 | 127.8503 | 2.7438 | 46.5953 | 8.023%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 79 | 77 | 609.7797 | 99.07% | 0.4924% | 0.4406% | 58.8797 | 0 | 0 | 58.8797 | 0 | 51.1114 | 0.97692 | 52.3189 | 51.1114 | 0.97692 | 52.3189 | 59.7499 | 1.142 | 52.3189 | 9.656%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 218 | 186 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 413.4942 | 0 | 0 | 413.4942 | 0 | 358.9399 | 2.3598 | 152.1037 | 358.9399 | 2.3598 | 152.1037 | 419.6048 | 2.7587 | 152.1037 | 8.46%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 273 | 259 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 117.6038 | 0 | 0 | 117.6038 | 0 | 102.0878 | 3.286 | 31.0674 | 102.0878 | 3.286 | 31.0674 | 119.3418 | 3.8414 | 31.0674 | 9.29%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 201 | 179 | 998.7912 | 96.62% | 2.787% | 0.5903% | 85.9427 | 0 | 0 | 85.9427 | 0 | 74.6039 | 2.271 | 32.8503 | 74.6039 | 2.271 | 32.8503 | 87.2128 | 2.6549 | 32.8503 | 8.605%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 71 | 66 | 261.4279 | 97.06% | 2.12% | 0.8249% | 23.5861 | 0 | 0 | 23.5861 | 0 | 20.4743 | 0.83736 | 24.451 | 20.4743 | 0.83736 | 24.451 | 23.9347 | 0.97888 | 24.451 | 9.022%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 201 | 183 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 131.2891 | 0 | 0 | 131.2891 | 0 | 113.9675 | 2.3218 | 49.0864 | 113.9675 | 2.3218 | 49.0864 | 133.2293 | 2.7142 | 49.0864 | 8.856%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 234 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 208.1629 | 0 | 0 | 208.1629 | 0 | 180.6989 | 2.9688 | 60.8655 | 180.6989 | 2.9688 | 60.8655 | 211.2391 | 3.4706 | 60.8655 | 7.546%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 115 | 105 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 92.115 | 0 | 0 | 92.115 | 0 | 79.9618 | 1.3322 | 60.0239 | 79.9618 | 1.3322 | 60.0239 | 93.4763 | 1.5573 | 60.0239 | 8.867%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 31 | 29 | 104.9439 | 97.78% | 1.295% | 0.9224% | 9.5996 | 0 | 0 | 9.5996 | 0 | 8.3331 | 0.36793 | 22.6485 | 8.3331 | 0.36793 | 22.6485 | 9.7415 | 0.43012 | 22.6485 | 9.147%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 155 | 151 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 208.0708 | 0 | 0 | 208.0708 | 0 | 180.619 | 1.9158 | 94.2796 | 180.619 | 1.9158 | 94.2796 | 211.1457 | 2.2396 | 94.2796 | 9.617%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 147 | 133 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 130.1927 | 0 | 0 | 130.1927 | 0 | 113.0158 | 1.6874 | 66.9759 | 113.0158 | 1.6874 | 66.9759 | 132.1167 | 1.9726 | 66.9759 | 8.85%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 377 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 2197.2181 | 0 | 0 | 2197.2181 | 0 | 1907.3285 | 4.7831 | 398.7634 | 1907.3285 | 4.7831 | 398.7634 | 2229.6888 | 5.5915 | 398.7634 | 8.36%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 248 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 576.6978 | 0 | 0 | 576.6978 | 0 | 500.6113 | 3.1464 | 159.1036 | 500.6113 | 3.1464 | 159.1036 | 585.2203 | 3.6782 | 159.1036 | 8.65%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 157 | 155 | 484.0355 | 97.4% | 1.48% | 1.12% | 46.5447 | 0 | 0 | 46.5447 | 0 | 40.4038 | 1.9665 | 20.5457 | 40.4038 | 1.9665 | 20.5457 | 47.2325 | 2.2989 | 20.5457 | 9.616%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 94 | 89 | 400.1895 | 97.86% | 1.359% | 0.7809% | 37.0794 | 0 | 0 | 37.0794 | 0 | 32.1873 | 1.1292 | 28.5053 | 32.1873 | 1.1292 | 28.5053 | 37.6273 | 1.32 | 28.5053 | 9.265%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 70 | 60 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 43.4342 | 0 | 0 | 43.4342 | 0 | 37.7037 | 0.76124 | 49.5295 | 37.7037 | 0.76124 | 49.5295 | 44.0761 | 0.8899 | 49.5295 | 8.461%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 150 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 188.6471 | 0 | 0 | 188.6471 | 0 | 163.758 | 1.9031 | 86.0483 | 163.758 | 1.9031 | 86.0483 | 191.435 | 2.2247 | 86.0483 | 8.543%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 160 | 1721.769 | 85.69% | 14.07% | 0.2459% | 120.4361 | 0 | 0 | 120.4361 | 0 | 104.5464 | 2.03 | 51.5015 | 104.5464 | 2.03 | 51.5015 | 122.2159 | 2.3731 | 51.5015 | 6.995%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 264 | 206 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1731.1083 | 0 | 0 | 1731.1083 | 0 | 1502.7149 | 2.6136 | 574.9638 | 1502.7149 | 2.6136 | 574.9638 | 1756.6908 | 3.0553 | 574.9638 | 7.744%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 205 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 999.0205 | 0 | 0 | 999.0205 | 0 | 867.2149 | 2.6009 | 333.4295 | 867.2149 | 2.6009 | 333.4295 | 1013.7841 | 3.0405 | 333.4295 | 7.865%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 193 | 19489.7064 | 99% | 0.9737% | 0.02962% | 1532.4175 | 0 | 0 | 1532.4175 | 0 | 1330.2383 | 2.4486 | 543.2544 | 1330.2383 | 2.4486 | 543.2544 | 1555.0637 | 2.8625 | 543.2544 | 7.863%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 50 | 1412.4296 | 98.09% | 1.785% | 0.1216% | 130.7071 | 0 | 0 | 130.7071 | 0 | 113.4623 | 0.63436 | 178.8597 | 113.4623 | 0.63436 | 178.8597 | 132.6387 | 0.74158 | 178.8597 | 9.254%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 117 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 499.1945 | 0 | 0 | 499.1945 | 0 | 433.3334 | 1.4844 | 291.9224 | 433.3334 | 1.4844 | 291.9224 | 506.5716 | 1.7353 | 291.9224 | 9.185%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 195 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 1013.3363 | 0 | 0 | 1013.3363 | 0 | 879.642 | 2.474 | 355.5514 | 879.642 | 2.474 | 355.5514 | 1028.3115 | 2.8922 | 355.5514 | 7.217%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 71.2816 | 99.9% | 0% | 0.09987% | 7.121 | 0 | 0 | 7.121 | 0 | 6.1815 | 0.025375 | 243.6109 | 6.1815 | 0.025375 | 243.6109 | 7.2263 | 0.029663 | 243.6109 | 9.99%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 333 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 131.2012 | 0 | 0 | 131.2012 | 0 | 113.8912 | 4.2249 | 26.9573 | 113.8912 | 4.2249 | 26.9573 | 133.1401 | 4.9389 | 26.9573 | 6.516%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 306 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 213.1484 | 0 | 0 | 213.1484 | 0 | 185.0267 | 3.8823 | 47.6589 | 185.0267 | 3.8823 | 47.6589 | 216.2983 | 4.5385 | 47.6589 | 7.815%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 297 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 981.8904 | 0 | 0 | 981.8904 | 0 | 852.3448 | 3.7681 | 226.1986 | 852.3448 | 3.7681 | 226.1986 | 996.4008 | 4.405 | 226.1986 | 9.188%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 247 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 291.8358 | 0 | 0 | 291.8358 | 0 | 253.3325 | 3.1338 | 80.8398 | 253.3325 | 3.1338 | 80.8398 | 296.1486 | 3.6634 | 80.8398 | 7.98%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 217 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 110.8226 | 0 | 0 | 110.8226 | 0 | 96.2012 | 2.7531 | 34.9423 | 96.2012 | 2.7531 | 34.9423 | 112.4603 | 3.2185 | 34.9423 | 7.703%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 116 | 114 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 984.8031 | 0 | 0 | 984.8031 | 0 | 854.8733 | 1.4464 | 591.0552 | 854.8733 | 1.4464 | 591.0552 | 999.3566 | 1.6908 | 591.0552 | 9.734%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 132 | 111 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 178.116 | 0 | 0 | 178.116 | 0 | 154.6163 | 1.4083 | 109.7902 | 154.6163 | 1.4083 | 109.7902 | 180.7483 | 1.6463 | 109.7902 | 8.101%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 272 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 134.619 | 0 | 0 | 134.619 | 0 | 116.8581 | 3.4509 | 33.8626 | 116.8581 | 3.4509 | 33.8626 | 136.6084 | 4.0342 | 33.8626 | 6.99%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 614 | 616 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 321.491 | 0 | 0 | 321.491 | 0 | 279.0752 | 7.8154 | 35.7085 | 279.0752 | 7.8154 | 35.7085 | 326.2421 | 9.1363 | 35.7085 | 8.966%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 97 | 54 | 3690.9623 | 99.91% | 0% | 0.09183% | 205.2876 | 0 | 0 | 205.2876 | 0 | 178.203 | 0.68511 | 260.1072 | 178.203 | 0.68511 | 260.1072 | 208.3213 | 0.80091 | 260.1072 | 5.562%
2028 | 221 | 221-1236F | Tier-3 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.012687 | 0 | 0 | 0.012687 | 0 | 0 | 0.014832 | 0 | 0%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 307 | 168 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 164.9318 | 0 | 0 | 164.9318 | 0 | 143.1716 | 2.1315 | 67.1705 | 143.1716 | 2.1315 | 67.1705 | 167.3692 | 2.4917 | 67.1705 | 5.043%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 293 | 223 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 200.1253 | 0 | 0 | 200.1253 | 0 | 173.7218 | 2.8293 | 61.4017 | 173.7218 | 2.8293 | 61.4017 | 203.0828 | 3.3074 | 61.4017 | 7.315%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 13 | 13 | 710.3273 | 99.46% | 0.4791% | 0.06249% | 70.648 | 0 | 0 | 70.648 | 0 | 61.3271 | 0.16493 | 371.8262 | 61.3271 | 0.16493 | 371.8262 | 71.692 | 0.19281 | 371.8262 | 9.946%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 244 | 151 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 236.2624 | 0 | 0 | 236.2624 | 0 | 205.0911 | 1.9158 | 107.0535 | 205.0911 | 1.9158 | 107.0535 | 239.7539 | 2.2396 | 107.0535 | 6.004%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 18 | 26 | 318.0967 | 33.4% | 66.33% | 0.2755% | 15.3453 | 0 | 0 | 15.3453 | 0 | 13.3208 | 0.32987 | 40.3819 | 13.3208 | 0.32987 | 40.3819 | 15.5721 | 0.38562 | 40.3819 | 4.824%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 99 | 76 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 157.0165 | 0 | 0 | 157.0165 | 0 | 136.3005 | 0.96423 | 141.3563 | 136.3005 | 0.96423 | 141.3563 | 159.3369 | 1.1272 | 141.3563 | 7.639%
2028 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 100 | 91 | 3904.259 | 99.88% | 0.03221% | 0.0896% | 354.8548 | 0 | 0 | 354.8548 | 0 | 308.0371 | 1.1545 | 266.8042 | 308.0371 | 1.1545 | 266.8042 | 360.0989 | 1.3497 | 266.8042 | 9.089%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | Tier-3---5 | 93 | 93 | 618.0174 | 98.68% | 0.7939% | 0.5237% | 60.9875 | 0 | 0 | 60.9875 | 0 | 52.9411 | 1.1799 | 44.8684 | 52.9411 | 1.1799 | 44.8684 | 61.8887 | 1.3793 | 44.8684 | 9.868%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 67 | 55 | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 365.8842 | 0 | 0 | 365.8842 | 0 | 317.6114 | 0.6978 | 455.1604 | 317.6114 | 0.6978 | 455.1604 | 371.2913 | 0.81574 | 455.1604 | 8.164%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 106 | 68 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 144.4234 | 0 | 0 | 144.4234 | 0 | 125.369 | 0.86274 | 145.3156 | 125.369 | 0.86274 | 145.3156 | 146.5577 | 1.0085 | 145.3156 | 6.214%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 123 | 107 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 833.2729 | 0 | 0 | 833.2729 | 0 | 723.3352 | 1.3575 | 532.8279 | 723.3352 | 1.3575 | 532.8279 | 845.5871 | 1.587 | 532.8279 | 8.664%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 76 | 57 | 1359.3953 | 95.15% | 4.696% | 0.1502% | 97.0139 | 0 | 0 | 97.0139 | 0 | 84.2144 | 0.72318 | 116.4508 | 84.2144 | 0.72318 | 116.4508 | 98.4476 | 0.8454 | 116.4508 | 7.137%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 367 | 257 | 7406.689 | 96.62% | 3.25% | 0.1263% | 501.1579 | 0 | 0 | 501.1579 | 0 | 435.0377 | 3.2606 | 133.4212 | 435.0377 | 3.2606 | 133.4212 | 508.5641 | 3.8117 | 133.4212 | 6.766%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 451 | 389 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 6779.655 | 0 | 0 | 6779.655 | 0 | 5885.1824 | 4.9354 | 1192.4535 | 5885.1824 | 4.9354 | 1192.4535 | 6879.8453 | 5.7695 | 1192.4535 | 8.561%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 18 | 17 | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 339.3326 | 0 | 0 | 339.3326 | 0 | 294.5628 | 0.21568 | 1365.7152 | 294.5628 | 0.21568 | 1365.7152 | 344.3473 | 0.25214 | 1365.7152 | 9.375%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 287 | 246 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 3851.9498 | 0 | 0 | 3851.9498 | 0 | 3343.7435 | 3.1211 | 1071.344 | 3343.7435 | 3.1211 | 1071.344 | 3908.8743 | 3.6486 | 1071.344 | 8.54%
2028 | 220 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 43 | 18 | 288.7705 | 86.56% | 13.18% | 0.2657% | 10.463 | 0 | 0 | 10.463 | 0 | 9.0826 | 0.22837 | 39.771 | 9.0826 | 0.22837 | 39.771 | 10.6176 | 0.26697 | 39.771 | 3.623%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 407 | 288 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 504.7808 | 0 | 0 | 504.7808 | 0 | 438.1826 | 3.6539 | 119.9206 | 438.1826 | 3.6539 | 119.9206 | 512.2405 | 4.2715 | 119.9206 | 6.797%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | Tier-3---1 | 79 | 75 | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 460.682 | 0 | 0 | 460.682 | 0 | 399.902 | 0.95155 | 420.2652 | 399.902 | 0.95155 | 420.2652 | 467.49 | 1.1124 | 420.2652 | 9.479%
2028 | 221 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 910 | 544 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 969.5191 | 0 | 0 | 969.5191 | 0 | 841.6058 | 6.9019 | 121.9385 | 841.6058 | 6.9019 | 121.9385 | 983.8468 | 8.0684 | 121.9385 | 5.78%
2028 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 5 | 17.3686 | 98.33% | 0% | 1.666% | 1.0675 | 0 | 0 | 1.0675 | 0 | 0.92662 | 0.063436 | 14.607 | 0.92662 | 0.063436 | 14.607 | 1.0832 | 0.074158 | 14.607 | 6.146%
2028 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 9 | 9 | 171.5883 | 99.37% | 0.4538% | 0.1789% | 17.0503 | 0 | 0 | 17.0503 | 0 | 14.8007 | 0.11419 | 129.6199 | 14.8007 | 0.11419 | 129.6199 | 17.3022 | 0.13348 | 129.6199 | 9.937%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 213 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 150.4557 | 0 | 0 | 150.4557 | 0 | 130.6053 | 2.7024 | 48.3295 | 130.6053 | 2.7024 | 48.3295 | 152.6791 | 3.1591 | 48.3295 | 7.521%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 328 | 221 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 422.9789 | 0 | 0 | 422.9789 | 0 | 367.1733 | 2.8039 | 130.9513 | 367.1733 | 2.8039 | 130.9513 | 429.2297 | 3.2778 | 130.9513 | 6.621%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 245 | 177 | 2072.8837 | 91.06% | 8.635% | 0.3% | 136.3741 | 0 | 0 | 136.3741 | 0 | 118.3816 | 2.2457 | 52.716 | 118.3816 | 2.2457 | 52.716 | 138.3895 | 2.6252 | 52.716 | 6.579%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 71 | 51 | 536.3838 | 78.97% | 20.71% | 0.32% | 30.4256 | 0 | 0 | 30.4256 | 0 | 26.4114 | 0.64705 | 40.8181 | 26.4114 | 0.64705 | 40.8181 | 30.8752 | 0.75641 | 40.8181 | 5.672%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 52 | 38 | 788.7224 | 98.19% | 1.606% | 0.2041% | 56.5939 | 0 | 0 | 56.5939 | 0 | 49.1272 | 0.48212 | 101.899 | 49.1272 | 0.48212 | 101.899 | 57.4303 | 0.5636 | 101.899 | 7.175%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 183 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 263.0824 | 0 | 0 | 263.0824 | 0 | 228.3727 | 2.3218 | 98.3613 | 228.3727 | 2.3218 | 98.3613 | 266.9703 | 2.7142 | 98.3613 | 7.574%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 6 | 121.6067 | 92.98% | 6.845% | 0.1786% | 11.3066 | 0 | 0 | 11.3066 | 0 | 9.8148 | 0.076124 | 128.9325 | 9.8148 | 0.076124 | 128.9325 | 11.4736 | 0.08899 | 128.9325 | 9.298%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 41 | 29 | 195.7251 | 81.71% | 17.81% | 0.4804% | 11.3124 | 0 | 0 | 11.3124 | 0 | 9.8199 | 0.36793 | 26.6896 | 9.8199 | 0.36793 | 26.6896 | 11.4796 | 0.43012 | 26.6896 | 5.78%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 245 | 2730.9177 | 98.3% | 1.373% | 0.325% | 184.2332 | 0 | 0 | 184.2332 | 0 | 159.9265 | 3.1084 | 51.45 | 159.9265 | 3.1084 | 51.45 | 186.9559 | 3.6337 | 51.45 | 6.746%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 613 | 5142.095 | 98.68% | 0.901% | 0.4182% | 360.8495 | 0 | 0 | 360.8495 | 0 | 313.2409 | 7.7773 | 40.2763 | 313.2409 | 7.7773 | 40.2763 | 366.1821 | 9.0918 | 40.2763 | 7.018%
2028 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 5 | 4 | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0041361 | 0 | 0 | 0.0041361 | 0 | 0.0035904 | 0.050749 | 0.070748 | 0.0035904 | 0.050749 | 0.070748 | 0.0041972 | 0.059326 | 0.070748 | 0.03619%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 292 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 212.6612 | 0 | 0 | 212.6612 | 0 | 184.6038 | 3.7047 | 49.8298 | 184.6038 | 3.7047 | 49.8298 | 215.8039 | 4.3308 | 49.8298 | 7.005%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 222 | 718.991 | 97.57% | 1.357% | 1.072% | 57.0469 | 0 | 0 | 57.0469 | 0 | 49.5204 | 2.8166 | 17.5818 | 49.5204 | 2.8166 | 17.5818 | 57.8899 | 3.2926 | 17.5818 | 7.934%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 89 | 447.7794 | 94.96% | 4.349% | 0.694% | 38.225 | 0 | 0 | 38.225 | 0 | 33.1818 | 1.1292 | 29.386 | 33.1818 | 1.1292 | 29.386 | 38.7899 | 1.32 | 29.386 | 8.537%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 327 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 159.6551 | 0 | 0 | 159.6551 | 0 | 138.591 | 4.1487 | 33.4055 | 138.591 | 4.1487 | 33.4055 | 162.0145 | 4.8499 | 33.4055 | 6.818%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 216 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 317.6971 | 0 | 0 | 317.6971 | 0 | 275.7818 | 2.7405 | 100.6336 | 275.7818 | 2.7405 | 100.6336 | 322.3921 | 3.2036 | 100.6336 | 6.432%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 130 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 209.157 | 0 | 0 | 209.157 | 0 | 181.5619 | 1.6493 | 110.081 | 181.5619 | 1.6493 | 110.081 | 212.2479 | 1.9281 | 110.081 | 4.781%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 270 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1184.3293 | 0 | 0 | 1184.3293 | 0 | 1028.075 | 3.4256 | 300.1181 | 1028.075 | 3.4256 | 300.1181 | 1201.8314 | 4.0045 | 300.1181 | 5.002%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 252 | 162 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 616.8774 | 0 | 0 | 616.8774 | 0 | 535.4898 | 2.0553 | 260.5357 | 535.4898 | 2.0553 | 260.5357 | 625.9937 | 2.4027 | 260.5357 | 6.347%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 137 | 97 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 194.444 | 0 | 0 | 194.444 | 0 | 168.7901 | 1.2307 | 137.1533 | 168.7901 | 1.2307 | 137.1533 | 197.3175 | 1.4387 | 137.1533 | 6.886%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 81 | 69 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 189.8927 | 0 | 0 | 189.8927 | 0 | 164.8393 | 0.87542 | 188.2967 | 164.8393 | 0.87542 | 188.2967 | 192.699 | 1.0234 | 188.2967 | 8.4%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 171 | 127 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 388.3774 | 0 | 0 | 388.3774 | 0 | 337.1369 | 1.6113 | 209.2347 | 337.1369 | 1.6113 | 209.2347 | 394.1169 | 1.8836 | 209.2347 | 7.284%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 498 | 306 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1282.7226 | 0 | 0 | 1282.7226 | 0 | 1113.4868 | 3.8823 | 286.8103 | 1113.4868 | 3.8823 | 286.8103 | 1301.6788 | 4.5385 | 286.8103 | 6.044%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 192 | 130 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 458.9623 | 0 | 0 | 458.9623 | 0 | 398.4092 | 1.6493 | 241.5556 | 398.4092 | 1.6493 | 241.5556 | 465.7449 | 1.9281 | 241.5556 | 6.625%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 126 | 113 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 323.9509 | 0 | 0 | 323.9509 | 0 | 281.2105 | 1.4337 | 196.1482 | 281.2105 | 1.4337 | 196.1482 | 328.7383 | 1.676 | 196.1482 | 8.914%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 223 | 158 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1988.3938 | 0 | 0 | 1988.3938 | 0 | 1726.0554 | 2.0046 | 861.0508 | 1726.0554 | 2.0046 | 861.0508 | 2017.7785 | 2.3434 | 861.0508 | 7.039%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 275 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1374.0091 | 0 | 0 | 1374.0091 | 0 | 1192.7294 | 3.489 | 341.8538 | 1192.7294 | 3.489 | 341.8538 | 1394.3143 | 4.0787 | 341.8538 | 5.074%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 46 | 663.2151 | 70.89% | 28.72% | 0.399% | 19.1377 | 0 | 0 | 19.1377 | 0 | 16.6128 | 0.58362 | 28.4652 | 16.6128 | 0.58362 | 28.4652 | 19.4205 | 0.68225 | 28.4652 | 2.886%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 59 | 29 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 122.9074 | 0 | 0 | 122.9074 | 0 | 106.6916 | 0.36793 | 289.977 | 106.6916 | 0.36793 | 289.977 | 124.7237 | 0.43012 | 289.977 | 4.858%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 499 | 344 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 2110.859 | 0 | 0 | 2110.859 | 0 | 1832.3632 | 4.3644 | 419.8404 | 1832.3632 | 4.3644 | 419.8404 | 2142.0535 | 5.1021 | 419.8404 | 6.833%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 651 | 565 | 65515.492 | 98.93% | 1.038% | 0.03019% | 5625.3221 | 0 | 0 | 5625.3221 | 0 | 4883.1463 | 7.1683 | 681.2122 | 4883.1463 | 7.1683 | 681.2122 | 5708.4537 | 8.3798 | 681.2122 | 8.586%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 110 | 860.3234 | 98.08% | 1.495% | 0.4234% | 73.0864 | 0 | 0 | 73.0864 | 0 | 63.4437 | 1.3956 | 45.4598 | 63.4437 | 1.3956 | 45.4598 | 74.1664 | 1.6315 | 45.4598 | 8.495%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 50 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 142.1904 | 0 | 0 | 142.1904 | 0 | 123.4305 | 0.63436 | 194.5735 | 123.4305 | 0.63436 | 194.5735 | 144.2917 | 0.74158 | 194.5735 | 8.97%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 134 | 111 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 89.2076 | 0 | 0 | 89.2076 | 0 | 77.438 | 1.4083 | 54.9873 | 77.438 | 1.4083 | 54.9873 | 90.526 | 1.6463 | 54.9873 | 7.99%
2028 | 1233 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 250 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 504.7804 | 0 | 0 | 504.7804 | 0 | 438.1823 | 3.1718 | 138.1484 | 438.1823 | 3.1718 | 138.1484 | 512.2401 | 3.7079 | 138.1484 | 8.052%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 101 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 66.6975 | 0 | 0 | 66.6975 | 0 | 57.8978 | 1.2814 | 45.1827 | 57.8978 | 1.2814 | 45.1827 | 67.6832 | 1.498 | 45.1827 | 6.478%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 52 | 38 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 27.166 | 0 | 0 | 27.166 | 0 | 23.5818 | 0.48212 | 48.9131 | 23.5818 | 0.48212 | 48.9131 | 27.5674 | 0.5636 | 48.9131 | 7.217%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 165 | 99 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 69.7467 | 0 | 0 | 69.7467 | 0 | 60.5447 | 1.256 | 48.2028 | 60.5447 | 1.256 | 48.2028 | 70.7775 | 1.4683 | 48.2028 | 5.903%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 71 | 40 | 791.3356 | 98.7% | 1.112% | 0.1837% | 44.0048 | 0 | 0 | 44.0048 | 0 | 38.199 | 0.50749 | 75.2703 | 38.199 | 0.50749 | 75.2703 | 44.6551 | 0.59326 | 75.2703 | 5.561%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 75 | 64 | 376.72 | 96.88% | 2.523% | 0.5996% | 31.143 | 0 | 0 | 31.143 | 0 | 27.0341 | 0.81199 | 33.2938 | 27.0341 | 0.81199 | 33.2938 | 31.6032 | 0.94922 | 33.2938 | 8.267%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 363 | 4437.6588 | 97.91% | 1.769% | 0.321% | 253.1626 | 0 | 0 | 253.1626 | 0 | 219.7616 | 4.6055 | 47.7174 | 219.7616 | 4.6055 | 47.7174 | 256.9039 | 5.3839 | 47.7174 | 5.705%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 269 | 189 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 260.4973 | 0 | 0 | 260.4973 | 0 | 226.1287 | 2.3979 | 94.3029 | 226.1287 | 2.3979 | 94.3029 | 264.347 | 2.8032 | 94.3029 | 6.96%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 265 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 273.401 | 0 | 0 | 273.401 | 0 | 237.3299 | 3.3621 | 70.5891 | 237.3299 | 3.3621 | 70.5891 | 277.4413 | 3.9304 | 70.5891 | 7.458%
2028 | 240 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 56 | 960.3446 | 65.96% | 33.81% | 0.2324% | 30.3183 | 0 | 0 | 30.3183 | 0 | 26.3182 | 0.71049 | 37.0425 | 26.3182 | 0.71049 | 37.0425 | 30.7663 | 0.83057 | 37.0425 | 3.157%
2028 | 242 | 242-1427F | Tier-2 | Tier-2---20 | Tier-2---19 | 5 | 3 | 24.991 | 71.07% | 28.66% | 0.2708% | 1.0657 | 0 | 0 | 1.0657 | 0 | 0.92509 | 0.038062 | 24.305 | 0.92509 | 0.038062 | 24.305 | 1.0814 | 0.044495 | 24.305 | 4.264%
2028 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 470 | 1 | 404.2589 | 29.5% | 68.39% | 2.113% | 0.025372 | 0 | 0 | 0.025372 | 0 | 0.022025 | 0.012687 | 1.736 | 0.022025 | 0.012687 | 1.736 | 0.025747 | 0.014832 | 1.736 | 0.006276%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 310 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 227.682 | 0 | 0 | 227.682 | 0 | 197.6428 | 3.9331 | 50.2517 | 197.6428 | 3.9331 | 50.2517 | 231.0467 | 4.5978 | 50.2517 | 6.722%
2028 | 246 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 161 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 89.2584 | 0 | 0 | 89.2584 | 0 | 77.4821 | 2.0427 | 37.9321 | 77.4821 | 2.0427 | 37.9321 | 90.5775 | 2.3879 | 37.9321 | 6.562%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 9 | 9 | 105.2026 | 98.18% | 1.532% | 0.2854% | 10.3291 | 0 | 0 | 10.3291 | 0 | 8.9663 | 0.11419 | 78.5241 | 8.9663 | 0.11419 | 78.5241 | 10.4817 | 0.13348 | 78.5241 | 9.818%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 292 | 3753.23 | 95.85% | 3.876% | 0.273% | 226.3951 | 0 | 0 | 226.3951 | 0 | 196.5257 | 3.7047 | 53.0478 | 196.5257 | 3.7047 | 53.0478 | 229.7408 | 4.3308 | 53.0478 | 6.032%
2028 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 98 | 86 | 49.4853 | 86.66% | 6.71% | 6.626% | 3.7635 | 0 | 0 | 3.7635 | 0 | 3.2669 | 1.0911 | 2.9942 | 3.2669 | 1.0911 | 2.9942 | 3.8191 | 1.2755 | 2.9942 | 7.605%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 96 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 460.0093 | 0 | 0 | 460.0093 | 0 | 399.3181 | 1.218 | 327.8528 | 399.3181 | 1.218 | 327.8528 | 466.8074 | 1.4238 | 327.8528 | 8.68%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 112 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 155.9138 | 0 | 0 | 155.9138 | 0 | 135.3433 | 1.421 | 95.2467 | 135.3433 | 1.421 | 95.2467 | 158.2179 | 1.6611 | 95.2467 | 7.743%
2028 | 283 | 283-80F | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 2 | 22.6843 | 50.28% | 49.56% | 0.1579% | 1.1406 | 0 | 0 | 1.1406 | 0 | 0.99014 | 0.025375 | 39.0209 | 0.99014 | 0.025375 | 39.0209 | 1.1575 | 0.029663 | 39.0209 | 5.028%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 170 | 2 | 481.2843 | 94.31% | 4.95% | 0.7414% | 0.53399 | 0 | 0 | 0.53399 | 0 | 0.46354 | 0.025375 | 18.2678 | 0.46354 | 0.025375 | 18.2678 | 0.54188 | 0.029663 | 18.2678 | 0.111%
2028 | 288 | 288-2375R | Tier-2 | Tier-2---19 | Tier-2---13 | 7 | 2 | 41.8014 | 98.23% | 1.253% | 0.5152% | 1.1732 | 0 | 0 | 1.1732 | 0 | 1.0184 | 0.025375 | 40.1354 | 1.0184 | 0.025375 | 40.1354 | 1.1905 | 0.029663 | 40.1354 | 2.807%
2028 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 34 | 550.61 | 92.88% | 6.93% | 0.1872% | 40.4378 | 0 | 0 | 40.4378 | 0 | 35.1027 | 0.43137 | 81.3752 | 35.1027 | 0.43137 | 81.3752 | 41.0354 | 0.50427 | 81.3752 | 7.344%
2028 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 43 | 29 | 3.2301 | 78.97% | 0% | 21.03% | 0.17202 | 0 | 0 | 0.17202 | 0 | 0.14933 | 0.36793 | 0.40586 | 0.14933 | 0.36793 | 0.40586 | 0.17457 | 0.43012 | 0.40586 | 5.326%
2028 | 198 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 68 | 458.7821 | 99.48% | 0% | 0.5194% | 44.9785 | 0 | 0 | 44.9785 | 0 | 39.0443 | 0.86274 | 45.2563 | 39.0443 | 0.86274 | 45.2563 | 45.6432 | 1.0085 | 45.2563 | 9.804%
2028 | 231 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 194 | 754.1323 | 92.41% | 6.882% | 0.7076% | 54.0793 | 0 | 0 | 54.0793 | 0 | 46.9444 | 2.4613 | 19.0727 | 46.9444 | 2.4613 | 19.0727 | 54.8785 | 2.8773 | 19.0727 | 7.171%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 49 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 202.683 | 0 | 0 | 202.683 | 0 | 175.942 | 0.62168 | 283.0119 | 175.942 | 0.62168 | 283.0119 | 205.6782 | 0.72675 | 283.0119 | 8.42%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 86 | 4762.848 | 95.55% | 4.384% | 0.07015% | 359.046 | 0 | 0 | 359.046 | 0 | 311.6753 | 1.0911 | 285.6505 | 311.6753 | 1.0911 | 285.6505 | 364.352 | 1.2755 | 285.6505 | 7.538%
2028 | 308 | 308-486AE | Tier-2 | Tier-2---16 | Tier-2---8 | 142 | 1 | 164.6778 | 2.383% | 96.2% | 1.419% | 0.002764 | 0 | 0 | 0.002764 | 0 | 0.0023994 | 0.012687 | 0.18911 | 0.0023994 | 0.012687 | 0.18911 | 0.0028049 | 0.014832 | 0.18911 | 0.001678%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 39 | 14 | 95.5263 | 19.37% | 79.9% | 0.729% | 0.66438 | 0 | 0 | 0.66438 | 0 | 0.57672 | 0.17762 | 3.2469 | 0.57672 | 0.17762 | 3.2469 | 0.6742 | 0.20764 | 3.2469 | 0.6955%
2028 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 14 | 7 | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9562 | 0 | 0 | 1.9562 | 0 | 1.6981 | 0.088811 | 19.1204 | 1.6981 | 0.088811 | 19.1204 | 1.9851 | 0.10382 | 19.1204 | 4.235%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 15 | 12 | 15.6056 | 49.38% | 48.09% | 2.529% | 0.61652 | 0 | 0 | 0.61652 | 0 | 0.53518 | 0.15225 | 3.5152 | 0.53518 | 0.15225 | 3.5152 | 0.62564 | 0.17798 | 3.5152 | 3.951%
2028 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 12 | 278.652 | 16.28% | 83.57% | 0.1501% | 3.8883 | 0 | 0 | 3.8883 | 0 | 3.3753 | 0.15225 | 22.17 | 3.3753 | 0.15225 | 22.17 | 3.9458 | 0.17798 | 22.17 | 1.395%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 79 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.15148 | 0 | 0 | 0.15148 | 0 | 0.1315 | 1.0023 | 0.13119 | 0.1315 | 1.0023 | 0.13119 | 0.15372 | 1.1717 | 0.13119 | 0.09476%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 15 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0086582 | 0 | 0 | 0.0086582 | 0 | 0.0075159 | 0.19031 | 0.039493 | 0.0075159 | 0.19031 | 0.039493 | 0.0087861 | 0.22247 | 0.039493 | 0.004284%
2028 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 9 | 9 | 14.6681 | 98.1% | 0% | 1.899% | 1.439 | 0 | 0 | 1.439 | 0 | 1.2491 | 0.11419 | 10.9393 | 1.2491 | 0.11419 | 10.9393 | 1.4602 | 0.13348 | 10.9393 | 9.81%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 39 | 34 | 209.8559 | 99.5% | 0% | 0.498% | 18.204 | 0 | 0 | 18.204 | 0 | 15.8023 | 0.43137 | 36.633 | 15.8023 | 0.43137 | 36.633 | 18.473 | 0.50427 | 36.633 | 8.675%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 15 | 8 | 302.428 | 99.27% | 0.6612% | 0.06922% | 16.0117 | 0 | 0 | 16.0117 | 0 | 13.8992 | 0.1015 | 136.9401 | 13.8992 | 0.1015 | 136.9401 | 16.2483 | 0.11865 | 136.9401 | 5.294%
2028 | 233 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 476 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 289.7593 | 0 | 0 | 289.7593 | 0 | 251.53 | 6.0392 | 41.6499 | 251.53 | 6.0392 | 41.6499 | 294.0414 | 7.0598 | 41.6499 | 8.044%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 709 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 1168.497 | 0 | 0 | 1168.497 | 0 | 1014.3316 | 8.9953 | 112.7625 | 1014.3316 | 8.9953 | 112.7625 | 1185.7652 | 10.5156 | 112.7625 | 8.424%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 711 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 476.0154 | 0 | 0 | 476.0154 | 0 | 413.2124 | 9.0207 | 45.8073 | 413.2124 | 9.0207 | 45.8073 | 483.05 | 10.5453 | 45.8073 | 8.545%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 297 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 1104.4919 | 0 | 0 | 1104.4919 | 0 | 958.7709 | 3.7681 | 254.4424 | 958.7709 | 3.7681 | 254.4424 | 1120.8141 | 4.405 | 254.4424 | 8.168%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 373 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 869.7107 | 0 | 0 | 869.7107 | 0 | 754.9656 | 4.7324 | 159.5326 | 754.9656 | 4.7324 | 159.5326 | 882.5633 | 5.5322 | 159.5326 | 7.764%
2028 | 1039 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 225 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1540.0982 | 0 | 0 | 1540.0982 | 0 | 1336.9056 | 2.8546 | 468.3272 | 1336.9056 | 2.8546 | 468.3272 | 1562.8579 | 3.3371 | 468.3272 | 6.549%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 83 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 688.1193 | 0 | 0 | 688.1193 | 0 | 597.3324 | 1.053 | 567.2429 | 597.3324 | 1.053 | 567.2429 | 698.2884 | 1.231 | 567.2429 | 7.525%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 279 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 1437.3667 | 0 | 0 | 1437.3667 | 0 | 1247.728 | 3.5398 | 352.49 | 1247.728 | 3.5398 | 352.49 | 1458.6083 | 4.138 | 352.49 | 7.722%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 161 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 709.5156 | 0 | 0 | 709.5156 | 0 | 615.9058 | 2.0427 | 301.5224 | 615.9058 | 2.0427 | 301.5224 | 720.0009 | 2.3879 | 301.5224 | 7.694%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 46 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 205.229 | 0 | 0 | 205.229 | 0 | 178.1521 | 0.58362 | 305.2561 | 178.1521 | 0.58362 | 305.2561 | 208.2619 | 0.68225 | 305.2561 | 8.147%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 25 | 25 | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 221.4151 | 0 | 0 | 221.4151 | 0 | 192.2028 | 0.31718 | 605.9695 | 192.2028 | 0.31718 | 605.9695 | 224.6872 | 0.37079 | 605.9695 | 9.993%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 28 | 25 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 157.6982 | 0 | 0 | 157.6982 | 0 | 136.8923 | 0.31718 | 431.5888 | 136.8923 | 0.31718 | 431.5888 | 160.0287 | 0.37079 | 431.5888 | 7.919%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 69 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 361.4968 | 0 | 0 | 361.4968 | 0 | 313.8028 | 0.87542 | 358.4584 | 313.8028 | 0.87542 | 358.4584 | 366.839 | 1.0234 | 358.4584 | 7.935%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 11 | 465.1006 | 62.84% | 37.09% | 0.07221% | 29.2268 | 0 | 0 | 29.2268 | 0 | 25.3708 | 0.13956 | 181.7909 | 25.3708 | 0.13956 | 181.7909 | 29.6587 | 0.16315 | 181.7909 | 6.284%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 147 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 1092.9655 | 0 | 0 | 1092.9655 | 0 | 948.7653 | 1.865 | 508.7127 | 948.7653 | 1.865 | 508.7127 | 1109.1174 | 2.1802 | 508.7127 | 8.075%
2028 | 350 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 327 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1382.7374 | 0 | 0 | 1382.7374 | 0 | 1200.3062 | 4.1487 | 289.318 | 1200.3062 | 4.1487 | 289.318 | 1403.1716 | 4.8499 | 289.318 | 6.742%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 75 | 3653.654 | 88.54% | 11.39% | 0.07412% | 272.5948 | 0 | 0 | 272.5948 | 0 | 236.6301 | 0.95155 | 248.6794 | 236.6301 | 0.95155 | 248.6794 | 276.6233 | 1.1124 | 248.6794 | 7.461%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 129 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 421.7122 | 0 | 0 | 421.7122 | 0 | 366.0737 | 1.6367 | 223.6711 | 366.0737 | 1.6367 | 223.6711 | 427.9443 | 1.9133 | 223.6711 | 5.622%
2028 | 355 | 355-65R | Tier-2 | Tier-2---21 | Tier-2---24 | 1 | 1 | 0.06699 | 46.11% | 0% | 53.89% | 0.0030886 | 0 | 0 | 0.0030886 | 0 | 0.0026811 | 0.012687 | 0.21132 | 0.0026811 | 0.012687 | 0.21132 | 0.0031343 | 0.014832 | 0.21132 | 4.611%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 58 | 35 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 81.9442 | 0 | 0 | 81.9442 | 0 | 71.1329 | 0.44406 | 160.1893 | 71.1329 | 0.44406 | 160.1893 | 83.1551 | 0.51911 | 160.1893 | 4.824%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 119 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 293.9946 | 0 | 0 | 293.9946 | 0 | 255.2065 | 1.5098 | 169.0347 | 255.2065 | 1.5098 | 169.0347 | 298.3393 | 1.765 | 169.0347 | 5.407%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 429 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 912.4735 | 0 | 0 | 912.4735 | 0 | 792.0865 | 5.4428 | 145.528 | 792.0865 | 5.4428 | 145.528 | 925.9581 | 6.3628 | 145.528 | 5.698%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 730 | 400 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 485.9291 | 0 | 0 | 485.9291 | 0 | 421.8181 | 5.0749 | 83.1182 | 421.8181 | 5.0749 | 83.1182 | 493.1102 | 5.9326 | 83.1182 | 5.228%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 40 | 22 | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 68.1695 | 0 | 0 | 68.1695 | 0 | 59.1756 | 0.27912 | 212.0073 | 59.1756 | 0.27912 | 212.0073 | 69.1769 | 0.32629 | 212.0073 | 5.448%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 48 | 44 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 465.8919 | 0 | 0 | 465.8919 | 0 | 404.4245 | 0.55824 | 724.4625 | 404.4245 | 0.55824 | 724.4625 | 472.7769 | 0.65259 | 724.4625 | 9.137%
2028 | 1458 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 17 | 10 | 878.9304 | 95.49% | 4.482% | 0.03213% | 49.3677 | 0 | 0 | 49.3677 | 0 | 42.8544 | 0.12687 | 337.7739 | 42.8544 | 0.12687 | 337.7739 | 50.0972 | 0.14832 | 337.7739 | 5.617%
2028 | 1458 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 141 | 16869.708 | 98.79% | 1.184% | 0.02933% | 867.0712 | 0 | 0 | 867.0712 | 0 | 752.6743 | 1.7889 | 420.7451 | 752.6743 | 1.7889 | 420.7451 | 879.8848 | 2.0913 | 420.7451 | 5.14%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 242 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 1149.9849 | 0 | 0 | 1149.9849 | 0 | 998.2618 | 3.0703 | 325.1324 | 998.2618 | 3.0703 | 325.1324 | 1166.9795 | 3.5892 | 325.1324 | 6.498%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 231 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 610.5815 | 0 | 0 | 610.5815 | 0 | 530.0246 | 2.9308 | 180.8486 | 530.0246 | 2.9308 | 180.8486 | 619.6048 | 3.4261 | 180.8486 | 5.853%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 172 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 727.1836 | 0 | 0 | 727.1836 | 0 | 631.2428 | 2.1822 | 289.2671 | 631.2428 | 2.1822 | 289.2671 | 737.93 | 2.551 | 289.2671 | 6.185%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 21 | 9 | 599.5834 | 97.21% | 2.746% | 0.04768% | 24.9785 | 0 | 0 | 24.9785 | 0 | 21.683 | 0.11419 | 189.8923 | 21.683 | 0.11419 | 189.8923 | 25.3476 | 0.13348 | 189.8923 | 4.166%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | Tier-3---3 | 14 | 13 | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 124.4356 | 0 | 0 | 124.4356 | 0 | 108.0182 | 0.16493 | 654.9149 | 108.0182 | 0.16493 | 654.9149 | 126.2746 | 0.19281 | 654.9149 | 9.254%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 344 | 227 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 2446.3909 | 0 | 0 | 2446.3909 | 0 | 2123.6268 | 2.88 | 737.3666 | 2123.6268 | 2.88 | 737.3666 | 2482.5439 | 3.3668 | 737.3666 | 6.506%
2028 | 283 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 140 | 38 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 35.1557 | 0 | 0 | 35.1557 | 0 | 30.5174 | 0.48212 | 63.2988 | 30.5174 | 0.48212 | 63.2988 | 35.6752 | 0.5636 | 63.2988 | 2.416%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 76 | 41 | 924.8041 | 18.79% | 81.02% | 0.1888% | 9.3732 | 0 | 0 | 9.3732 | 0 | 8.1365 | 0.52018 | 15.6418 | 8.1365 | 0.52018 | 15.6418 | 9.5117 | 0.6081 | 15.6418 | 1.014%
2028 | 1138 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 458 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 169.3729 | 0 | 0 | 169.3729 | 0 | 147.0267 | 5.8108 | 25.3024 | 147.0267 | 5.8108 | 25.3024 | 171.8759 | 6.7929 | 25.3024 | 5.399%
2028 | 401 | 401-684R | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 1 | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049818 | 0 | 0 | 0.049818 | 0 | 0.043245 | 0.012687 | 3.4085 | 0.043245 | 0.012687 | 3.4085 | 0.050554 | 0.014832 | 3.4085 | 3.121%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 193 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 102.5551 | 0 | 0 | 102.5551 | 0 | 89.0245 | 2.4486 | 36.3566 | 89.0245 | 2.4486 | 36.3566 | 104.0707 | 2.8625 | 36.3566 | 5.521%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 494 | 6370.0414 | 98.47% | 1.262% | 0.272% | 361.9772 | 0 | 0 | 361.9772 | 0 | 314.2198 | 6.2675 | 50.1346 | 314.2198 | 6.2675 | 50.1346 | 367.3266 | 7.3268 | 50.1346 | 5.682%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 47 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 13.271 | 0 | 0 | 13.271 | 0 | 11.5201 | 0.5963 | 19.3192 | 11.5201 | 0.5963 | 19.3192 | 13.4671 | 0.69708 | 19.3192 | 0.9827%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 84 | 81 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 330.5962 | 0 | 0 | 330.5962 | 0 | 286.979 | 1.0277 | 279.252 | 286.979 | 1.0277 | 279.252 | 335.4818 | 1.2014 | 279.252 | 9.397%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 49 | 582.1633 | 91.34% | 8.391% | 0.2732% | 54.2799 | 0 | 0 | 54.2799 | 0 | 47.1185 | 0.62168 | 75.7925 | 47.1185 | 0.62168 | 75.7925 | 55.0821 | 0.72675 | 75.7925 | 9.324%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 133 | 119 | 4750.1268 | 98% | 1.916% | 0.08125% | 416.5218 | 0 | 0 | 416.5218 | 0 | 361.5681 | 1.5098 | 239.4827 | 361.5681 | 1.5098 | 239.4827 | 422.6772 | 1.765 | 239.4827 | 8.769%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 97 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 506.3705 | 0 | 0 | 506.3705 | 0 | 439.5626 | 1.2307 | 357.1742 | 439.5626 | 1.2307 | 357.1742 | 513.8536 | 1.4387 | 357.1742 | 9.467%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 201 | 196 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 171.9277 | 0 | 0 | 171.9277 | 0 | 149.2445 | 2.4867 | 60.0169 | 149.2445 | 2.4867 | 60.0169 | 174.4685 | 2.907 | 60.0169 | 9.37%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 3 | 3 | 88.141 | 1.745% | 98.17% | 0.08447% | 0.15379 | 0 | 0 | 0.15379 | 0 | 0.1335 | 0.038062 | 3.5075 | 0.1335 | 0.038062 | 3.5075 | 0.15607 | 0.044495 | 3.5075 | 0.1745%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 89 | 852.9261 | 84.92% | 14.72% | 0.3553% | 44.4597 | 0 | 0 | 44.4597 | 0 | 38.594 | 1.1292 | 34.1791 | 38.594 | 1.1292 | 34.1791 | 45.1168 | 1.32 | 34.1791 | 5.213%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 144 | 71 | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0335 | 0 | 0 | 15.0335 | 0 | 13.05 | 0.9008 | 14.4872 | 13.05 | 0.9008 | 14.4872 | 15.2556 | 1.053 | 14.4872 | 2.857%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 408 | 11572.221 | 88.48% | 11.4% | 0.1243% | 547.4938 | 0 | 0 | 547.4938 | 0 | 475.2603 | 5.1764 | 91.8126 | 475.2603 | 5.1764 | 91.8126 | 555.5847 | 6.0513 | 91.8126 | 4.731%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 54 | 50 | 704.6091 | 96.62% | 3.132% | 0.2514% | 63.0339 | 0 | 0 | 63.0339 | 0 | 54.7175 | 0.63436 | 86.2557 | 54.7175 | 0.63436 | 86.2557 | 63.9654 | 0.74158 | 86.2557 | 8.946%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 25 | 25 | 549.9829 | 98.93% | 0.9134% | 0.161% | 54.4074 | 0 | 0 | 54.4074 | 0 | 47.2292 | 0.31718 | 148.9023 | 47.2292 | 0.31718 | 148.9023 | 55.2114 | 0.37079 | 148.9023 | 9.893%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 74 | 50 | 474.7376 | 91.31% | 8.325% | 0.3651% | 29.2893 | 0 | 0 | 29.2893 | 0 | 25.425 | 0.63436 | 40.0795 | 25.425 | 0.63436 | 40.0795 | 29.7221 | 0.74158 | 40.0795 | 6.17%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 73 | 26 | 141.3846 | 51% | 48.51% | 0.49% | 2.5682 | 0 | 0 | 2.5682 | 0 | 2.2294 | 0.32987 | 6.7584 | 2.2294 | 0.32987 | 6.7584 | 2.6062 | 0.38562 | 6.7584 | 1.816%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 122 | 84 | 333.8465 | 96.62% | 2.31% | 1.072% | 22.2086 | 0 | 0 | 22.2086 | 0 | 19.2785 | 1.0657 | 18.0895 | 19.2785 | 1.0657 | 18.0895 | 22.5368 | 1.2459 | 18.0895 | 6.652%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 354 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 292.8867 | 0 | 0 | 292.8867 | 0 | 254.2447 | 4.4913 | 56.6083 | 254.2447 | 4.4913 | 56.6083 | 297.215 | 5.2504 | 56.6083 | 8.579%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 465 | 363 | 571.2373 | 70.71% | 27.93% | 1.361% | 31.5311 | 0 | 0 | 31.5311 | 0 | 27.3711 | 4.6055 | 5.9431 | 27.3711 | 4.6055 | 5.9431 | 31.9971 | 5.3839 | 5.9431 | 5.52%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 275 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 746.4038 | 0 | 0 | 746.4038 | 0 | 647.9271 | 3.489 | 185.7054 | 647.9271 | 3.489 | 185.7054 | 757.4342 | 4.0787 | 185.7054 | 7.749%
2028 | 445 | 445-1315 | Tier-2 | Tier-2---19 | Tier-2---11 | 4 | 1 | 26.2494 | 99.59% | 0% | 0.4079% | 0.65356 | 0 | 0 | 0.65356 | 0 | 0.56733 | 0.012687 | 44.7164 | 0.56733 | 0.012687 | 44.7164 | 0.66322 | 0.014832 | 44.7164 | 2.49%
2028 | 445 | 445-1323 | Tier-2 | Tier-2---18 | Tier-2---12 | 6 | 8 | 78.5439 | 99.26% | 0.525% | 0.2138% | 10.3952 | 0 | 0 | 10.3952 | 0 | 9.0237 | 0.1015 | 88.9046 | 9.0237 | 0.1015 | 88.9046 | 10.5488 | 0.11865 | 88.9046 | 13.23%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 197 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 623.982 | 0 | 0 | 623.982 | 0 | 541.657 | 2.4994 | 216.7151 | 541.657 | 2.4994 | 216.7151 | 633.2032 | 2.9218 | 216.7151 | 8.606%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 73 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 107.0683 | 0 | 0 | 107.0683 | 0 | 92.9422 | 0.92617 | 100.3509 | 92.9422 | 0.92617 | 100.3509 | 108.6505 | 1.0827 | 100.3509 | 6.677%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 439 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 848.1098 | 0 | 0 | 848.1098 | 0 | 736.2146 | 5.5697 | 132.1816 | 736.2146 | 5.5697 | 132.1816 | 860.6432 | 6.5111 | 132.1816 | 7.986%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 220 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 138.3664 | 0 | 0 | 138.3664 | 0 | 120.111 | 2.7912 | 43.032 | 120.111 | 2.7912 | 43.032 | 140.4111 | 3.2629 | 43.032 | 7.832%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 197 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 257.8827 | 0 | 0 | 257.8827 | 0 | 223.859 | 2.4994 | 89.5652 | 223.859 | 2.4994 | 89.5652 | 261.6937 | 2.9218 | 89.5652 | 7.01%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 511 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 339.1443 | 0 | 0 | 339.1443 | 0 | 294.3993 | 6.4832 | 45.4095 | 294.3993 | 6.4832 | 45.4095 | 344.1562 | 7.5789 | 45.4095 | 7.671%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 25 | 22 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 115.6761 | 0 | 0 | 115.6761 | 0 | 100.4144 | 0.27912 | 359.7531 | 100.4144 | 0.27912 | 359.7531 | 117.3856 | 0.32629 | 359.7531 | 8.557%
2028 | 448 | 448-1196F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 4 | 16.696 | 99.41% | 0% | 0.5907% | 1.6597 | 0 | 0 | 1.6597 | 0 | 1.4408 | 0.050749 | 28.3898 | 1.4408 | 0.050749 | 28.3898 | 1.6843 | 0.059326 | 28.3898 | 9.941%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 51 | 45 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 104.1172 | 0 | 0 | 104.1172 | 0 | 90.3805 | 0.57093 | 158.3045 | 90.3805 | 0.57093 | 158.3045 | 105.6558 | 0.66742 | 158.3045 | 8.593%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 184 | 154 | 2612.2711 | 91.91% | 7.885% | 0.2065% | 200.9452 | 0 | 0 | 200.9452 | 0 | 174.4335 | 1.9538 | 89.2772 | 174.4335 | 1.9538 | 89.2772 | 203.9148 | 2.2841 | 89.2772 | 7.692%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 314 | 213 | 2119.752 | 55.7% | 43.96% | 0.3458% | 80.0895 | 0 | 0 | 80.0895 | 0 | 69.5229 | 2.7024 | 25.7264 | 69.5229 | 2.7024 | 25.7264 | 81.2731 | 3.1591 | 25.7264 | 3.778%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 151 | 520.639 | 76.18% | 22.78% | 1.038% | 29.6503 | 0 | 0 | 29.6503 | 0 | 25.7384 | 1.9158 | 13.4349 | 25.7384 | 1.9158 | 13.4349 | 30.0884 | 2.2396 | 13.4349 | 5.695%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 170 | 140 | 630.7627 | 79.12% | 20.09% | 0.7869% | 41.1002 | 0 | 0 | 41.1002 | 0 | 35.6776 | 1.7762 | 20.0863 | 35.6776 | 1.7762 | 20.0863 | 41.7076 | 2.0764 | 20.0863 | 6.516%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 493 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 573.9427 | 0 | 0 | 573.9427 | 0 | 498.2197 | 6.2548 | 79.6535 | 498.2197 | 6.2548 | 79.6535 | 582.4245 | 7.312 | 79.6535 | 6.304%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 303 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 386.9071 | 0 | 0 | 386.9071 | 0 | 335.8606 | 3.8442 | 87.367 | 335.8606 | 3.8442 | 87.367 | 392.6249 | 4.494 | 87.367 | 6.854%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 418 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 457.0253 | 0 | 0 | 457.0253 | 0 | 396.7277 | 5.3033 | 74.8079 | 396.7277 | 5.3033 | 74.8079 | 463.7792 | 6.1996 | 74.8079 | 6.791%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 72 | 55 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 110.7812 | 0 | 0 | 110.7812 | 0 | 96.1653 | 0.6978 | 137.8119 | 96.1653 | 0.6978 | 137.8119 | 112.4183 | 0.81574 | 137.8119 | 7.408%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 26 | 26 | 625.3129 | 96.7% | 3.156% | 0.1473% | 60.4656 | 0 | 0 | 60.4656 | 0 | 52.4881 | 0.32987 | 159.1178 | 52.4881 | 0.32987 | 159.1178 | 61.3592 | 0.38562 | 159.1178 | 9.67%
2028 | 441 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 130 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 409.3932 | 0 | 0 | 409.3932 | 0 | 355.38 | 1.6493 | 215.467 | 355.38 | 1.6493 | 215.467 | 415.4433 | 1.9281 | 215.467 | 7.782%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 161 | 123 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 169.3511 | 0 | 0 | 169.3511 | 0 | 147.0078 | 1.5605 | 94.2034 | 147.0078 | 1.5605 | 94.2034 | 171.8538 | 1.8243 | 94.2034 | 7.3%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 15 | 296.7138 | 97.11% | 2.719% | 0.1664% | 24.0127 | 0 | 0 | 24.0127 | 0 | 20.8446 | 0.19031 | 109.5302 | 20.8446 | 0.19031 | 109.5302 | 24.3676 | 0.22247 | 109.5302 | 8.093%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 126 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 494.986 | 0 | 0 | 494.986 | 0 | 429.6801 | 1.5986 | 268.7855 | 429.6801 | 1.5986 | 268.7855 | 502.301 | 1.8688 | 268.7855 | 5.982%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 22 | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.7456 | 0 | 0 | 36.7456 | 0 | 31.8976 | 0.27912 | 114.2789 | 31.8976 | 0.27912 | 114.2789 | 37.2886 | 0.32629 | 114.2789 | 4.638%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 41 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 63.1703 | 0 | 0 | 63.1703 | 0 | 54.8359 | 0.52018 | 105.4174 | 54.8359 | 0.52018 | 105.4174 | 64.1038 | 0.6081 | 105.4174 | 5.579%
2028 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 18 | 5 | 537.0702 | 32.53% | 67.41% | 0.0594% | 4.8529 | 0 | 0 | 4.8529 | 0 | 4.2127 | 0.063436 | 66.4076 | 4.2127 | 0.063436 | 66.4076 | 4.9247 | 0.074158 | 66.4076 | 0.9036%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 5 | 5 | 137.227 | 99.9% | 0% | 0.1049% | 13.7083 | 0 | 0 | 13.7083 | 0 | 11.8997 | 0.063436 | 187.5847 | 11.8997 | 0.063436 | 187.5847 | 13.9109 | 0.074158 | 187.5847 | 9.99%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 19 | 625.5425 | 99.9% | 0% | 0.09615% | 59.3694 | 0 | 0 | 59.3694 | 0 | 51.5365 | 0.24106 | 213.7925 | 51.5365 | 0.24106 | 213.7925 | 60.2468 | 0.2818 | 213.7925 | 9.491%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 10 | 181.2174 | 99.84% | 0% | 0.161% | 15.0771 | 0 | 0 | 15.0771 | 0 | 13.0879 | 0.12687 | 103.1579 | 13.0879 | 0.12687 | 103.1579 | 15.3 | 0.14832 | 103.1579 | 8.32%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 58 | 2823.7515 | 99.93% | 0% | 0.06613% | 230.5201 | 0 | 0 | 230.5201 | 0 | 200.1065 | 0.73586 | 271.9345 | 200.1065 | 0.73586 | 271.9345 | 233.9268 | 0.86023 | 271.9345 | 8.164%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 2 | 3 | 39.0262 | 97.23% | 2.586% | 0.1833% | 5.6918 | 0 | 0 | 5.6918 | 0 | 4.9409 | 0.038062 | 129.8115 | 4.9409 | 0.038062 | 129.8115 | 5.7759 | 0.044495 | 129.8115 | 14.58%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 53 | 41 | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 265.4015 | 0 | 0 | 265.4015 | 0 | 230.3858 | 0.52018 | 442.8972 | 230.3858 | 0.52018 | 442.8972 | 269.3236 | 0.6081 | 442.8972 | 7.713%
2028 | 454 | 454-49F | Tier-2 | Tier-2---13 | Tier-2---8 | 52 | 1 | 292.9743 | 76.06% | 23.59% | 0.3558% | 0.42851 | 0 | 0 | 0.42851 | 0 | 0.37198 | 0.012687 | 29.3187 | 0.37198 | 0.012687 | 29.3187 | 0.43484 | 0.014832 | 29.3187 | 0.1463%
2028 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 11 | 10 | 88.0149 | 97.35% | 2.233% | 0.4157% | 7.7894 | 0 | 0 | 7.7894 | 0 | 6.7617 | 0.12687 | 53.2952 | 6.7617 | 0.12687 | 53.2952 | 7.9045 | 0.14832 | 53.2952 | 8.85%
2028 | 260 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 198 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 116.9805 | 0 | 0 | 116.9805 | 0 | 101.5467 | 2.5121 | 40.4233 | 101.5467 | 2.5121 | 40.4233 | 118.7092 | 2.9367 | 40.4233 | 8.487%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 125 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 455.719 | 0 | 0 | 455.719 | 0 | 395.5938 | 1.5859 | 249.4426 | 395.5938 | 1.5859 | 249.4426 | 462.4537 | 1.8539 | 249.4426 | 8.656%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 475 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 1479.703 | 0 | 0 | 1479.703 | 0 | 1284.4786 | 6.0265 | 213.1397 | 1284.4786 | 6.0265 | 213.1397 | 1501.5702 | 7.045 | 213.1397 | 8.839%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 128 | 21 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 66.2676 | 0 | 0 | 66.2676 | 0 | 57.5246 | 0.26643 | 215.9064 | 57.5246 | 0.26643 | 215.9064 | 67.2469 | 0.31146 | 215.9064 | 1.558%
2028 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 16 | 800.5503 | 21.6% | 78.32% | 0.07823% | 13.8344 | 0 | 0 | 13.8344 | 0 | 12.0091 | 0.203 | 59.1593 | 12.0091 | 0.203 | 59.1593 | 14.0388 | 0.23731 | 59.1593 | 1.728%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 23 | 22 | 204.0835 | 99.63% | 0% | 0.368% | 19.4492 | 0 | 0 | 19.4492 | 0 | 16.8832 | 0.27912 | 60.487 | 16.8832 | 0.27912 | 60.487 | 19.7366 | 0.32629 | 60.487 | 9.53%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 154 | 23 | 733.6834 | 99.51% | 0% | 0.4917% | 10.9037 | 0 | 0 | 10.9037 | 0 | 9.4652 | 0.29181 | 32.4363 | 9.4652 | 0.29181 | 32.4363 | 11.0649 | 0.34113 | 32.4363 | 1.486%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 180 | 156 | 2978.814 | 97.34% | 2.471% | 0.184% | 251.3089 | 0 | 0 | 251.3089 | 0 | 218.1525 | 1.9792 | 110.2216 | 218.1525 | 1.9792 | 110.2216 | 255.0227 | 2.3137 | 110.2216 | 8.437%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 155 | 112 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 104.6866 | 0 | 0 | 104.6866 | 0 | 90.8748 | 1.421 | 63.9524 | 90.8748 | 1.421 | 63.9524 | 106.2337 | 1.6611 | 63.9524 | 7.079%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 408 | 329 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 205.8159 | 0 | 0 | 205.8159 | 0 | 178.6616 | 4.1741 | 42.8022 | 178.6616 | 4.1741 | 42.8022 | 208.8575 | 4.8796 | 42.8022 | 7.802%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 401 | 276 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 217.8673 | 0 | 0 | 217.8673 | 0 | 189.123 | 3.5017 | 54.009 | 189.123 | 3.5017 | 54.009 | 221.087 | 4.0935 | 54.009 | 6.382%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 129 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 142.774 | 0 | 0 | 142.774 | 0 | 123.9372 | 1.6367 | 75.7256 | 123.9372 | 1.6367 | 75.7256 | 144.884 | 1.9133 | 75.7256 | 8.744%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 249 | 205 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 538.5174 | 0 | 0 | 538.5174 | 0 | 467.4682 | 2.6009 | 179.7336 | 467.4682 | 2.6009 | 179.7336 | 546.4756 | 3.0405 | 179.7336 | 7.963%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 201 | 748.333 | 77.34% | 21.7% | 0.962% | 28.5115 | 0 | 0 | 28.5115 | 0 | 24.7498 | 2.5501 | 9.7053 | 24.7498 | 2.5501 | 9.7053 | 28.9328 | 2.9811 | 9.7053 | 3.81%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 276 | 149 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 108.5766 | 0 | 0 | 108.5766 | 0 | 94.2515 | 1.8904 | 49.8578 | 94.2515 | 1.8904 | 49.8578 | 110.1811 | 2.2099 | 49.8578 | 5.209%
2028 | 520 | 520-1936 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 3 | 63.7111 | 99.77% | 0% | 0.2279% | 4.7674 | 0 | 0 | 4.7674 | 0 | 4.1385 | 0.038062 | 108.7296 | 4.1385 | 0.038062 | 108.7296 | 4.8379 | 0.044495 | 108.7296 | 7.483%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 113 | 54 | 258.296 | 74.72% | 24.53% | 0.7505% | 9.2233 | 0 | 0 | 9.2233 | 0 | 8.0065 | 0.68511 | 11.6863 | 8.0065 | 0.68511 | 11.6863 | 9.3596 | 0.80091 | 11.6863 | 3.571%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 306 | 275 | 4997.7942 | 96.49% | 3.313% | 0.193% | 433.4028 | 0 | 0 | 433.4028 | 0 | 376.2219 | 3.489 | 107.8307 | 376.2219 | 3.489 | 107.8307 | 439.8076 | 4.0787 | 107.8307 | 8.672%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 219 | 176 | 2044.6463 | 97.57% | 2.13% | 0.298% | 160.3287 | 0 | 0 | 160.3287 | 0 | 139.1758 | 2.233 | 62.3278 | 139.1758 | 2.233 | 62.3278 | 162.6981 | 2.6104 | 62.3278 | 7.841%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 264 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 919.7864 | 0 | 0 | 919.7864 | 0 | 798.4346 | 3.3494 | 238.3782 | 798.4346 | 3.3494 | 238.3782 | 933.3791 | 3.9155 | 238.3782 | 8.104%
2028 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 136 | 810.9996 | 89.31% | 10.24% | 0.4457% | 49.5022 | 0 | 0 | 49.5022 | 0 | 42.9711 | 1.7255 | 24.904 | 42.9711 | 1.7255 | 24.904 | 50.2337 | 2.0171 | 24.904 | 6.104%
2028 | 239 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 276 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 683.0496 | 0 | 0 | 683.0496 | 0 | 592.9315 | 3.5017 | 169.3271 | 592.9315 | 3.5017 | 169.3271 | 693.1437 | 4.0935 | 169.3271 | 8.057%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 264 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 744.4805 | 0 | 0 | 744.4805 | 0 | 646.2576 | 3.3494 | 192.9447 | 646.2576 | 3.3494 | 192.9447 | 755.4825 | 3.9155 | 192.9447 | 8.544%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 247 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 382.9204 | 0 | 0 | 382.9204 | 0 | 332.3998 | 3.1338 | 106.0706 | 332.3998 | 3.1338 | 106.0706 | 388.5792 | 3.6634 | 106.0706 | 6.815%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 232 | 207 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 1085.4723 | 0 | 0 | 1085.4723 | 0 | 942.2607 | 2.6263 | 358.783 | 942.2607 | 2.6263 | 358.783 | 1101.5135 | 3.0701 | 358.783 | 8.867%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 437 | 328 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 670.0457 | 0 | 0 | 670.0457 | 0 | 581.6434 | 4.1614 | 139.77 | 581.6434 | 4.1614 | 139.77 | 679.9477 | 4.8648 | 139.77 | 7.435%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 34 | 112.7117 | 43.02% | 55.81% | 1.165% | 2.5762 | 0 | 0 | 2.5762 | 0 | 2.2363 | 0.43137 | 5.1843 | 2.2363 | 0.43137 | 5.1843 | 2.6143 | 0.50427 | 5.1843 | 2.286%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 42 | 116.9577 | 22.53% | 76.17% | 1.295% | 1.1902 | 0 | 0 | 1.1902 | 0 | 1.0332 | 0.53287 | 1.9389 | 1.0332 | 0.53287 | 1.9389 | 1.2078 | 0.62293 | 1.9389 | 1.018%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 354 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 317.7319 | 0 | 0 | 317.7319 | 0 | 275.812 | 4.4913 | 61.4103 | 275.812 | 4.4913 | 61.4103 | 322.4274 | 5.2504 | 61.4103 | 5.634%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 99 | 305.199 | 11.7% | 87.21% | 1.095% | 1.7759 | 0 | 0 | 1.7759 | 0 | 1.5416 | 1.256 | 1.2273 | 1.5416 | 1.256 | 1.2273 | 1.8022 | 1.4683 | 1.2273 | 0.5819%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 231 | 173 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 408.5997 | 0 | 0 | 408.5997 | 0 | 354.6911 | 2.1949 | 161.5978 | 354.6911 | 2.1949 | 161.5978 | 414.638 | 2.5659 | 161.5978 | 7.472%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 489 | 289 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 667.3334 | 0 | 0 | 667.3334 | 0 | 579.2889 | 3.6666 | 157.9896 | 579.2889 | 3.6666 | 157.9896 | 677.1953 | 4.2863 | 157.9896 | 5.896%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 283 | 223 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 1069.4603 | 0 | 0 | 1069.4603 | 0 | 928.3612 | 2.8293 | 328.128 | 928.3612 | 2.8293 | 328.128 | 1085.2648 | 3.3074 | 328.128 | 7.8%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 204 | 8801.877 | 98.2% | 1.718% | 0.0819% | 623.0646 | 0 | 0 | 623.0646 | 0 | 540.8607 | 2.5882 | 208.9712 | 540.8607 | 2.5882 | 208.9712 | 632.2723 | 3.0256 | 208.9712 | 7.079%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 842 | 634 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 3010.7489 | 0 | 0 | 3010.7489 | 0 | 2613.5263 | 8.0437 | 324.9142 | 2613.5263 | 8.0437 | 324.9142 | 3055.242 | 9.4032 | 324.9142 | 7.457%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 18 | 18 | 833.6308 | 67.75% | 32.17% | 0.07637% | 56.479 | 0 | 0 | 56.479 | 0 | 49.0274 | 0.22837 | 214.6831 | 49.0274 | 0.22837 | 214.6831 | 57.3136 | 0.26697 | 214.6831 | 6.775%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 92 | 11 | 519.9571 | 96.32% | 3.27% | 0.4047% | 5.9884 | 0 | 0 | 5.9884 | 0 | 5.1983 | 0.13956 | 37.2479 | 5.1983 | 0.13956 | 37.2479 | 6.0769 | 0.16315 | 37.2479 | 1.152%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 9 | 9 | 49.4293 | 99.41% | 0% | 0.5897% | 4.9138 | 0 | 0 | 4.9138 | 0 | 4.2655 | 0.11419 | 37.3557 | 4.2655 | 0.11419 | 37.3557 | 4.9864 | 0.13348 | 37.3557 | 9.941%
2028 | 1118 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 360 | 18774.394 | 95.55% | 4.388% | 0.06321% | 1622.6031 | 0 | 0 | 1622.6031 | 0 | 1408.5252 | 4.5674 | 308.385 | 1408.5252 | 4.5674 | 308.385 | 1646.5821 | 5.3394 | 308.385 | 8.643%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 631 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 2144.2272 | 0 | 0 | 2144.2272 | 0 | 1861.329 | 8.0057 | 232.501 | 1861.329 | 8.0057 | 232.501 | 2175.9148 | 9.3587 | 232.501 | 8.329%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 344 | 278 | 2610.8 | 93.6% | 6.065% | 0.3401% | 197.4758 | 0 | 0 | 197.4758 | 0 | 171.4218 | 3.5271 | 48.6018 | 171.4218 | 3.5271 | 48.6018 | 200.3941 | 4.1232 | 48.6018 | 7.564%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 551 | 445 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 316.6756 | 0 | 0 | 316.6756 | 0 | 274.895 | 5.6458 | 48.6898 | 274.895 | 5.6458 | 48.6898 | 321.3554 | 6.6001 | 48.6898 | 7.576%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 159 | 622.3042 | 87.18% | 11.98% | 0.8373% | 45.4006 | 0 | 0 | 45.4006 | 0 | 39.4107 | 2.0173 | 19.5366 | 39.4107 | 2.0173 | 19.5366 | 46.0716 | 2.3582 | 19.5366 | 7.296%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 198 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 128.3604 | 0 | 0 | 128.3604 | 0 | 111.4252 | 2.5121 | 44.3557 | 111.4252 | 2.5121 | 44.3557 | 130.2573 | 2.9367 | 44.3557 | 7.885%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 310 | 229 | 6201.607 | 97.29% | 2.601% | 0.1104% | 445.698 | 0 | 0 | 445.698 | 0 | 386.8949 | 2.9054 | 133.1645 | 386.8949 | 2.9054 | 133.1645 | 452.2845 | 3.3964 | 133.1645 | 7.187%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 242 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 1122.1435 | 0 | 0 | 1122.1435 | 0 | 974.0937 | 3.0703 | 317.2609 | 974.0937 | 3.0703 | 317.2609 | 1138.7267 | 3.5892 | 317.2609 | 7.316%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 46 | 34 | 2448.8293 | 98.64% | 1.317% | 0.04316% | 178.5379 | 0 | 0 | 178.5379 | 0 | 154.9826 | 0.43137 | 359.2817 | 154.9826 | 0.43137 | 359.2817 | 181.1764 | 0.50427 | 359.2817 | 7.291%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 188 | 158 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 474.2097 | 0 | 0 | 474.2097 | 0 | 411.6449 | 2.0046 | 205.351 | 411.6449 | 2.0046 | 205.351 | 481.2176 | 2.3434 | 205.351 | 8.27%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 313 | 270 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 898.1963 | 0 | 0 | 898.1963 | 0 | 779.693 | 3.4256 | 227.6098 | 779.693 | 3.4256 | 227.6098 | 911.4699 | 4.0045 | 227.6098 | 8.48%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 273 | 226 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 756.8138 | 0 | 0 | 756.8138 | 0 | 656.9637 | 2.8673 | 229.1206 | 656.9637 | 2.8673 | 229.1206 | 767.9981 | 3.3519 | 229.1206 | 8.148%
2028 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 4 | 17.7969 | 99.34% | 0% | 0.6614% | 1.7679 | 0 | 0 | 1.7679 | 0 | 1.5347 | 0.050749 | 30.2403 | 1.5347 | 0.050749 | 30.2403 | 1.794 | 0.059326 | 30.2403 | 9.934%
2028 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 4 | 3 | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.038062 | 0 | 0 | 0.038062 | 0 | 0 | 0.044495 | 0 | 0%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 102 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 227.9168 | 0 | 0 | 227.9168 | 0 | 197.8467 | 1.2941 | 152.8832 | 197.8467 | 1.2941 | 152.8832 | 231.285 | 1.5128 | 152.8832 | 7.269%
2028 | 75 | 75-2260F | Tier-3 | missing | missing | 2 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.012687 | 0 | 0 | 0.012687 | 0 | 0 | 0.014832 | 0 | 0%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 65 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 131.6342 | 0 | 0 | 131.6342 | 0 | 114.2671 | 0.82467 | 138.5603 | 114.2671 | 0.82467 | 138.5603 | 133.5795 | 0.96405 | 138.5603 | 7.705%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 69 | 58 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 162.6382 | 0 | 0 | 162.6382 | 0 | 141.1806 | 0.73586 | 191.8572 | 141.1806 | 0.73586 | 191.8572 | 165.0417 | 0.86023 | 191.8572 | 8.394%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 241 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 165.7574 | 0 | 0 | 165.7574 | 0 | 143.8882 | 3.0576 | 47.0586 | 143.8882 | 3.0576 | 47.0586 | 168.2069 | 3.5744 | 47.0586 | 7.496%
2028 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 24 | 21 | 42.5113 | 97.49% | 0.5175% | 1.991% | 3.6264 | 0 | 0 | 3.6264 | 0 | 3.148 | 0.26643 | 11.8153 | 3.148 | 0.26643 | 11.8153 | 3.68 | 0.31146 | 11.8153 | 8.531%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 186 | 143 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 1100.7243 | 0 | 0 | 1100.7243 | 0 | 955.5004 | 1.8143 | 526.6547 | 955.5004 | 1.8143 | 526.6547 | 1116.9909 | 2.1209 | 526.6547 | 7.577%
2028 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 29 | 29 | 5696.3358 | 99.98% | 0% | 0.01771% | 569.5327 | 0 | 0 | 569.5327 | 0 | 494.3915 | 0.36793 | 1343.7055 | 494.3915 | 0.36793 | 1343.7055 | 577.9493 | 0.43012 | 1343.7055 | 9.998%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | Tier-3---1 | 33 | 32 | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 695.0009 | 0 | 0 | 695.0009 | 0 | 603.3061 | 0.40599 | 1486 | 603.3061 | 0.40599 | 1486 | 705.2717 | 0.47461 | 1486 | 9.65%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 143 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 236.4489 | 0 | 0 | 236.4489 | 0 | 205.2531 | 1.8143 | 113.1318 | 205.2531 | 1.8143 | 113.1318 | 239.9432 | 2.1209 | 113.1318 | 2.589%
2028 | 73 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 9 | 5 | 324.1263 | 99.58% | 0.3619% | 0.05404% | 17.9321 | 0 | 0 | 17.9321 | 0 | 15.5662 | 0.063436 | 245.3833 | 15.5662 | 0.063436 | 245.3833 | 18.1971 | 0.074158 | 245.3833 | 5.532%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 48 | 3349.7594 | 92.58% | 7.304% | 0.116% | 105.5733 | 0 | 0 | 105.5733 | 0 | 91.6445 | 0.60899 | 150.4861 | 91.6445 | 0.60899 | 150.4861 | 107.1335 | 0.71192 | 150.4861 | 3.152%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 198 | 185 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 1142.7385 | 0 | 0 | 1142.7385 | 0 | 991.9715 | 2.3471 | 422.6283 | 991.9715 | 2.3471 | 422.6283 | 1159.626 | 2.7438 | 422.6283 | 9.275%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 159 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 180.6886 | 0 | 0 | 180.6886 | 0 | 156.8495 | 2.0173 | 77.753 | 156.8495 | 2.0173 | 77.753 | 183.3588 | 2.3582 | 77.753 | 8.658%
2028 | 222 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 206 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 75.9811 | 0 | 0 | 75.9811 | 0 | 65.9566 | 2.6136 | 25.2361 | 65.9566 | 2.6136 | 25.2361 | 77.104 | 3.0553 | 25.2361 | 4.728%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 80 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 553.4853 | 0 | 0 | 553.4853 | 0 | 480.4613 | 1.015 | 473.3687 | 480.4613 | 1.015 | 473.3687 | 561.6648 | 1.1865 | 473.3687 | 5.698%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 192 | 130 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 1235.3475 | 0 | 0 | 1235.3475 | 0 | 1072.3621 | 1.6493 | 650.1734 | 1072.3621 | 1.6493 | 650.1734 | 1253.6035 | 1.9281 | 650.1734 | 6.696%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 74 | 65 | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 223.8726 | 0 | 0 | 223.8726 | 0 | 194.336 | 0.82467 | 235.6519 | 194.336 | 0.82467 | 235.6519 | 227.181 | 0.96405 | 235.6519 | 8.729%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 180 | 106 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 314.028 | 0 | 0 | 314.028 | 0 | 272.5968 | 1.3449 | 202.6964 | 272.5968 | 1.3449 | 202.6964 | 318.6687 | 1.5721 | 202.6964 | 5.672%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 238 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 1016.9059 | 0 | 0 | 1016.9059 | 0 | 882.7406 | 3.0196 | 292.3393 | 882.7406 | 3.0196 | 292.3393 | 1031.9338 | 3.5299 | 292.3393 | 5.415%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 116 | 110 | 3034.8235 | 97.12% | 2.752% | 0.1275% | 279.4979 | 0 | 0 | 279.4979 | 0 | 242.6224 | 1.3956 | 173.8479 | 242.6224 | 1.3956 | 173.8479 | 283.6284 | 1.6315 | 173.8479 | 9.21%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 218 | 192 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 1746.0262 | 0 | 0 | 1746.0262 | 0 | 1515.6645 | 2.436 | 622.2043 | 1515.6645 | 2.436 | 622.2043 | 1771.8291 | 2.8477 | 622.2043 | 8.74%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 11 | 127.4062 | 99.28% | 0% | 0.716% | 3.6617 | 0 | 0 | 3.6617 | 0 | 3.1786 | 0.13956 | 22.7756 | 3.1786 | 0.13956 | 22.7756 | 3.7158 | 0.16315 | 22.7756 | 2.874%
2028 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 6 | 12.4137 | 98.83% | 0% | 1.166% | 0.56626 | 0 | 0 | 0.56626 | 0 | 0.49155 | 0.076124 | 6.4573 | 0.49155 | 0.076124 | 6.4573 | 0.57463 | 0.08899 | 6.4573 | 4.562%
2028 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 17 | 17 | 139.955 | 99.63% | 0% | 0.3714% | 13.9435 | 0 | 0 | 13.9435 | 0 | 12.1039 | 0.21568 | 56.1186 | 12.1039 | 0.21568 | 56.1186 | 14.1496 | 0.25214 | 56.1186 | 9.963%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 3 | 6.7153 | 99.02% | 0% | 0.9775% | 0.66497 | 0 | 0 | 0.66497 | 0 | 0.57723 | 0.038062 | 15.1657 | 0.57723 | 0.038062 | 15.1657 | 0.67479 | 0.044495 | 15.1657 | 9.902%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 16 | 16 | 330.3488 | 99.39% | 0.4551% | 0.1546% | 32.8335 | 0 | 0 | 32.8335 | 0 | 28.5016 | 0.203 | 140.4043 | 28.5016 | 0.203 | 140.4043 | 33.3187 | 0.23731 | 140.4043 | 9.939%
2028 | 260 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 40 | 36 | 232.5563 | 96.66% | 2.796% | 0.5416% | 20.2316 | 0 | 0 | 20.2316 | 0 | 17.5623 | 0.45674 | 38.4513 | 17.5623 | 0.45674 | 38.4513 | 20.5306 | 0.53394 | 38.4513 | 8.7%
2028 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 7 | 7 | 188.5529 | 99.88% | 0% | 0.1171% | 18.8332 | 0 | 0 | 18.8332 | 0 | 16.3484 | 0.088811 | 184.0813 | 16.3484 | 0.088811 | 184.0813 | 19.1115 | 0.10382 | 184.0813 | 9.988%
2028 | 599 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 159 | 8606.9717 | 99.86% | 0% | 0.1411% | 245.346 | 0 | 0 | 245.346 | 0 | 212.9763 | 2.0173 | 105.576 | 212.9763 | 2.0173 | 105.576 | 248.9718 | 2.3582 | 105.576 | 2.851%
2028 | 907 | 907-1475 | Tier-3 | Tier-3---21 | Tier-3---21 | 4 | 4 | 4.2814 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.050749 | 0 | 0 | 0.050749 | 0 | 0 | 0.059326 | 0 | 0%
2028 | 1021 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 162 | 123 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 625.5206 | 0 | 0 | 625.5206 | 0 | 542.9926 | 1.5605 | 347.9525 | 542.9926 | 1.5605 | 347.9525 | 634.7646 | 1.8243 | 347.9525 | 7.412%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 5 | 5 | 257.2419 | 98.67% | 1.294% | 0.04048% | 25.3809 | 0 | 0 | 25.3809 | 0 | 22.0323 | 0.063436 | 347.3126 | 22.0323 | 0.063436 | 347.3126 | 25.756 | 0.074158 | 347.3126 | 9.867%
2028 | 907 | 907-1604 | Tier-3 | Tier-3---19 | Tier-3---16 | 2 | 4 | 17.8439 | 83.33% | 16.48% | 0.1969% | 2.9738 | 0 | 0 | 2.9738 | 0 | 2.5814 | 0.050749 | 50.8662 | 2.5814 | 0.050749 | 50.8662 | 3.0177 | 0.059326 | 50.8662 | 16.67%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 117 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 717.4672 | 0 | 0 | 717.4672 | 0 | 622.8083 | 1.4844 | 419.5654 | 622.8083 | 1.4844 | 419.5654 | 728.07 | 1.7353 | 419.5654 | 7.884%
2028 | 1021 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 278 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1923.6578 | 0 | 0 | 1923.6578 | 0 | 1669.8603 | 3.5271 | 473.4417 | 1669.8603 | 3.5271 | 473.4417 | 1952.0858 | 4.1232 | 473.4417 | 7.107%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 33 | 29 | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 557.7619 | 0 | 0 | 557.7619 | 0 | 484.1737 | 0.36793 | 1315.9345 | 484.1737 | 0.36793 | 1315.9345 | 566.0045 | 0.43012 | 1315.9345 | 8.786%
2028 | 350 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 240 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 1227.927 | 0 | 0 | 1227.927 | 0 | 1065.9206 | 3.0449 | 350.0618 | 1065.9206 | 3.0449 | 350.0618 | 1246.0734 | 3.5596 | 350.0618 | 7.788%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 130 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 910.2348 | 0 | 0 | 910.2348 | 0 | 790.1431 | 1.6493 | 479.064 | 790.1431 | 1.6493 | 479.064 | 923.6863 | 1.9281 | 479.064 | 7.738%
2028 | 350 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 471 | 386 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 439.4181 | 0 | 0 | 439.4181 | 0 | 381.4435 | 4.8973 | 77.8886 | 381.4435 | 4.8973 | 77.8886 | 445.9118 | 5.725 | 77.8886 | 7.888%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 131 | 1466.2762 | 91.81% | 7.905% | 0.289% | 117.5619 | 0 | 0 | 117.5619 | 0 | 102.0514 | 1.662 | 61.4015 | 102.0514 | 1.662 | 61.4015 | 119.2993 | 1.9429 | 61.4015 | 8.018%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 89 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 566.4697 | 0 | 0 | 566.4697 | 0 | 491.7326 | 1.1292 | 435.4819 | 491.7326 | 1.1292 | 435.4819 | 574.841 | 1.32 | 435.4819 | 7.116%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 423 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 3155.1751 | 0 | 0 | 3155.1751 | 0 | 2738.8976 | 5.3667 | 510.3481 | 2738.8976 | 5.3667 | 510.3481 | 3201.8025 | 6.2738 | 510.3481 | 7.647%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 162 | 124 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 256.5556 | 0 | 0 | 256.5556 | 0 | 222.7069 | 1.5732 | 141.5609 | 222.7069 | 1.5732 | 141.5609 | 260.347 | 1.8391 | 141.5609 | 7.035%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 282 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1736.8596 | 0 | 0 | 1736.8596 | 0 | 1507.7074 | 3.5778 | 421.4044 | 1507.7074 | 3.5778 | 421.4044 | 1762.5271 | 4.1825 | 421.4044 | 7.697%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 7 | 5 | 153.3115 | 98.58% | 1.358% | 0.06577% | 10.7949 | 0 | 0 | 10.7949 | 0 | 9.3707 | 0.063436 | 147.7182 | 9.3707 | 0.063436 | 147.7182 | 10.9545 | 0.074158 | 147.7182 | 7.041%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 40 | 847.524 | 96.52% | 3.329% | 0.1488% | 62.9267 | 0 | 0 | 62.9267 | 0 | 54.6245 | 0.50749 | 107.6362 | 54.6245 | 0.50749 | 107.6362 | 63.8566 | 0.59326 | 107.6362 | 7.425%
2028 | 216 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 419 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 4541.9905 | 0 | 0 | 4541.9905 | 0 | 3942.7438 | 5.316 | 741.6784 | 3942.7438 | 5.316 | 741.6784 | 4609.1125 | 6.2144 | 741.6784 | 8.22%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 24 | 5703.0403 | 99.97% | 0% | 0.03309% | 220.6898 | 0 | 0 | 220.6898 | 0 | 191.5731 | 0.30449 | 629.1504 | 191.5731 | 0.30449 | 629.1504 | 223.9512 | 0.35596 | 629.1504 | 3.87%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 271 | 32313.161 | 99.26% | 0.708% | 0.02831% | 2813.0723 | 0 | 0 | 2813.0723 | 0 | 2441.9301 | 3.4383 | 710.2235 | 2441.9301 | 3.4383 | 710.2235 | 2854.6441 | 4.0194 | 710.2235 | 8.706%
2028 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 3 | 3 | 62.9838 | 99.88% | 0% | 0.1185% | 6.2909 | 0 | 0 | 6.2909 | 0 | 5.4609 | 0.038062 | 143.4751 | 5.4609 | 0.038062 | 143.4751 | 6.3839 | 0.044495 | 143.4751 | 9.988%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 194 | 106 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 67.9648 | 0 | 0 | 67.9648 | 0 | 58.9979 | 1.3449 | 43.8694 | 58.9979 | 1.3449 | 43.8694 | 68.9692 | 1.5721 | 43.8694 | 5.244%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 111 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 286.7483 | 0 | 0 | 286.7483 | 0 | 248.9162 | 1.4083 | 176.7508 | 248.9162 | 1.4083 | 176.7508 | 290.9859 | 1.6463 | 176.7508 | 8.417%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 35 | 1554.328 | 69.02% | 30.62% | 0.3611% | 12.7284 | 0 | 0 | 12.7284 | 0 | 11.0491 | 0.44406 | 24.8822 | 11.0491 | 0.44406 | 24.8822 | 12.9165 | 0.51911 | 24.8822 | 0.8189%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 252 | 24 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 14.5312 | 0 | 0 | 14.5312 | 0 | 12.614 | 0.30449 | 41.426 | 12.614 | 0.30449 | 41.426 | 14.7459 | 0.35596 | 41.426 | 0.7296%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 36 | 33 | 434.8834 | 99.47% | 0.2691% | 0.2608% | 39.6531 | 0 | 0 | 39.6531 | 0 | 34.4215 | 0.41868 | 82.2141 | 34.4215 | 0.41868 | 82.2141 | 40.2391 | 0.48944 | 82.2141 | 9.118%
2028 | 770 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 33 | 62.492 | 96.91% | 0.773% | 2.32% | 4.542 | 0 | 0 | 4.542 | 0 | 3.9427 | 0.41868 | 9.417 | 3.9427 | 0.41868 | 9.417 | 4.6091 | 0.48944 | 9.417 | 7.268%
2028 | 237 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 64 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 898.5928 | 0 | 0 | 898.5928 | 0 | 780.0371 | 0.81199 | 960.6527 | 780.0371 | 0.81199 | 960.6527 | 911.8723 | 0.94922 | 960.6527 | 6.933%
2028 | 176 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 260 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 1134.1213 | 0 | 0 | 1134.1213 | 0 | 984.4912 | 3.2987 | 298.4486 | 984.4912 | 3.2987 | 298.4486 | 1150.8815 | 3.8562 | 298.4486 | 7.487%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 478 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 2255.871 | 0 | 0 | 2255.871 | 0 | 1958.243 | 6.0645 | 322.9013 | 1958.243 | 6.0645 | 322.9013 | 2289.2084 | 7.0895 | 322.9013 | 7.92%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 106 | 88 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 661.8693 | 0 | 0 | 661.8693 | 0 | 574.5457 | 1.1165 | 514.6038 | 574.5457 | 1.1165 | 514.6038 | 671.6504 | 1.3052 | 514.6038 | 8.257%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 50 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 373.3143 | 0 | 0 | 373.3143 | 0 | 324.0612 | 0.63436 | 510.8438 | 324.0612 | 0.63436 | 510.8438 | 378.8312 | 0.74158 | 510.8438 | 8.579%
2028 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 3 | 191.8954 | 99.94% | 0% | 0.06293% | 28.7662 | 0 | 0 | 28.7662 | 0 | 24.9709 | 0.038062 | 656.0617 | 24.9709 | 0.038062 | 656.0617 | 29.1913 | 0.044495 | 656.0617 | 14.99%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 212 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 1096.8917 | 0 | 0 | 1096.8917 | 0 | 952.1735 | 2.6897 | 354.0066 | 952.1735 | 2.6897 | 354.0066 | 1113.1017 | 3.1443 | 354.0066 | 7.426%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 406 | 346 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 950.4557 | 0 | 0 | 950.4557 | 0 | 825.0575 | 4.3898 | 187.9486 | 825.0575 | 4.3898 | 187.9486 | 964.5016 | 5.1317 | 187.9486 | 8.435%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 213 | 190 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 704.8442 | 0 | 0 | 704.8442 | 0 | 611.8507 | 2.4106 | 253.8183 | 611.8507 | 2.4106 | 253.8183 | 715.2604 | 2.818 | 253.8183 | 8.789%
2028 | 235 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 474 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1566.3686 | 0 | 0 | 1566.3686 | 0 | 1359.71 | 6.0138 | 226.0992 | 1359.71 | 6.0138 | 226.0992 | 1589.5165 | 7.0302 | 226.0992 | 6.691%
2028 | 972 | 972-1641 | Tier-2 | Tier-2---13 | Tier-2---5 | 3 | 3 | 295.0839 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.038062 | 0 | 0 | 0.038062 | 0 | 0 | 0.044495 | 0 | 0%
2028 | 972 | 972-1642 | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 9 | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.11419 | 0 | 0 | 0.11419 | 0 | 0 | 0.13348 | 0 | 0%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 543 | 384 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1579.5972 | 0 | 0 | 1579.5972 | 0 | 1371.1933 | 4.8719 | 281.4483 | 1371.1933 | 4.8719 | 281.4483 | 1602.9406 | 5.6953 | 281.4483 | 6.893%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 189 | 155 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 743.7408 | 0 | 0 | 743.7408 | 0 | 645.6155 | 1.9665 | 328.3019 | 645.6155 | 1.9665 | 328.3019 | 754.7318 | 2.2989 | 328.3019 | 8.129%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 161 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 418.2068 | 0 | 0 | 418.2068 | 0 | 363.0307 | 2.0427 | 177.725 | 363.0307 | 2.0427 | 177.725 | 424.3871 | 2.3879 | 177.725 | 8.077%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 53 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 770.7303 | 0 | 0 | 770.7303 | 0 | 669.0441 | 0.67243 | 994.97 | 669.0441 | 0.67243 | 994.97 | 782.1202 | 0.78607 | 994.97 | 8.941%
2028 | 973 | 973-530AE | Tier-3 | Tier-3---17 | Tier-3---5 | 2 | 2 | 388.0062 | 6.476% | 93.52% | 0.007746% | 2.5128 | 0 | 0 | 2.5128 | 0 | 2.1813 | 0.025375 | 85.9627 | 2.1813 | 0.025375 | 85.9627 | 2.5499 | 0.029663 | 85.9627 | 0.6476%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 199 | 197 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 632.9032 | 0 | 0 | 632.9032 | 0 | 549.4012 | 2.4994 | 219.8136 | 549.4012 | 2.4994 | 219.8136 | 642.2563 | 2.9218 | 219.8136 | 9.705%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 389 | 305 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 256.5895 | 0 | 0 | 256.5895 | 0 | 222.7364 | 3.8696 | 57.5602 | 222.7364 | 3.8696 | 57.5602 | 260.3814 | 4.5236 | 57.5602 | 7.346%
2028 | 973 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 111 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 586.0659 | 0 | 0 | 586.0659 | 0 | 508.7434 | 1.4083 | 361.2492 | 508.7434 | 1.4083 | 361.2492 | 594.7268 | 1.6463 | 361.2492 | 8.246%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 30 | 13 | 6417.0381 | 80.3% | 19.69% | 0.01691% | 223.2839 | 0 | 0 | 223.2839 | 0 | 193.8249 | 0.16493 | 1175.1612 | 193.8249 | 0.16493 | 1175.1612 | 226.5836 | 0.19281 | 1175.1612 | 3.48%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 29 | 626.8618 | 65.87% | 33.98% | 0.153% | 41.2906 | 0 | 0 | 41.2906 | 0 | 35.8429 | 0.36793 | 97.4174 | 35.8429 | 0.36793 | 97.4174 | 41.9008 | 0.43012 | 97.4174 | 6.587%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 158 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 439.9608 | 0 | 0 | 439.9608 | 0 | 381.9147 | 2.0046 | 190.5199 | 381.9147 | 2.0046 | 190.5199 | 446.4626 | 2.3434 | 190.5199 | 9.613%
2028 | 354 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 55 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 234.5584 | 0 | 0 | 234.5584 | 0 | 203.612 | 0.6978 | 291.7909 | 203.612 | 0.6978 | 291.7909 | 238.0248 | 0.81574 | 291.7909 | 7.038%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 111 | 85 | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 107.9078 | 0 | 0 | 107.9078 | 0 | 93.671 | 1.0784 | 86.8595 | 93.671 | 1.0784 | 86.8595 | 109.5025 | 1.2607 | 86.8595 | 7.629%
2028 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 38 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 104.7414 | 0 | 0 | 104.7414 | 0 | 90.9224 | 0.48212 | 188.5898 | 90.9224 | 0.48212 | 188.5898 | 106.2893 | 0.5636 | 188.5898 | 9.242%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 24 | 1646.9837 | 34.54% | 65.41% | 0.04829% | 56.8815 | 0 | 0 | 56.8815 | 0 | 49.3769 | 0.30449 | 162.1598 | 49.3769 | 0.30449 | 162.1598 | 57.7221 | 0.35596 | 162.1598 | 3.454%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 70 | 765.4961 | 75% | 24.28% | 0.7274% | 13.8097 | 0 | 0 | 13.8097 | 0 | 11.9877 | 0.88811 | 13.498 | 11.9877 | 0.88811 | 13.498 | 14.0138 | 1.0382 | 13.498 | 1.804%
2028 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | Tier-2---20 | 8 | 1 | 2.3826 | 9.042% | 83.57% | 7.391% | 0.0026929 | 0 | 0 | 0.0026929 | 0 | 0.0023376 | 0.012687 | 0.18425 | 0.0023376 | 0.012687 | 0.18425 | 0.0027327 | 0.014832 | 0.18425 | 0.113%
2028 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | Tier-2---20 | 20 | 3 | 18.2465 | 16.87% | 78.76% | 4.376% | 0.046159 | 0 | 0 | 0.046159 | 0 | 0.040069 | 0.038062 | 1.0527 | 0.040069 | 0.038062 | 1.0527 | 0.046841 | 0.044495 | 1.0527 | 0.253%
2028 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 34 | 31 | 75.2008 | 96.65% | 1.975% | 1.378% | 6.6266 | 0 | 0 | 6.6266 | 0 | 5.7523 | 0.39331 | 14.6256 | 5.7523 | 0.39331 | 14.6256 | 6.7246 | 0.45978 | 14.6256 | 8.812%
2028 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 4 | 70.8201 | 99.8% | 0% | 0.2033% | 5.6541 | 0 | 0 | 5.6541 | 0 | 4.9081 | 0.050749 | 96.7133 | 4.9081 | 0.050749 | 96.7133 | 5.7376 | 0.059326 | 96.7133 | 7.984%
2028 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 3 | 21.8223 | 99.66% | 0% | 0.344% | 2.1747 | 0 | 0 | 2.1747 | 0 | 1.8878 | 0.038062 | 49.5983 | 1.8878 | 0.038062 | 49.5983 | 2.2069 | 0.044495 | 49.5983 | 9.966%
2028 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | Tier-3---17 | 3 | 2 | 0.76155 | 90.92% | 0% | 9.083% | 0.046158 | 0 | 0 | 0.046158 | 0 | 0.040068 | 0.025375 | 1.5791 | 0.040068 | 0.025375 | 1.5791 | 0.04684 | 0.029663 | 1.5791 | 6.061%
2028 | 239 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 332 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 735.9108 | 0 | 0 | 735.9108 | 0 | 638.8185 | 4.2122 | 151.6598 | 638.8185 | 4.2122 | 151.6598 | 746.7861 | 4.9241 | 151.6598 | 11.66%
2028 | 230 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 402 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 425.6045 | 0 | 0 | 425.6045 | 0 | 369.4524 | 5.1003 | 72.4375 | 369.4524 | 5.1003 | 72.4375 | 431.8941 | 5.9623 | 72.4375 | 6.404%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 106 | 1438.3629 | 99.75% | 0% | 0.2509% | 131.1068 | 0 | 0 | 131.1068 | 0 | 113.8093 | 1.3449 | 84.6258 | 113.8093 | 1.3449 | 84.6258 | 133.0443 | 1.5721 | 84.6258 | 9.115%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 9 | 9 | 108.0997 | 99.75% | 0% | 0.2497% | 10.783 | 0 | 0 | 10.783 | 0 | 9.3603 | 0.11419 | 81.9747 | 9.3603 | 0.11419 | 81.9747 | 10.9423 | 0.13348 | 81.9747 | 9.975%
2028 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 32 | 31 | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 394.5296 | 0 | 0 | 394.5296 | 0 | 342.4774 | 0.39331 | 870.7658 | 342.4774 | 0.39331 | 870.7658 | 400.36 | 0.45978 | 870.7658 | 9.681%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 31 | 41.7756 | 94.08% | 0% | 5.924% | 1.6031 | 0 | 0 | 1.6031 | 0 | 1.3916 | 0.39331 | 3.5381 | 1.3916 | 0.39331 | 3.5381 | 1.6268 | 0.45978 | 3.5381 | 3.837%
2028 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 184 | 8 | 259.6903 | 35.49% | 63.12% | 1.387% | 0.40074 | 0 | 0 | 0.40074 | 0 | 0.34787 | 0.1015 | 3.4273 | 0.34787 | 0.1015 | 3.4273 | 0.40666 | 0.11865 | 3.4273 | 0.1543%
2028 | 157 | CB 157 | Tier-3 | Tier-3---21 | Tier-3---11 | 2 | 2 | 6.0775 | 99.43% | 0% | 0.5677% | 0.6043 | 0 | 0 | 0.6043 | 0 | 0.52457 | 0.025375 | 20.673 | 0.52457 | 0.025375 | 20.673 | 0.61323 | 0.029663 | 20.673 | 9.943%
2028 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 154 | 2 | 396.8506 | 79.93% | 19.29% | 0.7702% | 0.41198 | 0 | 0 | 0.41198 | 0 | 0.35762 | 0.025375 | 14.0937 | 0.35762 | 0.025375 | 14.0937 | 0.41807 | 0.029663 | 14.0937 | 0.1038%
2028 | 197 | CB 196 | Tier-2 | Tier-2---15 | Tier-2---9 | 24 | 1 | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.017605 | 0 | 0 | 0.017605 | 0 | 0.015282 | 0.012687 | 1.2045 | 0.015282 | 0.012687 | 1.2045 | 0.017865 | 0.014832 | 1.2045 | 0.01309%
2028 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 478 | 80 | 1342.6559 | 29.9% | 69.37% | 0.7369% | 6.718 | 0 | 0 | 6.718 | 0 | 5.8317 | 1.015 | 5.7456 | 5.8317 | 1.015 | 5.7456 | 6.8173 | 1.1865 | 5.7456 | 0.5004%
2028 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 188 | 133.9861 | 95.12% | 0% | 4.877% | 12.415 | 0 | 0 | 12.415 | 0 | 10.777 | 2.3852 | 4.5183 | 10.777 | 2.3852 | 4.5183 | 12.5984 | 2.7883 | 4.5183 | 9.266%
2028 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 233 | 109 | 195.752 | 9.583% | 88.23% | 2.187% | 0.8776 | 0 | 0 | 0.8776 | 0 | 0.76181 | 1.3829 | 0.55087 | 0.76181 | 1.3829 | 0.55087 | 0.89057 | 1.6166 | 0.55087 | 0.4483%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 229 | 220 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 82.2684 | 0 | 0 | 82.2684 | 0 | 71.4143 | 2.7912 | 25.5855 | 71.4143 | 2.7912 | 25.5855 | 83.4842 | 3.2629 | 25.5855 | 7.765%
2028 | 210 | CB 210 | Tier-2 | Tier-2---21 | Tier-2---17 | 3 | 1 | 1.9532 | 96.21% | 0% | 3.789% | 0.062638 | 0 | 0 | 0.062638 | 0 | 0.054374 | 0.012687 | 4.2857 | 0.054374 | 0.012687 | 4.2857 | 0.063564 | 0.014832 | 4.2857 | 3.207%
2028 | 211 | CB 211 | Tier-2 | Tier-2---21 | Tier-2---24 | 2 | 1 | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.012687 | 0 | 0 | 0.012687 | 0 | 0 | 0.014832 | 0 | 0%
2028 | 212 | CB 212 | Tier-2 | Tier-2---19 | Tier-2---11 | 7 | 6 | 22.9809 | 99.09% | 0% | 0.9069% | 1.9519 | 0 | 0 | 1.9519 | 0 | 1.6944 | 0.076124 | 22.2585 | 1.6944 | 0.076124 | 22.2585 | 1.9808 | 0.08899 | 22.2585 | 8.494%
2028 | 214 | CB 214 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 59.1996 | 99.88% | 0% | 0.1188% | 3.942 | 0 | 0 | 3.942 | 0 | 3.4219 | 0.025375 | 134.8543 | 3.4219 | 0.025375 | 134.8543 | 4.0002 | 0.029663 | 134.8543 | 6.659%
2028 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 133.9133 | 99.89% | 0% | 0.1056% | 8.0263 | 0 | 0 | 8.0263 | 0 | 6.9674 | 0.038062 | 183.0536 | 6.9674 | 0.038062 | 183.0536 | 8.1449 | 0.044495 | 183.0536 | 5.994%
2028 | 217 | CB 217 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 26.6678 | 99.71% | 0% | 0.2895% | 1.7727 | 0 | 0 | 1.7727 | 0 | 1.5388 | 0.025375 | 60.6444 | 1.5388 | 0.025375 | 60.6444 | 1.7989 | 0.029663 | 60.6444 | 6.647%
2028 | 220 | CB 220 | Tier-3 | Tier-3---21 | Tier-3---24 | 2 | 1 | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.012687 | 0 | 0 | 0.012687 | 0 | 0 | 0.014832 | 0 | 0%
2028 | 1235 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 12 | 10 | 212.8275 | 99.81% | 0% | 0.1866% | 17.7025 | 0 | 0 | 17.7025 | 0 | 15.367 | 0.12687 | 121.1208 | 15.367 | 0.12687 | 121.1208 | 17.9641 | 0.14832 | 121.1208 | 8.318%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 174 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 166.1116 | 0 | 0 | 166.1116 | 0 | 144.1957 | 2.2076 | 65.3182 | 144.1957 | 2.2076 | 65.3182 | 168.5664 | 2.5807 | 65.3182 | 6.645%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 259 | 144 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 88.9279 | 0 | 0 | 88.9279 | 0 | 77.1952 | 1.827 | 42.2531 | 77.1952 | 1.827 | 42.2531 | 90.2421 | 2.1357 | 42.2531 | 5.414%
2028 | 230 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 613 | 396 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 263.2844 | 0 | 0 | 263.2844 | 0 | 228.548 | 5.0242 | 45.4897 | 228.548 | 5.0242 | 45.4897 | 267.1752 | 5.8733 | 45.4897 | 6.378%
2028 | 232 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 201 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 186.0305 | 0 | 0 | 186.0305 | 0 | 161.4866 | 2.5501 | 63.3245 | 161.4866 | 2.5501 | 63.3245 | 188.7796 | 2.9811 | 63.3245 | 5.646%
2028 | 971 | CB 235 | Tier-2 | Tier-2---12 | Tier-2---11 | 6 | 4 | 443.5427 | 99.96% | 0% | 0.03939% | 29.5579 | 0 | 0 | 29.5579 | 0 | 25.6582 | 0.050749 | 505.5878 | 25.6582 | 0.050749 | 505.5878 | 29.9947 | 0.059326 | 505.5878 | 6.664%
2028 | 235 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 161 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 592.8145 | 0 | 0 | 592.8145 | 0 | 514.6016 | 2.0427 | 251.928 | 514.6016 | 2.0427 | 251.928 | 601.5752 | 2.3879 | 251.928 | 4.664%
2028 | 236 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 41 | 14 | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 71.7723 | 0 | 0 | 71.7723 | 0 | 62.3031 | 0.17762 | 350.762 | 62.3031 | 0.17762 | 350.762 | 72.833 | 0.20764 | 350.762 | 3.399%
2028 | 239 | CB 239 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 1 | 10.6776 | 99.64% | 0% | 0.3633% | 0.53194 | 0 | 0 | 0.53194 | 0 | 0.46176 | 0.012687 | 36.3955 | 0.46176 | 0.012687 | 36.3955 | 0.5398 | 0.014832 | 36.3955 | 4.982%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 114 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 59.0928 | 0 | 0 | 59.0928 | 0 | 51.2964 | 1.4464 | 35.4661 | 51.2964 | 1.4464 | 35.4661 | 59.966 | 1.6908 | 35.4661 | 4.679%
2028 | 240 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 35 | 406.8184 | 64.36% | 35.02% | 0.6193% | 10.5338 | 0 | 0 | 10.5338 | 0 | 9.1441 | 0.44406 | 20.5922 | 9.1441 | 0.44406 | 20.5922 | 10.6895 | 0.51911 | 20.5922 | 2.589%
2028 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 197 | 16 | 295.5508 | 37.5% | 61.39% | 1.106% | 0.90024 | 0 | 0 | 0.90024 | 0 | 0.78147 | 0.203 | 3.8497 | 0.78147 | 0.203 | 3.8497 | 0.91355 | 0.23731 | 3.8497 | 0.3046%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 180 | 1438.4419 | 90% | 9.47% | 0.5268% | 76.9095 | 0 | 0 | 76.9095 | 0 | 66.7625 | 2.2837 | 29.2342 | 66.7625 | 2.2837 | 29.2342 | 78.0461 | 2.6697 | 29.2342 | 5.347%
2028 | 246 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 29 | 379.7423 | 70.28% | 29.01% | 0.71% | 8.5995 | 0 | 0 | 8.5995 | 0 | 7.4649 | 0.36793 | 20.2889 | 7.4649 | 0.36793 | 20.2889 | 8.7266 | 0.43012 | 20.2889 | 2.265%
2028 | 240 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 136 | 62 | 962.1527 | 99.5% | 0% | 0.4991% | 43.6439 | 0 | 0 | 43.6439 | 0 | 37.8858 | 0.78661 | 48.1632 | 37.8858 | 0.78661 | 48.1632 | 44.2889 | 0.91956 | 48.1632 | 4.536%
2028 | 1233 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 101 | 65 | 826.9208 | 97.04% | 2.672% | 0.2884% | 51.6421 | 0 | 0 | 51.6421 | 0 | 44.8287 | 0.82467 | 54.3593 | 44.8287 | 0.82467 | 54.3593 | 52.4053 | 0.96405 | 54.3593 | 6.245%
2028 | 280 | CB 280 | Tier-2 | Tier-2---14 | Tier-2---4 | 108 | 32 | 310.7968 | 16.09% | 83.08% | 0.8251% | 1.4817 | 0 | 0 | 1.4817 | 0 | 1.2862 | 0.40599 | 3.168 | 1.2862 | 0.40599 | 3.168 | 1.5036 | 0.47461 | 3.168 | 0.4767%
2028 | 283 | CB 283 | Tier-3 | Tier-3---21 | Tier-3---11 | 2 | 2 | 6.0451 | 99.41% | 0% | 0.5857% | 0.60097 | 0 | 0 | 0.60097 | 0 | 0.52168 | 0.025375 | 20.5593 | 0.52168 | 0.025375 | 20.5593 | 0.60986 | 0.029663 | 20.5593 | 9.941%
2028 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 17 | 13 | 94.6686 | 66.47% | 32.93% | 0.6021% | 4.8122 | 0 | 0 | 4.8122 | 0 | 4.1773 | 0.16493 | 25.3268 | 4.1773 | 0.16493 | 25.3268 | 4.8833 | 0.19281 | 25.3268 | 5.083%
2028 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 21 | 1 | 10.7713 | 97.26% | 0% | 2.741% | 0.049886 | 0 | 0 | 0.049886 | 0 | 0.043304 | 0.012687 | 3.4132 | 0.043304 | 0.012687 | 3.4132 | 0.050623 | 0.014832 | 3.4132 | 0.4631%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 21 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 138.7612 | 0 | 0 | 138.7612 | 0 | 120.4538 | 0.26643 | 452.0978 | 120.4538 | 0.26643 | 452.0978 | 140.8119 | 0.31146 | 452.0978 | 9.526%
2028 | 200 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 34 | 8 | 215.2852 | 96.83% | 2.614% | 0.5577% | 4.9049 | 0 | 0 | 4.9049 | 0 | 4.2578 | 0.1015 | 41.949 | 4.2578 | 0.1015 | 41.949 | 4.9774 | 0.11865 | 41.949 | 2.278%
2028 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 156 | 73 | 124.2501 | 33.35% | 64.03% | 2.615% | 1.9393 | 0 | 0 | 1.9393 | 0 | 1.6834 | 0.92617 | 1.8176 | 1.6834 | 0.92617 | 1.8176 | 1.968 | 1.0827 | 1.8176 | 1.561%
2028 | 200 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 48 | 25 | 261.2105 | 99.38% | 0% | 0.6196% | 13.5204 | 0 | 0 | 13.5204 | 0 | 11.7366 | 0.31718 | 37.0027 | 11.7366 | 0.31718 | 37.0027 | 13.7202 | 0.37079 | 37.0027 | 5.176%
2028 | 350 | CB 350 | Tier-2 | Tier-2---15 | Tier-2---11 | 4 | 1 | 133.5736 | 99.92% | 0% | 0.07821% | 3.3367 | 0 | 0 | 3.3367 | 0 | 2.8965 | 0.012687 | 228.2991 | 2.8965 | 0.012687 | 228.2991 | 3.386 | 0.014832 | 228.2991 | 2.498%
2028 | 353 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 110 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 1039.3116 | 0 | 0 | 1039.3116 | 0 | 902.1902 | 1.3956 | 646.4524 | 902.1902 | 1.3956 | 646.4524 | 1054.6706 | 1.6315 | 646.4524 | 7.119%
2028 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 5 | 4 | 87.8741 | 99.22% | 0.6237% | 0.1541% | 6.9753 | 0 | 0 | 6.9753 | 0 | 6.055 | 0.050749 | 119.3118 | 6.055 | 0.050749 | 119.3118 | 7.0783 | 0.059326 | 119.3118 | 7.938%
2028 | 353 | CB 353 | Tier-2 | Tier-2---19 | Tier-2---11 | 4 | 1 | 7.5897 | 98.6% | 0% | 1.398% | 0.18709 | 0 | 0 | 0.18709 | 0 | 0.16241 | 0.012687 | 12.8007 | 0.16241 | 0.012687 | 12.8007 | 0.18985 | 0.014832 | 12.8007 | 2.465%
2028 | 354 | CB 354 | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 2 | 12.0695 | 99.46% | 0% | 0.538% | 0.8003 | 0 | 0 | 0.8003 | 0 | 0.69472 | 0.025375 | 27.3784 | 0.69472 | 0.025375 | 27.3784 | 0.81213 | 0.029663 | 27.3784 | 6.631%
2028 | 356 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 168 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 620.6565 | 0 | 0 | 620.6565 | 0 | 538.7703 | 2.1315 | 252.77 | 538.7703 | 2.1315 | 252.77 | 629.8286 | 2.4917 | 252.77 | 5.498%
2028 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 2 | 6.8062 | 99.1% | 0% | 0.8997% | 0.44966 | 0 | 0 | 0.44966 | 0 | 0.39034 | 0.025375 | 15.3829 | 0.39034 | 0.025375 | 15.3829 | 0.45631 | 0.029663 | 15.3829 | 6.607%
2028 | 1166 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 106 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 383.8802 | 0 | 0 | 383.8802 | 0 | 333.2331 | 1.3449 | 247.784 | 333.2331 | 1.3449 | 247.784 | 389.5532 | 1.5721 | 247.784 | 6.282%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 21 | 6 | 861.4334 | 18.88% | 81.11% | 0.0161% | 4.6462 | 0 | 0 | 4.6462 | 0 | 4.0332 | 0.076124 | 52.9824 | 4.0332 | 0.076124 | 52.9824 | 4.7149 | 0.08899 | 52.9824 | 0.5394%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 145 | 5 | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.33127 | 0 | 0 | 0.33127 | 0 | 0.28757 | 0.063436 | 4.5332 | 0.28757 | 0.063436 | 4.5332 | 0.33617 | 0.074158 | 4.5332 | 0.04946%
2028 | 442 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 94 | 87 | 1133.0808 | 94.08% | 5.666% | 0.2577% | 98.6577 | 0 | 0 | 98.6577 | 0 | 85.6413 | 1.1038 | 77.5881 | 85.6413 | 1.1038 | 77.5881 | 100.1156 | 1.2903 | 77.5881 | 8.707%
2028 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 36 | 22 | 67.1473 | 98.29% | 0% | 1.71% | 4.0333 | 0 | 0 | 4.0333 | 0 | 3.5011 | 0.27912 | 12.5435 | 3.5011 | 0.27912 | 12.5435 | 4.0929 | 0.32629 | 12.5435 | 6.007%
2028 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 17 | 15 | 117.4434 | 97.68% | 1.947% | 0.3705% | 10.1225 | 0 | 0 | 10.1225 | 0 | 8.787 | 0.19031 | 46.1719 | 8.787 | 0.19031 | 46.1719 | 10.272 | 0.22247 | 46.1719 | 8.619%
2028 | 449 | CB 449 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 7.8127 | 98.22% | 0% | 1.784% | 0.4604 | 0 | 0 | 0.4604 | 0 | 0.39966 | 0.038062 | 10.5002 | 0.39966 | 0.038062 | 10.5002 | 0.4672 | 0.044495 | 10.5002 | 5.893%
2028 | 443 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 36 | 27 | 101.8709 | 98.65% | 0% | 1.347% | 7.5374 | 0 | 0 | 7.5374 | 0 | 6.543 | 0.34256 | 19.1003 | 6.543 | 0.34256 | 19.1003 | 7.6488 | 0.40045 | 19.1003 | 7.399%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 48 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 83.2699 | 0 | 0 | 83.2699 | 0 | 72.2837 | 0.60899 | 118.6945 | 72.2837 | 0.60899 | 118.6945 | 84.5005 | 0.71192 | 118.6945 | 1.203%
2028 | 1299 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 6 | 19.4193 | 94.64% | 0% | 5.361% | 0.35571 | 0 | 0 | 0.35571 | 0 | 0.30878 | 0.076124 | 4.0563 | 0.30878 | 0.076124 | 4.0563 | 0.36097 | 0.08899 | 4.0563 | 1.832%
2028 | 520 | CB 520 | Tier-2 | Tier-2---21 | Tier-2---11 | 2 | 2 | 1.7668 | 97.86% | 0% | 2.14% | 0.1729 | 0 | 0 | 0.1729 | 0 | 0.15009 | 0.025375 | 5.9149 | 0.15009 | 0.025375 | 5.9149 | 0.17546 | 0.029663 | 5.9149 | 9.786%
2028 | 520 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 14 | 11 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.16207 | 0 | 0 | 0.16207 | 0 | 0.14069 | 0.13956 | 1.0081 | 0.14069 | 0.13956 | 1.0081 | 0.16447 | 0.16315 | 1.0081 | 1.319%
2028 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 129 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 49.0233 | 0 | 0 | 49.0233 | 0 | 42.5554 | 1.6367 | 26.0014 | 42.5554 | 1.6367 | 26.0014 | 49.7477 | 1.9133 | 26.0014 | 4.563%
2028 | 522 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 126 | 305.5692 | 37.2% | 61.32% | 1.484% | 5.5296 | 0 | 0 | 5.5296 | 0 | 4.8001 | 1.5986 | 3.0027 | 4.8001 | 1.5986 | 3.0027 | 5.6113 | 1.8688 | 3.0027 | 1.81%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 90 | 12 | 481.3309 | 94.25% | 5.298% | 0.4514% | 6.0487 | 0 | 0 | 6.0487 | 0 | 5.2507 | 0.15225 | 34.488 | 5.2507 | 0.15225 | 34.488 | 6.1381 | 0.17798 | 34.488 | 1.257%
2028 | 1160 | CB 533 | Tier-2 | Tier-2---20 | Tier-2---20 | 14 | 1 | 10.6053 | 3.364% | 93.72% | 2.92% | 0.0025483 | 0 | 0 | 0.0025483 | 0 | 0.0022121 | 0.012687 | 0.17436 | 0.0022121 | 0.012687 | 0.17436 | 0.002586 | 0.014832 | 0.17436 | 0.02403%
2028 | 1161 | CB 534 | Tier-2 | Tier-2---21 | Tier-2---20 | 12 | 6 | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11347 | 0 | 0 | 0.11347 | 0 | 0.098496 | 0.076124 | 1.2939 | 0.098496 | 0.076124 | 1.2939 | 0.11514 | 0.08899 | 1.2939 | 1.8%
2028 | 535 | CB 535 | Tier-2 | Tier-2---16 | Tier-2---8 | 10 | 5 | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25563 | 0 | 0 | 0.25563 | 0 | 0.22191 | 0.063436 | 3.4981 | 0.22191 | 0.063436 | 3.4981 | 0.25941 | 0.074158 | 3.4981 | 0.2293%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 39 | 33 | 54.1099 | 76.19% | 21.99% | 1.82% | 3.4885 | 0 | 0 | 3.4885 | 0 | 3.0282 | 0.41868 | 7.2328 | 3.0282 | 0.41868 | 7.2328 | 3.54 | 0.48944 | 7.2328 | 6.447%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 5 | 67.245 | 99.24% | 0% | 0.7576% | 2.0855 | 0 | 0 | 2.0855 | 0 | 1.8103 | 0.063436 | 28.5378 | 1.8103 | 0.063436 | 28.5378 | 2.1163 | 0.074158 | 28.5378 | 3.101%
2028 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 43 | 35 | 949.4775 | 95.45% | 4.414% | 0.1311% | 73.7702 | 0 | 0 | 73.7702 | 0 | 64.0374 | 0.44406 | 144.2104 | 64.0374 | 0.44406 | 144.2104 | 74.8604 | 0.51911 | 144.2104 | 7.77%
2028 | 542 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 19 | 13 | 417.7025 | 78.37% | 21.49% | 0.1463% | 22.397 | 0 | 0 | 22.397 | 0 | 19.4421 | 0.16493 | 117.8773 | 19.4421 | 0.16493 | 117.8773 | 22.728 | 0.19281 | 117.8773 | 5.362%
2028 | 1094 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 262 | 4323.2442 | 99.81% | 0% | 0.1903% | 306.3779 | 0 | 0 | 306.3779 | 0 | 265.956 | 3.3241 | 80.0091 | 265.956 | 3.3241 | 80.0091 | 310.9056 | 3.8859 | 80.0091 | 7.087%
2028 | 67 | CB 67 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 10.8761 | 99.3% | 0% | 0.7025% | 0.71998 | 0 | 0 | 0.71998 | 0 | 0.62499 | 0.025375 | 24.6305 | 0.62499 | 0.025375 | 24.6305 | 0.73062 | 0.029663 | 24.6305 | 6.62%
2028 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 53 | 53 | 55.0677 | 92.66% | 4.028% | 3.312% | 5.1026 | 0 | 0 | 5.1026 | 0 | 4.4294 | 0.67243 | 6.5871 | 4.4294 | 0.67243 | 6.5871 | 5.178 | 0.78607 | 6.5871 | 9.266%
2028 | 78 | CB 78 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 3 | 25.281 | 99.56% | 0% | 0.4423% | 1.8877 | 0 | 0 | 1.8877 | 0 | 1.6386 | 0.038062 | 43.0519 | 1.6386 | 0.038062 | 43.0519 | 1.9156 | 0.044495 | 43.0519 | 7.467%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 24 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 27.6164 | 0 | 0 | 27.6164 | 0 | 23.9728 | 0.30449 | 78.7297 | 23.9728 | 0.30449 | 78.7297 | 28.0245 | 0.35596 | 78.7297 | 0.3223%
2028 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 12 | 8 | 42.6475 | 99.43% | 0% | 0.5747% | 2.8268 | 0 | 0 | 2.8268 | 0 | 2.4539 | 0.1015 | 24.1765 | 2.4539 | 0.1015 | 24.1765 | 2.8686 | 0.11865 | 24.1765 | 6.628%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 39 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 209.3563 | 0 | 0 | 209.3563 | 0 | 181.7349 | 0.4948 | 367.2864 | 181.7349 | 0.4948 | 367.2864 | 212.4502 | 0.57843 | 367.2864 | 7.634%
2028 | 75 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 30 | 337.7351 | 93.43% | 6.078% | 0.496% | 13.9205 | 0 | 0 | 13.9205 | 0 | 12.0839 | 0.38062 | 31.748 | 12.0839 | 0.38062 | 31.748 | 14.1262 | 0.44495 | 31.748 | 4.122%
2028 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 53 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 112.8379 | 0 | 0 | 112.8379 | 0 | 97.9506 | 0.67243 | 145.6674 | 97.9506 | 0.67243 | 145.6674 | 114.5054 | 0.78607 | 145.6674 | 6.818%
2028 | 236 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 4 | 3 | 251.0066 | 99.97% | 0% | 0.03372% | 18.8191 | 0 | 0 | 18.8191 | 0 | 16.3362 | 0.038062 | 429.2023 | 16.3362 | 0.038062 | 429.2023 | 19.0973 | 0.044495 | 429.2023 | 7.497%
2028 | 235 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 114 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 778.2289 | 0 | 0 | 778.2289 | 0 | 675.5534 | 1.4464 | 467.0743 | 675.5534 | 1.4464 | 467.0743 | 789.7296 | 1.6908 | 467.0743 | 6.793%
2028 | 973 | CB 973 | Tier-2 | Tier-2---14 | Tier-2---11 | 7 | 4 | 310.4015 | 99.93% | 0% | 0.0686% | 17.7251 | 0 | 0 | 17.7251 | 0 | 15.3865 | 0.050749 | 303.1874 | 15.3865 | 0.050749 | 303.1874 | 17.987 | 0.059326 | 303.1874 | 5.71%
2028 | 973 | CB 974 | Tier-2 | Tier-2---12 | Tier-2---11 | 7 | 5 | 334.3039 | 99.93% | 0% | 0.06503% | 23.8633 | 0 | 0 | 23.8633 | 0 | 20.7149 | 0.063436 | 326.546 | 20.7149 | 0.063436 | 326.546 | 24.216 | 0.074158 | 326.546 | 7.138%
2028 | 970 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 11 | 8 | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 94.4014 | 0 | 0 | 94.4014 | 0 | 81.9466 | 0.1015 | 807.3691 | 81.9466 | 0.1015 | 807.3691 | 95.7965 | 0.11865 | 807.3691 | 7.237%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 35 | 24 | 387.8494 | 99.7% | 0% | 0.3041% | 26.5145 | 0 | 0 | 26.5145 | 0 | 23.0163 | 0.30449 | 75.5885 | 23.0163 | 0.30449 | 75.5885 | 26.9063 | 0.35596 | 75.5885 | 6.836%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 14 | 11 | 132.7571 | 99.65% | 0% | 0.354% | 10.394 | 0 | 0 | 10.394 | 0 | 9.0227 | 0.13956 | 64.6507 | 9.0227 | 0.13956 | 64.6507 | 10.5476 | 0.16315 | 64.6507 | 7.829%
2028 | 982 | CB 982 | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.012687 | 0 | 0 | 0.012687 | 0 | 0 | 0.014832 | 0 | 0%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 6 | 2 | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.82631 | 0 | 0 | 0.82631 | 0 | 0.71729 | 0.025375 | 28.268 | 0.71729 | 0.025375 | 28.268 | 0.83852 | 0.029663 | 28.268 | 3.007%
2028 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 15.4911 | 99.81% | 0% | 0.1868% | 1.5462 | 0 | 0 | 1.5462 | 0 | 1.3422 | 0.025375 | 52.8961 | 1.3422 | 0.025375 | 52.8961 | 1.5691 | 0.029663 | 52.8961 | 9.981%
2028 | 520 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 161 | 346.5871 | 36.93% | 61.45% | 1.621% | 5.5543 | 0 | 0 | 5.5543 | 0 | 4.8215 | 2.0427 | 2.3604 | 4.8215 | 2.0427 | 2.3604 | 5.6364 | 2.3879 | 2.3604 | 1.603%
2028 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 109 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 61.1907 | 0 | 0 | 61.1907 | 0 | 53.1175 | 1.3829 | 38.4098 | 53.1175 | 1.3829 | 38.4098 | 62.095 | 1.6166 | 38.4098 | 5.943%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 80 | 67 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 125.5197 | 0 | 0 | 125.5197 | 0 | 108.9593 | 0.85005 | 128.1801 | 108.9593 | 0.85005 | 128.1801 | 127.3746 | 0.99372 | 128.1801 | 8.195%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 116 | 86 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 374.0843 | 0 | 0 | 374.0843 | 0 | 324.7295 | 1.0911 | 297.6148 | 324.7295 | 1.0911 | 297.6148 | 379.6125 | 1.2755 | 297.6148 | 7.307%
2028 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 403 | 5 | 638.0788 | 99.02% | 0% | 0.9838% | 0.78387 | 0 | 0 | 0.78387 | 0 | 0.68045 | 0.063436 | 10.7265 | 0.68045 | 0.063436 | 10.7265 | 0.79546 | 0.074158 | 10.7265 | 0.1228%
2028 | 221 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 190 | 153 | 6915.6819 | 99% | 0.9206% | 0.07911% | 551.3273 | 0 | 0 | 551.3273 | 0 | 478.5881 | 1.9412 | 246.548 | 478.5881 | 1.9412 | 246.548 | 559.4749 | 2.2692 | 246.548 | 7.972%
2028 | 222 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 247 | 132 | 3027.5479 | 94.73% | 5.109% | 0.164% | 153.2642 | 0 | 0 | 153.2642 | 0 | 133.0433 | 1.6747 | 79.442 | 133.0433 | 1.6747 | 79.442 | 155.5291 | 1.9578 | 79.442 | 5.062%
2028 | 237 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 179 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 524.2711 | 0 | 0 | 524.2711 | 0 | 455.1015 | 2.271 | 200.3947 | 455.1015 | 2.271 | 200.3947 | 532.0188 | 2.6549 | 200.3947 | 4.985%
2028 | 237 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 62 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 269.606 | 0 | 0 | 269.606 | 0 | 234.0356 | 0.78661 | 297.5236 | 234.0356 | 0.78661 | 297.5236 | 273.5903 | 0.91956 | 297.5236 | 5.155%
2028 | 237 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 93 | 916.1972 | 69.5% | 30.07% | 0.4286% | 24.5712 | 0 | 0 | 24.5712 | 0 | 21.3294 | 1.1799 | 18.077 | 21.3294 | 1.1799 | 18.077 | 24.9343 | 1.3793 | 18.077 | 2.682%
2028 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 29.7534 | 99.88% | 0% | 0.1212% | 2.9717 | 0 | 0 | 2.9717 | 0 | 2.5797 | 0.025375 | 101.6631 | 2.5797 | 0.025375 | 101.6631 | 3.0156 | 0.029663 | 101.6631 | 9.988%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 58 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 228.7681 | 0 | 0 | 228.7681 | 0 | 198.5856 | 0.73586 | 269.8677 | 198.5856 | 0.73586 | 269.8677 | 232.1488 | 0.86023 | 269.8677 | 6.117%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 225 | 184 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 257.6221 | 0 | 0 | 257.6221 | 0 | 223.6328 | 2.3345 | 95.7963 | 223.6328 | 2.3345 | 95.7963 | 261.4292 | 2.729 | 95.7963 | 7.664%
2028 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 220 | 27 | 94.186 | 2.003% | 94.63% | 3.363% | 0.023154 | 0 | 0 | 0.023154 | 0 | 0.020099 | 0.34256 | 0.058674 | 0.020099 | 0.34256 | 0.058674 | 0.023496 | 0.40045 | 0.058674 | 0.02458%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 138 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 71.5721 | 0 | 0 | 71.5721 | 0 | 62.1293 | 1.7508 | 35.4853 | 62.1293 | 1.7508 | 35.4853 | 72.6298 | 2.0468 | 35.4853 | 3.468%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 235 | 175 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 263.5885 | 0 | 0 | 263.5885 | 0 | 228.812 | 2.2203 | 103.0556 | 228.812 | 2.2203 | 103.0556 | 267.4838 | 2.5955 | 103.0556 | 7.087%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 122 | 74 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 562.6656 | 0 | 0 | 562.6656 | 0 | 488.4304 | 0.93886 | 520.238 | 488.4304 | 0.93886 | 520.238 | 570.9807 | 1.0975 | 520.238 | 6.025%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 306 | 6920.124 | 97.57% | 2.306% | 0.1195% | 477.1808 | 0 | 0 | 477.1808 | 0 | 414.2241 | 3.8823 | 106.6952 | 414.2241 | 3.8823 | 106.6952 | 484.2326 | 4.5385 | 106.6952 | 6.896%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 125 | 117 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 552.7852 | 0 | 0 | 552.7852 | 0 | 479.8536 | 1.4844 | 323.2615 | 479.8536 | 1.4844 | 323.2615 | 560.9543 | 1.7353 | 323.2615 | 9.296%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 103 | 81 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 295.9408 | 0 | 0 | 295.9408 | 0 | 256.8959 | 1.0277 | 249.9788 | 256.8959 | 1.0277 | 249.9788 | 300.3142 | 1.2014 | 249.9788 | 7.823%

## RIDI
RIDI - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 6500 | 2645380.3809 | 32764.9636 | 1.239% | 31255.5493 | 725.4653 | 43.0834 | 31255.5493 | 725.4653 | 43.0834 | 32925.5761 | 764.2279 | 43.0834
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 6500 | 2684191.9375 | 41211.9775 | 1.535% | 37502.3381 | 692.0446 | 54.1906 | 37502.3381 | 692.0446 | 54.1906 | 41617.0068 | 767.9742 | 54.1906
[9 empty] | Capital Cost only in Year 0 | 0.117 | K$/inspection | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 6500 | 2741256.7369 | 52318.3797 | 1.909% | 45415.7638 | 660.1636 | 68.7947 | 45415.7638 | 660.1636 | 68.7947 | 53091.5453 | 771.7387 | 68.7947
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 19500 | 8070829.0553 | 126295.3208 | 1.565% | 114173.6512 | 2077.6735 | 54.9526 | 114173.6512 | 2077.6735 | 54.9526 | 127634.1283 | 2303.9408 | 55.3982
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 29% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units in Scope (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 28 | 2758.283 | 96.49% | 3.415% | 0.0991% | 207.7896 | 0 | 0 | 207.7896 | 0 | 198.2172 | 3.1251 | 63.4279 | 198.2172 | 3.1251 | 63.4279 | 208.8082 | 3.2921 | 63.4279 | 7.533%
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 4 | 3 | 117.1572 | 99.03% | 0.8725% | 0.09309% | 25.2356 | 0 | 0 | 25.2356 | 0 | 24.0731 | 0.33483 | 71.8964 | 24.0731 | 0.33483 | 71.8964 | 25.3593 | 0.35272 | 71.8964 | 21.54%
2026 | 1001 | 1001-1232F | Tier-1 | Non-HFTD---15 | Non-HFTD---17 | 3 | 1 | 3.7082 | 98.25% | 0% | 1.746% | 0.3522 | 0 | 0 | 0.3522 | 0 | 0.33597 | 0.11161 | 3.0102 | 0.33597 | 0.11161 | 3.0102 | 0.35392 | 0.11757 | 3.0102 | 9.498%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 2 | 4222.2471 | 91.41% | 8.486% | 0.103% | 15.3326 | 0 | 0 | 15.3326 | 0 | 14.6263 | 0.22322 | 65.5239 | 14.6263 | 0.22322 | 65.5239 | 15.4078 | 0.23515 | 65.5239 | 0.3631%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 12 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 234.7753 | 0 | 0 | 234.7753 | 0 | 223.9597 | 1.3393 | 167.2189 | 223.9597 | 1.3393 | 167.2189 | 235.9262 | 1.4109 | 167.2189 | 0.6678%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 1 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 23.6333 | 0 | 0 | 23.6333 | 0 | 22.5445 | 0.11161 | 201.9938 | 22.5445 | 0.11161 | 201.9938 | 23.7491 | 0.11757 | 201.9938 | 0.335%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 1 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 32.3988 | 0 | 0 | 32.3988 | 0 | 30.9063 | 0.11161 | 276.9131 | 30.9063 | 0.11161 | 276.9131 | 32.5577 | 0.11757 | 276.9131 | 0.1721%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 1 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 20.3699 | 0 | 0 | 20.3699 | 0 | 19.4315 | 0.11161 | 174.1021 | 19.4315 | 0.11161 | 174.1021 | 20.4698 | 0.11757 | 174.1021 | 0.2078%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 1 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 16.3886 | 0 | 0 | 16.3886 | 0 | 15.6336 | 0.11161 | 140.0732 | 15.6336 | 0.11161 | 140.0732 | 16.4689 | 0.11757 | 140.0732 | 0.3231%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 6 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 33.7204 | 0 | 0 | 33.7204 | 0 | 32.167 | 0.66966 | 48.0348 | 32.167 | 0.66966 | 48.0348 | 33.8857 | 0.70544 | 48.0348 | 0.3561%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 35 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 98.1706 | 0 | 0 | 98.1706 | 0 | 93.6481 | 3.9064 | 23.9733 | 93.6481 | 3.9064 | 23.9733 | 98.6519 | 4.1151 | 23.9733 | 2.601%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 14 | 585.5086 | 87.68% | 11.85% | 0.4758% | 17.5147 | 0 | 0 | 17.5147 | 0 | 16.7079 | 1.5625 | 10.6927 | 16.7079 | 1.5625 | 10.6927 | 17.6006 | 1.646 | 10.6927 | 2.991%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 2 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 35.0114 | 0 | 0 | 35.0114 | 0 | 33.3985 | 0.22322 | 149.6213 | 33.3985 | 0.22322 | 149.6213 | 35.183 | 0.23515 | 149.6213 | 0.2963%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 98 | 1 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 19.3297 | 0 | 0 | 19.3297 | 0 | 18.4392 | 0.11161 | 165.2114 | 18.4392 | 0.11161 | 165.2114 | 19.4245 | 0.11757 | 165.2114 | 0.2919%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 3 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 59.5045 | 0 | 0 | 59.5045 | 0 | 56.7632 | 0.33483 | 169.5284 | 56.7632 | 0.33483 | 169.5284 | 59.7962 | 0.35272 | 169.5284 | 0.235%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 7 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 120.3001 | 0 | 0 | 120.3001 | 0 | 114.7581 | 0.78127 | 146.8866 | 114.7581 | 0.78127 | 146.8866 | 120.8898 | 0.82301 | 146.8866 | 0.4236%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 13 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 236.4882 | 0 | 0 | 236.4882 | 0 | 225.5937 | 1.4509 | 155.482 | 225.5937 | 1.4509 | 155.482 | 237.6474 | 1.5285 | 155.482 | 0.8858%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 49 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 413.8166 | 0 | 0 | 413.8166 | 0 | 394.7529 | 5.4689 | 72.1815 | 394.7529 | 5.4689 | 72.1815 | 415.8451 | 5.7611 | 72.1815 | 2.593%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 16 | 6 | 17.9659 | 86.84% | 10.72% | 2.434% | 1.6967 | 0 | 0 | 1.6967 | 0 | 1.6186 | 0.66966 | 2.417 | 1.6186 | 0.66966 | 2.417 | 1.705 | 0.70544 | 2.417 | 9.444%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 4 | 1 | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.25034 | 0 | 0 | 0.25034 | 0 | 0.23881 | 0.11161 | 2.1397 | 0.23881 | 0.11161 | 2.1397 | 0.25157 | 0.11757 | 2.1397 | 0.9245%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 44 | 5 | 730.5479 | 99.24% | 0.5863% | 0.172% | 23.8923 | 0 | 0 | 23.8923 | 0 | 22.7917 | 0.55805 | 40.8416 | 22.7917 | 0.55805 | 40.8416 | 24.0094 | 0.58787 | 40.8416 | 3.27%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 122 | 29 | 919.3728 | 93.93% | 5.62% | 0.4487% | 59.5303 | 0 | 0 | 59.5303 | 0 | 56.7879 | 3.2367 | 17.545 | 56.7879 | 3.2367 | 17.545 | 59.8221 | 3.4096 | 17.545 | 6.475%
2026 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 8 | 509.5021 | 91.97% | 7.519% | 0.512% | 13.5889 | 0 | 0 | 13.5889 | 0 | 12.9629 | 0.89288 | 14.518 | 12.9629 | 0.89288 | 14.518 | 13.6555 | 0.94059 | 14.518 | 2.667%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 29 | 1 | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.2396 | 0 | 0 | 1.2396 | 0 | 1.1825 | 0.11161 | 10.5952 | 1.1825 | 0.11161 | 10.5952 | 1.2457 | 0.11757 | 10.5952 | 0.8802%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 317 | 20 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 107.5223 | 0 | 0 | 107.5223 | 0 | 102.569 | 2.2322 | 45.9497 | 102.569 | 2.2322 | 45.9497 | 108.0494 | 2.3515 | 45.9497 | 1.823%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 18 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 80.855 | 0 | 0 | 80.855 | 0 | 77.1302 | 2.009 | 38.3927 | 77.1302 | 2.009 | 38.3927 | 81.2514 | 2.1163 | 38.3927 | 1.62%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 8 | 2514.2831 | 99.84% | 0% | 0.1648% | 34.8714 | 0 | 0 | 34.8714 | 0 | 33.2649 | 0.89288 | 37.2558 | 33.2649 | 0.89288 | 37.2558 | 35.0423 | 0.94059 | 37.2558 | 1.387%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 65 | 2 | 95.3301 | 98.77% | 0% | 1.235% | 0.84013 | 0 | 0 | 0.84013 | 0 | 0.80143 | 0.22322 | 3.5903 | 0.80143 | 0.22322 | 3.5903 | 0.84425 | 0.23515 | 3.5903 | 0.8813%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 34 | 2 | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 36.4722 | 0 | 0 | 36.4722 | 0 | 34.792 | 0.22322 | 155.864 | 34.792 | 0.22322 | 155.864 | 36.651 | 0.23515 | 155.864 | 1.7%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 54 | 1 | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 22.6891 | 0 | 0 | 22.6891 | 0 | 21.6439 | 0.11161 | 193.9241 | 21.6439 | 0.11161 | 193.9241 | 22.8003 | 0.11757 | 193.9241 | 0.5366%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 135 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 206.9418 | 0 | 0 | 206.9418 | 0 | 197.4084 | 15.0674 | 13.1017 | 197.4084 | 15.0674 | 13.1017 | 207.9562 | 15.8724 | 13.1017 | 4.437%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 65 | 1 | 240.2897 | 88.19% | 10.99% | 0.8202% | 0.94542 | 0 | 0 | 0.94542 | 0 | 0.90187 | 0.11161 | 8.0806 | 0.90187 | 0.11161 | 8.0806 | 0.95006 | 0.11757 | 8.0806 | 0.3935%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 37 | 6 | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.3999 | 0 | 0 | 11.3999 | 0 | 10.8747 | 0.66966 | 16.2392 | 10.8747 | 0.66966 | 16.2392 | 11.4558 | 0.70544 | 16.2392 | 4.597%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 7 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 64.3063 | 0 | 0 | 64.3063 | 0 | 61.3438 | 0.78127 | 78.518 | 61.3438 | 0.78127 | 78.518 | 64.6215 | 0.82301 | 78.518 | 1.622%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 5 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 146.2364 | 0 | 0 | 146.2364 | 0 | 139.4996 | 0.55805 | 249.9768 | 139.4996 | 0.55805 | 249.9768 | 146.9533 | 0.58787 | 249.9768 | 1.447%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 216 | 18 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 247.1706 | 0 | 0 | 247.1706 | 0 | 235.784 | 2.009 | 117.365 | 235.784 | 2.009 | 117.365 | 248.3822 | 2.1163 | 117.365 | 2.394%
2026 | 1173 | 1173-68 | Tier-1 | Non-HFTD---13 | Non-HFTD---22 | 68 | 3 | 6.4999 | 85.9% | 0% | 14.1% | 0.071438 | 0 | 0 | 0.071438 | 0 | 0.068147 | 0.33483 | 0.20353 | 0.068147 | 0.33483 | 0.20353 | 0.071789 | 0.35272 | 0.20353 | 1.099%
2026 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | Tier-2---13 | 29 | 2 | 70.6534 | 98.66% | 0% | 1.337% | 1.3942 | 0 | 0 | 1.3942 | 0 | 1.33 | 0.22322 | 5.958 | 1.33 | 0.22322 | 5.958 | 1.401 | 0.23515 | 5.958 | 1.973%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 1 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 11.7111 | 0 | 0 | 11.7111 | 0 | 11.1716 | 0.11161 | 100.0946 | 11.1716 | 0.11161 | 100.0946 | 11.7685 | 0.11757 | 100.0946 | 0.1905%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 58 | 1 | 2215.156 | 94.69% | 5.226% | 0.08401% | 10.4877 | 0 | 0 | 10.4877 | 0 | 10.0045 | 0.11161 | 89.6382 | 10.0045 | 0.11161 | 89.6382 | 10.5391 | 0.11757 | 89.6382 | 0.4735%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 11 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 114.3761 | 0 | 0 | 114.3761 | 0 | 109.1071 | 1.2277 | 88.8704 | 109.1071 | 1.2277 | 88.8704 | 114.9368 | 1.2933 | 88.8704 | 1.315%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 2 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 8.4854 | 0 | 0 | 8.4854 | 0 | 8.0945 | 0.22322 | 36.2625 | 8.0945 | 0.22322 | 36.2625 | 8.527 | 0.23515 | 36.2625 | 0.5444%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 166 | 12 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 73.492 | 0 | 0 | 73.492 | 0 | 70.1064 | 1.3393 | 52.3447 | 70.1064 | 1.3393 | 52.3447 | 73.8522 | 1.4109 | 52.3447 | 2.063%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 5 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 22.6505 | 0 | 0 | 22.6505 | 0 | 21.607 | 0.55805 | 38.7187 | 21.607 | 0.55805 | 38.7187 | 22.7615 | 0.58787 | 38.7187 | 0.7591%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 1 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 6.8574 | 0 | 0 | 6.8574 | 0 | 6.5415 | 0.11161 | 58.6101 | 6.5415 | 0.11161 | 58.6101 | 6.891 | 0.11757 | 58.6101 | 0.4946%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 167 | 6 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 44.2037 | 0 | 0 | 44.2037 | 0 | 42.1674 | 0.66966 | 62.9683 | 42.1674 | 0.66966 | 62.9683 | 44.4204 | 0.70544 | 62.9683 | 1.028%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 3 | 456.1931 | 99.77% | 0% | 0.2285% | 11.6465 | 0 | 0 | 11.6465 | 0 | 11.11 | 0.33483 | 33.1809 | 11.11 | 0.33483 | 33.1809 | 11.7036 | 0.35272 | 33.1809 | 2.553%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 26 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 137.8836 | 0 | 0 | 137.8836 | 0 | 131.5316 | 2.9019 | 45.3266 | 131.5316 | 2.9019 | 45.3266 | 138.5595 | 3.0569 | 45.3266 | 11.7%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 6 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 44.9617 | 0 | 0 | 44.9617 | 0 | 42.8904 | 0.66966 | 64.048 | 42.8904 | 0.66966 | 64.048 | 45.1821 | 0.70544 | 64.048 | 2.394%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 48 | 3 | 6815.4278 | 94.54% | 5.441% | 0.023% | 116.7805 | 0 | 0 | 116.7805 | 0 | 111.4006 | 0.33483 | 332.7079 | 111.4006 | 0.33483 | 332.7079 | 117.3529 | 0.35272 | 332.7079 | 1.713%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 267 | 40 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 506.6727 | 0 | 0 | 506.6727 | 0 | 483.3313 | 4.4644 | 108.2634 | 483.3313 | 4.4644 | 108.2634 | 509.1564 | 4.7029 | 108.2634 | 4.313%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 146 | 13 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 93.397 | 0 | 0 | 93.397 | 0 | 89.0944 | 1.4509 | 61.405 | 89.0944 | 1.4509 | 61.405 | 93.8548 | 1.5285 | 61.405 | 2.535%
2026 | 139 | 139-245AE | Tier-1 | Non-HFTD---14 | Non-HFTD---18 | 165 | 9 | 5.6722 | 51.84% | 0% | 48.16% | 0.046509 | 0 | 0 | 0.046509 | 0 | 0.044367 | 1.0045 | 0.044168 | 0.044367 | 1.0045 | 0.044168 | 0.046737 | 1.0582 | 0.044168 | 0.82%
2026 | 140 | 140-481R | Tier-1 | Non-HFTD---6 | Non-HFTD---12 | 247 | 20 | 76.5519 | 22.22% | 72.37% | 5.415% | 0.39942 | 0 | 0 | 0.39942 | 0 | 0.38102 | 2.2322 | 0.17069 | 0.38102 | 2.2322 | 0.17069 | 0.40137 | 2.3515 | 0.17069 | 0.5218%
2026 | 140 | 140-496 | Tier-1 | Non-HFTD---5 | Non-HFTD---9 | 98 | 13 | 76.0759 | 10.21% | 86.85% | 2.935% | 0.29885 | 0 | 0 | 0.29885 | 0 | 0.28508 | 1.4509 | 0.19648 | 0.28508 | 1.4509 | 0.19648 | 0.30032 | 1.5285 | 0.19648 | 0.3928%
2026 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | Non-HFTD---15 | 58 | 4 | 14.0801 | 87.11% | 0% | 12.89% | 0.2453 | 0 | 0 | 0.2453 | 0 | 0.234 | 0.44644 | 0.52415 | 0.234 | 0.44644 | 0.52415 | 0.2465 | 0.47029 | 0.52415 | 1.742%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 22 | 5 | 427.4478 | 90.46% | 9.431% | 0.1062% | 25.4858 | 0 | 0 | 25.4858 | 0 | 24.3118 | 0.55805 | 43.5655 | 24.3118 | 0.55805 | 43.5655 | 25.6108 | 0.58787 | 43.5655 | 5.962%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 36 | 1 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 16.3009 | 0 | 0 | 16.3009 | 0 | 15.5499 | 0.11161 | 139.3238 | 15.5499 | 0.11161 | 139.3238 | 16.3808 | 0.11757 | 139.3238 | 0.6891%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 80 | 8 | 4370.0987 | 98.67% | 1.293% | 0.03403% | 125.0516 | 0 | 0 | 125.0516 | 0 | 119.2907 | 0.89288 | 133.6021 | 119.2907 | 0.89288 | 133.6021 | 125.6646 | 0.94059 | 133.6021 | 2.862%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 11 | 37077.302 | 99.36% | 0.615% | 0.02874% | 266.4743 | 0 | 0 | 266.4743 | 0 | 254.1983 | 1.2277 | 207.0507 | 254.1983 | 1.2277 | 207.0507 | 267.7805 | 1.2933 | 207.0507 | 0.7187%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 87 | 3 | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.502 | 0.33483 | 10.4589 | 3.502 | 0.33483 | 10.4589 | 3.6891 | 0.35272 | 10.4589 | 0.8771%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 669 | 8 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 17.6579 | 0 | 0 | 17.6579 | 0 | 16.8444 | 0.89288 | 18.8653 | 16.8444 | 0.89288 | 18.8653 | 17.7444 | 0.94059 | 18.8653 | 0.3206%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 60 | 2 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 29.2341 | 0 | 0 | 29.2341 | 0 | 27.8873 | 0.22322 | 124.9319 | 27.8873 | 0.22322 | 124.9319 | 29.3774 | 0.23515 | 124.9319 | 0.9577%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 17 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 88.8051 | 0 | 0 | 88.8051 | 0 | 84.7141 | 1.8974 | 44.6481 | 84.7141 | 1.8974 | 44.6481 | 89.2404 | 1.9987 | 44.6481 | 2.291%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 250 | 1 | 3160.5079 | 95.27% | 4.501% | 0.231% | 3.4927 | 0 | 0 | 3.4927 | 0 | 3.3318 | 0.11161 | 29.8523 | 3.3318 | 0.11161 | 29.8523 | 3.5098 | 0.11757 | 29.8523 | 0.1105%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 554 | 1 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 0.87979 | 0 | 0 | 0.87979 | 0 | 0.83926 | 0.11161 | 7.5196 | 0.83926 | 0.11161 | 7.5196 | 0.8841 | 0.11757 | 7.5196 | 0.04268%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 173 | 3 | 1867.403 | 95.01% | 4.712% | 0.2778% | 8.9224 | 0 | 0 | 8.9224 | 0 | 8.5114 | 0.33483 | 25.42 | 8.5114 | 0.33483 | 25.42 | 8.9662 | 0.35272 | 25.42 | 0.4778%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 675 | 6 | 18749.5963 | 97% | 2.901% | 0.09453% | 46.8847 | 0 | 0 | 46.8847 | 0 | 44.7248 | 0.66966 | 66.7874 | 44.7248 | 0.66966 | 66.7874 | 47.1146 | 0.70544 | 66.7874 | 0.2501%
2026 | 168 | 168-702F | Tier-1 | Non-HFTD---5 | Non-HFTD---12 | 160 | 25 | 86.0496 | 96.13% | 0% | 3.875% | 3.748 | 0 | 0 | 3.748 | 0 | 3.5754 | 2.7903 | 1.2814 | 3.5754 | 2.7903 | 1.2814 | 3.7664 | 2.9393 | 1.2814 | 4.356%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 3 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 33.726 | 0 | 0 | 33.726 | 0 | 32.1723 | 0.33483 | 96.0854 | 32.1723 | 0.33483 | 96.0854 | 33.8913 | 0.35272 | 96.0854 | 0.8371%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 2 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 10.7518 | 0 | 0 | 10.7518 | 0 | 10.2565 | 0.22322 | 45.9478 | 10.2565 | 0.22322 | 45.9478 | 10.8045 | 0.23515 | 45.9478 | 0.1873%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 236 | 7 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 97.8997 | 0 | 0 | 97.8997 | 0 | 93.3897 | 0.78127 | 119.5357 | 93.3897 | 0.78127 | 119.5357 | 98.3797 | 0.82301 | 119.5357 | 0.8496%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 131 | 2 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 18.1751 | 0 | 0 | 18.1751 | 0 | 17.3379 | 0.22322 | 77.6716 | 17.3379 | 0.22322 | 77.6716 | 18.2642 | 0.23515 | 77.6716 | 0.4343%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 3 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 27.2698 | 0 | 0 | 27.2698 | 0 | 26.0136 | 0.33483 | 77.6918 | 26.0136 | 0.33483 | 77.6918 | 27.4035 | 0.35272 | 77.6918 | 0.2708%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 345 | 1 | 13172.958 | 96.8% | 3.124% | 0.0728% | 10.7189 | 0 | 0 | 10.7189 | 0 | 10.2251 | 0.11161 | 91.6149 | 10.2251 | 0.11161 | 91.6149 | 10.7715 | 0.11757 | 91.6149 | 0.08137%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 2 | 47.6106 | 91.21% | 0% | 8.789% | 0.12594 | 0 | 0 | 0.12594 | 0 | 0.12013 | 0.22322 | 0.53819 | 0.12013 | 0.22322 | 0.53819 | 0.12655 | 0.23515 | 0.53819 | 0.2645%
2026 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 45 | 7 | 0.95479 | 13.38% | 0% | 86.62% | 0.0057645 | 0 | 0 | 0.0057645 | 0 | 0.005499 | 0.78127 | 0.0070385 | 0.005499 | 0.78127 | 0.0070385 | 0.0057928 | 0.82301 | 0.0070385 | 0.6037%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 8 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 89.5857 | 0 | 0 | 89.5857 | 0 | 85.4587 | 0.89288 | 95.7113 | 85.4587 | 0.89288 | 95.7113 | 90.0249 | 0.94059 | 95.7113 | 0.7517%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 3 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 64.721 | 0 | 0 | 64.721 | 0 | 61.7394 | 0.33483 | 184.3903 | 61.7394 | 0.33483 | 184.3903 | 65.0382 | 0.35272 | 184.3903 | 3.337%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 4 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 46.81 | 0 | 0 | 46.81 | 0 | 44.6536 | 0.44644 | 100.0214 | 44.6536 | 0.44644 | 100.0214 | 47.0395 | 0.47029 | 100.0214 | 1.107%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 42 | 8 | 316.4778 | 66.23% | 33.5% | 0.2671% | 11.5781 | 0 | 0 | 11.5781 | 0 | 11.0448 | 0.89288 | 12.3698 | 11.0448 | 0.89288 | 12.3698 | 11.6349 | 0.94059 | 12.3698 | 3.658%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 114 | 13 | 471.2015 | 74.37% | 25.17% | 0.4626% | 11.5888 | 0 | 0 | 11.5888 | 0 | 11.0549 | 1.4509 | 7.6192 | 11.0549 | 1.4509 | 7.6192 | 11.6456 | 1.5285 | 7.6192 | 2.459%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 7 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 12.3735 | 0 | 0 | 12.3735 | 0 | 11.8035 | 0.78127 | 15.1081 | 11.8035 | 0.78127 | 15.1081 | 12.4342 | 0.82301 | 15.1081 | 0.7177%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 9 | 3 | 6.6189 | 96.38% | 0% | 3.621% | 0.61667 | 0 | 0 | 0.61667 | 0 | 0.58826 | 0.33483 | 1.7569 | 0.58826 | 0.33483 | 1.7569 | 0.61969 | 0.35272 | 1.7569 | 9.317%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 4 | 973.0999 | 95.53% | 4.02% | 0.4464% | 5.7361 | 0 | 0 | 5.7361 | 0 | 5.4718 | 0.44644 | 12.2565 | 5.4718 | 0.44644 | 12.2565 | 5.7642 | 0.47029 | 12.2565 | 0.5895%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 3 | 490.4615 | 96.36% | 1.259% | 2.378% | 1.2238 | 0 | 0 | 1.2238 | 0 | 1.1674 | 0.33483 | 3.4865 | 1.1674 | 0.33483 | 3.4865 | 1.2298 | 0.35272 | 3.4865 | 0.2495%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 4 | 1279.0443 | 99.78% | 0% | 0.2159% | 11.2158 | 0 | 0 | 11.2158 | 0 | 10.6991 | 0.44644 | 23.9654 | 10.6991 | 0.44644 | 23.9654 | 11.2708 | 0.47029 | 23.9654 | 0.8769%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 29 | 2976.5734 | 99.75% | 0% | 0.2502% | 60.4609 | 0 | 0 | 60.4609 | 0 | 57.6756 | 3.2367 | 17.8193 | 57.6756 | 3.2367 | 17.8193 | 60.7573 | 3.4096 | 17.8193 | 2.031%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 39 | 8462.8018 | 99.74% | 0% | 0.2593% | 89.3042 | 0 | 0 | 89.3042 | 0 | 85.1901 | 4.3528 | 19.5714 | 85.1901 | 4.3528 | 19.5714 | 89.7419 | 4.5854 | 19.5714 | 1.055%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 111 | 16 | 498.1496 | 90.1% | 9.186% | 0.7154% | 18.7617 | 0 | 0 | 18.7617 | 0 | 17.8974 | 1.7858 | 10.0223 | 17.8974 | 1.7858 | 10.0223 | 18.8537 | 1.8812 | 10.0223 | 3.766%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 221 | 19 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 22.1849 | 0 | 0 | 22.1849 | 0 | 21.1629 | 2.1206 | 9.9797 | 21.1629 | 2.1206 | 9.9797 | 22.2936 | 2.2339 | 9.9797 | 2.137%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 77 | 2 | 170.5929 | 70.47% | 28.1% | 1.432% | 0.90556 | 0 | 0 | 0.90556 | 0 | 0.86384 | 0.22322 | 3.8699 | 0.86384 | 0.22322 | 3.8699 | 0.91 | 0.23515 | 3.8699 | 0.5308%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 95 | 5 | 317.7725 | 50.82% | 48.53% | 0.6462% | 2.4651 | 0 | 0 | 2.4651 | 0 | 2.3515 | 0.55805 | 4.2138 | 2.3515 | 0.55805 | 4.2138 | 2.4772 | 0.58787 | 4.2138 | 0.7757%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 293 | 10 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.6252 | 0 | 0 | 10.6252 | 0 | 10.1357 | 1.1161 | 9.0814 | 10.1357 | 1.1161 | 9.0814 | 10.6773 | 1.1757 | 9.0814 | 0.8857%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 39 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 41.0603 | 0 | 0 | 41.0603 | 0 | 39.1688 | 4.3528 | 8.9985 | 39.1688 | 4.3528 | 8.9985 | 41.2616 | 4.5854 | 8.9985 | 2.269%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 279 | 8 | 1890.633 | 91.06% | 8.49% | 0.4466% | 14.3165 | 0 | 0 | 14.3165 | 0 | 13.6569 | 0.89288 | 15.2954 | 13.6569 | 0.89288 | 15.2954 | 14.3866 | 0.94059 | 15.2954 | 0.7572%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 287 | 3 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 5.0302 | 0 | 0 | 5.0302 | 0 | 4.7985 | 0.33483 | 14.3311 | 4.7985 | 0.33483 | 14.3311 | 5.0549 | 0.35272 | 14.3311 | 0.2893%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 219 | 1 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 1.975 | 0 | 0 | 1.975 | 0 | 1.884 | 0.11161 | 16.8799 | 1.884 | 0.11161 | 16.8799 | 1.9846 | 0.11757 | 16.8799 | 0.1258%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 79 | 1 | 609.7797 | 99.07% | 0.4924% | 0.4406% | 2.2175 | 0 | 0 | 2.2175 | 0 | 2.1154 | 0.11161 | 18.9534 | 2.1154 | 0.11161 | 18.9534 | 2.2284 | 0.11757 | 18.9534 | 0.3637%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 218 | 2 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 12.8939 | 0 | 0 | 12.8939 | 0 | 12.2999 | 0.22322 | 55.1022 | 12.2999 | 0.22322 | 55.1022 | 12.9571 | 0.23515 | 55.1022 | 0.2638%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 273 | 7 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 9.2176 | 0 | 0 | 9.2176 | 0 | 8.793 | 0.78127 | 11.2547 | 8.793 | 0.78127 | 11.2547 | 9.2628 | 0.82301 | 11.2547 | 0.7281%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 201 | 2 | 998.7912 | 96.62% | 2.787% | 0.5903% | 2.7847 | 0 | 0 | 2.7847 | 0 | 2.6564 | 0.22322 | 11.9006 | 2.6564 | 0.22322 | 11.9006 | 2.7984 | 0.23515 | 11.9006 | 0.2788%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 201 | 3 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 6.2416 | 0 | 0 | 6.2416 | 0 | 5.9541 | 0.33483 | 17.7824 | 5.9541 | 0.33483 | 17.7824 | 6.2722 | 0.35272 | 17.7824 | 0.421%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 2 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 5.1596 | 0 | 0 | 5.1596 | 0 | 4.9219 | 0.22322 | 22.0495 | 4.9219 | 0.22322 | 22.0495 | 5.1849 | 0.23515 | 22.0495 | 0.187%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 115 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 2.5441 | 0 | 0 | 2.5441 | 0 | 2.4269 | 0.11161 | 21.7447 | 2.4269 | 0.11161 | 21.7447 | 2.5566 | 0.11757 | 21.7447 | 0.2449%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 155 | 1 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 3.9961 | 0 | 0 | 3.9961 | 0 | 3.812 | 0.11161 | 34.1544 | 3.812 | 0.11161 | 34.1544 | 4.0156 | 0.11757 | 34.1544 | 0.1847%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 147 | 1 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 2.8388 | 0 | 0 | 2.8388 | 0 | 2.708 | 0.11161 | 24.2631 | 2.708 | 0.11161 | 24.2631 | 2.8527 | 0.11757 | 24.2631 | 0.193%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 16 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 270.4268 | 0 | 0 | 270.4268 | 0 | 257.9688 | 1.7858 | 144.4588 | 257.9688 | 1.7858 | 144.4588 | 271.7525 | 1.8812 | 144.4588 | 1.029%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 23 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 155.1038 | 0 | 0 | 155.1038 | 0 | 147.9585 | 2.567 | 57.638 | 147.9585 | 2.567 | 57.638 | 155.8641 | 2.7042 | 57.638 | 2.326%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 157 | 14 | 484.0355 | 97.4% | 1.48% | 1.12% | 12.1917 | 0 | 0 | 12.1917 | 0 | 11.6301 | 1.5625 | 7.443 | 11.6301 | 1.5625 | 7.443 | 12.2515 | 1.646 | 7.443 | 2.519%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 15 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 54.7077 | 0 | 0 | 54.7077 | 0 | 52.1874 | 1.6742 | 31.1725 | 52.1874 | 1.6742 | 31.1725 | 54.9758 | 1.7636 | 31.1725 | 2.477%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 5 | 1721.769 | 85.69% | 14.07% | 0.2459% | 10.9145 | 0 | 0 | 10.9145 | 0 | 10.4117 | 0.55805 | 18.6573 | 10.4117 | 0.55805 | 18.6573 | 10.968 | 0.58787 | 18.6573 | 0.6339%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 264 | 2 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 48.7399 | 0 | 0 | 48.7399 | 0 | 46.4946 | 0.22322 | 208.2904 | 46.4946 | 0.22322 | 208.2904 | 48.9789 | 0.23515 | 208.2904 | 0.218%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 1 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 14.1325 | 0 | 0 | 14.1325 | 0 | 13.4814 | 0.11161 | 120.7905 | 13.4814 | 0.11161 | 120.7905 | 14.2018 | 0.11757 | 120.7905 | 0.1113%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 1 | 19489.7064 | 99% | 0.9737% | 0.02962% | 23.026 | 0 | 0 | 23.026 | 0 | 21.9652 | 0.11161 | 196.8031 | 21.9652 | 0.11161 | 196.8031 | 23.1388 | 0.11757 | 196.8031 | 0.1181%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 1 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 12.3732 | 0 | 0 | 12.3732 | 0 | 11.8032 | 0.11161 | 105.7538 | 11.8032 | 0.11161 | 105.7538 | 12.4338 | 0.11757 | 105.7538 | 0.2277%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 12 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 180.8416 | 0 | 0 | 180.8416 | 0 | 172.5106 | 1.3393 | 128.8045 | 172.5106 | 1.3393 | 128.8045 | 181.728 | 1.4109 | 128.8045 | 1.288%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 18 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 20.5667 | 0 | 0 | 20.5667 | 0 | 19.6192 | 2.009 | 9.7658 | 19.6192 | 2.009 | 9.7658 | 20.6675 | 2.1163 | 9.7658 | 1.021%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 18 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 36.3606 | 0 | 0 | 36.3606 | 0 | 34.6855 | 2.009 | 17.2652 | 34.6855 | 2.009 | 17.2652 | 36.5388 | 2.1163 | 17.2652 | 1.333%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 6 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 57.5249 | 0 | 0 | 57.5249 | 0 | 54.8748 | 0.66966 | 81.9443 | 54.8748 | 0.66966 | 81.9443 | 57.8069 | 0.70544 | 81.9443 | 0.5383%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 2 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 6.8528 | 0 | 0 | 6.8528 | 0 | 6.5371 | 0.22322 | 29.2856 | 6.5371 | 0.22322 | 29.2856 | 6.8864 | 0.23515 | 29.2856 | 0.1874%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 21 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 31.1018 | 0 | 0 | 31.1018 | 0 | 29.669 | 2.3438 | 12.6585 | 29.669 | 2.3438 | 12.6585 | 31.2543 | 2.469 | 12.6585 | 2.162%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 116 | 1 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 25.052 | 0 | 0 | 25.052 | 0 | 23.8979 | 0.11161 | 214.1197 | 23.8979 | 0.11161 | 214.1197 | 25.1748 | 0.11757 | 214.1197 | 0.2476%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 132 | 2 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 9.307 | 0 | 0 | 9.307 | 0 | 8.8782 | 0.22322 | 39.7734 | 8.8782 | 0.22322 | 39.7734 | 9.3526 | 0.23515 | 39.7734 | 0.4233%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 3 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 4.3058 | 0 | 0 | 4.3058 | 0 | 4.1075 | 0.33483 | 12.2673 | 4.1075 | 0.33483 | 12.2673 | 4.3269 | 0.35272 | 12.2673 | 0.2236%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 614 | 13 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 19.6757 | 0 | 0 | 19.6757 | 0 | 18.7693 | 1.4509 | 12.936 | 18.7693 | 1.4509 | 12.936 | 19.7721 | 1.5285 | 12.936 | 0.5487%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 97 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 11.0247 | 0 | 0 | 11.0247 | 0 | 10.5168 | 0.11161 | 94.2282 | 10.5168 | 0.11161 | 94.2282 | 11.0787 | 0.11757 | 94.2282 | 0.2987%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 307 | 7 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 19.9293 | 0 | 0 | 19.9293 | 0 | 19.0112 | 0.78127 | 24.3337 | 19.0112 | 0.78127 | 24.3337 | 20.027 | 0.82301 | 24.3337 | 0.6094%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 293 | 1 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 2.6025 | 0 | 0 | 2.6025 | 0 | 2.4826 | 0.11161 | 22.2438 | 2.4826 | 0.11161 | 22.2438 | 2.6153 | 0.11757 | 22.2438 | 0.09512%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | Tier-2---5 | 13 | 7 | 710.3273 | 99.46% | 0.4791% | 0.06249% | 110.3196 | 0 | 0 | 110.3196 | 0 | 105.2374 | 0.78127 | 134.7003 | 105.2374 | 0.78127 | 134.7003 | 110.8604 | 0.82301 | 134.7003 | 15.53%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 244 | 2 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 9.075 | 0 | 0 | 9.075 | 0 | 8.6569 | 0.22322 | 38.782 | 8.6569 | 0.22322 | 38.782 | 9.1195 | 0.23515 | 38.782 | 0.2306%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 18 | 2 | 318.0967 | 33.4% | 66.33% | 0.2755% | 3.4232 | 0 | 0 | 3.4232 | 0 | 3.2655 | 0.22322 | 14.629 | 3.2655 | 0.22322 | 14.629 | 3.44 | 0.23515 | 14.629 | 1.076%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 99 | 24 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 143.794 | 0 | 0 | 143.794 | 0 | 137.1697 | 2.6786 | 51.2087 | 137.1697 | 2.6786 | 51.2087 | 144.4989 | 2.8218 | 51.2087 | 6.996%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 100 | 63 | 3904.259 | 99.88% | 0.03221% | 0.0896% | 712.4392 | 0 | 0 | 712.4392 | 0 | 679.6186 | 7.0314 | 96.6544 | 679.6186 | 7.0314 | 96.6544 | 715.9316 | 7.4071 | 96.6544 | 18.25%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 67 | 6 | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 115.7525 | 0 | 0 | 115.7525 | 0 | 110.42 | 0.66966 | 164.8896 | 110.42 | 0.66966 | 164.8896 | 116.3199 | 0.70544 | 164.8896 | 2.583%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 106 | 2 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 12.3185 | 0 | 0 | 12.3185 | 0 | 11.751 | 0.22322 | 52.643 | 11.751 | 0.22322 | 52.643 | 12.3789 | 0.23515 | 52.643 | 0.53%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 123 | 1 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 22.584 | 0 | 0 | 22.584 | 0 | 21.5436 | 0.11161 | 193.0259 | 21.5436 | 0.11161 | 193.0259 | 22.6947 | 0.11757 | 193.0259 | 0.2348%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 76 | 1 | 1359.3953 | 95.15% | 4.696% | 0.1502% | 4.9358 | 0 | 0 | 4.9358 | 0 | 4.7084 | 0.11161 | 42.1863 | 4.7084 | 0.11161 | 42.1863 | 4.96 | 0.11757 | 42.1863 | 0.3631%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 367 | 4 | 7406.689 | 96.62% | 3.25% | 0.1263% | 22.6204 | 0 | 0 | 22.6204 | 0 | 21.5783 | 0.44644 | 48.3341 | 21.5783 | 0.44644 | 48.3341 | 22.7312 | 0.47029 | 48.3341 | 0.3054%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 451 | 5 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 252.7121 | 0 | 0 | 252.7121 | 0 | 241.0702 | 0.55805 | 431.9865 | 241.0702 | 0.55805 | 431.9865 | 253.9509 | 0.58787 | 431.9865 | 0.3191%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 287 | 4 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 181.6367 | 0 | 0 | 181.6367 | 0 | 173.269 | 0.44644 | 388.1125 | 173.269 | 0.44644 | 388.1125 | 182.527 | 0.47029 | 388.1125 | 0.4027%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 43 | 2 | 288.7705 | 86.56% | 13.18% | 0.2657% | 3.3714 | 0 | 0 | 3.3714 | 0 | 3.2161 | 0.22322 | 14.4077 | 3.2161 | 0.22322 | 14.4077 | 3.3879 | 0.23515 | 14.4077 | 1.168%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 407 | 5 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 25.4143 | 0 | 0 | 25.4143 | 0 | 24.2435 | 0.55805 | 43.4433 | 24.2435 | 0.55805 | 43.4433 | 25.5389 | 0.58787 | 43.4433 | 0.3422%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 910 | 16 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 82.6943 | 0 | 0 | 82.6943 | 0 | 78.8847 | 1.7858 | 44.1743 | 78.8847 | 1.7858 | 44.1743 | 83.0996 | 1.8812 | 44.1743 | 0.493%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 28 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 57.3568 | 0 | 0 | 57.3568 | 0 | 54.7145 | 3.1251 | 17.5082 | 54.7145 | 3.1251 | 17.5082 | 57.638 | 3.2921 | 17.5082 | 2.867%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 328 | 13 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 72.1552 | 0 | 0 | 72.1552 | 0 | 68.8312 | 1.4509 | 47.4393 | 68.8312 | 1.4509 | 47.4393 | 72.5089 | 1.5285 | 47.4393 | 1.129%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 245 | 34 | 2072.8837 | 91.06% | 8.635% | 0.3% | 75.9689 | 0 | 0 | 75.9689 | 0 | 72.4691 | 3.7947 | 19.0973 | 72.4691 | 3.7947 | 19.0973 | 76.3413 | 3.9975 | 19.0973 | 3.665%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 71 | 3 | 536.3838 | 78.97% | 20.71% | 0.32% | 5.1903 | 0 | 0 | 5.1903 | 0 | 4.9511 | 0.33483 | 14.787 | 4.9511 | 0.33483 | 14.787 | 5.2157 | 0.35272 | 14.787 | 0.9676%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 52 | 1 | 788.7224 | 98.19% | 1.606% | 0.2041% | 4.319 | 0 | 0 | 4.319 | 0 | 4.12 | 0.11161 | 36.9146 | 4.12 | 0.11161 | 36.9146 | 4.3402 | 0.11757 | 36.9146 | 0.5476%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 2 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 8.3381 | 0 | 0 | 8.3381 | 0 | 7.954 | 0.22322 | 35.633 | 7.954 | 0.22322 | 35.633 | 8.379 | 0.23515 | 35.633 | 0.2401%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 41 | 2 | 195.7251 | 81.71% | 17.81% | 0.4804% | 2.2625 | 0 | 0 | 2.2625 | 0 | 2.1583 | 0.22322 | 9.6688 | 2.1583 | 0.22322 | 9.6688 | 2.2736 | 0.23515 | 9.6688 | 1.156%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 21 | 2730.9177 | 98.3% | 1.373% | 0.325% | 45.7951 | 0 | 0 | 45.7951 | 0 | 43.6854 | 2.3438 | 18.6386 | 43.6854 | 2.3438 | 18.6386 | 46.0196 | 2.469 | 18.6386 | 1.677%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 131 | 5142.095 | 98.68% | 0.901% | 0.4182% | 223.6325 | 0 | 0 | 223.6325 | 0 | 213.3302 | 14.6209 | 14.5908 | 213.3302 | 14.6209 | 14.5908 | 224.7287 | 15.4021 | 14.5908 | 4.349%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 5 | 1 | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0029987 | 0 | 0 | 0.0029987 | 0 | 0.0028605 | 0.11161 | 0.02563 | 0.0028605 | 0.11161 | 0.02563 | 0.0030134 | 0.11757 | 0.02563 | 0.02624%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 27 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 57.0252 | 0 | 0 | 57.0252 | 0 | 54.3982 | 3.0135 | 18.0517 | 54.3982 | 3.0135 | 18.0517 | 57.3048 | 3.1745 | 18.0517 | 1.878%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 29 | 718.991 | 97.57% | 1.357% | 1.072% | 21.611 | 0 | 0 | 21.611 | 0 | 20.6154 | 3.2367 | 6.3693 | 20.6154 | 3.2367 | 6.3693 | 21.7169 | 3.4096 | 6.3693 | 3.006%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 8 | 447.7794 | 94.96% | 4.349% | 0.694% | 9.9643 | 0 | 0 | 9.9643 | 0 | 9.5052 | 0.89288 | 10.6456 | 9.5052 | 0.89288 | 10.6456 | 10.0131 | 0.94059 | 10.6456 | 2.225%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 58 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 82.1223 | 0 | 0 | 82.1223 | 0 | 78.3391 | 6.4734 | 12.1017 | 78.3391 | 6.4734 | 12.1017 | 82.5248 | 6.8193 | 12.1017 | 3.507%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 41 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 174.8805 | 0 | 0 | 174.8805 | 0 | 166.8241 | 4.576 | 36.4562 | 166.8241 | 4.576 | 36.4562 | 175.7378 | 4.8205 | 36.4562 | 3.541%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 20 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 93.3162 | 0 | 0 | 93.3162 | 0 | 89.0173 | 2.2322 | 39.8787 | 89.0173 | 2.2322 | 39.8787 | 93.7736 | 2.3515 | 39.8787 | 2.133%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 32 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 407.0584 | 0 | 0 | 407.0584 | 0 | 388.306 | 3.5715 | 108.7229 | 388.306 | 3.5715 | 108.7229 | 409.0538 | 3.7624 | 108.7229 | 1.719%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 252 | 16 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 176.6859 | 0 | 0 | 176.6859 | 0 | 168.5463 | 1.7858 | 94.3835 | 168.5463 | 1.7858 | 94.3835 | 177.552 | 1.8812 | 94.3835 | 1.818%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 137 | 2 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 11.6266 | 0 | 0 | 11.6266 | 0 | 11.0909 | 0.22322 | 49.6861 | 11.0909 | 0.22322 | 49.6861 | 11.6835 | 0.23515 | 49.6861 | 0.4118%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 498 | 40 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 486.2608 | 0 | 0 | 486.2608 | 0 | 463.8598 | 4.4644 | 103.9019 | 463.8598 | 4.4644 | 103.9019 | 488.6445 | 4.7029 | 103.9019 | 2.291%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 192 | 2 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 20.4768 | 0 | 0 | 20.4768 | 0 | 19.5335 | 0.22322 | 87.5076 | 19.5335 | 0.22322 | 87.5076 | 20.5772 | 0.23515 | 87.5076 | 0.2956%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 126 | 3 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 24.9414 | 0 | 0 | 24.9414 | 0 | 23.7924 | 0.33483 | 71.058 | 23.7924 | 0.33483 | 71.058 | 25.0636 | 0.35272 | 71.058 | 0.6863%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 223 | 3 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 109.4875 | 0 | 0 | 109.4875 | 0 | 104.4436 | 0.33483 | 311.9302 | 104.4436 | 0.33483 | 311.9302 | 110.0242 | 0.35272 | 311.9302 | 0.3876%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 23 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 333.2597 | 0 | 0 | 333.2597 | 0 | 317.9071 | 2.567 | 123.8423 | 317.9071 | 2.567 | 123.8423 | 334.8933 | 2.7042 | 123.8423 | 1.231%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 2 | 663.2151 | 70.89% | 28.72% | 0.399% | 2.413 | 0 | 0 | 2.413 | 0 | 2.3018 | 0.22322 | 10.312 | 2.3018 | 0.22322 | 10.312 | 2.4248 | 0.23515 | 10.312 | 0.3638%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 59 | 3 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 36.8722 | 0 | 0 | 36.8722 | 0 | 35.1736 | 0.33483 | 105.0491 | 35.1736 | 0.33483 | 105.0491 | 37.053 | 0.35272 | 105.0491 | 1.457%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 499 | 9 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 160.1553 | 0 | 0 | 160.1553 | 0 | 152.7773 | 1.0045 | 152.0943 | 152.7773 | 1.0045 | 152.0943 | 160.9404 | 1.0582 | 152.0943 | 0.5184%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 651 | 6 | 65515.492 | 98.93% | 1.038% | 0.03019% | 173.24 | 0 | 0 | 173.24 | 0 | 165.2592 | 0.66966 | 246.7806 | 165.2592 | 0.66966 | 246.7806 | 174.0892 | 0.70544 | 246.7806 | 0.2644%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 3 | 860.3234 | 98.08% | 1.495% | 0.4234% | 5.7805 | 0 | 0 | 5.7805 | 0 | 5.5142 | 0.33483 | 16.4686 | 5.5142 | 0.33483 | 16.4686 | 5.8088 | 0.35272 | 16.4686 | 0.6719%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 10 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 82.4704 | 0 | 0 | 82.4704 | 0 | 78.6712 | 1.1161 | 70.4875 | 78.6712 | 1.1161 | 70.4875 | 82.8747 | 1.1757 | 70.4875 | 5.203%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 9 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 52.6991 | 0 | 0 | 52.6991 | 0 | 50.2713 | 1.0045 | 50.0466 | 50.2713 | 1.0045 | 50.0466 | 52.9574 | 1.0582 | 50.0466 | 0.8407%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 3 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 5.7452 | 0 | 0 | 5.7452 | 0 | 5.4806 | 0.33483 | 16.3682 | 5.4806 | 0.33483 | 16.3682 | 5.7734 | 0.35272 | 16.3682 | 0.558%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 52 | 4 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 8.2928 | 0 | 0 | 8.2928 | 0 | 7.9107 | 0.44644 | 17.7196 | 7.9107 | 0.44644 | 17.7196 | 8.3334 | 0.47029 | 17.7196 | 2.203%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 165 | 15 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 30.6463 | 0 | 0 | 30.6463 | 0 | 29.2345 | 1.6742 | 17.4623 | 29.2345 | 1.6742 | 17.4623 | 30.7965 | 1.7636 | 17.4623 | 2.594%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 71 | 2 | 791.3356 | 98.7% | 1.112% | 0.1837% | 6.3807 | 0 | 0 | 6.3807 | 0 | 6.0867 | 0.22322 | 27.2679 | 6.0867 | 0.22322 | 27.2679 | 6.412 | 0.23515 | 27.2679 | 0.8063%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 75 | 2 | 376.72 | 96.88% | 2.523% | 0.5996% | 2.8223 | 0 | 0 | 2.8223 | 0 | 2.6923 | 0.22322 | 12.0612 | 2.6923 | 0.22322 | 12.0612 | 2.8362 | 0.23515 | 12.0612 | 0.7492%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 82 | 4437.6588 | 97.91% | 1.769% | 0.321% | 165.8459 | 0 | 0 | 165.8459 | 0 | 158.2057 | 9.152 | 17.2864 | 158.2057 | 9.152 | 17.2864 | 166.6589 | 9.641 | 17.2864 | 3.737%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 269 | 9 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 35.9734 | 0 | 0 | 35.9734 | 0 | 34.3162 | 1.0045 | 34.1628 | 34.3162 | 1.0045 | 34.1628 | 36.1498 | 1.0582 | 34.1628 | 0.9612%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 3 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 8.9758 | 0 | 0 | 8.9758 | 0 | 8.5623 | 0.33483 | 25.5721 | 8.5623 | 0.33483 | 25.5721 | 9.0198 | 0.35272 | 25.5721 | 0.2449%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 9 | 960.3446 | 65.96% | 33.81% | 0.2324% | 14.1305 | 0 | 0 | 14.1305 | 0 | 13.4795 | 1.0045 | 13.4193 | 13.4795 | 1.0045 | 13.4193 | 14.1998 | 1.0582 | 13.4193 | 1.471%
2026 | 242 | 242-1427F | Tier-2 | Tier-2---20 | Tier-2---19 | 5 | 2 | 24.991 | 71.07% | 28.66% | 0.2708% | 2.0603 | 0 | 0 | 2.0603 | 0 | 1.9654 | 0.22322 | 8.8049 | 1.9654 | 0.22322 | 8.8049 | 2.0704 | 0.23515 | 8.8049 | 8.244%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 40 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 85.1971 | 0 | 0 | 85.1971 | 0 | 81.2723 | 4.4644 | 18.2045 | 81.2723 | 4.4644 | 18.2045 | 85.6148 | 4.7029 | 18.2045 | 2.515%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 16 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 25.7242 | 0 | 0 | 25.7242 | 0 | 24.5391 | 1.7858 | 13.7415 | 24.5391 | 1.7858 | 13.7415 | 25.8503 | 1.8812 | 13.7415 | 1.891%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 25 | 3753.23 | 95.85% | 3.876% | 0.273% | 56.2111 | 0 | 0 | 56.2111 | 0 | 53.6216 | 2.7903 | 19.2175 | 53.6216 | 2.7903 | 19.2175 | 56.4867 | 2.9393 | 19.2175 | 1.498%
2026 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 98 | 10 | 49.4853 | 86.66% | 6.71% | 6.626% | 1.2691 | 0 | 0 | 1.2691 | 0 | 1.2106 | 1.1161 | 1.0847 | 1.2106 | 1.1161 | 1.0847 | 1.2753 | 1.1757 | 1.0847 | 2.565%
2026 | 276 | 276-228 | Tier-1 | Non-HFTD---2 | Non-HFTD---8 | 773 | 92 | 290.9914 | 11.65% | 84% | 4.346% | 1.1706 | 0 | 0 | 1.1706 | 0 | 1.1166 | 10.2681 | 0.10875 | 1.1166 | 10.2681 | 0.10875 | 1.1763 | 10.8168 | 0.10875 | 0.4023%
2026 | 279 | 279-10AE | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 557 | 2 | 166.5714 | 5.911% | 88.12% | 5.969% | 0.010253 | 0 | 0 | 0.010253 | 0 | 0.0097808 | 0.22322 | 0.043817 | 0.0097808 | 0.22322 | 0.043817 | 0.010303 | 0.23515 | 0.043817 | 0.006155%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 6 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 83.3767 | 0 | 0 | 83.3767 | 0 | 79.5357 | 0.66966 | 118.7702 | 79.5357 | 0.66966 | 118.7702 | 83.7854 | 0.70544 | 118.7702 | 1.573%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 11 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 44.4076 | 0 | 0 | 44.4076 | 0 | 42.3618 | 1.2277 | 34.5047 | 42.3618 | 1.2277 | 34.5047 | 44.6253 | 1.2933 | 34.5047 | 2.205%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 170 | 24 | 481.2843 | 94.31% | 4.95% | 0.7414% | 18.5829 | 0 | 0 | 18.5829 | 0 | 17.7268 | 2.6786 | 6.6178 | 17.7268 | 2.6786 | 6.6178 | 18.674 | 2.8218 | 6.6178 | 3.861%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 43 | 4 | 3.2301 | 78.97% | 0% | 21.03% | 0.06881 | 0 | 0 | 0.06881 | 0 | 0.06564 | 0.44644 | 0.14703 | 0.06564 | 0.44644 | 0.14703 | 0.069147 | 0.47029 | 0.14703 | 2.13%
2026 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | Non-HFTD---13 | 100 | 6 | 92.0555 | 97.82% | 0% | 2.183% | 1.5668 | 0 | 0 | 1.5668 | 0 | 1.4946 | 0.66966 | 2.2319 | 1.4946 | 0.66966 | 2.2319 | 1.5745 | 0.70544 | 2.2319 | 1.702%
2026 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 1 | 458.7821 | 99.48% | 0% | 0.5194% | 1.9182 | 0 | 0 | 1.9182 | 0 | 1.8298 | 0.11161 | 16.3949 | 1.8298 | 0.11161 | 16.3949 | 1.9276 | 0.11757 | 16.3949 | 0.4181%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 2 | 754.1323 | 92.41% | 6.882% | 0.7076% | 1.6168 | 0 | 0 | 1.6168 | 0 | 1.5423 | 0.22322 | 6.9094 | 1.5423 | 0.22322 | 6.9094 | 1.6247 | 0.23515 | 6.9094 | 0.2144%
2026 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 233 | 36 | 4233.8665 | 96.93% | 2.943% | 0.1312% | 183.8738 | 0 | 0 | 183.8738 | 0 | 175.4031 | 4.018 | 43.6548 | 175.4031 | 4.018 | 43.6548 | 184.7752 | 4.2326 | 43.6548 | 4.343%
2026 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 152 | 52 | 2371.786 | 97.71% | 2.108% | 0.1806% | 229.9212 | 0 | 0 | 229.9212 | 0 | 219.3292 | 5.8037 | 37.7911 | 219.3292 | 5.8037 | 37.7911 | 231.0482 | 6.1138 | 37.7911 | 9.694%
2026 | 307 | 307-1492R | Tier-2 | Tier-2---9 | Tier-2---4 | 39 | 2 | 744.3133 | 92.56% | 7.329% | 0.1099% | 10.2458 | 0 | 0 | 10.2458 | 0 | 9.7738 | 0.22322 | 43.7856 | 9.7738 | 0.22322 | 43.7856 | 10.2961 | 0.23515 | 43.7856 | 1.377%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 3 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 35.9866 | 0 | 0 | 35.9866 | 0 | 34.3287 | 0.33483 | 102.5258 | 34.3287 | 0.33483 | 102.5258 | 36.163 | 0.35272 | 102.5258 | 1.495%
2026 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 98 | 7 | 2117.8574 | 97.53% | 2.33% | 0.1416% | 42.7858 | 0 | 0 | 42.7858 | 0 | 40.8147 | 0.78127 | 52.2415 | 40.8147 | 0.78127 | 52.2415 | 42.9955 | 0.82301 | 52.2415 | 2.02%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 8 | 4762.848 | 95.55% | 4.384% | 0.07015% | 96.8589 | 0 | 0 | 96.8589 | 0 | 92.3968 | 0.89288 | 103.4817 | 92.3968 | 0.89288 | 103.4817 | 97.3337 | 0.94059 | 103.4817 | 2.034%
2026 | 308 | 308-486AE | Tier-2 | Tier-2---16 | Tier-2---8 | 142 | 1 | 164.6778 | 2.383% | 96.2% | 1.419% | 0.0080157 | 0 | 0 | 0.0080157 | 0 | 0.0076464 | 0.11161 | 0.06851 | 0.0076464 | 0.11161 | 0.06851 | 0.008055 | 0.11757 | 0.06851 | 0.004867%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 39 | 6 | 95.5263 | 19.37% | 79.9% | 0.729% | 0.82573 | 0 | 0 | 0.82573 | 0 | 0.78769 | 0.66966 | 1.1762 | 0.78769 | 0.66966 | 1.1762 | 0.82977 | 0.70544 | 1.1762 | 0.8644%
2026 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 14 | 1 | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.81042 | 0 | 0 | 0.81042 | 0 | 0.77309 | 0.11161 | 6.9267 | 0.77309 | 0.11161 | 6.9267 | 0.8144 | 0.11757 | 6.9267 | 1.754%
2026 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 4 | 278.652 | 16.28% | 83.57% | 0.1501% | 3.7587 | 0 | 0 | 3.7587 | 0 | 3.5856 | 0.44644 | 8.0314 | 3.5856 | 0.44644 | 8.0314 | 3.7771 | 0.47029 | 8.0314 | 1.349%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 44 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.24467 | 0 | 0 | 0.24467 | 0 | 0.2334 | 4.9108 | 0.047527 | 0.2334 | 4.9108 | 0.047527 | 0.24587 | 5.1732 | 0.047527 | 0.1531%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 4 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0066957 | 0 | 0 | 0.0066957 | 0 | 0.0063872 | 0.44644 | 0.014307 | 0.0063872 | 0.44644 | 0.014307 | 0.0067285 | 0.47029 | 0.014307 | 0.003313%
2026 | 334 | 334-21 | Tier-1 | Non-HFTD---2 | Non-HFTD---5 | 183 | 12 | 378.2145 | 89.09% | 9.517% | 1.396% | 6.4074 | 0 | 0 | 6.4074 | 0 | 6.1123 | 1.3393 | 4.5637 | 6.1123 | 1.3393 | 4.5637 | 6.4388 | 1.4109 | 4.5637 | 1.694%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 15 | 1 | 302.428 | 99.27% | 0.6612% | 0.06922% | 5.8042 | 0 | 0 | 5.8042 | 0 | 5.5368 | 0.11161 | 49.6089 | 5.5368 | 0.11161 | 49.6089 | 5.8327 | 0.11757 | 49.6089 | 1.919%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 50 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 88.267 | 0 | 0 | 88.267 | 0 | 84.2007 | 5.5805 | 15.0884 | 84.2007 | 5.5805 | 15.0884 | 88.6997 | 5.8787 | 15.0884 | 2.45%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 67 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 320.2242 | 0 | 0 | 320.2242 | 0 | 305.4722 | 7.4779 | 40.8501 | 305.4722 | 7.4779 | 40.8501 | 321.7939 | 7.8774 | 40.8501 | 2.308%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 11 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 21.3571 | 0 | 0 | 21.3571 | 0 | 20.3732 | 1.2277 | 16.5945 | 20.3732 | 1.2277 | 16.5945 | 21.4618 | 1.2933 | 16.5945 | 0.3834%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 5 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 53.923 | 0 | 0 | 53.923 | 0 | 51.4389 | 0.55805 | 92.1761 | 51.4389 | 0.55805 | 92.1761 | 54.1873 | 0.58787 | 92.1761 | 0.3988%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 40 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 270.473 | 0 | 0 | 270.473 | 0 | 258.0129 | 4.4644 | 57.7934 | 258.0129 | 4.4644 | 57.7934 | 271.7989 | 4.7029 | 57.7934 | 2.415%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 24 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 476.4037 | 0 | 0 | 476.4037 | 0 | 454.4568 | 2.6786 | 169.6594 | 454.4568 | 2.6786 | 169.6594 | 478.739 | 2.8218 | 169.6594 | 2.026%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 1 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 24.0427 | 0 | 0 | 24.0427 | 0 | 22.9351 | 0.11161 | 205.4934 | 22.9351 | 0.11161 | 205.4934 | 24.1606 | 0.11757 | 205.4934 | 0.2629%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 17 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 253.9863 | 0 | 0 | 253.9863 | 0 | 242.2857 | 1.8974 | 127.6955 | 242.2857 | 1.8974 | 127.6955 | 255.2313 | 1.9987 | 127.6955 | 1.364%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 8 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 102.2408 | 0 | 0 | 102.2408 | 0 | 97.5307 | 0.89288 | 109.2316 | 97.5307 | 0.89288 | 109.2316 | 102.7419 | 0.94059 | 109.2316 | 1.109%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 8 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 103.5068 | 0 | 0 | 103.5068 | 0 | 98.7385 | 0.89288 | 110.5842 | 98.7385 | 0.89288 | 110.5842 | 104.0142 | 0.94059 | 110.5842 | 4.109%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 25 | 4 | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 102.7366 | 0 | 0 | 102.7366 | 0 | 98.0038 | 0.44644 | 219.5227 | 98.0038 | 0.44644 | 219.5227 | 103.2402 | 0.47029 | 219.5227 | 4.637%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 12 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 182.3201 | 0 | 0 | 182.3201 | 0 | 173.921 | 1.3393 | 129.8576 | 173.921 | 1.3393 | 129.8576 | 183.2138 | 1.4109 | 129.8576 | 4.002%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 2 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 43.1238 | 0 | 0 | 43.1238 | 0 | 41.1372 | 0.22322 | 184.2898 | 41.1372 | 0.22322 | 184.2898 | 43.3352 | 0.23515 | 184.2898 | 0.3186%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 3 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 36.7884 | 0 | 0 | 36.7884 | 0 | 35.0937 | 0.33483 | 104.8103 | 35.0937 | 0.33483 | 104.8103 | 36.9688 | 0.35272 | 104.8103 | 0.1794%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 3 | 3653.654 | 88.54% | 11.39% | 0.07412% | 31.621 | 0 | 0 | 31.621 | 0 | 30.1643 | 0.33483 | 90.0883 | 30.1643 | 0.33483 | 90.0883 | 31.776 | 0.35272 | 90.0883 | 0.8655%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 25 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 237.0088 | 0 | 0 | 237.0088 | 0 | 226.0903 | 2.7903 | 81.0287 | 226.0903 | 2.7903 | 81.0287 | 238.1706 | 2.9393 | 81.0287 | 3.16%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 58 | 7 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 47.5276 | 0 | 0 | 47.5276 | 0 | 45.3381 | 0.78127 | 58.0313 | 45.3381 | 0.78127 | 58.0313 | 47.7606 | 0.82301 | 58.0313 | 2.798%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 6 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 42.9875 | 0 | 0 | 42.9875 | 0 | 41.0071 | 0.66966 | 61.2357 | 41.0071 | 0.66966 | 61.2357 | 43.1982 | 0.70544 | 61.2357 | 0.7906%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 99 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 610.6554 | 0 | 0 | 610.6554 | 0 | 582.5237 | 11.0494 | 52.72 | 582.5237 | 11.0494 | 52.72 | 613.6488 | 11.6398 | 52.72 | 3.814%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 730 | 41 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 144.4424 | 0 | 0 | 144.4424 | 0 | 137.7883 | 4.576 | 30.111 | 137.7883 | 4.576 | 30.111 | 145.1505 | 4.8205 | 30.111 | 1.554%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 48 | 1 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 30.7065 | 0 | 0 | 30.7065 | 0 | 29.2919 | 0.11161 | 262.4488 | 29.2919 | 0.11161 | 262.4488 | 30.857 | 0.11757 | 262.4488 | 0.6022%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 9 | 16869.708 | 98.79% | 1.184% | 0.02933% | 160.5004 | 0 | 0 | 160.5004 | 0 | 153.1065 | 1.0045 | 152.422 | 153.1065 | 1.0045 | 152.422 | 161.2872 | 1.0582 | 152.422 | 0.9514%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 30 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 413.4243 | 0 | 0 | 413.4243 | 0 | 394.3787 | 3.3483 | 117.7847 | 394.3787 | 3.3483 | 117.7847 | 415.4509 | 3.5272 | 117.7847 | 2.336%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 18 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 137.9756 | 0 | 0 | 137.9756 | 0 | 131.6193 | 2.009 | 65.5155 | 131.6193 | 2.009 | 65.5155 | 138.6519 | 2.1163 | 65.5155 | 1.323%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 21 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 257.4737 | 0 | 0 | 257.4737 | 0 | 245.6125 | 2.3438 | 104.7919 | 245.6125 | 2.3438 | 104.7919 | 258.7359 | 2.469 | 104.7919 | 2.19%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 344 | 4 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 125.0138 | 0 | 0 | 125.0138 | 0 | 119.2547 | 0.44644 | 267.1235 | 119.2547 | 0.44644 | 267.1235 | 125.6266 | 0.47029 | 267.1235 | 0.3325%
2026 | 362 | 362-47F | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 650 | 61 | 174.2726 | 36.5% | 57.41% | 6.096% | 1.731 | 0 | 0 | 1.731 | 0 | 1.6513 | 6.8082 | 0.24254 | 1.6513 | 6.8082 | 0.24254 | 1.7395 | 7.172 | 0.24254 | 0.9933%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 140 | 5 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 13.4147 | 0 | 0 | 13.4147 | 0 | 12.7967 | 0.55805 | 22.931 | 12.7967 | 0.55805 | 22.931 | 13.4804 | 0.58787 | 22.931 | 0.9219%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 76 | 6 | 924.8041 | 18.79% | 81.02% | 0.1888% | 3.9779 | 0 | 0 | 3.9779 | 0 | 3.7946 | 0.66966 | 5.6665 | 3.7946 | 0.66966 | 5.6665 | 3.9974 | 0.70544 | 5.6665 | 0.4301%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 111 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 119.0418 | 0 | 0 | 119.0418 | 0 | 113.5577 | 12.3887 | 9.1662 | 113.5577 | 12.3887 | 9.1662 | 119.6253 | 13.0507 | 9.1662 | 3.795%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 61 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 94 | 0 | 0 | 94 | 0 | 89.6696 | 6.8082 | 13.1708 | 89.6696 | 6.8082 | 13.1708 | 94.4608 | 7.172 | 13.1708 | 5.06%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 67 | 6370.0414 | 98.47% | 1.262% | 0.272% | 142.3728 | 0 | 0 | 142.3728 | 0 | 135.814 | 7.4779 | 18.1621 | 135.814 | 7.4779 | 18.1621 | 143.0707 | 7.8774 | 18.1621 | 2.235%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 8 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 6.5508 | 0 | 0 | 6.5508 | 0 | 6.249 | 0.89288 | 6.9987 | 6.249 | 0.89288 | 6.9987 | 6.5829 | 0.94059 | 6.9987 | 0.4851%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 84 | 2 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 23.6723 | 0 | 0 | 23.6723 | 0 | 22.5818 | 0.22322 | 101.1638 | 22.5818 | 0.22322 | 101.1638 | 23.7884 | 0.23515 | 101.1638 | 0.6729%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 133 | 12 | 4750.1268 | 98% | 1.916% | 0.08125% | 121.8064 | 0 | 0 | 121.8064 | 0 | 116.195 | 1.3393 | 86.7567 | 116.195 | 1.3393 | 86.7567 | 122.4035 | 1.4109 | 86.7567 | 2.564%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 2 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 30.2778 | 0 | 0 | 30.2778 | 0 | 28.883 | 0.22322 | 129.3924 | 28.883 | 0.22322 | 129.3924 | 30.4262 | 0.23515 | 129.3924 | 0.5661%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 201 | 2 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 5.0877 | 0 | 0 | 5.0877 | 0 | 4.8533 | 0.22322 | 21.7421 | 4.8533 | 0.22322 | 21.7421 | 5.1126 | 0.23515 | 21.7421 | 0.2773%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 3 | 852.9261 | 84.92% | 14.72% | 0.3553% | 4.3461 | 0 | 0 | 4.3461 | 0 | 4.1459 | 0.33483 | 12.382 | 4.1459 | 0.33483 | 12.382 | 4.3674 | 0.35272 | 12.382 | 0.5095%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 144 | 4 | 526.1263 | 57.95% | 41.57% | 0.4783% | 2.4562 | 0 | 0 | 2.4562 | 0 | 2.343 | 0.44644 | 5.2482 | 2.343 | 0.44644 | 5.2482 | 2.4682 | 0.47029 | 5.2482 | 0.4668%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 15 | 11572.221 | 88.48% | 11.4% | 0.1243% | 58.3725 | 0 | 0 | 58.3725 | 0 | 55.6834 | 1.6742 | 33.2607 | 55.6834 | 1.6742 | 33.2607 | 58.6586 | 1.7636 | 33.2607 | 0.5044%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 25 | 1 | 549.9829 | 98.93% | 0.9134% | 0.161% | 6.3113 | 0 | 0 | 6.3113 | 0 | 6.0205 | 0.11161 | 53.9424 | 6.0205 | 0.11161 | 53.9424 | 6.3422 | 0.11757 | 53.9424 | 1.148%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 74 | 1 | 474.7376 | 91.31% | 8.325% | 0.3651% | 1.6988 | 0 | 0 | 1.6988 | 0 | 1.6205 | 0.11161 | 14.5195 | 1.6205 | 0.11161 | 14.5195 | 1.7071 | 0.11757 | 14.5195 | 0.3578%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 122 | 27 | 333.8465 | 96.62% | 2.31% | 1.072% | 20.7016 | 0 | 0 | 20.7016 | 0 | 19.7479 | 3.0135 | 6.5532 | 19.7479 | 3.0135 | 6.5532 | 20.8031 | 3.1745 | 6.5532 | 6.201%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 2 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 4.7987 | 0 | 0 | 4.7987 | 0 | 4.5776 | 0.22322 | 20.5073 | 4.5776 | 0.22322 | 20.5073 | 4.8222 | 0.23515 | 20.5073 | 0.1406%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 465 | 101 | 571.2373 | 70.71% | 27.93% | 1.361% | 25.4421 | 0 | 0 | 25.4421 | 0 | 24.27 | 11.2726 | 2.153 | 24.27 | 11.2726 | 2.153 | 25.5668 | 11.8749 | 2.153 | 4.454%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 6 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 47.227 | 0 | 0 | 47.227 | 0 | 45.0514 | 0.66966 | 67.2749 | 45.0514 | 0.66966 | 67.2749 | 47.4585 | 0.70544 | 67.2749 | 0.4903%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 3 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 27.5566 | 0 | 0 | 27.5566 | 0 | 26.2871 | 0.33483 | 78.5087 | 26.2871 | 0.33483 | 78.5087 | 27.6916 | 0.35272 | 78.5087 | 0.3801%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 1 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 4.2534 | 0 | 0 | 4.2534 | 0 | 4.0575 | 0.11161 | 36.3538 | 4.0575 | 0.11161 | 36.3538 | 4.2742 | 0.11757 | 36.3538 | 0.2652%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 3 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 16.8076 | 0 | 0 | 16.8076 | 0 | 16.0333 | 0.33483 | 47.885 | 16.0333 | 0.33483 | 47.885 | 16.89 | 0.35272 | 47.885 | 0.1583%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 6 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 10.9435 | 0 | 0 | 10.9435 | 0 | 10.4394 | 0.66966 | 15.5891 | 10.4394 | 0.66966 | 15.5891 | 10.9972 | 0.70544 | 15.5891 | 0.6194%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 21 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 79.7211 | 0 | 0 | 79.7211 | 0 | 76.0485 | 2.3438 | 32.4465 | 76.0485 | 2.3438 | 32.4465 | 80.1119 | 2.469 | 32.4465 | 2.167%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 19 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 36.5692 | 0 | 0 | 36.5692 | 0 | 34.8845 | 2.1206 | 16.4504 | 34.8845 | 2.1206 | 16.4504 | 36.7484 | 2.2339 | 16.4504 | 0.8272%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 25 | 1 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 15.2482 | 0 | 0 | 15.2482 | 0 | 14.5458 | 0.11161 | 130.3266 | 14.5458 | 0.11161 | 130.3266 | 15.323 | 0.11757 | 130.3266 | 1.128%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 51 | 3 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 20.1293 | 0 | 0 | 20.1293 | 0 | 19.202 | 0.33483 | 57.3485 | 19.202 | 0.33483 | 57.3485 | 20.228 | 0.35272 | 57.3485 | 1.661%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 314 | 13 | 2119.752 | 55.7% | 43.96% | 0.3458% | 14.1755 | 0 | 0 | 14.1755 | 0 | 13.5224 | 1.4509 | 9.3198 | 13.5224 | 1.4509 | 9.3198 | 14.245 | 1.5285 | 9.3198 | 0.6687%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 6 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 20.2568 | 0 | 0 | 20.2568 | 0 | 19.3236 | 0.66966 | 28.8558 | 19.3236 | 0.66966 | 28.8558 | 20.3561 | 0.70544 | 28.8558 | 0.2225%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 1 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 3.7031 | 0 | 0 | 3.7031 | 0 | 3.5325 | 0.11161 | 31.6502 | 3.5325 | 0.11161 | 31.6502 | 3.7212 | 0.11757 | 31.6502 | 0.0656%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 57 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 180.7327 | 0 | 0 | 180.7327 | 0 | 172.4067 | 6.3618 | 27.1004 | 172.4067 | 6.3618 | 27.1004 | 181.6187 | 6.7017 | 27.1004 | 2.685%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 72 | 7 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 40.8883 | 0 | 0 | 40.8883 | 0 | 39.0047 | 0.78127 | 49.9247 | 39.0047 | 0.78127 | 49.9247 | 41.0888 | 0.82301 | 49.9247 | 2.734%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 26 | 3 | 625.3129 | 96.7% | 3.156% | 0.1473% | 20.2327 | 0 | 0 | 20.2327 | 0 | 19.3006 | 0.33483 | 57.6431 | 19.3006 | 0.33483 | 57.6431 | 20.3319 | 0.35272 | 57.6431 | 3.236%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 5 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 45.6631 | 0 | 0 | 45.6631 | 0 | 43.5595 | 0.55805 | 78.0566 | 43.5595 | 0.55805 | 78.0566 | 45.8869 | 0.58787 | 78.0566 | 0.868%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 161 | 11 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 43.9211 | 0 | 0 | 43.9211 | 0 | 41.8978 | 1.2277 | 34.1268 | 41.8978 | 1.2277 | 34.1268 | 44.1364 | 1.2933 | 34.1268 | 1.893%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 23 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 262.0283 | 0 | 0 | 262.0283 | 0 | 249.9572 | 2.567 | 97.3721 | 249.9572 | 2.567 | 97.3721 | 263.3128 | 2.7042 | 97.3721 | 3.167%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 7 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 31.277 | 0 | 0 | 31.277 | 0 | 29.8361 | 0.78127 | 38.1892 | 29.8361 | 0.78127 | 38.1892 | 31.4303 | 0.82301 | 38.1892 | 2.762%
2026 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 18 | 5 | 537.0702 | 32.53% | 67.41% | 0.0594% | 14.0735 | 0 | 0 | 14.0735 | 0 | 13.4252 | 0.55805 | 24.0573 | 13.4252 | 0.55805 | 24.0573 | 14.1425 | 0.58787 | 24.0573 | 2.62%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 5 | 2 | 137.227 | 99.9% | 0% | 0.1049% | 15.9016 | 0 | 0 | 15.9016 | 0 | 15.1691 | 0.22322 | 67.9557 | 15.1691 | 0.22322 | 67.9557 | 15.9796 | 0.23515 | 67.9557 | 11.59%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 1 | 181.2174 | 99.84% | 0% | 0.161% | 4.3724 | 0 | 0 | 4.3724 | 0 | 4.1709 | 0.11161 | 37.3707 | 4.1709 | 0.11161 | 37.3707 | 4.3938 | 0.11757 | 37.3707 | 2.413%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 9 | 2823.7515 | 99.93% | 0% | 0.06613% | 103.7341 | 0 | 0 | 103.7341 | 0 | 98.9552 | 1.0045 | 98.5129 | 98.9552 | 1.0045 | 98.5129 | 104.2426 | 1.0582 | 98.5129 | 3.674%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 2 | 1 | 39.0262 | 97.23% | 2.586% | 0.1833% | 5.5021 | 0 | 0 | 5.5021 | 0 | 5.2486 | 0.11161 | 47.0264 | 5.2486 | 0.11161 | 47.0264 | 5.5291 | 0.11757 | 47.0264 | 14.1%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 5 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 8.5668 | 0 | 0 | 8.5668 | 0 | 8.1721 | 0.55805 | 14.644 | 8.1721 | 0.55805 | 14.644 | 8.6087 | 0.58787 | 14.644 | 0.6215%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 8 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 84.5815 | 0 | 0 | 84.5815 | 0 | 80.685 | 0.89288 | 90.3648 | 80.685 | 0.89288 | 90.3648 | 84.9961 | 0.94059 | 90.3648 | 1.606%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 67 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 605.2764 | 0 | 0 | 605.2764 | 0 | 577.3926 | 7.4779 | 77.2135 | 577.3926 | 7.4779 | 77.2135 | 608.2434 | 7.8774 | 77.2135 | 3.616%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 128 | 2 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 18.3025 | 0 | 0 | 18.3025 | 0 | 17.4593 | 0.22322 | 78.2157 | 17.4593 | 0.22322 | 78.2157 | 18.3922 | 0.23515 | 78.2157 | 0.4303%
2026 | 492 | 492-1090F | Tier-1 | Non-HFTD---8 | Non-HFTD---16 | 134 | 5 | 34.6286 | 4.526% | 88.49% | 6.986% | 0.01696 | 0 | 0 | 0.01696 | 0 | 0.016179 | 0.55805 | 0.028991 | 0.016179 | 0.55805 | 0.028991 | 0.017043 | 0.58787 | 0.028991 | 0.04898%
2026 | 492 | 492-1091F | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 258 | 15 | 120.6396 | 2.917% | 93.65% | 3.431% | 0.059332 | 0 | 0 | 0.059332 | 0 | 0.056599 | 1.6742 | 0.033807 | 0.056599 | 1.6742 | 0.033807 | 0.059623 | 1.7636 | 0.033807 | 0.04918%
2026 | 492 | 492-14R | Tier-1 | Non-HFTD---2 | Non-HFTD---8 | 453 | 65 | 216.5783 | 3.253% | 93.45% | 3.298% | 0.29319 | 0 | 0 | 0.29319 | 0 | 0.27969 | 7.2547 | 0.038553 | 0.27969 | 7.2547 | 0.038553 | 0.29463 | 7.6423 | 0.038553 | 0.1354%
2026 | 492 | 492-343R | Tier-1 | Non-HFTD---1 | Non-HFTD---9 | 107 | 8 | 272.4272 | 37.19% | 62.03% | 0.7764% | 2.1968 | 0 | 0 | 2.1968 | 0 | 2.0956 | 0.89288 | 2.347 | 2.0956 | 0.89288 | 2.347 | 2.2076 | 0.94059 | 2.347 | 0.8064%
2026 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 2 | 800.5503 | 21.6% | 78.32% | 0.07823% | 5.015 | 0 | 0 | 5.015 | 0 | 4.7839 | 0.22322 | 21.4315 | 4.7839 | 0.22322 | 21.4315 | 5.0395 | 0.23515 | 21.4315 | 0.6264%
2026 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 351 | 1 | 1424.1907 | 99.61% | 0% | 0.3928% | 1.1721 | 0 | 0 | 1.1721 | 0 | 1.1181 | 0.11161 | 10.0176 | 1.1181 | 0.11161 | 10.0176 | 1.1778 | 0.11757 | 10.0176 | 0.0823%
2026 | 511 | 511-831 | Tier-1 | Non-HFTD---5 | Non-HFTD---15 | 5 | 1 | 45.7736 | 11.2% | 88.5% | 0.2943% | 0.29746 | 0 | 0 | 0.29746 | 0 | 0.28376 | 0.11161 | 2.5424 | 0.28376 | 0.11161 | 2.5424 | 0.29892 | 0.11757 | 2.5424 | 0.6499%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 180 | 2 | 2978.814 | 97.34% | 2.471% | 0.184% | 9.3435 | 0 | 0 | 9.3435 | 0 | 8.9131 | 0.22322 | 39.9296 | 8.9131 | 0.22322 | 39.9296 | 9.3893 | 0.23515 | 39.9296 | 0.3137%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 155 | 18 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 48.7914 | 0 | 0 | 48.7914 | 0 | 46.5437 | 2.009 | 23.1678 | 46.5437 | 2.009 | 23.1678 | 49.0306 | 2.1163 | 23.1678 | 3.3%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 408 | 5 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 9.0709 | 0 | 0 | 9.0709 | 0 | 8.653 | 0.55805 | 15.5058 | 8.653 | 0.55805 | 15.5058 | 9.1154 | 0.58787 | 15.5058 | 0.3439%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 401 | 5 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 11.4459 | 0 | 0 | 11.4459 | 0 | 10.9186 | 0.55805 | 19.5657 | 10.9186 | 0.55805 | 19.5657 | 11.502 | 0.58787 | 19.5657 | 0.3353%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 1 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 3.2096 | 0 | 0 | 3.2096 | 0 | 3.0618 | 0.11161 | 27.4329 | 3.0618 | 0.11161 | 27.4329 | 3.2254 | 0.11757 | 27.4329 | 0.1966%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 249 | 5 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 38.0903 | 0 | 0 | 38.0903 | 0 | 36.3355 | 0.55805 | 65.1115 | 36.3355 | 0.55805 | 65.1115 | 38.277 | 0.58787 | 65.1115 | 0.5632%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 41 | 748.333 | 77.34% | 21.7% | 0.962% | 16.8658 | 0 | 0 | 16.8658 | 0 | 16.0888 | 4.576 | 3.5159 | 16.0888 | 4.576 | 3.5159 | 16.9484 | 4.8205 | 3.5159 | 2.254%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 276 | 29 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 61.2838 | 0 | 0 | 61.2838 | 0 | 58.4606 | 3.2367 | 18.0618 | 58.4606 | 3.2367 | 18.0618 | 61.5842 | 3.4096 | 18.0618 | 2.94%
2026 | 520 | 520-1936 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 2 | 63.7111 | 99.77% | 0% | 0.2279% | 9.2171 | 0 | 0 | 9.2171 | 0 | 8.7925 | 0.22322 | 39.3892 | 8.7925 | 0.22322 | 39.3892 | 9.2622 | 0.23515 | 39.3892 | 14.47%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 113 | 7 | 258.296 | 74.72% | 24.53% | 0.7505% | 3.4673 | 0 | 0 | 3.4673 | 0 | 3.3076 | 0.78127 | 4.2336 | 3.3076 | 0.78127 | 4.2336 | 3.4843 | 0.82301 | 4.2336 | 1.342%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 306 | 2 | 4997.7942 | 96.49% | 3.313% | 0.193% | 9.1409 | 0 | 0 | 9.1409 | 0 | 8.7198 | 0.22322 | 39.0635 | 8.7198 | 0.22322 | 39.0635 | 9.1857 | 0.23515 | 39.0635 | 0.1829%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 219 | 1 | 2044.6463 | 97.57% | 2.13% | 0.298% | 2.6418 | 0 | 0 | 2.6418 | 0 | 2.5201 | 0.11161 | 22.5793 | 2.5201 | 0.11161 | 22.5793 | 2.6547 | 0.11757 | 22.5793 | 0.1292%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 15 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 151.5557 | 0 | 0 | 151.5557 | 0 | 144.5739 | 1.6742 | 86.3565 | 144.5739 | 1.6742 | 86.3565 | 152.2986 | 1.7636 | 86.3565 | 1.335%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 24 | 810.9996 | 89.31% | 10.24% | 0.4457% | 25.3335 | 0 | 0 | 25.3335 | 0 | 24.1664 | 2.6786 | 9.0219 | 24.1664 | 2.6786 | 9.0219 | 25.4576 | 2.8218 | 9.0219 | 3.124%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 25 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 179.4242 | 0 | 0 | 179.4242 | 0 | 171.1585 | 2.7903 | 61.3416 | 171.1585 | 2.7903 | 61.3416 | 180.3038 | 2.9393 | 61.3416 | 2.116%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 30 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 245.3402 | 0 | 0 | 245.3402 | 0 | 234.0378 | 3.3483 | 69.8975 | 234.0378 | 3.3483 | 69.8975 | 246.5428 | 3.5272 | 69.8975 | 2.816%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 23 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 103.404 | 0 | 0 | 103.404 | 0 | 98.6404 | 2.567 | 38.4259 | 98.6404 | 2.567 | 38.4259 | 103.9109 | 2.7042 | 38.4259 | 1.84%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 232 | 1 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 15.2071 | 0 | 0 | 15.2071 | 0 | 14.5065 | 0.11161 | 129.9752 | 14.5065 | 0.11161 | 129.9752 | 15.2816 | 0.11757 | 129.9752 | 0.1242%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 437 | 56 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 331.7544 | 0 | 0 | 331.7544 | 0 | 316.4711 | 6.2502 | 50.6341 | 316.4711 | 6.2502 | 50.6341 | 333.3806 | 6.5841 | 50.6341 | 3.681%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 3 | 112.7117 | 43.02% | 55.81% | 1.165% | 0.65921 | 0 | 0 | 0.65921 | 0 | 0.62884 | 0.33483 | 1.8781 | 0.62884 | 0.33483 | 1.8781 | 0.66244 | 0.35272 | 1.8781 | 0.5849%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 5 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.41091 | 0 | 0 | 0.41091 | 0 | 0.39198 | 0.55805 | 0.7024 | 0.39198 | 0.55805 | 0.7024 | 0.41292 | 0.58787 | 0.7024 | 0.3513%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 52 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 135.3502 | 0 | 0 | 135.3502 | 0 | 129.1149 | 5.8037 | 22.2469 | 129.1149 | 5.8037 | 22.2469 | 136.0137 | 6.1138 | 22.2469 | 2.4%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 33 | 305.199 | 11.7% | 87.21% | 1.095% | 1.7167 | 0 | 0 | 1.7167 | 0 | 1.6376 | 3.6831 | 0.44463 | 1.6376 | 3.6831 | 0.44463 | 1.7251 | 3.8799 | 0.44463 | 0.5625%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 231 | 9 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 61.6442 | 0 | 0 | 61.6442 | 0 | 58.8044 | 1.0045 | 58.5415 | 58.8044 | 1.0045 | 58.5415 | 61.9464 | 1.0582 | 58.5415 | 1.127%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 489 | 34 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 227.6785 | 0 | 0 | 227.6785 | 0 | 217.1898 | 3.7947 | 57.2344 | 217.1898 | 3.7947 | 57.2344 | 228.7945 | 3.9975 | 57.2344 | 2.012%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 283 | 8 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 111.2622 | 0 | 0 | 111.2622 | 0 | 106.1366 | 0.89288 | 118.8699 | 106.1366 | 0.89288 | 118.8699 | 111.8076 | 0.94059 | 118.8699 | 0.8115%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 17 | 8801.877 | 98.2% | 1.718% | 0.0819% | 150.574 | 0 | 0 | 150.574 | 0 | 143.6373 | 1.8974 | 75.7033 | 143.6373 | 1.8974 | 75.7033 | 151.3121 | 1.9987 | 75.7033 | 1.711%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 842 | 38 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 523.3194 | 0 | 0 | 523.3194 | 0 | 499.2112 | 4.2412 | 117.7057 | 499.2112 | 4.2412 | 117.7057 | 525.8847 | 4.4678 | 117.7057 | 1.296%
2026 | 57 | 57-1295F | Tier-1 | Non-HFTD---14 | Non-HFTD---21 | 34 | 2 | 5.7785 | 18.72% | 64.33% | 16.95% | 0.018452 | 0 | 0 | 0.018452 | 0 | 0.017601 | 0.22322 | 0.078853 | 0.017601 | 0.22322 | 0.078853 | 0.018542 | 0.23515 | 0.078853 | 0.3193%
2026 | 57 | 57-1296F | Tier-1 | Non-HFTD---6 | Non-HFTD---12 | 74 | 33 | 54.2561 | 82.4% | 11.86% | 5.738% | 5.7819 | 0 | 0 | 5.7819 | 0 | 5.5155 | 3.6831 | 1.4975 | 5.5155 | 3.6831 | 1.4975 | 5.8102 | 3.8799 | 1.4975 | 10.66%
2026 | 57 | 57-736 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 81 | 6 | 116.8924 | 0.4896% | 98.37% | 1.142% | 0.012295 | 0 | 0 | 0.012295 | 0 | 0.011728 | 0.66966 | 0.017514 | 0.011728 | 0.66966 | 0.017514 | 0.012355 | 0.70544 | 0.017514 | 0.01052%
2026 | 586 | 586-3 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 84 | 4 | 516.8084 | 87.93% | 11.54% | 0.527% | 6.2755 | 0 | 0 | 6.2755 | 0 | 5.9864 | 0.44644 | 13.4092 | 5.9864 | 0.44644 | 13.4092 | 6.3063 | 0.47029 | 13.4092 | 1.214%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 92 | 1 | 519.9571 | 96.32% | 3.27% | 0.4047% | 1.5788 | 0 | 0 | 1.5788 | 0 | 1.506 | 0.11161 | 13.4937 | 1.506 | 0.11161 | 13.4937 | 1.5865 | 0.11757 | 13.4937 | 0.3036%
2026 | 59 | 59-465 | Tier-1 | Non-HFTD---6 | Non-HFTD---8 | 167 | 61 | 77.379 | 64.48% | 28.11% | 7.401% | 5.2856 | 0 | 0 | 5.2856 | 0 | 5.0421 | 6.8082 | 0.74059 | 5.0421 | 6.8082 | 0.74059 | 5.3115 | 7.172 | 0.74059 | 6.831%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 34 | 18774.394 | 95.55% | 4.388% | 0.06321% | 444.413 | 0 | 0 | 444.413 | 0 | 423.9398 | 3.7947 | 111.7177 | 423.9398 | 3.7947 | 111.7177 | 446.5915 | 3.9975 | 111.7177 | 2.367%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 51 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 502.5851 | 0 | 0 | 502.5851 | 0 | 479.4321 | 5.6921 | 84.2274 | 479.4321 | 5.6921 | 84.2274 | 505.0488 | 5.9962 | 84.2274 | 1.952%
2026 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 477 | 8 | 5312.2676 | 97.77% | 1.999% | 0.2313% | 25.2611 | 0 | 0 | 25.2611 | 0 | 24.0974 | 0.89288 | 26.9884 | 24.0974 | 0.89288 | 26.9884 | 25.3849 | 0.94059 | 26.9884 | 0.4755%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 551 | 21 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 43.3383 | 0 | 0 | 43.3383 | 0 | 41.3418 | 2.3438 | 17.6387 | 41.3418 | 2.3438 | 17.6387 | 43.5507 | 2.469 | 17.6387 | 1.037%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 6 | 622.3042 | 87.18% | 11.98% | 0.8373% | 4.9684 | 0 | 0 | 4.9684 | 0 | 4.7395 | 0.66966 | 7.0775 | 4.7395 | 0.66966 | 7.0775 | 4.9927 | 0.70544 | 7.0775 | 0.7984%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 15 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 28.2004 | 0 | 0 | 28.2004 | 0 | 26.9013 | 1.6742 | 16.0686 | 26.9013 | 1.6742 | 16.0686 | 28.3386 | 1.7636 | 16.0686 | 1.732%
2026 | 702 | 702-25 | Tier-1 | Non-HFTD---4 | Non-HFTD---13 | 20 | 3 | 105.79 | 16.96% | 82.58% | 0.4592% | 0.78055 | 0 | 0 | 0.78055 | 0 | 0.74459 | 0.33483 | 2.2238 | 0.74459 | 0.33483 | 2.2238 | 0.78438 | 0.35272 | 2.2238 | 0.7378%
2026 | 702 | 702-27R | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 513 | 104 | 127.2983 | 14.57% | 79% | 6.429% | 1.0906 | 0 | 0 | 1.0906 | 0 | 1.0403 | 11.6074 | 0.089626 | 1.0403 | 11.6074 | 0.089626 | 1.0959 | 12.2276 | 0.089626 | 0.8567%
2026 | 702 | 702-30 | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 328 | 57 | 100.3702 | 67.48% | 26.99% | 5.53% | 3.4131 | 0 | 0 | 3.4131 | 0 | 3.2559 | 6.3618 | 0.51179 | 3.2559 | 6.3618 | 0.51179 | 3.4299 | 6.7017 | 0.51179 | 3.401%
2026 | 702 | 702-448F | Tier-1 | Non-HFTD---19 | Non-HFTD---22 | 2 | 1 | 0.36733 | 90.03% | 0% | 9.967% | 0.047955 | 0 | 0 | 0.047955 | 0 | 0.045745 | 0.11161 | 0.40987 | 0.045745 | 0.11161 | 0.40987 | 0.04819 | 0.11757 | 0.40987 | 13.05%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 6 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 80.683 | 0 | 0 | 80.683 | 0 | 76.9661 | 0.66966 | 114.9331 | 76.9661 | 0.66966 | 114.9331 | 81.0786 | 0.70544 | 114.9331 | 0.5261%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 46 | 1 | 2448.8293 | 98.64% | 1.317% | 0.04316% | 15.2282 | 0 | 0 | 15.2282 | 0 | 14.5267 | 0.11161 | 130.1559 | 14.5267 | 0.11161 | 130.1559 | 15.3029 | 0.11757 | 130.1559 | 0.6219%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 188 | 6 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 52.2231 | 0 | 0 | 52.2231 | 0 | 49.8173 | 0.66966 | 74.3919 | 49.8173 | 0.66966 | 74.3919 | 52.4791 | 0.70544 | 74.3919 | 0.9108%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 313 | 4 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 38.5892 | 0 | 0 | 38.5892 | 0 | 36.8115 | 0.44644 | 82.4555 | 36.8115 | 0.44644 | 82.4555 | 38.7783 | 0.47029 | 82.4555 | 0.3643%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 273 | 1 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 9.7113 | 0 | 0 | 9.7113 | 0 | 9.2639 | 0.11161 | 83.0028 | 9.2639 | 0.11161 | 83.0028 | 9.7589 | 0.11757 | 83.0028 | 0.1046%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 12 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 77.7599 | 0 | 0 | 77.7599 | 0 | 74.1776 | 1.3393 | 55.3845 | 74.1776 | 1.3393 | 55.3845 | 78.141 | 1.4109 | 55.3845 | 2.48%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 7 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 41.1104 | 0 | 0 | 41.1104 | 0 | 39.2165 | 0.78127 | 50.1958 | 39.2165 | 0.78127 | 50.1958 | 41.3119 | 0.82301 | 50.1958 | 2.406%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 69 | 13 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 105.7148 | 0 | 0 | 105.7148 | 0 | 100.8448 | 1.4509 | 69.5035 | 100.8448 | 1.4509 | 69.5035 | 106.233 | 1.5285 | 69.5035 | 5.456%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 48 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 95.7404 | 0 | 0 | 95.7404 | 0 | 91.3298 | 5.3573 | 17.0478 | 91.3298 | 5.3573 | 17.0478 | 96.2097 | 5.6435 | 17.0478 | 4.33%
2026 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 29 | 1 | 5696.3358 | 99.98% | 0% | 0.01771% | 56.9533 | 0 | 0 | 56.9533 | 0 | 54.3295 | 0.11161 | 486.7801 | 54.3295 | 0.11161 | 486.7801 | 57.2325 | 0.11757 | 486.7801 | 0.9998%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 13 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 62.3365 | 0 | 0 | 62.3365 | 0 | 59.4648 | 1.4509 | 40.9839 | 59.4648 | 1.4509 | 40.9839 | 62.6421 | 1.5285 | 40.9839 | 0.6826%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 4 | 3349.7594 | 92.58% | 7.304% | 0.116% | 25.5136 | 0 | 0 | 25.5136 | 0 | 24.3382 | 0.44644 | 54.5161 | 24.3382 | 0.44644 | 54.5161 | 25.6386 | 0.47029 | 54.5161 | 0.7617%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 4 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 13.1823 | 0 | 0 | 13.1823 | 0 | 12.575 | 0.44644 | 28.1673 | 12.575 | 0.44644 | 28.1673 | 13.2469 | 0.47029 | 28.1673 | 0.6316%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 12 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 12.8356 | 0 | 0 | 12.8356 | 0 | 12.2443 | 1.3393 | 9.1422 | 12.2443 | 1.3393 | 9.1422 | 12.8986 | 1.4109 | 9.1422 | 0.7988%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 3 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 60.1915 | 0 | 0 | 60.1915 | 0 | 57.4186 | 0.33483 | 171.4858 | 57.4186 | 0.33483 | 171.4858 | 60.4866 | 0.35272 | 171.4858 | 0.6196%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 192 | 2 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 55.1155 | 0 | 0 | 55.1155 | 0 | 52.5764 | 0.22322 | 235.5363 | 52.5764 | 0.22322 | 235.5363 | 55.3857 | 0.23515 | 235.5363 | 0.2988%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 74 | 1 | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 9.9882 | 0 | 0 | 9.9882 | 0 | 9.528 | 0.11161 | 85.3689 | 9.528 | 0.11161 | 85.3689 | 10.0371 | 0.11757 | 85.3689 | 0.3894%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 180 | 2 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 17.1827 | 0 | 0 | 17.1827 | 0 | 16.3911 | 0.22322 | 73.4302 | 16.3911 | 0.22322 | 73.4302 | 17.2669 | 0.23515 | 73.4302 | 0.3103%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 6 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 74.3452 | 0 | 0 | 74.3452 | 0 | 70.9203 | 0.66966 | 105.9049 | 70.9203 | 0.66966 | 105.9049 | 74.7097 | 0.70544 | 105.9049 | 0.3959%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 218 | 1 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 26.3723 | 0 | 0 | 26.3723 | 0 | 25.1574 | 0.11161 | 225.404 | 25.1574 | 0.11161 | 225.404 | 26.5015 | 0.11757 | 225.404 | 0.132%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 1 | 127.4062 | 99.28% | 0% | 0.716% | 0.96535 | 0 | 0 | 0.96535 | 0 | 0.92088 | 0.11161 | 8.2508 | 0.92088 | 0.11161 | 8.2508 | 0.97008 | 0.11757 | 8.2508 | 0.7577%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 2 | 12.4137 | 98.83% | 0% | 1.166% | 0.54739 | 0 | 0 | 0.54739 | 0 | 0.52217 | 0.22322 | 2.3393 | 0.52217 | 0.22322 | 2.3393 | 0.55007 | 0.23515 | 2.3393 | 4.41%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 16 | 5 | 330.3488 | 99.39% | 0.4551% | 0.1546% | 29.7553 | 0 | 0 | 29.7553 | 0 | 28.3846 | 0.55805 | 50.8638 | 28.3846 | 0.55805 | 50.8638 | 29.9012 | 0.58787 | 50.8638 | 9.007%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 40 | 4 | 232.5563 | 96.66% | 2.796% | 0.5416% | 6.5191 | 0 | 0 | 6.5191 | 0 | 6.2187 | 0.44644 | 13.9296 | 6.2187 | 0.44644 | 13.9296 | 6.551 | 0.47029 | 13.9296 | 2.803%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 18 | 8606.9717 | 99.86% | 0% | 0.1411% | 80.5476 | 0 | 0 | 80.5476 | 0 | 76.8369 | 2.009 | 38.2467 | 76.8369 | 2.009 | 38.2467 | 80.9424 | 2.1163 | 38.2467 | 0.9358%
2026 | 907 | 907-1475 | Tier-3 | Tier-3---21 | Tier-3---21 | 4 | 2 | 4.2814 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.22322 | 0 | 0 | 0.22322 | 0 | 0 | 0.23515 | 0 | 0%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 162 | 11 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 162.2285 | 0 | 0 | 162.2285 | 0 | 154.755 | 1.2277 | 126.0517 | 154.755 | 1.2277 | 126.0517 | 163.0237 | 1.2933 | 126.0517 | 1.922%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 5 | 1 | 257.2419 | 98.67% | 1.294% | 0.04048% | 14.7209 | 0 | 0 | 14.7209 | 0 | 14.0428 | 0.11161 | 125.8199 | 14.0428 | 0.11161 | 125.8199 | 14.7931 | 0.11757 | 125.8199 | 5.723%
2026 | 907 | 907-1604 | Tier-3 | Tier-3---19 | Tier-3---16 | 2 | 1 | 17.8439 | 83.33% | 16.48% | 0.1969% | 2.156 | 0 | 0 | 2.156 | 0 | 2.0567 | 0.11161 | 18.4272 | 2.0567 | 0.11161 | 18.4272 | 2.1665 | 0.11757 | 18.4272 | 12.08%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 7 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 124.4836 | 0 | 0 | 124.4836 | 0 | 118.7489 | 0.78127 | 151.9947 | 118.7489 | 0.78127 | 151.9947 | 125.0938 | 0.82301 | 151.9947 | 1.368%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 30 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 602.008 | 0 | 0 | 602.008 | 0 | 574.2747 | 3.3483 | 171.5123 | 574.2747 | 3.3483 | 171.5123 | 604.959 | 3.5272 | 171.5123 | 2.224%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 10 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 148.3745 | 0 | 0 | 148.3745 | 0 | 141.5392 | 1.1161 | 126.8158 | 141.5392 | 1.1161 | 126.8158 | 149.1018 | 1.1757 | 126.8158 | 0.9411%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 15 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 304.5786 | 0 | 0 | 304.5786 | 0 | 290.5473 | 1.6742 | 173.549 | 290.5473 | 1.6742 | 173.549 | 306.0716 | 1.7636 | 173.549 | 2.589%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 471 | 28 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 92.4372 | 0 | 0 | 92.4372 | 0 | 88.1788 | 3.1251 | 28.2165 | 88.1788 | 3.1251 | 28.2165 | 92.8903 | 3.2921 | 28.2165 | 1.659%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 5 | 1466.2762 | 91.81% | 7.905% | 0.289% | 13.0126 | 0 | 0 | 13.0126 | 0 | 12.4131 | 0.55805 | 22.2437 | 12.4131 | 0.55805 | 22.2437 | 13.0764 | 0.58787 | 22.2437 | 0.8875%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 11 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 203.038 | 0 | 0 | 203.038 | 0 | 193.6845 | 1.2277 | 157.7607 | 193.6845 | 1.2277 | 157.7607 | 204.0333 | 1.2933 | 157.7607 | 2.551%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 27 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 584.043 | 0 | 0 | 584.043 | 0 | 557.1374 | 3.0135 | 184.8823 | 557.1374 | 3.0135 | 184.8823 | 586.906 | 3.1745 | 184.8823 | 1.416%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 162 | 13 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 78.0012 | 0 | 0 | 78.0012 | 0 | 74.4078 | 1.4509 | 51.2828 | 74.4078 | 1.4509 | 51.2828 | 78.3835 | 1.5285 | 51.2828 | 2.139%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 22 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 392.9491 | 0 | 0 | 392.9491 | 0 | 374.8467 | 2.4554 | 152.6609 | 374.8467 | 2.4554 | 152.6609 | 394.8753 | 2.5866 | 152.6609 | 1.741%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 4 | 847.524 | 96.52% | 3.329% | 0.1488% | 18.2487 | 0 | 0 | 18.2487 | 0 | 17.4081 | 0.44644 | 38.993 | 17.4081 | 0.44644 | 38.993 | 18.3382 | 0.47029 | 38.993 | 2.153%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 18 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 565.8518 | 0 | 0 | 565.8518 | 0 | 539.7842 | 2.009 | 268.6856 | 539.7842 | 2.009 | 268.6856 | 568.6256 | 2.1163 | 268.6856 | 1.024%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 1 | 5703.0403 | 99.97% | 0% | 0.03309% | 26.6667 | 0 | 0 | 26.6667 | 0 | 25.4382 | 0.11161 | 227.9204 | 25.4382 | 0.11161 | 227.9204 | 26.7974 | 0.11757 | 227.9204 | 0.4676%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 16 | 32313.161 | 99.26% | 0.708% | 0.02831% | 481.6478 | 0 | 0 | 481.6478 | 0 | 459.4593 | 1.7858 | 257.2905 | 459.4593 | 1.7858 | 257.2905 | 484.0088 | 1.8812 | 257.2905 | 1.491%
2026 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 3 | 1 | 62.9838 | 99.88% | 0% | 0.1185% | 6.0812 | 0 | 0 | 6.0812 | 0 | 5.8011 | 0.11161 | 51.9763 | 5.8011 | 0.11161 | 51.9763 | 6.111 | 0.11757 | 51.9763 | 9.655%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 194 | 29 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 53.923 | 0 | 0 | 53.923 | 0 | 51.4389 | 3.2367 | 15.8924 | 51.4389 | 3.2367 | 15.8924 | 54.1873 | 3.4096 | 15.8924 | 4.161%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 12 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 89.8995 | 0 | 0 | 89.8995 | 0 | 85.758 | 1.3393 | 64.031 | 85.758 | 1.3393 | 64.031 | 90.3402 | 1.4109 | 64.031 | 2.639%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 7 | 1554.328 | 69.02% | 30.62% | 0.3611% | 7.3825 | 0 | 0 | 7.3825 | 0 | 7.0424 | 0.78127 | 9.014 | 7.0424 | 0.78127 | 9.014 | 7.4186 | 0.82301 | 9.014 | 0.475%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 36 | 1 | 434.8834 | 99.47% | 0.2691% | 0.2608% | 3.4847 | 0 | 0 | 3.4847 | 0 | 3.3241 | 0.11161 | 29.7835 | 3.3241 | 0.11161 | 29.7835 | 3.5017 | 0.11757 | 29.7835 | 0.8013%
2026 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 3 | 62.492 | 96.91% | 0.773% | 2.32% | 1.1974 | 0 | 0 | 1.1974 | 0 | 1.1423 | 0.33483 | 3.4115 | 1.1423 | 0.33483 | 3.4115 | 1.2033 | 0.35272 | 3.4115 | 1.916%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 3 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 122.1525 | 0 | 0 | 122.1525 | 0 | 116.5252 | 0.33483 | 348.0127 | 116.5252 | 0.33483 | 348.0127 | 122.7512 | 0.35272 | 348.0127 | 0.9424%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 4 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 50.5993 | 0 | 0 | 50.5993 | 0 | 48.2683 | 0.44644 | 108.1181 | 48.2683 | 0.44644 | 108.1181 | 50.8473 | 0.47029 | 108.1181 | 0.334%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 2 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 27.3725 | 0 | 0 | 27.3725 | 0 | 26.1115 | 0.22322 | 116.9765 | 26.1115 | 0.22322 | 116.9765 | 27.5067 | 0.23515 | 116.9765 | 0.0961%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 2 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 43.3045 | 0 | 0 | 43.3045 | 0 | 41.3095 | 0.22322 | 185.0618 | 41.3095 | 0.22322 | 185.0618 | 43.5167 | 0.23515 | 185.0618 | 0.9952%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 1 | 191.8954 | 99.94% | 0% | 0.06293% | 27.8073 | 0 | 0 | 27.8073 | 0 | 26.5263 | 0.11161 | 237.6694 | 26.5263 | 0.11161 | 237.6694 | 27.9436 | 0.11757 | 237.6694 | 14.49%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 11 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 165.0512 | 0 | 0 | 165.0512 | 0 | 157.4476 | 1.2277 | 128.2449 | 157.4476 | 1.2277 | 128.2449 | 165.8602 | 1.2933 | 128.2449 | 1.117%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 406 | 3 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 23.8987 | 0 | 0 | 23.8987 | 0 | 22.7978 | 0.33483 | 68.0876 | 22.7978 | 0.33483 | 68.0876 | 24.0159 | 0.35272 | 68.0876 | 0.2121%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 213 | 2 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 21.5163 | 0 | 0 | 21.5163 | 0 | 20.5251 | 0.22322 | 91.95 | 20.5251 | 0.22322 | 91.95 | 21.6218 | 0.23515 | 91.95 | 0.2683%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 50 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 479.1634 | 0 | 0 | 479.1634 | 0 | 457.0893 | 5.5805 | 81.9083 | 457.0893 | 5.5805 | 81.9083 | 481.5122 | 5.8787 | 81.9083 | 2.047%
2026 | 972 | 972-1641 | Tier-2 | Tier-2---13 | Tier-2---5 | 3 | 1 | 295.0839 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.11161 | 0 | 0 | 0.11161 | 0 | 0 | 0.11757 | 0 | 0%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 543 | 62 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 739.6135 | 0 | 0 | 739.6135 | 0 | 705.541 | 6.9198 | 101.9594 | 705.541 | 6.9198 | 101.9594 | 743.239 | 7.2896 | 101.9594 | 3.228%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 2 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 15.0658 | 0 | 0 | 15.0658 | 0 | 14.3718 | 0.22322 | 64.3839 | 14.3718 | 0.22322 | 64.3839 | 15.1397 | 0.23515 | 64.3839 | 0.291%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 389 | 8 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 19.5176 | 0 | 0 | 19.5176 | 0 | 18.6185 | 0.89288 | 20.8522 | 18.6185 | 0.89288 | 20.8522 | 19.6133 | 0.94059 | 20.8522 | 0.5588%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 2 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 30.6233 | 0 | 0 | 30.6233 | 0 | 29.2125 | 0.22322 | 130.8686 | 29.2125 | 0.22322 | 130.8686 | 30.7734 | 0.23515 | 130.8686 | 0.4309%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 30 | 2 | 6417.0381 | 80.3% | 19.69% | 0.01691% | 99.619 | 0 | 0 | 99.619 | 0 | 95.0297 | 0.22322 | 425.722 | 95.0297 | 0.22322 | 425.722 | 100.1073 | 0.23515 | 425.722 | 1.552%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 1 | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.9388 | 0.11161 | 35.2911 | 3.9388 | 0.11161 | 35.2911 | 4.1493 | 0.11757 | 35.2911 | 0.6587%
2026 | CB 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 1 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 12.3676 | 0 | 0 | 12.3676 | 0 | 11.7979 | 0.11161 | 105.7062 | 11.7979 | 0.11161 | 105.7062 | 12.4283 | 0.11757 | 105.7062 | 0.3711%
2026 | CB 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 111 | 3 | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 11.0447 | 0 | 0 | 11.0447 | 0 | 10.5359 | 0.33483 | 31.4663 | 10.5359 | 0.33483 | 31.4663 | 11.0988 | 0.35272 | 31.4663 | 0.7808%
2026 | CB 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 1 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 7.9934 | 0 | 0 | 7.9934 | 0 | 7.6252 | 0.11161 | 68.3199 | 7.6252 | 0.11161 | 68.3199 | 8.0326 | 0.11757 | 68.3199 | 0.7053%
2026 | CB 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 15 | 765.4961 | 75% | 24.28% | 0.7274% | 8.5817 | 0 | 0 | 8.5817 | 0 | 8.1864 | 1.6742 | 4.8899 | 8.1864 | 1.6742 | 4.8899 | 8.6238 | 1.7636 | 4.8899 | 1.121%
2026 | CB 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 34 | 4 | 75.2008 | 96.65% | 1.975% | 1.378% | 2.4796 | 0 | 0 | 2.4796 | 0 | 2.3654 | 0.44644 | 5.2984 | 2.3654 | 0.44644 | 5.2984 | 2.4918 | 0.47029 | 5.2984 | 3.297%
2026 | CB 1180 | CB 1180 | Tier-1 | Non-HFTD---7 | Non-HFTD---17 | 39 | 5 | 35.2333 | 97.75% | 0% | 2.252% | 1.2805 | 0 | 0 | 1.2805 | 0 | 1.2215 | 0.55805 | 2.1888 | 1.2215 | 0.55805 | 2.1888 | 1.2867 | 0.58787 | 2.1888 | 3.634%
2026 | CB 120 | CB 120 | Tier-1 | Non-HFTD---5 | Non-HFTD---13 | 18 | 2 | 72.8901 | 46.84% | 52.05% | 1.107% | 1.1002 | 0 | 0 | 1.1002 | 0 | 1.0495 | 0.22322 | 4.7016 | 1.0495 | 0.22322 | 4.7016 | 1.1056 | 0.23515 | 4.7016 | 1.509%
2026 | CB 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 42 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 269.9817 | 0 | 0 | 269.9817 | 0 | 257.5442 | 4.6876 | 54.9413 | 257.5442 | 4.6876 | 54.9413 | 271.3052 | 4.9381 | 54.9413 | 4.278%
2026 | CB 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 44 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 135.0924 | 0 | 0 | 135.0924 | 0 | 128.8689 | 4.9108 | 26.2417 | 128.8689 | 4.9108 | 26.2417 | 135.7546 | 5.1732 | 26.2417 | 2.033%
2026 | CB 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 3 | 1438.3629 | 99.75% | 0% | 0.2509% | 10.7607 | 0 | 0 | 10.7607 | 0 | 10.2649 | 0.33483 | 30.6571 | 10.2649 | 0.33483 | 30.6571 | 10.8134 | 0.35272 | 30.6571 | 0.7481%
2026 | CB 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 1 | 41.7756 | 94.08% | 0% | 5.924% | 0.14996 | 0 | 0 | 0.14996 | 0 | 0.14306 | 0.11161 | 1.2817 | 0.14306 | 0.11161 | 1.2817 | 0.1507 | 0.11757 | 1.2817 | 0.359%
2026 | CB 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 184 | 3 | 259.6903 | 35.49% | 63.12% | 1.387% | 0.43581 | 0 | 0 | 0.43581 | 0 | 0.41573 | 0.33483 | 1.2416 | 0.41573 | 0.33483 | 1.2416 | 0.43794 | 0.35272 | 1.2416 | 0.1678%
2026 | CB 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 478 | 39 | 1342.6559 | 29.9% | 69.37% | 0.7369% | 9.4976 | 0 | 0 | 9.4976 | 0 | 9.0601 | 4.3528 | 2.0814 | 9.0601 | 4.3528 | 2.0814 | 9.5442 | 4.5854 | 2.0814 | 0.7074%
2026 | CB 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 44 | 133.9861 | 95.12% | 0% | 4.877% | 8.4263 | 0 | 0 | 8.4263 | 0 | 8.0381 | 4.9108 | 1.6368 | 8.0381 | 4.9108 | 1.6368 | 8.4676 | 5.1732 | 1.6368 | 6.289%
2026 | CB 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 233 | 39 | 195.752 | 9.583% | 88.23% | 2.187% | 0.91061 | 0 | 0 | 0.91061 | 0 | 0.86866 | 4.3528 | 0.19956 | 0.86866 | 4.3528 | 0.19956 | 0.91507 | 4.5854 | 0.19956 | 0.4652%
2026 | CB 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 229 | 20 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 21.6889 | 0 | 0 | 21.6889 | 0 | 20.6898 | 2.2322 | 9.2688 | 20.6898 | 2.2322 | 9.2688 | 21.7953 | 2.3515 | 9.2688 | 2.047%
2026 | CB 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 25 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 69.2131 | 0 | 0 | 69.2131 | 0 | 66.0246 | 2.7903 | 23.6626 | 66.0246 | 2.7903 | 23.6626 | 69.5524 | 2.9393 | 23.6626 | 2.769%
2026 | CB 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 259 | 24 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 42.9818 | 0 | 0 | 42.9818 | 0 | 41.0017 | 2.6786 | 15.3069 | 41.0017 | 2.6786 | 15.3069 | 43.1925 | 2.8218 | 15.3069 | 2.617%
2026 | CB 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 613 | 40 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 77.1237 | 0 | 0 | 77.1237 | 0 | 73.5708 | 4.4644 | 16.4794 | 73.5708 | 4.4644 | 16.4794 | 77.5018 | 4.7029 | 16.4794 | 1.868%
2026 | CB 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 42 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 112.7289 | 0 | 0 | 112.7289 | 0 | 107.5357 | 4.6876 | 22.9404 | 107.5357 | 4.6876 | 22.9404 | 113.2815 | 4.9381 | 22.9404 | 3.421%
2026 | CB 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 9 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 96.1022 | 0 | 0 | 96.1022 | 0 | 91.675 | 1.0045 | 91.2652 | 91.675 | 1.0045 | 91.2652 | 96.5733 | 1.0582 | 91.2652 | 0.756%
2026 | CB 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 41 | 3 | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 44.6014 | 0 | 0 | 44.6014 | 0 | 42.5467 | 0.33483 | 127.0695 | 42.5467 | 0.33483 | 127.0695 | 44.82 | 0.35272 | 127.0695 | 2.112%
2026 | CB 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 17 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 25.555 | 0 | 0 | 25.555 | 0 | 24.3778 | 1.8974 | 12.8482 | 24.3778 | 1.8974 | 12.8482 | 25.6803 | 1.9987 | 12.8482 | 2.023%
2026 | CB 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 8 | 406.8184 | 64.36% | 35.02% | 0.6193% | 6.9824 | 0 | 0 | 6.9824 | 0 | 6.6608 | 0.89288 | 7.4599 | 6.6608 | 0.89288 | 7.4599 | 7.0167 | 0.94059 | 7.4599 | 1.716%
2026 | CB 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 197 | 3 | 295.5508 | 37.5% | 61.39% | 1.106% | 0.48951 | 0 | 0 | 0.48951 | 0 | 0.46696 | 0.33483 | 1.3946 | 0.46696 | 0.33483 | 1.3946 | 0.49191 | 0.35272 | 1.3946 | 0.1656%
2026 | CB 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 21 | 1438.4419 | 90% | 9.47% | 0.5268% | 26.0211 | 0 | 0 | 26.0211 | 0 | 24.8223 | 2.3438 | 10.5906 | 24.8223 | 2.3438 | 10.5906 | 26.1486 | 2.469 | 10.5906 | 1.809%
2026 | CB 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 2 | 379.7423 | 70.28% | 29.01% | 0.71% | 1.7199 | 0 | 0 | 1.7199 | 0 | 1.6407 | 0.22322 | 7.35 | 1.6407 | 0.22322 | 7.35 | 1.7283 | 0.23515 | 7.35 | 0.4529%
2026 | CB 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 101 | 2 | 826.9208 | 97.04% | 2.672% | 0.2884% | 4.6081 | 0 | 0 | 4.6081 | 0 | 4.3958 | 0.22322 | 19.6926 | 4.3958 | 0.22322 | 19.6926 | 4.6307 | 0.23515 | 19.6926 | 0.5573%
2026 | CB 275 | CB 275 | Tier-1 | Non-HFTD---2 | Non-HFTD---9 | 66 | 14 | 206.6235 | 45.85% | 53.34% | 0.8107% | 5.8277 | 0 | 0 | 5.8277 | 0 | 5.5593 | 1.5625 | 3.5578 | 5.5593 | 1.5625 | 3.5578 | 5.8563 | 1.646 | 3.5578 | 2.82%
2026 | CB 276 | CB 276 | Tier-1 | Non-HFTD---10 | Non-HFTD---16 | 28 | 1 | 26.0793 | 53.94% | 42.4% | 3.659% | 0.14571 | 0 | 0 | 0.14571 | 0 | 0.13899 | 0.11161 | 1.2453 | 0.13899 | 0.11161 | 1.2453 | 0.14642 | 0.11757 | 1.2453 | 0.5587%
2026 | CB 277 | CB 277 | Tier-1 | Non-HFTD---11 | Non-HFTD---17 | 11 | 1 | 9.2421 | 96.22% | 0% | 3.783% | 0.23444 | 0 | 0 | 0.23444 | 0 | 0.22364 | 0.11161 | 2.0037 | 0.22364 | 0.11161 | 2.0037 | 0.23559 | 0.11757 | 2.0037 | 2.537%
2026 | CB 305 | CB 305 | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 170 | 22 | 2786.7739 | 97.11% | 2.732% | 0.1605% | 101.5604 | 0 | 0 | 101.5604 | 0 | 96.8817 | 2.4554 | 39.4563 | 96.8817 | 2.4554 | 39.4563 | 102.0583 | 2.5866 | 39.4563 | 3.644%
2026 | CB 306 | CB 306 | Tier-1 | Non-HFTD---1 | Non-HFTD---4 | 46 | 14 | 737.4997 | 97.09% | 2.802% | 0.1119% | 63.1955 | 0 | 0 | 63.1955 | 0 | 60.2843 | 1.5625 | 38.5809 | 60.2843 | 1.5625 | 38.5809 | 63.5053 | 1.646 | 38.5809 | 8.569%
2026 | CB 307 | CB 307 | Tier-1 | Non-HFTD---1 | Non-HFTD---4 | 30 | 6 | 601.8674 | 89.73% | 10.15% | 0.1197% | 31.3245 | 0 | 0 | 31.3245 | 0 | 29.8814 | 0.66966 | 44.6218 | 29.8814 | 0.66966 | 44.6218 | 31.478 | 0.70544 | 44.6218 | 5.205%
2026 | CB 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 156 | 15 | 124.2501 | 33.35% | 64.03% | 2.615% | 1.1556 | 0 | 0 | 1.1556 | 0 | 1.1024 | 1.6742 | 0.65846 | 1.1024 | 1.6742 | 0.65846 | 1.1613 | 1.7636 | 0.65846 | 0.9301%
2026 | CB 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 48 | 3 | 261.2105 | 99.38% | 0% | 0.6196% | 4.7051 | 0 | 0 | 4.7051 | 0 | 4.4884 | 0.33483 | 13.4049 | 4.4884 | 0.33483 | 13.4049 | 4.7282 | 0.35272 | 13.4049 | 1.801%
2026 | CB 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 20 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 214.2743 | 0 | 0 | 214.2743 | 0 | 204.4031 | 2.2322 | 91.5702 | 204.4031 | 2.2322 | 91.5702 | 215.3246 | 2.3515 | 91.5702 | 1.898%
2026 | CB 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 8 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 84.0191 | 0 | 0 | 84.0191 | 0 | 80.1485 | 0.89288 | 89.764 | 80.1485 | 0.89288 | 89.764 | 84.4309 | 0.94059 | 89.764 | 1.375%
2026 | CB 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 21 | 2 | 861.4334 | 18.88% | 81.11% | 0.0161% | 4.4913 | 0 | 0 | 4.4913 | 0 | 4.2844 | 0.22322 | 19.1938 | 4.2844 | 0.22322 | 19.1938 | 4.5134 | 0.23515 | 19.1938 | 0.5214%
2026 | CB 385 | CB 385 | Tier-1 | Non-HFTD---7 | Non-HFTD---15 | 143 | 1 | 37.1529 | 92.67% | 0% | 7.33% | 0.069823 | 0 | 0 | 0.069823 | 0 | 0.066606 | 0.11161 | 0.59677 | 0.066606 | 0.11161 | 0.59677 | 0.070165 | 0.11757 | 0.59677 | 0.1879%
2026 | CB 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 17 | 1 | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.957 | 0 | 0 | 1.957 | 0 | 1.8669 | 0.11161 | 16.7266 | 1.8669 | 0.11161 | 16.7266 | 1.9666 | 0.11757 | 16.7266 | 1.666%
2026 | CB 461 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 36 | 1 | 101.8709 | 98.65% | 0% | 1.347% | 0.80957 | 0 | 0 | 0.80957 | 0 | 0.77228 | 0.11161 | 6.9194 | 0.77228 | 0.11161 | 6.9194 | 0.81354 | 0.11757 | 6.9194 | 0.7947%
2026 | CB 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 14 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 70.4325 | 0 | 0 | 70.4325 | 0 | 67.1878 | 1.5625 | 42.9991 | 67.1878 | 1.5625 | 42.9991 | 70.7778 | 1.646 | 42.9991 | 1.018%
2026 | CB 474 | CB 474 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 170 | 27 | 794.8798 | 99.6% | 0% | 0.3957% | 36.4664 | 0 | 0 | 36.4664 | 0 | 34.7864 | 3.0135 | 11.5436 | 34.7864 | 3.0135 | 11.5436 | 36.6451 | 3.1745 | 11.5436 | 4.588%
2026 | CB 492 | CB 492 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 98 | 21 | 147.6974 | 50.2% | 48.6% | 1.193% | 4.6079 | 0 | 0 | 4.6079 | 0 | 4.3956 | 2.3438 | 1.8754 | 4.3956 | 2.3438 | 1.8754 | 4.6305 | 2.469 | 1.8754 | 3.12%
2026 | CB 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 1 | 19.4193 | 94.64% | 0% | 5.361% | 0.17193 | 0 | 0 | 0.17193 | 0 | 0.16401 | 0.11161 | 1.4695 | 0.16401 | 0.11161 | 1.4695 | 0.17277 | 0.11757 | 1.4695 | 0.8853%
2026 | CB 511 | CB 511 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 40 | 2 | 163.9412 | 95.95% | 3.193% | 0.8556% | 2.2809 | 0 | 0 | 2.2809 | 0 | 2.1758 | 0.22322 | 9.7475 | 2.1758 | 0.22322 | 9.7475 | 2.2921 | 0.23515 | 9.7475 | 1.391%
2026 | CB 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 14 | 1 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.042728 | 0 | 0 | 0.042728 | 0 | 0.040759 | 0.11161 | 0.3652 | 0.040759 | 0.11161 | 0.3652 | 0.042937 | 0.11757 | 0.3652 | 0.3479%
2026 | CB 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 22 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 24.2456 | 0 | 0 | 24.2456 | 0 | 23.1287 | 2.4554 | 9.4194 | 23.1287 | 2.4554 | 9.4194 | 24.3645 | 2.5866 | 9.4194 | 2.257%
2026 | CB 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 40 | 305.5692 | 37.2% | 61.32% | 1.484% | 5.0908 | 0 | 0 | 5.0908 | 0 | 4.8562 | 4.4644 | 1.0878 | 4.8562 | 4.4644 | 1.0878 | 5.1157 | 4.7029 | 1.0878 | 1.666%
2026 | CB 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 19 | 1 | 417.7025 | 78.37% | 21.49% | 0.1463% | 4.9963 | 0 | 0 | 4.9963 | 0 | 4.7661 | 0.11161 | 42.703 | 4.7661 | 0.11161 | 42.703 | 5.0207 | 0.11757 | 42.703 | 1.196%
2026 | CB 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 33 | 4323.2442 | 99.81% | 0% | 0.1903% | 111.9098 | 0 | 0 | 111.9098 | 0 | 106.7543 | 3.6831 | 28.9847 | 106.7543 | 3.6831 | 28.9847 | 112.4584 | 3.8799 | 28.9847 | 2.589%
2026 | CB 60 | CB 60 | Tier-1 | Non-HFTD---11 | Non-HFTD---18 | 105 | 1 | 10.2312 | 82.34% | 0% | 17.66% | 0.023267 | 0 | 0 | 0.023267 | 0 | 0.022195 | 0.11161 | 0.19886 | 0.022195 | 0.11161 | 0.19886 | 0.023381 | 0.11757 | 0.19886 | 0.2274%
2026 | CB 65 | CB 65 | Tier-1 | Non-HFTD---2 | Non-HFTD---9 | 188 | 66 | 189.2656 | 62.06% | 35.57% | 2.376% | 11.9579 | 0 | 0 | 11.9579 | 0 | 11.407 | 7.3663 | 1.5485 | 11.407 | 7.3663 | 1.5485 | 12.0165 | 7.7599 | 1.5485 | 6.318%
2026 | CB 66 | CB 66 | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 235 | 1 | 917.8674 | 93.46% | 5.958% | 0.5799% | 1.0586 | 0 | 0 | 1.0586 | 0 | 1.0099 | 0.11161 | 9.0482 | 1.0099 | 0.11161 | 9.0482 | 1.0638 | 0.11757 | 9.0482 | 0.1153%
2026 | CB 738 | CB 738 | Tier-1 | Non-HFTD---17 | Non-HFTD---24 | 14 | 1 | 2.031 | 77.55% | 0% | 22.45% | 0.032626 | 0 | 0 | 0.032626 | 0 | 0.031123 | 0.11161 | 0.27885 | 0.031123 | 0.11161 | 0.27885 | 0.032786 | 0.11757 | 0.27885 | 1.606%
2026 | CB 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 53 | 2 | 55.0677 | 92.66% | 4.028% | 3.312% | 0.55839 | 0 | 0 | 0.55839 | 0 | 0.53267 | 0.22322 | 2.3863 | 0.53267 | 0.22322 | 2.3863 | 0.56113 | 0.23515 | 2.3863 | 1.014%
2026 | CB 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 10 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 33.3698 | 0 | 0 | 33.3698 | 0 | 31.8325 | 1.1161 | 28.5212 | 31.8325 | 1.1161 | 28.5212 | 33.5333 | 1.1757 | 28.5212 | 0.3894%
2026 | CB 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 1 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 15.5675 | 0 | 0 | 15.5675 | 0 | 14.8504 | 0.11161 | 133.0557 | 14.8504 | 0.11161 | 133.0557 | 15.6438 | 0.11757 | 133.0557 | 0.5677%
2026 | CB 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 1 | 337.7351 | 93.43% | 6.078% | 0.496% | 1.3456 | 0 | 0 | 1.3456 | 0 | 1.2837 | 0.11161 | 11.5013 | 1.2837 | 0.11161 | 11.5013 | 1.3522 | 0.11757 | 11.5013 | 0.3984%
2026 | CB 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 4 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 24.6966 | 0 | 0 | 24.6966 | 0 | 23.5589 | 0.44644 | 52.7705 | 23.5589 | 0.44644 | 52.7705 | 24.8176 | 0.47029 | 52.7705 | 1.492%
2026 | CB 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 7 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 138.5794 | 0 | 0 | 138.5794 | 0 | 132.1953 | 0.78127 | 169.2056 | 132.1953 | 0.78127 | 169.2056 | 139.2587 | 0.82301 | 169.2056 | 1.21%
2026 | CB BK1 | CB BK1 | Tier-1 | Non-HFTD---8 | Non-HFTD---12 | 136 | 7 | 44.2018 | 7.123% | 86.74% | 6.139% | 0.046993 | 0 | 0 | 0.046993 | 0 | 0.044828 | 0.78127 | 0.057378 | 0.044828 | 0.78127 | 0.057378 | 0.047223 | 0.82301 | 0.057378 | 0.1063%
2026 | CB BK2 | CB BK2 | Tier-1 | Non-HFTD---9 | Non-HFTD---12 | 74 | 1 | 25.856 | 1.714% | 93.1% | 5.186% | 0.0017371 | 0 | 0 | 0.0017371 | 0 | 0.0016571 | 0.11161 | 0.014847 | 0.0016571 | 0.11161 | 0.014847 | 0.0017457 | 0.11757 | 0.014847 | 0.006719%
2026 | CB BK4 | CB BK4 | Tier-1 | Non-HFTD---8 | Non-HFTD---16 | 102 | 6 | 27.9552 | 2.318% | 91.59% | 6.093% | 0.011056 | 0 | 0 | 0.011056 | 0 | 0.010546 | 0.66966 | 0.015749 | 0.010546 | 0.66966 | 0.015749 | 0.01111 | 0.70544 | 0.015749 | 0.03955%
2026 | CB FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 43 | 346.5871 | 36.93% | 61.45% | 1.621% | 4.302 | 0 | 0 | 4.302 | 0 | 4.1038 | 4.7992 | 0.85509 | 4.1038 | 4.7992 | 0.85509 | 4.3231 | 5.0557 | 0.85509 | 1.241%
2026 | CB FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 23 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 37.4442 | 0 | 0 | 37.4442 | 0 | 35.7192 | 2.567 | 13.9146 | 35.7192 | 2.567 | 13.9146 | 37.6278 | 2.7042 | 13.9146 | 3.637%
2026 | CB JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 80 | 7 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 38.0306 | 0 | 0 | 38.0306 | 0 | 36.2786 | 0.78127 | 46.4354 | 36.2786 | 0.78127 | 46.4354 | 38.217 | 0.82301 | 46.4354 | 2.483%
2026 | CB MA1 | CB MA1 | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 475 | 3 | 187.6887 | 3.137% | 92.99% | 3.876% | 0.010785 | 0 | 0 | 0.010785 | 0 | 0.010288 | 0.33483 | 0.030727 | 0.010288 | 0.33483 | 0.030727 | 0.010838 | 0.35272 | 0.030727 | 0.005746%
2026 | CB MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 116 | 2 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 25.2289 | 0 | 0 | 25.2289 | 0 | 24.0667 | 0.22322 | 107.816 | 24.0667 | 0.22322 | 107.816 | 25.3526 | 0.23515 | 107.816 | 0.4928%
2026 | CB NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 403 | 2 | 638.0788 | 99.02% | 0% | 0.9838% | 0.90929 | 0 | 0 | 0.90929 | 0 | 0.8674 | 0.22322 | 3.8859 | 0.8674 | 0.22322 | 3.8859 | 0.91375 | 0.23515 | 3.8859 | 0.1425%
2026 | CB OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 190 | 25 | 6915.6819 | 99% | 0.9206% | 0.07911% | 261.2499 | 0 | 0 | 261.2499 | 0 | 249.2146 | 2.7903 | 89.3162 | 249.2146 | 2.7903 | 89.3162 | 262.5305 | 2.9393 | 89.3162 | 3.778%
2026 | CB PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 247 | 3 | 3027.5479 | 94.73% | 5.109% | 0.164% | 10.1015 | 0 | 0 | 10.1015 | 0 | 9.6361 | 0.33483 | 28.7792 | 9.6361 | 0.33483 | 28.7792 | 10.151 | 0.35272 | 28.7792 | 0.3337%
2026 | CB RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 15 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 127.4067 | 0 | 0 | 127.4067 | 0 | 121.5373 | 1.6742 | 72.5964 | 121.5373 | 1.6742 | 72.5964 | 128.0312 | 1.7636 | 72.5964 | 1.211%
2026 | CB RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 9 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 113.4954 | 0 | 0 | 113.4954 | 0 | 108.2669 | 1.0045 | 107.7829 | 108.2669 | 1.0045 | 107.7829 | 114.0518 | 1.0582 | 107.7829 | 2.17%
2026 | CB RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 25 | 916.1972 | 69.5% | 30.07% | 0.4286% | 19.1549 | 0 | 0 | 19.1549 | 0 | 18.2725 | 2.7903 | 6.5487 | 18.2725 | 2.7903 | 6.5487 | 19.2488 | 2.9393 | 6.5487 | 2.091%
2026 | CB RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 9 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 102.9456 | 0 | 0 | 102.9456 | 0 | 98.2031 | 1.0045 | 97.7641 | 98.2031 | 1.0045 | 97.7641 | 103.4503 | 1.0582 | 97.7641 | 2.753%
2026 | CB SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 225 | 21 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 85.2673 | 0 | 0 | 85.2673 | 0 | 81.3392 | 2.3438 | 34.7038 | 81.3392 | 2.3438 | 34.7038 | 85.6853 | 2.469 | 34.7038 | 2.537%
2026 | CB SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 220 | 17 | 94.186 | 2.003% | 94.63% | 3.363% | 0.042277 | 0 | 0 | 0.042277 | 0 | 0.04033 | 1.8974 | 0.021256 | 0.04033 | 1.8974 | 0.021256 | 0.042485 | 1.9987 | 0.021256 | 0.04489%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 13 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 19.5527 | 0 | 0 | 19.5527 | 0 | 18.6519 | 1.4509 | 12.8551 | 18.6519 | 1.4509 | 12.8551 | 19.6485 | 1.5285 | 12.8551 | 0.9473%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 235 | 22 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 96.0968 | 0 | 0 | 96.0968 | 0 | 91.6698 | 2.4554 | 37.3337 | 91.6698 | 2.4554 | 37.3337 | 96.5679 | 2.5866 | 37.3337 | 2.584%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 122 | 2 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 44.1008 | 0 | 0 | 44.1008 | 0 | 42.0692 | 0.22322 | 188.465 | 42.0692 | 0.22322 | 188.465 | 44.317 | 0.23515 | 188.465 | 0.4722%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 47 | 6920.124 | 97.57% | 2.306% | 0.1195% | 212.5482 | 0 | 0 | 212.5482 | 0 | 202.7565 | 5.2457 | 38.6522 | 202.7565 | 5.2457 | 38.6522 | 213.5901 | 5.526 | 38.6522 | 3.071%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 125 | 1 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 13.7015 | 0 | 0 | 13.7015 | 0 | 13.0703 | 0.11161 | 117.107 | 13.0703 | 0.11161 | 117.107 | 13.7687 | 0.11757 | 117.107 | 0.2304%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 103 | 4 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 42.3816 | 0 | 0 | 42.3816 | 0 | 40.4292 | 0.44644 | 90.5591 | 40.4292 | 0.44644 | 90.5591 | 42.5894 | 0.47029 | 90.5591 | 1.12%
2027 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 1 | 2758.283 | 96.49% | 3.415% | 0.0991% | 7.4211 | 0 | 0 | 7.4211 | 0 | 6.7531 | 0.10647 | 63.4279 | 6.7531 | 0.10647 | 63.4279 | 7.494 | 0.11815 | 63.4279 | 0.269%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 8 | 4222.2471 | 91.41% | 8.486% | 0.103% | 61.3304 | 0 | 0 | 61.3304 | 0 | 55.8098 | 0.85175 | 65.5239 | 55.8098 | 0.85175 | 65.5239 | 61.9331 | 0.9452 | 65.5239 | 1.453%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 54 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1056.4889 | 0 | 0 | 1056.4889 | 0 | 961.3905 | 5.7493 | 167.2189 | 961.3905 | 5.7493 | 167.2189 | 1066.872 | 6.3801 | 167.2189 | 3.005%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 11 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 259.966 | 0 | 0 | 259.966 | 0 | 236.5655 | 1.1712 | 201.9938 | 236.5655 | 1.1712 | 201.9938 | 262.5209 | 1.2996 | 201.9938 | 3.684%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 6 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 194.393 | 0 | 0 | 194.393 | 0 | 176.895 | 0.63881 | 276.9131 | 176.895 | 0.63881 | 276.9131 | 196.3035 | 0.7089 | 276.9131 | 1.033%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 69 | 2 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 42.1086 | 0 | 0 | 42.1086 | 0 | 38.3183 | 0.21294 | 179.9514 | 38.3183 | 0.21294 | 179.9514 | 42.5225 | 0.2363 | 179.9514 | 0.8364%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 12 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 244.4394 | 0 | 0 | 244.4394 | 0 | 222.4365 | 1.2776 | 174.1021 | 222.4365 | 1.2776 | 174.1021 | 246.8417 | 1.4178 | 174.1021 | 2.494%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 4 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 65.5543 | 0 | 0 | 65.5543 | 0 | 59.6535 | 0.42587 | 140.0732 | 59.6535 | 0.42587 | 140.0732 | 66.1985 | 0.4726 | 140.0732 | 1.292%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 66 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 370.9245 | 0 | 0 | 370.9245 | 0 | 337.5362 | 7.0269 | 48.0348 | 337.5362 | 7.0269 | 48.0348 | 374.5699 | 7.7979 | 48.0348 | 3.917%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 32 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 89.756 | 0 | 0 | 89.756 | 0 | 81.6767 | 3.407 | 23.9733 | 81.6767 | 3.407 | 23.9733 | 90.6381 | 3.7808 | 23.9733 | 2.378%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 19 | 585.5086 | 87.68% | 11.85% | 0.4758% | 23.77 | 0 | 0 | 23.77 | 0 | 21.6304 | 2.0229 | 10.6927 | 21.6304 | 2.0229 | 10.6927 | 24.0036 | 2.2448 | 10.6927 | 4.06%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 4 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 79.3393 | 0 | 0 | 79.3393 | 0 | 72.1977 | 0.42587 | 169.5284 | 72.1977 | 0.42587 | 169.5284 | 80.119 | 0.4726 | 169.5284 | 0.3134%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 6 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 103.1144 | 0 | 0 | 103.1144 | 0 | 93.8327 | 0.63881 | 146.8866 | 93.8327 | 0.63881 | 146.8866 | 104.1278 | 0.7089 | 146.8866 | 0.3631%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 3 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 54.5742 | 0 | 0 | 54.5742 | 0 | 49.6618 | 0.31941 | 155.482 | 49.6618 | 0.31941 | 155.482 | 55.1105 | 0.35445 | 155.482 | 0.2044%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 49 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 413.8166 | 0 | 0 | 413.8166 | 0 | 376.5675 | 5.217 | 72.1815 | 376.5675 | 5.217 | 72.1815 | 417.8836 | 5.7893 | 72.1815 | 2.593%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 4 | 1 | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.25034 | 0 | 0 | 0.25034 | 0 | 0.22781 | 0.10647 | 2.1397 | 0.22781 | 0.10647 | 2.1397 | 0.2528 | 0.11815 | 2.1397 | 0.9245%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 44 | 7 | 730.5479 | 99.24% | 0.5863% | 0.172% | 33.4492 | 0 | 0 | 33.4492 | 0 | 30.4384 | 0.74528 | 40.8416 | 30.4384 | 0.74528 | 40.8416 | 33.778 | 0.82705 | 40.8416 | 4.579%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 122 | 2 | 919.3728 | 93.93% | 5.62% | 0.4487% | 4.1055 | 0 | 0 | 4.1055 | 0 | 3.736 | 0.21294 | 17.545 | 3.736 | 0.21294 | 17.545 | 4.1459 | 0.2363 | 17.545 | 0.4466%
2027 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 1 | 509.5021 | 91.97% | 7.519% | 0.512% | 1.6986 | 0 | 0 | 1.6986 | 0 | 1.5457 | 0.10647 | 14.518 | 1.5457 | 0.10647 | 14.518 | 1.7153 | 0.11815 | 14.518 | 0.3334%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 29 | 3 | 140.8367 | 88.02% | 11.68% | 0.2956% | 3.7189 | 0 | 0 | 3.7189 | 0 | 3.3842 | 0.31941 | 10.5952 | 3.3842 | 0.31941 | 10.5952 | 3.7555 | 0.35445 | 10.5952 | 2.641%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 317 | 25 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 134.4029 | 0 | 0 | 134.4029 | 0 | 122.3048 | 2.6617 | 45.9497 | 122.3048 | 2.6617 | 45.9497 | 135.7238 | 2.9537 | 45.9497 | 2.278%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 60 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 269.5167 | 0 | 0 | 269.5167 | 0 | 245.2565 | 6.3881 | 38.3927 | 245.2565 | 6.3881 | 38.3927 | 272.1655 | 7.089 | 38.3927 | 5.4%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 15 | 2514.2831 | 99.84% | 0% | 0.1648% | 65.3839 | 0 | 0 | 65.3839 | 0 | 59.4984 | 1.597 | 37.2558 | 59.4984 | 1.597 | 37.2558 | 66.0265 | 1.7722 | 37.2558 | 2.6%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 65 | 9 | 95.3301 | 98.77% | 0% | 1.235% | 3.7806 | 0 | 0 | 3.7806 | 0 | 3.4403 | 0.95822 | 3.5903 | 3.4403 | 0.95822 | 3.5903 | 3.8178 | 1.0633 | 3.5903 | 3.966%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 93 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 142.5599 | 0 | 0 | 142.5599 | 0 | 129.7276 | 9.9016 | 13.1017 | 129.7276 | 9.9016 | 13.1017 | 143.961 | 10.9879 | 13.1017 | 3.057%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 65 | 1 | 240.2897 | 88.19% | 10.99% | 0.8202% | 0.94542 | 0 | 0 | 0.94542 | 0 | 0.86032 | 0.10647 | 8.0806 | 0.86032 | 0.10647 | 8.0806 | 0.95472 | 0.11815 | 8.0806 | 0.3935%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 1 | 206.5878 | 96.62% | 2.592% | 0.7875% | 1.1813 | 0 | 0 | 1.1813 | 0 | 1.075 | 0.10647 | 10.097 | 1.075 | 0.10647 | 10.097 | 1.193 | 0.11815 | 10.097 | 0.5718%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 37 | 1 | 247.9994 | 97.75% | 1.792% | 0.4608% | 1.9 | 0 | 0 | 1.9 | 0 | 1.729 | 0.10647 | 16.2392 | 1.729 | 0.10647 | 16.2392 | 1.9187 | 0.11815 | 16.2392 | 0.7661%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 9 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 82.6795 | 0 | 0 | 82.6795 | 0 | 75.2372 | 0.95822 | 78.518 | 75.2372 | 0.95822 | 78.518 | 83.492 | 1.0633 | 78.518 | 2.085%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 11 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 321.7201 | 0 | 0 | 321.7201 | 0 | 292.7609 | 1.1712 | 249.9768 | 292.7609 | 1.1712 | 249.9768 | 324.8819 | 1.2996 | 249.9768 | 3.183%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 216 | 27 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 370.7559 | 0 | 0 | 370.7559 | 0 | 337.3828 | 2.8746 | 117.365 | 337.3828 | 2.8746 | 117.365 | 374.3997 | 3.19 | 117.365 | 3.592%
2027 | 1173 | 1173-68 | Tier-1 | Non-HFTD---13 | Non-HFTD---22 | 68 | 3 | 6.4999 | 85.9% | 0% | 14.1% | 0.071438 | 0 | 0 | 0.071438 | 0 | 0.065008 | 0.31941 | 0.20353 | 0.065008 | 0.31941 | 0.20353 | 0.07214 | 0.35445 | 0.20353 | 1.099%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 2 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 23.4221 | 0 | 0 | 23.4221 | 0 | 21.3138 | 0.21294 | 100.0946 | 21.3138 | 0.21294 | 100.0946 | 23.6523 | 0.2363 | 100.0946 | 0.381%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 58 | 8 | 2215.156 | 94.69% | 5.226% | 0.08401% | 83.9013 | 0 | 0 | 83.9013 | 0 | 76.3491 | 0.85175 | 89.6382 | 76.3491 | 0.85175 | 89.6382 | 84.7259 | 0.9452 | 89.6382 | 3.788%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 6 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 62.387 | 0 | 0 | 62.387 | 0 | 56.7713 | 0.63881 | 88.8704 | 56.7713 | 0.63881 | 88.8704 | 63.0001 | 0.7089 | 88.8704 | 0.7174%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 4 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 16.9708 | 0 | 0 | 16.9708 | 0 | 15.4432 | 0.42587 | 36.2625 | 15.4432 | 0.42587 | 36.2625 | 17.1376 | 0.4726 | 36.2625 | 1.089%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 166 | 11 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 67.3677 | 0 | 0 | 67.3677 | 0 | 61.3037 | 1.1712 | 52.3447 | 61.3037 | 1.1712 | 52.3447 | 68.0297 | 1.2996 | 52.3447 | 1.891%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 18 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 81.5416 | 0 | 0 | 81.5416 | 0 | 74.2018 | 1.9164 | 38.7187 | 74.2018 | 1.9164 | 38.7187 | 82.343 | 2.1267 | 38.7187 | 2.733%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 2 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 13.7148 | 0 | 0 | 13.7148 | 0 | 12.4803 | 0.21294 | 58.6101 | 12.4803 | 0.21294 | 58.6101 | 13.8496 | 0.2363 | 58.6101 | 0.9892%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 167 | 3 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 22.1019 | 0 | 0 | 22.1019 | 0 | 20.1124 | 0.31941 | 62.9683 | 20.1124 | 0.31941 | 62.9683 | 22.3191 | 0.35445 | 62.9683 | 0.514%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 1 | 456.1931 | 99.77% | 0% | 0.2285% | 3.8822 | 0 | 0 | 3.8822 | 0 | 3.5327 | 0.10647 | 33.1809 | 3.5327 | 0.10647 | 33.1809 | 3.9203 | 0.11815 | 33.1809 | 0.851%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 3 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 15.9096 | 0 | 0 | 15.9096 | 0 | 14.4776 | 0.31941 | 45.3266 | 14.4776 | 0.31941 | 45.3266 | 16.066 | 0.35445 | 45.3266 | 1.351%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 3 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 22.4808 | 0 | 0 | 22.4808 | 0 | 20.4573 | 0.31941 | 64.048 | 20.4573 | 0.31941 | 64.048 | 22.7018 | 0.35445 | 64.048 | 1.197%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 152 | 1 | 6418.5082 | 93.04% | 6.917% | 0.04745% | 11.393 | 0 | 0 | 11.393 | 0 | 10.3675 | 0.10647 | 97.3762 | 10.3675 | 0.10647 | 97.3762 | 11.505 | 0.11815 | 97.3762 | 0.1775%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 48 | 2 | 6815.4278 | 94.54% | 5.441% | 0.023% | 77.8537 | 0 | 0 | 77.8537 | 0 | 70.8458 | 0.21294 | 332.7079 | 70.8458 | 0.21294 | 332.7079 | 78.6188 | 0.2363 | 332.7079 | 1.142%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 267 | 11 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 139.335 | 0 | 0 | 139.335 | 0 | 126.7929 | 1.1712 | 108.2634 | 126.7929 | 1.1712 | 108.2634 | 140.7044 | 1.2996 | 108.2634 | 1.186%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 146 | 7 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 50.2907 | 0 | 0 | 50.2907 | 0 | 45.7638 | 0.74528 | 61.405 | 45.7638 | 0.74528 | 61.405 | 50.7849 | 0.82705 | 61.405 | 1.365%
2027 | 139 | 139-245AE | Tier-1 | Non-HFTD---14 | Non-HFTD---18 | 165 | 11 | 5.6722 | 51.84% | 0% | 48.16% | 0.056845 | 0 | 0 | 0.056845 | 0 | 0.051728 | 1.1712 | 0.044168 | 0.051728 | 1.1712 | 0.044168 | 0.057403 | 1.2996 | 0.044168 | 1.002%
2027 | 140 | 140-481R | Tier-1 | Non-HFTD---6 | Non-HFTD---12 | 247 | 18 | 76.5519 | 22.22% | 72.37% | 5.415% | 0.35947 | 0 | 0 | 0.35947 | 0 | 0.32712 | 1.9164 | 0.17069 | 0.32712 | 1.9164 | 0.17069 | 0.36301 | 2.1267 | 0.17069 | 0.4696%
2027 | 140 | 140-496 | Tier-1 | Non-HFTD---5 | Non-HFTD---9 | 98 | 13 | 76.0759 | 10.21% | 86.85% | 2.935% | 0.29885 | 0 | 0 | 0.29885 | 0 | 0.27195 | 1.3841 | 0.19648 | 0.27195 | 1.3841 | 0.19648 | 0.30179 | 1.5359 | 0.19648 | 0.3928%
2027 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | Non-HFTD---15 | 58 | 11 | 14.0801 | 87.11% | 0% | 12.89% | 0.67458 | 0 | 0 | 0.67458 | 0 | 0.61386 | 1.1712 | 0.52415 | 0.61386 | 1.1712 | 0.52415 | 0.68121 | 1.2996 | 0.52415 | 4.791%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 22 | 1 | 427.4478 | 90.46% | 9.431% | 0.1062% | 5.0972 | 0 | 0 | 5.0972 | 0 | 4.6384 | 0.10647 | 43.5655 | 4.6384 | 0.10647 | 43.5655 | 5.1473 | 0.11815 | 43.5655 | 1.192%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 36 | 4 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 65.2036 | 0 | 0 | 65.2036 | 0 | 59.3343 | 0.42587 | 139.3238 | 59.3343 | 0.42587 | 139.3238 | 65.8444 | 0.4726 | 139.3238 | 2.756%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 80 | 6 | 4370.0987 | 98.67% | 1.293% | 0.03403% | 93.7887 | 0 | 0 | 93.7887 | 0 | 85.3464 | 0.63881 | 133.6021 | 85.3464 | 0.63881 | 133.6021 | 94.7104 | 0.7089 | 133.6021 | 2.146%
2027 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 2 | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.21294 | 0 | 0 | 0.21294 | 0 | 0 | 0.2363 | 0 | 0%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | Tier-3---1 | 188 | 2 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 48.8751 | 0 | 0 | 48.8751 | 0 | 44.4757 | 0.21294 | 208.868 | 44.4757 | 0.21294 | 208.868 | 49.3555 | 0.2363 | 208.868 | 0.3057%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 1 | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.0693 | 0 | 0 | 2.0693 | 0 | 1.883 | 0.10647 | 17.686 | 1.883 | 0.10647 | 17.686 | 2.0896 | 0.11815 | 17.686 | 1.235%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 127 | 6 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 110.9545 | 0 | 0 | 110.9545 | 0 | 100.9671 | 0.63881 | 158.0548 | 100.9671 | 0.63881 | 158.0548 | 112.0449 | 0.7089 | 158.0548 | 1.36%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 46 | 37077.302 | 99.36% | 0.615% | 0.02874% | 1114.3469 | 0 | 0 | 1114.3469 | 0 | 1014.0405 | 4.8975 | 207.0507 | 1014.0405 | 4.8975 | 207.0507 | 1125.2986 | 5.4349 | 207.0507 | 3.005%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 3 | 8.268 | 89.5% | 6.947% | 3.548% | 0.71536 | 0 | 0 | 0.71536 | 0 | 0.65096 | 0.31941 | 2.0381 | 0.65096 | 0.31941 | 2.0381 | 0.72239 | 0.35445 | 2.0381 | 8.652%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 87 | 3 | 418.5676 | 87.71% | 11.66% | 0.6303% | 3.6711 | 0 | 0 | 3.6711 | 0 | 3.3406 | 0.31941 | 10.4589 | 3.3406 | 0.31941 | 10.4589 | 3.7072 | 0.35445 | 10.4589 | 0.8771%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 669 | 46 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 101.5328 | 0 | 0 | 101.5328 | 0 | 92.3935 | 4.8975 | 18.8653 | 92.3935 | 4.8975 | 18.8653 | 102.5306 | 5.4349 | 18.8653 | 1.844%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 60 | 2 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 29.2341 | 0 | 0 | 29.2341 | 0 | 26.6026 | 0.21294 | 124.9319 | 26.6026 | 0.21294 | 124.9319 | 29.5214 | 0.2363 | 124.9319 | 0.9577%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 3 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 15.6715 | 0 | 0 | 15.6715 | 0 | 14.2608 | 0.31941 | 44.6481 | 14.2608 | 0.31941 | 44.6481 | 15.8255 | 0.35445 | 44.6481 | 0.4043%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 250 | 4 | 3160.5079 | 95.27% | 4.501% | 0.231% | 13.9709 | 0 | 0 | 13.9709 | 0 | 12.7133 | 0.42587 | 29.8523 | 12.7133 | 0.42587 | 29.8523 | 14.1082 | 0.4726 | 29.8523 | 0.442%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 554 | 15 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 13.1969 | 0 | 0 | 13.1969 | 0 | 12.009 | 1.597 | 7.5196 | 12.009 | 1.597 | 7.5196 | 13.3266 | 1.7722 | 7.5196 | 0.6403%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 173 | 4 | 1867.403 | 95.01% | 4.712% | 0.2778% | 11.8966 | 0 | 0 | 11.8966 | 0 | 10.8257 | 0.42587 | 25.42 | 10.8257 | 0.42587 | 25.42 | 12.0135 | 0.4726 | 25.42 | 0.6371%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 675 | 32 | 18749.5963 | 97% | 2.901% | 0.09453% | 250.0519 | 0 | 0 | 250.0519 | 0 | 227.5438 | 3.407 | 66.7874 | 227.5438 | 3.407 | 66.7874 | 252.5094 | 3.7808 | 66.7874 | 1.334%
2027 | 168 | 168-702F | Tier-1 | Non-HFTD---5 | Non-HFTD---12 | 160 | 9 | 86.0496 | 96.13% | 0% | 3.875% | 1.3493 | 0 | 0 | 1.3493 | 0 | 1.2278 | 0.95822 | 1.2814 | 1.2278 | 0.95822 | 1.2814 | 1.3626 | 1.0633 | 1.2814 | 1.568%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 5 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 56.2099 | 0 | 0 | 56.2099 | 0 | 51.1503 | 0.53234 | 96.0854 | 51.1503 | 0.53234 | 96.0854 | 56.7624 | 0.59075 | 96.0854 | 1.395%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 239 | 10 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 51.8942 | 0 | 0 | 51.8942 | 0 | 47.223 | 1.0647 | 44.354 | 47.223 | 1.0647 | 44.354 | 52.4042 | 1.1815 | 44.354 | 1.183%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 6 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 32.2554 | 0 | 0 | 32.2554 | 0 | 29.352 | 0.63881 | 45.9478 | 29.352 | 0.63881 | 45.9478 | 32.5724 | 0.7089 | 45.9478 | 0.5618%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 6 | 836.2457 | 79.76% | 20.09% | 0.1547% | 22.3181 | 0 | 0 | 22.3181 | 0 | 20.3091 | 0.63881 | 31.7921 | 20.3091 | 0.63881 | 31.7921 | 22.5374 | 0.7089 | 31.7921 | 2.669%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 236 | 3 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 41.957 | 0 | 0 | 41.957 | 0 | 38.1803 | 0.31941 | 119.5357 | 38.1803 | 0.31941 | 119.5357 | 42.3694 | 0.35445 | 119.5357 | 0.3641%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 131 | 1 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 9.0876 | 0 | 0 | 9.0876 | 0 | 8.2696 | 0.10647 | 77.6716 | 8.2696 | 0.10647 | 77.6716 | 9.1769 | 0.11815 | 77.6716 | 0.2172%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 3 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 27.2698 | 0 | 0 | 27.2698 | 0 | 24.8152 | 0.31941 | 77.6918 | 24.8152 | 0.31941 | 77.6918 | 27.5378 | 0.35445 | 77.6918 | 0.2708%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 4 | 404.4817 | 67.64% | 32.12% | 0.2398% | 6.3471 | 0 | 0 | 6.3471 | 0 | 5.7758 | 0.42587 | 13.5623 | 5.7758 | 0.42587 | 13.5623 | 6.4095 | 0.4726 | 13.5623 | 1.569%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 214 | 4 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 26.1313 | 0 | 0 | 26.1313 | 0 | 23.7791 | 0.42587 | 55.836 | 23.7791 | 0.42587 | 55.836 | 26.3881 | 0.4726 | 55.836 | 0.5296%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 345 | 1 | 13172.958 | 96.8% | 3.124% | 0.0728% | 10.7189 | 0 | 0 | 10.7189 | 0 | 9.7541 | 0.10647 | 91.6149 | 9.7541 | 0.10647 | 91.6149 | 10.8243 | 0.11815 | 91.6149 | 0.08137%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 176 | 3 | 2963.4059 | 78.23% | 21.66% | 0.1106% | 11.4595 | 0 | 0 | 11.4595 | 0 | 10.428 | 0.31941 | 32.6482 | 10.428 | 0.31941 | 32.6482 | 11.5721 | 0.35445 | 32.6482 | 0.3867%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 2 | 47.6106 | 91.21% | 0% | 8.789% | 0.12594 | 0 | 0 | 0.12594 | 0 | 0.1146 | 0.21294 | 0.53819 | 0.1146 | 0.21294 | 0.53819 | 0.12717 | 0.2363 | 0.53819 | 0.2645%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 9 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 100.784 | 0 | 0 | 100.784 | 0 | 91.712 | 0.95822 | 95.7113 | 91.712 | 0.95822 | 95.7113 | 101.7745 | 1.0633 | 95.7113 | 0.8457%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 9 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 194.163 | 0 | 0 | 194.163 | 0 | 176.6857 | 0.95822 | 184.3903 | 176.6857 | 0.95822 | 184.3903 | 196.0712 | 1.0633 | 184.3903 | 10.01%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 9 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 105.3225 | 0 | 0 | 105.3225 | 0 | 95.842 | 0.95822 | 100.0214 | 95.842 | 0.95822 | 100.0214 | 106.3576 | 1.0633 | 100.0214 | 2.49%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 42 | 2 | 316.4778 | 66.23% | 33.5% | 0.2671% | 2.8945 | 0 | 0 | 2.8945 | 0 | 2.634 | 0.21294 | 12.3698 | 2.634 | 0.21294 | 12.3698 | 2.923 | 0.2363 | 12.3698 | 0.9146%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 114 | 3 | 471.2015 | 74.37% | 25.17% | 0.4626% | 2.6743 | 0 | 0 | 2.6743 | 0 | 2.4336 | 0.31941 | 7.6192 | 2.4336 | 0.31941 | 7.6192 | 2.7006 | 0.35445 | 7.6192 | 0.5676%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 19 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 33.5852 | 0 | 0 | 33.5852 | 0 | 30.5621 | 2.0229 | 15.1081 | 30.5621 | 2.0229 | 15.1081 | 33.9153 | 2.2448 | 15.1081 | 1.948%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 4 | 973.0999 | 95.53% | 4.02% | 0.4464% | 5.7361 | 0 | 0 | 5.7361 | 0 | 5.2197 | 0.42587 | 12.2565 | 5.2197 | 0.42587 | 12.2565 | 5.7924 | 0.4726 | 12.2565 | 0.5895%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 24 | 490.4615 | 96.36% | 1.259% | 2.378% | 9.79 | 0 | 0 | 9.79 | 0 | 8.9088 | 2.5552 | 3.4865 | 8.9088 | 2.5552 | 3.4865 | 9.8862 | 2.8356 | 3.4865 | 1.996%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 4 | 1279.0443 | 99.78% | 0% | 0.2159% | 11.2158 | 0 | 0 | 11.2158 | 0 | 10.2062 | 0.42587 | 23.9654 | 10.2062 | 0.42587 | 23.9654 | 11.3261 | 0.4726 | 23.9654 | 0.8769%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 12 | 2976.5734 | 99.75% | 0% | 0.2502% | 25.0183 | 0 | 0 | 25.0183 | 0 | 22.7663 | 1.2776 | 17.8193 | 22.7663 | 1.2776 | 17.8193 | 25.2642 | 1.4178 | 17.8193 | 0.8405%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 76 | 8462.8018 | 99.74% | 0% | 0.2593% | 174.0286 | 0 | 0 | 174.0286 | 0 | 158.3637 | 8.0916 | 19.5714 | 158.3637 | 8.0916 | 19.5714 | 175.739 | 8.9794 | 19.5714 | 2.056%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 111 | 9 | 498.1496 | 90.1% | 9.186% | 0.7154% | 10.5535 | 0 | 0 | 10.5535 | 0 | 9.6035 | 0.95822 | 10.0223 | 9.6035 | 0.95822 | 10.0223 | 10.6572 | 1.0633 | 10.0223 | 2.119%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 221 | 8 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 9.341 | 0 | 0 | 9.341 | 0 | 8.5002 | 0.85175 | 9.9797 | 8.5002 | 0.85175 | 9.9797 | 9.4328 | 0.9452 | 9.9797 | 0.9%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 77 | 15 | 170.5929 | 70.47% | 28.1% | 1.432% | 6.7917 | 0 | 0 | 6.7917 | 0 | 6.1803 | 1.597 | 3.8699 | 6.1803 | 1.597 | 3.8699 | 6.8584 | 1.7722 | 3.8699 | 3.981%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 95 | 17 | 317.7725 | 50.82% | 48.53% | 0.6462% | 8.3813 | 0 | 0 | 8.3813 | 0 | 7.6269 | 1.81 | 4.2138 | 7.6269 | 1.81 | 4.2138 | 8.4637 | 2.0085 | 4.2138 | 2.638%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 293 | 7 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 7.4376 | 0 | 0 | 7.4376 | 0 | 6.7682 | 0.74528 | 9.0814 | 6.7682 | 0.74528 | 9.0814 | 7.5107 | 0.82705 | 9.0814 | 0.62%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 20 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 21.0566 | 0 | 0 | 21.0566 | 0 | 19.1612 | 2.1294 | 8.9985 | 19.1612 | 2.1294 | 8.9985 | 21.2635 | 2.363 | 8.9985 | 1.164%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 279 | 15 | 1890.633 | 91.06% | 8.49% | 0.4466% | 26.8433 | 0 | 0 | 26.8433 | 0 | 24.4271 | 1.597 | 15.2954 | 24.4271 | 1.597 | 15.2954 | 27.1072 | 1.7722 | 15.2954 | 1.42%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 287 | 5 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 8.3837 | 0 | 0 | 8.3837 | 0 | 7.6291 | 0.53234 | 14.3311 | 7.6291 | 0.53234 | 14.3311 | 8.4661 | 0.59075 | 14.3311 | 0.4821%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 219 | 2 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 3.9499 | 0 | 0 | 3.9499 | 0 | 3.5944 | 0.21294 | 16.8799 | 3.5944 | 0.21294 | 16.8799 | 3.9887 | 0.2363 | 16.8799 | 0.2515%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 79 | 2 | 609.7797 | 99.07% | 0.4924% | 0.4406% | 4.4351 | 0 | 0 | 4.4351 | 0 | 4.0359 | 0.21294 | 18.9534 | 4.0359 | 0.21294 | 18.9534 | 4.4787 | 0.2363 | 18.9534 | 0.7273%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 218 | 7 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 45.1287 | 0 | 0 | 45.1287 | 0 | 41.0665 | 0.74528 | 55.1022 | 41.0665 | 0.74528 | 55.1022 | 45.5722 | 0.82705 | 55.1022 | 0.9233%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 273 | 7 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 9.2176 | 0 | 0 | 9.2176 | 0 | 8.3879 | 0.74528 | 11.2547 | 8.3879 | 0.74528 | 11.2547 | 9.3082 | 0.82705 | 11.2547 | 0.7281%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 201 | 11 | 998.7912 | 96.62% | 2.787% | 0.5903% | 15.316 | 0 | 0 | 15.316 | 0 | 13.9374 | 1.1712 | 11.9006 | 13.9374 | 1.1712 | 11.9006 | 15.4666 | 1.2996 | 11.9006 | 1.533%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 71 | 16 | 261.4279 | 97.06% | 2.12% | 0.8249% | 16.5818 | 0 | 0 | 16.5818 | 0 | 15.0892 | 1.7035 | 8.8578 | 15.0892 | 1.7035 | 8.8578 | 16.7447 | 1.8904 | 8.8578 | 6.343%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 201 | 5 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 10.4027 | 0 | 0 | 10.4027 | 0 | 9.4663 | 0.53234 | 17.7824 | 9.4663 | 0.53234 | 17.7824 | 10.5049 | 0.59075 | 17.7824 | 0.7017%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 18 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 46.4363 | 0 | 0 | 46.4363 | 0 | 42.2564 | 1.9164 | 22.0495 | 42.2564 | 1.9164 | 22.0495 | 46.8927 | 2.1267 | 22.0495 | 1.683%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 115 | 8 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 20.353 | 0 | 0 | 20.353 | 0 | 18.521 | 0.85175 | 21.7447 | 18.521 | 0.85175 | 21.7447 | 20.5531 | 0.9452 | 21.7447 | 1.959%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 31 | 1 | 104.9439 | 97.78% | 1.295% | 0.9224% | 0.95996 | 0 | 0 | 0.95996 | 0 | 0.87355 | 0.10647 | 8.2048 | 0.87355 | 0.10647 | 8.2048 | 0.9694 | 0.11815 | 8.2048 | 0.9147%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 155 | 13 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 51.9488 | 0 | 0 | 51.9488 | 0 | 47.2727 | 1.3841 | 34.1544 | 47.2727 | 1.3841 | 34.1544 | 52.4593 | 1.5359 | 34.1544 | 2.401%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 147 | 12 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 34.0655 | 0 | 0 | 34.0655 | 0 | 30.9991 | 1.2776 | 24.2631 | 30.9991 | 1.2776 | 24.2631 | 34.4003 | 1.4178 | 24.2631 | 2.316%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 10 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 169.0168 | 0 | 0 | 169.0168 | 0 | 153.803 | 1.0647 | 144.4588 | 153.803 | 1.0647 | 144.4588 | 170.6779 | 1.1815 | 144.4588 | 0.6431%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 20 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 134.8729 | 0 | 0 | 134.8729 | 0 | 122.7325 | 2.1294 | 57.638 | 122.7325 | 2.1294 | 57.638 | 136.1984 | 2.363 | 57.638 | 2.023%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 157 | 15 | 484.0355 | 97.4% | 1.48% | 1.12% | 13.0625 | 0 | 0 | 13.0625 | 0 | 11.8867 | 1.597 | 7.443 | 11.8867 | 1.597 | 7.443 | 13.1909 | 1.7722 | 7.443 | 2.699%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 94 | 1 | 400.1895 | 97.86% | 1.359% | 0.7809% | 1.2082 | 0 | 0 | 1.2082 | 0 | 1.0994 | 0.10647 | 10.3265 | 1.0994 | 0.10647 | 10.3265 | 1.2201 | 0.11815 | 10.3265 | 0.3019%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 70 | 1 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 2.0993 | 0 | 0 | 2.0993 | 0 | 1.9104 | 0.10647 | 17.9429 | 1.9104 | 0.10647 | 17.9429 | 2.12 | 0.11815 | 17.9429 | 0.409%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 3 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 10.9415 | 0 | 0 | 10.9415 | 0 | 9.9566 | 0.31941 | 31.1725 | 9.9566 | 0.31941 | 31.1725 | 11.0491 | 0.35445 | 31.1725 | 0.4955%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 11 | 1721.769 | 85.69% | 14.07% | 0.2459% | 24.0119 | 0 | 0 | 24.0119 | 0 | 21.8505 | 1.1712 | 18.6573 | 21.8505 | 1.1712 | 18.6573 | 24.2479 | 1.2996 | 18.6573 | 1.395%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 264 | 2 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 48.7399 | 0 | 0 | 48.7399 | 0 | 44.3527 | 0.21294 | 208.2904 | 44.3527 | 0.21294 | 208.2904 | 49.219 | 0.2363 | 208.2904 | 0.218%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 19 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 268.5172 | 0 | 0 | 268.5172 | 0 | 244.347 | 2.0229 | 120.7905 | 244.347 | 2.0229 | 120.7905 | 271.1562 | 2.2448 | 120.7905 | 2.114%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 11 | 19489.7064 | 99% | 0.9737% | 0.02962% | 253.2856 | 0 | 0 | 253.2856 | 0 | 230.4864 | 1.1712 | 196.8031 | 230.4864 | 1.1712 | 196.8031 | 255.7749 | 1.2996 | 196.8031 | 1.3%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 7 | 1412.4296 | 98.09% | 1.785% | 0.1216% | 53.0671 | 0 | 0 | 53.0671 | 0 | 48.2903 | 0.74528 | 64.795 | 48.2903 | 0.74528 | 64.795 | 53.5886 | 0.82705 | 64.795 | 3.757%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 3 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 37.1196 | 0 | 0 | 37.1196 | 0 | 33.7783 | 0.31941 | 105.7538 | 33.7783 | 0.31941 | 105.7538 | 37.4844 | 0.35445 | 105.7538 | 0.683%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 8 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 120.561 | 0 | 0 | 120.561 | 0 | 109.7089 | 0.85175 | 128.8045 | 109.7089 | 0.85175 | 128.8045 | 121.7459 | 0.9452 | 128.8045 | 0.8586%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 24 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 27.4222 | 0 | 0 | 27.4222 | 0 | 24.9539 | 2.5552 | 9.7658 | 24.9539 | 2.5552 | 9.7658 | 27.6917 | 2.8356 | 9.7658 | 1.362%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 17 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 34.3406 | 0 | 0 | 34.3406 | 0 | 31.2495 | 1.81 | 17.2652 | 31.2495 | 1.81 | 17.2652 | 34.6781 | 2.0085 | 17.2652 | 1.259%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 7 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 67.1124 | 0 | 0 | 67.1124 | 0 | 61.0713 | 0.74528 | 81.9443 | 61.0713 | 0.74528 | 81.9443 | 67.7719 | 0.82705 | 81.9443 | 0.628%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 20 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 68.5283 | 0 | 0 | 68.5283 | 0 | 62.3598 | 2.1294 | 29.2856 | 62.3598 | 2.1294 | 29.2856 | 69.2017 | 2.363 | 29.2856 | 1.874%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 12 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 17.7725 | 0 | 0 | 17.7725 | 0 | 16.1727 | 1.2776 | 12.6585 | 16.1727 | 1.2776 | 12.6585 | 17.9471 | 1.4178 | 12.6585 | 1.235%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 132 | 2 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 9.307 | 0 | 0 | 9.307 | 0 | 8.4692 | 0.21294 | 39.7734 | 8.4692 | 0.21294 | 39.7734 | 9.3984 | 0.2363 | 39.7734 | 0.4233%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 9 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 12.9175 | 0 | 0 | 12.9175 | 0 | 11.7547 | 0.95822 | 12.2673 | 11.7547 | 0.95822 | 12.2673 | 13.0444 | 1.0633 | 12.2673 | 0.6707%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 614 | 105 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.9189 | 0 | 0 | 158.9189 | 0 | 144.614 | 11.1792 | 12.936 | 144.614 | 11.1792 | 12.936 | 160.4807 | 12.4057 | 12.936 | 4.432%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 97 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 11.0247 | 0 | 0 | 11.0247 | 0 | 10.0323 | 0.10647 | 94.2282 | 10.0323 | 0.10647 | 94.2282 | 11.1331 | 0.11815 | 94.2282 | 0.2987%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 307 | 4 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 11.3881 | 0 | 0 | 11.3881 | 0 | 10.3631 | 0.42587 | 24.3337 | 10.3631 | 0.42587 | 24.3337 | 11.5001 | 0.4726 | 24.3337 | 0.3482%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 293 | 3 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 7.8076 | 0 | 0 | 7.8076 | 0 | 7.1048 | 0.31941 | 22.2438 | 7.1048 | 0.31941 | 22.2438 | 7.8843 | 0.35445 | 22.2438 | 0.2854%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 244 | 12 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 54.4499 | 0 | 0 | 54.4499 | 0 | 49.5486 | 1.2776 | 38.782 | 49.5486 | 1.2776 | 38.782 | 54.985 | 1.4178 | 38.782 | 1.384%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 18 | 1 | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.7116 | 0 | 0 | 1.7116 | 0 | 1.5575 | 0.10647 | 14.629 | 1.5575 | 0.10647 | 14.629 | 1.7284 | 0.11815 | 14.629 | 0.5381%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 99 | 13 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 77.8884 | 0 | 0 | 77.8884 | 0 | 70.8774 | 1.3841 | 51.2087 | 70.8774 | 1.3841 | 51.2087 | 78.6539 | 1.5359 | 51.2087 | 3.789%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 67 | 1 | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 19.2921 | 0 | 0 | 19.2921 | 0 | 17.5555 | 0.10647 | 164.8896 | 17.5555 | 0.10647 | 164.8896 | 19.4817 | 0.11815 | 164.8896 | 0.4304%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 106 | 3 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 18.4777 | 0 | 0 | 18.4777 | 0 | 16.8145 | 0.31941 | 52.643 | 16.8145 | 0.31941 | 52.643 | 18.6593 | 0.35445 | 52.643 | 0.795%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 123 | 19 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 429.0966 | 0 | 0 | 429.0966 | 0 | 390.4721 | 2.0229 | 193.0259 | 390.4721 | 2.0229 | 193.0259 | 433.3137 | 2.2448 | 193.0259 | 4.461%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 367 | 8 | 7406.689 | 96.62% | 3.25% | 0.1263% | 45.2407 | 0 | 0 | 45.2407 | 0 | 41.1684 | 0.85175 | 48.3341 | 41.1684 | 0.85175 | 48.3341 | 45.6853 | 0.9452 | 48.3341 | 0.6108%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 451 | 3 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 151.6272 | 0 | 0 | 151.6272 | 0 | 137.9787 | 0.31941 | 431.9865 | 137.9787 | 0.31941 | 431.9865 | 153.1174 | 0.35445 | 431.9865 | 0.1915%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 287 | 3 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 136.2275 | 0 | 0 | 136.2275 | 0 | 123.9652 | 0.31941 | 388.1125 | 123.9652 | 0.31941 | 388.1125 | 137.5663 | 0.35445 | 388.1125 | 0.302%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 43 | 2 | 288.7705 | 86.56% | 13.18% | 0.2657% | 3.3714 | 0 | 0 | 3.3714 | 0 | 3.0679 | 0.21294 | 14.4077 | 3.0679 | 0.21294 | 14.4077 | 3.4045 | 0.2363 | 14.4077 | 1.168%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 407 | 9 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 45.7458 | 0 | 0 | 45.7458 | 0 | 41.628 | 0.95822 | 43.4433 | 41.628 | 0.95822 | 43.4433 | 46.1953 | 1.0633 | 43.4433 | 0.6159%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 910 | 28 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 144.715 | 0 | 0 | 144.715 | 0 | 131.6887 | 2.9811 | 44.1743 | 131.6887 | 2.9811 | 44.1743 | 146.1372 | 3.3082 | 44.1743 | 0.8628%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 2 | 17.3686 | 98.33% | 0% | 1.666% | 1.2382 | 0 | 0 | 1.2382 | 0 | 1.1268 | 0.21294 | 5.2916 | 1.1268 | 0.21294 | 5.2916 | 1.2504 | 0.2363 | 5.2916 | 7.129%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 45 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 92.1806 | 0 | 0 | 92.1806 | 0 | 83.8831 | 4.7911 | 17.5082 | 83.8831 | 4.7911 | 17.5082 | 93.0865 | 5.3167 | 17.5082 | 4.608%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 328 | 16 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 88.8064 | 0 | 0 | 88.8064 | 0 | 80.8126 | 1.7035 | 47.4393 | 80.8126 | 1.7035 | 47.4393 | 89.6792 | 1.8904 | 47.4393 | 1.39%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 245 | 32 | 2072.8837 | 91.06% | 8.635% | 0.3% | 71.5001 | 0 | 0 | 71.5001 | 0 | 65.0641 | 3.407 | 19.0973 | 65.0641 | 3.407 | 19.0973 | 72.2028 | 3.7808 | 19.0973 | 3.449%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 71 | 3 | 536.3838 | 78.97% | 20.71% | 0.32% | 5.1903 | 0 | 0 | 5.1903 | 0 | 4.7231 | 0.31941 | 14.787 | 4.7231 | 0.31941 | 14.787 | 5.2413 | 0.35445 | 14.787 | 0.9676%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 52 | 3 | 788.7224 | 98.19% | 1.606% | 0.2041% | 12.957 | 0 | 0 | 12.957 | 0 | 11.7907 | 0.31941 | 36.9146 | 11.7907 | 0.31941 | 36.9146 | 13.0844 | 0.35445 | 36.9146 | 1.643%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 16 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 66.7051 | 0 | 0 | 66.7051 | 0 | 60.7007 | 1.7035 | 35.633 | 60.7007 | 1.7035 | 35.633 | 67.3606 | 1.8904 | 35.633 | 1.92%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 41 | 5 | 195.7251 | 81.71% | 17.81% | 0.4804% | 5.6562 | 0 | 0 | 5.6562 | 0 | 5.1471 | 0.53234 | 9.6688 | 5.1471 | 0.53234 | 9.6688 | 5.7118 | 0.59075 | 9.6688 | 2.89%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 14 | 2730.9177 | 98.3% | 1.373% | 0.325% | 30.5301 | 0 | 0 | 30.5301 | 0 | 27.782 | 1.4906 | 18.6386 | 27.782 | 1.4906 | 18.6386 | 30.8301 | 1.6541 | 18.6386 | 1.118%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 131 | 5142.095 | 98.68% | 0.901% | 0.4182% | 223.6325 | 0 | 0 | 223.6325 | 0 | 203.5025 | 13.9474 | 14.5908 | 203.5025 | 13.9474 | 14.5908 | 225.8303 | 15.4776 | 14.5908 | 4.349%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 10 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 21.1205 | 0 | 0 | 21.1205 | 0 | 19.2193 | 1.0647 | 18.0517 | 19.2193 | 1.0647 | 18.0517 | 21.328 | 1.1815 | 18.0517 | 0.6957%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 33 | 718.991 | 97.57% | 1.357% | 1.072% | 24.5918 | 0 | 0 | 24.5918 | 0 | 22.3782 | 3.5135 | 6.3693 | 22.3782 | 3.5135 | 6.3693 | 24.8335 | 3.8989 | 6.3693 | 3.42%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 20 | 447.7794 | 94.96% | 4.349% | 0.694% | 24.9107 | 0 | 0 | 24.9107 | 0 | 22.6684 | 2.1294 | 10.6456 | 22.6684 | 2.1294 | 10.6456 | 25.1555 | 2.363 | 10.6456 | 5.563%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 38 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 53.8043 | 0 | 0 | 53.8043 | 0 | 48.9611 | 4.0458 | 12.1017 | 48.9611 | 4.0458 | 12.1017 | 54.333 | 4.4897 | 12.1017 | 2.298%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 31 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 132.2267 | 0 | 0 | 132.2267 | 0 | 120.3245 | 3.3005 | 36.4562 | 120.3245 | 3.3005 | 36.4562 | 133.5262 | 3.6626 | 36.4562 | 2.677%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 15 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 69.9872 | 0 | 0 | 69.9872 | 0 | 63.6874 | 1.597 | 39.8787 | 63.6874 | 1.597 | 39.8787 | 70.675 | 1.7722 | 39.8787 | 1.6%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 26 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 330.7349 | 0 | 0 | 330.7349 | 0 | 300.9643 | 2.7682 | 108.7229 | 300.9643 | 2.7682 | 108.7229 | 333.9854 | 3.0719 | 108.7229 | 1.397%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 252 | 18 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 198.7716 | 0 | 0 | 198.7716 | 0 | 180.8795 | 1.9164 | 94.3835 | 180.8795 | 1.9164 | 94.3835 | 200.7251 | 2.1267 | 94.3835 | 2.045%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 137 | 1 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 5.8133 | 0 | 0 | 5.8133 | 0 | 5.29 | 0.10647 | 49.6861 | 5.29 | 0.10647 | 49.6861 | 5.8704 | 0.11815 | 49.6861 | 0.2059%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 498 | 30 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 364.6956 | 0 | 0 | 364.6956 | 0 | 331.8681 | 3.1941 | 103.9019 | 331.8681 | 3.1941 | 103.9019 | 368.2798 | 3.5445 | 103.9019 | 1.718%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 192 | 4 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 40.9536 | 0 | 0 | 40.9536 | 0 | 37.2672 | 0.42587 | 87.5076 | 37.2672 | 0.42587 | 87.5076 | 41.356 | 0.4726 | 87.5076 | 0.5911%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 126 | 3 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 24.9414 | 0 | 0 | 24.9414 | 0 | 22.6963 | 0.31941 | 71.058 | 22.6963 | 0.31941 | 71.058 | 25.1865 | 0.35445 | 71.058 | 0.6863%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 223 | 8 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 291.9667 | 0 | 0 | 291.9667 | 0 | 265.6857 | 0.85175 | 311.9302 | 265.6857 | 0.85175 | 311.9302 | 294.8361 | 0.9452 | 311.9302 | 1.034%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 35 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 507.1343 | 0 | 0 | 507.1343 | 0 | 461.4853 | 3.7264 | 123.8423 | 461.4853 | 3.7264 | 123.8423 | 512.1183 | 4.1352 | 123.8423 | 1.873%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 2 | 663.2151 | 70.89% | 28.72% | 0.399% | 2.413 | 0 | 0 | 2.413 | 0 | 2.1958 | 0.21294 | 10.312 | 2.1958 | 0.21294 | 10.312 | 2.4367 | 0.2363 | 10.312 | 0.3638%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 59 | 1 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 12.2907 | 0 | 0 | 12.2907 | 0 | 11.1844 | 0.10647 | 105.0491 | 11.1844 | 0.10647 | 105.0491 | 12.4115 | 0.11815 | 105.0491 | 0.4858%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 499 | 11 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 195.7454 | 0 | 0 | 195.7454 | 0 | 178.1256 | 1.1712 | 152.0943 | 178.1256 | 1.1712 | 152.0943 | 197.6691 | 1.2996 | 152.0943 | 0.6336%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 651 | 10 | 65515.492 | 98.93% | 1.038% | 0.03019% | 288.7333 | 0 | 0 | 288.7333 | 0 | 262.7434 | 1.0647 | 246.7806 | 262.7434 | 1.0647 | 246.7806 | 291.571 | 1.1815 | 246.7806 | 0.4407%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 41 | 860.3234 | 98.08% | 1.495% | 0.4234% | 78.9997 | 0 | 0 | 78.9997 | 0 | 71.8887 | 4.3652 | 16.4686 | 71.8887 | 4.3652 | 16.4686 | 79.7761 | 4.8441 | 16.4686 | 9.183%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 1 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 8.247 | 0 | 0 | 8.247 | 0 | 7.5047 | 0.10647 | 70.4875 | 7.5047 | 0.10647 | 70.4875 | 8.3281 | 0.11815 | 70.4875 | 0.5203%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 134 | 3 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 6.9919 | 0 | 0 | 6.9919 | 0 | 6.3626 | 0.31941 | 19.9201 | 6.3626 | 0.31941 | 19.9201 | 7.0607 | 0.35445 | 19.9201 | 0.6263%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 31 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 181.519 | 0 | 0 | 181.519 | 0 | 165.1798 | 3.3005 | 50.0466 | 165.1798 | 3.3005 | 50.0466 | 183.303 | 3.6626 | 50.0466 | 2.896%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 4 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 7.6603 | 0 | 0 | 7.6603 | 0 | 6.9708 | 0.42587 | 16.3682 | 6.9708 | 0.42587 | 16.3682 | 7.7356 | 0.4726 | 16.3682 | 0.744%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 52 | 3 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 6.2196 | 0 | 0 | 6.2196 | 0 | 5.6597 | 0.31941 | 17.7196 | 5.6597 | 0.31941 | 17.7196 | 6.2807 | 0.35445 | 17.7196 | 1.652%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 165 | 6 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 12.2585 | 0 | 0 | 12.2585 | 0 | 11.1551 | 0.63881 | 17.4623 | 11.1551 | 0.63881 | 17.4623 | 12.379 | 0.7089 | 17.4623 | 1.038%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 71 | 2 | 791.3356 | 98.7% | 1.112% | 0.1837% | 6.3807 | 0 | 0 | 6.3807 | 0 | 5.8063 | 0.21294 | 27.2679 | 5.8063 | 0.21294 | 27.2679 | 6.4434 | 0.2363 | 27.2679 | 0.8063%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 75 | 5 | 376.72 | 96.88% | 2.523% | 0.5996% | 7.0558 | 0 | 0 | 7.0558 | 0 | 6.4207 | 0.53234 | 12.0612 | 6.4207 | 0.53234 | 12.0612 | 7.1252 | 0.59075 | 12.0612 | 1.873%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 49 | 4437.6588 | 97.91% | 1.769% | 0.321% | 99.103 | 0 | 0 | 99.103 | 0 | 90.1824 | 5.217 | 17.2864 | 90.1824 | 5.217 | 17.2864 | 100.077 | 5.7893 | 17.2864 | 2.233%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 269 | 9 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 35.9734 | 0 | 0 | 35.9734 | 0 | 32.7353 | 0.95822 | 34.1628 | 32.7353 | 0.95822 | 34.1628 | 36.327 | 1.0633 | 34.1628 | 0.9612%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 7 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 20.9435 | 0 | 0 | 20.9435 | 0 | 19.0583 | 0.74528 | 25.5721 | 19.0583 | 0.74528 | 25.5721 | 21.1494 | 0.82705 | 25.5721 | 0.5713%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 5 | 960.3446 | 65.96% | 33.81% | 0.2324% | 7.8503 | 0 | 0 | 7.8503 | 0 | 7.1436 | 0.53234 | 13.4193 | 7.1436 | 0.53234 | 13.4193 | 7.9274 | 0.59075 | 13.4193 | 0.8174%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 27 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 57.5081 | 0 | 0 | 57.5081 | 0 | 52.3316 | 2.8746 | 18.2045 | 52.3316 | 2.8746 | 18.2045 | 58.0732 | 3.19 | 18.2045 | 1.698%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 28 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 45.0173 | 0 | 0 | 45.0173 | 0 | 40.9651 | 2.9811 | 13.7415 | 40.9651 | 2.9811 | 13.7415 | 45.4597 | 3.3082 | 13.7415 | 3.309%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 9 | 2 | 105.2026 | 98.18% | 1.532% | 0.2854% | 6.6565 | 0 | 0 | 6.6565 | 0 | 6.0573 | 0.21294 | 28.4467 | 6.0573 | 0.21294 | 28.4467 | 6.7219 | 0.2363 | 28.4467 | 6.327%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 72 | 3753.23 | 95.85% | 3.876% | 0.273% | 161.888 | 0 | 0 | 161.888 | 0 | 147.3159 | 7.6657 | 19.2175 | 147.3159 | 7.6657 | 19.2175 | 163.479 | 8.5068 | 19.2175 | 4.313%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 98 | 7 | 49.4853 | 86.66% | 6.71% | 6.626% | 0.88836 | 0 | 0 | 0.88836 | 0 | 0.80839 | 0.74528 | 1.0847 | 0.80839 | 0.74528 | 1.0847 | 0.89709 | 0.82705 | 1.0847 | 1.795%
2027 | 276 | 276-228 | Tier-1 | Non-HFTD---2 | Non-HFTD---8 | 773 | 6 | 290.9914 | 11.65% | 84% | 4.346% | 0.076341 | 0 | 0 | 0.076341 | 0 | 0.069469 | 0.63881 | 0.10875 | 0.069469 | 0.63881 | 0.10875 | 0.077091 | 0.7089 | 0.10875 | 0.02623%
2027 | 279 | 279-10AE | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 557 | 1 | 166.5714 | 5.911% | 88.12% | 5.969% | 0.0051266 | 0 | 0 | 0.0051266 | 0 | 0.0046651 | 0.10647 | 0.043817 | 0.0046651 | 0.10647 | 0.043817 | 0.0051769 | 0.11815 | 0.043817 | 0.003078%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 11 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 152.8573 | 0 | 0 | 152.8573 | 0 | 139.098 | 1.1712 | 118.7702 | 139.098 | 1.1712 | 118.7702 | 154.3595 | 1.2996 | 118.7702 | 2.884%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 12 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 48.4446 | 0 | 0 | 48.4446 | 0 | 44.084 | 1.2776 | 34.5047 | 44.084 | 1.2776 | 34.5047 | 48.9207 | 1.4178 | 34.5047 | 2.406%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 170 | 32 | 481.2843 | 94.31% | 4.95% | 0.7414% | 24.7772 | 0 | 0 | 24.7772 | 0 | 22.5469 | 3.407 | 6.6178 | 22.5469 | 3.407 | 6.6178 | 25.0207 | 3.7808 | 6.6178 | 5.148%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 5 | 550.61 | 92.88% | 6.93% | 0.1872% | 17.2455 | 0 | 0 | 17.2455 | 0 | 15.6932 | 0.53234 | 29.4796 | 15.6932 | 0.53234 | 29.4796 | 17.415 | 0.59075 | 29.4796 | 3.132%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 43 | 8 | 3.2301 | 78.97% | 0% | 21.03% | 0.13762 | 0 | 0 | 0.13762 | 0 | 0.12523 | 0.85175 | 0.14703 | 0.12523 | 0.85175 | 0.14703 | 0.13897 | 0.9452 | 0.14703 | 4.261%
2027 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | Non-HFTD---13 | 100 | 10 | 92.0555 | 97.82% | 0% | 2.183% | 2.6113 | 0 | 0 | 2.6113 | 0 | 2.3763 | 1.0647 | 2.2319 | 2.3763 | 1.0647 | 2.2319 | 2.637 | 1.1815 | 2.2319 | 2.837%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 1 | 458.7821 | 99.48% | 0% | 0.5194% | 1.9182 | 0 | 0 | 1.9182 | 0 | 1.7455 | 0.10647 | 16.3949 | 1.7455 | 0.10647 | 16.3949 | 1.9371 | 0.11815 | 16.3949 | 0.4181%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 5 | 754.1323 | 92.41% | 6.882% | 0.7076% | 4.042 | 0 | 0 | 4.042 | 0 | 3.6782 | 0.53234 | 6.9094 | 3.6782 | 0.53234 | 6.9094 | 4.0817 | 0.59075 | 6.9094 | 0.536%
2027 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 233 | 6 | 4233.8665 | 96.93% | 2.943% | 0.1312% | 30.6456 | 0 | 0 | 30.6456 | 0 | 27.8871 | 0.63881 | 43.6548 | 27.8871 | 0.63881 | 43.6548 | 30.9468 | 0.7089 | 43.6548 | 0.7238%
2027 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 152 | 3 | 2371.786 | 97.71% | 2.108% | 0.1806% | 13.2647 | 0 | 0 | 13.2647 | 0 | 12.0707 | 0.31941 | 37.7911 | 12.0707 | 0.31941 | 37.7911 | 13.395 | 0.35445 | 37.7911 | 0.5593%
2027 | 307 | 307-1492R | Tier-2 | Tier-2---9 | Tier-2---4 | 39 | 3 | 744.3133 | 92.56% | 7.329% | 0.1099% | 15.3688 | 0 | 0 | 15.3688 | 0 | 13.9854 | 0.31941 | 43.7856 | 13.9854 | 0.31941 | 43.7856 | 15.5198 | 0.35445 | 43.7856 | 2.065%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 11 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 131.9508 | 0 | 0 | 131.9508 | 0 | 120.0734 | 1.1712 | 102.5258 | 120.0734 | 1.1712 | 102.5258 | 133.2476 | 1.2996 | 102.5258 | 5.481%
2027 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 98 | 10 | 2117.8574 | 97.53% | 2.33% | 0.1416% | 61.1225 | 0 | 0 | 61.1225 | 0 | 55.6207 | 1.0647 | 52.2415 | 55.6207 | 1.0647 | 52.2415 | 61.7232 | 1.1815 | 52.2415 | 2.886%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 14 | 4762.848 | 95.55% | 4.384% | 0.07015% | 169.5031 | 0 | 0 | 169.5031 | 0 | 154.2455 | 1.4906 | 103.4817 | 154.2455 | 1.4906 | 103.4817 | 171.169 | 1.6541 | 103.4817 | 3.559%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 39 | 1 | 95.5263 | 19.37% | 79.9% | 0.729% | 0.13762 | 0 | 0 | 0.13762 | 0 | 0.12523 | 0.10647 | 1.1762 | 0.12523 | 0.10647 | 1.1762 | 0.13897 | 0.11815 | 1.1762 | 0.1441%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 14 | 3 | 46.1951 | 84.69% | 14.76% | 0.5474% | 2.4313 | 0 | 0 | 2.4313 | 0 | 2.2124 | 0.31941 | 6.9267 | 2.2124 | 0.31941 | 6.9267 | 2.4552 | 0.35445 | 6.9267 | 5.263%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 15 | 1 | 15.6056 | 49.38% | 48.09% | 2.529% | 0.14899 | 0 | 0 | 0.14899 | 0 | 0.13558 | 0.10647 | 1.2734 | 0.13558 | 0.10647 | 1.2734 | 0.15046 | 0.11815 | 1.2734 | 0.9547%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 5 | 278.652 | 16.28% | 83.57% | 0.1501% | 4.6984 | 0 | 0 | 4.6984 | 0 | 4.2755 | 0.53234 | 8.0314 | 4.2755 | 0.53234 | 8.0314 | 4.7446 | 0.59075 | 8.0314 | 1.686%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 13 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.072289 | 0 | 0 | 0.072289 | 0 | 0.065782 | 1.3841 | 0.047527 | 0.065782 | 1.3841 | 0.047527 | 0.072999 | 1.5359 | 0.047527 | 0.04522%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 6 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.010044 | 0 | 0 | 0.010044 | 0 | 0.0091395 | 0.63881 | 0.014307 | 0.0091395 | 0.63881 | 0.014307 | 0.010142 | 0.7089 | 0.014307 | 0.004969%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 39 | 5 | 209.8559 | 99.5% | 0% | 0.498% | 7.7635 | 0 | 0 | 7.7635 | 0 | 7.0647 | 0.53234 | 13.2709 | 7.0647 | 0.53234 | 13.2709 | 7.8398 | 0.59075 | 13.2709 | 3.699%
2027 | 334 | 334-21 | Tier-1 | Non-HFTD---2 | Non-HFTD---5 | 183 | 3 | 378.2145 | 89.09% | 9.517% | 1.396% | 1.6019 | 0 | 0 | 1.6019 | 0 | 1.4577 | 0.31941 | 4.5637 | 1.4577 | 0.31941 | 4.5637 | 1.6176 | 0.35445 | 4.5637 | 0.4235%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 15 | 2 | 302.428 | 99.27% | 0.6612% | 0.06922% | 11.6085 | 0 | 0 | 11.6085 | 0 | 10.5636 | 0.21294 | 49.6089 | 10.5636 | 0.21294 | 49.6089 | 11.7226 | 0.2363 | 49.6089 | 3.838%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 46 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 81.2057 | 0 | 0 | 81.2057 | 0 | 73.896 | 4.8975 | 15.0884 | 73.896 | 4.8975 | 15.0884 | 82.0037 | 5.4349 | 15.0884 | 2.254%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 97 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 463.6082 | 0 | 0 | 463.6082 | 0 | 421.8771 | 10.3274 | 40.8501 | 421.8771 | 10.3274 | 40.8501 | 468.1645 | 11.4605 | 40.8501 | 3.342%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 61 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 118.4348 | 0 | 0 | 118.4348 | 0 | 107.774 | 6.4946 | 16.5945 | 107.774 | 6.4946 | 16.5945 | 119.5987 | 7.2071 | 16.5945 | 2.126%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 7 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 75.4922 | 0 | 0 | 75.4922 | 0 | 68.6969 | 0.74528 | 92.1761 | 68.6969 | 0.74528 | 92.1761 | 76.2341 | 0.82705 | 92.1761 | 0.5583%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 74 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 500.3751 | 0 | 0 | 500.3751 | 0 | 455.3345 | 7.8787 | 57.7934 | 455.3345 | 7.8787 | 57.7934 | 505.2928 | 8.7431 | 57.7934 | 4.467%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 29 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 575.6545 | 0 | 0 | 575.6545 | 0 | 523.8377 | 3.0876 | 169.6594 | 523.8377 | 3.0876 | 169.6594 | 581.312 | 3.4263 | 169.6594 | 2.448%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 7 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 168.2991 | 0 | 0 | 168.2991 | 0 | 153.1499 | 0.74528 | 205.4934 | 153.1499 | 0.74528 | 205.4934 | 169.9531 | 0.82705 | 205.4934 | 1.84%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 40 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 597.6148 | 0 | 0 | 597.6148 | 0 | 543.8214 | 4.2587 | 127.6955 | 543.8214 | 4.2587 | 127.6955 | 603.4882 | 4.726 | 127.6955 | 3.211%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 2 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 25.5602 | 0 | 0 | 25.5602 | 0 | 23.2594 | 0.21294 | 109.2316 | 23.2594 | 0.21294 | 109.2316 | 25.8114 | 0.2363 | 109.2316 | 0.2772%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 4 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 51.7534 | 0 | 0 | 51.7534 | 0 | 47.0949 | 0.42587 | 110.5842 | 47.0949 | 0.42587 | 110.5842 | 52.262 | 0.4726 | 110.5842 | 2.054%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 25 | 2 | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 51.3683 | 0 | 0 | 51.3683 | 0 | 46.7445 | 0.21294 | 219.5227 | 46.7445 | 0.21294 | 219.5227 | 51.8732 | 0.2363 | 219.5227 | 2.318%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 28 | 1 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 18.293 | 0 | 0 | 18.293 | 0 | 16.6464 | 0.10647 | 156.3504 | 16.6464 | 0.10647 | 156.3504 | 18.4728 | 0.11815 | 156.3504 | 0.9186%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 7 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 106.3534 | 0 | 0 | 106.3534 | 0 | 96.7801 | 0.74528 | 129.8576 | 96.7801 | 0.74528 | 129.8576 | 107.3986 | 0.82705 | 129.8576 | 2.335%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 3 | 465.1006 | 62.84% | 37.09% | 0.07221% | 23.1157 | 0 | 0 | 23.1157 | 0 | 21.035 | 0.31941 | 65.8568 | 21.035 | 0.31941 | 65.8568 | 23.3429 | 0.35445 | 65.8568 | 4.97%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 15 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 323.4286 | 0 | 0 | 323.4286 | 0 | 294.3156 | 1.597 | 184.2898 | 294.3156 | 1.597 | 184.2898 | 326.6072 | 1.7722 | 184.2898 | 2.39%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 40 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 490.5123 | 0 | 0 | 490.5123 | 0 | 446.3596 | 4.2587 | 104.8103 | 446.3596 | 4.2587 | 104.8103 | 495.3331 | 4.726 | 104.8103 | 2.392%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 2 | 3653.654 | 88.54% | 11.39% | 0.07412% | 21.0807 | 0 | 0 | 21.0807 | 0 | 19.1831 | 0.21294 | 90.0883 | 19.1831 | 0.21294 | 90.0883 | 21.2878 | 0.2363 | 90.0883 | 0.577%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 18 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 170.6463 | 0 | 0 | 170.6463 | 0 | 155.2859 | 1.9164 | 81.0287 | 155.2859 | 1.9164 | 81.0287 | 172.3235 | 2.1267 | 81.0287 | 2.275%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 58 | 3 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 20.369 | 0 | 0 | 20.369 | 0 | 18.5355 | 0.31941 | 58.0313 | 18.5355 | 0.31941 | 58.0313 | 20.5692 | 0.35445 | 58.0313 | 1.199%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 7 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 50.152 | 0 | 0 | 50.152 | 0 | 45.6377 | 0.74528 | 61.2357 | 45.6377 | 0.74528 | 61.2357 | 50.6449 | 0.82705 | 61.2357 | 0.9223%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 67 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 413.2718 | 0 | 0 | 413.2718 | 0 | 376.0717 | 7.1334 | 52.72 | 376.0717 | 7.1334 | 52.72 | 417.3334 | 7.916 | 52.72 | 2.581%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 730 | 27 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 95.1206 | 0 | 0 | 95.1206 | 0 | 86.5585 | 2.8746 | 30.111 | 86.5585 | 2.8746 | 30.111 | 96.0555 | 3.19 | 30.111 | 1.023%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 40 | 1 | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 8.986 | 0 | 0 | 8.986 | 0 | 8.1771 | 0.10647 | 76.8033 | 8.1771 | 0.10647 | 76.8033 | 9.0743 | 0.11815 | 76.8033 | 0.7182%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 48 | 1 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 30.7065 | 0 | 0 | 30.7065 | 0 | 27.9425 | 0.10647 | 262.4488 | 27.9425 | 0.10647 | 262.4488 | 31.0083 | 0.11815 | 262.4488 | 0.6022%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 17 | 1 | 878.9304 | 95.49% | 4.482% | 0.03213% | 14.3166 | 0 | 0 | 14.3166 | 0 | 13.0279 | 0.10647 | 122.3643 | 13.0279 | 0.10647 | 122.3643 | 14.4573 | 0.11815 | 122.3643 | 1.629%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 17 | 16869.708 | 98.79% | 1.184% | 0.02933% | 303.1674 | 0 | 0 | 303.1674 | 0 | 275.8782 | 1.81 | 152.422 | 275.8782 | 1.81 | 152.422 | 306.1469 | 2.0085 | 152.422 | 1.797%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 28 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 385.8627 | 0 | 0 | 385.8627 | 0 | 351.1298 | 2.9811 | 117.7847 | 351.1298 | 2.9811 | 117.7847 | 389.6549 | 3.3082 | 117.7847 | 2.18%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 43 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 329.6083 | 0 | 0 | 329.6083 | 0 | 299.9391 | 4.5781 | 65.5155 | 299.9391 | 4.5781 | 65.5155 | 332.8477 | 5.0804 | 65.5155 | 3.159%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 54 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 662.0753 | 0 | 0 | 662.0753 | 0 | 602.4795 | 5.7493 | 104.7919 | 602.4795 | 5.7493 | 104.7919 | 668.5822 | 6.3801 | 104.7919 | 5.631%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 344 | 6 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 187.5207 | 0 | 0 | 187.5207 | 0 | 170.6413 | 0.63881 | 267.1235 | 170.6413 | 0.63881 | 267.1235 | 189.3637 | 0.7089 | 267.1235 | 0.4987%
2027 | 361 | 361-45R | Tier-1 | Non-HFTD---5 | Non-HFTD---9 | 146 | 1 | 74.9226 | 4.739% | 91.81% | 3.451% | 0.0070519 | 0 | 0 | 0.0070519 | 0 | 0.0064171 | 0.10647 | 0.060273 | 0.0064171 | 0.10647 | 0.060273 | 0.0071212 | 0.11815 | 0.060273 | 0.009412%
2027 | 362 | 362-47F | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 650 | 41 | 174.2726 | 36.5% | 57.41% | 6.096% | 1.1635 | 0 | 0 | 1.1635 | 0 | 1.0587 | 4.3652 | 0.24254 | 1.0587 | 4.3652 | 0.24254 | 1.1749 | 4.8441 | 0.24254 | 0.6676%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 76 | 2 | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.326 | 0 | 0 | 1.326 | 0 | 1.2066 | 0.21294 | 5.6665 | 1.2066 | 0.21294 | 5.6665 | 1.339 | 0.2363 | 5.6665 | 0.1434%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 79 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 84.7234 | 0 | 0 | 84.7234 | 0 | 77.0971 | 8.411 | 9.1662 | 77.0971 | 8.411 | 9.1662 | 85.5561 | 9.3338 | 9.1662 | 2.701%
2027 | 401 | 401-684R | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 1 | 1.5961 | 62.42% | 35.57% | 2.007% | 0.14447 | 0 | 0 | 0.14447 | 0 | 0.13147 | 0.10647 | 1.2348 | 0.13147 | 0.10647 | 1.2348 | 0.14589 | 0.11815 | 1.2348 | 9.051%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 32 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 49.3115 | 0 | 0 | 49.3115 | 0 | 44.8728 | 3.407 | 13.1708 | 44.8728 | 3.407 | 13.1708 | 49.7961 | 3.7808 | 13.1708 | 2.655%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 73 | 6370.0414 | 98.47% | 1.262% | 0.272% | 155.1226 | 0 | 0 | 155.1226 | 0 | 141.1595 | 7.7722 | 18.1621 | 141.1595 | 7.7722 | 18.1621 | 156.6472 | 8.6249 | 18.1621 | 2.435%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 1 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 0.81885 | 0 | 0 | 0.81885 | 0 | 0.74514 | 0.10647 | 6.9987 | 0.74514 | 0.10647 | 6.9987 | 0.8269 | 0.11815 | 6.9987 | 0.06064%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 84 | 2 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 23.6723 | 0 | 0 | 23.6723 | 0 | 21.5415 | 0.21294 | 101.1638 | 21.5415 | 0.21294 | 101.1638 | 23.905 | 0.2363 | 101.1638 | 0.6729%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 133 | 13 | 4750.1268 | 98% | 1.916% | 0.08125% | 131.9569 | 0 | 0 | 131.9569 | 0 | 120.079 | 1.3841 | 86.7567 | 120.079 | 1.3841 | 86.7567 | 133.2538 | 1.5359 | 86.7567 | 2.778%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 3 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 45.4167 | 0 | 0 | 45.4167 | 0 | 41.3286 | 0.31941 | 129.3924 | 41.3286 | 0.31941 | 129.3924 | 45.8631 | 0.35445 | 129.3924 | 0.8491%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 201 | 1 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 2.5438 | 0 | 0 | 2.5438 | 0 | 2.3148 | 0.10647 | 21.7421 | 2.3148 | 0.10647 | 21.7421 | 2.5688 | 0.11815 | 21.7421 | 0.1386%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 5 | 852.9261 | 84.92% | 14.72% | 0.3553% | 7.2434 | 0 | 0 | 7.2434 | 0 | 6.5914 | 0.53234 | 12.382 | 6.5914 | 0.53234 | 12.382 | 7.3146 | 0.59075 | 12.382 | 0.8492%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 144 | 3 | 526.1263 | 57.95% | 41.57% | 0.4783% | 1.8421 | 0 | 0 | 1.8421 | 0 | 1.6763 | 0.31941 | 5.2482 | 1.6763 | 0.31941 | 5.2482 | 1.8602 | 0.35445 | 5.2482 | 0.3501%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 22 | 11572.221 | 88.48% | 11.4% | 0.1243% | 85.613 | 0 | 0 | 85.613 | 0 | 77.9067 | 2.3423 | 33.2607 | 77.9067 | 2.3423 | 33.2607 | 86.4544 | 2.5993 | 33.2607 | 0.7398%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 54 | 1 | 704.6091 | 96.62% | 3.132% | 0.2514% | 3.656 | 0 | 0 | 3.656 | 0 | 3.3269 | 0.10647 | 31.2476 | 3.3269 | 0.10647 | 31.2476 | 3.6919 | 0.11815 | 31.2476 | 0.5189%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 25 | 1 | 549.9829 | 98.93% | 0.9134% | 0.161% | 6.3113 | 0 | 0 | 6.3113 | 0 | 5.7432 | 0.10647 | 53.9424 | 5.7432 | 0.10647 | 53.9424 | 6.3733 | 0.11815 | 53.9424 | 1.148%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 74 | 1 | 474.7376 | 91.31% | 8.325% | 0.3651% | 1.6988 | 0 | 0 | 1.6988 | 0 | 1.5459 | 0.10647 | 14.5195 | 1.5459 | 0.10647 | 14.5195 | 1.7155 | 0.11815 | 14.5195 | 0.3578%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 122 | 13 | 333.8465 | 96.62% | 2.31% | 1.072% | 9.9674 | 0 | 0 | 9.9674 | 0 | 9.0702 | 1.3841 | 6.5532 | 9.0702 | 1.3841 | 6.5532 | 10.0654 | 1.5359 | 6.5532 | 2.986%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 4 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 9.5974 | 0 | 0 | 9.5974 | 0 | 8.7335 | 0.42587 | 20.5073 | 8.7335 | 0.42587 | 20.5073 | 9.6917 | 0.4726 | 20.5073 | 0.2811%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 465 | 34 | 571.2373 | 70.71% | 27.93% | 1.361% | 8.5647 | 0 | 0 | 8.5647 | 0 | 7.7937 | 3.6199 | 2.153 | 7.7937 | 3.6199 | 2.153 | 8.6488 | 4.0171 | 2.153 | 1.499%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 30 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 236.135 | 0 | 0 | 236.135 | 0 | 214.8796 | 3.1941 | 67.2749 | 214.8796 | 3.1941 | 67.2749 | 238.4557 | 3.5445 | 67.2749 | 2.451%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 3 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 27.5566 | 0 | 0 | 27.5566 | 0 | 25.0761 | 0.31941 | 78.5087 | 25.0761 | 0.31941 | 78.5087 | 27.8274 | 0.35445 | 78.5087 | 0.3801%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 2 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 8.5068 | 0 | 0 | 8.5068 | 0 | 7.7411 | 0.21294 | 36.3538 | 7.7411 | 0.21294 | 36.3538 | 8.5904 | 0.2363 | 36.3538 | 0.5305%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 17 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 95.2433 | 0 | 0 | 95.2433 | 0 | 86.6701 | 1.81 | 47.885 | 86.6701 | 1.81 | 47.885 | 96.1794 | 2.0085 | 47.885 | 0.8968%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 2 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 3.6478 | 0 | 0 | 3.6478 | 0 | 3.3195 | 0.21294 | 15.5891 | 3.3195 | 0.21294 | 15.5891 | 3.6837 | 0.2363 | 15.5891 | 0.2065%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 9 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 34.1662 | 0 | 0 | 34.1662 | 0 | 31.0908 | 0.95822 | 32.4465 | 31.0908 | 0.95822 | 32.4465 | 34.502 | 1.0633 | 32.4465 | 0.9288%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 6 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 11.5482 | 0 | 0 | 11.5482 | 0 | 10.5087 | 0.63881 | 16.4504 | 10.5087 | 0.63881 | 16.4504 | 11.6617 | 0.7089 | 16.4504 | 0.2612%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 51 | 2 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 13.4195 | 0 | 0 | 13.4195 | 0 | 12.2116 | 0.21294 | 57.3485 | 12.2116 | 0.21294 | 57.3485 | 13.5514 | 0.2363 | 57.3485 | 1.108%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 184 | 3 | 2612.2711 | 91.91% | 7.885% | 0.2065% | 11.3521 | 0 | 0 | 11.3521 | 0 | 10.3303 | 0.31941 | 32.3422 | 10.3303 | 0.31941 | 32.3422 | 11.4637 | 0.35445 | 32.3422 | 0.4346%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 314 | 8 | 2119.752 | 55.7% | 43.96% | 0.3458% | 8.7234 | 0 | 0 | 8.7234 | 0 | 7.9381 | 0.85175 | 9.3198 | 7.9381 | 0.85175 | 9.3198 | 8.8091 | 0.9452 | 9.3198 | 0.4115%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 4 | 520.639 | 76.18% | 22.78% | 1.038% | 2.2778 | 0 | 0 | 2.2778 | 0 | 2.0727 | 0.42587 | 4.867 | 2.0727 | 0.42587 | 4.867 | 2.3002 | 0.4726 | 4.867 | 0.4375%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 170 | 1 | 630.7627 | 79.12% | 20.09% | 0.7869% | 0.85136 | 0 | 0 | 0.85136 | 0 | 0.77473 | 0.10647 | 7.2766 | 0.77473 | 0.10647 | 7.2766 | 0.85973 | 0.11815 | 7.2766 | 0.135%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 17 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 57.3943 | 0 | 0 | 57.3943 | 0 | 52.228 | 1.81 | 28.8558 | 52.228 | 1.81 | 28.8558 | 57.9583 | 2.0085 | 28.8558 | 0.6304%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 18 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 66.6553 | 0 | 0 | 66.6553 | 0 | 60.6554 | 1.9164 | 31.6502 | 60.6554 | 1.9164 | 31.6502 | 67.3104 | 2.1267 | 31.6502 | 1.181%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 45 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 142.6837 | 0 | 0 | 142.6837 | 0 | 129.8403 | 4.7911 | 27.1004 | 129.8403 | 4.7911 | 27.1004 | 144.086 | 5.3167 | 27.1004 | 2.12%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 72 | 1 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 5.8412 | 0 | 0 | 5.8412 | 0 | 5.3154 | 0.10647 | 49.9247 | 5.3154 | 0.10647 | 49.9247 | 5.8986 | 0.11815 | 49.9247 | 0.3906%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 6 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 54.7957 | 0 | 0 | 54.7957 | 0 | 49.8633 | 0.63881 | 78.0566 | 49.8633 | 0.63881 | 78.0566 | 55.3342 | 0.7089 | 78.0566 | 1.042%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 161 | 7 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 27.9498 | 0 | 0 | 27.9498 | 0 | 25.434 | 0.74528 | 34.1268 | 25.434 | 0.74528 | 34.1268 | 28.2245 | 0.82705 | 34.1268 | 1.205%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 4 | 296.7138 | 97.11% | 2.719% | 0.1664% | 18.5698 | 0 | 0 | 18.5698 | 0 | 16.8983 | 0.42587 | 39.6792 | 16.8983 | 0.42587 | 39.6792 | 18.7524 | 0.4726 | 39.6792 | 6.259%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 25 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 284.8134 | 0 | 0 | 284.8134 | 0 | 259.1763 | 2.6617 | 97.3721 | 259.1763 | 2.6617 | 97.3721 | 287.6125 | 2.9537 | 97.3721 | 3.442%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 3 | 792.2018 | 92.77% | 7.138% | 0.09408% | 14.5312 | 0 | 0 | 14.5312 | 0 | 13.2232 | 0.31941 | 41.3995 | 13.2232 | 0.31941 | 41.3995 | 14.674 | 0.35445 | 41.3995 | 1.834%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 15 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 67.0221 | 0 | 0 | 67.0221 | 0 | 60.9892 | 1.597 | 38.1892 | 60.9892 | 1.597 | 38.1892 | 67.6808 | 1.7722 | 38.1892 | 5.919%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 5 | 625.5425 | 99.9% | 0% | 0.09615% | 45.3082 | 0 | 0 | 45.3082 | 0 | 41.2299 | 0.53234 | 77.45 | 41.2299 | 0.53234 | 77.45 | 45.7535 | 0.59075 | 77.45 | 7.243%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 3 | 2823.7515 | 99.93% | 0% | 0.06613% | 34.578 | 0 | 0 | 34.578 | 0 | 31.4655 | 0.31941 | 98.5129 | 31.4655 | 0.31941 | 98.5129 | 34.9178 | 0.35445 | 98.5129 | 1.225%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 7 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 11.9935 | 0 | 0 | 11.9935 | 0 | 10.9139 | 0.74528 | 14.644 | 10.9139 | 0.74528 | 14.644 | 12.1113 | 0.82705 | 14.644 | 0.8702%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 21 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 222.0263 | 0 | 0 | 222.0263 | 0 | 202.0409 | 2.2358 | 90.3648 | 202.0409 | 2.2358 | 90.3648 | 224.2084 | 2.4811 | 90.3648 | 4.217%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 29 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 261.9853 | 0 | 0 | 261.9853 | 0 | 238.4031 | 3.0876 | 77.2135 | 238.4031 | 3.0876 | 77.2135 | 264.5601 | 3.4263 | 77.2135 | 1.565%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 128 | 6 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 54.9074 | 0 | 0 | 54.9074 | 0 | 49.965 | 0.63881 | 78.2157 | 49.965 | 0.63881 | 78.2157 | 55.4471 | 0.7089 | 78.2157 | 1.291%
2027 | 492 | 492-1090F | Tier-1 | Non-HFTD---8 | Non-HFTD---16 | 134 | 1 | 34.6286 | 4.526% | 88.49% | 6.986% | 0.003392 | 0 | 0 | 0.003392 | 0 | 0.0030866 | 0.10647 | 0.028991 | 0.0030866 | 0.10647 | 0.028991 | 0.0034253 | 0.11815 | 0.028991 | 0.009795%
2027 | 492 | 492-14R | Tier-1 | Non-HFTD---2 | Non-HFTD---8 | 453 | 17 | 216.5783 | 3.253% | 93.45% | 3.298% | 0.076681 | 0 | 0 | 0.076681 | 0 | 0.069779 | 1.81 | 0.038553 | 0.069779 | 1.81 | 0.038553 | 0.077435 | 2.0085 | 0.038553 | 0.03541%
2027 | 492 | 492-343R | Tier-1 | Non-HFTD---1 | Non-HFTD---9 | 107 | 1 | 272.4272 | 37.19% | 62.03% | 0.7764% | 0.2746 | 0 | 0 | 0.2746 | 0 | 0.24988 | 0.10647 | 2.347 | 0.24988 | 0.10647 | 2.347 | 0.2773 | 0.11815 | 2.347 | 0.1008%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 4 | 800.5503 | 21.6% | 78.32% | 0.07823% | 10.0299 | 0 | 0 | 10.0299 | 0 | 9.1271 | 0.42587 | 21.4315 | 9.1271 | 0.42587 | 21.4315 | 10.1285 | 0.4726 | 21.4315 | 1.253%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 23 | 2 | 204.0835 | 99.63% | 0% | 0.368% | 5.1275 | 0 | 0 | 5.1275 | 0 | 4.666 | 0.21294 | 21.9125 | 4.666 | 0.21294 | 21.9125 | 5.1779 | 0.2363 | 21.9125 | 2.512%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 154 | 5 | 733.6834 | 99.51% | 0% | 0.4917% | 6.8741 | 0 | 0 | 6.8741 | 0 | 6.2553 | 0.53234 | 11.7506 | 6.2553 | 0.53234 | 11.7506 | 6.9417 | 0.59075 | 11.7506 | 0.9369%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 180 | 2 | 2978.814 | 97.34% | 2.471% | 0.184% | 9.3435 | 0 | 0 | 9.3435 | 0 | 8.5025 | 0.21294 | 39.9296 | 8.5025 | 0.21294 | 39.9296 | 9.4354 | 0.2363 | 39.9296 | 0.3137%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 155 | 16 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 43.3702 | 0 | 0 | 43.3702 | 0 | 39.4663 | 1.7035 | 23.1678 | 39.4663 | 1.7035 | 23.1678 | 43.7964 | 1.8904 | 23.1678 | 2.933%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 408 | 6 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 10.8851 | 0 | 0 | 10.8851 | 0 | 9.9053 | 0.63881 | 15.5058 | 9.9053 | 0.63881 | 15.5058 | 10.9921 | 0.7089 | 15.5058 | 0.4126%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 401 | 17 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 38.9162 | 0 | 0 | 38.9162 | 0 | 35.4132 | 1.81 | 19.5657 | 35.4132 | 1.81 | 19.5657 | 39.2986 | 2.0085 | 19.5657 | 1.14%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 9 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 28.8868 | 0 | 0 | 28.8868 | 0 | 26.2866 | 0.95822 | 27.4329 | 26.2866 | 0.95822 | 27.4329 | 29.1707 | 1.0633 | 27.4329 | 1.769%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 249 | 13 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 99.0347 | 0 | 0 | 99.0347 | 0 | 90.1202 | 1.3841 | 65.1115 | 90.1202 | 1.3841 | 65.1115 | 100.008 | 1.5359 | 65.1115 | 1.464%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 43 | 748.333 | 77.34% | 21.7% | 0.962% | 17.6885 | 0 | 0 | 17.6885 | 0 | 16.0963 | 4.5781 | 3.5159 | 16.0963 | 4.5781 | 3.5159 | 17.8623 | 5.0804 | 3.5159 | 2.364%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 276 | 35 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 73.9632 | 0 | 0 | 73.9632 | 0 | 67.3055 | 3.7264 | 18.0618 | 67.3055 | 3.7264 | 18.0618 | 74.6901 | 4.1352 | 18.0618 | 3.548%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 113 | 5 | 258.296 | 74.72% | 24.53% | 0.7505% | 2.4766 | 0 | 0 | 2.4766 | 0 | 2.2537 | 0.53234 | 4.2336 | 2.2537 | 0.53234 | 4.2336 | 2.501 | 0.59075 | 4.2336 | 0.9588%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 306 | 2 | 4997.7942 | 96.49% | 3.313% | 0.193% | 9.1409 | 0 | 0 | 9.1409 | 0 | 8.3181 | 0.21294 | 39.0635 | 8.3181 | 0.21294 | 39.0635 | 9.2307 | 0.2363 | 39.0635 | 0.1829%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 219 | 6 | 2044.6463 | 97.57% | 2.13% | 0.298% | 15.8507 | 0 | 0 | 15.8507 | 0 | 14.4239 | 0.63881 | 22.5793 | 14.4239 | 0.63881 | 22.5793 | 16.0065 | 0.7089 | 22.5793 | 0.7752%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 18 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 181.8669 | 0 | 0 | 181.8669 | 0 | 165.4964 | 1.9164 | 86.3565 | 165.4964 | 1.9164 | 86.3565 | 183.6542 | 2.1267 | 86.3565 | 1.602%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 20 | 810.9996 | 89.31% | 10.24% | 0.4457% | 21.1112 | 0 | 0 | 21.1112 | 0 | 19.2109 | 2.1294 | 9.0219 | 19.2109 | 2.1294 | 9.0219 | 21.3187 | 2.363 | 9.0219 | 2.603%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 22 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 157.8933 | 0 | 0 | 157.8933 | 0 | 143.6808 | 2.3423 | 61.3416 | 143.6808 | 2.3423 | 61.3416 | 159.4451 | 2.5993 | 61.3416 | 1.862%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 22 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 179.9161 | 0 | 0 | 179.9161 | 0 | 163.7212 | 2.3423 | 69.8975 | 163.7212 | 2.3423 | 69.8975 | 181.6843 | 2.5993 | 69.8975 | 2.065%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 22 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 98.9082 | 0 | 0 | 98.9082 | 0 | 90.0051 | 2.3423 | 38.4259 | 90.0051 | 2.3423 | 38.4259 | 99.8802 | 2.5993 | 38.4259 | 1.76%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 232 | 1 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 15.2071 | 0 | 0 | 15.2071 | 0 | 13.8383 | 0.10647 | 129.9752 | 13.8383 | 0.10647 | 129.9752 | 15.3566 | 0.11815 | 129.9752 | 0.1242%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 437 | 35 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 207.3465 | 0 | 0 | 207.3465 | 0 | 188.6825 | 3.7264 | 50.6341 | 188.6825 | 3.7264 | 50.6341 | 209.3843 | 4.1352 | 50.6341 | 2.301%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 9 | 112.7117 | 43.02% | 55.81% | 1.165% | 1.9776 | 0 | 0 | 1.9776 | 0 | 1.7996 | 0.95822 | 1.8781 | 1.7996 | 0.95822 | 1.8781 | 1.9971 | 1.0633 | 1.8781 | 1.755%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 1 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.082181 | 0 | 0 | 0.082181 | 0 | 0.074784 | 0.10647 | 0.7024 | 0.074784 | 0.10647 | 0.7024 | 0.082989 | 0.11815 | 0.7024 | 0.07027%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 78 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 203.0253 | 0 | 0 | 203.0253 | 0 | 184.7503 | 8.3045 | 22.2469 | 184.7503 | 8.3045 | 22.2469 | 205.0206 | 9.2157 | 22.2469 | 3.6%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 17 | 305.199 | 11.7% | 87.21% | 1.095% | 0.88437 | 0 | 0 | 0.88437 | 0 | 0.80476 | 1.81 | 0.44463 | 0.80476 | 1.81 | 0.44463 | 0.89306 | 2.0085 | 0.44463 | 0.2898%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 231 | 27 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 184.9327 | 0 | 0 | 184.9327 | 0 | 168.2862 | 2.8746 | 58.5415 | 168.2862 | 2.8746 | 58.5415 | 186.7502 | 3.19 | 58.5415 | 3.382%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 489 | 40 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 267.857 | 0 | 0 | 267.857 | 0 | 243.7462 | 4.2587 | 57.2344 | 243.7462 | 4.2587 | 57.2344 | 270.4895 | 4.726 | 57.2344 | 2.367%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 283 | 16 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 222.5245 | 0 | 0 | 222.5245 | 0 | 202.4942 | 1.7035 | 118.8699 | 202.4942 | 1.7035 | 118.8699 | 224.7114 | 1.8904 | 118.8699 | 1.623%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 29 | 8801.877 | 98.2% | 1.718% | 0.0819% | 256.8615 | 0 | 0 | 256.8615 | 0 | 233.7404 | 3.0876 | 75.7033 | 233.7404 | 3.0876 | 75.7033 | 259.3859 | 3.4263 | 75.7033 | 2.918%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 842 | 107 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1473.5574 | 0 | 0 | 1473.5574 | 0 | 1340.9172 | 11.3921 | 117.7057 | 1340.9172 | 11.3921 | 117.7057 | 1488.0394 | 12.642 | 117.7057 | 3.65%
2027 | 57 | 57-736 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 81 | 4 | 116.8924 | 0.4896% | 98.37% | 1.142% | 0.0081964 | 0 | 0 | 0.0081964 | 0 | 0.0074587 | 0.42587 | 0.017514 | 0.0074587 | 0.42587 | 0.017514 | 0.008277 | 0.4726 | 0.017514 | 0.007012%
2027 | 586 | 586-3 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 84 | 11 | 516.8084 | 87.93% | 11.54% | 0.527% | 17.2577 | 0 | 0 | 17.2577 | 0 | 15.7043 | 1.1712 | 13.4092 | 15.7043 | 1.1712 | 13.4092 | 17.4273 | 1.2996 | 13.4092 | 3.339%
2027 | 59 | 59-465 | Tier-1 | Non-HFTD---6 | Non-HFTD---8 | 167 | 3 | 77.379 | 64.48% | 28.11% | 7.401% | 0.25995 | 0 | 0 | 0.25995 | 0 | 0.23655 | 0.31941 | 0.74059 | 0.23655 | 0.31941 | 0.74059 | 0.2625 | 0.35445 | 0.74059 | 0.3359%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 10 | 18774.394 | 95.55% | 4.388% | 0.06321% | 130.7097 | 0 | 0 | 130.7097 | 0 | 118.944 | 1.0647 | 111.7177 | 118.944 | 1.0647 | 111.7177 | 131.9943 | 1.1815 | 111.7177 | 0.6962%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 34 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 335.0567 | 0 | 0 | 335.0567 | 0 | 304.8971 | 3.6199 | 84.2274 | 304.8971 | 3.6199 | 84.2274 | 338.3497 | 4.0171 | 84.2274 | 1.302%
2027 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 477 | 6 | 5312.2676 | 97.77% | 1.999% | 0.2313% | 18.9458 | 0 | 0 | 18.9458 | 0 | 17.2405 | 0.63881 | 26.9884 | 17.2405 | 0.63881 | 26.9884 | 19.132 | 0.7089 | 26.9884 | 0.3566%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 344 | 26 | 2610.8 | 93.6% | 6.065% | 0.3401% | 53.56 | 0 | 0 | 53.56 | 0 | 48.7388 | 2.7682 | 17.6068 | 48.7388 | 2.7682 | 17.6068 | 54.0864 | 3.0719 | 17.6068 | 2.051%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 551 | 44 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 90.804 | 0 | 0 | 90.804 | 0 | 82.6304 | 4.6846 | 17.6387 | 82.6304 | 4.6846 | 17.6387 | 91.6965 | 5.1986 | 17.6387 | 2.172%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 8 | 622.3042 | 87.18% | 11.98% | 0.8373% | 6.6245 | 0 | 0 | 6.6245 | 0 | 6.0282 | 0.85175 | 7.0775 | 6.0282 | 0.85175 | 7.0775 | 6.6896 | 0.9452 | 7.0775 | 1.065%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 10 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 18.8003 | 0 | 0 | 18.8003 | 0 | 17.108 | 1.0647 | 16.0686 | 17.108 | 1.0647 | 16.0686 | 18.985 | 1.1815 | 16.0686 | 1.155%
2027 | 702 | 702-25 | Tier-1 | Non-HFTD---4 | Non-HFTD---13 | 20 | 1 | 105.79 | 16.96% | 82.58% | 0.4592% | 0.26018 | 0 | 0 | 0.26018 | 0 | 0.23676 | 0.10647 | 2.2238 | 0.23676 | 0.10647 | 2.2238 | 0.26274 | 0.11815 | 2.2238 | 0.2459%
2027 | 702 | 702-27R | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 513 | 3 | 127.2983 | 14.57% | 79% | 6.429% | 0.031459 | 0 | 0 | 0.031459 | 0 | 0.028627 | 0.31941 | 0.089626 | 0.028627 | 0.31941 | 0.089626 | 0.031768 | 0.35445 | 0.089626 | 0.02471%
2027 | 702 | 702-30 | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 328 | 4 | 100.3702 | 67.48% | 26.99% | 5.53% | 0.23952 | 0 | 0 | 0.23952 | 0 | 0.21796 | 0.42587 | 0.51179 | 0.21796 | 0.42587 | 0.51179 | 0.24187 | 0.4726 | 0.51179 | 0.2386%
2027 | 702 | 702-448F | Tier-1 | Non-HFTD---19 | Non-HFTD---22 | 2 | 1 | 0.36733 | 90.03% | 0% | 9.967% | 0.047955 | 0 | 0 | 0.047955 | 0 | 0.043638 | 0.10647 | 0.40987 | 0.043638 | 0.10647 | 0.40987 | 0.048426 | 0.11815 | 0.40987 | 13.05%
2027 | 703 | 703-279R | Tier-1 | Non-HFTD---2 | Non-HFTD---4 | 443 | 4 | 201.9742 | 33.23% | 63.5% | 3.273% | 0.17573 | 0 | 0 | 0.17573 | 0 | 0.15991 | 0.42587 | 0.37548 | 0.15991 | 0.42587 | 0.37548 | 0.17745 | 0.4726 | 0.37548 | 0.087%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 310 | 18 | 6201.607 | 97.29% | 2.601% | 0.1104% | 101.5958 | 0 | 0 | 101.5958 | 0 | 92.4508 | 1.9164 | 48.2411 | 92.4508 | 1.9164 | 48.2411 | 102.5943 | 2.1267 | 48.2411 | 1.638%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 10 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 134.4717 | 0 | 0 | 134.4717 | 0 | 122.3675 | 1.0647 | 114.9331 | 122.3675 | 1.0647 | 114.9331 | 135.7933 | 1.1815 | 114.9331 | 0.8768%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | Tier-3---3 | 46 | 2 | 2448.8293 | 98.64% | 1.317% | 0.04316% | 30.4565 | 0 | 0 | 30.4565 | 0 | 27.715 | 0.21294 | 130.1559 | 27.715 | 0.21294 | 130.1559 | 30.7558 | 0.2363 | 130.1559 | 1.244%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 313 | 7 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 67.5311 | 0 | 0 | 67.5311 | 0 | 61.4523 | 0.74528 | 82.4555 | 61.4523 | 0.74528 | 82.4555 | 68.1947 | 0.82705 | 82.4555 | 0.6376%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 273 | 1 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 9.7113 | 0 | 0 | 9.7113 | 0 | 8.8372 | 0.10647 | 83.0028 | 8.8372 | 0.10647 | 83.0028 | 9.8068 | 0.11815 | 83.0028 | 0.1046%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 13 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 84.2399 | 0 | 0 | 84.2399 | 0 | 76.6571 | 1.3841 | 55.3845 | 76.6571 | 1.3841 | 55.3845 | 85.0678 | 1.5359 | 55.3845 | 2.687%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 8 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 46.9833 | 0 | 0 | 46.9833 | 0 | 42.7542 | 0.85175 | 50.1958 | 42.7542 | 0.85175 | 50.1958 | 47.445 | 0.9452 | 50.1958 | 2.75%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 69 | 3 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 24.3957 | 0 | 0 | 24.3957 | 0 | 22.1998 | 0.31941 | 69.5035 | 22.1998 | 0.31941 | 69.5035 | 24.6355 | 0.35445 | 69.5035 | 1.259%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 44 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 87.762 | 0 | 0 | 87.762 | 0 | 79.8622 | 4.6846 | 17.0478 | 79.8622 | 4.6846 | 17.0478 | 88.6245 | 5.1986 | 17.0478 | 3.969%
2027 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 24 | 19 | 42.5113 | 97.49% | 0.5175% | 1.991% | 9.5151 | 0 | 0 | 9.5151 | 0 | 8.6586 | 2.0229 | 4.2803 | 8.6586 | 2.0229 | 4.2803 | 9.6086 | 2.2448 | 4.2803 | 22.38%
2027 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 29 | 1 | 5696.3358 | 99.98% | 0% | 0.01771% | 56.9533 | 0 | 0 | 56.9533 | 0 | 51.8267 | 0.10647 | 486.7801 | 51.8267 | 0.10647 | 486.7801 | 57.513 | 0.11815 | 486.7801 | 0.9998%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 9 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 43.1561 | 0 | 0 | 43.1561 | 0 | 39.2714 | 0.95822 | 40.9839 | 39.2714 | 0.95822 | 40.9839 | 43.5802 | 1.0633 | 40.9839 | 0.4726%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 5 | 3349.7594 | 92.58% | 7.304% | 0.116% | 31.8919 | 0 | 0 | 31.8919 | 0 | 29.0212 | 0.53234 | 54.5161 | 29.0212 | 0.53234 | 54.5161 | 32.2054 | 0.59075 | 54.5161 | 0.9521%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 198 | 1 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 17.9132 | 0 | 0 | 17.9132 | 0 | 16.3008 | 0.10647 | 153.1043 | 16.3008 | 0.10647 | 153.1043 | 18.0892 | 0.11815 | 153.1043 | 0.1454%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 4 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 13.1823 | 0 | 0 | 13.1823 | 0 | 11.9957 | 0.42587 | 28.1673 | 11.9957 | 0.42587 | 28.1673 | 13.3119 | 0.4726 | 28.1673 | 0.6316%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 10 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 10.6964 | 0 | 0 | 10.6964 | 0 | 9.7336 | 1.0647 | 9.1422 | 9.7336 | 1.0647 | 9.1422 | 10.8015 | 1.1815 | 9.1422 | 0.6656%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 1 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 20.0638 | 0 | 0 | 20.0638 | 0 | 18.2578 | 0.10647 | 171.4858 | 18.2578 | 0.10647 | 171.4858 | 20.261 | 0.11815 | 171.4858 | 0.2065%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 192 | 2 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 55.1155 | 0 | 0 | 55.1155 | 0 | 50.1544 | 0.21294 | 235.5363 | 50.1544 | 0.21294 | 235.5363 | 55.6572 | 0.2363 | 235.5363 | 0.2988%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 74 | 3 | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 29.9645 | 0 | 0 | 29.9645 | 0 | 27.2673 | 0.31941 | 85.3689 | 27.2673 | 0.31941 | 85.3689 | 30.259 | 0.35445 | 85.3689 | 1.168%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 180 | 4 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 34.3653 | 0 | 0 | 34.3653 | 0 | 31.272 | 0.42587 | 73.4302 | 31.272 | 0.42587 | 73.4302 | 34.7031 | 0.4726 | 73.4302 | 0.6207%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 8 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 99.127 | 0 | 0 | 99.127 | 0 | 90.2042 | 0.85175 | 105.9049 | 90.2042 | 0.85175 | 105.9049 | 100.1012 | 0.9452 | 105.9049 | 0.5278%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 218 | 2 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 52.7445 | 0 | 0 | 52.7445 | 0 | 47.9968 | 0.21294 | 225.404 | 47.9968 | 0.21294 | 225.404 | 53.2629 | 0.2363 | 225.404 | 0.264%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 5 | 127.4062 | 99.28% | 0% | 0.716% | 4.8267 | 0 | 0 | 4.8267 | 0 | 4.3923 | 0.53234 | 8.2508 | 4.3923 | 0.53234 | 8.2508 | 4.8742 | 0.59075 | 8.2508 | 3.788%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 3 | 12.4137 | 98.83% | 0% | 1.166% | 0.82108 | 0 | 0 | 0.82108 | 0 | 0.74717 | 0.31941 | 2.3393 | 0.74717 | 0.31941 | 2.3393 | 0.82915 | 0.35445 | 2.3393 | 6.614%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 20 | 8606.9717 | 99.86% | 0% | 0.1411% | 89.4973 | 0 | 0 | 89.4973 | 0 | 81.4413 | 2.1294 | 38.2467 | 81.4413 | 2.1294 | 38.2467 | 90.3769 | 2.363 | 38.2467 | 1.04%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 162 | 17 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 250.7168 | 0 | 0 | 250.7168 | 0 | 228.1489 | 1.81 | 126.0517 | 228.1489 | 1.81 | 126.0517 | 253.1808 | 2.0085 | 126.0517 | 2.971%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 12 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 213.4005 | 0 | 0 | 213.4005 | 0 | 194.1916 | 1.2776 | 151.9947 | 194.1916 | 1.2776 | 151.9947 | 215.4978 | 1.4178 | 151.9947 | 2.345%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 34 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 682.2757 | 0 | 0 | 682.2757 | 0 | 620.8616 | 3.6199 | 171.5123 | 620.8616 | 3.6199 | 171.5123 | 688.9811 | 4.0171 | 171.5123 | 2.521%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 26 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 385.7737 | 0 | 0 | 385.7737 | 0 | 351.0488 | 2.7682 | 126.8158 | 351.0488 | 2.7682 | 126.8158 | 389.5651 | 3.0719 | 126.8158 | 2.447%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 13 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 263.9681 | 0 | 0 | 263.9681 | 0 | 240.2074 | 1.3841 | 173.549 | 240.2074 | 1.3841 | 173.549 | 266.5624 | 1.5359 | 173.549 | 2.244%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 471 | 39 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 128.7518 | 0 | 0 | 128.7518 | 0 | 117.1624 | 4.1523 | 28.2165 | 117.1624 | 4.1523 | 28.2165 | 130.0171 | 4.6078 | 28.2165 | 2.311%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 24 | 1466.2762 | 91.81% | 7.905% | 0.289% | 62.4604 | 0 | 0 | 62.4604 | 0 | 56.8381 | 2.5552 | 22.2437 | 56.8381 | 2.5552 | 22.2437 | 63.0742 | 2.8356 | 22.2437 | 4.26%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 21 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.618 | 0 | 0 | 387.618 | 0 | 352.7271 | 2.2358 | 157.7607 | 352.7271 | 2.2358 | 157.7607 | 391.4275 | 2.4811 | 157.7607 | 4.869%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 49 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 1059.93 | 0 | 0 | 1059.93 | 0 | 964.5218 | 5.217 | 184.8823 | 964.5218 | 5.217 | 184.8823 | 1070.3469 | 5.7893 | 184.8823 | 2.569%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 162 | 10 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 60.0009 | 0 | 0 | 60.0009 | 0 | 54.6 | 1.0647 | 51.2828 | 54.6 | 1.0647 | 51.2828 | 60.5906 | 1.1815 | 51.2828 | 1.645%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 16 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 285.7812 | 0 | 0 | 285.7812 | 0 | 260.057 | 1.7035 | 152.6609 | 260.057 | 1.7035 | 152.6609 | 288.5898 | 1.8904 | 152.6609 | 1.267%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 11 | 847.524 | 96.52% | 3.329% | 0.1488% | 50.184 | 0 | 0 | 50.184 | 0 | 45.6668 | 1.1712 | 38.993 | 45.6668 | 1.1712 | 38.993 | 50.6773 | 1.2996 | 38.993 | 5.921%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 39 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 1226.0122 | 0 | 0 | 1226.0122 | 0 | 1115.6544 | 4.1523 | 268.6856 | 1115.6544 | 4.1523 | 268.6856 | 1238.0614 | 4.6078 | 268.6856 | 2.219%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 3 | 5703.0403 | 99.97% | 0% | 0.03309% | 80.0001 | 0 | 0 | 80.0001 | 0 | 72.799 | 0.31941 | 227.9204 | 72.799 | 0.31941 | 227.9204 | 80.7863 | 0.35445 | 227.9204 | 1.403%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 17 | 32313.161 | 99.26% | 0.708% | 0.02831% | 511.7508 | 0 | 0 | 511.7508 | 0 | 465.6863 | 1.81 | 257.2905 | 465.6863 | 1.81 | 257.2905 | 516.7803 | 2.0085 | 257.2905 | 1.584%
2027 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 3 | 1 | 62.9838 | 99.88% | 0% | 0.1185% | 6.0812 | 0 | 0 | 6.0812 | 0 | 5.5338 | 0.10647 | 51.9763 | 5.5338 | 0.10647 | 51.9763 | 6.141 | 0.11815 | 51.9763 | 9.655%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 194 | 11 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 20.4536 | 0 | 0 | 20.4536 | 0 | 18.6125 | 1.1712 | 15.8924 | 18.6125 | 1.1712 | 15.8924 | 20.6546 | 1.2996 | 15.8924 | 1.578%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 4 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 29.9665 | 0 | 0 | 29.9665 | 0 | 27.2691 | 0.42587 | 64.031 | 27.2691 | 0.42587 | 64.031 | 30.261 | 0.4726 | 64.031 | 0.8796%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 4 | 1554.328 | 69.02% | 30.62% | 0.3611% | 4.2185 | 0 | 0 | 4.2185 | 0 | 3.8388 | 0.42587 | 9.014 | 3.8388 | 0.42587 | 9.014 | 4.26 | 0.4726 | 9.014 | 0.2714%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 252 | 1 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 1.7559 | 0 | 0 | 1.7559 | 0 | 1.5978 | 0.10647 | 15.0073 | 1.5978 | 0.10647 | 15.0073 | 1.7731 | 0.11815 | 15.0073 | 0.08816%
2027 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 4 | 62.492 | 96.91% | 0.773% | 2.32% | 1.5966 | 0 | 0 | 1.5966 | 0 | 1.4529 | 0.42587 | 3.4115 | 1.4529 | 0.42587 | 3.4115 | 1.6123 | 0.4726 | 3.4115 | 2.555%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 2 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 81.435 | 0 | 0 | 81.435 | 0 | 74.1047 | 0.21294 | 348.0127 | 74.1047 | 0.21294 | 348.0127 | 82.2353 | 0.2363 | 348.0127 | 0.6283%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 5 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 63.2491 | 0 | 0 | 63.2491 | 0 | 57.5558 | 0.53234 | 108.1181 | 57.5558 | 0.53234 | 108.1181 | 63.8707 | 0.59075 | 108.1181 | 0.4175%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 13 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 177.9212 | 0 | 0 | 177.9212 | 0 | 161.9059 | 1.3841 | 116.9765 | 161.9059 | 1.3841 | 116.9765 | 179.6698 | 1.5359 | 116.9765 | 0.6246%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 106 | 2 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 43.6232 | 0 | 0 | 43.6232 | 0 | 39.6965 | 0.21294 | 186.4239 | 39.6965 | 0.21294 | 186.4239 | 44.0519 | 0.2363 | 186.4239 | 0.5442%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 1 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 21.6522 | 0 | 0 | 21.6522 | 0 | 19.7032 | 0.10647 | 185.0618 | 19.7032 | 0.10647 | 185.0618 | 21.865 | 0.11815 | 185.0618 | 0.4976%
2027 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 1 | 191.8954 | 99.94% | 0% | 0.06293% | 27.8073 | 0 | 0 | 27.8073 | 0 | 25.3043 | 0.10647 | 237.6694 | 25.3043 | 0.10647 | 237.6694 | 28.0806 | 0.11815 | 237.6694 | 14.49%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 29 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 435.1349 | 0 | 0 | 435.1349 | 0 | 395.9668 | 3.0876 | 128.2449 | 395.9668 | 3.0876 | 128.2449 | 439.4113 | 3.4263 | 128.2449 | 2.946%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 406 | 3 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 23.8987 | 0 | 0 | 23.8987 | 0 | 21.7475 | 0.31941 | 68.0876 | 21.7475 | 0.31941 | 68.0876 | 24.1336 | 0.35445 | 68.0876 | 0.2121%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 46 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 440.8303 | 0 | 0 | 440.8303 | 0 | 401.1496 | 4.8975 | 81.9083 | 401.1496 | 4.8975 | 81.9083 | 445.1628 | 5.4349 | 81.9083 | 1.883%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 543 | 39 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 465.2407 | 0 | 0 | 465.2407 | 0 | 423.3627 | 4.1523 | 101.9594 | 423.3627 | 4.1523 | 101.9594 | 469.8131 | 4.6078 | 101.9594 | 2.03%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 6 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 45.1975 | 0 | 0 | 45.1975 | 0 | 41.1291 | 0.63881 | 64.3839 | 41.1291 | 0.63881 | 64.3839 | 45.6417 | 0.7089 | 64.3839 | 0.8729%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 389 | 8 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 19.5176 | 0 | 0 | 19.5176 | 0 | 17.7608 | 0.85175 | 20.8522 | 17.7608 | 0.85175 | 20.8522 | 19.7094 | 0.9452 | 20.8522 | 0.5588%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 2 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 30.6233 | 0 | 0 | 30.6233 | 0 | 27.8668 | 0.21294 | 130.8686 | 27.8668 | 0.21294 | 130.8686 | 30.9242 | 0.2363 | 130.8686 | 0.4309%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 30 | 2 | 6417.0381 | 80.3% | 19.69% | 0.01691% | 99.619 | 0 | 0 | 99.619 | 0 | 90.6519 | 0.21294 | 425.722 | 90.6519 | 0.21294 | 425.722 | 100.598 | 0.2363 | 425.722 | 1.552%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 7 | 626.8618 | 65.87% | 33.98% | 0.153% | 28.9034 | 0 | 0 | 28.9034 | 0 | 26.3017 | 0.74528 | 35.2911 | 26.3017 | 0.74528 | 35.2911 | 29.1875 | 0.82705 | 35.2911 | 4.611%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 26 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 209.956 | 0 | 0 | 209.956 | 0 | 191.0571 | 2.7682 | 69.0191 | 191.0571 | 2.7682 | 69.0191 | 212.0194 | 3.0719 | 69.0191 | 4.587%
2027 | CB 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 111 | 7 | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 25.7709 | 0 | 0 | 25.7709 | 0 | 23.4512 | 0.74528 | 31.4663 | 23.4512 | 0.74528 | 31.4663 | 26.0242 | 0.82705 | 31.4663 | 1.822%
2027 | CB 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 5 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 39.9671 | 0 | 0 | 39.9671 | 0 | 36.3695 | 0.53234 | 68.3199 | 36.3695 | 0.53234 | 68.3199 | 40.3599 | 0.59075 | 68.3199 | 3.527%
2027 | CB 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 2 | 1646.9837 | 34.54% | 65.41% | 0.04829% | 13.7464 | 0 | 0 | 13.7464 | 0 | 12.509 | 0.21294 | 58.7451 | 12.509 | 0.21294 | 58.7451 | 13.8815 | 0.2363 | 58.7451 | 0.8346%
2027 | CB 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 6 | 765.4961 | 75% | 24.28% | 0.7274% | 3.4327 | 0 | 0 | 3.4327 | 0 | 3.1237 | 0.63881 | 4.8899 | 3.1237 | 0.63881 | 4.8899 | 3.4664 | 0.7089 | 4.8899 | 0.4484%
2027 | CB 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 34 | 2 | 75.2008 | 96.65% | 1.975% | 1.378% | 1.2398 | 0 | 0 | 1.2398 | 0 | 1.1282 | 0.21294 | 5.2984 | 1.1282 | 0.21294 | 5.2984 | 1.252 | 0.2363 | 5.2984 | 1.649%
2027 | CB 1180 | CB 1180 | Tier-1 | Non-HFTD---7 | Non-HFTD---17 | 39 | 4 | 35.2333 | 97.75% | 0% | 2.252% | 1.0244 | 0 | 0 | 1.0244 | 0 | 0.93216 | 0.42587 | 2.1888 | 0.93216 | 0.42587 | 2.1888 | 1.0344 | 0.4726 | 2.1888 | 2.907%
2027 | CB 120 | CB 120 | Tier-1 | Non-HFTD---5 | Non-HFTD---13 | 18 | 4 | 72.8901 | 46.84% | 52.05% | 1.107% | 2.2004 | 0 | 0 | 2.2004 | 0 | 2.0023 | 0.42587 | 4.7016 | 2.0023 | 0.42587 | 4.7016 | 2.222 | 0.4726 | 4.7016 | 3.019%
2027 | CB 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 23 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 147.8471 | 0 | 0 | 147.8471 | 0 | 134.5389 | 2.4488 | 54.9413 | 134.5389 | 2.4488 | 54.9413 | 149.3002 | 2.7174 | 54.9413 | 2.343%
2027 | CB 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 31 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 95.1787 | 0 | 0 | 95.1787 | 0 | 86.6113 | 3.3005 | 26.2417 | 86.6113 | 3.3005 | 26.2417 | 96.1141 | 3.6626 | 26.2417 | 1.432%
2027 | CB 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 8 | 1438.3629 | 99.75% | 0% | 0.2509% | 28.6951 | 0 | 0 | 28.6951 | 0 | 26.1121 | 0.85175 | 30.6571 | 26.1121 | 0.85175 | 30.6571 | 28.9771 | 0.9452 | 30.6571 | 1.995%
2027 | CB 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 1 | 41.7756 | 94.08% | 0% | 5.924% | 0.14996 | 0 | 0 | 0.14996 | 0 | 0.13647 | 0.10647 | 1.2817 | 0.13647 | 0.10647 | 1.2817 | 0.15144 | 0.11815 | 1.2817 | 0.359%
2027 | CB 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | Non-HFTD---22 | 16 | 2 | 4.2012 | 88.77% | 0% | 11.23% | 0.1352 | 0 | 0 | 0.1352 | 0 | 0.12303 | 0.21294 | 0.57776 | 0.12303 | 0.21294 | 0.57776 | 0.13653 | 0.2363 | 0.57776 | 3.218%
2027 | CB 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 184 | 4 | 259.6903 | 35.49% | 63.12% | 1.387% | 0.58108 | 0 | 0 | 0.58108 | 0 | 0.52877 | 0.42587 | 1.2416 | 0.52877 | 0.42587 | 1.2416 | 0.58679 | 0.4726 | 1.2416 | 0.2238%
2027 | CB 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 478 | 17 | 1342.6559 | 29.9% | 69.37% | 0.7369% | 4.14 | 0 | 0 | 4.14 | 0 | 3.7673 | 1.81 | 2.0814 | 3.7673 | 1.81 | 2.0814 | 4.1807 | 2.0085 | 2.0814 | 0.3083%
2027 | CB 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 18 | 133.9861 | 95.12% | 0% | 4.877% | 3.4471 | 0 | 0 | 3.4471 | 0 | 3.1368 | 1.9164 | 1.6368 | 3.1368 | 1.9164 | 1.6368 | 3.481 | 2.1267 | 1.6368 | 2.573%
2027 | CB 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 233 | 9 | 195.752 | 9.583% | 88.23% | 2.187% | 0.21014 | 0 | 0 | 0.21014 | 0 | 0.19122 | 0.95822 | 0.19956 | 0.19122 | 0.95822 | 0.19956 | 0.21221 | 1.0633 | 0.19956 | 0.1074%
2027 | CB 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 229 | 33 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 35.7868 | 0 | 0 | 35.7868 | 0 | 32.5655 | 3.5135 | 9.2688 | 32.5655 | 3.5135 | 9.2688 | 36.1385 | 3.8989 | 9.2688 | 3.378%
2027 | CB 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 24 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 66.4446 | 0 | 0 | 66.4446 | 0 | 60.4637 | 2.5552 | 23.6626 | 60.4637 | 2.5552 | 23.6626 | 67.0976 | 2.8356 | 23.6626 | 2.658%
2027 | CB 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 259 | 14 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 25.0727 | 0 | 0 | 25.0727 | 0 | 22.8158 | 1.4906 | 15.3069 | 22.8158 | 1.4906 | 15.3069 | 25.3191 | 1.6541 | 15.3069 | 1.526%
2027 | CB 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 613 | 45 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 86.7642 | 0 | 0 | 86.7642 | 0 | 78.9542 | 4.7911 | 16.4794 | 78.9542 | 4.7911 | 16.4794 | 87.6169 | 5.3167 | 16.4794 | 2.102%
2027 | CB 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 38 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 101.9928 | 0 | 0 | 101.9928 | 0 | 92.8121 | 4.0458 | 22.9404 | 92.8121 | 4.0458 | 22.9404 | 102.9952 | 4.4897 | 22.9404 | 3.096%
2027 | CB 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 18 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 192.2045 | 0 | 0 | 192.2045 | 0 | 174.9034 | 1.9164 | 91.2652 | 174.9034 | 1.9164 | 91.2652 | 194.0934 | 2.1267 | 91.2652 | 1.512%
2027 | CB 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 17 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 25.555 | 0 | 0 | 25.555 | 0 | 23.2547 | 1.81 | 12.8482 | 23.2547 | 1.81 | 12.8482 | 25.8062 | 2.0085 | 12.8482 | 2.023%
2027 | CB 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 1 | 406.8184 | 64.36% | 35.02% | 0.6193% | 0.8728 | 0 | 0 | 0.8728 | 0 | 0.79424 | 0.10647 | 7.4599 | 0.79424 | 0.10647 | 7.4599 | 0.88138 | 0.11815 | 7.4599 | 0.2145%
2027 | CB 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 197 | 1 | 295.5508 | 37.5% | 61.39% | 1.106% | 0.16317 | 0 | 0 | 0.16317 | 0 | 0.14848 | 0.10647 | 1.3946 | 0.14848 | 0.10647 | 1.3946 | 0.16477 | 0.11815 | 1.3946 | 0.05521%
2027 | CB 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 23 | 1438.4419 | 90% | 9.47% | 0.5268% | 28.4992 | 0 | 0 | 28.4992 | 0 | 25.9339 | 2.4488 | 10.5906 | 25.9339 | 2.4488 | 10.5906 | 28.7793 | 2.7174 | 10.5906 | 1.981%
2027 | CB 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 6 | 379.7423 | 70.28% | 29.01% | 0.71% | 5.1597 | 0 | 0 | 5.1597 | 0 | 4.6953 | 0.63881 | 7.35 | 4.6953 | 0.63881 | 7.35 | 5.2104 | 0.7089 | 7.35 | 1.359%
2027 | CB 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 101 | 13 | 826.9208 | 97.04% | 2.672% | 0.2884% | 29.9524 | 0 | 0 | 29.9524 | 0 | 27.2563 | 1.3841 | 19.6926 | 27.2563 | 1.3841 | 19.6926 | 30.2468 | 1.5359 | 19.6926 | 3.622%
2027 | CB 275 | CB 275 | Tier-1 | Non-HFTD---2 | Non-HFTD---9 | 66 | 2 | 206.6235 | 45.85% | 53.34% | 0.8107% | 0.83253 | 0 | 0 | 0.83253 | 0 | 0.7576 | 0.21294 | 3.5578 | 0.7576 | 0.21294 | 3.5578 | 0.84072 | 0.2363 | 3.5578 | 0.4029%
2027 | CB 276 | CB 276 | Tier-1 | Non-HFTD---10 | Non-HFTD---16 | 28 | 2 | 26.0793 | 53.94% | 42.4% | 3.659% | 0.29141 | 0 | 0 | 0.29141 | 0 | 0.26518 | 0.21294 | 1.2453 | 0.26518 | 0.21294 | 1.2453 | 0.29428 | 0.2363 | 1.2453 | 1.117%
2027 | CB 277 | CB 277 | Tier-1 | Non-HFTD---11 | Non-HFTD---17 | 11 | 1 | 9.2421 | 96.22% | 0% | 3.783% | 0.23444 | 0 | 0 | 0.23444 | 0 | 0.21333 | 0.10647 | 2.0037 | 0.21333 | 0.10647 | 2.0037 | 0.23674 | 0.11815 | 2.0037 | 2.537%
2027 | CB 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 17 | 1 | 94.6686 | 66.47% | 32.93% | 0.6021% | 1.0735 | 0 | 0 | 1.0735 | 0 | 0.97685 | 0.10647 | 9.1751 | 0.97685 | 0.10647 | 9.1751 | 1.084 | 0.11815 | 9.1751 | 1.134%
2027 | CB 305 | CB 305 | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 170 | 6 | 2786.7739 | 97.11% | 2.732% | 0.1605% | 27.6983 | 0 | 0 | 27.6983 | 0 | 25.2051 | 0.63881 | 39.4563 | 25.2051 | 0.63881 | 39.4563 | 27.9705 | 0.7089 | 39.4563 | 0.9939%
2027 | CB 306 | CB 306 | Tier-1 | Non-HFTD---1 | Non-HFTD---4 | 46 | 1 | 737.4997 | 97.09% | 2.802% | 0.1119% | 4.514 | 0 | 0 | 4.514 | 0 | 4.1076 | 0.10647 | 38.5809 | 4.1076 | 0.10647 | 38.5809 | 4.5583 | 0.11815 | 38.5809 | 0.6121%
2027 | CB 307 | CB 307 | Tier-1 | Non-HFTD---1 | Non-HFTD---4 | 30 | 4 | 601.8674 | 89.73% | 10.15% | 0.1197% | 20.883 | 0 | 0 | 20.883 | 0 | 19.0032 | 0.42587 | 44.6218 | 19.0032 | 0.42587 | 44.6218 | 21.0882 | 0.4726 | 44.6218 | 3.47%
2027 | CB 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 156 | 16 | 124.2501 | 33.35% | 64.03% | 2.615% | 1.2326 | 0 | 0 | 1.2326 | 0 | 1.1217 | 1.7035 | 0.65846 | 1.1217 | 1.7035 | 0.65846 | 1.2448 | 1.8904 | 0.65846 | 0.9921%
2027 | CB 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 4 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 109.6001 | 0 | 0 | 109.6001 | 0 | 99.7346 | 0.42587 | 234.1883 | 99.7346 | 0.42587 | 234.1883 | 110.6773 | 0.4726 | 234.1883 | 0.7507%
2027 | CB 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 38 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 407.1211 | 0 | 0 | 407.1211 | 0 | 370.4746 | 4.0458 | 91.5702 | 370.4746 | 4.0458 | 91.5702 | 411.1223 | 4.4897 | 91.5702 | 3.607%
2027 | CB 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 13 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 136.531 | 0 | 0 | 136.531 | 0 | 124.2413 | 1.3841 | 89.764 | 124.2413 | 1.3841 | 89.764 | 137.8728 | 1.5359 | 89.764 | 2.234%
2027 | CB 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 94 | 1 | 1133.0808 | 94.08% | 5.666% | 0.2577% | 3.2886 | 0 | 0 | 3.2886 | 0 | 2.9926 | 0.10647 | 28.1076 | 2.9926 | 0.10647 | 28.1076 | 3.3209 | 0.11815 | 28.1076 | 0.2902%
2027 | CB 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 36 | 10 | 67.1473 | 98.29% | 0% | 1.71% | 5.3166 | 0 | 0 | 5.3166 | 0 | 4.838 | 1.0647 | 4.5441 | 4.838 | 1.0647 | 4.5441 | 5.3688 | 1.1815 | 4.5441 | 7.918%
2027 | CB 461 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 36 | 2 | 101.8709 | 98.65% | 0% | 1.347% | 1.6191 | 0 | 0 | 1.6191 | 0 | 1.4734 | 0.21294 | 6.9194 | 1.4734 | 0.21294 | 6.9194 | 1.6351 | 0.2363 | 6.9194 | 1.589%
2027 | CB 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 2 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 10.0618 | 0 | 0 | 10.0618 | 0 | 9.1561 | 0.21294 | 42.9991 | 9.1561 | 0.21294 | 42.9991 | 10.1607 | 0.2363 | 42.9991 | 0.1454%
2027 | CB 474 | CB 474 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 170 | 10 | 794.8798 | 99.6% | 0% | 0.3957% | 13.5061 | 0 | 0 | 13.5061 | 0 | 12.2903 | 1.0647 | 11.5436 | 12.2903 | 1.0647 | 11.5436 | 13.6388 | 1.1815 | 11.5436 | 1.699%
2027 | CB 492 | CB 492 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 98 | 2 | 147.6974 | 50.2% | 48.6% | 1.193% | 0.43885 | 0 | 0 | 0.43885 | 0 | 0.39934 | 0.21294 | 1.8754 | 0.39934 | 0.21294 | 1.8754 | 0.44316 | 0.2363 | 1.8754 | 0.2971%
2027 | CB 493 | CB 493 | Tier-1 | Non-HFTD---17 | Non-HFTD---24 | 8 | 1 | 1.0505 | 81.53% | 0% | 18.47% | 0.031047 | 0 | 0 | 0.031047 | 0 | 0.028252 | 0.10647 | 0.26536 | 0.028252 | 0.10647 | 0.26536 | 0.031352 | 0.11815 | 0.26536 | 2.955%
2027 | CB 511 | CB 511 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 40 | 1 | 163.9412 | 95.95% | 3.193% | 0.8556% | 1.1405 | 0 | 0 | 1.1405 | 0 | 1.0378 | 0.10647 | 9.7475 | 1.0378 | 0.10647 | 9.7475 | 1.1517 | 0.11815 | 9.7475 | 0.6956%
2027 | CB 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 14 | 1 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.042728 | 0 | 0 | 0.042728 | 0 | 0.038882 | 0.10647 | 0.3652 | 0.038882 | 0.10647 | 0.3652 | 0.043148 | 0.11815 | 0.3652 | 0.3479%
2027 | CB 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 38 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 41.8788 | 0 | 0 | 41.8788 | 0 | 38.1091 | 4.0458 | 9.4194 | 38.1091 | 4.0458 | 9.4194 | 42.2904 | 4.4897 | 9.4194 | 3.898%
2027 | CB 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 26 | 305.5692 | 37.2% | 61.32% | 1.484% | 3.309 | 0 | 0 | 3.309 | 0 | 3.0111 | 2.7682 | 1.0878 | 3.0111 | 2.7682 | 1.0878 | 3.3415 | 3.0719 | 1.0878 | 1.083%
2027 | CB 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 90 | 3 | 481.3309 | 94.25% | 5.298% | 0.4514% | 4.3853 | 0 | 0 | 4.3853 | 0 | 3.9906 | 0.31941 | 12.4939 | 3.9906 | 0.31941 | 12.4939 | 4.4284 | 0.35445 | 12.4939 | 0.9111%
2027 | CB 589 | CB 589 | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 31 | 3 | 115.513 | 99.19% | 0% | 0.8071% | 3.2157 | 0 | 0 | 3.2157 | 0 | 2.9262 | 0.31941 | 9.1614 | 2.9262 | 0.31941 | 9.1614 | 3.2473 | 0.35445 | 9.1614 | 2.784%
2027 | CB 59 | CB 59 | Tier-1 | Non-HFTD---5 | Non-HFTD---13 | 11 | 1 | 54.4254 | 99.08% | 0.2847% | 0.6369% | 1.4216 | 0 | 0 | 1.4216 | 0 | 1.2937 | 0.10647 | 12.1507 | 1.2937 | 0.10647 | 12.1507 | 1.4356 | 0.11815 | 12.1507 | 2.612%
2027 | CB 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 49 | 4323.2442 | 99.81% | 0% | 0.1903% | 166.1691 | 0 | 0 | 166.1691 | 0 | 151.2116 | 5.217 | 28.9847 | 151.2116 | 5.217 | 28.9847 | 167.8022 | 5.7893 | 28.9847 | 3.844%
2027 | CB 65 | CB 65 | Tier-1 | Non-HFTD---2 | Non-HFTD---9 | 188 | 6 | 189.2656 | 62.06% | 35.57% | 2.376% | 1.0871 | 0 | 0 | 1.0871 | 0 | 0.98923 | 0.63881 | 1.5485 | 0.98923 | 0.63881 | 1.5485 | 1.0978 | 0.7089 | 1.5485 | 0.5744%
2027 | CB 702 | CB 702 | Tier-1 | Non-HFTD---5 | Non-HFTD---13 | 21 | 2 | 63.7539 | 98.86% | 0% | 1.141% | 1.7407 | 0 | 0 | 1.7407 | 0 | 1.584 | 0.21294 | 7.439 | 1.584 | 0.21294 | 7.439 | 1.7578 | 0.2363 | 7.439 | 2.73%
2027 | CB 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 3 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 10.0109 | 0 | 0 | 10.0109 | 0 | 9.1098 | 0.31941 | 28.5212 | 9.1098 | 0.31941 | 28.5212 | 10.1093 | 0.35445 | 28.5212 | 0.1168%
2027 | CB 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 2 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 31.135 | 0 | 0 | 31.135 | 0 | 28.3325 | 0.21294 | 133.0557 | 28.3325 | 0.21294 | 133.0557 | 31.441 | 0.2363 | 133.0557 | 1.135%
2027 | CB 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 4 | 337.7351 | 93.43% | 6.078% | 0.496% | 5.3826 | 0 | 0 | 5.3826 | 0 | 4.8981 | 0.42587 | 11.5013 | 4.8981 | 0.42587 | 11.5013 | 5.4355 | 0.4726 | 11.5013 | 1.594%
2027 | CB 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 3 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 59.3912 | 0 | 0 | 59.3912 | 0 | 54.0451 | 0.31941 | 169.2056 | 54.0451 | 0.31941 | 169.2056 | 59.9748 | 0.35445 | 169.2056 | 0.5184%
2027 | CB 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 11 | 1 | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 34.2205 | 0 | 0 | 34.2205 | 0 | 31.1402 | 0.10647 | 292.4831 | 31.1402 | 0.10647 | 292.4831 | 34.5568 | 0.11815 | 292.4831 | 2.624%
2027 | CB 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 35 | 1 | 387.8494 | 99.7% | 0% | 0.3041% | 3.2038 | 0 | 0 | 3.2038 | 0 | 2.9154 | 0.10647 | 27.3832 | 2.9154 | 0.10647 | 27.3832 | 3.2353 | 0.11815 | 27.3832 | 0.8261%
2027 | CB CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 6 | 2 | 27.4807 | 90.21% | 9.514% | 0.2799% | 2.3963 | 0 | 0 | 2.3963 | 0 | 2.1806 | 0.21294 | 10.2405 | 2.1806 | 0.21294 | 10.2405 | 2.4198 | 0.2363 | 10.2405 | 8.72%
2027 | CB FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 21 | 346.5871 | 36.93% | 61.45% | 1.621% | 2.101 | 0 | 0 | 2.101 | 0 | 1.9118 | 2.2358 | 0.85509 | 1.9118 | 2.2358 | 0.85509 | 2.1216 | 2.4811 | 0.85509 | 0.6062%
2027 | CB FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 22 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 35.8162 | 0 | 0 | 35.8162 | 0 | 32.5923 | 2.3423 | 13.9146 | 32.5923 | 2.3423 | 13.9146 | 36.1682 | 2.5993 | 13.9146 | 3.479%
2027 | CB JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 80 | 1 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 5.4329 | 0 | 0 | 5.4329 | 0 | 4.9439 | 0.10647 | 46.4354 | 4.9439 | 0.10647 | 46.4354 | 5.4863 | 0.11815 | 46.4354 | 0.3547%
2027 | CB MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 116 | 8 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 100.9158 | 0 | 0 | 100.9158 | 0 | 91.832 | 0.85175 | 107.816 | 91.832 | 0.85175 | 107.816 | 101.9076 | 0.9452 | 107.816 | 1.971%
2027 | CB OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 190 | 3 | 6915.6819 | 99% | 0.9206% | 0.07911% | 31.35 | 0 | 0 | 31.35 | 0 | 28.5281 | 0.31941 | 89.3162 | 28.5281 | 0.31941 | 89.3162 | 31.6581 | 0.35445 | 89.3162 | 0.4533%
2027 | CB PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 247 | 7 | 3027.5479 | 94.73% | 5.109% | 0.164% | 23.5702 | 0 | 0 | 23.5702 | 0 | 21.4485 | 0.74528 | 28.7792 | 21.4485 | 0.74528 | 28.7792 | 23.8018 | 0.82705 | 28.7792 | 0.7785%
2027 | CB RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 23 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 195.3569 | 0 | 0 | 195.3569 | 0 | 177.7721 | 2.4488 | 72.5964 | 177.7721 | 2.4488 | 72.5964 | 197.2768 | 2.7174 | 72.5964 | 1.858%
2027 | CB RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 3 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 37.8318 | 0 | 0 | 37.8318 | 0 | 34.4264 | 0.31941 | 107.7829 | 34.4264 | 0.31941 | 107.7829 | 38.2036 | 0.35445 | 107.7829 | 0.7234%
2027 | CB RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 5 | 916.1972 | 69.5% | 30.07% | 0.4286% | 3.831 | 0 | 0 | 3.831 | 0 | 3.4861 | 0.53234 | 6.5487 | 3.4861 | 0.53234 | 6.5487 | 3.8686 | 0.59075 | 6.5487 | 0.4181%
2027 | CB RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 16 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.0145 | 0 | 0 | 183.0145 | 0 | 166.5407 | 1.7035 | 97.7641 | 166.5407 | 1.7035 | 97.7641 | 184.8131 | 1.8904 | 97.7641 | 4.894%
2027 | CB SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 225 | 27 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 109.6294 | 0 | 0 | 109.6294 | 0 | 99.7613 | 2.8746 | 34.7038 | 99.7613 | 2.8746 | 34.7038 | 110.7068 | 3.19 | 34.7038 | 3.261%
2027 | CB SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 220 | 9 | 94.186 | 2.003% | 94.63% | 3.363% | 0.022382 | 0 | 0 | 0.022382 | 0 | 0.020367 | 0.95822 | 0.021256 | 0.020367 | 0.95822 | 0.021256 | 0.022602 | 1.0633 | 0.021256 | 0.02376%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 18 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 27.0729 | 0 | 0 | 27.0729 | 0 | 24.636 | 1.9164 | 12.8551 | 24.636 | 1.9164 | 12.8551 | 27.339 | 2.1267 | 12.8551 | 1.312%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 235 | 10 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 43.6804 | 0 | 0 | 43.6804 | 0 | 39.7485 | 1.0647 | 37.3337 | 39.7485 | 1.0647 | 37.3337 | 44.1097 | 1.1815 | 37.3337 | 1.174%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 29 | 6920.124 | 97.57% | 2.306% | 0.1195% | 131.1468 | 0 | 0 | 131.1468 | 0 | 119.3418 | 3.0876 | 38.6522 | 119.3418 | 3.0876 | 38.6522 | 132.4357 | 3.4263 | 38.6522 | 1.895%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 125 | 1 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 13.7015 | 0 | 0 | 13.7015 | 0 | 12.4682 | 0.10647 | 117.107 | 12.4682 | 0.10647 | 117.107 | 13.8362 | 0.11815 | 117.107 | 0.2304%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 103 | 3 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 31.7862 | 0 | 0 | 31.7862 | 0 | 28.925 | 0.31941 | 90.5591 | 28.925 | 0.31941 | 90.5591 | 32.0986 | 0.35445 | 90.5591 | 0.8403%
2028 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 1 | 2758.283 | 96.49% | 3.415% | 0.0991% | 7.4211 | 0 | 0 | 7.4211 | 0 | 6.442 | 0.10156 | 63.4279 | 6.442 | 0.10156 | 63.4279 | 7.5307 | 0.11873 | 63.4279 | 0.269%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 4 | 1 | 117.1572 | 99.03% | 0.8725% | 0.09309% | 8.4119 | 0 | 0 | 8.4119 | 0 | 7.3021 | 0.10156 | 71.8964 | 7.3021 | 0.10156 | 71.8964 | 8.5362 | 0.11873 | 71.8964 | 7.18%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 10 | 6 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 70.5717 | 0 | 0 | 70.5717 | 0 | 61.2608 | 0.60938 | 100.5295 | 61.2608 | 0.60938 | 100.5295 | 71.6146 | 0.71237 | 100.5295 | 17.25%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 26 | 4222.2471 | 91.41% | 8.486% | 0.103% | 199.3237 | 0 | 0 | 199.3237 | 0 | 173.026 | 2.6407 | 65.5239 | 173.026 | 2.6407 | 65.5239 | 202.2693 | 3.087 | 65.5239 | 4.721%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 60 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1173.8765 | 0 | 0 | 1173.8765 | 0 | 1019.0013 | 6.0938 | 167.2189 | 1019.0013 | 6.0938 | 167.2189 | 1191.2242 | 7.1237 | 167.2189 | 3.339%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 6 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 141.7996 | 0 | 0 | 141.7996 | 0 | 123.0913 | 0.60938 | 201.9938 | 123.0913 | 0.60938 | 201.9938 | 143.8951 | 0.71237 | 201.9938 | 2.01%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 16 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 518.3813 | 0 | 0 | 518.3813 | 0 | 449.9888 | 1.625 | 276.9131 | 449.9888 | 1.625 | 276.9131 | 526.042 | 1.8997 | 276.9131 | 2.754%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 69 | 21 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 442.1405 | 0 | 0 | 442.1405 | 0 | 383.8068 | 2.1328 | 179.9514 | 383.8068 | 2.1328 | 179.9514 | 448.6745 | 2.4933 | 179.9514 | 8.782%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 13 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 264.8093 | 0 | 0 | 264.8093 | 0 | 229.8718 | 1.3203 | 174.1021 | 229.8718 | 1.3203 | 174.1021 | 268.7227 | 1.5435 | 174.1021 | 2.702%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 9 | 2 | 694.7204 | 99.22% | 0.7469% | 0.03547% | 44.4206 | 0 | 0 | 44.4206 | 0 | 38.56 | 0.20313 | 189.8315 | 38.56 | 0.20313 | 189.8315 | 45.077 | 0.23746 | 189.8315 | 6.394%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 6 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 98.3314 | 0 | 0 | 98.3314 | 0 | 85.3581 | 0.60938 | 140.0732 | 85.3581 | 0.60938 | 140.0732 | 99.7845 | 0.71237 | 140.0732 | 1.939%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 50 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 281.0034 | 0 | 0 | 281.0034 | 0 | 243.9293 | 5.0782 | 48.0348 | 243.9293 | 5.0782 | 48.0348 | 285.1561 | 5.9365 | 48.0348 | 2.967%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 49 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 137.4389 | 0 | 0 | 137.4389 | 0 | 119.3059 | 4.9766 | 23.9733 | 119.3059 | 4.9766 | 23.9733 | 139.47 | 5.8177 | 23.9733 | 3.642%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 4 | 585.5086 | 87.68% | 11.85% | 0.4758% | 5.0042 | 0 | 0 | 5.0042 | 0 | 4.344 | 0.40625 | 10.6927 | 4.344 | 0.40625 | 10.6927 | 5.0782 | 0.47492 | 10.6927 | 0.8547%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 85 | 4 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 68.7132 | 0 | 0 | 68.7132 | 0 | 59.6476 | 0.40625 | 146.8231 | 59.6476 | 0.40625 | 146.8231 | 69.7287 | 0.47492 | 146.8231 | 1.341%
2028 | 1030 | 1030-1735F | Tier-3 | missing | missing | 6 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.10156 | 0 | 0 | 0.10156 | 0 | 0 | 0.11873 | 0 | 0%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 8 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 140.0455 | 0 | 0 | 140.0455 | 0 | 121.5686 | 0.81251 | 149.6213 | 121.5686 | 0.81251 | 149.6213 | 142.1151 | 0.94983 | 149.6213 | 1.185%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 20 | 2 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 62.0329 | 0 | 0 | 62.0329 | 0 | 53.8486 | 0.20313 | 265.0978 | 53.8486 | 0.20313 | 265.0978 | 62.9496 | 0.23746 | 265.0978 | 2.884%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 5 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 99.1741 | 0 | 0 | 99.1741 | 0 | 86.0896 | 0.50782 | 169.5284 | 86.0896 | 0.50782 | 169.5284 | 100.6397 | 0.59365 | 169.5284 | 0.3917%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 28 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 481.2004 | 0 | 0 | 481.2004 | 0 | 417.7133 | 2.8438 | 146.8866 | 417.7133 | 2.8438 | 146.8866 | 488.3116 | 3.3244 | 146.8866 | 1.694%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 19 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 345.6366 | 0 | 0 | 345.6366 | 0 | 300.0351 | 1.9297 | 155.482 | 300.0351 | 1.9297 | 155.482 | 350.7444 | 2.2559 | 155.482 | 1.295%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 37 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 312.4738 | 0 | 0 | 312.4738 | 0 | 271.2476 | 3.7579 | 72.1815 | 271.2476 | 3.7579 | 72.1815 | 317.0915 | 4.393 | 72.1815 | 1.958%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 44 | 1 | 730.5479 | 99.24% | 0.5863% | 0.172% | 4.7785 | 0 | 0 | 4.7785 | 0 | 4.148 | 0.10156 | 40.8416 | 4.148 | 0.10156 | 40.8416 | 4.8491 | 0.11873 | 40.8416 | 0.6541%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 122 | 2 | 919.3728 | 93.93% | 5.62% | 0.4487% | 4.1055 | 0 | 0 | 4.1055 | 0 | 3.5639 | 0.20313 | 17.545 | 3.5639 | 0.20313 | 17.545 | 4.1662 | 0.23746 | 17.545 | 0.4466%
2028 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 3 | 509.5021 | 91.97% | 7.519% | 0.512% | 5.0958 | 0 | 0 | 5.0958 | 0 | 4.4235 | 0.30469 | 14.518 | 4.4235 | 0.30469 | 14.518 | 5.1711 | 0.35619 | 14.518 | 1%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | Tier-2---7 | 29 | 4 | 140.8367 | 88.02% | 11.68% | 0.2956% | 4.9585 | 0 | 0 | 4.9585 | 0 | 4.3043 | 0.40625 | 10.5952 | 4.3043 | 0.40625 | 10.5952 | 5.0318 | 0.47492 | 10.5952 | 3.521%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 317 | 24 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 129.0268 | 0 | 0 | 129.0268 | 0 | 112.0037 | 2.4375 | 45.9497 | 112.0037 | 2.4375 | 45.9497 | 130.9335 | 2.8495 | 45.9497 | 2.187%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 19 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 85.347 | 0 | 0 | 85.347 | 0 | 74.0867 | 1.9297 | 38.3927 | 74.0867 | 1.9297 | 38.3927 | 86.6082 | 2.2559 | 38.3927 | 1.71%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 6 | 2514.2831 | 99.84% | 0% | 0.1648% | 26.1535 | 0 | 0 | 26.1535 | 0 | 22.703 | 0.60938 | 37.2558 | 22.703 | 0.60938 | 37.2558 | 26.54 | 0.71237 | 37.2558 | 1.04%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 65 | 2 | 95.3301 | 98.77% | 0% | 1.235% | 0.84013 | 0 | 0 | 0.84013 | 0 | 0.72929 | 0.20313 | 3.5903 | 0.72929 | 0.20313 | 3.5903 | 0.85255 | 0.23746 | 3.5903 | 0.8813%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 12 | 5 | 417.0013 | 94.5% | 5.418% | 0.08666% | 47.6142 | 0 | 0 | 47.6142 | 0 | 41.3322 | 0.50782 | 81.3917 | 41.3322 | 0.50782 | 81.3917 | 48.3178 | 0.59365 | 81.3917 | 11.42%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 73 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 111.9019 | 0 | 0 | 111.9019 | 0 | 97.1381 | 7.4141 | 13.1017 | 97.1381 | 7.4141 | 13.1017 | 113.5555 | 8.6672 | 13.1017 | 2.399%
2028 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | Tier-2---8 | 65 | 1 | 240.2897 | 88.19% | 10.99% | 0.8202% | 0.94542 | 0 | 0 | 0.94542 | 0 | 0.82069 | 0.10156 | 8.0806 | 0.82069 | 0.10156 | 8.0806 | 0.9594 | 0.11873 | 8.0806 | 0.3935%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 37 | 1 | 247.9994 | 97.75% | 1.792% | 0.4608% | 1.9 | 0 | 0 | 1.9 | 0 | 1.6493 | 0.10156 | 16.2392 | 1.6493 | 0.10156 | 16.2392 | 1.9281 | 0.11873 | 16.2392 | 0.7661%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 10 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 91.8661 | 0 | 0 | 91.8661 | 0 | 79.7457 | 1.0156 | 78.518 | 79.7457 | 1.0156 | 78.518 | 93.2237 | 1.1873 | 78.518 | 2.317%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 9 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 263.2255 | 0 | 0 | 263.2255 | 0 | 228.4969 | 0.91407 | 249.9768 | 228.4969 | 0.91407 | 249.9768 | 267.1155 | 1.0686 | 249.9768 | 2.604%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 216 | 7 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 96.1219 | 0 | 0 | 96.1219 | 0 | 83.4401 | 0.71095 | 117.365 | 83.4401 | 0.71095 | 117.365 | 97.5424 | 0.8311 | 117.365 | 0.9312%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 2 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 23.4221 | 0 | 0 | 23.4221 | 0 | 20.3319 | 0.20313 | 100.0946 | 20.3319 | 0.20313 | 100.0946 | 23.7683 | 0.23746 | 100.0946 | 0.381%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 58 | 4 | 2215.156 | 94.69% | 5.226% | 0.08401% | 41.9507 | 0 | 0 | 41.9507 | 0 | 36.4159 | 0.40625 | 89.6382 | 36.4159 | 0.40625 | 89.6382 | 42.5706 | 0.47492 | 89.6382 | 1.894%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 3 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 31.1935 | 0 | 0 | 31.1935 | 0 | 27.078 | 0.30469 | 88.8704 | 27.078 | 0.30469 | 88.8704 | 31.6545 | 0.35619 | 88.8704 | 0.3587%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 4 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 16.9708 | 0 | 0 | 16.9708 | 0 | 14.7318 | 0.40625 | 36.2625 | 14.7318 | 0.40625 | 36.2625 | 17.2216 | 0.47492 | 36.2625 | 1.089%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 166 | 15 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 91.865 | 0 | 0 | 91.865 | 0 | 79.7448 | 1.5235 | 52.3447 | 79.7448 | 1.5235 | 52.3447 | 93.2226 | 1.7809 | 52.3447 | 2.579%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 23 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 104.1921 | 0 | 0 | 104.1921 | 0 | 90.4455 | 2.336 | 38.7187 | 90.4455 | 2.336 | 38.7187 | 105.7319 | 2.7308 | 38.7187 | 3.492%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 1 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 6.8574 | 0 | 0 | 6.8574 | 0 | 5.9527 | 0.10156 | 58.6101 | 5.9527 | 0.10156 | 58.6101 | 6.9587 | 0.11873 | 58.6101 | 0.4946%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 167 | 36 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 265.2224 | 0 | 0 | 265.2224 | 0 | 230.2303 | 3.6563 | 62.9683 | 230.2303 | 3.6563 | 62.9683 | 269.1418 | 4.2742 | 62.9683 | 6.168%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 1 | 456.1931 | 99.77% | 0% | 0.2285% | 3.8822 | 0 | 0 | 3.8822 | 0 | 3.37 | 0.10156 | 33.1809 | 3.37 | 0.10156 | 33.1809 | 3.9395 | 0.11873 | 33.1809 | 0.851%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 3 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 15.9096 | 0 | 0 | 15.9096 | 0 | 13.8106 | 0.30469 | 45.3266 | 13.8106 | 0.30469 | 45.3266 | 16.1448 | 0.35619 | 45.3266 | 1.351%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 6 | 158.2514 | 99.48% | 0.3681% | 0.155% | 39.131 | 0 | 0 | 39.131 | 0 | 33.9682 | 0.60938 | 55.7421 | 33.9682 | 0.60938 | 55.7421 | 39.7092 | 0.71237 | 55.7421 | 24.73%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 152 | 4 | 6418.5082 | 93.04% | 6.917% | 0.04745% | 45.572 | 0 | 0 | 45.572 | 0 | 39.5595 | 0.40625 | 97.3762 | 39.5595 | 0.40625 | 97.3762 | 46.2455 | 0.47492 | 97.3762 | 0.71%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 48 | 4 | 6815.4278 | 94.54% | 5.441% | 0.023% | 155.7073 | 0 | 0 | 155.7073 | 0 | 135.1641 | 0.40625 | 332.7079 | 135.1641 | 0.40625 | 332.7079 | 158.0084 | 0.47492 | 332.7079 | 2.285%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 267 | 8 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 101.3345 | 0 | 0 | 101.3345 | 0 | 87.965 | 0.81251 | 108.2634 | 87.965 | 0.81251 | 108.2634 | 102.8321 | 0.94983 | 108.2634 | 0.8625%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 146 | 1 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 7.1844 | 0 | 0 | 7.1844 | 0 | 6.2365 | 0.10156 | 61.405 | 6.2365 | 0.10156 | 61.405 | 7.2906 | 0.11873 | 61.405 | 0.195%
2028 | 139 | 139-245AE | Tier-1 | Non-HFTD---14 | Non-HFTD---18 | 165 | 1 | 5.6722 | 51.84% | 0% | 48.16% | 0.0051677 | 0 | 0 | 0.0051677 | 0 | 0.0044859 | 0.10156 | 0.044168 | 0.0044859 | 0.10156 | 0.044168 | 0.0052441 | 0.11873 | 0.044168 | 0.09111%
2028 | 140 | 140-481R | Tier-1 | Non-HFTD---6 | Non-HFTD---12 | 247 | 7 | 76.5519 | 22.22% | 72.37% | 5.415% | 0.1398 | 0 | 0 | 0.1398 | 0 | 0.12135 | 0.71095 | 0.17069 | 0.12135 | 0.71095 | 0.17069 | 0.14186 | 0.8311 | 0.17069 | 0.1826%
2028 | 140 | 140-496 | Tier-1 | Non-HFTD---5 | Non-HFTD---9 | 98 | 3 | 76.0759 | 10.21% | 86.85% | 2.935% | 0.068965 | 0 | 0 | 0.068965 | 0 | 0.059866 | 0.30469 | 0.19648 | 0.059866 | 0.30469 | 0.19648 | 0.069985 | 0.35619 | 0.19648 | 0.09065%
2028 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | Non-HFTD---15 | 58 | 11 | 14.0801 | 87.11% | 0% | 12.89% | 0.67458 | 0 | 0 | 0.67458 | 0 | 0.58558 | 1.1172 | 0.52415 | 0.58558 | 1.1172 | 0.52415 | 0.68455 | 1.306 | 0.52415 | 4.791%
2028 | 1458 | 1458-1057F | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 1 | 155.9987 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.10156 | 0 | 0 | 0.10156 | 0 | 0 | 0.11873 | 0 | 0%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 36 | 1 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 16.3009 | 0 | 0 | 16.3009 | 0 | 14.1502 | 0.10156 | 139.3238 | 14.1502 | 0.10156 | 139.3238 | 16.5418 | 0.11873 | 139.3238 | 0.6891%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 80 | 4 | 4370.0987 | 98.67% | 1.293% | 0.03403% | 62.5258 | 0 | 0 | 62.5258 | 0 | 54.2765 | 0.40625 | 133.6021 | 54.2765 | 0.40625 | 133.6021 | 63.4498 | 0.47492 | 133.6021 | 1.431%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 1 | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.0693 | 0 | 0 | 2.0693 | 0 | 1.7963 | 0.10156 | 17.686 | 1.7963 | 0.10156 | 17.686 | 2.0998 | 0.11873 | 17.686 | 1.235%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 127 | 12 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 221.9089 | 0 | 0 | 221.9089 | 0 | 192.6314 | 1.2188 | 158.0548 | 192.6314 | 1.2188 | 158.0548 | 225.1883 | 1.4247 | 158.0548 | 2.719%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 12 | 37077.302 | 99.36% | 0.615% | 0.02874% | 290.6992 | 0 | 0 | 290.6992 | 0 | 252.3458 | 1.2188 | 207.0507 | 252.3458 | 1.2188 | 207.0507 | 294.9952 | 1.4247 | 207.0507 | 0.784%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 1 | 8.268 | 89.5% | 6.947% | 3.548% | 0.23845 | 0 | 0 | 0.23845 | 0 | 0.20699 | 0.10156 | 2.0381 | 0.20699 | 0.10156 | 2.0381 | 0.24198 | 0.11873 | 2.0381 | 2.884%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 87 | 4 | 418.5676 | 87.71% | 11.66% | 0.6303% | 4.8948 | 0 | 0 | 4.8948 | 0 | 4.249 | 0.40625 | 10.4589 | 4.249 | 0.40625 | 10.4589 | 4.9671 | 0.47492 | 10.4589 | 1.169%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 669 | 20 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 44.1447 | 0 | 0 | 44.1447 | 0 | 38.3205 | 2.0313 | 18.8653 | 38.3205 | 2.0313 | 18.8653 | 44.7971 | 2.3746 | 18.8653 | 0.8016%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 60 | 2 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 29.2341 | 0 | 0 | 29.2341 | 0 | 25.3771 | 0.20313 | 124.9319 | 25.3771 | 0.20313 | 124.9319 | 29.6661 | 0.23746 | 124.9319 | 0.9577%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 2 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 10.4477 | 0 | 0 | 10.4477 | 0 | 9.0693 | 0.20313 | 44.6481 | 9.0693 | 0.20313 | 44.6481 | 10.6021 | 0.23746 | 44.6481 | 0.2695%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 250 | 21 | 3160.5079 | 95.27% | 4.501% | 0.231% | 73.347 | 0 | 0 | 73.347 | 0 | 63.67 | 2.1328 | 29.8523 | 63.67 | 2.1328 | 29.8523 | 74.431 | 2.4933 | 29.8523 | 2.321%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 554 | 19 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 16.716 | 0 | 0 | 16.716 | 0 | 14.5106 | 1.9297 | 7.5196 | 14.5106 | 1.9297 | 7.5196 | 16.9631 | 2.2559 | 7.5196 | 0.811%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 173 | 12 | 1867.403 | 95.01% | 4.712% | 0.2778% | 35.6897 | 0 | 0 | 35.6897 | 0 | 30.981 | 1.2188 | 25.42 | 30.981 | 1.2188 | 25.42 | 36.2171 | 1.4247 | 25.42 | 1.911%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 675 | 93 | 18749.5963 | 97% | 2.901% | 0.09453% | 726.7132 | 0 | 0 | 726.7132 | 0 | 630.8344 | 9.4454 | 66.7874 | 630.8344 | 9.4454 | 66.7874 | 737.4526 | 11.0418 | 66.7874 | 3.876%
2028 | 168 | 168-702F | Tier-1 | Non-HFTD---5 | Non-HFTD---12 | 160 | 2 | 86.0496 | 96.13% | 0% | 3.875% | 0.29984 | 0 | 0 | 0.29984 | 0 | 0.26028 | 0.20313 | 1.2814 | 0.26028 | 0.20313 | 1.2814 | 0.30427 | 0.23746 | 1.2814 | 0.3485%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 3 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 33.726 | 0 | 0 | 33.726 | 0 | 29.2763 | 0.30469 | 96.0854 | 29.2763 | 0.30469 | 96.0854 | 34.2244 | 0.35619 | 96.0854 | 0.8371%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 239 | 30 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 155.6825 | 0 | 0 | 155.6825 | 0 | 135.1425 | 3.0469 | 44.354 | 135.1425 | 3.0469 | 44.354 | 157.9832 | 3.5619 | 44.354 | 3.55%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 13 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 69.8866 | 0 | 0 | 69.8866 | 0 | 60.6662 | 1.3203 | 45.9478 | 60.6662 | 1.3203 | 45.9478 | 70.9194 | 1.5435 | 45.9478 | 1.217%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 8 | 836.2457 | 79.76% | 20.09% | 0.1547% | 29.7574 | 0 | 0 | 29.7574 | 0 | 25.8314 | 0.81251 | 31.7921 | 25.8314 | 0.81251 | 31.7921 | 30.1972 | 0.94983 | 31.7921 | 3.558%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 236 | 7 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 97.8997 | 0 | 0 | 97.8997 | 0 | 84.9834 | 0.71095 | 119.5357 | 84.9834 | 0.71095 | 119.5357 | 99.3465 | 0.8311 | 119.5357 | 0.8496%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 131 | 4 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 36.3503 | 0 | 0 | 36.3503 | 0 | 31.5544 | 0.40625 | 77.6716 | 31.5544 | 0.40625 | 77.6716 | 36.8875 | 0.47492 | 77.6716 | 0.8686%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 19 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 172.709 | 0 | 0 | 172.709 | 0 | 149.9226 | 1.9297 | 77.6918 | 149.9226 | 1.9297 | 77.6918 | 175.2613 | 2.2559 | 77.6918 | 1.715%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 1 | 404.4817 | 67.64% | 32.12% | 0.2398% | 1.5868 | 0 | 0 | 1.5868 | 0 | 1.3774 | 0.10156 | 13.5623 | 1.3774 | 0.10156 | 13.5623 | 1.6102 | 0.11873 | 13.5623 | 0.3923%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 172 | 11 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 61.6514 | 0 | 0 | 61.6514 | 0 | 53.5174 | 1.1172 | 47.9032 | 53.5174 | 1.1172 | 47.9032 | 62.5625 | 1.306 | 47.9032 | 1.813%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 214 | 8 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 52.2625 | 0 | 0 | 52.2625 | 0 | 45.3673 | 0.81251 | 55.836 | 45.3673 | 0.81251 | 55.836 | 53.0349 | 0.94983 | 55.836 | 1.059%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 345 | 15 | 13172.958 | 96.8% | 3.124% | 0.0728% | 160.7841 | 0 | 0 | 160.7841 | 0 | 139.5711 | 1.5235 | 91.6149 | 139.5711 | 1.5235 | 91.6149 | 163.1602 | 1.7809 | 91.6149 | 1.221%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 5 | 1635.841 | 89.24% | 10.7% | 0.05535% | 70.5613 | 0 | 0 | 70.5613 | 0 | 61.2518 | 0.50782 | 120.6176 | 61.2518 | 0.50782 | 120.6176 | 71.604 | 0.59365 | 120.6176 | 4.313%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 1 | 47.6106 | 91.21% | 0% | 8.789% | 0.062968 | 0 | 0 | 0.062968 | 0 | 0.05466 | 0.10156 | 0.53819 | 0.05466 | 0.10156 | 0.53819 | 0.063899 | 0.11873 | 0.53819 | 0.1323%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 13 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 145.5768 | 0 | 0 | 145.5768 | 0 | 126.3702 | 1.3203 | 95.7113 | 126.3702 | 1.3203 | 95.7113 | 147.7282 | 1.5435 | 95.7113 | 1.222%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 1 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 21.5737 | 0 | 0 | 21.5737 | 0 | 18.7273 | 0.10156 | 184.3903 | 18.7273 | 0.10156 | 184.3903 | 21.8925 | 0.11873 | 184.3903 | 1.112%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 3 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 35.1075 | 0 | 0 | 35.1075 | 0 | 30.4756 | 0.30469 | 100.0214 | 30.4756 | 0.30469 | 100.0214 | 35.6263 | 0.35619 | 100.0214 | 0.83%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 42 | 4 | 316.4778 | 66.23% | 33.5% | 0.2671% | 5.7891 | 0 | 0 | 5.7891 | 0 | 5.0253 | 0.40625 | 12.3698 | 5.0253 | 0.40625 | 12.3698 | 5.8746 | 0.47492 | 12.3698 | 1.829%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 114 | 1 | 471.2015 | 74.37% | 25.17% | 0.4626% | 0.89144 | 0 | 0 | 0.89144 | 0 | 0.77383 | 0.10156 | 7.6192 | 0.77383 | 0.10156 | 7.6192 | 0.90462 | 0.11873 | 7.6192 | 0.1892%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 17 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 30.0499 | 0 | 0 | 30.0499 | 0 | 26.0853 | 1.7266 | 15.1081 | 26.0853 | 1.7266 | 15.1081 | 30.494 | 2.0184 | 15.1081 | 1.743%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 2 | 973.0999 | 95.53% | 4.02% | 0.4464% | 2.868 | 0 | 0 | 2.868 | 0 | 2.4896 | 0.20313 | 12.2565 | 2.4896 | 0.20313 | 12.2565 | 2.9104 | 0.23746 | 12.2565 | 0.2947%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 18 | 490.4615 | 96.36% | 1.259% | 2.378% | 7.3425 | 0 | 0 | 7.3425 | 0 | 6.3738 | 1.8281 | 3.4865 | 6.3738 | 1.8281 | 3.4865 | 7.451 | 2.1371 | 3.4865 | 1.497%
2028 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 102 | 1 | 124.0064 | 98.52% | 0% | 1.478% | 0.34736 | 0 | 0 | 0.34736 | 0 | 0.30153 | 0.10156 | 2.9689 | 0.30153 | 0.10156 | 2.9689 | 0.35249 | 0.11873 | 2.9689 | 0.2801%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 1 | 1279.0443 | 99.78% | 0% | 0.2159% | 2.804 | 0 | 0 | 2.804 | 0 | 2.434 | 0.10156 | 23.9654 | 2.434 | 0.10156 | 23.9654 | 2.8454 | 0.11873 | 23.9654 | 0.2192%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 11 | 2976.5734 | 99.75% | 0% | 0.2502% | 22.9334 | 0 | 0 | 22.9334 | 0 | 19.9077 | 1.1172 | 17.8193 | 19.9077 | 1.1172 | 17.8193 | 23.2724 | 1.306 | 17.8193 | 0.7705%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 43 | 8462.8018 | 99.74% | 0% | 0.2593% | 98.4636 | 0 | 0 | 98.4636 | 0 | 85.4728 | 4.3672 | 19.5714 | 85.4728 | 4.3672 | 19.5714 | 99.9187 | 5.1053 | 19.5714 | 1.163%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 111 | 2 | 498.1496 | 90.1% | 9.186% | 0.7154% | 2.3452 | 0 | 0 | 2.3452 | 0 | 2.0358 | 0.20313 | 10.0223 | 2.0358 | 0.20313 | 10.0223 | 2.3799 | 0.23746 | 10.0223 | 0.4708%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 221 | 21 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 24.5202 | 0 | 0 | 24.5202 | 0 | 21.2851 | 2.1328 | 9.9797 | 21.2851 | 2.1328 | 9.9797 | 24.8825 | 2.4933 | 9.9797 | 2.362%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 77 | 1 | 170.5929 | 70.47% | 28.1% | 1.432% | 0.45278 | 0 | 0 | 0.45278 | 0 | 0.39304 | 0.10156 | 3.8699 | 0.39304 | 0.10156 | 3.8699 | 0.45947 | 0.11873 | 3.8699 | 0.2654%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 95 | 3 | 317.7725 | 50.82% | 48.53% | 0.6462% | 1.4791 | 0 | 0 | 1.4791 | 0 | 1.2839 | 0.30469 | 4.2138 | 1.2839 | 0.30469 | 4.2138 | 1.5009 | 0.35619 | 4.2138 | 0.4654%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 293 | 10 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 10.6252 | 0 | 0 | 10.6252 | 0 | 9.2234 | 1.0156 | 9.0814 | 9.2234 | 1.0156 | 9.0814 | 10.7822 | 1.1873 | 9.0814 | 0.8857%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 18 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 18.9509 | 0 | 0 | 18.9509 | 0 | 16.4506 | 1.8281 | 8.9985 | 16.4506 | 1.8281 | 8.9985 | 19.231 | 2.1371 | 8.9985 | 1.047%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 279 | 7 | 1890.633 | 91.06% | 8.49% | 0.4466% | 12.5269 | 0 | 0 | 12.5269 | 0 | 10.8742 | 0.71095 | 15.2954 | 10.8742 | 0.71095 | 15.2954 | 12.712 | 0.8311 | 15.2954 | 0.6626%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 287 | 6 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 10.0605 | 0 | 0 | 10.0605 | 0 | 8.7331 | 0.60938 | 14.3311 | 8.7331 | 0.60938 | 14.3311 | 10.2091 | 0.71237 | 14.3311 | 0.5785%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 219 | 13 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 25.6744 | 0 | 0 | 25.6744 | 0 | 22.287 | 1.3203 | 16.8799 | 22.287 | 1.3203 | 16.8799 | 26.0538 | 1.5435 | 16.8799 | 1.635%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | Tier-2---3 | 79 | 1 | 609.7797 | 99.07% | 0.4924% | 0.4406% | 2.2175 | 0 | 0 | 2.2175 | 0 | 1.925 | 0.10156 | 18.9534 | 1.925 | 0.10156 | 18.9534 | 2.2503 | 0.11873 | 18.9534 | 0.3637%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | Tier-3---1 | 218 | 10 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 64.4695 | 0 | 0 | 64.4695 | 0 | 55.9637 | 1.0156 | 55.1022 | 55.9637 | 1.0156 | 55.1022 | 65.4223 | 1.1873 | 55.1022 | 1.319%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 273 | 7 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 9.2176 | 0 | 0 | 9.2176 | 0 | 8.0015 | 0.71095 | 11.2547 | 8.0015 | 0.71095 | 11.2547 | 9.3538 | 0.8311 | 11.2547 | 0.7281%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | Tier-3---3 | 201 | 12 | 998.7912 | 96.62% | 2.787% | 0.5903% | 16.7084 | 0 | 0 | 16.7084 | 0 | 14.504 | 1.2188 | 11.9006 | 14.504 | 1.2188 | 11.9006 | 16.9553 | 1.4247 | 11.9006 | 1.673%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 71 | 1 | 261.4279 | 97.06% | 2.12% | 0.8249% | 1.0364 | 0 | 0 | 1.0364 | 0 | 0.89963 | 0.10156 | 8.8578 | 0.89963 | 0.10156 | 8.8578 | 1.0517 | 0.11873 | 8.8578 | 0.3964%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 201 | 3 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 6.2416 | 0 | 0 | 6.2416 | 0 | 5.4181 | 0.30469 | 17.7824 | 5.4181 | 0.30469 | 17.7824 | 6.3339 | 0.35619 | 17.7824 | 0.421%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 22 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 56.7555 | 0 | 0 | 56.7555 | 0 | 49.2675 | 2.2344 | 22.0495 | 49.2675 | 2.2344 | 22.0495 | 57.5943 | 2.612 | 22.0495 | 2.057%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 115 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 2.5441 | 0 | 0 | 2.5441 | 0 | 2.2085 | 0.10156 | 21.7447 | 2.2085 | 0.10156 | 21.7447 | 2.5817 | 0.11873 | 21.7447 | 0.2449%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 155 | 2 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 7.9921 | 0 | 0 | 7.9921 | 0 | 6.9377 | 0.20313 | 34.1544 | 6.9377 | 0.20313 | 34.1544 | 8.1102 | 0.23746 | 34.1544 | 0.3694%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 147 | 4 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 11.3552 | 0 | 0 | 11.3552 | 0 | 9.857 | 0.40625 | 24.2631 | 9.857 | 0.40625 | 24.2631 | 11.523 | 0.47492 | 24.2631 | 0.7719%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 12 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 202.8201 | 0 | 0 | 202.8201 | 0 | 176.0611 | 1.2188 | 144.4588 | 176.0611 | 1.2188 | 144.4588 | 205.8174 | 1.4247 | 144.4588 | 0.7717%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 17 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 114.6419 | 0 | 0 | 114.6419 | 0 | 99.5167 | 1.7266 | 57.638 | 99.5167 | 1.7266 | 57.638 | 116.3361 | 2.0184 | 57.638 | 1.72%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 4 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 14.5887 | 0 | 0 | 14.5887 | 0 | 12.664 | 0.40625 | 31.1725 | 12.664 | 0.40625 | 31.1725 | 14.8043 | 0.47492 | 31.1725 | 0.6606%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 1 | 1721.769 | 85.69% | 14.07% | 0.2459% | 2.1829 | 0 | 0 | 2.1829 | 0 | 1.8949 | 0.10156 | 18.6573 | 1.8949 | 0.10156 | 18.6573 | 2.2152 | 0.11873 | 18.6573 | 0.1268%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 264 | 18 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 438.6595 | 0 | 0 | 438.6595 | 0 | 380.785 | 1.8281 | 208.2904 | 380.785 | 1.8281 | 208.2904 | 445.142 | 2.1371 | 208.2904 | 1.962%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 28 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 395.7096 | 0 | 0 | 395.7096 | 0 | 343.5017 | 2.8438 | 120.7905 | 343.5017 | 2.8438 | 120.7905 | 401.5574 | 3.3244 | 120.7905 | 3.115%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 16 | 19489.7064 | 99% | 0.9737% | 0.02962% | 368.4154 | 0 | 0 | 368.4154 | 0 | 319.8086 | 1.625 | 196.8031 | 319.8086 | 1.625 | 196.8031 | 373.8599 | 1.8997 | 196.8031 | 1.89%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 4 | 1412.4296 | 98.09% | 1.785% | 0.1216% | 30.324 | 0 | 0 | 30.324 | 0 | 26.3232 | 0.40625 | 64.795 | 26.3232 | 0.40625 | 64.795 | 30.7722 | 0.47492 | 64.795 | 2.147%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 5 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 61.866 | 0 | 0 | 61.866 | 0 | 53.7037 | 0.50782 | 105.7538 | 53.7037 | 0.50782 | 105.7538 | 62.7802 | 0.59365 | 105.7538 | 1.138%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 10 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 150.7013 | 0 | 0 | 150.7013 | 0 | 130.8186 | 1.0156 | 128.8045 | 130.8186 | 1.0156 | 128.8045 | 152.9284 | 1.1873 | 128.8045 | 1.073%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 16 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 18.2815 | 0 | 0 | 18.2815 | 0 | 15.8695 | 1.625 | 9.7658 | 15.8695 | 1.625 | 9.7658 | 18.5517 | 1.8997 | 9.7658 | 0.9079%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 9 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 18.1803 | 0 | 0 | 18.1803 | 0 | 15.7817 | 0.91407 | 17.2652 | 15.7817 | 0.91407 | 17.2652 | 18.449 | 1.0686 | 17.2652 | 0.6665%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 14 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 134.2247 | 0 | 0 | 134.2247 | 0 | 116.5158 | 1.4219 | 81.9443 | 116.5158 | 1.4219 | 81.9443 | 136.2083 | 1.6622 | 81.9443 | 1.256%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 3 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 10.2792 | 0 | 0 | 10.2792 | 0 | 8.923 | 0.30469 | 29.2856 | 8.923 | 0.30469 | 29.2856 | 10.4311 | 0.35619 | 29.2856 | 0.2811%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 14 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 20.7346 | 0 | 0 | 20.7346 | 0 | 17.9989 | 1.4219 | 12.6585 | 17.9989 | 1.4219 | 12.6585 | 21.041 | 1.6622 | 12.6585 | 1.441%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | Tier-3---3 | 132 | 3 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 13.9604 | 0 | 0 | 13.9604 | 0 | 12.1186 | 0.30469 | 39.7734 | 12.1186 | 0.30469 | 39.7734 | 14.1668 | 0.35619 | 39.7734 | 0.6349%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 15 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 21.5291 | 0 | 0 | 21.5291 | 0 | 18.6887 | 1.5235 | 12.2673 | 18.6887 | 1.5235 | 12.2673 | 21.8473 | 1.7809 | 12.2673 | 1.118%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 614 | 22 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 33.2973 | 0 | 0 | 33.2973 | 0 | 28.9042 | 2.2344 | 12.936 | 28.9042 | 2.2344 | 12.936 | 33.7894 | 2.612 | 12.936 | 0.9286%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | Tier-3---2 | 97 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 11.0247 | 0 | 0 | 11.0247 | 0 | 9.5702 | 0.10156 | 94.2282 | 9.5702 | 0.10156 | 94.2282 | 11.1876 | 0.11873 | 94.2282 | 0.2987%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 307 | 4 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 11.3881 | 0 | 0 | 11.3881 | 0 | 9.8857 | 0.40625 | 24.3337 | 9.8857 | 0.40625 | 24.3337 | 11.5564 | 0.47492 | 24.3337 | 0.3482%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | Tier-3---3 | 293 | 7 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 18.2177 | 0 | 0 | 18.2177 | 0 | 15.8141 | 0.71095 | 22.2438 | 15.8141 | 0.71095 | 22.2438 | 18.4869 | 0.8311 | 22.2438 | 0.6659%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | Tier-3---1 | 244 | 9 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 40.8374 | 0 | 0 | 40.8374 | 0 | 35.4495 | 0.91407 | 38.782 | 35.4495 | 0.91407 | 38.782 | 41.4409 | 1.0686 | 38.782 | 1.038%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | Tier-3---5 | 18 | 1 | 318.0967 | 33.4% | 66.33% | 0.2755% | 1.7116 | 0 | 0 | 1.7116 | 0 | 1.4858 | 0.10156 | 14.629 | 1.4858 | 0.10156 | 14.629 | 1.7369 | 0.11873 | 14.629 | 0.5381%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | Tier-2---3 | 99 | 2 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 11.9828 | 0 | 0 | 11.9828 | 0 | 10.4019 | 0.20313 | 51.2087 | 10.4019 | 0.20313 | 51.2087 | 12.1599 | 0.23746 | 51.2087 | 0.583%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | Tier-3---1 | 67 | 1 | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 19.2921 | 0 | 0 | 19.2921 | 0 | 16.7468 | 0.10156 | 164.8896 | 16.7468 | 0.10156 | 164.8896 | 19.5772 | 0.11873 | 164.8896 | 0.4304%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | Tier-3---3 | 106 | 1 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 6.1592 | 0 | 0 | 6.1592 | 0 | 5.3466 | 0.10156 | 52.643 | 5.3466 | 0.10156 | 52.643 | 6.2503 | 0.11873 | 52.643 | 0.265%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | Tier-3---1 | 123 | 1 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 22.584 | 0 | 0 | 22.584 | 0 | 19.6044 | 0.10156 | 193.0259 | 19.6044 | 0.10156 | 193.0259 | 22.9178 | 0.11873 | 193.0259 | 0.2348%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | Tier-3---3 | 76 | 3 | 1359.3953 | 95.15% | 4.696% | 0.1502% | 14.8074 | 0 | 0 | 14.8074 | 0 | 12.8538 | 0.30469 | 42.1863 | 12.8538 | 0.30469 | 42.1863 | 15.0262 | 0.35619 | 42.1863 | 1.089%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | Tier-3---1 | 367 | 22 | 7406.689 | 96.62% | 3.25% | 0.1263% | 124.412 | 0 | 0 | 124.412 | 0 | 107.9977 | 2.2344 | 48.3341 | 107.9977 | 2.2344 | 48.3341 | 126.2505 | 2.612 | 48.3341 | 1.68%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | Tier-3---1 | 451 | 8 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 404.3393 | 0 | 0 | 404.3393 | 0 | 350.9929 | 0.81251 | 431.9865 | 350.9929 | 0.81251 | 431.9865 | 410.3147 | 0.94983 | 431.9865 | 0.5106%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | Tier-3---3 | 18 | 1 | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 57.8862 | 0 | 0 | 57.8862 | 0 | 50.249 | 0.10156 | 494.7534 | 50.249 | 0.10156 | 494.7534 | 58.7416 | 0.11873 | 494.7534 | 1.599%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | Tier-3---1 | 287 | 13 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 590.3191 | 0 | 0 | 590.3191 | 0 | 512.4355 | 1.3203 | 388.1125 | 512.4355 | 1.3203 | 388.1125 | 599.0429 | 1.5435 | 388.1125 | 1.309%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | Tier-3---10 | 43 | 1 | 288.7705 | 86.56% | 13.18% | 0.2657% | 1.6857 | 0 | 0 | 1.6857 | 0 | 1.4633 | 0.10156 | 14.4077 | 1.4633 | 0.10156 | 14.4077 | 1.7106 | 0.11873 | 14.4077 | 0.5838%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 407 | 9 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 45.7458 | 0 | 0 | 45.7458 | 0 | 39.7103 | 0.91407 | 43.4433 | 39.7103 | 0.91407 | 43.4433 | 46.4218 | 1.0686 | 43.4433 | 0.6159%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | Tier-3---1 | 910 | 32 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 165.3886 | 0 | 0 | 165.3886 | 0 | 143.568 | 3.25 | 44.1743 | 143.568 | 3.25 | 44.1743 | 167.8327 | 3.7993 | 44.1743 | 0.9861%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 28 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 57.3568 | 0 | 0 | 57.3568 | 0 | 49.7894 | 2.8438 | 17.5082 | 49.7894 | 2.8438 | 17.5082 | 58.2044 | 3.3244 | 17.5082 | 2.867%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 328 | 4 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 22.2016 | 0 | 0 | 22.2016 | 0 | 19.2724 | 0.40625 | 47.4393 | 19.2724 | 0.40625 | 47.4393 | 22.5297 | 0.47492 | 47.4393 | 0.3475%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 245 | 18 | 2072.8837 | 91.06% | 8.635% | 0.3% | 40.2188 | 0 | 0 | 40.2188 | 0 | 34.9125 | 1.8281 | 19.0973 | 34.9125 | 1.8281 | 19.0973 | 40.8132 | 2.1371 | 19.0973 | 1.94%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 71 | 8 | 536.3838 | 78.97% | 20.71% | 0.32% | 13.8407 | 0 | 0 | 13.8407 | 0 | 12.0146 | 0.81251 | 14.787 | 12.0146 | 0.81251 | 14.787 | 14.0452 | 0.94983 | 14.787 | 2.58%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 29 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 120.9029 | 0 | 0 | 120.9029 | 0 | 104.9516 | 2.9453 | 35.633 | 104.9516 | 2.9453 | 35.633 | 122.6896 | 3.4431 | 35.633 | 3.481%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 1 | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.4648 | 0 | 0 | 5.4648 | 0 | 4.7438 | 0.10156 | 46.708 | 4.7438 | 0.10156 | 46.708 | 5.5456 | 0.11873 | 46.708 | 4.494%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 56 | 2730.9177 | 98.3% | 1.373% | 0.325% | 122.1203 | 0 | 0 | 122.1203 | 0 | 106.0084 | 5.6876 | 18.6386 | 106.0084 | 5.6876 | 18.6386 | 123.925 | 6.6488 | 18.6386 | 4.472%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 121 | 5142.095 | 98.68% | 0.901% | 0.4182% | 206.5613 | 0 | 0 | 206.5613 | 0 | 179.3087 | 12.2892 | 14.5908 | 179.3087 | 12.2892 | 14.5908 | 209.6139 | 14.3662 | 14.5908 | 4.017%
2028 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 5 | 1 | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0029987 | 0 | 0 | 0.0029987 | 0 | 0.002603 | 0.10156 | 0.02563 | 0.002603 | 0.10156 | 0.02563 | 0.003043 | 0.11873 | 0.02563 | 0.02624%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 42 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 88.7059 | 0 | 0 | 88.7059 | 0 | 77.0025 | 4.2657 | 18.0517 | 77.0025 | 4.2657 | 18.0517 | 90.0168 | 4.9866 | 18.0517 | 2.922%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 24 | 718.991 | 97.57% | 1.357% | 1.072% | 17.885 | 0 | 0 | 17.885 | 0 | 15.5253 | 2.4375 | 6.3693 | 15.5253 | 2.4375 | 6.3693 | 18.1493 | 2.8495 | 6.3693 | 2.488%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 1 | 447.7794 | 94.96% | 4.349% | 0.694% | 1.2455 | 0 | 0 | 1.2455 | 0 | 1.0812 | 0.10156 | 10.6456 | 1.0812 | 0.10156 | 10.6456 | 1.2639 | 0.11873 | 10.6456 | 0.2782%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 8 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 11.3272 | 0 | 0 | 11.3272 | 0 | 9.8328 | 0.81251 | 12.1017 | 9.8328 | 0.81251 | 12.1017 | 11.4946 | 0.94983 | 12.1017 | 0.4837%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 24 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 102.3691 | 0 | 0 | 102.3691 | 0 | 88.863 | 2.4375 | 36.4562 | 88.863 | 2.4375 | 36.4562 | 103.8819 | 2.8495 | 36.4562 | 2.073%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 8 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 37.3265 | 0 | 0 | 37.3265 | 0 | 32.4018 | 0.81251 | 39.8787 | 32.4018 | 0.81251 | 39.8787 | 37.8781 | 0.94983 | 39.8787 | 0.8532%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 62 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 788.6756 | 0 | 0 | 788.6756 | 0 | 684.6218 | 6.2969 | 108.7229 | 684.6218 | 6.2969 | 108.7229 | 800.3307 | 7.3612 | 108.7229 | 3.331%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 252 | 32 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 353.3718 | 0 | 0 | 353.3718 | 0 | 306.7497 | 3.25 | 94.3835 | 306.7497 | 3.25 | 94.3835 | 358.5939 | 3.7993 | 94.3835 | 3.636%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 137 | 8 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 46.5062 | 0 | 0 | 46.5062 | 0 | 40.3704 | 0.81251 | 49.6861 | 40.3704 | 0.81251 | 49.6861 | 47.1935 | 0.94983 | 49.6861 | 1.647%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 171 | 7 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 62.0792 | 0 | 0 | 62.0792 | 0 | 53.8888 | 0.71095 | 75.7988 | 53.8888 | 0.71095 | 75.7988 | 62.9966 | 0.8311 | 75.7988 | 1.164%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 498 | 55 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 668.6087 | 0 | 0 | 668.6087 | 0 | 580.3959 | 5.586 | 103.9019 | 580.3959 | 5.586 | 103.9019 | 678.4894 | 6.5301 | 103.9019 | 3.15%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | Tier-3---1 | 192 | 16 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 163.8142 | 0 | 0 | 163.8142 | 0 | 142.2014 | 1.625 | 87.5076 | 142.2014 | 1.625 | 87.5076 | 166.2351 | 1.8997 | 87.5076 | 2.365%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | Tier-3---1 | 126 | 4 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 33.2551 | 0 | 0 | 33.2551 | 0 | 28.8676 | 0.40625 | 71.058 | 28.8676 | 0.40625 | 71.058 | 33.7466 | 0.47492 | 71.058 | 0.9151%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 223 | 7 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 255.4708 | 0 | 0 | 255.4708 | 0 | 221.7653 | 0.71095 | 311.9302 | 221.7653 | 0.71095 | 311.9302 | 259.2462 | 0.8311 | 311.9302 | 0.9043%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 38 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 550.6029 | 0 | 0 | 550.6029 | 0 | 477.9592 | 3.8594 | 123.8423 | 477.9592 | 3.8594 | 123.8423 | 558.7398 | 4.5117 | 123.8423 | 2.033%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 4 | 663.2151 | 70.89% | 28.72% | 0.399% | 4.826 | 0 | 0 | 4.826 | 0 | 4.1893 | 0.40625 | 10.312 | 4.1893 | 0.40625 | 10.312 | 4.8973 | 0.47492 | 10.312 | 0.7277%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | Tier-2---1 | 59 | 6 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 73.7444 | 0 | 0 | 73.7444 | 0 | 64.015 | 0.60938 | 105.0491 | 64.015 | 0.60938 | 105.0491 | 74.8342 | 0.71237 | 105.0491 | 2.915%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | Tier-3---1 | 499 | 35 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 622.8261 | 0 | 0 | 622.8261 | 0 | 540.6537 | 3.5547 | 152.0943 | 540.6537 | 3.5547 | 152.0943 | 632.0303 | 4.1555 | 152.0943 | 2.016%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 651 | 42 | 65515.492 | 98.93% | 1.038% | 0.03019% | 1212.6801 | 0 | 0 | 1212.6801 | 0 | 1052.6853 | 4.2657 | 246.7806 | 1052.6853 | 4.2657 | 246.7806 | 1230.6012 | 4.9866 | 246.7806 | 1.851%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 17 | 860.3234 | 98.08% | 1.495% | 0.4234% | 32.756 | 0 | 0 | 32.756 | 0 | 28.4343 | 1.7266 | 16.4686 | 28.4343 | 1.7266 | 16.4686 | 33.24 | 2.0184 | 16.4686 | 3.807%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 134 | 15 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 34.9597 | 0 | 0 | 34.9597 | 0 | 30.3473 | 1.5235 | 19.9201 | 30.3473 | 1.5235 | 19.9201 | 35.4764 | 1.7809 | 19.9201 | 3.131%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 22 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 128.8199 | 0 | 0 | 128.8199 | 0 | 111.8241 | 2.2344 | 50.0466 | 111.8241 | 2.2344 | 50.0466 | 130.7237 | 2.612 | 50.0466 | 2.055%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 7 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 13.4055 | 0 | 0 | 13.4055 | 0 | 11.6369 | 0.71095 | 16.3682 | 11.6369 | 0.71095 | 16.3682 | 13.6037 | 0.8311 | 16.3682 | 1.302%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 165 | 9 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 18.3878 | 0 | 0 | 18.3878 | 0 | 15.9618 | 0.91407 | 17.4623 | 15.9618 | 0.91407 | 17.4623 | 18.6595 | 1.0686 | 17.4623 | 1.556%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 75 | 2 | 376.72 | 96.88% | 2.523% | 0.5996% | 2.8223 | 0 | 0 | 2.8223 | 0 | 2.45 | 0.20313 | 12.0612 | 2.45 | 0.20313 | 12.0612 | 2.864 | 0.23746 | 12.0612 | 0.7492%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 40 | 4437.6588 | 97.91% | 1.769% | 0.321% | 80.9004 | 0 | 0 | 80.9004 | 0 | 70.2269 | 4.0625 | 17.2864 | 70.2269 | 4.0625 | 17.2864 | 82.096 | 4.7492 | 17.2864 | 1.823%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 269 | 12 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 47.9646 | 0 | 0 | 47.9646 | 0 | 41.6364 | 1.2188 | 34.1628 | 41.6364 | 1.2188 | 34.1628 | 48.6734 | 1.4247 | 34.1628 | 1.282%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 11 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 32.9113 | 0 | 0 | 32.9113 | 0 | 28.5691 | 1.1172 | 25.5721 | 28.5691 | 1.1172 | 25.5721 | 33.3977 | 1.306 | 25.5721 | 0.8978%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 13 | 960.3446 | 65.96% | 33.81% | 0.2324% | 20.4107 | 0 | 0 | 20.4107 | 0 | 17.7178 | 1.3203 | 13.4193 | 17.7178 | 1.3203 | 13.4193 | 20.7123 | 1.5435 | 13.4193 | 2.125%
2028 | 242 | 242-1427F | Tier-2 | Tier-2---20 | Tier-2---19 | 5 | 1 | 24.991 | 71.07% | 28.66% | 0.2708% | 1.0302 | 0 | 0 | 1.0302 | 0 | 0.89426 | 0.10156 | 8.8049 | 0.89426 | 0.10156 | 8.8049 | 1.0454 | 0.11873 | 8.8049 | 4.122%
2028 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 470 | 1 | 404.2589 | 29.5% | 68.39% | 2.113% | 0.07358 | 0 | 0 | 0.07358 | 0 | 0.063872 | 0.10156 | 0.62889 | 0.063872 | 0.10156 | 0.62889 | 0.074667 | 0.11873 | 0.62889 | 0.0182%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 42 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 89.457 | 0 | 0 | 89.457 | 0 | 77.6545 | 4.2657 | 18.2045 | 77.6545 | 4.2657 | 18.2045 | 90.779 | 4.9866 | 18.2045 | 2.641%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 27 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 43.4095 | 0 | 0 | 43.4095 | 0 | 37.6823 | 2.7422 | 13.7415 | 37.6823 | 2.7422 | 13.7415 | 44.051 | 3.2057 | 13.7415 | 3.191%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 43 | 3753.23 | 95.85% | 3.876% | 0.273% | 96.6831 | 0 | 0 | 96.6831 | 0 | 83.9273 | 4.3672 | 19.2175 | 83.9273 | 4.3672 | 19.2175 | 98.1119 | 5.1053 | 19.2175 | 2.576%
2028 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 98 | 3 | 49.4853 | 86.66% | 6.71% | 6.626% | 0.38072 | 0 | 0 | 0.38072 | 0 | 0.33049 | 0.30469 | 1.0847 | 0.33049 | 0.30469 | 1.0847 | 0.38635 | 0.35619 | 1.0847 | 0.7694%
2028 | 276 | 276-228 | Tier-1 | Non-HFTD---2 | Non-HFTD---8 | 773 | 1 | 290.9914 | 11.65% | 84% | 4.346% | 0.012723 | 0 | 0 | 0.012723 | 0 | 0.011045 | 0.10156 | 0.10875 | 0.011045 | 0.10156 | 0.10875 | 0.012912 | 0.11873 | 0.10875 | 0.004372%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 10 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 138.9611 | 0 | 0 | 138.9611 | 0 | 120.6273 | 1.0156 | 118.7702 | 120.6273 | 1.0156 | 118.7702 | 141.0147 | 1.1873 | 118.7702 | 2.622%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 14 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 56.5187 | 0 | 0 | 56.5187 | 0 | 49.062 | 1.4219 | 34.5047 | 49.062 | 1.4219 | 34.5047 | 57.354 | 1.6622 | 34.5047 | 2.807%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 170 | 7 | 481.2843 | 94.31% | 4.95% | 0.7414% | 5.42 | 0 | 0 | 5.42 | 0 | 4.7049 | 0.71095 | 6.6178 | 4.7049 | 0.71095 | 6.6178 | 5.5001 | 0.8311 | 6.6178 | 1.126%
2028 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 7 | 550.61 | 92.88% | 6.93% | 0.1872% | 24.1438 | 0 | 0 | 24.1438 | 0 | 20.9584 | 0.71095 | 29.4796 | 20.9584 | 0.71095 | 29.4796 | 24.5006 | 0.8311 | 29.4796 | 4.385%
2028 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | Non-HFTD---13 | 100 | 8 | 92.0555 | 97.82% | 0% | 2.183% | 2.0891 | 0 | 0 | 2.0891 | 0 | 1.8134 | 0.81251 | 2.2319 | 1.8134 | 0.81251 | 2.2319 | 2.1199 | 0.94983 | 2.2319 | 2.269%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 1 | 458.7821 | 99.48% | 0% | 0.5194% | 1.9182 | 0 | 0 | 1.9182 | 0 | 1.6651 | 0.10156 | 16.3949 | 1.6651 | 0.10156 | 16.3949 | 1.9465 | 0.11873 | 16.3949 | 0.4181%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 4 | 754.1323 | 92.41% | 6.882% | 0.7076% | 3.2336 | 0 | 0 | 3.2336 | 0 | 2.807 | 0.40625 | 6.9094 | 2.807 | 0.40625 | 6.9094 | 3.2814 | 0.47492 | 6.9094 | 0.4288%
2028 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 233 | 6 | 4233.8665 | 96.93% | 2.943% | 0.1312% | 30.6456 | 0 | 0 | 30.6456 | 0 | 26.6024 | 0.60938 | 43.6548 | 26.6024 | 0.60938 | 43.6548 | 31.0985 | 0.71237 | 43.6548 | 0.7238%
2028 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 152 | 2 | 2371.786 | 97.71% | 2.108% | 0.1806% | 8.8431 | 0 | 0 | 8.8431 | 0 | 7.6764 | 0.20313 | 37.7911 | 7.6764 | 0.20313 | 37.7911 | 8.9738 | 0.23746 | 37.7911 | 0.3728%
2028 | 307 | 307-1492R | Tier-2 | Tier-2---9 | Tier-2---4 | 39 | 3 | 744.3133 | 92.56% | 7.329% | 0.1099% | 15.3688 | 0 | 0 | 15.3688 | 0 | 13.3411 | 0.30469 | 43.7856 | 13.3411 | 0.30469 | 43.7856 | 15.5959 | 0.35619 | 43.7856 | 2.065%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 5 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 59.9776 | 0 | 0 | 59.9776 | 0 | 52.0645 | 0.50782 | 102.5258 | 52.0645 | 0.50782 | 102.5258 | 60.864 | 0.59365 | 102.5258 | 2.492%
2028 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 98 | 2 | 2117.8574 | 97.53% | 2.33% | 0.1416% | 12.2245 | 0 | 0 | 12.2245 | 0 | 10.6117 | 0.20313 | 52.2415 | 10.6117 | 0.20313 | 52.2415 | 12.4052 | 0.23746 | 52.2415 | 0.5772%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 2 | 4762.848 | 95.55% | 4.384% | 0.07015% | 24.2147 | 0 | 0 | 24.2147 | 0 | 21.02 | 0.20313 | 103.4817 | 21.02 | 0.20313 | 103.4817 | 24.5726 | 0.23746 | 103.4817 | 0.5084%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | Tier-2---8 | 39 | 2 | 95.5263 | 19.37% | 79.9% | 0.729% | 0.27524 | 0 | 0 | 0.27524 | 0 | 0.23893 | 0.20313 | 1.1762 | 0.23893 | 0.20313 | 1.1762 | 0.27931 | 0.23746 | 1.1762 | 0.2881%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 15 | 1 | 15.6056 | 49.38% | 48.09% | 2.529% | 0.14899 | 0 | 0 | 0.14899 | 0 | 0.12934 | 0.10156 | 1.2734 | 0.12934 | 0.10156 | 1.2734 | 0.1512 | 0.11873 | 1.2734 | 0.9547%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 7 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.038925 | 0 | 0 | 0.038925 | 0 | 0.033789 | 0.71095 | 0.047527 | 0.033789 | 0.71095 | 0.047527 | 0.0395 | 0.8311 | 0.047527 | 0.02435%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 2 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.0033478 | 0 | 0 | 0.0033478 | 0 | 0.0029061 | 0.20313 | 0.014307 | 0.0029061 | 0.20313 | 0.014307 | 0.0033973 | 0.23746 | 0.014307 | 0.001656%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 39 | 4 | 209.8559 | 99.5% | 0% | 0.498% | 6.2108 | 0 | 0 | 6.2108 | 0 | 5.3914 | 0.40625 | 13.2709 | 5.3914 | 0.40625 | 13.2709 | 6.3026 | 0.47492 | 13.2709 | 2.96%
2028 | 334 | 334-21 | Tier-1 | Non-HFTD---2 | Non-HFTD---5 | 183 | 1 | 378.2145 | 89.09% | 9.517% | 1.396% | 0.53395 | 0 | 0 | 0.53395 | 0 | 0.46351 | 0.10156 | 4.5637 | 0.46351 | 0.10156 | 4.5637 | 0.54184 | 0.11873 | 4.5637 | 0.1412%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 15 | 1 | 302.428 | 99.27% | 0.6612% | 0.06922% | 5.8042 | 0 | 0 | 5.8042 | 0 | 5.0385 | 0.10156 | 49.6089 | 5.0385 | 0.10156 | 49.6089 | 5.89 | 0.11873 | 49.6089 | 1.919%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 54 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 95.3284 | 0 | 0 | 95.3284 | 0 | 82.7513 | 5.4844 | 15.0884 | 82.7513 | 5.4844 | 15.0884 | 96.7372 | 6.4114 | 15.0884 | 2.647%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 89 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 425.3725 | 0 | 0 | 425.3725 | 0 | 369.251 | 9.0392 | 40.8501 | 369.251 | 9.0392 | 40.8501 | 431.6587 | 10.5669 | 40.8501 | 3.066%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 70 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 135.9087 | 0 | 0 | 135.9087 | 0 | 117.9776 | 7.1095 | 16.5945 | 117.9776 | 7.1095 | 16.5945 | 137.9172 | 8.311 | 16.5945 | 2.44%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 47 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 506.8762 | 0 | 0 | 506.8762 | 0 | 440.0016 | 4.7735 | 92.1761 | 440.0016 | 4.7735 | 92.1761 | 514.3669 | 5.5803 | 92.1761 | 3.749%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 36 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 243.4257 | 0 | 0 | 243.4257 | 0 | 211.3094 | 3.6563 | 57.7934 | 211.3094 | 3.6563 | 57.7934 | 247.0231 | 4.2742 | 57.7934 | 2.173%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 29 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 575.6545 | 0 | 0 | 575.6545 | 0 | 499.7056 | 2.9453 | 169.6594 | 499.7056 | 2.9453 | 169.6594 | 584.1616 | 3.4431 | 169.6594 | 2.448%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 18 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 432.769 | 0 | 0 | 432.769 | 0 | 375.6717 | 1.8281 | 205.4934 | 375.6717 | 1.8281 | 205.4934 | 439.1645 | 2.1371 | 205.4934 | 4.733%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 35 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 522.913 | 0 | 0 | 522.913 | 0 | 453.9226 | 3.5547 | 127.6955 | 453.9226 | 3.5547 | 127.6955 | 530.6406 | 4.1555 | 127.6955 | 2.809%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 38 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 485.6436 | 0 | 0 | 485.6436 | 0 | 421.5703 | 3.8594 | 109.2316 | 421.5703 | 3.8594 | 109.2316 | 492.8205 | 4.5117 | 109.2316 | 5.266%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 1 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 12.9383 | 0 | 0 | 12.9383 | 0 | 11.2313 | 0.10156 | 110.5842 | 11.2313 | 0.10156 | 110.5842 | 13.1296 | 0.11873 | 110.5842 | 0.5136%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 25 | 1 | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 25.6842 | 0 | 0 | 25.6842 | 0 | 22.2955 | 0.10156 | 219.5227 | 22.2955 | 0.10156 | 219.5227 | 26.0637 | 0.11873 | 219.5227 | 1.159%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 2 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 30.3867 | 0 | 0 | 30.3867 | 0 | 26.3776 | 0.20313 | 129.8576 | 26.3776 | 0.20313 | 129.8576 | 30.8357 | 0.23746 | 129.8576 | 0.667%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 33 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 711.5428 | 0 | 0 | 711.5428 | 0 | 617.6656 | 3.3516 | 184.2898 | 617.6656 | 3.3516 | 184.2898 | 722.0581 | 3.9181 | 184.2898 | 5.257%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 61 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 748.0313 | 0 | 0 | 748.0313 | 0 | 649.3399 | 6.1954 | 104.8103 | 649.3399 | 6.1954 | 104.8103 | 759.0858 | 7.2425 | 104.8103 | 3.647%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 4 | 3653.654 | 88.54% | 11.39% | 0.07412% | 42.1613 | 0 | 0 | 42.1613 | 0 | 36.5988 | 0.40625 | 90.0883 | 36.5988 | 0.40625 | 90.0883 | 42.7844 | 0.47492 | 90.0883 | 1.154%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 15 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 142.2053 | 0 | 0 | 142.2053 | 0 | 123.4435 | 1.5235 | 81.0287 | 123.4435 | 1.5235 | 81.0287 | 144.3068 | 1.7809 | 81.0287 | 1.896%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 8 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 57.3166 | 0 | 0 | 57.3166 | 0 | 49.7545 | 0.81251 | 61.2357 | 49.7545 | 0.81251 | 61.2357 | 58.1636 | 0.94983 | 61.2357 | 1.054%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 44 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 271.4024 | 0 | 0 | 271.4024 | 0 | 235.595 | 4.4688 | 52.72 | 235.595 | 4.4688 | 52.72 | 275.4132 | 5.2241 | 52.72 | 1.695%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 730 | 41 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 144.4424 | 0 | 0 | 144.4424 | 0 | 125.3854 | 4.1641 | 30.111 | 125.3854 | 4.1641 | 30.111 | 146.577 | 4.8679 | 30.111 | 1.554%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 48 | 1 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 30.7065 | 0 | 0 | 30.7065 | 0 | 26.6553 | 0.10156 | 262.4488 | 26.6553 | 0.10156 | 262.4488 | 31.1603 | 0.11873 | 262.4488 | 0.6022%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 17 | 4 | 878.9304 | 95.49% | 4.482% | 0.03213% | 57.2665 | 0 | 0 | 57.2665 | 0 | 49.7111 | 0.40625 | 122.3643 | 49.7111 | 0.40625 | 122.3643 | 58.1128 | 0.47492 | 122.3643 | 6.515%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 29 | 16869.708 | 98.79% | 1.184% | 0.02933% | 517.168 | 0 | 0 | 517.168 | 0 | 448.9355 | 2.9453 | 152.422 | 448.9355 | 2.9453 | 152.422 | 524.8107 | 3.4431 | 152.422 | 3.066%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 20 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 275.6162 | 0 | 0 | 275.6162 | 0 | 239.2528 | 2.0313 | 117.7847 | 239.2528 | 2.0313 | 117.7847 | 279.6893 | 2.3746 | 117.7847 | 1.557%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 29 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 222.294 | 0 | 0 | 222.294 | 0 | 192.9657 | 2.9453 | 65.5155 | 192.9657 | 2.9453 | 65.5155 | 225.5791 | 3.4431 | 65.5155 | 2.131%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 31 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 380.0803 | 0 | 0 | 380.0803 | 0 | 329.9345 | 3.1485 | 104.7919 | 329.9345 | 3.1485 | 104.7919 | 385.6971 | 3.6806 | 104.7919 | 3.233%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 344 | 15 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 468.8018 | 0 | 0 | 468.8018 | 0 | 406.9505 | 1.5235 | 267.1235 | 406.9505 | 1.5235 | 267.1235 | 475.7298 | 1.7809 | 267.1235 | 1.247%
2028 | 362 | 362-47F | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 650 | 34 | 174.2726 | 36.5% | 57.41% | 6.096% | 0.96483 | 0 | 0 | 0.96483 | 0 | 0.83753 | 3.4532 | 0.24254 | 0.83753 | 3.4532 | 0.24254 | 0.97909 | 4.0368 | 0.24254 | 0.5536%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 76 | 2 | 924.8041 | 18.79% | 81.02% | 0.1888% | 1.326 | 0 | 0 | 1.326 | 0 | 1.151 | 0.20313 | 5.6665 | 1.151 | 0.20313 | 5.6665 | 1.3456 | 0.23746 | 5.6665 | 0.1434%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 84 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 90.0857 | 0 | 0 | 90.0857 | 0 | 78.2002 | 8.5313 | 9.1662 | 78.2002 | 8.5313 | 9.1662 | 91.4169 | 9.9732 | 9.1662 | 2.872%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 29 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 44.6885 | 0 | 0 | 44.6885 | 0 | 38.7926 | 2.9453 | 13.1708 | 38.7926 | 2.9453 | 13.1708 | 45.3489 | 3.4431 | 13.1708 | 2.406%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 79 | 6370.0414 | 98.47% | 1.262% | 0.272% | 167.8724 | 0 | 0 | 167.8724 | 0 | 145.7242 | 8.0235 | 18.1621 | 145.7242 | 8.0235 | 18.1621 | 170.3533 | 9.3796 | 18.1621 | 2.635%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 3 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 2.4565 | 0 | 0 | 2.4565 | 0 | 2.1324 | 0.30469 | 6.9987 | 2.1324 | 0.30469 | 6.9987 | 2.4928 | 0.35619 | 6.9987 | 0.1819%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 84 | 5 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 59.1808 | 0 | 0 | 59.1808 | 0 | 51.3728 | 0.50782 | 101.1638 | 51.3728 | 0.50782 | 101.1638 | 60.0554 | 0.59365 | 101.1638 | 1.682%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 1 | 582.1633 | 91.34% | 8.391% | 0.2732% | 3.2125 | 0 | 0 | 3.2125 | 0 | 2.7886 | 0.10156 | 27.4571 | 2.7886 | 0.10156 | 27.4571 | 3.26 | 0.11873 | 27.4571 | 0.5518%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 133 | 4 | 4750.1268 | 98% | 1.916% | 0.08125% | 40.6021 | 0 | 0 | 40.6021 | 0 | 35.2453 | 0.40625 | 86.7567 | 35.2453 | 0.40625 | 86.7567 | 41.2021 | 0.47492 | 86.7567 | 0.8548%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 16 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 242.2226 | 0 | 0 | 242.2226 | 0 | 210.265 | 1.625 | 129.3924 | 210.265 | 1.625 | 129.3924 | 245.8022 | 1.8997 | 129.3924 | 4.528%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 201 | 10 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 25.4383 | 0 | 0 | 25.4383 | 0 | 22.0821 | 1.0156 | 21.7421 | 22.0821 | 1.0156 | 21.7421 | 25.8142 | 1.1873 | 21.7421 | 1.386%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 3 | 852.9261 | 84.92% | 14.72% | 0.3553% | 4.3461 | 0 | 0 | 4.3461 | 0 | 3.7727 | 0.30469 | 12.382 | 3.7727 | 0.30469 | 12.382 | 4.4103 | 0.35619 | 12.382 | 0.5095%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 144 | 4 | 526.1263 | 57.95% | 41.57% | 0.4783% | 2.4562 | 0 | 0 | 2.4562 | 0 | 2.1321 | 0.40625 | 5.2482 | 2.1321 | 0.40625 | 5.2482 | 2.4925 | 0.47492 | 5.2482 | 0.4668%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 12 | 11572.221 | 88.48% | 11.4% | 0.1243% | 46.698 | 0 | 0 | 46.698 | 0 | 40.5369 | 1.2188 | 33.2607 | 40.5369 | 1.2188 | 33.2607 | 47.3881 | 1.4247 | 33.2607 | 0.4035%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | Tier-3---10 | 25 | 1 | 549.9829 | 98.93% | 0.9134% | 0.161% | 6.3113 | 0 | 0 | 6.3113 | 0 | 5.4786 | 0.10156 | 53.9424 | 5.4786 | 0.10156 | 53.9424 | 6.4045 | 0.11873 | 53.9424 | 1.148%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 74 | 1 | 474.7376 | 91.31% | 8.325% | 0.3651% | 1.6988 | 0 | 0 | 1.6988 | 0 | 1.4747 | 0.10156 | 14.5195 | 1.4747 | 0.10156 | 14.5195 | 1.7239 | 0.11873 | 14.5195 | 0.3578%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 122 | 2 | 333.8465 | 96.62% | 2.31% | 1.072% | 1.5335 | 0 | 0 | 1.5335 | 0 | 1.3311 | 0.20313 | 6.5532 | 1.3311 | 0.20313 | 6.5532 | 1.5561 | 0.23746 | 6.5532 | 0.4593%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 12 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 28.7922 | 0 | 0 | 28.7922 | 0 | 24.9935 | 1.2188 | 20.5073 | 24.9935 | 1.2188 | 20.5073 | 29.2177 | 1.4247 | 20.5073 | 0.8434%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 465 | 35 | 571.2373 | 70.71% | 27.93% | 1.361% | 8.8166 | 0 | 0 | 8.8166 | 0 | 7.6533 | 3.5547 | 2.153 | 7.6533 | 3.5547 | 2.153 | 8.9469 | 4.1555 | 2.153 | 1.543%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 22 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 173.1657 | 0 | 0 | 173.1657 | 0 | 150.3191 | 2.2344 | 67.2749 | 150.3191 | 2.2344 | 67.2749 | 175.7247 | 2.612 | 67.2749 | 1.798%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 23 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 211.267 | 0 | 0 | 211.267 | 0 | 183.3935 | 2.336 | 78.5087 | 183.3935 | 2.336 | 78.5087 | 214.3891 | 2.7308 | 78.5087 | 2.914%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 16 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 68.0544 | 0 | 0 | 68.0544 | 0 | 59.0756 | 1.625 | 36.3538 | 59.0756 | 1.625 | 36.3538 | 69.0601 | 1.8997 | 36.3538 | 4.244%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 117 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 655.498 | 0 | 0 | 655.498 | 0 | 569.015 | 11.8829 | 47.885 | 569.015 | 11.8829 | 47.885 | 665.1851 | 13.8913 | 47.885 | 6.172%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 5 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 9.1196 | 0 | 0 | 9.1196 | 0 | 7.9164 | 0.50782 | 15.5891 | 7.9164 | 0.50782 | 15.5891 | 9.2544 | 0.59365 | 15.5891 | 0.5162%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 8 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 30.3699 | 0 | 0 | 30.3699 | 0 | 26.3631 | 0.81251 | 32.4465 | 26.3631 | 0.81251 | 32.4465 | 30.8188 | 0.94983 | 32.4465 | 0.8256%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 7 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 13.4729 | 0 | 0 | 13.4729 | 0 | 11.6953 | 0.71095 | 16.4504 | 11.6953 | 0.71095 | 16.4504 | 13.672 | 0.8311 | 16.4504 | 0.3047%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | Tier-3---5 | 184 | 6 | 2612.2711 | 91.91% | 7.885% | 0.2065% | 22.7042 | 0 | 0 | 22.7042 | 0 | 19.7087 | 0.60938 | 32.3422 | 19.7087 | 0.60938 | 32.3422 | 23.0397 | 0.71237 | 32.3422 | 0.8691%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 314 | 8 | 2119.752 | 55.7% | 43.96% | 0.3458% | 8.7234 | 0 | 0 | 8.7234 | 0 | 7.5724 | 0.81251 | 9.3198 | 7.5724 | 0.81251 | 9.3198 | 8.8523 | 0.94983 | 9.3198 | 0.4115%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 10 | 520.639 | 76.18% | 22.78% | 1.038% | 5.6944 | 0 | 0 | 5.6944 | 0 | 4.9431 | 1.0156 | 4.867 | 4.9431 | 1.0156 | 4.867 | 5.7786 | 1.1873 | 4.867 | 1.094%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 170 | 1 | 630.7627 | 79.12% | 20.09% | 0.7869% | 0.85136 | 0 | 0 | 0.85136 | 0 | 0.73904 | 0.10156 | 7.2766 | 0.73904 | 0.10156 | 7.2766 | 0.86394 | 0.11873 | 7.2766 | 0.135%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 16 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 54.0181 | 0 | 0 | 54.0181 | 0 | 46.8913 | 1.625 | 28.8558 | 46.8913 | 1.625 | 28.8558 | 54.8164 | 1.8997 | 28.8558 | 0.5933%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 6 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 22.2184 | 0 | 0 | 22.2184 | 0 | 19.287 | 0.60938 | 31.6502 | 19.287 | 0.60938 | 31.6502 | 22.5468 | 0.71237 | 31.6502 | 0.3936%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 51 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 161.7082 | 0 | 0 | 161.7082 | 0 | 140.3733 | 5.1797 | 27.1004 | 140.3733 | 5.1797 | 27.1004 | 164.098 | 6.0552 | 27.1004 | 2.403%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 72 | 5 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 29.2059 | 0 | 0 | 29.2059 | 0 | 25.3527 | 0.50782 | 49.9247 | 25.3527 | 0.50782 | 49.9247 | 29.6376 | 0.59365 | 49.9247 | 1.953%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 26 | 6 | 625.3129 | 96.7% | 3.156% | 0.1473% | 40.4655 | 0 | 0 | 40.4655 | 0 | 35.1267 | 0.60938 | 57.6431 | 35.1267 | 0.60938 | 57.6431 | 41.0635 | 0.71237 | 57.6431 | 6.471%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 11 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 100.4588 | 0 | 0 | 100.4588 | 0 | 87.2048 | 1.1172 | 78.0566 | 87.2048 | 1.1172 | 78.0566 | 101.9434 | 1.306 | 78.0566 | 1.91%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 161 | 7 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 27.9498 | 0 | 0 | 27.9498 | 0 | 24.2623 | 0.71095 | 34.1268 | 24.2623 | 0.71095 | 34.1268 | 28.3629 | 0.8311 | 34.1268 | 1.205%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 1 | 296.7138 | 97.11% | 2.719% | 0.1664% | 4.6425 | 0 | 0 | 4.6425 | 0 | 4.03 | 0.10156 | 39.6792 | 4.03 | 0.10156 | 39.6792 | 4.7111 | 0.11873 | 39.6792 | 1.565%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 23 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 262.0283 | 0 | 0 | 262.0283 | 0 | 227.4577 | 2.336 | 97.3721 | 227.4577 | 2.336 | 97.3721 | 265.9006 | 2.7308 | 97.3721 | 3.167%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 13 | 792.2018 | 92.77% | 7.138% | 0.09408% | 62.9686 | 0 | 0 | 62.9686 | 0 | 54.6608 | 1.3203 | 41.3995 | 54.6608 | 1.3203 | 41.3995 | 63.8991 | 1.5435 | 41.3995 | 7.949%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 12 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.6177 | 0 | 0 | 53.6177 | 0 | 46.5437 | 1.2188 | 38.1892 | 46.5437 | 1.2188 | 38.1892 | 54.4101 | 1.4247 | 38.1892 | 4.735%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 2 | 625.5425 | 99.9% | 0% | 0.09615% | 18.1233 | 0 | 0 | 18.1233 | 0 | 15.7322 | 0.20313 | 77.45 | 15.7322 | 0.20313 | 77.45 | 18.3911 | 0.23746 | 77.45 | 2.897%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 3 | 2823.7515 | 99.93% | 0% | 0.06613% | 34.578 | 0 | 0 | 34.578 | 0 | 30.016 | 0.30469 | 98.5129 | 30.016 | 0.30469 | 98.5129 | 35.089 | 0.35619 | 98.5129 | 1.225%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 53 | 15 | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 281.5845 | 0 | 0 | 281.5845 | 0 | 244.4337 | 1.5235 | 160.447 | 244.4337 | 1.5235 | 160.447 | 285.7458 | 1.7809 | 160.447 | 8.183%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 7 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 11.9935 | 0 | 0 | 11.9935 | 0 | 10.4111 | 0.71095 | 14.644 | 10.4111 | 0.71095 | 14.644 | 12.1707 | 0.8311 | 14.644 | 0.8702%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 12 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 126.8722 | 0 | 0 | 126.8722 | 0 | 110.1333 | 1.2188 | 90.3648 | 110.1333 | 1.2188 | 90.3648 | 128.7471 | 1.4247 | 90.3648 | 2.41%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 17 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 153.5776 | 0 | 0 | 153.5776 | 0 | 133.3154 | 1.7266 | 77.2135 | 133.3154 | 1.7266 | 77.2135 | 155.8472 | 2.0184 | 77.2135 | 0.9174%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 128 | 1 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 9.1512 | 0 | 0 | 9.1512 | 0 | 7.9439 | 0.10156 | 78.2157 | 7.9439 | 0.10156 | 78.2157 | 9.2865 | 0.11873 | 78.2157 | 0.2151%
2028 | 492 | 492-1090F | Tier-1 | Non-HFTD---8 | Non-HFTD---16 | 134 | 2 | 34.6286 | 4.526% | 88.49% | 6.986% | 0.0067839 | 0 | 0 | 0.0067839 | 0 | 0.0058889 | 0.20313 | 0.028991 | 0.0058889 | 0.20313 | 0.028991 | 0.0068842 | 0.23746 | 0.028991 | 0.01959%
2028 | 492 | 492-14R | Tier-1 | Non-HFTD---2 | Non-HFTD---8 | 453 | 3 | 216.5783 | 3.253% | 93.45% | 3.298% | 0.013532 | 0 | 0 | 0.013532 | 0 | 0.011747 | 0.30469 | 0.038553 | 0.011747 | 0.30469 | 0.038553 | 0.013732 | 0.35619 | 0.038553 | 0.006248%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 23 | 1 | 204.0835 | 99.63% | 0% | 0.368% | 2.5638 | 0 | 0 | 2.5638 | 0 | 2.2255 | 0.10156 | 21.9125 | 2.2255 | 0.10156 | 21.9125 | 2.6016 | 0.11873 | 21.9125 | 1.256%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | Tier-2---3 | 180 | 12 | 2978.814 | 97.34% | 2.471% | 0.184% | 56.0612 | 0 | 0 | 56.0612 | 0 | 48.6648 | 1.2188 | 39.9296 | 48.6648 | 1.2188 | 39.9296 | 56.8897 | 1.4247 | 39.9296 | 1.882%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 155 | 13 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 35.2383 | 0 | 0 | 35.2383 | 0 | 30.5891 | 1.3203 | 23.1678 | 30.5891 | 1.3203 | 23.1678 | 35.759 | 1.5435 | 23.1678 | 2.383%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 408 | 19 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 34.4695 | 0 | 0 | 34.4695 | 0 | 29.9218 | 1.9297 | 15.5058 | 29.9218 | 1.9297 | 15.5058 | 34.9789 | 2.2559 | 15.5058 | 1.307%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | Tier-2---3 | 401 | 51 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 116.7485 | 0 | 0 | 116.7485 | 0 | 101.3453 | 5.1797 | 19.5657 | 101.3453 | 5.1797 | 19.5657 | 118.4738 | 6.0552 | 19.5657 | 3.42%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 7 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 22.4675 | 0 | 0 | 22.4675 | 0 | 19.5033 | 0.71095 | 27.4329 | 19.5033 | 0.71095 | 27.4329 | 22.7996 | 0.8311 | 27.4329 | 1.376%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 249 | 10 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 76.1805 | 0 | 0 | 76.1805 | 0 | 66.1296 | 1.0156 | 65.1115 | 66.1296 | 1.0156 | 65.1115 | 77.3063 | 1.1873 | 65.1115 | 1.126%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 16 | 748.333 | 77.34% | 21.7% | 0.962% | 6.5818 | 0 | 0 | 6.5818 | 0 | 5.7134 | 1.625 | 3.5159 | 5.7134 | 1.625 | 3.5159 | 6.679 | 1.8997 | 3.5159 | 0.8795%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 276 | 25 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 52.8309 | 0 | 0 | 52.8309 | 0 | 45.8606 | 2.5391 | 18.0618 | 45.8606 | 2.5391 | 18.0618 | 53.6116 | 2.9682 | 18.0618 | 2.534%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 113 | 11 | 258.296 | 74.72% | 24.53% | 0.7505% | 5.4486 | 0 | 0 | 5.4486 | 0 | 4.7297 | 1.1172 | 4.2336 | 4.7297 | 1.1172 | 4.2336 | 5.5291 | 1.306 | 4.2336 | 2.109%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | Tier-3---1 | 306 | 2 | 4997.7942 | 96.49% | 3.313% | 0.193% | 9.1409 | 0 | 0 | 9.1409 | 0 | 7.9349 | 0.20313 | 39.0635 | 7.9349 | 0.20313 | 39.0635 | 9.2759 | 0.23746 | 39.0635 | 0.1829%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | Tier-2---1 | 219 | 5 | 2044.6463 | 97.57% | 2.13% | 0.298% | 13.2089 | 0 | 0 | 13.2089 | 0 | 11.4662 | 0.50782 | 22.5793 | 11.4662 | 0.50782 | 22.5793 | 13.4041 | 0.59365 | 22.5793 | 0.646%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 23 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 232.3854 | 0 | 0 | 232.3854 | 0 | 201.7257 | 2.336 | 86.3565 | 201.7257 | 2.336 | 86.3565 | 235.8196 | 2.7308 | 86.3565 | 2.047%
2028 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 10 | 810.9996 | 89.31% | 10.24% | 0.4457% | 10.5556 | 0 | 0 | 10.5556 | 0 | 9.163 | 1.0156 | 9.0219 | 9.163 | 1.0156 | 9.0219 | 10.7116 | 1.1873 | 9.0219 | 1.302%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 15 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 107.6545 | 0 | 0 | 107.6545 | 0 | 93.4512 | 1.5235 | 61.3416 | 93.4512 | 1.5235 | 61.3416 | 109.2455 | 1.7809 | 61.3416 | 1.27%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 19 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 155.3821 | 0 | 0 | 155.3821 | 0 | 134.8818 | 1.9297 | 69.8975 | 134.8818 | 1.9297 | 69.8975 | 157.6783 | 2.2559 | 69.8975 | 1.783%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 24 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 107.8998 | 0 | 0 | 107.8998 | 0 | 93.6641 | 2.4375 | 38.4259 | 93.6641 | 2.4375 | 38.4259 | 109.4944 | 2.8495 | 38.4259 | 1.92%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | Tier-3---1 | 232 | 31 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 471.4201 | 0 | 0 | 471.4201 | 0 | 409.2234 | 3.1485 | 129.9752 | 409.2234 | 3.1485 | 129.9752 | 478.3868 | 3.6806 | 129.9752 | 3.851%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 437 | 34 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 201.4223 | 0 | 0 | 201.4223 | 0 | 174.8477 | 3.4532 | 50.6341 | 174.8477 | 3.4532 | 50.6341 | 204.3989 | 4.0368 | 50.6341 | 2.235%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 6 | 112.7117 | 43.02% | 55.81% | 1.165% | 1.3184 | 0 | 0 | 1.3184 | 0 | 1.1445 | 0.60938 | 1.8781 | 1.1445 | 0.60938 | 1.8781 | 1.3379 | 0.71237 | 1.8781 | 1.17%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 12 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.98618 | 0 | 0 | 0.98618 | 0 | 0.85607 | 1.2188 | 0.7024 | 0.85607 | 1.2188 | 0.7024 | 1.0007 | 1.4247 | 0.7024 | 0.8432%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 50 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 130.1444 | 0 | 0 | 130.1444 | 0 | 112.9738 | 5.0782 | 22.2469 | 112.9738 | 5.0782 | 22.2469 | 132.0677 | 5.9365 | 22.2469 | 2.308%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 6 | 305.199 | 11.7% | 87.21% | 1.095% | 0.31213 | 0 | 0 | 0.31213 | 0 | 0.27095 | 0.60938 | 0.44463 | 0.27095 | 0.60938 | 0.44463 | 0.31674 | 0.71237 | 0.44463 | 0.1023%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 231 | 27 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 184.9327 | 0 | 0 | 184.9327 | 0 | 160.5336 | 2.7422 | 58.5415 | 160.5336 | 2.7422 | 58.5415 | 187.6656 | 3.2057 | 58.5415 | 3.382%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 489 | 39 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 261.1606 | 0 | 0 | 261.1606 | 0 | 226.7044 | 3.961 | 57.2344 | 226.7044 | 3.961 | 57.2344 | 265.02 | 4.6304 | 57.2344 | 2.308%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 283 | 28 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 389.4178 | 0 | 0 | 389.4178 | 0 | 338.04 | 2.8438 | 118.8699 | 338.04 | 2.8438 | 118.8699 | 395.1727 | 3.3244 | 118.8699 | 2.84%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 30 | 8801.877 | 98.2% | 1.718% | 0.0819% | 265.7187 | 0 | 0 | 265.7187 | 0 | 230.6612 | 3.0469 | 75.7033 | 230.6612 | 3.0469 | 75.7033 | 269.6456 | 3.5619 | 75.7033 | 3.019%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 842 | 93 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1280.7555 | 0 | 0 | 1280.7555 | 0 | 1111.7792 | 9.4454 | 117.7057 | 1111.7792 | 9.4454 | 117.7057 | 1299.6826 | 11.0418 | 117.7057 | 3.172%
2028 | 57 | 57-736 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 81 | 4 | 116.8924 | 0.4896% | 98.37% | 1.142% | 0.0081964 | 0 | 0 | 0.0081964 | 0 | 0.007115 | 0.40625 | 0.017514 | 0.007115 | 0.40625 | 0.017514 | 0.0083176 | 0.47492 | 0.017514 | 0.007012%
2028 | 586 | 586-3 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 84 | 5 | 516.8084 | 87.93% | 11.54% | 0.527% | 7.8444 | 0 | 0 | 7.8444 | 0 | 6.8095 | 0.50782 | 13.4092 | 6.8095 | 0.50782 | 13.4092 | 7.9603 | 0.59365 | 13.4092 | 1.518%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 92 | 2 | 519.9571 | 96.32% | 3.27% | 0.4047% | 3.1575 | 0 | 0 | 3.1575 | 0 | 2.7409 | 0.20313 | 13.4937 | 2.7409 | 0.20313 | 13.4937 | 3.2042 | 0.23746 | 13.4937 | 0.6073%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 9 | 1 | 49.4293 | 99.41% | 0% | 0.5897% | 1.5833 | 0 | 0 | 1.5833 | 0 | 1.3744 | 0.10156 | 13.5327 | 1.3744 | 0.10156 | 13.5327 | 1.6067 | 0.11873 | 13.5327 | 3.203%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 25 | 18774.394 | 95.55% | 4.388% | 0.06321% | 326.7742 | 0 | 0 | 326.7742 | 0 | 283.6613 | 2.5391 | 111.7177 | 283.6613 | 2.5391 | 111.7177 | 331.6033 | 2.9682 | 111.7177 | 1.741%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 69 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 679.9681 | 0 | 0 | 679.9681 | 0 | 590.2566 | 7.0079 | 84.2274 | 590.2566 | 7.0079 | 84.2274 | 690.0167 | 8.1923 | 84.2274 | 2.641%
2028 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 477 | 1 | 5312.2676 | 97.77% | 1.999% | 0.2313% | 3.1576 | 0 | 0 | 3.1576 | 0 | 2.741 | 0.10156 | 26.9884 | 2.741 | 0.10156 | 26.9884 | 3.2043 | 0.11873 | 26.9884 | 0.05944%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 344 | 41 | 2610.8 | 93.6% | 6.065% | 0.3401% | 84.46 | 0 | 0 | 84.46 | 0 | 73.3168 | 4.1641 | 17.6068 | 73.3168 | 4.1641 | 17.6068 | 85.7081 | 4.8679 | 17.6068 | 3.235%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 551 | 46 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 94.9315 | 0 | 0 | 94.9315 | 0 | 82.4067 | 4.6719 | 17.6387 | 82.4067 | 4.6719 | 17.6387 | 96.3344 | 5.4615 | 17.6387 | 2.271%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 19 | 622.3042 | 87.18% | 11.98% | 0.8373% | 15.7332 | 0 | 0 | 15.7332 | 0 | 13.6574 | 1.9297 | 7.0775 | 13.6574 | 1.9297 | 7.0775 | 15.9657 | 2.2559 | 7.0775 | 2.528%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 20 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 37.6005 | 0 | 0 | 37.6005 | 0 | 32.6397 | 2.0313 | 16.0686 | 32.6397 | 2.0313 | 16.0686 | 38.1562 | 2.3746 | 16.0686 | 2.31%
2028 | 702 | 702-25 | Tier-1 | Non-HFTD---4 | Non-HFTD---13 | 20 | 3 | 105.79 | 16.96% | 82.58% | 0.4592% | 0.78055 | 0 | 0 | 0.78055 | 0 | 0.67757 | 0.30469 | 2.2238 | 0.67757 | 0.30469 | 2.2238 | 0.79209 | 0.35619 | 2.2238 | 0.7378%
2028 | 702 | 702-27R | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 513 | 4 | 127.2983 | 14.57% | 79% | 6.429% | 0.041945 | 0 | 0 | 0.041945 | 0 | 0.036411 | 0.40625 | 0.089626 | 0.036411 | 0.40625 | 0.089626 | 0.042565 | 0.47492 | 0.089626 | 0.03295%
2028 | 702 | 702-30 | Tier-1 | Non-HFTD---3 | Non-HFTD---8 | 328 | 1 | 100.3702 | 67.48% | 26.99% | 5.53% | 0.059879 | 0 | 0 | 0.059879 | 0 | 0.051979 | 0.10156 | 0.51179 | 0.051979 | 0.10156 | 0.51179 | 0.060764 | 0.11873 | 0.51179 | 0.05966%
2028 | 702 | 702-448F | Tier-1 | Non-HFTD---19 | Non-HFTD---22 | 2 | 1 | 0.36733 | 90.03% | 0% | 9.967% | 0.047955 | 0 | 0 | 0.047955 | 0 | 0.041628 | 0.10156 | 0.40987 | 0.041628 | 0.10156 | 0.40987 | 0.048663 | 0.11873 | 0.40987 | 13.05%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 310 | 14 | 6201.607 | 97.29% | 2.601% | 0.1104% | 79.0189 | 0 | 0 | 79.0189 | 0 | 68.5936 | 1.4219 | 48.2411 | 68.5936 | 1.4219 | 48.2411 | 80.1867 | 1.6622 | 48.2411 | 1.274%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 3 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 40.3415 | 0 | 0 | 40.3415 | 0 | 35.0191 | 0.30469 | 114.9331 | 35.0191 | 0.30469 | 114.9331 | 40.9377 | 0.35619 | 114.9331 | 0.263%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 188 | 5 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 43.5192 | 0 | 0 | 43.5192 | 0 | 37.7775 | 0.50782 | 74.3919 | 37.7775 | 0.50782 | 74.3919 | 44.1624 | 0.59365 | 74.3919 | 0.759%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | Tier-3---1 | 313 | 18 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 173.6513 | 0 | 0 | 173.6513 | 0 | 150.7406 | 1.8281 | 82.4555 | 150.7406 | 1.8281 | 82.4555 | 176.2175 | 2.1371 | 82.4555 | 1.64%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 273 | 7 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 67.9793 | 0 | 0 | 67.9793 | 0 | 59.0105 | 0.71095 | 83.0028 | 59.0105 | 0.71095 | 83.0028 | 68.9839 | 0.8311 | 83.0028 | 0.7319%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 8 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 51.8399 | 0 | 0 | 51.8399 | 0 | 45.0004 | 0.81251 | 55.3845 | 45.0004 | 0.81251 | 55.3845 | 52.606 | 0.94983 | 55.3845 | 1.653%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 13 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 76.3478 | 0 | 0 | 76.3478 | 0 | 66.2749 | 1.3203 | 50.1958 | 66.2749 | 1.3203 | 50.1958 | 77.4761 | 1.5435 | 50.1958 | 4.469%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 69 | 4 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 32.5276 | 0 | 0 | 32.5276 | 0 | 28.2361 | 0.40625 | 69.5035 | 28.2361 | 0.40625 | 69.5035 | 33.0083 | 0.47492 | 69.5035 | 1.679%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 16 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 31.9135 | 0 | 0 | 31.9135 | 0 | 27.703 | 1.625 | 17.0478 | 27.703 | 1.625 | 17.0478 | 32.3851 | 1.8997 | 17.0478 | 1.443%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 186 | 5 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 111.6119 | 0 | 0 | 111.6119 | 0 | 96.8864 | 0.50782 | 190.7896 | 96.8864 | 0.50782 | 190.7896 | 113.2613 | 0.59365 | 190.7896 | 0.7683%
2028 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 29 | 1 | 5696.3358 | 99.98% | 0% | 0.01771% | 56.9533 | 0 | 0 | 56.9533 | 0 | 49.4391 | 0.10156 | 486.7801 | 49.4391 | 0.10156 | 486.7801 | 57.7949 | 0.11873 | 486.7801 | 0.9998%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 2 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 9.5902 | 0 | 0 | 9.5902 | 0 | 8.325 | 0.20313 | 40.9839 | 8.325 | 0.20313 | 40.9839 | 9.732 | 0.23746 | 40.9839 | 0.105%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 4 | 3349.7594 | 92.58% | 7.304% | 0.116% | 25.5136 | 0 | 0 | 25.5136 | 0 | 22.1474 | 0.40625 | 54.5161 | 22.1474 | 0.40625 | 54.5161 | 25.8906 | 0.47492 | 54.5161 | 0.7617%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 198 | 3 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 53.7396 | 0 | 0 | 53.7396 | 0 | 46.6495 | 0.30469 | 153.1043 | 46.6495 | 0.30469 | 153.1043 | 54.5338 | 0.35619 | 153.1043 | 0.4362%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 3 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 9.8867 | 0 | 0 | 9.8867 | 0 | 8.5823 | 0.30469 | 28.1673 | 8.5823 | 0.30469 | 28.1673 | 10.0328 | 0.35619 | 28.1673 | 0.4737%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 3 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 3.2089 | 0 | 0 | 3.2089 | 0 | 2.7855 | 0.30469 | 9.1422 | 2.7855 | 0.30469 | 9.1422 | 3.2563 | 0.35619 | 9.1422 | 0.1997%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 4 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 80.2554 | 0 | 0 | 80.2554 | 0 | 69.6669 | 0.40625 | 171.4858 | 69.6669 | 0.40625 | 171.4858 | 81.4414 | 0.47492 | 171.4858 | 0.8262%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 192 | 14 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 385.8085 | 0 | 0 | 385.8085 | 0 | 334.9069 | 1.4219 | 235.5363 | 334.9069 | 1.4219 | 235.5363 | 391.51 | 1.6622 | 235.5363 | 2.091%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | Tier-3---3 | 74 | 2 | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 19.9763 | 0 | 0 | 19.9763 | 0 | 17.3408 | 0.20313 | 85.3689 | 17.3408 | 0.20313 | 85.3689 | 20.2715 | 0.23746 | 85.3689 | 0.7789%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 180 | 2 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 17.1827 | 0 | 0 | 17.1827 | 0 | 14.9157 | 0.20313 | 73.4302 | 14.9157 | 0.20313 | 73.4302 | 17.4366 | 0.23746 | 73.4302 | 0.3103%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 8 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 99.127 | 0 | 0 | 99.127 | 0 | 86.0487 | 0.81251 | 105.9049 | 86.0487 | 0.81251 | 105.9049 | 100.5919 | 0.94983 | 105.9049 | 0.5278%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 218 | 26 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 685.679 | 0 | 0 | 685.679 | 0 | 595.2141 | 2.6407 | 225.404 | 595.2141 | 2.6407 | 225.404 | 695.8121 | 3.087 | 225.404 | 3.432%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 1 | 127.4062 | 99.28% | 0% | 0.716% | 0.96535 | 0 | 0 | 0.96535 | 0 | 0.83799 | 0.10156 | 8.2508 | 0.83799 | 0.10156 | 8.2508 | 0.97961 | 0.11873 | 8.2508 | 0.7577%
2028 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 2 | 12.4137 | 98.83% | 0% | 1.166% | 0.54739 | 0 | 0 | 0.54739 | 0 | 0.47517 | 0.20313 | 2.3393 | 0.47517 | 0.20313 | 2.3393 | 0.55547 | 0.23746 | 2.3393 | 4.41%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | Tier-2---8 | 40 | 1 | 232.5563 | 96.66% | 2.796% | 0.5416% | 1.6298 | 0 | 0 | 1.6298 | 0 | 1.4147 | 0.10156 | 13.9296 | 1.4147 | 0.10156 | 13.9296 | 1.6539 | 0.11873 | 13.9296 | 0.7008%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 14 | 8606.9717 | 99.86% | 0% | 0.1411% | 62.6481 | 0 | 0 | 62.6481 | 0 | 54.3826 | 1.4219 | 38.2467 | 54.3826 | 1.4219 | 38.2467 | 63.5739 | 1.6622 | 38.2467 | 0.7279%
2028 | 907 | 907-1475 | Tier-3 | Tier-3---21 | Tier-3---21 | 4 | 1 | 4.2814 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.10156 | 0 | 0 | 0.10156 | 0 | 0 | 0.11873 | 0 | 0%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 162 | 15 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 221.2207 | 0 | 0 | 221.2207 | 0 | 192.034 | 1.5235 | 126.0517 | 192.034 | 1.5235 | 126.0517 | 224.4899 | 1.7809 | 126.0517 | 2.621%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 15 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 266.7506 | 0 | 0 | 266.7506 | 0 | 231.5569 | 1.5235 | 151.9947 | 231.5569 | 1.5235 | 151.9947 | 270.6927 | 1.7809 | 151.9947 | 2.931%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 28 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 561.8741 | 0 | 0 | 561.8741 | 0 | 487.7434 | 2.8438 | 171.5123 | 487.7434 | 2.8438 | 171.5123 | 570.1776 | 3.3244 | 171.5123 | 2.076%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 26 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 385.7737 | 0 | 0 | 385.7737 | 0 | 334.8767 | 2.6407 | 126.8158 | 334.8767 | 2.6407 | 126.8158 | 391.4747 | 3.087 | 126.8158 | 2.447%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 17 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 345.189 | 0 | 0 | 345.189 | 0 | 299.6466 | 1.7266 | 173.549 | 299.6466 | 1.7266 | 173.549 | 350.2903 | 2.0184 | 173.549 | 2.934%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 471 | 78 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 257.5035 | 0 | 0 | 257.5035 | 0 | 223.5299 | 7.922 | 28.2165 | 223.5299 | 7.922 | 28.2165 | 261.3089 | 9.2609 | 28.2165 | 4.622%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 15 | 1466.2762 | 91.81% | 7.905% | 0.289% | 39.0377 | 0 | 0 | 39.0377 | 0 | 33.8873 | 1.5235 | 22.2437 | 33.8873 | 1.5235 | 22.2437 | 39.6146 | 1.7809 | 22.2437 | 2.662%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 9 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 166.122 | 0 | 0 | 166.122 | 0 | 144.2047 | 0.91407 | 157.7607 | 144.2047 | 0.91407 | 157.7607 | 168.577 | 1.0686 | 157.7607 | 2.087%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 24 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 519.1494 | 0 | 0 | 519.1494 | 0 | 450.6555 | 2.4375 | 184.8823 | 450.6555 | 2.4375 | 184.8823 | 526.8214 | 2.8495 | 184.8823 | 1.258%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 162 | 8 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 48.0007 | 0 | 0 | 48.0007 | 0 | 41.6678 | 0.81251 | 51.2828 | 41.6678 | 0.81251 | 51.2828 | 48.7101 | 0.94983 | 51.2828 | 1.316%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 31 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 553.701 | 0 | 0 | 553.701 | 0 | 480.6486 | 3.1485 | 152.6609 | 480.6486 | 3.1485 | 152.6609 | 561.8836 | 3.6806 | 152.6609 | 2.454%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 49 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 1540.3744 | 0 | 0 | 1540.3744 | 0 | 1337.1453 | 4.9766 | 268.6856 | 1337.1453 | 4.9766 | 268.6856 | 1563.1381 | 5.8177 | 268.6856 | 2.788%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 1 | 5703.0403 | 99.97% | 0% | 0.03309% | 26.6667 | 0 | 0 | 26.6667 | 0 | 23.1484 | 0.10156 | 227.9204 | 23.1484 | 0.10156 | 227.9204 | 27.0608 | 0.11873 | 227.9204 | 0.4676%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 40 | 32313.161 | 99.26% | 0.708% | 0.02831% | 1204.1195 | 0 | 0 | 1204.1195 | 0 | 1045.2542 | 4.0625 | 257.2905 | 1045.2542 | 4.0625 | 257.2905 | 1221.9141 | 4.7492 | 257.2905 | 3.726%
2028 | 909 | 909-812 | Tier-2 | Tier-2---17 | Tier-2---11 | 3 | 1 | 62.9838 | 99.88% | 0% | 0.1185% | 6.0812 | 0 | 0 | 6.0812 | 0 | 5.2789 | 0.10156 | 51.9763 | 5.2789 | 0.10156 | 51.9763 | 6.1711 | 0.11873 | 51.9763 | 9.655%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 194 | 2 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 3.7188 | 0 | 0 | 3.7188 | 0 | 3.2282 | 0.20313 | 15.8924 | 3.2282 | 0.20313 | 15.8924 | 3.7738 | 0.23746 | 15.8924 | 0.2869%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 1 | 1554.328 | 69.02% | 30.62% | 0.3611% | 1.0546 | 0 | 0 | 1.0546 | 0 | 0.91549 | 0.10156 | 9.014 | 0.91549 | 0.10156 | 9.014 | 1.0702 | 0.11873 | 9.014 | 0.06785%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 36 | 1 | 434.8834 | 99.47% | 0.2691% | 0.2608% | 3.4847 | 0 | 0 | 3.4847 | 0 | 3.0249 | 0.10156 | 29.7835 | 3.0249 | 0.10156 | 29.7835 | 3.5362 | 0.11873 | 29.7835 | 0.8013%
2028 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 5 | 62.492 | 96.91% | 0.773% | 2.32% | 1.9957 | 0 | 0 | 1.9957 | 0 | 1.7324 | 0.50782 | 3.4115 | 1.7324 | 0.50782 | 3.4115 | 2.0252 | 0.59365 | 3.4115 | 3.194%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 8 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 325.7399 | 0 | 0 | 325.7399 | 0 | 282.7635 | 0.81251 | 348.0127 | 282.7635 | 0.81251 | 348.0127 | 330.5537 | 0.94983 | 348.0127 | 2.513%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 30 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 379.4944 | 0 | 0 | 379.4944 | 0 | 329.4259 | 3.0469 | 108.1181 | 329.4259 | 3.0469 | 108.1181 | 385.1026 | 3.5619 | 108.1181 | 2.505%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 33 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 451.6461 | 0 | 0 | 451.6461 | 0 | 392.0583 | 3.3516 | 116.9765 | 392.0583 | 3.3516 | 116.9765 | 458.3206 | 3.9181 | 116.9765 | 1.586%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 106 | 14 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 305.3624 | 0 | 0 | 305.3624 | 0 | 265.0745 | 1.4219 | 186.4239 | 265.0745 | 1.4219 | 186.4239 | 309.8751 | 1.6622 | 186.4239 | 3.81%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 1 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 21.6522 | 0 | 0 | 21.6522 | 0 | 18.7955 | 0.10156 | 185.0618 | 18.7955 | 0.10156 | 185.0618 | 21.9722 | 0.11873 | 185.0618 | 0.4976%
2028 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 1 | 191.8954 | 99.94% | 0% | 0.06293% | 27.8073 | 0 | 0 | 27.8073 | 0 | 24.1386 | 0.10156 | 237.6694 | 24.1386 | 0.10156 | 237.6694 | 28.2183 | 0.11873 | 237.6694 | 14.49%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 25 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 375.1163 | 0 | 0 | 375.1163 | 0 | 325.6254 | 2.5391 | 128.2449 | 325.6254 | 2.5391 | 128.2449 | 380.6598 | 2.9682 | 128.2449 | 2.54%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | Tier-3---1 | 406 | 18 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 143.3924 | 0 | 0 | 143.3924 | 0 | 124.474 | 1.8281 | 68.0876 | 124.474 | 1.8281 | 68.0876 | 145.5115 | 2.1371 | 68.0876 | 1.273%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 213 | 1 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 10.7581 | 0 | 0 | 10.7581 | 0 | 9.3388 | 0.10156 | 91.95 | 9.3388 | 0.10156 | 91.95 | 10.9171 | 0.11873 | 91.95 | 0.1342%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 38 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 364.1642 | 0 | 0 | 364.1642 | 0 | 316.1182 | 3.8594 | 81.9083 | 316.1182 | 3.8594 | 81.9083 | 369.5458 | 4.5117 | 81.9083 | 1.556%
2028 | 972 | 972-1642 | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 4 | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.40625 | 0 | 0 | 0.40625 | 0 | 0 | 0.47492 | 0 | 0%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 543 | 53 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 632.2502 | 0 | 0 | 632.2502 | 0 | 548.8344 | 5.3829 | 101.9594 | 548.8344 | 5.3829 | 101.9594 | 641.5937 | 6.2926 | 101.9594 | 2.759%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 189 | 10 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 139.1515 | 0 | 0 | 139.1515 | 0 | 120.7926 | 1.0156 | 118.9329 | 120.7926 | 1.0156 | 118.9329 | 141.2079 | 1.1873 | 118.9329 | 1.521%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 9 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 67.7963 | 0 | 0 | 67.7963 | 0 | 58.8516 | 0.91407 | 64.3839 | 58.8516 | 0.91407 | 64.3839 | 68.7982 | 1.0686 | 64.3839 | 1.309%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 11 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 463.8924 | 0 | 0 | 463.8924 | 0 | 402.6888 | 1.1172 | 360.4447 | 402.6888 | 1.1172 | 360.4447 | 470.7478 | 1.306 | 360.4447 | 5.382%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 389 | 18 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 43.9147 | 0 | 0 | 43.9147 | 0 | 38.1208 | 1.8281 | 20.8522 | 38.1208 | 1.8281 | 20.8522 | 44.5636 | 2.1371 | 20.8522 | 1.257%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 6 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 91.8698 | 0 | 0 | 91.8698 | 0 | 79.749 | 0.60938 | 130.8686 | 79.749 | 0.60938 | 130.8686 | 93.2274 | 0.71237 | 130.8686 | 1.293%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | Tier-3---1 | 30 | 2 | 6417.0381 | 80.3% | 19.69% | 0.01691% | 99.619 | 0 | 0 | 99.619 | 0 | 86.4757 | 0.20313 | 425.722 | 86.4757 | 0.20313 | 425.722 | 101.0911 | 0.23746 | 425.722 | 1.552%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 1 | 626.8618 | 65.87% | 33.98% | 0.153% | 4.1291 | 0 | 0 | 4.1291 | 0 | 3.5843 | 0.10156 | 35.2911 | 3.5843 | 0.10156 | 35.2911 | 4.1901 | 0.11873 | 35.2911 | 0.6587%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 18 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 145.3541 | 0 | 0 | 145.3541 | 0 | 126.1769 | 1.8281 | 69.0191 | 126.1769 | 1.8281 | 69.0191 | 147.5022 | 2.1371 | 69.0191 | 3.176%
2028 | CB 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 5 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 61.8381 | 0 | 0 | 61.8381 | 0 | 53.6795 | 0.50782 | 105.7062 | 53.6795 | 0.50782 | 105.7062 | 62.752 | 0.59365 | 105.7062 | 1.855%
2028 | CB 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 111 | 9 | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 33.1341 | 0 | 0 | 33.1341 | 0 | 28.7625 | 0.91407 | 31.4663 | 28.7625 | 0.91407 | 31.4663 | 33.6237 | 1.0686 | 31.4663 | 2.342%
2028 | CB 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 1 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 7.9934 | 0 | 0 | 7.9934 | 0 | 6.9388 | 0.10156 | 68.3199 | 6.9388 | 0.10156 | 68.3199 | 8.1116 | 0.11873 | 68.3199 | 0.7053%
2028 | CB 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 7 | 765.4961 | 75% | 24.28% | 0.7274% | 4.0048 | 0 | 0 | 4.0048 | 0 | 3.4764 | 0.71095 | 4.8899 | 3.4764 | 0.71095 | 4.8899 | 4.064 | 0.8311 | 4.8899 | 0.5232%
2028 | CB 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 34 | 4 | 75.2008 | 96.65% | 1.975% | 1.378% | 2.4796 | 0 | 0 | 2.4796 | 0 | 2.1525 | 0.40625 | 5.2984 | 2.1525 | 0.40625 | 5.2984 | 2.5163 | 0.47492 | 5.2984 | 3.297%
2028 | CB 120 | CB 120 | Tier-1 | Non-HFTD---5 | Non-HFTD---13 | 18 | 4 | 72.8901 | 46.84% | 52.05% | 1.107% | 2.2004 | 0 | 0 | 2.2004 | 0 | 1.9101 | 0.40625 | 4.7016 | 1.9101 | 0.40625 | 4.7016 | 2.2329 | 0.47492 | 4.7016 | 3.019%
2028 | CB 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 21 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 134.9909 | 0 | 0 | 134.9909 | 0 | 117.1809 | 2.1328 | 54.9413 | 117.1809 | 2.1328 | 54.9413 | 136.9858 | 2.4933 | 54.9413 | 2.139%
2028 | CB 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 29 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 89.0382 | 0 | 0 | 89.0382 | 0 | 77.2909 | 2.9453 | 26.2417 | 77.2909 | 2.9453 | 26.2417 | 90.354 | 3.4431 | 26.2417 | 1.34%
2028 | CB 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 6 | 1438.3629 | 99.75% | 0% | 0.2509% | 21.5213 | 0 | 0 | 21.5213 | 0 | 18.6819 | 0.60938 | 30.6571 | 18.6819 | 0.60938 | 30.6571 | 21.8393 | 0.71237 | 30.6571 | 1.496%
2028 | CB 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 1 | 41.7756 | 94.08% | 0% | 5.924% | 0.14996 | 0 | 0 | 0.14996 | 0 | 0.13018 | 0.10156 | 1.2817 | 0.13018 | 0.10156 | 1.2817 | 0.15218 | 0.11873 | 1.2817 | 0.359%
2028 | CB 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 478 | 2 | 1342.6559 | 29.9% | 69.37% | 0.7369% | 0.48706 | 0 | 0 | 0.48706 | 0 | 0.4228 | 0.20313 | 2.0814 | 0.4228 | 0.20313 | 2.0814 | 0.49425 | 0.23746 | 2.0814 | 0.03628%
2028 | CB 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 233 | 6 | 195.752 | 9.583% | 88.23% | 2.187% | 0.14009 | 0 | 0 | 0.14009 | 0 | 0.12161 | 0.60938 | 0.19956 | 0.12161 | 0.60938 | 0.19956 | 0.14216 | 0.71237 | 0.19956 | 0.07157%
2028 | CB 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 229 | 11 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 11.9289 | 0 | 0 | 11.9289 | 0 | 10.3551 | 1.1172 | 9.2688 | 10.3551 | 1.1172 | 9.2688 | 12.1052 | 1.306 | 9.2688 | 1.126%
2028 | CB 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 18 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 49.8335 | 0 | 0 | 49.8335 | 0 | 43.2587 | 1.8281 | 23.6626 | 43.2587 | 1.8281 | 23.6626 | 50.5699 | 2.1371 | 23.6626 | 1.993%
2028 | CB 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 259 | 13 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 23.2818 | 0 | 0 | 23.2818 | 0 | 20.2101 | 1.3203 | 15.3069 | 20.2101 | 1.3203 | 15.3069 | 23.6259 | 1.5435 | 15.3069 | 1.417%
2028 | CB 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 613 | 37 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 71.3394 | 0 | 0 | 71.3394 | 0 | 61.9273 | 3.7579 | 16.4794 | 61.9273 | 3.7579 | 16.4794 | 72.3937 | 4.393 | 16.4794 | 1.728%
2028 | CB 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 32 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 85.8887 | 0 | 0 | 85.8887 | 0 | 74.557 | 3.25 | 22.9404 | 74.557 | 3.25 | 22.9404 | 87.158 | 3.7993 | 22.9404 | 2.607%
2028 | CB 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 36 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 384.4089 | 0 | 0 | 384.4089 | 0 | 333.692 | 3.6563 | 91.2652 | 333.692 | 3.6563 | 91.2652 | 390.0898 | 4.2742 | 91.2652 | 3.024%
2028 | CB 237 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 41 | 1 | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 14.8671 | 0 | 0 | 14.8671 | 0 | 12.9056 | 0.10156 | 127.0695 | 12.9056 | 0.10156 | 127.0695 | 15.0868 | 0.11873 | 127.0695 | 0.7041%
2028 | CB 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 11 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 16.5356 | 0 | 0 | 16.5356 | 0 | 14.354 | 1.1172 | 12.8482 | 14.354 | 1.1172 | 12.8482 | 16.78 | 1.306 | 12.8482 | 1.309%
2028 | CB 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 1 | 406.8184 | 64.36% | 35.02% | 0.6193% | 0.8728 | 0 | 0 | 0.8728 | 0 | 0.75765 | 0.10156 | 7.4599 | 0.75765 | 0.10156 | 7.4599 | 0.8857 | 0.11873 | 7.4599 | 0.2145%
2028 | CB 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 197 | 1 | 295.5508 | 37.5% | 61.39% | 1.106% | 0.16317 | 0 | 0 | 0.16317 | 0 | 0.14164 | 0.10156 | 1.3946 | 0.14164 | 0.10156 | 1.3946 | 0.16558 | 0.11873 | 1.3946 | 0.05521%
2028 | CB 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 11 | 1438.4419 | 90% | 9.47% | 0.5268% | 13.6301 | 0 | 0 | 13.6301 | 0 | 11.8318 | 1.1172 | 10.5906 | 11.8318 | 1.1172 | 10.5906 | 13.8315 | 1.306 | 10.5906 | 0.9476%
2028 | CB 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 101 | 6 | 826.9208 | 97.04% | 2.672% | 0.2884% | 13.8242 | 0 | 0 | 13.8242 | 0 | 12.0003 | 0.60938 | 19.6926 | 12.0003 | 0.60938 | 19.6926 | 14.0285 | 0.71237 | 19.6926 | 1.672%
2028 | CB 276 | CB 276 | Tier-1 | Non-HFTD---10 | Non-HFTD---16 | 28 | 1 | 26.0793 | 53.94% | 42.4% | 3.659% | 0.14571 | 0 | 0 | 0.14571 | 0 | 0.12648 | 0.10156 | 1.2453 | 0.12648 | 0.10156 | 1.2453 | 0.14786 | 0.11873 | 1.2453 | 0.5587%
2028 | CB 305 | CB 305 | Tier-1 | Non-HFTD---1 | Non-HFTD---2 | 170 | 7 | 2786.7739 | 97.11% | 2.732% | 0.1605% | 32.3147 | 0 | 0 | 32.3147 | 0 | 28.0512 | 0.71095 | 39.4563 | 28.0512 | 0.71095 | 39.4563 | 32.7922 | 0.8311 | 39.4563 | 1.16%
2028 | CB 307 | CB 307 | Tier-1 | Non-HFTD---1 | Non-HFTD---4 | 30 | 4 | 601.8674 | 89.73% | 10.15% | 0.1197% | 20.883 | 0 | 0 | 20.883 | 0 | 18.1278 | 0.40625 | 44.6218 | 18.1278 | 0.40625 | 44.6218 | 21.1916 | 0.47492 | 44.6218 | 3.47%
2028 | CB 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 156 | 9 | 124.2501 | 33.35% | 64.03% | 2.615% | 0.69336 | 0 | 0 | 0.69336 | 0 | 0.60188 | 0.91407 | 0.65846 | 0.60188 | 0.91407 | 0.65846 | 0.70361 | 1.0686 | 0.65846 | 0.558%
2028 | CB 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 48 | 1 | 261.2105 | 99.38% | 0% | 0.6196% | 1.5684 | 0 | 0 | 1.5684 | 0 | 1.3614 | 0.10156 | 13.4049 | 1.3614 | 0.10156 | 13.4049 | 1.5915 | 0.11873 | 13.4049 | 0.6004%
2028 | CB 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 9 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 246.6003 | 0 | 0 | 246.6003 | 0 | 214.0651 | 0.91407 | 234.1883 | 214.0651 | 0.91407 | 234.1883 | 250.2446 | 1.0686 | 234.1883 | 1.689%
2028 | CB 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 21 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 224.988 | 0 | 0 | 224.988 | 0 | 195.3042 | 2.1328 | 91.5702 | 195.3042 | 2.1328 | 91.5702 | 228.3129 | 2.4933 | 91.5702 | 1.993%
2028 | CB 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 13 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 136.531 | 0 | 0 | 136.531 | 0 | 118.5178 | 1.3203 | 89.764 | 118.5178 | 1.3203 | 89.764 | 138.5487 | 1.5435 | 89.764 | 2.234%
2028 | CB 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 21 | 3 | 861.4334 | 18.88% | 81.11% | 0.0161% | 6.737 | 0 | 0 | 6.737 | 0 | 5.8482 | 0.30469 | 19.1938 | 5.8482 | 0.30469 | 19.1938 | 6.8366 | 0.35619 | 19.1938 | 0.7821%
2028 | CB 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 36 | 2 | 67.1473 | 98.29% | 0% | 1.71% | 1.0633 | 0 | 0 | 1.0633 | 0 | 0.92303 | 0.20313 | 4.5441 | 0.92303 | 0.20313 | 4.5441 | 1.079 | 0.23746 | 4.5441 | 1.584%
2028 | CB 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 6 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 30.1854 | 0 | 0 | 30.1854 | 0 | 26.2029 | 0.60938 | 42.9991 | 26.2029 | 0.60938 | 42.9991 | 30.6314 | 0.71237 | 42.9991 | 0.4361%
2028 | CB 474 | CB 474 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 170 | 2 | 794.8798 | 99.6% | 0% | 0.3957% | 2.7012 | 0 | 0 | 2.7012 | 0 | 2.3448 | 0.20313 | 11.5436 | 2.3448 | 0.20313 | 11.5436 | 2.7411 | 0.23746 | 11.5436 | 0.3398%
2028 | CB 492 | CB 492 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 98 | 4 | 147.6974 | 50.2% | 48.6% | 1.193% | 0.87769 | 0 | 0 | 0.87769 | 0 | 0.76189 | 0.40625 | 1.8754 | 0.76189 | 0.40625 | 1.8754 | 0.89066 | 0.47492 | 1.8754 | 0.5943%
2028 | CB 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 14 | 2 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.085456 | 0 | 0 | 0.085456 | 0 | 0.074181 | 0.20313 | 0.3652 | 0.074181 | 0.20313 | 0.3652 | 0.086719 | 0.23746 | 0.3652 | 0.6957%
2028 | CB 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 20 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 22.0415 | 0 | 0 | 22.0415 | 0 | 19.1334 | 2.0313 | 9.4194 | 19.1334 | 2.0313 | 9.4194 | 22.3672 | 2.3746 | 9.4194 | 2.052%
2028 | CB 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 23 | 305.5692 | 37.2% | 61.32% | 1.484% | 2.9272 | 0 | 0 | 2.9272 | 0 | 2.541 | 2.336 | 1.0878 | 2.541 | 2.336 | 1.0878 | 2.9704 | 2.7308 | 1.0878 | 0.9579%
2028 | CB 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 90 | 1 | 481.3309 | 94.25% | 5.298% | 0.4514% | 1.4618 | 0 | 0 | 1.4618 | 0 | 1.2689 | 0.10156 | 12.4939 | 1.2689 | 0.10156 | 12.4939 | 1.4834 | 0.11873 | 12.4939 | 0.3037%
2028 | CB 536 | CB 536 | Tier-2 | Tier-2---18 | Tier-2---14 | 39 | 1 | 54.1099 | 76.19% | 21.99% | 1.82% | 0.30656 | 0 | 0 | 0.30656 | 0 | 0.26612 | 0.10156 | 2.6202 | 0.26612 | 0.10156 | 2.6202 | 0.31109 | 0.11873 | 2.6202 | 0.5666%
2028 | CB 589 | CB 589 | Tier-1 | Non-HFTD---4 | Non-HFTD---7 | 31 | 1 | 115.513 | 99.19% | 0% | 0.8071% | 1.0719 | 0 | 0 | 1.0719 | 0 | 0.93047 | 0.10156 | 9.1614 | 0.93047 | 0.10156 | 9.1614 | 1.0877 | 0.11873 | 9.1614 | 0.9279%
2028 | CB 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 13 | 4323.2442 | 99.81% | 0% | 0.1903% | 44.0857 | 0 | 0 | 44.0857 | 0 | 38.2692 | 1.3203 | 28.9847 | 38.2692 | 1.3203 | 28.9847 | 44.7372 | 1.5435 | 28.9847 | 1.02%
2028 | CB 65 | CB 65 | Tier-1 | Non-HFTD---2 | Non-HFTD---9 | 188 | 2 | 189.2656 | 62.06% | 35.57% | 2.376% | 0.36236 | 0 | 0 | 0.36236 | 0 | 0.31455 | 0.20313 | 1.5485 | 0.31455 | 0.20313 | 1.5485 | 0.36771 | 0.23746 | 1.5485 | 0.1915%
2028 | CB 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 1 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 3.337 | 0 | 0 | 3.337 | 0 | 2.8967 | 0.10156 | 28.5212 | 2.8967 | 0.10156 | 28.5212 | 3.3863 | 0.11873 | 28.5212 | 0.03894%
2028 | CB 791 | CB 791 | Tier-1 | Non-HFTD---1 | Non-HFTD---7 | 89 | 1 | 969.8887 | 99.78% | 0% | 0.2167% | 3.1535 | 0 | 0 | 3.1535 | 0 | 2.7374 | 0.10156 | 26.9527 | 2.7374 | 0.10156 | 26.9527 | 3.2001 | 0.11873 | 26.9527 | 0.3251%
2028 | CB 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 9 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 140.1077 | 0 | 0 | 140.1077 | 0 | 121.6226 | 0.91407 | 133.0557 | 121.6226 | 0.91407 | 133.0557 | 142.1782 | 1.0686 | 133.0557 | 5.109%
2028 | CB 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 1 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 6.1741 | 0 | 0 | 6.1741 | 0 | 5.3596 | 0.10156 | 52.7705 | 5.3596 | 0.10156 | 52.7705 | 6.2654 | 0.11873 | 52.7705 | 0.3731%
2028 | CB 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 6 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 118.7823 | 0 | 0 | 118.7823 | 0 | 103.1108 | 0.60938 | 169.2056 | 103.1108 | 0.60938 | 169.2056 | 120.5377 | 0.71237 | 169.2056 | 1.037%
2028 | CB 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 11 | 1 | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 34.2205 | 0 | 0 | 34.2205 | 0 | 29.7056 | 0.10156 | 292.4831 | 29.7056 | 0.10156 | 292.4831 | 34.7262 | 0.11873 | 292.4831 | 2.624%
2028 | CB 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 14 | 1 | 132.7571 | 99.65% | 0% | 0.354% | 2.7402 | 0 | 0 | 2.7402 | 0 | 2.3787 | 0.10156 | 23.4208 | 2.3787 | 0.10156 | 23.4208 | 2.7807 | 0.11873 | 23.4208 | 2.064%
2028 | CB FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 21 | 346.5871 | 36.93% | 61.45% | 1.621% | 2.101 | 0 | 0 | 2.101 | 0 | 1.8238 | 2.1328 | 0.85509 | 1.8238 | 2.1328 | 0.85509 | 2.132 | 2.4933 | 0.85509 | 0.6062%
2028 | CB FB2 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 17 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 27.6762 | 0 | 0 | 27.6762 | 0 | 24.0247 | 1.7266 | 13.9146 | 24.0247 | 1.7266 | 13.9146 | 28.0852 | 2.0184 | 13.9146 | 2.688%
2028 | CB JU1 | CB JU1 | Tier-3 | Tier-3---15 | Tier-3---3 | 80 | 2 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 10.8659 | 0 | 0 | 10.8659 | 0 | 9.4323 | 0.20313 | 46.4354 | 9.4323 | 0.20313 | 46.4354 | 11.0265 | 0.23746 | 46.4354 | 0.7094%
2028 | CB MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 116 | 16 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 201.8315 | 0 | 0 | 201.8315 | 0 | 175.2029 | 1.625 | 107.816 | 175.2029 | 1.625 | 107.816 | 204.8142 | 1.8997 | 107.816 | 3.942%
2028 | CB NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 403 | 1 | 638.0788 | 99.02% | 0% | 0.9838% | 0.45465 | 0 | 0 | 0.45465 | 0 | 0.39466 | 0.10156 | 3.8859 | 0.39466 | 0.10156 | 3.8859 | 0.46137 | 0.11873 | 3.8859 | 0.07125%
2028 | CB OK1 | CB OK1 | Tier-3 | Tier-3---7 | Tier-3---1 | 190 | 4 | 6915.6819 | 99% | 0.9206% | 0.07911% | 41.8 | 0 | 0 | 41.8 | 0 | 36.2851 | 0.40625 | 89.3162 | 36.2851 | 0.40625 | 89.3162 | 42.4177 | 0.47492 | 89.3162 | 0.6044%
2028 | CB PE1 | CB PE1 | Tier-3 | Tier-3---13 | Tier-3---3 | 247 | 4 | 3027.5479 | 94.73% | 5.109% | 0.164% | 13.4687 | 0 | 0 | 13.4687 | 0 | 11.6917 | 0.40625 | 28.7792 | 11.6917 | 0.40625 | 28.7792 | 13.6677 | 0.47492 | 28.7792 | 0.4449%
2028 | CB RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 9 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 76.444 | 0 | 0 | 76.444 | 0 | 66.3584 | 0.91407 | 72.5964 | 66.3584 | 0.91407 | 72.5964 | 77.5737 | 1.0686 | 72.5964 | 0.7269%
2028 | CB RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 6 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 75.6636 | 0 | 0 | 75.6636 | 0 | 65.681 | 0.60938 | 107.7829 | 65.681 | 0.60938 | 107.7829 | 76.7818 | 0.71237 | 107.7829 | 1.447%
2028 | CB RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 9 | 916.1972 | 69.5% | 30.07% | 0.4286% | 6.8958 | 0 | 0 | 6.8958 | 0 | 5.986 | 0.91407 | 6.5487 | 5.986 | 0.91407 | 6.5487 | 6.9977 | 1.0686 | 6.5487 | 0.7527%
2028 | CB RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 4 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 45.7536 | 0 | 0 | 45.7536 | 0 | 39.7171 | 0.40625 | 97.7641 | 39.7171 | 0.40625 | 97.7641 | 46.4298 | 0.47492 | 97.7641 | 1.223%
2028 | CB SL1 | CB SL1 | Tier-3 | Tier-3---11 | Tier-3---1 | 225 | 20 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 81.207 | 0 | 0 | 81.207 | 0 | 70.4929 | 2.0313 | 34.7038 | 70.4929 | 2.0313 | 34.7038 | 82.407 | 2.3746 | 34.7038 | 2.416%
2028 | CB SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 220 | 2 | 94.186 | 2.003% | 94.63% | 3.363% | 0.0049738 | 0 | 0 | 0.0049738 | 0 | 0.0043176 | 0.20313 | 0.021256 | 0.0043176 | 0.20313 | 0.021256 | 0.0050473 | 0.23746 | 0.021256 | 0.005281%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 13 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 19.5527 | 0 | 0 | 19.5527 | 0 | 16.973 | 1.3203 | 12.8551 | 16.973 | 1.3203 | 12.8551 | 19.8416 | 1.5435 | 12.8551 | 0.9473%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 235 | 32 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 139.7772 | 0 | 0 | 139.7772 | 0 | 121.3357 | 3.25 | 37.3337 | 121.3357 | 3.25 | 37.3337 | 141.8428 | 3.7993 | 37.3337 | 3.758%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | Tier-3---1 | 122 | 5 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 110.252 | 0 | 0 | 110.252 | 0 | 95.706 | 0.50782 | 188.465 | 95.706 | 0.50782 | 188.465 | 111.8814 | 0.59365 | 188.465 | 1.181%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 14 | 6920.124 | 97.57% | 2.306% | 0.1195% | 63.3122 | 0 | 0 | 63.3122 | 0 | 54.9591 | 1.4219 | 38.6522 | 54.9591 | 1.4219 | 38.6522 | 64.2479 | 1.6622 | 38.6522 | 0.9149%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 125 | 2 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 27.403 | 0 | 0 | 27.403 | 0 | 23.7876 | 0.20313 | 117.107 | 23.7876 | 0.20313 | 117.107 | 27.808 | 0.23746 | 117.107 | 0.4608%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 103 | 10 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 105.9541 | 0 | 0 | 105.9541 | 0 | 91.9751 | 1.0156 | 90.5591 | 91.9751 | 1.0156 | 90.5591 | 107.5199 | 1.1873 | 90.5591 | 2.801%

## Wood pole Intrusive Primary
Wood Pole Intrusive - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 1003 | 52450.6146 | 1376.7399 | 2.625% | 1313.3164 | 158.1285 | 8.3054 | 1313.3164 | 158.1285 | 8.3054 | 1383.4887 | 166.5776 | 8.3054
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 4906 | 266043.1681 | 10487.5072 | 3.942% | 9543.4887 | 737.8266 | 12.9346 | 9543.4887 | 737.8266 | 12.9346 | 10590.5779 | 818.7792 | 12.9346
[9 empty] | Capital Cost only in Year 0 | 0.16527 | K$/inspection | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 11137 | 889727.5255 | 47408.4446 | 5.328% | 41153.6201 | 1597.7632 | 25.757 | 41153.6201 | 1597.7632 | 25.757 | 48109.0508 | 1867.8034 | 25.757
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 17046 | 1208221.3082 | 59272.6918 | 4.906% | 52010.4251 | 2493.7184 | 20.8566 | 52010.4251 | 2493.7184 | 20.8566 | 60083.1174 | 2853.1602 | 21.0584
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 10% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] |  | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 26 | 973.0999 | 95.53% | 4.02% | 0.4464% | 12.8567 | 0 | 0 | 12.8567 | 0 | 12.2644 | 4.099 | 2.992 | 12.2644 | 4.099 | 2.992 | 12.9197 | 4.3181 | 2.992 | 1.321%
2026 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 102 | 1 | 124.0064 | 98.52% | 0% | 1.478% | 0.11978 | 0 | 0 | 0.11978 | 0 | 0.11426 | 0.15766 | 0.72475 | 0.11426 | 0.15766 | 0.72475 | 0.12037 | 0.16608 | 0.72475 | 0.09659%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 14 | 1279.0443 | 99.78% | 0% | 0.2159% | 13.5363 | 0 | 0 | 13.5363 | 0 | 12.9127 | 2.2072 | 5.8503 | 12.9127 | 2.2072 | 5.8503 | 13.6027 | 2.3251 | 5.8503 | 1.058%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 96 | 2976.5734 | 99.75% | 0% | 0.2502% | 69.016 | 0 | 0 | 69.016 | 0 | 65.8366 | 15.1349 | 4.35 | 65.8366 | 15.1349 | 4.35 | 69.3543 | 15.9436 | 4.35 | 2.319%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 324 | 8462.8018 | 99.74% | 0% | 0.2593% | 255.8315 | 0 | 0 | 255.8315 | 0 | 244.0459 | 51.0804 | 4.7777 | 244.0459 | 51.0804 | 4.7777 | 257.0856 | 53.8097 | 4.7777 | 3.023%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 183 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 133.2774 | 0 | 0 | 133.2774 | 0 | 127.1376 | 28.851 | 4.4067 | 127.1376 | 28.851 | 4.4067 | 133.9307 | 30.3925 | 4.4067 | 4.39%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 2 | 550.61 | 92.88% | 6.93% | 0.1872% | 2.3787 | 0 | 0 | 2.3787 | 0 | 2.2691 | 0.31531 | 7.1964 | 2.2691 | 0.31531 | 7.1964 | 2.3904 | 0.33216 | 7.1964 | 0.432%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 47 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 194.4102 | 0 | 0 | 194.4102 | 0 | 185.4541 | 7.4098 | 25.0282 | 185.4541 | 7.4098 | 25.0282 | 195.3632 | 7.8057 | 25.0282 | 8.076%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 52 | 4762.848 | 95.55% | 4.384% | 0.07015% | 217.0976 | 0 | 0 | 217.0976 | 0 | 207.0963 | 8.1981 | 25.2615 | 207.0963 | 8.1981 | 25.2615 | 218.1618 | 8.6361 | 25.2615 | 4.558%
2026 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | Non-HFTD---6 | 351 | 18 | 1424.1907 | 99.61% | 0% | 0.3928% | 7.2749 | 0 | 0 | 7.2749 | 0 | 6.9397 | 2.8378 | 2.4455 | 6.9397 | 2.8378 | 2.4455 | 7.3105 | 2.9894 | 2.4455 | 0.5108%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 25 | 4323.2442 | 99.81% | 0% | 0.1903% | 29.2345 | 0 | 0 | 29.2345 | 0 | 27.8878 | 3.9414 | 7.0756 | 27.8878 | 3.9414 | 7.0756 | 29.3778 | 4.152 | 7.0756 | 0.6762%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 77 | 8606.9717 | 99.86% | 0% | 0.1411% | 118.8154 | 0 | 0 | 118.8154 | 0 | 113.3418 | 12.1395 | 9.3366 | 113.3418 | 12.1395 | 9.3366 | 119.3978 | 12.7881 | 9.3366 | 1.38%
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 4 | 1 | 117.1572 | 99.03% | 0.8725% | 0.09309% | 2.9006 | 0 | 0 | 2.9006 | 0 | 2.767 | 0.15766 | 17.5511 | 2.767 | 0.15766 | 17.5511 | 2.9149 | 0.16608 | 17.5511 | 2.476%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 10 | 7 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 28.3909 | 0 | 0 | 28.3909 | 0 | 27.083 | 1.1036 | 24.5408 | 27.083 | 1.1036 | 24.5408 | 28.5301 | 1.1626 | 24.5408 | 6.94%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 82 | 30 | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 104.9287 | 0 | 0 | 104.9287 | 0 | 100.0948 | 4.7297 | 21.1632 | 100.0948 | 4.7297 | 21.1632 | 105.443 | 4.9824 | 21.1632 | 3.631%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 96 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 186.0436 | 0 | 0 | 186.0436 | 0 | 177.473 | 15.1349 | 11.726 | 177.473 | 15.1349 | 11.726 | 186.9556 | 15.9436 | 11.726 | 1.965%
2026 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 403 | 4 | 638.0788 | 99.02% | 0% | 0.9838% | 0.6271 | 0 | 0 | 0.6271 | 0 | 0.59821 | 0.63062 | 0.9486 | 0.59821 | 0.63062 | 0.9486 | 0.63017 | 0.66432 | 0.9486 | 0.09828%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 75 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 290.741 | 0 | 0 | 290.741 | 0 | 264.5704 | 11.2795 | 23.456 | 264.5704 | 11.2795 | 23.456 | 293.5984 | 12.517 | 23.456 | 7.216%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 86 | 42 | 2651.4354 | 70.65% | 29.24% | 0.1064% | 91.4843 | 0 | 0 | 91.4843 | 0 | 83.2495 | 6.3165 | 13.1797 | 83.2495 | 6.3165 | 13.1797 | 92.3834 | 7.0095 | 13.1797 | 3.45%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 70 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 129.763 | 0 | 0 | 129.763 | 0 | 118.0826 | 10.5275 | 11.2166 | 118.0826 | 10.5275 | 11.2166 | 131.0383 | 11.6825 | 11.2166 | 2.26%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 28 | 836.2457 | 79.76% | 20.09% | 0.1547% | 35.9141 | 0 | 0 | 35.9141 | 0 | 32.6814 | 4.211 | 7.761 | 32.6814 | 4.211 | 7.761 | 36.2671 | 4.673 | 7.761 | 4.295%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 96 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 300.9085 | 0 | 0 | 300.9085 | 0 | 273.8227 | 14.4377 | 18.9658 | 273.8227 | 14.4377 | 18.9658 | 303.8658 | 16.0218 | 18.9658 | 2.989%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 8 | 404.4817 | 67.64% | 32.12% | 0.2398% | 4.3773 | 0 | 0 | 4.3773 | 0 | 3.9833 | 1.2031 | 3.3108 | 3.9833 | 1.2031 | 3.3108 | 4.4204 | 1.3351 | 3.3108 | 1.082%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 176 | 6 | 2963.4059 | 78.23% | 21.66% | 0.1106% | 7.9031 | 0 | 0 | 7.9031 | 0 | 7.1917 | 0.90236 | 7.9699 | 7.1917 | 0.90236 | 7.9699 | 7.9808 | 1.0014 | 7.9699 | 0.2667%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 6 | 47.6106 | 91.21% | 0% | 8.789% | 0.13028 | 0 | 0 | 0.13028 | 0 | 0.11855 | 0.90236 | 0.13138 | 0.11855 | 0.90236 | 0.13138 | 0.13156 | 1.0014 | 0.13138 | 0.2736%
2027 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 45 | 7 | 0.95479 | 13.38% | 0% | 86.62% | 0.0019878 | 0 | 0 | 0.0019878 | 0 | 0.0018088 | 1.0527 | 0.0017182 | 0.0018088 | 1.0527 | 0.0017182 | 0.0020073 | 1.1683 | 0.0017182 | 0.2082%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 82 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 316.6393 | 0 | 0 | 316.6393 | 0 | 288.1374 | 12.3322 | 23.3646 | 288.1374 | 12.3322 | 23.3646 | 319.7512 | 13.6853 | 23.3646 | 2.657%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 22 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 163.6623 | 0 | 0 | 163.6623 | 0 | 148.9304 | 3.3086 | 45.0126 | 148.9304 | 3.3086 | 45.0126 | 165.2707 | 3.6717 | 45.0126 | 8.44%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 66 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 266.3327 | 0 | 0 | 266.3327 | 0 | 242.3592 | 9.9259 | 24.4168 | 242.3592 | 9.9259 | 24.4168 | 268.9502 | 11.015 | 24.4168 | 6.296%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 19 | 9 | 655.8009 | 99.14% | 0.7615% | 0.1019% | 30.796 | 0 | 0 | 30.796 | 0 | 28.024 | 1.3535 | 20.7043 | 28.024 | 1.3535 | 20.7043 | 31.0987 | 1.502 | 20.7043 | 4.696%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | Tier-2---6 | 42 | 21 | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.4802 | 0 | 0 | 10.4802 | 0 | 9.5369 | 3.1582 | 3.0197 | 9.5369 | 3.1582 | 3.0197 | 10.5832 | 3.5048 | 3.0197 | 3.312%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | Tier-2---6 | 114 | 44 | 471.2015 | 74.37% | 25.17% | 0.4626% | 13.5253 | 0 | 0 | 13.5253 | 0 | 12.3079 | 6.6173 | 1.86 | 12.3079 | 6.6173 | 1.86 | 13.6583 | 7.3433 | 1.86 | 2.87%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 129 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.6297 | 0 | 0 | 78.6297 | 0 | 71.5519 | 19.4007 | 3.6881 | 71.5519 | 19.4007 | 3.6881 | 79.4025 | 21.5293 | 3.6881 | 4.561%
2027 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 29 | 28 | 183.5383 | 99.34% | 0.09556% | 0.5689% | 17.6032 | 0 | 0 | 17.6032 | 0 | 16.0187 | 4.211 | 3.804 | 16.0187 | 4.211 | 3.804 | 17.7762 | 4.673 | 3.804 | 9.591%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 9 | 9 | 6.6189 | 96.38% | 0% | 3.621% | 0.63793 | 0 | 0 | 0.63793 | 0 | 0.58051 | 1.3535 | 0.42888 | 0.58051 | 1.3535 | 0.42888 | 0.6442 | 1.502 | 0.42888 | 9.638%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 27 | 973.0999 | 95.53% | 4.02% | 0.4464% | 13.3512 | 0 | 0 | 13.3512 | 0 | 12.1494 | 4.0606 | 2.992 | 12.1494 | 4.0606 | 2.992 | 13.4824 | 4.5061 | 2.992 | 1.372%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | Tier-2---2 | 478 | 114 | 1342.6559 | 29.9% | 69.37% | 0.7369% | 9.5732 | 0 | 0 | 9.5732 | 0 | 8.7115 | 17.1448 | 0.50811 | 8.7115 | 17.1448 | 0.50811 | 9.6673 | 19.0259 | 0.50811 | 0.713%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 116 | 133.9861 | 95.12% | 0% | 4.877% | 7.6603 | 0 | 0 | 7.6603 | 0 | 6.9708 | 17.4456 | 0.39957 | 6.9708 | 17.4456 | 0.39957 | 7.7356 | 19.3596 | 0.39957 | 5.717%
2027 | 203 | CB 203 | Tier-2 | Tier-2---13 | Tier-2---4 | 233 | 90 | 195.752 | 9.583% | 88.23% | 2.187% | 0.72462 | 0 | 0 | 0.72462 | 0 | 0.6594 | 13.5353 | 0.048717 | 0.6594 | 13.5353 | 0.048717 | 0.73174 | 15.0204 | 0.048717 | 0.3702%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 210 | 490.4615 | 96.36% | 1.259% | 2.378% | 29.5388 | 0 | 0 | 29.5388 | 0 | 26.8799 | 31.5825 | 0.8511 | 26.8799 | 31.5825 | 0.8511 | 29.8291 | 35.0476 | 0.8511 | 6.023%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 229 | 156 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 58.3358 | 0 | 0 | 58.3358 | 0 | 53.0848 | 23.4613 | 2.2627 | 53.0848 | 23.4613 | 2.2627 | 58.9091 | 26.0354 | 2.2627 | 5.506%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 10 | 2730.9177 | 98.3% | 1.373% | 0.325% | 7.5197 | 0 | 0 | 7.5197 | 0 | 6.8428 | 1.5039 | 4.55 | 6.8428 | 1.5039 | 4.55 | 7.5936 | 1.6689 | 4.55 | 0.2754%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | Tier-2---6 | 170 | 2 | 481.2843 | 94.31% | 4.95% | 0.7414% | 0.53399 | 0 | 0 | 0.53399 | 0 | 0.48592 | 0.30079 | 1.6155 | 0.48592 | 0.30079 | 1.6155 | 0.53924 | 0.33379 | 1.6155 | 0.111%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 26 | 550.61 | 92.88% | 6.93% | 0.1872% | 30.923 | 0 | 0 | 30.923 | 0 | 28.1395 | 3.9102 | 7.1964 | 28.1395 | 3.9102 | 7.1964 | 31.227 | 4.3392 | 7.1964 | 5.616%
2027 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 17 | 2 | 94.6686 | 66.47% | 32.93% | 0.6021% | 0.74033 | 0 | 0 | 0.74033 | 0 | 0.67369 | 0.30079 | 2.2398 | 0.67369 | 0.30079 | 2.2398 | 0.74761 | 0.33379 | 2.2398 | 0.782%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | Tier-2---24 | 43 | 22 | 3.2301 | 78.97% | 0% | 21.03% | 0.1305 | 0 | 0 | 0.1305 | 0 | 0.11875 | 3.3086 | 0.035892 | 0.11875 | 3.3086 | 0.035892 | 0.13178 | 3.6717 | 0.035892 | 4.04%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 3 | 458.7821 | 99.48% | 0% | 0.5194% | 1.9843 | 0 | 0 | 1.9843 | 0 | 1.8057 | 0.45118 | 4.0022 | 1.8057 | 0.45118 | 4.0022 | 2.0038 | 0.50068 | 4.0022 | 0.4325%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 127 | 754.1323 | 92.41% | 6.882% | 0.7076% | 35.4024 | 0 | 0 | 35.4024 | 0 | 32.2157 | 19.0999 | 1.6867 | 32.2157 | 19.0999 | 1.6867 | 35.7504 | 21.1955 | 1.6867 | 4.694%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 3 | 4762.848 | 95.55% | 4.384% | 0.07015% | 12.5249 | 0 | 0 | 12.5249 | 0 | 11.3975 | 0.45118 | 25.2615 | 11.3975 | 0.45118 | 25.2615 | 12.648 | 0.50068 | 25.2615 | 0.263%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 14 | 29 | 46.1951 | 84.69% | 14.76% | 0.5474% | 8.1042 | 0 | 0 | 8.1042 | 0 | 7.3748 | 4.3614 | 1.6909 | 7.3748 | 4.3614 | 1.6909 | 8.1839 | 4.8399 | 1.6909 | 17.54%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 79 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.15148 | 0 | 0 | 0.15148 | 0 | 0.13785 | 11.881 | 0.011602 | 0.13785 | 11.881 | 0.011602 | 0.15297 | 13.1846 | 0.011602 | 0.09476%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 14 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.008081 | 0 | 0 | 0.008081 | 0 | 0.0073536 | 2.1055 | 0.0034926 | 0.0073536 | 2.1055 | 0.0034926 | 0.0081604 | 2.3365 | 0.0034926 | 0.003998%
2027 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 9 | 2 | 14.6681 | 98.1% | 0% | 1.899% | 0.31977 | 0 | 0 | 0.31977 | 0 | 0.29098 | 0.30079 | 0.96741 | 0.29098 | 0.30079 | 0.96741 | 0.32291 | 0.33379 | 0.96741 | 2.18%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 39 | 23 | 209.8559 | 99.5% | 0% | 0.498% | 12.3145 | 0 | 0 | 12.3145 | 0 | 11.206 | 3.459 | 3.2396 | 11.206 | 3.459 | 3.2396 | 12.4355 | 3.8385 | 3.2396 | 5.868%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 19 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 125.5459 | 0 | 0 | 125.5459 | 0 | 114.2451 | 2.8575 | 39.9813 | 114.2451 | 2.8575 | 39.9813 | 126.7797 | 3.171 | 39.9813 | 8.618%
2027 | 330 | CB 330 | Tier-2 | Tier-2---16 | Tier-2---8 | 156 | 63 | 124.2501 | 33.35% | 64.03% | 2.615% | 1.6736 | 0 | 0 | 1.6736 | 0 | 1.523 | 9.4747 | 0.16074 | 1.523 | 9.4747 | 0.16074 | 1.6901 | 10.5143 | 0.16074 | 1.347%
2027 | 331 | CB 331 | Tier-2 | Tier-2---14 | Tier-2---7 | 48 | 10 | 261.2105 | 99.38% | 0% | 0.6196% | 5.4082 | 0 | 0 | 5.4082 | 0 | 4.9214 | 1.5039 | 3.2723 | 4.9214 | 1.5039 | 3.2723 | 5.4613 | 1.6689 | 3.2723 | 2.07%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 106 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 386.4497 | 0 | 0 | 386.4497 | 0 | 351.664 | 15.9416 | 22.0595 | 351.664 | 15.9416 | 22.0595 | 390.2478 | 17.6907 | 22.0595 | 7.34%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 384 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 1196.223 | 0 | 0 | 1196.223 | 0 | 1088.5467 | 57.7508 | 18.849 | 1088.5467 | 57.7508 | 18.849 | 1207.9795 | 64.0871 | 18.849 | 7.146%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 48 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 83.2699 | 0 | 0 | 83.2699 | 0 | 75.7745 | 7.2188 | 10.4968 | 75.7745 | 7.2188 | 10.4968 | 84.0883 | 8.0109 | 10.4968 | 1.203%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | Tier-2---2 | 128 | 17 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 53.6452 | 0 | 0 | 53.6452 | 0 | 48.8164 | 2.5567 | 19.0937 | 48.8164 | 2.5567 | 19.0937 | 54.1724 | 2.8372 | 19.0937 | 1.261%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 9 | 800.5503 | 21.6% | 78.32% | 0.07823% | 7.7818 | 0 | 0 | 7.7818 | 0 | 7.0814 | 1.3535 | 5.2318 | 7.0814 | 1.3535 | 5.2318 | 7.8583 | 1.502 | 5.2318 | 0.9721%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 12 | 67.245 | 99.24% | 0% | 0.7576% | 5.0052 | 0 | 0 | 5.0052 | 0 | 4.5546 | 1.8047 | 2.5237 | 4.5546 | 1.8047 | 2.5237 | 5.0544 | 2.0027 | 2.5237 | 7.443%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | Tier-2---2 | 43 | 15 | 949.4775 | 95.45% | 4.414% | 0.1311% | 31.6158 | 0 | 0 | 31.6158 | 0 | 28.77 | 2.2559 | 12.7533 | 28.77 | 2.2559 | 12.7533 | 31.9265 | 2.5034 | 12.7533 | 3.33%
2027 | 568 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 25 | 490.4615 | 96.36% | 1.259% | 2.378% | 3.5165 | 0 | 0 | 3.5165 | 0 | 3.2 | 3.7598 | 0.8511 | 3.2 | 3.7598 | 0.8511 | 3.5511 | 4.1723 | 0.8511 | 0.717%
2027 | 569 | 204-32R | Tier-2 | Tier-2---11 | Tier-2---4 | 336 | 3 | 490.4615 | 96.36% | 1.259% | 2.378% | 0.42198 | 0 | 0 | 0.42198 | 0 | 0.384 | 0.45118 | 0.8511 | 0.384 | 0.45118 | 0.8511 | 0.42613 | 0.50068 | 0.8511 | 0.08604%
2027 | 576 | CB 576 | Tier-2 | Tier-2---12 | Tier-2---4 | 19 | 8 | 417.7025 | 78.37% | 21.49% | 0.1463% | 13.7828 | 0 | 0 | 13.7828 | 0 | 12.5421 | 1.2031 | 10.4245 | 12.5421 | 1.2031 | 10.4245 | 13.9182 | 1.3351 | 10.4245 | 3.3%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 286 | 18774.394 | 95.55% | 4.388% | 0.06321% | 1289.068 | 0 | 0 | 1289.068 | 0 | 1173.0343 | 43.0123 | 27.2721 | 1173.0343 | 43.0123 | 27.2721 | 1301.7369 | 47.7315 | 27.2721 | 6.866%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 533 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1811.2094 | 0 | 0 | 1811.2094 | 0 | 1648.1759 | 80.1593 | 20.5613 | 1648.1759 | 80.1593 | 20.5613 | 1829.0098 | 88.9542 | 20.5613 | 7.036%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 200 | 4323.2442 | 99.81% | 0% | 0.1903% | 233.8762 | 0 | 0 | 233.8762 | 0 | 212.8242 | 30.0785 | 7.0756 | 212.8242 | 30.0785 | 7.0756 | 236.1748 | 33.3787 | 7.0756 | 5.41%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 106 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 175.2698 | 0 | 0 | 175.2698 | 0 | 159.4932 | 15.9416 | 10.0048 | 159.4932 | 15.9416 | 10.0048 | 176.9924 | 17.6907 | 10.0048 | 1.919%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 20 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 23.0136 | 0 | 0 | 23.0136 | 0 | 20.9421 | 3.0079 | 6.9625 | 20.9421 | 3.0079 | 6.9625 | 23.2398 | 3.3379 | 6.9625 | 0.2686%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 44 | 3349.7594 | 92.58% | 7.304% | 0.116% | 96.7755 | 0 | 0 | 96.7755 | 0 | 88.0644 | 6.6173 | 13.3083 | 88.0644 | 6.6173 | 13.3083 | 97.7267 | 7.3433 | 13.3083 | 2.889%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 11 | 127.4062 | 99.28% | 0% | 0.716% | 3.6617 | 0 | 0 | 3.6617 | 0 | 3.3321 | 1.6543 | 2.0142 | 3.3321 | 1.6543 | 2.0142 | 3.6977 | 1.8358 | 2.0142 | 2.874%
2027 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 7 | 5 | 188.5529 | 99.88% | 0% | 0.1171% | 13.4523 | 0 | 0 | 13.4523 | 0 | 12.2414 | 0.75196 | 16.2792 | 12.2414 | 0.75196 | 16.2792 | 13.5845 | 0.83447 | 16.2792 | 7.134%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 67 | 8606.9717 | 99.86% | 0% | 0.1411% | 103.3848 | 0 | 0 | 103.3848 | 0 | 94.0788 | 10.0763 | 9.3366 | 94.0788 | 10.0763 | 9.3366 | 104.4009 | 11.1819 | 9.3366 | 1.201%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 91 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 235.082 | 0 | 0 | 235.082 | 0 | 213.9214 | 13.6857 | 15.631 | 213.9214 | 13.6857 | 15.631 | 237.3923 | 15.1873 | 15.631 | 6.901%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 31 | 1554.328 | 69.02% | 30.62% | 0.3611% | 11.2737 | 0 | 0 | 11.2737 | 0 | 10.2589 | 4.6622 | 2.2005 | 10.2589 | 4.6622 | 2.2005 | 11.3845 | 5.1737 | 2.2005 | 0.7253%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 252 | 21 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 12.7148 | 0 | 0 | 12.7148 | 0 | 11.5703 | 3.1582 | 3.6635 | 11.5703 | 3.1582 | 3.6635 | 12.8397 | 3.5048 | 3.6635 | 0.6384%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 6 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 12.7741 | 0 | 0 | 12.7741 | 0 | 11.6243 | 0.90236 | 12.8821 | 11.6243 | 0.90236 | 12.8821 | 12.8996 | 1.0014 | 12.8821 | 0.7718%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 35 | 17 | 387.8494 | 99.7% | 0% | 0.3041% | 18.7811 | 0 | 0 | 18.7811 | 0 | 17.0906 | 2.5567 | 6.6847 | 17.0906 | 2.5567 | 6.6847 | 18.9657 | 2.8372 | 6.6847 | 4.842%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 14 | 9 | 132.7571 | 99.65% | 0% | 0.354% | 8.5042 | 0 | 0 | 8.5042 | 0 | 7.7387 | 1.3535 | 5.7174 | 7.7387 | 1.3535 | 5.7174 | 8.5878 | 1.502 | 5.7174 | 6.406%
2027 | 982 | CB 982 | Tier-2 | missing | missing | 1 | 2 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.30079 | 0 | 0 | 0.30079 | 0 | 0 | 0.33379 | 0 | 0%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 22 | 626.8618 | 65.87% | 33.98% | 0.153% | 31.3239 | 0 | 0 | 31.3239 | 0 | 28.5043 | 3.3086 | 8.6151 | 28.5043 | 3.3086 | 8.6151 | 31.6318 | 3.6717 | 8.6151 | 4.997%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 74 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 206.0576 | 0 | 0 | 206.0576 | 0 | 187.5096 | 11.1291 | 16.8486 | 187.5096 | 11.1291 | 16.8486 | 208.0827 | 12.3501 | 16.8486 | 4.502%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 95 | 4222.2471 | 91.41% | 8.486% | 0.103% | 251.1373 | 0 | 0 | 251.1373 | 0 | 228.5315 | 14.2873 | 15.9954 | 228.5315 | 14.2873 | 15.9954 | 253.6054 | 15.8549 | 15.9954 | 5.948%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 1 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 2.9122 | 0 | 0 | 2.9122 | 0 | 2.65 | 0.15039 | 17.6207 | 2.65 | 0.15039 | 17.6207 | 2.9408 | 0.16689 | 17.6207 | 0.01825%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 16 | 12 | 17.9659 | 86.84% | 10.72% | 2.434% | 1.1701 | 0 | 0 | 1.1701 | 0 | 1.0648 | 1.8047 | 0.59002 | 1.0648 | 1.8047 | 0.59002 | 1.1816 | 2.0027 | 0.59002 | 6.513%
2027 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | Tier-2---12 | 40 | 1 | 40.9949 | 23.55% | 73.64% | 2.81% | 0.024132 | 0 | 0 | 0.024132 | 0 | 0.02196 | 0.15039 | 0.14602 | 0.02196 | 0.15039 | 0.14602 | 0.02437 | 0.16689 | 0.14602 | 0.05887%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 4 | 4 | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.3453 | 0 | 0 | 0.3453 | 0 | 0.31422 | 0.60157 | 0.52232 | 0.31422 | 0.60157 | 0.52232 | 0.34869 | 0.66757 | 0.52232 | 1.275%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 3 | 3 | 6.3934 | 34.35% | 64.55% | 1.103% | 0.21961 | 0 | 0 | 0.21961 | 0 | 0.19984 | 0.45118 | 0.44293 | 0.19984 | 0.45118 | 0.44293 | 0.22176 | 0.50068 | 0.44293 | 3.435%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 123 | 2514.2831 | 99.84% | 0% | 0.1648% | 184.8785 | 0 | 0 | 184.8785 | 0 | 168.2369 | 18.4983 | 9.0947 | 168.2369 | 18.4983 | 9.0947 | 186.6955 | 20.5279 | 9.0947 | 7.353%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | Tier-2---13 | 65 | 33 | 95.3301 | 98.77% | 0% | 1.235% | 4.7801 | 0 | 0 | 4.7801 | 0 | 4.3498 | 4.963 | 0.87645 | 4.3498 | 4.963 | 0.87645 | 4.8271 | 5.5075 | 0.87645 | 5.014%
2027 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 4 | 3 | 54.719 | 98.75% | 1.065% | 0.1855% | 4.0526 | 0 | 0 | 4.0526 | 0 | 3.6878 | 0.45118 | 8.1737 | 3.6878 | 0.45118 | 8.1737 | 4.0924 | 0.50068 | 8.1737 | 7.406%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 34 | 20 | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 125.7661 | 0 | 0 | 125.7661 | 0 | 114.4454 | 3.0079 | 38.0489 | 114.4454 | 3.0079 | 38.0489 | 127.0021 | 3.3379 | 38.0489 | 5.863%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 14 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 38.5889 | 0 | 0 | 38.5889 | 0 | 35.1154 | 2.1055 | 16.678 | 35.1154 | 2.1055 | 16.678 | 38.9682 | 2.3365 | 16.678 | 3.405%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | Tier-2---1 | 54 | 6 | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 46.943 | 0 | 0 | 46.943 | 0 | 42.7175 | 0.90236 | 47.34 | 42.7175 | 0.90236 | 47.34 | 47.4044 | 1.0014 | 47.34 | 1.11%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | Tier-2---4 | 12 | 12 | 417.0013 | 94.5% | 5.418% | 0.08666% | 39.4048 | 0 | 0 | 39.4048 | 0 | 35.8578 | 1.8047 | 19.869 | 35.8578 | 1.8047 | 19.869 | 39.7921 | 2.0027 | 19.869 | 9.45%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 22 | 1646.9837 | 34.54% | 65.41% | 0.04829% | 52.1414 | 0 | 0 | 52.1414 | 0 | 47.4479 | 3.3086 | 14.3406 | 47.4479 | 3.3086 | 14.3406 | 52.6538 | 3.6717 | 14.3406 | 3.166%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 14 | 788.3757 | 99.4% | 0.5205% | 0.07536% | 57.7447 | 0 | 0 | 57.7447 | 0 | 52.5469 | 2.1055 | 24.957 | 52.5469 | 2.1055 | 24.957 | 58.3122 | 2.3365 | 24.957 | 7.325%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 44 | 3 | 411.5414 | 99.65% | 0% | 0.3468% | 2.7962 | 0 | 0 | 2.7962 | 0 | 2.5445 | 0.45118 | 5.6398 | 2.5445 | 0.45118 | 5.6398 | 2.8237 | 0.50068 | 5.6398 | 0.6795%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 24 | 456.1931 | 99.77% | 0% | 0.2285% | 32.1283 | 0 | 0 | 32.1283 | 0 | 29.2363 | 3.6094 | 8.1 | 29.2363 | 3.6094 | 8.1 | 32.444 | 4.0054 | 8.1 | 7.043%
2027 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 2 | 2 | 2.4589 | 98.62% | 0% | 1.38% | 0.2425 | 0 | 0 | 0.2425 | 0 | 0.22067 | 0.30079 | 0.73365 | 0.22067 | 0.30079 | 0.73365 | 0.24488 | 0.33379 | 0.73365 | 9.862%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 49 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 89.606 | 0 | 0 | 89.606 | 0 | 81.5403 | 7.3692 | 11.0649 | 81.5403 | 7.3692 | 11.0649 | 90.4867 | 8.1778 | 11.0649 | 7.606%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 7 | 158.2514 | 99.48% | 0.3681% | 0.155% | 15.7423 | 0 | 0 | 15.7423 | 0 | 14.3253 | 1.0527 | 13.6075 | 14.3253 | 1.0527 | 13.6075 | 15.8971 | 1.1683 | 13.6075 | 9.948%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 17 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 43.9281 | 0 | 0 | 43.9281 | 0 | 39.9739 | 2.5567 | 15.6351 | 39.9739 | 2.5567 | 15.6351 | 44.3598 | 2.8372 | 15.6351 | 2.339%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 68 | 1438.3629 | 99.75% | 0% | 0.2509% | 84.1063 | 0 | 0 | 84.1063 | 0 | 76.5355 | 10.2267 | 7.4839 | 76.5355 | 10.2267 | 7.4839 | 84.9328 | 11.3488 | 7.4839 | 5.847%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 9 | 6 | 108.0997 | 99.75% | 0% | 0.2497% | 7.1887 | 0 | 0 | 7.1887 | 0 | 6.5416 | 0.90236 | 7.2494 | 6.5416 | 0.90236 | 7.2494 | 7.2593 | 1.0014 | 7.2494 | 6.65%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | Tier-2---1 | 152 | 7 | 6418.5082 | 93.04% | 6.917% | 0.04745% | 27.5004 | 0 | 0 | 27.5004 | 0 | 25.025 | 1.0527 | 23.7711 | 25.025 | 1.0527 | 23.7711 | 27.7706 | 1.1683 | 23.7711 | 0.4285%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | Tier-2---2 | 48 | 21 | 6815.4278 | 94.54% | 5.441% | 0.023% | 281.8839 | 0 | 0 | 281.8839 | 0 | 256.5105 | 3.1582 | 81.2193 | 256.5105 | 3.1582 | 81.2193 | 284.6542 | 3.5048 | 81.2193 | 4.136%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | Tier-2---1 | 267 | 156 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 681.3874 | 0 | 0 | 681.3874 | 0 | 620.0533 | 23.4613 | 26.4288 | 620.0533 | 23.4613 | 26.4288 | 688.084 | 26.0354 | 26.4288 | 5.8%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | Tier-2---2 | 146 | 84 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 208.0993 | 0 | 0 | 208.0993 | 0 | 189.3676 | 12.633 | 14.9899 | 189.3676 | 12.633 | 14.9899 | 210.1445 | 14.019 | 14.9899 | 5.647%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 32 | 1 | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 12.7268 | 0 | 0 | 12.7268 | 0 | 11.5812 | 0.15039 | 77.0063 | 11.5812 | 0.15039 | 77.0063 | 12.8518 | 0.16689 | 77.0063 | 0.3123%
2027 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 2 | 41.7756 | 94.08% | 0% | 5.924% | 0.10342 | 0 | 0 | 0.10342 | 0 | 0.094114 | 0.30079 | 0.31289 | 0.094114 | 0.30079 | 0.31289 | 0.10444 | 0.33379 | 0.31289 | 0.2476%
2027 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | Tier-2---8 | 220 | 29 | 94.186 | 2.003% | 94.63% | 3.363% | 0.024869 | 0 | 0 | 0.024869 | 0 | 0.022631 | 4.3614 | 0.0051888 | 0.022631 | 4.3614 | 0.0051888 | 0.025113 | 4.8399 | 0.0051888 | 0.0264%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 207 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1206.4301 | 0 | 0 | 1206.4301 | 0 | 1047.2599 | 29.6971 | 35.2647 | 1047.2599 | 29.6971 | 35.2647 | 1224.2588 | 34.7163 | 35.2647 | 4.59%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 139 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 323.2298 | 0 | 0 | 323.2298 | 0 | 280.5846 | 19.9416 | 14.0703 | 280.5846 | 19.9416 | 14.0703 | 328.0066 | 23.3119 | 14.0703 | 4.848%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 157 | 105 | 484.0355 | 97.4% | 1.48% | 1.12% | 31.5303 | 0 | 0 | 31.5303 | 0 | 27.3703 | 15.0638 | 1.817 | 27.3703 | 15.0638 | 1.817 | 31.9962 | 17.6097 | 1.817 | 6.514%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 94 | 54 | 400.1895 | 97.86% | 1.359% | 0.7809% | 22.4976 | 0 | 0 | 22.4976 | 0 | 19.5294 | 7.7471 | 2.5209 | 19.5294 | 7.7471 | 2.5209 | 22.8301 | 9.0564 | 2.5209 | 5.622%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 70 | 18 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 13.0303 | 0 | 0 | 13.0303 | 0 | 11.3111 | 2.5824 | 4.3802 | 11.3111 | 2.5824 | 4.3802 | 13.2228 | 3.0188 | 4.3802 | 2.538%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 119 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 149.66 | 0 | 0 | 149.66 | 0 | 129.9147 | 17.0723 | 7.6097 | 129.9147 | 17.0723 | 7.6097 | 151.8717 | 19.9577 | 7.6097 | 6.777%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 118 | 1721.769 | 85.69% | 14.07% | 0.2459% | 88.8216 | 0 | 0 | 88.8216 | 0 | 77.1029 | 16.9288 | 4.5545 | 77.1029 | 16.9288 | 4.5545 | 90.1342 | 19.79 | 4.5545 | 5.159%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | Tier-3---1 | 264 | 95 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 798.3267 | 0 | 0 | 798.3267 | 0 | 692.9996 | 13.6291 | 50.847 | 692.9996 | 13.6291 | 50.847 | 810.1244 | 15.9326 | 50.847 | 3.571%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 137 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 667.6381 | 0 | 0 | 667.6381 | 0 | 579.5534 | 19.6546 | 29.4869 | 579.5534 | 19.6546 | 29.4869 | 677.5045 | 22.9765 | 29.4869 | 5.256%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 146 | 19489.7064 | 99% | 0.9737% | 0.02962% | 1159.2381 | 0 | 0 | 1159.2381 | 0 | 1006.2942 | 20.9458 | 48.0428 | 1006.2942 | 20.9458 | 48.0428 | 1176.3694 | 24.4859 | 48.0428 | 5.948%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | Tier-2---3 | 53 | 17 | 1412.4296 | 98.09% | 1.785% | 0.1216% | 44.4404 | 0 | 0 | 44.4404 | 0 | 38.5772 | 2.4389 | 15.8175 | 38.5772 | 2.4389 | 15.8175 | 45.0971 | 2.8511 | 15.8175 | 3.146%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 37 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 157.8649 | 0 | 0 | 157.8649 | 0 | 137.037 | 5.3082 | 25.8162 | 137.037 | 5.3082 | 25.8162 | 160.1979 | 6.2053 | 25.8162 | 2.905%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 166 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 862.635 | 0 | 0 | 862.635 | 0 | 748.8234 | 23.8151 | 31.4432 | 748.8234 | 23.8151 | 31.4432 | 875.3831 | 27.8401 | 31.4432 | 6.144%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 1 | 71.2816 | 99.9% | 0% | 0.09987% | 3.5605 | 0 | 0 | 3.5605 | 0 | 3.0908 | 0.14346 | 21.5438 | 3.0908 | 0.14346 | 21.5438 | 3.6131 | 0.16771 | 21.5438 | 4.995%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 143 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 56.3417 | 0 | 0 | 56.3417 | 0 | 48.9082 | 20.5154 | 2.384 | 48.9082 | 20.5154 | 2.384 | 57.1743 | 23.9828 | 2.384 | 2.798%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 137 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 95.4292 | 0 | 0 | 95.4292 | 0 | 82.8387 | 19.6546 | 4.2147 | 82.8387 | 19.6546 | 4.2147 | 96.8394 | 22.9765 | 4.2147 | 3.499%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 90 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 297.5425 | 0 | 0 | 297.5425 | 0 | 258.2863 | 12.9118 | 20.0039 | 258.2863 | 12.9118 | 20.0039 | 301.9396 | 15.094 | 20.0039 | 2.784%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 102 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 120.5152 | 0 | 0 | 120.5152 | 0 | 104.6151 | 14.6334 | 7.1491 | 104.6151 | 14.6334 | 7.1491 | 122.2962 | 17.1066 | 7.1491 | 3.295%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 158 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 80.6911 | 0 | 0 | 80.6911 | 0 | 70.0451 | 22.6674 | 3.0901 | 70.0451 | 22.6674 | 3.0901 | 81.8836 | 26.4984 | 3.0901 | 5.609%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 116 | 102 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 881.1396 | 0 | 0 | 881.1396 | 0 | 764.8866 | 14.6334 | 52.27 | 764.8866 | 14.6334 | 52.27 | 894.1612 | 17.1066 | 52.27 | 8.71%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 96 | 860.3234 | 98.08% | 1.495% | 0.4234% | 63.7845 | 0 | 0 | 63.7845 | 0 | 55.3691 | 13.7726 | 4.0202 | 55.3691 | 13.7726 | 4.0202 | 64.7271 | 16.1003 | 4.0202 | 7.414%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | Tier-3---3 | 55 | 41 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 116.5961 | 0 | 0 | 116.5961 | 0 | 101.213 | 5.882 | 17.2071 | 101.213 | 5.882 | 17.2071 | 118.3192 | 6.8762 | 17.2071 | 7.355%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 134 | 79 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 63.4901 | 0 | 0 | 63.4901 | 0 | 55.1136 | 11.3337 | 4.8628 | 55.1136 | 11.3337 | 4.8628 | 64.4284 | 13.2492 | 4.8628 | 5.687%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 154 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 310.9447 | 0 | 0 | 310.9447 | 0 | 269.9203 | 22.0935 | 12.2172 | 269.9203 | 22.0935 | 12.2172 | 315.5399 | 25.8276 | 12.2172 | 4.96%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 76 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 50.1882 | 0 | 0 | 50.1882 | 0 | 43.5667 | 10.9033 | 3.9957 | 43.5667 | 10.9033 | 3.9957 | 50.9299 | 12.7461 | 3.9957 | 4.875%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 52 | 16 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 11.4383 | 0 | 0 | 11.4383 | 0 | 9.9292 | 2.2954 | 4.3256 | 9.9292 | 2.2954 | 4.3256 | 11.6073 | 2.6834 | 4.3256 | 3.039%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | Tier-3---1 | 464 | 238 | 3753.23 | 95.85% | 3.876% | 0.273% | 184.5275 | 0 | 0 | 184.5275 | 0 | 160.1819 | 34.1445 | 4.6913 | 160.1819 | 34.1445 | 4.6913 | 187.2545 | 39.9153 | 4.6913 | 4.916%
2028 | 249 | CB 249 | Tier-3 | Tier-3---16 | Tier-3---4 | 101 | 42 | 826.9208 | 97.04% | 2.672% | 0.2884% | 33.3688 | 0 | 0 | 33.3688 | 0 | 28.9663 | 6.0255 | 4.8073 | 28.9663 | 6.0255 | 4.8073 | 33.8619 | 7.0439 | 4.8073 | 4.035%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | Tier-2---8 | 15 | 1 | 302.428 | 99.27% | 0.6612% | 0.06922% | 2.0015 | 0 | 0 | 2.0015 | 0 | 1.7374 | 0.14346 | 12.1103 | 1.7374 | 0.14346 | 12.1103 | 2.031 | 0.16771 | 12.1103 | 0.6618%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 208 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 126.6175 | 0 | 0 | 126.6175 | 0 | 109.9123 | 29.8406 | 3.6833 | 109.9123 | 29.8406 | 3.6833 | 128.4887 | 34.884 | 3.6833 | 3.515%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 549 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 904.8024 | 0 | 0 | 904.8024 | 0 | 785.4274 | 78.762 | 9.9722 | 785.4274 | 78.762 | 9.9722 | 918.1736 | 92.0736 | 9.9722 | 6.523%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 341 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 228.2999 | 0 | 0 | 228.2999 | 0 | 198.1792 | 48.9214 | 4.051 | 198.1792 | 48.9214 | 4.051 | 231.6737 | 57.1896 | 4.051 | 4.098%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 138 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 513.1982 | 0 | 0 | 513.1982 | 0 | 445.4895 | 19.7981 | 22.5016 | 445.4895 | 19.7981 | 22.5016 | 520.7823 | 23.1442 | 22.5016 | 3.795%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 315 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 734.4742 | 0 | 0 | 734.4742 | 0 | 637.5714 | 45.1913 | 14.1083 | 637.5714 | 45.1913 | 14.1083 | 745.3283 | 52.8291 | 14.1083 | 6.557%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 162 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1108.8707 | 0 | 0 | 1108.8707 | 0 | 962.5721 | 23.2412 | 41.4166 | 962.5721 | 23.2412 | 41.4166 | 1125.2577 | 27.1693 | 41.4166 | 4.715%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 61 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 505.7262 | 0 | 0 | 505.7262 | 0 | 439.0033 | 8.7513 | 50.1642 | 439.0033 | 8.7513 | 50.1642 | 513.1999 | 10.2304 | 50.1642 | 5.531%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 69 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 651.9318 | 0 | 0 | 651.9318 | 0 | 565.9193 | 9.899 | 57.1691 | 565.9193 | 9.899 | 57.1691 | 661.5661 | 11.5721 | 57.1691 | 4.465%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 201 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 1035.5223 | 0 | 0 | 1035.5223 | 0 | 898.9008 | 28.8363 | 31.1725 | 898.9008 | 28.8363 | 31.1725 | 1050.8253 | 33.71 | 31.1725 | 5.563%
2028 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 5 | 2 | 87.8741 | 99.22% | 0.6237% | 0.1541% | 3.4876 | 0 | 0 | 3.4876 | 0 | 3.0275 | 0.28693 | 10.5514 | 3.0275 | 0.28693 | 10.5514 | 3.5392 | 0.33542 | 10.5514 | 3.969%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 130 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 572.9008 | 0 | 0 | 572.9008 | 0 | 497.3152 | 18.6504 | 26.6652 | 497.3152 | 18.6504 | 26.6652 | 581.3672 | 21.8025 | 26.6652 | 6.212%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 32 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 142.768 | 0 | 0 | 142.768 | 0 | 123.9319 | 4.5909 | 26.9954 | 123.9319 | 4.5909 | 26.9954 | 144.8778 | 5.3668 | 26.9954 | 5.668%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | Tier-2---1 | 25 | 21 | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 185.9887 | 0 | 0 | 185.9887 | 0 | 161.4503 | 3.0128 | 53.589 | 161.4503 | 3.0128 | 53.589 | 188.7373 | 3.5219 | 53.589 | 8.394%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 28 | 24 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 151.3903 | 0 | 0 | 151.3903 | 0 | 131.4166 | 3.4431 | 38.1676 | 131.4166 | 3.4431 | 38.1676 | 153.6275 | 4.0251 | 38.1676 | 7.602%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 49 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 256.7151 | 0 | 0 | 256.7151 | 0 | 222.8454 | 7.0298 | 31.7003 | 222.8454 | 7.0298 | 31.7003 | 260.5089 | 8.2179 | 31.7003 | 5.635%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 7 | 465.1006 | 62.84% | 37.09% | 0.07221% | 18.5989 | 0 | 0 | 18.5989 | 0 | 16.145 | 1.0043 | 16.0767 | 16.145 | 1.0043 | 16.0767 | 18.8737 | 1.174 | 16.0767 | 3.999%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 106 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 788.1248 | 0 | 0 | 788.1248 | 0 | 684.1437 | 15.2072 | 44.9881 | 684.1437 | 15.2072 | 44.9881 | 799.7718 | 17.7774 | 44.9881 | 5.823%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 245 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1035.9959 | 0 | 0 | 1035.9959 | 0 | 899.312 | 35.1488 | 25.5859 | 899.312 | 35.1488 | 25.5859 | 1051.3059 | 41.0893 | 25.5859 | 5.051%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 42 | 3653.654 | 88.54% | 11.39% | 0.07412% | 152.6531 | 0 | 0 | 152.6531 | 0 | 132.5128 | 6.0255 | 21.992 | 132.5128 | 6.0255 | 21.992 | 154.909 | 7.0439 | 21.992 | 4.178%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 14 | 296.7138 | 97.11% | 2.719% | 0.1664% | 22.4119 | 0 | 0 | 22.4119 | 0 | 19.455 | 2.0085 | 9.6863 | 19.455 | 2.0085 | 9.6863 | 22.7431 | 2.348 | 9.6863 | 7.553%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 110 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 432.1306 | 0 | 0 | 432.1306 | 0 | 375.1176 | 15.7811 | 23.7701 | 375.1176 | 15.7811 | 23.7701 | 438.5167 | 18.4483 | 23.7701 | 5.223%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 16 | 792.2018 | 92.77% | 7.138% | 0.09408% | 26.7241 | 0 | 0 | 26.7241 | 0 | 23.1982 | 2.2954 | 10.1063 | 23.1982 | 2.2954 | 10.1063 | 27.119 | 2.6834 | 10.1063 | 3.373%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 39 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 60.0888 | 0 | 0 | 60.0888 | 0 | 52.161 | 5.5951 | 9.3226 | 52.161 | 5.5951 | 9.3226 | 60.9768 | 6.5408 | 9.3226 | 5.307%
2028 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 18 | 5 | 537.0702 | 32.53% | 67.41% | 0.0594% | 4.8529 | 0 | 0 | 4.8529 | 0 | 4.2127 | 0.71732 | 5.8728 | 4.2127 | 0.71732 | 5.8728 | 4.9247 | 0.83856 | 5.8728 | 0.9036%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 5 | 4 | 137.227 | 99.9% | 0% | 0.1049% | 10.9666 | 0 | 0 | 10.9666 | 0 | 9.5198 | 0.57386 | 16.5891 | 9.5198 | 0.57386 | 16.5891 | 11.1287 | 0.67085 | 16.5891 | 7.992%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 15 | 625.5425 | 99.9% | 0% | 0.09615% | 46.8706 | 0 | 0 | 46.8706 | 0 | 40.6867 | 2.152 | 18.9068 | 40.6867 | 2.152 | 18.9068 | 47.5632 | 2.5157 | 18.9068 | 7.493%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 8 | 181.2174 | 99.84% | 0% | 0.161% | 12.0617 | 0 | 0 | 12.0617 | 0 | 10.4704 | 1.1477 | 9.1228 | 10.4704 | 1.1477 | 9.1228 | 12.24 | 1.3417 | 9.1228 | 6.656%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 40 | 2823.7515 | 99.93% | 0% | 0.06613% | 158.9794 | 0 | 0 | 158.9794 | 0 | 138.0045 | 5.7386 | 24.0486 | 138.0045 | 5.7386 | 24.0486 | 161.3288 | 6.7085 | 24.0486 | 5.63%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 2 | 2 | 39.0262 | 97.23% | 2.586% | 0.1833% | 3.7945 | 0 | 0 | 3.7945 | 0 | 3.2939 | 0.28693 | 11.4799 | 3.2939 | 0.28693 | 11.4799 | 3.8506 | 0.33542 | 11.4799 | 9.723%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 53 | 29 | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 187.723 | 0 | 0 | 187.723 | 0 | 162.9558 | 4.1605 | 39.1677 | 162.9558 | 4.1605 | 39.1677 | 190.4972 | 4.8636 | 39.1677 | 5.455%
2028 | 454 | 454-49F | Tier-2 | Tier-2---13 | Tier-2---8 | 52 | 1 | 292.9743 | 76.06% | 23.59% | 0.3558% | 0.42851 | 0 | 0 | 0.42851 | 0 | 0.37198 | 0.14346 | 2.5928 | 0.37198 | 0.14346 | 2.5928 | 0.43484 | 0.16771 | 2.5928 | 0.1463%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 179 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 504.7803 | 0 | 0 | 504.7803 | 0 | 438.1822 | 25.6801 | 17.0631 | 438.1822 | 25.6801 | 17.0631 | 512.24 | 30.0204 | 17.0631 | 5.793%
2028 | 907 | 907-1475 | Tier-3 | Tier-3---21 | Tier-3---21 | 4 | 4 | 4.2814 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.57386 | 0 | 0 | 0.57386 | 0 | 0 | 0.67085 | 0 | 0%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | Tier-3---2 | 162 | 90 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 457.698 | 0 | 0 | 457.698 | 0 | 397.3117 | 12.9118 | 30.7712 | 397.3117 | 12.9118 | 30.7712 | 464.4619 | 15.094 | 30.7712 | 5.423%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | Tier-3---9 | 5 | 5 | 257.2419 | 98.67% | 1.294% | 0.04048% | 25.3809 | 0 | 0 | 25.3809 | 0 | 22.0323 | 0.71732 | 30.7146 | 22.0323 | 0.71732 | 30.7146 | 25.756 | 0.83856 | 30.7146 | 9.867%
2028 | 907 | 907-1604 | Tier-3 | Tier-3---19 | Tier-3---16 | 2 | 4 | 17.8439 | 83.33% | 16.48% | 0.1969% | 2.9738 | 0 | 0 | 2.9738 | 0 | 2.5814 | 0.57386 | 4.4984 | 2.5814 | 0.57386 | 4.4984 | 3.0177 | 0.67085 | 4.4984 | 16.67%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 78 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 478.3115 | 0 | 0 | 478.3115 | 0 | 415.2056 | 11.1902 | 37.1043 | 415.2056 | 11.1902 | 37.1043 | 485.38 | 13.0815 | 37.1043 | 5.256%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 214 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1480.8013 | 0 | 0 | 1480.8013 | 0 | 1285.4321 | 30.7014 | 41.8689 | 1285.4321 | 30.7014 | 41.8689 | 1502.6847 | 35.8903 | 41.8689 | 5.471%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 33 | 4 | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 76.9327 | 0 | 0 | 76.9327 | 0 | 66.7826 | 0.57386 | 116.3748 | 66.7826 | 0.57386 | 116.3748 | 78.0696 | 0.67085 | 116.3748 | 1.212%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 35 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 187.8839 | 0 | 0 | 187.8839 | 0 | 163.0954 | 5.0213 | 32.481 | 163.0954 | 5.0213 | 32.481 | 190.6604 | 5.8699 | 32.481 | 6.851%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 151 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 772.5707 | 0 | 0 | 772.5707 | 0 | 670.6417 | 21.6631 | 30.9578 | 670.6417 | 21.6631 | 30.9578 | 783.9878 | 25.3244 | 30.9578 | 4.9%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 112 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 784.2023 | 0 | 0 | 784.2023 | 0 | 680.7387 | 16.068 | 42.3661 | 680.7387 | 16.068 | 42.3661 | 795.7913 | 18.7837 | 42.3661 | 6.666%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 292 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 2044.5274 | 0 | 0 | 2044.5274 | 0 | 1774.783 | 41.8916 | 42.3661 | 1774.783 | 41.8916 | 42.3661 | 2074.7416 | 48.9718 | 42.3661 | 17.38%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 110 | 1466.2762 | 91.81% | 7.905% | 0.289% | 98.7161 | 0 | 0 | 98.7161 | 0 | 85.692 | 15.7811 | 5.43 | 85.692 | 15.7811 | 5.43 | 100.175 | 18.4483 | 5.43 | 6.732%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 73 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 464.6324 | 0 | 0 | 464.6324 | 0 | 403.3312 | 10.4729 | 38.5119 | 403.3312 | 10.4729 | 38.5119 | 471.4988 | 12.2429 | 38.5119 | 5.837%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 222 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 1655.9075 | 0 | 0 | 1655.9075 | 0 | 1437.4356 | 31.8491 | 45.1327 | 1437.4356 | 31.8491 | 45.1327 | 1680.3786 | 37.232 | 45.1327 | 4.013%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | Tier-2---1 | 162 | 98 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 202.7617 | 0 | 0 | 202.7617 | 0 | 176.0103 | 14.0595 | 12.5189 | 176.0103 | 14.0595 | 12.5189 | 205.7581 | 16.4357 | 12.5189 | 5.56%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 213 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1311.8833 | 0 | 0 | 1311.8833 | 0 | 1138.8003 | 30.5579 | 37.2669 | 1138.8003 | 30.5579 | 37.2669 | 1331.2705 | 35.7226 | 37.2669 | 5.814%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | Tier-2---10 | 7 | 1 | 153.3115 | 98.58% | 1.358% | 0.06577% | 2.159 | 0 | 0 | 2.159 | 0 | 1.8741 | 0.14346 | 13.0635 | 1.8741 | 0.14346 | 13.0635 | 2.1909 | 0.16771 | 13.0635 | 1.408%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 32 | 847.524 | 96.52% | 3.329% | 0.1488% | 50.3414 | 0 | 0 | 50.3414 | 0 | 43.6996 | 4.5909 | 9.5188 | 43.6996 | 4.5909 | 9.5188 | 51.0853 | 5.3668 | 9.5188 | 5.94%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 329 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 3566.384 | 0 | 0 | 3566.384 | 0 | 3095.8537 | 47.1998 | 65.5904 | 3095.8537 | 47.1998 | 65.5904 | 3619.0883 | 55.1771 | 65.5904 | 6.455%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 17 | 5703.0403 | 99.97% | 0% | 0.03309% | 156.3219 | 0 | 0 | 156.3219 | 0 | 135.6976 | 2.4389 | 55.639 | 135.6976 | 2.4389 | 55.639 | 158.6321 | 2.8511 | 55.639 | 2.741%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 219 | 32313.161 | 99.26% | 0.708% | 0.02831% | 2273.2946 | 0 | 0 | 2273.2946 | 0 | 1973.3679 | 31.4187 | 62.8087 | 1973.3679 | 31.4187 | 62.8087 | 2306.8896 | 36.7288 | 62.8087 | 7.035%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 343 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 2314.021 | 0 | 0 | 2314.021 | 0 | 2008.721 | 49.2083 | 40.8208 | 2008.721 | 49.2083 | 40.8208 | 2348.2178 | 57.5251 | 40.8208 | 6.582%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 53 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 431.9184 | 0 | 0 | 431.9184 | 0 | 374.9333 | 7.6036 | 49.3099 | 374.9333 | 7.6036 | 49.3099 | 438.3013 | 8.8887 | 49.3099 | 6.122%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 99 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 1106.0291 | 0 | 0 | 1106.0291 | 0 | 960.1054 | 14.203 | 67.5989 | 960.1054 | 14.203 | 67.5989 | 1122.3741 | 16.6034 | 67.5989 | 5.875%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 69 | 47 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 341.225 | 0 | 0 | 341.225 | 0 | 296.2055 | 6.7428 | 43.929 | 296.2055 | 6.7428 | 43.929 | 346.2677 | 7.8824 | 43.929 | 6.778%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 16 | 14 | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 120.8196 | 0 | 0 | 120.8196 | 0 | 104.8793 | 2.0085 | 52.2177 | 104.8793 | 2.0085 | 52.2177 | 122.605 | 2.348 | 52.2177 | 8.713%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 12 | 6 | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.5589 | 0 | 0 | 39.5589 | 0 | 34.3397 | 0.86079 | 39.8934 | 34.3397 | 0.86079 | 39.8934 | 40.1435 | 1.0063 | 39.8934 | 4.98%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 75 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 526.809 | 0 | 0 | 526.809 | 0 | 457.3046 | 10.7598 | 42.5011 | 457.3046 | 10.7598 | 42.5011 | 534.5942 | 12.5784 | 42.5011 | 5.375%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 9 | 6 | 694.7204 | 99.22% | 0.7469% | 0.03547% | 45.9523 | 0 | 0 | 45.9523 | 0 | 39.8896 | 0.86079 | 46.3409 | 39.8896 | 0.86079 | 46.3409 | 46.6314 | 1.0063 | 46.3409 | 6.615%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 66 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 372.9812 | 0 | 0 | 372.9812 | 0 | 323.772 | 9.4687 | 34.1941 | 323.772 | 9.4687 | 34.1941 | 378.4931 | 11.069 | 34.1941 | 7.353%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 37 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 71.7043 | 0 | 0 | 71.7043 | 0 | 62.244 | 5.3082 | 11.726 | 62.244 | 5.3082 | 11.726 | 72.764 | 6.2053 | 11.726 | 0.7572%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 81 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 78.3431 | 0 | 0 | 78.3431 | 0 | 68.0069 | 11.6206 | 5.8523 | 68.0069 | 11.6206 | 5.8523 | 79.5008 | 13.5846 | 5.8523 | 2.076%
2028 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 17 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 72.4999 | 0 | 0 | 72.4999 | 0 | 62.9346 | 2.4389 | 25.8046 | 62.9346 | 2.4389 | 25.8046 | 73.5713 | 2.8511 | 25.8046 | 2.175%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 85 | 48 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 284.3306 | 0 | 0 | 284.3306 | 0 | 246.8175 | 6.8863 | 35.8419 | 246.8175 | 6.8863 | 35.8419 | 288.5324 | 8.0502 | 35.8419 | 5.549%
2028 | 1030 | 1030-1735F | Tier-3 | missing | missing | 6 | 3 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.43039 | 0 | 0 | 0.43039 | 0 | 0 | 0.50313 | 0 | 0%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 90 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 543.28 | 0 | 0 | 543.28 | 0 | 471.6024 | 12.9118 | 36.5249 | 471.6024 | 12.9118 | 36.5249 | 551.3086 | 15.094 | 36.5249 | 4.597%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 20 | 10 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 106.9533 | 0 | 0 | 106.9533 | 0 | 92.8424 | 1.4346 | 64.7146 | 92.8424 | 1.4346 | 64.7146 | 108.5338 | 1.6771 | 64.7146 | 4.972%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 98 | 32 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 213.2936 | 0 | 0 | 213.2936 | 0 | 185.1527 | 4.5909 | 40.3307 | 185.1527 | 4.5909 | 40.3307 | 216.4456 | 5.3668 | 40.3307 | 3.222%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 85 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 581.3655 | 0 | 0 | 581.3655 | 0 | 504.6632 | 12.1945 | 41.3846 | 504.6632 | 12.1945 | 41.3846 | 589.957 | 14.2555 | 41.3846 | 2.296%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 208 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1232.6316 | 0 | 0 | 1232.6316 | 0 | 1070.0046 | 29.8406 | 35.8573 | 1070.0046 | 29.8406 | 35.8573 | 1250.8476 | 34.884 | 35.8573 | 4.34%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 201 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1260.8521 | 0 | 0 | 1260.8521 | 0 | 1094.5018 | 28.8363 | 37.9556 | 1094.5018 | 28.8363 | 37.9556 | 1279.4851 | 33.71 | 37.9556 | 4.723%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 293 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 853.2602 | 0 | 0 | 853.2602 | 0 | 740.6854 | 42.0351 | 17.6207 | 740.6854 | 42.0351 | 17.6207 | 865.8697 | 49.1395 | 17.6207 | 5.347%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 75 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 109.7252 | 0 | 0 | 109.7252 | 0 | 95.2486 | 10.7598 | 8.8522 | 95.2486 | 10.7598 | 8.8522 | 111.3467 | 12.5784 | 8.8522 | 7.04%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | Tier-3---1 | 166 | 105 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 221.7431 | 0 | 0 | 221.7431 | 0 | 192.4875 | 15.0638 | 12.7782 | 192.4875 | 15.0638 | 12.7782 | 225.02 | 17.6097 | 12.7782 | 6.225%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 132 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 206.1973 | 0 | 0 | 206.1973 | 0 | 178.9927 | 18.9373 | 9.4519 | 178.9927 | 18.9373 | 9.4519 | 209.2445 | 22.1379 | 9.4519 | 6.911%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 42 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 99.3139 | 0 | 0 | 99.3139 | 0 | 86.2109 | 6.0255 | 14.3077 | 86.2109 | 6.0255 | 14.3077 | 100.7815 | 7.0439 | 14.3077 | 7.163%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | Tier-3---1 | 167 | 126 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 320.0959 | 0 | 0 | 320.0959 | 0 | 277.8641 | 18.0765 | 15.3716 | 277.8641 | 18.0765 | 15.3716 | 324.8264 | 21.1317 | 15.3716 | 7.444%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 66 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 146.2955 | 0 | 0 | 146.2955 | 0 | 126.994 | 9.4687 | 13.4121 | 126.994 | 9.4687 | 13.4121 | 148.4575 | 11.069 | 13.4121 | 2.318%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 6 | 1 | 27.4807 | 90.21% | 9.514% | 0.2799% | 0.41315 | 0 | 0 | 0.41315 | 0 | 0.35864 | 0.14346 | 2.4999 | 0.35864 | 0.14346 | 2.4999 | 0.41926 | 0.16771 | 2.4999 | 1.503%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 51 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 201.1581 | 0 | 0 | 201.1581 | 0 | 174.6184 | 7.3167 | 23.8658 | 174.6184 | 7.3167 | 23.8658 | 204.1309 | 8.5533 | 23.8658 | 5.379%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 82 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 42.5284 | 0 | 0 | 42.5284 | 0 | 36.9174 | 11.7641 | 3.1381 | 36.9174 | 11.7641 | 3.1381 | 43.1568 | 13.7523 | 3.1381 | 2.06%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 212 | 6920.124 | 97.57% | 2.306% | 0.1195% | 330.5959 | 0 | 0 | 330.5959 | 0 | 286.9788 | 30.4145 | 9.4356 | 286.9788 | 30.4145 | 9.4356 | 335.4814 | 35.5548 | 9.4356 | 4.777%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | Tier-3---1 | 125 | 72 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 340.1755 | 0 | 0 | 340.1755 | 0 | 295.2945 | 10.3294 | 28.5877 | 295.2945 | 10.3294 | 28.5877 | 345.2026 | 12.0752 | 28.5877 | 5.721%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | Tier-3---1 | 103 | 58 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 211.9082 | 0 | 0 | 211.9082 | 0 | 183.9501 | 8.3209 | 22.1069 | 183.9501 | 8.3209 | 22.1069 | 215.0398 | 9.7273 | 22.1069 | 5.602%

## OH Detail Inspection
OH Detail - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2026 | 19638 | 2432751.9045 | 197133.102 | 8.103% | 188051.5863 | 1280.8413 | 146.8188 | 188051.5863 | 1280.8413 | 146.8188 | 198099.4407 | 1349.2784 | 146.8188
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 15365 | 1114433.6972 | 78283.5513 | 7.025% | 71236.9653 | 955.9784 | 74.5173 | 71236.9653 | 955.9784 | 74.5173 | 79052.9182 | 1060.8661 | 74.5173
[9 empty] | Capital Cost only in Year 0 | 0.068372 | K$/inspection | 2025-05-01 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 10276 | 664609.6054 | 51542.0883 | 7.755% | 44741.8922 | 609.8978 | 73.3597 | 44741.8922 | 609.8978 | 73.3597 | 52303.7818 | 712.9774 | 73.3597
[9 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [9 empty] | Total 2026-2028 | 45279 | 4211795.2071 | 326958.7415 | 7.763% | 304030.4438 | 2846.7174 | 106.8004 | 304030.4438 | 2846.7174 | 106.8004 | 329456.1407 | 3123.1219 | 105.4894
[9 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[9 empty] | Lifetime | 1 | Years | 2025-05-01
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[9 empty] | Mitigation Effectiveness Estimate (%) | 29% | % | 2025-05-01
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[13 empty] | [1] | [1] |  | [2]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units in Scope (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 310 | 151 | 6201.607 | 97.29% | 2.601% | 0.1104% | 852.2757 | 0 | 0 | 852.2757 | 0 | 813.0131 | 9.8486 | 82.551 | 813.0131 | 9.8486 | 82.551 | 856.4535 | 10.3748 | 82.551 | 13.74%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 188 | 1 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 8.7038 | 0 | 0 | 8.7038 | 0 | 8.3029 | 0.065223 | 127.3007 | 8.3029 | 0.065223 | 127.3007 | 8.7465 | 0.068708 | 127.3007 | 0.1518%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | Tier-3---1 | 188 | 77 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 670.1964 | 0 | 0 | 670.1964 | 0 | 639.3218 | 5.0221 | 127.3007 | 639.3218 | 5.0221 | 127.3007 | 673.4817 | 5.2905 | 127.3007 | 11.69%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 4 | 17.7969 | 99.34% | 0% | 0.6614% | 5.127 | 0 | 0 | 5.127 | 0 | 4.8908 | 0.26089 | 18.7465 | 4.8908 | 0.26089 | 18.7465 | 5.1521 | 0.27483 | 18.7465 | 28.81%
2026 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 4 | 1 | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.065223 | 0 | 0 | 0.065223 | 0 | 0 | 0.068708 | 0 | 0%
2026 | 75 | 75-2258F | Tier-3 | Tier-3---21 | Tier-3---18 | 4 | 2 | 4.4231 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.13045 | 0 | 0 | 0.13045 | 0 | 0 | 0.13742 | 0 | 0%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | Tier-3---6 | 140 | 102 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 660.9588 | 0 | 0 | 660.9588 | 0 | 630.5098 | 6.6527 | 94.775 | 630.5098 | 6.6527 | 94.775 | 664.1988 | 7.0082 | 94.775 | 21.08%
2026 | 75 | 75-2260F | Tier-3 | missing | missing | 2 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.065223 | 0 | 0 | 0.065223 | 0 | 0 | 0.068708 | 0 | 0%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 1 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 5.8729 | 0 | 0 | 5.8729 | 0 | 5.6024 | 0.065223 | 85.896 | 5.6024 | 0.065223 | 85.896 | 5.9017 | 0.068708 | 85.896 | 0.3438%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | Tier-3---6 | 84 | 64 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 375.8663 | 0 | 0 | 375.8663 | 0 | 358.5509 | 4.1742 | 85.896 | 358.5509 | 4.1742 | 85.896 | 377.7088 | 4.3973 | 85.896 | 22%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | Tier-3---6 | 69 | 45 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 365.936 | 0 | 0 | 365.936 | 0 | 349.0781 | 2.935 | 118.9356 | 349.0781 | 2.935 | 118.9356 | 367.7298 | 3.0918 | 118.9356 | 18.89%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 5 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 9.973 | 0 | 0 | 9.973 | 0 | 9.5135 | 0.32611 | 29.1725 | 9.5135 | 0.32611 | 29.1725 | 10.0218 | 0.34354 | 29.1725 | 0.451%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | Tier-2---2 | 319 | 115 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 229.3779 | 0 | 0 | 229.3779 | 0 | 218.811 | 7.5006 | 29.1725 | 218.811 | 7.5006 | 29.1725 | 230.5023 | 7.9014 | 29.1725 | 10.37%
2026 | 75 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 4 | 337.7351 | 93.43% | 6.078% | 0.496% | 5.3826 | 0 | 0 | 5.3826 | 0 | 5.1346 | 0.26089 | 19.6812 | 5.1346 | 0.26089 | 19.6812 | 5.409 | 0.27483 | 19.6812 | 1.594%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 116 | 79 | 3034.8235 | 97.12% | 2.752% | 0.1275% | 582.1179 | 0 | 0 | 582.1179 | 0 | 555.3009 | 5.1526 | 107.7713 | 555.3009 | 5.1526 | 107.7713 | 584.9714 | 5.4279 | 107.7713 | 19.18%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | Tier-2---2 | 194 | 10 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 18.5941 | 0 | 0 | 18.5941 | 0 | 17.7375 | 0.65223 | 27.1954 | 17.7375 | 0.65223 | 27.1954 | 18.6853 | 0.68708 | 27.1954 | 1.435%
2026 | 91 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 90 | 6 | 481.3309 | 94.25% | 5.298% | 0.4514% | 8.7707 | 0 | 0 | 8.7707 | 0 | 8.3666 | 0.39134 | 21.3797 | 8.3666 | 0.39134 | 21.3797 | 8.8137 | 0.41225 | 21.3797 | 1.822%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 6 | 337.7351 | 93.43% | 6.078% | 0.496% | 8.0739 | 0 | 0 | 8.0739 | 0 | 7.7019 | 0.39134 | 19.6812 | 7.7019 | 0.39134 | 19.6812 | 8.1135 | 0.41225 | 19.6812 | 2.391%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 68 | 20 | 337.7351 | 93.43% | 6.078% | 0.496% | 26.9129 | 0 | 0 | 26.9129 | 0 | 25.6731 | 1.3045 | 19.6812 | 25.6731 | 1.3045 | 19.6812 | 27.0449 | 1.3742 | 19.6812 | 7.969%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | Tier-3---10 | 87 | 11 | 418.5676 | 87.71% | 11.66% | 0.6303% | 13.4606 | 0 | 0 | 13.4606 | 0 | 12.8405 | 0.71745 | 17.8975 | 12.8405 | 0.71745 | 17.8975 | 13.5266 | 0.75578 | 17.8975 | 3.216%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | Tier-3---3 | 60 | 55 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 803.9365 | 0 | 0 | 803.9365 | 0 | 766.9008 | 3.5872 | 213.7856 | 766.9008 | 3.5872 | 213.7856 | 807.8774 | 3.7789 | 213.7856 | 26.34%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | Tier-3---3 | 554 | 329 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 289.4512 | 0 | 0 | 289.4512 | 0 | 276.1167 | 21.4582 | 12.8676 | 276.1167 | 21.4582 | 12.8676 | 290.87 | 22.6048 | 12.8676 | 14.04%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | Tier-3---1 | 675 | 562 | 18749.5963 | 97% | 2.901% | 0.09453% | 4391.5357 | 0 | 0 | 4391.5357 | 0 | 4189.2267 | 36.6551 | 114.2877 | 4189.2267 | 36.6551 | 114.2877 | 4413.0629 | 38.6136 | 114.2877 | 23.42%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | Tier-3---1 | 239 | 25 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 129.7354 | 0 | 0 | 129.7354 | 0 | 123.7587 | 1.6306 | 75.8993 | 123.7587 | 1.6306 | 75.8993 | 130.3713 | 1.7177 | 75.8993 | 2.958%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | Tier-3---1 | 131 | 126 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 1145.034 | 0 | 0 | 1145.034 | 0 | 1092.2847 | 8.218 | 132.9129 | 1092.2847 | 8.218 | 132.9129 | 1150.6469 | 8.6571 | 132.9129 | 27.36%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 172 | 1 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 5.6047 | 0 | 0 | 5.6047 | 0 | 5.3465 | 0.065223 | 81.9728 | 5.3465 | 0.065223 | 81.9728 | 5.6321 | 0.068708 | 81.9728 | 0.1648%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | Tier-3---1 | 172 | 104 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 582.8861 | 0 | 0 | 582.8861 | 0 | 556.0337 | 6.7831 | 81.9728 | 556.0337 | 6.7831 | 81.9728 | 585.7434 | 7.1456 | 81.9728 | 17.14%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | Tier-3---1 | 345 | 260 | 13172.958 | 96.8% | 3.124% | 0.0728% | 2786.9244 | 0 | 0 | 2786.9244 | 0 | 2658.5366 | 16.9579 | 156.773 | 2658.5366 | 16.9579 | 156.773 | 2800.5858 | 17.864 | 156.773 | 21.16%
2026 | 176 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 1 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 12.6498 | 0 | 0 | 12.6498 | 0 | 12.0671 | 0.065223 | 185.0136 | 12.0671 | 0.065223 | 185.0136 | 12.7118 | 0.068708 | 185.0136 | 0.0835%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | Tier-3---3 | 30 | 27 | 1635.841 | 89.24% | 10.7% | 0.05535% | 381.0308 | 0 | 0 | 381.0308 | 0 | 363.4775 | 1.761 | 206.4029 | 363.4775 | 1.761 | 206.4029 | 382.8986 | 1.8551 | 206.4029 | 23.29%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 41 | 973.0999 | 95.53% | 4.02% | 0.4464% | 58.7946 | 0 | 0 | 58.7946 | 0 | 56.086 | 2.6741 | 20.9736 | 56.086 | 2.6741 | 20.9736 | 59.0828 | 2.817 | 20.9736 | 6.042%
2026 | 205 | 205-1550 | Tier-2 | Tier-2---15 | Tier-2---13 | 102 | 1 | 124.0064 | 98.52% | 0% | 1.478% | 0.34736 | 0 | 0 | 0.34736 | 0 | 0.33135 | 0.065223 | 5.0804 | 0.33135 | 0.065223 | 5.0804 | 0.34906 | 0.068708 | 5.0804 | 0.2801%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 39 | 2976.5734 | 99.75% | 0% | 0.2502% | 81.3095 | 0 | 0 | 81.3095 | 0 | 77.5637 | 2.5437 | 30.4927 | 77.5637 | 2.5437 | 30.4927 | 81.7081 | 2.6796 | 30.4927 | 2.732%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 137 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 2315.5298 | 0 | 0 | 2315.5298 | 0 | 2208.8581 | 8.9355 | 247.2004 | 2208.8581 | 8.9355 | 247.2004 | 2326.8804 | 9.4129 | 247.2004 | 8.811%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 24 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 161.8475 | 0 | 0 | 161.8475 | 0 | 154.3915 | 1.5653 | 98.6311 | 154.3915 | 1.5653 | 98.6311 | 162.6408 | 1.649 | 98.6311 | 2.428%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 32 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 116.7097 | 0 | 0 | 116.7097 | 0 | 111.3331 | 2.0871 | 53.3429 | 111.3331 | 2.0871 | 53.3429 | 117.2818 | 2.1986 | 53.3429 | 5.285%
2026 | 214 | CB 214 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 59.1996 | 99.88% | 0% | 0.1188% | 11.4317 | 0 | 0 | 11.4317 | 0 | 10.905 | 0.13045 | 83.5986 | 10.905 | 0.13045 | 83.5986 | 11.4877 | 0.13742 | 83.5986 | 19.31%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | Tier-2---1 | 256 | 5 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 70.6624 | 0 | 0 | 70.6624 | 0 | 67.4072 | 0.32611 | 206.6988 | 67.4072 | 0.32611 | 206.6988 | 71.0088 | 0.34354 | 206.6988 | 0.5563%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 1 | 19489.7064 | 99% | 0.9737% | 0.02962% | 23.026 | 0 | 0 | 23.026 | 0 | 21.9652 | 0.065223 | 336.7729 | 21.9652 | 0.065223 | 336.7729 | 23.1388 | 0.068708 | 336.7729 | 0.1181%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | Tier-2---1 | 243 | 149 | 19489.7064 | 99% | 0.9737% | 0.02962% | 3430.8684 | 0 | 0 | 3430.8684 | 0 | 3272.8154 | 9.7182 | 336.7729 | 3272.8154 | 9.7182 | 336.7729 | 3447.6864 | 10.2374 | 336.7729 | 17.6%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 32 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 395.9423 | 0 | 0 | 395.9423 | 0 | 377.702 | 2.0871 | 180.9678 | 377.702 | 2.0871 | 180.9678 | 397.8832 | 2.1986 | 180.9678 | 7.285%
2026 | 215 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 1 | 71.2816 | 99.9% | 0% | 0.09987% | 10.3255 | 0 | 0 | 10.3255 | 0 | 9.8498 | 0.065223 | 151.0187 | 9.8498 | 0.065223 | 151.0187 | 10.3761 | 0.068708 | 151.0187 | 14.49%
2026 | 215 | CB 215 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 133.9133 | 99.89% | 0% | 0.1056% | 23.2763 | 0 | 0 | 23.2763 | 0 | 22.204 | 0.19567 | 113.4782 | 22.204 | 0.19567 | 113.4782 | 23.3904 | 0.20612 | 113.4782 | 17.38%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 1 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 15.0701 | 0 | 0 | 15.0701 | 0 | 14.3759 | 0.065223 | 220.4126 | 14.3759 | 0.065223 | 220.4126 | 15.144 | 0.068708 | 220.4126 | 0.1073%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | Tier-3---1 | 268 | 190 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 2863.3247 | 0 | 0 | 2863.3247 | 0 | 2731.4172 | 12.3923 | 220.4126 | 2731.4172 | 12.3923 | 220.4126 | 2877.3606 | 13.0544 | 220.4126 | 20.39%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 1 | 71.2816 | 99.9% | 0% | 0.09987% | 10.3255 | 0 | 0 | 10.3255 | 0 | 9.8498 | 0.065223 | 151.0187 | 9.8498 | 0.065223 | 151.0187 | 10.3761 | 0.068708 | 151.0187 | 14.49%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | Tier-2---3 | 456 | 272 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 310.7853 | 0 | 0 | 310.7853 | 0 | 296.4681 | 17.7405 | 16.7113 | 296.4681 | 17.7405 | 16.7113 | 312.3087 | 18.6884 | 16.7113 | 15.43%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | Tier-2---3 | 344 | 45 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 90.9015 | 0 | 0 | 90.9015 | 0 | 86.7139 | 2.935 | 29.5446 | 86.7139 | 2.935 | 29.5446 | 91.3471 | 3.0918 | 29.5446 | 3.333%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | Tier-3---1 | 319 | 13 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 124.6373 | 0 | 0 | 124.6373 | 0 | 118.8955 | 0.84789 | 140.2245 | 118.8955 | 0.84789 | 140.2245 | 125.2482 | 0.8932 | 140.2245 | 1.166%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 113 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 387.1846 | 0 | 0 | 387.1846 | 0 | 369.3478 | 7.3702 | 50.114 | 369.3478 | 7.3702 | 50.114 | 389.0826 | 7.764 | 50.114 | 10.59%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | Tier-2---3 | 256 | 104 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 154.0281 | 0 | 0 | 154.0281 | 0 | 146.9323 | 6.7831 | 21.6614 | 146.9323 | 6.7831 | 21.6614 | 154.7831 | 7.1456 | 21.6614 | 10.71%
2026 | 217 | CB 217 | Tier-3 | Tier-3---20 | Tier-3---11 | 3 | 2 | 26.6678 | 99.71% | 0% | 0.2895% | 5.1409 | 0 | 0 | 5.1409 | 0 | 4.904 | 0.13045 | 37.5945 | 4.904 | 0.13045 | 37.5945 | 5.1661 | 0.13742 | 37.5945 | 19.28%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 14 | 2730.9177 | 98.3% | 1.373% | 0.325% | 30.5301 | 0 | 0 | 30.5301 | 0 | 29.1236 | 0.91312 | 31.8948 | 29.1236 | 0.91312 | 31.8948 | 30.6797 | 0.96191 | 31.8948 | 1.118%
2026 | 231 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 1 | 754.1323 | 92.41% | 6.882% | 0.7076% | 0.8084 | 0 | 0 | 0.8084 | 0 | 0.77116 | 0.065223 | 11.8235 | 0.77116 | 0.065223 | 11.8235 | 0.81236 | 0.068708 | 11.8235 | 0.1072%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 19 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 40.1289 | 0 | 0 | 40.1289 | 0 | 38.2802 | 1.2392 | 30.8903 | 38.2802 | 1.2392 | 30.8903 | 40.3256 | 1.3054 | 30.8903 | 1.322%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 28 | 718.991 | 97.57% | 1.357% | 1.072% | 20.8658 | 0 | 0 | 20.8658 | 0 | 19.9045 | 1.8262 | 10.8992 | 19.9045 | 1.8262 | 10.8992 | 20.9681 | 1.9238 | 10.8992 | 2.902%
2026 | 233 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 1 | 585.5086 | 87.68% | 11.85% | 0.4758% | 1.2511 | 0 | 0 | 1.2511 | 0 | 1.1934 | 0.065223 | 18.2976 | 1.1934 | 0.065223 | 18.2976 | 1.2572 | 0.068708 | 18.2976 | 0.2137%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 21 | 447.7794 | 94.96% | 4.349% | 0.694% | 26.1562 | 0 | 0 | 26.1562 | 0 | 24.9512 | 1.3697 | 18.2169 | 24.9512 | 1.3697 | 18.2169 | 26.2844 | 1.4429 | 18.2169 | 5.841%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 99 | 1 | 447.7794 | 94.96% | 4.349% | 0.694% | 1.2455 | 0 | 0 | 1.2455 | 0 | 1.1882 | 0.065223 | 18.2169 | 1.1882 | 0.065223 | 18.2169 | 1.2516 | 0.068708 | 18.2169 | 0.2782%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 72 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 101.9449 | 0 | 0 | 101.9449 | 0 | 97.2485 | 4.696 | 20.7087 | 97.2485 | 4.696 | 20.7087 | 102.4446 | 4.9469 | 20.7087 | 4.354%
2026 | 233 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 1 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 1.7653 | 0 | 0 | 1.7653 | 0 | 1.684 | 0.065223 | 25.8195 | 1.684 | 0.065223 | 25.8195 | 1.774 | 0.068708 | 25.8195 | 0.04901%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 1 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 4.6658 | 0 | 0 | 4.6658 | 0 | 4.4509 | 0.065223 | 68.2412 | 4.4509 | 0.065223 | 68.2412 | 4.6887 | 0.068708 | 68.2412 | 0.1066%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | Tier-2---1 | 241 | 129 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 601.8895 | 0 | 0 | 601.8895 | 0 | 574.1617 | 8.4137 | 68.2412 | 574.1617 | 8.4137 | 68.2412 | 604.8399 | 8.8633 | 68.2412 | 13.76%
2026 | 235 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 9.5833 | 0 | 0 | 9.5833 | 0 | 9.1418 | 0.065223 | 140.1629 | 9.1418 | 0.065223 | 140.1629 | 9.6302 | 0.068708 | 140.1629 | 0.04094%
2026 | 235 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 10.678 | 0 | 0 | 10.678 | 0 | 10.1861 | 0.065223 | 156.1746 | 10.1861 | 0.065223 | 156.1746 | 10.7304 | 0.068708 | 156.1746 | 0.084%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 1 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 12.7206 | 0 | 0 | 12.7206 | 0 | 12.1346 | 0.065223 | 186.0485 | 12.1346 | 0.065223 | 186.0485 | 12.7829 | 0.068708 | 186.0485 | 0.05372%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 9 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 114.4852 | 0 | 0 | 114.4852 | 0 | 109.2111 | 0.587 | 186.0485 | 109.2111 | 0.587 | 186.0485 | 115.0464 | 0.61837 | 186.0485 | 0.4835%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | Tier-2---1 | 531 | 260 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 3307.3492 | 0 | 0 | 3307.3492 | 0 | 3154.9865 | 16.9579 | 186.0485 | 3154.9865 | 16.9579 | 186.0485 | 3323.5617 | 17.864 | 186.0485 | 13.97%
2026 | 235 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 2 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 39.5941 | 0 | 0 | 39.5941 | 0 | 37.7701 | 0.13045 | 289.5475 | 37.7701 | 0.13045 | 289.5475 | 39.7882 | 0.13742 | 289.5475 | 0.3456%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | Tier-3---1 | 252 | 162 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 1788.9445 | 0 | 0 | 1788.9445 | 0 | 1706.5315 | 10.5661 | 161.5107 | 1706.5315 | 10.5661 | 161.5107 | 1797.7139 | 11.1306 | 161.5107 | 18.41%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | Tier-3---3 | 137 | 91 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 529.008 | 0 | 0 | 529.008 | 0 | 504.6377 | 5.9353 | 85.0238 | 504.6377 | 5.9353 | 85.0238 | 531.6012 | 6.2524 | 85.0238 | 18.74%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | Tier-3---3 | 81 | 69 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 550.6889 | 0 | 0 | 550.6889 | 0 | 525.3198 | 4.5004 | 116.7284 | 525.3198 | 4.5004 | 116.7284 | 553.3884 | 4.7408 | 116.7284 | 24.36%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | Tier-3---1 | 171 | 44 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 390.2123 | 0 | 0 | 390.2123 | 0 | 372.236 | 2.8698 | 129.7083 | 372.236 | 2.8698 | 129.7083 | 392.1251 | 3.0231 | 129.7083 | 7.318%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | Tier-3---1 | 498 | 127 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1543.8782 | 0 | 0 | 1543.8782 | 0 | 1472.7549 | 8.2833 | 177.7987 | 1472.7549 | 8.2833 | 177.7987 | 1551.4462 | 8.7259 | 177.7987 | 7.275%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 10.678 | 0 | 0 | 10.678 | 0 | 10.1861 | 0.065223 | 156.1746 | 10.1861 | 0.065223 | 156.1746 | 10.7304 | 0.068708 | 156.1746 | 0.084%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 150 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 1601.7038 | 0 | 0 | 1601.7038 | 0 | 1527.9166 | 9.7834 | 156.1746 | 1527.9166 | 9.7834 | 156.1746 | 1609.5553 | 10.3061 | 156.1746 | 12.6%
2026 | 236 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 41 | 5 | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 74.3356 | 0 | 0 | 74.3356 | 0 | 70.9111 | 0.32611 | 217.4435 | 70.9111 | 0.32611 | 217.4435 | 74.7 | 0.34354 | 217.4435 | 3.52%
2026 | 236 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 4 | 2 | 251.0066 | 99.97% | 0% | 0.03372% | 36.3837 | 0 | 0 | 36.3837 | 0 | 34.7076 | 0.13045 | 266.0701 | 34.7076 | 0.13045 | 266.0701 | 36.562 | 0.13742 | 266.0701 | 14.5%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | Tier-3---1 | 223 | 75 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 2737.1877 | 0 | 0 | 2737.1877 | 0 | 2611.0911 | 4.8917 | 533.7805 | 2611.0911 | 4.8917 | 533.7805 | 2750.6053 | 5.1531 | 533.7805 | 9.689%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 3 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 43.4687 | 0 | 0 | 43.4687 | 0 | 41.4661 | 0.19567 | 211.9211 | 41.4661 | 0.19567 | 211.9211 | 43.6817 | 0.20612 | 211.9211 | 0.1605%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 2 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 28.9791 | 0 | 0 | 28.9791 | 0 | 27.6441 | 0.13045 | 211.9211 | 27.6441 | 0.13045 | 211.9211 | 29.1212 | 0.13742 | 211.9211 | 0.107%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | Tier-2---1 | 536 | 154 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 2231.3907 | 0 | 0 | 2231.3907 | 0 | 2128.5951 | 10.0443 | 211.9211 | 2128.5951 | 10.0443 | 211.9211 | 2242.3289 | 10.581 | 211.9211 | 8.24%
2026 | 237 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 4 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 42.7121 | 0 | 0 | 42.7121 | 0 | 40.7444 | 0.26089 | 156.1746 | 40.7444 | 0.26089 | 156.1746 | 42.9215 | 0.27483 | 156.1746 | 0.336%
2026 | 237 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 1 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 8.4938 | 0 | 0 | 8.4938 | 0 | 8.1025 | 0.065223 | 124.2282 | 8.1025 | 0.065223 | 124.2282 | 8.5354 | 0.068708 | 124.2282 | 0.08076%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 1 | 663.2151 | 70.89% | 28.72% | 0.399% | 1.2065 | 0 | 0 | 1.2065 | 0 | 1.1509 | 0.065223 | 17.6461 | 1.1509 | 0.065223 | 17.6461 | 1.2124 | 0.068708 | 17.6461 | 0.1819%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 7 | 663.2151 | 70.89% | 28.72% | 0.399% | 8.4455 | 0 | 0 | 8.4455 | 0 | 8.0565 | 0.45656 | 17.6461 | 8.0565 | 0.45656 | 17.6461 | 8.4869 | 0.48095 | 17.6461 | 1.273%
2026 | 237 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 2 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 25.2212 | 0 | 0 | 25.2212 | 0 | 24.0593 | 0.13045 | 184.4401 | 24.0593 | 0.13045 | 184.4401 | 25.3448 | 0.13742 | 184.4401 | 0.4823%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | Tier-3---1 | 651 | 33 | 65515.492 | 98.93% | 1.038% | 0.03019% | 952.8201 | 0 | 0 | 952.8201 | 0 | 908.9256 | 2.1523 | 422.2954 | 908.9256 | 2.1523 | 422.2954 | 957.4907 | 2.2673 | 422.2954 | 1.454%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | Tier-3---4 | 127 | 52 | 860.3234 | 98.08% | 1.495% | 0.4234% | 100.1948 | 0 | 0 | 100.1948 | 0 | 95.579 | 3.3916 | 28.1813 | 95.579 | 3.3916 | 28.1813 | 100.6859 | 3.5728 | 28.1813 | 11.65%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | Tier-3---3 | 134 | 17 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 39.621 | 0 | 0 | 39.621 | 0 | 37.7958 | 1.1088 | 34.0876 | 37.7958 | 1.1088 | 34.0876 | 39.8153 | 1.168 | 34.0876 | 3.549%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | Tier-3---1 | 305 | 11 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 64.41 | 0 | 0 | 64.41 | 0 | 61.4427 | 0.71745 | 85.6406 | 61.4427 | 0.71745 | 85.6406 | 64.7257 | 0.75578 | 85.6406 | 1.027%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 29 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 61.7679 | 0 | 0 | 61.7679 | 0 | 58.9224 | 1.8915 | 31.1519 | 58.9224 | 1.8915 | 31.1519 | 62.0707 | 1.9925 | 31.1519 | 1.824%
2026 | 246 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 1 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 1.6078 | 0 | 0 | 1.6078 | 0 | 1.5337 | 0.065223 | 23.5148 | 1.5337 | 0.065223 | 23.5148 | 1.6156 | 0.068708 | 23.5148 | 0.1182%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 21 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 33.763 | 0 | 0 | 33.763 | 0 | 32.2076 | 1.3697 | 23.5148 | 32.2076 | 1.3697 | 23.5148 | 33.9285 | 1.4429 | 23.5148 | 2.482%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | Tier-2---12 | 9 | 9 | 105.2026 | 98.18% | 1.532% | 0.2854% | 29.9544 | 0 | 0 | 29.9544 | 0 | 28.5744 | 0.587 | 48.6785 | 28.5744 | 0.587 | 48.6785 | 30.1012 | 0.61837 | 48.6785 | 28.47%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 68 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 944.9358 | 0 | 0 | 944.9358 | 0 | 901.4046 | 4.4351 | 203.2417 | 901.4046 | 4.4351 | 203.2417 | 949.5678 | 4.6721 | 203.2417 | 17.83%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 1 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 4.0371 | 0 | 0 | 4.0371 | 0 | 3.8511 | 0.065223 | 59.0451 | 3.8511 | 0.065223 | 59.0451 | 4.0568 | 0.068708 | 59.0451 | 0.2005%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | Tier-3---3 | 127 | 97 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 391.5941 | 0 | 0 | 391.5941 | 0 | 373.5542 | 6.3266 | 59.0451 | 373.5542 | 6.3266 | 59.0451 | 393.5137 | 6.6646 | 59.0451 | 19.45%
2026 | 283 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 140 | 1 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 2.6829 | 0 | 0 | 2.6829 | 0 | 2.5593 | 0.065223 | 39.24 | 2.5593 | 0.065223 | 39.24 | 2.6961 | 0.068708 | 39.24 | 0.1844%
2026 | 283 | 283-80F | Tier-3 | Tier-3---19 | Tier-3---19 | 2 | 2 | 22.6843 | 50.28% | 49.56% | 0.1579% | 3.3078 | 0 | 0 | 3.3078 | 0 | 3.1554 | 0.13045 | 24.1897 | 3.1554 | 0.13045 | 24.1897 | 3.324 | 0.13742 | 24.1897 | 14.58%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 4 | 754.1323 | 92.41% | 6.882% | 0.7076% | 3.2336 | 0 | 0 | 3.2336 | 0 | 3.0846 | 0.26089 | 11.8235 | 3.0846 | 0.26089 | 11.8235 | 3.2495 | 0.27483 | 11.8235 | 0.4288%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 46 | 4762.848 | 95.55% | 4.384% | 0.07015% | 556.9387 | 0 | 0 | 556.9387 | 0 | 531.2817 | 3.0002 | 177.0798 | 531.2817 | 3.0002 | 177.0798 | 559.6688 | 3.1605 | 177.0798 | 11.69%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 200 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 353.0681 | 0 | 0 | 353.0681 | 0 | 336.803 | 13.0445 | 25.8195 | 336.803 | 13.0445 | 25.8195 | 354.7988 | 13.7415 | 25.8195 | 9.802%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | Tier-2---1 | 826 | 641 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 3063.6377 | 0 | 0 | 3063.6377 | 0 | 2922.5022 | 41.8077 | 69.9035 | 2922.5022 | 41.8077 | 69.9035 | 3078.6555 | 44.0415 | 69.9035 | 22.09%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | Tier-2---1 | 807 | 314 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 609.6478 | 0 | 0 | 609.6478 | 0 | 581.5626 | 20.4799 | 28.3968 | 581.5626 | 20.4799 | 28.3968 | 612.6363 | 21.5742 | 28.3968 | 10.94%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | Tier-3---1 | 361 | 120 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 1294.1521 | 0 | 0 | 1294.1521 | 0 | 1234.5332 | 7.8267 | 157.7333 | 1234.5332 | 7.8267 | 157.7333 | 1300.496 | 8.2449 | 157.7333 | 9.571%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 1 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 6.7618 | 0 | 0 | 6.7618 | 0 | 6.4503 | 0.065223 | 98.8971 | 6.4503 | 0.065223 | 98.8971 | 6.795 | 0.068708 | 98.8971 | 0.06037%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | Tier-2---1 | 475 | 355 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 2400.4481 | 0 | 0 | 2400.4481 | 0 | 2289.8644 | 23.154 | 98.8971 | 2289.8644 | 23.154 | 98.8971 | 2412.215 | 24.3912 | 98.8971 | 21.43%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 1 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 19.8502 | 0 | 0 | 19.8502 | 0 | 18.9357 | 0.065223 | 290.3242 | 18.9357 | 0.065223 | 290.3242 | 19.9475 | 0.068708 | 290.3242 | 0.08441%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 38 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 754.3059 | 0 | 0 | 754.3059 | 0 | 719.5566 | 2.4785 | 290.3242 | 719.5566 | 2.4785 | 290.3242 | 758.0035 | 2.6109 | 290.3242 | 3.207%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 1 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 24.0427 | 0 | 0 | 24.0427 | 0 | 22.9351 | 0.065223 | 351.6439 | 22.9351 | 0.065223 | 351.6439 | 24.1606 | 0.068708 | 351.6439 | 0.2629%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | Tier-3---1 | 110 | 59 | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 1418.5207 | 0 | 0 | 1418.5207 | 0 | 1353.1723 | 3.8481 | 351.6439 | 1353.1723 | 3.8481 | 351.6439 | 1425.4742 | 4.0537 | 351.6439 | 15.51%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 1 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 27.4 | 0 | 0 | 27.4 | 0 | 26.1378 | 0.065223 | 400.7472 | 26.1378 | 0.065223 | 400.7472 | 27.5343 | 0.068708 | 400.7472 | 0.1877%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 84 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 2301.6027 | 0 | 0 | 2301.6027 | 0 | 2195.5726 | 5.4787 | 400.7472 | 2195.5726 | 5.4787 | 400.7472 | 2312.8851 | 5.7714 | 400.7472 | 15.76%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 159 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 2375.519 | 0 | 0 | 2375.519 | 0 | 2266.0837 | 10.3704 | 218.5148 | 2266.0837 | 10.3704 | 218.5148 | 2387.1637 | 10.9245 | 218.5148 | 12.76%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | Tier-2---1 | 204 | 120 | 9221.8022 | 97.49% | 2.457% | 0.05523% | 1533.6114 | 0 | 0 | 1533.6114 | 0 | 1462.961 | 7.8267 | 186.919 | 1462.961 | 7.8267 | 186.919 | 1541.1291 | 8.2449 | 186.919 | 16.63%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | Tier-2---1 | 28 | 25 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 457.3248 | 0 | 0 | 457.3248 | 0 | 436.2568 | 1.6306 | 267.5495 | 436.2568 | 1.6306 | 267.5495 | 459.5666 | 1.7177 | 267.5495 | 22.97%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | Tier-2---1 | 82 | 26 | 4555.6189 | 94.3% | 5.656% | 0.04182% | 395.0269 | 0 | 0 | 395.0269 | 0 | 376.8288 | 1.6958 | 222.2147 | 376.8288 | 1.6958 | 222.2147 | 396.9633 | 1.7864 | 222.2147 | 8.671%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | Tier-2---5 | 11 | 11 | 465.1006 | 62.84% | 37.09% | 0.07221% | 84.7577 | 0 | 0 | 84.7577 | 0 | 80.8531 | 0.71745 | 112.6954 | 80.8531 | 0.71745 | 112.6954 | 85.1732 | 0.75578 | 112.6954 | 18.22%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 2 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 43.1238 | 0 | 0 | 43.1238 | 0 | 41.1372 | 0.13045 | 315.3599 | 41.1372 | 0.13045 | 315.3599 | 43.3352 | 0.13742 | 315.3599 | 0.3186%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | Tier-2---1 | 181 | 72 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 1552.4571 | 0 | 0 | 1552.4571 | 0 | 1480.9386 | 4.696 | 315.3599 | 1480.9386 | 4.696 | 315.3599 | 1560.0672 | 4.9469 | 315.3599 | 11.47%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 13 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 159.4165 | 0 | 0 | 159.4165 | 0 | 152.0725 | 0.84789 | 179.3533 | 152.0725 | 0.84789 | 179.3533 | 160.198 | 0.8932 | 179.3533 | 0.7773%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | Tier-2---2 | 89 | 10 | 3653.654 | 88.54% | 11.39% | 0.07412% | 105.4033 | 0 | 0 | 105.4033 | 0 | 100.5476 | 0.65223 | 154.1607 | 100.5476 | 0.65223 | 154.1607 | 105.92 | 0.68708 | 154.1607 | 2.885%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 118 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 1118.6816 | 0 | 0 | 1118.6816 | 0 | 1067.1463 | 7.6963 | 138.6577 | 1067.1463 | 7.6963 | 138.6577 | 1124.1654 | 8.1075 | 138.6577 | 14.91%
2026 | 355 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 1 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 10.5024 | 0 | 0 | 10.5024 | 0 | 10.0186 | 0.065223 | 153.6057 | 10.0186 | 0.065223 | 153.6057 | 10.5539 | 0.068708 | 153.6057 | 0.1719%
2026 | 355 | 355-65R | Tier-2 | Tier-2---21 | Tier-2---24 | 1 | 1 | 0.06699 | 46.11% | 0% | 53.89% | 0.008957 | 0 | 0 | 0.008957 | 0 | 0.0085444 | 0.065223 | 0.131 | 0.0085444 | 0.065223 | 0.131 | 0.0090009 | 0.068708 | 0.131 | 13.37%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | Tier-2---2 | 58 | 35 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 237.6381 | 0 | 0 | 237.6381 | 0 | 226.6906 | 2.2828 | 99.3041 | 226.6906 | 2.2828 | 99.3041 | 238.803 | 2.4048 | 99.3041 | 13.99%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 148 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 1585.6295 | 0 | 0 | 1585.6295 | 0 | 1512.5828 | 9.6529 | 156.6965 | 1512.5828 | 9.6529 | 156.6965 | 1593.4022 | 10.1687 | 156.6965 | 14.05%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 94 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 673.4701 | 0 | 0 | 673.4701 | 0 | 642.4447 | 6.1309 | 104.7876 | 642.4447 | 6.1309 | 104.7876 | 676.7714 | 6.4585 | 104.7876 | 12.39%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 1 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 6.1682 | 0 | 0 | 6.1682 | 0 | 5.8841 | 0.065223 | 90.2153 | 5.8841 | 0.065223 | 90.2153 | 6.1985 | 0.068708 | 90.2153 | 0.03852%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 1 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 6.1682 | 0 | 0 | 6.1682 | 0 | 5.8841 | 0.065223 | 90.2153 | 5.8841 | 0.065223 | 90.2153 | 6.1985 | 0.068708 | 90.2153 | 0.03852%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 71 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 437.9448 | 0 | 0 | 437.9448 | 0 | 417.7695 | 4.6308 | 90.2153 | 417.7695 | 4.6308 | 90.2153 | 440.0915 | 4.8782 | 90.2153 | 2.735%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | Tier-3---1 | 730 | 400 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 1409.1944 | 0 | 0 | 1409.1944 | 0 | 1344.2757 | 26.089 | 51.5265 | 1344.2757 | 26.089 | 51.5265 | 1416.1022 | 27.483 | 51.5265 | 15.16%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | Tier-2---3 | 40 | 22 | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 197.6916 | 0 | 0 | 197.6916 | 0 | 188.5843 | 1.4349 | 131.4271 | 188.5843 | 1.4349 | 131.4271 | 198.6606 | 1.5116 | 131.4271 | 15.8%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 17 | 9 | 878.9304 | 95.49% | 4.482% | 0.03213% | 128.8496 | 0 | 0 | 128.8496 | 0 | 122.9138 | 0.587 | 209.392 | 122.9138 | 0.587 | 209.392 | 129.4812 | 0.61837 | 209.392 | 14.66%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 138 | 16869.708 | 98.79% | 1.184% | 0.02933% | 2461.0062 | 0 | 0 | 2461.0062 | 0 | 2347.6327 | 9.0007 | 260.8273 | 2347.6327 | 9.0007 | 260.8273 | 2473.07 | 9.4816 | 260.8273 | 14.59%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 173 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 2384.0803 | 0 | 0 | 2384.0803 | 0 | 2274.2506 | 11.2835 | 201.5553 | 2274.2506 | 11.2835 | 201.5553 | 2395.7669 | 11.8864 | 201.5553 | 13.47%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 127 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 973.4943 | 0 | 0 | 973.4943 | 0 | 928.6474 | 8.2833 | 112.1112 | 928.6474 | 8.2833 | 112.1112 | 978.2663 | 8.7259 | 112.1112 | 9.331%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 170 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 2084.3112 | 0 | 0 | 2084.3112 | 0 | 1988.2913 | 11.0878 | 179.3218 | 1988.2913 | 11.0878 | 179.3218 | 2094.5284 | 11.6803 | 179.3218 | 17.73%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 78 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 819.1859 | 0 | 0 | 819.1859 | 0 | 781.4477 | 5.0874 | 153.6057 | 781.4477 | 5.0874 | 153.6057 | 823.2015 | 5.3592 | 153.6057 | 13.41%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 21 | 5 | 599.5834 | 97.21% | 2.746% | 0.04768% | 40.2431 | 0 | 0 | 40.2431 | 0 | 38.3892 | 0.32611 | 117.7176 | 38.3892 | 0.32611 | 117.7176 | 40.4404 | 0.34354 | 117.7176 | 6.712%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 21 | 4 | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.9827 | 0 | 0 | 8.9827 | 0 | 8.5689 | 0.26089 | 32.8447 | 8.5689 | 0.26089 | 32.8447 | 9.0267 | 0.27483 | 32.8447 | 1.043%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | Tier-3---2 | 140 | 9 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 24.1464 | 0 | 0 | 24.1464 | 0 | 23.034 | 0.587 | 39.24 | 23.034 | 0.587 | 39.24 | 24.2648 | 0.61837 | 39.24 | 1.659%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 2 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 2.1449 | 0 | 0 | 2.1449 | 0 | 2.0461 | 0.13045 | 15.6854 | 2.0461 | 0.13045 | 15.6854 | 2.1554 | 0.13742 | 15.6854 | 0.06838%
2026 | 401 | 401-684R | Tier-2 | Tier-2---21 | Tier-2---20 | 2 | 1 | 1.5961 | 62.42% | 35.57% | 2.007% | 0.14447 | 0 | 0 | 0.14447 | 0 | 0.13782 | 0.065223 | 2.113 | 0.13782 | 0.065223 | 2.113 | 0.14518 | 0.068708 | 2.113 | 9.051%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 1 | 6370.0414 | 98.47% | 1.262% | 0.272% | 2.125 | 0 | 0 | 2.125 | 0 | 2.0271 | 0.065223 | 31.0793 | 2.0271 | 0.065223 | 31.0793 | 2.1354 | 0.068708 | 31.0793 | 0.03336%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 15 | 6370.0414 | 98.47% | 1.262% | 0.272% | 31.8745 | 0 | 0 | 31.8745 | 0 | 30.4061 | 0.97834 | 31.0793 | 30.4061 | 0.97834 | 31.0793 | 32.0308 | 1.0306 | 31.0793 | 0.5004%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | Tier-3---5 | 201 | 196 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 498.5904 | 0 | 0 | 498.5904 | 0 | 475.6214 | 12.7836 | 37.2055 | 475.6214 | 12.7836 | 37.2055 | 501.0345 | 13.4667 | 37.2055 | 27.17%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 40 | 852.9261 | 84.92% | 14.72% | 0.3553% | 57.9475 | 0 | 0 | 57.9475 | 0 | 55.278 | 2.6089 | 21.1882 | 55.278 | 2.6089 | 21.1882 | 58.2316 | 2.7483 | 21.1882 | 6.794%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 68 | 11572.221 | 88.48% | 11.4% | 0.1243% | 264.622 | 0 | 0 | 264.622 | 0 | 252.4314 | 4.4351 | 56.9163 | 252.4314 | 4.4351 | 56.9163 | 265.9192 | 4.6721 | 56.9163 | 2.287%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | Tier-2---5 | 122 | 84 | 333.8465 | 96.62% | 2.31% | 1.072% | 64.405 | 0 | 0 | 64.405 | 0 | 61.438 | 5.4787 | 11.214 | 61.438 | 5.4787 | 11.214 | 64.7207 | 5.7714 | 11.214 | 19.29%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 344 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 825.3778 | 0 | 0 | 825.3778 | 0 | 787.3544 | 22.4366 | 35.0925 | 787.3544 | 22.4366 | 35.0925 | 829.4238 | 23.6354 | 35.0925 | 24.18%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | Tier-2---5 | 465 | 363 | 571.2373 | 70.71% | 27.93% | 1.361% | 91.4403 | 0 | 0 | 91.4403 | 0 | 87.2278 | 23.6758 | 3.6843 | 87.2278 | 23.6758 | 3.6843 | 91.8885 | 24.9408 | 3.6843 | 16.01%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 17 | 3 | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.871 | 0 | 0 | 5.871 | 0 | 5.6006 | 0.19567 | 28.6228 | 5.6006 | 0.19567 | 28.6228 | 5.8998 | 0.20612 | 28.6228 | 4.999%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 17 | 12 | 117.4434 | 97.68% | 1.947% | 0.3705% | 23.4841 | 0 | 0 | 23.4841 | 0 | 22.4022 | 0.78267 | 28.6228 | 22.4022 | 0.78267 | 28.6228 | 23.5992 | 0.82449 | 28.6228 | 20%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 42 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 330.589 | 0 | 0 | 330.589 | 0 | 315.3595 | 2.7393 | 115.122 | 315.3595 | 2.7393 | 115.122 | 332.2095 | 2.8857 | 115.122 | 3.432%
2026 | 445 | 445-1315 | Tier-2 | Tier-2---19 | Tier-2---11 | 4 | 1 | 26.2494 | 99.59% | 0% | 0.4079% | 1.8953 | 0 | 0 | 1.8953 | 0 | 1.808 | 0.065223 | 27.7205 | 1.808 | 0.065223 | 27.7205 | 1.9046 | 0.068708 | 27.7205 | 7.22%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 36 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 153.1223 | 0 | 0 | 153.1223 | 0 | 146.0683 | 2.348 | 62.2093 | 146.0683 | 2.348 | 62.2093 | 153.8729 | 2.4735 | 62.2093 | 9.549%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 13 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 49.3512 | 0 | 0 | 49.3512 | 0 | 47.0776 | 0.84789 | 55.5231 | 47.0776 | 0.84789 | 55.5231 | 49.5931 | 0.8932 | 55.5231 | 1.342%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 21 | 520.639 | 76.18% | 22.78% | 1.038% | 11.9583 | 0 | 0 | 11.9583 | 0 | 11.4074 | 1.3697 | 8.3285 | 11.4074 | 1.3697 | 8.3285 | 12.0169 | 1.4429 | 8.3285 | 2.297%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 170 | 10 | 630.7627 | 79.12% | 20.09% | 0.7869% | 8.5136 | 0 | 0 | 8.5136 | 0 | 8.1214 | 0.65223 | 12.4518 | 8.1214 | 0.65223 | 12.4518 | 8.5553 | 0.68708 | 12.4518 | 1.35%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 1 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 3.1707 | 0 | 0 | 3.1707 | 0 | 3.0247 | 0.065223 | 46.3747 | 3.0247 | 0.065223 | 46.3747 | 3.1863 | 0.068708 | 46.3747 | 0.04711%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | Tier-3---5 | 26 | 26 | 625.3129 | 96.7% | 3.156% | 0.1473% | 175.3503 | 0 | 0 | 175.3503 | 0 | 167.2723 | 1.6958 | 98.6399 | 167.2723 | 1.6958 | 98.6399 | 176.2099 | 1.7864 | 98.6399 | 28.04%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 56 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 505.9027 | 0 | 0 | 505.9027 | 0 | 482.5968 | 3.6525 | 132.1291 | 482.5968 | 3.6525 | 132.1291 | 508.3826 | 3.8476 | 132.1291 | 3.022%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | Tier-2---2 | 155 | 90 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 243.9572 | 0 | 0 | 243.9572 | 0 | 232.7186 | 5.87 | 39.6452 | 232.7186 | 5.87 | 39.6452 | 245.1531 | 6.1837 | 39.6452 | 16.5%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 16 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 51.3544 | 0 | 0 | 51.3544 | 0 | 48.9886 | 1.0436 | 46.9437 | 48.9886 | 1.0436 | 46.9437 | 51.6061 | 1.0993 | 46.9437 | 3.145%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | Tier-3---1 | 249 | 13 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 99.0347 | 0 | 0 | 99.0347 | 0 | 94.4723 | 0.84789 | 111.42 | 94.4723 | 0.84789 | 111.42 | 99.5201 | 0.8932 | 111.42 | 1.464%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 1 | 748.333 | 77.34% | 21.7% | 0.962% | 0.41136 | 0 | 0 | 0.41136 | 0 | 0.39241 | 0.065223 | 6.0165 | 0.39241 | 0.065223 | 6.0165 | 0.41338 | 0.068708 | 6.0165 | 0.05497%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 58 | 748.333 | 77.34% | 21.7% | 0.962% | 23.8589 | 0 | 0 | 23.8589 | 0 | 22.7597 | 3.7829 | 6.0165 | 22.7597 | 3.7829 | 6.0165 | 23.9758 | 3.985 | 6.0165 | 3.188%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | Tier-3---2 | 276 | 133 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 281.0603 | 0 | 0 | 281.0603 | 0 | 268.1124 | 8.6746 | 30.9077 | 268.1124 | 8.6746 | 30.9077 | 282.438 | 9.1381 | 30.9077 | 13.48%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | Tier-2---4 | 113 | 5 | 258.296 | 74.72% | 24.53% | 0.7505% | 2.4766 | 0 | 0 | 2.4766 | 0 | 2.3625 | 0.32611 | 7.2446 | 2.3625 | 0.32611 | 7.2446 | 2.4888 | 0.34354 | 7.2446 | 0.9588%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 119 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 1202.342 | 0 | 0 | 1202.342 | 0 | 1146.9526 | 7.7615 | 147.7748 | 1146.9526 | 7.7615 | 147.7748 | 1208.2359 | 8.1762 | 147.7748 | 10.59%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 88 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 631.5734 | 0 | 0 | 631.5734 | 0 | 602.4781 | 5.7396 | 104.9689 | 602.4781 | 5.7396 | 104.9689 | 634.6693 | 6.0463 | 104.9689 | 7.45%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 23 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 188.0941 | 0 | 0 | 188.0941 | 0 | 179.429 | 1.5001 | 119.6098 | 179.429 | 1.5001 | 119.6098 | 189.0161 | 1.5803 | 119.6098 | 2.159%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 125 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 561.9783 | 0 | 0 | 561.9783 | 0 | 536.0891 | 8.1528 | 65.755 | 536.0891 | 8.1528 | 65.755 | 564.7331 | 8.5884 | 65.755 | 10%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 61 | 305.199 | 11.7% | 87.21% | 1.095% | 3.1733 | 0 | 0 | 3.1733 | 0 | 3.0271 | 3.9786 | 0.76086 | 3.0271 | 3.9786 | 0.76086 | 3.1889 | 4.1912 | 0.76086 | 1.04%
2026 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 6 | 305.5692 | 37.2% | 61.32% | 1.484% | 0.76361 | 0 | 0 | 0.76361 | 0 | 0.72844 | 0.39134 | 1.8614 | 0.72844 | 0.39134 | 1.8614 | 0.76736 | 0.41225 | 1.8614 | 0.2499%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | Tier-3---2 | 231 | 173 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 1184.939 | 0 | 0 | 1184.939 | 0 | 1130.3513 | 11.2835 | 100.1773 | 1130.3513 | 11.2835 | 100.1773 | 1190.7475 | 11.8864 | 100.1773 | 21.67%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | Tier-3---2 | 489 | 289 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 1935.2668 | 0 | 0 | 1935.2668 | 0 | 1846.1131 | 18.8493 | 97.9405 | 1846.1131 | 18.8493 | 97.9405 | 1944.7535 | 19.8565 | 97.9405 | 17.1%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | Tier-3---1 | 283 | 223 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 3101.4348 | 0 | 0 | 3101.4348 | 0 | 2958.5581 | 14.5446 | 203.4123 | 2958.5581 | 14.5446 | 203.4123 | 3116.6379 | 15.3218 | 203.4123 | 22.62%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 1 | 8801.877 | 98.2% | 1.718% | 0.0819% | 8.8573 | 0 | 0 | 8.8573 | 0 | 8.4493 | 0.065223 | 129.5449 | 8.4493 | 0.065223 | 129.5449 | 8.9007 | 0.068708 | 129.5449 | 0.1006%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | Tier-3---1 | 283 | 203 | 8801.877 | 98.2% | 1.718% | 0.0819% | 1798.0302 | 0 | 0 | 1798.0302 | 0 | 1715.1986 | 13.2402 | 129.5449 | 1715.1986 | 13.2402 | 129.5449 | 1806.844 | 13.9476 | 129.5449 | 20.43%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | Tier-3---1 | 842 | 629 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 8662.314 | 0 | 0 | 8662.314 | 0 | 8263.2591 | 41.025 | 201.42 | 8263.2591 | 41.025 | 201.42 | 8704.7763 | 43.217 | 201.42 | 21.45%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 90 | 6 | 481.3309 | 94.25% | 5.298% | 0.4514% | 8.7707 | 0 | 0 | 8.7707 | 0 | 8.3666 | 0.39134 | 21.3797 | 8.3666 | 0.39134 | 21.3797 | 8.8137 | 0.41225 | 21.3797 | 1.822%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 3 | 4323.2442 | 99.81% | 0% | 0.1903% | 10.1736 | 0 | 0 | 10.1736 | 0 | 9.7049 | 0.19567 | 49.5991 | 9.7049 | 0.19567 | 49.5991 | 10.2235 | 0.20612 | 49.5991 | 0.2353%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 75 | 8606.9717 | 99.86% | 0% | 0.1411% | 335.6148 | 0 | 0 | 335.6148 | 0 | 320.1537 | 4.8917 | 65.4484 | 320.1537 | 4.8917 | 65.4484 | 337.26 | 5.1531 | 65.4484 | 3.899%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | Tier-3---2 | 148 | 23 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 409.0176 | 0 | 0 | 409.0176 | 0 | 390.175 | 1.5001 | 260.096 | 390.175 | 1.5001 | 260.096 | 411.0226 | 1.5803 | 260.096 | 4.494%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | Tier-3---2 | 388 | 66 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1324.4176 | 0 | 0 | 1324.4176 | 0 | 1263.4044 | 4.3047 | 293.4948 | 1263.4044 | 4.3047 | 293.4948 | 1330.9099 | 4.5347 | 293.4948 | 4.893%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | Tier-3---6 | 51 | 4 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 62.2701 | 0 | 0 | 62.2701 | 0 | 59.4014 | 0.26089 | 227.6873 | 59.4014 | 0.26089 | 227.6873 | 62.5753 | 0.27483 | 227.6873 | 2.271%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | Tier-2---1 | 303 | 28 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 415.4486 | 0 | 0 | 415.4486 | 0 | 396.3098 | 1.8262 | 217.0095 | 396.3098 | 1.8262 | 217.0095 | 417.4851 | 1.9238 | 217.0095 | 2.635%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | Tier-2---1 | 166 | 109 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 2213.2709 | 0 | 0 | 2213.2709 | 0 | 2111.3101 | 7.1093 | 296.9802 | 2111.3101 | 7.1093 | 296.9802 | 2224.1203 | 7.4891 | 296.9802 | 18.81%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | Tier-2---1 | 471 | 101 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 333.4341 | 0 | 0 | 333.4341 | 0 | 318.0735 | 6.5875 | 48.2845 | 318.0735 | 6.5875 | 48.2845 | 335.0686 | 6.9395 | 48.2845 | 5.985%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | Tier-2---3 | 150 | 59 | 1466.2762 | 91.81% | 7.905% | 0.289% | 153.5484 | 0 | 0 | 153.5484 | 0 | 146.4748 | 3.8481 | 38.0639 | 146.4748 | 3.8481 | 38.0639 | 154.3011 | 4.0537 | 38.0639 | 10.47%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | Tier-2---1 | 123 | 89 | 7960.2903 | 98.35% | 1.621% | 0.03193% | 1642.7621 | 0 | 0 | 1642.7621 | 0 | 1567.0834 | 5.8048 | 269.9629 | 1567.0834 | 5.8048 | 269.9629 | 1650.8148 | 6.115 | 269.9629 | 20.64%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | Tier-2---1 | 547 | 365 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 7895.3967 | 0 | 0 | 7895.3967 | 0 | 7531.6721 | 23.8062 | 316.3738 | 7531.6721 | 23.8062 | 316.3738 | 7934.0996 | 25.0782 | 316.3738 | 19.14%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | Tier-3---1 | 363 | 159 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 2839.9503 | 0 | 0 | 2839.9503 | 0 | 2709.1196 | 10.3704 | 261.236 | 2709.1196 | 10.3704 | 261.236 | 2853.8716 | 10.9245 | 261.236 | 12.59%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 3 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 94.3086 | 0 | 0 | 94.3086 | 0 | 89.964 | 0.19567 | 459.7795 | 89.964 | 0.19567 | 459.7795 | 94.7709 | 0.20612 | 459.7795 | 0.1707%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | Tier-3---1 | 506 | 364 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 11442.7809 | 0 | 0 | 11442.7809 | 0 | 10915.6356 | 23.741 | 459.7795 | 10915.6356 | 23.741 | 459.7795 | 11498.873 | 25.0095 | 459.7795 | 20.71%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 4 | 5703.0403 | 99.97% | 0% | 0.03309% | 106.6667 | 0 | 0 | 106.6667 | 0 | 101.7528 | 0.26089 | 390.0214 | 101.7528 | 0.26089 | 390.0214 | 107.1896 | 0.27483 | 390.0214 | 1.87%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | Tier-2---7 | 62 | 1 | 5703.0403 | 99.97% | 0% | 0.03309% | 26.6667 | 0 | 0 | 26.6667 | 0 | 25.4382 | 0.065223 | 390.0214 | 25.4382 | 0.065223 | 390.0214 | 26.7974 | 0.068708 | 390.0214 | 0.4676%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | Tier-2---1 | 309 | 93 | 32313.161 | 99.26% | 0.708% | 0.02831% | 2799.5779 | 0 | 0 | 2799.5779 | 0 | 2670.6071 | 6.0657 | 440.28 | 2670.6071 | 6.0657 | 440.28 | 2813.3013 | 6.3898 | 440.28 | 8.664%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | Tier-3---1 | 92 | 4 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 162.87 | 0 | 0 | 162.87 | 0 | 155.3669 | 0.26089 | 595.5255 | 155.3669 | 0.26089 | 595.5255 | 163.6683 | 0.27483 | 595.5255 | 1.257%
2026 | 970 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 10.678 | 0 | 0 | 10.678 | 0 | 10.1861 | 0.065223 | 156.1746 | 10.1861 | 0.065223 | 156.1746 | 10.7304 | 0.068708 | 156.1746 | 0.084%
2026 | 970 | CB 970 | Tier-2 | Tier-2---14 | Tier-2---11 | 4 | 1 | 251.0066 | 99.97% | 0% | 0.03372% | 18.1918 | 0 | 0 | 18.1918 | 0 | 17.3538 | 0.065223 | 266.0701 | 17.3538 | 0.065223 | 266.0701 | 18.281 | 0.068708 | 266.0701 | 7.248%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | Tier-3---1 | 344 | 192 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 2428.7644 | 0 | 0 | 2428.7644 | 0 | 2316.8762 | 12.5227 | 185.0136 | 2316.8762 | 12.5227 | 185.0136 | 2440.6701 | 13.1918 | 185.0136 | 16.03%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 1 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 13.6862 | 0 | 0 | 13.6862 | 0 | 13.0557 | 0.065223 | 200.1722 | 13.0557 | 0.065223 | 200.1722 | 13.7533 | 0.068708 | 200.1722 | 0.04805%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | Tier-3---1 | 597 | 303 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 4146.9327 | 0 | 0 | 4146.9327 | 0 | 3955.8921 | 19.7624 | 200.1722 | 3955.8921 | 19.7624 | 200.1722 | 4167.2608 | 20.8184 | 200.1722 | 14.56%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | Tier-3---1 | 106 | 88 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 1919.4209 | 0 | 0 | 1919.4209 | 0 | 1830.9971 | 5.7396 | 319.0119 | 1830.9971 | 5.7396 | 319.0119 | 1928.8298 | 6.0463 | 319.0119 | 23.95%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 1 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 21.6522 | 0 | 0 | 21.6522 | 0 | 20.6548 | 0.065223 | 316.681 | 20.6548 | 0.065223 | 316.681 | 21.7584 | 0.068708 | 316.681 | 0.4976%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | Tier-3---1 | 58 | 49 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 1060.9593 | 0 | 0 | 1060.9593 | 0 | 1012.0831 | 3.1959 | 316.681 | 1012.0831 | 3.1959 | 316.681 | 1066.1601 | 3.3667 | 316.681 | 24.38%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 1 | 191.8954 | 99.94% | 0% | 0.06293% | 27.8073 | 0 | 0 | 27.8073 | 0 | 26.5263 | 0.065223 | 406.7041 | 26.5263 | 0.065223 | 406.7041 | 27.9436 | 0.068708 | 406.7041 | 14.49%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | Tier-2---11 | 2 | 2 | 191.8954 | 99.94% | 0% | 0.06293% | 55.6146 | 0 | 0 | 55.6146 | 0 | 53.0526 | 0.13045 | 406.7041 | 53.0526 | 0.13045 | 406.7041 | 55.8873 | 0.13742 | 406.7041 | 28.98%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 1 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 15.0047 | 0 | 0 | 15.0047 | 0 | 14.3134 | 0.065223 | 219.4549 | 14.3134 | 0.065223 | 219.4549 | 15.0782 | 0.068708 | 219.4549 | 0.1016%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | Tier-3---1 | 281 | 211 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 3165.9813 | 0 | 0 | 3165.9813 | 0 | 3020.131 | 13.762 | 219.4549 | 3020.131 | 13.762 | 219.4549 | 3181.5008 | 14.4973 | 219.4549 | 21.43%
2026 | 971 | CB 235 | Tier-2 | Tier-2---12 | Tier-2---11 | 6 | 4 | 443.5427 | 99.96% | 0% | 0.03939% | 85.7178 | 0 | 0 | 85.7178 | 0 | 81.769 | 0.26089 | 313.4227 | 81.769 | 0.26089 | 313.4227 | 86.138 | 0.27483 | 313.4227 | 19.33%
2026 | 971 | CB 237 | Tier-2 | Tier-2---8 | Tier-2---1 | 41 | 1 | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 14.8671 | 0 | 0 | 14.8671 | 0 | 14.1822 | 0.065223 | 217.4435 | 14.1822 | 0.065223 | 217.4435 | 14.94 | 0.068708 | 217.4435 | 0.7041%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 2 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 39.5941 | 0 | 0 | 39.5941 | 0 | 37.7701 | 0.13045 | 289.5475 | 37.7701 | 0.13045 | 289.5475 | 39.7882 | 0.13742 | 289.5475 | 0.3456%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | Tier-2---1 | 167 | 107 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 2118.2844 | 0 | 0 | 2118.2844 | 0 | 2020.6994 | 6.9788 | 289.5475 | 2020.6994 | 6.9788 | 289.5475 | 2128.6682 | 7.3517 | 289.5475 | 18.49%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | Tier-3---1 | 213 | 190 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 2044.0481 | 0 | 0 | 2044.0481 | 0 | 1949.883 | 12.3923 | 157.3464 | 1949.883 | 12.3923 | 157.3464 | 2054.068 | 13.0544 | 157.3464 | 25.49%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 9.5833 | 0 | 0 | 9.5833 | 0 | 9.1418 | 0.065223 | 140.1629 | 9.1418 | 0.065223 | 140.1629 | 9.6302 | 0.068708 | 140.1629 | 0.04094%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 457 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 4379.5532 | 0 | 0 | 4379.5532 | 0 | 4177.7963 | 29.8067 | 140.1629 | 4177.7963 | 29.8067 | 140.1629 | 4401.0216 | 31.3993 | 140.1629 | 18.71%
2026 | 972 | 972-1642 | Tier-2 | Tier-2---16 | Tier-2---10 | 9 | 9 | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.587 | 0 | 0 | 0.587 | 0 | 0 | 0.61837 | 0 | 0%
2026 | 972 | 972-1641 | Tier-2 | Tier-2---13 | Tier-2---5 | 3 | 3 | 295.0839 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.19567 | 0 | 0 | 0.19567 | 0 | 0 | 0.20612 | 0 | 0%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | Tier-2---1 | 543 | 384 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 4580.8318 | 0 | 0 | 4580.8318 | 0 | 4369.8023 | 25.0455 | 174.4747 | 4369.8023 | 25.0455 | 174.4747 | 4603.2869 | 26.3837 | 174.4747 | 19.99%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | Tier-3---1 | 189 | 155 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 2156.8482 | 0 | 0 | 2156.8482 | 0 | 2057.4867 | 10.1095 | 203.5201 | 2057.4867 | 10.1095 | 203.5201 | 2167.421 | 10.6497 | 203.5201 | 23.57%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 57 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 429.3763 | 0 | 0 | 429.3763 | 0 | 409.5958 | 3.7177 | 110.1749 | 409.5958 | 3.7177 | 110.1749 | 431.4811 | 3.9163 | 110.1749 | 8.293%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 1 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 42.172 | 0 | 0 | 42.172 | 0 | 40.2293 | 0.065223 | 616.7994 | 40.2293 | 0.065223 | 616.7994 | 42.3788 | 0.068708 | 616.7994 | 0.4892%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 199 | 16 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 149.0696 | 0 | 0 | 149.0696 | 0 | 142.2023 | 1.0436 | 136.2663 | 142.2023 | 1.0436 | 136.2663 | 149.8003 | 1.0993 | 136.2663 | 2.286%
2026 | 974 | 973-1245R | Tier-3 | Tier-3---6 | Tier-3---1 | 59 | 3 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 126.5161 | 0 | 0 | 126.5161 | 0 | 120.6878 | 0.19567 | 616.7994 | 120.6878 | 0.19567 | 616.7994 | 127.1363 | 0.20612 | 616.7994 | 1.468%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 4 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 61.2465 | 0 | 0 | 61.2465 | 0 | 58.425 | 0.26089 | 223.9447 | 58.425 | 0.26089 | 223.9447 | 61.5468 | 0.27483 | 223.9447 | 0.8618%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 1 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 15.3116 | 0 | 0 | 15.3116 | 0 | 14.6063 | 0.065223 | 223.9447 | 14.6063 | 0.065223 | 223.9447 | 15.3867 | 0.068708 | 223.9447 | 0.2154%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | Tier-3---3 | 11 | 2 | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 68.4411 | 0 | 0 | 68.4411 | 0 | 65.2881 | 0.13045 | 500.5023 | 65.2881 | 0.13045 | 500.5023 | 68.7765 | 0.13742 | 500.5023 | 5.247%
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 4 | 1 | 117.1572 | 99.03% | 0.8725% | 0.09309% | 8.4119 | 0 | 0 | 8.4119 | 0 | 8.0244 | 0.065223 | 123.0304 | 8.0244 | 0.065223 | 123.0304 | 8.4531 | 0.068708 | 123.0304 | 7.18%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 516 | 156 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 3052.079 | 0 | 0 | 3052.079 | 0 | 2911.476 | 10.1747 | 286.1479 | 2911.476 | 10.1747 | 286.1479 | 3067.0401 | 10.7184 | 286.1479 | 8.682%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 85 | 29 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 685.3648 | 0 | 0 | 685.3648 | 0 | 653.7915 | 1.8915 | 345.6553 | 653.7915 | 1.8915 | 345.6553 | 688.7244 | 1.9925 | 345.6553 | 9.714%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 168 | 56 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 1814.3346 | 0 | 0 | 1814.3346 | 0 | 1730.752 | 3.6525 | 473.8586 | 1730.752 | 3.6525 | 473.8586 | 1823.2284 | 3.8476 | 473.8586 | 9.638%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | Tier-3---1 | 69 | 25 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 526.3577 | 0 | 0 | 526.3577 | 0 | 502.1095 | 1.6306 | 307.9359 | 502.1095 | 1.6306 | 307.9359 | 528.9379 | 1.7177 | 307.9359 | 10.46%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | Tier-3---3 | 16 | 16 | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 400.4305 | 0 | 0 | 400.4305 | 0 | 381.9835 | 1.0436 | 366.0384 | 381.9835 | 1.0436 | 366.0384 | 402.3934 | 1.0993 | 366.0384 | 28.88%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 12 | 10 | 794.3626 | 99.6% | 0.3592% | 0.04176% | 191.2012 | 0 | 0 | 191.2012 | 0 | 182.393 | 0.65223 | 279.647 | 182.393 | 0.65223 | 279.647 | 192.1385 | 0.68708 | 279.647 | 24.07%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 104 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 2118.4746 | 0 | 0 | 2118.4746 | 0 | 2020.8809 | 6.7831 | 297.9266 | 2020.8809 | 6.7831 | 297.9266 | 2128.8593 | 7.1456 | 297.9266 | 21.62%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 139 | 1 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 20.3699 | 0 | 0 | 20.3699 | 0 | 19.4315 | 0.065223 | 297.9266 | 19.4315 | 0.065223 | 297.9266 | 20.4698 | 0.068708 | 297.9266 | 0.2078%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | Tier-3---4 | 9 | 9 | 694.7204 | 99.22% | 0.7469% | 0.03547% | 199.8926 | 0 | 0 | 199.8926 | 0 | 190.6839 | 0.587 | 324.843 | 190.6839 | 0.587 | 324.843 | 200.8725 | 0.61837 | 324.843 | 28.77%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 72 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 1179.9768 | 0 | 0 | 1179.9768 | 0 | 1125.6177 | 4.696 | 239.6958 | 1125.6177 | 4.696 | 239.6958 | 1185.761 | 4.9469 | 239.6958 | 23.26%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 82 | 6 | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 60.8586 | 0 | 0 | 60.8586 | 0 | 58.055 | 0.39134 | 148.351 | 58.055 | 0.39134 | 148.351 | 61.157 | 0.41225 | 148.351 | 2.106%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 99 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 556.3867 | 0 | 0 | 556.3867 | 0 | 530.7551 | 6.457 | 82.1979 | 530.7551 | 6.457 | 82.1979 | 559.1141 | 6.802 | 82.1979 | 5.875%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | Tier-2---1 | 380 | 140 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 392.6825 | 0 | 0 | 392.6825 | 0 | 374.5924 | 9.1312 | 41.0235 | 374.5924 | 9.1312 | 41.0235 | 394.6074 | 9.6191 | 41.0235 | 10.41%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 1 | 585.5086 | 87.68% | 11.85% | 0.4758% | 1.2511 | 0 | 0 | 1.2511 | 0 | 1.1934 | 0.065223 | 18.2976 | 1.1934 | 0.065223 | 18.2976 | 1.2572 | 0.068708 | 18.2976 | 0.2137%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | Tier-2---4 | 119 | 45 | 585.5086 | 87.68% | 11.85% | 0.4758% | 56.2973 | 0 | 0 | 56.2973 | 0 | 53.7038 | 2.935 | 18.2976 | 53.7038 | 2.935 | 18.2976 | 56.5733 | 3.0918 | 18.2976 | 9.615%
2026 | 1023 | 354-1706R | Tier-2 | Tier-2---1 | Tier-2---1 | 481 | 4 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 49.0512 | 0 | 0 | 49.0512 | 0 | 46.7915 | 0.26089 | 179.3533 | 46.7915 | 0.26089 | 179.3533 | 49.2917 | 0.27483 | 179.3533 | 0.2392%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 1 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 12.3676 | 0 | 0 | 12.3676 | 0 | 11.7979 | 0.065223 | 180.8863 | 11.7979 | 0.065223 | 180.8863 | 12.4283 | 0.068708 | 180.8863 | 0.3711%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 78 | 4 | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 49.4705 | 0 | 0 | 49.4705 | 0 | 47.1915 | 0.26089 | 180.8863 | 47.1915 | 0.26089 | 180.8863 | 49.713 | 0.27483 | 180.8863 | 1.484%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 85 | 7 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 120.2481 | 0 | 0 | 120.2481 | 0 | 114.7086 | 0.45656 | 251.2463 | 114.7086 | 0.45656 | 251.2463 | 120.8376 | 0.48095 | 251.2463 | 2.347%
2026 | 1030 | 1030-1735F | Tier-3 | missing | missing | 6 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.065223 | 0 | 0 | 0.065223 | 0 | 0 | 0.068708 | 0 | 0%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 1 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 17.5057 | 0 | 0 | 17.5057 | 0 | 16.6992 | 0.065223 | 256.0346 | 16.6992 | 0.065223 | 256.0346 | 17.5915 | 0.068708 | 256.0346 | 0.1481%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | Tier-3---1 | 193 | 125 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 2188.2111 | 0 | 0 | 2188.2111 | 0 | 2087.4047 | 8.1528 | 256.0346 | 2087.4047 | 8.1528 | 256.0346 | 2198.9376 | 8.5884 | 256.0346 | 18.52%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | Tier-3---1 | 20 | 3 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 93.0493 | 0 | 0 | 93.0493 | 0 | 88.7627 | 0.19567 | 453.64 | 88.7627 | 0.19567 | 453.64 | 93.5055 | 0.20612 | 453.64 | 4.326%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 98 | 9 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 173.9676 | 0 | 0 | 173.9676 | 0 | 165.9532 | 0.587 | 282.7126 | 165.9532 | 0.587 | 282.7126 | 174.8203 | 0.61837 | 282.7126 | 2.628%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 81 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1606.6207 | 0 | 0 | 1606.6207 | 0 | 1532.607 | 5.283 | 290.1 | 1532.607 | 5.283 | 290.1 | 1614.4963 | 5.5653 | 290.1 | 6.346%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 113 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1941.9874 | 0 | 0 | 1941.9874 | 0 | 1852.524 | 7.3702 | 251.3549 | 1852.524 | 7.3702 | 251.3549 | 1951.5069 | 7.764 | 251.3549 | 6.838%
2026 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | Tier-2---12 | 237 | 1 | 117.3021 | 94.99% | 0% | 5.009% | 0.13634 | 0 | 0 | 0.13634 | 0 | 0.13006 | 0.065223 | 1.9942 | 0.13006 | 0.065223 | 1.9942 | 0.13701 | 0.068708 | 1.9942 | 0.1162%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | Tier-3---7 | 44 | 38 | 730.5479 | 99.24% | 0.5863% | 0.172% | 181.5816 | 0 | 0 | 181.5816 | 0 | 173.2165 | 2.4785 | 69.8888 | 173.2165 | 2.4785 | 69.8888 | 182.4717 | 2.6109 | 69.8888 | 24.86%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | Tier-3---5 | 122 | 117 | 919.3728 | 93.93% | 5.62% | 0.4487% | 240.174 | 0 | 0 | 240.174 | 0 | 229.1096 | 7.631 | 30.0234 | 229.1096 | 7.631 | 30.0234 | 241.3513 | 8.0388 | 30.0234 | 26.12%
2026 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 54 | 509.5021 | 91.97% | 7.519% | 0.512% | 91.725 | 0 | 0 | 91.725 | 0 | 87.4994 | 3.522 | 24.8435 | 87.4994 | 3.522 | 24.8435 | 92.1746 | 3.7102 | 24.8435 | 18%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | Tier-3---2 | 317 | 215 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 1155.8649 | 0 | 0 | 1155.8649 | 0 | 1102.6166 | 14.0229 | 78.63 | 1102.6166 | 14.0229 | 78.63 | 1161.5309 | 14.7721 | 78.63 | 19.59%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 1 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 4.4919 | 0 | 0 | 4.4919 | 0 | 4.285 | 0.065223 | 65.6983 | 4.285 | 0.065223 | 65.6983 | 4.514 | 0.068708 | 65.6983 | 0.09%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 1 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 4.4919 | 0 | 0 | 4.4919 | 0 | 4.285 | 0.065223 | 65.6983 | 4.285 | 0.065223 | 65.6983 | 4.514 | 0.068708 | 65.6983 | 0.09%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | Tier-3---2 | 321 | 223 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 1001.7038 | 0 | 0 | 1001.7038 | 0 | 955.5574 | 14.5446 | 65.6983 | 955.5574 | 14.5446 | 65.6983 | 1006.6141 | 15.3218 | 65.6983 | 20.07%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 111 | 84 | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 309.2512 | 0 | 0 | 309.2512 | 0 | 295.0046 | 5.4787 | 53.8458 | 295.0046 | 5.4787 | 53.8458 | 310.7671 | 5.7714 | 53.8458 | 21.86%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 63 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 96.5728 | 0 | 0 | 96.5728 | 0 | 92.1239 | 4.109 | 22.4199 | 92.1239 | 4.109 | 22.4199 | 97.0462 | 4.3286 | 22.4199 | 2.071%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 33 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 303.1581 | 0 | 0 | 303.1581 | 0 | 289.1922 | 2.1523 | 134.3614 | 289.1922 | 2.1523 | 134.3614 | 304.6441 | 2.2673 | 134.3614 | 7.645%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 39 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 1140.644 | 0 | 0 | 1140.644 | 0 | 1088.0969 | 2.5437 | 427.7647 | 1088.0969 | 2.5437 | 427.7647 | 1146.2354 | 2.6796 | 427.7647 | 11.28%
2026 | 1166 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 1 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 10.5024 | 0 | 0 | 10.5024 | 0 | 10.0186 | 0.065223 | 153.6057 | 10.0186 | 0.065223 | 153.6057 | 10.5539 | 0.068708 | 153.6057 | 0.1719%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | Tier-3---1 | 216 | 186 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 2554.0963 | 0 | 0 | 2554.0963 | 0 | 2436.4344 | 12.1314 | 200.837 | 2436.4344 | 12.1314 | 200.837 | 2566.6164 | 12.7796 | 200.837 | 24.74%
2026 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 1 | 70.8201 | 99.8% | 0% | 0.2033% | 4.0992 | 0 | 0 | 4.0992 | 0 | 3.9104 | 0.065223 | 59.9543 | 3.9104 | 0.065223 | 59.9543 | 4.1193 | 0.068708 | 59.9543 | 5.788%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 4 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 46.8443 | 0 | 0 | 46.8443 | 0 | 44.6862 | 0.26089 | 171.2836 | 44.6862 | 0.26089 | 171.2836 | 47.0739 | 0.27483 | 171.2836 | 0.762%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 105 | 12 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 50.9125 | 0 | 0 | 50.9125 | 0 | 48.567 | 0.78267 | 62.0529 | 48.567 | 0.78267 | 62.0529 | 51.1621 | 0.82449 | 62.0529 | 3.267%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | Tier-3---1 | 187 | 34 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 154.0231 | 0 | 0 | 154.0231 | 0 | 146.9276 | 2.2176 | 66.2562 | 146.9276 | 2.2176 | 66.2562 | 154.7781 | 2.3361 | 66.2562 | 5.162%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | Tier-3---3 | 58 | 7 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 48.0017 | 0 | 0 | 48.0017 | 0 | 45.7904 | 0.45656 | 100.2947 | 45.7904 | 0.45656 | 100.2947 | 48.237 | 0.48095 | 100.2947 | 3.462%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 57 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 366.4038 | 0 | 0 | 366.4038 | 0 | 349.5243 | 3.7177 | 94.0166 | 349.5243 | 3.7177 | 94.0166 | 368.1999 | 3.9163 | 94.0166 | 5.805%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 4 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 12.2811 | 0 | 0 | 12.2811 | 0 | 11.7154 | 0.26089 | 44.9053 | 11.7154 | 0.26089 | 44.9053 | 12.3413 | 0.27483 | 44.9053 | 0.1848%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | Tier-2---5 | 22 | 18 | 427.4478 | 90.46% | 9.431% | 0.1062% | 91.749 | 0 | 0 | 91.749 | 0 | 87.5223 | 1.174 | 74.5501 | 87.5223 | 1.174 | 74.5501 | 92.1988 | 1.2367 | 74.5501 | 21.46%
2026 | 1458 | 1458-1057F | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 1 | 155.9987 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.065223 | 0 | 0 | 0.065223 | 0 | 0 | 0.068708 | 0 | 0%
2026 | 1458 | 1458-1057F | Tier-3 | Tier-3---18 | Tier-3---10 | 3 | 2 | 155.9987 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.13045 | 0 | 0 | 0.13045 | 0 | 0 | 0.13742 | 0 | 0%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | Tier-3---1 | 36 | 29 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 472.7258 | 0 | 0 | 472.7258 | 0 | 450.9483 | 1.8915 | 238.4134 | 450.9483 | 1.8915 | 238.4134 | 475.043 | 1.9925 | 238.4134 | 19.98%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | Tier-2---1 | 80 | 52 | 4370.0987 | 98.67% | 1.293% | 0.03403% | 812.8352 | 0 | 0 | 812.8352 | 0 | 775.3895 | 3.3916 | 228.6223 | 775.3895 | 3.3916 | 228.6223 | 816.8196 | 3.5728 | 228.6223 | 18.6%
2026 | 1458 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 1 | 16869.708 | 98.79% | 1.184% | 0.02933% | 17.8334 | 0 | 0 | 17.8334 | 0 | 17.0118 | 0.065223 | 260.8273 | 17.0118 | 0.065223 | 260.8273 | 17.9208 | 0.068708 | 260.8273 | 0.1057%
2026 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | Tier-2---14 | 2 | 3 | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.19567 | 0 | 0 | 0.19567 | 0 | 0 | 0.20612 | 0 | 0%
2026 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | Tier-2---14 | 2 | 5 | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.32611 | 0 | 0 | 0.32611 | 0 | 0 | 0.34354 | 0 | 0%
2026 | 1458 | 1458-1119F | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.065223 | 0 | 0 | 0.065223 | 0 | 0 | 0.068708 | 0 | 0%
2026 | 1458 | 1458-454F | Tier-2 | Tier-2---18 | Tier-2---10 | 2 | 1 | 84.0912 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.065223 | 0 | 0 | 0.065223 | 0 | 0 | 0.068708 | 0 | 0%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 6 | 167.5686 | 29.81% | 70.17% | 0.01889% | 12.4156 | 0 | 0 | 12.4156 | 0 | 11.8436 | 0.39134 | 30.2647 | 11.8436 | 0.39134 | 30.2647 | 12.4765 | 0.41225 | 30.2647 | 7.409%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | Tier-2---11 | 2 | 2 | 81.0039 | 99.95% | 0% | 0.04716% | 23.4801 | 0 | 0 | 23.4801 | 0 | 22.3984 | 0.13045 | 171.7073 | 22.3984 | 0.13045 | 171.7073 | 23.5952 | 0.13742 | 171.7073 | 28.99%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 198 | 37077.302 | 99.36% | 0.615% | 0.02874% | 4796.5366 | 0 | 0 | 4796.5366 | 0 | 4575.5701 | 12.9141 | 354.3088 | 4575.5701 | 12.9141 | 354.3088 | 4820.0491 | 13.6041 | 354.3088 | 12.94%
2026 | 1458 | 357-2047F | Tier-2 | Tier-2---10 | Tier-2---3 | 17 | 1 | 878.9304 | 95.49% | 4.482% | 0.03213% | 14.3166 | 0 | 0 | 14.3166 | 0 | 13.6571 | 0.065223 | 209.392 | 13.6571 | 0.065223 | 209.392 | 14.3868 | 0.068708 | 209.392 | 1.629%
2026 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 15.4911 | 99.81% | 0% | 0.1868% | 4.484 | 0 | 0 | 4.484 | 0 | 4.2775 | 0.13045 | 32.7912 | 4.2775 | 0.13045 | 32.7912 | 4.506 | 0.13742 | 32.7912 | 28.95%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | Tier-2---1 | 116 | 86 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 1084.8444 | 0 | 0 | 1084.8444 | 0 | 1034.8679 | 5.6091 | 184.4966 | 1034.8679 | 5.6091 | 184.4966 | 1090.1623 | 5.9088 | 184.4966 | 21.19%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 42 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 356.7387 | 0 | 0 | 356.7387 | 0 | 340.3044 | 2.7393 | 124.2282 | 340.3044 | 2.7393 | 124.2282 | 358.4874 | 2.8857 | 124.2282 | 3.392%
2026 | RA1 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 1 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 12.6106 | 0 | 0 | 12.6106 | 0 | 12.0297 | 0.065223 | 184.4401 | 12.0297 | 0.065223 | 184.4401 | 12.6724 | 0.068708 | 184.4401 | 0.2411%
2026 | RA2 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 14 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 134.1657 | 0 | 0 | 134.1657 | 0 | 127.985 | 0.91312 | 140.1629 | 127.985 | 0.91312 | 140.1629 | 134.8234 | 0.96191 | 140.1629 | 0.5731%
2026 | RA2 | CB 236 | Tier-2 | Tier-2---1 | Tier-2---1 | 337 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 10.678 | 0 | 0 | 10.678 | 0 | 10.1861 | 0.065223 | 156.1746 | 10.1861 | 0.065223 | 156.1746 | 10.7304 | 0.068708 | 156.1746 | 0.084%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 1 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 12.6106 | 0 | 0 | 12.6106 | 0 | 12.0297 | 0.065223 | 184.4401 | 12.0297 | 0.065223 | 184.4401 | 12.6724 | 0.068708 | 184.4401 | 0.2411%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 13 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 163.9379 | 0 | 0 | 163.9379 | 0 | 156.3856 | 0.84789 | 184.4401 | 156.3856 | 0.84789 | 184.4401 | 164.7415 | 0.8932 | 184.4401 | 3.135%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 43 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 542.256 | 0 | 0 | 542.256 | 0 | 517.2754 | 2.8046 | 184.4401 | 517.2754 | 2.8046 | 184.4401 | 544.9141 | 2.9544 | 184.4401 | 10.37%
2026 | RA3 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 1 | 663.2151 | 70.89% | 28.72% | 0.399% | 1.2065 | 0 | 0 | 1.2065 | 0 | 1.1509 | 0.065223 | 17.6461 | 1.1509 | 0.065223 | 17.6461 | 1.2124 | 0.068708 | 17.6461 | 0.1819%
2026 | RA3 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 4 | 663.2151 | 70.89% | 28.72% | 0.399% | 4.826 | 0 | 0 | 4.826 | 0 | 4.6037 | 0.26089 | 17.6461 | 4.6037 | 0.26089 | 17.6461 | 4.8497 | 0.27483 | 17.6461 | 0.7277%
2026 | RA3 | 237-26F | Tier-2 | Tier-2---10 | Tier-2---3 | 113 | 3 | 663.2151 | 70.89% | 28.72% | 0.399% | 3.6195 | 0 | 0 | 3.6195 | 0 | 3.4528 | 0.19567 | 17.6461 | 3.4528 | 0.19567 | 17.6461 | 3.6373 | 0.20612 | 17.6461 | 0.5458%
2026 | RA3 | 972-1590F | Tier-3 | Tier-3---2 | Tier-3---1 | 697 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 9.5833 | 0 | 0 | 9.5833 | 0 | 9.1418 | 0.065223 | 140.1629 | 9.1418 | 0.065223 | 140.1629 | 9.6302 | 0.068708 | 140.1629 | 0.04094%
2026 | RA3 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 2 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 16.9876 | 0 | 0 | 16.9876 | 0 | 16.205 | 0.13045 | 124.2282 | 16.205 | 0.13045 | 124.2282 | 17.0708 | 0.13742 | 124.2282 | 0.1615%
2026 | RA3 | CB RA1 | Tier-2 | Tier-2---2 | Tier-2---1 | 353 | 4 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 33.9751 | 0 | 0 | 33.9751 | 0 | 32.4099 | 0.26089 | 124.2282 | 32.4099 | 0.26089 | 124.2282 | 34.1417 | 0.27483 | 124.2282 | 0.323%
2026 | RA3 | CB RA2 | Tier-2 | Tier-2---4 | Tier-2---1 | 118 | 2 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 25.2212 | 0 | 0 | 25.2212 | 0 | 24.0593 | 0.13045 | 184.4401 | 24.0593 | 0.13045 | 184.4401 | 25.3448 | 0.13742 | 184.4401 | 0.4823%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 1 | 916.1972 | 69.5% | 30.07% | 0.4286% | 0.7662 | 0 | 0 | 0.7662 | 0 | 0.7309 | 0.065223 | 11.2062 | 0.7309 | 0.065223 | 11.2062 | 0.76995 | 0.068708 | 11.2062 | 0.08363%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 4 | 916.1972 | 69.5% | 30.07% | 0.4286% | 3.0648 | 0 | 0 | 3.0648 | 0 | 2.9236 | 0.26089 | 11.2062 | 2.9236 | 0.26089 | 11.2062 | 3.0798 | 0.27483 | 11.2062 | 0.3345%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 2 | 916.1972 | 69.5% | 30.07% | 0.4286% | 1.5324 | 0 | 0 | 1.5324 | 0 | 1.4618 | 0.13045 | 11.2062 | 1.4618 | 0.13045 | 11.2062 | 1.5399 | 0.13742 | 11.2062 | 0.1673%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 3 | 916.1972 | 69.5% | 30.07% | 0.4286% | 2.2986 | 0 | 0 | 2.2986 | 0 | 2.1927 | 0.19567 | 11.2062 | 2.1927 | 0.19567 | 11.2062 | 2.3099 | 0.20612 | 11.2062 | 0.2509%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 1 | 916.1972 | 69.5% | 30.07% | 0.4286% | 0.7662 | 0 | 0 | 0.7662 | 0 | 0.7309 | 0.065223 | 11.2062 | 0.7309 | 0.065223 | 11.2062 | 0.76995 | 0.068708 | 11.2062 | 0.08363%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | Tier-2---3 | 241 | 44 | 916.1972 | 69.5% | 30.07% | 0.4286% | 33.7127 | 0 | 0 | 33.7127 | 0 | 32.1596 | 2.8698 | 11.2062 | 32.1596 | 2.8698 | 11.2062 | 33.878 | 3.0231 | 11.2062 | 3.68%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | Tier-3---1 | 235 | 175 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 764.4065 | 0 | 0 | 764.4065 | 0 | 729.1919 | 11.414 | 63.886 | 729.1919 | 11.414 | 63.886 | 768.1536 | 12.0238 | 63.886 | 20.55%
2026 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 64 | 346.5871 | 36.93% | 61.45% | 1.621% | 6.4029 | 0 | 0 | 6.4029 | 0 | 6.108 | 4.1742 | 1.4633 | 6.108 | 4.1742 | 1.4633 | 6.4343 | 4.3973 | 1.4633 | 1.847%
2027 | 67 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 1 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 5.2238 | 0 | 0 | 5.2238 | 0 | 4.7536 | 0.062218 | 76.4027 | 4.7536 | 0.062218 | 76.4027 | 5.2752 | 0.069044 | 76.4027 | 0.1348%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 344 | 76 | 2610.8 | 93.6% | 6.065% | 0.3401% | 156.5599 | 0 | 0 | 156.5599 | 0 | 142.4674 | 4.7286 | 30.1291 | 142.4674 | 4.7286 | 30.1291 | 158.0986 | 5.2474 | 30.1291 | 5.997%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 551 | 430 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 887.4032 | 0 | 0 | 887.4032 | 0 | 807.5248 | 26.7537 | 30.1837 | 807.5248 | 26.7537 | 30.1837 | 896.1246 | 29.6891 | 30.1837 | 21.23%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 29 | 622.3042 | 87.18% | 11.98% | 0.8373% | 24.0138 | 0 | 0 | 24.0138 | 0 | 21.8522 | 1.8043 | 12.1111 | 21.8522 | 1.8043 | 12.1111 | 24.2498 | 2.0023 | 12.1111 | 3.859%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 233 | 198 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 372.2451 | 0 | 0 | 372.2451 | 0 | 338.738 | 12.3191 | 27.4969 | 338.738 | 12.3191 | 27.4969 | 375.9035 | 13.6708 | 27.4969 | 22.87%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | Tier-3---1 | 310 | 75 | 6201.607 | 97.29% | 2.601% | 0.1104% | 423.3157 | 0 | 0 | 423.3157 | 0 | 385.2116 | 4.6663 | 82.551 | 385.2116 | 4.6663 | 82.551 | 427.4761 | 5.1783 | 82.551 | 6.826%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 1 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 13.4472 | 0 | 0 | 13.4472 | 0 | 12.2367 | 0.062218 | 196.6756 | 12.2367 | 0.062218 | 196.6756 | 13.5793 | 0.069044 | 196.6756 | 0.08768%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | Tier-3---1 | 326 | 82 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 1102.6683 | 0 | 0 | 1102.6683 | 0 | 1003.4131 | 5.1019 | 196.6756 | 1003.4131 | 5.1019 | 196.6756 | 1113.5053 | 5.6616 | 196.6756 | 7.19%
2027 | 73 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 9 | 1 | 324.1263 | 99.58% | 0.3619% | 0.05404% | 10.4006 | 0 | 0 | 10.4006 | 0 | 9.4644 | 0.062218 | 152.1174 | 9.4644 | 0.062218 | 152.1174 | 10.5028 | 0.069044 | 152.1174 | 3.209%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | Tier-3---1 | 273 | 2 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 19.4227 | 0 | 0 | 19.4227 | 0 | 17.6744 | 0.12444 | 142.0359 | 17.6744 | 0.12444 | 142.0359 | 19.6135 | 0.13809 | 142.0359 | 0.2091%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | Tier-3---1 | 186 | 8 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 178.579 | 0 | 0 | 178.579 | 0 | 162.5045 | 0.49774 | 326.4825 | 162.5045 | 0.49774 | 326.4825 | 180.3341 | 0.55235 | 326.4825 | 1.229%
2027 | 78 | CB 78 | Tier-3 | Tier-3---20 | Tier-3---11 | 4 | 3 | 25.281 | 99.56% | 0% | 0.4423% | 5.4743 | 0 | 0 | 5.4743 | 0 | 4.9815 | 0.18665 | 26.6886 | 4.9815 | 0.18665 | 26.6886 | 5.5281 | 0.20713 | 26.6886 | 21.65%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | Tier-3---5 | 9 | 4 | 324.1263 | 99.58% | 0.3619% | 0.05404% | 41.6025 | 0 | 0 | 41.6025 | 0 | 37.8577 | 0.24887 | 152.1174 | 37.8577 | 0.24887 | 152.1174 | 42.0114 | 0.27618 | 152.1174 | 12.84%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 198 | 113 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 2024.1915 | 0 | 0 | 2024.1915 | 0 | 1841.9867 | 7.0306 | 261.9947 | 1841.9867 | 7.0306 | 261.9947 | 2044.0851 | 7.802 | 261.9947 | 16.43%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 9 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 29.6602 | 0 | 0 | 29.6602 | 0 | 26.9904 | 0.55996 | 48.2004 | 26.9904 | 0.55996 | 48.2004 | 29.9517 | 0.6214 | 48.2004 | 1.421%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 1 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 20.0638 | 0 | 0 | 20.0638 | 0 | 18.2578 | 0.062218 | 293.4496 | 18.2578 | 0.062218 | 293.4496 | 20.261 | 0.069044 | 293.4496 | 0.2065%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | Tier-3---1 | 138 | 46 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 922.9368 | 0 | 0 | 922.9368 | 0 | 839.8599 | 2.862 | 293.4496 | 839.8599 | 2.862 | 293.4496 | 932.0074 | 3.176 | 293.4496 | 9.501%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | Tier-3---1 | 192 | 15 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 413.3663 | 0 | 0 | 413.3663 | 0 | 376.1577 | 0.93327 | 403.0539 | 376.1577 | 0.93327 | 403.0539 | 417.4288 | 1.0357 | 403.0539 | 2.241%
2027 | 79 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 1 | 11572.221 | 88.48% | 11.4% | 0.1243% | 3.8915 | 0 | 0 | 3.8915 | 0 | 3.5412 | 0.062218 | 56.9163 | 3.5412 | 0.062218 | 56.9163 | 3.9297 | 0.069044 | 56.9163 | 0.03363%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | Tier-3---3 | 180 | 106 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 910.6811 | 0 | 0 | 910.6811 | 0 | 828.7074 | 6.5951 | 125.655 | 828.7074 | 6.5951 | 125.655 | 919.6313 | 7.3187 | 125.655 | 16.45%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 1 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 12.3909 | 0 | 0 | 12.3909 | 0 | 11.2755 | 0.062218 | 181.2263 | 11.2755 | 0.062218 | 181.2263 | 12.5126 | 0.069044 | 181.2263 | 0.06598%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | Tier-3---1 | 427 | 237 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 2936.6362 | 0 | 0 | 2936.6362 | 0 | 2672.299 | 14.7456 | 181.2263 | 2672.299 | 14.7456 | 181.2263 | 2965.4974 | 16.3635 | 181.2263 | 15.64%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | Tier-3---5 | 116 | 16 | 3034.8235 | 97.12% | 2.752% | 0.1275% | 117.8973 | 0 | 0 | 117.8973 | 0 | 107.2849 | 0.99549 | 107.7713 | 107.2849 | 0.99549 | 107.7713 | 119.056 | 1.1047 | 107.7713 | 3.885%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | Tier-3---1 | 218 | 80 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 2109.7817 | 0 | 0 | 2109.7817 | 0 | 1919.8726 | 4.9774 | 385.7153 | 1919.8726 | 4.9774 | 385.7153 | 2130.5165 | 5.5235 | 385.7153 | 10.56%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | Tier-3---3 | 669 | 307 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 677.621 | 0 | 0 | 677.621 | 0 | 616.6259 | 19.1009 | 32.2826 | 616.6259 | 19.1009 | 32.2826 | 684.2806 | 21.1966 | 32.2826 | 12.3%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | Tier-3---3 | 213 | 155 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 809.6938 | 0 | 0 | 809.6938 | 0 | 736.8104 | 9.6438 | 76.4027 | 736.8104 | 9.6438 | 76.4027 | 817.6515 | 10.7019 | 76.4027 | 20.89%
2027 | 157 | 157-207R | Tier-3 | Tier-3---16 | Tier-3---7 | 23 | 20 | 719.0865 | 99.89% | 0% | 0.1123% | 181.1312 | 0 | 0 | 181.1312 | 0 | 164.8269 | 1.2444 | 132.4594 | 164.8269 | 1.2444 | 132.4594 | 182.9113 | 1.3809 | 132.4594 | 25.19%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | Tier-3---3 | 250 | 23 | 3160.5079 | 95.27% | 4.501% | 0.231% | 80.3325 | 0 | 0 | 80.3325 | 0 | 73.1015 | 1.431 | 51.0837 | 73.1015 | 1.431 | 51.0837 | 81.122 | 1.588 | 51.0837 | 2.542%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | Tier-3---3 | 173 | 80 | 1867.403 | 95.01% | 4.712% | 0.2778% | 237.9313 | 0 | 0 | 237.9313 | 0 | 216.5142 | 4.9774 | 43.4992 | 216.5142 | 4.9774 | 43.4992 | 240.2696 | 5.5235 | 43.4992 | 12.74%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 37 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 198.9081 | 0 | 0 | 198.9081 | 0 | 181.0037 | 2.3021 | 78.6267 | 181.0037 | 2.3021 | 78.6267 | 200.863 | 2.5546 | 78.6267 | 3.464%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 1 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 11.1982 | 0 | 0 | 11.1982 | 0 | 10.1902 | 0.062218 | 163.7828 | 10.1902 | 0.062218 | 163.7828 | 11.3083 | 0.069044 | 163.7828 | 0.09397%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 137 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 1534.1558 | 0 | 0 | 1534.1558 | 0 | 1396.0609 | 8.5239 | 163.7828 | 1396.0609 | 8.5239 | 163.7828 | 1549.2334 | 9.4591 | 163.7828 | 12.87%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | Tier-2---1 | 26 | 16 | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 345.1786 | 0 | 0 | 345.1786 | 0 | 314.1078 | 0.99549 | 315.5319 | 314.1078 | 0.99549 | 315.5319 | 348.571 | 1.1047 | 315.5319 | 17.8%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | Tier-2---1 | 104 | 42 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 491.5049 | 0 | 0 | 491.5049 | 0 | 447.2628 | 2.6132 | 171.1583 | 447.2628 | 2.6132 | 171.1583 | 496.3354 | 2.8999 | 171.1583 | 11.62%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 5 | 973.0999 | 95.53% | 4.02% | 0.4464% | 7.1701 | 0 | 0 | 7.1701 | 0 | 6.5247 | 0.31109 | 20.9736 | 6.5247 | 0.31109 | 20.9736 | 7.2405 | 0.34522 | 20.9736 | 0.7368%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 62 | 133.9861 | 95.12% | 0% | 4.877% | 11.8735 | 0 | 0 | 11.8735 | 0 | 10.8047 | 3.8575 | 2.8009 | 10.8047 | 3.8575 | 2.8009 | 11.9902 | 4.2807 | 2.8009 | 8.862%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 5 | 2976.5734 | 99.75% | 0% | 0.2502% | 10.4243 | 0 | 0 | 10.4243 | 0 | 9.486 | 0.31109 | 30.4927 | 9.486 | 0.31109 | 30.4927 | 10.5267 | 0.34522 | 30.4927 | 0.3502%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 24 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 25.2679 | 0 | 0 | 25.2679 | 0 | 22.9935 | 1.4932 | 15.3985 | 22.9935 | 1.4932 | 15.3985 | 25.5162 | 1.6571 | 15.3985 | 1.396%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 13 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 33.5374 | 0 | 0 | 33.5374 | 0 | 30.5185 | 0.80883 | 37.7316 | 30.5185 | 0.80883 | 37.7316 | 33.867 | 0.89758 | 37.7316 | 1.216%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 71 | 1721.769 | 85.69% | 14.07% | 0.2459% | 154.9862 | 0 | 0 | 154.9862 | 0 | 141.0353 | 4.4175 | 31.9267 | 141.0353 | 4.4175 | 31.9267 | 156.5094 | 4.9021 | 31.9267 | 9.002%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 28 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 40.1877 | 0 | 0 | 40.1877 | 0 | 36.5703 | 1.7421 | 20.992 | 36.5703 | 1.7421 | 20.992 | 40.5827 | 1.9332 | 20.992 | 2.087%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | Tier-2---17 | 8 | 5 | 17.3686 | 98.33% | 0% | 1.666% | 3.0956 | 0 | 0 | 3.0956 | 0 | 2.817 | 0.31109 | 9.0551 | 2.817 | 0.31109 | 9.0551 | 3.126 | 0.34522 | 9.0551 | 17.82%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | Tier-2---8 | 9 | 3 | 171.5883 | 99.37% | 0.4538% | 0.1789% | 16.4819 | 0 | 0 | 16.4819 | 0 | 14.9983 | 0.18665 | 80.3537 | 14.9983 | 0.18665 | 80.3537 | 16.6439 | 0.20713 | 80.3537 | 9.605%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 1 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 2.0485 | 0 | 0 | 2.0485 | 0 | 1.8641 | 0.062218 | 29.9603 | 1.8641 | 0.062218 | 29.9603 | 2.0686 | 0.069044 | 29.9603 | 0.1024%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | Tier-2---1 | 269 | 161 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 329.8016 | 0 | 0 | 329.8016 | 0 | 300.115 | 10.0171 | 29.9603 | 300.115 | 10.0171 | 29.9603 | 333.0429 | 11.1161 | 29.9603 | 16.49%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | Tier-2---1 | 328 | 221 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 1226.6388 | 0 | 0 | 1226.6388 | 0 | 1116.2246 | 13.7502 | 81.179 | 1116.2246 | 13.7502 | 81.179 | 1238.6941 | 15.2588 | 81.179 | 19.2%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | Tier-2---2 | 245 | 157 | 2072.8837 | 91.06% | 8.635% | 0.3% | 350.7974 | 0 | 0 | 350.7974 | 0 | 319.2209 | 9.7682 | 32.6796 | 319.2209 | 9.7682 | 32.6796 | 354.245 | 10.84 | 32.6796 | 16.92%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | Tier-2---4 | 71 | 6 | 536.3838 | 78.97% | 20.71% | 0.32% | 10.3805 | 0 | 0 | 10.3805 | 0 | 9.4461 | 0.37331 | 25.3038 | 9.4461 | 0.37331 | 25.3038 | 10.4825 | 0.41427 | 25.3038 | 1.935%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 52 | 3 | 788.7224 | 98.19% | 1.606% | 0.2041% | 12.957 | 0 | 0 | 12.957 | 0 | 11.7907 | 0.18665 | 63.169 | 11.7907 | 0.18665 | 63.169 | 13.0844 | 0.20713 | 63.169 | 1.643%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | Tier-2---4 | 52 | 25 | 788.7224 | 98.19% | 1.606% | 0.2041% | 107.9753 | 0 | 0 | 107.9753 | 0 | 98.256 | 1.5554 | 63.169 | 98.256 | 1.5554 | 63.169 | 109.0365 | 1.7261 | 63.169 | 13.69%
2027 | 230 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 5 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 15.3514 | 0 | 0 | 15.3514 | 0 | 13.9696 | 0.31109 | 44.9053 | 13.9696 | 0.31109 | 44.9053 | 15.5023 | 0.34522 | 44.9053 | 0.231%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | Tier-2---2 | 236 | 183 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 762.939 | 0 | 0 | 762.939 | 0 | 694.2641 | 11.3859 | 60.9759 | 694.2641 | 11.3859 | 60.9759 | 770.4372 | 12.6351 | 60.9759 | 21.96%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 1 | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.4648 | 0 | 0 | 5.4648 | 0 | 4.9729 | 0.062218 | 79.9275 | 4.9729 | 0.062218 | 79.9275 | 5.5185 | 0.069044 | 79.9275 | 4.494%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 1 | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.4648 | 0 | 0 | 5.4648 | 0 | 4.9729 | 0.062218 | 79.9275 | 4.9729 | 0.062218 | 79.9275 | 5.5185 | 0.069044 | 79.9275 | 4.494%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | Tier-2---8 | 6 | 4 | 121.6067 | 92.98% | 6.845% | 0.1786% | 21.8593 | 0 | 0 | 21.8593 | 0 | 19.8917 | 0.24887 | 79.9275 | 19.8917 | 0.24887 | 79.9275 | 22.0742 | 0.27618 | 79.9275 | 17.98%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | Tier-2---8 | 41 | 14 | 195.7251 | 81.71% | 17.81% | 0.4804% | 15.8374 | 0 | 0 | 15.8374 | 0 | 14.4118 | 0.87105 | 16.5453 | 14.4118 | 0.87105 | 16.5453 | 15.9931 | 0.96662 | 16.5453 | 8.092%
2027 | 230 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 1 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 3.0703 | 0 | 0 | 3.0703 | 0 | 2.7939 | 0.062218 | 44.9053 | 2.7939 | 0.062218 | 44.9053 | 3.1005 | 0.069044 | 44.9053 | 0.0462%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 12 | 3 | 212.8275 | 99.81% | 0% | 0.1866% | 15.4012 | 0 | 0 | 15.4012 | 0 | 14.0149 | 0.18665 | 75.0849 | 14.0149 | 0.18665 | 75.0849 | 15.5526 | 0.20713 | 75.0849 | 7.236%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 1 | 2730.9177 | 98.3% | 1.373% | 0.325% | 2.1807 | 0 | 0 | 2.1807 | 0 | 1.9844 | 0.062218 | 31.8948 | 1.9844 | 0.062218 | 31.8948 | 2.2022 | 0.069044 | 31.8948 | 0.07985%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 108 | 2730.9177 | 98.3% | 1.373% | 0.325% | 235.5178 | 0 | 0 | 235.5178 | 0 | 214.318 | 6.7195 | 31.8948 | 214.318 | 6.7195 | 31.8948 | 237.8324 | 7.4568 | 31.8948 | 8.624%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 429 | 5142.095 | 98.68% | 0.901% | 0.4182% | 732.3537 | 0 | 0 | 732.3537 | 0 | 666.4319 | 26.6915 | 24.968 | 666.4319 | 26.6915 | 24.968 | 739.5513 | 29.62 | 24.968 | 14.24%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 50 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 138.4263 | 0 | 0 | 138.4263 | 0 | 125.966 | 3.1109 | 40.4919 | 125.966 | 3.1109 | 40.4919 | 139.7867 | 3.4522 | 40.4919 | 5.537%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | Tier-2---15 | 5 | 4 | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.011995 | 0 | 0 | 0.011995 | 0 | 0.010915 | 0.24887 | 0.043858 | 0.010915 | 0.24887 | 0.043858 | 0.012113 | 0.27618 | 0.043858 | 0.1049%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | Tier-2---2 | 259 | 65 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 116.4091 | 0 | 0 | 116.4091 | 0 | 105.9307 | 4.0442 | 26.1935 | 105.9307 | 4.0442 | 26.1935 | 117.5532 | 4.4879 | 26.1935 | 7.087%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 64 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 135.171 | 0 | 0 | 135.171 | 0 | 123.0037 | 3.9819 | 30.8903 | 123.0037 | 3.9819 | 30.8903 | 136.4994 | 4.4188 | 30.8903 | 4.453%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 57 | 718.991 | 97.57% | 1.357% | 1.072% | 42.4768 | 0 | 0 | 42.4768 | 0 | 38.6533 | 3.5464 | 10.8992 | 38.6533 | 3.5464 | 10.8992 | 42.8942 | 3.9355 | 10.8992 | 5.908%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | Tier-2---1 | 412 | 60 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 84.9541 | 0 | 0 | 84.9541 | 0 | 77.3071 | 3.7331 | 20.7087 | 77.3071 | 3.7331 | 20.7087 | 85.789 | 4.1427 | 20.7087 | 3.628%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 613 | 161 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 310.4229 | 0 | 0 | 310.4229 | 0 | 282.4806 | 10.0171 | 28.1999 | 282.4806 | 10.0171 | 28.1999 | 313.4737 | 11.1161 | 28.1999 | 7.52%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 1 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 4.2654 | 0 | 0 | 4.2654 | 0 | 3.8814 | 0.062218 | 62.3845 | 3.8814 | 0.062218 | 62.3845 | 4.3073 | 0.069044 | 62.3845 | 0.08635%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | Tier-2---2 | 334 | 154 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 656.8682 | 0 | 0 | 656.8682 | 0 | 597.7411 | 9.5816 | 62.3845 | 597.7411 | 9.5816 | 62.3845 | 663.3239 | 10.6328 | 62.3845 | 13.3%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | Tier-2---2 | 352 | 94 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 252.298 | 0 | 0 | 252.298 | 0 | 229.5878 | 5.8485 | 39.2559 | 229.5878 | 5.8485 | 39.2559 | 254.7776 | 6.4902 | 39.2559 | 7.657%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | Tier-3---4 | 108 | 11 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 21.0659 | 0 | 0 | 21.0659 | 0 | 19.1696 | 0.6844 | 28.0095 | 19.1696 | 0.6844 | 28.0095 | 21.2729 | 0.75949 | 28.0095 | 2.046%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 165 | 99 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 202.2656 | 0 | 0 | 202.2656 | 0 | 184.0589 | 6.1596 | 29.8818 | 184.0589 | 6.1596 | 29.8818 | 204.2534 | 6.8354 | 29.8818 | 17.12%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 71 | 40 | 791.3356 | 98.7% | 1.112% | 0.1837% | 127.6139 | 0 | 0 | 127.6139 | 0 | 116.1269 | 2.4887 | 46.6614 | 116.1269 | 2.4887 | 46.6614 | 128.8681 | 2.7618 | 46.6614 | 16.13%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 75 | 64 | 376.72 | 96.88% | 2.523% | 0.5996% | 90.3146 | 0 | 0 | 90.3146 | 0 | 82.1851 | 3.9819 | 20.6394 | 82.1851 | 3.9819 | 20.6394 | 91.2022 | 4.4188 | 20.6394 | 23.97%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 46 | 4437.6588 | 97.91% | 1.769% | 0.321% | 93.0355 | 0 | 0 | 93.0355 | 0 | 84.661 | 2.862 | 29.5808 | 84.661 | 2.862 | 29.5808 | 93.9499 | 3.176 | 29.5808 | 2.096%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 623 | 317 | 4437.6588 | 97.91% | 1.769% | 0.321% | 641.136 | 0 | 0 | 641.136 | 0 | 583.425 | 19.7231 | 29.5808 | 583.425 | 19.7231 | 29.5808 | 647.4371 | 21.8871 | 29.5808 | 14.45%
2027 | 240 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 1 | 960.3446 | 65.96% | 33.81% | 0.2324% | 1.5701 | 0 | 0 | 1.5701 | 0 | 1.4287 | 0.062218 | 22.9633 | 1.4287 | 0.062218 | 22.9633 | 1.5855 | 0.069044 | 22.9633 | 0.1635%
2027 | 240 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 136 | 41 | 962.1527 | 99.5% | 0% | 0.4991% | 83.6978 | 0 | 0 | 83.6978 | 0 | 76.1638 | 2.5509 | 29.8572 | 76.1638 | 2.5509 | 29.8572 | 84.5204 | 2.8308 | 29.8572 | 8.699%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | Tier-3---2 | 269 | 189 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 755.4422 | 0 | 0 | 755.4422 | 0 | 687.4421 | 11.7592 | 58.46 | 687.4421 | 11.7592 | 58.46 | 762.8667 | 13.0494 | 58.46 | 20.19%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 264 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 789.8708 | 0 | 0 | 789.8708 | 0 | 718.7717 | 16.4255 | 43.7594 | 718.7717 | 16.4255 | 43.7594 | 797.6337 | 18.2277 | 43.7594 | 21.55%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 2 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 3.0065 | 0 | 0 | 3.0065 | 0 | 2.7359 | 0.12444 | 21.986 | 2.7359 | 0.12444 | 21.986 | 3.036 | 0.13809 | 21.986 | 0.238%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 22 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 33.0712 | 0 | 0 | 33.0712 | 0 | 30.0944 | 1.3688 | 21.986 | 30.0944 | 1.3688 | 21.986 | 33.3962 | 1.519 | 21.986 | 2.618%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 82 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 123.2654 | 0 | 0 | 123.2654 | 0 | 112.1699 | 5.1019 | 21.986 | 112.1699 | 5.1019 | 21.986 | 124.4769 | 5.6616 | 21.986 | 9.759%
2027 | 240 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 1 | 406.8184 | 64.36% | 35.02% | 0.6193% | 0.8728 | 0 | 0 | 0.8728 | 0 | 0.79424 | 0.062218 | 12.7655 | 0.79424 | 0.062218 | 12.7655 | 0.88138 | 0.069044 | 12.7655 | 0.2145%
2027 | 240 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 136 | 12 | 962.1527 | 99.5% | 0% | 0.4991% | 24.4969 | 0 | 0 | 24.4969 | 0 | 22.2919 | 0.74662 | 29.8572 | 22.2919 | 0.74662 | 29.8572 | 24.7377 | 0.82853 | 29.8572 | 2.546%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | Tier-2---3 | 117 | 55 | 960.3446 | 65.96% | 33.81% | 0.2324% | 86.353 | 0 | 0 | 86.353 | 0 | 78.58 | 3.422 | 22.9633 | 78.58 | 3.422 | 22.9633 | 87.2016 | 3.7974 | 22.9633 | 8.992%
2027 | 242 | 242-1427F | Tier-2 | Tier-2---20 | Tier-2---19 | 5 | 3 | 24.991 | 71.07% | 28.66% | 0.2708% | 3.0905 | 0 | 0 | 3.0905 | 0 | 2.8123 | 0.18665 | 15.0671 | 2.8123 | 0.18665 | 15.0671 | 3.1209 | 0.20713 | 15.0671 | 12.37%
2027 | 242 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 2 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 3.0065 | 0 | 0 | 3.0065 | 0 | 2.7359 | 0.12444 | 21.986 | 2.7359 | 0.12444 | 21.986 | 3.036 | 0.13809 | 21.986 | 0.238%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 1 | 406.8184 | 64.36% | 35.02% | 0.6193% | 0.8728 | 0 | 0 | 0.8728 | 0 | 0.79424 | 0.062218 | 12.7655 | 0.79424 | 0.062218 | 12.7655 | 0.88138 | 0.069044 | 12.7655 | 0.2145%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | Tier-2---5 | 87 | 33 | 406.8184 | 64.36% | 35.02% | 0.6193% | 28.8025 | 0 | 0 | 28.8025 | 0 | 26.2099 | 2.0532 | 12.7655 | 26.2099 | 2.0532 | 12.7655 | 29.0856 | 2.2785 | 12.7655 | 7.08%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | Tier-2---4 | 197 | 16 | 295.5508 | 37.5% | 61.39% | 1.106% | 2.6107 | 0 | 0 | 2.6107 | 0 | 2.3757 | 0.99549 | 2.3865 | 2.3757 | 0.99549 | 2.3865 | 2.6364 | 1.1047 | 2.3865 | 0.8833%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 185 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 394.0367 | 0 | 0 | 394.0367 | 0 | 358.5681 | 11.5103 | 31.1519 | 358.5681 | 11.5103 | 31.1519 | 397.9093 | 12.7732 | 31.1519 | 11.63%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 1 | 1438.4419 | 90% | 9.47% | 0.5268% | 1.2391 | 0 | 0 | 1.2391 | 0 | 1.1276 | 0.062218 | 18.1228 | 1.1276 | 0.062218 | 18.1228 | 1.2513 | 0.069044 | 18.1228 | 0.08614%
2027 | 246 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 1 | 379.7423 | 70.28% | 29.01% | 0.71% | 0.85995 | 0 | 0 | 0.85995 | 0 | 0.78254 | 0.062218 | 12.5775 | 0.78254 | 0.062218 | 12.5775 | 0.8684 | 0.069044 | 12.5775 | 0.2265%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | Tier-3---2 | 227 | 139 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 223.4787 | 0 | 0 | 223.4787 | 0 | 203.3626 | 8.6483 | 23.5148 | 203.3626 | 8.6483 | 23.5148 | 225.675 | 9.5972 | 23.5148 | 16.43%
2027 | 247 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 2 | 1438.4419 | 90% | 9.47% | 0.5268% | 2.4782 | 0 | 0 | 2.4782 | 0 | 2.2551 | 0.12444 | 18.1228 | 2.2551 | 0.12444 | 18.1228 | 2.5026 | 0.13809 | 18.1228 | 0.1723%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 5 | 379.7423 | 70.28% | 29.01% | 0.71% | 4.2998 | 0 | 0 | 4.2998 | 0 | 3.9127 | 0.31109 | 12.5775 | 3.9127 | 0.31109 | 12.5775 | 4.342 | 0.34522 | 12.5775 | 1.132%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 11 | 379.7423 | 70.28% | 29.01% | 0.71% | 9.4595 | 0 | 0 | 9.4595 | 0 | 8.608 | 0.6844 | 12.5775 | 8.608 | 0.6844 | 12.5775 | 9.5524 | 0.75949 | 12.5775 | 2.491%
2027 | 248 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 238 | 6 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 9.0194 | 0 | 0 | 9.0194 | 0 | 8.2076 | 0.37331 | 21.986 | 8.2076 | 0.37331 | 21.986 | 9.1081 | 0.41427 | 21.986 | 0.7141%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | Tier-2---6 | 136 | 9 | 962.1527 | 99.5% | 0% | 0.4991% | 18.3727 | 0 | 0 | 18.3727 | 0 | 16.7189 | 0.55996 | 29.8572 | 16.7189 | 0.55996 | 29.8572 | 18.5533 | 0.6214 | 29.8572 | 1.91%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | Tier-2---12 | 98 | 54 | 49.4853 | 86.66% | 6.71% | 6.626% | 6.853 | 0 | 0 | 6.853 | 0 | 6.2362 | 3.3598 | 1.8561 | 6.2362 | 3.3598 | 1.8561 | 6.9204 | 3.7284 | 1.8561 | 13.85%
2027 | 260 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 86 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 147.3481 | 0 | 0 | 147.3481 | 0 | 134.0848 | 5.3507 | 25.0591 | 134.0848 | 5.3507 | 25.0591 | 148.7963 | 5.9378 | 25.0591 | 10.69%
2027 | 260 | 1162-363 | Tier-2 | Tier-2---13 | Tier-2---8 | 37 | 30 | 247.9994 | 97.75% | 1.792% | 0.4608% | 56.9994 | 0 | 0 | 56.9994 | 0 | 51.8687 | 1.8665 | 27.7887 | 51.8687 | 1.8665 | 27.7887 | 57.5596 | 2.0713 | 27.7887 | 22.98%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | Tier-3---1 | 109 | 28 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 389.0912 | 0 | 0 | 389.0912 | 0 | 354.0677 | 1.7421 | 203.2417 | 354.0677 | 1.7421 | 203.2417 | 392.9152 | 1.9332 | 203.2417 | 7.342%
2027 | 283 | CB 283 | Tier-3 | Tier-3---21 | Tier-3---11 | 2 | 2 | 6.0451 | 99.41% | 0% | 0.5857% | 1.7428 | 0 | 0 | 1.7428 | 0 | 1.5859 | 0.12444 | 12.7451 | 1.5859 | 0.12444 | 12.7451 | 1.76 | 0.13809 | 12.7451 | 28.83%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | Tier-2---2 | 43 | 23 | 550.61 | 92.88% | 6.93% | 0.1872% | 79.3295 | 0 | 0 | 79.3295 | 0 | 72.1888 | 1.431 | 50.4459 | 72.1888 | 1.431 | 50.4459 | 80.1091 | 1.588 | 50.4459 | 14.41%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 15 | 754.1323 | 92.41% | 6.882% | 0.7076% | 12.126 | 0 | 0 | 12.126 | 0 | 11.0345 | 0.93327 | 11.8235 | 11.0345 | 0.93327 | 11.8235 | 12.2452 | 1.0357 | 11.8235 | 1.608%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | Tier-2---1 | 53 | 24 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 287.8926 | 0 | 0 | 287.8926 | 0 | 261.9783 | 1.4932 | 175.444 | 261.9783 | 1.4932 | 175.444 | 290.722 | 1.6571 | 175.444 | 11.96%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | Tier-2---1 | 109 | 7 | 4762.848 | 95.55% | 4.384% | 0.07015% | 84.7515 | 0 | 0 | 84.7515 | 0 | 77.1228 | 0.43553 | 177.0798 | 77.1228 | 0.43553 | 177.0798 | 85.5845 | 0.48331 | 177.0798 | 1.779%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | Tier-2---12 | 14 | 7 | 46.1951 | 84.69% | 14.76% | 0.5474% | 5.673 | 0 | 0 | 5.673 | 0 | 5.1623 | 0.43553 | 11.8531 | 5.1623 | 0.43553 | 11.8531 | 5.7287 | 0.48331 | 11.8531 | 12.28%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 15 | 5 | 15.6056 | 49.38% | 48.09% | 2.529% | 0.74497 | 0 | 0 | 0.74497 | 0 | 0.67791 | 0.31109 | 2.1791 | 0.67791 | 0.31109 | 2.1791 | 0.75229 | 0.34522 | 2.1791 | 4.774%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | Tier-2---9 | 14 | 12 | 278.652 | 16.28% | 83.57% | 0.1501% | 11.2762 | 0 | 0 | 11.2762 | 0 | 10.2611 | 0.74662 | 13.7436 | 10.2611 | 0.74662 | 13.7436 | 11.387 | 0.82853 | 13.7436 | 4.047%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 62 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.34476 | 0 | 0 | 0.34476 | 0 | 0.31373 | 3.8575 | 0.081329 | 0.31373 | 3.8575 | 0.081329 | 0.34815 | 4.2807 | 0.081329 | 0.2157%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | Tier-2---9 | 53 | 15 | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.025109 | 0 | 0 | 0.025109 | 0 | 0.022849 | 0.93327 | 0.024482 | 0.022849 | 0.93327 | 0.024482 | 0.025356 | 1.0357 | 0.024482 | 0.01242%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | Tier-2---1 | 565 | 128 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 225.9636 | 0 | 0 | 225.9636 | 0 | 205.6238 | 7.9639 | 25.8195 | 205.6238 | 7.9639 | 25.8195 | 228.1843 | 8.8377 | 25.8195 | 6.273%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | Tier-2---1 | 56 | 9 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 116.4451 | 0 | 0 | 116.4451 | 0 | 105.9635 | 0.55996 | 189.2336 | 105.9635 | 0.55996 | 189.2336 | 117.5896 | 0.6214 | 189.2336 | 4.623%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | Tier-2---2 | 226 | 11 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 104.2839 | 0 | 0 | 104.2839 | 0 | 94.8969 | 0.6844 | 138.6577 | 94.8969 | 0.6844 | 138.6577 | 105.3088 | 0.75949 | 138.6577 | 1.39%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 19 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 203.5605 | 0 | 0 | 203.5605 | 0 | 185.2373 | 1.1821 | 156.6965 | 185.2373 | 1.1821 | 156.6965 | 205.5611 | 1.3118 | 156.6965 | 1.803%
2027 | 355 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 1 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 10.5024 | 0 | 0 | 10.5024 | 0 | 9.557 | 0.062218 | 153.6057 | 9.557 | 0.062218 | 153.6057 | 10.6056 | 0.069044 | 153.6057 | 0.1719%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | Tier-2---2 | 216 | 25 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 179.1144 | 0 | 0 | 179.1144 | 0 | 162.9916 | 1.5554 | 104.7876 | 162.9916 | 1.5554 | 104.7876 | 180.8747 | 1.7261 | 104.7876 | 3.294%
2027 | 356 | CB 355 | Tier-2 | Tier-2---3 | Tier-2---1 | 302 | 1 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 10.7137 | 0 | 0 | 10.7137 | 0 | 9.7493 | 0.062218 | 156.6965 | 9.7493 | 0.062218 | 156.6965 | 10.819 | 0.069044 | 156.6965 | 0.09491%
2027 | 356 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 1 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 2.1299 | 0 | 0 | 2.1299 | 0 | 1.9382 | 0.062218 | 31.1519 | 1.9382 | 0.062218 | 31.1519 | 2.1509 | 0.069044 | 31.1519 | 0.06289%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | Tier-3---1 | 736 | 258 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 1591.4049 | 0 | 0 | 1591.4049 | 0 | 1448.1568 | 16.0522 | 90.2153 | 1448.1568 | 16.0522 | 90.2153 | 1607.0451 | 17.8134 | 90.2153 | 9.938%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 2 | 6.8062 | 99.1% | 0% | 0.8997% | 1.304 | 0 | 0 | 1.304 | 0 | 1.1866 | 0.12444 | 9.5362 | 1.1866 | 0.12444 | 9.5362 | 1.3168 | 0.13809 | 9.5362 | 19.16%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | Tier-3---1 | 48 | 44 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 1351.0865 | 0 | 0 | 1351.0865 | 0 | 1229.4703 | 2.7376 | 449.107 | 1229.4703 | 2.7376 | 449.107 | 1364.3649 | 3.038 | 449.107 | 26.5%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | Tier-3---1 | 271 | 2 | 16869.708 | 98.79% | 1.184% | 0.02933% | 35.6668 | 0 | 0 | 35.6668 | 0 | 32.4563 | 0.12444 | 260.8273 | 32.4563 | 0.12444 | 260.8273 | 36.0173 | 0.13809 | 260.8273 | 0.2114%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | Tier-3---1 | 363 | 69 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 950.8759 | 0 | 0 | 950.8759 | 0 | 865.2842 | 4.293 | 201.5553 | 865.2842 | 4.293 | 201.5553 | 960.2211 | 4.7641 | 201.5553 | 5.373%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | Tier-3---1 | 383 | 104 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 797.1922 | 0 | 0 | 797.1922 | 0 | 725.434 | 6.4707 | 112.1112 | 725.434 | 6.4707 | 112.1112 | 805.0269 | 7.1806 | 112.1112 | 7.641%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | Tier-2---1 | 272 | 2 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 24.5213 | 0 | 0 | 24.5213 | 0 | 22.3141 | 0.12444 | 179.3218 | 22.3141 | 0.12444 | 179.3218 | 24.7623 | 0.13809 | 179.3218 | 0.2086%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | Tier-3---1 | 162 | 25 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 262.5596 | 0 | 0 | 262.5596 | 0 | 238.9257 | 1.5554 | 153.6057 | 238.9257 | 1.5554 | 153.6057 | 265.14 | 1.7261 | 153.6057 | 4.297%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | Tier-2---5 | 21 | 4 | 599.5834 | 97.21% | 2.746% | 0.04768% | 32.1945 | 0 | 0 | 32.1945 | 0 | 29.2966 | 0.24887 | 117.7176 | 29.2966 | 0.24887 | 117.7176 | 32.5109 | 0.27618 | 117.7176 | 5.369%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | Tier-3---1 | 344 | 66 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 2062.7278 | 0 | 0 | 2062.7278 | 0 | 1877.0542 | 4.1064 | 457.1065 | 1877.0542 | 4.1064 | 457.1065 | 2083.0002 | 4.5569 | 457.1065 | 5.486%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | Tier-3---3 | 21 | 2 | 861.4334 | 18.88% | 81.11% | 0.0161% | 4.4913 | 0 | 0 | 4.4913 | 0 | 4.0871 | 0.12444 | 32.8447 | 4.0871 | 0.12444 | 32.8447 | 4.5355 | 0.13809 | 32.8447 | 0.5214%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | Tier-2---3 | 76 | 41 | 924.8041 | 18.79% | 81.02% | 0.1888% | 27.1822 | 0 | 0 | 27.1822 | 0 | 24.7354 | 2.5509 | 9.6966 | 24.7354 | 2.5509 | 9.6966 | 27.4493 | 2.8308 | 9.6966 | 2.939%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 455 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 487.9639 | 0 | 0 | 487.9639 | 0 | 444.0405 | 28.3092 | 15.6854 | 444.0405 | 28.3092 | 15.6854 | 492.7596 | 31.4152 | 15.6854 | 15.56%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | Tier-2---3 | 145 | 5 | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.96069 | 0 | 0 | 0.96069 | 0 | 0.87422 | 0.31109 | 2.8102 | 0.87422 | 0.31109 | 2.8102 | 0.97014 | 0.34522 | 2.8102 | 0.1434%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 83 | 6370.0414 | 98.47% | 1.262% | 0.272% | 176.3723 | 0 | 0 | 176.3723 | 0 | 160.4964 | 5.1641 | 31.0793 | 160.4964 | 5.1641 | 31.0793 | 178.1057 | 5.7307 | 31.0793 | 2.769%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | Tier-3---3 | 84 | 58 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 686.4973 | 0 | 0 | 686.4973 | 0 | 624.7032 | 3.6086 | 173.1132 | 624.7032 | 3.6086 | 173.1132 | 693.2441 | 4.0046 | 173.1132 | 19.51%
2027 | 441 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 1 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 9.1326 | 0 | 0 | 9.1326 | 0 | 8.3106 | 0.062218 | 133.5718 | 8.3106 | 0.062218 | 133.5718 | 9.2224 | 0.069044 | 133.5718 | 0.1736%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | Tier-3---10 | 48 | 49 | 582.1633 | 91.34% | 8.391% | 0.2732% | 157.4117 | 0 | 0 | 157.4117 | 0 | 143.2425 | 3.0487 | 46.9851 | 143.2425 | 3.0487 | 46.9851 | 158.9588 | 3.3832 | 46.9851 | 27.04%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | Tier-3---3 | 133 | 21 | 4750.1268 | 98% | 1.916% | 0.08125% | 213.1612 | 0 | 0 | 213.1612 | 0 | 193.9737 | 1.3066 | 148.4596 | 193.9737 | 1.3066 | 148.4596 | 215.2561 | 1.4499 | 148.4596 | 4.487%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 1 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 15.1389 | 0 | 0 | 15.1389 | 0 | 13.7762 | 0.062218 | 221.4186 | 13.7762 | 0.062218 | 221.4186 | 15.2877 | 0.069044 | 221.4186 | 0.283%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | Tier-3---3 | 101 | 90 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 1362.5019 | 0 | 0 | 1362.5019 | 0 | 1239.8582 | 5.5996 | 221.4186 | 1239.8582 | 5.5996 | 221.4186 | 1375.8925 | 6.214 | 221.4186 | 25.47%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 94 | 43 | 1133.0808 | 94.08% | 5.666% | 0.2577% | 141.4093 | 0 | 0 | 141.4093 | 0 | 128.6805 | 2.6754 | 48.0982 | 128.6805 | 2.6754 | 48.0982 | 142.7991 | 2.9689 | 48.0982 | 12.48%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | Tier-3---19 | 3 | 3 | 88.141 | 1.745% | 98.17% | 0.08447% | 0.446 | 0 | 0 | 0.446 | 0 | 0.40586 | 0.18665 | 2.1744 | 0.40586 | 0.18665 | 2.1744 | 0.45039 | 0.20713 | 2.1744 | 0.506%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | Tier-3---5 | 145 | 49 | 852.9261 | 84.92% | 14.72% | 0.3553% | 70.9857 | 0 | 0 | 70.9857 | 0 | 64.596 | 3.0487 | 21.1882 | 64.596 | 3.0487 | 21.1882 | 71.6834 | 3.3832 | 21.1882 | 8.323%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | Tier-3---10 | 144 | 71 | 526.1263 | 57.95% | 41.57% | 0.4783% | 43.597 | 0 | 0 | 43.597 | 0 | 39.6727 | 4.4175 | 8.9809 | 39.6727 | 4.4175 | 8.9809 | 44.0255 | 4.9021 | 8.9809 | 8.286%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | Tier-3---1 | 763 | 160 | 11572.221 | 88.48% | 11.4% | 0.1243% | 622.64 | 0 | 0 | 622.64 | 0 | 566.5939 | 9.9549 | 56.9163 | 566.5939 | 9.9549 | 56.9163 | 628.7593 | 11.0471 | 56.9163 | 5.38%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 54 | 24 | 704.6091 | 96.62% | 3.132% | 0.2514% | 87.7432 | 0 | 0 | 87.7432 | 0 | 79.8451 | 1.4932 | 53.4714 | 79.8451 | 1.4932 | 53.4714 | 88.6055 | 1.6571 | 53.4714 | 12.45%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | Tier-3---19 | 73 | 26 | 141.3846 | 51% | 48.51% | 0.49% | 7.4478 | 0 | 0 | 7.4478 | 0 | 6.7774 | 1.6177 | 4.1896 | 6.7774 | 1.6177 | 4.1896 | 7.521 | 1.7952 | 4.1896 | 5.268%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 144 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 1133.448 | 0 | 0 | 1133.448 | 0 | 1031.4223 | 8.9594 | 115.122 | 1031.4223 | 8.9594 | 115.122 | 1144.5875 | 9.9424 | 115.122 | 11.77%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 97 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 890.9956 | 0 | 0 | 890.9956 | 0 | 810.7938 | 6.0351 | 134.3455 | 810.7938 | 6.0351 | 134.3455 | 899.7522 | 6.6973 | 134.3455 | 12.29%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 36 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 153.1223 | 0 | 0 | 153.1223 | 0 | 139.3392 | 2.2398 | 62.2093 | 139.3392 | 2.2398 | 62.2093 | 154.6272 | 2.4856 | 62.2093 | 9.549%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 1 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 3.7962 | 0 | 0 | 3.7962 | 0 | 3.4545 | 0.062218 | 55.5231 | 3.4545 | 0.062218 | 55.5231 | 3.8336 | 0.069044 | 55.5231 | 0.1032%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 144 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 806.7668 | 0 | 0 | 806.7668 | 0 | 734.1468 | 8.9594 | 81.9417 | 734.1468 | 8.9594 | 81.9417 | 814.6957 | 9.9424 | 81.9417 | 7.597%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 147 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 268.1163 | 0 | 0 | 268.1163 | 0 | 243.9821 | 9.146 | 26.6763 | 243.9821 | 9.146 | 26.6763 | 270.7513 | 10.1495 | 26.6763 | 15.18%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | Tier-2---5 | 97 | 1 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 4.2534 | 0 | 0 | 4.2534 | 0 | 3.8705 | 0.062218 | 62.2093 | 3.8705 | 0.062218 | 62.2093 | 4.2952 | 0.069044 | 62.2093 | 0.2652%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 125 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 474.5303 | 0 | 0 | 474.5303 | 0 | 431.8161 | 7.7772 | 55.5231 | 431.8161 | 7.7772 | 55.5231 | 479.194 | 8.6305 | 55.5231 | 12.9%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 494 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 950.7986 | 0 | 0 | 950.7986 | 0 | 865.2138 | 30.7357 | 28.1502 | 865.2138 | 30.7357 | 28.1502 | 960.143 | 34.1079 | 28.1502 | 21.51%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 25 | 13 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 198.2268 | 0 | 0 | 198.2268 | 0 | 180.3837 | 0.80883 | 223.0173 | 180.3837 | 0.80883 | 223.0173 | 200.175 | 0.89758 | 223.0173 | 14.66%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 29 | 520.639 | 76.18% | 22.78% | 1.038% | 16.5138 | 0 | 0 | 16.5138 | 0 | 15.0274 | 1.8043 | 8.3285 | 15.0274 | 1.8043 | 8.3285 | 16.6761 | 2.0023 | 8.3285 | 3.172%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 30 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 101.284 | 0 | 0 | 101.284 | 0 | 92.1671 | 1.8665 | 49.3786 | 92.1671 | 1.8665 | 49.3786 | 102.2794 | 2.0713 | 49.3786 | 1.112%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 9 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 33.3276 | 0 | 0 | 33.3276 | 0 | 30.3277 | 0.55996 | 54.1604 | 30.3277 | 0.55996 | 54.1604 | 33.6552 | 0.6214 | 54.1604 | 0.5904%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 194 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 615.1254 | 0 | 0 | 615.1254 | 0 | 559.7558 | 12.0703 | 46.3747 | 559.7558 | 12.0703 | 46.3747 | 621.1708 | 13.3946 | 46.3747 | 9.14%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | Tier-3---3 | 72 | 55 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 321.2654 | 0 | 0 | 321.2654 | 0 | 292.3471 | 3.422 | 85.432 | 292.3471 | 3.422 | 85.432 | 324.4228 | 3.7974 | 85.432 | 21.48%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | Tier-3---1 | 165 | 101 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 922.3944 | 0 | 0 | 922.3944 | 0 | 839.3664 | 6.284 | 133.5718 | 839.3664 | 6.284 | 133.5718 | 931.4597 | 6.9735 | 133.5718 | 17.53%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | Tier-3---3 | 161 | 56 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 223.5986 | 0 | 0 | 223.5986 | 0 | 203.4716 | 3.4842 | 58.3983 | 203.4716 | 3.4842 | 58.3983 | 225.7961 | 3.8665 | 58.3983 | 9.638%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | Tier-2---14 | 11 | 10 | 88.0149 | 97.35% | 2.233% | 0.4157% | 22.5893 | 0 | 0 | 22.5893 | 0 | 20.556 | 0.62218 | 33.0387 | 20.556 | 0.62218 | 33.0387 | 22.8113 | 0.69044 | 33.0387 | 25.67%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | Tier-2---3 | 231 | 1 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 1.7134 | 0 | 0 | 1.7134 | 0 | 1.5591 | 0.062218 | 25.0591 | 1.5591 | 0.062218 | 25.0591 | 1.7302 | 0.069044 | 25.0591 | 0.1243%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | Tier-2---2 | 142 | 125 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 1321.5852 | 0 | 0 | 1321.5852 | 0 | 1202.6245 | 7.7772 | 154.6338 | 1202.6245 | 7.7772 | 154.6338 | 1334.5737 | 8.6305 | 154.6338 | 25.1%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | Tier-3---1 | 534 | 96 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 867.2617 | 0 | 0 | 867.2617 | 0 | 789.1963 | 5.9729 | 132.1291 | 789.1963 | 5.9729 | 132.1291 | 875.7851 | 6.6283 | 132.1291 | 5.181%
2027 | 470 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 1 | 3349.7594 | 92.58% | 7.304% | 0.116% | 6.3784 | 0 | 0 | 6.3784 | 0 | 5.8042 | 0.062218 | 93.289 | 5.8042 | 0.062218 | 93.289 | 6.4411 | 0.069044 | 93.289 | 0.1904%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 381 | 48 | 6922.0493 | 95.49% | 4.388% | 0.1268% | 241.4829 | 0 | 0 | 241.4829 | 0 | 219.7461 | 2.9865 | 73.5808 | 219.7461 | 2.9865 | 73.5808 | 243.8561 | 3.3141 | 73.5808 | 3.489%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | Tier-2---1 | 408 | 14 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 25.3986 | 0 | 0 | 25.3986 | 0 | 23.1123 | 0.87105 | 26.5339 | 23.1123 | 0.87105 | 26.5339 | 25.6482 | 0.96662 | 26.5339 | 0.9628%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | Tier-2---1 | 145 | 43 | 1632.8033 | 98.29% | 1.436% | 0.2778% | 138.0149 | 0 | 0 | 138.0149 | 0 | 125.5917 | 2.6754 | 46.9437 | 125.5917 | 2.6754 | 46.9437 | 139.3713 | 2.9689 | 46.9437 | 8.453%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | Tier-2---4 | 408 | 22 | 748.333 | 77.34% | 21.7% | 0.962% | 9.0499 | 0 | 0 | 9.0499 | 0 | 8.2353 | 1.3688 | 6.0165 | 8.2353 | 1.3688 | 6.0165 | 9.1389 | 1.519 | 6.0165 | 1.209%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | Tier-3---1 | 315 | 12 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 121.2446 | 0 | 0 | 121.2446 | 0 | 110.3309 | 0.74662 | 147.7748 | 110.3309 | 0.74662 | 147.7748 | 122.4362 | 0.82853 | 147.7748 | 1.068%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 101 | 810.9996 | 89.31% | 10.24% | 0.4457% | 106.6116 | 0 | 0 | 106.6116 | 0 | 97.0151 | 6.284 | 15.4384 | 97.0151 | 6.284 | 15.4384 | 107.6594 | 6.9735 | 15.4384 | 13.15%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | Tier-3---1 | 335 | 3 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 21.5309 | 0 | 0 | 21.5309 | 0 | 19.5928 | 0.18665 | 104.9689 | 19.5928 | 0.18665 | 104.9689 | 21.7425 | 0.20713 | 104.9689 | 0.254%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 1 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 8.178 | 0 | 0 | 8.178 | 0 | 7.4419 | 0.062218 | 119.6098 | 7.4419 | 0.062218 | 119.6098 | 8.2584 | 0.069044 | 119.6098 | 0.09386%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | Tier-3---2 | 307 | 165 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 1349.3709 | 0 | 0 | 1349.3709 | 0 | 1227.9091 | 10.266 | 119.6098 | 1227.9091 | 10.266 | 119.6098 | 1362.6324 | 11.3923 | 119.6098 | 15.49%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 70 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 314.7078 | 0 | 0 | 314.7078 | 0 | 286.3798 | 4.3553 | 65.755 | 286.3798 | 4.3553 | 65.755 | 317.8008 | 4.8331 | 65.755 | 5.601%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | Tier-2---2 | 358 | 1 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 4.4958 | 0 | 0 | 4.4958 | 0 | 4.0911 | 0.062218 | 65.755 | 4.0911 | 0.062218 | 65.755 | 4.54 | 0.069044 | 65.755 | 0.08002%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | Tier-2---2 | 437 | 135 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 799.765 | 0 | 0 | 799.765 | 0 | 727.7752 | 8.3994 | 86.6459 | 727.7752 | 8.3994 | 86.6459 | 807.625 | 9.321 | 86.6459 | 8.874%
2027 | 521 | CB 521 | Tier-2 | Tier-2---20 | Tier-2---21 | 14 | 10 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.42728 | 0 | 0 | 0.42728 | 0 | 0.38882 | 0.62218 | 0.62493 | 0.38882 | 0.62218 | 0.62493 | 0.43148 | 0.69044 | 0.62493 | 3.479%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 8 | 112.7117 | 43.02% | 55.81% | 1.165% | 1.7579 | 0 | 0 | 1.7579 | 0 | 1.5997 | 0.49774 | 3.2138 | 1.5997 | 0.49774 | 3.2138 | 1.7752 | 0.55235 | 3.2138 | 1.56%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | Tier-2---8 | 64 | 26 | 112.7117 | 43.02% | 55.81% | 1.165% | 5.7132 | 0 | 0 | 5.7132 | 0 | 5.1989 | 1.6177 | 3.2138 | 5.1989 | 1.6177 | 3.2138 | 5.7693 | 1.7952 | 3.2138 | 5.069%
2027 | 522 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 6 | 305.5692 | 37.2% | 61.32% | 1.484% | 0.76361 | 0 | 0 | 0.76361 | 0 | 0.69488 | 0.37331 | 1.8614 | 0.69488 | 0.37331 | 1.8614 | 0.77112 | 0.41427 | 1.8614 | 0.2499%
2027 | 522 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 1 | 2730.9177 | 98.3% | 1.373% | 0.325% | 2.1807 | 0 | 0 | 2.1807 | 0 | 1.9844 | 0.062218 | 31.8948 | 1.9844 | 0.062218 | 31.8948 | 2.2022 | 0.069044 | 31.8948 | 0.07985%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 41 | 116.9577 | 22.53% | 76.17% | 1.295% | 3.3694 | 0 | 0 | 3.3694 | 0 | 3.0661 | 2.5509 | 1.202 | 3.0661 | 2.5509 | 1.202 | 3.4025 | 2.8308 | 1.202 | 2.881%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 1 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 2.6029 | 0 | 0 | 2.6029 | 0 | 2.3686 | 0.062218 | 38.0693 | 2.3686 | 0.062218 | 38.0693 | 2.6285 | 0.069044 | 38.0693 | 0.04615%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | Tier-2---2 | 606 | 353 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 918.8197 | 0 | 0 | 918.8197 | 0 | 836.1134 | 21.9629 | 38.0693 | 836.1134 | 21.9629 | 38.0693 | 927.8498 | 24.3726 | 38.0693 | 16.29%
2027 | 522 | 521-1819R | Tier-2 | Tier-2---9 | Tier-2---2 | 199 | 1 | 810.9996 | 89.31% | 10.24% | 0.4457% | 1.0556 | 0 | 0 | 1.0556 | 0 | 0.96055 | 0.062218 | 15.4384 | 0.96055 | 0.062218 | 15.4384 | 1.0659 | 0.069044 | 15.4384 | 0.1302%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | Tier-2---2 | 253 | 129 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 142.1675 | 0 | 0 | 142.1675 | 0 | 129.3704 | 8.0261 | 16.1187 | 129.3704 | 8.0261 | 16.1187 | 143.5647 | 8.9067 | 16.1187 | 13.23%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | Tier-2---4 | 199 | 38 | 305.199 | 11.7% | 87.21% | 1.095% | 1.9768 | 0 | 0 | 1.9768 | 0 | 1.7989 | 2.3643 | 0.76086 | 1.7989 | 2.3643 | 0.76086 | 1.9962 | 2.6237 | 0.76086 | 0.6477%
2027 | 523 | CB 523 | Tier-2 | Tier-2---13 | Tier-2---4 | 259 | 104 | 305.5692 | 37.2% | 61.32% | 1.484% | 13.236 | 0 | 0 | 13.236 | 0 | 12.0446 | 6.4707 | 1.8614 | 12.0446 | 6.4707 | 1.8614 | 13.3661 | 7.1806 | 1.8614 | 4.332%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | Tier-2---11 | 9 | 9 | 49.4293 | 99.41% | 0% | 0.5897% | 14.25 | 0 | 0 | 14.25 | 0 | 12.9673 | 0.55996 | 23.1575 | 12.9673 | 0.55996 | 23.1575 | 14.39 | 0.6214 | 23.1575 | 28.83%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 303 | 18774.394 | 95.55% | 4.388% | 0.06321% | 3960.5037 | 0 | 0 | 3960.5037 | 0 | 3604.0044 | 18.852 | 191.1733 | 3604.0044 | 18.852 | 191.1733 | 3999.4274 | 20.9204 | 191.1733 | 21.1%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 514 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 5065.2696 | 0 | 0 | 5065.2696 | 0 | 4609.3263 | 31.98 | 144.1315 | 4609.3263 | 31.98 | 144.1315 | 5115.0508 | 35.4888 | 144.1315 | 19.68%
2027 | 599 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 1 | 8606.9717 | 99.86% | 0% | 0.1411% | 4.4749 | 0 | 0 | 4.4749 | 0 | 4.0721 | 0.062218 | 65.4484 | 4.0721 | 0.062218 | 65.4484 | 4.5188 | 0.069044 | 65.4484 | 0.05199%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 106 | 4323.2442 | 99.81% | 0% | 0.1903% | 359.4678 | 0 | 0 | 359.4678 | 0 | 327.1108 | 6.5951 | 49.5991 | 327.1108 | 6.5951 | 49.5991 | 363.0006 | 7.3187 | 49.5991 | 8.315%
2027 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 24 | 20 | 42.5113 | 97.49% | 0.5175% | 1.991% | 10.0159 | 0 | 0 | 10.0159 | 0 | 9.1143 | 1.2444 | 7.3245 | 9.1143 | 1.2444 | 7.3245 | 10.1143 | 1.3809 | 7.3245 | 23.56%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 53 | 1 | 55.0677 | 92.66% | 4.028% | 3.312% | 0.2792 | 0 | 0 | 0.2792 | 0 | 0.25407 | 0.062218 | 4.0835 | 0.25407 | 0.062218 | 4.0835 | 0.28194 | 0.069044 | 4.0835 | 0.507%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 53 | 39 | 55.0677 | 92.66% | 4.028% | 3.312% | 10.8887 | 0 | 0 | 10.8887 | 0 | 9.9086 | 2.4265 | 4.0835 | 9.9086 | 2.4265 | 4.0835 | 10.9957 | 2.6927 | 4.0835 | 19.77%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 33 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 158.2389 | 0 | 0 | 158.2389 | 0 | 143.9952 | 2.0532 | 70.1324 | 143.9952 | 2.0532 | 70.1324 | 159.7941 | 2.2785 | 70.1324 | 1.733%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 708 | 24 | 8569.0681 | 95.07% | 4.755% | 0.1724% | 80.0875 | 0 | 0 | 80.0875 | 0 | 72.8785 | 1.4932 | 48.8059 | 72.8785 | 1.4932 | 48.8059 | 80.8745 | 1.6571 | 48.8059 | 0.9346%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | Tier-2---1 | 141 | 11 | 3349.7594 | 92.58% | 7.304% | 0.116% | 70.1623 | 0 | 0 | 70.1623 | 0 | 63.8467 | 0.6844 | 93.289 | 63.8467 | 0.6844 | 93.289 | 70.8518 | 0.75949 | 93.289 | 2.095%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | Tier-2---17 | 13 | 6 | 12.4137 | 98.83% | 0% | 1.166% | 1.6422 | 0 | 0 | 1.6422 | 0 | 1.4943 | 0.37331 | 4.003 | 1.4943 | 0.37331 | 4.003 | 1.6583 | 0.41427 | 4.003 | 13.23%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | Tier-2---11 | 17 | 17 | 139.955 | 99.63% | 0% | 0.3714% | 40.4362 | 0 | 0 | 40.4362 | 0 | 36.7964 | 1.0577 | 34.7889 | 36.7964 | 1.0577 | 34.7889 | 40.8336 | 1.1738 | 34.7889 | 28.89%
2027 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 12 | 8 | 42.6475 | 99.43% | 0% | 0.5747% | 8.1978 | 0 | 0 | 8.1978 | 0 | 7.4599 | 0.49774 | 14.9874 | 7.4599 | 0.49774 | 14.9874 | 8.2784 | 0.55235 | 14.9874 | 19.22%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | Tier-2---4 | 16 | 5 | 330.3488 | 99.39% | 0.4551% | 0.1546% | 29.7553 | 0 | 0 | 29.7553 | 0 | 27.077 | 0.31109 | 87.0391 | 27.077 | 0.31109 | 87.0391 | 30.0478 | 0.34522 | 87.0391 | 9.007%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 31 | 8606.9717 | 99.86% | 0% | 0.1411% | 138.7208 | 0 | 0 | 138.7208 | 0 | 126.234 | 1.9288 | 65.4484 | 126.234 | 1.9288 | 65.4484 | 140.0841 | 2.1404 | 65.4484 | 1.612%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 83 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 621.8047 | 0 | 0 | 621.8047 | 0 | 565.8338 | 5.1641 | 109.5709 | 565.8338 | 5.1641 | 109.5709 | 627.9158 | 5.7307 | 109.5709 | 18.25%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 252 | 10 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 17.5585 | 0 | 0 | 17.5585 | 0 | 15.978 | 0.62218 | 25.6807 | 15.978 | 0.62218 | 25.6807 | 17.7311 | 0.69044 | 25.6807 | 0.8816%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 17 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 104.9605 | 0 | 0 | 104.9605 | 0 | 95.5126 | 1.0577 | 90.3018 | 95.5126 | 1.0577 | 90.3018 | 105.992 | 1.1738 | 90.3018 | 6.342%
2027 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 12 | 62.492 | 96.91% | 0.773% | 2.32% | 4.7897 | 0 | 0 | 4.7897 | 0 | 4.3586 | 0.74662 | 5.8378 | 4.3586 | 0.74662 | 5.8378 | 4.8368 | 0.82853 | 5.8378 | 7.664%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 74 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 557.4359 | 0 | 0 | 557.4359 | 0 | 507.259 | 4.6041 | 110.1749 | 507.259 | 4.6041 | 110.1749 | 562.9143 | 5.1093 | 110.1749 | 10.77%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | Tier-3---1 | 199 | 76 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 708.0805 | 0 | 0 | 708.0805 | 0 | 644.3436 | 4.7286 | 136.2663 | 644.3436 | 4.7286 | 136.2663 | 715.0395 | 5.2474 | 136.2663 | 10.86%
2027 | 974 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 344 | 1 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 2.9919 | 0 | 0 | 2.9919 | 0 | 2.7226 | 0.062218 | 43.7594 | 2.7226 | 0.062218 | 43.7594 | 3.0213 | 0.069044 | 43.7594 | 0.08162%
2027 | 974 | 973-1226R | Tier-3 | Tier-3---10 | Tier-3---1 | 194 | 1 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 7.5329 | 0 | 0 | 7.5329 | 0 | 6.8549 | 0.062218 | 110.1749 | 6.8549 | 0.062218 | 110.1749 | 7.607 | 0.069044 | 110.1749 | 0.1455%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | Tier-3---1 | 389 | 305 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 744.1095 | 0 | 0 | 744.1095 | 0 | 677.1295 | 18.9765 | 35.6826 | 677.1295 | 18.9765 | 35.6826 | 751.4226 | 21.0585 | 35.6826 | 21.3%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | Tier-3---1 | 134 | 16 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 244.9861 | 0 | 0 | 244.9861 | 0 | 222.934 | 0.99549 | 223.9447 | 222.934 | 0.99549 | 223.9447 | 247.3938 | 1.1047 | 223.9447 | 3.447%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | Tier-2---2 | 29 | 2 | 626.8618 | 65.87% | 33.98% | 0.153% | 8.2581 | 0 | 0 | 8.2581 | 0 | 7.5148 | 0.12444 | 60.3908 | 7.5148 | 0.12444 | 60.3908 | 8.3393 | 0.13809 | 60.3908 | 1.317%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 103 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 831.7487 | 0 | 0 | 831.7487 | 0 | 756.88 | 6.4084 | 118.1066 | 756.88 | 6.4084 | 118.1066 | 839.9231 | 7.1116 | 118.1066 | 18.17%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | Tier-2---5 | 10 | 2 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 23.5239 | 0 | 0 | 23.5239 | 0 | 21.4064 | 0.12444 | 172.0278 | 21.4064 | 0.12444 | 172.0278 | 23.7551 | 0.13809 | 172.0278 | 5.751%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | Tier-2---1 | 146 | 49 | 4222.2471 | 91.41% | 8.486% | 0.103% | 375.6485 | 0 | 0 | 375.6485 | 0 | 341.835 | 3.0487 | 112.1256 | 341.835 | 3.0487 | 112.1256 | 379.3403 | 3.3832 | 112.1256 | 8.897%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | Tier-2---11 | 10 | 10 | 114.5301 | 99.76% | 0% | 0.2395% | 33.1342 | 0 | 0 | 33.1342 | 0 | 30.1517 | 0.62218 | 48.4614 | 30.1517 | 0.62218 | 48.4614 | 33.4598 | 0.69044 | 48.4614 | 28.93%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 82 | 40 | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 405.7243 | 0 | 0 | 405.7243 | 0 | 369.2036 | 2.4887 | 148.351 | 369.2036 | 2.4887 | 148.351 | 409.7117 | 2.7618 | 148.351 | 14.04%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 141 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 792.4296 | 0 | 0 | 792.4296 | 0 | 721.1001 | 8.7727 | 82.1979 | 721.1001 | 8.7727 | 82.1979 | 800.2175 | 9.7352 | 82.1979 | 8.368%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 13 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 109.7881 | 0 | 0 | 109.7881 | 0 | 99.9057 | 0.80883 | 123.5183 | 99.9057 | 0.80883 | 123.5183 | 110.8671 | 0.89758 | 123.5183 | 0.688%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | Tier-2---16 | 16 | 12 | 17.9659 | 86.84% | 10.72% | 2.434% | 3.3934 | 0 | 0 | 3.3934 | 0 | 3.088 | 0.74662 | 4.136 | 3.088 | 0.74662 | 4.136 | 3.4268 | 0.82853 | 4.136 | 18.89%
2027 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | Tier-2---12 | 40 | 1 | 40.9949 | 23.55% | 73.64% | 2.81% | 0.069984 | 0 | 0 | 0.069984 | 0 | 0.063685 | 0.062218 | 1.0236 | 0.063685 | 0.062218 | 1.0236 | 0.070672 | 0.069044 | 1.0236 | 0.1707%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | Tier-2---16 | 4 | 4 | 27.0781 | 12.75% | 86.83% | 0.4178% | 1.0014 | 0 | 0 | 1.0014 | 0 | 0.91122 | 0.24887 | 3.6614 | 0.91122 | 0.24887 | 3.6614 | 1.0112 | 0.27618 | 3.6614 | 3.698%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | Tier-2---21 | 3 | 3 | 6.3934 | 34.35% | 64.55% | 1.103% | 0.63686 | 0 | 0 | 0.63686 | 0 | 0.57953 | 0.18665 | 3.1048 | 0.57953 | 0.18665 | 3.1048 | 0.64312 | 0.20713 | 3.1048 | 9.961%
2027 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | Tier-3---10 | 80 | 18 | 509.5021 | 91.97% | 7.519% | 0.512% | 30.575 | 0 | 0 | 30.575 | 0 | 27.8228 | 1.1199 | 24.8435 | 27.8228 | 1.1199 | 24.8435 | 30.8755 | 1.2428 | 24.8435 | 6.001%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 1 | 2514.2831 | 99.84% | 0% | 0.1648% | 4.3589 | 0 | 0 | 4.3589 | 0 | 3.9666 | 0.062218 | 63.7527 | 3.9666 | 0.062218 | 63.7527 | 4.4018 | 0.069044 | 63.7527 | 0.1734%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | Tier-2---6 | 167 | 25 | 2514.2831 | 99.84% | 0% | 0.1648% | 108.9731 | 0 | 0 | 108.9731 | 0 | 99.164 | 1.5554 | 63.7527 | 99.164 | 1.5554 | 63.7527 | 110.0441 | 1.7261 | 63.7527 | 4.334%
2027 | 1094 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 369 | 1 | 4323.2442 | 99.81% | 0% | 0.1903% | 3.3912 | 0 | 0 | 3.3912 | 0 | 3.086 | 0.062218 | 49.5991 | 3.086 | 0.062218 | 49.5991 | 3.4245 | 0.069044 | 49.5991 | 0.07844%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | Tier-2---3 | 19 | 17 | 788.3757 | 99.4% | 0.5205% | 0.07536% | 203.3437 | 0 | 0 | 203.3437 | 0 | 185.04 | 1.0577 | 174.9449 | 185.04 | 1.0577 | 174.9449 | 205.3422 | 1.1738 | 174.9449 | 25.79%
2027 | 1118 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 13.071 | 0 | 0 | 13.071 | 0 | 11.8944 | 0.062218 | 191.1733 | 11.8944 | 0.062218 | 191.1733 | 13.1994 | 0.069044 | 191.1733 | 0.06962%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | Tier-2---1 | 804 | 334 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 511.9893 | 0 | 0 | 511.9893 | 0 | 465.9033 | 20.7808 | 22.4199 | 465.9033 | 20.7808 | 22.4199 | 517.0211 | 23.0608 | 22.4199 | 10.98%
2027 | 1138 | 396-699R | Tier-2 | Tier-2---5 | Tier-2---1 | 748 | 1 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 1.0724 | 0 | 0 | 1.0724 | 0 | 0.97591 | 0.062218 | 15.6854 | 0.97591 | 0.062218 | 15.6854 | 1.083 | 0.069044 | 15.6854 | 0.03419%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | Tier-2---3 | 291 | 70 | 765.4961 | 75% | 24.28% | 0.7274% | 40.0481 | 0 | 0 | 40.0481 | 0 | 36.4432 | 4.3553 | 8.3676 | 36.4432 | 4.3553 | 8.3676 | 40.4417 | 4.8331 | 8.3676 | 5.232%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | Tier-2---8 | 49 | 7 | 206.5878 | 96.62% | 2.592% | 0.7875% | 8.2694 | 0 | 0 | 8.2694 | 0 | 7.5251 | 0.43553 | 17.2781 | 7.5251 | 0.43553 | 17.2781 | 8.3507 | 0.48331 | 17.2781 | 4.003%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | Tier-3---1 | 123 | 66 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 606.3161 | 0 | 0 | 606.3161 | 0 | 551.7394 | 4.1064 | 134.3614 | 551.7394 | 4.1064 | 134.3614 | 612.2749 | 4.5569 | 134.3614 | 15.29%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | Tier-3---1 | 100 | 55 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 1608.6005 | 0 | 0 | 1608.6005 | 0 | 1463.8045 | 3.422 | 427.7647 | 1463.8045 | 3.422 | 427.7647 | 1624.4097 | 3.7974 | 427.7647 | 15.91%
2027 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | Tier-3---11 | 5 | 3 | 70.8201 | 99.8% | 0% | 0.2033% | 12.2976 | 0 | 0 | 12.2976 | 0 | 11.1907 | 0.18665 | 59.9543 | 11.1907 | 0.18665 | 59.9543 | 12.4185 | 0.20713 | 59.9543 | 17.36%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | Tier-3---3 | 149 | 69 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 808.0634 | 0 | 0 | 808.0634 | 0 | 735.3267 | 4.293 | 171.2836 | 735.3267 | 4.293 | 171.2836 | 816.005 | 4.7641 | 171.2836 | 13.15%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 7 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 72.7848 | 0 | 0 | 72.7848 | 0 | 66.2332 | 0.43553 | 152.0765 | 66.2332 | 0.43553 | 152.0765 | 73.5001 | 0.48331 | 152.0765 | 0.8369%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 240 | 168 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 1079.9269 | 0 | 0 | 1079.9269 | 0 | 982.7188 | 10.4526 | 94.0166 | 982.7188 | 10.4526 | 94.0166 | 1090.5404 | 11.5994 | 94.0166 | 17.11%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 622 | 203 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 623.2671 | 0 | 0 | 623.2671 | 0 | 567.1646 | 12.6302 | 44.9053 | 567.1646 | 12.6302 | 44.9053 | 629.3925 | 14.016 | 44.9053 | 9.379%
2027 | 1235 | CB 230 | Tier-2 | Tier-2---14 | Tier-2---11 | 12 | 1 | 212.8275 | 99.81% | 0% | 0.1866% | 5.1337 | 0 | 0 | 5.1337 | 0 | 4.6716 | 0.062218 | 75.0849 | 4.6716 | 0.062218 | 75.0849 | 5.1842 | 0.069044 | 75.0849 | 2.412%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 44 | 12 | 411.5414 | 99.65% | 0% | 0.3468% | 32.4363 | 0 | 0 | 32.4363 | 0 | 29.5166 | 0.74662 | 39.5339 | 29.5166 | 0.74662 | 39.5339 | 32.7551 | 0.82853 | 39.5339 | 7.882%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | Tier-2---4 | 64 | 52 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 275.7672 | 0 | 0 | 275.7672 | 0 | 250.9444 | 3.2353 | 77.5637 | 250.9444 | 3.2353 | 77.5637 | 278.4774 | 3.5903 | 77.5637 | 23.41%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 9 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 67.4425 | 0 | 0 | 67.4425 | 0 | 61.3718 | 0.55996 | 109.6 | 61.3718 | 0.55996 | 109.6 | 68.1053 | 0.6214 | 109.6 | 3.59%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | Tier-3---11 | 2 | 2 | 58.2342 | 99.94% | 0% | 0.06312% | 16.8773 | 0 | 0 | 16.8773 | 0 | 15.3581 | 0.12444 | 123.4216 | 15.3581 | 0.12444 | 123.4216 | 17.0431 | 0.13809 | 123.4216 | 28.98%
2027 | 1458 | 1458-454F | Tier-2 | Tier-2---18 | Tier-2---10 | 2 | 1 | 84.0912 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.062218 | 0 | 0 | 0.062218 | 0 | 0 | 0.069044 | 0 | 0%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | Tier-3---1 | 127 | 108 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 1997.1805 | 0 | 0 | 1997.1805 | 0 | 1817.407 | 6.7195 | 270.4662 | 1817.407 | 6.7195 | 270.4662 | 2016.8087 | 7.4568 | 270.4662 | 24.48%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | Tier-3---1 | 441 | 29 | 37077.302 | 99.36% | 0.615% | 0.02874% | 702.523 | 0 | 0 | 702.523 | 0 | 639.2864 | 1.8043 | 354.3088 | 639.2864 | 1.8043 | 354.3088 | 709.4274 | 2.0023 | 354.3088 | 1.895%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | Tier-2---20 | 9 | 7 | 8.268 | 89.5% | 6.947% | 3.548% | 1.6692 | 0 | 0 | 1.6692 | 0 | 1.5189 | 0.43553 | 3.4876 | 1.5189 | 0.43553 | 3.4876 | 1.6856 | 0.48331 | 3.4876 | 20.19%
2027 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | Tier-2---4 | 184 | 8 | 259.6903 | 35.49% | 63.12% | 1.387% | 1.1622 | 0 | 0 | 1.1622 | 0 | 1.0575 | 0.49774 | 2.1247 | 1.0575 | 0.49774 | 2.1247 | 1.1736 | 0.55235 | 2.1247 | 0.4475%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 4 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 45.7536 | 0 | 0 | 45.7536 | 0 | 41.6352 | 0.24887 | 167.2957 | 41.6352 | 0.24887 | 167.2957 | 46.2033 | 0.27618 | 167.2957 | 1.223%
2027 | FB1 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 2 | 2730.9177 | 98.3% | 1.373% | 0.325% | 4.3614 | 0 | 0 | 4.3614 | 0 | 3.9689 | 0.12444 | 31.8948 | 3.9689 | 0.12444 | 31.8948 | 4.4043 | 0.13809 | 31.8948 | 0.1597%
2027 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 7 | 346.5871 | 36.93% | 61.45% | 1.621% | 0.70032 | 0 | 0 | 0.70032 | 0 | 0.63728 | 0.43553 | 1.4633 | 0.63728 | 0.43553 | 1.4633 | 0.7072 | 0.48331 | 1.4633 | 0.2021%
2027 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | Tier-2---4 | 371 | 74 | 346.5871 | 36.93% | 61.45% | 1.621% | 7.4034 | 0 | 0 | 7.4034 | 0 | 6.737 | 4.6041 | 1.4633 | 6.737 | 4.6041 | 1.4633 | 7.4762 | 5.1093 | 1.4633 | 2.136%
2027 | FB1 | 522-36 | Tier-2 | Tier-2---16 | Tier-2---8 | 93 | 1 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.082181 | 0 | 0 | 0.082181 | 0 | 0.074784 | 0.062218 | 1.202 | 0.074784 | 0.062218 | 1.202 | 0.082989 | 0.069044 | 1.202 | 0.07027%
2027 | FB1 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 1 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 1.628 | 0 | 0 | 1.628 | 0 | 1.4815 | 0.062218 | 23.8109 | 1.4815 | 0.062218 | 23.8109 | 1.644 | 0.069044 | 23.8109 | 0.1581%
2027 | FB1 | CB FB2 | Tier-2 | Tier-2---9 | Tier-2---2 | 173 | 70 | 1029.5845 | 94.33% | 5.316% | 0.3556% | 113.9607 | 0 | 0 | 113.9607 | 0 | 103.7027 | 4.3553 | 23.8109 | 103.7027 | 4.3553 | 23.8109 | 115.0807 | 4.8331 | 23.8109 | 11.07%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 190 | 54 | 622.3042 | 87.18% | 11.98% | 0.8373% | 44.7153 | 0 | 0 | 44.7153 | 0 | 38.8158 | 3.205 | 12.1111 | 38.8158 | 3.205 | 12.1111 | 45.3761 | 3.7467 | 12.1111 | 7.185%
2028 | 78 | 78-35R | Tier-3 | Tier-3---10 | Tier-3---7 | 29 | 24 | 5696.3358 | 99.98% | 0% | 0.01771% | 1366.8784 | 0 | 0 | 1366.8784 | 0 | 1186.5396 | 1.4244 | 832.9867 | 1186.5396 | 1.4244 | 832.9867 | 1387.0783 | 1.6652 | 832.9867 | 24%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | Tier-3---1 | 198 | 21 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 376.1772 | 0 | 0 | 376.1772 | 0 | 326.5463 | 1.2464 | 261.9947 | 326.5463 | 1.2464 | 261.9947 | 381.7364 | 1.457 | 261.9947 | 3.053%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | Tier-3---5 | 179 | 72 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 237.2816 | 0 | 0 | 237.2816 | 0 | 205.9759 | 4.2733 | 48.2004 | 205.9759 | 4.2733 | 48.2004 | 240.7882 | 4.9956 | 48.2004 | 11.37%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 101 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 108.0333 | 0 | 0 | 108.0333 | 0 | 93.78 | 5.9945 | 15.6443 | 93.78 | 5.9945 | 15.6443 | 109.6299 | 7.0077 | 15.6443 | 6.723%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | Tier-2---1 | 103 | 71 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 798.1811 | 0 | 0 | 798.1811 | 0 | 692.8732 | 4.214 | 164.423 | 692.8732 | 4.214 | 164.423 | 809.9767 | 4.9262 | 164.423 | 19.81%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | Tier-2---3 | 86 | 62 | 2651.4354 | 70.65% | 29.24% | 0.1064% | 391.6401 | 0 | 0 | 391.6401 | 0 | 339.9691 | 3.6798 | 92.3879 | 339.9691 | 3.6798 | 92.3879 | 397.4278 | 4.3017 | 92.3879 | 14.77%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | Tier-3---1 | 300 | 180 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 967.6612 | 0 | 0 | 967.6612 | 0 | 839.993 | 10.6833 | 78.6267 | 839.993 | 10.6833 | 78.6267 | 981.9614 | 12.4889 | 78.6267 | 16.85%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | Tier-2---3 | 52 | 43 | 836.2457 | 79.76% | 20.09% | 0.1547% | 159.9461 | 0 | 0 | 159.9461 | 0 | 138.8436 | 2.5521 | 54.4032 | 138.8436 | 2.5521 | 54.4032 | 162.3098 | 2.9835 | 54.4032 | 19.13%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | Tier-3---1 | 236 | 66 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 923.0548 | 0 | 0 | 923.0548 | 0 | 801.2717 | 3.9172 | 204.5516 | 801.2717 | 3.9172 | 204.5516 | 936.6958 | 4.5793 | 204.5516 | 8.01%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | Tier-3---1 | 312 | 250 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 2272.4862 | 0 | 0 | 2272.4862 | 0 | 1972.6662 | 14.8379 | 132.9476 | 1972.6662 | 14.8379 | 132.9476 | 2306.0692 | 17.3457 | 132.9476 | 22.57%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | Tier-2---5 | 50 | 9 | 404.4817 | 67.64% | 32.12% | 0.2398% | 14.2811 | 0 | 0 | 14.2811 | 0 | 12.3969 | 0.53417 | 23.208 | 12.3969 | 0.53417 | 23.208 | 14.4921 | 0.62445 | 23.208 | 3.531%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 214 | 166 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 1084.4476 | 0 | 0 | 1084.4476 | 0 | 941.3712 | 9.8524 | 95.5476 | 941.3712 | 9.8524 | 95.5476 | 1100.4737 | 11.5175 | 95.5476 | 21.98%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | Tier-2---1 | 176 | 7 | 2963.4059 | 78.23% | 21.66% | 0.1106% | 26.7389 | 0 | 0 | 26.7389 | 0 | 23.2111 | 0.41546 | 55.8682 | 23.2111 | 0.41546 | 55.8682 | 27.134 | 0.48568 | 55.8682 | 0.9023%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | Tier-2---12 | 200 | 7 | 47.6106 | 91.21% | 0% | 8.789% | 0.44078 | 0 | 0 | 0.44078 | 0 | 0.38262 | 0.41546 | 0.92096 | 0.38262 | 0.41546 | 0.92096 | 0.44729 | 0.48568 | 0.92096 | 0.9258%
2028 | 178 | 178-982 | Tier-2 | Tier-2---21 | Tier-2---25 | 45 | 7 | 0.95479 | 13.38% | 0% | 86.62% | 0.0057645 | 0 | 0 | 0.0057645 | 0 | 0.005004 | 0.41546 | 0.012044 | 0.005004 | 0.41546 | 0.012044 | 0.0058497 | 0.48568 | 0.012044 | 0.6037%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | Tier-2---1 | 291 | 1 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 11.1982 | 0 | 0 | 11.1982 | 0 | 9.7208 | 0.059352 | 163.7828 | 9.7208 | 0.059352 | 163.7828 | 11.3637 | 0.069383 | 163.7828 | 0.09397%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | Tier-2---3 | 19 | 19 | 655.8009 | 99.14% | 0.7615% | 0.1019% | 188.5402 | 0 | 0 | 188.5402 | 0 | 163.6652 | 1.1277 | 145.1342 | 163.6652 | 1.1277 | 145.1342 | 191.3265 | 1.3183 | 145.1342 | 28.75%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | Tier-2---2 | 260 | 161 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 284.5907 | 0 | 0 | 284.5907 | 0 | 247.0433 | 9.5556 | 25.8532 | 247.0433 | 9.5556 | 25.8532 | 288.7964 | 11.1706 | 25.8532 | 16.51%
2028 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 154 | 2 | 396.8506 | 79.93% | 19.29% | 0.7702% | 1.1947 | 0 | 0 | 1.1947 | 0 | 1.0371 | 0.1187 | 8.737 | 1.0371 | 0.1187 | 8.737 | 1.2124 | 0.13877 | 8.737 | 0.3011%
2028 | 197 | 197-1150F | Tier-2 | Tier-2---15 | Tier-2---9 | 29 | 29 | 183.5383 | 99.34% | 0.09556% | 0.5689% | 52.8725 | 0 | 0 | 52.8725 | 0 | 45.8968 | 1.7212 | 26.6656 | 45.8968 | 1.7212 | 26.6656 | 53.6538 | 2.0121 | 26.6656 | 28.81%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | Tier-2---17 | 9 | 9 | 6.6189 | 96.38% | 0% | 3.621% | 1.85 | 0 | 0 | 1.85 | 0 | 1.6059 | 0.53417 | 3.0064 | 1.6059 | 0.53417 | 3.0064 | 1.8773 | 0.62445 | 3.0064 | 27.95%
2028 | 197 | CB 196 | Tier-2 | Tier-2---15 | Tier-2---9 | 24 | 1 | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.051054 | 0 | 0 | 0.051054 | 0 | 0.044318 | 0.059352 | 0.74671 | 0.044318 | 0.059352 | 0.74671 | 0.051809 | 0.069383 | 0.74671 | 0.03797%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | Tier-2---2 | 188 | 28 | 973.0999 | 95.53% | 4.02% | 0.4464% | 40.1524 | 0 | 0 | 40.1524 | 0 | 34.8549 | 1.6618 | 20.9736 | 34.8549 | 1.6618 | 20.9736 | 40.7458 | 1.9427 | 20.9736 | 4.126%
2028 | 202 | CB 202 | Tier-2 | Tier-2---16 | Tier-2---8 | 193 | 73 | 133.9861 | 95.12% | 0% | 4.877% | 13.98 | 0 | 0 | 13.98 | 0 | 12.1356 | 4.3327 | 2.8009 | 12.1356 | 4.3327 | 2.8009 | 14.1866 | 5.0649 | 2.8009 | 10.43%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | Tier-2---6 | 132 | 9 | 1279.0443 | 99.78% | 0% | 0.2159% | 25.2356 | 0 | 0 | 25.2356 | 0 | 21.9061 | 0.53417 | 41.0101 | 21.9061 | 0.53417 | 41.0101 | 25.6085 | 0.62445 | 41.0101 | 1.973%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | Tier-2---2 | 413 | 22 | 2976.5734 | 99.75% | 0% | 0.2502% | 45.8669 | 0 | 0 | 45.8669 | 0 | 39.8155 | 1.3057 | 30.4927 | 39.8155 | 1.3057 | 30.4927 | 46.5447 | 1.5264 | 30.4927 | 1.541%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | Tier-2---1 | 1069 | 253 | 8462.8018 | 99.74% | 0% | 0.2593% | 579.3321 | 0 | 0 | 579.3321 | 0 | 502.898 | 15.016 | 33.4909 | 502.898 | 15.016 | 33.4909 | 587.8935 | 17.5538 | 33.4909 | 6.846%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | Tier-2---10 | 111 | 93 | 498.1496 | 90.1% | 9.186% | 0.7154% | 109.0524 | 0 | 0 | 109.0524 | 0 | 94.6646 | 5.5197 | 17.1503 | 94.6646 | 5.5197 | 17.1503 | 110.6639 | 6.4526 | 17.1503 | 21.89%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | Tier-2---5 | 221 | 177 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 206.6698 | 0 | 0 | 206.6698 | 0 | 179.4029 | 10.5052 | 17.0775 | 179.4029 | 10.5052 | 17.0775 | 209.724 | 12.2808 | 17.0775 | 19.91%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | Tier-2---10 | 77 | 72 | 170.5929 | 70.47% | 28.1% | 1.432% | 32.6001 | 0 | 0 | 32.6001 | 0 | 28.299 | 4.2733 | 6.6223 | 28.299 | 4.2733 | 6.6223 | 33.0819 | 4.9956 | 6.6223 | 19.11%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | Tier-2---10 | 95 | 71 | 317.7725 | 50.82% | 48.53% | 0.6462% | 35.0042 | 0 | 0 | 35.0042 | 0 | 30.3859 | 4.214 | 7.2108 | 30.3859 | 4.214 | 7.2108 | 35.5215 | 4.9262 | 7.2108 | 11.02%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | Tier-2---5 | 293 | 249 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 264.5675 | 0 | 0 | 264.5675 | 0 | 229.6618 | 14.7786 | 15.5402 | 229.6618 | 14.7786 | 15.5402 | 268.4773 | 17.2763 | 15.5402 | 22.05%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | Tier-2---5 | 420 | 132 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 138.9735 | 0 | 0 | 138.9735 | 0 | 120.638 | 7.8344 | 15.3985 | 120.638 | 7.8344 | 15.3985 | 141.0272 | 9.1585 | 15.3985 | 7.68%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | Tier-3---3 | 279 | 122 | 1890.633 | 91.06% | 8.49% | 0.4466% | 218.3259 | 0 | 0 | 218.3259 | 0 | 189.5211 | 7.2409 | 26.1737 | 189.5211 | 7.2409 | 26.1737 | 221.5523 | 8.4647 | 26.1737 | 11.55%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | Tier-2---3 | 287 | 250 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 419.1859 | 0 | 0 | 419.1859 | 0 | 363.8807 | 14.8379 | 24.5237 | 363.8807 | 14.8379 | 24.5237 | 425.3807 | 17.3457 | 24.5237 | 24.11%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | Tier-2---3 | 219 | 185 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 365.3664 | 0 | 0 | 365.3664 | 0 | 317.1619 | 10.9801 | 28.8853 | 317.1619 | 10.9801 | 28.8853 | 370.7658 | 12.8358 | 28.8853 | 23.27%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | Tier-2---3 | 273 | 228 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 300.2303 | 0 | 0 | 300.2303 | 0 | 260.6195 | 13.5322 | 19.2592 | 260.6195 | 13.5322 | 19.2592 | 304.6672 | 15.8193 | 19.2592 | 23.72%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | Tier-2---5 | 71 | 66 | 261.4279 | 97.06% | 2.12% | 0.8249% | 68.3998 | 0 | 0 | 68.3998 | 0 | 59.3754 | 3.9172 | 15.1576 | 59.3754 | 3.9172 | 15.1576 | 69.4106 | 4.5793 | 15.1576 | 26.16%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | Tier-2---3 | 201 | 183 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 380.7384 | 0 | 0 | 380.7384 | 0 | 330.5057 | 10.8614 | 30.4295 | 330.5057 | 10.8614 | 30.4295 | 386.365 | 12.697 | 30.4295 | 25.68%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | Tier-2---3 | 297 | 221 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 570.135 | 0 | 0 | 570.135 | 0 | 494.9143 | 13.1167 | 37.7316 | 494.9143 | 13.1167 | 37.7316 | 578.5605 | 15.3336 | 37.7316 | 20.67%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | Tier-2---3 | 115 | 105 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 267.1334 | 0 | 0 | 267.1334 | 0 | 231.8892 | 6.2319 | 37.2099 | 231.8892 | 6.2319 | 37.2099 | 271.0812 | 7.2852 | 37.2099 | 25.72%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | Tier-2---10 | 31 | 29 | 104.9439 | 97.78% | 1.295% | 0.9224% | 27.8389 | 0 | 0 | 27.8389 | 0 | 24.166 | 1.7212 | 14.0402 | 24.166 | 1.7212 | 14.0402 | 28.2503 | 2.0121 | 14.0402 | 26.53%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | Tier-2---3 | 155 | 69 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 275.7282 | 0 | 0 | 275.7282 | 0 | 239.3501 | 4.0953 | 58.4456 | 239.3501 | 4.0953 | 58.4456 | 279.803 | 4.7874 | 58.4456 | 12.74%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | Tier-2---3 | 147 | 133 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 377.5589 | 0 | 0 | 377.5589 | 0 | 327.7457 | 7.8938 | 41.5195 | 327.7457 | 7.8938 | 41.5195 | 383.1385 | 9.2279 | 41.5195 | 25.67%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | Tier-3---1 | 446 | 15 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 253.5252 | 0 | 0 | 253.5252 | 0 | 220.0764 | 0.89028 | 247.2004 | 220.0764 | 0.89028 | 247.2004 | 257.2718 | 1.0407 | 247.2004 | 0.9647%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | Tier-3---2 | 285 | 140 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 944.1102 | 0 | 0 | 944.1102 | 0 | 819.5492 | 8.3092 | 98.6311 | 819.5492 | 8.3092 | 98.6311 | 958.0623 | 9.7136 | 98.6311 | 14.16%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | Tier-3---4 | 157 | 155 | 484.0355 | 97.4% | 1.48% | 1.12% | 134.9796 | 0 | 0 | 134.9796 | 0 | 117.1711 | 9.1995 | 12.7367 | 117.1711 | 9.1995 | 12.7367 | 136.9744 | 10.7543 | 12.7367 | 27.89%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | Tier-3---4 | 94 | 89 | 400.1895 | 97.86% | 1.359% | 0.7809% | 107.5302 | 0 | 0 | 107.5302 | 0 | 93.3432 | 5.2823 | 17.6709 | 93.3432 | 5.2823 | 17.6709 | 109.1193 | 6.1751 | 17.6709 | 26.87%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | Tier-3---4 | 70 | 60 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 125.9593 | 0 | 0 | 125.9593 | 0 | 109.3409 | 3.5611 | 30.7042 | 109.3409 | 3.5611 | 30.7042 | 127.8207 | 4.163 | 30.7042 | 24.54%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | Tier-3---2 | 174 | 89 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 324.5988 | 0 | 0 | 324.5988 | 0 | 281.7729 | 5.2823 | 53.3429 | 281.7729 | 5.2823 | 53.3429 | 329.3958 | 6.1751 | 53.3429 | 14.7%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | Tier-3---5 | 196 | 89 | 1721.769 | 85.69% | 14.07% | 0.2459% | 194.2784 | 0 | 0 | 194.2784 | 0 | 168.6464 | 5.2823 | 31.9267 | 168.6464 | 5.2823 | 31.9267 | 197.1495 | 6.1751 | 31.9267 | 11.28%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 1 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 12.3732 | 0 | 0 | 12.3732 | 0 | 10.7407 | 0.059352 | 180.9678 | 10.7407 | 0.059352 | 180.9678 | 12.556 | 0.069383 | 180.9678 | 0.2277%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | Tier-3---1 | 126 | 9 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 111.3588 | 0 | 0 | 111.3588 | 0 | 96.6667 | 0.53417 | 180.9678 | 96.6667 | 0.53417 | 180.9678 | 113.0044 | 0.62445 | 180.9678 | 2.049%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | Tier-3---1 | 293 | 84 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 287.8187 | 0 | 0 | 287.8187 | 0 | 249.8454 | 4.9855 | 50.114 | 249.8454 | 4.9855 | 50.114 | 292.0721 | 5.8282 | 50.114 | 7.87%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | Tier-3---1 | 116 | 38 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 951.9764 | 0 | 0 | 951.9764 | 0 | 826.3775 | 2.2554 | 366.4055 | 826.3775 | 2.2554 | 366.4055 | 966.0447 | 2.6365 | 366.4055 | 9.41%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | Tier-3---5 | 328 | 92 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 132.0454 | 0 | 0 | 132.0454 | 0 | 114.624 | 5.4604 | 20.992 | 114.624 | 5.4604 | 20.992 | 133.9968 | 6.3832 | 20.992 | 6.856%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | Tier-3---3 | 614 | 30 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 45.4054 | 0 | 0 | 45.4054 | 0 | 39.4148 | 1.7806 | 22.1363 | 39.4148 | 1.7806 | 22.1363 | 46.0764 | 2.0815 | 22.1363 | 1.266%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | Tier-3---1 | 407 | 3 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 15.2486 | 0 | 0 | 15.2486 | 0 | 13.2368 | 0.17806 | 74.3409 | 13.2368 | 0.17806 | 74.3409 | 15.4739 | 0.20815 | 74.3409 | 0.2053%
2028 | 222 | 79-668R | Tier-3 | Tier-3---15 | Tier-3---5 | 309 | 1 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 1.0696 | 0 | 0 | 1.0696 | 0 | 0.92851 | 0.059352 | 15.6443 | 0.92851 | 0.059352 | 15.6443 | 1.0854 | 0.069383 | 15.6443 | 0.06656%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | Tier-2---2 | 357 | 40 | 2730.9177 | 98.3% | 1.373% | 0.325% | 87.2288 | 0 | 0 | 87.2288 | 0 | 75.7203 | 2.3741 | 31.8948 | 75.7203 | 2.3741 | 31.8948 | 88.5179 | 2.7753 | 31.8948 | 3.194%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | Tier-2---1 | 862 | 67 | 5142.095 | 98.68% | 0.901% | 0.4182% | 114.3769 | 0 | 0 | 114.3769 | 0 | 99.2866 | 3.9766 | 24.968 | 99.2866 | 3.9766 | 24.968 | 116.0672 | 4.6486 | 24.968 | 2.224%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 1 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 2.112 | 0 | 0 | 2.112 | 0 | 1.8334 | 0.059352 | 30.8903 | 1.8334 | 0.059352 | 30.8903 | 2.1433 | 0.069383 | 30.8903 | 0.06957%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 412 | 95 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 200.6444 | 0 | 0 | 200.6444 | 0 | 174.1724 | 5.6384 | 30.8903 | 174.1724 | 5.6384 | 30.8903 | 203.6095 | 6.5914 | 30.8903 | 6.609%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 273 | 18 | 718.991 | 97.57% | 1.357% | 1.072% | 13.4137 | 0 | 0 | 13.4137 | 0 | 11.644 | 1.0683 | 10.8992 | 11.644 | 1.0683 | 10.8992 | 13.6119 | 1.2489 | 10.8992 | 1.866%
2028 | 243 | 243-14R | Tier-2 | Tier-2---11 | Tier-2---4 | 470 | 1 | 404.2589 | 29.5% | 68.39% | 2.113% | 0.07358 | 0 | 0 | 0.07358 | 0 | 0.063872 | 0.059352 | 1.0762 | 0.063872 | 0.059352 | 1.0762 | 0.074667 | 0.069383 | 1.0762 | 0.0182%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | Tier-3---2 | 436 | 95 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 202.3432 | 0 | 0 | 202.3432 | 0 | 175.6471 | 5.6384 | 31.1519 | 175.6471 | 5.6384 | 31.1519 | 205.3334 | 6.5914 | 31.1519 | 5.974%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 303 | 171 | 1438.4419 | 90% | 9.47% | 0.5268% | 211.8857 | 0 | 0 | 211.8857 | 0 | 183.9306 | 10.1491 | 18.1228 | 183.9306 | 10.1491 | 18.1228 | 215.017 | 11.8645 | 18.1228 | 14.73%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | Tier-2---4 | 90 | 12 | 379.7423 | 70.28% | 29.01% | 0.71% | 10.3194 | 0 | 0 | 10.3194 | 0 | 8.9579 | 0.71222 | 12.5775 | 8.9579 | 0.71222 | 12.5775 | 10.4719 | 0.83259 | 12.5775 | 2.717%
2028 | 292 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 17 | 1 | 94.6686 | 66.47% | 32.93% | 0.6021% | 1.0735 | 0 | 0 | 1.0735 | 0 | 0.93185 | 0.059352 | 15.7005 | 0.93185 | 0.059352 | 15.7005 | 1.0893 | 0.069383 | 15.7005 | 1.134%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | Tier-2---6 | 69 | 1 | 458.7821 | 99.48% | 0% | 0.5194% | 1.9182 | 0 | 0 | 1.9182 | 0 | 1.6651 | 0.059352 | 28.0552 | 1.6651 | 0.059352 | 28.0552 | 1.9465 | 0.069383 | 28.0552 | 0.4181%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 1 | 754.1323 | 92.41% | 6.882% | 0.7076% | 0.8084 | 0 | 0 | 0.8084 | 0 | 0.70175 | 0.059352 | 11.8235 | 0.70175 | 0.059352 | 11.8235 | 0.82035 | 0.069383 | 11.8235 | 0.1072%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | Tier-2---2 | 250 | 173 | 754.1323 | 92.41% | 6.882% | 0.7076% | 139.8536 | 0 | 0 | 139.8536 | 0 | 121.402 | 10.2678 | 11.8235 | 121.402 | 10.2678 | 11.8235 | 141.9203 | 12.0032 | 11.8235 | 18.54%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | Tier-2---16 | 15 | 7 | 15.6056 | 49.38% | 48.09% | 2.529% | 1.043 | 0 | 0 | 1.043 | 0 | 0.90535 | 0.41546 | 2.1791 | 0.90535 | 0.41546 | 2.1791 | 1.0584 | 0.48568 | 2.1791 | 6.683%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | Tier-2---9 | 195 | 17 | 159.8581 | 2.339% | 95.81% | 1.853% | 0.094532 | 0 | 0 | 0.094532 | 0 | 0.08206 | 1.009 | 0.081329 | 0.08206 | 1.009 | 0.081329 | 0.095929 | 1.1795 | 0.081329 | 0.05913%
2028 | 315 | 315-1192F | Tier-2 | Tier-2---19 | Tier-2---17 | 9 | 9 | 14.6681 | 98.1% | 0% | 1.899% | 4.173 | 0 | 0 | 4.173 | 0 | 3.6224 | 0.53417 | 6.7814 | 3.6224 | 0.53417 | 6.7814 | 4.2346 | 0.62445 | 6.7814 | 28.45%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | Tier-2---7 | 39 | 34 | 209.8559 | 99.5% | 0% | 0.498% | 52.7917 | 0 | 0 | 52.7917 | 0 | 45.8266 | 2.018 | 22.7094 | 45.8266 | 2.018 | 22.7094 | 53.5718 | 2.359 | 22.7094 | 25.16%
2028 | 315 | CB 315 | Tier-2 | Tier-2---19 | Tier-2---17 | 21 | 1 | 10.7713 | 97.26% | 0% | 2.741% | 0.14467 | 0 | 0 | 0.14467 | 0 | 0.12558 | 0.059352 | 2.1159 | 0.12558 | 0.059352 | 2.1159 | 0.14681 | 0.069383 | 2.1159 | 1.343%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 22 | 21 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 402.4076 | 0 | 0 | 402.4076 | 0 | 349.316 | 1.2464 | 280.2633 | 349.316 | 1.2464 | 280.2633 | 408.3544 | 1.457 | 280.2633 | 27.62%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 149 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 2957.6731 | 0 | 0 | 2957.6731 | 0 | 2567.453 | 8.8434 | 290.3242 | 2567.453 | 8.8434 | 290.3242 | 3001.3818 | 10.338 | 290.3242 | 12.58%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 154 | 7 | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 191.8002 | 0 | 0 | 191.8002 | 0 | 166.4951 | 0.41546 | 400.7472 | 166.4951 | 0.41546 | 400.7472 | 194.6347 | 0.48568 | 400.7472 | 1.314%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 359 | 29 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 433.2708 | 0 | 0 | 433.2708 | 0 | 376.1073 | 1.7212 | 218.5148 | 376.1073 | 1.7212 | 218.5148 | 439.6737 | 2.0121 | 218.5148 | 2.328%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | Tier-2---2 | 342 | 168 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 258.8853 | 0 | 0 | 258.8853 | 0 | 224.7293 | 9.9711 | 22.5381 | 224.7293 | 9.9711 | 22.5381 | 262.7111 | 11.6563 | 22.5381 | 13.94%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 1 | 6370.0414 | 98.47% | 1.262% | 0.272% | 2.125 | 0 | 0 | 2.125 | 0 | 1.8446 | 0.059352 | 31.0793 | 1.8446 | 0.059352 | 31.0793 | 2.1564 | 0.069383 | 31.0793 | 0.03336%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | Tier-3---1 | 856 | 386 | 6370.0414 | 98.47% | 1.262% | 0.272% | 820.2375 | 0 | 0 | 820.2375 | 0 | 712.0196 | 22.9097 | 31.0793 | 712.0196 | 22.9097 | 31.0793 | 832.359 | 26.7818 | 31.0793 | 12.88%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | Tier-2---2 | 459 | 24 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 19.6524 | 0 | 0 | 19.6524 | 0 | 17.0595 | 1.4244 | 11.9763 | 17.0595 | 1.4244 | 11.9763 | 19.9428 | 1.6652 | 11.9763 | 1.455%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | Tier-3---5 | 54 | 1 | 704.6091 | 96.62% | 3.132% | 0.2514% | 3.656 | 0 | 0 | 3.656 | 0 | 3.1736 | 0.059352 | 53.4714 | 3.1736 | 0.059352 | 53.4714 | 3.71 | 0.069383 | 53.4714 | 0.5189%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | Tier-3---10 | 74 | 33 | 474.7376 | 91.31% | 8.325% | 0.3651% | 56.0597 | 0 | 0 | 56.0597 | 0 | 48.6635 | 1.9586 | 24.846 | 48.6635 | 1.9586 | 24.846 | 56.8881 | 2.2896 | 24.846 | 11.81%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | Tier-2---1 | 403 | 10 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 23.9935 | 0 | 0 | 23.9935 | 0 | 20.828 | 0.59352 | 35.0925 | 20.828 | 0.59352 | 35.0925 | 24.3481 | 0.69383 | 35.0925 | 0.7028%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | Tier-3---1 | 337 | 12 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 94.454 | 0 | 0 | 94.454 | 0 | 81.9922 | 0.71222 | 115.122 | 81.9922 | 0.71222 | 115.122 | 95.8499 | 0.83259 | 115.122 | 0.9806%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | Tier-2---3 | 220 | 97 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 890.9956 | 0 | 0 | 890.9956 | 0 | 773.4422 | 5.7571 | 134.3455 | 773.4422 | 5.7571 | 134.3455 | 904.1628 | 6.7301 | 134.3455 | 12.29%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | Tier-2---1 | 526 | 68 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 380.9732 | 0 | 0 | 380.9732 | 0 | 330.7096 | 4.0359 | 81.9417 | 330.7096 | 4.0359 | 81.9417 | 386.6033 | 4.718 | 81.9417 | 3.587%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | Tier-2---5 | 238 | 46 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 83.9003 | 0 | 0 | 83.9003 | 0 | 72.831 | 2.7302 | 26.6763 | 72.831 | 2.7302 | 26.6763 | 85.1402 | 3.1916 | 26.6763 | 4.749%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | Tier-2---3 | 246 | 18 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 68.3324 | 0 | 0 | 68.3324 | 0 | 59.3169 | 1.0683 | 55.5231 | 59.3169 | 1.0683 | 55.5231 | 69.3422 | 1.2489 | 55.5231 | 1.858%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 1 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 1.9247 | 0 | 0 | 1.9247 | 0 | 1.6708 | 0.059352 | 28.1502 | 1.6708 | 0.059352 | 28.1502 | 1.9531 | 0.069383 | 28.1502 | 0.04354%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | Tier-2---3 | 587 | 9 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 17.3222 | 0 | 0 | 17.3222 | 0 | 15.0368 | 0.53417 | 28.1502 | 15.0368 | 0.53417 | 28.1502 | 17.5782 | 0.62445 | 28.1502 | 0.3918%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | Tier-2---5 | 25 | 9 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 137.234 | 0 | 0 | 137.234 | 0 | 119.128 | 0.53417 | 223.0173 | 119.128 | 0.53417 | 223.0173 | 139.262 | 0.62445 | 223.0173 | 10.15%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | Tier-3---5 | 51 | 45 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 301.9398 | 0 | 0 | 301.9398 | 0 | 262.1034 | 2.6708 | 98.1357 | 262.1034 | 2.6708 | 98.1357 | 306.4019 | 3.1222 | 98.1357 | 24.92%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | Tier-3---5 | 314 | 213 | 2119.752 | 55.7% | 43.96% | 0.3458% | 232.2595 | 0 | 0 | 232.2595 | 0 | 201.6164 | 12.6419 | 15.9483 | 201.6164 | 12.6419 | 15.9483 | 235.6919 | 14.7785 | 15.9483 | 10.96%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | Tier-3---10 | 202 | 101 | 520.639 | 76.18% | 22.78% | 1.038% | 57.5137 | 0 | 0 | 57.5137 | 0 | 49.9256 | 5.9945 | 8.3285 | 49.9256 | 5.9945 | 8.3285 | 58.3636 | 7.0077 | 8.3285 | 11.05%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | Tier-3---10 | 170 | 82 | 630.7627 | 79.12% | 20.09% | 0.7869% | 69.8116 | 0 | 0 | 69.8116 | 0 | 60.601 | 4.8668 | 12.4518 | 60.601 | 4.8668 | 12.4518 | 70.8433 | 5.6894 | 12.4518 | 11.07%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | Tier-3---1 | 717 | 336 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 1134.3809 | 0 | 0 | 1134.3809 | 0 | 984.7166 | 19.9422 | 49.3786 | 984.7166 | 19.9422 | 49.3786 | 1151.1449 | 23.3126 | 49.3786 | 12.46%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | Tier-3---3 | 413 | 65 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 240.6997 | 0 | 0 | 240.6997 | 0 | 208.943 | 3.8579 | 54.1604 | 208.943 | 3.8579 | 54.1604 | 244.2567 | 4.5099 | 54.1604 | 4.264%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | Tier-3---1 | 557 | 79 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 250.4892 | 0 | 0 | 250.4892 | 0 | 217.441 | 4.6888 | 46.3747 | 217.441 | 4.6888 | 46.3747 | 254.191 | 5.4812 | 46.3747 | 3.722%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | Tier-2---8 | 18 | 15 | 296.7138 | 97.11% | 2.719% | 0.1664% | 69.6369 | 0 | 0 | 69.6369 | 0 | 60.4494 | 0.89028 | 67.8997 | 60.4494 | 0.89028 | 67.8997 | 70.666 | 1.0407 | 67.8997 | 23.47%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | Tier-2---1 | 209 | 126 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 1435.4594 | 0 | 0 | 1435.4594 | 0 | 1246.0724 | 7.4783 | 166.6248 | 1246.0724 | 7.4783 | 166.6248 | 1456.6728 | 8.7422 | 166.6248 | 17.35%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | Tier-2---4 | 44 | 22 | 792.2018 | 92.77% | 7.138% | 0.09408% | 106.5622 | 0 | 0 | 106.5622 | 0 | 92.5029 | 1.3057 | 70.8435 | 92.5029 | 1.3057 | 70.8435 | 108.137 | 1.5264 | 70.8435 | 13.45%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | Tier-2---4 | 70 | 41 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 183.1938 | 0 | 0 | 183.1938 | 0 | 159.0242 | 2.4334 | 65.3501 | 159.0242 | 2.4334 | 65.3501 | 185.9011 | 2.8447 | 65.3501 | 16.18%
2028 | 450 | 450-50R | Tier-2 | Tier-2---11 | Tier-2---4 | 18 | 5 | 537.0702 | 32.53% | 67.41% | 0.0594% | 14.0735 | 0 | 0 | 14.0735 | 0 | 12.2167 | 0.29676 | 41.1673 | 12.2167 | 0.29676 | 41.1673 | 14.2815 | 0.34691 | 41.1673 | 2.62%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | Tier-2---11 | 5 | 5 | 137.227 | 99.9% | 0% | 0.1049% | 39.7541 | 0 | 0 | 39.7541 | 0 | 34.5091 | 0.29676 | 116.287 | 34.5091 | 0.29676 | 116.287 | 40.3416 | 0.34691 | 116.287 | 28.97%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | Tier-2---11 | 20 | 19 | 625.5425 | 99.9% | 0% | 0.09615% | 172.1713 | 0 | 0 | 172.1713 | 0 | 149.4559 | 1.1277 | 132.5337 | 149.4559 | 1.1277 | 132.5337 | 174.7156 | 1.3183 | 132.5337 | 27.52%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | Tier-2---11 | 12 | 10 | 181.2174 | 99.84% | 0% | 0.161% | 43.7237 | 0 | 0 | 43.7237 | 0 | 37.955 | 0.59352 | 63.9494 | 37.955 | 0.59352 | 63.9494 | 44.3699 | 0.69383 | 63.9494 | 24.13%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | Tier-2---7 | 71 | 58 | 2823.7515 | 99.93% | 0% | 0.06613% | 668.5083 | 0 | 0 | 668.5083 | 0 | 580.3088 | 3.4424 | 168.577 | 580.3088 | 3.4424 | 168.577 | 678.3876 | 4.0242 | 168.577 | 23.67%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | Tier-2---14 | 2 | 3 | 39.0262 | 97.23% | 2.586% | 0.1833% | 16.5063 | 0 | 0 | 16.5063 | 0 | 14.3285 | 0.17806 | 80.4725 | 14.3285 | 0.17806 | 80.4725 | 16.7502 | 0.20815 | 80.4725 | 42.3%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 53 | 1 | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 18.7723 | 0 | 0 | 18.7723 | 0 | 16.2956 | 0.059352 | 274.5597 | 16.2956 | 0.059352 | 274.5597 | 19.0497 | 0.069383 | 274.5597 | 0.5455%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | Tier-2---2 | 53 | 45 | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 844.7535 | 0 | 0 | 844.7535 | 0 | 733.3011 | 2.6708 | 274.5597 | 733.3011 | 2.6708 | 274.5597 | 857.2373 | 3.1222 | 274.5597 | 24.55%
2028 | 454 | 454-49F | Tier-2 | Tier-2---13 | Tier-2---8 | 52 | 1 | 292.9743 | 76.06% | 23.59% | 0.3558% | 1.2427 | 0 | 0 | 1.2427 | 0 | 1.0787 | 0.059352 | 18.1752 | 1.0787 | 0.059352 | 18.1752 | 1.261 | 0.069383 | 18.1752 | 0.4242%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 1 | 19.4193 | 94.64% | 0% | 5.361% | 0.17193 | 0 | 0 | 0.17193 | 0 | 0.14924 | 0.059352 | 2.5146 | 0.14924 | 0.059352 | 2.5146 | 0.17447 | 0.069383 | 2.5146 | 0.8853%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 1 | 19.4193 | 94.64% | 0% | 5.361% | 0.17193 | 0 | 0 | 0.17193 | 0 | 0.14924 | 0.059352 | 2.5146 | 0.14924 | 0.059352 | 2.5146 | 0.17447 | 0.069383 | 2.5146 | 0.8853%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 3 | 19.4193 | 94.64% | 0% | 5.361% | 0.51578 | 0 | 0 | 0.51578 | 0 | 0.44773 | 0.17806 | 2.5146 | 0.44773 | 0.17806 | 2.5146 | 0.5234 | 0.20815 | 2.5146 | 2.656%
2028 | 500 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 16 | 800.5503 | 21.6% | 78.32% | 0.07823% | 40.1197 | 0 | 0 | 40.1197 | 0 | 34.8265 | 0.94963 | 36.6739 | 34.8265 | 0.94963 | 36.6739 | 40.7126 | 1.1101 | 36.6739 | 5.012%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | Tier-2---7 | 23 | 3 | 204.0835 | 99.63% | 0% | 0.368% | 7.6913 | 0 | 0 | 7.6913 | 0 | 6.6765 | 0.17806 | 37.497 | 6.6765 | 0.17806 | 37.497 | 7.8049 | 0.20815 | 37.497 | 3.769%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | Tier-2---6 | 154 | 23 | 733.6834 | 99.51% | 0% | 0.4917% | 31.6208 | 0 | 0 | 31.6208 | 0 | 27.4489 | 1.3651 | 20.1078 | 27.4489 | 1.3651 | 20.1078 | 32.0881 | 1.5958 | 20.1078 | 4.31%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | Tier-2---2 | 18 | 18 | 833.6308 | 67.75% | 32.17% | 0.07637% | 163.7891 | 0 | 0 | 163.7891 | 0 | 142.1796 | 1.0683 | 133.0858 | 142.1796 | 1.0683 | 133.0858 | 166.2096 | 1.2489 | 133.0858 | 19.65%
2028 | 540 | CB 292 | Tier-2 | Tier-2---18 | Tier-2---8 | 17 | 8 | 94.6686 | 66.47% | 32.93% | 0.6021% | 8.5879 | 0 | 0 | 8.5879 | 0 | 7.4548 | 0.47481 | 15.7005 | 7.4548 | 0.47481 | 15.7005 | 8.7148 | 0.55506 | 15.7005 | 9.072%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 3 | 67.245 | 99.24% | 0% | 0.7576% | 3.6287 | 0 | 0 | 3.6287 | 0 | 3.15 | 0.17806 | 17.6911 | 3.15 | 0.17806 | 17.6911 | 3.6824 | 0.20815 | 17.6911 | 5.396%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | Tier-2---11 | 16 | 2 | 67.245 | 99.24% | 0% | 0.7576% | 2.4192 | 0 | 0 | 2.4192 | 0 | 2.1 | 0.1187 | 17.6911 | 2.1 | 0.1187 | 17.6911 | 2.4549 | 0.13877 | 17.6911 | 3.598%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | Tier-2---4 | 92 | 11 | 519.9571 | 96.32% | 3.27% | 0.4047% | 17.3664 | 0 | 0 | 17.3664 | 0 | 15.0751 | 0.65287 | 23.0906 | 15.0751 | 0.65287 | 23.0906 | 17.623 | 0.76321 | 23.0906 | 3.34%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | Tier-2---1 | 398 | 45 | 18774.394 | 95.55% | 4.388% | 0.06321% | 588.1936 | 0 | 0 | 588.1936 | 0 | 510.5904 | 2.6708 | 191.1733 | 510.5904 | 2.6708 | 191.1733 | 596.886 | 3.1222 | 191.1733 | 3.133%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | Tier-2---1 | 753 | 50 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 492.7305 | 0 | 0 | 492.7305 | 0 | 427.7222 | 2.9676 | 144.1315 | 427.7222 | 2.9676 | 144.1315 | 500.0121 | 3.4691 | 144.1315 | 1.914%
2028 | 770 | 770-259R | Tier-2 | Tier-2---17 | Tier-2---15 | 24 | 6 | 42.5113 | 97.49% | 0.5175% | 1.991% | 3.0048 | 0 | 0 | 3.0048 | 0 | 2.6083 | 0.35611 | 7.3245 | 2.6083 | 0.35611 | 7.3245 | 3.0492 | 0.4163 | 7.3245 | 7.068%
2028 | 770 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 1 | 62.492 | 96.91% | 0.773% | 2.32% | 0.39914 | 0 | 0 | 0.39914 | 0 | 0.34648 | 0.059352 | 5.8378 | 0.34648 | 0.059352 | 5.8378 | 0.40504 | 0.069383 | 5.8378 | 0.6387%
2028 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 53 | 13 | 55.0677 | 92.66% | 4.028% | 3.312% | 3.6296 | 0 | 0 | 3.6296 | 0 | 3.1507 | 0.77157 | 4.0835 | 3.1507 | 0.77157 | 4.0835 | 3.6832 | 0.90198 | 4.0835 | 6.591%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | Tier-2---1 | 521 | 110 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 527.463 | 0 | 0 | 527.463 | 0 | 457.8723 | 6.5287 | 70.1324 | 457.8723 | 6.5287 | 70.1324 | 535.2579 | 7.6321 | 70.1324 | 5.776%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 1 | 127.4062 | 99.28% | 0% | 0.716% | 0.96535 | 0 | 0 | 0.96535 | 0 | 0.83799 | 0.059352 | 14.119 | 0.83799 | 0.059352 | 14.119 | 0.97961 | 0.069383 | 14.119 | 0.7577%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | Tier-2---11 | 38 | 10 | 127.4062 | 99.28% | 0% | 0.716% | 9.6535 | 0 | 0 | 9.6535 | 0 | 8.3799 | 0.59352 | 14.119 | 8.3799 | 0.59352 | 14.119 | 9.7961 | 0.69383 | 14.119 | 7.577%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | Tier-2---11 | 3 | 3 | 6.7153 | 99.02% | 0% | 0.9775% | 1.9284 | 0 | 0 | 1.9284 | 0 | 1.674 | 0.17806 | 9.4015 | 1.674 | 0.17806 | 9.4015 | 1.9569 | 0.20815 | 9.4015 | 28.72%
2028 | 855 | 855-46AE | Tier-2 | Tier-2---15 | Tier-2---11 | 7 | 7 | 188.5529 | 99.88% | 0% | 0.1171% | 54.6163 | 0 | 0 | 54.6163 | 0 | 47.4105 | 0.41546 | 114.1152 | 47.4105 | 0.41546 | 114.1152 | 55.4234 | 0.48568 | 114.1152 | 28.97%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | Tier-2---2 | 557 | 8 | 8606.9717 | 99.86% | 0% | 0.1411% | 35.7989 | 0 | 0 | 35.7989 | 0 | 31.0758 | 0.47481 | 65.4484 | 31.0758 | 0.47481 | 65.4484 | 36.328 | 0.55506 | 65.4484 | 0.4159%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | Tier-3---2 | 33 | 4 | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 223.1048 | 0 | 0 | 223.1048 | 0 | 193.6695 | 0.23741 | 815.7709 | 193.6695 | 0.23741 | 815.7709 | 226.4018 | 0.27753 | 815.7709 | 3.514%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 131 | 28 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 209.7654 | 0 | 0 | 209.7654 | 0 | 182.0901 | 1.6618 | 109.5709 | 182.0901 | 1.6618 | 109.5709 | 212.8654 | 1.9427 | 109.5709 | 6.158%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 295 | 35 | 1554.328 | 69.02% | 30.62% | 0.3611% | 36.9123 | 0 | 0 | 36.9123 | 0 | 32.0423 | 2.0773 | 15.4249 | 32.0423 | 2.0773 | 15.4249 | 37.4578 | 2.4284 | 15.4249 | 2.375%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | Tier-2---2 | 252 | 14 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 24.5819 | 0 | 0 | 24.5819 | 0 | 21.3387 | 0.83092 | 25.6807 | 21.3387 | 0.83092 | 25.6807 | 24.9452 | 0.97136 | 25.6807 | 1.234%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | Tier-2---4 | 36 | 33 | 434.8834 | 99.47% | 0.2691% | 0.2608% | 114.9939 | 0 | 0 | 114.9939 | 0 | 99.8222 | 1.9586 | 50.966 | 99.8222 | 1.9586 | 50.966 | 116.6933 | 2.2896 | 50.966 | 26.44%
2028 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 62 | 36 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 222.2693 | 0 | 0 | 222.2693 | 0 | 192.9442 | 2.1367 | 90.3018 | 192.9442 | 2.1367 | 90.3018 | 225.554 | 2.4978 | 90.3018 | 13.43%
2028 | 968 | 968-476F | Tier-2 | Tier-2---17 | Tier-2---12 | 44 | 20 | 62.492 | 96.91% | 0.773% | 2.32% | 7.9828 | 0 | 0 | 7.9828 | 0 | 6.9296 | 1.187 | 5.8378 | 6.9296 | 1.187 | 5.8378 | 8.1008 | 1.3877 | 5.8378 | 12.77%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 35 | 21 | 387.8494 | 99.7% | 0% | 0.3041% | 67.2806 | 0 | 0 | 67.2806 | 0 | 58.4039 | 1.2464 | 46.8587 | 58.4039 | 1.2464 | 46.8587 | 68.2749 | 1.457 | 46.8587 | 17.35%
2028 | 981 | CB 980 | Tier-2 | Tier-2---12 | Tier-2---7 | 35 | 3 | 387.8494 | 99.7% | 0% | 0.3041% | 9.6115 | 0 | 0 | 9.6115 | 0 | 8.3434 | 0.17806 | 46.8587 | 8.3434 | 0.17806 | 46.8587 | 9.7536 | 0.20815 | 46.8587 | 2.478%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 14 | 10 | 132.7571 | 99.65% | 0% | 0.354% | 27.4023 | 0 | 0 | 27.4023 | 0 | 23.787 | 0.59352 | 40.0781 | 23.787 | 0.59352 | 40.0781 | 27.8073 | 0.69383 | 40.0781 | 20.64%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | Tier-2---11 | 14 | 1 | 132.7571 | 99.65% | 0% | 0.354% | 2.7402 | 0 | 0 | 2.7402 | 0 | 2.3787 | 0.059352 | 40.0781 | 2.3787 | 0.059352 | 40.0781 | 2.7807 | 0.069383 | 40.0781 | 2.064%
2028 | 982 | CB 982 | Tier-2 | missing | missing | 1 | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.059352 | 0 | 0 | 0.059352 | 0 | 0 | 0.069383 | 0 | 0%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 54 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 436.0624 | 0 | 0 | 436.0624 | 0 | 378.5306 | 3.205 | 118.1066 | 378.5306 | 3.205 | 118.1066 | 442.5066 | 3.7467 | 118.1066 | 9.528%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 89 | 1 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 16.3886 | 0 | 0 | 16.3886 | 0 | 14.2263 | 0.059352 | 239.6958 | 14.2263 | 0.059352 | 239.6958 | 16.6308 | 0.069383 | 239.6958 | 0.3231%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | Tier-2---2 | 82 | 7 | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 71.0017 | 0 | 0 | 71.0017 | 0 | 61.6341 | 0.41546 | 148.351 | 61.6341 | 0.41546 | 148.351 | 72.051 | 0.48568 | 148.351 | 2.457%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | Tier-2---1 | 469 | 20 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 112.4014 | 0 | 0 | 112.4014 | 0 | 97.5717 | 1.187 | 82.1979 | 97.5717 | 1.187 | 82.1979 | 114.0624 | 1.3877 | 82.1979 | 1.187%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | Tier-3---1 | 85 | 18 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 309.2095 | 0 | 0 | 309.2095 | 0 | 268.414 | 1.0683 | 251.2463 | 268.414 | 1.0683 | 251.2463 | 313.779 | 1.2489 | 251.2463 | 6.034%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | Tier-3---1 | 98 | 14 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 270.6162 | 0 | 0 | 270.6162 | 0 | 234.9125 | 0.83092 | 282.7126 | 234.9125 | 0.83092 | 282.7126 | 274.6154 | 0.97136 | 282.7126 | 4.087%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | Tier-3---1 | 367 | 79 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1566.951 | 0 | 0 | 1566.951 | 0 | 1360.2156 | 4.6888 | 290.1 | 1360.2156 | 4.6888 | 290.1 | 1590.1076 | 5.4812 | 290.1 | 6.189%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | Tier-3---1 | 472 | 53 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 910.8436 | 0 | 0 | 910.8436 | 0 | 790.6717 | 3.1456 | 251.3549 | 790.6717 | 3.1456 | 251.3549 | 924.3042 | 3.6773 | 251.3549 | 3.207%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | Tier-3---1 | 422 | 372 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 6767.2005 | 0 | 0 | 6767.2005 | 0 | 5874.3711 | 22.0788 | 266.0636 | 5874.3711 | 22.0788 | 266.0636 | 6867.2067 | 25.8104 | 266.0636 | 25.35%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | Tier-2---1 | 534 | 216 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 1824.1712 | 0 | 0 | 1824.1712 | 0 | 1583.4995 | 12.82 | 123.5183 | 1583.4995 | 12.82 | 123.5183 | 1851.129 | 14.9867 | 123.5183 | 11.43%
2028 | 1039 | 351-819R | Tier-2 | Tier-2---1 | Tier-2---1 | 341 | 1 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 19.8502 | 0 | 0 | 19.8502 | 0 | 17.2312 | 0.059352 | 290.3242 | 17.2312 | 0.059352 | 290.3242 | 20.1435 | 0.069383 | 290.3242 | 0.08441%
2028 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 4 | 1 | 54.719 | 98.75% | 1.065% | 0.1855% | 3.9175 | 0 | 0 | 3.9175 | 0 | 3.4006 | 0.059352 | 57.2966 | 3.4006 | 0.059352 | 57.2966 | 3.9754 | 0.069383 | 57.2966 | 7.159%
2028 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | Tier-2---14 | 4 | 3 | 54.719 | 98.75% | 1.065% | 0.1855% | 11.7525 | 0 | 0 | 11.7525 | 0 | 10.2019 | 0.17806 | 57.2966 | 10.2019 | 0.17806 | 57.2966 | 11.9262 | 0.20815 | 57.2966 | 21.48%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | Tier-2---2 | 34 | 1 | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 18.2361 | 0 | 0 | 18.2361 | 0 | 15.8301 | 0.059352 | 266.7172 | 15.8301 | 0.059352 | 266.7172 | 18.5056 | 0.069383 | 266.7172 | 0.8502%
2028 | 1101 | 500-1531 | Tier-2 | Tier-2---10 | Tier-2---4 | 20 | 1 | 800.5503 | 21.6% | 78.32% | 0.07823% | 2.5075 | 0 | 0 | 2.5075 | 0 | 2.1767 | 0.059352 | 36.6739 | 2.1767 | 0.059352 | 36.6739 | 2.5445 | 0.069383 | 36.6739 | 0.3132%
2028 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | Tier-2---4 | 41 | 58 | 1133.279 | 99.72% | 0.1529% | 0.1272% | 463.6185 | 0 | 0 | 463.6185 | 0 | 402.4511 | 3.4424 | 116.9101 | 402.4511 | 3.4424 | 116.9101 | 470.4699 | 4.0242 | 116.9101 | 40.91%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | Tier-2---2 | 24 | 2 | 1646.9837 | 34.54% | 65.41% | 0.04829% | 13.7464 | 0 | 0 | 13.7464 | 0 | 11.9327 | 0.1187 | 100.5257 | 11.9327 | 0.1187 | 100.5257 | 13.9495 | 0.13877 | 100.5257 | 0.8346%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | Tier-3---5 | 58 | 40 | 2215.156 | 94.69% | 5.226% | 0.08401% | 419.5066 | 0 | 0 | 419.5066 | 0 | 364.1591 | 2.3741 | 153.3904 | 364.1591 | 2.3741 | 153.3904 | 425.7061 | 2.7753 | 153.3904 | 18.94%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | Tier-3---3 | 234 | 183 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 1902.8031 | 0 | 0 | 1902.8031 | 0 | 1651.7572 | 10.8614 | 152.0765 | 1651.7572 | 10.8614 | 152.0765 | 1930.9229 | 12.697 | 152.0765 | 21.88%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | Tier-2---7 | 44 | 32 | 411.5414 | 99.65% | 0% | 0.3468% | 86.4968 | 0 | 0 | 86.4968 | 0 | 75.0849 | 1.8993 | 39.5339 | 75.0849 | 1.8993 | 39.5339 | 87.7751 | 2.2202 | 39.5339 | 21.02%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | Tier-2---7 | 34 | 31 | 456.1931 | 99.77% | 0% | 0.2285% | 120.3472 | 0 | 0 | 120.3472 | 0 | 104.4692 | 1.8399 | 56.7798 | 104.4692 | 1.8399 | 56.7798 | 122.1257 | 2.1509 | 56.7798 | 26.38%
2028 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | Tier-2---17 | 2 | 2 | 2.4589 | 98.62% | 0% | 1.38% | 0.70325 | 0 | 0 | 0.70325 | 0 | 0.61047 | 0.1187 | 5.1428 | 0.61047 | 0.1187 | 5.1428 | 0.71364 | 0.13877 | 5.1428 | 28.6%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | Tier-2---8 | 7 | 7 | 158.2514 | 99.48% | 0.3681% | 0.155% | 45.6528 | 0 | 0 | 45.6528 | 0 | 39.6296 | 0.41546 | 95.3869 | 39.6296 | 0.41546 | 95.3869 | 46.3275 | 0.48568 | 95.3869 | 28.85%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | Tier-2---2 | 72 | 59 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 442.1231 | 0 | 0 | 442.1231 | 0 | 383.7917 | 3.5017 | 109.6 | 383.7917 | 3.5017 | 109.6 | 448.6569 | 4.0936 | 109.6 | 23.54%
2028 | 1243 | 991-1206R | Tier-2 | Tier-2---4 | Tier-2---2 | 164 | 1 | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 8.0752 | 0 | 0 | 8.0752 | 0 | 7.0098 | 0.059352 | 118.1066 | 7.0098 | 0.059352 | 118.1066 | 8.1946 | 0.069383 | 118.1066 | 0.1764%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | Tier-2---6 | 116 | 106 | 1438.3629 | 99.75% | 0% | 0.2509% | 380.2097 | 0 | 0 | 380.2097 | 0 | 330.0468 | 6.2913 | 52.461 | 330.0468 | 6.2913 | 52.461 | 385.8285 | 7.3546 | 52.461 | 26.43%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | Tier-2---11 | 9 | 9 | 108.0997 | 99.75% | 0% | 0.2497% | 31.2706 | 0 | 0 | 31.2706 | 0 | 27.1449 | 0.53417 | 50.8175 | 27.1449 | 0.53417 | 50.8175 | 31.7328 | 0.62445 | 50.8175 | 28.93%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 2 | 41.7756 | 94.08% | 0% | 5.924% | 0.29993 | 0 | 0 | 0.29993 | 0 | 0.26036 | 0.1187 | 2.1933 | 0.26036 | 0.1187 | 2.1933 | 0.30436 | 0.13877 | 2.1933 | 0.718%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | Tier-2---12 | 76 | 21 | 41.7756 | 94.08% | 0% | 5.924% | 3.1493 | 0 | 0 | 3.1493 | 0 | 2.7338 | 1.2464 | 2.1933 | 2.7338 | 1.2464 | 2.1933 | 3.1958 | 1.457 | 2.1933 | 7.538%
2028 | 1299 | CB 499 | Tier-2 | Tier-2---19 | Tier-2---15 | 31 | 1 | 19.4193 | 94.64% | 0% | 5.361% | 0.17193 | 0 | 0 | 0.17193 | 0 | 0.14924 | 0.059352 | 2.5146 | 0.14924 | 0.059352 | 2.5146 | 0.17447 | 0.069383 | 2.5146 | 0.8853%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | Tier-3---19 | 6 | 2 | 27.4807 | 90.21% | 9.514% | 0.2799% | 2.3963 | 0 | 0 | 2.3963 | 0 | 2.0801 | 0.1187 | 17.5238 | 2.0801 | 0.1187 | 17.5238 | 2.4317 | 0.13877 | 17.5238 | 8.72%
2028 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | Tier-2---2 | 403 | 5 | 638.0788 | 99.02% | 0% | 0.9838% | 2.2732 | 0 | 0 | 2.2732 | 0 | 1.9733 | 0.29676 | 6.6496 | 1.9733 | 0.29676 | 6.6496 | 2.3068 | 0.34691 | 6.6496 | 0.3563%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 2 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 22.8768 | 0 | 0 | 22.8768 | 0 | 19.8586 | 0.1187 | 167.2957 | 19.8586 | 0.1187 | 167.2957 | 23.2149 | 0.13877 | 167.2957 | 0.6117%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | Tier-2---2 | 94 | 52 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 594.797 | 0 | 0 | 594.797 | 0 | 516.3226 | 3.0863 | 167.2957 | 516.3226 | 3.0863 | 167.2957 | 603.587 | 3.6079 | 167.2957 | 15.9%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | Tier-3---3 | 314 | 138 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 207.5591 | 0 | 0 | 207.5591 | 0 | 180.1749 | 8.1905 | 21.9979 | 180.1749 | 8.1905 | 21.9979 | 210.6265 | 9.5748 | 21.9979 | 10.06%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 433 | 1 | 6920.124 | 97.57% | 2.306% | 0.1195% | 4.5223 | 0 | 0 | 4.5223 | 0 | 3.9257 | 0.059352 | 66.1422 | 3.9257 | 0.059352 | 66.1422 | 4.5891 | 0.069383 | 66.1422 | 0.06535%

## System Protection---->
back to index

## FCP
Falling Conductor Protection - Risk & Cost Benefit | [27 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[28 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [27 empty] | 2026 | 37 | 93535.6293 | 1689.7231 | 1.807% | 21365.8907 | 4009.6947 | 5.3286 | 21365.8907 | 4009.6947 | 5.3286 | 35589.0959 | 4223.9382 | 8.4256
[10 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 27 | 92120.5683 | 1741.3051 | 1.89% | 21003.7956 | 2791.1989 | 7.525 | 21003.7956 | 2791.1989 | 7.525 | 36855.3029 | 3097.4427 | 11.8986
[10 empty] | Capital Cost only in Year 0 | 113.4236 | K$/unit | 2025-05-01 | Removed UG trace ffrom the calculation |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 17 | 95161.5911 | 1785.2136 | 1.876% | 20541.4232 | 1676.4608 | 12.2529 | 20541.4232 | 1676.4608 | 12.2529 | 37969.8585 | 1959.8017 | 19.3743
[10 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To prevent double counting of foundational costs, SDG&E assumes no foundational costs for this program. | [9 empty] | Total 2026-2028 | 81 | 280817.7886 | 5216.2418 | 1.858% | 62911.1095 | 8477.3544 | 7.4211 | 62911.1095 | 8477.3544 | 7.4211 | 110414.2573 | 9281.1827 | 11.8966
[10 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[10 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[10 empty] | Lifetime | 20 | Years | 2025-05-01 | Expected lifetime (defined as 20 years) of the infrastructure
[10 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[10 empty] | Mitigation Effectiveness Estimate (%) | 8% | % | 2025-05-01
[10 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.18 | M$/mile | 2025-05-01 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[14 empty] | [1] | [1] | [1] | [2]
[9 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Circuit OH Miles | OH Miles Protected | Total Unit | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 75 | CB 75 | Tier-3 | Tier-3---21 | Tier-3---17 | 16.86 | 5.2 | 1 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 77.1863 | 0 | 0 | 77.1863 | 0 | 975.9903 | 108.3701 | 9.0061 | 975.9903 | 108.3701 | 9.0061 | 1625.7039 | 114.1605 | 14.2405 | 2.462%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 54.46 | 20.07 | 11 | 4437.6588 | 97.91% | 1.769% | 0.321% | 128.0975 | 0 | 0 | 128.0975 | 0 | 1619.7431 | 1192.0714 | 1.3588 | 1619.7431 | 1192.0714 | 1.3588 | 2698.0009 | 1255.7654 | 2.1485 | 2.887%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | Tier-2---14 | 36.48 | 18.64 | 7 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 136.2958 | 0 | 0 | 136.2958 | 0 | 1723.4073 | 758.5909 | 2.2719 | 1723.4073 | 758.5909 | 2.2719 | 2870.674 | 799.1234 | 3.5923 | 3.992%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | Tier-2---1 | 30.36 | 6.3 | 2 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 276.1538 | 0 | 0 | 276.1538 | 0 | 3491.8568 | 216.7403 | 16.1108 | 3491.8568 | 216.7403 | 16.1108 | 5816.3747 | 228.321 | 25.4746 | 1.65%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | Tier-3---6 | 71.28 | 11.28 | 6 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 506.2077 | 0 | 0 | 506.2077 | 0 | 6400.7995 | 650.2208 | 9.844 | 6400.7995 | 650.2208 | 9.844 | 10661.7914 | 684.9629 | 15.5655 | 1.254%
2026 | 920 | CB 920 | Tier-1 | Non-HFTD---1 | Non-HFTD---11 | 7.51 | 2.48 | 2 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 89.4028 | 0 | 0 | 89.4028 | 0 | 1130.4631 | 216.7403 | 5.2158 | 1130.4631 | 216.7403 | 5.2158 | 1883.0088 | 228.321 | 8.2472 | 2.624%
2026 | 928 | CB 928 | Tier-2 | Tier-2---7 | Tier-2---2 | 5.27 | 1.69 | 1 | 1655.0106 | 79.76% | 20.12% | 0.1245% | 33.8639 | 0 | 0 | 33.8639 | 0 | 428.1956 | 108.3701 | 3.9512 | 428.1956 | 108.3701 | 3.9512 | 713.244 | 114.1605 | 6.2477 | 2.046%
2026 | 1022 | CB 1022 | Tier-3 | missing | missing | 7.77 | 1.67 | 2 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 167.8774 | 0 | 0 | 167.8774 | 0 | 2122.744 | 216.7403 | 9.794 | 2122.744 | 216.7403 | 9.794 | 3535.8479 | 228.321 | 15.4863 | 1.713%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | Tier-2---14 | 9.29 | 3.15 | 2 | 247.9994 | 97.75% | 1.792% | 0.4608% | 6.5756 | 0 | 0 | 6.5756 | 0 | 83.1464 | 216.7403 | 0.38362 | 83.1464 | 216.7403 | 0.38362 | 138.4966 | 228.321 | 0.60659 | 2.651%
2026 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | Tier-3---11 | 22.74 | 7.45 | 3 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 268.0624 | 0 | 0 | 268.0624 | 0 | 3389.5445 | 325.1104 | 10.4258 | 3389.5445 | 325.1104 | 10.4258 | 5645.9535 | 342.4815 | 16.4854 | 2.597%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | Tier-2---6 | 7 | 2.12 | 1 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 30.1375 | 0 | 0 | 30.1375 | 0 | 363.5219 | 103.3777 | 3.5164 | 363.5219 | 103.3777 | 3.5164 | 637.8709 | 114.7201 | 5.5602 | 2.325%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | Tier-2---2 | 45.29 | 3.63 | 1 | 5142.095 | 98.68% | 0.901% | 0.4182% | 32.5362 | 0 | 0 | 32.5362 | 0 | 392.4552 | 103.3777 | 3.7963 | 392.4552 | 103.3777 | 3.7963 | 688.64 | 114.7201 | 6.0028 | 0.6327%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 57.92 | 12.66 | 7 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 71.2665 | 0 | 0 | 71.2665 | 0 | 859.6238 | 723.6442 | 1.1879 | 859.6238 | 723.6442 | 1.1879 | 1508.3796 | 803.0407 | 1.8783 | 1.727%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | Tier-2---1 | 21.11 | 5.35 | 2 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 473.2339 | 0 | 0 | 473.2339 | 0 | 5708.194 | 206.7555 | 27.6084 | 5708.194 | 206.7555 | 27.6084 | 10016.1524 | 229.4402 | 43.6547 | 2.012%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | Tier-2---14 | 11.54 | 2.23 | 1 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 285.9215 | 0 | 0 | 285.9215 | 0 | 3448.814 | 103.3777 | 33.3613 | 3448.814 | 103.3777 | 33.3613 | 6051.6246 | 114.7201 | 52.7512 | 1.536%
2027 | 442 | CB 442 | Tier-3 | missing | missing | 37.31 | 11.01 | 7 | 11572.221 | 88.48% | 11.4% | 0.1243% | 241.7106 | 0 | 0 | 241.7106 | 0 | 2915.5368 | 723.6442 | 4.029 | 2915.5368 | 723.6442 | 4.029 | 5115.8845 | 803.0407 | 6.3706 | 2.089%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | Tier-2---1 | 7.21 | 1.46 | 1 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 139.5554 | 0 | 0 | 139.5554 | 0 | 1683.331 | 103.3777 | 16.2833 | 1683.331 | 103.3777 | 16.2833 | 2953.7363 | 114.7201 | 25.7473 | 1.528%
2027 | 791 | CB 791 | Tier-1 | Non-HFTD---1 | Non-HFTD---7 | 2.62 | 1.52 | 1 | 3349.7594 | 92.58% | 7.304% | 0.116% | 143.9343 | 0 | 0 | 143.9343 | 0 | 1736.1501 | 103.3777 | 16.7942 | 1736.1501 | 103.3777 | 16.7942 | 3046.4179 | 114.7201 | 26.5552 | 4.297%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | Tier-2---2 | 43.04 | 10.11 | 2 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 170.799 | 0 | 0 | 170.799 | 0 | 2060.1944 | 206.7555 | 9.9644 | 2060.1944 | 206.7555 | 9.9644 | 3615.0175 | 229.4402 | 15.7558 | 1.804%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | Tier-2---6 | 36.91 | 11.95 | 4 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 152.2102 | 0 | 0 | 152.2102 | 0 | 1835.9744 | 413.511 | 4.44 | 1835.9744 | 413.511 | 4.44 | 3221.5793 | 458.8804 | 7.0205 | 2.58%
2028 | 182 | CB 182 | Tier-1 | missing | missing | 15.26 | 5.8 | 1 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 341.6704 | 0 | 0 | 341.6704 | 0 | 3931.4041 | 98.6153 | 39.8661 | 3931.4041 | 98.6153 | 39.8661 | 7267.0163 | 115.2825 | 63.0366 | 2.867%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | Tier-2---4 | 31.71 | 17.43 | 4 | 1059.5314 | 80.82% | 18.41% | 0.7661% | 37.6562 | 0 | 0 | 37.6562 | 0 | 433.2887 | 394.4614 | 1.0984 | 433.2887 | 394.4614 | 1.0984 | 800.9138 | 461.1298 | 1.7369 | 3.554%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | Tier-2---2 | 16.23 | 3.66 | 1 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 57.7705 | 0 | 0 | 57.7705 | 0 | 664.7317 | 98.6153 | 6.7407 | 664.7317 | 98.6153 | 6.7407 | 1228.7253 | 115.2825 | 10.6584 | 1.706%
2028 | 300 | CB 300 | Tier-2 | missing | missing | 14.17 | 10.65 | 2 | 754.1323 | 92.41% | 6.882% | 0.7076% | 41.9024 | 0 | 0 | 41.9024 | 0 | 482.1471 | 197.2307 | 2.4446 | 482.1471 | 197.2307 | 2.4446 | 891.2264 | 230.5649 | 3.8654 | 5.556%
2028 | 354 | CB 354 | Tier-2 | Tier-2---19 | Tier-2---11 | 20.6 | 5.04 | 2 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 398.0983 | 0 | 0 | 398.0983 | 0 | 4580.6877 | 197.2307 | 23.225 | 4580.6877 | 197.2307 | 23.225 | 8467.1866 | 230.5649 | 36.7237 | 1.941%
2028 | 411 | CB 411 | Tier-1 | Non-HFTD---17 | Non-HFTD---17 | 27.3 | 5.21 | 2 | 6370.0414 | 98.47% | 1.262% | 0.272% | 95.762 | 0 | 0 | 95.762 | 0 | 1101.8779 | 197.2307 | 5.5867 | 1101.8779 | 197.2307 | 5.5867 | 2036.7697 | 230.5649 | 8.8338 | 1.503%
2028 | 597 | CB 597 | Tier-2 | Tier-2---14 | Tier-2---11 | 16.71 | 3.95 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 339.2372 | 0 | 0 | 339.2372 | 0 | 3903.4072 | 98.6153 | 39.5822 | 3903.4072 | 98.6153 | 39.5822 | 7215.2653 | 115.2825 | 62.5877 | 1.807%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | Tier-2---2 | 34.31 | 6.91 | 3 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 412.2719 | 0 | 0 | 412.2719 | 0 | 4743.7751 | 295.846 | 16.0346 | 4743.7751 | 295.846 | 16.0346 | 8768.646 | 345.8474 | 25.3541 | 1.601%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | Tier-2---2 | 17.49 | 2.02 | 1 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 60.8446 | 0 | 0 | 60.8446 | 0 | 700.1038 | 98.6153 | 7.0993 | 700.1038 | 98.6153 | 7.0993 | 1294.1091 | 115.2825 | 11.2256 | 0.9156%

## EFD
Early Fault Detector - Risk & Cost Benefit | [27 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[28 empty] | Year | Total Units | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [27 empty] | 2026 | 46 | 60993.9474 | 9408.507 | 15.43% | 118966.907 | 1734.1304 | 68.6032 | 118966.907 | 1734.1304 | 68.6032 | 198162.7969 | 1826.7873 | 108.4761
[10 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2027 | 37 | 47534.0231 | 7322.3638 | 15.4% | 88323.0808 | 1330.5864 | 66.3791 | 88323.0808 | 1330.5864 | 66.3791 | 154980.2688 | 1476.5752 | 104.9593
[10 empty] | Capital Cost only in Year 0 | 39.519 | K$/unit | 2025-05-01 | Removed UG trace from the calculation |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2028 | 51 | 88483.8681 | 13931.5964 | 15.74% | 160302.8466 | 1749.5606 | 91.6246 | 160302.8466 | 1749.5606 | 91.6246 | 296312.3025 | 2045.2562 | 144.8778
[10 empty] | Service Drop factor | 0% | % | 2025-05-01 |  |  |  |  | [2] To prevent double counting of foundational costs, SDG&E assumes no foundational costs for this program. | [9 empty] | Total 2026-2028 | 134 | 197011.8387 | 30662.4671 | 15.56% | 367592.8344 | 4814.2774 | 76.3547 | 367592.8344 | 4814.2774 | 76.3547 | 649455.3682 | 5348.6188 | 121.4249
[10 empty] | OH to UG conversion factor | 0% | % | 2025-05-01
[10 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-05-01
[10 empty] | Lifetime | 20 | Years | 2025-05-01 | Expected lifetime (defined as 20 years) of the infrastructure
[10 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-05-01
[10 empty] | Mitigation Effectiveness Estimate (%) | 16% | % | 2025-05-01
[10 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-05-01
[14 empty] | [1] | [1] | [1] | [2]
[9 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Protected miles | Total coverge | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | Tier-3---3 | 22.2 | 100% | 1 | 1558.5389 | 98.56% | 1.214% | 0.2225% | 245.7844 | 0 | 0 | 245.7844 | 0 | 3107.8479 | 37.6985 | 82.4396 | 3107.8479 | 37.6985 | 82.4396 | 5176.7323 | 39.7128 | 130.3544 | 15.77%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | Tier-2---2 | 6.63 | 100% | 3 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 480.09 | 0 | 0 | 480.09 | 0 | 6070.5506 | 113.0955 | 53.6763 | 6070.5506 | 113.0955 | 53.6763 | 10111.6967 | 119.1383 | 84.8736 | 15.81%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | Tier-2---2 | 20.73 | 100% | 3 | 718.991 | 97.57% | 1.357% | 1.072% | 112.2435 | 0 | 0 | 112.2435 | 0 | 1419.276 | 113.0955 | 12.5494 | 1419.276 | 113.0955 | 12.5494 | 2364.0834 | 119.1383 | 19.8432 | 15.61%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | Tier-2---6 | 0.27 | 100% | 1 | 447.7794 | 94.96% | 4.349% | 0.694% | 68.0319 | 0 | 0 | 68.0319 | 0 | 860.2365 | 37.6985 | 22.8189 | 860.2365 | 37.6985 | 22.8189 | 1432.8932 | 39.7128 | 36.0814 | 15.19%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | Tier-3---4 | 4.87 | 100% | 1 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 59.4792 | 0 | 0 | 59.4792 | 0 | 752.0915 | 37.6985 | 19.9502 | 752.0915 | 37.6985 | 19.9502 | 1252.7564 | 39.7128 | 31.5454 | 15.8%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | Tier-2---2 | 0.39 | 100% | 1 | 1181.5361 | 98.38% | 1.316% | 0.2998% | 185.9913 | 0 | 0 | 185.9913 | 0 | 2351.7879 | 37.6985 | 62.3841 | 2351.7879 | 37.6985 | 62.3841 | 3917.3656 | 39.7128 | 98.6425 | 15.74%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | Tier-3---4 | 13.88 | 100% | 1 | 791.3356 | 98.7% | 1.112% | 0.1837% | 124.9736 | 0 | 0 | 124.9736 | 0 | 1580.2427 | 37.6985 | 41.9179 | 1580.2427 | 37.6985 | 41.9179 | 2632.2053 | 39.7128 | 66.2811 | 15.79%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | Tier-3---4 | 1.01 | 100% | 1 | 376.72 | 96.88% | 2.523% | 0.5996% | 58.3931 | 0 | 0 | 58.3931 | 0 | 738.3576 | 37.6985 | 19.5859 | 738.3576 | 37.6985 | 19.5859 | 1229.8799 | 39.7128 | 30.9694 | 15.5%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | Tier-3---1 | 6.48 | 100% | 2 | 4437.6588 | 97.91% | 1.769% | 0.321% | 695.1859 | 0 | 0 | 695.1859 | 0 | 8790.3548 | 75.397 | 116.5876 | 8790.3548 | 75.397 | 116.5876 | 14642.0659 | 79.4255 | 184.3496 | 15.67%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | Tier-3---1 | 1.32 | 100% | 2 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 567.8486 | 0 | 0 | 567.8486 | 0 | 7180.2249 | 75.397 | 95.2323 | 7180.2249 | 75.397 | 95.2323 | 11960.0776 | 79.4255 | 150.5823 | 15.49%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 11.13 | 100% | 1 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 2959.2238 | 0 | 0 | 2959.2238 | 0 | 37418.2328 | 37.6985 | 992.5659 | 37418.2328 | 37.6985 | 992.5659 | 62327.4308 | 39.7128 | 1569.4557 | 15.9%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | Tier-3---3 | 1.06 | 100% | 3 | 2610.8 | 93.6% | 6.065% | 0.3401% | 390.9736 | 0 | 0 | 390.9736 | 0 | 4943.709 | 113.0955 | 43.7127 | 4943.709 | 113.0955 | 43.7127 | 8234.7204 | 119.1383 | 69.119 | 14.98%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | Tier-3---1 | 89.33 | 100% | 6 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 627.3734 | 0 | 0 | 627.3734 | 0 | 7932.8927 | 226.1909 | 35.0717 | 7932.8927 | 226.1909 | 35.0717 | 13213.794 | 238.2766 | 55.4557 | 15.01%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | Tier-3---5 | 5.37 | 100% | 5 | 622.3042 | 87.18% | 11.98% | 0.8373% | 86.8037 | 0 | 0 | 86.8037 | 0 | 1097.5992 | 188.4924 | 5.823 | 1097.5992 | 188.4924 | 5.823 | 1828.2674 | 198.5638 | 9.2075 | 13.95%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | Tier-3---3 | 2.91 | 100% | 3 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 241.6805 | 0 | 0 | 241.6805 | 0 | 3055.9564 | 113.0955 | 27.021 | 3055.9564 | 113.0955 | 27.021 | 5090.2967 | 119.1383 | 42.7259 | 14.85%
2026 | 1079 | CB 1079 | Tier-1 | Non-HFTD---9 | Non-HFTD---15 | 6.13 | 100% | 1 | 15.9736 | 90.06% | 0% | 9.938% | 2.3018 | 0 | 0 | 2.3018 | 0 | 29.1053 | 37.6985 | 0.77205 | 29.1053 | 37.6985 | 0.77205 | 48.4806 | 39.7128 | 1.2208 | 14.41%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 23.27 | 100% | 2 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 851.1739 | 0 | 0 | 851.1739 | 0 | 10762.7627 | 75.397 | 142.7479 | 10762.7627 | 75.397 | 142.7479 | 17927.4994 | 79.4255 | 225.7146 | 13.49%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | Tier-2---2 | 9.23 | 100% | 1 | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 651.6102 | 0 | 0 | 651.6102 | 0 | 8239.3571 | 37.6985 | 218.5594 | 8239.3571 | 37.6985 | 218.5594 | 13724.2708 | 39.7128 | 345.5884 | 15.99%
2026 | 176 | CB 176 | Tier-1 | Non-HFTD---10 | Non-HFTD---20 | 59.02 | 100% | 1 | 15.5544 | 4.631% | 94.88% | 0.4893% | 0.11526 | 0 | 0 | 0.11526 | 0 | 1.4574 | 37.6985 | 0.038658 | 1.4574 | 37.6985 | 0.038658 | 2.4275 | 39.7128 | 0.061127 | 0.741%
2026 | 178 | CB 178 | Tier-1 | Non-HFTD---1 | Non-HFTD---7 | 5.18 | 100% | 1 | 644.514 | 99.63% | 0% | 0.3655% | 102.7453 | 0 | 0 | 102.7453 | 0 | 1299.1744 | 37.6985 | 34.4622 | 1299.1744 | 37.6985 | 34.4622 | 2164.0306 | 39.7128 | 54.4921 | 15.94%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | Tier-2---2 | 92.64 | 100% | 2 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 652.0943 | 0 | 0 | 652.0943 | 0 | 8245.4779 | 75.397 | 109.3609 | 8245.4779 | 75.397 | 109.3609 | 13734.4663 | 79.4255 | 172.9225 | 15.8%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | Tier-2---2 | 54.33 | 100% | 1 | 1263.0316 | 97.68% | 1.949% | 0.3739% | 197.3906 | 0 | 0 | 197.3906 | 0 | 2495.9272 | 37.6985 | 66.2076 | 2495.9272 | 37.6985 | 66.2076 | 4157.4579 | 39.7128 | 104.6882 | 15.63%
2026 | 835 | CB 835 | Tier-2 | Tier-2---17 | Tier-2---11 | 1.57 | 100% | 1 | 42.6475 | 99.43% | 0% | 0.5747% | 6.7844 | 0 | 0 | 6.7844 | 0 | 85.7859 | 37.6985 | 2.2756 | 85.7859 | 37.6985 | 2.2756 | 142.8933 | 39.7128 | 3.5982 | 15.91%
2026 | 920 | CB 920 | Tier-1 | Non-HFTD---1 | Non-HFTD---11 | 14.85 | 100% | 1 | 251.9037 | 99.78% | 0% | 0.2231% | 40.2147 | 0 | 0 | 40.2147 | 0 | 508.4987 | 37.6985 | 13.4886 | 508.4987 | 37.6985 | 13.4886 | 847.0047 | 39.7128 | 21.3283 | 15.96%
2026 | 921 | CB 921 | Tier-1 | missing | missing | 4.91 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 37.6985 | 0 | 0 | 37.6985 | 0 | 0 | 39.7128 | 0 | 0%
2027 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | Tier-2---3 | 6.34 | 100% | 1 | 1005.6854 | 94.09% | 5.81% | 0.1042% | 151.3925 | 0 | 0 | 151.3925 | 0 | 1826.1118 | 35.9618 | 50.7792 | 1826.1118 | 35.9618 | 50.7792 | 3204.2733 | 39.9074 | 80.2926 | 15.05%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 7.77 | 100% | 3 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 1562.1643 | 0 | 0 | 1562.1643 | 0 | 18842.9813 | 107.8854 | 174.6574 | 18842.9813 | 107.8854 | 174.6574 | 33063.7278 | 119.7223 | 276.1701 | 15.94%
2027 | 1286 | CB 1286 | Tier-1 | Non-HFTD---15 | Non-HFTD---24 | 1.15 | 100% | 1 | 2.6947 | 57.45% | 0% | 42.55% | 0.24768 | 0 | 0 | 0.24768 | 0 | 2.9875 | 35.9618 | 0.083075 | 2.9875 | 35.9618 | 0.083075 | 5.2422 | 39.9074 | 0.13136 | 9.191%
2027 | 180 | CB 180 | Tier-1 | Non-HFTD---13 | Non-HFTD---22 | 2.34 | 100% | 1 | 7.7122 | 90.8% | 0% | 9.202% | 1.1204 | 0 | 0 | 1.1204 | 0 | 13.5143 | 35.9618 | 0.3758 | 13.5143 | 35.9618 | 0.3758 | 23.7135 | 39.9074 | 0.59421 | 14.53%
2027 | 181 | CB 181 | Tier-1 | Non-HFTD---15 | Non-HFTD---24 | 3.23 | 100% | 1 | 2.8335 | 82.32% | 0% | 17.68% | 0.37322 | 0 | 0 | 0.37322 | 0 | 4.5018 | 35.9618 | 0.12518 | 4.5018 | 35.9618 | 0.12518 | 7.8993 | 39.9074 | 0.19794 | 13.17%
2027 | 182 | CB 182 | Tier-1 | missing | missing | 18.46 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 183 | CB 183 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 5.6 | 100% | 1 | 128.8021 | 22.66% | 75.77% | 1.57% | 4.6691 | 0 | 0 | 4.6691 | 0 | 56.3188 | 35.9618 | 1.5661 | 56.3188 | 35.9618 | 1.5661 | 98.8224 | 39.9074 | 2.4763 | 3.625%
2027 | 184 | CB 184 | Tier-1 | Non-HFTD---6 | Non-HFTD---12 | 0.53 | 100% | 1 | 52.4866 | 0.7232% | 98.61% | 0.668% | 0.060731 | 0 | 0 | 0.060731 | 0 | 0.73254 | 35.9618 | 0.02037 | 0.73254 | 35.9618 | 0.02037 | 1.2854 | 39.9074 | 0.032209 | 0.1157%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | Tier-2---9 | 12.1 | 100% | 1 | 396.8506 | 79.93% | 19.29% | 0.7702% | 50.7555 | 0 | 0 | 50.7555 | 0 | 612.2184 | 35.9618 | 17.0241 | 612.2184 | 35.9618 | 17.0241 | 1074.2579 | 39.9074 | 26.9187 | 12.79%
2027 | 186 | CB 186 | Tier-1 | Non-HFTD---5 | Non-HFTD---9 | 6.01 | 100% | 1 | 92.3894 | 96.63% | 0% | 3.367% | 14.2847 | 0 | 0 | 14.2847 | 0 | 172.303 | 35.9618 | 4.7913 | 172.303 | 35.9618 | 4.7913 | 302.3396 | 39.9074 | 7.576 | 15.46%
2027 | 187 | CB 187 | Tier-1 | Non-HFTD---7 | Non-HFTD---12 | 4.27 | 100% | 1 | 43.4605 | 90.51% | 0% | 9.49% | 6.2938 | 0 | 0 | 6.2938 | 0 | 75.9163 | 35.9618 | 2.111 | 75.9163 | 35.9618 | 2.111 | 133.21 | 39.9074 | 3.338 | 14.48%
2027 | 188 | CB 188 | Tier-1 | Non-HFTD---1 | Non-HFTD---4 | 11 | 100% | 1 | 378.367 | 98.23% | 0% | 1.765% | 59.47 | 0 | 0 | 59.47 | 0 | 717.3325 | 35.9618 | 19.9471 | 717.3325 | 35.9618 | 19.9471 | 1258.7014 | 39.9074 | 31.5405 | 15.72%
2027 | 189 | CB 189 | Tier-1 | Non-HFTD---7 | Non-HFTD---13 | 5.04 | 100% | 1 | 36.5503 | 96.65% | 0% | 3.352% | 5.652 | 0 | 0 | 5.652 | 0 | 68.1752 | 35.9618 | 1.8958 | 68.1752 | 35.9618 | 1.8958 | 119.6268 | 39.9074 | 2.9976 | 15.46%
2027 | 196 | 196-915AE | Tier-1 | Non-HFTD---16 | Non-HFTD---21 | 0.27 | 100% | 1 | 3.8074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 307 | 307-1492R | Tier-2 | Tier-2---9 | Tier-2---4 | 7 | 100% | 1 | 744.3133 | 92.56% | 7.329% | 0.1099% | 110.2311 | 0 | 0 | 110.2311 | 0 | 1329.618 | 35.9618 | 36.9731 | 1329.618 | 35.9618 | 36.9731 | 2333.0771 | 39.9074 | 58.4622 | 14.81%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | Tier-3---2 | 0.88 | 100% | 1 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 232.5903 | 0 | 0 | 232.5903 | 0 | 2805.5271 | 35.9618 | 78.0141 | 2805.5271 | 35.9618 | 78.0141 | 4922.8508 | 39.9074 | 123.3567 | 15.97%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | Tier-3---1 | 6.02 | 100% | 1 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 2959.2238 | 0 | 0 | 2959.2238 | 0 | 35694.452 | 35.9618 | 992.5659 | 35694.452 | 35.9618 | 992.5659 | 62632.9575 | 39.9074 | 1569.4557 | 15.9%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | Tier-3---5 | 26.37 | 100% | 1 | 1133.0808 | 94.08% | 5.666% | 0.2577% | 170.553 | 0 | 0 | 170.553 | 0 | 2057.2274 | 35.9618 | 57.2059 | 2057.2274 | 35.9618 | 57.2059 | 3609.8114 | 39.9074 | 90.4546 | 15.05%
2027 | 442 | CB 442 | Tier-3 | missing | missing | 39.62 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 770 | CB 770 | Tier-1 | Non-HFTD---13 | Non-HFTD---18 | 4.24 | 100% | 1 | 5.4599 | 68.13% | 0% | 31.87% | 0.5952 | 0 | 0 | 0.5952 | 0 | 7.1794 | 35.9618 | 0.19964 | 7.1794 | 35.9618 | 0.19964 | 12.5977 | 39.9074 | 0.31567 | 10.9%
2027 | 771 | CB 771 | Tier-1 | Non-HFTD---9 | Non-HFTD---15 | 3.29 | 100% | 1 | 24.0595 | 89.94% | 0% | 10.06% | 3.4624 | 0 | 0 | 3.4624 | 0 | 41.7638 | 35.9618 | 1.1613 | 41.7638 | 35.9618 | 1.1613 | 73.2828 | 39.9074 | 1.8363 | 14.39%
2027 | 773 | CB 773 | Tier-2 | missing | missing | 0.67 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 774 | CB 774 | Tier-1 | missing | missing | 0.03 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 775 | CB 775 | Tier-1 | Non-HFTD---17 | Non-HFTD---24 | 2.17 | 100% | 1 | 1.2409 | 63.86% | 0% | 36.14% | 0.12678 | 0 | 0 | 0.12678 | 0 | 1.5293 | 35.9618 | 0.042525 | 1.5293 | 35.9618 | 0.042525 | 2.6834 | 39.9074 | 0.06724 | 10.22%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | Tier-2---12 | 2.68 | 100% | 1 | 55.0677 | 92.66% | 4.028% | 3.312% | 8.1641 | 0 | 0 | 8.1641 | 0 | 98.4764 | 35.9618 | 2.7384 | 98.4764 | 35.9618 | 2.7384 | 172.7963 | 39.9074 | 4.3299 | 14.83%
2027 | 777 | CB 777 | Tier-1 | missing | missing | 0.97 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 1006 | CB 1006 | Tier-2 | missing | missing | 0.52 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | Tier-3---1 | 2.59 | 100% | 2 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 851.1739 | 0 | 0 | 851.1739 | 0 | 10266.9444 | 71.9236 | 142.7479 | 10266.9444 | 71.9236 | 142.7479 | 18015.3793 | 79.8149 | 225.7146 | 13.49%
2027 | 197 | CB 197 | Tier-2 | Tier-2---21 | Tier-2---17 | 2.06 | 100% | 1 | 1.9198 | 98.18% | 0% | 1.817% | 0.30159 | 0 | 0 | 0.30159 | 0 | 3.6378 | 35.9618 | 0.10116 | 3.6378 | 35.9618 | 0.10116 | 6.3833 | 39.9074 | 0.15995 | 15.71%
2027 | 214 | CB 214 | Tier-3 | Tier-3---20 | Tier-3---11 | 63.48 | 100% | 1 | 59.1996 | 99.88% | 0% | 0.1188% | 9.4607 | 0 | 0 | 9.4607 | 0 | 114.1158 | 35.9618 | 3.1732 | 114.1158 | 35.9618 | 3.1732 | 200.2386 | 39.9074 | 5.0176 | 15.98%
2027 | 216 | CB 216 | Tier-3 | missing | missing | 7.18 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 35.9618 | 0 | 0 | 39.9074 | 0 | 0%
2027 | 296 | CB 296 | Tier-2 | Tier-2---19 | Tier-2---11 | 1.04 | 100% | 1 | 39.5699 | 99.22% | 0% | 0.7837% | 6.2816 | 0 | 0 | 6.2816 | 0 | 75.7689 | 35.9618 | 2.1069 | 75.7689 | 35.9618 | 2.1069 | 132.9514 | 39.9074 | 3.3315 | 15.87%
2027 | 329 | CB 329 | Tier-2 | Tier-2---14 | Tier-2---9 | 1.53 | 100% | 1 | 215.2852 | 96.83% | 2.614% | 0.5577% | 33.3532 | 0 | 0 | 33.3532 | 0 | 402.3095 | 35.9618 | 11.1871 | 402.3095 | 35.9618 | 11.1871 | 705.9314 | 39.9074 | 17.6892 | 15.49%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | Tier-3---1 | 16.47 | 100% | 1 | 6920.124 | 97.57% | 2.306% | 0.1195% | 1080.3623 | 0 | 0 | 1080.3623 | 0 | 13031.4378 | 35.9618 | 362.3689 | 13031.4378 | 35.9618 | 362.3689 | 22866.2283 | 39.9074 | 572.9816 | 15.61%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | Tier-3---1 | 53.69 | 100% | 6 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 5569.8417 | 0 | 0 | 5569.8417 | 0 | 64088.9574 | 205.8307 | 311.3674 | 64088.9574 | 205.8307 | 311.3674 | 118465.4356 | 240.6184 | 492.3374 | 15.84%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | Tier-3---1 | 0.02 | 100% | 1 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 1108.3188 | 0 | 0 | 1108.3188 | 0 | 12752.7857 | 34.3051 | 371.746 | 12752.7857 | 34.3051 | 371.746 | 23572.927 | 40.1031 | 587.8086 | 15.71%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | Tier-3---1 | 0.49 | 100% | 2 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 3003.0366 | 0 | 0 | 3003.0366 | 0 | 34554.2108 | 68.6102 | 503.6307 | 34554.2108 | 68.6102 | 503.6307 | 63871.84 | 80.2061 | 796.3461 | 15.95%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | Tier-3---3 | 0.01 | 100% | 1 | 794.3626 | 99.6% | 0.3592% | 0.04176% | 126.5884 | 0 | 0 | 126.5884 | 0 | 1456.5798 | 34.3051 | 42.4596 | 1456.5798 | 34.3051 | 42.4596 | 2692.4195 | 40.1031 | 67.1375 | 15.94%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | Tier-3---1 | 0.05 | 100% | 3 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 1562.1643 | 0 | 0 | 1562.1643 | 0 | 17974.924 | 102.9153 | 174.6574 | 17974.924 | 102.9153 | 174.6574 | 33225.8049 | 120.3092 | 276.1701 | 15.94%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | Tier-3---1 | 0.16 | 100% | 2 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 804.7351 | 0 | 0 | 804.7351 | 0 | 9259.6228 | 68.6102 | 134.9598 | 9259.6228 | 68.6102 | 134.9598 | 17115.979 | 80.2061 | 213.3999 | 15.87%
2028 | 1201 | CB 1201 | Tier-2 | missing | missing | 1.86 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 34.3051 | 0 | 0 | 34.3051 | 0 | 0 | 40.1031 | 0 | 0%
2028 | 1202 | CB 1202 | Tier-2 | missing | missing | 2.89 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 34.3051 | 0 | 0 | 34.3051 | 0 | 0 | 40.1031 | 0 | 0%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | Tier-3---1 | 0.33 | 100% | 2 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 771.3229 | 0 | 0 | 771.3229 | 0 | 8875.1684 | 68.6102 | 129.3564 | 8875.1684 | 68.6102 | 129.3564 | 16405.3331 | 80.2061 | 204.5396 | 15.63%
2028 | 190 | CB 190 | Tier-1 | Non-HFTD---5 | Non-HFTD---17 | 2.2 | 100% | 1 | 50.7497 | 97.95% | 0% | 2.052% | 7.9534 | 0 | 0 | 7.9534 | 0 | 91.5147 | 34.3051 | 2.6677 | 91.5147 | 34.3051 | 2.6677 | 169.1606 | 40.1031 | 4.2181 | 15.67%
2028 | 191 | CB 191 | Tier-1 | Non-HFTD---11 | Non-HFTD---18 | 5.03 | 100% | 1 | 11.195 | 80.08% | 0% | 19.92% | 1.4345 | 0 | 0 | 1.4345 | 0 | 16.5056 | 34.3051 | 0.48114 | 16.5056 | 34.3051 | 0.48114 | 30.5098 | 40.1031 | 0.76078 | 12.81%
2028 | 192 | CB 192 | Tier-1 | Non-HFTD---4 | Non-HFTD---9 | 5.28 | 100% | 1 | 109.5816 | 97.38% | 0% | 2.615% | 17.0745 | 0 | 0 | 17.0745 | 0 | 196.4665 | 34.3051 | 5.727 | 196.4665 | 34.3051 | 5.727 | 363.1592 | 40.1031 | 9.0556 | 15.58%
2028 | 194 | CB 194 | Tier-1 | Non-HFTD---7 | Non-HFTD---12 | 3.91 | 100% | 1 | 41.3648 | 90.26% | 0% | 9.742% | 5.9736 | 0 | 0 | 5.9736 | 0 | 68.7352 | 34.3051 | 2.0036 | 68.7352 | 34.3051 | 2.0036 | 127.0537 | 40.1031 | 3.1682 | 14.44%
2028 | 198 | CB 198 | Tier-1 | Non-HFTD---7 | Non-HFTD---15 | 8.22 | 100% | 1 | 42.3989 | 95.29% | 0% | 4.712% | 6.4642 | 0 | 0 | 6.4642 | 0 | 74.3796 | 34.3051 | 2.1682 | 74.3796 | 34.3051 | 2.1682 | 137.4872 | 40.1031 | 3.4283 | 15.25%
2028 | 199 | CB 199 | Tier-1 | Non-HFTD---5 | Non-HFTD---12 | 5.1 | 100% | 1 | 86.2492 | 95.28% | 0% | 4.716% | 13.1491 | 0 | 0 | 13.1491 | 0 | 151.299 | 34.3051 | 4.4104 | 151.299 | 34.3051 | 4.4104 | 279.669 | 40.1031 | 6.9738 | 15.25%
2028 | 213 | CB 213 | Tier-1 | missing | missing | 0.87 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 34.3051 | 0 | 0 | 34.3051 | 0 | 0 | 40.1031 | 0 | 0%
2028 | 334 | CB 334 | Tier-2 | Tier-2---17 | Tier-2---9 | 9.91 | 100% | 1 | 70.5162 | 95.08% | 0% | 4.917% | 10.7278 | 0 | 0 | 10.7278 | 0 | 123.4387 | 34.3051 | 3.5983 | 123.4387 | 34.3051 | 3.5983 | 228.1707 | 40.1031 | 5.6896 | 15.21%
2028 | 443 | CB 443 | Tier-2 | Tier-2---17 | Tier-2---13 | 3.35 | 100% | 1 | 67.1473 | 98.29% | 0% | 1.71% | 10.5598 | 0 | 0 | 10.5598 | 0 | 121.5056 | 34.3051 | 3.5419 | 121.5056 | 34.3051 | 3.5419 | 224.5975 | 40.1031 | 5.6005 | 15.73%
2028 | 460 | CB 460 | Tier-2 | Tier-2---17 | Tier-2---17 | 1.01 | 100% | 1 | 58.9173 | 99.11% | 0% | 0.8919% | 9.3427 | 0 | 0 | 9.3427 | 0 | 107.501 | 34.3051 | 3.1337 | 107.501 | 34.3051 | 3.1337 | 198.7105 | 40.1031 | 4.955 | 15.86%
2028 | 461 | CB 461 | Tier-2 | Tier-2---15 | Tier-2---13 | 2.86 | 100% | 1 | 101.8709 | 98.65% | 0% | 1.347% | 16.0798 | 0 | 0 | 16.0798 | 0 | 185.0208 | 34.3051 | 5.3934 | 185.0208 | 34.3051 | 5.3934 | 342.0023 | 40.1031 | 8.5281 | 15.78%
2028 | 462 | CB 462 | Tier-2 | Tier-2---19 | Tier-2---13 | 4.95 | 100% | 1 | 42.4238 | 96.69% | 0% | 3.313% | 6.5629 | 0 | 0 | 6.5629 | 0 | 75.5159 | 34.3051 | 2.2013 | 75.5159 | 34.3051 | 2.2013 | 139.5876 | 40.1031 | 3.4807 | 15.47%
2028 | 463 | CB 463 | Tier-2 | Tier-2---17 | Tier-2---7 | 12.94 | 100% | 1 | 99.9729 | 99.18% | 0% | 0.8185% | 15.8647 | 0 | 0 | 15.8647 | 0 | 182.5464 | 34.3051 | 5.3213 | 182.5464 | 34.3051 | 5.3213 | 337.4285 | 40.1031 | 8.414 | 15.87%
2028 | 497 | CB 497 | Tier-1 | Non-HFTD---4 | Non-HFTD---13 | 4.1 | 100% | 1 | 116.2654 | 98.23% | 0% | 1.77% | 18.2733 | 0 | 0 | 18.2733 | 0 | 210.2598 | 34.3051 | 6.1291 | 210.2598 | 34.3051 | 6.1291 | 388.6553 | 40.1031 | 9.6914 | 15.72%
2028 | 498 | CB 498 | Tier-1 | Non-HFTD---11 | Non-HFTD---17 | 0.29 | 100% | 1 | 11.9856 | 98.23% | 0% | 1.767% | 1.8838 | 0 | 0 | 1.8838 | 0 | 21.6759 | 34.3051 | 0.63186 | 21.6759 | 34.3051 | 0.63186 | 40.0668 | 40.1031 | 0.9991 | 15.72%
2028 | 900 | CB 900 | Tier-1 | Non-HFTD---19 | Non-HFTD---22 | 1.68 | 100% | 1 | 0.53356 | 93.68% | 0% | 6.317% | 0.079976 | 0 | 0 | 0.079976 | 0 | 0.92024 | 34.3051 | 0.026825 | 0.92024 | 34.3051 | 0.026825 | 1.701 | 40.1031 | 0.042416 | 14.99%
2028 | 901 | CB 901 | Tier-1 | missing | missing | 1.97 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 34.3051 | 0 | 0 | 34.3051 | 0 | 0 | 40.1031 | 0 | 0%
2028 | 902 | CB 902 | Tier-1 | Non-HFTD---6 | Non-HFTD---12 | 6.9 | 100% | 1 | 88.9578 | 94.13% | 0% | 5.869% | 13.3979 | 0 | 0 | 13.3979 | 0 | 154.1617 | 34.3051 | 4.4938 | 154.1617 | 34.3051 | 4.4938 | 284.9607 | 40.1031 | 7.1057 | 15.06%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | Tier-3---2 | 0.03 | 100% | 1 | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 541.4635 | 0 | 0 | 541.4635 | 0 | 6230.3085 | 34.3051 | 181.6146 | 6230.3085 | 34.3051 | 181.6146 | 11516.4333 | 40.1031 | 287.1709 | 15.89%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | Tier-2---2 | 7.96 | 100% | 2 | 1554.328 | 69.02% | 30.62% | 0.3611% | 171.6511 | 0 | 0 | 171.6511 | 0 | 1975.0905 | 68.6102 | 28.7871 | 1975.0905 | 68.6102 | 28.7871 | 3650.8622 | 80.2061 | 45.5185 | 11.04%
2028 | 920 | 920-823 | Tier-2 | Tier-2---11 | Tier-2---4 | 0.21 | 100% | 2 | 458.2189 | 68.35% | 31.14% | 0.5113% | 50.1079 | 0 | 0 | 50.1079 | 0 | 576.5632 | 68.6102 | 8.4035 | 576.5632 | 68.6102 | 8.4035 | 1065.7501 | 80.2061 | 13.2876 | 10.94%
2028 | 1139 | CB 1139 | Tier-1 | Non-HFTD---17 | Non-HFTD---22 | 2.62 | 100% | 1 | 1.9809 | 88.52% | 0% | 11.48% | 0.28058 | 0 | 0 | 0.28058 | 0 | 3.2284 | 34.3051 | 0.09411 | 3.2284 | 34.3051 | 0.09411 | 5.9676 | 40.1031 | 0.14881 | 14.16%
2028 | 1201 | CB 1201 | Tier-2 | missing | missing | 1.86 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 34.3051 | 0 | 0 | 34.3051 | 0 | 0 | 40.1031 | 0 | 0%
2028 | 1221 | CB 1221 | Tier-1 | missing | missing | 0.34 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 34.3051 | 0 | 0 | 34.3051 | 0 | 0 | 40.1031 | 0 | 0%
2028 | 212 | CB 212 | Tier-2 | Tier-2---19 | Tier-2---11 | 85.2 | 100% | 1 | 22.9809 | 99.09% | 0% | 0.9069% | 3.6436 | 0 | 0 | 3.6436 | 0 | 41.9247 | 34.3051 | 1.2221 | 41.9247 | 34.3051 | 1.2221 | 77.4959 | 40.1031 | 1.9324 | 15.85%
2028 | 221 | CB 221 | Tier-3 | missing | missing | 87.91 | 100% | 1 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 34.3051 | 0 | 0 | 34.3051 | 0 | 0 | 40.1031 | 0 | 0%
2028 | 462 | CB 462 | Tier-2 | Tier-2---19 | Tier-2---13 | 3.16 | 100% | 1 | 42.4238 | 96.69% | 0% | 3.313% | 6.5629 | 0 | 0 | 6.5629 | 0 | 75.5159 | 34.3051 | 2.2013 | 75.5159 | 34.3051 | 2.2013 | 139.5876 | 40.1031 | 3.4807 | 15.47%
2028 | 463 | CB 463 | Tier-2 | Tier-2---17 | Tier-2---7 | 11.39 | 100% | 1 | 99.9729 | 99.18% | 0% | 0.8185% | 15.8647 | 0 | 0 | 15.8647 | 0 | 182.5464 | 34.3051 | 5.3213 | 182.5464 | 34.3051 | 5.3213 | 337.4285 | 40.1031 | 8.414 | 15.87%
2028 | 859 | CB 859 | Tier-1 | Non-HFTD---13 | Non-HFTD---17 | 24.76 | 100% | 1 | 6.3536 | 96.15% | 0% | 3.853% | 0.97741 | 0 | 0 | 0.97741 | 0 | 11.2465 | 34.3051 | 0.32784 | 11.2465 | 34.3051 | 0.32784 | 20.7887 | 40.1031 | 0.51838 | 15.38%
2028 | 920 | CB 920 | Tier-1 | Non-HFTD---1 | Non-HFTD---11 | 15.78 | 100% | 1 | 251.9037 | 99.78% | 0% | 0.2231% | 40.2147 | 0 | 0 | 40.2147 | 0 | 462.7269 | 34.3051 | 13.4886 | 462.7269 | 34.3051 | 13.4886 | 855.329 | 40.1031 | 21.3283 | 15.96%

## Microgrid (Capital)
Microgrid (Capital) - Risk & Cost Benefit
|  | Assumptions | Value | Units | Last Update | Comments | [26 empty] | Summary Table | [7 empty] | WACC | WACC | H.D.R | H.D.R | S.D.R | S.D.R
|  | Mitigation Effectiveness | 100% | % | 2025-04-25 | SME assumption | [26 empty] | ` | Total Units (Microgrid) | BCR (7.45%) | BCR (6.09%) | BCR (2%) | Risk Reduction (K$) | Baseline (K$) | % Risk Reduction | Risk Reduced (K$) Year 20 | Total Cost Capital + O&M (K$) Year 20 | Risk Reduced (K$) Year 20 | Total Cost (K$) Year 20 | Risk Reduced (K$) Year 20 | Total Cost (K$) Year 20
|  | lifetime | 20 | Year | 2025-04-25 | [27 empty] | 2028 | 1 | 6.6899e-06 | 6.064e-06 | 6.9441e-06 | 6.7611 | 6.7611 | 100% | 0.077796 | 11628.8443 | 0.070517 | 11628.8443 | 0.1438 | 20708.581
|  | Microgrid Capital Cost (K$) | 910 | K$ | 2025-04-25 | Based on Capital cost forecasts
|  | O&M Microgrid (K$/Year) | 424 | K$/year | 2025-04-25 | Based on O&M cost forecasts
|  | PSPS Events per year | 1 | events/year | 2025-04-25 | SME assumption
|  |  | Safety Customer Weights --> |  |  | 1 | 1 | 1 | 1 | 10 | 10 | 10 | 1 | 5
[18 empty] | per event | per event | per event | per event | annual | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
# | Year | Actual Segment | Cost (K$) | HFTD | Total Customers | Commercial | Industrial | Residential | MBL | Urgent | Essential | Sensitive | Life Support | AFN | Total Safety Customers | Fatalities | Serious Injuries | Safety (M$) | Reliability (M$) | Financial (M$) | Total Risk Year 0 (M$) | Total Risk Reduction (M$) | Risk Reduced (K$) Year 20 | Total Cost Capital + O&M (K$) Year 20 | BCR (7.45%) | Risk Reduced (K$) Year 20 | Total Cost (K$) Year 20 | BCR (6.09%) | Risk Reduced (K$) Year 20 | Total Cost (K$) Year 20 | BCR (2%) | Risk Reduction %
1 | 2028 | TBD | 910 | Tier 2 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 11 | 1.584e-06 | 6.336e-06 | 3.0294e-05 | 0.0052848 | 0.001446 | 0.0067611 | 0.0067611 | 0.077796 | 11628.8443 | 6.6899e-06 | 0.070517 | 11628.8443 | 6.064e-06 | 0.1438 | 20708.581 | 6.9441e-06 | 100%

## Master Input---->
back to index

## Template
CCC - Risk & Cost Benefit | [26 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[27 empty] | Year | Total Units (miles) | Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | BCR SDR
back to index | [26 empty] | 2025 | 6 | 117.1572 | 1.1603 | 0.9903% | 1.1603 | 1.2749 | 0.91006 | 1.1603 | 1.2749 | 0.91006 | 1.1603 | 0.14787 | 7.8463
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [9 empty] | 2026 | 0 | 0 | 0 | --- | 0 | 0 | #DIV/0! | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Capital Cost (k$/tree) | 0.019111 | K$/unit | 2025-04-17 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes from the SRP program. All risk reduction is considered to fall within the financial attribute. | [9 empty] | 2027 | 0 | 0 | 0 | --- | 0 | 0 | #DIV/0! | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Service Drop factor | 0% | % | 2025-04-17 | Factor to account for Service drop miles | [13 empty] | 2028 | 0 | 0 | 0 | --- | 0 | 0 | #DIV/0! | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | OH to UG conversion factor | 0% | % | 2025-04-17 | Factor to account for OH to UG extra miles | [13 empty] | 2029 | 0 | 0 | 0 | --- | 0 | 0 | #DIV/0! | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Long-term costs (M$/mile/year) Year 0 | 0.005534 | $/unit | 2025-04-17 | Includes ongoingFoundational costs expected over the entire lifespan. | [13 empty] | 2030 | 0 | 0 | 0 | --- | 0 | 0 | #DIV/0! | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Lifetime | 1 | Years | 2025-04-17 | [14 empty] | 2031 | 0 | 0 | 0 | --- | 0 | 0 | #DIV/0! | 0 | 0 | --- | 0 | 0 | ---
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-04-17 | [14 empty] | Total 2025-2031 | 6 | 117.1572 | 1.1603 | 0.9903% | 1.1603 | 1.2749 | 0.91006 | 1.1603 | 1.2749 | 0.91006 | 1.1603 | 0.14787 | 7.8463
[9 empty] | Mitigation Effectiveness Estimate (%) | 1% | % | 2025-04-17
[9 empty] | O&M | 0 | K$/unit
[13 empty] | [1] | [1]
[8 empty] | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR WACC | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR HDR | PV Risk Reduced (K$) Year 55 | PV Total Cost Capital + O&M (K$) Year 55 | BCR SDR | Risk Reduction %
2025 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | Tier-2---12 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 1.1603 | 0 | 0 | 1.1603 | 0.033204 | 1.1603 | 1.2749 | 0.91006 | 1.1603 | 1.2749 | 0.91006 | 1.1603 | 0.14787 | 7.8463 | 0.9903%

## raw_WP_RA
upstreamardfacilityid | Baseline | Wildfire | PSPS | PEDS | Wildfire (%) | PSPS (%) | PEDS (%) | Risk Reduction CCC | Risk Reduction SUG | CCC Safety Risk Reduction | CCC Reliability Risk Reduction | CCC Financial Risk Reduction | SUG Safety Risk Reduction | SUG Reliability Risk Reduction | SUG Financial Risk Reduction | Feeder | back to index |  | upstreamardfacilityid | base_all_sim_total_cost_mean | if_cc_mit_all_sim_total_cost_mean | if_ug_mit_all_sim_total_cost_mean | base_wf_sim_total_cost_mean | if_cc_mit_wf_sim_total_cost_mean | if_ug_mit_wf_sim_total_cost_mean | base_psps_sim_total_cost_mean | if_cc_mit_psps_sim_total_cost_mean | if_ug_mit_psps_sim_total_cost_mean | base_peds_sim_total_cost_mean | base_all_sim_safety_cost_mean | if_cc_mit_all_sim_safety_cost_mean | if_ug_mit_all_sim_safety_cost_mean | base_wf_sim_safety_cost_mean | if_cc_mit_wf_sim_safety_cost_mean | if_ug_mit_wf_sim_safety_cost_mean | base_psps_sim_safety_cost_mean | if_cc_mit_psps_sim_safety_cost_mean | if_ug_mit_psps_sim_safety_cost_mean | base_peds_sim_safety_cost_mean | base_all_sim_financial_cost_mean | if_cc_mit_all_sim_financial_cost_mean | if_ug_mit_all_sim_financial_cost_mean | base_wf_sim_financial_cost_mean | if_cc_mit_wf_sim_financial_cost_mean | if_ug_mit_wf_sim_financial_cost_mean | base_psps_sim_financial_cost_mean | if_cc_mit_psps_sim_financial_cost_mean | if_ug_mit_psps_sim_financial_cost_mean | base_peds_sim_financial_cost_mean | base_all_sim_reliability_cost_mean | if_cc_mit_all_sim_reliability_cost_mean | if_ug_mit_all_sim_reliability_cost_mean | base_wf_sim_reliability_cost_mean | if_cc_mit_wf_sim_reliability_cost_mean | if_ug_mit_wf_sim_reliability_cost_mean | base_psps_sim_reliability_cost_mean | if_cc_mit_psps_sim_reliability_cost_mean | if_ug_mit_psps_sim_reliability_cost_mean | base_peds_sim_reliability_cost_mean | base_wf_sim_events_per_year | if_cc_mit_wf_sim_events_per_year | if_ug_mit_wf_sim_events_per_year | base_psps_sim_events_per_year | if_cc_mit_psps_sim_events_per_year | if_ug_mit_psps_sim_events_per_year | base_peds_sim_events_per_year | num_sim_runs | risk_attitude | Last Updated: | 2025-04-17 | back to index
100-1122R | 1118.7752 | 586.1806 | 0 | 532.5946 | 52.39% | 0% | 47.61% | 344.2444 | 577.8854 | 55.2496 | 13.4511 | 275.5437 | 94.504 | 23.0576 | 460.3239 | 100 |  | 0 | 100-1122R | 1118.7752 | 774.5307 | 540.8898 | 586.1806 | 241.9362 | 8.2952 | 0 | 0 | 0 | 532.5946 | 96.4331 | 41.1835 | 1.9291 | 96.0323 | 40.7827 | 1.5284 | 0 | 0 | 0 | 0.40076 | 515.2325 | 239.6888 | 54.9086 | 466.8513 | 191.3075 | 6.5274 | 0 | 0 | 0 | 48.3813 | 507.1096 | 493.6585 | 484.052 | 23.297 | 9.8459 | 0.23949 | 0 | 0 | 0 | 483.8125 | 0.0014516 | 0.0006286 | 1.62e-05 | 0 | 0 | 0 | 0.0007534 | 5000000 | scaled
1001-1130R | 2758282.9631 | 2661345.2595 | 94204.2314 | 2733.4722 | 96.49% | 3.415% | 0.0991% | 1405158.7473 | 2715638.8148 | 76181.8791 | 40717.6502 | 1288259.218 | 146534.2676 | 84471.3912 | 2484633.156 | 1001 |  | 1 | 1001-1130R | 2758282.9631 | 1353124.2158 | 42644.1483 | 2661345.2595 | 1297445.2565 | 31586.2639 | 94204.2314 | 52945.4872 | 8324.4123 | 2733.4722 | 148325.5545 | 72143.6754 | 1791.2869 | 148157.5028 | 72048.3246 | 1774.5618 | 165.9948 | 93.2939 | 14.6682 | 2.0568 | 2515389.7952 | 1227130.5772 | 30756.6392 | 2506242.2023 | 1221880.6141 | 29721.9384 | 8899.2825 | 5001.6527 | 786.3903 | 248.3105 | 94567.6134 | 53849.9632 | 10096.2222 | 6945.5545 | 3516.3178 | 89.7637 | 85138.9541 | 47850.5406 | 7523.3537 | 2483.1048 | 0.010126 | 0.0047698 | 0.0001212 | 0.092166 | 0.052326 | 0.0092166 | 0.0038744 | 5000000 | scaled
1001-1140R | 1005685.3515 | 946203.319 | 58434.1701 | 1047.8623 | 94.09% | 5.81% | 0.1042% | 473996.1389 | 986348.2331 | 25761.5506 | 25374.6295 | 422859.9588 | 53419.5357 | 52787.9065 | 880140.7909 | 1001 |  | 2 | 1001-1140R | 1005685.3515 | 531689.2126 | 19337.1184 | 946203.319 | 497807.0034 | 13125.2638 | 58434.1701 | 32834.3468 | 5163.9923 | 1047.8623 | 54171.2693 | 28409.7187 | 751.7336 | 54100.343 | 28369.5195 | 744.7468 | 70.1379 | 39.4107 | 6.1983 | 0.78848 | 893046.6978 | 470186.739 | 12905.9069 | 887363.129 | 466951.4218 | 12316.8575 | 5588.3802 | 3140.1287 | 493.8609 | 95.1885 | 58467.3844 | 33092.7549 | 5679.478 | 4739.8471 | 2486.0622 | 63.6595 | 52775.6521 | 29654.8074 | 4663.9331 | 951.8853 | 0.0040564 | 0.002024 | 5.2e-05 | 0.0923 | 0.05239 | 0.00923 | 0.001476 | 5000000 | scaled
1001-1231F | 117157.2378 | 116025.9492 | 1022.2238 | 109.0648 | 99.03% | 0.8725% | 0.09309% | 63034.1964 | 116973.7448 | 3462.2374 | 418.5678 | 59153.3912 | 6389.2641 | 875.2196 | 109709.2611 | 1001 |  | 3 | 1001-1231F | 117157.2378 | 54123.0414 | 183.493 | 116025.9492 | 53444.6614 | 0.031463 | 1022.2238 | 569.3152 | 74.3967 | 109.0648 | 6389.4028 | 2927.1654 | 0.13873 | 6388.5422 | 2926.6498 | 0 | 0.77852 | 0.43359 | 0.05666 | 0.082068 | 109725.1067 | 50571.7154 | 15.8455 | 109633.61 | 50516.3678 | 0 | 81.5891 | 45.4401 | 5.938 | 9.9075 | 1042.7283 | 624.1605 | 167.5087 | 3.7969 | 1.6438 | 0.031463 | 939.8562 | 523.4416 | 68.4021 | 99.0752 | 0.0003102 | 0.0001342 | 3.4e-06 | 0.024629 | 0.014045 | 0.0024628 | 0.0001496 | 5000000 | scaled
1001-1232F | 3708.17 | 3643.4162 | 0 | 64.7538 | 98.25% | 0% | 1.746% | 2872.7027 | 3639.956 | 159.5013 | 668.0566 | 2045.1448 | 194.8038 | 1115.0522 | 2330.1 | 1001 |  | 4 | 1001-1232F | 3708.17 | 835.4673 | 68.214 | 3643.4162 | 770.7135 | 3.4602 | 0 | 0 | 0 | 64.7538 | 194.8525 | 35.3512 | 0.048725 | 194.8038 | 35.3025 | 0 | 0 | 0 | 0 | 0.048725 | 2335.9823 | 290.8375 | 5.8823 | 2330.1 | 284.9552 | 0 | 0 | 0 | 0 | 5.8823 | 1177.3351 | 509.2785 | 62.283 | 1118.5124 | 450.4558 | 3.4602 | 0 | 0 | 0 | 58.8228 | 0.0001606 | 9.24e-05 | 2.4e-06 | 0 | 0 | 0 | 9.3e-05 | 5000000 | scaled
1001-1814AE | 409062.1599 | 405584.4516 | 3156.546 | 321.1622 | 99.15% | 0.7717% | 0.07851% | 138997.6689 | 402330.4094 | 7647.8267 | 1273.4063 | 130076.4359 | 21929.4209 | 2655.7067 | 377745.2818 | 1001 |  | 5 | 1001-1814AE | 409062.1599 | 270064.491 | 6731.7505 | 405584.4516 | 267968.0277 | 6131.6042 | 3156.546 | 1775.3011 | 278.984 | 321.1622 | 22283.2362 | 14635.4095 | 353.8152 | 22280.5905 | 14633.8157 | 353.3611 | 2.404 | 1.3521 | 0.21247 | 0.24166 | 383574.7954 | 253498.3595 | 5829.5137 | 383293.6801 | 253327.4887 | 5778.0719 | 251.9407 | 141.6962 | 22.2672 | 29.1746 | 3204.1283 | 1930.722 | 548.4216 | 10.181 | 6.7232 | 0.17124 | 2902.2014 | 1632.2528 | 256.5044 | 291.746 | 0.001377 | 0.0008758 | 2.24e-05 | 0.092384 | 0.052484 | 0.0092384 | 0.000452 | 5000000 | scaled
1001-1820F | 4222247.108 | 3859583.2958 | 358314.2717 | 4349.5404 | 91.41% | 8.486% | 0.103% | 2113504.6177 | 4158865.0737 | 111530.0098 | 143557.472 | 1858417.1359 | 219477.7403 | 300236.4669 | 3639150.8665 | 1001 |  | 6 | 1001-1820F | 4222247.108 | 2108742.4903 | 63382.0342 | 3859583.2958 | 1902614.5292 | 26827.7235 | 358314.2717 | 201778.4206 | 32204.7703 | 4349.5404 | 221124.9717 | 109594.9619 | 1647.2314 | 220571.6984 | 109281.9659 | 1594.5253 | 550.0004 | 309.7231 | 49.4332 | 3.2729 | 3667749.786 | 1809332.6501 | 28598.9195 | 3633248.9713 | 1789731.5062 | 25138.4332 | 34105.6995 | 19206.0287 | 3065.3711 | 395.1152 | 333372.3502 | 189814.8782 | 33135.8833 | 5762.6261 | 3601.0571 | 94.7651 | 323658.5718 | 182262.6688 | 29089.9659 | 3951.1523 | 0.018664 | 0.0096044 | 0.0002442 | 0.10374 | 0.058922 | 0.010374 | 0.0060576 | 5000000 | scaled
1001-1821F | 4094.1428 | 0 | 4094.1428 | 0 | 0% | 100% | 0% | 228.523 | 474.9034 | 0.2685 | 194.4875 | 33.767 | 0.55799 | 404.1728 | 70.1726 | 1001 |  | 7 | 1001-1821F | 4094.1428 | 3865.6198 | 3619.2393 | 0 | 0 | 0 | 4094.1428 | 3865.6198 | 3619.2393 | 0 | 4.8104 | 4.5419 | 4.2524 | 0 | 0 | 0 | 4.8104 | 4.5419 | 4.2524 | 0 | 604.9584 | 571.1914 | 534.7857 | 0 | 0 | 0 | 604.9584 | 571.1914 | 534.7857 | 0 | 3484.374 | 3289.8865 | 3080.2011 | 0 | 0 | 0 | 3484.374 | 3289.8865 | 3080.2011 | 0 | 0 | 0 | 0 | 0.092451 | 0.092451 | 0.092451 | 0 | 5000000 | scaled
1006-829F | 114530.0544 | 114255.809 | 0 | 274.2453 | 99.76% | 0% | 0.2395% | 43282.5829 | 113103.7358 | 4059.0574 | 2.1043 | 39221.4212 | 10269.6456 | 4.5809 | 102829.5093 | 1006 |  | 8 | 1006-829F | 114530.0544 | 71247.4715 | 1426.3185 | 114255.809 | 70973.2261 | 1152.0732 | 0 | 0 | 0 | 274.2453 | 10384.5424 | 6325.485 | 114.8968 | 10384.336 | 6325.2787 | 114.6904 | 0 | 0 | 0 | 0.20636 | 103891.7426 | 64670.3214 | 1062.2334 | 103866.83 | 64645.4087 | 1037.3207 | 0 | 0 | 0 | 24.9126 | 253.7694 | 251.6651 | 249.1884 | 4.643 | 2.5388 | 0.062075 | 0 | 0 | 0 | 249.1263 | 0.001818 | 0.0009892 | 2.5e-05 | 0 | 0 | 0 | 0.0003932 | 5000000 | scaled
1021-14F | 1554.9669 | 0 | 1554.9669 | 0 | 0% | 100% | 0% | 82.6888 | 171.9447 | 1.0727 | 64.7525 | 16.8635 | 2.2307 | 134.6476 | 35.0664 | 1021 |  | 9 | 1021-14F | 1554.9669 | 1472.2781 | 1383.0222 | 0 | 0 | 0 | 1554.9669 | 1472.2781 | 1383.0222 | 0 | 20.1729 | 19.1002 | 17.9422 | 0 | 0 | 0 | 20.1729 | 19.1002 | 17.9422 | 0 | 317.1197 | 300.2561 | 282.0533 | 0 | 0 | 0 | 317.1197 | 300.2561 | 282.0533 | 0 | 1217.6743 | 1152.9218 | 1083.0267 | 0 | 0 | 0 | 1217.6743 | 1152.9218 | 1083.0267 | 0 | 0 | 0 | 0 | 0.097521 | 0.097521 | 0.097521 | 0 | 5000000 | scaled
1021-16F | 775.228 | 0 | 775.228 | 0 | 0% | 100% | 0% | 41.3621 | 85.905 | 0.5366 | 32.3901 | 8.4354 | 1.1145 | 67.2711 | 17.5194 | 1021 |  | 10 | 1021-16F | 775.228 | 733.8659 | 689.323 | 0 | 0 | 0 | 775.228 | 733.8659 | 689.323 | 0 | 10.0572 | 9.5206 | 8.9427 | 0 | 0 | 0 | 10.0572 | 9.5206 | 8.9427 | 0 | 158.0999 | 149.6645 | 140.5804 | 0 | 0 | 0 | 158.0999 | 149.6645 | 140.5804 | 0 | 607.071 | 574.6808 | 539.7999 | 0 | 0 | 0 | 607.071 | 574.6808 | 539.7999 | 0 | 0 | 0 | 0 | 0.097212 | 0.097212 | 0.097212 | 0 | 5000000 | scaled
1021-1748F | 35156122.4002 | 34811510.8905 | 331735.5921 | 12875.9176 | 99.02% | 0.9436% | 0.03662% | 16187397.1505 | 34567679.6556 | 1046877.9819 | 136757.9171 | 15003761.2515 | 2236411.3435 | 286657.3501 | 32044610.962 | 1021 |  | 11 | 1021-1748F | 35156122.4002 | 18968725.2497 | 588442.7446 | 34811510.8905 | 18769132.9027 | 546089.2421 | 331735.5921 | 186716.4294 | 29477.5849 | 12875.9176 | 2271850.052 | 1224972.0701 | 35438.7085 | 2271414.7203 | 1224722.8094 | 35391.1977 | 425.643 | 239.572 | 37.8221 | 9.6887 | 32559049.5107 | 17555288.2593 | 514438.5488 | 32526717.0743 | 17536578.7209 | 510499.8083 | 31162.7793 | 17539.8812 | 2769.0833 | 1169.6572 | 325222.8375 | 188464.9204 | 38565.4874 | 13379.0959 | 7831.3724 | 198.236 | 300147.1698 | 168936.9762 | 26670.6796 | 11696.5718 | 0.051371 | 0.027669 | 0.0007104 | 0.096065 | 0.054604 | 0.0096064 | 0.0182 | 5000000 | scaled
1021-1760R | 7055715.6839 | 6926992.6786 | 126531.8319 | 2191.1734 | 98.18% | 1.793% | 0.03106% | 3522182.7955 | 6965460.4233 | 218723.4429 | 50665.0059 | 3252794.3466 | 432418.2816 | 105589.7427 | 6427452.3991 | 1021 |  | 12 | 1021-1760R | 7055715.6839 | 3533532.8885 | 90255.2606 | 6926992.6786 | 3460119.9683 | 76816.475 | 126531.8319 | 71221.7468 | 11247.6122 | 2191.1734 | 437384.2832 | 218660.8402 | 4966.0016 | 437166.7837 | 218537.6943 | 4945.1655 | 215.8507 | 121.4972 | 19.1873 | 1.6488 | 6500527.3669 | 3247733.0203 | 73074.9678 | 6488886.478 | 3241093.6334 | 71858.837 | 11441.8412 | 6440.3392 | 1017.0831 | 199.0477 | 117804.0339 | 67139.0279 | 12214.2912 | 939.417 | 488.6407 | 12.4725 | 114874.14 | 64659.9103 | 10211.3418 | 1990.4769 | 0.0083966 | 0.0042932 | 0.0001096 | 0.096787 | 0.055013 | 0.0096788 | 0.0031074 | 5000000 | scaled
1021-25R | 18825689.9208 | 18768978.8338 | 52369.3413 | 4341.7458 | 99.7% | 0.2782% | 0.02306% | 8115433.846 | 18558061.1277 | 531159.0921 | 20837.8343 | 7563436.9197 | 1213173.9142 | 43437.2592 | 17301449.9543 | 1021 |  | 13 | 1021-25R | 18825689.9208 | 10710256.0747 | 267628.7931 | 18768978.8338 | 10676442.6112 | 258631.4711 | 52369.3413 | 29471.7178 | 4655.5762 | 4341.7458 | 1229855.2446 | 698696.1525 | 16681.3303 | 1229760.6411 | 698641.4844 | 16669.9436 | 91.3364 | 51.4011 | 8.1197 | 3.267 | 17544293.2196 | 9980856.3 | 242843.2654 | 17538271.2587 | 9977294.8933 | 241948.5749 | 5627.5537 | 3166.9995 | 500.2833 | 394.4072 | 51541.4566 | 30703.6223 | 8104.1973 | 946.9339 | 506.2335 | 12.9525 | 46650.4511 | 26253.3172 | 4147.1732 | 3944.0716 | 0.020462 | 0.011145 | 0.0002834 | 0.096999 | 0.05512 | 0.0096998 | 0.0061486 | 5000000 | scaled
1021-855 | 5034375.2727 | 5009473.3713 | 22862.7294 | 2039.172 | 99.51% | 0.4541% | 0.0405% | 2323134.2104 | 4931060.4403 | 116842.0994 | 9099.3224 | 2197192.7887 | 248201.5838 | 18961.6486 | 4663897.2079 | 1021 |  | 14 | 1021-855 | 5034375.2727 | 2711241.0622 | 103314.8324 | 5009473.3713 | 2696338.6359 | 99242.6396 | 22862.7294 | 12863.2543 | 2033.0208 | 2039.172 | 253082.8932 | 136240.7938 | 4881.3094 | 253064.2676 | 136229.6434 | 4878.2552 | 17.0911 | 9.616 | 1.5198 | 1.5344 | 4758641.2735 | 2561448.4848 | 94744.0656 | 4756243.4273 | 2560018.3665 | 94362.0744 | 2212.6064 | 1244.8785 | 196.7514 | 185.2398 | 22651.106 | 13551.7836 | 3689.4574 | 165.6764 | 90.626 | 2.31 | 20633.0318 | 11608.7599 | 1834.7495 | 1852.3978 | 0.0089948 | 0.004926 | 0.000125 | 0.097178 | 0.055209 | 0.0097178 | 0.0029158 | 5000000 | scaled
1021-883R | 1386629.8745 | 1380794.9907 | 5282.084 | 552.7998 | 99.58% | 0.3809% | 0.03987% | 636041.0458 | 1354346.098 | 31838.8765 | 2133.8843 | 602068.2849 | 68370.1803 | 4445.8029 | 1281530.1148 | 1021 |  | 15 | 1021-883R | 1386629.8745 | 750588.8287 | 32283.7765 | 1380794.9907 | 747063.4538 | 31261.3016 | 5282.084 | 2972.5751 | 469.6751 | 552.7998 | 69917.1709 | 38078.2943 | 1546.9906 | 69912.7321 | 38075.6145 | 1546.2169 | 4.0228 | 2.2639 | 0.3577 | 0.41596 | 1311332.6196 | 709264.3347 | 29802.5049 | 1310860.8118 | 708976.861 | 29714.8009 | 421.5911 | 237.257 | 37.4873 | 50.2167 | 5380.0839 | 3246.1996 | 934.281 | 21.4467 | 10.9783 | 0.28377 | 4856.4701 | 2733.0542 | 431.8301 | 502.1671 | 0.002428 | 0.0013364 | 3.42e-05 | 0.097208 | 0.055234 | 0.0097208 | 0.000783 | 5000000 | scaled
1021-92 | 794362.5658 | 791177.5446 | 2853.327 | 331.6943 | 99.6% | 0.3592% | 0.04176% | 309470.6214 | 777111.7746 | 15552.9894 | 1063.7963 | 292853.8357 | 39283.1978 | 2219.2255 | 735609.3513 | 1021 |  | 16 | 1021-92 | 794362.5658 | 484891.9444 | 17250.7912 | 791177.5446 | 482953.9386 | 16665.3723 | 2853.327 | 1606.3115 | 253.7246 | 331.6943 | 40104.8019 | 24551.8125 | 821.6041 | 40102.5398 | 24550.43 | 821.1755 | 2.0124 | 1.1329 | 0.17895 | 0.24959 | 751521.0881 | 458667.2524 | 15911.7369 | 751069.1455 | 458399.6578 | 15844.097 | 421.8113 | 237.4633 | 37.5085 | 30.1313 | 2736.6758 | 1672.8795 | 517.4503 | 5.8593 | 3.8509 | 0.099736 | 2429.5032 | 1367.7153 | 216.0372 | 301.3134 | 0.0012864 | 0.0008502 | 2.18e-05 | 0.097262 | 0.05528 | 0.0097262 | 0.0004652 | 5000000 | scaled
1022-17F | 9800679.2209 | 9763526.9192 | 33870.5622 | 3281.7394 | 99.62% | 0.3456% | 0.03348% | 4321365.2599 | 9696245.4914 | 259087.1284 | 13588.7702 | 4048689.3612 | 580679.8936 | 28325.5289 | 9087240.0689 | 1022 |  | 17 | 1022-17F | 9800679.2209 | 5479313.961 | 104433.7295 | 9763526.9192 | 5457020.4486 | 98164.9079 | 33870.5622 | 19011.773 | 2987.0821 | 3281.7394 | 586616.8053 | 327529.6769 | 5936.9117 | 586563.6707 | 327498.7688 | 5929.9741 | 50.6652 | 28.4387 | 4.4682 | 2.4694 | 9180073.3727 | 5131384.0114 | 92833.3038 | 9176251.9757 | 5129108.2545 | 92224.4663 | 3523.2815 | 1977.6415 | 310.7221 | 298.1155 | 33989.0429 | 20400.2727 | 5663.514 | 711.2728 | 413.4253 | 10.4676 | 30296.6155 | 17005.6928 | 2671.8918 | 2981.1546 | 0.014095 | 0.0078516 | 0.000199 | 0.090782 | 0.051484 | 0.0090782 | 0.0045734 | 5000000 | scaled
1022-26R | 694720.3524 | 689284.7819 | 5189.1765 | 246.3939 | 99.22% | 0.7469% | 0.03547% | 200440.9009 | 686640.458 | 9986.9285 | 2015.1729 | 188438.7994 | 34491.4672 | 4194.5125 | 647954.4783 | 1022 |  | 18 | 1022-26R | 694720.3524 | 494279.4515 | 8079.8943 | 689284.7819 | 491119.8376 | 7375.6776 | 5189.1765 | 2913.22 | 457.8229 | 246.3939 | 34907.7651 | 24920.8366 | 416.2979 | 34903.7793 | 24918.5176 | 415.7772 | 3.8004 | 2.1335 | 0.33529 | 0.1854 | 654989.253 | 466550.4536 | 7034.7747 | 654369.4486 | 466192.6765 | 6959.6837 | 597.4218 | 335.3945 | 52.7084 | 22.3826 | 4823.3342 | 2808.1613 | 628.8217 | 11.554 | 8.6435 | 0.21672 | 4587.9543 | 2575.6919 | 404.7791 | 223.8259 | 0.0011886 | 0.0008762 | 2.22e-05 | 0.091119 | 0.051685 | 0.0091118 | 0.0003546 | 5000000 | scaled
1022-322R | 5072199.4815 | 5029594.3965 | 40132.4725 | 2472.6125 | 99.16% | 0.7912% | 0.04875% | 2293396.1318 | 5004833.7998 | 143554.855 | 16013.4705 | 2133827.8063 | 312351.068 | 33318.0047 | 4659164.7272 | 1022 |  | 19 | 1022-322R | 5072199.4815 | 2778803.3497 | 67365.6817 | 5029594.3965 | 2753792.4137 | 61352.4279 | 40132.4725 | 22538.3235 | 3540.6413 | 2472.6125 | 316372.6732 | 172817.8182 | 4021.6052 | 316318.5352 | 172786.5987 | 4015.1325 | 52.2774 | 29.3589 | 4.6121 | 1.8606 | 4717068.7193 | 2583240.913 | 57903.9922 | 4712909.4068 | 2580806.5796 | 57332.2441 | 3934.6987 | 2209.7196 | 347.1343 | 224.6138 | 38758.089 | 22744.6185 | 5440.0843 | 366.4545 | 199.2354 | 5.0513 | 36145.4964 | 20299.245 | 3188.8949 | 2246.1381 | 0.011253 | 0.0060686 | 0.0001544 | 0.091155 | 0.051729 | 0.0091154 | 0.0034584 | 5000000 | scaled
1023-200R | 2889973.2177 | 2868050.8454 | 19336.8689 | 2585.5034 | 99.24% | 0.6691% | 0.08946% | 972620.234 | 2842025.5966 | 52582.2706 | 7730.515 | 912307.4484 | 153671.3385 | 16220.8669 | 2672133.3913 | 1023 |  | 20 | 1023-200R | 2889973.2177 | 1917352.9837 | 47947.6211 | 2868050.8454 | 1903929.3076 | 43715.8702 | 19336.8689 | 10838.1727 | 1646.2475 | 2585.5034 | 156015.0359 | 103432.7653 | 2343.6975 | 155992.7446 | 103419.4161 | 2340.0198 | 20.3459 | 11.4037 | 1.7321 | 1.9455 | 2713900.3021 | 1801592.8537 | 41766.9109 | 2711765.7879 | 1800293.2476 | 41370.3154 | 1899.6453 | 1064.7372 | 161.7266 | 234.8689 | 20057.8797 | 12327.3647 | 3837.0128 | 292.3129 | 216.6439 | 5.535 | 17416.8777 | 9762.0317 | 1482.7887 | 2348.689 | 0.011031 | 0.0071706 | 0.0001822 | 0.068467 | 0.038881 | 0.0068466 | 0.0036162 | 5000000 | scaled
1023-46AE | 9469914.9237 | 9089006.5352 | 367772.8429 | 13135.5456 | 95.98% | 3.884% | 0.1387% | 4307850.4551 | 9310162.1857 | 233027.4006 | 148000.0753 | 3926822.9792 | 502322.0169 | 309509.6012 | 8498330.5677 | 1023 |  | 21 | 1023-46AE | 9469914.9237 | 5162064.4686 | 159752.738 | 9089006.5352 | 4942771.8326 | 115351.6313 | 367772.8429 | 206157.0904 | 31265.5611 | 13135.5456 | 508813.3881 | 275785.9875 | 6491.3712 | 508250.8337 | 275466.3011 | 6434.5028 | 552.6703 | 309.8024 | 46.9843 | 9.8841 | 8611351.8955 | 4684528.9162 | 113021.3278 | 8574780.0136 | 4663503.9831 | 108820.433 | 35378.6399 | 19831.6912 | 3007.6528 | 1193.242 | 349749.6401 | 201749.5648 | 40240.039 | 5975.6879 | 3801.5485 | 96.6955 | 331841.5327 | 186015.5968 | 28210.924 | 11932.4195 | 0.053269 | 0.027688 | 0.000703 | 0.06737 | 0.03826 | 0.006737 | 0.018496 | 5000000 | scaled
1023-48R | 3773847.2966 | 3675353.5853 | 88211.5049 | 10282.2064 | 97.39% | 2.337% | 0.2725% | 1935829.3664 | 3694279.9494 | 114833.9069 | 36447.6084 | 1784547.8511 | 218953.6664 | 75721.9765 | 3399604.3066 | 1023 |  | 22 | 1023-48R | 3773847.2966 | 1838017.9302 | 79567.3472 | 3675353.5853 | 1778311.6468 | 61786.9679 | 88211.5049 | 49424.0771 | 7498.1729 | 10282.2064 | 222705.0283 | 107871.1214 | 3751.3619 | 222570.2324 | 107792.1945 | 3732.8246 | 127.0588 | 71.1899 | 10.8003 | 7.737 | 3459407.6281 | 1674859.7769 | 59803.3215 | 3448189.3157 | 1668163.5546 | 57995.0932 | 10284.2697 | 5762.1797 | 874.1857 | 934.0427 | 91734.6403 | 55287.0319 | 16012.6638 | 4594.0372 | 2355.8977 | 59.0501 | 77800.1764 | 43590.7075 | 6613.187 | 9340.4267 | 0.046087 | 0.02204 | 0.0005604 | 0.067662 | 0.038409 | 0.0067662 | 0.014413 | 5000000 | scaled
1023-89R | 585508.6346 | 513362.5128 | 69359.9995 | 2786.1223 | 87.68% | 11.85% | 0.4758% | 320967.4105 | 572759.3962 | 19389.3598 | 27595.4835 | 273982.5671 | 34311.877 | 57390.7617 | 481056.7575 | 1023 |  | 23 | 1023-89R | 585508.6346 | 264541.2241 | 12749.2384 | 513362.5128 | 222876.0405 | 4068.1573 | 69359.9995 | 38879.0614 | 5894.9588 | 2786.1223 | 34609.611 | 15220.2512 | 297.734 | 34528.0498 | 15173.6115 | 288.8837 | 79.4647 | 44.5432 | 6.7538 | 2.0965 | 485675.5143 | 211692.9472 | 4618.7568 | 478476.0734 | 207546.1475 | 3775.2882 | 6946.3476 | 3893.7064 | 590.3753 | 253.0933 | 65223.5093 | 37628.0258 | 7832.7477 | 358.3896 | 156.2814 | 3.9854 | 62334.1871 | 34940.8118 | 5297.8297 | 2530.9326 | 0.011787 | 0.005512 | 0.00014 | 0.06766 | 0.038423 | 0.006766 | 0.0039564 | 5000000 | scaled
1030-1728R | 5124158.6734 | 5035020.7149 | 87660.8236 | 1477.1349 | 98.26% | 1.711% | 0.02883% | 2308438.9048 | 5013609.7 | 129870.2863 | 35077.3675 | 2143491.251 | 281747.3906 | 73260.3897 | 4658601.9196 | 1030 |  | 24 | 1030-1728R | 5124158.6734 | 2815719.7686 | 110548.9734 | 5035020.7149 | 2764620.1458 | 100751.4178 | 87660.8236 | 49622.4879 | 8320.4207 | 1477.1349 | 287496.9475 | 157626.6611 | 5749.5568 | 287398.4634 | 157570.4295 | 5739.2031 | 97.3726 | 55.1201 | 9.2422 | 1.1115 | 4754406.3808 | 2610915.1299 | 95804.4612 | 4747277.9668 | 2606821.6961 | 95006.4124 | 6994.2301 | 3959.2498 | 663.8648 | 134.1839 | 82255.345 | 47177.9776 | 8994.9554 | 344.2847 | 228.0201 | 5.8023 | 80569.2209 | 45608.1181 | 7647.3136 | 1341.8395 | 0.0075448 | 0.004265 | 0.0001084 | 0.22578 | 0.12836 | 0.022578 | 0.0021176 | 5000000 | scaled
1030-1777 | 11817577.2193 | 11650337.6053 | 163206.4337 | 4033.1803 | 98.58% | 1.381% | 0.03413% | 4420841.3006 | 11626288.9681 | 232933.6804 | 66648.2895 | 4121259.3307 | 613582.8663 | 140982.6217 | 10871723.48 | 1030 |  | 25 | 1030-1777 | 11817577.2193 | 7396735.9187 | 191288.2513 | 11650337.6053 | 7300267.4116 | 171770.0486 | 163206.4337 | 92435.3268 | 15485.0224 | 4033.1803 | 623052.9952 | 390119.3148 | 9470.1289 | 622757.6783 | 389950.74 | 9439.3623 | 292.2821 | 165.54 | 27.7317 | 3.0348 | 11035698.4283 | 6914439.0976 | 163974.9483 | 11020642.6917 | 6905753.0992 | 162214.8453 | 14689.3597 | 8319.6216 | 1393.7261 | 366.3769 | 158825.7958 | 92177.5063 | 17843.1741 | 6937.2354 | 4563.5724 | 115.8409 | 148224.7918 | 83950.1652 | 14063.5646 | 3663.7686 | 0.016484 | 0.010352 | 0.000273 | 0.22414 | 0.1275 | 0.022414 | 0.0056742 | 5000000 | scaled
1030-1823F | 2150973.8719 | 2139065.0261 | 11371.7045 | 537.1412 | 99.45% | 0.5287% | 0.02497% | 803263.8144 | 2109038.4013 | 40224.614 | 4459.4945 | 758579.7059 | 105932.8489 | 9319.0459 | 1993786.5065 | 1030 |  | 26 | 1030-1823F | 2150973.8719 | 1347710.0575 | 41935.4705 | 2139065.0261 | 1340771.1267 | 40381.4905 | 11371.7045 | 6401.7896 | 1016.8388 | 537.1412 | 107915.9334 | 67691.3194 | 1983.0844 | 107878.8317 | 67670.2561 | 1979.3988 | 36.6975 | 20.6591 | 3.2814 | 0.40418 | 2032343.798 | 1273764.0922 | 38557.2915 | 2031086.2888 | 1273034.8424 | 38400.416 | 1208.715 | 680.4555 | 108.0813 | 48.7943 | 10714.1405 | 6254.6459 | 1395.0946 | 99.9056 | 66.0282 | 1.6757 | 10126.2921 | 5700.675 | 905.4761 | 487.9428 | 0.0034008 | 0.0020876 | 5.26e-05 | 0.10191 | 0.057891 | 0.010191 | 0.0007404 | 5000000 | scaled
1030-18R | 6620909.8177 | 6532115.4055 | 86685.2051 | 2109.2071 | 98.66% | 1.309% | 0.03186% | 1986638.4447 | 6511385.7742 | 108648.4015 | 34379.2165 | 1843610.8267 | 357898.1969 | 71768.8057 | 6081718.7715 | 1030 |  | 27 | 1030-18R | 6620909.8177 | 4634271.373 | 109524.0435 | 6532115.4055 | 4583107.7993 | 99188.993 | 86685.2051 | 49054.3666 | 8225.8435 | 2109.2071 | 363411.4554 | 254763.0539 | 5513.2585 | 363301.8528 | 254700.3418 | 5501.4214 | 108.0155 | 61.125 | 10.2499 | 1.5871 | 6176309.765 | 4332698.9383 | 94590.9935 | 6168571.447 | 4328236.7187 | 93683.2591 | 7546.7162 | 4270.6178 | 716.1327 | 191.6018 | 81188.5973 | 46809.3807 | 9419.7915 | 242.1057 | 170.7388 | 4.3125 | 79030.4734 | 44722.6237 | 7499.4609 | 1916.0182 | 0.010395 | 0.0072688 | 0.000185 | 0.2251 | 0.12794 | 0.02251 | 0.0029306 | 5000000 | scaled
1030-20R | 25318461.9928 | 25101310.8982 | 206672.9701 | 10478.1245 | 99.14% | 0.8163% | 0.04139% | 7403267.149 | 24900756.2248 | 459991.1778 | 80420.7075 | 6862855.2637 | 1553775.4842 | 169845.0278 | 23177135.7128 | 1030 |  | 28 | 1030-20R | 25318461.9928 | 17915194.8438 | 417705.7681 | 25101310.8982 | 17787756.3882 | 387628.5408 | 206672.9701 | 116960.3311 | 19599.1028 | 10478.1245 | 1578483.7163 | 1118492.5385 | 24708.2321 | 1577997.6427 | 1118214.0373 | 24655.0003 | 478.1891 | 270.6167 | 45.3474 | 7.8845 | 23543223.1292 | 16680367.8655 | 366087.4164 | 23518515.0058 | 16665971.8737 | 362882.733 | 23756.2834 | 13444.1517 | 2252.8434 | 951.84 | 196755.1473 | 116334.4399 | 26910.1196 | 4798.2497 | 3570.4772 | 90.8076 | 182438.4976 | 103245.5627 | 17300.912 | 9518.4 | 0.049346 | 0.034848 | 0.0008856 | 0.22257 | 0.12651 | 0.022257 | 0.014767 | 5000000 | scaled
1030-42R | 28398789.4867 | 27971255.8292 | 416330.7729 | 11202.8845 | 98.49% | 1.466% | 0.03945% | 9802007.6063 | 27896644.117 | 601987.8389 | 164565.8231 | 9035453.9444 | 1719777.0488 | 345709.3287 | 25831157.7395 | 1030 |  | 29 | 1030-42R | 28398789.4867 | 18596781.8803 | 502145.3697 | 27971255.8292 | 18349968.574 | 451499.8227 | 416330.7729 | 235610.4218 | 39442.6624 | 11202.8845 | 1747835.2619 | 1145847.423 | 28058.2131 | 1747077.391 | 1145414.8686 | 27978.7822 | 749.4411 | 424.1246 | 71.0011 | 8.4298 | 26259471.5282 | 17224017.5839 | 428313.7887 | 26217297.0731 | 17199708.4122 | 423396.9688 | 41156.7774 | 23291.494 | 3899.1422 | 1017.6777 | 391482.6965 | 226916.8735 | 45773.3679 | 6881.3651 | 4845.2932 | 124.0717 | 374424.5544 | 211894.8033 | 35472.5191 | 10176.777 | 0.048528 | 0.031438 | 0.0008074 | 0.21804 | 0.12395 | 0.021804 | 0.015712 | 5000000 | scaled
1030-989R | 26696216.0546 | 26471622.1415 | 212509.788 | 12084.1251 | 99.16% | 0.796% | 0.04527% | 9579303.6479 | 26217012.9234 | 535879.0998 | 81442.3883 | 8961982.1598 | 1468504.0584 | 171055.712 | 24577453.153 | 1030 |  | 30 | 1030-989R | 26696216.0546 | 17116912.4067 | 479203.1312 | 26471622.1415 | 16984580.466 | 446972.5012 | 212509.788 | 120247.8156 | 20146.5049 | 12084.1251 | 1493694.8284 | 957815.7286 | 25190.77 | 1493451.642 | 957674.1749 | 25159.4844 | 234.0934 | 132.4608 | 22.1927 | 9.0929 | 25002854.0971 | 16040871.9373 | 425400.9442 | 24974859.984 | 16024554.9961 | 421753.3638 | 26896.383 | 15219.211 | 2549.8501 | 1097.7302 | 199667.1291 | 118224.7408 | 28611.4171 | 3310.5155 | 2351.2951 | 59.653 | 185379.3116 | 104896.1438 | 17574.4621 | 10977.302 | 0.068619 | 0.043488 | 0.0011038 | 0.22133 | 0.1258 | 0.022133 | 0.017072 | 5000000 | scaled
1039-13 | 15957171.1285 | 15550885.1225 | 394286.4327 | 11999.5733 | 97.45% | 2.471% | 0.0752% | 8824120.463 | 15756108.0081 | 788307.5522 | 163564.2498 | 7872248.6611 | 1404334.8482 | 338762.3369 | 14013010.8229 | 1039 |  | 31 | 1039-13 | 15957171.1285 | 7133050.6655 | 201063.1204 | 15550885.1225 | 6900345.2603 | 155309.6082 | 394286.4327 | 220705.8319 | 33753.9389 | 11999.5733 | 1418584.3323 | 630276.7802 | 14249.4841 | 1417932.0693 | 629907.6943 | 14185.3891 | 643.2338 | 360.0566 | 55.0657 | 9.0293 | 14158109.1716 | 6285860.5106 | 145098.3487 | 14121706.6039 | 6265003.9207 | 140985.2772 | 35312.5183 | 19766.5404 | 3023.0221 | 1090.0495 | 380477.6245 | 216913.3747 | 41715.2876 | 11246.4493 | 5433.6454 | 138.9419 | 358330.6807 | 200579.2348 | 30675.8511 | 10900.4945 | 0.047778 | 0.021666 | 0.0005504 | 0.070461 | 0.039915 | 0.007046 | 0.016862 | 5000000 | scaled
1039-14AE | 282519.7809 | 0 | 282519.7809 | 0 | 0% | 100% | 0% | 26858.6835 | 56018.8654 | 34.4156 | 24539.5788 | 2284.6892 | 71.7802 | 51181.9336 | 4765.1515 | 1039 |  | 32 | 1039-14AE | 282519.7809 | 255661.0973 | 226500.9155 | 0 | 0 | 0 | 282519.7809 | 255661.0973 | 226500.9155 | 0 | 362.0089 | 327.5933 | 290.2287 | 0 | 0 | 0 | 362.0089 | 327.5933 | 290.2287 | 0 | 24032.0749 | 21747.3857 | 19266.9233 | 0 | 0 | 0 | 24032.0749 | 21747.3857 | 19266.9233 | 0 | 258125.6971 | 233586.1183 | 206943.7635 | 0 | 0 | 0 | 258125.6971 | 233586.1183 | 206943.7635 | 0 | 0 | 0 | 0 | 0.042185 | 0.042185 | 0.042185 | 0 | 5000000 | scaled
1047-35F | 2344.7819 | 1150.7629 | 0 | 1194.0189 | 49.08% | 0% | 50.92% | 653.8454 | 1137.4847 | 1.7192 | 643.2929 | 8.8332 | 2.578 | 1121.6387 | 13.2679 | 1047 |  | 33 | 1047-35F | 2344.7819 | 1690.9365 | 1207.2972 | 1150.7629 | 496.9176 | 13.2783 | 0 | 0 | 0 | 1194.0189 | 3.5656 | 1.8463 | 0.98753 | 2.6671 | 0.94788 | 0.089073 | 0 | 0 | 0 | 0.89846 | 122.1985 | 113.3653 | 108.9306 | 13.733 | 4.8998 | 0.46507 | 0 | 0 | 0 | 108.4655 | 2219.0178 | 1575.7249 | 1097.3791 | 1134.3628 | 491.0699 | 12.7241 | 0 | 0 | 0 | 1084.655 | 0.002996 | 0.0012974 | 3.34e-05 | 0 | 0 | 0 | 0.001658 | 5000000 | scaled
1047-36F | 7628.4805 | 2559.7424 | 0 | 5068.738 | 33.56% | 0% | 66.44% | 1454.6142 | 2531.2942 | 6.1724 | 1416.5223 | 31.9195 | 9.7692 | 2471.0084 | 50.5165 | 1047 |  | 34 | 1047-36F | 7628.4805 | 6173.8663 | 5097.1863 | 2559.7424 | 1105.1282 | 28.4482 | 0 | 0 | 0 | 5068.738 | 13.7398 | 7.5673 | 3.9705 | 9.9257 | 3.7533 | 0.15647 | 0 | 0 | 0 | 3.8141 | 511.7715 | 479.852 | 461.2549 | 51.3238 | 19.4043 | 0.8073 | 0 | 0 | 0 | 460.4476 | 7102.9692 | 5686.447 | 4631.9608 | 2498.4929 | 1081.9706 | 27.4845 | 0 | 0 | 0 | 4604.4763 | 0.013662 | 0.0059168 | 0.0001494 | 0 | 0 | 0 | 0.0070846 | 5000000 | scaled
1049-3F | 8896.2884 | 3656.6708 | 0 | 5239.6175 | 41.1% | 0% | 58.9% | 2109.2165 | 3640.5615 | 163.6768 | 1027.5874 | 917.9523 | 279.8166 | 1794.0227 | 1566.7222 | 1049 |  | 35 | 1049-3F | 8896.2884 | 6787.0719 | 5255.7268 | 3656.6708 | 1547.4543 | 16.1093 | 0 | 0 | 0 | 5239.6175 | 283.9256 | 120.2488 | 4.109 | 279.9829 | 116.3061 | 0.16632 | 0 | 0 | 0 | 3.9426 | 2043.5651 | 1125.6128 | 476.8429 | 1567.5946 | 649.6423 | 0.87243 | 0 | 0 | 0 | 475.9704 | 6568.7977 | 5541.2103 | 4774.775 | 1809.0933 | 781.5058 | 15.0705 | 0 | 0 | 0 | 4759.7045 | 0.012635 | 0.005471 | 0.0001384 | 0 | 0 | 0 | 0.0073626 | 5000000 | scaled
1049-4F | 3714.0874 | 2055.5823 | 0 | 1658.5051 | 55.35% | 0% | 44.65% | 1305.1182 | 2051.3462 | 145.8357 | 108.7272 | 1050.5553 | 230.5913 | 189.2309 | 1631.5239 | 1049 |  | 36 | 1049-4F | 3714.0874 | 2408.9691 | 1662.7412 | 2055.5823 | 750.4641 | 4.2361 | 0 | 0 | 0 | 1658.5051 | 232.2752 | 86.4395 | 1.6839 | 231.0272 | 85.1915 | 0.4359 | 0 | 0 | 0 | 1.248 | 1784.4 | 733.8446 | 152.8761 | 1633.7402 | 583.1849 | 2.2163 | 0 | 0 | 0 | 150.6597 | 1697.4122 | 1588.685 | 1508.1812 | 190.8148 | 82.0877 | 1.5839 | 0 | 0 | 0 | 1506.5973 | 0.003898 | 0.0016876 | 4.28e-05 | 0 | 0 | 0 | 0.0023162 | 5000000 | scaled
1049-7F | 4396.8706 | 1836.7465 | 0 | 2560.1241 | 41.77% | 0% | 58.23% | 993.6 | 1818.0778 | 46.4398 | 704.8374 | 242.3228 | 85.5962 | 1282.7559 | 449.7257 | 1049 |  | 37 | 1049-7F | 4396.8706 | 3403.2706 | 2578.7928 | 1836.7465 | 843.1465 | 18.6687 | 0 | 0 | 0 | 2560.1241 | 88.5466 | 42.1068 | 2.9504 | 86.6202 | 40.1804 | 1.0239 | 0 | 0 | 0 | 1.9264 | 687.5004 | 445.1775 | 237.7747 | 454.937 | 212.6141 | 5.2112 | 0 | 0 | 0 | 232.5634 | 3620.8237 | 2915.9863 | 2338.0678 | 1295.1894 | 590.352 | 12.4335 | 0 | 0 | 0 | 2325.6342 | 0.007077 | 0.0031702 | 7.96e-05 | 0 | 0 | 0 | 0.00361 | 5000000 | scaled
105-239F | 2456.5837 | 2248.5934 | 0 | 207.9903 | 91.53% | 0% | 8.467% | 1345.9756 | 2198.4095 | 130.4022 | 219.9209 | 995.6525 | 216.6228 | 371.6143 | 1610.1724 | 105 |  | 38 | 105-239F | 2456.5837 | 1110.6081 | 258.1742 | 2248.5934 | 902.6178 | 50.1839 | 0 | 0 | 0 | 207.9903 | 222.2987 | 91.8965 | 5.6759 | 222.1422 | 91.74 | 5.5194 | 0 | 0 | 0 | 0.15651 | 1670.2873 | 674.6348 | 60.1149 | 1651.3934 | 655.7408 | 41.221 | 0 | 0 | 0 | 18.894 | 563.9976 | 344.0768 | 192.3833 | 375.0578 | 155.137 | 3.4435 | 0 | 0 | 0 | 188.9398 | 0.0007738 | 0.000335 | 8.4e-06 | 0 | 0 | 0 | 0.000294 | 5000000 | scaled
1071-226F | 15052.821 | 14799.468 | 0 | 253.353 | 98.32% | 0% | 1.683% | 8442.8842 | 14609.2556 | 701.886 | 1766.7607 | 5974.2375 | 1210.3854 | 3097.8361 | 10301.0341 | 1071 |  | 39 | 1071-226F | 15052.821 | 6609.9368 | 443.5655 | 14799.468 | 6356.5838 | 190.2125 | 0 | 0 | 0 | 253.353 | 1225.5718 | 523.6858 | 15.1864 | 1225.3811 | 523.4952 | 14.9958 | 0 | 0 | 0 | 0.19064 | 10460.5463 | 4486.3088 | 159.5122 | 10437.5316 | 4463.294 | 136.4975 | 0 | 0 | 0 | 23.0148 | 3366.7029 | 1599.9423 | 268.8668 | 3136.5553 | 1369.7946 | 38.7192 | 0 | 0 | 0 | 230.1476 | 0.0013586 | 0.0005882 | 1.52e-05 | 0 | 0 | 0 | 0.0003482 | 5000000 | scaled
1072-6 | 193612.1217 | 714.8884 | 192796.5728 | 100.6605 | 0.3692% | 99.58% | 0.05199% | 87035.4406 | 180648.8687 | 168.717 | 79193.2739 | 7673.4497 | 313.1258 | 164629.2478 | 15706.4951 | 1072 |  | 40 | 1072-6 | 193612.1217 | 106576.6811 | 12963.2529 | 714.8884 | 234.5094 | 0.042198 | 192796.5728 | 106241.5113 | 12862.5502 | 100.6605 | 328.6403 | 159.9233 | 15.5145 | 97.1539 | 32.3276 | 0 | 231.4106 | 127.52 | 15.4387 | 0.075744 | 16794.5536 | 9121.1039 | 1088.0585 | 613.5772 | 200.3911 | 0 | 16171.8324 | 8911.5687 | 1078.9144 | 9.1441 | 176488.9278 | 97295.6539 | 11859.68 | 4.1573 | 1.7907 | 0.042198 | 176393.3298 | 97202.4225 | 11768.1971 | 91.4407 | 0.00073 | 0.000316 | 8e-06 | 0.016061 | 0.0091076 | 0.001606 | 0.0001496 | 5000000 | scaled
1073-3F | 1202.2019 | 0 | 1202.2019 | 0 | 0% | 100% | 0% | 192.3244 | 400.1797 | 0.80911 | 151.9443 | 39.5709 | 1.6836 | 316.1587 | 82.3374 | 1073 |  | 41 | 1073-3F | 1202.2019 | 1009.8775 | 802.0222 | 0 | 0 | 0 | 1202.2019 | 1009.8775 | 802.0222 | 0 | 5.0577 | 4.2486 | 3.3741 | 0 | 0 | 0 | 5.0577 | 4.2486 | 3.3741 | 0 | 247.3544 | 207.7834 | 165.0169 | 0 | 0 | 0 | 247.3544 | 207.7834 | 165.0169 | 0 | 949.7899 | 797.8456 | 633.6312 | 0 | 0 | 0 | 949.7899 | 797.8456 | 633.6312 | 0 | 0 | 0 | 0 | 0.016295 | 0.016295 | 0.016295 | 0 | 5000000 | scaled
1073-480 | 99118.627 | 2763.9934 | 96173.6284 | 181.0052 | 2.789% | 97.03% | 0.1826% | 44719.7758 | 92506.0503 | 145.5237 | 40410.7088 | 4163.5432 | 258.991 | 83830.9486 | 8416.1106 | 1073 |  | 42 | 1073-480 | 99118.627 | 54398.8512 | 6612.5767 | 2763.9934 | 1131.0339 | 13.2509 | 96173.6284 | 53086.8121 | 6418.3207 | 181.0052 | 266.8797 | 121.356 | 7.8887 | 150.5786 | 57.098 | 0 | 116.1649 | 64.1218 | 7.7525 | 0.1362 | 8973.4126 | 4809.8694 | 557.302 | 852.6057 | 319.9045 | 0 | 8104.3643 | 4473.5223 | 540.8594 | 16.4426 | 89878.3346 | 49467.6258 | 6047.386 | 1760.8091 | 754.0314 | 13.2509 | 87953.0991 | 48549.168 | 5869.7088 | 164.4264 | 0.0006842 | 0.0002964 | 7.6e-06 | 0.016225 | 0.0092154 | 0.0016224 | 0.0002626 | 5000000 | scaled
1073-872F | 17965.8791 | 15601.9726 | 1926.6608 | 437.2457 | 86.84% | 10.72% | 2.434% | 8578.0542 | 17317.8494 | 713.0536 | 808.7486 | 7056.2521 | 1414.0867 | 1678.6829 | 14225.0798 | 1073 |  | 43 | 1073-872F | 17965.8791 | 9387.8249 | 648.0297 | 15601.9726 | 7887.6405 | 82.2719 | 1926.6608 | 1062.9387 | 128.5121 | 437.2457 | 1422.9412 | 709.8876 | 8.8545 | 1420.243 | 708.2515 | 8.3675 | 2.3692 | 1.3071 | 0.15803 | 0.32901 | 14348.6705 | 7292.4184 | 123.5906 | 14155.2458 | 7167.8996 | 73.6185 | 153.705 | 84.799 | 10.2524 | 39.7197 | 2194.2674 | 1385.5188 | 515.5845 | 26.4838 | 11.4893 | 0.2859 | 1770.5867 | 976.8326 | 118.1017 | 397.197 | 0.0016362 | 0.0007086 | 1.82e-05 | 0.016356 | 0.0092852 | 0.0016356 | 0.0005918 | 5000000 | scaled
1073-874F | 40994.8871 | 9652.9701 | 30189.9757 | 1151.9413 | 23.55% | 73.64% | 2.81% | 18490.8839 | 36944.2226 | 458.7463 | 12153.2219 | 5878.9157 | 793.3933 | 25161.4746 | 10989.3547 | 1073 |  | 44 | 1073-874F | 40994.8871 | 22504.0032 | 4050.6645 | 9652.9701 | 4677.9891 | 885.4176 | 30189.9757 | 16674.0728 | 2013.3056 | 1151.9413 | 872.6651 | 413.9188 | 79.2717 | 821.5258 | 385.2863 | 75.0524 | 50.2725 | 27.7657 | 3.3526 | 0.8668 | 12031.1878 | 6152.2721 | 1041.8331 | 5736.5577 | 2628.8685 | 524.3929 | 6189.9871 | 3418.7604 | 412.7971 | 104.6431 | 28091.0342 | 15937.8123 | 2929.5596 | 3094.8867 | 1663.8343 | 285.9723 | 23949.7162 | 13227.5466 | 1597.1559 | 1046.4314 | 0.003574 | 0.0017202 | 0.0001356 | 0.016342 | 0.0092866 | 0.0016342 | 0.0016488 | 5000000 | scaled
1073-886F | 27078.0985 | 3452.9675 | 23512.0119 | 113.1191 | 12.75% | 86.83% | 0.4178% | 13136.0295 | 25396.0524 | 229.3682 | 9596.1479 | 3310.5134 | 318.6175 | 19981.9213 | 5095.5136 | 1073 |  | 45 | 1073-886F | 27078.0985 | 13942.0691 | 1682.0461 | 3452.9675 | 851.699 | 0.28946 | 23512.0119 | 12977.251 | 1568.6376 | 113.1191 | 320.538 | 91.1698 | 1.9205 | 292.9428 | 75.9007 | 0 | 27.51 | 15.1839 | 1.8354 | 0.085118 | 5246.8971 | 1936.3837 | 151.3835 | 3121.5851 | 758.732 | 0 | 2115.0361 | 1167.3759 | 141.1077 | 10.2758 | 21510.6634 | 11914.5156 | 1528.7421 | 38.4396 | 17.0662 | 0.28946 | 21369.4657 | 11794.6912 | 1425.6945 | 102.7581 | 0.0002762 | 0.0001196 | 3e-06 | 0.016346 | 0.009283 | 0.0016346 | 0.0001542 | 5000000 | scaled
1073-887F | 6393.3665 | 2196.0607 | 4126.8081 | 70.4977 | 34.35% | 64.55% | 1.103% | 3000.7685 | 6047.4856 | 102.1907 | 1593.8327 | 1304.7451 | 198.3209 | 3317.7642 | 2531.4005 | 1073 |  | 46 | 1073-887F | 6393.3665 | 3392.598 | 345.8809 | 2196.0607 | 1044.9756 | 0.044419 | 4126.8081 | 2277.1247 | 275.3387 | 70.4977 | 198.9173 | 96.7265 | 0.59632 | 190.7216 | 92.1804 | 0 | 8.1427 | 4.493 | 0.54327 | 0.053047 | 2575.7615 | 1271.0164 | 44.361 | 2000.4548 | 950.6985 | 0 | 568.9027 | 313.9139 | 37.9569 | 6.4041 | 3618.6877 | 2024.855 | 300.9236 | 4.8843 | 2.0966 | 0.044419 | 3549.7628 | 1958.7178 | 236.8385 | 64.0406 | 0.0001412 | 6.1e-05 | 1.6e-06 | 0.016396 | 0.0093092 | 0.0016396 | 0.0001018 | 5000000 | scaled
1073-888F | 67344.1791 | 0 | 67344.1791 | 0 | 0% | 100% | 0% | 10774.816 | 22410.7053 | 11.7094 | 9823.3601 | 939.7464 | 24.3546 | 20431.7577 | 1954.593 | 1073 |  | 47 | 1073-888F | 67344.1791 | 56569.3631 | 44933.4738 | 0 | 0 | 0 | 67344.1791 | 56569.3631 | 44933.4738 | 0 | 73.1857 | 61.4762 | 48.831 | 0 | 0 | 0 | 73.1857 | 61.4762 | 48.831 | 0 | 5873.5527 | 4933.8063 | 3918.9597 | 0 | 0 | 0 | 5873.5527 | 4933.8063 | 3918.9597 | 0 | 61397.4408 | 51574.0806 | 40965.683 | 0 | 0 | 0 | 61397.4408 | 51574.0806 | 40965.683 | 0 | 0 | 0 | 0 | 0.016349 | 0.016349 | 0.016349 | 0 | 5000000 | scaled
1076-37F | 25755.9692 | 18421.398 | 0 | 7334.5712 | 71.52% | 0% | 28.48% | 9768.7981 | 18215.9364 | 109.8559 | 9228.547 | 430.3952 | 184.5943 | 17308.41 | 722.9321 | 1076 |  | 48 | 1076-37F | 25755.9692 | 15987.1711 | 7540.0328 | 18421.398 | 8652.5999 | 205.4616 | 0 | 0 | 0 | 7334.5712 | 190.2967 | 80.4409 | 5.7024 | 184.7777 | 74.9218 | 0.18342 | 0 | 0 | 0 | 5.519 | 1389.9227 | 959.5275 | 666.9907 | 723.6453 | 293.2501 | 0.7132 | 0 | 0 | 0 | 666.2775 | 24175.7497 | 14947.2027 | 6867.3397 | 17512.975 | 8284.428 | 204.565 | 0 | 0 | 0 | 6662.7747 | 0.020909 | 0.009368 | 0.0002392 | 0 | 0 | 0 | 0.010307 | 5000000 | scaled
1077-8R | 24383.2116 | 22128.3008 | 0 | 2254.9108 | 90.75% | 0% | 9.248% | 11314.4306 | 21716.9756 | 1046.2799 | 556.8443 | 9711.3065 | 1974.4805 | 1057.1645 | 18685.3306 | 1077 |  | 49 | 1077-8R | 24383.2116 | 13068.781 | 2666.2361 | 22128.3008 | 10813.8702 | 411.3253 | 0 | 0 | 0 | 2254.9108 | 2012.9293 | 966.6494 | 38.4488 | 2011.2325 | 964.9526 | 36.7521 | 0 | 0 | 0 | 1.6967 | 19252.38 | 9541.0735 | 567.0494 | 19047.5423 | 9336.2359 | 362.2117 | 0 | 0 | 0 | 204.8376 | 3117.9024 | 2561.0581 | 2060.7379 | 1069.526 | 512.6817 | 12.3615 | 0 | 0 | 0 | 2048.3764 | 0.0062946 | 0.0028518 | 7.36e-05 | 0 | 0 | 0 | 0.00315 | 5000000 | scaled
1079-9 | 117302.1432 | 111426.6382 | 0 | 5875.505 | 94.99% | 0% | 5.009% | 42843.8293 | 110622.4399 | 7540.0513 | 3911.6685 | 31392.1095 | 19062.0703 | 11403.9805 | 80156.3892 | 1079 |  | 50 | 1079-9 | 117302.1432 | 74458.3139 | 6679.7033 | 111426.6382 | 68582.809 | 804.1983 | 0 | 0 | 0 | 5875.505 | 19190.5483 | 11650.497 | 128.478 | 19186.1272 | 11646.0759 | 124.0569 | 0 | 0 | 0 | 4.4211 | 81160.0729 | 49767.9634 | 1003.6837 | 80626.338 | 49234.2285 | 469.9488 | 0 | 0 | 0 | 533.7349 | 16951.5219 | 13039.8535 | 5547.5415 | 11614.173 | 7702.5046 | 210.1926 | 0 | 0 | 0 | 5337.3489 | 0.018953 | 0.0094764 | 0.0002544 | 0 | 0 | 0 | 0.0083026 | 5000000 | scaled
1081-11 | 174685.4114 | 32405.6085 | 138002.6007 | 4277.2022 | 18.55% | 79% | 2.449% | 74710.7534 | 160849.4773 | 661.0218 | 66258.4833 | 7791.2483 | 1586.6424 | 142031.2968 | 17231.538 | 1081 |  | 51 | 1081-11 | 174685.4114 | 99974.658 | 13835.9341 | 32405.6085 | 19219.4515 | 280.6568 | 138002.6007 | 76478.0043 | 9278.0751 | 4277.2022 | 1606.1443 | 945.1225 | 19.5019 | 1429.9247 | 846.0306 | 4.6524 | 173.0012 | 95.8734 | 11.6311 | 3.2185 | 18413.1445 | 10621.8963 | 1181.6065 | 6522.7285 | 3859.2679 | 19.7783 | 11501.8721 | 6374.0844 | 773.2842 | 388.544 | 154666.1226 | 88407.6392 | 12634.8257 | 24452.9553 | 14514.153 | 256.2262 | 126327.7275 | 70008.0465 | 8493.1598 | 3885.4398 | 0.014567 | 0.006916 | 0.0001756 | 0.010889 | 0.0062054 | 0.0010888 | 0.005939 | 5000000 | scaled
1081-38AE | 213067.9419 | 166262.6209 | 45883.2766 | 922.0444 | 78.03% | 21.53% | 0.4327% | 114900.4401 | 208316.305 | 8331.1408 | 19557.4241 | 87011.8753 | 14574.9596 | 40586.4966 | 153154.8487 | 1081 |  | 52 | 1081-38AE | 213067.9419 | 98167.5018 | 4751.637 | 166262.6209 | 71824.5642 | 758.3347 | 45883.2766 | 25420.8932 | 3071.2578 | 922.0444 | 14652.8887 | 6321.7479 | 77.9291 | 14590.8831 | 6287.0853 | 73.1313 | 61.3118 | 33.9688 | 4.104 | 0.69381 | 154180.5476 | 67168.6723 | 1025.6989 | 149967.2472 | 64797.0071 | 665.5234 | 4129.5412 | 2287.906 | 276.4163 | 83.7591 | 44234.5056 | 24677.0816 | 3648.009 | 1704.4905 | 740.4717 | 19.68 | 41692.4237 | 23099.0184 | 2790.7375 | 837.5915 | 0.0030068 | 0.0013016 | 3.3e-05 | 0.011026 | 0.0062828 | 0.0011026 | 0.0012972 | 5000000 | scaled
1081-666F | 169874.5207 | 136342.3922 | 29758.0318 | 3774.0967 | 80.26% | 17.52% | 2.222% | 89329.0729 | 162692.5854 | 8377.9587 | 12654.1302 | 68296.984 | 14875.4173 | 26222.7737 | 121594.3945 | 1081 |  | 53 | 1081-666F | 169874.5207 | 80545.4478 | 7181.9353 | 136342.3922 | 60308.044 | 1413.2538 | 29758.0318 | 16463.3072 | 1994.5849 | 3774.0967 | 15037.3065 | 6659.3479 | 161.8893 | 14994.4133 | 6634.3489 | 156.3647 | 40.0534 | 22.1591 | 2.6846 | 2.8399 | 123364.1124 | 55067.1284 | 1769.7179 | 120316.6626 | 53227.9918 | 1245.5952 | 2704.6082 | 1496.2951 | 181.2812 | 342.8415 | 31473.1018 | 18818.9716 | 5250.3281 | 1031.3163 | 445.7033 | 11.2938 | 27013.3702 | 14944.853 | 1810.6191 | 3428.4153 | 0.011232 | 0.0048834 | 0.000124 | 0.010812 | 0.0061528 | 0.0010812 | 0.0053196 | 5000000 | scaled
1081-668F | 32959.1187 | 5006.4721 | 27394.0445 | 558.6021 | 15.19% | 83.12% | 1.695% | 14748.29 | 30130.5802 | 288.3188 | 11971.4329 | 2488.5383 | 512.4651 | 24990.3208 | 4627.7944 | 1081 |  | 54 | 1081-668F | 32959.1187 | 18210.8287 | 2828.5385 | 5006.4721 | 2498.744 | 434.9351 | 27394.0445 | 15153.4826 | 1835.0013 | 558.6021 | 568.3977 | 280.0789 | 55.9327 | 533.9515 | 260.8366 | 53.2331 | 34.0259 | 18.822 | 2.2792 | 0.42033 | 5200.7094 | 2712.1711 | 572.9151 | 2777.8825 | 1349.2691 | 363.2763 | 2372.0832 | 1312.1582 | 158.895 | 50.7438 | 27190.0115 | 15218.5786 | 2199.6908 | 1694.6381 | 888.6383 | 18.4257 | 24987.9354 | 13822.5024 | 1673.8271 | 507.4379 | 0.0017146 | 0.0008274 | 2.12e-05 | 0.010792 | 0.0061402 | 0.0010792 | 0.0007968 | 5000000 | scaled
1085-109F | 288289.2845 | 0 | 288289.2845 | 0 | 0% | 100% | 0% | 60999.2888 | 127815.8533 | 43.7644 | 57597.6224 | 3357.9019 | 92.1351 | 120659.6059 | 7064.1123 | 1085 |  | 55 | 1085-109F | 288289.2845 | 227289.9956 | 160473.4312 | 0 | 0 | 0 | 288289.2845 | 227289.9956 | 160473.4312 | 0 | 266.3637 | 222.5993 | 174.2286 | 0 | 0 | 0 | 266.3637 | 222.5993 | 174.2286 | 0 | 19733.4068 | 16375.5048 | 12669.2945 | 0 | 0 | 0 | 19733.4068 | 16375.5048 | 12669.2945 | 0 | 268289.514 | 210691.8916 | 147629.9081 | 0 | 0 | 0 | 268289.514 | 210691.8916 | 147629.9081 | 0 | 0 | 0 | 0 | 0.0074098 | 0.0074098 | 0.0074098 | 0 | 5000000 | scaled
1085-412F | 80.1172 | 0 | 80.1172 | 0 | 0% | 100% | 0% | 12.5948 | 26.3794 | 0.0082717 | 9.9859 | 2.6006 | 0.017325 | 20.9151 | 5.4469 | 1085 |  | 56 | 1085-412F | 80.1172 | 67.5224 | 53.7378 | 0 | 0 | 0 | 80.1172 | 67.5224 | 53.7378 | 0 | 0.052617 | 0.044346 | 0.035293 | 0 | 0 | 0 | 0.052617 | 0.044346 | 0.035293 | 0 | 16.543 | 13.9423 | 11.096 | 0 | 0 | 0 | 16.543 | 13.9423 | 11.096 | 0 | 63.5216 | 53.5357 | 42.6065 | 0 | 0 | 0 | 63.5216 | 53.5357 | 42.6065 | 0 | 0 | 0 | 0 | 0.007627 | 0.007627 | 0.007627 | 0 | 5000000 | scaled
1085-8F | 93881.604 | 0 | 93881.604 | 0 | 0% | 100% | 0% | 14742.7395 | 30883.7872 | 15.9602 | 13491.3273 | 1235.452 | 33.4342 | 28262.2698 | 2588.0832 | 1085 |  | 57 | 1085-8F | 93881.604 | 79138.8644 | 62997.8167 | 0 | 0 | 0 | 93881.604 | 79138.8644 | 62997.8167 | 0 | 101.6345 | 85.6743 | 68.2003 | 0 | 0 | 0 | 101.6345 | 85.6743 | 68.2003 | 0 | 7867.3447 | 6631.8928 | 5279.2616 | 0 | 0 | 0 | 7867.3447 | 6631.8928 | 5279.2616 | 0 | 85912.6248 | 72421.2974 | 57650.3549 | 0 | 0 | 0 | 85912.6248 | 72421.2974 | 57650.3549 | 0 | 0 | 0 | 0 | 0.007448 | 0.007448 | 0.007448 | 0 | 5000000 | scaled
1090-1734 | 730547.8922 | 725008.3664 | 4283.2261 | 1256.2997 | 99.24% | 0.5863% | 0.172% | 394775.2737 | 716393.1565 | 23678.4931 | 2264.2903 | 368832.4903 | 43123.2585 | 4730.542 | 668539.3561 | 1090 |  | 58 | 1090-1734 | 730547.8922 | 335772.6185 | 14154.7356 | 725008.3664 | 332123.8073 | 12612.0725 | 4283.2261 | 2392.5115 | 286.3634 | 1256.2997 | 43870.3111 | 20191.818 | 747.0526 | 43862.6764 | 20187.1361 | 745.6601 | 6.6893 | 3.7365 | 0.44723 | 0.94533 | 680531.2819 | 311698.7916 | 11991.9258 | 680027.2732 | 311366.8874 | 11851.7361 | 389.8856 | 217.7811 | 26.0666 | 114.1231 | 6146.2992 | 3882.0089 | 1415.7572 | 1118.4168 | 569.7838 | 14.6764 | 3886.6512 | 2170.9939 | 259.8497 | 1141.2312 | 0.0064908 | 0.0030648 | 7.84e-05 | 0.0051852 | 0.0029778 | 0.0005186 | 0.0017736 | 5000000 | scaled
1090-636R | 919372.7965 | 863578.6076 | 51668.7349 | 4125.4539 | 93.93% | 5.62% | 0.4487% | 334773.2602 | 896118.6091 | 16546.918 | 18532.7232 | 299693.619 | 45384.3378 | 38977.8387 | 811756.4326 | 1090 |  | 59 | 1090-636R | 919372.7965 | 584599.5363 | 23254.1874 | 863578.6076 | 551197.5448 | 14135.6454 | 51668.7349 | 29276.5376 | 4993.088 | 4125.4539 | 46189.2102 | 29642.2922 | 804.8724 | 45856.6307 | 29452.5007 | 769.9288 | 329.4752 | 186.6872 | 31.8393 | 3.1043 | 826347.2808 | 526653.6618 | 14590.8481 | 817033.5011 | 521213.875 | 13352.253 | 8939.0206 | 5065.0277 | 863.8361 | 374.7591 | 46836.3055 | 28303.5824 | 7858.4668 | 688.4758 | 531.1691 | 13.4636 | 42400.2391 | 24024.8227 | 4097.4126 | 3747.5906 | 0.027416 | 0.018962 | 0.0004808 | 0.3514 | 0.19964 | 0.03514 | 0.0058268 | 5000000 | scaled
1090-639R | 509502.0987 | 468582.4441 | 38311.1916 | 2608.4629 | 91.97% | 7.519% | 0.512% | 214403.736 | 496667.0082 | 9505.7689 | 13234.2762 | 191663.6908 | 22111.4907 | 27723.0775 | 446832.44 | 1090 |  | 60 | 1090-639R | 509502.0987 | 295098.3627 | 12835.0905 | 468582.4441 | 270783.0151 | 6525.0482 | 38311.1916 | 21706.8847 | 3701.5793 | 2608.4629 | 22453.286 | 12947.5171 | 341.7953 | 22110.2924 | 12752.3284 | 306.8825 | 341.0308 | 193.226 | 32.95 | 1.9628 | 454037.1876 | 262373.4968 | 7204.7476 | 445954.8255 | 257691.3827 | 6209.7796 | 7845.4075 | 4445.1594 | 758.0134 | 236.9546 | 33011.6251 | 19777.3489 | 5288.5476 | 517.3262 | 339.304 | 8.3861 | 30124.7533 | 17068.4993 | 2910.6159 | 2369.5456 | 0.016946 | 0.010723 | 0.0002718 | 0.34947 | 0.19854 | 0.034947 | 0.0036424 | 5000000 | scaled
1090-69F | 1112.1569 | 0 | 1112.1569 | 0 | 0% | 100% | 0% | 177.5386 | 369.4528 | 0.1166 | 140.763 | 36.659 | 0.24264 | 292.9238 | 76.2863 | 1090 |  | 61 | 1090-69F | 1112.1569 | 934.6183 | 742.704 | 0 | 0 | 0 | 1112.1569 | 934.6183 | 742.704 | 0 | 0.73041 | 0.61382 | 0.48777 | 0 | 0 | 0 | 0.73041 | 0.61382 | 0.48777 | 0 | 229.6433 | 192.9843 | 153.357 | 0 | 0 | 0 | 229.6433 | 192.9843 | 153.357 | 0 | 881.7831 | 741.0201 | 588.8593 | 0 | 0 | 0 | 881.7831 | 741.0201 | 588.8593 | 0 | 0 | 0 | 0 | 0.0066172 | 0.0066172 | 0.0066172 | 0 | 5000000 | scaled
1090-70F | 140836.6813 | 123963.7422 | 16456.6324 | 416.3066 | 88.02% | 11.68% | 0.2956% | 89666.3193 | 138389.1535 | 4858.7776 | 6968.6782 | 77838.8636 | 7430.274 | 14521.1705 | 116437.709 | 1090 |  | 62 | 1090-70F | 140836.6813 | 51170.3619 | 2447.5278 | 123963.7422 | 41677.6508 | 931.9569 | 16456.6324 | 9076.4045 | 1099.2642 | 416.3066 | 7498.829 | 2640.0514 | 68.555 | 7474.5673 | 2626.5297 | 66.6421 | 23.9484 | 13.2084 | 1.5997 | 0.31326 | 117425.0704 | 39586.2069 | 987.3614 | 116041.0833 | 38805.93 | 859.6229 | 1346.1696 | 742.4593 | 89.921 | 37.8176 | 15912.7819 | 8944.1037 | 1391.6114 | 448.0917 | 245.1911 | 5.692 | 15086.5144 | 8320.7368 | 1007.7436 | 378.1758 | 0.0013874 | 0.0006604 | 1.66e-05 | 0.0063116 | 0.0035818 | 0.0006312 | 0.000601 | 5000000 | scaled
1090-73F | 5899045.3617 | 5876650.6475 | 14873.685 | 7521.0292 | 99.62% | 0.2521% | 0.1275% | 2895854.2768 | 5851184.0442 | 216402.3043 | 6697.5747 | 2672754.3977 | 433327.9738 | 13866.8579 | 5403989.2125 | 1090 |  | 63 | 1090-73F | 5899045.3617 | 3003191.0849 | 47861.3175 | 5876650.6475 | 2987385.8189 | 39345.6618 | 14873.685 | 8284.2368 | 994.6265 | 7521.0292 | 436429.2244 | 220026.92 | 3101.2505 | 436402.2673 | 220009.3984 | 3094.167 | 21.2978 | 11.8623 | 1.4242 | 5.6593 | 5441008.045 | 2768253.6472 | 37018.8325 | 5438826.7822 | 2766736.0603 | 36235.4403 | 1498.0473 | 834.3715 | 100.1768 | 683.2154 | 21608.0924 | 14910.5177 | 7741.2345 | 1421.598 | 640.3602 | 16.0545 | 13354.3399 | 7438.0031 | 893.0255 | 6832.1544 | 0.030984 | 0.014402 | 0.0003648 | 0.005206 | 0.0029818 | 0.0005206 | 0.010563 | 5000000 | scaled
1090-74F | 4990919.9691 | 4972118.9145 | 10937.5089 | 7863.5456 | 99.62% | 0.2191% | 0.1576% | 2482838.9333 | 4923712.0597 | 189625.0119 | 6287.1216 | 2286926.7999 | 373879.3773 | 13008.5331 | 4536824.1493 | 1090 |  | 64 | 1090-74F | 4990919.9691 | 2508081.0358 | 67207.9094 | 4972118.9145 | 2494128.5821 | 58612.8431 | 10937.5089 | 6088.9081 | 731.5207 | 7863.5456 | 378377.6037 | 188752.5919 | 4498.2265 | 378353.4086 | 188736.4994 | 4491.0869 | 18.2781 | 10.1754 | 1.2225 | 5.9171 | 4591675.8309 | 2304749.031 | 54851.6816 | 4590013.1344 | 2303506.7457 | 54073.9232 | 948.3666 | 527.9554 | 63.4285 | 714.3299 | 20866.5344 | 14579.4129 | 7858.0013 | 3752.3715 | 1885.337 | 47.8329 | 9970.8642 | 5550.7772 | 666.8697 | 7143.2987 | 0.029392 | 0.013614 | 0.0003472 | 0.0052052 | 0.0029796 | 0.0005206 | 0.01114 | 5000000 | scaled
1094-35F | 2514283.0628 | 2510139.2574 | 0 | 4143.8054 | 99.84% | 0% | 0.1648% | 1320787.6386 | 2458523.2785 | 75153.6096 | 1037.9874 | 1244596.0416 | 140092.555 | 1973.8016 | 2316456.9219 | 1094 |  | 65 | 1094-35F | 2514283.0628 | 1193495.4241 | 55759.7843 | 2510139.2574 | 1189351.6187 | 51615.9789 | 0 | 0 | 0 | 4143.8054 | 142960.3586 | 67806.749 | 2867.8036 | 142957.2405 | 67803.6309 | 2864.6855 | 0 | 0 | 0 | 3.1181 | 2365560.1844 | 1120964.1428 | 49103.2625 | 2365183.7583 | 1120587.7167 | 48726.8364 | 0 | 0 | 0 | 376.4261 | 5762.5197 | 4724.5323 | 3788.7181 | 1998.2585 | 960.2711 | 24.4569 | 0 | 0 | 0 | 3764.2612 | 0.014536 | 0.0068752 | 0.0001752 | 0 | 0 | 0 | 0.0058616 | 5000000 | scaled
1094-7 | 95330.0513 | 94152.929 | 0 | 1177.1223 | 98.77% | 0% | 1.235% | 49224.2964 | 93265.2008 | 3673.5194 | 773.538 | 44777.239 | 6957.9242 | 1334.3958 | 84972.8808 | 1094 |  | 66 | 1094-7 | 95330.0513 | 46105.7549 | 2064.8505 | 94152.929 | 44928.6326 | 887.7282 | 0 | 0 | 0 | 1177.1223 | 7034.135 | 3360.6156 | 76.2108 | 7033.2492 | 3359.7298 | 75.325 | 0 | 0 | 0 | 0.88575 | 85878.41 | 41101.1711 | 905.5292 | 85771.4794 | 40994.2405 | 798.5986 | 0 | 0 | 0 | 106.9306 | 2417.5063 | 1643.9683 | 1083.1105 | 1348.2003 | 574.6623 | 13.8045 | 0 | 0 | 0 | 1069.306 | 0.0048814 | 0.0021136 | 5.34e-05 | 0 | 0 | 0 | 0.001626 | 5000000 | scaled
1094-8AE | 1727.6701 | 1475.671 | 0 | 251.9991 | 85.41% | 0% | 14.59% | 830.4534 | 1465.5755 | 80.1214 | 1.3496 | 748.9825 | 148.5199 | 5.3127 | 1311.7429 | 1094 |  | 67 | 1094-8AE | 1727.6701 | 897.2167 | 262.0946 | 1475.671 | 645.2176 | 10.0955 | 0 | 0 | 0 | 251.9991 | 150.0362 | 69.9148 | 1.5163 | 149.8466 | 69.7252 | 1.3266 | 0 | 0 | 0 | 0.18962 | 1343.3092 | 594.3267 | 31.5664 | 1320.4175 | 571.4349 | 8.6746 | 0 | 0 | 0 | 22.8918 | 234.3247 | 232.9752 | 229.012 | 5.407 | 4.0574 | 0.09425 | 0 | 0 | 0 | 228.9177 | 0.0007004 | 0.0004302 | 1.08e-05 | 0 | 0 | 0 | 0.0003578 | 5000000 | scaled
1100-1168F | 54718.9543 | 54034.5106 | 582.9419 | 101.5017 | 98.75% | 1.065% | 0.1855% | 31208.5639 | 54567.5015 | 1733.8962 | 206.2825 | 29268.3853 | 3074.5911 | 429.9374 | 51062.973 | 1100 |  | 68 | 1100-1168F | 54718.9543 | 23510.3903 | 151.4528 | 54034.5106 | 23082.2727 | 0.13511 | 582.9419 | 326.6159 | 49.8159 | 101.5017 | 3075.3137 | 1341.4176 | 0.72265 | 3067.6747 | 1337.1039 | 0 | 7.5626 | 4.2373 | 0.64627 | 0.076377 | 51082.3529 | 21813.9676 | 19.3799 | 50954.2473 | 21738.1371 | 0 | 118.8851 | 66.61 | 10.1595 | 9.2205 | 561.2876 | 355.0052 | 131.3502 | 12.5885 | 7.0316 | 0.13511 | 456.4942 | 255.7687 | 39.0102 | 92.2049 | 0.0005028 | 0.0002822 | 7.2e-06 | 0.070255 | 0.039847 | 0.0070256 | 0.0001462 | 5000000 | scaled
1100-1172R | 2144978.849 | 2138023.8044 | 5788.8739 | 1166.1707 | 99.68% | 0.2699% | 0.05437% | 813629.138 | 2094189.3224 | 89443.3655 | 2033.8089 | 722151.9637 | 230073.514 | 4233.9329 | 1859881.8755 | 1100 |  | 69 | 1100-1172R | 2144978.849 | 1331349.711 | 50789.5267 | 2138023.8044 | 1326942.9057 | 49128.6963 | 5788.8739 | 3240.6346 | 494.6597 | 1166.1707 | 235465.256 | 146021.8905 | 5391.742 | 235424.7063 | 145998.8044 | 5387.4745 | 39.6721 | 22.2086 | 3.39 | 0.87751 | 1903829.5886 | 1181677.6249 | 43947.7131 | 1902535.7508 | 1180906.6969 | 43740.271 | 1187.902 | 664.9923 | 101.5063 | 105.9357 | 5684.0044 | 3650.1956 | 1450.0716 | 63.3472 | 37.4044 | 0.95074 | 4561.2997 | 2553.4337 | 389.7634 | 1059.3575 | 0.0089602 | 0.0052508 | 0.0001332 | 0.070194 | 0.039774 | 0.0070194 | 0.001644 | 5000000 | scaled
1103-13AE | 94466.2276 | 94244.816 | 0 | 221.4117 | 99.77% | 0% | 0.2344% | 48552.4476 | 92804.8913 | 2998.4361 | 2.1135 | 45551.8979 | 5675.2545 | 3.6928 | 87125.9439 | 1103 |  | 70 | 1103-13AE | 94466.2276 | 45913.7801 | 1661.3364 | 94244.816 | 45692.3684 | 1439.9247 | 0 | 0 | 0 | 221.4117 | 5769.5363 | 2771.1002 | 94.2818 | 5769.3697 | 2770.9336 | 94.1152 | 0 | 0 | 0 | 0.16661 | 88491.8265 | 42939.9285 | 1365.8825 | 88471.7133 | 42919.8154 | 1345.7694 | 0 | 0 | 0 | 20.1132 | 204.8648 | 202.7513 | 201.172 | 3.733 | 1.6194 | 0.040138 | 0 | 0 | 0 | 201.1319 | 0.0010262 | 0.0004446 | 1.12e-05 | 0 | 0 | 0 | 0.0003188 | 5000000 | scaled
1105-1479 | 4228043.5461 | 4224870.7096 | 1373.4345 | 1799.402 | 99.92% | 0.03248% | 0.04256% | 1283644.8929 | 4112881.4603 | 123888.2802 | 514.3813 | 1159242.2314 | 397700.3298 | 1078.3554 | 3714102.7751 | 1105 |  | 71 | 1105-1479 | 4228043.5461 | 2944398.6532 | 115162.0858 | 4224870.7096 | 2941827.1346 | 113241.2499 | 1373.4345 | 772.1166 | 121.4339 | 1799.402 | 408487.0481 | 284598.7679 | 10786.7184 | 408475.5907 | 284591.7339 | 10784.4711 | 10.1035 | 5.68 | 0.89331 | 1.354 | 3816740.4875 | 2657498.2561 | 102637.7124 | 3816375.3432 | 2657221.4138 | 102456.4212 | 201.6854 | 113.3834 | 17.8323 | 163.4589 | 2816.0105 | 2301.6291 | 1737.6551 | 19.7757 | 13.9868 | 0.35766 | 1161.6457 | 653.0533 | 102.7084 | 1634.5891 | 0.010576 | 0.0075218 | 0.0001914 | 0.092486 | 0.052524 | 0.0092486 | 0.0024988 | 5000000 | scaled
1105-1483 | 417001.2973 | 394048.1697 | 22591.7751 | 361.3525 | 94.5% | 5.418% | 0.08666% | 231816.5736 | 414351.1886 | 11559.3779 | 7998.2956 | 212258.9001 | 20399.4078 | 16652.1257 | 377299.655 | 1105 |  | 72 | 1105-1483 | 417001.2973 | 185184.7238 | 2650.1088 | 394048.1697 | 172171.2105 | 392.4676 | 22591.7751 | 12652.1607 | 1896.2887 | 361.3525 | 20430.8584 | 8871.4806 | 31.4506 | 20383.0379 | 8844.5798 | 27.1876 | 47.5486 | 26.6288 | 3.9911 | 0.27191 | 378064.8009 | 165805.9008 | 765.1459 | 373658.3044 | 163323.6711 | 365.207 | 4373.671 | 2449.4042 | 367.1134 | 32.8255 | 18505.638 | 10507.3424 | 1853.5123 | 6.8273 | 2.9596 | 0.072954 | 18170.5555 | 10176.1277 | 1525.1842 | 328.2551 | 0.0008972 | 0.0003886 | 1e-05 | 0.062422 | 0.035451 | 0.0062422 | 0.0004996 | 5000000 | scaled
1117-1121F | 101566.2718 | 18451.1165 | 82929.1031 | 186.0522 | 18.17% | 81.65% | 0.1832% | 45141.4269 | 95483.912 | 652.1271 | 34047.7217 | 10441.578 | 1403.4829 | 70790.5343 | 23289.8948 | 1117 |  | 73 | 1117-1121F | 101566.2718 | 56424.8449 | 6082.3597 | 18451.1165 | 10488.0457 | 342.1644 | 82929.1031 | 45750.747 | 5554.1432 | 186.0522 | 1436.2859 | 784.1587 | 32.803 | 1325.2518 | 722.8401 | 25.2359 | 110.8941 | 61.1786 | 7.4271 | 0.14 | 24109.9397 | 13668.3617 | 820.0448 | 16780.9821 | 9617.5083 | 313.4217 | 7312.0565 | 4033.9523 | 489.722 | 16.9011 | 76020.0463 | 41972.3245 | 5229.5119 | 344.8826 | 147.6973 | 3.5068 | 75506.1525 | 41655.6161 | 5056.9941 | 169.0111 | 0.0005396 | 0.0002336 | 6e-06 | 0.0062352 | 0.003539 | 0.0006236 | 0.0002542 | 5000000 | scaled
1118-1718F | 788375.657 | 783677.6985 | 4103.8402 | 594.1183 | 99.4% | 0.5205% | 0.07536% | 300081.1705 | 776071.3912 | 22183.9002 | 1417.213 | 276480.0572 | 56988.4152 | 2952.7263 | 716130.2497 | 1118 |  | 74 | 1118-1718F | 788375.657 | 488294.4865 | 12304.2658 | 783677.6985 | 485390.2974 | 11341.0301 | 4103.8402 | 2310.0708 | 369.1174 | 594.1183 | 57821.4705 | 35637.5703 | 833.0553 | 57793.1652 | 35621.4417 | 830.1026 | 27.8583 | 15.6816 | 2.5057 | 0.44705 | 726770.7378 | 450290.6806 | 10640.4881 | 725874.5869 | 449762.643 | 10510.7686 | 842.1808 | 474.0675 | 75.7494 | 53.9701 | 3783.4487 | 2366.2357 | 830.7223 | 9.9463 | 6.2127 | 0.1589 | 3233.8012 | 1820.3218 | 290.8623 | 539.7012 | 0.0021904 | 0.0012636 | 3.24e-05 | 0.10477 | 0.059477 | 0.010477 | 0.0008522 | 5000000 | scaled
1119-6F | 14112.606 | 13593.2244 | 0 | 519.3816 | 96.32% | 0% | 3.68% | 6215.4839 | 13570.472 | 388.1958 | 2715.448 | 3111.84 | 876.3889 | 5342.6576 | 7351.4255 | 1119 |  | 75 | 1119-6F | 14112.606 | 7897.1222 | 542.134 | 13593.2244 | 7377.7406 | 22.7524 | 0 | 0 | 0 | 519.3816 | 876.7797 | 488.5839 | 0.39082 | 876.3889 | 488.1931 | 0 | 0 | 0 | 0 | 0.39082 | 7398.6065 | 4286.7664 | 47.181 | 7351.4255 | 4239.5854 | 0 | 0 | 0 | 0 | 47.181 | 5837.2198 | 3121.7718 | 494.5622 | 5365.41 | 2649.962 | 22.7524 | 0 | 0 | 0 | 471.8098 | 0.0015138 | 0.0006986 | 1.76e-05 | 0 | 0 | 0 | 0.0007632 | 5000000 | scaled
1119-9F | 44057.8268 | 761.5686 | 41945.4368 | 1350.8213 | 1.729% | 95.21% | 3.066% | 19239.2267 | 39823.8541 | 53.1934 | 17318.8756 | 1867.1577 | 93.5197 | 35966.5526 | 3763.7818 | 1119 |  | 76 | 1119-9F | 44057.8268 | 24818.6001 | 4233.9727 | 761.5686 | 329.7632 | 80.1588 | 41945.4368 | 23138.0156 | 2802.9925 | 1350.8213 | 105.4424 | 52.249 | 11.9228 | 52.8786 | 22.7979 | 7.4617 | 51.5474 | 28.4347 | 3.4446 | 1.0164 | 4207.0562 | 2339.8986 | 443.2745 | 297.8469 | 128.4734 | 67.5331 | 3786.4998 | 2088.7157 | 253.0318 | 122.7095 | 39745.3281 | 22426.4525 | 3778.7754 | 410.8431 | 178.4919 | 5.164 | 38107.3896 | 21020.8652 | 2546.516 | 1227.0953 | 0.0034356 | 0.0014878 | 3.76e-05 | 0.0062422 | 0.003543 | 0.0006242 | 0.0018724 | 5000000 | scaled
1138-6R | 4663877.8673 | 4249838.818 | 399553.8585 | 14485.1909 | 91.12% | 8.567% | 0.3106% | 2529205.6449 | 4571063.8105 | 193156.1515 | 163466.3902 | 2172583.1032 | 345694.8769 | 339773.2869 | 3885595.6467 | 1138 |  | 77 | 1138-6R | 4663877.8673 | 2134672.2224 | 92814.0568 | 4249838.818 | 1895347.4107 | 42438.7043 | 399553.8585 | 224839.6208 | 35890.1616 | 14485.1909 | 349324.6481 | 156168.4966 | 3629.7711 | 348677.4688 | 155799.5454 | 3561.7173 | 636.2796 | 358.0515 | 57.1542 | 10.8996 | 3928730.6542 | 1756147.551 | 43135.0075 | 3893522.5151 | 1735759.6076 | 38774.7675 | 33892.2944 | 19072.0987 | 3044.3954 | 1315.8447 | 385822.565 | 222356.1748 | 46049.2781 | 7638.834 | 3788.2576 | 102.2195 | 365025.2845 | 205409.4706 | 32788.612 | 13158.4466 | 0.048464 | 0.022247 | 0.0006716 | 0.10269 | 0.058291 | 0.010269 | 0.02037 | 5000000 | scaled
1139-4F | 472177.0734 | 1225.1707 | 468726.8593 | 2225.0435 | 0.2595% | 99.27% | 0.4712% | 205664.3941 | 427871.8055 | 363.5369 | 186863.9195 | 18436.9377 | 732.0205 | 388913.9422 | 38225.8428 | 1139 |  | 78 | 1139-4F | 472177.0734 | 266512.6793 | 44305.2679 | 1225.1707 | 499.621 | 19.0666 | 468726.8593 | 263788.0148 | 42061.1579 | 2225.0435 | 798.9866 | 435.4497 | 66.9662 | 91.0585 | 36.3131 | 1.9163 | 706.2538 | 397.4624 | 63.3756 | 1.6743 | 42154.5092 | 23717.5715 | 3928.6664 | 553.7542 | 217.3101 | 11.6399 | 41398.6305 | 23298.1369 | 3714.902 | 202.1245 | 429223.5776 | 242359.6581 | 40309.6354 | 580.3579 | 245.9979 | 5.5104 | 426621.9749 | 240092.4155 | 38282.8803 | 2021.2447 | 0.0076212 | 0.0033468 | 8.48e-05 | 0.10153 | 0.057641 | 0.010153 | 0.0031544 | 5000000 | scaled
1139-5 | 335856.5349 | 1244.8238 | 334164.6331 | 447.078 | 0.3706% | 99.5% | 0.1331% | 146735.1472 | 305412.3968 | 198.2576 | 132605.7106 | 13931.1789 | 412.9724 | 275980.6576 | 29018.7668 | 1139 |  | 79 | 1139-5 | 335856.5349 | 189121.3878 | 30444.1381 | 1244.8238 | 539.3298 | 13.4644 | 334164.6331 | 188134.9799 | 29983.5957 | 447.078 | 454.0161 | 255.7585 | 41.0437 | 0 | 0 | 0 | 453.6797 | 255.4221 | 40.7073 | 0.33641 | 31919.8044 | 17988.6255 | 2901.0376 | 0 | 0 | 0 | 31879.1916 | 17948.0127 | 2860.4248 | 40.6129 | 303482.7143 | 170877.0037 | 27502.0567 | 1244.8238 | 539.3298 | 13.4644 | 301831.7618 | 169931.5452 | 27082.4636 | 406.1287 | 0.001902 | 0.000824 | 2.06e-05 | 0.10161 | 0.05771 | 0.010161 | 0.000649 | 5000000 | scaled
114-18AE | 66683.4264 | 3124.9257 | 60888.8544 | 2669.6463 | 4.686% | 91.31% | 4.003% | 28686.1588 | 59890.5155 | 152.1831 | 25588.8541 | 2945.1216 | 311.9151 | 53386.8473 | 6191.7532 | 114 |  | 80 | 114-18AE | 66683.4264 | 37997.2676 | 6792.9109 | 3124.9257 | 1550.765 | 20.2215 | 60888.8544 | 33776.8562 | 4103.0431 | 2669.6463 | 320.5834 | 168.4003 | 8.6683 | 243.654 | 124.8308 | 1.6109 | 74.9205 | 41.5606 | 5.0486 | 2.0088 | 6780.0986 | 3834.977 | 588.3455 | 1531.249 | 815.3006 | 8.477 | 5006.3372 | 2777.1639 | 337.3559 | 242.5125 | 59582.7444 | 33993.8903 | 6195.8971 | 1350.0227 | 610.6336 | 10.1336 | 55807.5967 | 30958.1317 | 3760.6386 | 2425.125 | 0.0081338 | 0.0035232 | 8.98e-05 | 0.0074536 | 0.004251 | 0.0007454 | 0.0037986 | 5000000 | scaled
114-48 | 88860.6048 | 3625.4415 | 81459.1885 | 3775.9748 | 4.08% | 91.67% | 4.249% | 38398.7346 | 79577.6225 | 110.685 | 34458.236 | 3829.8136 | 220.2251 | 71388.7361 | 7968.6613 | 114 |  | 81 | 114-48 | 88860.6048 | 50461.8703 | 9282.9823 | 3625.4415 | 1596.3952 | 44.0843 | 81459.1885 | 45089.5002 | 5462.9232 | 3775.9748 | 232.9541 | 122.2691 | 12.729 | 128.7637 | 63.3287 | 3.0909 | 101.3491 | 56.099 | 6.7968 | 2.8413 | 8866.141 | 5036.3275 | 897.4797 | 398.1174 | 195.938 | 9.5774 | 8125.0115 | 4497.3773 | 544.8902 | 343.0121 | 79761.5097 | 45303.2737 | 8372.7735 | 3098.5604 | 1337.1285 | 31.416 | 73232.8279 | 40536.0239 | 4911.2362 | 3430.1214 | 0.011506 | 0.0049826 | 0.000126 | 0.010723 | 0.006104 | 0.0010724 | 0.0052914 | 5000000 | scaled
1140-8F | 97447.0968 | 538.0691 | 96282.2653 | 626.7624 | 0.5522% | 98.8% | 0.6432% | 42462.0611 | 88178.4006 | 86.8383 | 38257.2547 | 4117.968 | 162.8414 | 79546.119 | 8469.4401 | 1140 |  | 82 | 1140-8F | 97447.0968 | 54985.0357 | 9268.6962 | 538.0691 | 221.3977 | 6.3579 | 96282.2653 | 54136.8756 | 8635.5758 | 626.7624 | 173.4286 | 86.5903 | 10.5872 | 69.4374 | 27.9125 | 0.83092 | 103.5196 | 58.2062 | 9.2847 | 0.47162 | 9327.9887 | 5210.0207 | 858.5486 | 384.7672 | 156.5704 | 4.6003 | 8886.286 | 4996.5148 | 797.0128 | 56.9355 | 87945.6794 | 49688.4247 | 8399.5604 | 83.8644 | 36.9148 | 0.92675 | 87292.4597 | 49082.1547 | 7829.2784 | 569.3553 | 0.0018234 | 0.000789 | 2.02e-05 | 0.10144 | 0.057535 | 0.010144 | 0.0008748 | 5000000 | scaled
116-12R | 54554.885 | 3024.7688 | 49064.2678 | 2465.8483 | 5.544% | 89.94% | 4.52% | 23628.1362 | 48783.4599 | 41.2092 | 21751.505 | 1835.422 | 74.9838 | 44909.8059 | 3798.6703 | 116 |  | 83 | 116-12R | 54554.885 | 30926.7488 | 5771.425 | 3024.7688 | 1276.1526 | 33.3155 | 49064.2678 | 27184.7479 | 3272.2612 | 2465.8483 | 81.1438 | 39.9346 | 6.16 | 14.7464 | 2.3188 | 0 | 64.542 | 35.7604 | 4.3045 | 1.8555 | 4290.1268 | 2454.7047 | 491.4565 | 55.8759 | 8.7691 | 0 | 4010.2515 | 2221.9363 | 267.4572 | 223.9993 | 50183.6144 | 28432.1094 | 5273.8085 | 2954.1466 | 1265.0647 | 33.3155 | 44989.4743 | 24927.0512 | 3000.4995 | 2239.9935 | 0.0065216 | 0.002824 | 7.2e-05 | 0.014482 | 0.0082546 | 0.0014482 | 0.0034574 | 5000000 | scaled
116-31F | 141477.223 | 524.697 | 139419.8512 | 1532.6747 | 0.3709% | 98.55% | 1.083% | 62567.274 | 130643.4479 | 93.1281 | 57202.2348 | 5271.9112 | 181.8414 | 119508.8741 | 10952.7324 | 116 |  | 84 | 116-31F | 141477.223 | 78909.949 | 10833.775 | 524.697 | 184.5379 | 3.2052 | 139419.8512 | 77192.7363 | 9297.8951 | 1532.6747 | 194.3116 | 101.1836 | 12.4702 | 23.4637 | 6.0753 | 0 | 169.6946 | 93.955 | 11.3169 | 1.1533 | 11865.572 | 6593.6609 | 912.8396 | 126.2286 | 31.7842 | 0 | 11600.1142 | 6422.6475 | 773.6104 | 139.2292 | 129417.3393 | 72215.1045 | 9908.4652 | 375.0047 | 146.6785 | 3.2052 | 127650.0424 | 70676.1338 | 8512.9678 | 1392.2922 | 0.0042646 | 0.0018466 | 4.68e-05 | 0.014351 | 0.0081742 | 0.001435 | 0.0021658 | 5000000 | scaled
116-32F | 87668.6781 | 0 | 87668.6781 | 0 | 0% | 100% | 0% | 13980.3306 | 29205.0348 | 17.2524 | 12814.1525 | 1148.9257 | 36.0405 | 26768.8783 | 2400.1159 | 116 |  | 85 | 116-32F | 87668.6781 | 73688.3475 | 58463.6433 | 0 | 0 | 0 | 87668.6781 | 73688.3475 | 58463.6433 | 0 | 108.1876 | 90.9352 | 72.1471 | 0 | 0 | 0 | 108.1876 | 90.9352 | 72.1471 | 0 | 7204.7505 | 6055.8249 | 4804.6346 | 0 | 0 | 0 | 7204.7505 | 6055.8249 | 4804.6346 | 0 | 80355.7399 | 67541.5875 | 53586.8616 | 0 | 0 | 0 | 80355.7399 | 67541.5875 | 53586.8616 | 0 | 0 | 0 | 0 | 0.0144 | 0.0144 | 0.0144 | 0 | 5000000 | scaled
1161-53AE | 29935.0541 | 0 | 29935.0541 | 0 | 0% | 100% | 0% | 2447.2258 | 5106.376 | 1.6072 | 1940.304 | 505.3145 | 3.3536 | 4048.6341 | 1054.3882 | 1161 |  | 86 | 1161-53AE | 29935.0541 | 27487.8283 | 24828.6781 | 0 | 0 | 0 | 29935.0541 | 27487.8283 | 24828.6781 | 0 | 19.66 | 18.0528 | 16.3064 | 0 | 0 | 0 | 19.66 | 18.0528 | 16.3064 | 0 | 6181.1289 | 5675.8143 | 5126.7407 | 0 | 0 | 0 | 6181.1289 | 5675.8143 | 5126.7407 | 0 | 23734.2653 | 21793.9612 | 19685.6311 | 0 | 0 | 0 | 23734.2653 | 21793.9612 | 19685.6311 | 0 | 0 | 0 | 0 | 0.057168 | 0.057168 | 0.057168 | 0 | 5000000 | scaled
1161-54 | 980.4547 | 0 | 980.4547 | 0 | 0% | 100% | 0% | 80.1888 | 167.1389 | 1.0403 | 62.7948 | 16.3537 | 2.1683 | 130.8843 | 34.0863 | 1161 |  | 87 | 1161-54 | 980.4547 | 900.266 | 813.3158 | 0 | 0 | 0 | 980.4547 | 900.266 | 813.3158 | 0 | 12.7196 | 11.6793 | 10.5513 | 0 | 0 | 0 | 12.7196 | 11.6793 | 10.5513 | 0 | 199.9537 | 183.6001 | 165.8675 | 0 | 0 | 0 | 199.9537 | 183.6001 | 165.8675 | 0 | 767.7813 | 704.9865 | 636.8971 | 0 | 0 | 0 | 767.7813 | 704.9865 | 636.8971 | 0 | 0 | 0 | 0 | 0.057338 | 0.057338 | 0.057338 | 0 | 5000000 | scaled
1161-55 | 1454.8528 | 0 | 1454.8528 | 0 | 0% | 100% | 0% | 118.8112 | 247.7445 | 0.07803 | 94.2005 | 24.5327 | 0.16271 | 196.4263 | 51.1554 | 1161 |  | 88 | 1161-55 | 1454.8528 | 1336.0416 | 1207.1084 | 0 | 0 | 0 | 1454.8528 | 1336.0416 | 1207.1084 | 0 | 0.95548 | 0.87745 | 0.79277 | 0 | 0 | 0 | 0.95548 | 0.87745 | 0.79277 | 0 | 300.4048 | 275.8721 | 249.2493 | 0 | 0 | 0 | 300.4048 | 275.8721 | 249.2493 | 0 | 1153.4926 | 1059.2921 | 957.0662 | 0 | 0 | 0 | 1153.4926 | 1059.2921 | 957.0662 | 0 | 0 | 0 | 0 | 0.057441 | 0.057441 | 0.057441 | 0 | 5000000 | scaled
1161-61 | 4368.0124 | 0 | 4368.0124 | 0 | 0% | 100% | 0% | 356.4273 | 743.7062 | 0.23409 | 282.5965 | 73.5968 | 0.48843 | 589.6538 | 153.5639 | 1161 |  | 89 | 1161-61 | 4368.0124 | 4011.585 | 3624.3062 | 0 | 0 | 0 | 4368.0124 | 4011.585 | 3624.3062 | 0 | 2.8687 | 2.6346 | 2.3803 | 0 | 0 | 0 | 2.8687 | 2.6346 | 2.3803 | 0 | 901.9275 | 828.3307 | 748.3636 | 0 | 0 | 0 | 901.9275 | 828.3307 | 748.3636 | 0 | 3463.2162 | 3180.6197 | 2873.5624 | 0 | 0 | 0 | 3463.2162 | 3180.6197 | 2873.5624 | 0 | 0 | 0 | 0 | 0.057489 | 0.057489 | 0.057489 | 0 | 5000000 | scaled
1161-62 | 6317.5192 | 0 | 6317.5192 | 0 | 0% | 100% | 0% | 515.0528 | 1075.2424 | 0.44226 | 408.2815 | 106.329 | 0.92327 | 852.343 | 221.9762 | 1161 |  | 90 | 1161-62 | 6317.5192 | 5802.4664 | 5242.2768 | 0 | 0 | 0 | 6317.5192 | 5802.4664 | 5242.2768 | 0 | 5.4246 | 4.9823 | 4.5013 | 0 | 0 | 0 | 5.4246 | 4.9823 | 4.5013 | 0 | 1304.2071 | 1197.8781 | 1082.2309 | 0 | 0 | 0 | 1304.2071 | 1197.8781 | 1082.2309 | 0 | 5007.8875 | 4599.6059 | 4155.5445 | 0 | 0 | 0 | 5007.8875 | 4599.6059 | 4155.5445 | 0 | 0 | 0 | 0 | 0.057556 | 0.057556 | 0.057556 | 0 | 5000000 | scaled
1161-74 | 1461.7172 | 1391.5065 | 0 | 70.2107 | 95.2% | 0% | 4.803% | 964.8219 | 1391.5065 | 71.1429 | 0 | 893.679 | 102.5827 | 0 | 1288.9237 | 1161 |  | 91 | 1161-74 | 1461.7172 | 496.8953 | 70.2107 | 1391.5065 | 426.6846 | 0 | 0 | 0 | 0 | 70.2107 | 102.6356 | 31.4927 | 0.052831 | 102.5827 | 31.4399 | 0 | 0 | 0 | 0 | 0.052831 | 1295.3017 | 401.6227 | 6.378 | 1288.9237 | 395.2447 | 0 | 0 | 0 | 0 | 6.378 | 63.7799 | 63.7799 | 63.7799 | 0 | 0 | 0 | 0 | 0 | 0 | 63.7799 | 0.0001132 | 4.9e-05 | 1.2e-06 | 0 | 0 | 0 | 9.74e-05 | 5000000 | scaled
1162-324R | 240289.6501 | 211905.5549 | 26413.3474 | 1970.7478 | 88.19% | 10.99% | 0.8202% | 59502.3518 | 224799.1184 | 3071.088 | 9623.4869 | 46807.7769 | 12734.5401 | 20883.1622 | 191181.4161 | 1162 |  | 92 | 1162-324R | 240289.6501 | 180787.2983 | 15490.5317 | 211905.5549 | 164010.0477 | 11326.9087 | 26413.3474 | 14806.5028 | 2192.8753 | 1970.7478 | 13404.6936 | 10333.6056 | 670.1536 | 13276.5256 | 10261.107 | 658.1531 | 126.6851 | 71.0157 | 10.5176 | 1.4829 | 202447.6334 | 155639.8564 | 11266.2173 | 196837.2502 | 152416.181 | 10636.2737 | 5431.3591 | 3044.6513 | 450.9195 | 179.0241 | 24437.3231 | 14813.8362 | 3554.1609 | 1791.7791 | 1332.7596 | 32.4819 | 20855.3032 | 11690.8357 | 1731.4382 | 1790.2408 | 0.0081596 | 0.0061212 | 0.0001558 | 0.057729 | 0.032831 | 0.005773 | 0.0027692 | 5000000 | scaled
1162-329R | 206587.8377 | 199607.0303 | 5354.0204 | 1626.787 | 96.62% | 2.592% | 0.7875% | 79232.1404 | 201987.1356 | 4599.0705 | 1936.4123 | 72696.6575 | 11869.9044 | 4070.3732 | 186046.858 | 1162 |  | 93 | 1162-329R | 206587.8377 | 127355.6974 | 4600.7022 | 199607.0303 | 122728.433 | 2529.3342 | 5354.0204 | 3000.4774 | 444.5809 | 1626.787 | 12035.2273 | 7436.1568 | 165.3229 | 11974.423 | 7401.543 | 159.1515 | 59.5802 | 33.3897 | 4.9473 | 1.2241 | 188648.5595 | 115951.902 | 2601.7015 | 187460.1096 | 115220.9149 | 2367.509 | 1040.6715 | 583.2087 | 86.4141 | 147.7784 | 5904.0509 | 3967.6386 | 1833.6778 | 172.4977 | 105.9751 | 2.6738 | 4253.7688 | 2383.879 | 353.2195 | 1477.7845 | 0.0099208 | 0.0055956 | 0.0001422 | 0.057817 | 0.032869 | 0.0057816 | 0.0022816 | 5000000 | scaled
1162-363 | 247999.3526 | 242411.3636 | 4445.3103 | 1142.6787 | 97.75% | 1.792% | 0.4608% | 71622.9104 | 236098.2893 | 4084.1233 | 1547.8303 | 65990.9568 | 13340.5338 | 3247.1446 | 219510.6109 | 1162 |  | 94 | 1162-363 | 247999.3526 | 176376.4422 | 11901.0633 | 242411.3636 | 172742.3171 | 10389.216 | 4445.3103 | 2491.4464 | 369.1685 | 1142.6787 | 13899.4781 | 9815.3548 | 558.9444 | 13846.965 | 9785.545 | 553.7949 | 51.6533 | 28.9499 | 4.2896 | 0.85983 | 229524.2997 | 163533.343 | 10013.6888 | 228512.6791 | 162920.7394 | 9834.4957 | 907.8189 | 508.8019 | 75.3914 | 103.8017 | 4575.5747 | 3027.7445 | 1328.4301 | 51.7194 | 36.0327 | 0.9254 | 3485.8381 | 1953.6946 | 289.4875 | 1038.0172 | 0.0052862 | 0.0034926 | 8.9e-05 | 0.057914 | 0.032926 | 0.0057914 | 0.001629 | 5000000 | scaled
1162-385F | 3430.6393 | 0 | 3430.6393 | 0 | 0% | 100% | 0% | 278.7516 | 581.7037 | 0.67877 | 220.6174 | 57.4555 | 1.4165 | 460.3881 | 119.8991 | 1162 |  | 95 | 1162-385F | 3430.6393 | 3151.8877 | 2848.9357 | 0 | 0 | 0 | 3430.6393 | 3151.8877 | 2848.9357 | 0 | 8.3537 | 7.675 | 6.9373 | 0 | 0 | 0 | 8.3537 | 7.675 | 6.9373 | 0 | 707.1138 | 649.6583 | 587.2147 | 0 | 0 | 0 | 707.1138 | 649.6583 | 587.2147 | 0 | 2715.1718 | 2494.5544 | 2254.7837 | 0 | 0 | 0 | 2715.1718 | 2494.5544 | 2254.7837 | 0 | 0 | 0 | 0 | 0.057998 | 0.057998 | 0.057998 | 0 | 5000000 | scaled
1162-387F | 12197.2449 | 0 | 12197.2449 | 0 | 0% | 100% | 0% | 990.2133 | 2069.4139 | 0.65393 | 789.446 | 200.1133 | 1.3666 | 1649.8371 | 418.2102 | 1162 |  | 96 | 1162-387F | 12197.2449 | 11207.0316 | 10127.831 | 0 | 0 | 0 | 12197.2449 | 11207.0316 | 10127.831 | 0 | 8.055 | 7.401 | 6.6883 | 0 | 0 | 0 | 8.055 | 7.401 | 6.6883 | 0 | 2464.9552 | 2264.8419 | 2046.745 | 0 | 0 | 0 | 2464.9552 | 2264.8419 | 2046.745 | 0 | 9724.2347 | 8934.7887 | 8074.3976 | 0 | 0 | 0 | 9724.2347 | 8934.7887 | 8074.3976 | 0 | 0 | 0 | 0 | 0.058154 | 0.058154 | 0.058154 | 0 | 5000000 | scaled
1166-15R | 3965221.7427 | 3896388.7437 | 65726.9864 | 3106.0126 | 98.26% | 1.658% | 0.07833% | 1868981.4329 | 3917977.1771 | 103186.8805 | 26322.0541 | 1739472.4984 | 215636.979 | 55032.7138 | 3647307.4843 | 1166 |  | 97 | 1166-15R | 3965221.7427 | 2096240.3098 | 47244.5656 | 3896388.7437 | 2055944.9533 | 37973.2941 | 65726.9864 | 37189.3439 | 6165.259 | 3106.0126 | 217804.5572 | 114617.6768 | 2167.5782 | 217711.7887 | 114564.1722 | 2156.7585 | 90.4313 | 51.1674 | 8.4826 | 2.3372 | 3683946.2293 | 1944473.7309 | 36638.7451 | 3677763.1515 | 1940852.7438 | 35803.0799 | 5900.9256 | 3338.8348 | 553.5129 | 282.1523 | 63470.9561 | 37148.9021 | 8438.2423 | 913.8036 | 528.0374 | 13.4557 | 59735.6295 | 33799.3417 | 5603.2635 | 2821.5231 | 0.015585 | 0.0082502 | 0.00021 | 0.17399 | 0.098963 | 0.017399 | 0.004392 | 5000000 | scaled
1166-18R | 10108490.1387 | 10085269.383 | 19839.3591 | 3381.3966 | 99.77% | 0.1963% | 0.03345% | 4000668.0906 | 9936849.2209 | 258007.1685 | 8273.9291 | 3734386.993 | 641394.8611 | 18293.8036 | 9277160.5562 | 1166 |  | 98 | 1166-18R | 10108490.1387 | 6107822.0481 | 171640.9178 | 10085269.383 | 6093219.3807 | 166398.4171 | 19839.3591 | 11221.2708 | 1861.1041 | 3381.3966 | 652199.7979 | 394192.6294 | 10804.9368 | 652123.803 | 394148.541 | 10795.5022 | 73.4505 | 41.5441 | 6.8903 | 2.5444 | 9433234.8784 | 5698847.8854 | 156074.3222 | 9430690.0214 | 5697275.0657 | 155557.2392 | 2237.6886 | 1265.6513 | 209.9146 | 307.1684 | 23055.4623 | 14781.5332 | 4761.6587 | 2455.5586 | 1795.774 | 45.6757 | 17528.2199 | 9914.0754 | 1644.2992 | 3071.6838 | 0.034692 | 0.021179 | 0.0005388 | 0.1742 | 0.099047 | 0.01742 | 0.004761 | 5000000 | scaled
1166-342R | 10322641.9923 | 10227749.4926 | 88974.2171 | 5918.2825 | 99.08% | 0.8619% | 0.05733% | 4127049.9048 | 10166648.9147 | 218356.3884 | 35243.993 | 3873449.5235 | 538085.7331 | 74135.5115 | 9554427.6701 | 1166 |  | 99 | 1166-342R | 10322641.9923 | 6195592.0874 | 155993.0776 | 10227749.4926 | 6139341.8762 | 141732.0058 | 88974.2171 | 50331.9287 | 8342.7892 | 5918.2825 | 545775.4157 | 327419.0273 | 7689.6827 | 545647.8465 | 327344.9284 | 7673.6852 | 123.116 | 69.6456 | 11.5441 | 4.4533 | 9689827.8197 | 5816378.2962 | 135400.1496 | 9680391.8474 | 5810806.9566 | 134028.1626 | 8898.3514 | 5033.7188 | 834.3661 | 537.6208 | 87038.7568 | 51794.7639 | 12903.2454 | 1709.7987 | 1189.9912 | 30.158 | 79952.7498 | 45228.5643 | 7496.879 | 5376.2084 | 0.037336 | 0.022147 | 0.0005624 | 0.17309 | 0.098437 | 0.017309 | 0.0083452 | 5000000 | scaled
1173-68 | 6499.8985 | 5583.6911 | 0 | 916.2074 | 85.9% | 0% | 14.1% | 3169.7597 | 5573.9835 | 632.3877 | 36.2882 | 2501.0837 | 1104.03 | 63.8921 | 4406.0614 | 1173 |  | 100 | 1173-68 | 6499.8985 | 3330.1388 | 925.915 | 5583.6911 | 2413.9315 | 9.7076 | 0 | 0 | 0 | 916.2074 | 1106.9675 | 474.5798 | 2.9374 | 1106.278 | 473.8903 | 2.248 | 0 | 0 | 0 | 0.68942 | 4496.1524 | 1995.0687 | 90.091 | 4412.9235 | 1911.8398 | 6.8621 | 0 | 0 | 0 | 83.2289 | 896.7787 | 860.4904 | 832.8866 | 64.4896 | 28.2014 | 0.59753 | 0 | 0 | 0 | 832.289 | 0.00248 | 0.0010736 | 2.74e-05 | 0 | 0 | 0 | 0.0012892 | 5000000 | scaled
1173-69 | 238.6847 | 28.7008 | 0 | 209.9839 | 12.02% | 0% | 87.98% | 16.2717 | 28.3851 | 0 | 16.2717 | 0 | 0 | 28.3851 | 0 | 1173 |  | 101 | 1173-69 | 238.6847 | 222.413 | 210.2997 | 28.7008 | 12.4291 | 0.31574 | 0 | 0 | 0 | 209.9839 | 0.15801 | 0.15801 | 0.15801 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15801 | 19.0751 | 19.0751 | 19.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 19.0751 | 219.4516 | 203.1799 | 191.0666 | 28.7008 | 12.4291 | 0.31574 | 0 | 0 | 0 | 190.7508 | 0.000647 | 0.0002802 | 7.2e-06 | 0 | 0 | 0 | 0.000299 | 5000000 | scaled
1173-70 | 15376.365 | 104.2249 | 14949.8078 | 322.3323 | 0.6778% | 97.23% | 2.096% | 6700.5238 | 14049.032 | 6.1187 | 5751.8313 | 942.5738 | 12.8482 | 12056.9371 | 1979.2468 | 1173 |  | 102 | 1173-70 | 15376.365 | 8675.8412 | 1327.333 | 104.2249 | 45.1387 | 1.0964 | 14949.8078 | 8308.3702 | 1003.9043 | 322.3323 | 14.0156 | 7.8969 | 1.1674 | 0 | 0 | 0 | 13.7731 | 7.6544 | 0.92488 | 0.24254 | 2151.0049 | 1208.4311 | 171.7582 | 0 | 0 | 0 | 2121.724 | 1179.1502 | 142.4773 | 29.2809 | 13211.3445 | 7459.5132 | 1154.4074 | 104.2249 | 45.1387 | 1.0964 | 12814.3107 | 7121.5656 | 860.5021 | 292.8089 | 0.000741 | 0.000321 | 8e-06 | 0.0075054 | 0.0042888 | 0.0007506 | 0.0004506 | 5000000 | scaled
1180-9 | 4069.7193 | 2332.5264 | 0 | 1737.1929 | 57.31% | 0% | 42.69% | 1154.8631 | 2324.8705 | 92.1419 | 749.8823 | 312.839 | 209.8762 | 1369.5754 | 745.4189 | 1180 |  | 103 | 1180-9 | 4069.7193 | 2914.8562 | 1744.8489 | 2332.5264 | 1177.6633 | 7.6559 | 0 | 0 | 0 | 1737.1929 | 211.1834 | 119.0415 | 1.3072 | 209.8762 | 117.7343 | 0 | 0 | 0 | 0 | 1.3072 | 903.2267 | 590.3878 | 157.8078 | 745.4189 | 432.58 | 0 | 0 | 0 | 0 | 157.8078 | 2955.3093 | 2205.427 | 1585.7339 | 1377.2313 | 627.349 | 7.6559 | 0 | 0 | 0 | 1578.0779 | 0.005041 | 0.0021828 | 5.54e-05 | 0 | 0 | 0 | 0.002469 | 5000000 | scaled
120-360F | 24545.7737 | 285.6246 | 23418.1827 | 841.9664 | 1.164% | 95.41% | 3.43% | 10558.5688 | 22125.8794 | 10.6551 | 9360.2435 | 1187.6703 | 22.5326 | 19607.4215 | 2495.9253 | 120 |  | 104 | 120-360F | 24545.7737 | 13987.2048 | 2419.8942 | 285.6246 | 124.2709 | 3.1748 | 23418.1827 | 13020.9676 | 1574.753 | 841.9664 | 24.7639 | 14.1089 | 2.2314 | 0.3693 | 0.26367 | 0 | 23.7611 | 13.2116 | 1.5978 | 0.63355 | 2752.2115 | 1564.5413 | 256.2862 | 1.8963 | 1.3544 | 0 | 2673.8304 | 1486.702 | 179.8014 | 76.4848 | 21768.7982 | 12408.5547 | 2161.3766 | 283.359 | 122.6527 | 3.1748 | 20720.5912 | 11521.054 | 1393.3538 | 764.848 | 0.001772 | 0.000767 | 1.96e-05 | 0.0074712 | 0.004271 | 0.0007472 | 0.0011704 | 5000000 | scaled
120-367F | 8156.3086 | 0 | 8123.3567 | 32.9519 | 0% | 99.6% | 0.404% | 3612.4295 | 7578.083 | 5.6754 | 3300.9351 | 305.819 | 11.9057 | 6924.6362 | 641.5411 | 120 |  | 105 | 120-367F | 8156.3086 | 4543.8791 | 578.2256 | 0 | 0 | 0 | 8123.3567 | 4510.9272 | 545.2737 | 32.9519 | 12.7871 | 7.1118 | 0.88146 | 0 | 0 | 0 | 12.7623 | 7.087 | 0.85666 | 0.024795 | 690.6959 | 384.8769 | 49.1548 | 0 | 0 | 0 | 687.7026 | 381.8835 | 46.1615 | 2.9934 | 7452.8255 | 4151.8904 | 528.1893 | 0 | 0 | 0 | 7422.8918 | 4121.9567 | 498.2556 | 29.9337 | 4.58e-05 | 1.98e-05 | 6e-07 | 0.0074896 | 0.0042766 | 0.000749 | 4.98e-05 | 5000000 | scaled
120-368F | 30116.209 | 299.5447 | 28777.2168 | 1039.4475 | 0.9946% | 95.55% | 3.451% | 12922.7792 | 27124.4675 | 22.7172 | 11783.8222 | 1116.2398 | 46.5794 | 24738.108 | 2339.7801 | 120 |  | 106 | 120-368F | 30116.209 | 17193.4298 | 2991.7416 | 299.5447 | 140.6795 | 14.2785 | 28777.2168 | 16013.3028 | 1938.0155 | 1039.4475 | 51.4636 | 28.7464 | 4.8842 | 13.4521 | 7.2477 | 1.5949 | 37.2293 | 20.7165 | 2.5072 | 0.78215 | 2608.7802 | 1492.5404 | 269.0001 | 69.7542 | 37.7988 | 9.9431 | 2444.6018 | 1360.3174 | 164.6329 | 94.4241 | 27455.9652 | 15672.1431 | 2717.8572 | 216.3384 | 95.633 | 2.7406 | 26295.3856 | 14632.2688 | 1770.8754 | 944.2412 | 0.0025592 | 0.0011084 | 2.78e-05 | 0.007464 | 0.0042694 | 0.0007464 | 0.0014358 | 5000000 | scaled
1201-282F | 70653.4269 | 69709.0498 | 0 | 944.3771 | 98.66% | 0% | 1.337% | 35261.7192 | 68861.4961 | 5735.6715 | 2837.9547 | 26688.0931 | 11220.5717 | 5356.5182 | 52284.4063 | 1201 |  | 107 | 1201-282F | 70653.4269 | 35391.7076 | 1791.9307 | 69709.0498 | 34447.3306 | 847.5537 | 0 | 0 | 0 | 944.3771 | 11359.7912 | 5624.1196 | 139.2195 | 11359.0806 | 5623.409 | 138.5089 | 0 | 0 | 0 | 0.71061 | 53014.8709 | 26326.7778 | 730.4646 | 52929.083 | 26240.99 | 644.6768 | 0 | 0 | 0 | 85.7879 | 6278.7648 | 3440.8102 | 922.2466 | 5420.8862 | 2582.9316 | 64.368 | 0 | 0 | 0 | 857.8786 | 0.0057104 | 0.0027322 | 6.94e-05 | 0 | 0 | 0 | 0.0013338 | 5000000 | scaled
1202-9 | 73442.0912 | 71121.2834 | 0 | 2320.8078 | 96.84% | 0% | 3.16% | 38623.1012 | 70546.1454 | 6095.6544 | 6964.5513 | 25562.8955 | 11127.7479 | 12275.7378 | 47142.6597 | 1202 |  | 108 | 1202-9 | 73442.0912 | 34818.99 | 2895.9457 | 71121.2834 | 32498.1822 | 575.1379 | 0 | 0 | 0 | 2320.8078 | 11220.6581 | 5125.0037 | 92.9102 | 11218.9117 | 5123.2573 | 91.1638 | 0 | 0 | 0 | 1.7463 | 47714.6099 | 22151.7145 | 571.9502 | 47503.7862 | 21940.8907 | 361.1264 | 0 | 0 | 0 | 210.8238 | 14506.8232 | 7542.2719 | 2231.0854 | 12398.5855 | 5434.0342 | 122.8477 | 0 | 0 | 0 | 2108.2377 | 0.0086548 | 0.003832 | 9.8e-05 | 0 | 0 | 0 | 0.003165 | 5000000 | scaled
1215-10R | 157887.7895 | 123932.8324 | 33535.8543 | 419.1029 | 78.49% | 21.24% | 0.2654% | 81405.9135 | 154176.4876 | 3757.0044 | 11371.1823 | 66277.7268 | 6993.3422 | 23694.1623 | 123488.9831 | 1215 |  | 109 | 1215-10R | 157887.7895 | 76481.876 | 3711.3019 | 123932.8324 | 57040.7458 | 0.10401 | 33535.8543 | 19022.0273 | 3292.095 | 419.1029 | 7036.3666 | 3279.3622 | 43.0244 | 6600.9835 | 3032.27 | 0 | 435.0677 | 246.7768 | 42.709 | 0.31536 | 124198.444 | 57920.7172 | 709.4608 | 117321.0766 | 54003.297 | 0 | 6839.2957 | 3879.3486 | 671.3892 | 38.0716 | 26652.979 | 15281.7967 | 2958.8167 | 10.7722 | 5.1788 | 0.10401 | 26261.4908 | 14895.9019 | 2577.9967 | 380.716 | 0.0017822 | 0.0007962 | 2.04e-05 | 0.66328 | 0.37679 | 0.066328 | 0.0005912 | 5000000 | scaled
1215-12R | 6147283.8671 | 6017063.678 | 125737.3971 | 4482.792 | 97.88% | 2.045% | 0.07292% | 2078132.4158 | 6024463.9286 | 106856.0976 | 49872.3436 | 1921403.9747 | 311683.3146 | 104493.2046 | 5608287.4094 | 1215 |  | 110 | 1215-12R | 6147283.8671 | 4069151.4513 | 122819.9385 | 6017063.678 | 3993390.6116 | 105997.7023 | 125737.3971 | 71278.0476 | 12339.4441 | 4482.792 | 317298.2428 | 210442.1452 | 5614.9282 | 317114.5959 | 210336.5784 | 5593.8636 | 180.2737 | 102.1936 | 17.6915 | 3.3732 | 5710171.7168 | 3788767.7421 | 101884.3074 | 5698556.9242 | 3782007.1706 | 100377.2141 | 11207.5727 | 6353.3517 | 1099.8734 | 407.2199 | 119813.9075 | 69941.564 | 15320.7029 | 1392.1578 | 1046.8626 | 26.6247 | 114349.5507 | 64822.5024 | 11221.8793 | 4072.199 | 0.040774 | 0.027165 | 0.0006894 | 0.65196 | 0.37015 | 0.065196 | 0.0063332 | 5000000 | scaled
1215-28R | 2215155.9721 | 2097533.216 | 115761.7845 | 1860.9717 | 94.69% | 5.226% | 0.08401% | 718724.2452 | 2174576.6984 | 35235.3011 | 43814.4331 | 639674.511 | 108560.8707 | 92040.8102 | 1973975.0176 | 1215 |  | 111 | 1215-28R | 2215155.9721 | 1496431.7269 | 40579.2737 | 2097533.216 | 1428947.8531 | 27358.2121 | 115761.7845 | 65622.9022 | 11360.09 | 1860.9717 | 110049.1573 | 74813.8563 | 1488.2867 | 109349.3978 | 74416.5709 | 1418.354 | 698.3592 | 395.885 | 68.5323 | 1.4003 | 2001577.7782 | 1361903.2671 | 27602.7606 | 1985748.3319 | 1352856.6695 | 25896.9019 | 15660.3943 | 8877.5456 | 1536.8067 | 169.0519 | 103529.0366 | 59714.6035 | 11488.2265 | 2435.4863 | 1674.6126 | 42.9561 | 99403.0309 | 56349.4715 | 9754.751 | 1690.5194 | 0.01425 | 0.0097526 | 0.000248 | 0.65068 | 0.36943 | 0.065068 | 0.0026234 | 5000000 | scaled
1215-3 | 9511.9634 | 0 | 9511.9634 | 0 | 0% | 100% | 0% | 84.1452 | 175.7366 | 1.0916 | 65.893 | 17.1605 | 2.2799 | 137.617 | 35.8397 | 1215 |  | 112 | 1215-3 | 9511.9634 | 9427.8182 | 9336.2268 | 0 | 0 | 0 | 9511.9634 | 9427.8182 | 9336.2268 | 0 | 123.4007 | 122.3091 | 121.1209 | 0 | 0 | 0 | 123.4007 | 122.3091 | 121.1209 | 0 | 1939.868 | 1922.7074 | 1904.0283 | 0 | 0 | 0 | 1939.868 | 1922.7074 | 1904.0283 | 0 | 7448.6947 | 7382.8017 | 7311.0776 | 0 | 0 | 0 | 7448.6947 | 7382.8017 | 7311.0776 | 0 | 0 | 0 | 0 | 0.65837 | 0.65837 | 0.65837 | 0 | 5000000 | scaled
1215-32R | 8696504.1653 | 8389974.3077 | 299792.8752 | 6736.9824 | 96.48% | 3.447% | 0.07747% | 4037904.0691 | 8548983.3762 | 201694.0048 | 115437.8075 | 3720772.2567 | 427037.8259 | 240632.9468 | 7881312.6035 | 1215 |  | 113 | 1215-32R | 8696504.1653 | 4658600.0962 | 147520.789 | 8389974.3077 | 4481934.5955 | 111396.1568 | 299792.8752 | 169928.5183 | 29387.6498 | 6736.9824 | 432904.5617 | 231210.5569 | 5866.7358 | 431656.1089 | 230500.7133 | 5739.7819 | 1243.3834 | 704.7743 | 121.8845 | 5.0694 | 7990871.3607 | 4270099.104 | 109558.7572 | 7956397.6455 | 4250293.619 | 105627.4185 | 33861.7231 | 19193.493 | 3319.3466 | 611.9921 | 272728.2428 | 157290.4353 | 32095.2961 | 1920.5532 | 1140.2633 | 28.9565 | 264687.7686 | 150030.2511 | 25946.4187 | 6119.921 | 0.056995 | 0.030714 | 0.00078 | 0.61487 | 0.34908 | 0.061487 | 0.0094616 | 5000000 | scaled
122-196 | 868.4323 | 722.659 | 0 | 145.7733 | 83.21% | 0% | 16.79% | 409.5592 | 717.0433 | 14.5963 | 318.594 | 76.3688 | 25.2349 | 559.7262 | 132.0823 | 122 |  | 114 | 122-196 | 868.4323 | 458.8731 | 151.3889 | 722.659 | 313.0998 | 5.6156 | 0 | 0 | 0 | 145.7733 | 25.3446 | 10.7482 | 0.10969 | 25.2349 | 10.6385 | 0 | 0 | 0 | 0 | 0.10969 | 145.3244 | 68.9556 | 13.2421 | 132.0823 | 55.7135 | 0 | 0 | 0 | 0 | 13.2421 | 697.7633 | 379.1693 | 138.0371 | 565.3418 | 246.7478 | 5.6156 | 0 | 0 | 0 | 132.4215 | 0.0002368 | 0.0001026 | 2.6e-06 | 0 | 0 | 0 | 0.000209 | 5000000 | scaled
1221-2095F | 19642.0615 | 19394.3438 | 0 | 247.7177 | 98.74% | 0% | 1.261% | 10673.2229 | 18700.8098 | 3258.0178 | 1.6176 | 7413.5875 | 5685.9399 | 2.8404 | 13012.0295 | 1221 |  | 115 | 1221-2095F | 19642.0615 | 8968.8386 | 941.2517 | 19394.3438 | 8721.1209 | 693.534 | 0 | 0 | 0 | 247.7177 | 5894.5229 | 2636.5051 | 208.5831 | 5894.3365 | 2636.3187 | 208.3967 | 0 | 0 | 0 | 0.1864 | 13519.6377 | 6106.0502 | 507.6082 | 13497.1349 | 6083.5473 | 485.1054 | 0 | 0 | 0 | 22.5028 | 227.9009 | 226.2833 | 225.0604 | 2.8724 | 1.2548 | 0.032002 | 0 | 0 | 0 | 225.0284 | 0.001325 | 0.0005738 | 1.46e-05 | 0 | 0 | 0 | 0.0003464 | 5000000 | scaled
123-437 | 1105.2687 | 830.0048 | 0 | 275.2639 | 75.1% | 0% | 24.9% | 490.6218 | 827.8568 | 53.0031 | 133.2196 | 304.3991 | 88.5829 | 232.5098 | 506.7642 | 123 |  | 116 | 123-437 | 1105.2687 | 614.6469 | 277.4119 | 830.0048 | 339.383 | 2.148 | 0 | 0 | 0 | 275.2639 | 88.79 | 35.7869 | 0.20713 | 88.5829 | 35.5798 | 0 | 0 | 0 | 0 | 0.20713 | 531.7693 | 227.3702 | 25.0052 | 506.7642 | 202.3651 | 0 | 0 | 0 | 0 | 25.0052 | 484.7094 | 351.4898 | 252.1996 | 234.6578 | 101.4382 | 2.148 | 0 | 0 | 0 | 250.0516 | 0.0006432 | 0.0002784 | 7e-06 | 0 | 0 | 0 | 0.000383 | 5000000 | scaled
123-557 | 44.9854 | 11.1687 | 0 | 33.8167 | 24.83% | 0% | 75.17% | 8.049 | 11.0573 | 0.60964 | 4.2613 | 3.1781 | 0.60964 | 7.2696 | 3.1781 | 123 |  | 117 | 123-557 | 44.9854 | 36.9364 | 33.9281 | 11.1687 | 3.1197 | 0.11142 | 0 | 0 | 0 | 33.8167 | 0.63509 | 0.025446 | 0.025446 | 0.60964 | 0 | 0 | 0 | 0 | 0 | 0.025446 | 6.25 | 3.0719 | 3.0719 | 3.1781 | 0 | 0 | 0 | 0 | 0 | 3.0719 | 38.1003 | 33.839 | 30.8307 | 7.381 | 3.1197 | 0.11142 | 0 | 0 | 0 | 30.7193 | 1.28e-05 | 5.6e-06 | 2e-07 | 0 | 0 | 0 | 4.86e-05 | 5000000 | scaled
1233-259R | 1558538.9319 | 1536152.4329 | 18918.3414 | 3468.1576 | 98.56% | 1.214% | 0.2225% | 656700.4159 | 1530872.2485 | 40455.1407 | 10112.0441 | 606133.2312 | 93572.5277 | 21408.1786 | 1415891.5422 | 1233 |  | 118 | 1233-259R | 1558538.9319 | 901838.516 | 27666.6835 | 1536152.4329 | 887713.4479 | 22497.1824 | 18918.3414 | 10656.9105 | 1701.3435 | 3468.1576 | 94945.2523 | 54490.1116 | 1372.7246 | 94857.7791 | 54439.6974 | 1362.483 | 84.8635 | 47.8045 | 7.6318 | 2.6097 | 1437524.079 | 831390.8478 | 21632.5368 | 1434036.7431 | 829288.8142 | 21032.2005 | 3172.2861 | 1786.9838 | 285.2865 | 315.0498 | 26069.6007 | 15957.5566 | 4661.4221 | 7257.9107 | 3984.9363 | 102.4989 | 15661.1919 | 8822.1222 | 1408.4251 | 3150.4981 | 0.016925 | 0.0091542 | 0.0002322 | 0.10568 | 0.060051 | 0.010568 | 0.004885 | 5000000 | scaled
1233-264F | 833.1206 | 0 | 833.1206 | 0 | 0% | 100% | 0% | 40.3723 | 83.975 | 0.52376 | 31.615 | 8.2335 | 1.0894 | 65.7597 | 17.1258 | 1233 |  | 119 | 1233-264F | 833.1206 | 792.7482 | 749.1455 | 0 | 0 | 0 | 833.1206 | 792.7482 | 749.1455 | 0 | 10.8082 | 10.2845 | 9.7188 | 0 | 0 | 0 | 10.8082 | 10.2845 | 9.7188 | 0 | 169.9064 | 161.6729 | 152.7806 | 0 | 0 | 0 | 169.9064 | 161.6729 | 152.7806 | 0 | 652.4059 | 620.7908 | 586.6461 | 0 | 0 | 0 | 652.4059 | 620.7908 | 586.6461 | 0 | 0 | 0 | 0 | 0.10565 | 0.10565 | 0.10565 | 0 | 5000000 | scaled
1233-585R | 3561958.681 | 3505652.5681 | 51908.639 | 4397.4739 | 98.42% | 1.457% | 0.1235% | 1632190.6895 | 3512271.4634 | 95714.9827 | 20930.0506 | 1515545.6563 | 205049.3828 | 43451.4253 | 3263770.6552 | 1233 |  | 120 | 1233-585R | 3561958.681 | 1929767.9915 | 49687.2176 | 3505652.5681 | 1896136.2169 | 40623.4212 | 51908.639 | 29234.3007 | 4666.3225 | 4397.4739 | 207515.1971 | 111800.2144 | 2465.8143 | 207445.7084 | 111759.6339 | 2456.5561 | 66.1797 | 37.2716 | 5.9492 | 3.309 | 3302783.1409 | 1787237.4846 | 39012.4856 | 3297308.7926 | 1783979.9064 | 38156.8103 | 5074.8787 | 2858.1087 | 456.2058 | 399.4695 | 51660.343 | 30730.2924 | 8208.9177 | 898.0671 | 396.6766 | 10.0548 | 46767.5805 | 26338.9204 | 4204.1675 | 3994.6954 | 0.018499 | 0.0094252 | 0.0002396 | 0.10516 | 0.059743 | 0.010516 | 0.0062246 | 5000000 | scaled
1233-587R | 2983729.0544 | 2921127.9574 | 57541.4404 | 5059.6565 | 97.9% | 1.929% | 0.1696% | 1486962.9738 | 2932592.4278 | 87032.799 | 23874.3151 | 1376055.8597 | 171258.345 | 49546.6058 | 2711787.4769 | 1233 |  | 121 | 1233-587R | 2983729.0544 | 1496766.0806 | 51136.6266 | 2921127.9574 | 1459285.7789 | 40904.7168 | 57541.4404 | 32420.6451 | 5172.2532 | 5059.6565 | 173654.6151 | 86621.816 | 2396.2701 | 173580.4848 | 86578.3866 | 2386.1417 | 70.3231 | 39.6222 | 6.3212 | 3.8072 | 2751241.9928 | 1375186.1332 | 39454.5159 | 2745156.4999 | 1371556.7194 | 38489.1981 | 5625.8703 | 3169.7911 | 505.6951 | 459.6227 | 58832.4465 | 34958.1314 | 9285.8406 | 2390.9727 | 1150.6729 | 29.377 | 51845.2471 | 29211.2319 | 4660.2369 | 4596.2266 | 0.022854 | 0.011499 | 0.0002922 | 0.1049 | 0.059623 | 0.01049 | 0.0071282 | 5000000 | scaled
1233-589R | 1386490.5084 | 1371477.111 | 13027.2956 | 1986.1018 | 98.92% | 0.9396% | 0.1432% | 590833.6902 | 1361306.2516 | 32691.6765 | 4885.215 | 553256.7986 | 75678.4531 | 10176.8913 | 1275450.9073 | 1233 |  | 122 | 1233-589R | 1386490.5084 | 795656.8182 | 25184.2568 | 1371477.111 | 786335.2717 | 22027.2748 | 13027.2956 | 7335.4447 | 1170.8802 | 1986.1018 | 76889.2136 | 44197.537 | 1210.7605 | 76853.8806 | 44176.9887 | 1206.2247 | 33.8385 | 19.0539 | 3.0414 | 1.4945 | 1296627.4816 | 743370.683 | 21176.5744 | 1294476.9032 | 742080.9014 | 20819.0796 | 1970.1596 | 1109.3628 | 177.076 | 180.4188 | 12973.8132 | 8088.5982 | 2796.9219 | 146.3272 | 77.3816 | 1.9706 | 11023.2975 | 6207.0281 | 990.7629 | 1804.1885 | 0.0098092 | 0.0055462 | 0.000141 | 0.10495 | 0.059617 | 0.010495 | 0.002747 | 5000000 | scaled
1233-591R | 4300183.7991 | 4242541.5206 | 52712.8052 | 4929.4733 | 98.66% | 1.226% | 0.1146% | 1912829.2872 | 4246309.2074 | 118608.8261 | 20802.9587 | 1773417.5025 | 262140.2955 | 43338.0822 | 3940830.8297 | 1233 |  | 123 | 1233-591R | 4300183.7991 | 2387354.5119 | 53874.5917 | 4242541.5206 | 2352742.3776 | 44207.5842 | 52712.8052 | 29682.661 | 4737.5342 | 4929.4733 | 265086.2099 | 146477.3838 | 2945.9144 | 264996.8357 | 146425.4365 | 2934.506 | 85.6649 | 48.238 | 7.6991 | 3.7093 | 3983035.5388 | 2209618.0363 | 42204.709 | 3977144.9967 | 2206105.4213 | 41267.7486 | 5442.7453 | 3064.8182 | 489.1637 | 447.7967 | 52062.0505 | 31259.0918 | 8723.9683 | 399.6882 | 211.5197 | 5.3296 | 47184.3949 | 26569.6047 | 4240.6714 | 4477.9673 | 0.019856 | 0.010425 | 0.0002682 | 0.10462 | 0.059422 | 0.010462 | 0.0069414 | 5000000 | scaled
1233-617F | 1629.6715 | 0 | 1629.6715 | 0 | 0% | 100% | 0% | 79.1697 | 164.8619 | 0.051995 | 62.7703 | 16.3473 | 0.10827 | 130.7121 | 34.0414 | 1233 |  | 124 | 1233-617F | 1629.6715 | 1550.5018 | 1464.8096 | 0 | 0 | 0 | 1629.6715 | 1550.5018 | 1464.8096 | 0 | 1.0703 | 1.0183 | 0.96202 | 0 | 0 | 0 | 1.0703 | 1.0183 | 0.96202 | 0 | 336.5021 | 320.1548 | 302.4607 | 0 | 0 | 0 | 336.5021 | 320.1548 | 302.4607 | 0 | 1292.0991 | 1229.3287 | 1161.3869 | 0 | 0 | 0 | 1292.0991 | 1229.3287 | 1161.3869 | 0 | 0 | 0 | 0 | 0.10458 | 0.10458 | 0.10458 | 0 | 5000000 | scaled
124-206R | 5028.946 | 2626.9384 | 0 | 2402.0076 | 52.24% | 0% | 47.76% | 1165.5664 | 2591.3776 | 12.5553 | 1087.3164 | 65.6947 | 26.1051 | 2428.4959 | 136.7766 | 124 |  | 125 | 124-206R | 5028.946 | 3863.3796 | 2437.5684 | 2626.9384 | 1461.372 | 35.5608 | 0 | 0 | 0 | 2402.0076 | 28.041 | 15.4857 | 1.9359 | 26.2336 | 13.6783 | 0.12849 | 0 | 0 | 0 | 1.8074 | 355.6919 | 289.9972 | 218.9154 | 137.4919 | 71.7972 | 0.71536 | 0 | 0 | 0 | 218.2 | 4645.213 | 3557.8966 | 2216.7171 | 2463.2129 | 1375.8965 | 34.7169 | 0 | 0 | 0 | 2182.0001 | 0.0062754 | 0.0032118 | 8.18e-05 | 0 | 0 | 0 | 0.0033654 | 5000000 | scaled
124-258R | 1249.8654 | 967.659 | 0 | 282.2064 | 77.42% | 0% | 22.58% | 489.6706 | 955.5409 | 3.823 | 466.0626 | 19.785 | 8.3784 | 903.7856 | 43.377 | 124 |  | 126 | 124-258R | 1249.8654 | 760.1948 | 294.3245 | 967.659 | 477.9884 | 12.118 | 0 | 0 | 0 | 282.2064 | 8.6601 | 4.837 | 0.28172 | 8.4477 | 4.6247 | 0.069366 | 0 | 0 | 0 | 0.21235 | 69.3812 | 49.5962 | 26.0042 | 43.7454 | 23.9604 | 0.3684 | 0 | 0 | 0 | 25.6358 | 1171.8241 | 705.7616 | 268.0385 | 915.4659 | 449.4033 | 11.6803 | 0 | 0 | 0 | 256.3583 | 0.0009552 | 0.0004694 | 1.22e-05 | 0 | 0 | 0 | 0.000412 | 5000000 | scaled
1242-1079R | 411541.4092 | 410114.2946 | 0 | 1427.1145 | 99.65% | 0% | 0.3468% | 94493.7341 | 399654.4625 | 32846.2356 | 401.4307 | 61246.0678 | 139043.0862 | 1648.4256 | 258962.9507 | 1242 |  | 127 | 1242-1079R | 411541.4092 | 317047.675 | 11886.9467 | 410114.2946 | 315620.5605 | 10459.8321 | 0 | 0 | 0 | 1427.1145 | 142672.0969 | 109825.8613 | 3629.0108 | 142671.023 | 109824.7875 | 3627.9369 | 0 | 0 | 0 | 1.0739 | 265891.0993 | 204645.0314 | 6928.1486 | 265761.4592 | 204515.3914 | 6798.5085 | 0 | 0 | 0 | 129.6401 | 2978.213 | 2576.7823 | 1329.7873 | 1681.8124 | 1280.3817 | 33.3867 | 0 | 0 | 0 | 1296.4006 | 0.0047078 | 0.0035718 | 9.1e-05 | 0 | 0 | 0 | 0.0020238 | 5000000 | scaled
1242-1084 | 456193.1498 | 455150.6916 | 0 | 1042.4581 | 99.77% | 0% | 0.2285% | 201745.7558 | 447321.9151 | 33486.8364 | 16.8421 | 168242.0772 | 74029.5581 | 39.5525 | 373252.8045 | 1242 |  | 128 | 1242-1084 | 456193.1498 | 254447.394 | 8871.2346 | 455150.6916 | 253404.9359 | 7828.7765 | 0 | 0 | 0 | 1042.4581 | 75323.3656 | 41836.5292 | 1293.8076 | 75322.5812 | 41835.7448 | 1293.0231 | 0 | 0 | 0 | 0.78442 | 379882.66 | 211640.5828 | 6629.8555 | 379787.9624 | 211545.8852 | 6535.1579 | 0 | 0 | 0 | 94.6976 | 987.1241 | 970.282 | 947.5716 | 40.148 | 23.3059 | 0.59549 | 0 | 0 | 0 | 946.9761 | 0.0044936 | 0.0025438 | 6.48e-05 | 0 | 0 | 0 | 0.0015024 | 5000000 | scaled
1242-127AE | 2458.9495 | 2425.0046 | 0 | 33.9449 | 98.62% | 0% | 1.38% | 847.75 | 2425.0046 | 61.6753 | 0 | 786.0747 | 176.0034 | 0 | 2249.0013 | 1242 |  | 129 | 1242-127AE | 2458.9495 | 1611.1995 | 33.9449 | 2425.0046 | 1577.2546 | 0 | 0 | 0 | 0 | 33.9449 | 176.0289 | 114.3536 | 0.025542 | 176.0034 | 114.328 | 0 | 0 | 0 | 0 | 0.025542 | 2252.0848 | 1466.0101 | 3.0836 | 2249.0013 | 1462.9266 | 0 | 0 | 0 | 0 | 3.0836 | 30.8358 | 30.8358 | 30.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8358 | 0.0001304 | 5.64e-05 | 1.4e-06 | 0 | 0 | 0 | 4.82e-05 | 5000000 | scaled
1243-156F | 583.7849 | 0 | 583.7849 | 0 | 0% | 100% | 0% | 40.0582 | 83.508 | 0.026308 | 31.7605 | 8.2714 | 0.054844 | 66.21 | 17.2431 | 1243 |  | 130 | 1243-156F | 583.7849 | 543.7266 | 500.2769 | 0 | 0 | 0 | 583.7849 | 543.7266 | 500.2769 | 0 | 0.3834 | 0.3571 | 0.32856 | 0 | 0 | 0 | 0.3834 | 0.3571 | 0.32856 | 0 | 120.5426 | 112.2712 | 103.2995 | 0 | 0 | 0 | 120.5426 | 112.2712 | 103.2995 | 0 | 462.8589 | 431.0983 | 396.6488 | 0 | 0 | 0 | 462.8589 | 431.0983 | 396.6488 | 0 | 0 | 0 | 0 | 0.071432 | 0.071432 | 0.071432 | 0 | 5000000 | scaled
1243-158F | 1166.1103 | 0 | 1166.1103 | 0 | 0% | 100% | 0% | 80.0758 | 166.9655 | 0.05259 | 63.4888 | 16.5344 | 0.10966 | 132.3801 | 34.4758 | 1243 |  | 131 | 1243-158F | 1166.1103 | 1086.0345 | 999.1448 | 0 | 0 | 0 | 1166.1103 | 1086.0345 | 999.1448 | 0 | 0.76585 | 0.71326 | 0.65619 | 0 | 0 | 0 | 0.76585 | 0.71326 | 0.65619 | 0 | 240.7839 | 224.2494 | 206.3081 | 0 | 0 | 0 | 240.7839 | 224.2494 | 206.3081 | 0 | 924.5606 | 861.0718 | 792.1805 | 0 | 0 | 0 | 924.5606 | 861.0718 | 792.1805 | 0 | 0 | 0 | 0 | 0.071331 | 0.071331 | 0.071331 | 0 | 5000000 | scaled
1243-319R | 1178043.0426 | 1170364.668 | 6119.3499 | 1559.0247 | 99.35% | 0.5195% | 0.1323% | 518742.5605 | 1159643.8163 | 26461.7183 | 2311.2357 | 489969.6065 | 59381.5245 | 4800.4735 | 1095461.8184 | 1243 |  | 132 | 1243-319R | 1178043.0426 | 659300.4821 | 18399.2263 | 1170364.668 | 654314.3615 | 16315.8359 | 6119.3499 | 3427.0958 | 524.3656 | 1559.0247 | 60211.4173 | 33749.699 | 829.8928 | 60173.518 | 33727.9577 | 825.5726 | 36.7262 | 20.5682 | 3.1471 | 1.1731 | 1111177.5196 | 621207.913 | 15715.7012 | 1110033.5741 | 620504.9469 | 15488.1896 | 1002.3226 | 561.3432 | 85.8888 | 141.6229 | 6654.1058 | 4342.87 | 1853.6323 | 157.5759 | 81.4569 | 2.0738 | 5080.3011 | 2845.1843 | 435.3298 | 1416.2287 | 0.0075476 | 0.0039476 | 9.98e-05 | 0.071271 | 0.040386 | 0.007127 | 0.0022328 | 5000000 | scaled
1243-38R | 158251.3723 | 157423.4341 | 582.5986 | 245.3396 | 99.48% | 0.3681% | 0.155% | 89590.0353 | 157760.5965 | 4824.9063 | 204.3947 | 84560.7343 | 8464.146 | 424.6671 | 148871.7833 | 1243 |  | 133 | 1243-38R | 158251.3723 | 68661.3371 | 490.7759 | 157423.4341 | 68089.5252 | 195.5179 | 582.5986 | 326.4723 | 49.9184 | 245.3396 | 8477.1296 | 3652.2233 | 12.9835 | 8476.5623 | 3651.8243 | 12.7661 | 0.38262 | 0.21441 | 0.032784 | 0.18461 | 149087.1044 | 64526.37 | 215.3211 | 148944.5199 | 64436.6717 | 182.7269 | 120.2977 | 67.4115 | 10.3074 | 22.2868 | 687.1384 | 482.7437 | 262.4712 | 2.3519 | 1.0292 | 0.02486 | 461.9183 | 258.8463 | 39.5782 | 222.8682 | 0.0009756 | 0.000427 | 1.1e-05 | 0.071274 | 0.040414 | 0.0071274 | 0.0003408 | 5000000 | scaled
1243-45R | 1878382.5676 | 1860483.1499 | 15562.993 | 2336.4246 | 99.05% | 0.8285% | 0.1244% | 629861.5629 | 1834748.5604 | 32978.3565 | 5662.9889 | 591220.2175 | 97301.5541 | 12073.9338 | 1725373.0725 | 1243 |  | 134 | 1243-45R | 1878382.5676 | 1248521.0047 | 43634.0072 | 1860483.1499 | 1237468.7941 | 39964.0546 | 15562.993 | 8715.786 | 1333.528 | 2336.4246 | 99441.9496 | 66463.5931 | 2140.3955 | 99346.8887 | 66409.5824 | 2130.6427 | 93.3028 | 52.2526 | 7.9947 | 1.7581 | 1763663.268 | 1172443.0505 | 38290.1956 | 1760445.4387 | 1170547.5809 | 37820.4169 | 3005.5869 | 1683.2271 | 257.5362 | 212.2424 | 15277.3499 | 9614.3611 | 3203.4161 | 690.8225 | 511.6307 | 12.995 | 12464.1033 | 6980.3062 | 1067.9971 | 2122.4241 | 0.013051 | 0.0089902 | 0.000229 | 0.071233 | 0.040363 | 0.0071234 | 0.0033314 | 5000000 | scaled
1250-27R | 6418508.1687 | 5971509.076 | 443953.3672 | 3045.7255 | 93.04% | 6.917% | 0.04745% | 1647436.1464 | 6237945.5636 | 134062.373 | 186509.0563 | 1326864.7172 | 535586.0742 | 401295.7901 | 5301063.6992 | 1250 |  | 135 | 1250-27R | 6418508.1687 | 4771072.0223 | 180562.6052 | 5971509.076 | 4519499.6204 | 139084.8573 | 443953.3672 | 248526.6764 | 38432.0224 | 3045.7255 | 548235.9995 | 414173.6265 | 12649.9253 | 547619.4182 | 413827.4533 | 12594.4558 | 614.2894 | 343.8814 | 53.1776 | 2.2918 | 5430488.3486 | 4103623.6314 | 129424.6494 | 5392760.9102 | 4082381.8853 | 125905.9471 | 37450.7626 | 20965.0703 | 3242.0264 | 276.6758 | 439783.8207 | 253274.7644 | 38488.0306 | 31128.7476 | 23290.2818 | 584.4543 | 405888.3152 | 227217.7247 | 35136.8184 | 2766.7579 | 0.016583 | 0.010993 | 0.000279 | 0.076513 | 0.043331 | 0.0076512 | 0.004274 | 5000000 | scaled
1250-671R | 6815427.7597 | 6443060.7288 | 370799.4193 | 1567.6116 | 94.54% | 5.441% | 0.023% | 2913028.8231 | 6712281.7884 | 178011.3711 | 154062.5629 | 2580954.8891 | 413818.2924 | 319584.1675 | 5978879.3285 | 1250 |  | 136 | 1250-671R | 6815427.7597 | 3902398.9366 | 103145.9713 | 6443060.7288 | 3693148.1864 | 69452.5282 | 370799.4193 | 207683.1386 | 32125.8314 | 1567.6116 | 418470.8076 | 240459.4365 | 4652.5151 | 417981.4332 | 240184.8211 | 4609.0387 | 488.1948 | 273.4358 | 42.2969 | 1.1796 | 6046411.9735 | 3465457.0844 | 67532.645 | 6015425.6855 | 3448039.1559 | 64717.947 | 30843.8851 | 17275.5256 | 2672.295 | 142.4029 | 350544.9786 | 196482.4158 | 30960.8111 | 9653.6101 | 4924.2095 | 125.5425 | 339467.3394 | 190134.1772 | 29411.2395 | 1424.0291 | 0.01265 | 0.0076202 | 0.000193 | 0.077213 | 0.043749 | 0.0077214 | 0.002187 | 5000000 | scaled
1250-677R | 11748908.7781 | 11662207.457 | 80325.5814 | 6375.7396 | 99.26% | 0.6837% | 0.05427% | 4961332.9583 | 11552299.57 | 278658.5046 | 32604.2057 | 4650070.2481 | 648785.395 | 68546.7372 | 10834967.4378 | 1250 |  | 137 | 1250-677R | 11748908.7781 | 6787575.8197 | 196609.208 | 11662207.457 | 6736212.3376 | 183267.781 | 80325.5814 | 44987.7426 | 6965.6875 | 6375.7396 | 659186.9756 | 380528.471 | 10401.5805 | 659004.9399 | 380424.4081 | 10381.4132 | 177.2382 | 99.2653 | 15.3698 | 4.7975 | 11009091.9369 | 6359021.6888 | 174124.4991 | 11000353.8044 | 6353872.9467 | 172837.7928 | 8158.9559 | 4569.5655 | 707.5297 | 579.1766 | 80629.8656 | 48025.66 | 12083.1284 | 2848.7128 | 1914.9827 | 48.575 | 71989.3873 | 40318.9117 | 6242.788 | 5791.7655 | 0.029543 | 0.016689 | 0.0004254 | 0.078076 | 0.044233 | 0.0078076 | 0.0089662 | 5000000 | scaled
1250-8R | 3684980.1605 | 3616964.705 | 65291.9982 | 2723.4573 | 98.15% | 1.772% | 0.07391% | 1477547.4677 | 3588711.5962 | 75844.0193 | 26826.9363 | 1374876.5121 | 183571.0902 | 56431.6426 | 3348708.8634 | 1250 |  | 138 | 1250-8R | 3684980.1605 | 2207432.6929 | 96268.5643 | 3616964.705 | 2168139.7597 | 87883.0387 | 65291.9982 | 36569.4759 | 5662.0683 | 2723.4573 | 188035.7643 | 112191.745 | 4464.6741 | 187906.5625 | 112118.4787 | 4451.5982 | 127.1524 | 71.217 | 11.0266 | 2.0493 | 3432879.3724 | 2058002.8603 | 84170.509 | 3426468.3225 | 2054303.2537 | 83388.6017 | 6163.6491 | 3452.2058 | 534.5066 | 247.4007 | 64065.0239 | 37238.0876 | 7633.3813 | 2589.82 | 1718.0272 | 42.8388 | 59001.1967 | 33046.0531 | 5116.5352 | 2474.0073 | 0.010354 | 0.0051374 | 0.0001304 | 0.078089 | 0.044247 | 0.0078088 | 0.003846 | 5000000 | scaled
1297-34F | 97116.8879 | 3562.5743 | 91815.1845 | 1739.1292 | 3.668% | 94.54% | 1.791% | 43126.2378 | 89204.2372 | 45.7261 | 39298.9463 | 3781.5654 | 95.3105 | 81226.7186 | 7882.2081 | 1297 |  | 139 | 1297-34F | 97116.8879 | 53990.6501 | 7912.6507 | 3562.5743 | 1542.4953 | 39.0704 | 91815.1845 | 50709.0256 | 6134.4512 | 1739.1292 | 103.4431 | 57.7169 | 8.1326 | 0 | 0 | 0 | 102.1344 | 56.4083 | 6.8239 | 1.3086 | 8604.5313 | 4822.9658 | 722.3232 | 0 | 0 | 0 | 8446.5476 | 4664.9821 | 564.3395 | 157.9837 | 88408.9136 | 49109.9673 | 7182.195 | 3562.5743 | 1542.4953 | 39.0704 | 83266.5025 | 45987.6351 | 5563.2878 | 1579.8369 | 0.0038892 | 0.001684 | 4.26e-05 | 0.0061944 | 0.0035196 | 0.0006194 | 0.0024492 | 5000000 | scaled
1297-35F | 50400.8685 | 1821.2403 | 47098.56 | 1481.0682 | 3.614% | 93.45% | 2.939% | 21777.4759 | 45743.4034 | 23.0558 | 19929.6558 | 1824.7643 | 48.0105 | 41895.5639 | 3799.829 | 1297 |  | 140 | 1297-35F | 50400.8685 | 28623.3927 | 4657.4651 | 1821.2403 | 1150.4081 | 29.6158 | 47098.56 | 25991.9164 | 3146.7811 | 1481.0682 | 52.5624 | 29.5066 | 4.5518 | 0 | 0 | 0 | 51.4479 | 28.3922 | 3.4374 | 1.1145 | 4206.4236 | 2381.6593 | 406.5946 | 0 | 0 | 0 | 4071.8824 | 2247.1181 | 272.0534 | 134.5412 | 46141.8826 | 26212.2267 | 4246.3187 | 1821.2403 | 1150.4081 | 29.6158 | 42975.2298 | 23716.4061 | 2871.2904 | 1345.4125 | 0.0033756 | 0.0019922 | 5.12e-05 | 0.0062094 | 0.0035254 | 0.000621 | 0.0021008 | 5000000 | scaled
1297-36F | 27690.0017 | 0 | 27690.0017 | 0 | 0% | 100% | 0% | 4424.7691 | 9198.5181 | 6.8725 | 3987.0464 | 430.8502 | 14.287 | 8288.5498 | 895.6813 | 1297 |  | 141 | 1297-36F | 27690.0017 | 23265.2327 | 18491.4836 | 0 | 0 | 0 | 27690.0017 | 23265.2327 | 18491.4836 | 0 | 43.0076 | 36.1351 | 28.7206 | 0 | 0 | 0 | 43.0076 | 36.1351 | 28.7206 | 0 | 2696.2405 | 2265.3904 | 1800.5592 | 0 | 0 | 0 | 2696.2405 | 2265.3904 | 1800.5592 | 0 | 24950.7536 | 20963.7072 | 16662.2038 | 0 | 0 | 0 | 24950.7536 | 20963.7072 | 16662.2038 | 0 | 0 | 0 | 0 | 0.0062154 | 0.0062154 | 0.0062154 | 0 | 5000000 | scaled
130-13F | 6063.8774 | 2931.4983 | 0 | 3132.3791 | 48.34% | 0% | 51.66% | 1648.1728 | 2898.3622 | 4.108 | 1622.75 | 21.3149 | 7.3647 | 2852.812 | 38.1855 | 130 |  | 142 | 130-13F | 6063.8774 | 4415.7046 | 3165.5152 | 2931.4983 | 1283.3254 | 33.1361 | 0 | 0 | 0 | 3132.3791 | 9.9053 | 5.7974 | 2.5407 | 7.5483 | 3.4403 | 0.18366 | 0 | 0 | 0 | 2.357 | 323.6758 | 302.3609 | 285.4903 | 39.1283 | 17.8135 | 0.94281 | 0 | 0 | 0 | 284.5475 | 5730.2963 | 4107.5463 | 2877.4843 | 2884.8216 | 1262.0716 | 32.0096 | 0 | 0 | 0 | 2845.4747 | 0.0093878 | 0.0041924 | 0.0001066 | 0 | 0 | 0 | 0.0044382 | 5000000 | scaled
130-14F | 1014.1504 | 415.5722 | 0 | 598.5782 | 40.98% | 0% | 59.02% | 245.4905 | 411.5239 | 5.0436 | 213.9982 | 26.4487 | 6.9165 | 368.1571 | 36.4503 | 130 |  | 143 | 130-14F | 1014.1504 | 768.66 | 602.6266 | 415.5722 | 170.0818 | 4.0484 | 0 | 0 | 0 | 598.5782 | 7.3669 | 2.3233 | 0.45041 | 6.9165 | 1.8729 | 0 | 0 | 0 | 0 | 0.45041 | 90.8255 | 64.3768 | 54.3753 | 36.4503 | 10.0015 | 0 | 0 | 0 | 0 | 54.3753 | 915.958 | 701.9599 | 547.8009 | 372.2055 | 158.2074 | 4.0484 | 0 | 0 | 0 | 543.7525 | 0.0016652 | 0.000721 | 1.84e-05 | 0 | 0 | 0 | 0.0008488 | 5000000 | scaled
130-692R | 38855.0688 | 30933.9536 | 0 | 7921.1152 | 79.61% | 0% | 20.39% | 15230.7132 | 30543.5507 | 83.0522 | 14809.5326 | 338.1284 | 157.7908 | 29742.9312 | 642.8287 | 130 |  | 144 | 130-692R | 38855.0688 | 23624.3556 | 8311.5181 | 30933.9536 | 15703.2404 | 390.4029 | 0 | 0 | 0 | 7921.1152 | 164.2524 | 81.2002 | 6.4615 | 158.292 | 75.2398 | 0.50116 | 0 | 0 | 0 | 5.9604 | 1364.4474 | 1026.319 | 721.6187 | 644.8879 | 306.7595 | 2.0591 | 0 | 0 | 0 | 719.5595 | 37326.3691 | 22516.8365 | 7583.4379 | 30130.7738 | 15321.2412 | 387.8426 | 0 | 0 | 0 | 7195.5953 | 0.018522 | 0.0088726 | 0.0002246 | 0 | 0 | 0 | 0.011094 | 5000000 | scaled
137-34AE | 3188.4386 | 796.2811 | 0 | 2392.1575 | 24.97% | 0% | 75.03% | 451.5691 | 787.6384 | 0 | 451.5691 | 0 | 0 | 787.6384 | 0 | 137 |  | 145 | 137-34AE | 3188.4386 | 2736.8696 | 2400.8003 | 796.2811 | 344.712 | 8.6428 | 0 | 0 | 0 | 2392.1575 | 1.8 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 217.3052 | 217.3052 | 217.3052 | 0 | 0 | 0 | 0 | 0 | 0 | 217.3052 | 2969.3334 | 2517.7643 | 2181.695 | 796.2811 | 344.712 | 8.6428 | 0 | 0 | 0 | 2173.0523 | 0.0066508 | 0.0028798 | 7.3e-05 | 0 | 0 | 0 | 0.0033244 | 5000000 | scaled
137-767F | 10680.4291 | 8724.194 | 0 | 1956.2351 | 81.68% | 0% | 18.32% | 4360.5785 | 8587.3635 | 304.8526 | 1854.9631 | 2200.7629 | 613.5368 | 3519.5024 | 4454.3244 | 137 |  | 146 | 137-767F | 10680.4291 | 6319.8506 | 2093.0656 | 8724.194 | 4363.6155 | 136.8305 | 0 | 0 | 0 | 1956.2351 | 625.476 | 320.6234 | 11.9392 | 624.004 | 319.1514 | 10.4672 | 0 | 0 | 0 | 1.472 | 4714.6096 | 2513.8467 | 260.2852 | 4536.9038 | 2336.141 | 82.5794 | 0 | 0 | 0 | 177.7057 | 5340.3436 | 3485.3805 | 1820.8412 | 3563.2862 | 1708.3231 | 43.7838 | 0 | 0 | 0 | 1777.0574 | 0.00434 | 0.0019186 | 4.86e-05 | 0 | 0 | 0 | 0.0027492 | 5000000 | scaled
138-358R | 38845.5543 | 33572.6718 | 0 | 5272.8825 | 86.43% | 0% | 13.57% | 17208.3752 | 33151.8429 | 50.9352 | 16975.0414 | 182.3985 | 105.4266 | 32668.8806 | 377.5357 | 138 |  | 147 | 138-358R | 38845.5543 | 21637.1792 | 5693.7114 | 33572.6718 | 16364.2966 | 420.8288 | 0 | 0 | 0 | 5272.8825 | 111.4296 | 60.4944 | 6.003 | 107.462 | 56.5267 | 2.0354 | 0 | 0 | 0 | 3.9677 | 863.8133 | 681.4148 | 486.2775 | 384.821 | 202.4226 | 7.2853 | 0 | 0 | 0 | 478.9923 | 37870.3114 | 20895.27 | 5201.4308 | 33080.3888 | 16105.3473 | 411.5082 | 0 | 0 | 0 | 4789.9226 | 0.015257 | 0.0071078 | 0.0001816 | 0 | 0 | 0 | 0.0073954 | 5000000 | scaled
138-360F | 1398.7823 | 568.6799 | 0 | 830.1024 | 40.66% | 0% | 59.34% | 298.1319 | 561.5566 | 0 | 298.1319 | 0 | 0 | 561.5566 | 0 | 138 |  | 148 | 138-360F | 1398.7823 | 1100.6503 | 837.2257 | 568.6799 | 270.5479 | 7.1233 | 0 | 0 | 0 | 830.1024 | 0.62463 | 0.62463 | 0.62463 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62463 | 75.4071 | 75.4071 | 75.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4071 | 1322.7506 | 1024.6186 | 761.194 | 568.6799 | 270.5479 | 7.1233 | 0 | 0 | 0 | 754.0707 | 0.0012432 | 0.0006462 | 1.68e-05 | 0 | 0 | 0 | 0.0011736 | 5000000 | scaled
138-366 | 162.9995 | 12.1063 | 0 | 150.8932 | 7.427% | 0% | 92.57% | 6.8427 | 11.9309 | 0 | 6.8427 | 0 | 0 | 11.9309 | 0 | 138 |  | 149 | 138-366 | 162.9995 | 156.1568 | 151.0686 | 12.1063 | 5.2636 | 0.17545 | 0 | 0 | 0 | 150.8932 | 0.11354 | 0.11354 | 0.11354 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11354 | 13.7072 | 13.7072 | 13.7072 | 0 | 0 | 0 | 0 | 0 | 0 | 13.7072 | 149.1787 | 142.336 | 137.2479 | 12.1063 | 5.2636 | 0.17545 | 0 | 0 | 0 | 137.0724 | 0.0001996 | 8.64e-05 | 2.4e-06 | 0 | 0 | 0 | 0.0002064 | 5000000 | scaled
139-243AE | 282.478 | 37.2281 | 0 | 245.2499 | 13.18% | 0% | 86.82% | 21.0782 | 36.825 | 0 | 21.0782 | 0 | 0 | 36.825 | 0 | 139 |  | 150 | 139-243AE | 282.478 | 261.3998 | 245.653 | 37.2281 | 16.1499 | 0.4031 | 0 | 0 | 0 | 245.2499 | 0.18454 | 0.18454 | 0.18454 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18454 | 22.2787 | 22.2787 | 22.2787 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2787 | 260.0148 | 238.9366 | 223.1898 | 37.2281 | 16.1499 | 0.4031 | 0 | 0 | 0 | 222.7867 | 0.0004384 | 0.00019 | 4.6e-06 | 0 | 0 | 0 | 0.0003426 | 5000000 | scaled
139-245AE | 5672.1786 | 2940.2479 | 0 | 2731.9308 | 51.84% | 0% | 48.16% | 1706.3203 | 2924.2516 | 81.5833 | 1259.2287 | 365.5083 | 133.5099 | 2194.9414 | 595.8002 | 139 |  | 151 | 139-245AE | 5672.1786 | 3965.8584 | 2747.9271 | 2940.2479 | 1233.9276 | 15.9963 | 0 | 0 | 0 | 2731.9308 | 135.5656 | 53.9823 | 2.0557 | 133.5099 | 51.9266 | 0 | 0 | 0 | 0 | 2.0557 | 843.9707 | 478.4624 | 248.1705 | 595.8002 | 230.292 | 0 | 0 | 0 | 0 | 248.1705 | 4692.6423 | 3433.4136 | 2497.7009 | 2210.9377 | 951.709 | 15.9963 | 0 | 0 | 0 | 2481.7046 | 0.00657 | 0.0028986 | 7.36e-05 | 0 | 0 | 0 | 0.0038812 | 5000000 | scaled
139-426F | 7505.4059 | 6400.1454 | 0 | 1105.2605 | 85.27% | 0% | 14.73% | 3629.0003 | 6330.4184 | 0 | 3629.0003 | 0 | 0 | 6330.4184 | 0 | 139 |  | 152 | 139-426F | 7505.4059 | 3876.4056 | 1174.9875 | 6400.1454 | 2771.1451 | 69.7271 | 0 | 0 | 0 | 1105.2605 | 0.83167 | 0.83167 | 0.83167 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83167 | 100.4026 | 100.4026 | 100.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4026 | 7404.1716 | 3775.1713 | 1073.7533 | 6400.1454 | 2771.1451 | 69.7271 | 0 | 0 | 0 | 1004.0262 | 0.0028464 | 0.0012478 | 3.14e-05 | 0 | 0 | 0 | 0.001586 | 5000000 | scaled
139-48 | 22125.2744 | 17506.5094 | 0 | 4618.765 | 79.12% | 0% | 20.88% | 9927.5643 | 17314.0536 | 6.6068 | 9887.0109 | 33.9466 | 11.7225 | 17242.1145 | 60.2165 | 139 |  | 153 | 139-48 | 22125.2744 | 12197.7102 | 4811.2208 | 17506.5094 | 7578.9451 | 192.4558 | 0 | 0 | 0 | 4618.765 | 15.2784 | 8.6716 | 3.5559 | 11.8029 | 5.1962 | 0.080402 | 0 | 0 | 0 | 3.4755 | 480.2048 | 446.2582 | 419.9882 | 60.633 | 26.6864 | 0.41646 | 0 | 0 | 0 | 419.5718 | 21629.7913 | 11742.7804 | 4387.6767 | 17434.0735 | 7547.0626 | 191.9589 | 0 | 0 | 0 | 4195.7178 | 0.014016 | 0.0060676 | 0.000154 | 0 | 0 | 0 | 0.0066318 | 5000000 | scaled
140-481R | 76551.9048 | 17009.6042 | 55396.8833 | 4145.4173 | 22.22% | 72.37% | 5.415% | 34744.9438 | 68465.7169 | 508.0811 | 30088.1608 | 4148.7019 | 779.6787 | 60088.7033 | 7597.3348 | 140 |  | 154 | 140-481R | 76551.9048 | 41806.961 | 8086.188 | 17009.6042 | 7178.6405 | 240.4856 | 55396.8833 | 30482.9032 | 3700.2851 | 4145.4173 | 801.4849 | 293.4037 | 21.8061 | 731.7478 | 253.6271 | 14.2371 | 66.6178 | 36.6574 | 4.4498 | 3.1193 | 8386.0833 | 4237.3815 | 788.7485 | 2634.5914 | 903.185 | 53.1534 | 5374.9194 | 2957.6239 | 359.0226 | 376.5725 | 67364.3366 | 37276.1758 | 7275.6333 | 13643.265 | 6021.8284 | 173.0951 | 49955.3461 | 27488.6219 | 3336.8127 | 3765.7255 | 0.0099122 | 0.004414 | 0.0001114 | 0.00619 | 0.003505 | 0.000619 | 0.0059086 | 5000000 | scaled
140-496 | 76075.8832 | 7768.52 | 66074.6137 | 2232.7496 | 10.21% | 86.85% | 2.935% | 33772.9737 | 69321.794 | 195.1135 | 30176.2466 | 3401.6136 | 343.7838 | 62263.4122 | 6714.598 | 140 |  | 155 | 140-496 | 76075.8832 | 42302.9095 | 6754.0893 | 7768.52 | 3662.8806 | 104.5034 | 66074.6137 | 36407.2794 | 4416.8363 | 2232.7496 | 355.4709 | 160.3574 | 11.6871 | 268.6941 | 111.7888 | 4.3186 | 85.0967 | 46.8885 | 5.6884 | 1.6801 | 7319.4647 | 3917.851 | 604.8667 | 1451.9696 | 593.7787 | 23.3806 | 5664.6706 | 3121.2478 | 378.6617 | 202.8245 | 68400.9477 | 38224.7011 | 6137.5355 | 6047.8563 | 2957.313 | 76.8042 | 60324.8464 | 33239.143 | 4032.4863 | 2028.245 | 0.0052262 | 0.0024944 | 6.26e-05 | 0.0061644 | 0.0034946 | 0.0006164 | 0.0031492 | 5000000 | scaled
1406-19F | 15067.3711 | 12634.8396 | 0 | 2432.5315 | 83.86% | 0% | 16.14% | 4630.301 | 12429.563 | 232.6411 | 3097.2434 | 1300.4165 | 597.6624 | 8416.0993 | 3415.8013 | 1406 |  | 156 | 1406-19F | 15067.3711 | 10437.0701 | 2637.8082 | 12634.8396 | 8004.5387 | 205.2767 | 0 | 0 | 0 | 2432.5315 | 610.8062 | 378.1651 | 13.1438 | 608.9758 | 376.3347 | 11.3134 | 0 | 0 | 0 | 1.8304 | 3702.0485 | 2401.632 | 286.2472 | 3481.0757 | 2180.6592 | 65.2744 | 0 | 0 | 0 | 220.9728 | 10754.5164 | 7657.273 | 2338.4171 | 8544.7881 | 5447.5447 | 128.6889 | 0 | 0 | 0 | 2209.7282 | 0.010114 | 0.0045906 | 0.0001162 | 0 | 0 | 0 | 0.0034554 | 5000000 | scaled
1406-436 | 817.1931 | 420.1888 | 0 | 397.0044 | 51.42% | 0% | 48.58% | 229.625 | 415.7595 | 2.0179 | 217.1814 | 10.4257 | 3.3418 | 395.0799 | 17.3378 | 1406 |  | 157 | 1406-436 | 817.1931 | 587.5681 | 401.4336 | 420.1888 | 190.5638 | 4.4293 | 0 | 0 | 0 | 397.0044 | 3.6405 | 1.6226 | 0.29873 | 3.3418 | 1.3239 | 0 | 0 | 0 | 0 | 0.29873 | 53.4019 | 42.9762 | 36.0641 | 17.3378 | 6.9121 | 0 | 0 | 0 | 0 | 36.0641 | 760.1507 | 542.9693 | 365.0708 | 399.5092 | 182.3278 | 4.4293 | 0 | 0 | 0 | 360.6415 | 0.0009526 | 0.0004508 | 1.14e-05 | 0 | 0 | 0 | 0.0005516 | 5000000 | scaled
141-194F | 23005.2092 | 0 | 23005.2092 | 0 | 0% | 100% | 0% | 3676.163 | 7641.1337 | 4.1739 | 3351.0628 | 320.9263 | 8.6758 | 6965.3926 | 667.0652 | 141 |  | 158 | 141-194F | 23005.2092 | 19329.0462 | 15364.0755 | 0 | 0 | 0 | 23005.2092 | 19329.0462 | 15364.0755 | 0 | 26.1203 | 21.9464 | 17.4445 | 0 | 0 | 0 | 26.1203 | 21.9464 | 17.4445 | 0 | 2008.3374 | 1687.4111 | 1341.2722 | 0 | 0 | 0 | 2008.3374 | 1687.4111 | 1341.2722 | 0 | 20970.7514 | 17619.6887 | 14005.3588 | 0 | 0 | 0 | 20970.7514 | 17619.6887 | 14005.3588 | 0 | 0 | 0 | 0 | 0.0061866 | 0.0061866 | 0.0061866 | 0 | 5000000 | scaled
141-195F | 1819.7015 | 0 | 1819.7015 | 0 | 0% | 100% | 0% | 290.8634 | 604.4285 | 0.3818 | 230.4622 | 60.0194 | 0.7934 | 478.9118 | 124.7233 | 141 |  | 159 | 141-195F | 1819.7015 | 1528.8381 | 1215.2731 | 0 | 0 | 0 | 1819.7015 | 1528.8381 | 1215.2731 | 0 | 2.3886 | 2.0068 | 1.5952 | 0 | 0 | 0 | 2.3886 | 2.0068 | 1.5952 | 0 | 375.4938 | 315.4744 | 250.7705 | 0 | 0 | 0 | 375.4938 | 315.4744 | 250.7705 | 0 | 1441.8191 | 1211.3569 | 962.9073 | 0 | 0 | 0 | 1441.8191 | 1211.3569 | 962.9073 | 0 | 0 | 0 | 0 | 0.0061828 | 0.0061828 | 0.0061828 | 0 | 5000000 | scaled
1418-31R | 2727.5199 | 2149.4253 | 0 | 578.0946 | 78.81% | 0% | 21.19% | 920.7709 | 2131.9017 | 59.8218 | 523.05 | 337.8991 | 116.6594 | 1372.2854 | 642.957 | 1418 |  | 160 | 1418-31R | 2727.5199 | 1806.749 | 595.6181 | 2149.4253 | 1228.6544 | 17.5236 | 0 | 0 | 0 | 578.0946 | 117.0944 | 57.2726 | 0.435 | 116.6594 | 56.8376 | 0 | 0 | 0 | 0 | 0.435 | 695.4715 | 357.5724 | 52.5145 | 642.957 | 305.0579 | 0 | 0 | 0 | 0 | 52.5145 | 1914.954 | 1391.904 | 542.6686 | 1389.8089 | 866.7589 | 17.5236 | 0 | 0 | 0 | 525.1451 | 0.0016394 | 0.0009606 | 2.44e-05 | 0 | 0 | 0 | 0.0008134 | 5000000 | scaled
1418-581R | 5069.196 | 3913.2935 | 0 | 1155.9025 | 77.2% | 0% | 22.8% | 2095.562 | 3884.8279 | 120.3585 | 1316.5409 | 658.6625 | 191.7202 | 2655.2244 | 1037.8833 | 1418 |  | 161 | 1418-581R | 5069.196 | 2973.634 | 1184.3681 | 3913.2935 | 1817.7315 | 28.4656 | 0 | 0 | 0 | 1155.9025 | 192.6112 | 72.2527 | 0.89106 | 191.7414 | 71.3829 | 0.021283 | 0 | 0 | 0 | 0.86978 | 1143.0029 | 484.3404 | 105.1196 | 1038 | 379.3374 | 0.11665 | 0 | 0 | 0 | 105.003 | 3733.5818 | 2417.0409 | 1078.3574 | 2683.5521 | 1367.0112 | 28.3277 | 0 | 0 | 0 | 1050.0297 | 0.0038918 | 0.0020364 | 5.16e-05 | 0 | 0 | 0 | 0.0016256 | 5000000 | scaled
142-33 | 118712.3932 | 24352.5802 | 87704.302 | 6655.511 | 20.51% | 73.88% | 5.606% | 52298.3424 | 105815.8479 | 681.6877 | 46234.8654 | 5381.7894 | 1333.8784 | 93510.2584 | 10971.711 | 142 |  | 162 | 142-33 | 118712.3932 | 66414.0508 | 12896.5453 | 24352.5802 | 11361.7131 | 372.4623 | 87704.302 | 48396.8267 | 5868.572 | 6655.511 | 1373.6099 | 691.9223 | 39.7315 | 1245.4281 | 618.9447 | 26.4815 | 123.1738 | 67.9695 | 8.2419 | 5.0081 | 12165.7213 | 6783.9319 | 1194.0102 | 4158.8609 | 2094.6341 | 94.1098 | 7402.2692 | 4084.7066 | 495.3092 | 604.5912 | 105173.062 | 58938.1966 | 11662.8035 | 18948.2913 | 8648.1343 | 251.871 | 80178.8589 | 44244.1506 | 5365.0208 | 6045.9117 | 0.021913 | 0.0094886 | 0.0002418 | 0.0061124 | 0.00347 | 0.0006112 | 0.0094136 | 5000000 | scaled
142-8R | 40889.2555 | 2617.5272 | 32982.0932 | 5289.6351 | 6.402% | 80.66% | 12.94% | 16413.6459 | 33374.0002 | 45.4355 | 14923.367 | 1444.8434 | 75.3226 | 30390.0394 | 2908.6383 | 142 |  | 163 | 142-8R | 40889.2555 | 24475.6096 | 7515.2553 | 2617.5272 | 982.3782 | 22.7971 | 32982.0932 | 18203.5963 | 2202.8231 | 5289.6351 | 82.1748 | 36.7392 | 6.8522 | 36.2798 | 9.6253 | 0.072519 | 41.9147 | 23.1337 | 2.7994 | 3.9803 | 3584.3193 | 2139.4759 | 675.681 | 187.1752 | 49.2048 | 0.36969 | 2916.63 | 1609.757 | 194.7972 | 480.5141 | 37222.7615 | 22299.3945 | 6832.7221 | 2394.0722 | 923.5481 | 22.3548 | 30023.5485 | 16570.7056 | 2005.2265 | 4805.1408 | 0.01424 | 0.0061672 | 0.0001556 | 0.0061308 | 0.0034814 | 0.000613 | 0.0073538 | 5000000 | scaled
143-147F | 25659.1321 | 355.8763 | 24946.3411 | 356.9148 | 1.387% | 97.22% | 1.391% | 11348.5913 | 23634.1691 | 30.8874 | 9916.2271 | 1401.4769 | 65.1718 | 20635.003 | 2933.9943 | 143 |  | 164 | 143-147F | 25659.1321 | 14310.5408 | 2024.963 | 355.8763 | 188.383 | 0.49823 | 24946.3411 | 13765.243 | 1667.55 | 356.9148 | 67.2083 | 36.321 | 2.0366 | 40.4907 | 21.4579 | 0 | 26.4491 | 14.5944 | 1.768 | 0.26857 | 3158.2054 | 1756.7286 | 224.2111 | 256.6476 | 141.1343 | 0 | 2869.1354 | 1583.1719 | 191.7887 | 32.4224 | 22433.7184 | 12517.4913 | 1798.7153 | 58.738 | 25.7908 | 0.49823 | 22050.7566 | 12167.4766 | 1473.9933 | 324.2238 | 0.0006432 | 0.0002784 | 7e-06 | 0.0061146 | 0.0034712 | 0.0006114 | 0.000494 | 5000000 | scaled
143-178F | 7656.553 | 2701.8618 | 4888.9469 | 65.7443 | 35.29% | 63.85% | 0.8587% | 3831.8974 | 7264.2304 | 143.7178 | 1741.2503 | 1946.9292 | 246.0671 | 3621.9644 | 3396.199 | 143 |  | 165 | 143-178F | 7656.553 | 3824.6557 | 392.3226 | 2701.8618 | 1063.3117 | 0 | 4888.9469 | 2695.5996 | 326.5783 | 65.7443 | 246.5037 | 102.7859 | 0.4366 | 240.6588 | 99.541 | 0 | 5.7954 | 3.1954 | 0.38713 | 0.04947 | 3469.0991 | 1522.1698 | 72.9001 | 2461.2029 | 963.7707 | 0 | 1001.9239 | 552.4269 | 66.9278 | 5.9723 | 3940.9503 | 2199.7 | 318.9859 | 0 | 0 | 0 | 3881.2277 | 2139.9774 | 259.2633 | 59.7226 | 0.000236 | 0.0001022 | 2.6e-06 | 0.0061318 | 0.0034786 | 0.0006132 | 9.48e-05 | 5000000 | scaled
143-179F | 1370.1837 | 878.8853 | 453.6622 | 37.6361 | 64.14% | 33.11% | 2.747% | 889.0643 | 1302.2419 | 59.6278 | 160.3369 | 669.0997 | 79.006 | 333.5389 | 889.697 | 143 |  | 166 | 143-179F | 1370.1837 | 481.1193 | 67.9417 | 878.8853 | 193.305 | 0.0022209 | 453.6622 | 250.1782 | 30.3034 | 37.6361 | 79.2687 | 19.6408 | 0.26263 | 75.7326 | 17.6781 | 0 | 3.5078 | 1.9344 | 0.23431 | 0.02832 | 899.3288 | 230.2291 | 9.6318 | 802.8988 | 175.518 | 0 | 93.0111 | 51.2922 | 6.2129 | 3.4189 | 391.5862 | 231.2494 | 58.0473 | 0.25396 | 0.10886 | 0.0022209 | 357.1434 | 196.9516 | 23.8562 | 34.1889 | 5.58e-05 | 2.42e-05 | 6e-07 | 0.006126 | 0.0034758 | 0.0006126 | 5.38e-05 | 5000000 | scaled
143-33 | 7551.611 | 52.5699 | 7390.3443 | 108.6969 | 0.6961% | 97.86% | 1.439% | 3357.5311 | 6948.8455 | 9.0875 | 2633.3273 | 715.1164 | 14.3072 | 5476.0991 | 1458.4392 | 143 |  | 167 | 143-33 | 7551.611 | 4194.0799 | 602.7655 | 52.5699 | 8.6186 | 0.10586 | 7390.3443 | 4076.7644 | 493.9628 | 108.6969 | 15.0036 | 5.9161 | 0.6964 | 5.7264 | 0.76185 | 0 | 9.1954 | 5.0725 | 0.61461 | 0.081791 | 1570.2491 | 855.1327 | 111.8099 | 35.2795 | 3.9642 | 0 | 1525.0955 | 841.2944 | 101.9358 | 9.8741 | 5966.3584 | 3333.0311 | 490.2593 | 11.564 | 3.8926 | 0.10586 | 5856.0534 | 3230.3976 | 391.4124 | 98.741 | 0.0002208 | 9.56e-05 | 2.6e-06 | 0.0061142 | 0.00347 | 0.0006114 | 0.0001492 | 5000000 | scaled
1434-10AE | 17676.2465 | 13956.9865 | 0 | 3719.2601 | 78.96% | 0% | 21.04% | 7276.533 | 13589.5991 | 824.4792 | 4065.8093 | 2386.2446 | 1505.5444 | 7751.3733 | 4332.6814 | 1434 |  | 168 | 1434-10AE | 17676.2465 | 10399.7135 | 4086.6474 | 13956.9865 | 6680.4534 | 367.3874 | 0 | 0 | 0 | 3719.2601 | 1568.6043 | 744.1251 | 63.0599 | 1565.8057 | 741.3265 | 60.2613 | 0 | 0 | 0 | 2.7986 | 4864.6562 | 2478.4115 | 531.9748 | 4526.796 | 2140.5514 | 194.1147 | 0 | 0 | 0 | 337.8601 | 11242.9861 | 7177.1768 | 3491.6128 | 7864.3848 | 3798.5755 | 113.0114 | 0 | 0 | 0 | 3378.6013 | 0.012302 | 0.005496 | 0.00014 | 0 | 0 | 0 | 0.0051986 | 5000000 | scaled
1434-11 | 1327.9687 | 1148.6474 | 0 | 179.3214 | 86.5% | 0% | 13.5% | 672.8278 | 1138.3037 | 27.683 | 497.2272 | 147.9176 | 45.6878 | 849.3341 | 243.2818 | 1434 |  | 169 | 1434-11 | 1327.9687 | 655.141 | 189.665 | 1148.6474 | 475.8196 | 10.3437 | 0 | 0 | 0 | 179.3214 | 46.0773 | 18.3943 | 0.38954 | 45.9424 | 18.2594 | 0.25461 | 0 | 0 | 0 | 0.13493 | 260.9249 | 113.0073 | 17.6431 | 244.6352 | 96.7177 | 1.3534 | 0 | 0 | 0 | 16.2897 | 1020.9665 | 523.7394 | 171.6324 | 858.0698 | 360.8426 | 8.7357 | 0 | 0 | 0 | 162.8968 | 0.0005008 | 0.0002168 | 5.8e-06 | 0 | 0 | 0 | 0.0002542 | 5000000 | scaled
1434-2 | 5895.7196 | 2593.4574 | 0 | 3302.2622 | 43.99% | 0% | 56.01% | 1468.5778 | 2564.6966 | 4.8521 | 1438.7513 | 24.9744 | 9.0082 | 2509.3103 | 46.378 | 1434 |  | 170 | 1434-2 | 5895.7196 | 4427.1419 | 3331.0231 | 2593.4574 | 1124.8797 | 28.7609 | 0 | 0 | 0 | 3302.2622 | 11.5955 | 6.7434 | 2.5873 | 9.1106 | 4.2585 | 0.10247 | 0 | 0 | 0 | 2.4848 | 346.8858 | 321.9114 | 300.5077 | 46.906 | 21.9316 | 0.52799 | 0 | 0 | 0 | 299.9798 | 5537.2383 | 4098.4871 | 3027.928 | 2537.4407 | 1098.6895 | 28.1304 | 0 | 0 | 0 | 2999.7976 | 0.009821 | 0.0042524 | 0.000108 | 0 | 0 | 0 | 0.0047048 | 5000000 | scaled
1434-37R | 34365.7672 | 28084.6996 | 0 | 6281.0676 | 81.72% | 0% | 18.28% | 15948.4301 | 27790.8183 | 1013.2267 | 11797.0843 | 3138.1192 | 1774.2277 | 20521.7654 | 5494.8252 | 1434 |  | 171 | 1434-37R | 34365.7672 | 18417.3371 | 6574.9489 | 28084.6996 | 12136.2695 | 293.8813 | 0 | 0 | 0 | 6281.0676 | 1798.1514 | 784.9247 | 23.9237 | 1793.4251 | 780.1984 | 19.1974 | 0 | 0 | 0 | 4.7263 | 6124.5763 | 2986.4572 | 629.7512 | 5553.9999 | 2415.8807 | 59.1747 | 0 | 0 | 0 | 570.5765 | 26443.0394 | 14645.9552 | 5921.274 | 20737.2746 | 8940.1904 | 215.5092 | 0 | 0 | 0 | 5705.7648 | 0.018915 | 0.008219 | 0.0002072 | 0 | 0 | 0 | 0.0087782 | 5000000 | scaled
1435-1075F | 4689.2811 | 3284.7817 | 0 | 1404.4994 | 70.05% | 0% | 29.95% | 1868.8418 | 3259.3342 | 444.4983 | 277.3174 | 1147.026 | 770.7278 | 490.6579 | 1997.9485 | 1435 |  | 172 | 1435-1075F | 4689.2811 | 2820.4393 | 1429.9469 | 3284.7817 | 1415.94 | 25.4475 | 0 | 0 | 0 | 1404.4994 | 777.8266 | 333.3283 | 7.0988 | 776.7697 | 332.2714 | 6.042 | 0 | 0 | 0 | 1.0568 | 2140.0524 | 993.0264 | 142.1039 | 2012.4667 | 865.4407 | 14.5182 | 0 | 0 | 0 | 127.5857 | 1771.4021 | 1494.0847 | 1280.7442 | 495.5453 | 218.2278 | 4.8874 | 0 | 0 | 0 | 1275.8568 | 0.0047928 | 0.0020752 | 5.28e-05 | 0 | 0 | 0 | 0.0019728 | 5000000 | scaled
1435-49F | 2133.37 | 414.2719 | 0 | 1719.0981 | 19.42% | 0% | 80.58% | 232.0312 | 409.9869 | 2.4601 | 216.5195 | 13.0515 | 4.3689 | 382.4776 | 23.1405 | 1435 |  | 173 | 1435-49F | 2133.37 | 1901.3388 | 1723.383 | 414.2719 | 182.2407 | 4.2849 | 0 | 0 | 0 | 1719.0981 | 5.6625 | 3.2023 | 1.2936 | 4.3689 | 1.9088 | 0 | 0 | 0 | 0 | 1.2936 | 179.3045 | 166.253 | 156.164 | 23.1405 | 10.0889 | 0 | 0 | 0 | 0 | 156.164 | 1948.403 | 1731.8835 | 1565.9254 | 386.7625 | 170.243 | 4.2849 | 0 | 0 | 0 | 1561.6405 | 0.0041316 | 0.0018366 | 4.6e-05 | 0 | 0 | 0 | 0.0024156 | 5000000 | scaled
1435-50 | 15088.2307 | 8942.1721 | 0 | 6146.0586 | 59.27% | 0% | 40.73% | 4884.7396 | 8831.7917 | 781.3114 | 1605.1755 | 2498.2527 | 1430.7246 | 2807.693 | 4593.3741 | 1435 |  | 174 | 1435-50 | 15088.2307 | 10203.4911 | 6256.439 | 8942.1721 | 4057.4325 | 110.3803 | 0 | 0 | 0 | 6146.0586 | 1454.8637 | 673.5523 | 24.1391 | 1450.239 | 668.9276 | 19.5144 | 0 | 0 | 0 | 4.6247 | 5213.6858 | 2715.4331 | 620.3117 | 4655.3737 | 2157.121 | 61.9995 | 0 | 0 | 0 | 558.3122 | 8419.6812 | 6814.5057 | 5611.9882 | 2836.5594 | 1231.3839 | 28.8664 | 0 | 0 | 0 | 5583.1218 | 0.017517 | 0.007908 | 0.0001996 | 0 | 0 | 0 | 0.0086324 | 5000000 | scaled
1438-331F | 124.8311 | 18.6792 | 0 | 106.1519 | 14.96% | 0% | 85.04% | 10.5839 | 18.4693 | 0 | 10.5839 | 0 | 0 | 18.4693 | 0 | 1438 |  | 175 | 1438-331F | 124.8311 | 114.2472 | 106.3618 | 18.6792 | 8.0953 | 0.20988 | 0 | 0 | 0 | 106.1519 | 0.079876 | 0.079876 | 0.079876 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079876 | 9.6429 | 9.6429 | 9.6429 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6429 | 115.1083 | 104.5244 | 96.639 | 18.6792 | 8.0953 | 0.20988 | 0 | 0 | 0 | 96.4291 | 0.0002056 | 8.9e-05 | 2.2e-06 | 0 | 0 | 0 | 0.0001494 | 5000000 | scaled
1438-333F | 313.7963 | 65.4874 | 0 | 248.3089 | 20.87% | 0% | 79.13% | 32.6208 | 65.0039 | 1.2316 | 25.1045 | 6.2847 | 3.074 | 45.9151 | 16.0148 | 1438 |  | 176 | 1438-333F | 313.7963 | 281.1755 | 248.7924 | 65.4874 | 32.8666 | 0.48342 | 0 | 0 | 0 | 248.3089 | 3.2609 | 2.0293 | 0.18684 | 3.074 | 1.8424 | 0 | 0 | 0 | 0 | 0.18684 | 38.5713 | 32.2866 | 22.5566 | 16.0148 | 9.7301 | 0 | 0 | 0 | 0 | 22.5566 | 271.9641 | 246.8596 | 226.049 | 46.3986 | 21.2941 | 0.48342 | 0 | 0 | 0 | 225.5655 | 0.0009042 | 0.0003916 | 1e-05 | 0 | 0 | 0 | 0.000351 | 5000000 | scaled
1439-29 | 746.5371 | 398.4699 | 0 | 348.0672 | 53.38% | 0% | 46.62% | 190.4241 | 392.8294 | 18.7465 | 60.5524 | 111.1251 | 40.2119 | 110.6325 | 241.985 | 1439 |  | 177 | 1439-29 | 746.5371 | 556.1131 | 353.7077 | 398.4699 | 208.0458 | 5.6405 | 0 | 0 | 0 | 348.0672 | 41.176 | 22.4294 | 0.96409 | 40.9141 | 22.1675 | 0.70218 | 0 | 0 | 0 | 0.26191 | 277.4512 | 166.3261 | 35.4662 | 245.8326 | 134.7074 | 3.8476 | 0 | 0 | 0 | 31.6187 | 427.9099 | 367.3575 | 317.2774 | 111.7232 | 51.1709 | 1.0907 | 0 | 0 | 0 | 316.1867 | 0.0005974 | 0.000273 | 7e-06 | 0 | 0 | 0 | 0.0004978 | 5000000 | scaled
144-29 | 11682.0378 | 20.3457 | 11486.9602 | 174.7319 | 0.1742% | 98.33% | 1.496% | 5164.5209 | 10739.031 | 7.2506 | 4709.0242 | 448.2461 | 14.9479 | 9792.4273 | 931.6558 | 144 |  | 178 | 144-29 | 11682.0378 | 6517.5169 | 943.0069 | 20.3457 | 9.3093 | 0.12141 | 11486.9602 | 6333.4757 | 768.1536 | 174.7319 | 16.0349 | 8.7843 | 1.0871 | 1.6135 | 0.77394 | 0 | 14.2899 | 7.8789 | 0.95559 | 0.13148 | 1013.7022 | 565.4561 | 82.0464 | 8.2703 | 3.9778 | 0 | 989.5591 | 545.6055 | 66.1736 | 15.8728 | 10652.3007 | 5943.2765 | 859.8735 | 10.4619 | 4.5576 | 0.12141 | 10483.1112 | 5779.9913 | 701.0244 | 158.7277 | 0.000366 | 0.0001584 | 4.2e-06 | 0.0061102 | 0.003466 | 0.000611 | 0.000252 | 5000000 | scaled
144-442F | 88451.1102 | 1479.7017 | 84606.8221 | 2364.5865 | 1.673% | 95.65% | 2.673% | 38664.9725 | 80404.8108 | 48.0312 | 35355.027 | 3261.9143 | 98.378 | 73507.8697 | 6798.5631 | 144 |  | 179 | 144-442F | 88451.1102 | 49786.1377 | 8046.2994 | 1479.7017 | 636.3255 | 16.1903 | 84606.8221 | 46785.2258 | 5665.5227 | 2364.5865 | 107.0057 | 58.9745 | 8.6278 | 4.2601 | 1.3637 | 0.087496 | 100.9663 | 55.8316 | 6.761 | 1.7793 | 7500.1926 | 4238.2782 | 701.6295 | 21.9075 | 6.9722 | 0.44447 | 7263.4844 | 4016.5054 | 486.3844 | 214.8007 | 80843.9119 | 45488.8849 | 7336.0422 | 1453.5341 | 627.9896 | 15.6583 | 77242.3713 | 42712.8888 | 5172.3773 | 2148.0065 | 0.0061768 | 0.0026748 | 6.74e-05 | 0.0060302 | 0.00343 | 0.000603 | 0.003302 | 5000000 | scaled
144-445F | 44171.9629 | 1564.5854 | 39594.446 | 3012.9315 | 3.542% | 89.64% | 6.821% | 18628.2033 | 38493.4033 | 30.1275 | 17105.5679 | 1492.5078 | 59.1362 | 35343.4411 | 3090.8259 | 144 |  | 180 | 144-445F | 44171.9629 | 25543.7596 | 5678.5596 | 1564.5854 | 670.3433 | 16.8254 | 39594.446 | 21860.4848 | 2648.8027 | 3012.9315 | 64.9376 | 34.8101 | 5.8014 | 10.5585 | 3.7714 | 0.048084 | 52.112 | 28.7715 | 3.4862 | 2.2671 | 3582.5217 | 2090.0139 | 491.6958 | 53.8537 | 19.2153 | 0.24687 | 3254.9713 | 1797.1018 | 217.7522 | 273.6968 | 40524.5035 | 23418.9356 | 5181.0624 | 1500.1732 | 647.3566 | 16.5304 | 36287.3627 | 20034.6114 | 2427.5643 | 2736.9676 | 0.0066316 | 0.002873 | 7.28e-05 | 0.006043 | 0.0034324 | 0.0006042 | 0.0042058 | 5000000 | scaled
1448-368 | 14080.1073 | 12265.0308 | 0 | 1815.0765 | 87.11% | 0% | 12.89% | 3848.5767 | 12047.2402 | 248.3203 | 2275.5307 | 1324.7256 | 830.23 | 6682.4003 | 4534.6099 | 1448 |  | 181 | 1448-368 | 14080.1073 | 10231.5305 | 2032.867 | 12265.0308 | 8416.454 | 217.7906 | 0 | 0 | 0 | 1815.0765 | 847.2328 | 598.9125 | 17.0028 | 845.867 | 597.5467 | 15.637 | 0 | 0 | 0 | 1.3658 | 4786.0748 | 3461.3491 | 251.4649 | 4621.192 | 3296.4663 | 86.5821 | 0 | 0 | 0 | 164.8828 | 8446.7997 | 6171.2689 | 1764.3994 | 6797.9718 | 4522.441 | 115.5715 | 0 | 0 | 0 | 1648.8279 | 0.005244 | 0.0033502 | 8.48e-05 | 0 | 0 | 0 | 0.0025496 | 5000000 | scaled
145-633 | 10355.1696 | 3579.757 | 6630.7392 | 144.6734 | 34.57% | 64.03% | 1.397% | 4910.5138 | 9744.1433 | 66.6262 | 4265.4585 | 578.4291 | 131.5282 | 8440.8466 | 1171.7684 | 145 |  | 182 | 145-633 | 10355.1696 | 5444.6558 | 611.0263 | 3579.757 | 1648.2042 | 22.9567 | 6630.7392 | 3651.7783 | 443.3962 | 144.6734 | 132.1943 | 65.5681 | 0.66601 | 123.7535 | 60.8706 | 0 | 8.3318 | 4.5886 | 0.55715 | 0.10886 | 1220.8202 | 642.3911 | 49.0518 | 670.6713 | 333.5007 | 0 | 537.0067 | 295.7482 | 35.9095 | 13.1422 | 9002.1551 | 4736.6967 | 561.3086 | 2785.3322 | 1253.833 | 22.9567 | 6085.4007 | 3351.4414 | 406.9296 | 131.4223 | 0.000479 | 0.0002074 | 5.4e-06 | 0.0060386 | 0.003422 | 0.0006038 | 0.0001892 | 5000000 | scaled
1458-1056 | 427447.797 | 386681.6177 | 40312.1118 | 454.0675 | 90.46% | 9.431% | 0.1062% | 211612.0703 | 398201.43 | 10424.0825 | 15809.4325 | 185378.5553 | 19420.3621 | 32856.224 | 345924.8439 | 1458 |  | 183 | 1458-1056 | 427447.797 | 215835.7267 | 29246.3669 | 386681.6177 | 192674.529 | 25076.8127 | 40312.1118 | 22707.1302 | 3715.4868 | 454.0675 | 20703.2872 | 10279.2047 | 1282.9251 | 20651.7119 | 10250.004 | 1277.8614 | 51.2336 | 28.859 | 4.7221 | 0.34167 | 370143.7677 | 184765.2124 | 24218.9237 | 365988.3774 | 182406.5378 | 23798.4837 | 4114.1425 | 2317.4268 | 379.1923 | 41.2478 | 36600.7421 | 20791.3096 | 3744.5181 | 41.5284 | 17.9873 | 0.4677 | 36146.7357 | 20360.8443 | 3331.5724 | 412.478 | 0.001097 | 0.0004752 | 1.18e-05 | 0.13333 | 0.075618 | 0.013333 | 0.000647 | 5000000 | scaled
1458-1057F | 155998.7084 | 0 | 155998.7084 | 0 | 0% | 100% | 0% | 5886.3519 | 12224.4933 | 9.3361 | 5378.6191 | 498.3967 | 19.3888 | 11170.0582 | 1035.0463 | 1458 |  | 184 | 1458-1057F | 155998.7084 | 150112.3565 | 143774.215 | 0 | 0 | 0 | 155998.7084 | 150112.3565 | 143774.215 | 0 | 247.4241 | 238.0879 | 228.0352 | 0 | 0 | 0 | 247.4241 | 238.0879 | 228.0352 | 0 | 13208.3911 | 12709.9944 | 12173.3448 | 0 | 0 | 0 | 13208.3911 | 12709.9944 | 12173.3448 | 0 | 142542.8932 | 137164.2742 | 131372.8351 | 0 | 0 | 0 | 142542.8932 | 137164.2742 | 131372.8351 | 0 | 0 | 0 | 0 | 0.13292 | 0.13292 | 0.13292 | 0 | 5000000 | scaled
1458-1058F | 2365689.624 | 2023558.5327 | 341127.0422 | 1004.0491 | 85.54% | 14.42% | 0.04244% | 855947.2953 | 2269920.9458 | 45366.2731 | 134876.1789 | 675704.8434 | 124665.7306 | 280558.9197 | 1864696.2955 | 1458 |  | 185 | 1458-1058F | 2365689.624 | 1509742.3286 | 95768.6781 | 2023558.5327 | 1316490.2194 | 63331.4554 | 341127.0422 | 192248.0602 | 31433.1737 | 1004.0491 | 128526.049 | 83159.776 | 3860.3184 | 127857.1669 | 82782.4861 | 3797.9984 | 668.1266 | 376.5343 | 61.5646 | 0.75551 | 1927224.2155 | 1251519.372 | 62527.9199 | 1895613.6473 | 1233664.8818 | 59532.358 | 31519.3597 | 17763.2817 | 2904.3535 | 91.2085 | 309939.3595 | 175063.1806 | 29380.4397 | 87.7185 | 42.8514 | 1.099 | 308939.5559 | 174108.2441 | 28467.2557 | 912.0851 | 0.0047804 | 0.0029402 | 7.46e-05 | 0.13214 | 0.074979 | 0.013214 | 0.0014158 | 5000000 | scaled
1458-1061 | 4370098.6983 | 4312122.8435 | 56488.804 | 1487.0508 | 98.67% | 1.293% | 0.03403% | 2488066.7414 | 4337558.9132 | 249366.6813 | 22668.0997 | 2216031.9603 | 434327.6385 | 47129.3279 | 3856101.9468 | 1458 |  | 186 | 1458-1061 | 4370098.6983 | 1882031.9569 | 32539.785 | 4312122.8435 | 1848706.0406 | 25842.3242 | 56488.804 | 31838.8655 | 5210.4101 | 1487.0508 | 437035.2263 | 187668.545 | 2707.5878 | 436935.6352 | 187611.9241 | 2697.386 | 98.4721 | 55.502 | 9.0829 | 1.119 | 3879807.7161 | 1663775.7557 | 23705.7693 | 3875039.1977 | 1661029.1221 | 23143.3062 | 4633.4337 | 2611.5489 | 427.3783 | 135.0847 | 53255.7559 | 30587.6562 | 6126.428 | 148.0106 | 64.9944 | 1.632 | 51756.8982 | 29171.8147 | 4773.9489 | 1350.8471 | 0.0058536 | 0.0025724 | 6.56e-05 | 0.13434 | 0.076225 | 0.013434 | 0.002086 | 5000000 | scaled
1458-1062F | 76809.2982 | 0 | 76809.2982 | 0 | 0% | 100% | 0% | 2868.3656 | 5952.3458 | 4.5578 | 2630.2282 | 233.5796 | 9.4582 | 5458.1703 | 484.7174 | 1458 |  | 187 | 1458-1062F | 76809.2982 | 73940.9326 | 70856.9524 | 0 | 0 | 0 | 76809.2982 | 73940.9326 | 70856.9524 | 0 | 122.0485 | 117.4907 | 112.5903 | 0 | 0 | 0 | 122.0485 | 117.4907 | 112.5903 | 0 | 6254.8115 | 6021.2319 | 5770.0942 | 0 | 0 | 0 | 6254.8115 | 6021.2319 | 5770.0942 | 0 | 70432.4382 | 67802.21 | 64974.2679 | 0 | 0 | 0 | 70432.4382 | 67802.21 | 64974.2679 | 0 | 0 | 0 | 0 | 0.1345 | 0.1345 | 0.1345 | 0 | 5000000 | scaled
1458-1075F | 58234.1999 | 58197.4423 | 0 | 36.7576 | 99.94% | 0% | 0.06312% | 34969.7703 | 58197.3475 | 1760.9225 | 7.2291 | 33201.6187 | 2942.2993 | 12.6457 | 55242.4025 | 1458 |  | 188 | 1458-1075F | 58234.1999 | 23264.4296 | 36.8524 | 58197.4423 | 23227.672 | 0.09476 | 0 | 0 | 0 | 36.7576 | 2942.327 | 1181.4045 | 0.027659 | 2942.2993 | 1181.3769 | 0 | 0 | 0 | 0 | 0.027659 | 55245.7416 | 22044.1229 | 3.3391 | 55242.4025 | 22040.7838 | 0 | 0 | 0 | 0 | 3.3391 | 46.1313 | 38.9022 | 33.4856 | 12.7404 | 5.5113 | 0.09476 | 0 | 0 | 0 | 33.3909 | 7.9e-05 | 3.42e-05 | 8e-07 | 0 | 0 | 0 | 5.1e-05 | 5000000 | scaled
1458-1115F | 66507.4376 | 0 | 66507.4376 | 0 | 0% | 100% | 0% | 29157.9944 | 60638.7162 | 55.6727 | 23158.5384 | 5943.7834 | 115.7802 | 48161.8871 | 12361.0489 | 1458 |  | 189 | 1458-1115F | 66507.4376 | 37349.4432 | 5868.7214 | 0 | 0 | 0 | 66507.4376 | 37349.4432 | 5868.7214 | 0 | 126.9857 | 71.313 | 11.2054 | 0 | 0 | 0 | 126.9857 | 71.313 | 11.2054 | 0 | 13557.3729 | 7613.5895 | 1196.324 | 0 | 0 | 0 | 13557.3729 | 7613.5895 | 1196.324 | 0 | 52823.0791 | 29664.5407 | 4661.1919 | 0 | 0 | 0 | 52823.0791 | 29664.5407 | 4661.1919 | 0 | 0 | 0 | 0 | 0.091242 | 0.051775 | 0.0091242 | 0 | 5000000 | scaled
1458-1117F | 139463.092 | 0 | 139463.092 | 0 | 0% | 100% | 0% | 61139.2384 | 127156.5917 | 78.2888 | 55300.2036 | 5760.746 | 162.8239 | 115012.6432 | 11981.1245 | 1458 |  | 190 | 1458-1117F | 139463.092 | 78323.8537 | 12306.5004 | 0 | 0 | 0 | 139463.092 | 78323.8537 | 12306.5004 | 0 | 178.5824 | 100.2936 | 15.7585 | 0 | 0 | 0 | 178.5824 | 100.2936 | 15.7585 | 0 | 13140.6846 | 7379.9386 | 1159.5601 | 0 | 0 | 0 | 13140.6846 | 7379.9386 | 1159.5601 | 0 | 126143.825 | 70843.6214 | 11131.1818 | 0 | 0 | 0 | 126143.825 | 70843.6214 | 11131.1818 | 0 | 0 | 0 | 0 | 0.091116 | 0.051703 | 0.0091116 | 0 | 5000000 | scaled
1458-1131R | 15987426.5024 | 15842278.1898 | 142065.243 | 3083.0696 | 99.09% | 0.8886% | 0.01928% | 4135789.7585 | 15690314.9304 | 213185.23 | 55892.3912 | 3866712.1373 | 812008.0315 | 117006.9309 | 14761299.968 | 1458 |  | 191 | 1458-1131R | 15987426.5024 | 11851636.7439 | 297111.572 | 15842278.1898 | 11768419.79 | 280900.3414 | 142065.243 | 80133.8843 | 13128.1611 | 3083.0696 | 826641.1563 | 613455.9263 | 14633.1248 | 826262.4437 | 613241.2968 | 14596.0227 | 376.3927 | 212.3095 | 34.7822 | 2.3199 | 15029173.0095 | 11162460.8722 | 267873.0415 | 15014666.4686 | 11154156.1634 | 266278.3138 | 14226.4727 | 8024.6406 | 1314.6595 | 280.0682 | 131612.3366 | 75719.9455 | 14605.4057 | 1349.2775 | 1022.3298 | 26.0049 | 127462.3776 | 71896.9342 | 11778.7193 | 2800.6815 | 0.017363 | 0.01278 | 0.0003244 | 0.13775 | 0.078207 | 0.013775 | 0.0043008 | 5000000 | scaled
1458-454F | 84091.208 | 0 | 84091.208 | 0 | 0% | 100% | 0% | 3128.0592 | 6491.4755 | 4.007 | 2811.7265 | 312.3258 | 8.3155 | 5835.0089 | 648.1511 | 1458 |  | 192 | 1458-454F | 84091.208 | 80963.1488 | 77599.7325 | 0 | 0 | 0 | 84091.208 | 80963.1488 | 77599.7325 | 0 | 107.7192 | 103.7122 | 99.4038 | 0 | 0 | 0 | 107.7192 | 103.7122 | 99.4038 | 0 | 8396.2132 | 8083.8874 | 7748.062 | 0 | 0 | 0 | 8396.2132 | 8083.8874 | 7748.062 | 0 | 75587.2756 | 72775.5491 | 69752.2667 | 0 | 0 | 0 | 75587.2756 | 72775.5491 | 69752.2667 | 0 | 0 | 0 | 0 | 0.13508 | 0.13508 | 0.13508 | 0 | 5000000 | scaled
1458-456F | 167568.5932 | 49947.8362 | 117589.0967 | 31.6603 | 29.81% | 70.17% | 0.01889% | 67864.139 | 157156.4226 | 1008.499 | 45868.5807 | 20987.0593 | 2852.8743 | 95508.882 | 58794.6662 | 1458 |  | 193 | 1458-456F | 167568.5932 | 99704.4542 | 10412.1706 | 49947.8362 | 33571.067 | 0.0040717 | 117589.0967 | 66101.7269 | 10380.5062 | 31.6603 | 2865.3985 | 1856.8995 | 12.5242 | 2723.772 | 1777.2749 | 0 | 141.6027 | 79.6008 | 12.5004 | 0.023823 | 59917.9176 | 38930.8584 | 1123.2514 | 47223.5675 | 31793.5763 | 0 | 12691.4741 | 7134.406 | 1120.3754 | 2.876 | 104785.277 | 58916.6964 | 9276.395 | 0.49673 | 0.21579 | 0.0040717 | 104756.0198 | 58887.7201 | 9247.6305 | 28.7605 | 0.0002032 | 8.8e-05 | 2.2e-06 | 0.091507 | 0.051971 | 0.0091508 | 5.02e-05 | 5000000 | scaled
1458-519 | 81003.9492 | 80965.7496 | 0 | 38.1996 | 99.95% | 0% | 0.04716% | 20658.7485 | 80729.1818 | 1069.2119 | 49.8913 | 19539.6454 | 4181.0979 | 203.8372 | 76344.2467 | 1458 |  | 194 | 1458-519 | 81003.9492 | 60345.2007 | 274.7674 | 80965.7496 | 60307.001 | 236.5677 | 0 | 0 | 0 | 38.1996 | 4199.3588 | 3130.147 | 18.2609 | 4199.3301 | 3130.1182 | 18.2322 | 0 | 0 | 0 | 0.028744 | 76562.2549 | 57022.6094 | 218.0082 | 76558.7848 | 57019.1394 | 214.5381 | 0 | 0 | 0 | 3.4701 | 242.3355 | 192.4443 | 38.4983 | 207.6347 | 157.7434 | 3.7975 | 0 | 0 | 0 | 34.7008 | 0.000162 | 0.000123 | 3.2e-06 | 0 | 0 | 0 | 5.5e-05 | 5000000 | scaled
1458-565R | 8159979.2875 | 8098401.0314 | 58030.6786 | 3547.5774 | 99.25% | 0.7112% | 0.04348% | 4348312.8654 | 8123647.314 | 225465.843 | 23032.6725 | 4099814.3499 | 421034.8795 | 47843.2436 | 7654769.1908 | 1458 |  | 195 | 1458-565R | 8159979.2875 | 3811666.422 | 36331.9735 | 8098401.0314 | 3775400.0263 | 27428.0811 | 58030.6786 | 32718.8184 | 5356.315 | 3547.5774 | 422612.1786 | 197146.3356 | 1577.2991 | 422547.3929 | 197108.6438 | 1568.8962 | 62.1163 | 35.0224 | 5.7334 | 2.6694 | 7681480.7447 | 3581666.3948 | 26711.5539 | 7675356.2505 | 3578072.7211 | 25853.7354 | 5802.2299 | 3271.4094 | 535.5542 | 322.2644 | 55886.3641 | 32853.6916 | 8043.1205 | 497.3881 | 218.6614 | 5.4495 | 52166.3324 | 29412.3866 | 4815.0274 | 3222.6436 | 0.017757 | 0.008382 | 0.0002128 | 0.13549 | 0.076905 | 0.013549 | 0.0049412 | 5000000 | scaled
1458-601R | 37077301.9797 | 36838604.201 | 228042.0393 | 10655.7393 | 99.36% | 0.615% | 0.02874% | 16631850.8439 | 36448598.7769 | 1485211.0093 | 93623.2482 | 15053016.5865 | 3259707.625 | 196842.6016 | 32992048.5503 | 1458 |  | 196 | 1458-601R | 37077301.9797 | 20445451.1358 | 628703.2028 | 36838604.201 | 20306168.0691 | 596975.6748 | 228042.0393 | 128627.3274 | 21071.7887 | 10655.7393 | 3313484.3296 | 1828273.3203 | 53776.7046 | 3312996.7234 | 1827994.7901 | 53724.3711 | 479.5881 | 270.5121 | 44.3154 | 8.0181 | 33538107.1211 | 18485090.5346 | 546058.5708 | 33515526.8902 | 18471932.1465 | 543093.5569 | 21612.2562 | 12190.4135 | 1997.0392 | 967.9747 | 225710.529 | 132087.2809 | 28867.9275 | 10080.5874 | 6241.1325 | 157.7468 | 205950.195 | 116166.4017 | 19030.4341 | 9679.7466 | 0.051536 | 0.028952 | 0.0007366 | 0.13764 | 0.078145 | 0.013764 | 0.015035 | 5000000 | scaled
1458-8 | 31853.3509 | 0 | 31853.3509 | 0 | 0% | 100% | 0% | 1155.544 | 2402.4953 | 10.2862 | 908.6243 | 236.6336 | 21.386 | 1889.1236 | 491.9856 | 1458 |  | 197 | 1458-8 | 31853.3509 | 30697.8069 | 29450.8557 | 0 | 0 | 0 | 31853.3509 | 30697.8069 | 29450.8557 | 0 | 283.5457 | 273.2595 | 262.1597 | 0 | 0 | 0 | 283.5457 | 273.2595 | 262.1597 | 0 | 6522.9638 | 6286.3303 | 6030.9782 | 0 | 0 | 0 | 6522.9638 | 6286.3303 | 6030.9782 | 0 | 25046.8414 | 24138.2171 | 23157.7177 | 0 | 0 | 0 | 25046.8414 | 24138.2171 | 23157.7177 | 0 | 0 | 0 | 0 | 0.13902 | 0.13902 | 0.13902 | 0 | 5000000 | scaled
1458-9 | 1056.4015 | 0 | 1056.4015 | 0 | 0% | 100% | 0% | 38.241 | 79.5065 | 0.025115 | 30.3197 | 7.8962 | 0.052216 | 63.0374 | 16.4169 | 1458 |  | 198 | 1458-9 | 1056.4015 | 1018.1606 | 976.895 | 0 | 0 | 0 | 1056.4015 | 1018.1606 | 976.895 | 0 | 0.6938 | 0.66868 | 0.64158 | 0 | 0 | 0 | 0.6938 | 0.66868 | 0.64158 | 0 | 218.1307 | 210.2345 | 201.7138 | 0 | 0 | 0 | 218.1307 | 210.2345 | 201.7138 | 0 | 837.577 | 807.2574 | 774.5396 | 0 | 0 | 0 | 837.577 | 807.2574 | 774.5396 | 0 | 0 | 0 | 0 | 0.13949 | 0.13949 | 0.13949 | 0 | 5000000 | scaled
146-275R | 50176.3891 | 15770.6481 | 33901.3459 | 504.3951 | 31.43% | 67.56% | 1.005% | 19683.3816 | 47039.3403 | 414.3203 | 14951.7142 | 4317.3471 | 1436.6106 | 30581.7979 | 15020.9317 | 146 |  | 199 | 146-275R | 50176.3891 | 30493.0075 | 3137.0488 | 15770.6481 | 11307.2469 | 363.2737 | 33901.3459 | 18681.3655 | 2269.38 | 504.3951 | 1473.4302 | 1059.1099 | 36.8196 | 1433.5098 | 1036.9414 | 33.7932 | 39.5409 | 21.789 | 2.6469 | 0.37954 | 15579.8982 | 11262.5512 | 558.9665 | 12524.2962 | 9558.1884 | 311.6699 | 3009.7825 | 1658.5432 | 201.477 | 45.8196 | 33123.0606 | 18171.3464 | 2541.2627 | 1812.8421 | 712.1171 | 17.8106 | 30852.0225 | 17001.0333 | 2065.2562 | 458.196 | 0.0021928 | 0.0014306 | 3.64e-05 | 0.0060332 | 0.0034206 | 0.0006034 | 0.0007176 | 5000000 | scaled
1480-26F | 1575.3538 | 397.3181 | 0 | 1178.0358 | 25.22% | 0% | 74.78% | 217.2858 | 391.8355 | 1.6743 | 206.8984 | 8.7131 | 3.1538 | 372.2913 | 16.3905 | 1480 |  | 200 | 1480-26F | 1575.3538 | 1358.068 | 1183.5183 | 397.3181 | 180.0322 | 5.4825 | 0 | 0 | 0 | 1178.0358 | 4.2416 | 2.5674 | 1.0878 | 3.3552 | 1.681 | 0.2014 | 0 | 0 | 0 | 0.88643 | 124.4539 | 115.7408 | 108.0634 | 17.4404 | 8.7272 | 1.0499 | 0 | 0 | 0 | 107.0136 | 1446.6583 | 1239.7598 | 1074.367 | 376.5225 | 169.6241 | 4.2313 | 0 | 0 | 0 | 1070.1358 | 0.0024 | 0.0011056 | 2.8e-05 | 0 | 0 | 0 | 0.0016818 | 5000000 | scaled
1481-5AE | 36.0921 | 0.5447 | 0 | 35.5474 | 1.509% | 0% | 98.49% | 0.40034 | 0.54137 | 0.033895 | 0.18989 | 0.17656 | 0.033895 | 0.33092 | 0.17656 | 1481 |  | 201 | 1481-5AE | 36.0921 | 35.6918 | 35.5508 | 0.5447 | 0.14436 | 0.0033314 | 0 | 0 | 0 | 35.5474 | 0.060643 | 0.026748 | 0.026748 | 0.033895 | 0 | 0 | 0 | 0 | 0 | 0.026748 | 3.4057 | 3.2292 | 3.2292 | 0.17656 | 0 | 0 | 0 | 0 | 0 | 3.2292 | 32.6258 | 32.4359 | 32.2949 | 0.33425 | 0.14436 | 0.0033314 | 0 | 0 | 0 | 32.2915 | 6.02e-05 | 2.6e-05 | 6e-07 | 0 | 0 | 0 | 5.3e-05 | 5000000 | scaled
1482-28 | 5045.7268 | 2778.3299 | 0 | 2267.3969 | 55.06% | 0% | 44.94% | 1568.545 | 2736.0758 | 0 | 1568.545 | 0 | 0 | 2736.0758 | 0 | 1482 |  | 202 | 1482-28 | 5045.7268 | 3477.1817 | 2309.651 | 2778.3299 | 1209.7848 | 42.2541 | 0 | 0 | 0 | 2267.3969 | 1.7061 | 1.7061 | 1.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7061 | 205.9719 | 205.9719 | 205.9719 | 0 | 0 | 0 | 0 | 0 | 0 | 205.9719 | 4838.0487 | 3269.5037 | 2101.9729 | 2778.3299 | 1209.7848 | 42.2541 | 0 | 0 | 0 | 2059.7189 | 0.0059002 | 0.0025714 | 9.28e-05 | 0 | 0 | 0 | 0.0031632 | 5000000 | scaled
1483-39 | 1246.9688 | 434.5696 | 0 | 812.3992 | 34.85% | 0% | 65.15% | 249.5812 | 429.7029 | 3.4072 | 228.6736 | 17.5003 | 5.0322 | 398.8144 | 25.8562 | 1483 |  | 203 | 1483-39 | 1246.9688 | 997.3876 | 817.2659 | 434.5696 | 184.9884 | 4.8667 | 0 | 0 | 0 | 812.3992 | 5.6975 | 2.2903 | 0.6653 | 5.0862 | 1.679 | 0.053995 | 0 | 0 | 0 | 0.6113 | 99.9331 | 82.4327 | 74.0768 | 26.1342 | 8.6338 | 0.27795 | 0 | 0 | 0 | 73.7989 | 1141.3382 | 912.6646 | 742.5238 | 403.3492 | 174.6756 | 4.5348 | 0 | 0 | 0 | 737.989 | 0.0021682 | 0.0009388 | 2.44e-05 | 0 | 0 | 0 | 0.0011506 | 5000000 | scaled
1483-40 | 314.4327 | 70.3452 | 0 | 244.0874 | 22.37% | 0% | 77.63% | 39.9025 | 69.5549 | 0 | 39.9025 | 0 | 0 | 69.5549 | 0 | 1483 |  | 204 | 1483-40 | 314.4327 | 274.5302 | 244.8777 | 70.3452 | 30.4428 | 0.79028 | 0 | 0 | 0 | 244.0874 | 0.18367 | 0.18367 | 0.18367 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18367 | 22.1731 | 22.1731 | 22.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 22.1731 | 292.0759 | 252.1735 | 222.521 | 70.3452 | 30.4428 | 0.79028 | 0 | 0 | 0 | 221.7307 | 0.0007574 | 0.000328 | 8.6e-06 | 0 | 0 | 0 | 0.0003396 | 5000000 | scaled
149-129R | 5359.5889 | 4904.8402 | 125.3807 | 329.368 | 91.52% | 2.339% | 6.145% | 3317.3242 | 4946.2406 | 280.1475 | 45.4507 | 2991.7261 | 432.5165 | 95.159 | 4418.5651 | 149 |  | 205 | 149-129R | 5359.5889 | 2042.2646 | 413.3483 | 4904.8402 | 1643.5549 | 75.5992 | 125.3807 | 69.3417 | 8.3811 | 329.368 | 440.5005 | 160.353 | 7.9841 | 440.1703 | 160.0597 | 7.7307 | 0.082344 | 0.045541 | 0.0055043 | 0.24784 | 4518.0488 | 1526.3227 | 99.4836 | 4462.2396 | 1482.0847 | 67.833 | 25.8892 | 14.318 | 1.7306 | 29.92 | 401.0396 | 355.5889 | 305.8806 | 2.4303 | 1.4106 | 0.035402 | 99.4091 | 54.9782 | 6.645 | 299.2002 | 0.0006254 | 0.0003526 | 9e-06 | 0.005968 | 0.003395 | 0.0005968 | 0.0004486 | 5000000 | scaled
149-154R | 62.5895 | 0 | 62.5895 | 0 | 0% | 100% | 0% | 9.9337 | 20.7567 | 0.006524 | 7.876 | 2.0512 | 0.013632 | 16.4571 | 4.2859 | 149 |  | 206 | 149-154R | 62.5895 | 52.6558 | 41.8328 | 0 | 0 | 0 | 62.5895 | 52.6558 | 41.8328 | 0 | 0.041106 | 0.034582 | 0.027474 | 0 | 0 | 0 | 0.041106 | 0.034582 | 0.027474 | 0 | 12.9238 | 10.8726 | 8.6378 | 0 | 0 | 0 | 12.9238 | 10.8726 | 8.6378 | 0 | 49.6246 | 41.7486 | 33.1675 | 0 | 0 | 0 | 49.6246 | 41.7486 | 33.1675 | 0 | 0 | 0 | 0 | 0.0059584 | 0.0059584 | 0.0059584 | 0 | 5000000 | scaled
150-434AE | 24532.3728 | 23680.0442 | 0 | 852.3286 | 96.53% | 0% | 3.474% | 9822.9776 | 22865.819 | 1119.5293 | 11.8169 | 8691.6315 | 2611.7507 | 21.3352 | 20232.7331 | 150 |  | 207 | 150-434AE | 24532.3728 | 14709.3952 | 1666.5538 | 23680.0442 | 13857.0666 | 814.2252 | 0 | 0 | 0 | 852.3286 | 2695.5768 | 1576.0476 | 83.8261 | 2694.9355 | 1575.4062 | 83.1848 | 0 | 0 | 0 | 0.64135 | 21040.9449 | 12349.3134 | 808.2118 | 20963.5188 | 12271.8873 | 730.7857 | 0 | 0 | 0 | 77.4261 | 795.8511 | 784.0342 | 774.5158 | 21.5899 | 9.773 | 0.25466 | 0 | 0 | 0 | 774.2612 | 0.0030544 | 0.0014922 | 3.78e-05 | 0 | 0 | 0 | 0.0011882 | 5000000 | scaled
150-506 | 17137.6555 | 16567.1918 | 0 | 570.4638 | 96.67% | 0% | 3.329% | 8423.8681 | 16538.7919 | 681.2155 | 0.054034 | 7742.5986 | 1332.8117 | 0.22203 | 15205.7582 | 150 |  | 208 | 150-506 | 17137.6555 | 8713.7875 | 598.8636 | 16567.1918 | 8143.3237 | 28.3998 | 0 | 0 | 0 | 570.4638 | 1336.5879 | 655.3725 | 3.7762 | 1336.1587 | 654.9432 | 3.347 | 0 | 0 | 0 | 0.42926 | 15282.6287 | 7540.0301 | 76.8705 | 15230.8074 | 7488.2088 | 25.0491 | 0 | 0 | 0 | 51.8213 | 518.4389 | 518.3849 | 518.2169 | 0.22574 | 0.1717 | 0.003713 | 0 | 0 | 0 | 518.2132 | 0.0018804 | 0.0008466 | 2.16e-05 | 0 | 0 | 0 | 0.0007864 | 5000000 | scaled
151-1044F | 907.5777 | 92.5956 | 0 | 814.9821 | 10.2% | 0% | 89.8% | 53.3784 | 91.5876 | 0.33737 | 51.3262 | 1.7148 | 0.34565 | 89.4849 | 1.7571 | 151 |  | 209 | 151-1044F | 907.5777 | 854.1993 | 815.9901 | 92.5956 | 39.2172 | 1.0079 | 0 | 0 | 0 | 814.9821 | 0.9589 | 0.62152 | 0.61325 | 0.34565 | 0.0082767 | 0 | 0 | 0 | 0 | 0.61325 | 75.7906 | 74.0759 | 74.0335 | 1.7571 | 0.042329 | 0 | 0 | 0 | 0 | 74.0335 | 830.8282 | 779.502 | 741.3433 | 90.4928 | 39.1666 | 1.0079 | 0 | 0 | 0 | 740.3354 | 0.0029646 | 0.0012836 | 3.34e-05 | 0 | 0 | 0 | 0.001137 | 5000000 | scaled
151-97 | 93.7753 | 22.4855 | 0 | 71.2898 | 23.98% | 0% | 76.02% | 12.7619 | 22.2486 | 0 | 12.7619 | 0 | 0 | 22.2486 | 0 | 151 |  | 210 | 151-97 | 93.7753 | 81.0134 | 71.5267 | 22.4855 | 9.7236 | 0.2369 | 0 | 0 | 0 | 71.2898 | 0.053643 | 0.053643 | 0.053643 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053643 | 6.476 | 6.476 | 6.476 | 0 | 0 | 0 | 0 | 0 | 0 | 6.476 | 87.2457 | 74.4838 | 64.997 | 22.4855 | 9.7236 | 0.2369 | 0 | 0 | 0 | 64.7601 | 0.0003242 | 0.0001402 | 3.4e-06 | 0 | 0 | 0 | 9.7e-05 | 5000000 | scaled
152-1713F | 9672.7599 | 6681.3015 | 0 | 2991.4584 | 69.07% | 0% | 30.93% | 4437.8883 | 6650.2398 | 846.186 | 863.3433 | 2728.3591 | 1239.9488 | 1482.8124 | 3927.4786 | 152 |  | 211 | 152-1713F | 9672.7599 | 5234.8715 | 3022.5201 | 6681.3015 | 2243.4132 | 31.0617 | 0 | 0 | 0 | 2991.4584 | 1247.3635 | 401.1775 | 7.4147 | 1245.1125 | 398.9265 | 5.1637 | 0 | 0 | 0 | 2.251 | 4213.1484 | 1484.7894 | 285.6698 | 3941.4023 | 1213.0432 | 13.9237 | 0 | 0 | 0 | 271.7461 | 4212.248 | 3348.9047 | 2729.4356 | 1494.7867 | 631.4434 | 11.9743 | 0 | 0 | 0 | 2717.4613 | 0.0093892 | 0.0040662 | 0.0001026 | 0 | 0 | 0 | 0.0042354 | 5000000 | scaled
152-1716F | 4298.9201 | 3519.9009 | 0 | 779.0191 | 81.88% | 0% | 18.12% | 1857.33 | 3518.6765 | 300.0334 | 102.975 | 1454.3217 | 557.8307 | 184.7611 | 2776.0846 | 152 |  | 212 | 152-1716F | 4298.9201 | 2441.59 | 780.2436 | 3519.9009 | 1662.5709 | 1.2245 | 0 | 0 | 0 | 779.0191 | 558.4169 | 258.3835 | 0.58619 | 557.8307 | 257.7973 | 0 | 0 | 0 | 0 | 0.58619 | 2846.8512 | 1392.5296 | 70.7666 | 2776.0846 | 1321.7629 | 0 | 0 | 0 | 0 | 70.7666 | 893.6519 | 790.677 | 708.8908 | 185.9856 | 83.0106 | 1.2245 | 0 | 0 | 0 | 707.6663 | 0.0025234 | 0.0010922 | 2.8e-05 | 0 | 0 | 0 | 0.0010652 | 5000000 | scaled
152-513AE | 12034.4749 | 8338.8008 | 0 | 3695.6741 | 69.29% | 0% | 30.71% | 4779.078 | 8251.393 | 118.8708 | 4047.8838 | 612.3234 | 204.0148 | 6997.123 | 1050.2552 | 152 |  | 213 | 152-513AE | 12034.4749 | 7255.3969 | 3783.0819 | 8338.8008 | 3559.7227 | 87.4078 | 0 | 0 | 0 | 3695.6741 | 208.3837 | 89.5129 | 4.3688 | 205.6028 | 86.732 | 1.588 | 0 | 0 | 0 | 2.7809 | 1394.1277 | 781.8043 | 343.8725 | 1058.4101 | 446.0867 | 8.155 | 0 | 0 | 0 | 335.7176 | 10431.9635 | 6384.0797 | 3434.8405 | 7074.7879 | 3026.9041 | 77.6649 | 0 | 0 | 0 | 3357.1757 | 0.014362 | 0.006219 | 0.0001588 | 0 | 0 | 0 | 0.0051796 | 5000000 | scaled
1525-23R | 8267.974 | 7400.2431 | 574.352 | 293.379 | 89.5% | 6.947% | 3.548% | 3358.0618 | 5524.9288 | 219.1549 | 202.4676 | 2936.4392 | 386.3859 | 424.4357 | 4714.1072 | 1525 |  | 214 | 1525-23R | 8267.974 | 4909.9122 | 2743.0452 | 7400.2431 | 4297.5323 | 2406.2224 | 574.352 | 319.0009 | 43.4439 | 293.379 | 543.5846 | 324.4297 | 157.1987 | 535.9127 | 320.0705 | 156.4143 | 7.4512 | 4.1385 | 0.56361 | 0.22076 | 6999.2613 | 4062.8221 | 2285.1541 | 6855.4773 | 3971.1144 | 2249.6435 | 117.1332 | 65.057 | 8.8599 | 26.6507 | 725.1281 | 522.6604 | 300.6924 | 8.8531 | 6.3475 | 0.16461 | 449.7675 | 249.8055 | 34.0203 | 266.5075 | 0.001793 | 0.0012946 | 3.3e-05 | 0.030627 | 0.017381 | 0.0030628 | 0.0004022 | 5000000 | scaled
153-1119R | 8011.5612 | 6044.4057 | 0 | 1967.1555 | 75.45% | 0% | 24.55% | 3350.0058 | 5976.4039 | 0 | 3350.0058 | 0 | 0 | 5976.4039 | 0 | 153 |  | 215 | 153-1119R | 8011.5612 | 4661.5554 | 2035.1573 | 6044.4057 | 2694.3999 | 68.0018 | 0 | 0 | 0 | 1967.1555 | 1.4802 | 1.4802 | 1.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4802 | 178.6978 | 178.6978 | 178.6978 | 0 | 0 | 0 | 0 | 0 | 0 | 178.6978 | 7831.3832 | 4481.3775 | 1854.9793 | 6044.4057 | 2694.3999 | 68.0018 | 0 | 0 | 0 | 1786.9775 | 0.0045034 | 0.0020284 | 5.1e-05 | 0 | 0 | 0 | 0.0028218 | 5000000 | scaled
153-581F | 9378.0031 | 5211.6199 | 0 | 4166.3832 | 55.57% | 0% | 44.43% | 3055.547 | 5168.5907 | 95.714 | 2626.1508 | 333.6822 | 149.9679 | 4496.6643 | 521.9585 | 153 |  | 216 | 153-581F | 9378.0031 | 6322.4561 | 4209.4124 | 5211.6199 | 2156.0728 | 43.0292 | 0 | 0 | 0 | 4166.3832 | 153.103 | 57.389 | 3.1351 | 149.9679 | 54.254 | 0 | 0 | 0 | 0 | 3.1351 | 900.4356 | 566.7534 | 378.4771 | 521.9585 | 188.2763 | 0 | 0 | 0 | 0 | 378.4771 | 8324.4645 | 5698.3137 | 3827.8002 | 4539.6934 | 1913.5426 | 43.0292 | 0 | 0 | 0 | 3784.7711 | 0.013997 | 0.00606 | 0.0001542 | 0 | 0 | 0 | 0.0058772 | 5000000 | scaled
154-13 | 288.3909 | 10.5158 | 0 | 277.8751 | 3.646% | 0% | 96.35% | 2.7777 | 10.3163 | 0 | 2.7777 | 0 | 0 | 10.3163 | 0 | 154 |  | 217 | 154-13 | 288.3909 | 285.6132 | 278.0746 | 10.5158 | 7.7381 | 0.19951 | 0 | 0 | 0 | 277.8751 | 0.20909 | 0.20909 | 0.20909 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20909 | 25.2424 | 25.2424 | 25.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 25.2424 | 262.9394 | 260.1618 | 252.6232 | 10.5158 | 7.7381 | 0.19951 | 0 | 0 | 0 | 252.4237 | 0.0010424 | 0.0006758 | 1.74e-05 | 0 | 0 | 0 | 0.0003908 | 5000000 | scaled
154-876R | 9995.7312 | 5858.8442 | 0 | 4136.887 | 58.61% | 0% | 41.39% | 2254.2031 | 5766.4228 | 0 | 2254.2031 | 0 | 0 | 5766.4228 | 0 | 154 |  | 218 | 154-876R | 9995.7312 | 7741.5281 | 4229.3084 | 5858.8442 | 3604.641 | 92.4213 | 0 | 0 | 0 | 4136.887 | 3.1129 | 3.1129 | 3.1129 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1129 | 375.7977 | 375.7977 | 375.7977 | 0 | 0 | 0 | 0 | 0 | 0 | 375.7977 | 9616.8207 | 7362.6176 | 3850.3979 | 5858.8442 | 3604.641 | 92.4213 | 0 | 0 | 0 | 3757.9765 | 0.012849 | 0.0061322 | 0.0001572 | 0 | 0 | 0 | 0.005857 | 5000000 | scaled
154-878R | 14227.4616 | 7462.3386 | 0 | 6765.123 | 52.45% | 0% | 47.55% | 4230.3792 | 7379.3134 | 0.91083 | 4224.7815 | 4.6869 | 1.8086 | 7368.212 | 9.2928 | 154 |  | 219 | 154-878R | 14227.4616 | 9997.0824 | 6848.1481 | 7462.3386 | 3231.9594 | 83.0251 | 0 | 0 | 0 | 6765.123 | 6.9299 | 6.0191 | 5.1213 | 1.8394 | 0.92856 | 0.030742 | 0 | 0 | 0 | 5.0905 | 624.0091 | 619.3222 | 614.7163 | 9.4607 | 4.7738 | 0.16784 | 0 | 0 | 0 | 614.5484 | 13596.5226 | 9371.7411 | 6228.3106 | 7451.0385 | 3226.257 | 82.8265 | 0 | 0 | 0 | 6145.4841 | 0.01897 | 0.008214 | 0.0002098 | 0 | 0 | 0 | 0.0095698 | 5000000 | scaled
154-894R | 8668.8446 | 2681.7092 | 0 | 5987.1354 | 30.94% | 0% | 69.06% | 1379.8177 | 2650.8471 | 27.3492 | 1271.7075 | 80.7609 | 51.8802 | 2445.6946 | 153.2722 | 154 |  | 220 | 154-894R | 8668.8446 | 7289.0269 | 6017.9975 | 2681.7092 | 1301.8915 | 30.8621 | 0 | 0 | 0 | 5987.1354 | 56.3854 | 29.0361 | 4.5051 | 51.8802 | 24.531 | 0 | 0 | 0 | 0 | 4.5051 | 697.1477 | 616.3867 | 543.8755 | 153.2722 | 72.5113 | 0 | 0 | 0 | 0 | 543.8755 | 7915.3116 | 6643.604 | 5469.6169 | 2476.5568 | 1204.8493 | 30.8621 | 0 | 0 | 0 | 5438.7548 | 0.015279 | 0.0068282 | 0.0001748 | 0 | 0 | 0 | 0.0084364 | 5000000 | scaled
154-897F | 316.7041 | 6.9027 | 0 | 309.8014 | 2.18% | 0% | 97.82% | 3.9133 | 6.8253 | 0 | 3.9133 | 0 | 0 | 6.8253 | 0 | 154 |  | 221 | 154-897F | 316.7041 | 312.7908 | 309.8788 | 6.9027 | 2.9894 | 0.077363 | 0 | 0 | 0 | 309.8014 | 0.23312 | 0.23312 | 0.23312 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23312 | 28.1426 | 28.1426 | 28.1426 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1426 | 288.3284 | 284.4151 | 281.5031 | 6.9027 | 2.9894 | 0.077363 | 0 | 0 | 0 | 281.4257 | 0.0015718 | 0.0006806 | 1.76e-05 | 0 | 0 | 0 | 0.0004412 | 5000000 | scaled
155-1236R | 27977.2902 | 25033.7293 | 0 | 2943.5608 | 89.48% | 0% | 10.52% | 13983.6034 | 24794.3332 | 1021.1223 | 8976.0777 | 3986.4034 | 1829.3517 | 15794.3359 | 7170.6456 | 155 |  | 222 | 155-1236R | 27977.2902 | 13993.6868 | 3182.9569 | 25033.7293 | 11050.126 | 239.3961 | 0 | 0 | 0 | 2943.5608 | 1847.2047 | 826.0824 | 17.8529 | 1844.9897 | 823.8674 | 15.638 | 0 | 0 | 0 | 2.2149 | 7497.2913 | 3510.8879 | 326.6457 | 7229.8962 | 3243.4929 | 59.2506 | 0 | 0 | 0 | 267.3951 | 18632.7942 | 9656.7165 | 2838.4582 | 15958.8434 | 6982.7657 | 164.5075 | 0 | 0 | 0 | 2673.9508 | 0.0089004 | 0.0038538 | 9.86e-05 | 0 | 0 | 0 | 0.0041198 | 5000000 | scaled
155-40 | 3749.156 | 947.1905 | 0 | 2801.9655 | 25.26% | 0% | 74.74% | 535.6322 | 936.9768 | 2.4022 | 520.9197 | 12.3103 | 4.5971 | 908.8338 | 23.5459 | 155 |  | 223 | 155-40 | 3749.156 | 3213.5238 | 2812.1792 | 947.1905 | 411.5583 | 10.2137 | 0 | 0 | 0 | 2801.9655 | 6.7055 | 4.3033 | 2.1084 | 4.5971 | 2.1949 | 0 | 0 | 0 | 0 | 2.1084 | 278.0784 | 265.7681 | 254.5325 | 23.5459 | 11.2356 | 0 | 0 | 0 | 0 | 254.5325 | 3464.3721 | 2943.4524 | 2555.5383 | 919.0475 | 398.1278 | 10.2137 | 0 | 0 | 0 | 2545.3246 | 0.0082376 | 0.0035672 | 9.12e-05 | 0 | 0 | 0 | 0.0039504 | 5000000 | scaled
156-529AE | 2061.718 | 840.3382 | 0 | 1221.3798 | 40.76% | 0% | 59.24% | 485.5106 | 831.7213 | 4.0616 | 460.4519 | 20.9971 | 6.4286 | 792.1668 | 33.1259 | 156 |  | 224 | 156-529AE | 2061.718 | 1576.2074 | 1229.9966 | 840.3382 | 354.8276 | 8.6169 | 0 | 0 | 0 | 1221.3798 | 7.3477 | 3.2861 | 0.91905 | 6.4286 | 2.367 | 0 | 0 | 0 | 0 | 0.91905 | 144.0769 | 123.0798 | 110.951 | 33.1259 | 12.1288 | 0 | 0 | 0 | 0 | 110.951 | 1910.2935 | 1449.8415 | 1118.1266 | 800.7837 | 340.3318 | 8.6169 | 0 | 0 | 0 | 1109.5098 | 0.0036644 | 0.0015868 | 4.02e-05 | 0 | 0 | 0 | 0.001766 | 5000000 | scaled
156-538 | 34335.7843 | 30195.2509 | 0 | 4140.5334 | 87.94% | 0% | 12.06% | 18187.0941 | 29946.2209 | 2248.4223 | 6751.8116 | 9186.8602 | 3648.1189 | 11565.2388 | 14732.8632 | 156 |  | 225 | 156-538 | 34335.7843 | 16148.6902 | 4389.5634 | 30195.2509 | 12008.1568 | 249.03 | 0 | 0 | 0 | 4140.5334 | 3677.1161 | 1428.6938 | 28.9972 | 3674.0005 | 1425.5782 | 25.8816 | 0 | 0 | 0 | 3.1156 | 15207.7106 | 6020.8504 | 474.8474 | 14831.5817 | 5644.7215 | 98.7185 | 0 | 0 | 0 | 376.1289 | 15450.9576 | 8699.1459 | 3885.7188 | 11689.6687 | 4937.8571 | 124.4299 | 0 | 0 | 0 | 3761.2889 | 0.012818 | 0.0055502 | 0.0001422 | 0 | 0 | 0 | 0.0058556 | 5000000 | scaled
157-165R | 418567.6391 | 367108.5943 | 48820.7744 | 2638.2704 | 87.71% | 11.66% | 0.6303% | 136110.7772 | 405041.1815 | 5852.6459 | 18945.1025 | 111313.0288 | 18748.5793 | 42040.4207 | 344252.1815 | 157 |  | 226 | 157-165R | 418567.6391 | 282456.8618 | 13526.4576 | 367108.5943 | 252180.9411 | 6224.1313 | 48820.7744 | 27637.6504 | 4664.0559 | 2638.2704 | 19100.5821 | 13247.9361 | 352.0028 | 18957.4361 | 13166.0392 | 336.5319 | 141.1608 | 79.9117 | 13.4857 | 1.9852 | 350880.1944 | 239567.1656 | 6628.0129 | 344564.5416 | 235887.859 | 5807.8854 | 6075.9905 | 3439.6444 | 580.4652 | 239.6623 | 48586.8626 | 29641.7601 | 6546.4419 | 3586.6166 | 3127.0429 | 79.714 | 42603.6231 | 24118.0943 | 4070.1051 | 2396.6229 | 0.0171 | 0.011811 | 0.0003 | 0.26179 | 0.14874 | 0.026179 | 0.0037264 | 5000000 | scaled
157-189R | 5507023.9246 | 5091861.4926 | 398405.2954 | 16757.1366 | 92.46% | 7.234% | 0.3043% | 1329931.9772 | 5347672.6602 | 62677.2939 | 152929.3301 | 1114325.3531 | 273501.2401 | 322811.8961 | 4751359.5239 | 157 |  | 227 | 157-189R | 5507023.9246 | 4177091.9474 | 159351.2644 | 5091861.4926 | 3934701.8598 | 104558.1587 | 398405.2954 | 225632.951 | 38035.9691 | 16757.1366 | 279371.1347 | 216693.8407 | 5869.8945 | 278436.2244 | 216158.8953 | 5769.2328 | 922.3011 | 522.3362 | 88.0526 | 12.6092 | 4856055.71 | 3741730.3569 | 104696.1861 | 4807244.0158 | 3713426.2005 | 98659.2056 | 47289.4644 | 26781.9267 | 4514.7507 | 1522.2298 | 371597.0799 | 218667.7498 | 48785.1838 | 6181.2523 | 5116.764 | 129.7204 | 350193.5299 | 198328.6881 | 33433.1658 | 15222.2977 | 0.089417 | 0.065261 | 0.0016654 | 0.25732 | 0.14627 | 0.025732 | 0.023761 | 5000000 | scaled
157-1928R | 3052674.4598 | 3024212.5715 | 26568.0107 | 1893.8776 | 99.07% | 0.8703% | 0.06204% | 442791.3871 | 2952955.9083 | 22739.2807 | 10176.5316 | 409875.5748 | 154488.934 | 21371.4163 | 2777095.558 | 157 |  | 228 | 157-1928R | 3052674.4598 | 2609883.0727 | 99718.5515 | 3024212.5715 | 2592948.28 | 95283.4372 | 26568.0107 | 15040.9151 | 2541.2367 | 1893.8776 | 159386.1525 | 136646.8718 | 4897.2185 | 159360.1489 | 136631.5321 | 4893.4425 | 24.5785 | 13.9146 | 2.3509 | 1.4251 | 2867951.2779 | 2458075.7031 | 90855.7199 | 2864661.1174 | 2456138.405 | 90385.4299 | 3118.1193 | 1765.257 | 298.2489 | 172.0411 | 25337.0294 | 15160.4977 | 3965.6131 | 191.3051 | 178.3429 | 4.5648 | 23425.3129 | 13261.7435 | 2240.6369 | 1720.4113 | 0.0095218 | 0.0081752 | 0.000208 | 0.26902 | 0.15284 | 0.026902 | 0.0026628 | 5000000 | scaled
157-204R | 3876133.3857 | 3836813.9225 | 32325.7406 | 6993.7226 | 98.99% | 0.834% | 0.1804% | 1382169.9246 | 3799843.0874 | 80730.894 | 24292.4939 | 1277146.5367 | 219883.9983 | 49153.2564 | 3530805.8327 | 157 |  | 229 | 157-204R | 3876133.3857 | 2493963.4611 | 76290.2983 | 3836813.9225 | 2468665.0611 | 66203.2457 | 32325.7406 | 18304.6773 | 3093.3299 | 6993.7226 | 223756.8168 | 143025.9227 | 3872.8185 | 223648.3467 | 142962.2182 | 3857.6797 | 103.2075 | 58.442 | 9.8762 | 5.2626 | 3593857.8296 | 2316711.2929 | 63051.9969 | 3589388.9263 | 2313905.1819 | 62049.8368 | 3833.5887 | 2170.7965 | 366.8456 | 635.3146 | 58518.7393 | 34226.2454 | 9365.4829 | 23776.6494 | 11797.6611 | 295.7291 | 28388.9443 | 16075.4388 | 2716.6082 | 6353.1455 | 0.046093 | 0.029607 | 0.0007524 | 0.27181 | 0.15445 | 0.027181 | 0.0098664 | 5000000 | scaled
157-207R | 719086.4935 | 718278.8873 | 0 | 807.6062 | 99.89% | 0% | 0.1123% | 179047.2731 | 704389.9654 | 10602.8638 | 5114.9854 | 163329.4239 | 42163.5895 | 21129.9435 | 641096.4325 | 157 |  | 230 | 157-207R | 719086.4935 | 540039.2204 | 14696.5281 | 718278.8873 | 539231.6141 | 13888.9219 | 0 | 0 | 0 | 807.6062 | 42991.6408 | 32388.777 | 828.0514 | 42991.0331 | 32388.1693 | 827.4437 | 0 | 0 | 0 | 0.6077 | 653813.7626 | 490484.3387 | 12717.3301 | 653740.3991 | 490410.9752 | 12643.9666 | 0 | 0 | 0 | 73.3635 | 22281.0901 | 17166.1047 | 1151.1466 | 21547.4551 | 16432.4696 | 417.5116 | 0 | 0 | 0 | 733.635 | 0.0084054 | 0.0064232 | 0.000163 | 0 | 0 | 0 | 0.001135 | 5000000 | scaled
157-232R | 3160507.9457 | 3010962.3601 | 142243.2326 | 7302.353 | 95.27% | 4.501% | 0.231% | 1003435.6351 | 3092923.04 | 51967.6319 | 55954.1285 | 895513.8747 | 164192.5117 | 123414.8322 | 2805315.6961 | 157 |  | 231 | 157-232R | 3160507.9457 | 2157072.3106 | 67584.9057 | 3010962.3601 | 2069192.0808 | 46663.23 | 142243.2326 | 80577.8767 | 13619.3226 | 7302.353 | 166803.4742 | 114835.8422 | 2610.9625 | 166616.9876 | 114727.8193 | 2588.1383 | 180.9918 | 102.5282 | 17.3294 | 5.4948 | 2851112.6702 | 1955598.7955 | 45796.9741 | 2837573.2124 | 1947641.3939 | 43900.7783 | 12876.1071 | 7294.0509 | 1232.845 | 663.3507 | 142591.8013 | 86637.6728 | 19176.9691 | 6772.1602 | 6822.8676 | 174.3134 | 129186.1336 | 73181.2977 | 12369.1483 | 6633.5075 | 0.036403 | 0.024821 | 0.0006308 | 0.27502 | 0.15633 | 0.027502 | 0.010244 | 5000000 | scaled
157-257R | 2061187.627 | 1680703.7028 | 366718.3239 | 13765.6002 | 81.54% | 17.79% | 0.6678% | 645243.0316 | 1981241.6377 | 27883.6573 | 142911.4948 | 474447.8795 | 94740.7174 | 300550.9033 | 1585950.017 | 157 |  | 232 | 157-257R | 2061187.627 | 1415944.5954 | 79945.9893 | 1680703.7028 | 1194334.0483 | 31077.7926 | 366718.3239 | 207844.9469 | 35102.5964 | 13765.6002 | 96556.8891 | 68673.2318 | 1816.1717 | 95981.1751 | 68342.4469 | 1751.6971 | 565.3558 | 320.4267 | 54.1163 | 10.3582 | 1620113.2871 | 1145665.4076 | 34163.2701 | 1580508.6898 | 1122676.9658 | 29241.5038 | 38354.1207 | 21737.9653 | 3671.2897 | 1250.4765 | 344517.4508 | 201605.956 | 43966.5475 | 4213.838 | 3314.6356 | 84.5917 | 327798.8474 | 185786.5549 | 31377.1903 | 12504.7655 | 0.074373 | 0.053391 | 0.0013548 | 0.27299 | 0.15527 | 0.027299 | 0.019499 | 5000000 | scaled
157-273R | 1867403.0023 | 1774228.8839 | 87986.0651 | 5188.0533 | 95.01% | 4.712% | 0.2778% | 542749.3224 | 1823207.8056 | 30480.5399 | 36806.3494 | 475462.4331 | 105117.1863 | 82947.4235 | 1635143.1958 | 157 |  | 233 | 157-273R | 1867403.0023 | 1324653.6799 | 44195.1967 | 1774228.8839 | 1269610.1758 | 30572.227 | 87986.0651 | 49855.4508 | 8434.9164 | 5188.0533 | 106980.4502 | 76499.9103 | 1863.2639 | 106820.325 | 76407.4869 | 1844.3837 | 156.2214 | 88.5196 | 14.9764 | 3.9038 | 1664977.4905 | 1189515.0573 | 29834.2947 | 1655394.7877 | 1183880.9788 | 28489.5288 | 9111.4164 | 5162.7922 | 873.4796 | 471.2863 | 95445.0616 | 58638.7122 | 12497.6381 | 12013.7712 | 9321.7101 | 238.3146 | 78718.4273 | 44604.139 | 7546.4603 | 4712.8632 | 0.032501 | 0.023677 | 0.0006016 | 0.28315 | 0.16098 | 0.028315 | 0.0073038 | 5000000 | scaled
157-81R | 18749596.2803 | 18188039.2067 | 543833.1499 | 17723.9237 | 97% | 2.901% | 0.09453% | 7420382.7538 | 18404692.1926 | 404433.4054 | 213409.7112 | 6802539.6372 | 1014043.8795 | 448426.3101 | 16942222.003 | 157 |  | 234 | 157-81R | 18749596.2803 | 11329213.5265 | 344904.0877 | 18188039.2067 | 11003440.283 | 275096.2956 | 543833.1499 | 308049.3198 | 52083.8684 | 17723.9237 | 1029849.2792 | 625415.8738 | 15805.3997 | 1029117.7389 | 624995.7172 | 15723.2793 | 718.2036 | 406.8199 | 68.7836 | 13.3367 | 17208218.6863 | 10405679.0491 | 265996.6833 | 17153004.4284 | 10373705.3838 | 259252.8599 | 53604.2045 | 30363.612 | 5133.77 | 1610.0534 | 511528.3148 | 298118.6036 | 63102.0048 | 5917.0394 | 4739.182 | 120.1564 | 489510.7417 | 277278.8879 | 46881.3147 | 16100.5336 | 0.083238 | 0.052286 | 0.00133 | 0.27592 | 0.15683 | 0.027592 | 0.024981 | 5000000 | scaled
158-29 | 14981.6018 | 4343.4993 | 0 | 10638.1025 | 28.99% | 0% | 71.01% | 2472.9866 | 4295.5382 | 39.2168 | 2319.117 | 114.6527 | 64.3765 | 4043.2072 | 187.9545 | 158 |  | 235 | 158-29 | 14981.6018 | 12508.6153 | 10686.0636 | 4343.4993 | 1870.5127 | 47.9611 | 0 | 0 | 0 | 10638.1025 | 73.2598 | 34.0429 | 8.8833 | 65.2549 | 26.0381 | 0.87842 | 0 | 0 | 0 | 8.0048 | 1156.9584 | 1042.3057 | 969.0039 | 190.5859 | 75.9332 | 2.6314 | 0 | 0 | 0 | 966.3725 | 13751.3837 | 11432.2666 | 9708.1765 | 4087.6585 | 1768.5415 | 44.4513 | 0 | 0 | 0 | 9663.7252 | 0.028264 | 0.012237 | 0.0003126 | 0 | 0 | 0 | 0.015033 | 5000000 | scaled
159-1010F | 72.8645 | 10.3174 | 0 | 62.5471 | 14.16% | 0% | 85.84% | 5.8514 | 10.2048 | 0 | 5.8514 | 0 | 0 | 10.2048 | 0 | 159 |  | 236 | 159-1010F | 72.8645 | 67.013 | 62.6596 | 10.3174 | 4.4659 | 0.11253 | 0 | 0 | 0 | 62.5471 | 0.047065 | 0.047065 | 0.047065 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047065 | 5.6818 | 5.6818 | 5.6818 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6818 | 67.1356 | 61.2842 | 56.9307 | 10.3174 | 4.4659 | 0.11253 | 0 | 0 | 0 | 56.8182 | 0.0002934 | 0.000127 | 3.2e-06 | 0 | 0 | 0 | 9.6e-05 | 5000000 | scaled
159-31R | 17924.8013 | 7689.385 | 0 | 10235.4163 | 42.9% | 0% | 57.1% | 4358.7512 | 7600.2378 | 17.0941 | 4262.6005 | 79.0566 | 29.0383 | 7436.8024 | 134.3971 | 159 |  | 237 | 159-31R | 17924.8013 | 13566.0501 | 10324.5635 | 7689.385 | 3330.6338 | 89.1472 | 0 | 0 | 0 | 10235.4163 | 37.4116 | 20.3176 | 8.3733 | 29.7098 | 12.6157 | 0.67151 | 0 | 0 | 0 | 7.7018 | 1067.2974 | 988.2407 | 932.9003 | 137.5052 | 58.4485 | 3.108 | 0 | 0 | 0 | 929.7922 | 16820.0923 | 12557.4918 | 9383.2899 | 7522.1701 | 3259.5696 | 85.3676 | 0 | 0 | 0 | 9297.9222 | 0.026716 | 0.011587 | 0.0003238 | 0 | 0 | 0 | 0.014386 | 5000000 | scaled
159-37F | 7088.9812 | 2401.2908 | 0 | 4687.6904 | 33.87% | 0% | 66.13% | 1354.8623 | 2375.2215 | 1.4495 | 1345.8846 | 7.5283 | 3.835 | 2351.2406 | 20.1459 | 159 |  | 238 | 159-37F | 7088.9812 | 5734.1189 | 4713.7598 | 2401.2908 | 1046.4285 | 26.0694 | 0 | 0 | 0 | 4687.6904 | 7.3623 | 5.9129 | 3.5273 | 3.835 | 2.3855 | 0 | 0 | 0 | 0 | 3.5273 | 445.9789 | 438.4506 | 425.833 | 20.1459 | 12.6176 | 0 | 0 | 0 | 0 | 425.833 | 6635.64 | 5289.7554 | 4284.3994 | 2377.3099 | 1031.4253 | 26.0694 | 0 | 0 | 0 | 4258.3301 | 0.013058 | 0.005654 | 0.0001432 | 0 | 0 | 0 | 0.0066108 | 5000000 | scaled
159-38F | 2247.2178 | 515.4353 | 0 | 1731.7825 | 22.94% | 0% | 77.06% | 291.457 | 509.52 | 1.0448 | 285.0658 | 5.3464 | 2.0238 | 497.1435 | 10.3527 | 159 |  | 239 | 159-38F | 2247.2178 | 1955.7608 | 1737.6978 | 515.4353 | 223.9783 | 5.9153 | 0 | 0 | 0 | 1731.7825 | 3.3735 | 2.3286 | 1.3496 | 2.0704 | 1.0255 | 0.046507 | 0 | 0 | 0 | 1.3031 | 167.907 | 162.5606 | 157.5543 | 10.5907 | 5.2443 | 0.23797 | 0 | 0 | 0 | 157.3163 | 2075.9374 | 1790.8716 | 1578.7939 | 502.7743 | 217.7085 | 5.6308 | 0 | 0 | 0 | 1573.1631 | 0.0046566 | 0.0020168 | 5.2e-05 | 0 | 0 | 0 | 0.0024634 | 5000000 | scaled
160-20R | 17108.6865 | 11846.8267 | 0 | 5261.8598 | 69.24% | 0% | 30.76% | 6445.1009 | 11706.6502 | 37.1089 | 6217.7591 | 190.2329 | 58.2293 | 11349.8405 | 298.5804 | 160 |  | 240 | 160-20R | 17108.6865 | 10663.5856 | 5402.0363 | 11846.8267 | 5401.7258 | 140.1765 | 0 | 0 | 0 | 5261.8598 | 62.9378 | 25.8289 | 4.7085 | 58.9784 | 21.8695 | 0.74909 | 0 | 0 | 0 | 3.9594 | 780.4182 | 590.1853 | 481.8378 | 302.4273 | 112.1944 | 3.8468 | 0 | 0 | 0 | 477.9909 | 16265.3305 | 10047.5714 | 4915.49 | 11485.421 | 5267.6619 | 135.5806 | 0 | 0 | 0 | 4779.9095 | 0.011259 | 0.0049572 | 0.000127 | 0 | 0 | 0 | 0.007456 | 5000000 | scaled
161-610R | 29937.3639 | 20225.7446 | 0 | 9711.6193 | 67.56% | 0% | 32.44% | 11529.6633 | 20001.3338 | 96.6838 | 10936.5983 | 496.3812 | 165.0797 | 18988.8187 | 847.4354 | 161 |  | 241 | 161-610R | 29937.3639 | 18407.7006 | 9936.0301 | 20225.7446 | 8696.0812 | 224.4108 | 0 | 0 | 0 | 9711.6193 | 175.3457 | 78.6619 | 10.266 | 168.038 | 71.3542 | 2.9583 | 0 | 0 | 0 | 7.3077 | 1744.8485 | 1248.4672 | 897.4131 | 862.6383 | 366.2571 | 15.2029 | 0 | 0 | 0 | 882.2101 | 28017.1697 | 17080.5714 | 9028.351 | 19195.0682 | 8258.4699 | 206.2496 | 0 | 0 | 0 | 8822.1015 | 0.027835 | 0.012052 | 0.000305 | 0 | 0 | 0 | 0.013744 | 5000000 | scaled
161-974F | 2987.1246 | 2189.0733 | 0 | 798.0513 | 73.28% | 0% | 26.72% | 1290.4176 | 2170.3231 | 151.579 | 160.3874 | 978.4513 | 250.3352 | 326.4411 | 1593.5469 | 161 |  | 242 | 161-974F | 2987.1246 | 1696.7069 | 816.8015 | 2189.0733 | 898.6556 | 18.7501 | 0 | 0 | 0 | 798.0513 | 252.8805 | 101.3015 | 2.5454 | 252.28 | 100.701 | 1.9449 | 0 | 0 | 0 | 0.60051 | 1678.2607 | 699.8094 | 84.7138 | 1605.7652 | 627.3139 | 12.2183 | 0 | 0 | 0 | 72.4955 | 1055.9834 | 895.596 | 729.5423 | 331.0281 | 170.6407 | 4.587 | 0 | 0 | 0 | 724.9553 | 0.0035512 | 0.0016398 | 4.14e-05 | 0 | 0 | 0 | 0.0011224 | 5000000 | scaled
161-975F | 8586.1588 | 6585.678 | 0 | 2000.4808 | 76.7% | 0% | 23.3% | 3319.773 | 6501.8881 | 0.95063 | 3313.8141 | 5.0082 | 1.9923 | 6489.4067 | 10.489 | 161 |  | 243 | 161-975F | 8586.1588 | 5266.3858 | 2084.2707 | 6585.678 | 3265.9051 | 83.7899 | 0 | 0 | 0 | 2000.4808 | 3.6419 | 2.6912 | 1.6495 | 2.1366 | 1.1859 | 0.14425 | 0 | 0 | 0 | 1.5053 | 192.9696 | 187.9614 | 182.4805 | 11.2445 | 6.2363 | 0.7555 | 0 | 0 | 0 | 181.725 | 8389.5474 | 5075.7332 | 1900.1406 | 6572.2969 | 3258.4828 | 82.8902 | 0 | 0 | 0 | 1817.2504 | 0.0056884 | 0.0025394 | 6.52e-05 | 0 | 0 | 0 | 0.0028314 | 5000000 | scaled
161-989F | 821.8126 | 640.8335 | 0 | 180.9791 | 77.98% | 0% | 22.02% | 296.0681 | 640.7495 | 30.9638 | 5.3314 | 259.773 | 63.6624 | 9.4159 | 567.6711 | 161 |  | 244 | 161-989F | 821.8126 | 525.7444 | 181.0631 | 640.8335 | 344.7654 | 0.084025 | 0 | 0 | 0 | 180.9791 | 63.7986 | 32.8348 | 0.13618 | 63.6624 | 32.6986 | 0 | 0 | 0 | 0 | 0.13618 | 584.1114 | 324.3384 | 16.4403 | 567.6711 | 307.8982 | 0 | 0 | 0 | 0 | 16.4403 | 173.9025 | 168.5712 | 164.4867 | 9.4999 | 4.1686 | 0.084025 | 0 | 0 | 0 | 164.4026 | 0.0004302 | 0.0001864 | 4.8e-06 | 0 | 0 | 0 | 0.0002536 | 5000000 | scaled
161-991F | 10717.709 | 4759.0289 | 0 | 5958.6801 | 44.4% | 0% | 55.6% | 2553.7021 | 4710.6193 | 180.0985 | 1752.546 | 621.0576 | 329.8459 | 3249.2219 | 1131.5515 | 161 |  | 245 | 161-991F | 10717.709 | 8164.0069 | 6007.0897 | 4759.0289 | 2205.3268 | 48.4096 | 0 | 0 | 0 | 5958.6801 | 338.3862 | 158.2877 | 8.5403 | 333.9025 | 153.8039 | 4.0566 | 0 | 0 | 0 | 4.4837 | 1686.1348 | 1065.0772 | 554.5833 | 1144.8442 | 523.7867 | 13.2927 | 0 | 0 | 0 | 541.2906 | 8693.188 | 6940.642 | 5443.966 | 3280.2822 | 1527.7362 | 31.0603 | 0 | 0 | 0 | 5412.9058 | 0.016783 | 0.0074112 | 0.0001884 | 0 | 0 | 0 | 0.0084854 | 5000000 | scaled
162-19F | 15155.4896 | 8021.5455 | 0 | 7133.9441 | 52.93% | 0% | 47.07% | 4329.6113 | 7936.6106 | 299.98 | 2434.6391 | 1594.9922 | 550.5674 | 4456.1136 | 2929.9296 | 162 |  | 246 | 162-19F | 15155.4896 | 10825.8783 | 7218.879 | 8021.5455 | 3691.9342 | 84.9349 | 0 | 0 | 0 | 7133.9441 | 561.0688 | 261.0888 | 10.5014 | 555.7008 | 255.7208 | 5.1333 | 0 | 0 | 0 | 5.3681 | 3605.1783 | 2010.1861 | 675.2487 | 2957.126 | 1362.1337 | 27.1964 | 0 | 0 | 0 | 648.0524 | 10989.2424 | 8554.6033 | 6533.1288 | 4508.7188 | 2074.0797 | 52.6052 | 0 | 0 | 0 | 6480.5236 | 0.019192 | 0.0084924 | 0.0002166 | 0 | 0 | 0 | 0.010063 | 5000000 | scaled
162-44R | 6377.9481 | 2283.5935 | 0 | 4094.3546 | 35.8% | 0% | 64.2% | 1257.685 | 2256.5274 | 7.9585 | 1224.3027 | 25.4237 | 14.2223 | 2196.8012 | 45.5039 | 162 |  | 247 | 162-44R | 6377.9481 | 5120.2631 | 4121.4207 | 2283.5935 | 1025.9086 | 27.0661 | 0 | 0 | 0 | 4094.3546 | 17.7213 | 9.7628 | 3.499 | 14.6404 | 6.6819 | 0.41814 | 0 | 0 | 0 | 3.0809 | 418.7813 | 393.3575 | 373.2774 | 46.8473 | 21.4236 | 1.3434 | 0 | 0 | 0 | 371.934 | 5941.4455 | 4717.1428 | 3744.6443 | 2222.1058 | 997.803 | 25.3046 | 0 | 0 | 0 | 3719.3397 | 0.010361 | 0.0045188 | 0.0001154 | 0 | 0 | 0 | 0.0057706 | 5000000 | scaled
163-29R | 28436.2269 | 17337.2392 | 0 | 11098.9877 | 60.97% | 0% | 39.03% | 9743.1956 | 17233.0314 | 414.9743 | 7008.4201 | 2319.8013 | 744.6335 | 12316.5959 | 4171.802 | 163 |  | 248 | 163-29R | 28436.2269 | 18693.0313 | 11203.1955 | 17337.2392 | 7594.0435 | 104.2077 | 0 | 0 | 0 | 11098.9877 | 755.2991 | 340.3248 | 10.6655 | 746.9474 | 331.9732 | 2.3139 | 0 | 0 | 0 | 8.3516 | 5191.8688 | 2872.0675 | 1020.0668 | 4183.6292 | 1863.8279 | 11.8271 | 0 | 0 | 0 | 1008.2396 | 22489.059 | 15480.6389 | 10172.4631 | 12406.6626 | 5398.2425 | 90.0667 | 0 | 0 | 0 | 10082.3964 | 0.02851 | 0.012373 | 0.0003142 | 0 | 0 | 0 | 0.01555 | 5000000 | scaled
163-33R | 25042.5523 | 11573.0912 | 0 | 13469.4611 | 46.21% | 0% | 53.79% | 6209.2311 | 11452.6855 | 64.4813 | 5944.8387 | 199.9111 | 144.8076 | 10858.6954 | 449.1825 | 163 |  | 249 | 163-33R | 25042.5523 | 18833.3212 | 13589.8669 | 11573.0912 | 5363.8601 | 120.4057 | 0 | 0 | 0 | 13469.4611 | 155.1321 | 90.6508 | 10.3245 | 144.9968 | 80.5155 | 0.18921 | 0 | 0 | 0 | 10.1353 | 1673.3555 | 1473.4444 | 1224.173 | 449.7805 | 249.8693 | 0.59795 | 0 | 0 | 0 | 1223.5751 | 23214.0647 | 17269.226 | 12355.3693 | 10978.3139 | 5033.4753 | 119.6186 | 0 | 0 | 0 | 12235.7507 | 0.025223 | 0.011143 | 0.0002844 | 0 | 0 | 0 | 0.019194 | 5000000 | scaled
165-35R | 6403.2002 | 2776.8255 | 0 | 3626.3748 | 43.37% | 0% | 56.63% | 1565.216 | 2760.989 | 128.12 | 734.0334 | 703.0626 | 221.3284 | 1316.3201 | 1223.3405 | 165 |  | 250 | 165-35R | 6403.2002 | 4837.9842 | 3642.2112 | 2776.8255 | 1211.6094 | 15.8364 | 0 | 0 | 0 | 3626.3748 | 224.7488 | 96.6288 | 3.4204 | 222.0201 | 93.9001 | 0.69169 | 0 | 0 | 0 | 2.7287 | 1556.3246 | 853.2621 | 332.9842 | 1226.9023 | 523.8397 | 3.5618 | 0 | 0 | 0 | 329.4224 | 4622.1267 | 3888.0933 | 3305.8066 | 1327.9031 | 593.8697 | 11.5829 | 0 | 0 | 0 | 3294.2237 | 0.0093216 | 0.0040364 | 0.0001022 | 0 | 0 | 0 | 0.0050576 | 5000000 | scaled
165-621F | 101146.8183 | 92716.6093 | 0 | 8430.209 | 91.67% | 0% | 8.335% | 48961.6254 | 91489.7542 | 3354.7422 | 22826.3112 | 22780.5721 | 6327.3136 | 41599.9852 | 43562.4553 | 165 |  | 251 | 165-621F | 101146.8183 | 52185.1928 | 9657.0641 | 92716.6093 | 43754.9838 | 1226.8551 | 0 | 0 | 0 | 8430.209 | 6420.1573 | 3065.4151 | 92.8437 | 6413.8138 | 3059.0717 | 86.5002 | 0 | 0 | 0 | 6.3435 | 44955.9958 | 22175.4237 | 1393.5405 | 44190.1899 | 21409.6178 | 627.7345 | 0 | 0 | 0 | 765.806 | 49770.6652 | 26944.354 | 8170.68 | 42112.6056 | 19286.2944 | 512.6204 | 0 | 0 | 0 | 7658.0596 | 0.025641 | 0.011264 | 0.0002858 | 0 | 0 | 0 | 0.011887 | 5000000 | scaled
166-462F | 8465.9831 | 3878.2864 | 0 | 4587.6967 | 45.81% | 0% | 54.19% | 2209.8277 | 3837.0584 | 14.5054 | 2121.0808 | 74.2414 | 22.8964 | 3697.071 | 117.091 | 166 |  | 252 | 166-462F | 8465.9831 | 6256.1555 | 4628.9247 | 3878.2864 | 1668.4587 | 41.228 | 0 | 0 | 0 | 4587.6967 | 26.3485 | 11.8431 | 3.4521 | 22.8964 | 8.391 | 0 | 0 | 0 | 0 | 3.4521 | 533.8405 | 459.5991 | 416.7495 | 117.091 | 42.8496 | 0 | 0 | 0 | 0 | 416.7495 | 7905.7941 | 5784.7133 | 4208.7231 | 3738.299 | 1617.2181 | 41.228 | 0 | 0 | 0 | 4167.4951 | 0.013771 | 0.0059622 | 0.0001522 | 0 | 0 | 0 | 0.0064052 | 5000000 | scaled
166-463F | 159.515 | 17.0949 | 0 | 142.4201 | 10.72% | 0% | 89.28% | 9.6833 | 16.8791 | 0 | 9.6833 | 0 | 0 | 16.8791 | 0 | 166 |  | 253 | 166-463F | 159.515 | 149.8317 | 142.6359 | 17.0949 | 7.4116 | 0.2158 | 0 | 0 | 0 | 142.4201 | 0.10717 | 0.10717 | 0.10717 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10717 | 12.9375 | 12.9375 | 12.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9375 | 146.4703 | 136.787 | 129.5912 | 17.0949 | 7.4116 | 0.2158 | 0 | 0 | 0 | 129.3754 | 0.0001882 | 8.16e-05 | 2.2e-06 | 0 | 0 | 0 | 0.0001992 | 5000000 | scaled
166-465F | 544.0531 | 57.1677 | 0 | 486.8855 | 10.51% | 0% | 89.49% | 20.6084 | 56.2386 | 0 | 20.6084 | 0 | 0 | 56.2386 | 0 | 166 |  | 254 | 166-465F | 544.0531 | 523.4447 | 487.8146 | 57.1677 | 36.5592 | 0.92909 | 0 | 0 | 0 | 486.8855 | 0.36637 | 0.36637 | 0.36637 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36637 | 44.229 | 44.229 | 44.229 | 0 | 0 | 0 | 0 | 0 | 0 | 44.229 | 499.4578 | 478.8493 | 443.2192 | 57.1677 | 36.5592 | 0.92909 | 0 | 0 | 0 | 442.2901 | 0.0012034 | 0.0006682 | 1.68e-05 | 0 | 0 | 0 | 0.0006804 | 5000000 | scaled
166-982F | 2919.185 | 1241.393 | 0 | 1677.7921 | 42.53% | 0% | 57.47% | 692.2731 | 1228.6658 | 7.4155 | 646.8258 | 38.0317 | 16.0861 | 1130.1056 | 82.4741 | 166 |  | 255 | 166-982F | 2919.185 | 2226.912 | 1690.5192 | 1241.393 | 549.1199 | 12.7271 | 0 | 0 | 0 | 1677.7921 | 17.3553 | 9.9398 | 1.2692 | 16.0928 | 8.6773 | 0.0067002 | 0 | 0 | 0 | 1.2625 | 234.9207 | 196.889 | 152.4466 | 82.5089 | 44.4772 | 0.034799 | 0 | 0 | 0 | 152.4118 | 2666.9091 | 2020.0832 | 1536.8034 | 1142.7913 | 495.9654 | 12.6856 | 0 | 0 | 0 | 1524.1178 | 0.0041522 | 0.0017986 | 4.6e-05 | 0 | 0 | 0 | 0.0023564 | 5000000 | scaled
166-984F | 4539.1878 | 1363.8636 | 0 | 3175.3243 | 30.05% | 0% | 69.95% | 771.839 | 1348.8534 | 1.5032 | 762.5806 | 7.7551 | 3.0699 | 1329.9505 | 15.833 | 166 |  | 256 | 166-984F | 4539.1878 | 3767.3489 | 3190.3345 | 1363.8636 | 592.0246 | 15.0102 | 0 | 0 | 0 | 3175.3243 | 5.4848 | 3.9816 | 2.4149 | 3.0955 | 1.5923 | 0.025618 | 0 | 0 | 0 | 2.3893 | 304.4137 | 296.6586 | 288.5807 | 15.9651 | 8.21 | 0.13207 | 0 | 0 | 0 | 288.4486 | 4229.2893 | 3466.7087 | 2899.3388 | 1344.803 | 582.2224 | 14.8525 | 0 | 0 | 0 | 2884.4863 | 0.0088412 | 0.0038284 | 9.78e-05 | 0 | 0 | 0 | 0.0044642 | 5000000 | scaled
167-32F | 1715.6589 | 1194.5915 | 0 | 521.0673 | 69.63% | 0% | 30.37% | 597.1756 | 1187.2967 | 104.6933 | 57.7322 | 434.7501 | 209.6515 | 99.9975 | 877.6478 | 167 |  | 257 | 167-32F | 1715.6589 | 1118.4833 | 528.3621 | 1194.5915 | 597.416 | 7.2948 | 0 | 0 | 0 | 521.0673 | 211.3966 | 106.7033 | 1.7451 | 211.0045 | 106.3112 | 1.353 | 0 | 0 | 0 | 0.39209 | 929.9773 | 495.2272 | 52.3296 | 882.6432 | 447.8931 | 4.9954 | 0 | 0 | 0 | 47.3341 | 574.285 | 516.5528 | 474.2875 | 100.9438 | 43.2117 | 0.94635 | 0 | 0 | 0 | 473.3411 | 0.0014642 | 0.0006338 | 1.6e-05 | 0 | 0 | 0 | 0.0007478 | 5000000 | scaled
168-702F | 86049.6211 | 82715.2549 | 0 | 3334.3662 | 96.13% | 0% | 3.875% | 40947.3854 | 82198.5288 | 6119.6594 | 2825.8085 | 32001.9174 | 12278.6353 | 5351.2956 | 64568.5978 | 168 |  | 258 | 168-702F | 86049.6211 | 45102.2357 | 3851.0923 | 82715.2549 | 41767.8695 | 516.7261 | 0 | 0 | 0 | 3334.3662 | 12354.8649 | 6235.2054 | 76.2295 | 12352.3559 | 6232.6964 | 73.7205 | 0 | 0 | 0 | 2.509 | 65236.8256 | 33234.9081 | 668.2277 | 64933.9294 | 32932.012 | 365.3316 | 0 | 0 | 0 | 302.8961 | 8457.9307 | 5632.1221 | 3106.635 | 5428.9696 | 2603.1611 | 77.674 | 0 | 0 | 0 | 3028.9611 | 0.014289 | 0.0069072 | 0.0001758 | 0 | 0 | 0 | 0.0046154 | 5000000 | scaled
168-703F | 2769.0967 | 1119.0332 | 0 | 1650.0635 | 40.41% | 0% | 59.59% | 620.7609 | 1107.8635 | 7.3082 | 575.7863 | 37.6664 | 16.5367 | 1006.0227 | 85.3041 | 168 |  | 259 | 168-703F | 2769.0967 | 2148.3358 | 1661.2332 | 1119.0332 | 498.2723 | 11.1698 | 0 | 0 | 0 | 1650.0635 | 17.8169 | 10.5088 | 1.2802 | 16.5753 | 9.2672 | 0.038624 | 0 | 0 | 0 | 1.2416 | 235.3944 | 197.728 | 150.0904 | 85.5015 | 47.8351 | 0.19746 | 0 | 0 | 0 | 149.8929 | 2515.8854 | 1940.099 | 1509.8626 | 1016.9564 | 441.1701 | 10.9337 | 0 | 0 | 0 | 1498.929 | 0.003616 | 0.0015656 | 3.92e-05 | 0 | 0 | 0 | 0.0022836 | 5000000 | scaled
169-35F | 38.1507 | 3.3736 | 0 | 34.7771 | 8.843% | 0% | 91.16% | 1.9122 | 3.3373 | 0 | 1.9122 | 0 | 0 | 3.3373 | 0 | 169 |  | 260 | 169-35F | 38.1507 | 36.2384 | 34.8133 | 3.3736 | 1.4614 | 0.036275 | 0 | 0 | 0 | 34.7771 | 0.026169 | 0.026169 | 0.026169 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026169 | 3.1592 | 3.1592 | 3.1592 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1592 | 34.9653 | 33.0531 | 31.628 | 3.3736 | 1.4614 | 0.036275 | 0 | 0 | 0 | 31.5917 | 0.0001302 | 5.64e-05 | 1.4e-06 | 0 | 0 | 0 | 4.8e-05 | 5000000 | scaled
170-3R | 134607.5717 | 96026.3636 | 33230.9125 | 5350.2956 | 71.34% | 24.69% | 3.975% | 69825.4048 | 126174.9387 | 5614.8619 | 17872.1196 | 46338.4233 | 9754.8931 | 35858.142 | 80561.9036 | 170 |  | 261 | 170-3R | 134607.5717 | 64782.1669 | 8432.633 | 96026.3636 | 40922.5782 | 668.9087 | 33230.9125 | 18509.2931 | 2413.4287 | 5350.2956 | 9839.1067 | 4224.2447 | 84.2136 | 9795.8433 | 4198.3639 | 77.338 | 39.2375 | 21.8549 | 2.8497 | 4.0259 | 81771.1386 | 35432.7153 | 1209.2349 | 78424.5196 | 33353.3676 | 515.4568 | 2860.5944 | 1593.3231 | 207.7536 | 486.0245 | 42997.3265 | 25125.2069 | 7139.1845 | 7806.0007 | 3370.8466 | 76.1139 | 30331.0806 | 16894.1152 | 2202.8255 | 4860.2451 | 0.027063 | 0.012202 | 0.00031 | 0.024481 | 0.013965 | 0.002448 | 0.0074726 | 5000000 | scaled
170-410R | 29166.7063 | 9045.2272 | 13245.7325 | 6875.7466 | 31.01% | 45.41% | 23.57% | 11045.0316 | 21223.099 | 494.787 | 5436.3231 | 5113.9215 | 856.7685 | 11224.6999 | 9141.6306 | 170 |  | 262 | 170-410R | 29166.7063 | 18121.6747 | 7943.6074 | 9045.2272 | 3867.5033 | 105.9163 | 13245.7325 | 7378.4247 | 961.9444 | 6875.7466 | 872.9521 | 378.1651 | 16.1837 | 855.9762 | 366.417 | 10.1528 | 11.8022 | 6.5743 | 0.85711 | 5.1738 | 9997.3376 | 4883.4162 | 855.707 | 7387.2348 | 3152.8095 | 86.9162 | 1985.5053 | 1106.0092 | 144.1933 | 624.5975 | 18296.4166 | 12860.0934 | 7071.7167 | 802.0162 | 348.2768 | 8.8473 | 11248.4251 | 6265.8413 | 816.894 | 6245.9753 | 0.069145 | 0.030813 | 0.0007822 | 0.02451 | 0.013982 | 0.002451 | 0.009706 | 5000000 | scaled
170-42 | 23954.2202 | 20673.1889 | 1858.788 | 1422.2433 | 86.3% | 7.76% | 5.937% | 12507.4938 | 22134.6183 | 1147.0467 | 2616.3006 | 8744.1466 | 2010.3105 | 4778.5084 | 15345.7994 | 170 |  | 263 | 170-42 | 23954.2202 | 11446.7263 | 1819.6019 | 20673.1889 | 8988.8407 | 262.3857 | 1858.788 | 1035.6424 | 134.973 | 1422.2433 | 2037.5091 | 890.4625 | 27.1986 | 2035.1968 | 888.7002 | 26.0383 | 1.2421 | 0.69207 | 0.090196 | 1.0702 | 15700.1985 | 6956.052 | 354.3991 | 15213.0142 | 6627.3985 | 199.207 | 357.9868 | 199.4559 | 25.9946 | 129.1976 | 6216.5125 | 3600.2119 | 1438.0041 | 3424.978 | 1472.742 | 37.1405 | 1499.559 | 835.4944 | 108.8881 | 1291.9755 | 0.011109 | 0.0048104 | 0.000123 | 0.024503 | 0.013979 | 0.0024504 | 0.0019822 | 5000000 | scaled
170-46 | 63310.6973 | 25125.7829 | 30211.1438 | 7973.7706 | 39.69% | 47.72% | 12.59% | 26895.7606 | 52844.3888 | 646.6464 | 20707.9289 | 5541.1853 | 1189.5111 | 41177.0122 | 10477.8656 | 170 |  | 264 | 170-46 | 63310.6973 | 36414.9367 | 10466.3084 | 25125.7829 | 11613.2799 | 299.7769 | 30211.1438 | 16827.8861 | 2192.7609 | 7973.7706 | 1212.5607 | 565.9143 | 23.0496 | 1159.2448 | 533.5589 | 13.6153 | 47.3158 | 26.3554 | 3.4342 | 6 | 11510.1971 | 5969.0117 | 1032.3315 | 7778.1056 | 3569.3251 | 89.6827 | 3007.7487 | 1675.3438 | 218.306 | 724.3428 | 50587.9396 | 29880.0107 | 9410.9274 | 16188.4324 | 7510.3959 | 196.4789 | 27156.0793 | 15126.187 | 1971.0207 | 7243.4278 | 0.06411 | 0.028805 | 0.0007314 | 0.024472 | 0.013959 | 0.0024472 | 0.011257 | 5000000 | scaled
170-463F | 4084.1596 | 0 | 4084.1596 | 0 | 0% | 100% | 0% | 535.8355 | 1121.0634 | 0.73411 | 492.3596 | 42.7418 | 1.5359 | 1030.104 | 89.4235 | 170 |  | 265 | 170-463F | 4084.1596 | 3548.3241 | 2963.0962 | 0 | 0 | 0 | 4084.1596 | 3548.3241 | 2963.0962 | 0 | 5.5954 | 4.8613 | 4.0595 | 0 | 0 | 0 | 5.5954 | 4.8613 | 4.0595 | 0 | 325.7799 | 283.0381 | 236.3564 | 0 | 0 | 0 | 325.7799 | 283.0381 | 236.3564 | 0 | 3752.7842 | 3260.4246 | 2722.6802 | 0 | 0 | 0 | 3752.7842 | 3260.4246 | 2722.6802 | 0 | 0 | 0 | 0 | 0.024508 | 0.024508 | 0.024508 | 0 | 5000000 | scaled
170-464F | 2961.9496 | 0 | 2961.9496 | 0 | 0% | 100% | 0% | 389.7873 | 813.4254 | 0.53274 | 346.3074 | 42.9472 | 1.1117 | 722.6896 | 89.624 | 170 |  | 266 | 170-464F | 2961.9496 | 2572.1623 | 2148.5242 | 0 | 0 | 0 | 2961.9496 | 2572.1623 | 2148.5242 | 0 | 4.0482 | 3.5155 | 2.9365 | 0 | 0 | 0 | 4.0482 | 3.5155 | 2.9365 | 0 | 326.3506 | 283.4035 | 236.7266 | 0 | 0 | 0 | 326.3506 | 283.4035 | 236.7266 | 0 | 2631.5507 | 2285.2433 | 1908.8611 | 0 | 0 | 0 | 2631.5507 | 2285.2433 | 1908.8611 | 0 | 0 | 0 | 0 | 0.024547 | 0.024547 | 0.024547 | 0 | 5000000 | scaled
170-465F | 24847.0507 | 0 | 24847.0507 | 0 | 0% | 100% | 0% | 3271.3822 | 6830.2697 | 3.3831 | 2995.1009 | 272.8981 | 7.0636 | 6253.4262 | 569.7799 | 170 |  | 267 | 170-465F | 24847.0507 | 21575.6685 | 18016.781 | 0 | 0 | 0 | 24847.0507 | 21575.6685 | 18016.781 | 0 | 25.6957 | 22.3126 | 18.6322 | 0 | 0 | 0 | 25.6957 | 22.3126 | 18.6322 | 0 | 2072.7366 | 1799.8385 | 1502.9567 | 0 | 0 | 0 | 2072.7366 | 1799.8385 | 1502.9567 | 0 | 22748.6183 | 19753.5174 | 16495.1921 | 0 | 0 | 0 | 22748.6183 | 19753.5174 | 16495.1921 | 0 | 0 | 0 | 0 | 0.024542 | 0.024542 | 0.024542 | 0 | 5000000 | scaled
170-879 | 10367.5101 | 0 | 10367.5101 | 0 | 0% | 100% | 0% | 1366.4941 | 2852.0984 | 1.3766 | 1240.2269 | 124.8906 | 2.8732 | 2588.5578 | 260.6673 | 170 |  | 268 | 170-879 | 10367.5101 | 9001.016 | 7515.4117 | 0 | 0 | 0 | 10367.5101 | 9001.016 | 7515.4117 | 0 | 10.4443 | 9.0677 | 7.5711 | 0 | 0 | 0 | 10.4443 | 9.0677 | 7.5711 | 0 | 947.5379 | 822.6472 | 686.8705 | 0 | 0 | 0 | 947.5379 | 822.6472 | 686.8705 | 0 | 9409.5279 | 8169.3011 | 6820.9701 | 0 | 0 | 0 | 9409.5279 | 8169.3011 | 6820.9701 | 0 | 0 | 0 | 0 | 0.02456 | 0.02456 | 0.02456 | 0 | 5000000 | scaled
171-34 | 81203.497 | 36273.3696 | 41936.381 | 2993.7464 | 44.67% | 51.64% | 3.687% | 37584.9163 | 74225.5634 | 2033.1164 | 16827.2284 | 18724.5715 | 3774.4023 | 34772.5213 | 35678.6397 | 171 |  | 269 | 171-34 | 81203.497 | 43618.5807 | 6977.9337 | 36273.3696 | 17316.046 | 943.9267 | 41936.381 | 23308.7882 | 3040.2606 | 2993.7464 | 3874.3772 | 1841.2608 | 99.9749 | 3811.1345 | 1805.109 | 93.3006 | 60.9901 | 33.8991 | 4.4216 | 2.2527 | 37243.5358 | 18518.9643 | 1564.8961 | 30596.1008 | 14703.4347 | 830.7391 | 6375.481 | 3543.5756 | 462.2031 | 271.954 | 40085.584 | 23258.3557 | 5313.0627 | 1866.1343 | 807.5023 | 19.887 | 35499.9099 | 19731.3136 | 2573.6359 | 2719.5398 | 0.01493 | 0.0068876 | 0.0001746 | 0.024509 | 0.013948 | 0.002451 | 0.0042478 | 5000000 | scaled
171-566 | 2584.8939 | 0 | 2584.8939 | 0 | 0% | 100% | 0% | 341.3405 | 711.8745 | 1.0089 | 273.4362 | 66.8953 | 2.1042 | 570.2584 | 139.512 | 171 |  | 270 | 171-566 | 2584.8939 | 2243.5534 | 1873.0193 | 0 | 0 | 0 | 2584.8939 | 2243.5534 | 1873.0193 | 0 | 7.6405 | 6.6316 | 5.5363 | 0 | 0 | 0 | 7.6405 | 6.6316 | 5.5363 | 0 | 506.5831 | 439.6878 | 367.0711 | 0 | 0 | 0 | 506.5831 | 439.6878 | 367.0711 | 0 | 2070.6703 | 1797.234 | 1500.4119 | 0 | 0 | 0 | 2070.6703 | 1797.234 | 1500.4119 | 0 | 0 | 0 | 0 | 0.024557 | 0.024557 | 0.024557 | 0 | 5000000 | scaled
171-567 | 70655.3623 | 40358.6227 | 27428.3915 | 2868.3481 | 57.12% | 38.82% | 4.06% | 34958.6382 | 65477.3259 | 2491.7904 | 12943.4894 | 19523.3584 | 4405.4018 | 26326.0021 | 34745.9221 | 171 |  | 271 | 171-567 | 70655.3623 | 35696.7241 | 5178.0364 | 40358.6227 | 17604.1263 | 323.1181 | 27428.3915 | 15224.2496 | 1986.5702 | 2868.3481 | 4445.8028 | 1954.0123 | 40.401 | 4409.967 | 1933.1612 | 35.8035 | 33.6774 | 18.6928 | 2.4392 | 2.1583 | 35442.0941 | 15918.7357 | 696.1721 | 32632.5151 | 14243.3303 | 250.9904 | 2549.0163 | 1414.8427 | 184.6189 | 260.5627 | 30767.4654 | 17823.976 | 4441.4634 | 3316.1406 | 1427.6349 | 36.3241 | 24845.6977 | 13790.7141 | 1799.5121 | 2605.6271 | 0.012622 | 0.0054962 | 0.0001396 | 0.024545 | 0.01395 | 0.0024546 | 0.0040366 | 5000000 | scaled
171-568 | 31078.0959 | 18653.1841 | 10951.6001 | 1473.3118 | 60.02% | 35.24% | 4.741% | 16157.2649 | 28744.0635 | 1210.4589 | 4825.838 | 10120.968 | 2021.1752 | 9813.1413 | 16909.7469 | 171 |  | 272 | 171-568 | 31078.0959 | 14920.831 | 2334.0325 | 18653.1841 | 7365.68 | 67.6224 | 10951.6001 | 6081.8392 | 793.0983 | 1473.3118 | 2031.9911 | 821.5323 | 10.8159 | 2003.5519 | 805.2459 | 7.7281 | 27.3306 | 15.1777 | 1.9792 | 1.1086 | 17212.9215 | 7091.9535 | 303.1746 | 15393.2656 | 6021.9174 | 47.2535 | 1685.8193 | 936.1994 | 122.0845 | 133.8366 | 11833.1833 | 7007.3453 | 2020.0419 | 1256.3665 | 538.5167 | 12.6409 | 9238.4502 | 5130.4621 | 669.0346 | 1338.3665 | 0.0058784 | 0.0025452 | 6.46e-05 | 0.024582 | 0.013975 | 0.0024582 | 0.0020906 | 5000000 | scaled
171-667F | 237.4698 | 0 | 237.4698 | 0 | 0% | 100% | 0% | 31.4439 | 65.647 | 0.020651 | 24.9306 | 6.4927 | 0.043114 | 52.0488 | 13.5551 | 171 |  | 273 | 171-667F | 237.4698 | 206.0259 | 171.8228 | 0 | 0 | 0 | 237.4698 | 206.0259 | 171.8228 | 0 | 0.15596 | 0.13531 | 0.11285 | 0 | 0 | 0 | 0.15596 | 0.13531 | 0.11285 | 0 | 49.0339 | 42.5412 | 35.4788 | 0 | 0 | 0 | 49.0339 | 42.5412 | 35.4788 | 0 | 188.28 | 163.3494 | 136.2312 | 0 | 0 | 0 | 188.28 | 163.3494 | 136.2312 | 0 | 0 | 0 | 0 | 0.024527 | 0.024527 | 0.024527 | 0 | 5000000 | scaled
171-6R | 40340.4278 | 21901.327 | 16616.919 | 1822.1818 | 54.29% | 41.19% | 4.517% | 20640.2244 | 37150.3954 | 1475.3173 | 6914.6281 | 12250.279 | 2444.8971 | 14394.9428 | 20310.5556 | 171 |  | 274 | 171-6R | 40340.4278 | 19700.2033 | 3190.0324 | 21901.327 | 8639.2521 | 165.8294 | 16616.919 | 9238.7694 | 1202.0212 | 1822.1818 | 2467.1782 | 991.8609 | 22.2811 | 2446.3237 | 979.6573 | 19.5006 | 19.4834 | 10.8325 | 1.4094 | 1.3711 | 20717.6841 | 8467.4051 | 407.1286 | 19196.3566 | 7548.0718 | 143.5256 | 1355.7993 | 753.8051 | 98.0747 | 165.5282 | 17155.5655 | 10240.9374 | 2760.6227 | 258.6468 | 111.523 | 2.8032 | 15241.6363 | 8474.1319 | 1102.5371 | 1655.2824 | 0.0093526 | 0.0040498 | 0.0001026 | 0.024507 | 0.01395 | 0.0024506 | 0.0025782 | 5000000 | scaled
171-704R | 80614.2651 | 49460.6306 | 27655.316 | 3498.3185 | 61.35% | 34.31% | 4.34% | 41475.5305 | 74478.6749 | 2979.6063 | 11541.9972 | 26953.927 | 5014.9049 | 23897.3617 | 45566.4083 | 171 |  | 275 | 171-704R | 80614.2651 | 39138.7346 | 6135.5902 | 49460.6306 | 20271.2091 | 636.972 | 27655.316 | 15369.207 | 2000.2996 | 3498.3185 | 5088.2916 | 2108.6854 | 73.3868 | 5028.6293 | 2074.3591 | 66.6294 | 57.03 | 31.6939 | 4.125 | 2.6324 | 46657.1581 | 19703.231 | 1090.7497 | 43383.6444 | 17742.8228 | 559.1736 | 2955.7241 | 1642.6185 | 213.7865 | 317.7896 | 28868.8154 | 17326.8182 | 4971.4536 | 1048.357 | 454.0272 | 11.169 | 24642.5619 | 13694.8945 | 1782.3882 | 3177.8965 | 0.018668 | 0.0080828 | 0.000205 | 0.024497 | 0.013937 | 0.0024496 | 0.004923 | 5000000 | scaled
171-708R | 144381.4552 | 92868.3854 | 43163.8452 | 8349.2246 | 64.32% | 29.9% | 5.783% | 70842.5817 | 132086.5349 | 5552.1552 | 18878.2865 | 46412.14 | 9842.0972 | 38918.1104 | 83326.3273 | 171 |  | 276 | 171-708R | 144381.4552 | 73538.8735 | 12294.9203 | 92868.3854 | 41217.7277 | 824.9291 | 43163.8452 | 23971.9212 | 3120.7666 | 8349.2246 | 9942.386 | 4390.2308 | 100.2889 | 9877.2689 | 4351.2733 | 89.7526 | 58.8346 | 32.675 | 4.2538 | 6.2825 | 85069.0957 | 38656.9557 | 1742.7684 | 80477.3517 | 35769.6081 | 707.1701 | 3833.2947 | 2128.8983 | 277.149 | 758.4493 | 49369.9735 | 30491.6869 | 10451.8631 | 2513.7648 | 1096.8463 | 28.0065 | 39271.7159 | 21810.3479 | 2839.3638 | 7584.4928 | 0.048082 | 0.021161 | 0.0005378 | 0.024461 | 0.013908 | 0.0024462 | 0.011783 | 5000000 | scaled
172-567R | 141921.9139 | 88263.1825 | 46516.0801 | 7142.6512 | 62.19% | 32.78% | 5.033% | 66711.4133 | 130101.2243 | 5094.4612 | 20892.3029 | 40724.6492 | 9609.0733 | 43197.9238 | 77294.2272 | 172 |  | 277 | 172-567R | 141921.9139 | 75210.5006 | 11820.6896 | 88263.1825 | 42257.5751 | 1315.7535 | 46516.0801 | 25810.2742 | 3362.2848 | 7142.6512 | 9761.5118 | 4667.0506 | 152.4385 | 9697.5369 | 4629.1606 | 142.8281 | 58.6002 | 32.5154 | 4.2358 | 5.3746 | 79350.1684 | 38625.5192 | 2055.9412 | 74840.5929 | 35834.48 | 1128.0357 | 3860.7322 | 2142.1959 | 279.0622 | 648.8433 | 52810.2336 | 31917.9307 | 9612.3099 | 3725.0527 | 1793.9345 | 44.8898 | 42596.7476 | 23635.5629 | 3078.9868 | 6488.4333 | 0.035018 | 0.017116 | 0.0004332 | 0.024426 | 0.013876 | 0.0024426 | 0.010111 | 5000000 | scaled
172-569R | 174580.6003 | 122593.6417 | 41586.5453 | 10400.4134 | 70.22% | 23.82% | 5.957% | 82133.5583 | 159549.4953 | 7417.2111 | 22392.1053 | 52324.2419 | 13994.5012 | 47037.0535 | 98517.9407 | 172 |  | 278 | 172-569R | 174580.6003 | 92447.042 | 15031.105 | 122593.6417 | 58954.9632 | 1625.4889 | 41586.5453 | 23091.6655 | 3005.2027 | 10400.4134 | 14192.3793 | 6775.1682 | 197.8782 | 14130.9003 | 6737.5504 | 186.175 | 53.653 | 29.7918 | 3.8772 | 7.826 | 101054.2168 | 48729.9749 | 2536.2761 | 95562.2508 | 45260.2891 | 1262.8984 | 4547.1853 | 2524.9051 | 328.597 | 944.7807 | 59334.0042 | 36941.8988 | 12296.9507 | 12900.4905 | 6957.1236 | 176.4154 | 36985.7069 | 20536.9685 | 2672.7286 | 9447.8067 | 0.08953 | 0.043867 | 0.0011146 | 0.024426 | 0.013885 | 0.0024426 | 0.014699 | 5000000 | scaled
172-615R | 65021.1187 | 20405.3685 | 41059.6642 | 3556.086 | 31.38% | 63.15% | 5.469% | 29263.9087 | 58276.8445 | 405.0321 | 24943.8905 | 3914.9861 | 747.1345 | 49911.7465 | 7617.9634 | 172 |  | 279 | 172-615R | 65021.1187 | 35757.21 | 6744.2742 | 20405.3685 | 9408.8458 | 220.6162 | 41059.6642 | 22792.2781 | 2967.572 | 3556.086 | 760.2103 | 355.1782 | 13.0758 | 705.7109 | 323.735 | 6.6544 | 51.8236 | 28.7674 | 3.7455 | 2.6758 | 8267.0914 | 4352.1052 | 649.1279 | 3948.1719 | 1810.948 | 37.2897 | 3995.8822 | 2218.1199 | 288.8009 | 323.0373 | 55993.817 | 31049.9265 | 6082.0705 | 15751.4857 | 7274.1628 | 176.672 | 37011.9584 | 20545.3909 | 2675.0256 | 3230.3729 | 0.024124 | 0.010853 | 0.0002758 | 0.024442 | 0.013891 | 0.0024442 | 0.0050134 | 5000000 | scaled
172-630R | 66310.7427 | 4322.9071 | 60000.3608 | 1987.4749 | 6.519% | 90.48% | 2.997% | 28912.8887 | 59940.6438 | 273.866 | 24284.4819 | 4354.5408 | 518.218 | 50643.3189 | 8779.1068 | 172 |  | 280 | 172-630R | 66310.7427 | 37397.854 | 6370.099 | 4322.9071 | 2089.9555 | 48.3697 | 60000.3608 | 33320.4237 | 4334.2544 | 1987.4749 | 530.4647 | 256.5986 | 12.2466 | 455.715 | 214.4224 | 5.4595 | 73.2541 | 40.6807 | 5.2917 | 1.4955 | 9396.8351 | 5042.2944 | 617.7283 | 3739.6579 | 1820.3732 | 41.5684 | 5476.6336 | 3041.3776 | 395.6163 | 180.5436 | 56383.4429 | 32098.961 | 5740.124 | 127.5341 | 55.1599 | 1.3418 | 54450.473 | 30238.3654 | 3933.3464 | 1805.4358 | 0.025913 | 0.012932 | 0.000329 | 0.024419 | 0.013884 | 0.002442 | 0.0028048 | 5000000 | scaled
175-2024R | 4029008.4568 | 3992843.5947 | 32825.1404 | 3339.7217 | 99.1% | 0.8147% | 0.08289% | 1685731.7347 | 3957978.8402 | 173854.4943 | 12388.0264 | 1499489.2139 | 408261.847 | 26985.7973 | 3522731.1959 | 175 |  | 281 | 175-2024R | 4029008.4568 | 2343276.7222 | 71029.6166 | 3992843.5947 | 2321358.1742 | 64627.8143 | 32825.1404 | 18578.8263 | 3062.0806 | 3339.7217 | 414998.5177 | 241144.0233 | 6736.6707 | 414958.3538 | 241120.2002 | 6730.6454 | 37.6508 | 21.3101 | 3.5122 | 2.513 | 3581417.5481 | 2081928.3342 | 58686.3523 | 3575405.3172 | 2078393.7788 | 57850.4219 | 5708.8483 | 3231.1728 | 532.5477 | 303.3826 | 32592.391 | 20204.3646 | 5606.5937 | 2479.9236 | 1844.1952 | 46.747 | 27078.6413 | 15326.3434 | 2526.0207 | 3033.8261 | 0.023973 | 0.013438 | 0.0003424 | 0.16247 | 0.092481 | 0.016247 | 0.0046958 | 5000000 | scaled
175-24R | 2651435.357 | 1873250.8015 | 775363.8159 | 2820.7395 | 70.65% | 29.24% | 0.1064% | 1099627.188 | 2547696.6693 | 86730.0008 | 310271.6155 | 702625.5718 | 210043.5052 | 653150.2393 | 1684502.9248 | 175 |  | 282 | 175-24R | 2651435.357 | 1551808.1689 | 103738.6877 | 1873250.8015 | 1110595.0312 | 28785.2177 | 775363.8159 | 438392.3982 | 72132.7304 | 2820.7395 | 213405.8385 | 126675.8377 | 3362.3333 | 212329.0142 | 126066.0765 | 3260.2304 | 1074.7017 | 607.6387 | 99.9804 | 2.1225 | 1716387.4918 | 1013761.9201 | 31884.5671 | 1647927.0945 | 974942.9011 | 25283.2404 | 68204.1595 | 38562.781 | 6345.0888 | 256.2379 | 721642.0266 | 411370.4112 | 68491.7873 | 12994.6928 | 9586.0536 | 241.747 | 706084.9547 | 399221.9784 | 65687.6613 | 2562.3791 | 0.01588 | 0.0093882 | 0.0002374 | 0.15504 | 0.088179 | 0.015504 | 0.0039928 | 5000000 | scaled
175-64R | 4385400.4311 | 4276794.127 | 101222.6408 | 7383.6633 | 97.52% | 2.308% | 0.1684% | 1885194.6063 | 4316821.6997 | 129895.9353 | 38882.1872 | 1716416.4837 | 297774.0882 | 81450.5569 | 3937597.0545 | 175 |  | 283 | 175-64R | 4385400.4311 | 2500205.8248 | 68578.7314 | 4276794.127 | 2435526.4975 | 51762.6179 | 101222.6408 | 57295.664 | 9432.4503 | 7383.6633 | 301509.089 | 171613.1536 | 3735.0007 | 301326.0503 | 171507.136 | 3712.906 | 177.4827 | 100.4616 | 16.5388 | 5.556 | 3987462.7829 | 2271046.2991 | 49865.7284 | 3974309.1977 | 2263309.8201 | 48031.7749 | 12482.8481 | 7065.7421 | 1163.2165 | 670.737 | 96428.5592 | 57546.372 | 14978.0023 | 1158.879 | 709.5414 | 17.937 | 88562.31 | 50129.4604 | 8252.695 | 6707.3703 | 0.032071 | 0.017997 | 0.0004582 | 0.15981 | 0.090991 | 0.015981 | 0.01044 | 5000000 | scaled
175-90R | 5741494.8572 | 5561271.4512 | 171774.1421 | 8449.2639 | 96.86% | 2.992% | 0.1472% | 1692965.8342 | 5608118.2188 | 96079.8272 | 65491.7672 | 1531394.2399 | 322420.7418 | 138454.2134 | 5147243.2636 | 175 |  | 284 | 175-90R | 5741494.8572 | 4048529.023 | 133376.6384 | 5561271.4512 | 3942846.156 | 108931.6188 | 171774.1421 | 97233.6031 | 15995.7557 | 8449.2639 | 328814.1049 | 232734.2777 | 6393.3631 | 328529.551 | 232570.4457 | 6361.0994 | 278.196 | 157.4742 | 25.9059 | 6.3578 | 5252606.5155 | 3721212.2756 | 105363.2519 | 5229399.3971 | 3707742.7026 | 102506.1219 | 22439.5814 | 12702.0361 | 2089.5931 | 767.5369 | 160074.2368 | 94582.4697 | 21620.0234 | 3342.5031 | 2533.0077 | 64.3975 | 149056.3646 | 84374.0927 | 13880.2567 | 7675.3692 | 0.03489 | 0.024301 | 0.0006176 | 0.15822 | 0.090088 | 0.015822 | 0.011806 | 5000000 | scaled
175-94R | 836245.7431 | 666976.4591 | 167975.653 | 1293.631 | 79.76% | 20.09% | 0.1547% | 351173.3196 | 805747.7126 | 19773.0039 | 65331.4277 | 266068.888 | 46878.2332 | 137730.6395 | 621138.84 | 175 |  | 285 | 175-94R | 836245.7431 | 485072.4235 | 30498.0305 | 666976.4591 | 388709.7003 | 13568.7594 | 167975.653 | 95069.0922 | 15635.6401 | 1293.631 | 47859.6611 | 28086.6572 | 981.4279 | 47596.7084 | 27937.4115 | 956.0687 | 261.9793 | 148.2723 | 24.3858 | 0.97342 | 635543.8558 | 369474.9679 | 14405.0159 | 616932.5417 | 358890.5273 | 12566.0473 | 18493.7998 | 10466.9262 | 1721.4542 | 117.5143 | 152842.2262 | 87510.7985 | 15111.5867 | 2447.209 | 1881.7614 | 46.6433 | 149219.8739 | 84453.8938 | 13889.8001 | 1175.1433 | 0.0063844 | 0.00378 | 9.6e-05 | 0.15732 | 0.089566 | 0.015732 | 0.0018426 | 5000000 | scaled
176-161R | 11523304.9395 | 11381448.7362 | 135086.7031 | 6769.5001 | 98.77% | 1.172% | 0.05875% | 4816703.6056 | 11315353.5626 | 267833.2013 | 58958.1962 | 4489912.2082 | 630964.3031 | 127416.1462 | 10556973.1133 | 176 |  | 286 | 176-161R | 11523304.9395 | 6706601.3338 | 207951.3768 | 11381448.7362 | 6623475.4011 | 188503.548 | 135086.7031 | 76356.4327 | 12678.3288 | 6769.5001 | 641431.2124 | 373598.0111 | 10466.9093 | 641100.2468 | 373408.7214 | 10431.2313 | 325.8717 | 184.1958 | 30.5841 | 5.0938 | 10736730.1706 | 6246817.9624 | 179757.0572 | 10721412.3949 | 6237892.3863 | 177762.2026 | 14702.8297 | 8310.6301 | 1379.9086 | 614.946 | 145143.5565 | 86185.3604 | 17727.4103 | 18936.0946 | 12174.2934 | 310.1141 | 120058.0018 | 67861.6068 | 11267.836 | 6149.4602 | 0.033477 | 0.019537 | 0.000496 | 0.18118 | 0.10294 | 0.018118 | 0.0095082 | 5000000 | scaled
176-164R | 4184746.7473 | 4105075.4627 | 75288.4941 | 4382.7905 | 98.1% | 1.799% | 0.1047% | 1729576.5025 | 4132066.8188 | 97211.6013 | 28687.8605 | 1603677.0408 | 232976.7374 | 60140.7996 | 3838949.2818 | 176 |  | 287 | 176-164R | 4184746.7473 | 2455170.2448 | 52679.9286 | 4105075.4627 | 2408229.5166 | 41231.3088 | 75288.4941 | 42557.9377 | 7065.8292 | 4382.7905 | 235403.8232 | 138192.222 | 2427.0858 | 235328.5482 | 138148.2379 | 2417.0329 | 71.9771 | 40.6861 | 6.7551 | 3.2979 | 3879063.7008 | 2275386.66 | 40114.419 | 3868887.2981 | 2269461.2139 | 38798.5924 | 9778.267 | 5527.3104 | 917.6909 | 398.1357 | 70279.2233 | 41591.3628 | 10138.4238 | 859.6164 | 620.0647 | 15.6835 | 65438.25 | 36989.9412 | 6141.3833 | 3981.3569 | 0.019734 | 0.01187 | 0.000301 | 0.18132 | 0.10302 | 0.018131 | 0.0062214 | 5000000 | scaled
176-1834R | 10068516.8214 | 9779526.9047 | 280260.2381 | 8729.6787 | 97.13% | 2.784% | 0.0867% | 2679403.4824 | 9873015.5625 | 220239.2783 | 120786.0307 | 2338378.1733 | 826655.7343 | 255869.2638 | 8790490.5644 | 176 |  | 288 | 176-1834R | 10068516.8214 | 7389113.339 | 195501.2589 | 9779526.9047 | 7222011.7842 | 160493.822 | 280260.2381 | 158371.8762 | 26277.7582 | 8729.6787 | 840562.3465 | 620323.0682 | 13906.6123 | 840161.5335 | 620093.7165 | 13863.0785 | 394.2444 | 222.783 | 36.9651 | 6.5686 | 8940036.4473 | 6601658.2739 | 149545.8829 | 8912157.8668 | 6585559.5235 | 146213.2919 | 27085.5883 | 15305.7582 | 2539.5987 | 792.9922 | 287918.0276 | 167131.9969 | 32048.7638 | 27207.5044 | 16358.5441 | 417.4516 | 252780.4054 | 142843.335 | 23701.1944 | 7930.1178 | 0.041194 | 0.030109 | 0.000764 | 0.1786 | 0.10145 | 0.01786 | 0.012255 | 5000000 | scaled
176-1836R | 404481.7118 | 273583.5311 | 129928.3705 | 969.8102 | 67.64% | 32.12% | 0.2398% | 181253.6216 | 386944.0853 | 11475.8839 | 53698.741 | 116078.9966 | 25022.3852 | 113810.782 | 248110.9181 | 176 |  | 289 | 176-1836R | 404481.7118 | 223228.0902 | 17537.6265 | 273583.5311 | 149203.5662 | 4918.9673 | 129928.3705 | 73054.7138 | 11648.849 | 969.8102 | 25490.8458 | 14014.9619 | 468.4606 | 25328.349 | 13923.2755 | 453.2275 | 161.7671 | 90.9567 | 14.5034 | 0.72975 | 253589.2765 | 137510.2799 | 5478.3584 | 242035.9864 | 130975.658 | 4362.3377 | 11465.1919 | 6446.5237 | 1027.9225 | 88.0982 | 125401.5894 | 71702.8484 | 11590.8074 | 6219.1958 | 4304.6327 | 103.402 | 118301.4114 | 66517.2335 | 10606.4232 | 880.9822 | 0.003945 | 0.0025354 | 6.4e-05 | 0.10106 | 0.05733 | 0.010106 | 0.0013708 | 5000000 | scaled
176-1845R | 3401023.3781 | 3324151.4369 | 71858.0781 | 5013.863 | 97.74% | 2.113% | 0.1474% | 1385246.4847 | 3324537.5636 | 80229.8615 | 28019.7302 | 1276996.893 | 193215.2099 | 58573.7016 | 3072748.6522 | 176 |  | 290 | 176-1845R | 3401023.3781 | 2015776.8933 | 76485.8144 | 3324151.4369 | 1970133.8293 | 64730.6483 | 71858.0781 | 40629.201 | 6741.3031 | 5013.863 | 196911.2589 | 116681.3974 | 3696.0491 | 196816.2584 | 116626.0437 | 3683.7178 | 91.2277 | 51.581 | 8.5584 | 3.7728 | 3134957.2783 | 1857960.3853 | 62208.6261 | 3126890.3785 | 1853201.3478 | 61039.103 | 7611.4371 | 4303.5747 | 714.0603 | 455.4627 | 69154.8409 | 41135.1106 | 10581.1393 | 444.8 | 306.4378 | 7.8275 | 64155.4134 | 36274.0454 | 6018.6843 | 4554.6275 | 0.022022 | 0.013357 | 0.0003396 | 0.18066 | 0.10268 | 0.018066 | 0.0070988 | 5000000 | scaled
176-194R | 4934160.3361 | 4820768.4196 | 107488.4773 | 5903.4392 | 97.7% | 2.178% | 0.1196% | 1530561.5342 | 4808594.4369 | 87125.0365 | 41369.3134 | 1402067.1842 | 277323.5761 | 87177.634 | 4444093.2268 | 176 |  | 291 | 176-194R | 4934160.3361 | 3403598.8019 | 125565.8992 | 4820768.4196 | 3336909.9132 | 109580.8216 | 107488.4773 | 60785.4495 | 10081.6384 | 5903.4392 | 283683.2596 | 196558.2231 | 6359.6835 | 283469.3547 | 196435.3283 | 6335.5952 | 209.4628 | 118.4526 | 19.6461 | 4.4421 | 4549003.6859 | 3146936.5017 | 104910.4591 | 4536148.4711 | 3139433.7853 | 103218.7594 | 12318.9423 | 6966.4439 | 1155.4273 | 536.2725 | 101473.3906 | 60104.0772 | 14295.7566 | 1150.5939 | 1040.7996 | 26.467 | 94960.0722 | 53700.553 | 8906.565 | 5362.7246 | 0.026897 | 0.018697 | 0.0004752 | 0.18022 | 0.10245 | 0.018022 | 0.0082982 | 5000000 | scaled
176-197F | 13172958.0173 | 12751842.4782 | 411525.6854 | 9589.8537 | 96.8% | 3.124% | 0.0728% | 4742072.9967 | 12927174.2609 | 449706.3668 | 164333.5122 | 4128033.1177 | 1238815.4496 | 345378.0965 | 11342980.7148 | 176 |  | 292 | 176-197F | 13172958.0173 | 8430885.0207 | 245783.7565 | 12751842.4782 | 8188517.3617 | 197635.5062 | 411525.6854 | 232777.8052 | 38558.3965 | 9589.8537 | 1258478.5952 | 808772.2284 | 19663.1456 | 1257764.3104 | 808365.0618 | 19589.6799 | 707.0687 | 399.9505 | 66.2497 | 7.2161 | 11525406.69 | 7397373.5722 | 182425.9751 | 11485530.1591 | 7374439.1901 | 177900.1699 | 39005.3819 | 22063.2333 | 3654.6564 | 871.1489 | 389072.7322 | 224739.2201 | 43694.6357 | 8548.0087 | 5713.1098 | 145.6565 | 371813.2348 | 210314.6214 | 34837.4904 | 8711.4888 | 0.042242 | 0.027034 | 0.0006882 | 0.17673 | 0.1005 | 0.017673 | 0.013442 | 5000000 | scaled
176-200F | 1635841.0079 | 1459888.3134 | 175047.2729 | 905.4216 | 89.24% | 10.7% | 0.05535% | 480036.5814 | 1591512.9788 | 22683.6557 | 69366.028 | 387986.8977 | 80497.7247 | 144854.8692 | 1366160.3849 | 176 |  | 293 | 176-200F | 1635841.0079 | 1155804.4265 | 44328.029 | 1459888.3134 | 1055820.2417 | 27006.8429 | 175047.2729 | 99078.7631 | 16415.7645 | 905.4216 | 82060.2112 | 59376.5555 | 1562.4865 | 81815.9419 | 59238.0006 | 1538.9617 | 243.588 | 137.8736 | 22.8434 | 0.6813 | 1393115.2561 | 1005128.3584 | 26954.8712 | 1378049.1012 | 996565.0469 | 25467.4458 | 14983.9058 | 8481.0624 | 1405.1762 | 82.2491 | 160665.5406 | 91299.5125 | 15810.6714 | 23.2702 | 17.1942 | 0.43538 | 159819.7791 | 90459.8271 | 14987.7448 | 822.4912 | 0.0040796 | 0.0029024 | 7.36e-05 | 0.17994 | 0.10238 | 0.017994 | 0.0012764 | 5000000 | scaled
177-941AE | 569509.132 | 565012.4521 | 0 | 4496.6799 | 99.21% | 0% | 0.7896% | 231246.4489 | 557808.944 | 28677.9477 | 1698.5617 | 200869.9395 | 68297.3768 | 5297.5789 | 484213.9882 | 177 |  | 294 | 177-941AE | 569509.132 | 338262.6832 | 11700.1881 | 565012.4521 | 333766.0032 | 7203.5081 | 0 | 0 | 0 | 4496.6799 | 69196.046 | 40518.0984 | 898.6692 | 69192.6624 | 40514.7147 | 895.2856 | 0 | 0 | 0 | 3.3836 | 490837.0912 | 289967.1517 | 6623.1031 | 490428.6097 | 289558.6703 | 6214.6216 | 0 | 0 | 0 | 408.4815 | 9475.9948 | 7777.4331 | 4178.4158 | 5391.1799 | 3692.6182 | 93.601 | 0 | 0 | 0 | 4084.8148 | 0.018956 | 0.010311 | 0.0002622 | 0 | 0 | 0 | 0.0063394 | 5000000 | scaled
177-955 | 2963405.8552 | 2318246.7809 | 641882.4257 | 3276.6486 | 78.23% | 21.66% | 0.1106% | 1533150.7938 | 2878693.0665 | 149601.4012 | 254865.3584 | 1128684.0343 | 274116.5758 | 529996.816 | 2074579.6747 | 177 |  | 295 | 177-955 | 2963405.8552 | 1430255.0614 | 84712.7888 | 2318246.7809 | 1066121.2075 | 24011.3456 | 641882.4257 | 360857.2053 | 57424.7946 | 3276.6486 | 277063.1141 | 127461.7129 | 2946.5382 | 275970.387 | 126846.3178 | 2846.5345 | 1090.2615 | 612.9296 | 97.5382 | 2.4656 | 2101322.2143 | 972638.18 | 26742.5396 | 2041966.4999 | 939138.9217 | 21161.3691 | 59058.0613 | 33201.6053 | 5283.5175 | 297.653 | 585020.5269 | 330155.1685 | 55023.7109 | 309.894 | 135.9681 | 3.4421 | 581734.1029 | 327042.6704 | 52043.7389 | 2976.53 | 0.014615 | 0.0065842 | 0.0001668 | 0.098029 | 0.055608 | 0.009803 | 0.004614 | 5000000 | scaled
178-48 | 2395.0613 | 2189.6102 | 0 | 205.451 | 91.42% | 0% | 8.578% | 690.5396 | 2189.5436 | 60.7592 | 4.3316 | 625.4489 | 187.2239 | 7.5326 | 1994.7871 | 178 |  | 296 | 178-48 | 2395.0613 | 1704.5217 | 205.5177 | 2189.6102 | 1499.0706 | 0.066628 | 0 | 0 | 0 | 205.451 | 187.3785 | 126.6193 | 0.1546 | 187.2239 | 126.4647 | 0 | 0 | 0 | 0 | 0.1546 | 2013.4504 | 1388.0015 | 18.6633 | 1994.7871 | 1369.3382 | 0 | 0 | 0 | 0 | 18.6633 | 194.2324 | 189.9008 | 186.6998 | 7.5992 | 3.2676 | 0.066628 | 0 | 0 | 0 | 186.6331 | 0.0005136 | 0.0002224 | 5.8e-06 | 0 | 0 | 0 | 0.000305 | 5000000 | scaled
178-968AE | 47610.602 | 43426.331 | 0 | 4184.2709 | 91.21% | 0% | 8.789% | 17874.1602 | 43317.8708 | 1694.8796 | 6222.4647 | 9956.8159 | 4259.0462 | 10853.4525 | 28205.3722 | 178 |  | 297 | 178-968AE | 47610.602 | 29736.4417 | 4292.7311 | 43426.331 | 25552.1708 | 108.4602 | 0 | 0 | 0 | 4184.2709 | 4271.3505 | 2576.4709 | 12.3043 | 4268.202 | 2573.3224 | 9.1558 | 0 | 0 | 0 | 3.1485 | 28624.6151 | 18667.7992 | 419.243 | 28244.5131 | 18287.6972 | 39.1409 | 0 | 0 | 0 | 380.102 | 14714.6363 | 8492.1716 | 3861.1838 | 10913.6159 | 4691.1512 | 60.1635 | 0 | 0 | 0 | 3801.0204 | 0.012615 | 0.0055994 | 0.000143 | 0 | 0 | 0 | 0.0058514 | 5000000 | scaled
178-982 | 954.789 | 127.7852 | 0 | 827.0038 | 13.38% | 0% | 86.62% | 71.7552 | 126.4359 | 0.67732 | 68.6903 | 2.3876 | 1.464 | 119.8129 | 5.159 | 178 |  | 298 | 178-982 | 954.789 | 883.0338 | 828.353 | 127.7852 | 56.03 | 1.3492 | 0 | 0 | 0 | 827.0038 | 2.0863 | 1.409 | 0.62229 | 1.464 | 0.78669 | 0 | 0 | 0 | 0 | 0.62229 | 80.2846 | 77.897 | 75.1256 | 5.159 | 2.7714 | 0 | 0 | 0 | 0 | 75.1256 | 872.418 | 803.7278 | 752.6052 | 121.1621 | 52.4719 | 1.3492 | 0 | 0 | 0 | 751.2559 | 0.0021782 | 0.0009432 | 2.4e-05 | 0 | 0 | 0 | 0.0011672 | 5000000 | scaled
178-983AE | 24306.4971 | 24141.654 | 0 | 164.8432 | 99.32% | 0% | 0.6782% | 16249.329 | 24119.5666 | 1075.4674 | 2.6822 | 15171.1794 | 1613.5325 | 4.6762 | 22501.3579 | 178 |  | 299 | 178-983AE | 24306.4971 | 8057.1682 | 186.9306 | 24141.654 | 7892.325 | 22.0874 | 0 | 0 | 0 | 164.8432 | 1616.1263 | 540.6589 | 2.5938 | 1616.0022 | 540.5349 | 2.4698 | 0 | 0 | 0 | 0.12404 | 22535.9033 | 7364.7239 | 34.5454 | 22520.9288 | 7349.7494 | 19.5709 | 0 | 0 | 0 | 14.9745 | 154.4676 | 151.7854 | 149.7914 | 4.7229 | 2.0408 | 0.046716 | 0 | 0 | 0 | 149.7447 | 0.000622 | 0.0002692 | 6.8e-06 | 0 | 0 | 0 | 0.000228 | 5000000 | scaled
180-1156 | 1321.9335 | 688.451 | 0 | 633.4825 | 52.08% | 0% | 47.92% | 445.9276 | 686.1942 | 53.7111 | 55.5929 | 336.6236 | 76.0226 | 150.6505 | 459.5211 | 180 |  | 300 | 180-1156 | 1321.9335 | 876.006 | 635.7394 | 688.451 | 242.5235 | 2.2569 | 0 | 0 | 0 | 633.4825 | 76.5252 | 22.8141 | 0.50269 | 76.0486 | 22.3374 | 0.026012 | 0 | 0 | 0 | 0.47668 | 517.1999 | 180.5763 | 57.6788 | 459.6539 | 123.0303 | 0.1328 | 0 | 0 | 0 | 57.546 | 728.2084 | 672.6155 | 577.5579 | 152.7486 | 97.1557 | 2.098 | 0 | 0 | 0 | 575.4598 | 0.001951 | 0.001014 | 2.6e-05 | 0 | 0 | 0 | 0.000899 | 5000000 | scaled
180-13 | 4684.3077 | 3891.8824 | 0 | 792.4253 | 83.08% | 0% | 16.92% | 2264.8994 | 3849.8351 | 250.754 | 384.6732 | 1629.4723 | 424.2721 | 711.5791 | 2713.9839 | 180 |  | 301 | 180-13 | 4684.3077 | 2419.4083 | 834.4725 | 3891.8824 | 1626.983 | 42.0473 | 0 | 0 | 0 | 792.4253 | 429.6472 | 178.8933 | 5.3751 | 429.051 | 178.297 | 4.7789 | 0 | 0 | 0 | 0.59627 | 2815.0654 | 1185.5931 | 101.0815 | 2743.081 | 1113.6087 | 29.097 | 0 | 0 | 0 | 71.9845 | 1439.595 | 1054.9218 | 728.0159 | 719.7505 | 335.0773 | 8.1714 | 0 | 0 | 0 | 719.8446 | 0.0024814 | 0.0011042 | 2.78e-05 | 0 | 0 | 0 | 0.0011454 | 5000000 | scaled
181-49 | 64766.387 | 5259.6933 | 59258.4581 | 248.2355 | 8.121% | 91.5% | 0.3833% | 29322.497 | 59378.9302 | 230.0318 | 23803.3964 | 5289.0689 | 397.0086 | 49395.2135 | 9586.708 | 181 |  | 302 | 181-49 | 64766.387 | 35443.89 | 5387.4568 | 5259.6933 | 2013.4113 | 0.30612 | 59258.4581 | 33182.2431 | 5138.9151 | 248.2355 | 405.1391 | 175.1073 | 8.1305 | 313.3512 | 123.6278 | 0 | 91.6011 | 51.2928 | 7.9437 | 0.18679 | 10053.7609 | 4764.6921 | 467.0529 | 4905.5061 | 1871.9631 | 0 | 5125.7049 | 2870.1791 | 444.503 | 22.5499 | 54307.487 | 30504.0906 | 4912.2734 | 40.836 | 17.8204 | 0.30612 | 54041.1521 | 30260.7713 | 4686.4684 | 225.4989 | 0.0003466 | 0.0001738 | 4.6e-06 | 0.078148 | 0.044274 | 0.0078148 | 0.000357 | 5000000 | scaled
181-53F | 294622.8915 | 49952.934 | 243695.4369 | 974.5205 | 16.95% | 82.71% | 0.3308% | 115560.1685 | 272107.9617 | 682.6608 | 100257.7164 | 14619.7913 | 3267.0627 | 207362.7038 | 61478.1952 | 181 |  | 303 | 181-53F | 294622.8915 | 179062.723 | 22514.9297 | 49952.934 | 41607.8419 | 418.9869 | 243695.4369 | 136480.3605 | 21121.4223 | 974.5205 | 3326.6319 | 2643.9712 | 59.5693 | 2990.9136 | 2455.6313 | 29.8023 | 334.9851 | 187.6066 | 29.0336 | 0.7333 | 63717.2868 | 49097.4955 | 2239.0915 | 42840.8273 | 37366.7955 | 348.8463 | 20787.9333 | 11642.1738 | 1801.7191 | 88.5261 | 227578.9728 | 127321.2563 | 20216.2689 | 4121.1931 | 1785.4151 | 40.3382 | 222572.5185 | 124650.5801 | 19290.6696 | 885.2611 | 0.0026156 | 0.0012702 | 3.24e-05 | 0.077546 | 0.043936 | 0.0077546 | 0.0013656 | 5000000 | scaled
181-54F | 2723.6374 | 804.5027 | 1062.7067 | 856.4279 | 29.54% | 39.02% | 31.44% | 794.8123 | 1796.2902 | 32.6328 | 376.9783 | 385.2012 | 70.5448 | 788.2027 | 937.5428 | 181 |  | 304 | 181-54F | 2723.6374 | 1928.825 | 927.3471 | 804.5027 | 485.3025 | 0.054413 | 1062.7067 | 587.0946 | 70.8648 | 856.4279 | 71.3883 | 38.7555 | 0.84347 | 67.7591 | 36.4621 | 0 | 2.9847 | 1.6489 | 0.19903 | 0.64443 | 1029.9422 | 644.741 | 92.3995 | 733.1836 | 445.9776 | 0 | 218.9601 | 120.965 | 14.601 | 77.7985 | 1622.3069 | 1245.3285 | 834.1042 | 3.56 | 2.8629 | 0.054413 | 840.7619 | 464.4807 | 56.0648 | 777.985 | 0.0029286 | 0.001467 | 3.72e-05 | 0.014421 | 0.0081976 | 0.0014422 | 0.0012096 | 5000000 | scaled
182-2240F | 11917198.9064 | 11236831.9909 | 673429.9826 | 6936.9329 | 94.29% | 5.651% | 0.05821% | 3853560.7968 | 11693792.1911 | 675425.836 | 282854.3929 | 2895280.5679 | 2097095.2516 | 619695.7604 | 8977001.1792 | 182 |  | 305 | 182-2240F | 11917198.9064 | 8063638.1096 | 223406.7152 | 11236831.9909 | 7678108.5683 | 156288.69 | 673429.9826 | 378592.6084 | 60181.0923 | 6936.9329 | 2126949.5863 | 1451523.7504 | 29854.3347 | 2125995.8288 | 1450985.2764 | 29764.3488 | 948.5377 | 533.2542 | 84.7661 | 5.2198 | 9108544.0338 | 6213263.4659 | 131542.8546 | 9044469.1589 | 6176965.6056 | 125242.9595 | 63444.7191 | 35667.7046 | 5669.7394 | 630.1557 | 681705.2862 | 398850.8933 | 62009.5259 | 66367.0031 | 50157.6864 | 1281.3817 | 609036.7258 | 342391.6496 | 54426.5868 | 6301.5573 | 0.038653 | 0.025539 | 0.0006484 | 0.097041 | 0.055055 | 0.0097042 | 0.0098096 | 5000000 | scaled
182-2250 | 1939213.1723 | 1934190.4572 | 4123.3262 | 899.3889 | 99.74% | 0.2126% | 0.04638% | 1113891.1166 | 1919269.7839 | 57606.4038 | 1632.6222 | 1054652.0906 | 99047.1807 | 3388.0366 | 1816834.5666 | 182 |  | 306 | 182-2250 | 1939213.1723 | 825322.0558 | 19943.3884 | 1934190.4572 | 822106.4813 | 18675.0731 | 4123.3262 | 2316.1855 | 368.9264 | 899.3889 | 99984.4208 | 42378.017 | 937.2401 | 99978.6483 | 42374.4779 | 936.1074 | 5.0957 | 2.8624 | 0.45592 | 0.67676 | 1834693.1379 | 780041.0473 | 17858.5713 | 1834184.214 | 779719.3635 | 17738.6453 | 427.2228 | 239.9828 | 38.2249 | 81.7011 | 4535.6136 | 2902.9914 | 1147.577 | 27.5948 | 12.64 | 0.32039 | 3691.0077 | 2073.3404 | 330.2456 | 817.011 | 0.0045462 | 0.0020888 | 5.26e-05 | 0.099121 | 0.056181 | 0.009912 | 0.0012898 | 5000000 | scaled
182-2252R | 4229944.5723 | 4196758.1646 | 30693.8966 | 2492.511 | 99.22% | 0.7256% | 0.05893% | 2158076.0038 | 4157266.4309 | 114576.6817 | 12274.6483 | 2031224.6738 | 219801.2344 | 25437.7172 | 3912027.4793 | 182 |  | 307 | 182-2252R | 4229944.5723 | 2071868.5684 | 72678.1414 | 4196758.1646 | 2052143.8495 | 67440.1045 | 30693.8966 | 17232.2079 | 2745.5259 | 2492.511 | 223345.6764 | 108768.9947 | 3544.442 | 223301.1022 | 108743.1472 | 3538.7471 | 42.6987 | 23.972 | 3.8193 | 1.8755 | 3976423.4519 | 1945198.778 | 64395.9725 | 3973160.5298 | 1943267.6004 | 63897.9404 | 3036.5007 | 1704.7562 | 271.6107 | 226.4214 | 30175.444 | 17900.7957 | 4737.7268 | 296.5327 | 133.1019 | 3.417 | 27614.6973 | 15503.4798 | 2470.0958 | 2264.2141 | 0.010686 | 0.0050384 | 0.0001286 | 0.098852 | 0.055998 | 0.0098852 | 0.0035338 | 5000000 | scaled
182-2254R | 655800.9495 | 650138.7556 | 4993.8178 | 668.376 | 99.14% | 0.7615% | 0.1019% | 159824.3094 | 652644.7149 | 8821.083 | 1887.771 | 149115.4554 | 36021.768 | 3924.5185 | 612698.4284 | 182 |  | 308 | 182-2254R | 655800.9495 | 495976.6401 | 3156.2346 | 650138.7556 | 492503.7213 | 2041.183 | 4993.8178 | 2804.5428 | 446.6756 | 668.376 | 36152.2663 | 27331.1833 | 130.4984 | 36144.1416 | 27326.4 | 129.3137 | 7.6218 | 4.2804 | 0.68173 | 0.50293 | 614732.6959 | 465617.2405 | 2034.2676 | 613979.7169 | 465167.7477 | 1911.6318 | 692.2633 | 388.7771 | 61.92 | 60.7157 | 4915.9872 | 3028.2163 | 991.4687 | 14.8971 | 9.5736 | 0.23743 | 4293.9328 | 2411.4853 | 384.0739 | 607.1574 | 0.0024736 | 0.0017506 | 4.44e-05 | 0.09881 | 0.055989 | 0.009881 | 0.000943 | 5000000 | scaled
183-439 | 316477.7532 | 209604.2625 | 106028.0211 | 845.4696 | 66.23% | 33.5% | 0.2671% | 169027.24 | 301815.3686 | 7706.7237 | 43314.845 | 118005.6713 | 12980.489 | 90357.6491 | 198477.2306 | 183 |  | 309 | 183-439 | 316477.7532 | 147450.5132 | 14662.3846 | 209604.2625 | 88011.5001 | 6745.5975 | 106028.0211 | 58593.5435 | 7071.3175 | 845.4696 | 13367.7352 | 5661.0114 | 387.2462 | 13208.5183 | 5572.7399 | 376.0338 | 158.5807 | 87.6354 | 10.5762 | 0.63619 | 205528.9561 | 87523.2848 | 7051.7255 | 196371.1681 | 82428.1188 | 6369.2851 | 9080.985 | 5018.3629 | 605.6373 | 76.803 | 97581.062 | 54266.217 | 7223.4129 | 24.5762 | 10.6414 | 0.27851 | 96788.4554 | 53487.5452 | 6455.104 | 768.0304 | 0.0030348 | 0.0013146 | 3.38e-05 | 0.014224 | 0.0080878 | 0.0014224 | 0.001163 | 5000000 | scaled
183-440 | 471201.4781 | 350429.5219 | 118592.208 | 2179.7482 | 74.37% | 25.17% | 0.4626% | 234041.4586 | 458093.4842 | 11456.3262 | 48995.4383 | 173589.6941 | 21942.9242 | 102472.554 | 333678.006 | 183 |  | 310 | 183-440 | 471201.4781 | 237160.0195 | 13107.994 | 350429.5219 | 169334.2654 | 3020.3164 | 118592.208 | 65646.0059 | 7907.9294 | 2179.7482 | 22160.7274 | 10704.4012 | 217.8032 | 21996.0265 | 10612.4997 | 205.2898 | 163.0607 | 90.2612 | 10.8732 | 1.6402 | 337334.6945 | 163745.0004 | 3656.6885 | 327242.6096 | 158070.1846 | 2798.925 | 9894.0751 | 5476.806 | 659.7537 | 198.0098 | 111706.0563 | 62710.618 | 9233.5023 | 1190.8859 | 651.5812 | 16.1015 | 108535.0722 | 60078.9387 | 7237.3025 | 1980.0982 | 0.0080636 | 0.0036858 | 9.34e-05 | 0.014196 | 0.008084 | 0.0014196 | 0.003076 | 5000000 | scaled
185-40AE | 24177.5129 | 10855.0355 | 13213.0712 | 109.4062 | 44.9% | 54.65% | 0.4525% | 11665.5808 | 22679.8883 | 723.029 | 4731.0424 | 6211.5094 | 1325.7246 | 9910.7487 | 11443.415 | 185 |  | 311 | 185-40AE | 24177.5129 | 12511.9322 | 1497.6246 | 10855.0355 | 5099.2395 | 507.1622 | 13213.0712 | 7303.2864 | 881.0562 | 109.4062 | 1390.6536 | 667.6246 | 64.9291 | 1366.8946 | 654.4554 | 63.268 | 23.6768 | 13.0869 | 1.5788 | 0.082325 | 12075.837 | 5864.3276 | 632.422 | 9357.1067 | 4357.1534 | 441.8595 | 2708.7918 | 1497.2357 | 180.624 | 9.9385 | 10711.0222 | 5979.9799 | 800.2735 | 131.0342 | 87.6307 | 2.0347 | 10480.6026 | 5792.9638 | 698.8534 | 99.3854 | 0.0005264 | 0.000345 | 8.8e-06 | 0.0143 | 0.0081324 | 0.00143 | 0.000146 | 5000000 | scaled
185-51F | 1723970.7412 | 1584784.2802 | 133165.1506 | 6021.3105 | 91.93% | 7.724% | 0.3493% | 758346.8311 | 1695274.6883 | 60063.9094 | 55760.4643 | 642522.4574 | 133877.4359 | 116262.4093 | 1445134.8431 | 185 |  | 312 | 185-51F | 1723970.7412 | 965623.9102 | 28696.0529 | 1584784.2802 | 886023.8049 | 13790.8129 | 133165.1506 | 73578.7948 | 8883.9295 | 6021.3105 | 135095.1378 | 75031.2285 | 1217.7019 | 134899.5075 | 74921.1079 | 1200.4221 | 191.0995 | 105.5897 | 12.7489 | 4.5308 | 1458995.6707 | 816473.2133 | 13860.8276 | 1447033.8395 | 809619.0952 | 12552.3216 | 11414.8512 | 6307.1381 | 761.5261 | 546.98 | 129879.9327 | 74119.4683 | 13617.5234 | 2850.9332 | 1483.6017 | 38.0692 | 121559.1998 | 67166.067 | 8109.6545 | 5469.7997 | 0.025513 | 0.013262 | 0.0003356 | 0.014198 | 0.0080716 | 0.0014198 | 0.0085106 | 5000000 | scaled
185-52F | 1998.573 | 5.8373 | 1920.5971 | 72.1386 | 0.2921% | 96.1% | 3.61% | 861.3598 | 1798.3702 | 3.5241 | 694.3183 | 163.5174 | 7.7309 | 1447.6976 | 342.9418 | 185 |  | 313 | 185-52F | 1998.573 | 1137.2132 | 200.2028 | 5.8373 | 4.1489 | 0.0029612 | 1920.5971 | 1060.9258 | 128.0613 | 72.1386 | 8.2728 | 4.7486 | 0.54186 | 0.9061 | 0.65504 | 0 | 7.3124 | 4.0393 | 0.48757 | 0.054282 | 373.6628 | 210.1454 | 30.7211 | 4.651 | 3.3724 | 0 | 362.4587 | 200.2199 | 24.168 | 6.5531 | 1616.6374 | 922.3192 | 168.9399 | 0.28021 | 0.12141 | 0.0029612 | 1550.826 | 856.6666 | 103.4057 | 65.5312 | 0.0001514 | 6.56e-05 | 1.6e-06 | 0.014324 | 0.0081412 | 0.0014324 | 0.0001016 | 5000000 | scaled
186-940R | 708016.0499 | 192782.5361 | 513154.713 | 2078.8008 | 27.23% | 72.48% | 0.2936% | 328153.3854 | 663455.1842 | 10978.1848 | 210096.6732 | 107078.5274 | 20727.5823 | 437767.8612 | 204959.7407 | 186 |  | 314 | 186-940R | 708016.0499 | 379862.6645 | 44560.8656 | 192782.5361 | 91306.6389 | 1398.3743 | 513154.713 | 286477.2248 | 41083.6906 | 2078.8008 | 20942.5759 | 9964.3912 | 214.9936 | 20237.8933 | 9570.2993 | 157.137 | 703.1184 | 392.5276 | 56.2924 | 1.5642 | 209819.4392 | 102740.9118 | 4859.6985 | 165608.734 | 77976.1274 | 1146.4233 | 44021.8655 | 24575.9447 | 3524.4355 | 188.8397 | 477254.0347 | 267157.3615 | 39486.1735 | 6935.9087 | 3760.2122 | 94.814 | 468429.7291 | 261508.7525 | 37502.9627 | 1888.3968 | 0.0070982 | 0.0032878 | 8.36e-05 | 0.041559 | 0.02359 | 0.0041558 | 0.0029284 | 5000000 | scaled
188-11F | 2209344.0258 | 2206186.7224 | 0 | 3157.3034 | 99.86% | 0% | 0.1429% | 1251682.0249 | 2189635.2621 | 119647.9003 | 968.5399 | 1131065.5847 | 209293.9594 | 1690.6347 | 1978650.668 | 188 |  | 315 | 188-11F | 2209344.0258 | 957662.0009 | 19708.7637 | 2206186.7224 | 954504.6975 | 16551.4603 | 0 | 0 | 0 | 3157.3034 | 210929.3363 | 91281.436 | 1635.377 | 210926.9605 | 91279.0603 | 1633.0012 | 0 | 0 | 0 | 2.3758 | 1993837.3297 | 862771.745 | 15186.6617 | 1993550.5181 | 862484.9334 | 14899.85 | 0 | 0 | 0 | 286.8116 | 4577.3598 | 3608.8199 | 2886.7251 | 1709.2438 | 740.7038 | 18.609 | 0 | 0 | 0 | 2868.116 | 0.014855 | 0.0065382 | 0.0001666 | 0 | 0 | 0 | 0.004478 | 5000000 | scaled
188-12F | 374.4512 | 227.4308 | 0 | 147.0204 | 60.74% | 0% | 39.26% | 102.6863 | 227.3808 | 14.5296 | 1.8141 | 86.3426 | 31.6396 | 3.9402 | 191.801 | 188 |  | 316 | 188-12F | 374.4512 | 271.7649 | 147.0704 | 227.4308 | 124.7445 | 0.049971 | 0 | 0 | 0 | 147.0204 | 31.7502 | 17.2206 | 0.11063 | 31.6396 | 17.1099 | 0 | 0 | 0 | 0 | 0.11063 | 205.1565 | 118.8138 | 13.3554 | 191.801 | 105.4584 | 0 | 0 | 0 | 0 | 13.3554 | 137.5446 | 135.7305 | 133.6043 | 3.9902 | 2.1761 | 0.049971 | 0 | 0 | 0 | 133.5544 | 0.000454 | 0.0002786 | 7e-06 | 0 | 0 | 0 | 0.0002018 | 5000000 | scaled
189-645 | 13588.1421 | 12535.9707 | 0 | 1052.1714 | 92.26% | 0% | 7.743% | 7600.8448 | 12477.7276 | 427.4919 | 4527.8267 | 2645.5262 | 680.2218 | 7652.8421 | 4144.6637 | 189 |  | 317 | 189-645 | 13588.1421 | 5987.2973 | 1110.4145 | 12535.9707 | 4935.1259 | 58.2431 | 0 | 0 | 0 | 1052.1714 | 682.6776 | 255.1857 | 2.4558 | 681.8858 | 254.394 | 1.664 | 0 | 0 | 0 | 0.79173 | 4248.7708 | 1603.2446 | 104.1071 | 4153.1909 | 1507.6646 | 8.5271 | 0 | 0 | 0 | 95.58 | 8656.6937 | 4128.8671 | 1003.8517 | 7700.894 | 3173.0673 | 48.0519 | 0 | 0 | 0 | 955.7997 | 0.0037328 | 0.0016168 | 4.06e-05 | 0 | 0 | 0 | 0.0015446 | 5000000 | scaled
189-750 | 1724.8402 | 1521.4026 | 0 | 203.4376 | 88.21% | 0% | 11.79% | 457.0292 | 1494.8701 | 0.77288 | 452.3116 | 3.9447 | 2.1657 | 1481.652 | 11.0524 | 189 |  | 318 | 189-750 | 1724.8402 | 1267.811 | 229.9701 | 1521.4026 | 1064.3734 | 26.5324 | 0 | 0 | 0 | 203.4376 | 2.3188 | 1.5459 | 0.15308 | 2.1657 | 1.3928 | 0 | 0 | 0 | 0 | 0.15308 | 29.5328 | 25.5882 | 18.4804 | 11.0524 | 7.1078 | 0 | 0 | 0 | 0 | 18.4804 | 1692.9885 | 1240.6769 | 211.3366 | 1508.1844 | 1055.8728 | 26.5324 | 0 | 0 | 0 | 184.8041 | 0.0007198 | 0.0004726 | 1.18e-05 | 0 | 0 | 0 | 0.0002932 | 5000000 | scaled
189-782F | 270400.0684 | 176793.9415 | 92115.4347 | 1490.6923 | 65.38% | 34.07% | 0.5513% | 139841.0451 | 259538.4067 | 18347.8331 | 37556.3653 | 83936.8466 | 32311.2031 | 78193.8428 | 149033.3608 | 189 |  | 319 | 189-782F | 270400.0684 | 130559.0233 | 10861.6618 | 176793.9415 | 77601.8593 | 1985.678 | 92115.4347 | 51466.4718 | 7385.2915 | 1490.6923 | 32684.32 | 14336.4869 | 373.1169 | 32561.803 | 14267.5395 | 362.2624 | 121.3953 | 67.8257 | 9.7328 | 1.1217 | 151387.5025 | 67450.6559 | 2354.1417 | 143762.3528 | 63130.5975 | 1618.2419 | 7489.7342 | 4184.6428 | 600.4843 | 135.4155 | 86328.246 | 48771.8806 | 8134.4031 | 469.7857 | 203.7222 | 5.1737 | 84504.3052 | 47214.0033 | 6775.0744 | 1354.1551 | 0.0073756 | 0.0031934 | 8.06e-05 | 0.042636 | 0.024217 | 0.0042636 | 0.0021042 | 5000000 | scaled
189-783F | 1922.0286 | 1631.3444 | 0 | 290.6842 | 84.88% | 0% | 15.12% | 762.4069 | 1609.7794 | 7.647 | 715.7582 | 39.0017 | 16.3409 | 1510.1017 | 83.3368 | 189 |  | 320 | 189-783F | 1922.0286 | 1159.6217 | 312.2492 | 1631.3444 | 868.9375 | 21.565 | 0 | 0 | 0 | 290.6842 | 16.7106 | 9.0635 | 0.36968 | 16.4918 | 8.8448 | 0.15095 | 0 | 0 | 0 | 0.21873 | 110.5132 | 71.5115 | 27.1764 | 84.1072 | 45.1056 | 0.77046 | 0 | 0 | 0 | 26.4059 | 1794.8048 | 1079.0466 | 284.7031 | 1530.7453 | 814.9871 | 20.6436 | 0 | 0 | 0 | 264.0595 | 0.0009536 | 0.0004736 | 1.2e-05 | 0 | 0 | 0 | 0.0004082 | 5000000 | scaled
190-1122F | 22262.3253 | 21987.8912 | 0 | 274.4341 | 98.77% | 0% | 1.233% | 12483.4134 | 21869.7429 | 912.5197 | 2.0195 | 11568.8742 | 1596.2234 | 3.5193 | 20270.0001 | 190 |  | 321 | 190-1122F | 22262.3253 | 9778.9119 | 392.5824 | 21987.8912 | 9504.4778 | 118.1483 | 0 | 0 | 0 | 274.4341 | 1606.1384 | 693.6187 | 9.915 | 1605.9319 | 693.4122 | 9.7085 | 0 | 0 | 0 | 0.2065 | 20403.3311 | 8834.4569 | 133.331 | 20378.4014 | 8809.5272 | 108.4012 | 0 | 0 | 0 | 24.9298 | 252.8558 | 250.8363 | 249.3364 | 3.558 | 1.5385 | 0.038601 | 0 | 0 | 0 | 249.2978 | 0.0010618 | 0.0004596 | 1.18e-05 | 0 | 0 | 0 | 0.0003902 | 5000000 | scaled
190-1125F | 1331.4132 | 1299.0141 | 0 | 32.3992 | 97.57% | 0% | 2.433% | 698.2573 | 1299.0104 | 50.5363 | 0.063232 | 647.6578 | 103.5484 | 0.23922 | 1195.2227 | 190 |  | 322 | 190-1125F | 1331.4132 | 633.1559 | 32.4029 | 1299.0141 | 600.7568 | 0.0037016 | 0 | 0 | 0 | 32.3992 | 103.5728 | 53.0365 | 0.024379 | 103.5484 | 53.0121 | 0 | 0 | 0 | 0 | 0.024379 | 1198.1659 | 550.5081 | 2.9432 | 1195.2227 | 547.5649 | 0 | 0 | 0 | 0 | 2.9432 | 29.6746 | 29.6113 | 29.4353 | 0.24293 | 0.17969 | 0.0037016 | 0 | 0 | 0 | 29.4316 | 0.000107 | 8.12e-05 | 2e-06 | 0 | 0 | 0 | 5.04e-05 | 5000000 | scaled
190-1868R | 12069.8746 | 11788.3225 | 0 | 281.5521 | 97.67% | 0% | 2.333% | 5442.0963 | 11629.529 | 138.3095 | 4551.1791 | 752.6078 | 274.9684 | 9858.6456 | 1495.9151 | 190 |  | 323 | 190-1868R | 12069.8746 | 6627.7783 | 440.3456 | 11788.3225 | 6346.2262 | 158.7935 | 0 | 0 | 0 | 281.5521 | 279.4895 | 141.18 | 4.5211 | 279.2776 | 140.9682 | 4.3093 | 0 | 0 | 0 | 0.21186 | 1544.9517 | 792.344 | 49.0366 | 1519.3753 | 766.7676 | 23.4602 | 0 | 0 | 0 | 25.5764 | 10245.4334 | 5694.2543 | 386.7878 | 9989.6695 | 5438.4905 | 131.024 | 0 | 0 | 0 | 255.7639 | 0.0012072 | 0.0006418 | 1.62e-05 | 0 | 0 | 0 | 0.0003856 | 5000000 | scaled
191-1050R | 34116.3546 | 30386.4377 | 0 | 3729.9169 | 89.07% | 0% | 10.93% | 16180.2042 | 30199.2129 | 1538.7299 | 599.7547 | 14041.7196 | 2855.5516 | 1204.5786 | 26139.0828 | 191 |  | 324 | 191-1050R | 34116.3546 | 17936.1505 | 3917.1417 | 30386.4377 | 14206.2336 | 187.2248 | 0 | 0 | 0 | 3729.9169 | 2876.0857 | 1337.3558 | 20.5341 | 2873.279 | 1334.5492 | 17.7275 | 0 | 0 | 0 | 2.8066 | 26629.7212 | 12588.0016 | 490.6384 | 26290.893 | 12249.1734 | 151.8102 | 0 | 0 | 0 | 338.8282 | 4610.5478 | 4010.7931 | 3405.9692 | 1222.2657 | 622.511 | 17.6872 | 0 | 0 | 0 | 3388.282 | 0.0095052 | 0.004191 | 0.0001066 | 0 | 0 | 0 | 0.00528 | 5000000 | scaled
192-657AE | 94561.0459 | 93545.6971 | 0 | 1015.3488 | 98.93% | 0% | 1.074% | 55055.3355 | 91963.7583 | 5626.7348 | 17764.0984 | 31664.5022 | 9217.7609 | 32291.5427 | 50454.4546 | 192 |  | 325 | 192-657AE | 94561.0459 | 39505.7104 | 2597.2876 | 93545.6971 | 38490.3616 | 1581.9388 | 0 | 0 | 0 | 1015.3488 | 9389.7581 | 3763.0232 | 171.9971 | 9388.9941 | 3762.2592 | 171.2331 | 0 | 0 | 0 | 0.76402 | 51563.5688 | 19899.0666 | 1109.1142 | 51471.3338 | 19806.8316 | 1016.8792 | 0 | 0 | 0 | 92.235 | 33607.719 | 15843.6206 | 1316.1763 | 32685.3692 | 14921.2708 | 393.8265 | 0 | 0 | 0 | 922.3498 | 0.0047748 | 0.0024122 | 6.14e-05 | 0 | 0 | 0 | 0.0014442 | 5000000 | scaled
192-757 | 34548.945 | 0 | 34548.945 | 0 | 0% | 100% | 0% | 5474.2382 | 11420.2456 | 6.481 | 4904.2113 | 563.5459 | 13.5205 | 10231.067 | 1175.6582 | 192 |  | 326 | 192-757 | 34548.945 | 29074.7068 | 23128.6994 | 0 | 0 | 0 | 34548.945 | 29074.7068 | 23128.6994 | 0 | 40.9026 | 34.4216 | 27.3821 | 0 | 0 | 0 | 40.9026 | 34.4216 | 27.3821 | 0 | 3556.6441 | 2993.0982 | 2380.9859 | 0 | 0 | 0 | 3556.6441 | 2993.0982 | 2380.9859 | 0 | 30951.3984 | 26047.187 | 20720.3313 | 0 | 0 | 0 | 30951.3984 | 26047.187 | 20720.3313 | 0 | 0 | 0 | 0 | 0.010741 | 0.010741 | 0.010741 | 0 | 5000000 | scaled
196-38F | 96899.663 | 0 | 96899.663 | 0 | 0% | 100% | 0% | 15512.7253 | 32241.0959 | 20.7475 | 14157.1143 | 1334.8634 | 43.121 | 29423.6423 | 2774.3326 | 196 |  | 327 | 196-38F | 96899.663 | 81386.9377 | 64658.5671 | 0 | 0 | 0 | 96899.663 | 81386.9377 | 64658.5671 | 0 | 129.5988 | 108.8512 | 86.4778 | 0 | 0 | 0 | 129.5988 | 108.8512 | 86.4778 | 0 | 8338.1749 | 7003.3114 | 5563.8423 | 0 | 0 | 0 | 8338.1749 | 7003.3114 | 5563.8423 | 0 | 88431.8893 | 74274.775 | 59008.247 | 0 | 0 | 0 | 88431.8893 | 74274.775 | 59008.247 | 0 | 0 | 0 | 0 | 0.016339 | 0.016339 | 0.016339 | 0 | 5000000 | scaled
196-43F | 93765.1171 | 4819.2537 | 88696.2602 | 249.6031 | 5.14% | 94.59% | 0.2662% | 41510.1711 | 87590.6598 | 196.4008 | 36869.7525 | 4444.0179 | 514.1255 | 76502.4821 | 10574.0522 | 196 |  | 328 | 196-43F | 93765.1171 | 52254.9459 | 6174.4573 | 4819.2537 | 3075.1794 | 5.341 | 88696.2602 | 48930.1634 | 5919.5132 | 249.6031 | 523.4263 | 327.0256 | 9.3008 | 386.6916 | 251.5103 | 0 | 136.5469 | 75.3274 | 9.113 | 0.18782 | 11110.9837 | 6666.9658 | 536.9314 | 3382.8277 | 2393.4869 | 0 | 7705.4818 | 4250.8048 | 514.2573 | 22.6741 | 82130.7071 | 45260.9545 | 5628.225 | 1049.7344 | 430.1821 | 5.341 | 80854.2315 | 44604.0312 | 5396.1428 | 226.7412 | 0.000624 | 0.0002704 | 7e-06 | 0.016374 | 0.0092948 | 0.0016374 | 0.0003582 | 5000000 | scaled
197-1150F | 183538.3491 | 182318.8763 | 175.3984 | 1044.0744 | 99.34% | 0.09556% | 0.5689% | 89235.5988 | 180685.5586 | 6151.5598 | 64.1361 | 83019.9028 | 12384.4115 | 132.6327 | 168168.5144 | 197 |  | 329 | 197-1150F | 183538.3491 | 94302.7503 | 2852.7905 | 182318.8763 | 93161.927 | 1797.0128 | 175.3984 | 96.7489 | 11.7033 | 1044.0744 | 12517.2388 | 6365.679 | 132.8273 | 12514.1777 | 6363.6382 | 131.8898 | 2.2755 | 1.2551 | 0.15183 | 0.78563 | 169930.8203 | 86910.9175 | 1762.306 | 169800.2052 | 86796.3421 | 1665.0748 | 35.7707 | 19.731 | 2.3868 | 94.8444 | 1090.29 | 1026.1538 | 957.6573 | 4.4934 | 1.9466 | 0.048203 | 137.3522 | 75.7628 | 9.1647 | 948.4444 | 0.0038112 | 0.0018172 | 4.56e-05 | 0.016495 | 0.0093624 | 0.0016494 | 0.0014708 | 5000000 | scaled
197-1151F | 40964.5873 | 0 | 40964.5873 | 0 | 0% | 100% | 0% | 6546.4592 | 13628.7461 | 8.7064 | 5956.0738 | 581.6789 | 18.1255 | 12399.6523 | 1210.9683 | 197 |  | 330 | 197-1151F | 40964.5873 | 34418.1281 | 27335.8412 | 0 | 0 | 0 | 40964.5873 | 34418.1281 | 27335.8412 | 0 | 54.4806 | 45.7742 | 36.3551 | 0 | 0 | 0 | 54.4806 | 45.7742 | 36.3551 | 0 | 3639.8666 | 3058.1876 | 2428.8983 | 0 | 0 | 0 | 3639.8666 | 3058.1876 | 2428.8983 | 0 | 37270.2401 | 31314.1662 | 24870.5878 | 0 | 0 | 0 | 37270.2401 | 31314.1662 | 24870.5878 | 0 | 0 | 0 | 0 | 0.016455 | 0.016455 | 0.016455 | 0 | 5000000 | scaled
197-1152F | 45172.9197 | 0 | 45172.9197 | 0 | 0% | 100% | 0% | 7227.5721 | 15029.6225 | 8.7323 | 6610.6501 | 608.1898 | 18.1586 | 13746.7429 | 1264.7211 | 197 |  | 331 | 197-1152F | 45172.9197 | 37945.3476 | 30143.2972 | 0 | 0 | 0 | 45172.9197 | 37945.3476 | 30143.2972 | 0 | 54.5773 | 45.8451 | 36.4187 | 0 | 0 | 0 | 54.5773 | 45.8451 | 36.4187 | 0 | 3801.236 | 3193.0463 | 2536.515 | 0 | 0 | 0 | 3801.236 | 3193.0463 | 2536.515 | 0 | 41317.1064 | 34706.4563 | 27570.3635 | 0 | 0 | 0 | 41317.1064 | 34706.4563 | 27570.3635 | 0 | 0 | 0 | 0 | 0.016485 | 0.016485 | 0.016485 | 0 | 5000000 | scaled
197-1155F | 6618.9413 | 6379.3003 | 0 | 239.641 | 96.38% | 0% | 3.621% | 2301.5642 | 6162.8574 | 215.4778 | 21.0615 | 2065.0249 | 577.647 | 37.4276 | 5547.7827 | 197 |  | 332 | 197-1155F | 6618.9413 | 4317.3771 | 456.0839 | 6379.3003 | 4077.7361 | 216.4429 | 0 | 0 | 0 | 239.641 | 597.7355 | 382.2577 | 20.0884 | 597.5551 | 382.0773 | 19.9081 | 0 | 0 | 0 | 0.18032 | 5765.6519 | 3700.627 | 217.8692 | 5743.8828 | 3678.8579 | 196.1 | 0 | 0 | 0 | 21.7692 | 255.5539 | 234.4924 | 218.1263 | 37.8624 | 16.8009 | 0.43477 | 0 | 0 | 0 | 217.6915 | 0.0006924 | 0.0004312 | 1.1e-05 | 0 | 0 | 0 | 0.0003392 | 5000000 | scaled
197-1157F | 63165.5174 | 824.3028 | 61987.4406 | 353.774 | 1.305% | 98.13% | 0.5601% | 28197.4743 | 58673.0608 | 70.0654 | 23845.3757 | 4282.0333 | 147.5591 | 49586.3299 | 8939.1717 | 197 |  | 333 | 197-1157F | 63165.5174 | 34968.043 | 4492.4566 | 824.3028 | 441.5484 | 0.26503 | 61987.4406 | 34172.7206 | 4138.4176 | 353.774 | 153.0286 | 82.9632 | 5.4695 | 74.8251 | 39.7314 | 0 | 77.9372 | 42.9656 | 5.2033 | 0.2662 | 9559.6631 | 5277.6298 | 620.4913 | 714.84 | 387.1947 | 0 | 8812.686 | 4858.298 | 588.3543 | 32.1371 | 53452.8257 | 29607.45 | 3866.4958 | 34.6377 | 14.6223 | 0.26503 | 53096.8174 | 29271.457 | 3544.8601 | 321.3707 | 0.0008542 | 0.00037 | 9.6e-06 | 0.01652 | 0.0093712 | 0.001652 | 0.000496 | 5000000 | scaled
197-969F | 78761.0057 | 0 | 78761.0057 | 0 | 0% | 100% | 0% | 12579.9469 | 26202.8669 | 16.075 | 11525.2482 | 1038.6237 | 33.4827 | 24006.0269 | 2163.3572 | 197 |  | 334 | 197-969F | 78761.0057 | 66181.0588 | 52558.1389 | 0 | 0 | 0 | 78761.0057 | 66181.0588 | 52558.1389 | 0 | 100.6429 | 84.5679 | 67.1602 | 0 | 0 | 0 | 100.6429 | 84.5679 | 67.1602 | 0 | 6502.6545 | 5464.0308 | 4339.2973 | 0 | 0 | 0 | 6502.6545 | 5464.0308 | 4339.2973 | 0 | 72157.7083 | 60632.4601 | 48151.6814 | 0 | 0 | 0 | 72157.7083 | 60632.4601 | 48151.6814 | 0 | 0 | 0 | 0 | 0.016506 | 0.016506 | 0.016506 | 0 | 5000000 | scaled
198-37R | 973099.8875 | 929636.9633 | 39119.1651 | 4343.759 | 95.53% | 4.02% | 0.4464% | 321675.3382 | 940499.7394 | 115319.5745 | 24030.9954 | 182324.7683 | 338763.5628 | 65819.3644 | 535916.8122 | 198 |  | 335 | 198-37R | 973099.8875 | 651424.5493 | 32600.148 | 929636.9633 | 625326.7089 | 25637.111 | 39119.1651 | 21754.0814 | 2619.278 | 4343.759 | 348440.1772 | 233120.6026 | 9676.6143 | 348392.1707 | 233092.4554 | 9670.3503 | 44.7379 | 24.8787 | 2.9955 | 3.2685 | 551923.0271 | 369598.2589 | 16006.2149 | 548086.1034 | 367289.3946 | 15381.1386 | 3442.3337 | 1914.2742 | 230.4862 | 394.59 | 72736.6832 | 48705.6878 | 6917.3188 | 33158.6893 | 24944.8588 | 585.6221 | 35632.0935 | 19814.9285 | 2385.7963 | 3945.9004 | 0.018892 | 0.011676 | 0.0002972 | 0.0056146 | 0.0032104 | 0.0005614 | 0.0061646 | 5000000 | scaled
199-39AE | 5506.3297 | 3584.2738 | 0 | 1922.0559 | 65.09% | 0% | 34.91% | 1737.7966 | 3572.7758 | 162.4482 | 381.7756 | 1193.5728 | 335.6577 | 664.9401 | 2572.178 | 199 |  | 336 | 199-39AE | 5506.3297 | 3768.5331 | 1933.5539 | 3584.2738 | 1846.4772 | 11.498 | 0 | 0 | 0 | 1922.0559 | 338.076 | 175.6278 | 2.4183 | 336.6297 | 174.1815 | 0.97201 | 0 | 0 | 0 | 1.4463 | 2752.0662 | 1558.4934 | 179.8882 | 2577.4653 | 1383.8925 | 5.2873 | 0 | 0 | 0 | 174.6009 | 2416.1876 | 2034.4119 | 1751.2474 | 670.1788 | 288.4032 | 5.2387 | 0 | 0 | 0 | 1746.0087 | 0.0046544 | 0.002015 | 5.22e-05 | 0 | 0 | 0 | 0.0027414 | 5000000 | scaled
203-21R | 165993.6898 | 7751.2673 | 156642.0527 | 1600.3697 | 4.67% | 94.37% | 0.9641% | 74657.2668 | 153861.4335 | 396.5617 | 66481.3028 | 7779.4022 | 739.7232 | 137419.3972 | 15702.3131 | 203 |  | 337 | 203-21R | 165993.6898 | 91336.423 | 12132.2563 | 7751.2673 | 3405.5293 | 71.4369 | 156642.0527 | 86330.524 | 10460.4497 | 1600.3697 | 759.9736 | 363.4119 | 20.2505 | 544.2074 | 243.9556 | 4.7179 | 214.562 | 118.2521 | 14.3283 | 1.2042 | 16780.5085 | 9001.1062 | 1078.1953 | 3048.481 | 1367.684 | 25.5095 | 13586.6488 | 7488.0435 | 907.3072 | 145.3787 | 148453.2077 | 81971.9049 | 11033.8105 | 4158.5789 | 1793.8897 | 41.2095 | 142840.842 | 78724.2284 | 9538.8142 | 1453.7868 | 0.0046468 | 0.0020114 | 5.06e-05 | 0.016416 | 0.0093098 | 0.0016416 | 0.0022336 | 5000000 | scaled
204-32R | 490461.4768 | 472621.3902 | 6175.7404 | 11664.3461 | 96.36% | 1.259% | 2.378% | 231782.5462 | 473489.9499 | 15419.4771 | 2498.8186 | 213864.2504 | 31686.2195 | 5264.2411 | 436539.4893 | 204 |  | 338 | 204-32R | 490461.4768 | 258678.9306 | 16971.5269 | 472621.3902 | 243613.0782 | 4895.1891 | 6175.7404 | 3401.5063 | 411.9917 | 11664.3461 | 32027.0462 | 16607.5691 | 340.8268 | 31952.1907 | 16562.397 | 327.6415 | 66.0785 | 36.3951 | 4.4082 | 8.777 | 442239.9554 | 228375.705 | 5700.4661 | 439917.9778 | 226620.8073 | 4556.6539 | 1262.3804 | 695.3004 | 84.215 | 1059.5972 | 16194.4751 | 13695.6566 | 10930.234 | 751.2217 | 429.8738 | 10.8936 | 4847.2815 | 2669.8108 | 323.3685 | 10595.9719 | 0.054026 | 0.028824 | 0.000732 | 0.016632 | 0.009427 | 0.0016632 | 0.016447 | 5000000 | scaled
205-1550 | 124006.4072 | 122173.7477 | 0 | 1832.6596 | 98.52% | 0% | 1.478% | 63857.0172 | 121053.5357 | 4515.097 | 2911.2644 | 56430.6559 | 8508.5553 | 4994.5582 | 107550.4223 | 205 |  | 339 | 205-1550 | 124006.4072 | 60149.39 | 2952.8715 | 122173.7477 | 58316.7305 | 1120.212 | 0 | 0 | 0 | 1832.6596 | 8590.9752 | 4075.8782 | 82.4199 | 8589.5962 | 4074.4992 | 81.0409 | 0 | 0 | 0 | 1.379 | 108699.9499 | 52269.2941 | 1149.5277 | 108533.4699 | 52102.814 | 983.0476 | 0 | 0 | 0 | 166.48 | 6715.4821 | 3804.2177 | 1720.9239 | 5050.6816 | 2139.4172 | 56.1234 | 0 | 0 | 0 | 1664.8005 | 0.0062072 | 0.002742 | 6.96e-05 | 0 | 0 | 0 | 0.0025818 | 5000000 | scaled
205-369R | 370182.5355 | 359719.1346 | 0 | 10463.4008 | 97.17% | 0% | 2.827% | 208513.2267 | 356075.2833 | 16218.8554 | 9852.112 | 182442.2593 | 27770.2018 | 18039.1522 | 310265.9293 | 205 |  | 340 | 205-369R | 370182.5355 | 161669.3087 | 14107.2521 | 359719.1346 | 151205.9079 | 3643.8513 | 0 | 0 | 0 | 10463.4008 | 28066.6547 | 11847.7993 | 296.4529 | 28058.7814 | 11839.9259 | 288.5795 | 0 | 0 | 0 | 7.8734 | 314360.8063 | 131918.547 | 4094.877 | 313410.3038 | 130968.0445 | 3144.3745 | 0 | 0 | 0 | 950.5025 | 27755.0744 | 17902.9624 | 9715.9222 | 18250.0495 | 8397.9374 | 210.8973 | 0 | 0 | 0 | 9505.025 | 0.031948 | 0.013931 | 0.0003534 | 0 | 0 | 0 | 0.014686 | 5000000 | scaled
206-1105 | 1279044.3418 | 1276283.4138 | 0 | 2760.928 | 99.78% | 0% | 0.2159% | 713141.8287 | 1261782.7041 | 43318.9765 | 991.8282 | 668831.0239 | 76593.4413 | 1728.9064 | 1183460.3563 | 206 |  | 341 | 206-1105 | 1279044.3418 | 565902.5131 | 17261.6377 | 1276283.4138 | 563141.5851 | 14500.7097 | 0 | 0 | 0 | 2760.928 | 77497.2908 | 34178.3143 | 903.8495 | 77495.2133 | 34176.2368 | 901.772 | 0 | 0 | 0 | 2.0775 | 1197290.5728 | 528459.5489 | 13830.2165 | 1197039.7682 | 528208.7443 | 13579.4119 | 0 | 0 | 0 | 250.8046 | 4256.4781 | 3264.6499 | 2527.5717 | 1748.4322 | 756.604 | 19.5258 | 0 | 0 | 0 | 2508.0459 | 0.010109 | 0.004377 | 0.0001114 | 0 | 0 | 0 | 0.0039104 | 5000000 | scaled
206-1817 | 2976573.4131 | 2969126.7016 | 0 | 7446.7115 | 99.75% | 0% | 0.2502% | 1631143.8419 | 2937070.1035 | 95837.4105 | 1971.1261 | 1533335.3053 | 173154.4003 | 3697.3405 | 2760218.3626 | 206 |  | 342 | 206-1817 | 2976573.4131 | 1345429.5712 | 39503.3096 | 2969126.7016 | 1337982.8597 | 32056.5981 | 0 | 0 | 0 | 7446.7115 | 175054.5868 | 79217.1762 | 1900.1864 | 175048.9834 | 79211.5728 | 1894.583 | 0 | 0 | 0 | 5.6034 | 2791011.9702 | 1257676.6649 | 30793.6076 | 2790335.5058 | 1257000.2005 | 30117.1432 | 0 | 0 | 0 | 676.4644 | 10506.8561 | 8535.7301 | 6809.5156 | 3742.2124 | 1771.0863 | 44.8719 | 0 | 0 | 0 | 6764.6437 | 0.027806 | 0.012572 | 0.0003194 | 0 | 0 | 0 | 0.010402 | 5000000 | scaled
206-953R | 1585851.9327 | 1580692.2595 | 0 | 5159.6732 | 99.67% | 0% | 0.3254% | 852542.4149 | 1566154.9993 | 54744.6608 | 3049.5992 | 794748.1549 | 100627.9925 | 6623.4959 | 1458903.5108 | 206 |  | 343 | 206-953R | 1585851.9327 | 733309.5178 | 19696.9334 | 1580692.2595 | 728149.8445 | 14537.2602 | 0 | 0 | 0 | 5159.6732 | 101577.5974 | 46832.9366 | 949.6049 | 101573.7149 | 46829.0541 | 945.7224 | 0 | 0 | 0 | 3.8825 | 1472867.4322 | 678119.2773 | 13963.9214 | 1472398.724 | 677650.5691 | 13495.2131 | 0 | 0 | 0 | 468.7082 | 11406.903 | 8357.3038 | 4783.4071 | 6719.8205 | 3670.2214 | 96.3246 | 0 | 0 | 0 | 4687.0825 | 0.018726 | 0.00853 | 0.0002178 | 0 | 0 | 0 | 0.0072756 | 5000000 | scaled
206-961F | 734.9748 | 534.573 | 0 | 200.4018 | 72.73% | 0% | 27.27% | 436.5002 | 534.3949 | 45.8259 | 12.8926 | 377.7817 | 58.2386 | 21.1108 | 455.0456 | 206 |  | 344 | 206-961F | 734.9748 | 298.4746 | 200.5799 | 534.573 | 98.0728 | 0.17805 | 0 | 0 | 0 | 200.4018 | 58.3894 | 12.5635 | 0.1508 | 58.2386 | 12.4127 | 0 | 0 | 0 | 0 | 0.1508 | 473.2502 | 95.4685 | 18.2046 | 455.0456 | 77.2639 | 0 | 0 | 0 | 0 | 18.2046 | 203.3352 | 190.4426 | 182.2244 | 21.2888 | 8.3962 | 0.17805 | 0 | 0 | 0 | 182.0464 | 0.0006146 | 0.0002662 | 6.6e-06 | 0 | 0 | 0 | 0.0002912 | 5000000 | scaled
206-963F | 308008.4782 | 304622.4649 | 0 | 3386.0133 | 98.9% | 0% | 1.099% | 146363.3408 | 301407.656 | 10999.7815 | 9856.0505 | 125507.5088 | 22569.1737 | 21904.5619 | 256933.9204 | 206 |  | 345 | 206-963F | 308008.4782 | 161645.1374 | 6600.8222 | 304622.4649 | 158259.1241 | 3214.8089 | 0 | 0 | 0 | 3386.0133 | 22807.2632 | 11807.4817 | 238.0896 | 22804.7154 | 11804.9339 | 235.5417 | 0 | 0 | 0 | 2.5479 | 259871.3603 | 134363.8516 | 2937.4399 | 259563.7726 | 134056.2638 | 2629.8521 | 0 | 0 | 0 | 307.5878 | 25329.8546 | 15473.8041 | 3425.2927 | 22253.9769 | 12397.9265 | 349.4151 | 0 | 0 | 0 | 3075.8776 | 0.010107 | 0.0047956 | 0.0001218 | 0 | 0 | 0 | 0.0047494 | 5000000 | scaled
206-974 | 1943671.9016 | 1937613.9402 | 0 | 6057.9614 | 99.69% | 0% | 0.3117% | 1105375.1219 | 1917871.1854 | 71579.728 | 4796.2658 | 1028999.1281 | 124197.7579 | 8368.5238 | 1785304.9037 | 206 |  | 346 | 206-974 | 1943671.9016 | 838296.7798 | 25800.7162 | 1937613.9402 | 832238.8183 | 19742.7548 | 0 | 0 | 0 | 6057.9614 | 125493.2706 | 53913.5426 | 1295.5127 | 125488.7122 | 53908.9842 | 1290.9543 | 0 | 0 | 0 | 4.5584 | 1804213.9678 | 775214.8397 | 18909.0642 | 1803663.6585 | 774664.5304 | 18358.7548 | 0 | 0 | 0 | 550.3094 | 13964.6632 | 9168.3974 | 5596.1394 | 8461.5695 | 3665.3037 | 93.0457 | 0 | 0 | 0 | 5503.0936 | 0.02043 | 0.0088468 | 0.000224 | 0 | 0 | 0 | 0.0085284 | 5000000 | scaled
207-101R | 42865.1365 | 35873.7541 | 0 | 6991.3824 | 83.69% | 0% | 16.31% | 15052.1746 | 35496.8223 | 1212.9601 | 5801.6167 | 8037.5977 | 2920.0379 | 11958.3178 | 20618.4665 | 207 |  | 347 | 207-101R | 42865.1365 | 27812.9619 | 7368.3142 | 35873.7541 | 20821.5795 | 376.9319 | 0 | 0 | 0 | 6991.3824 | 2957.7126 | 1744.7525 | 37.6747 | 2952.4518 | 1739.4917 | 32.4139 | 0 | 0 | 0 | 5.2608 | 21462.6305 | 13425.0328 | 844.1641 | 20827.5286 | 12789.9308 | 209.0621 | 0 | 0 | 0 | 635.102 | 18444.7933 | 12643.1766 | 6486.4755 | 12093.7737 | 6292.157 | 135.4559 | 0 | 0 | 0 | 6351.0196 | 0.022787 | 0.010971 | 0.0002788 | 0 | 0 | 0 | 0.009846 | 5000000 | scaled
209-1769F | 8462801.8216 | 8440861.3147 | 0 | 21940.507 | 99.74% | 0% | 0.2593% | 4604981.1649 | 8313600.7011 | 279427.4682 | 7594.763 | 4317958.9337 | 503419.7123 | 13683.0989 | 7796497.8899 | 209 |  | 348 | 209-1769F | 8462801.8216 | 3857820.6568 | 149201.1205 | 8440861.3147 | 3835880.1498 | 127260.6136 | 0 | 0 | 0 | 21940.507 | 510879.137 | 231451.6688 | 7459.4246 | 510862.6274 | 231435.1592 | 7442.9151 | 0 | 0 | 0 | 16.5095 | 7918145.4533 | 3600186.5196 | 121647.5634 | 7916152.3626 | 3598193.4289 | 119654.4727 | 0 | 0 | 0 | 1993.0907 | 33777.2314 | 26182.4684 | 20094.1325 | 13846.3247 | 6251.5617 | 163.2258 | 0 | 0 | 0 | 19930.9068 | 0.08071 | 0.035575 | 0.000919 | 0 | 0 | 0 | 0.030983 | 5000000 | scaled
209-660R | 6801.7341 | 6167.3172 | 0 | 634.4168 | 90.67% | 0% | 9.327% | 3356.7726 | 6082.1708 | 57.3728 | 3005.0256 | 294.3741 | 105.4532 | 5433.8982 | 542.8194 | 209 |  | 349 | 209-660R | 6801.7341 | 3444.9615 | 719.5632 | 6167.3172 | 2810.5447 | 85.1464 | 0 | 0 | 0 | 634.4168 | 109.5395 | 52.1666 | 4.0863 | 109.0621 | 51.6893 | 3.6089 | 0 | 0 | 0 | 0.47738 | 619.3435 | 324.9694 | 76.5241 | 561.7126 | 267.3385 | 18.8932 | 0 | 0 | 0 | 57.6309 | 6072.8511 | 3067.8255 | 638.9528 | 5496.5425 | 2491.5169 | 62.6442 | 0 | 0 | 0 | 576.3086 | 0.0016228 | 0.0007026 | 1.8e-05 | 0 | 0 | 0 | 0.0008848 | 5000000 | scaled
209-661 | 118711.2283 | 117657.145 | 0 | 1054.0834 | 99.11% | 0% | 0.8879% | 64454.5271 | 116947.3049 | 4376.5203 | 3654.7724 | 56423.2345 | 8009.3149 | 8485.7872 | 100452.2029 | 209 |  | 350 | 209-661 | 118711.2283 | 54256.7012 | 1763.9234 | 117657.145 | 53202.6178 | 709.84 | 0 | 0 | 0 | 1054.0834 | 8065.8053 | 3689.285 | 56.4904 | 8065.0121 | 3688.4918 | 55.6972 | 0 | 0 | 0 | 0.79316 | 101091.3101 | 44668.0756 | 639.1072 | 100995.5564 | 44572.3219 | 543.3535 | 0 | 0 | 0 | 95.7537 | 9554.113 | 5899.3407 | 1068.3258 | 8596.5765 | 4941.8041 | 110.7893 | 0 | 0 | 0 | 957.5366 | 0.0029158 | 0.00135 | 3.34e-05 | 0 | 0 | 0 | 0.0015096 | 5000000 | scaled
210-172R | 498149.5699 | 448825.0802 | 45760.7733 | 3563.7165 | 90.1% | 9.186% | 0.7154% | 270213.0396 | 486291.4923 | 9694.2796 | 18764.6084 | 241754.1516 | 17494.0999 | 38055.547 | 430741.8453 | 210 |  | 351 | 210-172R | 498149.5699 | 227936.5303 | 11858.0777 | 448825.0802 | 198448.7728 | 3899.2964 | 45760.7733 | 25924.0411 | 4395.0648 | 3563.7165 | 17708.5114 | 8014.2319 | 214.4115 | 17161.7167 | 7703.3035 | 159.471 | 544.1131 | 308.2468 | 52.259 | 2.6816 | 435617.1632 | 193863.0116 | 4875.3178 | 426187.6157 | 188380.7237 | 3677.0249 | 9105.817 | 5158.5574 | 874.5625 | 323.7304 | 44823.8953 | 26059.2869 | 6768.3483 | 5475.7478 | 2364.7456 | 62.8006 | 36110.8431 | 20457.2369 | 3468.2433 | 3237.3044 | 0.023388 | 0.010549 | 0.0002674 | 0.29744 | 0.16905 | 0.029744 | 0.005045 | 5000000 | scaled
210-392R | 1037895.6522 | 889811.7026 | 141601.8867 | 6482.0629 | 85.73% | 13.64% | 0.6245% | 445473.8102 | 1007425.6653 | 19213.4014 | 56067.1227 | 370193.286 | 43570.8932 | 116900.701 | 846954.0711 | 210 |  | 352 | 210-392R | 1037895.6522 | 592421.842 | 30469.9869 | 889811.7026 | 505671.8896 | 10385.8508 | 141601.8867 | 80267.8895 | 13602.0732 | 6482.0629 | 44129.6304 | 24916.2289 | 558.7372 | 43729.5682 | 24687.3386 | 515.8988 | 395.1846 | 224.0128 | 37.9609 | 4.8775 | 858712.5289 | 488519.2428 | 11758.4578 | 844368.3535 | 480133.1096 | 9848.3046 | 13755.3403 | 7797.2982 | 1321.3182 | 588.835 | 135053.4929 | 78986.3702 | 18152.7919 | 1713.7809 | 851.4414 | 21.6475 | 127451.3618 | 72246.5785 | 12242.7942 | 5888.3503 | 0.040655 | 0.022858 | 0.000581 | 0.29796 | 0.16945 | 0.029796 | 0.0090946 | 5000000 | scaled
210-394R | 170592.87 | 120220.794 | 47928.6718 | 2443.4042 | 70.47% | 28.1% | 1.432% | 74814.5496 | 162028.8862 | 2887.3065 | 16698.3927 | 55228.8504 | 6054.4413 | 34861.6155 | 121112.8293 | 210 |  | 353 | 210-394R | 170592.87 | 95778.3204 | 8563.9838 | 120220.794 | 66157.5165 | 1514.2624 | 47928.6718 | 27177.3997 | 4606.3172 | 2443.4042 | 6130.4929 | 3243.1865 | 76.0516 | 6014.3864 | 3176.5535 | 63.231 | 114.268 | 64.7943 | 10.982 | 1.8386 | 123687.2236 | 68458.3732 | 2574.3943 | 114066.8975 | 62907.1781 | 1449.1779 | 9398.3656 | 5329.2346 | 903.2559 | 221.9605 | 40775.1535 | 24076.7607 | 5913.5379 | 139.5101 | 73.7849 | 1.8534 | 38416.0382 | 21783.3707 | 3692.0793 | 2219.6051 | 0.012758 | 0.0069782 | 0.0001786 | 0.30224 | 0.17193 | 0.030224 | 0.0034144 | 5000000 | scaled
210-9R | 317772.4997 | 161505.4673 | 154213.5674 | 2053.4649 | 50.82% | 48.53% | 0.6462% | 153137.4481 | 299303.1403 | 5351.3653 | 61817.8886 | 85968.1941 | 9941.1462 | 128854.5463 | 160507.4478 | 210 |  | 354 | 210-9R | 317772.4997 | 164635.0516 | 18469.3594 | 161505.4673 | 75134.9791 | 1594.4381 | 154213.5674 | 87446.6076 | 14821.4564 | 2053.4649 | 10073.1857 | 4721.8203 | 132.0395 | 9846.0481 | 4592.3533 | 108.8127 | 225.5924 | 127.9219 | 21.6817 | 1.5452 | 163377.0332 | 77408.839 | 2869.5854 | 150611.6365 | 70089.4751 | 1474.0939 | 12578.8585 | 7132.8258 | 1208.9533 | 186.5382 | 144322.2808 | 82504.3922 | 15467.7345 | 1047.7828 | 453.1507 | 11.5315 | 141409.1165 | 80185.8599 | 13590.8214 | 1865.3816 | 0.0088812 | 0.0039588 | 0.0001006 | 0.30218 | 0.1719 | 0.030218 | 0.002905 | 5000000 | scaled
211-279R | 1199632.2461 | 1073511.5836 | 117562.3496 | 8558.313 | 89.49% | 9.8% | 0.7134% | 628630.9441 | 1168197.1772 | 22470.252 | 56327.0806 | 549833.6115 | 41351.0717 | 114031.614 | 1012814.4915 | 211 |  | 355 | 211-279R | 1199632.2461 | 571001.3021 | 31435.0689 | 1073511.5836 | 495763.0695 | 11572.5873 | 117562.3496 | 66679.9196 | 11304.1687 | 8558.313 | 41826.2848 | 19356.0328 | 475.2132 | 41606.1896 | 19228.4102 | 448.2293 | 213.6554 | 121.1827 | 20.544 | 6.4399 | 1025603.6733 | 475770.0618 | 12789.1818 | 1013477.2719 | 468555.6291 | 10920.4834 | 11348.9584 | 6436.9897 | 1091.2553 | 777.443 | 132202.288 | 75875.2074 | 18170.674 | 18428.1221 | 7979.0301 | 203.8745 | 105999.7358 | 60121.7472 | 10192.3694 | 7774.4301 | 0.055187 | 0.025186 | 0.0006386 | 0.30593 | 0.17406 | 0.030593 | 0.012013 | 5000000 | scaled
211-312R | 1809514.7304 | 1524787.4196 | 272926.761 | 11800.5499 | 84.26% | 15.08% | 0.6521% | 917497.6501 | 1754440.5929 | 50132.8923 | 107314.0976 | 760050.6603 | 94555.378 | 223717.8698 | 1436167.3451 | 211 |  | 356 | 211-312R | 1809514.7304 | 892017.0803 | 55074.1375 | 1524787.4196 | 725414.0728 | 17031.5338 | 272926.761 | 154802.4576 | 26242.0538 | 11800.5499 | 95656.1431 | 45523.2508 | 1100.7651 | 95238.2646 | 45282.3895 | 1052.5601 | 408.999 | 231.9818 | 39.3255 | 8.8795 | 1455828.1802 | 695777.5199 | 19660.8351 | 1427354.326 | 679163.3619 | 15954.1593 | 27401.8842 | 15542.1879 | 2634.7058 | 1071.97 | 258030.4071 | 150716.3095 | 34312.5373 | 2194.829 | 968.3214 | 24.8144 | 245115.8778 | 139028.2879 | 23568.0226 | 10719.7003 | 0.068207 | 0.032682 | 0.0008354 | 0.30536 | 0.17374 | 0.030536 | 0.016737 | 5000000 | scaled
211-771R | 1890633.0335 | 1721676.6645 | 160513.2299 | 8443.1391 | 91.06% | 8.49% | 0.4466% | 1025997.3214 | 1847807.4651 | 39197.1466 | 61609.2638 | 925190.911 | 69627.2133 | 128249.4028 | 1649930.8489 | 211 |  | 357 | 211-771R | 1890633.0335 | 864635.7121 | 42825.5684 | 1721676.6645 | 765128.1108 | 18940.6811 | 160513.2299 | 91064.4623 | 15441.7483 | 8443.1391 | 70423.843 | 31226.6964 | 796.6296 | 70079.9902 | 31028.8685 | 757.8082 | 337.4996 | 191.4747 | 32.4682 | 6.3532 | 1670855.0926 | 745664.1816 | 20924.2437 | 1649300.4126 | 733103.6519 | 18157.4378 | 20787.6995 | 11793.5492 | 1999.8253 | 766.9805 | 149354.0979 | 87744.8341 | 21104.6951 | 2296.2617 | 995.5903 | 25.4351 | 139388.0308 | 79079.4384 | 13409.4547 | 7669.8053 | 0.0528 | 0.024003 | 0.0006094 | 0.30961 | 0.1762 | 0.030961 | 0.01189 | 5000000 | scaled
212-1177R | 1738925.2296 | 1659398.1014 | 71222.6311 | 8304.4971 | 95.43% | 4.096% | 0.4776% | 359825.5662 | 1689990.2693 | 17640.1667 | 29516.4501 | 312668.9494 | 88217.0967 | 72566.4533 | 1529206.7194 | 212 |  | 358 | 212-1177R | 1738925.2296 | 1379099.6634 | 48934.9603 | 1659398.1014 | 1330711.4374 | 34274.8333 | 71222.6311 | 40083.7288 | 6355.6299 | 8304.4971 | 90117.0188 | 72476.8521 | 1899.9222 | 89894.71 | 72349.0058 | 1874.3929 | 216.06 | 121.5974 | 19.2804 | 6.2489 | 1562791.8261 | 1250122.8767 | 33585.1067 | 1553282.7945 | 1244441.4213 | 32049.4901 | 8754.6453 | 4927.0692 | 781.2304 | 754.3862 | 86016.3847 | 56499.9346 | 13449.9315 | 16220.5969 | 13921.0103 | 350.9503 | 62251.9258 | 35035.0622 | 5555.1192 | 7543.862 | 0.038856 | 0.030981 | 0.0007862 | 0.10004 | 0.056827 | 0.010004 | 0.01164 | 5000000 | scaled
212-1204R | 1570376.2068 | 1491430.4435 | 72901.975 | 6043.7883 | 94.97% | 4.642% | 0.3849% | 409408.1605 | 1529836.371 | 20835.8453 | 29597.756 | 358974.5591 | 79866.0109 | 65691.4687 | 1384278.8915 | 212 |  | 359 | 212-1204R | 1570376.2068 | 1160968.0463 | 40539.8357 | 1491430.4435 | 1113740.6352 | 27720.4444 | 72901.975 | 41183.6227 | 6775.603 | 6043.7883 | 81424.0289 | 60588.1836 | 1558.018 | 81299.4614 | 60515.8345 | 1542.3155 | 120.0197 | 67.8013 | 11.1548 | 4.5478 | 1411637.5085 | 1052662.9493 | 27358.617 | 1402703.0719 | 1047376.8575 | 26030.2439 | 8385.4147 | 4737.07 | 779.3512 | 549.0219 | 77314.6694 | 47716.9134 | 11623.2007 | 7427.9102 | 5847.9432 | 147.885 | 64396.5405 | 36378.7515 | 5985.0971 | 5490.2187 | 0.034015 | 0.025086 | 0.0006368 | 0.1497 | 0.085077 | 0.01497 | 0.0084874 | 5000000 | scaled
212-638R | 609779.7244 | 604090.7433 | 3002.3128 | 2686.6683 | 99.07% | 0.4924% | 0.4406% | 156662.5741 | 593944.0247 | 6638.2 | 1744.7858 | 148279.5883 | 25197.7767 | 4701.267 | 564044.9809 | 212 |  | 360 | 212-638R | 609779.7244 | 453117.1503 | 15835.6997 | 604090.7433 | 448745.6601 | 12885.413 | 3002.3128 | 1684.8219 | 263.6184 | 2686.6683 | 25753.9736 | 19115.7736 | 556.1969 | 25747.8387 | 19111.4437 | 553.8141 | 4.1133 | 2.3083 | 0.36117 | 2.0216 | 576598.7295 | 428319.1413 | 12553.7486 | 576115.1862 | 427940.6898 | 12288.6619 | 239.4846 | 134.3927 | 21.028 | 244.0588 | 7427.0213 | 5682.2355 | 2725.7542 | 2227.7185 | 1693.5267 | 42.9371 | 2758.7149 | 1548.1209 | 242.2293 | 2440.5879 | 0.01604 | 0.011938 | 0.000303 | 0.087245 | 0.049478 | 0.0087244 | 0.00379 | 5000000 | scaled
212-725R | 4887826.6998 | 4846329.5478 | 35508.5272 | 5988.6249 | 99.15% | 0.7265% | 0.1225% | 1317367.4238 | 4791823.1186 | 63634.9637 | 13660.9433 | 1240071.5168 | 232348.7963 | 29097.2761 | 4530377.0462 | 212 |  | 361 | 212-725R | 4887826.6998 | 3570459.2761 | 96003.5813 | 4846329.5478 | 3544531.5023 | 86897.3214 | 35508.5272 | 19939.1489 | 3117.635 | 5988.6249 | 236619.5386 | 172984.575 | 4270.7423 | 236479.3032 | 172903.8525 | 4254.3191 | 135.7292 | 76.2162 | 11.917 | 4.5062 | 4613977.8953 | 3373906.3785 | 83600.849 | 4608405.0269 | 3370538.5068 | 82615.3065 | 5028.8576 | 2823.8609 | 441.5318 | 544.0108 | 37229.266 | 23568.3227 | 8131.9899 | 1445.2177 | 1089.143 | 27.6957 | 30343.9404 | 17039.0718 | 2664.1863 | 5440.1079 | 0.043677 | 0.032053 | 0.0008148 | 0.087233 | 0.049502 | 0.0087232 | 0.0084998 | 5000000 | scaled
212-734R | 1265959.6441 | 1239607.9706 | 17542.0399 | 8809.6336 | 97.92% | 1.386% | 0.6959% | 312920.9544 | 1227285.523 | 11855.3975 | 13228.0968 | 287837.4602 | 46832.808 | 41952.9243 | 1138499.7907 | 212 |  | 362 | 212-734R | 1265959.6441 | 953038.6896 | 38674.121 | 1239607.9706 | 934352.9292 | 28298.6723 | 17542.0399 | 9876.1269 | 1565.8151 | 8809.6336 | 47973.1269 | 36117.7294 | 1140.3189 | 47738.9213 | 35982.9754 | 1113.3763 | 227.5766 | 128.1251 | 20.3137 | 6.629 | 1166238.6201 | 878401.1599 | 27738.8294 | 1161860.8267 | 875586.7514 | 26619.2242 | 3577.5203 | 2014.1354 | 319.332 | 800.2732 | 51747.8971 | 38519.8003 | 9794.9727 | 30008.2226 | 22783.2024 | 566.0718 | 13736.943 | 7733.8663 | 1226.1694 | 8002.7315 | 0.064592 | 0.049067 | 0.0012464 | 0.10037 | 0.057036 | 0.010037 | 0.012573 | 5000000 | scaled
212-739R | 998791.2358 | 965054.7656 | 27840.7085 | 5895.7617 | 96.62% | 2.787% | 0.5903% | 316339.7819 | 977199.3579 | 16178.8296 | 11358.7061 | 288802.2462 | 50172.5381 | 24949.4919 | 902077.3279 | 212 |  | 363 | 212-739R | 998791.2358 | 682451.4539 | 21591.8779 | 965054.7656 | 660932.6461 | 13252.4042 | 27840.7085 | 15623.046 | 2443.712 | 5895.7617 | 50890.9894 | 34712.1598 | 718.4513 | 50836.335 | 34679.5431 | 709.607 | 50.218 | 28.1803 | 4.4079 | 4.4364 | 915411.2322 | 626608.9859 | 13333.9042 | 911335.1801 | 624086.6427 | 12487.5646 | 3540.477 | 1986.7682 | 310.7646 | 535.575 | 32489.0143 | 21130.3082 | 7539.5224 | 2883.2505 | 2166.4603 | 55.2326 | 24250.0135 | 13608.0975 | 2128.5395 | 5355.7503 | 0.035565 | 0.023904 | 0.0006066 | 0.087122 | 0.049404 | 0.0087122 | 0.0082824 | 5000000 | scaled
212-743R | 261427.8714 | 253729.516 | 5541.9002 | 2156.4552 | 97.06% | 2.12% | 0.8249% | 92755.4285 | 256632.23 | 4162.8996 | 2223.4741 | 86369.0548 | 11970.4582 | 4638.1579 | 240023.6138 | 212 |  | 364 | 212-743R | 261427.8714 | 168672.4429 | 4795.6415 | 253729.516 | 163395.8394 | 2144.5857 | 5541.9002 | 3120.1483 | 494.6006 | 2156.4552 | 12072.7063 | 7909.8067 | 102.248 | 12064.8788 | 7904.6906 | 100.0716 | 6.2048 | 3.4934 | 0.55377 | 1.6227 | 242311.1429 | 155942.0881 | 2287.5291 | 241573.3576 | 155441.1036 | 2043.2728 | 541.8914 | 305.0906 | 48.3624 | 195.8939 | 7044.0223 | 4820.5482 | 2405.8643 | 91.2796 | 50.0451 | 1.2413 | 4993.8039 | 2811.5644 | 445.6844 | 1958.9387 | 0.01316 | 0.0077172 | 0.0001952 | 0.10033 | 0.057009 | 0.010033 | 0.0030568 | 5000000 | scaled
212-758R | 1482461.7895 | 1442027.7956 | 34331.3121 | 6102.6818 | 97.27% | 2.316% | 0.4117% | 221421.2442 | 1443071.6853 | 10807.9234 | 13554.6764 | 197058.6444 | 74526.9245 | 29839.5047 | 1338705.2561 | 212 |  | 365 | 212-758R | 1482461.7895 | 1261040.5453 | 39390.1041 | 1442027.7956 | 1235609.262 | 30223.6826 | 34331.3121 | 19328.6014 | 3063.7398 | 6102.6818 | 76141.4689 | 65333.5455 | 1614.5444 | 76087.7778 | 65301.3105 | 1605.5707 | 49.0991 | 27.6429 | 4.3816 | 4.5921 | 1368209.869 | 1171151.2246 | 29504.6129 | 1363322.3558 | 1168157.285 | 28563.5499 | 4333.1414 | 2439.5678 | 386.6912 | 554.3718 | 38110.4515 | 24555.7751 | 8270.9468 | 2617.662 | 2150.6665 | 54.5619 | 29949.0716 | 16861.3908 | 2672.6669 | 5543.7179 | 0.033816 | 0.029089 | 0.000739 | 0.10027 | 0.056978 | 0.010027 | 0.0086122 | 5000000 | scaled
212-773R | 2758566.7114 | 2642067.3385 | 109237.1393 | 7262.2336 | 95.78% | 3.96% | 0.2633% | 944850.6924 | 2699031.4406 | 50301.0315 | 43326.9238 | 851222.7372 | 146093.6786 | 91223.5564 | 2461714.2055 | 212 |  | 366 | 212-773R | 2758566.7114 | 1813716.019 | 59535.2708 | 2642067.3385 | 1744761.6261 | 42119.5109 | 109237.1393 | 61692.1594 | 10153.5264 | 7262.2336 | 148464.9768 | 98163.9453 | 2371.2982 | 148345.3935 | 98094.0317 | 2355.2263 | 114.1187 | 64.449 | 10.6073 | 5.4646 | 2503096.045 | 1651873.3078 | 41381.8395 | 2491719.2143 | 1645161.0579 | 39725.9829 | 10717.1244 | 6052.5436 | 996.1503 | 659.7063 | 107005.6896 | 63678.7659 | 15782.1332 | 2002.7307 | 1506.5364 | 38.3017 | 98405.8962 | 55575.1667 | 9146.7688 | 6597.0627 | 0.038893 | 0.025923 | 0.0006598 | 0.14975 | 0.08508 | 0.014975 | 0.010168 | 5000000 | scaled
212-799R | 1038800.4924 | 1008878.3087 | 26373.4381 | 3548.7456 | 97.12% | 2.539% | 0.3416% | 327533.7119 | 1015703.1495 | 16084.9858 | 10351.2133 | 301097.5128 | 50556.6713 | 22044.895 | 943101.5831 | 212 |  | 367 | 212-799R | 1038800.4924 | 711266.7805 | 23097.3429 | 1008878.3087 | 692872.5498 | 17194.6291 | 26373.4381 | 14845.4851 | 2353.9682 | 3548.7456 | 51431.9897 | 35347.0038 | 875.3183 | 51348.6587 | 35298.93 | 865.4486 | 80.6606 | 45.4035 | 7.1994 | 2.6703 | 960018.7166 | 658921.2039 | 16917.1335 | 956499.2751 | 656799.217 | 16309.4076 | 3197.0711 | 1799.6164 | 285.3554 | 322.3705 | 27349.7861 | 16998.5728 | 5304.8911 | 1030.3749 | 774.4027 | 19.7729 | 23095.7064 | 13000.4652 | 2061.4134 | 3223.7048 | 0.019599 | 0.013283 | 0.000337 | 0.10033 | 0.057001 | 0.010033 | 0.0049968 | 5000000 | scaled
212-880R | 104943.9464 | 102616.691 | 1359.2306 | 968.0248 | 97.78% | 1.295% | 0.9224% | 15747.6756 | 101977.2114 | 680.6379 | 549.2865 | 14517.7513 | 4430.2053 | 1158.5003 | 96388.5058 | 212 |  | 368 | 212-880R | 104943.9464 | 89196.2708 | 2966.735 | 102616.691 | 87462.914 | 1877.3782 | 1359.2306 | 765.3321 | 121.332 | 968.0248 | 4515.6674 | 3835.0295 | 85.4621 | 4513.9038 | 3833.7182 | 84.6413 | 1.0352 | 0.58287 | 0.092406 | 0.72841 | 98278.4255 | 83760.6742 | 1889.9197 | 98082.002 | 83611.653 | 1792.2995 | 108.4874 | 61.0852 | 9.6842 | 87.936 | 2149.8535 | 1600.5671 | 991.3532 | 20.7852 | 17.5428 | 0.43748 | 1249.708 | 703.664 | 111.5555 | 879.3603 | 0.0055194 | 0.004596 | 0.0001166 | 0.10045 | 0.057077 | 0.010045 | 0.0013892 | 5000000 | scaled
212-886R | 2163524.8176 | 2135825.9125 | 22371.1462 | 5327.7589 | 98.72% | 1.034% | 0.2463% | 822111.6147 | 2119136.5613 | 42123.4136 | 8484.4927 | 771503.7084 | 109136.9122 | 17832.6349 | 1992167.0142 | 212 |  | 369 | 212-886R | 2163524.8176 | 1341413.2029 | 44388.2563 | 2135825.9125 | 1323449.1937 | 36981.0473 | 22371.1462 | 12636.2503 | 2079.4501 | 5327.7589 | 111101.8825 | 68978.4689 | 1964.9703 | 111062.2176 | 68954.3198 | 1957.647 | 35.656 | 20.1401 | 3.3143 | 4.009 | 2027987.9647 | 1256484.2562 | 35820.9505 | 2024000.7726 | 1254021.5024 | 35011.3412 | 3503.2148 | 1978.7765 | 325.632 | 483.9773 | 24434.9704 | 15950.4778 | 6602.3355 | 762.9223 | 473.3714 | 12.059 | 18832.2754 | 10637.3336 | 1750.5038 | 4839.7727 | 0.030079 | 0.018387 | 0.000467 | 0.15012 | 0.085305 | 0.015012 | 0.0074656 | 5000000 | scaled
212-888R | 1471062.1959 | 1438972.0881 | 27695.1883 | 4394.9195 | 97.82% | 1.883% | 0.2988% | 610338.736 | 1441634.89 | 32964.3806 | 10760.8148 | 566613.5405 | 77888.4743 | 22563.9285 | 1341182.4872 | 212 |  | 370 | 212-888R | 1471062.1959 | 860723.46 | 29427.3059 | 1438972.0881 | 840736.2537 | 22559.96 | 27695.1883 | 15592.2868 | 2472.4264 | 4394.9195 | 79138.2144 | 46173.8337 | 1249.7401 | 79110.587 | 46156.8344 | 1244.2619 | 24.3203 | 13.6922 | 2.1711 | 3.307 | 1363185.9031 | 796572.3626 | 22003.4159 | 1359478.6731 | 794310.7378 | 21308.8647 | 3307.9926 | 1862.3874 | 295.3137 | 399.2375 | 28738.0785 | 17977.2636 | 6174.15 | 382.8281 | 268.6815 | 6.8335 | 24362.8754 | 13716.2072 | 2174.9416 | 3992.375 | 0.024497 | 0.014392 | 0.0003658 | 0.10043 | 0.057063 | 0.010043 | 0.0062312 | 5000000 | scaled
213-262F | 161.6751 | 128.102 | 0 | 33.5731 | 79.23% | 0% | 20.77% | 103.5024 | 128.0872 | 10.8071 | 0.93685 | 91.7585 | 13.5395 | 1.6498 | 112.8979 | 213 |  | 371 | 213-262F | 161.6751 | 58.1727 | 33.5879 | 128.102 | 24.5996 | 0.014806 | 0 | 0 | 0 | 33.5731 | 13.5648 | 2.7577 | 0.025263 | 13.5395 | 2.7324 | 0 | 0 | 0 | 0 | 0.025263 | 115.9478 | 24.1893 | 3.0498 | 112.8979 | 21.1395 | 0 | 0 | 0 | 0 | 3.0498 | 32.1626 | 31.2258 | 30.5128 | 1.6646 | 0.72775 | 0.014806 | 0 | 0 | 0 | 30.498 | 0.0001478 | 6.4e-05 | 1.6e-06 | 0 | 0 | 0 | 4.98e-05 | 5000000 | scaled
213-263F | 32297.4199 | 31746.5341 | 0 | 550.8858 | 98.29% | 0% | 1.706% | 18147.1243 | 31702.4381 | 2215.8323 | 5498.4742 | 10432.8178 | 3877.2844 | 9615.537 | 18209.6167 | 213 |  | 372 | 213-263F | 32297.4199 | 14150.2956 | 594.9818 | 31746.5341 | 13599.4098 | 44.096 | 0 | 0 | 0 | 550.8858 | 3877.6989 | 1661.8666 | 0.41452 | 3877.2844 | 1661.4521 | 0 | 0 | 0 | 0 | 0.41452 | 18259.6595 | 7826.8418 | 50.0428 | 18209.6167 | 7776.7989 | 0 | 0 | 0 | 0 | 50.0428 | 10160.0614 | 4661.5873 | 544.5244 | 9659.633 | 4161.1588 | 44.096 | 0 | 0 | 0 | 500.4284 | 0.0022326 | 0.000967 | 2.46e-05 | 0 | 0 | 0 | 0.0007838 | 5000000 | scaled
214-1122R | 26281150.1655 | 25993614.3166 | 275469.895 | 12065.9539 | 98.91% | 1.048% | 0.04591% | 9918462.909 | 25787324.9713 | 509548.7929 | 108740.7235 | 9300173.3926 | 1325344.5091 | 230940.914 | 24231039.5481 | 214 |  | 373 | 214-1122R | 26281150.1655 | 16362687.2565 | 493825.1942 | 25993614.3166 | 16194803.479 | 455875.1664 | 275469.895 | 155817.8235 | 25884.0738 | 12065.9539 | 1348977.8164 | 839429.0235 | 23633.3072 | 1348418.3995 | 839108.6492 | 23572.5164 | 550.3377 | 311.2951 | 51.7116 | 9.0792 | 24667086.3 | 15366912.9074 | 436046.7519 | 24635960.7517 | 15348830.8466 | 432129.0029 | 30029.4688 | 16985.9813 | 2821.6695 | 1096.0795 | 265086.0491 | 156345.3256 | 34145.1351 | 9235.1654 | 6863.9832 | 173.6471 | 244890.0885 | 138520.5472 | 23010.6928 | 10960.7952 | 0.066356 | 0.040277 | 0.0010234 | 0.18583 | 0.10565 | 0.018583 | 0.016987 | 5000000 | scaled
214-1135R | 6666921.5731 | 6627374.3046 | 31346.5489 | 8200.7196 | 99.41% | 0.4702% | 0.123% | 2969601.4392 | 6563900.2805 | 185612.9012 | 14186.1083 | 2769802.4297 | 407535.2534 | 34034.2471 | 6122330.78 | 214 |  | 374 | 214-1135R | 6666921.5731 | 3697320.1339 | 103021.2926 | 6627374.3046 | 3671621.8585 | 92307.0719 | 31346.5489 | 17497.5558 | 2513.5012 | 8200.7196 | 413361.1301 | 227748.2289 | 5825.8767 | 413267.8925 | 227693.4577 | 5812.7245 | 87.0668 | 48.6004 | 6.9814 | 6.1708 | 6209752.3162 | 3439949.8865 | 87421.5363 | 6204470.8133 | 3436672.6414 | 86312.8177 | 4536.5439 | 2532.2861 | 363.7596 | 744.959 | 43808.1268 | 29622.0184 | 9773.8797 | 9635.5987 | 7255.7593 | 181.5297 | 26722.9383 | 14916.6693 | 2142.7602 | 7449.5898 | 0.036405 | 0.01899 | 0.0004838 | 0.042859 | 0.02432 | 0.0042858 | 0.011513 | 5000000 | scaled
214-17AE | 484035.5133 | 471452.7484 | 7163.8313 | 5418.9337 | 97.4% | 1.48% | 1.12% | 221123.0155 | 470817.5003 | 12075.7569 | 2771.0916 | 206276.167 | 25889.0776 | 5739.5118 | 439188.911 | 214 |  | 375 | 214-17AE | 484035.5133 | 262912.4979 | 13218.013 | 471452.7484 | 253494.0831 | 7224.4257 | 7163.8313 | 3999.481 | 574.6536 | 5418.9337 | 26282.1822 | 14206.4252 | 393.1046 | 26255.1772 | 14189.5476 | 387.1878 | 22.9274 | 12.8001 | 1.8391 | 4.0776 | 446610.5067 | 240334.3397 | 7421.5957 | 444929.7657 | 239178.5652 | 6834.0009 | 1188.4813 | 663.5148 | 95.3352 | 492.2596 | 11142.8245 | 8371.733 | 5403.3128 | 267.8054 | 125.9704 | 3.237 | 5952.4226 | 3323.1661 | 477.4793 | 4922.5965 | 0.02137 | 0.010801 | 0.0002748 | 0.042967 | 0.024388 | 0.0042968 | 0.0076194 | 5000000 | scaled
214-4R | 400189.4629 | 391624.8997 | 5439.4986 | 3125.0646 | 97.86% | 1.359% | 0.7809% | 211297.8928 | 392200.4785 | 12303.3966 | 2186.0009 | 196808.4954 | 22653.3131 | 4513.3618 | 365033.8037 | 214 |  | 376 | 214-4R | 400189.4629 | 188891.5701 | 7988.9844 | 391624.8997 | 182728.6178 | 4427.5887 | 5439.4986 | 3037.8877 | 436.3311 | 3125.0646 | 22905.3716 | 10601.975 | 252.0585 | 22886.9861 | 10590.6687 | 248.4208 | 16.034 | 8.9547 | 1.2862 | 2.3515 | 369568.5902 | 172760.0949 | 4534.7866 | 368328.1913 | 171942.0104 | 4174.1763 | 956.5159 | 534.2014 | 76.7272 | 283.883 | 7715.5011 | 5529.5003 | 3202.1393 | 409.7223 | 195.9386 | 4.9916 | 4466.9488 | 2494.7316 | 358.3177 | 2838.8301 | 0.012296 | 0.0055432 | 0.0001404 | 0.042997 | 0.024415 | 0.0042996 | 0.0043832 | 5000000 | scaled
214-536R | 513329.1103 | 506732.7143 | 4540.4132 | 2055.9829 | 98.71% | 0.8845% | 0.4005% | 173796.5996 | 504886.5551 | 9950.6781 | 3676.6354 | 160169.2862 | 29060.6301 | 10169.3722 | 465656.5527 | 214 |  | 377 | 214-536R | 513329.1103 | 339532.5107 | 8442.5552 | 506732.7143 | 334943.6782 | 6022.404 | 4540.4132 | 2532.8496 | 364.1684 | 2055.9829 | 29429.2035 | 19478.5254 | 368.5734 | 29414.5546 | 19469.6696 | 365.9754 | 13.1018 | 7.3088 | 1.0508 | 1.5471 | 471428.9547 | 311259.6684 | 5772.4019 | 470594.5111 | 310711.5979 | 5533.6875 | 647.6767 | 361.3036 | 51.9475 | 186.7669 | 12470.9522 | 8794.3168 | 2301.58 | 6723.6485 | 4762.4107 | 122.7411 | 3879.6347 | 2164.2372 | 311.17 | 1867.6689 | 0.0077628 | 0.005459 | 0.0001388 | 0.043089 | 0.024443 | 0.0043088 | 0.002892 | 5000000 | scaled
214-583R | 2208313.3513 | 2188306.5727 | 15051.2713 | 4955.5073 | 99.09% | 0.6816% | 0.2244% | 1142178.5788 | 2180050.5666 | 68963.7739 | 12576.06 | 1060638.7449 | 131300.9166 | 24009.8548 | 2024739.7952 | 214 |  | 378 | 214-583R | 2208313.3513 | 1066134.7725 | 28262.7847 | 2188306.5727 | 1052782.5264 | 22099.9723 | 15051.2713 | 8396.7388 | 1207.3051 | 4955.5073 | 132635.6487 | 63671.8748 | 1334.7321 | 132601.7384 | 63651.3085 | 1328.5823 | 30.1815 | 16.8375 | 2.4209 | 3.7289 | 2045951.2885 | 985312.5436 | 21211.4933 | 2043919.6109 | 983980.0926 | 20634.4738 | 1581.5159 | 882.2893 | 126.8579 | 450.1617 | 29726.414 | 17150.354 | 5716.5593 | 11785.2233 | 5151.1253 | 136.9163 | 13439.5739 | 7497.6119 | 1078.0263 | 4501.6167 | 0.020393 | 0.0094972 | 0.000241 | 0.043118 | 0.024463 | 0.0043118 | 0.0069024 | 5000000 | scaled
214-613R | 1721769.027 | 1475341.9619 | 242193.3314 | 4233.7337 | 85.69% | 14.07% | 0.2459% | 924933.6547 | 1678347.6689 | 47198.4227 | 95862.2802 | 781872.9518 | 84413.21 | 198964.9392 | 1394969.5197 | 214 |  | 379 | 214-613R | 1721769.027 | 796835.3723 | 43421.3581 | 1475341.9619 | 655327.0131 | 15669.7714 | 242193.3314 | 137274.6254 | 23517.8529 | 4233.7337 | 85346.693 | 38148.2703 | 933.483 | 84881.3294 | 37883.1232 | 885.4181 | 462.1779 | 261.9613 | 44.8791 | 3.1857 | 1412620.7051 | 630747.7532 | 17651.1854 | 1386186.2509 | 615598.1576 | 14737.0541 | 26049.8589 | 14765.0003 | 2529.536 | 384.5953 | 223801.6289 | 127939.3487 | 24836.6897 | 4274.3816 | 1845.7323 | 47.2992 | 215681.2946 | 122247.6637 | 20943.4378 | 3845.9527 | 0.016958 | 0.0079234 | 0.0002004 | 0.40998 | 0.23292 | 0.040998 | 0.005945 | 5000000 | scaled
214-647R | 22354308.5327 | 22185077.5014 | 163192.3476 | 6038.6837 | 99.24% | 0.73% | 0.02701% | 7216932.7329 | 22019248.8459 | 356497.0933 | 64228.2273 | 6796207.4123 | 1090644.9404 | 135136.4957 | 20793467.4098 | 214 |  | 380 | 214-647R | 22354308.5327 | 15137375.7997 | 335059.6868 | 22185077.5014 | 15038986.0202 | 313681.4821 | 163192.3476 | 92351.0958 | 15339.521 | 6038.6837 | 1106446.3725 | 749949.2792 | 15801.4321 | 1105952.0175 | 749667.5495 | 15750.8476 | 489.8111 | 277.1857 | 46.0406 | 4.5439 | 21093450.4143 | 14297243.0019 | 299983.0045 | 21076367.814 | 14287337.774 | 297880.3031 | 16534.0421 | 9356.6698 | 1554.1433 | 548.5582 | 154411.7459 | 90183.5186 | 19275.2502 | 2757.6699 | 1980.6967 | 50.3314 | 146168.4944 | 82717.2403 | 13739.3372 | 5485.5816 | 0.042459 | 0.028997 | 0.0007374 | 0.18745 | 0.10661 | 0.018745 | 0.0085248 | 5000000 | scaled
215-1531R | 12702411.9104 | 12475572.5359 | 220695.3654 | 6144.0091 | 98.21% | 1.737% | 0.04837% | 5443209.1762 | 12461133.2225 | 327904.516 | 88071.869 | 5027232.7912 | 752494.8095 | 185380.2097 | 11523258.2033 | 215 |  | 381 | 215-1531R | 12702411.9104 | 7259202.7342 | 241278.6879 | 12475572.5359 | 7128160.8725 | 214494.8645 | 220695.3654 | 124897.8526 | 20639.8143 | 6144.0091 | 765658.7811 | 437754.2651 | 13163.9716 | 765379.7569 | 437594.3505 | 13133.686 | 274.4011 | 155.2915 | 25.6625 | 4.6232 | 11727017.5933 | 6699784.8021 | 203759.39 | 11705992.5157 | 6687643.8397 | 201287.1591 | 20466.9517 | 11582.8364 | 1914.1049 | 558.126 | 209735.536 | 121663.667 | 24355.3263 | 4200.2634 | 2922.6823 | 74.0194 | 199954.0127 | 113159.7247 | 18700.0469 | 5581.2599 | 0.026648 | 0.014948 | 0.0003792 | 0.16755 | 0.095329 | 0.016755 | 0.00871 | 5000000 | scaled
215-1534R | 19489706.3687 | 19294168.695 | 189765.6478 | 5772.0259 | 99% | 0.9737% | 0.02962% | 8717883.1684 | 19188686.8399 | 541796.4009 | 75837.9399 | 8100248.8276 | 1190940.4121 | 158379.2603 | 17839367.1675 | 215 |  | 382 | 215-1534R | 19489706.3687 | 10771823.2004 | 301019.5288 | 19294168.695 | 10658653.9065 | 277502.6653 | 189765.6478 | 107397.268 | 17744.8377 | 5772.0259 | 1208263.0965 | 666466.6956 | 17322.6844 | 1207973.3698 | 666300.8405 | 17291.6552 | 285.3835 | 161.5119 | 26.686 | 4.3433 | 18101642.0279 | 10001393.2004 | 262274.8604 | 18084396.6113 | 9991405.6222 | 260186.9503 | 16721.0819 | 9463.2434 | 1563.5753 | 524.3348 | 179801.2443 | 103963.3044 | 21421.984 | 1798.714 | 947.4439 | 24.0598 | 172759.1825 | 97772.5127 | 16154.5764 | 5243.3478 | 0.022842 | 0.012266 | 0.0003122 | 0.1672 | 0.095133 | 0.01672 | 0.0081584 | 5000000 | scaled
215-1544R | 1412429.6019 | 1385494.8684 | 25217.6287 | 1717.1047 | 98.09% | 1.785% | 0.1216% | 429501.163 | 1359250.4504 | 35514.3004 | 9911.4906 | 384075.372 | 112303.9898 | 20757.3925 | 1226189.0681 | 215 |  | 383 | 215-1544R | 1412429.6019 | 982928.4389 | 53179.1515 | 1385494.8684 | 967024.1085 | 49200.1134 | 25217.6287 | 14187.2256 | 2261.9334 | 1717.1047 | 116224.0619 | 80709.7615 | 3920.0721 | 116168.9329 | 80678.1812 | 3913.951 | 53.837 | 30.2882 | 4.829 | 1.2921 | 1271866.7299 | 887791.3579 | 45677.6618 | 1269021.5032 | 886122.4291 | 45280.4631 | 2689.2438 | 1512.9459 | 241.2158 | 155.983 | 24338.8101 | 14427.3195 | 3581.4176 | 304.4324 | 223.4983 | 5.6993 | 22474.548 | 12643.9915 | 2015.8886 | 1559.8297 | 0.0083662 | 0.0056268 | 0.0001426 | 0.098125 | 0.055699 | 0.0098124 | 0.0024172 | 5000000 | scaled
215-38R | 5434815.4519 | 5375940.6103 | 54849.6154 | 4025.2262 | 98.92% | 1.009% | 0.07406% | 1603042.4615 | 5353965.3201 | 98777.1845 | 24341.7022 | 1479923.5748 | 333216.7352 | 56697.3761 | 4964051.2088 | 215 |  | 384 | 215-38R | 5434815.4519 | 3831772.9904 | 80850.1318 | 5375940.6103 | 3796907.367 | 71902.0155 | 54849.6154 | 30840.3972 | 4922.8901 | 4025.2262 | 337744.046 | 238966.8615 | 4527.3108 | 337616.4889 | 238893.8139 | 4513.1052 | 124.5282 | 70.0187 | 11.1767 | 3.0289 | 5032075.2284 | 3552151.6535 | 68024.0196 | 5025873.9331 | 3548504.7823 | 67134.6019 | 5835.641 | 3281.2169 | 523.7634 | 365.6543 | 64996.1775 | 40654.4753 | 8298.8014 | 12450.1883 | 9508.7707 | 254.3084 | 48889.4462 | 27489.1616 | 4387.95 | 3656.543 | 0.020867 | 0.014705 | 0.000374 | 0.098782 | 0.056037 | 0.0098782 | 0.0056306 | 5000000 | scaled
216-1859F | 14041287.7051 | 13926878.6549 | 108865.6056 | 5543.4446 | 99.19% | 0.7753% | 0.03948% | 7159458.6267 | 13845282.0339 | 441781.5073 | 43612.8031 | 6674064.3163 | 854141.8217 | 90609.892 | 12900530.3202 | 216 |  | 385 | 216-1859F | 14041287.7051 | 6881829.0784 | 196005.6711 | 13926878.6549 | 6814958.682 | 180481.078 | 108865.6056 | 61326.9518 | 9981.1486 | 5543.4446 | 865565.3615 | 423783.8542 | 11423.5398 | 865377.8346 | 423676.3937 | 11402.5579 | 183.3557 | 103.2892 | 16.8106 | 4.1713 | 13071028.1239 | 6396963.8076 | 170497.8038 | 13060390.2122 | 6390751.2876 | 169065.0845 | 10134.3414 | 5708.9497 | 929.149 | 503.5703 | 104694.2196 | 61081.4165 | 14084.3276 | 1110.6081 | 531.0007 | 13.4356 | 98547.9085 | 55514.7128 | 9035.189 | 5035.703 | 0.024139 | 0.011704 | 0.0002958 | 0.12517 | 0.071026 | 0.012517 | 0.0077338 | 5000000 | scaled
216-220R | 71281.5532 | 71210.3647 | 0 | 71.1885 | 99.9% | 0% | 0.09987% | 17002.0014 | 71206.9423 | 923.7343 | 0 | 16078.2671 | 3688.5887 | 0 | 67518.3536 | 216 |  | 386 | 216-220R | 71281.5532 | 54279.5517 | 74.6109 | 71210.3647 | 54208.3632 | 3.4224 | 0 | 0 | 0 | 71.1885 | 3689.1786 | 2765.4442 | 0.58986 | 3689.125 | 2765.3907 | 0.5363 | 0 | 0 | 0 | 0.053567 | 67527.7065 | 51449.4394 | 9.3529 | 67521.2397 | 51442.9726 | 2.8861 | 0 | 0 | 0 | 6.4668 | 64.6681 | 64.6681 | 64.6681 | 0 | 0 | 0 | 0 | 0 | 0 | 64.6681 | 0.0001854 | 0.0001408 | 3.6e-06 | 0 | 0 | 0 | 9.96e-05 | 5000000 | scaled
217-41AE | 2013596.5771 | 1796628.9519 | 207510.3844 | 9457.2408 | 89.22% | 10.31% | 0.4697% | 700732.5246 | 1951620.3402 | 39206.6903 | 82482.5264 | 579043.3079 | 113394.7876 | 173527.7419 | 1664697.8106 | 217 |  | 387 | 217-41AE | 2013596.5771 | 1312864.0525 | 61976.2369 | 1796628.9519 | 1186338.5351 | 33291.7864 | 207510.3844 | 117068.2767 | 19227.2098 | 9457.2408 | 115533.4192 | 76326.7289 | 2138.6316 | 114895.0045 | 75963.4617 | 2073.0214 | 631.2984 | 356.1509 | 58.494 | 7.1163 | 1698999.8477 | 1119956.5398 | 34302.0371 | 1672556.7454 | 1104664.0645 | 31072.408 | 25584.0001 | 14433.3731 | 2370.5269 | 859.1022 | 199063.3101 | 116580.7838 | 25535.5682 | 9177.202 | 5711.0089 | 146.3569 | 181295.0859 | 102278.7526 | 16798.189 | 8591.0223 | 0.04004 | 0.026808 | 0.0006812 | 0.14338 | 0.081393 | 0.014338 | 0.013221 | 5000000 | scaled
217-48AE | 2727584.5153 | 2396177.964 | 321334.4889 | 10072.0624 | 87.85% | 11.78% | 0.3693% | 1004775.387 | 2643179.9068 | 55686.6585 | 123998.9842 | 825089.7444 | 151493.64 | 257832.331 | 2233853.9358 | 217 |  | 388 | 217-48AE | 2727584.5153 | 1722809.1282 | 84404.6085 | 2396177.964 | 1531423.3648 | 44560.8289 | 321334.4889 | 181313.7011 | 29771.7172 | 10072.0624 | 154348.9476 | 98662.2891 | 2855.3076 | 153756.7582 | 98324.8424 | 2793.5644 | 584.6105 | 329.8678 | 54.1643 | 7.5789 | 2280258.7833 | 1455169.039 | 46404.8476 | 2238672.3533 | 1431305.1145 | 41721.6725 | 40671.477 | 22948.9715 | 3768.2221 | 914.953 | 292976.7843 | 168977.8001 | 35144.4533 | 3748.8524 | 1793.4078 | 45.5921 | 280078.4015 | 158034.8619 | 25949.3309 | 9149.5304 | 0.045211 | 0.028496 | 0.0007242 | 0.14291 | 0.081142 | 0.014291 | 0.014237 | 5000000 | scaled
217-835R | 10686932.5847 | 10546229.7286 | 130572.3311 | 10130.5249 | 98.68% | 1.222% | 0.09479% | 2932256.2983 | 10437126.0342 | 170937.9574 | 48735.9786 | 2712582.3623 | 610332.2348 | 103821.7068 | 9722972.0926 | 217 |  | 389 | 217-835R | 10686932.5847 | 7754676.2864 | 249806.5505 | 10546229.7286 | 7670669.2725 | 227320.6452 | 130572.3311 | 73876.489 | 12355.3804 | 10130.5249 | 623744.8746 | 452806.9172 | 13412.6398 | 623236.3583 | 452515.894 | 13357.62 | 500.8934 | 283.4003 | 47.3969 | 7.6229 | 9939850.4599 | 7227268.0976 | 216878.3673 | 9916663.3332 | 7213749.4706 | 213851.1061 | 22266.8629 | 12598.3632 | 2106.9974 | 920.2638 | 123337.2503 | 74601.2717 | 19515.5435 | 6330.0372 | 4403.908 | 111.9191 | 107804.5749 | 60994.7254 | 10200.9861 | 9202.6382 | 0.058771 | 0.041596 | 0.0010562 | 0.21117 | 0.12001 | 0.021117 | 0.014184 | 5000000 | scaled
217-837R | 3657183.3822 | 3461858.2787 | 187410.7511 | 7914.3524 | 94.66% | 5.124% | 0.2164% | 1199813.6723 | 3586485.7341 | 76579.8618 | 82554.2227 | 1040679.5877 | 231238.965 | 176667.6034 | 3178579.1656 | 217 |  | 390 | 217-837R | 3657183.3822 | 2457369.7099 | 70697.6481 | 3461858.2787 | 2344076.5802 | 46060.6215 | 187410.7511 | 105378.7773 | 16722.6743 | 7914.3524 | 234509.9048 | 157930.043 | 3270.9398 | 234167.2442 | 157734.7624 | 3234.9403 | 336.7053 | 189.3253 | 30.0442 | 5.9553 | 3223550.1359 | 2182870.5481 | 44970.9702 | 3202415.2114 | 2170671.947 | 42430.3058 | 20415.9793 | 11479.6559 | 1821.7192 | 718.9452 | 199123.3415 | 116569.1188 | 22455.7381 | 25275.8232 | 15669.8708 | 395.3754 | 166658.0664 | 93709.7961 | 14870.9108 | 7189.4519 | 0.038224 | 0.024851 | 0.0006312 | 0.093318 | 0.052956 | 0.0093318 | 0.01115 | 5000000 | scaled
217-972R | 1438659.3628 | 1307400.2329 | 124584.4907 | 6674.6392 | 90.88% | 8.66% | 0.4639% | 649214.9824 | 1411059.0145 | 40183.3293 | 47505.2327 | 561526.4203 | 87495.3552 | 99326.5921 | 1224237.0672 | 217 |  | 391 | 217-972R | 1438659.3628 | 789444.3804 | 27600.3483 | 1307400.2329 | 712442.7846 | 9376.287 | 124584.4907 | 70326.9566 | 11549.4221 | 6674.6392 | 88238.9535 | 48055.6242 | 743.5983 | 87762.1971 | 47784.3117 | 694.8445 | 471.734 | 266.2901 | 43.7314 | 5.0225 | 1235063.9981 | 673537.5777 | 10826.9309 | 1217503.2314 | 663360.6032 | 8648.8658 | 16954.4379 | 9570.6457 | 1571.7363 | 606.3288 | 115356.4112 | 67851.1785 | 16029.8191 | 2134.8044 | 1297.8697 | 32.5766 | 107158.3188 | 60490.0208 | 9933.9545 | 6063.288 | 0.028671 | 0.015698 | 0.0003998 | 0.14428 | 0.081944 | 0.014428 | 0.0093218 | 5000000 | scaled
217-983R | 10116962.9104 | 10020803.7313 | 92061.404 | 4097.7751 | 99.05% | 0.91% | 0.0405% | 5037821.9417 | 9947122.8892 | 257788.1275 | 36900.5177 | 4743133.2965 | 509062.4108 | 77022.3372 | 9361038.1412 | 217 |  | 392 | 217-983R | 10116962.9104 | 5079140.9686 | 169840.0212 | 10020803.7313 | 5022929.3046 | 157028.9469 | 92061.404 | 52113.889 | 8713.2993 | 4097.7751 | 517297.1159 | 259508.9884 | 8234.7051 | 517165.1514 | 259432.9483 | 8219.4235 | 128.8811 | 72.9567 | 12.1982 | 3.0834 | 9511006.8537 | 4767873.5572 | 149968.7125 | 9502098.3134 | 4762669.1077 | 148788.5364 | 8536.2956 | 4832.2048 | 807.9314 | 372.2447 | 88658.9407 | 51758.423 | 11636.6036 | 1540.2664 | 827.2486 | 20.9869 | 83396.2274 | 47208.7275 | 7893.1697 | 3722.4469 | 0.025816 | 0.013327 | 0.0003392 | 0.21217 | 0.12064 | 0.021217 | 0.0058128 | 5000000 | scaled
220-288R | 2198679.8663 | 2118136.7464 | 76362.619 | 4180.5009 | 96.34% | 3.473% | 0.1901% | 501706.879 | 2147419.1619 | 23380.3724 | 31143.1393 | 447183.3673 | 102996.2183 | 70454.464 | 1973968.4796 | 220 |  | 393 | 220-288R | 2198679.8663 | 1696972.9873 | 51260.7044 | 2118136.7464 | 1649527.0542 | 39705.1284 | 76362.619 | 43265.4323 | 7375.0751 | 4180.5009 | 104940.9048 | 81560.5324 | 1944.6865 | 104845.7901 | 81505.279 | 1932.6584 | 91.969 | 52.1077 | 8.8823 | 3.1457 | 2012941.1944 | 1565757.8271 | 38972.7148 | 2001718.2372 | 1559234.5429 | 37545.723 | 10843.1976 | 6143.5246 | 1047.2322 | 379.7596 | 80797.7671 | 49654.6279 | 10343.3031 | 11572.7191 | 8787.2323 | 226.747 | 65427.4524 | 37069.7999 | 6318.9606 | 3797.5956 | 0.024519 | 0.018552 | 0.000472 | 0.34486 | 0.19592 | 0.034486 | 0.0058558 | 5000000 | scaled
220-294R | 1925887.6447 | 1623346.7665 | 294263.9944 | 8276.8838 | 84.29% | 15.28% | 0.4298% | 832447.2095 | 1867462.8264 | 38034.4185 | 114631.6869 | 679781.1041 | 86934.8691 | 240646.9105 | 1539881.0467 | 220 |  | 394 | 220-294R | 1925887.6447 | 1093440.4351 | 58424.8183 | 1623346.7665 | 918371.5663 | 21627.1881 | 294263.9944 | 166791.985 | 28520.7464 | 8276.8838 | 88212.4974 | 50178.0788 | 1277.6283 | 87251.9489 | 49630.9317 | 1178.9052 | 954.3204 | 540.919 | 92.4949 | 6.2281 | 1564028.3211 | 884247.217 | 24147.2744 | 1532105.9721 | 865827.5821 | 20374.2825 | 31170.4713 | 17667.7571 | 3021.1141 | 751.8778 | 273646.8262 | 159015.1393 | 32999.9156 | 3988.8456 | 2913.0525 | 74.0003 | 262139.2027 | 148583.3088 | 25407.1373 | 7518.778 | 0.047871 | 0.027814 | 0.0007052 | 0.38452 | 0.21848 | 0.038452 | 0.01158 | 5000000 | scaled
220-298R | 3585631.4391 | 3204472.4076 | 360773.6342 | 20385.3974 | 89.37% | 10.06% | 0.5685% | 1459754.7888 | 3474591.3347 | 59038.0716 | 138166.896 | 1262549.8212 | 139895.2964 | 290546.0281 | 3044150.0102 | 220 |  | 395 | 220-298R | 3585631.4391 | 2125876.6503 | 111040.1043 | 3204472.4076 | 1900946.094 | 55692.9722 | 360773.6342 | 204545.159 | 34961.7348 | 20385.3974 | 142360.6713 | 83322.5997 | 2465.3748 | 141873.0804 | 83039.5114 | 2404.2707 | 472.2515 | 267.7489 | 45.7648 | 15.3394 | 3103503.2288 | 1840953.4077 | 59353.2186 | 3057108.4466 | 1813847.3923 | 53184.8405 | 44542.9588 | 25254.1919 | 4316.5547 | 1851.8235 | 339767.539 | 201600.643 | 49221.5109 | 5490.8806 | 4059.1903 | 103.861 | 315758.4239 | 179023.2181 | 30599.4153 | 18518.2346 | 0.090418 | 0.057197 | 0.0014522 | 0.38271 | 0.21751 | 0.038271 | 0.028642 | 5000000 | scaled
221-1230F | 3690962.2783 | 3687572.8112 | 0 | 3389.4671 | 99.91% | 0% | 0.09183% | 892491.0902 | 3615073.2993 | 48989.1521 | 0 | 843501.9381 | 198681.5659 | 0 | 3416391.7334 | 221 |  | 396 | 221-1230F | 3690962.2783 | 2798471.1882 | 75888.979 | 3687572.8112 | 2795081.7211 | 72499.5119 | 0 | 0 | 0 | 3389.4671 | 202655.8916 | 153666.7395 | 3974.3257 | 202653.3411 | 153664.1891 | 3971.7752 | 0 | 0 | 0 | 2.5505 | 3485227.3716 | 2641725.4335 | 68835.6382 | 3484919.4701 | 2641417.532 | 68527.7367 | 0 | 0 | 0 | 307.9015 | 3079.0151 | 3079.0151 | 3079.0151 | 0 | 0 | 0 | 0 | 0 | 0 | 3079.0151 | 0.031093 | 0.023619 | 0.0005996 | 0 | 0 | 0 | 0.0047506 | 5000000 | scaled
221-1235F | 236176.8559 | 0 | 236176.8559 | 0 | 0% | 100% | 0% | 7336.7005 | 15314.0551 | 10.7303 | 6658.6029 | 667.3673 | 22.3976 | 13898.6472 | 1393.0103 | 221 |  | 397 | 221-1235F | 236176.8559 | 228840.1555 | 220862.8009 | 0 | 0 | 0 | 236176.8559 | 228840.1555 | 220862.8009 | 0 | 345.4206 | 334.6903 | 323.023 | 0 | 0 | 0 | 345.4206 | 334.6903 | 323.023 | 0 | 21483.3226 | 20815.9554 | 20090.3124 | 0 | 0 | 0 | 21483.3226 | 20815.9554 | 20090.3124 | 0 | 214348.1127 | 207689.5098 | 200449.4655 | 0 | 0 | 0 | 214348.1127 | 207689.5098 | 200449.4655 | 0 | 0 | 0 | 0 | 0.16409 | 0.16409 | 0.16409 | 0 | 5000000 | scaled
221-1237F | 2479.9057 | 0 | 2479.9057 | 0 | 0% | 100% | 0% | 76.5702 | 159.8282 | 0.050288 | 60.7093 | 15.8106 | 0.10497 | 126.7211 | 33.0021 | 221 |  | 398 | 221-1237F | 2479.9057 | 2403.3355 | 2320.0776 | 0 | 0 | 0 | 2479.9057 | 2403.3355 | 2320.0776 | 0 | 1.6287 | 1.5784 | 1.5237 | 0 | 0 | 0 | 1.6287 | 1.5784 | 1.5237 | 0 | 512.0624 | 496.2519 | 479.0604 | 0 | 0 | 0 | 512.0624 | 496.2519 | 479.0604 | 0 | 1966.2146 | 1905.5053 | 1839.4935 | 0 | 0 | 0 | 1966.2146 | 1905.5053 | 1839.4935 | 0 | 0 | 0 | 0 | 0.16564 | 0.16564 | 0.16564 | 0 | 5000000 | scaled
221-1249R | 329371.7883 | 200693.7086 | 116714.123 | 11963.9566 | 60.93% | 35.44% | 3.632% | 139788.4215 | 303211.7352 | 6758.4376 | 56034.4452 | 76995.5388 | 14166.4134 | 115412.0108 | 173633.3111 | 221 |  | 399 | 221-1249R | 329371.7883 | 189583.3667 | 26160.053 | 200693.7086 | 111696.7973 | 3279.4358 | 116714.123 | 65922.6128 | 10916.6607 | 11963.9566 | 14427.5731 | 7669.1355 | 261.1598 | 14118.476 | 7490.6332 | 224.0884 | 300.0947 | 169.4998 | 28.0689 | 9.0025 | 178602.1459 | 101606.6071 | 4968.8348 | 165870.3086 | 93942.4369 | 2792.823 | 11645.0233 | 6577.3562 | 1089.1978 | 1086.814 | 136342.0693 | 80307.6241 | 20930.0585 | 20704.9241 | 10263.7272 | 262.5244 | 104769.0051 | 59175.7568 | 9799.394 | 10868.1401 | 0.14162 | 0.067133 | 0.0017054 | 0.16493 | 0.093666 | 0.016493 | 0.016882 | 5000000 | scaled
221-1251R | 1814850.4819 | 1589147.8656 | 216249.2746 | 9453.3418 | 87.56% | 11.92% | 0.5209% | 973578.6311 | 1768873.6486 | 57980.9655 | 91460.564 | 824137.1016 | 103729.0852 | 188272.7798 | 1476871.7836 | 221 |  | 400 | 221-1251R | 1814850.4819 | 841271.8508 | 45976.8333 | 1589147.8656 | 709732.5827 | 16301.1492 | 216249.2746 | 122085.9264 | 20222.3423 | 9453.3418 | 104850.6006 | 46869.6352 | 1121.5154 | 104548.2898 | 46695.8648 | 1086.797 | 295.1975 | 166.657 | 27.6051 | 7.1133 | 1494752.7552 | 670615.6536 | 17880.9716 | 1473212.9461 | 658081.1832 | 15088.2541 | 20681.061 | 11675.7224 | 1933.9695 | 858.748 | 215247.1261 | 123786.5621 | 26974.3463 | 11386.6296 | 4955.5347 | 126.0981 | 195273.0161 | 110243.547 | 18260.7678 | 8587.4804 | 0.097077 | 0.042922 | 0.0010896 | 0.16444 | 0.093342 | 0.016444 | 0.013264 | 5000000 | scaled
221-23R | 3270237.5696 | 3013932.7368 | 250367.2007 | 5937.6321 | 92.16% | 7.656% | 0.1816% | 860096.8864 | 3182548.4219 | 54659.9493 | 102033.0406 | 703403.8965 | 215308.5906 | 217255.4375 | 2749984.3938 | 221 |  | 401 | 221-23R | 3270237.5696 | 2410140.6833 | 87689.1478 | 3013932.7368 | 2262792.5863 | 58336.507 | 250367.2007 | 141410.4649 | 23415.0087 | 5937.6321 | 219640.9518 | 164981.0025 | 4332.3612 | 219321.8077 | 164798.8016 | 4298.4639 | 314.6762 | 177.733 | 29.4294 | 4.4679 | 2806381.0117 | 2102977.1151 | 56396.6179 | 2784308.2986 | 2090275.4452 | 53843.3844 | 21533.3345 | 12162.2913 | 2013.8549 | 539.3786 | 244215.6062 | 142182.5656 | 26960.1687 | 10302.6305 | 7718.3395 | 194.6587 | 228519.19 | 129070.4405 | 21371.7244 | 5393.7856 | 0.026617 | 0.019963 | 0.000507 | 0.16449 | 0.093411 | 0.016449 | 0.0083448 | 5000000 | scaled
221-344R | 2735928.315 | 2629449.2922 | 98624.0236 | 7854.9991 | 96.11% | 3.605% | 0.2871% | 793834.2705 | 2671926.1773 | 41988.949 | 38440.1121 | 713405.2094 | 144771.6969 | 80640.493 | 2446513.9873 | 221 |  | 402 | 221-344R | 2735928.315 | 1942094.0445 | 64002.1377 | 2629449.2922 | 1878534.4294 | 46919.4345 | 98624.0236 | 55704.616 | 9227.7041 | 7854.9991 | 147436.0294 | 105447.0804 | 2664.3324 | 147315.908 | 105376.6614 | 2647.7357 | 114.2107 | 64.5083 | 10.6861 | 5.9106 | 2492491.8773 | 1779086.6679 | 45977.89 | 2480920.4232 | 1772240.3776 | 44248.4228 | 10857.9006 | 6132.7368 | 1015.9137 | 713.5535 | 96000.4083 | 57560.2962 | 15359.9153 | 1212.961 | 917.3904 | 23.276 | 87651.9123 | 49507.3709 | 8201.1043 | 7135.535 | 0.034505 | 0.024575 | 0.0006244 | 0.16595 | 0.094249 | 0.016595 | 0.011042 | 5000000 | scaled
221-35 | 710327.2529 | 706480.0529 | 3403.2868 | 443.9132 | 99.46% | 0.4791% | 0.06249% | 286282.068 | 701258.1436 | 15583.6697 | 2117.0331 | 268581.3652 | 38218.945 | 4415.6146 | 658623.5839 | 221 |  | 403 | 221-35 | 710327.2529 | 424045.1849 | 9069.1093 | 706480.0529 | 421678.5472 | 8306.6879 | 3403.2868 | 1922.7246 | 318.5082 | 443.9132 | 38670.753 | 23087.0832 | 451.8079 | 38664.6822 | 23083.5082 | 450.937 | 5.7367 | 3.241 | 0.53689 | 0.33403 | 666536.1864 | 397954.8213 | 7912.6025 | 666066.4236 | 397671.8805 | 7832.0868 | 429.4374 | 242.6154 | 40.1904 | 40.3254 | 5120.3135 | 3003.2804 | 704.6989 | 1748.9471 | 923.1585 | 23.6642 | 2968.1127 | 1676.8681 | 277.7809 | 403.2538 | 0.0054186 | 0.0031092 | 7.9e-05 | 0.16676 | 0.094731 | 0.016676 | 0.0006292 | 5000000 | scaled
221-37AE | 3934773.2911 | 3817749.2995 | 111681.1543 | 5342.8373 | 97.03% | 2.838% | 0.1358% | 1193250.5148 | 3842463.3494 | 69257.3141 | 47784.642 | 1076208.5588 | 226082.306 | 108736.9665 | 3507644.0769 | 221 |  | 404 | 221-37AE | 3934773.2911 | 2741522.7762 | 92309.9417 | 3817749.2995 | 2673103.0499 | 76518.608 | 111681.1543 | 63076.889 | 10448.4964 | 5342.8373 | 230720.0159 | 161462.7017 | 4637.7098 | 230520.2751 | 161348.1396 | 4615.3786 | 195.7204 | 110.5418 | 18.3109 | 4.0203 | 3580797.6723 | 2504589.1135 | 73153.5955 | 3568261.7656 | 2497297.6781 | 71540.8404 | 12050.5597 | 6806.0885 | 1127.408 | 485.347 | 123255.6029 | 75470.9609 | 14518.6364 | 18967.2587 | 14457.2322 | 362.3889 | 99434.8742 | 56160.2588 | 9302.7775 | 4853.47 | 0.025889 | 0.017931 | 0.0004556 | 0.16588 | 0.094203 | 0.016588 | 0.0074814 | 5000000 | scaled
221-38AE | 318096.6552 | 106237.0339 | 210983.2568 | 876.3646 | 33.4% | 66.33% | 0.2755% | 118547.047 | 296521.4748 | 1844.2006 | 77753.398 | 38949.4484 | 6987.3162 | 162056.8343 | 127477.3243 | 221 |  | 405 | 221-38AE | 318096.6552 | 199549.6083 | 21575.1805 | 106237.0339 | 79469.3077 | 963.053 | 210983.2568 | 119203.936 | 19735.7628 | 876.3646 | 7070.024 | 5225.8234 | 82.7079 | 6831.0666 | 5090.5274 | 59.7576 | 238.298 | 134.6366 | 22.2908 | 0.65944 | 131456.5515 | 92507.1031 | 3979.2272 | 99328.7268 | 74320.4957 | 901.7685 | 32048.2151 | 18106.9979 | 2997.8491 | 79.6096 | 179570.0797 | 101816.6818 | 17513.2454 | 77.2404 | 58.2846 | 1.5269 | 178696.7437 | 100962.3015 | 16715.6229 | 796.0956 | 0.002513 | 0.0018668 | 4.74e-05 | 0.16541 | 0.093963 | 0.016541 | 0.0012514 | 5000000 | scaled
221-675R | 2055423.9984 | 2045345.9152 | 6846.5017 | 3231.5815 | 99.51% | 0.3331% | 0.1572% | 951907.5877 | 2029583.6214 | 47224.2324 | 10505.4536 | 894177.9018 | 101467.5349 | 21267.9001 | 1906848.1864 | 221 |  | 406 | 221-675R | 2055423.9984 | 1103516.4107 | 25840.377 | 2045345.9152 | 1096416.3531 | 21968.0971 | 6846.5017 | 3868.4761 | 640.6984 | 3231.5815 | 102576.9848 | 55352.7524 | 1109.4499 | 102527.8077 | 55323.9082 | 1102.6438 | 46.7454 | 26.4125 | 4.3745 | 2.4317 | 1927880.2375 | 1033702.3357 | 21032.051 | 1926727.215 | 1032923.1544 | 20658.063 | 859.4634 | 485.6222 | 80.4289 | 293.5591 | 24966.7762 | 14461.3227 | 3698.8761 | 16090.8925 | 8169.2906 | 207.3903 | 5940.293 | 3356.4413 | 555.895 | 2935.5908 | 0.049303 | 0.024982 | 0.0006348 | 0.16686 | 0.094794 | 0.016686 | 0.0045574 | 5000000 | scaled
221-6R | 3904259.0089 | 3899503.1774 | 1257.6822 | 3498.1493 | 99.88% | 0.03221% | 0.0896% | 2041278.3744 | 3847334.4105 | 109154.0285 | 6644.2478 | 1925480.0981 | 205430.2257 | 12968.7966 | 3628935.3882 | 221 |  | 407 | 221-6R | 3904259.0089 | 1862980.6345 | 56924.5984 | 3899503.1774 | 1858771.8907 | 53308.7313 | 1257.6822 | 710.5945 | 117.7179 | 3498.1493 | 208256.7767 | 99102.7482 | 2826.551 | 208245.9331 | 99095.4765 | 2823.1502 | 8.2114 | 4.6394 | 0.76857 | 2.6322 | 3679611.6528 | 1754131.5547 | 50676.2646 | 3679035.7125 | 1753667.9158 | 50334.3262 | 258.1661 | 145.8647 | 24.1641 | 317.7743 | 16390.5794 | 9746.3316 | 3421.7828 | 12221.5319 | 6008.4985 | 151.2549 | 991.3048 | 560.0904 | 92.7852 | 3177.7427 | 0.043987 | 0.021638 | 0.0005492 | 0.1671 | 0.094924 | 0.01671 | 0.0049536 | 5000000 | scaled
221-782R | 618017.4372 | 609874.5108 | 4906.4472 | 3236.4792 | 98.68% | 0.7939% | 0.5237% | 147154.7028 | 598563.5955 | 8814.6556 | 125.7666 | 138214.2805 | 35736.6274 | 320.8824 | 562506.0857 | 221 |  | 408 | 221-782R | 618017.4372 | 470862.7344 | 19453.8417 | 609874.5108 | 462842.5097 | 11566.5003 | 4906.4472 | 4783.7455 | 4650.8622 | 3236.4792 | 36458.3453 | 27643.6897 | 721.718 | 36402.7514 | 27589.4252 | 668.8932 | 53.1586 | 51.8292 | 50.3895 | 2.4353 | 574645.8689 | 436431.5884 | 12139.7832 | 573349.0768 | 435159.8742 | 10895.228 | 1002.7881 | 977.7102 | 950.5512 | 294.004 | 6913.2229 | 6787.4563 | 6592.3405 | 122.6826 | 93.2103 | 2.3792 | 3850.5005 | 3754.2062 | 3649.9215 | 2940.0398 | 0.023554 | 0.017894 | 0.0004548 | 0.21911 | 0.21911 | 0.21911 | 0.0045352 | 5000000 | scaled
221-788 | 4481914.2591 | 4457135.1181 | 22835.2096 | 1943.9315 | 99.45% | 0.5095% | 0.04337% | 2139096.3392 | 4409030.5359 | 140661.8802 | 16351.996 | 1982082.4629 | 290137.245 | 34556.9165 | 4084336.3745 | 221 |  | 409 | 221-788 | 4481914.2591 | 2342817.92 | 72883.7233 | 4457135.1181 | 2327970.9401 | 68802.6325 | 22835.2096 | 12903.0484 | 2137.1592 | 1943.9315 | 294674.9716 | 154013.0913 | 4537.7266 | 294597.1203 | 153968.4652 | 4529.1146 | 76.3886 | 43.1634 | 7.1492 | 1.4627 | 4148831.1856 | 2166748.7227 | 64494.8111 | 4145727.8351 | 2164918.3658 | 64044.3058 | 2926.7624 | 1653.7688 | 273.9172 | 176.5881 | 38408.102 | 22056.106 | 3851.1856 | 16810.1627 | 9084.1091 | 229.2121 | 19832.0586 | 11206.1162 | 1856.0927 | 1765.8807 | 0.019879 | 0.010558 | 0.0002682 | 0.16714 | 0.094957 | 0.016714 | 0.002731 | 5000000 | scaled
221-823 | 17379.5628 | 0 | 17379.5628 | 0 | 0% | 100% | 0% | 534.5009 | 1113.3159 | 6.2229 | 427.5382 | 100.7398 | 12.9616 | 890.5225 | 209.8318 | 221 |  | 410 | 221-823 | 17379.5628 | 16845.062 | 16266.2469 | 0 | 0 | 0 | 17379.5628 | 16845.062 | 16266.2469 | 0 | 202.3392 | 196.1163 | 189.3775 | 0 | 0 | 0 | 202.3392 | 196.1163 | 189.3775 | 0 | 3275.606 | 3174.8661 | 3065.7742 | 0 | 0 | 0 | 3275.606 | 3174.8661 | 3065.7742 | 0 | 13901.6177 | 13474.0795 | 13011.0952 | 0 | 0 | 0 | 13901.6177 | 13474.0795 | 13011.0952 | 0 | 0 | 0 | 0 | 0.16737 | 0.16737 | 0.16737 | 0 | 5000000 | scaled
221-824 | 2324221.4688 | 2251306.5968 | 70429.858 | 2485.0141 | 96.86% | 3.03% | 0.1069% | 632457.8372 | 2282267.162 | 37847.9215 | 27948.6547 | 566661.2611 | 139536.9959 | 59775.481 | 2082954.6851 | 221 |  | 411 | 221-824 | 2324221.4688 | 1691763.6316 | 41954.3068 | 2251306.5968 | 1649479.4985 | 32877.8444 | 70429.858 | 39799.1191 | 6591.4483 | 2485.0141 | 141642.3202 | 103794.3987 | 2105.3243 | 141556.6197 | 103745.1571 | 2095.6088 | 83.8306 | 47.3717 | 7.8456 | 1.8699 | 2114633.9794 | 1547972.7183 | 31679.2943 | 2106570.2049 | 1543317.7932 | 30720.0015 | 7838.0341 | 4429.1848 | 733.5525 | 225.7404 | 67945.1692 | 39996.5145 | 8169.6882 | 3179.7722 | 2416.5482 | 62.2342 | 62507.9932 | 35322.5626 | 5850.0502 | 2257.4038 | 0.013232 | 0.0096596 | 0.0002458 | 0.16723 | 0.09502 | 0.016723 | 0.0035026 | 5000000 | scaled
222-1433R | 9617971.1979 | 9578744.2722 | 35404.348 | 3822.5777 | 99.59% | 0.3681% | 0.03974% | 3293439.1119 | 9442150.2272 | 166931.0234 | 13746.6949 | 3112761.3936 | 478326.2632 | 28710.3337 | 8935113.6302 | 222 |  | 412 | 222-1433R | 9617971.1979 | 6324532.086 | 175820.9707 | 9578744.2722 | 6300654.2865 | 168579.6325 | 35404.348 | 20055.2218 | 3418.7605 | 3822.5777 | 486802.352 | 319871.3286 | 8476.0887 | 486760.22 | 319846.2154 | 8469.4217 | 39.2557 | 22.2368 | 3.7907 | 2.8764 | 9095932.1634 | 5983170.7698 | 160818.5332 | 9091813.741 | 5980687.2954 | 160107.1303 | 3771.1769 | 2136.2288 | 364.1573 | 347.2456 | 35236.6825 | 21489.9876 | 6526.3487 | 170.3113 | 120.7757 | 3.0804 | 31593.9155 | 17896.7561 | 3050.8126 | 3472.4557 | 0.023884 | 0.014956 | 0.0003806 | 0.34341 | 0.19505 | 0.034341 | 0.0053688 | 5000000 | scaled
222-1503R | 1359395.3002 | 1293518.5316 | 63834.5508 | 2042.2177 | 95.15% | 4.696% | 0.1502% | 402489.0243 | 1316097.6508 | 20544.9661 | 26151.1839 | 355792.8744 | 68970.5566 | 56121.1819 | 1191005.9124 | 222 |  | 413 | 222-1503R | 1359395.3002 | 956906.2758 | 43297.6493 | 1293518.5316 | 918749.8004 | 35200.3844 | 63834.5508 | 36114.2577 | 6055.0473 | 2042.2177 | 70858.6117 | 50313.6456 | 1888.0552 | 70788.1356 | 50273.1066 | 1879.9792 | 68.9395 | 39.0024 | 6.5393 | 1.5367 | 1225055.3565 | 869262.4821 | 34049.4441 | 1218322.2848 | 865372.7006 | 33242.8572 | 6547.5552 | 3704.2651 | 621.0705 | 185.5165 | 63481.3319 | 37330.1481 | 7360.15 | 4408.1112 | 3103.9932 | 77.548 | 57218.0562 | 32370.9903 | 5427.4375 | 1855.1646 | 0.0096618 | 0.006805 | 0.0001728 | 0.22215 | 0.12624 | 0.022215 | 0.002837 | 5000000 | scaled
222-1523R | 7406689.0243 | 7156613.2119 | 240718.3378 | 9357.4746 | 96.62% | 3.25% | 0.1263% | 2516457.7548 | 7258845.2024 | 129345.4116 | 95621.296 | 2291491.0471 | 379136.2198 | 203373.4371 | 6676335.5455 | 222 |  | 414 | 222-1523R | 7406689.0243 | 4890231.2696 | 147843.8219 | 7156613.2119 | 4744673.5304 | 115687.1392 | 240718.3378 | 136200.2646 | 22799.2081 | 9357.4746 | 385430.2189 | 256084.8073 | 6293.9991 | 384858.3382 | 255758.1756 | 6233.4601 | 564.8396 | 319.5905 | 53.4978 | 7.0412 | 6788808.7547 | 4497317.7076 | 112473.2093 | 6763339.5351 | 4482537.949 | 109291.4081 | 24619.1803 | 13929.7193 | 2331.7618 | 850.0394 | 232450.0507 | 136828.7546 | 29076.6136 | 8415.3387 | 6377.4058 | 162.271 | 215534.318 | 121950.9548 | 20413.9486 | 8500.394 | 0.040774 | 0.02782 | 0.0007088 | 0.215 | 0.12218 | 0.0215 | 0.013238 | 5000000 | scaled
222-1986R | 79194348.7939 | 78602169.7569 | 578529.8095 | 13649.2275 | 99.25% | 0.7305% | 0.01724% | 25042472.619 | 77815789.7296 | 1461066.8789 | 222647.9592 | 23358757.7809 | 4554635.5248 | 466737.191 | 72794417.0138 | 222 |  | 415 | 222-1986R | 79194348.7939 | 54151876.1749 | 1378559.0643 | 78602169.7569 | 53810545.7009 | 1309138.9993 | 578529.8095 | 327681.2465 | 55770.8376 | 13649.2275 | 4631500.5985 | 3170433.7196 | 76865.0737 | 4630882.5843 | 3170079.2209 | 76796.216 | 607.7436 | 344.228 | 58.5871 | 10.2706 | 74034447.865 | 50675690.0841 | 1240030.8512 | 73965106.7104 | 50635877.4003 | 1232225.9192 | 68101.2494 | 38572.7786 | 6565.0268 | 1239.9052 | 528400.3304 | 305752.3712 | 61663.1395 | 6180.4621 | 4589.0797 | 116.8641 | 509820.8166 | 288764.2398 | 49147.2237 | 12399.0517 | 0.06916 | 0.047464 | 0.0012066 | 0.32662 | 0.18553 | 0.032662 | 0.019293 | 5000000 | scaled
222-1988R | 3619435.5667 | 3592933.5686 | 25896.588 | 605.4102 | 99.27% | 0.7155% | 0.01673% | 927412.818 | 3564102.0806 | 45359.1419 | 406.2907 | 881647.3854 | 174152.5712 | 887.2386 | 3389062.2708 | 222 |  | 416 | 222-1988R | 3619435.5667 | 2692022.7487 | 55333.4862 | 3592933.5686 | 2665948.8155 | 29728.6027 | 25896.588 | 25468.5231 | 24999.4733 | 605.4102 | 175649.4331 | 130290.2912 | 1496.8619 | 175623.0324 | 130264.3194 | 1471.36 | 25.9452 | 25.5163 | 25.0464 | 0.45555 | 3419669.8301 | 2538022.4447 | 30607.5593 | 3417235.6527 | 2535627.5947 | 28255.802 | 2379.1815 | 2339.8542 | 2296.7614 | 54.9959 | 24116.3035 | 23710.0128 | 23229.065 | 74.8835 | 56.9014 | 1.4407 | 23491.4613 | 23103.1526 | 22677.6655 | 549.9588 | 0.0034242 | 0.0026016 | 6.6e-05 | 0.34035 | 0.34035 | 0.34035 | 0.0008364 | 5000000 | scaled
222-1990R | 45106640.152 | 44939414.3997 | 158286.7628 | 8938.9896 | 99.63% | 0.3509% | 0.01982% | 12851427.1841 | 44116237.0729 | 634770.6534 | 66537.7649 | 12150118.7658 | 2187227.344 | 154148.0491 | 41774861.6797 | 222 |  | 417 | 222-1990R | 45106640.152 | 32255212.9679 | 990403.0792 | 44939414.3997 | 32156604.4363 | 966190.7931 | 158286.7628 | 89669.5421 | 15273.2965 | 8938.9896 | 2235328.9789 | 1600558.3254 | 48101.6348 | 2234648.9358 | 1600170.1648 | 48029.9393 | 673.3168 | 381.4343 | 64.9692 | 6.7263 | 42695379.2375 | 30545260.4717 | 920517.5578 | 42672107.4406 | 30531724.9735 | 917538.361 | 22459.773 | 12723.4743 | 2167.1728 | 812.0239 | 175931.9357 | 109394.1708 | 21783.8865 | 32658.0233 | 24709.298 | 622.4928 | 135153.673 | 76564.6335 | 13041.1545 | 8120.2393 | 0.063955 | 0.046383 | 0.0011794 | 0.33553 | 0.1906 | 0.033553 | 0.01263 | 5000000 | scaled
222-1992R | 288770.5254 | 249949.0365 | 38054.1024 | 767.3865 | 86.56% | 13.18% | 0.2657% | 64835.4227 | 245969.44 | 3362.5068 | 1136.9481 | 60335.9678 | 12736.9104 | 3057.4294 | 230175.1002 | 222 |  | 418 | 222-1992R | 288770.5254 | 223935.1027 | 42801.0854 | 249949.0365 | 186068.8461 | 5972.3298 | 38054.1024 | 37098.87 | 36061.3691 | 767.3865 | 13130.9307 | 9768.4238 | 394.0203 | 13051.1177 | 9690.5999 | 318.3566 | 79.2355 | 77.2465 | 75.0862 | 0.57743 | 241643.6914 | 181307.7237 | 11468.5912 | 235484.4437 | 175301.3352 | 5628.2269 | 6089.5379 | 5936.6786 | 5770.6544 | 69.7099 | 33995.9033 | 32858.9552 | 30938.4739 | 1413.475 | 1076.911 | 25.7463 | 31885.3291 | 31084.945 | 30215.6285 | 697.0992 | 0.0023848 | 0.0018118 | 4.62e-05 | 0.21767 | 0.21767 | 0.21767 | 0.0010976 | 5000000 | scaled
222-2013R | 7426975.8578 | 7133534.366 | 283167.7861 | 10273.7057 | 96.05% | 3.813% | 0.1383% | 2270922.5764 | 7276447.3754 | 124847.7209 | 110597.7806 | 2035477.0749 | 408533.7656 | 231820.0708 | 6636093.539 | 222 |  | 419 | 222-2013R | 7426975.8578 | 5156053.2814 | 150528.4824 | 7133534.366 | 4985593.9966 | 113420.6223 | 283167.7861 | 160185.579 | 26834.1544 | 10273.7057 | 415223.2117 | 290375.4908 | 6689.4461 | 414863.9716 | 290168.9143 | 6648.405 | 351.5095 | 198.8459 | 33.3105 | 7.7306 | 6746563.9571 | 4711086.8822 | 110470.4182 | 6715893.6997 | 4693331.6543 | 106719.1474 | 29736.9869 | 16821.9575 | 2818.0003 | 933.2705 | 265188.6889 | 154590.9083 | 33368.6182 | 2776.6946 | 2093.4281 | 53.0699 | 253079.2897 | 143164.7756 | 23982.8437 | 9332.7046 | 0.046653 | 0.031833 | 0.0008102 | 0.21814 | 0.12395 | 0.021814 | 0.014479 | 5000000 | scaled
222-2063 | 4859776.4656 | 4852517.2036 | 4593.5252 | 2665.7369 | 99.85% | 0.09452% | 0.05485% | 1197057.866 | 4740452.169 | 61998.8206 | 108.3667 | 1134950.6787 | 245771.8336 | 250.2879 | 4494430.0475 | 222 |  | 420 | 222-2063 | 4859776.4656 | 3662718.5996 | 119324.2966 | 4852517.2036 | 3655575.1445 | 112306.4975 | 4593.5252 | 4477.7182 | 4352.0623 | 2665.7369 | 251553.9637 | 189555.1431 | 5782.1301 | 251544.5868 | 189545.952 | 5773.1407 | 7.371 | 7.1852 | 6.9835 | 2.0059 | 4601936.4573 | 3466985.7787 | 107506.4098 | 4600921.8142 | 3465990.6106 | 106532.3731 | 772.4857 | 753.0107 | 731.8793 | 242.1574 | 6286.0446 | 6177.6779 | 6035.7567 | 50.8025 | 38.5819 | 0.98364 | 3813.6684 | 3717.5224 | 3613.1994 | 2421.5736 | 0.017105 | 0.012993 | 0.0003302 | 0.21691 | 0.21691 | 0.21691 | 0.0037484 | 5000000 | scaled
222-2085 | 16772308.2179 | 16218058.7657 | 533521.2809 | 20728.1713 | 96.7% | 3.181% | 0.1236% | 4824438.9284 | 16437567.0592 | 272521.1511 | 216524.2336 | 4335393.5437 | 946434.3842 | 473729.0669 | 15017403.608 | 222 |  | 421 | 222-2085 | 16772308.2179 | 11947869.2895 | 334741.1587 | 16218058.7657 | 11625329.5914 | 263573.0959 | 533521.2809 | 301811.5268 | 50439.8916 | 20728.1713 | 962210.1164 | 689688.9653 | 15775.7322 | 961446.5488 | 689250.2433 | 15689.4207 | 747.9703 | 423.1247 | 70.7142 | 15.5973 | 15271885.0928 | 10936491.5491 | 254481.4848 | 15210681.7591 | 10901051.2157 | 246990.2877 | 59320.3724 | 33557.3721 | 5608.2358 | 1882.9613 | 538213.0087 | 321688.7751 | 64483.9418 | 45930.4578 | 35028.1324 | 893.3875 | 473452.9383 | 267831.03 | 44760.9416 | 18829.6127 | 0.11419 | 0.081905 | 0.0020816 | 0.20777 | 0.11808 | 0.020777 | 0.029211 | 5000000 | scaled
222-2108 | 46876.9983 | 0 | 46876.9983 | 0 | 0% | 100% | 0% | 1158.445 | 2415.8485 | 1.5708 | 1028.5249 | 128.3493 | 3.2758 | 2144.9101 | 267.6626 | 222 |  | 422 | 222-2108 | 46876.9983 | 45718.5533 | 44461.1498 | 0 | 0 | 0 | 46876.9983 | 45718.5533 | 44461.1498 | 0 | 63.5636 | 61.9928 | 60.2878 | 0 | 0 | 0 | 63.5636 | 61.9928 | 60.2878 | 0 | 5193.7112 | 5065.3619 | 4926.0486 | 0 | 0 | 0 | 5193.7112 | 5065.3619 | 4926.0486 | 0 | 41619.7235 | 40591.1986 | 39474.8134 | 0 | 0 | 0 | 41619.7235 | 40591.1986 | 39474.8134 | 0 | 0 | 0 | 0 | 0.22216 | 0.22216 | 0.22216 | 0 | 5000000 | scaled
223-47AE | 19415.2625 | 18727.7624 | 0 | 687.5002 | 96.46% | 0% | 3.541% | 10050.6169 | 18696.5941 | 744.2009 | 989.5519 | 8316.864 | 1361.4952 | 1765.6999 | 15569.3989 | 223 |  | 423 | 223-47AE | 19415.2625 | 9364.6457 | 718.6684 | 18727.7624 | 8677.1455 | 31.1683 | 0 | 0 | 0 | 687.5002 | 1364.8436 | 620.6427 | 3.3483 | 1364.3263 | 620.1253 | 2.831 | 0 | 0 | 0 | 0.51732 | 15649.0902 | 7332.2262 | 79.6913 | 15586.6373 | 7269.7732 | 17.2383 | 0 | 0 | 0 | 62.453 | 2401.3287 | 1411.7768 | 635.6288 | 1776.7988 | 787.2469 | 11.0989 | 0 | 0 | 0 | 624.5299 | 0.0034198 | 0.0014806 | 3.76e-05 | 0 | 0 | 0 | 0.0009874 | 5000000 | scaled
223-526R | 76100.6588 | 74311.9718 | 0 | 1788.6871 | 97.65% | 0% | 2.35% | 44971.8446 | 73485.6573 | 3643.2347 | 1923.3354 | 39405.2745 | 5975.6035 | 3390.6192 | 64119.4346 | 223 |  | 424 | 223-526R | 76100.6588 | 31128.8142 | 2615.0015 | 74311.9718 | 29340.1272 | 826.3144 | 0 | 0 | 0 | 1788.6871 | 6039.1353 | 2395.9006 | 63.5318 | 6037.7894 | 2394.5547 | 62.1859 | 0 | 0 | 0 | 1.3459 | 65004.2333 | 25598.9587 | 884.7986 | 64841.7477 | 25436.4732 | 722.3131 | 0 | 0 | 0 | 162.4856 | 5057.2903 | 3133.9549 | 1666.671 | 3432.4347 | 1509.0993 | 41.8155 | 0 | 0 | 0 | 1624.8556 | 0.0073658 | 0.0031894 | 8.12e-05 | 0 | 0 | 0 | 0.0025218 | 5000000 | scaled
223-536R | 17368.5899 | 17079.2265 | 0 | 289.3634 | 98.33% | 0% | 1.666% | 8800.9112 | 17079.1983 | 690.8241 | 1.7913 | 8108.2958 | 1294.252 | 3.1473 | 15781.7991 | 223 |  | 425 | 223-536R | 17368.5899 | 8567.6787 | 289.3916 | 17079.2265 | 8278.3153 | 0.028132 | 0 | 0 | 0 | 289.3634 | 1294.4697 | 603.6456 | 0.21774 | 1294.252 | 603.4279 | 0 | 0 | 0 | 0 | 0.21774 | 15808.0851 | 7699.7893 | 26.286 | 15781.7991 | 7673.5033 | 0 | 0 | 0 | 0 | 26.286 | 266.0351 | 264.2438 | 262.8879 | 3.1754 | 1.3841 | 0.028132 | 0 | 0 | 0 | 262.8597 | 0.0014854 | 0.0006432 | 1.64e-05 | 0 | 0 | 0 | 0.0003998 | 5000000 | scaled
230-1008R | 171588.2724 | 170502.5113 | 778.7361 | 307.025 | 99.37% | 0.4538% | 0.1789% | 43010.5084 | 166292.7573 | 2752.3823 | 394.1691 | 39863.957 | 10542.0812 | 1517.2388 | 154233.4373 | 230 |  | 426 | 230-1008R | 171588.2724 | 128577.764 | 5295.5151 | 170502.5113 | 127557.9047 | 4347.2342 | 778.7361 | 712.8343 | 641.2559 | 307.025 | 10814.778 | 8062.3957 | 272.6968 | 10813.9539 | 8061.6218 | 271.9774 | 0.59308 | 0.54289 | 0.48838 | 0.23103 | 158361.1146 | 118497.1576 | 4127.6773 | 158271.0692 | 118412.3722 | 4048.6049 | 62.1551 | 56.8951 | 51.182 | 27.8904 | 2412.3797 | 2018.2106 | 895.141 | 1417.4882 | 1083.9107 | 26.6519 | 715.988 | 655.3963 | 589.5855 | 278.9036 | 0.0021824 | 0.001658 | 4.22e-05 | 0.053074 | 0.053074 | 0.053074 | 0.0004404 | 5000000 | scaled
230-127AE | 2000465.4437 | 1900120.7077 | 92848.8962 | 7495.8398 | 94.98% | 4.641% | 0.3747% | 957109.9164 | 1965601.6827 | 58162.0042 | 37908.1664 | 861039.7458 | 119397.6268 | 79307.7963 | 1766896.2597 | 230 |  | 427 | 230-127AE | 2000465.4437 | 1043355.5273 | 34863.7609 | 1900120.7077 | 983813.2855 | 19722.5605 | 92848.8962 | 52046.4019 | 7645.3606 | 7495.8398 | 120687.9088 | 62525.9046 | 1290.282 | 120538.5137 | 62439.6826 | 1272.8046 | 143.7548 | 80.5817 | 11.837 | 5.6404 | 1786692.6641 | 925652.9182 | 19796.4044 | 1777579.9797 | 920245.5738 | 18421.1897 | 8431.7571 | 4726.4172 | 694.2875 | 680.9272 | 93084.8708 | 55176.7044 | 13777.0745 | 2002.2143 | 1128.0291 | 28.5662 | 84273.3843 | 47239.4031 | 6939.2361 | 6809.2722 | 0.030463 | 0.015632 | 0.0003958 | 0.052935 | 0.030125 | 0.0052934 | 0.01059 | 5000000 | scaled
230-133AE | 6388693.9467 | 6277695.8362 | 103148.0092 | 7850.1013 | 98.26% | 1.615% | 0.1229% | 2088883.5687 | 6255094.1319 | 120310.6787 | 42241.6741 | 1926331.2159 | 361399.4823 | 88961.7774 | 5804732.8722 | 230 |  | 428 | 230-133AE | 6388693.9467 | 4299810.3781 | 133599.8149 | 6277695.8362 | 4234124.6282 | 117257.1725 | 103148.0092 | 57835.6486 | 8492.541 | 7850.1013 | 368224.6719 | 247913.9932 | 6825.1896 | 368089.4371 | 247835.5714 | 6808.6347 | 129.3279 | 72.5149 | 10.648 | 5.9069 | 5916644.1009 | 3990312.885 | 111911.2288 | 5906161.2177 | 3984121.8108 | 110393.74 | 9769.7746 | 5477.9657 | 804.3802 | 713.1086 | 103825.1739 | 61583.4998 | 14863.3964 | 3445.1814 | 2167.2459 | 54.7978 | 93248.9067 | 52285.1681 | 7677.5128 | 7131.0858 | 0.03163 | 0.020694 | 0.0005252 | 0.05296 | 0.030152 | 0.005296 | 0.010974 | 5000000 | scaled
230-1586R | 2072883.7273 | 1887664.4635 | 179000.8324 | 6218.4314 | 91.06% | 8.635% | 0.3% | 1055899.6147 | 2033722.0919 | 60234.6735 | 76702.537 | 918962.4041 | 115992.8123 | 162271.0938 | 1755458.1858 | 230 |  | 429 | 230-1586R | 2072883.7273 | 1016984.1127 | 39161.6354 | 1887664.4635 | 910393.2821 | 18207.0985 | 179000.8324 | 100372.3992 | 14736.1055 | 6218.4314 | 117181.9289 | 56947.2554 | 1189.1166 | 116911.1823 | 56793.3824 | 1162.5337 | 266.0674 | 149.1938 | 21.9038 | 4.6792 | 1774166.3087 | 855203.9046 | 18708.1229 | 1757787.085 | 845771.3332 | 16841.3332 | 15814.3371 | 8867.6848 | 1301.9031 | 564.8866 | 181535.4898 | 104832.9527 | 19264.3959 | 12966.1962 | 7828.5665 | 203.2317 | 162920.4279 | 91355.5205 | 13412.2986 | 5648.8657 | 0.023023 | 0.011316 | 0.0002882 | 0.052837 | 0.030083 | 0.0052836 | 0.0087656 | 5000000 | scaled
230-1606R | 536383.8374 | 423572.2986 | 111094.9689 | 1716.5698 | 78.97% | 20.71% | 0.32% | 246826.3307 | 524033.3688 | 12754.8479 | 45321.861 | 188749.6219 | 27336.1896 | 94385.5756 | 402311.6036 | 230 |  | 430 | 230-1606R | 536383.8374 | 289557.5067 | 12350.4686 | 423572.2986 | 225538.0847 | 1483.2879 | 111094.9689 | 62302.8522 | 9150.6108 | 1716.5698 | 27474.5702 | 14719.7223 | 138.3806 | 27291.1804 | 14616.3087 | 122.09 | 182.0981 | 102.1219 | 14.999 | 1.2917 | 404628.7091 | 215879.0872 | 2317.1054 | 394526.7317 | 210145.3408 | 1341.9407 | 9946.043 | 5577.812 | 819.2303 | 155.9344 | 104280.5581 | 58958.6971 | 9894.9825 | 1754.3865 | 776.4351 | 19.2572 | 100966.8278 | 56622.9183 | 8316.3815 | 1559.3438 | 0.0073136 | 0.0038624 | 9.78e-05 | 0.053089 | 0.030232 | 0.005309 | 0.002415 | 5000000 | scaled
230-181 | 788722.3733 | 774443.4469 | 12668.9441 | 1609.9824 | 98.19% | 1.606% | 0.2041% | 220256.0813 | 764095.9201 | 13738.6076 | 15672.1708 | 190845.303 | 48155.9217 | 56709.1733 | 659230.8251 | 230 |  | 431 | 230-181 | 788722.3733 | 568466.292 | 24626.4532 | 774443.4469 | 559752.0009 | 21972.6403 | 12668.9441 | 7104.3088 | 1043.8305 | 1609.9824 | 49481.1354 | 35742.5279 | 1325.2137 | 49462.3213 | 35731.4455 | 1322.5519 | 17.6026 | 9.871 | 1.4503 | 1.2115 | 679224.2342 | 488378.9312 | 19993.4091 | 677952.3632 | 487601.4708 | 19754.4142 | 1125.619 | 631.2085 | 92.743 | 146.2519 | 60017.0037 | 44344.8329 | 3307.8304 | 47028.7623 | 36419.0846 | 895.6742 | 11525.7224 | 6463.2293 | 949.6372 | 1462.519 | 0.0075204 | 0.0054758 | 0.0001396 | 0.053426 | 0.030417 | 0.0053426 | 0.0022952 | 5000000 | scaled
230-2060R | 3473455.3851 | 3392757.0341 | 74143.8925 | 6554.4586 | 97.68% | 2.135% | 0.1887% | 1087078.5154 | 3397246.5356 | 64168.9969 | 30066.0971 | 992843.4214 | 201253.8339 | 63641.5515 | 3132351.1503 | 230 |  | 432 | 230-2060R | 3473455.3851 | 2386376.8698 | 76208.8496 | 3392757.0341 | 2338252.1244 | 63547.2118 | 74143.8925 | 41570.2867 | 6107.1792 | 6554.4586 | 205124.4977 | 140955.5008 | 3870.6639 | 205029.8644 | 140900.276 | 3858.3432 | 89.7013 | 50.2928 | 7.3886 | 4.932 | 3193157.4165 | 2200313.9951 | 60806.2662 | 3185784.7322 | 2195918.7672 | 59652.6156 | 6777.2728 | 3799.8163 | 558.2391 | 595.4115 | 75173.4709 | 45107.3739 | 11531.9195 | 1942.4375 | 1433.0812 | 36.253 | 67276.9184 | 37720.1775 | 5541.5515 | 5954.1151 | 0.025912 | 0.017388 | 0.0004414 | 0.053361 | 0.030378 | 0.005336 | 0.0091416 | 5000000 | scaled
230-2067 | 121606.7192 | 113065.5535 | 8323.9346 | 217.2311 | 92.98% | 6.845% | 0.1786% | 70127.2529 | 120703.3234 | 3980.2867 | 3337.0023 | 62809.9639 | 6836.3402 | 6970.8566 | 106896.1266 | 230 |  | 433 | 230-2067 | 121606.7192 | 51479.4663 | 903.3958 | 113065.5535 | 46594.504 | 0.054413 | 8323.9346 | 4667.7312 | 686.1103 | 217.2311 | 6837.4169 | 2857.1301 | 1.0766 | 6826.1745 | 2850.7541 | 0 | 11.0789 | 6.2126 | 0.91319 | 0.16346 | 106975.3509 | 44165.3869 | 79.2242 | 106233.8712 | 43740.927 | 0 | 721.7463 | 404.7266 | 59.4908 | 19.7334 | 7793.9514 | 4456.9492 | 823.0949 | 5.5078 | 2.823 | 0.054413 | 7591.1095 | 4256.792 | 625.7063 | 197.3342 | 0.0006702 | 0.000351 | 8.8e-06 | 0.053646 | 0.030541 | 0.0053646 | 0.000303 | 5000000 | scaled
230-371AE | 195725.1119 | 159934.5688 | 34850.1819 | 940.3612 | 81.71% | 17.81% | 0.4804% | 106086.2557 | 190015.5008 | 6073.867 | 13580.4955 | 86431.8932 | 10650.9483 | 28352.5604 | 151011.9921 | 230 |  | 434 | 230-371AE | 195725.1119 | 89638.8563 | 5709.6111 | 159934.5688 | 69155.295 | 1896.4971 | 34850.1819 | 19543.2001 | 2872.7528 | 940.3612 | 10769.4842 | 4695.6172 | 118.5359 | 10729.2104 | 4672.7218 | 114.5668 | 39.5662 | 22.1879 | 3.2615 | 0.70759 | 153211.8329 | 66779.9397 | 2199.8407 | 149074.0892 | 64422.0662 | 1780.3788 | 4052.3206 | 2272.4505 | 334.0389 | 85.4231 | 31743.7948 | 18163.2993 | 3391.2345 | 131.2692 | 60.507 | 1.5515 | 30758.2951 | 17248.5617 | 2535.4524 | 854.2306 | 0.0039598 | 0.0019024 | 4.82e-05 | 0.053708 | 0.03058 | 0.0053708 | 0.0013382 | 5000000 | scaled
231-1136R | 2730917.723 | 2684541.5144 | 37502.001 | 8874.2076 | 98.3% | 1.373% | 0.325% | 1368552.045 | 2649940.3834 | 104596.4987 | 38822.3428 | 1225133.2034 | 202504.2583 | 80870.688 | 2366565.4371 | 231 |  | 435 | 231-1136R | 2730917.723 | 1362365.6781 | 80977.3396 | 2684541.5144 | 1332641.6348 | 69587.1936 | 37502.001 | 20849.8357 | 2515.9385 | 8874.2076 | 207840.248 | 103243.7493 | 5335.9897 | 207777.471 | 103205.8824 | 5325.5486 | 56.0995 | 31.1894 | 3.7636 | 6.6776 | 2431252.3556 | 1206119.1522 | 64686.9185 | 2427050.5837 | 1203425.1568 | 63652.9728 | 3395.6328 | 1887.8562 | 227.8066 | 806.1391 | 91825.1194 | 53002.7766 | 10954.4314 | 49713.4598 | 26010.5955 | 608.6722 | 34050.2687 | 18930.7901 | 2284.3683 | 8061.3909 | 0.036478 | 0.018212 | 0.000795 | 0.0056314 | 0.0032192 | 0.0005632 | 0.012545 | 5000000 | scaled
231-1635R | 5142094.9811 | 5074261.8471 | 46327.9087 | 21505.2253 | 98.68% | 0.901% | 0.4182% | 2720917.7662 | 5050015.2088 | 210030.1497 | 25973.2432 | 2484914.3734 | 390819.1064 | 52887.5781 | 4606308.5243 | 231 |  | 436 | 231-1635R | 5142094.9811 | 2421177.2149 | 92079.7724 | 5074261.8471 | 2373876.1179 | 67467.2007 | 46327.9087 | 25795.8717 | 3107.3463 | 21505.2253 | 396005.847 | 185975.6973 | 5186.7406 | 395921.0114 | 185921.2883 | 5165.9538 | 68.6536 | 38.2271 | 4.6048 | 16.182 | 4670689.7528 | 2185775.3794 | 64381.2285 | 4664361.6208 | 2181386.0159 | 62134.2632 | 4374.5826 | 2435.8141 | 293.4159 | 1953.5494 | 75399.3814 | 49426.1382 | 22511.8033 | 13979.215 | 6568.8137 | 166.9837 | 41884.6724 | 23321.8306 | 2809.3257 | 19535.494 | 0.080559 | 0.038025 | 0.0009656 | 0.0056128 | 0.0032132 | 0.0005612 | 0.030305 | 5000000 | scaled
232-40AE | 11429.7304 | 51.7014 | 11267.6057 | 110.4233 | 0.4523% | 98.58% | 0.9661% | 5008.6462 | 10564.7259 | 6.5312 | 4570.4191 | 431.6958 | 17.3602 | 9607.1241 | 940.2416 | 232 |  | 437 | 232-40AE | 11429.7304 | 6421.0842 | 865.0044 | 51.7014 | 42.7945 | 0.10216 | 11267.6057 | 6267.8664 | 754.479 | 110.4233 | 18.3519 | 11.8207 | 0.99175 | 4.6986 | 4.1889 | 0 | 13.5702 | 7.5487 | 0.90866 | 0.08309 | 1015.4862 | 583.7903 | 75.2445 | 31.5368 | 31.9947 | 0 | 973.9185 | 541.7647 | 65.2136 | 10.0309 | 10395.8923 | 5825.4732 | 788.7682 | 15.466 | 6.6109 | 0.10216 | 10280.117 | 5718.5529 | 688.3567 | 100.3093 | 0.0001712 | 7.4e-05 | 1.8e-06 | 0.0056362 | 0.0032236 | 0.0005636 | 0.000147 | 5000000 | scaled
233-123R | 3035804.5149 | 3000562.2494 | 24952.003 | 10290.2625 | 98.84% | 0.8219% | 0.339% | 1507987.041 | 2979546.0527 | 94277.3324 | 14005.9711 | 1399703.7374 | 186263.0386 | 29066.9408 | 2764216.0734 | 233 |  | 438 | 233-123R | 3035804.5149 | 1527817.4739 | 56258.4622 | 3000562.2494 | 1503607.552 | 44293.226 | 24952.003 | 13919.6594 | 1674.9736 | 10290.2625 | 189062.3976 | 94785.0652 | 2799.359 | 189020.0375 | 94758.0107 | 2789.2922 | 34.6171 | 19.3114 | 2.3238 | 7.7431 | 2806713.6514 | 1407009.914 | 42497.578 | 2803353.4939 | 1404722.1216 | 41399.9928 | 2425.383 | 1353.0179 | 162.8107 | 934.7745 | 40028.4659 | 26022.4948 | 10961.5251 | 8188.7181 | 4127.4197 | 103.941 | 22492.0029 | 12547.3302 | 1509.8392 | 9347.7449 | 0.041026 | 0.02033 | 0.0005178 | 0.005638 | 0.0032332 | 0.0005638 | 0.014587 | 5000000 | scaled
233-41R | 718990.9984 | 701522.1709 | 9758.7762 | 7710.0513 | 97.57% | 1.357% | 1.072% | 333403.5097 | 703458.71 | 26828.1695 | 8182.4797 | 298392.8605 | 56327.0306 | 18701.7445 | 628429.9349 | 233 |  | 439 | 233-41R | 718990.9984 | 385587.4887 | 15532.2884 | 701522.1709 | 372448.8272 | 7168.8402 | 9758.7762 | 5428.6102 | 653.3969 | 7710.0513 | 56972.0629 | 30143.8934 | 645.0323 | 56952.98 | 30130.7037 | 638.3414 | 13.2813 | 7.3881 | 0.88924 | 5.8016 | 635579.1265 | 337186.2659 | 7149.1915 | 633784.8261 | 335877.3573 | 6375.5624 | 1093.914 | 608.5223 | 73.2428 | 700.3863 | 26439.8091 | 18257.3294 | 7738.0646 | 10784.3648 | 6440.7662 | 154.9364 | 8651.5809 | 4812.6998 | 579.2648 | 7003.8634 | 0.028021 | 0.014197 | 0.0003606 | 0.0056456 | 0.003229 | 0.0005646 | 0.010821 | 5000000 | scaled
233-81F | 447779.3576 | 425199.1869 | 19472.4826 | 3107.6881 | 94.96% | 4.349% | 0.694% | 205332.709 | 435625.6051 | 13632.4766 | 8491.5453 | 183208.6872 | 28782.6394 | 18175.8286 | 388667.1371 | 233 |  | 440 | 233-81F | 447779.3576 | 242446.6485 | 12153.7524 | 425199.1869 | 228492.0102 | 7740.7686 | 19472.4826 | 10846.9502 | 1305.2958 | 3107.6881 | 29336.0459 | 15703.5694 | 553.4066 | 29308.3206 | 15687.0894 | 549.3664 | 25.3869 | 14.1415 | 1.7018 | 2.3384 | 396241.6157 | 213032.9286 | 7574.4786 | 394045.5042 | 211684.5571 | 7163.8862 | 1913.807 | 1066.0669 | 128.2879 | 282.3045 | 22201.6959 | 13710.1506 | 4025.8673 | 1845.3621 | 1120.3637 | 27.5161 | 17533.2887 | 9766.7418 | 1175.3061 | 2823.0451 | 0.012005 | 0.0062002 | 0.0001578 | 0.005644 | 0.0032322 | 0.0005644 | 0.0043904 | 5000000 | scaled
233-86F | 2341674.0922 | 2011556.5905 | 318414.1585 | 11703.3432 | 85.9% | 13.6% | 0.4998% | 1172205.5369 | 2289635.7915 | 68258.4173 | 128579.9125 | 975367.207 | 131737.0751 | 268567.2523 | 1889331.4641 | 233 |  | 441 | 233-86F | 2341674.0922 | 1169468.5553 | 52038.3007 | 2011556.5905 | 979071.5953 | 14108.3368 | 318414.1585 | 178693.6168 | 26226.6207 | 11703.3432 | 132813.6644 | 64555.2471 | 1076.5893 | 132393.7922 | 64315.7511 | 1033.9249 | 411.0658 | 230.6896 | 33.858 | 8.8064 | 1905780.8589 | 930413.6519 | 16449.3948 | 1876225.8902 | 913360.9343 | 13039.4863 | 28491.829 | 15989.5778 | 2346.7687 | 1063.1397 | 303079.5689 | 174499.6564 | 34512.3166 | 2936.9081 | 1394.91 | 34.9256 | 289511.2637 | 162473.3494 | 23845.9939 | 10631.3971 | 0.050826 | 0.024309 | 0.0006208 | 0.053128 | 0.030269 | 0.0053128 | 0.016442 | 5000000 | scaled
234-48R | 4939379.2504 | 4912538.7809 | 19343.3759 | 7497.0936 | 99.46% | 0.3916% | 0.1518% | 2686077.1743 | 4880749.6511 | 233294.8342 | 9557.0152 | 2443225.3249 | 423830.6789 | 20066.5119 | 4436852.4603 | 234 |  | 442 | 234-48R | 4939379.2504 | 2253302.076 | 58629.5992 | 4912538.7809 | 2235038.4791 | 49835.5898 | 19343.3759 | 10766.5033 | 1296.9158 | 7497.0936 | 428202.0575 | 194907.2233 | 4371.3786 | 428170.9912 | 194887.4305 | 4364.0326 | 25.4249 | 14.1515 | 1.7047 | 5.6413 | 4483071.5279 | 2039846.203 | 46219.0676 | 4480652.2077 | 2038197.6375 | 45421.4801 | 1738.2791 | 967.5244 | 116.5464 | 681.0411 | 28105.6649 | 18548.6497 | 8039.153 | 3715.582 | 1953.4111 | 50.0772 | 17579.6718 | 9784.8274 | 1178.6647 | 6810.4111 | 0.031747 | 0.014372 | 0.0003646 | 0.0056438 | 0.0032294 | 0.0005644 | 0.010541 | 5000000 | scaled
235-897R | 4375038.1439 | 3877449.0208 | 492961.9345 | 4627.1887 | 88.63% | 11.27% | 0.1058% | 2257381.3067 | 4293593.8531 | 127647.9096 | 201946.225 | 1927787.1721 | 239786.4067 | 420905.4182 | 3632902.0281 | 235 |  | 443 | 235-897R | 4375038.1439 | 2117656.8372 | 81444.2908 | 3877449.0208 | 1835764.6656 | 32625.9871 | 492961.9345 | 277264.9829 | 44191.1151 | 4627.1887 | 242022.0499 | 114374.1403 | 2235.6431 | 241411.3022 | 114029.1036 | 2177.7235 | 607.2658 | 341.5549 | 54.4378 | 3.4818 | 3667827.3058 | 1740040.1336 | 34925.2777 | 3619727.8244 | 1712802.8029 | 30230.788 | 47679.1443 | 26816.9938 | 4274.1526 | 420.337 | 465188.7883 | 263242.5633 | 44283.37 | 16309.8941 | 8932.7592 | 217.4755 | 444675.5243 | 250106.4342 | 39862.5246 | 4203.3699 | 0.014436 | 0.0071858 | 0.0001826 | 0.097015 | 0.055062 | 0.0097014 | 0.0064498 | 5000000 | scaled
235-899R | 23678661.1441 | 23291809.548 | 377288.9261 | 9562.67 | 98.37% | 1.593% | 0.04039% | 11253213.3023 | 23296131.4736 | 713792.5467 | 161600.3515 | 10377820.4041 | 1476002.9182 | 342963.7692 | 21477164.7861 | 235 |  | 444 | 235-899R | 23678661.1441 | 12425447.8418 | 382529.6705 | 23291809.548 | 12203361.965 | 339049.0287 | 377288.9261 | 212523.2068 | 33917.9718 | 9562.67 | 1497868.1457 | 784075.5991 | 21865.2275 | 1497210.7051 | 783702.1267 | 21799.5754 | 650.245 | 366.2767 | 58.4565 | 7.1956 | 21797730.0273 | 11419909.6232 | 320565.2412 | 21764359.1968 | 11400732.796 | 316774.6444 | 32502.151 | 18308.1476 | 2921.9173 | 868.6795 | 383062.9711 | 221462.6196 | 40099.2019 | 30239.6461 | 18927.0423 | 474.809 | 344136.53 | 193848.7824 | 30937.598 | 8686.7949 | 0.034984 | 0.017852 | 0.0004542 | 0.10653 | 0.060524 | 0.010653 | 0.013452 | 5000000 | scaled
235-911 | 849.9119 | 0 | 849.9119 | 0 | 0% | 100% | 0% | 40.9679 | 85.3186 | 0.53149 | 32.0814 | 8.355 | 1.1069 | 66.8119 | 17.3999 | 235 |  | 445 | 235-911 | 849.9119 | 808.944 | 764.5932 | 0 | 0 | 0 | 849.9119 | 808.944 | 764.5932 | 0 | 11.0261 | 10.4946 | 9.9192 | 0 | 0 | 0 | 11.0261 | 10.4946 | 9.9192 | 0 | 173.3309 | 164.9759 | 155.931 | 0 | 0 | 0 | 173.3309 | 164.9759 | 155.931 | 0 | 665.5549 | 633.4735 | 598.743 | 0 | 0 | 0 | 665.5549 | 633.4735 | 598.743 | 0 | 0 | 0 | 0 | 0.10783 | 0.10783 | 0.10783 | 0 | 5000000 | scaled
236-1535R | 9719042.1331 | 9595870.9957 | 117498.9316 | 5672.2058 | 98.73% | 1.209% | 0.05836% | 4564578.8009 | 9616312.5244 | 318440.193 | 48430.8488 | 4197707.7591 | 668556.2252 | 101380.3024 | 8846375.9968 | 236 |  | 446 | 236-1535R | 9719042.1331 | 5154463.3323 | 102729.6087 | 9595870.9957 | 5082708.6399 | 86501.3435 | 117498.9316 | 66082.4865 | 10556.0594 | 5672.2058 | 674768.9165 | 356328.7235 | 6212.6914 | 674594.2054 | 356228.5967 | 6193.1107 | 170.443 | 95.8587 | 15.3125 | 4.2682 | 8928097.364 | 4730389.605 | 81721.3672 | 8916832.5062 | 4723828.6686 | 80240.361 | 10749.5908 | 6045.6693 | 965.7392 | 515.2671 | 116175.8526 | 67745.0037 | 14795.5502 | 4444.284 | 2651.3746 | 67.8718 | 106578.8979 | 59940.9585 | 9575.0077 | 5152.6706 | 0.020791 | 0.010393 | 0.0002644 | 0.099676 | 0.056554 | 0.0099676 | 0.0080044 | 5000000 | scaled
236-1561R | 2823578.0947 | 2746271.3929 | 73882.5515 | 3424.1503 | 97.26% | 2.617% | 0.1213% | 1052926.0173 | 2786015.1892 | 60772.2569 | 29120.2002 | 963033.5602 | 161629.0288 | 61027.1461 | 2563359.0144 | 236 |  | 447 | 236-1561R | 2823578.0947 | 1770652.0774 | 37562.9054 | 2746271.3929 | 1725475.0496 | 27249.0701 | 73882.5515 | 41752.8775 | 6889.685 | 3424.1503 | 163306.9087 | 102534.6518 | 1677.8799 | 163212.7156 | 102480.3005 | 1666.7599 | 91.6165 | 51.7748 | 8.5434 | 2.5766 | 2589914.4422 | 1626880.882 | 26555.4278 | 2582361.6156 | 1622477.322 | 25569.0667 | 7241.7744 | 4092.5078 | 675.3089 | 311.0522 | 70356.7438 | 41236.5435 | 9329.5977 | 697.0616 | 517.4271 | 13.2434 | 66549.1606 | 37608.5949 | 6205.8327 | 3110.5216 | 0.015422 | 0.00959 | 0.0002446 | 0.15742 | 0.089475 | 0.015742 | 0.0048156 | 5000000 | scaled
236-1563R | 2260662.3602 | 2229175.5852 | 29107.6182 | 2379.1568 | 98.61% | 1.288% | 0.1052% | 1023409.227 | 2233194.2676 | 59548.8994 | 10246.0479 | 953614.2798 | 130152.5075 | 21383.5885 | 2081658.1716 | 236 |  | 448 | 236-1563R | 2260662.3602 | 1237253.1332 | 27468.0926 | 2229175.5852 | 1218428.4313 | 22374.5924 | 29107.6182 | 16445.545 | 2714.3434 | 2379.1568 | 131504.0368 | 71955.1374 | 1351.5293 | 131440.1373 | 71918.256 | 1343.9472 | 62.1092 | 35.0912 | 5.7918 | 1.7902 | 2103426.286 | 1149812.0062 | 21768.1144 | 2097596.0817 | 1146423.9767 | 21028.466 | 5614.0801 | 3171.9053 | 523.5242 | 216.1242 | 25732.0375 | 15485.9896 | 4348.4489 | 139.3663 | 86.1987 | 2.1792 | 23431.4288 | 13238.5486 | 2185.0274 | 2161.2424 | 0.011349 | 0.0062126 | 0.0001584 | 0.15741 | 0.089444 | 0.015741 | 0.0033984 | 5000000 | scaled
236-1567R | 5332003.6622 | 5229333.7728 | 98148.246 | 4521.6435 | 98.07% | 1.841% | 0.0848% | 2113263.3082 | 5250125.2123 | 145573.1779 | 39133.9205 | 1928556.2098 | 362409.1144 | 82426.0596 | 4805290.0383 | 236 |  | 449 | 236-1567R | 5332003.6622 | 3218740.3541 | 81878.4499 | 5229333.7728 | 3158727.3287 | 68206.4789 | 98148.246 | 55491.3819 | 9150.3275 | 4521.6435 | 367132.1489 | 221558.971 | 4723.0345 | 366978.4927 | 221470.6176 | 4705.624 | 150.2538 | 84.951 | 14.0081 | 3.4024 | 4870021.1574 | 2941464.9476 | 64731.1191 | 4860438.3774 | 2935868.4851 | 63465.2646 | 9172.0308 | 5185.7133 | 855.1053 | 410.7492 | 94850.3559 | 55716.4354 | 12424.2963 | 1916.9027 | 1388.226 | 35.5903 | 88825.9613 | 50220.7176 | 8281.2141 | 4107.4919 | 0.01797 | 0.010488 | 0.0002662 | 0.15699 | 0.089266 | 0.015699 | 0.0063284 | 5000000 | scaled
236-1569R | 21222913.1191 | 20875680.9896 | 336363.0898 | 10869.0397 | 98.36% | 1.585% | 0.05121% | 10999627.173 | 20882737.9892 | 610255.5253 | 134883.4681 | 10254488.1796 | 1157607.8987 | 280935.9462 | 19444194.1443 | 236 |  | 450 | 236-1569R | 21222913.1191 | 10223285.946 | 340175.1298 | 20875680.9896 | 10022221.6895 | 297959.9717 | 336363.0898 | 190195.2168 | 31346.1184 | 10869.0397 | 1174151.3358 | 563895.8105 | 16543.4371 | 1173671.6128 | 563620.999 | 16491.3147 | 471.5444 | 266.633 | 43.9438 | 8.1786 | 19729698.9435 | 9475210.7639 | 285504.7992 | 19695068.6666 | 9455200.1497 | 281382.2197 | 33642.9259 | 19023.2632 | 3135.2285 | 987.351 | 319062.8397 | 184179.3716 | 38126.8935 | 6940.7101 | 3400.5408 | 86.4373 | 302248.6195 | 170905.3207 | 28166.9461 | 9873.5101 | 0.043476 | 0.021057 | 0.0005344 | 0.1556 | 0.088493 | 0.01556 | 0.015264 | 5000000 | scaled
236-1573R | 6927855.8046 | 6778519.8437 | 144709.0316 | 4626.9292 | 97.84% | 2.089% | 0.06679% | 3099003.5228 | 6815680.8626 | 198036.214 | 57078.363 | 2843888.9459 | 434471.415 | 119079.0995 | 6262130.3481 | 236 |  | 451 | 236-1573R | 6927855.8046 | 3828852.2817 | 112174.9419 | 6778519.8437 | 3742429.8466 | 94054.4096 | 144709.0316 | 81795.5059 | 13493.6032 | 4626.9292 | 440611.9665 | 242575.7525 | 6140.5515 | 440396.0305 | 242452.1829 | 6117.2592 | 212.4544 | 120.088 | 19.8106 | 3.4816 | 6351813.7055 | 3507924.7596 | 89683.3574 | 6337010.3219 | 3499374.5424 | 87921.8738 | 14383.0702 | 8129.9038 | 1341.1702 | 420.3134 | 135430.1326 | 78351.7696 | 16351.0331 | 1113.4914 | 603.1213 | 15.2765 | 130113.507 | 73545.5142 | 12132.6224 | 4203.1342 | 0.021156 | 0.011302 | 0.0002868 | 0.1572 | 0.08936 | 0.01572 | 0.0065236 | 5000000 | scaled
237-1761R | 3634146.4134 | 3612196.0957 | 17960.9578 | 3989.3599 | 99.4% | 0.4942% | 0.1098% | 1508386.0896 | 3590887.4873 | 85770.3414 | 7026.0431 | 1415589.705 | 202595.6437 | 14683.7452 | 3373608.0983 | 237 |  | 452 | 237-1761R | 3634146.4134 | 2125760.3238 | 43258.9261 | 3612196.0957 | 2111654.1094 | 37630.956 | 17960.9578 | 10116.8545 | 1638.6102 | 3989.3599 | 204729.7367 | 118959.3953 | 2134.0929 | 204699.9429 | 118941.3023 | 2128.6468 | 26.7919 | 15.0911 | 2.4443 | 3.0019 | 3409661.3369 | 1994071.6319 | 36053.2386 | 3407177.4879 | 1992514.2866 | 35497.2985 | 2121.4528 | 1194.949 | 193.5439 | 362.3962 | 19755.3398 | 12729.2966 | 5071.5945 | 318.6649 | 198.5205 | 5.0107 | 15812.7131 | 8906.8143 | 1442.622 | 3623.9618 | 0.025622 | 0.016754 | 0.000426 | 0.1181 | 0.067028 | 0.011809 | 0.0056356 | 5000000 | scaled
237-1765R | 28249252.4704 | 28064039.1156 | 179613.607 | 5599.7477 | 99.34% | 0.6358% | 0.01982% | 9797552.4994 | 27804422.2971 | 746417.1697 | 71035.7828 | 8980099.5469 | 2124389.4767 | 148586.7537 | 25531446.0667 | 237 |  | 453 | 237-1765R | 28249252.4704 | 18451699.971 | 444830.1733 | 28064039.1156 | 18344459.6917 | 422189.6848 | 179613.607 | 101640.5316 | 17040.7408 | 5599.7477 | 2156873.9255 | 1410456.7557 | 32484.4487 | 2156568.1366 | 1410281.8854 | 32451.6233 | 301.5752 | 170.6567 | 28.6118 | 4.2136 | 25923282.1587 | 16943182.6118 | 391836.092 | 25905711.2334 | 16933018.6719 | 389708.6366 | 17062.2403 | 9655.255 | 1618.7705 | 508.6849 | 169096.3862 | 98060.6034 | 20509.6325 | 1759.7455 | 1159.1343 | 29.4248 | 162249.7915 | 91814.6199 | 15393.3585 | 5086.8492 | 0.02585 | 0.01706 | 0.000433 | 0.22538 | 0.1281 | 0.022538 | 0.0078522 | 5000000 | scaled
237-17R | 27080737.569 | 26780685.6631 | 290058.8995 | 9993.0064 | 98.89% | 1.071% | 0.0369% | 13329515.8212 | 26678700.2272 | 871216.2975 | 122772.4967 | 12335527.027 | 1747175.6309 | 264550.7685 | 24666973.8278 | 237 |  | 454 | 237-17R | 27080737.569 | 13751221.7477 | 402037.3418 | 26780685.6631 | 13577907.1291 | 365969.7649 | 290058.8995 | 163321.6122 | 26074.5705 | 9993.0064 | 1771336.8298 | 900120.5323 | 24161.1989 | 1770910.9425 | 899877.4452 | 24116.0707 | 418.3679 | 235.5677 | 37.6088 | 7.5194 | 25011549.6651 | 12676022.6381 | 344575.8374 | 24985718.1816 | 12661081.2312 | 341427.5723 | 24923.712 | 14033.6353 | 2240.4935 | 907.7715 | 297851.074 | 175078.5773 | 33300.3055 | 24056.5389 | 16948.4527 | 426.1218 | 264716.8196 | 149052.4091 | 23796.4682 | 9077.7155 | 0.034759 | 0.018136 | 0.0004588 | 0.1066 | 0.060536 | 0.01066 | 0.014037 | 5000000 | scaled
237-26F | 663215.1491 | 470121.1852 | 190447.5449 | 2646.419 | 70.89% | 28.72% | 0.399% | 242633.147 | 643135.3876 | 8813.184 | 74864.8018 | 158955.1613 | 25834.368 | 155734.0408 | 461566.9787 | 237 |  | 455 | 237-26F | 663215.1491 | 420582.002 | 20079.7614 | 470121.1852 | 310866.7317 | 316.2941 | 190447.5449 | 107068.8514 | 17117.0484 | 2646.419 | 25883.3028 | 17070.1188 | 48.9348 | 25654.0021 | 16940.3351 | 26.5133 | 227.3094 | 127.7924 | 20.4301 | 1.9913 | 463853.532 | 304898.3708 | 2286.5533 | 443975.9689 | 293618.0347 | 281.2017 | 19637.1607 | 11039.9335 | 1764.9491 | 240.4025 | 173478.3142 | 98613.5124 | 17744.2734 | 491.2142 | 308.3618 | 8.5791 | 170583.0749 | 95901.1255 | 15331.6692 | 2404.0251 | 0.0052096 | 0.0031682 | 8.02e-05 | 0.10004 | 0.056742 | 0.010004 | 0.0037196 | 5000000 | scaled
237-28F | 2530225.4549 | 2500529.9117 | 28244.7097 | 1450.8335 | 98.83% | 1.116% | 0.05734% | 969803.203 | 2502875.1934 | 49608.5384 | 11979.5769 | 908215.0877 | 129431.5137 | 26570.2515 | 2346873.4282 | 237 |  | 456 | 237-28F | 2530225.4549 | 1560422.2519 | 27350.2615 | 2500529.9117 | 1543085.6097 | 23357.3193 | 28244.7097 | 15885.8087 | 2542.1087 | 1450.8335 | 130695.9887 | 81087.4503 | 1264.475 | 130650.7634 | 81061.5363 | 1259.4111 | 44.1336 | 24.8223 | 3.9722 | 1.0917 | 2369357.0023 | 1461141.9147 | 22483.5741 | 2365470.6155 | 1458898.4066 | 22013.8548 | 3754.5921 | 2111.7134 | 337.9246 | 131.7947 | 30172.4638 | 18192.887 | 3602.2123 | 4408.5327 | 3125.6668 | 84.0533 | 24445.984 | 13749.2731 | 2200.212 | 1317.9471 | 0.0043736 | 0.0027798 | 7.04e-05 | 0.1016 | 0.057637 | 0.01016 | 0.002067 | 5000000 | scaled
237-2R | 30894123.4063 | 30619728.0088 | 262352.8253 | 12042.5722 | 99.11% | 0.8492% | 0.03898% | 10150729.4351 | 30328613.5015 | 918247.1082 | 105599.4856 | 9126882.8412 | 2753828.3894 | 224269.3006 | 27350515.8115 | 237 |  | 457 | 237-2R | 30894123.4063 | 20743393.9713 | 565509.9048 | 30619728.0088 | 20583633.9668 | 529535.9865 | 262352.8253 | 147717.4323 | 23931.3461 | 12042.5722 | 2801991.6942 | 1883744.586 | 48163.3048 | 2801583.4254 | 1883510.7512 | 48117.8282 | 399.2072 | 224.7731 | 36.415 | 9.0616 | 27835349.5347 | 18708466.6935 | 484833.7232 | 27806467.7874 | 18691726.8564 | 481205.016 | 27787.7918 | 15645.8817 | 2534.7517 | 1093.9555 | 256782.1774 | 151182.6918 | 32512.8768 | 11676.7961 | 8396.3592 | 213.1423 | 234165.8263 | 131846.7775 | 21360.1794 | 10939.5551 | 0.046938 | 0.031413 | 0.0007972 | 0.11764 | 0.066743 | 0.011764 | 0.01698 | 5000000 | scaled
237-30R | 65515491.9922 | 64815658.7441 | 680055.5135 | 19777.7346 | 98.93% | 1.038% | 0.03019% | 24710318.4296 | 64388339.0681 | 1399725.7024 | 265138.3404 | 23045454.3867 | 3671711.8478 | 556261.2397 | 60160365.9806 | 237 |  | 458 | 237-30R | 65515491.9922 | 40805173.5627 | 1127152.9242 | 64815658.7441 | 40400289.6882 | 1041618.8446 | 680055.5135 | 385106.1399 | 65756.3449 | 19777.7346 | 3732010.3451 | 2332284.6427 | 60298.4973 | 3730787.6198 | 2331585.7755 | 60166.8257 | 1207.8432 | 683.9851 | 116.7895 | 14.8821 | 61150542.8261 | 38105088.4394 | 990176.8456 | 61075246.6684 | 38061670.0348 | 981273.3605 | 73499.5348 | 41621.7817 | 7106.8621 | 1796.623 | 632938.821 | 367800.4806 | 76677.5813 | 9624.4559 | 7033.8779 | 178.6584 | 605348.1355 | 342800.3731 | 58532.6933 | 17966.2295 | 0.10832 | 0.069509 | 0.0017654 | 0.35613 | 0.2022 | 0.035613 | 0.028031 | 5000000 | scaled
239-2207R | 860323.3976 | 843815.2137 | 12865.5144 | 3642.6696 | 98.08% | 1.495% | 0.4234% | 524944.7613 | 843017.8031 | 36733.4963 | 4943.3171 | 483267.948 | 59633.4059 | 10276.5568 | 773107.8404 | 239 |  | 459 | 239-2207R | 860323.3976 | 335378.6363 | 17305.5946 | 843815.2137 | 324519.1425 | 12602.2881 | 12865.5144 | 7216.8242 | 1060.6369 | 3642.6696 | 60505.1654 | 23771.6691 | 871.7595 | 60484.0776 | 23758.6366 | 867.506 | 18.3468 | 10.2915 | 1.5125 | 2.741 | 785331.4488 | 302063.5009 | 12223.6084 | 783046.2761 | 300636.3635 | 11731.5952 | 1954.2702 | 1096.2348 | 161.1106 | 330.9026 | 14486.7834 | 9543.4664 | 4210.2266 | 284.86 | 124.1424 | 3.1868 | 10892.8974 | 6110.2979 | 898.0137 | 3309.026 | 0.019164 | 0.0085622 | 0.0002168 | 0.053893 | 0.030692 | 0.0053894 | 0.0051662 | 5000000 | scaled
239-2211R | 1585171.8415 | 1564094.2986 | 19341.6452 | 1735.8977 | 98.67% | 1.22% | 0.1095% | 676753.3957 | 1567013.2977 | 38632.7922 | 7412.6667 | 630707.9368 | 88239.2779 | 15405.2524 | 1463368.7673 | 239 |  | 460 | 239-2211R | 1585171.8415 | 908418.4457 | 18158.5438 | 1564094.2986 | 895792.3281 | 14682.3916 | 19341.6452 | 10890.2199 | 1740.2544 | 1735.8977 | 89116.2335 | 50483.4412 | 876.9555 | 89098.8673 | 50473.0926 | 874.2043 | 16.0599 | 9.0425 | 1.445 | 1.3062 | 1477567.4342 | 846859.4973 | 14198.6668 | 1474798.0576 | 845231.3098 | 13805.9916 | 2611.6864 | 1470.4974 | 234.9851 | 157.6901 | 18488.1738 | 11075.5072 | 3082.9214 | 197.3736 | 87.9258 | 2.1957 | 16713.8989 | 9410.68 | 1503.8243 | 1576.9014 | 0.008224 | 0.004183 | 0.0001058 | 0.10833 | 0.061511 | 0.010833 | 0.0024646 | 5000000 | scaled
239-2213R | 1116470.4872 | 1076921.0119 | 36064.4478 | 3485.0275 | 96.46% | 3.23% | 0.3121% | 620285.6177 | 1095362.4148 | 36124.646 | 18267.9417 | 565893.0299 | 64010.9405 | 36428.7143 | 994922.76 | 239 |  | 461 | 239-2213R | 1116470.4872 | 496184.8695 | 21108.0724 | 1076921.0119 | 472397.6219 | 14378.1525 | 36064.4478 | 20302.2202 | 3244.8924 | 3485.0275 | 64860.5019 | 28735.8559 | 849.5615 | 64808.028 | 28705.17 | 842.4537 | 49.8515 | 28.0635 | 4.4854 | 2.6224 | 1009100.485 | 443207.4551 | 14177.725 | 1004197.9864 | 440309.2644 | 13448.5257 | 4585.9163 | 2581.6084 | 412.617 | 316.5823 | 42509.5002 | 24241.5585 | 6080.7859 | 7914.9975 | 3383.1875 | 87.1732 | 31428.68 | 17692.5482 | 2827.79 | 3165.8228 | 0.016121 | 0.0075498 | 0.0001916 | 0.10835 | 0.061512 | 0.010835 | 0.0049334 | 5000000 | scaled
239-2215R | 6268656.9491 | 6158320.4267 | 102173.5112 | 8163.0111 | 98.24% | 1.63% | 0.1302% | 2999782.3709 | 6163868.6473 | 187457.3687 | 44657.57 | 2767667.4322 | 383930.2763 | 91537.9866 | 5688400.3845 | 239 |  | 462 | 239-2215R | 6268656.9491 | 3268874.5782 | 104788.3017 | 6158320.4267 | 3203195.1083 | 87438.0613 | 102173.5112 | 57516.4587 | 9187.2293 | 8163.0111 | 389438.0553 | 201980.6865 | 5507.7789 | 389286.5939 | 201892.7398 | 5488.5698 | 145.319 | 81.8043 | 13.0668 | 6.1424 | 5772032.5564 | 3004365.1242 | 83632.1719 | 5759638.1488 | 2997063.8469 | 81842.8362 | 11652.874 | 6559.7437 | 1047.8022 | 741.5335 | 107186.3375 | 62528.7674 | 15648.3509 | 9395.684 | 4238.5215 | 106.6553 | 90375.3182 | 50874.9107 | 8126.3604 | 7415.3352 | 0.035052 | 0.017824 | 0.0004516 | 0.10761 | 0.061091 | 0.010761 | 0.011414 | 5000000 | scaled
239-2217R | 1029567.3189 | 713201.354 | 313244.4026 | 3121.5623 | 69.27% | 30.42% | 0.3032% | 498158.8396 | 990374.2783 | 23478.9606 | 130575.334 | 344104.545 | 45690.3458 | 272426.3885 | 672257.544 | 239 |  | 463 | 239-2217R | 1029567.3189 | 531408.4792 | 39193.0406 | 713201.354 | 352603.2088 | 10273.0694 | 313244.4026 | 175683.7082 | 25798.4089 | 3121.5623 | 46362.8582 | 22883.8976 | 672.5125 | 45901.8871 | 22624.3296 | 632.3921 | 458.6223 | 257.2192 | 37.7715 | 2.3489 | 684306.9768 | 340202.4318 | 12049.4328 | 656513.808 | 324490.0542 | 9500.2121 | 27509.604 | 15428.8128 | 2265.6558 | 283.5649 | 298897.4838 | 168322.1498 | 26471.0954 | 10785.659 | 5488.825 | 140.4653 | 285276.1763 | 159997.6762 | 23494.9815 | 2835.6485 | 0.015505 | 0.0076296 | 0.0001938 | 0.053275 | 0.030339 | 0.0053274 | 0.0044262 | 5000000 | scaled
239-89R | 376425.1446 | 371745.0705 | 3157.5544 | 1522.5197 | 98.76% | 0.8388% | 0.4045% | 118410.416 | 371665.974 | 7518.1189 | 11113.53 | 99778.767 | 23371.4733 | 41778.6626 | 306515.8382 | 239 |  | 464 | 239-89R | 376425.1446 | 258014.7286 | 4759.1705 | 371745.0705 | 254721.3168 | 2976.3814 | 3157.5544 | 1770.8921 | 260.2695 | 1522.5197 | 23582.9657 | 16064.8468 | 211.4924 | 23572.7742 | 16058.6278 | 209.6011 | 9.0458 | 5.0733 | 0.74562 | 1.1456 | 308833.7551 | 209054.9881 | 2317.9169 | 308095.0444 | 208579.949 | 2130.1204 | 600.404 | 336.7323 | 49.4898 | 138.3067 | 44008.4238 | 32894.8938 | 2229.7612 | 40077.2519 | 30082.74 | 636.6599 | 2548.1046 | 1429.0865 | 210.034 | 1383.0673 | 0.0086026 | 0.0057328 | 0.0001458 | 0.054024 | 0.030765 | 0.0054024 | 0.0021588 | 5000000 | scaled
240-1028R | 1181536.0887 | 1162445.8063 | 15548.4516 | 3541.8308 | 98.38% | 1.316% | 0.2998% | 621917.7105 | 1158614.6569 | 46591.6257 | 7575.7302 | 567750.3546 | 86750.1076 | 15736.3673 | 1056128.1819 | 240 |  | 465 | 240-1028R | 1181536.0887 | 559618.3782 | 22921.4319 | 1162445.8063 | 547438.5239 | 18256.6181 | 15548.4516 | 8638.0236 | 1122.983 | 3541.8308 | 88095.3447 | 41503.719 | 1345.2371 | 88071.479 | 41489.2758 | 1341.0408 | 21.2006 | 11.7781 | 1.5312 | 2.6651 | 1073443.7346 | 505693.38 | 17315.5526 | 1071520.9658 | 504482.1791 | 16878.1766 | 1601.0264 | 889.4586 | 115.6337 | 321.7423 | 19997.0094 | 12421.2792 | 4260.6421 | 2853.3615 | 1467.069 | 37.4007 | 13926.2246 | 7736.7869 | 1005.818 | 3217.4233 | 0.015729 | 0.0073288 | 0.0001862 | 0.024472 | 0.013922 | 0.0024472 | 0.0049732 | 5000000 | scaled
240-1044 | 791335.5765 | 781085.1174 | 8797.135 | 1453.3241 | 98.7% | 1.112% | 0.1837% | 442443.8317 | 787300.9379 | 28952.0461 | 6250.3654 | 407241.4202 | 51436.9009 | 12033.8441 | 723830.1929 | 240 |  | 466 | 240-1044 | 791335.5765 | 348891.7449 | 4034.6387 | 781085.1174 | 342515.5209 | 1835.645 | 8797.135 | 4922.8999 | 745.6696 | 1453.3241 | 51586.7654 | 22634.7193 | 149.8646 | 51570.9477 | 22625.3861 | 147.5229 | 14.7241 | 8.2396 | 1.2481 | 1.0936 | 725674.6019 | 318433.1817 | 1844.409 | 724564.0347 | 317753.5637 | 1629.4437 | 978.5462 | 547.597 | 82.9443 | 132.021 | 14074.2093 | 7823.8439 | 2040.3651 | 4950.135 | 2136.5711 | 58.6783 | 7803.8647 | 4367.0632 | 661.4773 | 1320.2096 | 0.008136 | 0.0035638 | 9.04e-05 | 0.066178 | 0.037525 | 0.0066178 | 0.0019944 | 5000000 | scaled
240-1148 | 376720.0338 | 364956.6627 | 9504.4604 | 2258.9107 | 96.88% | 2.523% | 0.5996% | 183320.6106 | 369672.9536 | 11369.4698 | 3522.7224 | 168428.4185 | 22767.5965 | 7332.6186 | 339572.7385 | 240 |  | 467 | 240-1148 | 376720.0338 | 193399.4232 | 7047.0802 | 364956.6627 | 185867.3198 | 4102.5057 | 9504.4604 | 5273.1927 | 685.6638 | 2258.9107 | 23028.2951 | 11658.8253 | 260.6986 | 23010.7084 | 11648.3113 | 257.8528 | 15.887 | 8.8143 | 1.1461 | 1.6998 | 343748.666 | 175320.2475 | 4175.9274 | 341764.2393 | 174127.91 | 3842.3708 | 1779.2256 | 987.1365 | 128.3556 | 205.201 | 9943.0727 | 6420.3503 | 2610.4541 | 181.715 | 91.0985 | 2.2821 | 7709.3477 | 4277.2419 | 556.1621 | 2052.0099 | 0.0098646 | 0.0050836 | 0.0001286 | 0.024427 | 0.013879 | 0.0024426 | 0.0031906 | 5000000 | scaled
240-2004R | 4437658.7596 | 4344911.7762 | 78502.7252 | 14244.2583 | 97.91% | 1.769% | 0.321% | 2146821.2801 | 4367734.4008 | 160907.5632 | 32393.0654 | 1953520.6514 | 327317.21 | 69077.7467 | 3971339.4442 | 240 |  | 468 | 240-2004R | 4437658.7596 | 2290837.4795 | 69924.3588 | 4344911.7762 | 2233015.4242 | 50018.8754 | 78502.7252 | 43577.797 | 5661.2251 | 14244.2583 | 331234.6095 | 170327.0463 | 3917.3996 | 331065.9439 | 170228.6495 | 3895.2909 | 157.9473 | 87.6784 | 11.3904 | 10.7183 | 4019325.4733 | 2065804.8219 | 47986.0292 | 4008990.805 | 2059492.258 | 46040.1001 | 9040.7101 | 5018.6058 | 651.9709 | 1293.9582 | 87098.6767 | 54705.6113 | 18020.93 | 4855.0273 | 3294.5168 | 83.4845 | 69304.0677 | 38471.5128 | 4997.8638 | 12939.5817 | 0.051336 | 0.026755 | 0.0006796 | 0.024322 | 0.013823 | 0.0024322 | 0.020117 | 5000000 | scaled
240-2006R | 3742572.1436 | 3707607.3748 | 28285.6294 | 6679.1393 | 99.07% | 0.7558% | 0.1785% | 1494799.5279 | 3682771.0539 | 85038.0269 | 11933.9965 | 1397827.5044 | 210419.5399 | 24945.7698 | 3447405.7441 | 240 |  | 469 | 240-2006R | 3742572.1436 | 2247772.6157 | 59801.0898 | 3707607.3748 | 2225386.875 | 51082.5013 | 28285.6294 | 15706.6014 | 2039.4491 | 6679.1393 | 213386.2612 | 128348.2342 | 2966.7213 | 213320.2487 | 128309.3434 | 2957.2982 | 60.9866 | 33.865 | 4.3973 | 5.0258 | 3496346.8763 | 2098519.3719 | 48941.1322 | 3492495.5109 | 2096110.9393 | 48100.4506 | 3244.6278 | 1801.6949 | 233.944 | 606.7376 | 32839.0062 | 20905.0097 | 7893.2363 | 1791.6152 | 966.5922 | 24.7525 | 24980.015 | 13871.0415 | 1801.1079 | 6067.3759 | 0.036178 | 0.02233 | 0.0005662 | 0.024387 | 0.013866 | 0.0024386 | 0.009426 | 5000000 | scaled
240-2032R | 3665735.0887 | 3549053.9682 | 107379.2653 | 9301.8552 | 96.82% | 2.929% | 0.2538% | 1343462.7253 | 3602695.0634 | 80033.6542 | 42958.1506 | 1220470.9206 | 215717.1356 | 89967.4917 | 3297010.4361 | 240 |  | 470 | 240-2032R | 3665735.0887 | 2322272.3634 | 63040.0253 | 3549053.9682 | 2252878.5145 | 44642.2915 | 107379.2653 | 60091.9938 | 9095.8787 | 9301.8552 | 218502.3935 | 138468.7393 | 2785.2578 | 218362.0164 | 138387.0986 | 2766.9603 | 133.3778 | 74.6414 | 11.2982 | 6.9993 | 3340627.2812 | 2120156.3606 | 43616.8451 | 3328802.2129 | 2113166.6587 | 41841.7579 | 10980.0814 | 6144.715 | 930.1003 | 844.9869 | 106605.414 | 63647.2634 | 16637.9223 | 1889.7389 | 1324.7571 | 33.5732 | 96265.8061 | 53872.6374 | 8154.4802 | 8449.8689 | 0.043791 | 0.027734 | 0.0007042 | 0.065853 | 0.037342 | 0.0065854 | 0.013132 | 5000000 | scaled
241-570 | 1283068.1629 | 448908.1156 | 821364.1204 | 12795.9269 | 34.99% | 64.02% | 0.9973% | 608103.2415 | 1191538.9317 | 29348.7513 | 353282.138 | 225472.3521 | 52788.6608 | 726376.4745 | 412373.7963 | 241 |  | 471 | 241-570 | 1283068.1629 | 674964.9215 | 91529.2313 | 448908.1156 | 201346.4662 | 5518.5029 | 821364.1204 | 460822.5284 | 73214.8015 | 12795.9269 | 53552.1738 | 24203.4225 | 763.513 | 52281.4771 | 23486.2775 | 641.4753 | 1261.0682 | 707.5165 | 112.4092 | 9.6285 | 424054.2115 | 198581.8594 | 11680.4152 | 354282.7737 | 158926.6812 | 4402.3473 | 68609.047 | 38492.7875 | 6115.6771 | 1162.3908 | 805461.7776 | 452179.6396 | 79085.3031 | 42343.8648 | 18933.5075 | 474.6803 | 751494.0052 | 421622.2244 | 66986.7152 | 11623.9076 | 0.047012 | 0.020708 | 0.0005262 | 0.094459 | 0.053482 | 0.0094458 | 0.018043 | 5000000 | scaled
241-746 | 290982.4206 | 28895.3908 | 261875.266 | 211.7639 | 9.93% | 90% | 0.07278% | 130711.1517 | 267189.2894 | 1470.4199 | 106962.7383 | 22277.9935 | 2741.3491 | 220954.0922 | 43493.8482 | 241 |  | 472 | 241-746 | 290982.4206 | 160271.2689 | 23793.1312 | 28895.3908 | 13195.4858 | 199.3103 | 261875.266 | 146864.0192 | 23382.057 | 211.7639 | 2789.8601 | 1319.4403 | 48.5111 | 2436.5324 | 1121.2182 | 16.8184 | 353.1683 | 198.0627 | 31.5333 | 0.15935 | 45738.1975 | 23460.2039 | 2244.3493 | 22331.8395 | 10325.0793 | 136.9466 | 23387.1212 | 13115.8879 | 2088.1659 | 19.2368 | 242454.363 | 135491.6247 | 21500.2708 | 4127.0189 | 1749.1883 | 45.5453 | 238134.9764 | 133550.0687 | 21262.3577 | 192.3678 | 0.0014584 | 0.0006314 | 1.6e-05 | 0.096699 | 0.054728 | 0.0096698 | 0.0003004 | 5000000 | scaled
241-820AE | 286770.1837 | 42737.4073 | 242086.7983 | 1945.9781 | 14.9% | 84.42% | 0.6786% | 130477.0323 | 262704.9575 | 4373.072 | 100548.1446 | 25555.8157 | 7654.498 | 207734.4907 | 47315.9688 | 241 |  | 473 | 241-820AE | 286770.1837 | 156293.1515 | 24065.2262 | 42737.4073 | 18481.1231 | 508.1557 | 242086.7983 | 135866.0502 | 21611.0924 | 1945.9781 | 7769.9646 | 3396.8926 | 115.4666 | 7453.8891 | 3218.8595 | 85.917 | 314.6112 | 176.5688 | 28.0853 | 1.4643 | 49656.6217 | 24100.806 | 2340.6529 | 29113.6263 | 12493.9248 | 345.786 | 20366.2214 | 11430.1072 | 1818.0929 | 176.774 | 229343.5974 | 128795.4529 | 21609.1067 | 6169.8919 | 2768.3388 | 76.4528 | 221405.9657 | 124259.3742 | 19764.9141 | 1767.7399 | 0.0070306 | 0.0031178 | 7.82e-05 | 0.096465 | 0.054635 | 0.0096464 | 0.0027474 | 5000000 | scaled
242-1411F | 861030.8326 | 2838.9304 | 857977.6012 | 214.301 | 0.3297% | 99.65% | 0.02489% | 377577.6503 | 784447.9597 | 600.9415 | 343316.2798 | 33660.4289 | 1232.9805 | 713336.7627 | 69878.2164 | 242 |  | 474 | 242-1411F | 861030.8326 | 483453.1823 | 76582.8729 | 2838.9304 | 1423.8881 | 1.5943 | 857977.6012 | 481814.9932 | 76366.9777 | 214.301 | 1330.4184 | 729.4768 | 97.4378 | 238.7122 | 116.336 | 0.12021 | 1091.545 | 612.9796 | 97.1564 | 0.16125 | 76484.8256 | 42824.3967 | 6606.6092 | 2466.1503 | 1249.15 | 0.61122 | 73999.2081 | 41555.7794 | 6586.5308 | 19.4672 | 783215.5886 | 439899.3087 | 69878.8258 | 134.0679 | 58.4021 | 0.86283 | 782886.8481 | 439646.2342 | 69683.2905 | 194.6725 | 0.0005318 | 0.0002304 | 5.8e-06 | 0.092884 | 0.052655 | 0.0092884 | 0.000304 | 5000000 | scaled
242-1413F | 367353.6892 | 30385.1486 | 335623.6304 | 1344.9102 | 8.271% | 91.36% | 0.3661% | 165206.7921 | 335880.0212 | 1688.5999 | 130836.1154 | 32682.0768 | 2909.7566 | 271811.2499 | 61159.0148 | 242 |  | 475 | 242-1413F | 367353.6892 | 202146.8971 | 31473.668 | 30385.1486 | 12298.6837 | 195.6419 | 335623.6304 | 188503.3031 | 29933.1158 | 1344.9102 | 2970.4653 | 1281.8655 | 60.7088 | 2494.1712 | 1013.9109 | 17.308 | 475.2821 | 266.9426 | 42.3888 | 1.012 | 64756.2897 | 32074.2129 | 3597.275 | 27636.9713 | 11172.5613 | 175.4544 | 36997.1458 | 20779.4791 | 3299.648 | 122.1726 | 299626.9341 | 168790.8187 | 27815.6842 | 254.006 | 112.2116 | 2.8796 | 298151.2024 | 167456.8815 | 26591.079 | 1221.7257 | 0.0034676 | 0.0015744 | 4.02e-05 | 0.095204 | 0.053967 | 0.0095204 | 0.0018928 | 5000000 | scaled
242-1420F | 89560.1408 | 11211.9262 | 77463.2659 | 884.9488 | 12.52% | 86.49% | 0.9881% | 41149.0626 | 81726.2699 | 418.973 | 31893.2667 | 8836.8229 | 655.6413 | 64419.3379 | 16651.2907 | 242 |  | 476 | 242-1420F | 89560.1408 | 48411.0783 | 7833.8709 | 11211.9262 | 4010.6797 | 32.5578 | 77463.2659 | 43515.4498 | 6916.3643 | 884.9488 | 665.12 | 246.1469 | 9.4786 | 573.1036 | 194.1643 | 0.65645 | 91.3505 | 51.3167 | 8.1563 | 0.6659 | 17970.7556 | 9133.9327 | 1319.4649 | 4050.304 | 1278.8062 | 3.3555 | 13840.0623 | 7774.7372 | 1235.7201 | 80.3894 | 70924.2653 | 39030.9986 | 6504.9273 | 6588.5187 | 2537.7092 | 28.5459 | 63531.853 | 35689.3959 | 5672.4879 | 803.8935 | 0.0023538 | 0.0010194 | 2.66e-05 | 0.096372 | 0.054639 | 0.0096372 | 0.0012786 | 5000000 | scaled
242-1426F | 960344.5769 | 633435.469 | 324677.7231 | 2231.3848 | 65.96% | 33.81% | 0.2324% | 451193.758 | 919866.2195 | 28770.303 | 131583.8747 | 290839.5803 | 58254.5787 | 274186.5734 | 587425.0673 | 242 |  | 477 | 242-1426F | 960344.5769 | 509150.819 | 40478.3575 | 633435.469 | 324442.5361 | 9287.582 | 324677.7231 | 182476.8981 | 28959.3906 | 2231.3848 | 59137.8749 | 30367.5719 | 883.2961 | 58732.1489 | 30138.8085 | 845.5784 | 404.0469 | 227.0843 | 36.0387 | 1.679 | 598478.0478 | 307638.4674 | 11052.9805 | 570576.8276 | 291868.5149 | 8379.7309 | 27698.5196 | 15567.252 | 2470.5491 | 202.7005 | 302728.6543 | 171144.7796 | 28542.0808 | 4126.4925 | 2435.2127 | 62.2727 | 296575.1566 | 166682.5617 | 26452.8029 | 2027.0052 | 0.0089968 | 0.0045172 | 0.0001148 | 0.095082 | 0.053938 | 0.0095082 | 0.0031654 | 5000000 | scaled
242-1427F | 24990.9617 | 17761.5887 | 7161.6867 | 67.6863 | 71.07% | 28.66% | 0.2708% | 10535.0137 | 24283.8092 | 487.9284 | 2629.5321 | 7417.5532 | 1136.4397 | 5467.1424 | 17680.2271 | 242 |  | 478 | 242-1427F | 24990.9617 | 14455.948 | 707.1525 | 17761.5887 | 10363.3815 | 0.016287 | 7161.6867 | 4024.8802 | 639.4499 | 67.6863 | 1137.7778 | 649.8494 | 1.3381 | 1123.311 | 641.6968 | 0 | 14.4159 | 8.1017 | 1.2872 | 0.050932 | 17788.7097 | 10371.1564 | 108.4826 | 16636.4457 | 9720.889 | 0 | 1146.1153 | 644.1188 | 102.3339 | 6.1487 | 6064.4742 | 3434.9421 | 597.3318 | 1.832 | 0.79572 | 0.016287 | 6001.1555 | 3372.6597 | 535.8289 | 61.4867 | 0.0003116 | 0.000135 | 3.6e-06 | 0.096499 | 0.054736 | 0.00965 | 9.68e-05 | 5000000 | scaled
242-776F | 89086.8198 | 10165.8129 | 78504.4383 | 416.5686 | 11.41% | 88.12% | 0.4676% | 40121.6302 | 81629.7072 | 236.2522 | 35384.2691 | 4501.109 | 444.5252 | 72124.3541 | 9060.8279 | 242 |  | 479 | 242-776F | 89086.8198 | 48965.1896 | 7457.1126 | 10165.8129 | 4464.7216 | 33.0701 | 78504.4383 | 44083.8995 | 7007.4738 | 416.5686 | 452.2171 | 215.9649 | 7.6918 | 369.2439 | 169.2342 | 0 | 82.6597 | 46.4173 | 7.3784 | 0.31345 | 9751.5394 | 5250.4305 | 690.7115 | 2399.6208 | 1105.394 | 0 | 7314.0772 | 4107.1951 | 652.8702 | 37.8414 | 78883.0633 | 43498.7943 | 6758.7092 | 7396.9482 | 3190.0934 | 33.0701 | 71107.7014 | 39930.2871 | 6347.2253 | 378.4138 | 0.0012746 | 0.0005516 | 1.4e-05 | 0.096061 | 0.054444 | 0.009606 | 0.000598 | 5000000 | scaled
243-14R | 404258.8944 | 119250.4179 | 276467.9023 | 8540.5741 | 29.5% | 68.39% | 2.113% | 189515.5909 | 374662.9843 | 5980.3632 | 119828.9203 | 63706.3074 | 10594.0021 | 249136.9411 | 114932.0411 | 243 |  | 480 | 243-14R | 404258.8944 | 214743.3035 | 29595.9101 | 119250.4179 | 52886.9769 | 1140.5914 | 276467.9023 | 153315.7525 | 19914.7445 | 8540.5741 | 10734.5174 | 4754.1542 | 140.5153 | 10283.5778 | 4501.2222 | 102.0693 | 444.5131 | 246.5055 | 32.0195 | 6.4265 | 118250.2118 | 54543.9044 | 3318.1707 | 94125.5449 | 40819.9359 | 860.4582 | 23348.8353 | 12948.1369 | 1681.8809 | 775.8316 | 275274.1652 | 155445.2449 | 26137.2241 | 14841.2953 | 7565.8188 | 178.064 | 252674.5539 | 140121.11 | 18200.8441 | 7758.316 | 0.030372 | 0.013333 | 0.0003404 | 0.024004 | 0.013631 | 0.0024004 | 0.012069 | 5000000 | scaled
243-20R | 388803.9632 | 281395.0371 | 101973.0237 | 5435.9023 | 72.37% | 26.23% | 1.398% | 150443.4418 | 372375.7004 | 13837.7552 | 50049.1667 | 86556.5198 | 36051.2197 | 109213.2017 | 227111.279 | 243 |  | 481 | 243-20R | 388803.9632 | 238360.5214 | 16428.2628 | 281395.0371 | 176319.0569 | 3643.5915 | 101973.0237 | 56605.5621 | 7348.7689 | 5435.9023 | 36528.9066 | 22691.1513 | 477.6869 | 36365.8725 | 22598.8308 | 462.1421 | 158.9437 | 88.2302 | 11.4544 | 4.0903 | 231008.1503 | 144451.6305 | 3896.8713 | 222023.3112 | 139244.4262 | 2791.1566 | 8491.0379 | 4713.4032 | 611.9136 | 493.8011 | 121266.9063 | 71217.7396 | 12053.7046 | 23005.8533 | 14475.8 | 390.2928 | 93323.0421 | 51803.9287 | 6725.4009 | 4938.0109 | 0.026267 | 0.013664 | 0.0003484 | 0.024263 | 0.013791 | 0.0024262 | 0.0076318 | 5000000 | scaled
244-29 | 494907.6296 | 187283.9913 | 295272.8804 | 12350.7579 | 37.84% | 59.66% | 2.496% | 233350.9842 | 458299.2873 | 16918.8421 | 134178.8026 | 82253.3395 | 30604.7764 | 275482.4514 | 152212.0595 | 244 |  | 482 | 244-29 | 494907.6296 | 261556.6454 | 36608.3424 | 187283.9913 | 85195.6915 | 3006.8881 | 295272.8804 | 164010.196 | 21250.6964 | 12350.7579 | 31138.2669 | 14219.4248 | 533.4905 | 30707.3848 | 13975.9586 | 493.8553 | 421.5886 | 234.1726 | 30.3416 | 9.2935 | 157406.9596 | 75153.62 | 5194.9001 | 130543.9346 | 59733.7131 | 2220.3718 | 25741.0736 | 14297.9556 | 1852.577 | 1121.9513 | 306362.4032 | 172183.6006 | 30879.9518 | 26032.6719 | 11486.0198 | 292.6609 | 269110.2182 | 149478.0678 | 19367.7778 | 11219.5131 | 0.040788 | 0.017968 | 0.000458 | 0.024 | 0.013651 | 0.0024 | 0.017483 | 5000000 | scaled
244-32F | 51190.9972 | 4231.4069 | 46386.0009 | 573.5893 | 8.266% | 90.61% | 1.12% | 23245.7546 | 47232.9749 | 45.0585 | 20753.3939 | 2447.3022 | 76.3312 | 42139.5605 | 5017.0833 | 244 |  | 483 | 244-32F | 51190.9972 | 27945.2426 | 3958.0222 | 4231.4069 | 1607.6382 | 43.8709 | 46386.0009 | 25764.0151 | 3340.5621 | 573.5893 | 81.4097 | 36.3512 | 5.0785 | 26.053 | 5.4127 | 0.69137 | 54.9251 | 30.5068 | 3.9555 | 0.43161 | 5451.9957 | 3004.6935 | 434.9124 | 134.2999 | 27.9396 | 3.5972 | 5265.5906 | 2924.6487 | 379.2099 | 52.1052 | 45657.5918 | 24904.1979 | 3518.0313 | 4071.0541 | 1574.2859 | 39.5823 | 41065.4853 | 22808.8596 | 2957.3966 | 521.0524 | 0.0013794 | 0.000597 | 1.52e-05 | 0.024429 | 0.0139 | 0.0024428 | 0.0008006 | 5000000 | scaled
244-33F | 53966.9639 | 85.6875 | 53733.9257 | 147.3506 | 0.1588% | 99.57% | 0.273% | 23976.1406 | 49951.8492 | 40.3344 | 21230.1134 | 2705.6928 | 78.8297 | 44262.9853 | 5610.0343 | 244 |  | 484 | 244-33F | 53966.9639 | 29990.8232 | 4015.1146 | 85.6875 | 26.4295 | 0.062186 | 53733.9257 | 29817.0431 | 3867.7018 | 147.3506 | 84.1104 | 43.7759 | 5.2807 | 12.1759 | 3.81 | 0 | 71.8236 | 39.855 | 5.1698 | 0.11088 | 6053.3223 | 3347.6295 | 443.288 | 67.3068 | 20.0219 | 0 | 5972.63 | 3314.2221 | 429.9025 | 13.3854 | 47829.5312 | 26599.4178 | 3566.546 | 6.2048 | 2.5976 | 0.062186 | 47689.4721 | 26462.9659 | 3432.6295 | 133.8543 | 0.0003972 | 0.000172 | 4.2e-06 | 0.024429 | 0.013885 | 0.0024428 | 0.000198 | 5000000 | scaled
245-486 | 294230.8654 | 105012.0964 | 186512.7276 | 2706.0414 | 35.69% | 63.39% | 0.9197% | 143614.2493 | 277356.5265 | 6655.3487 | 76119.0014 | 60839.8993 | 11554.5785 | 158589.2359 | 107212.7122 | 245 |  | 485 | 245-486 | 294230.8654 | 150616.616 | 16874.3388 | 105012.0964 | 44461.2864 | 752.958 | 186512.7276 | 103449.2883 | 13415.3395 | 2706.0414 | 11663.2275 | 5007.8788 | 108.649 | 11392.3822 | 4856.7476 | 87.2781 | 268.8091 | 149.095 | 19.3347 | 2.0362 | 109241.6579 | 48401.7586 | 2028.9457 | 93431.753 | 39523.3192 | 663.6458 | 15564.0863 | 8632.6208 | 1119.4812 | 245.8186 | 173325.98 | 97206.9786 | 14736.7441 | 187.9612 | 81.2196 | 2.0341 | 170679.8322 | 94667.5725 | 12276.5235 | 2458.1865 | 0.01145 | 0.0049584 | 0.0001254 | 0.024236 | 0.013773 | 0.0024236 | 0.0037972 | 5000000 | scaled
246-34R | 3387005.7991 | 3202236.9481 | 176039.3904 | 8729.4605 | 94.54% | 5.197% | 0.2577% | 1646636.976 | 3315922.2972 | 120564.728 | 75298.1502 | 1450774.0978 | 241910.2558 | 159938.0392 | 2914074.0021 | 246 |  | 486 | 246-34R | 3387005.7991 | 1740368.8231 | 71083.5019 | 3202236.9481 | 1633951.15 | 49694.3827 | 176039.3904 | 97688.2125 | 12659.6587 | 8729.4605 | 245629.7038 | 125064.9758 | 3719.448 | 245361.3131 | 124913.1162 | 3694.0508 | 261.8221 | 145.291 | 18.8286 | 6.5686 | 2961954.5518 | 1511180.454 | 47880.5497 | 2942955.6899 | 1500284.6166 | 45778.3064 | 18205.8718 | 10102.8472 | 1309.2531 | 792.9902 | 179421.5434 | 104123.3933 | 19483.5042 | 13919.9452 | 8753.4172 | 222.0255 | 157571.6965 | 87440.0743 | 11331.5769 | 7929.9017 | 0.033834 | 0.016941 | 0.00043 | 0.02429 | 0.01381 | 0.002429 | 0.012364 | 5000000 | scaled
247-46 | 1360332.8405 | 1258488.2986 | 97751.2623 | 4093.2796 | 92.51% | 7.186% | 0.3009% | 710780.6878 | 1338371.4233 | 41544.8044 | 40516.4399 | 628719.4435 | 77605.8173 | 84404.9621 | 1176360.6438 | 247 |  | 487 | 247-46 | 1360332.8405 | 649552.1527 | 21961.4172 | 1258488.2986 | 591244.8023 | 10837.5069 | 97751.2623 | 54214.0707 | 7030.6307 | 4093.2796 | 78364.9865 | 36820.1821 | 759.1692 | 78204.1301 | 36729.5973 | 744.7413 | 157.7763 | 87.5047 | 11.3479 | 3.0801 | 1187424.2996 | 558704.8561 | 11063.6558 | 1178384.2457 | 553525.5181 | 10068.3694 | 8668.2176 | 4807.5017 | 623.4501 | 371.8363 | 94543.5543 | 54027.1144 | 10138.5922 | 1899.9228 | 989.6869 | 24.3962 | 88925.2683 | 49319.0643 | 6395.8327 | 3718.3632 | 0.015102 | 0.0070748 | 0.0001794 | 0.024399 | 0.013864 | 0.00244 | 0.0057268 | 5000000 | scaled
247-48 | 105202.5635 | 103290.899 | 1611.3945 | 300.27 | 98.18% | 1.532% | 0.2854% | 43999.3544 | 102461.714 | 2823.8209 | 595.3701 | 40580.1633 | 6471.9668 | 1240.0963 | 94749.6509 | 247 |  | 488 | 247-48 | 105202.5635 | 61203.2091 | 2740.8495 | 103290.899 | 60009.4541 | 2324.7055 | 1611.3945 | 893.485 | 115.874 | 300.27 | 6624.3278 | 3800.5069 | 152.361 | 6620.0177 | 3798.0164 | 151.8414 | 4.0841 | 2.2646 | 0.29369 | 0.22594 | 96969.8086 | 56389.6453 | 2220.1577 | 96662.6724 | 56207.1922 | 2172.7565 | 279.8595 | 155.1763 | 20.1245 | 27.2767 | 1608.4271 | 1013.057 | 368.3308 | 8.209 | 4.2455 | 0.10762 | 1327.4508 | 736.0441 | 95.4559 | 272.7673 | 0.0012446 | 0.0006818 | 1.74e-05 | 0.024558 | 0.013949 | 0.0024558 | 0.000413 | 5000000 | scaled
248-30AE | 242.2985 | 0 | 242.2985 | 0 | 0% | 100% | 0% | 32.7382 | 68.1522 | 0.42472 | 25.6368 | 6.6766 | 0.88415 | 53.3691 | 13.899 | 248 |  | 489 | 248-30AE | 242.2985 | 209.5603 | 174.1462 | 0 | 0 | 0 | 242.2985 | 209.5603 | 174.1462 | 0 | 3.1434 | 2.7187 | 2.2592 | 0 | 0 | 0 | 3.1434 | 2.7187 | 2.2592 | 0 | 49.4143 | 42.7377 | 35.5154 | 0 | 0 | 0 | 49.4143 | 42.7377 | 35.5154 | 0 | 189.7408 | 164.1039 | 136.3717 | 0 | 0 | 0 | 189.7408 | 164.1039 | 136.3717 | 0 | 0 | 0 | 0 | 0.024556 | 0.024556 | 0.024556 | 0 | 5000000 | scaled
249-11 | 1141.509 | 0 | 1141.509 | 0 | 0% | 100% | 0% | 108.6263 | 225.903 | 1.0604 | 85.3406 | 22.2253 | 2.2052 | 177.4773 | 46.2205 | 249 |  | 490 | 249-11 | 1141.509 | 1032.8827 | 915.606 | 0 | 0 | 0 | 1141.509 | 1032.8827 | 915.606 | 0 | 11.1429 | 10.0826 | 8.9378 | 0 | 0 | 0 | 11.1429 | 10.0826 | 8.9378 | 0 | 233.5566 | 211.3313 | 187.3361 | 0 | 0 | 0 | 233.5566 | 211.3313 | 187.3361 | 0 | 896.8094 | 811.4688 | 719.3321 | 0 | 0 | 0 | 896.8094 | 811.4688 | 719.3321 | 0 | 0 | 0 | 0 | 0.043158 | 0.043158 | 0.043158 | 0 | 5000000 | scaled
249-12 | 759.5793 | 0 | 759.5793 | 0 | 0% | 100% | 0% | 72.2773 | 150.4259 | 0.49533 | 56.9504 | 14.8316 | 1.0309 | 118.527 | 30.8681 | 249 |  | 491 | 249-12 | 759.5793 | 687.302 | 609.1534 | 0 | 0 | 0 | 759.5793 | 687.302 | 609.1534 | 0 | 5.2055 | 4.7102 | 4.1746 | 0 | 0 | 0 | 5.2055 | 4.7102 | 4.1746 | 0 | 155.869 | 141.0373 | 125.0009 | 0 | 0 | 0 | 155.869 | 141.0373 | 125.0009 | 0 | 598.5048 | 541.5544 | 479.9778 | 0 | 0 | 0 | 598.5048 | 541.5544 | 479.9778 | 0 | 0 | 0 | 0 | 0.043197 | 0.043197 | 0.043197 | 0 | 5000000 | scaled
249-13 | 760.5912 | 0 | 760.5912 | 0 | 0% | 100% | 0% | 72.4422 | 150.6754 | 0.49646 | 57.0803 | 14.8655 | 1.0326 | 118.7235 | 30.9192 | 249 |  | 492 | 249-13 | 760.5912 | 688.149 | 609.9158 | 0 | 0 | 0 | 760.5912 | 688.149 | 609.9158 | 0 | 5.2125 | 4.716 | 4.1799 | 0 | 0 | 0 | 5.2125 | 4.716 | 4.1799 | 0 | 156.0766 | 141.2112 | 125.1574 | 0 | 0 | 0 | 156.0766 | 141.2112 | 125.1574 | 0 | 599.3021 | 542.2218 | 480.5786 | 0 | 0 | 0 | 599.3021 | 542.2218 | 480.5786 | 0 | 0 | 0 | 0 | 0.04325 | 0.04325 | 0.04325 | 0 | 5000000 | scaled
249-24R | 3753230.0343 | 3597511.4758 | 145470.9455 | 10247.613 | 95.85% | 3.876% | 0.273% | 1860775.8286 | 3676797.2247 | 138492.439 | 59993.3597 | 1662290.0299 | 273017.7201 | 124192.0696 | 3279587.4349 | 249 |  | 493 | 249-24R | 3753230.0343 | 1892454.2057 | 76432.8096 | 3597511.4758 | 1801108.6888 | 54529.9347 | 145470.9455 | 81097.9039 | 11655.2619 | 10247.613 | 277202.2159 | 138709.7769 | 4184.4958 | 276852.2252 | 138511.25 | 4149.361 | 342.2797 | 190.8159 | 27.4238 | 7.711 | 3332009.3141 | 1669719.2842 | 52421.8792 | 3316626.386 | 1660731.5919 | 50333.0696 | 14452.0279 | 8056.7921 | 1157.9094 | 930.9002 | 144018.5043 | 84025.1446 | 19826.4346 | 4032.8646 | 1865.8469 | 47.504 | 130676.6379 | 72850.2959 | 10469.9288 | 9309.0018 | 0.043458 | 0.021394 | 0.0005426 | 0.043014 | 0.024401 | 0.0043014 | 0.014465 | 5000000 | scaled
250-288F | 221.9396 | 110.7355 | 0 | 111.2042 | 49.89% | 0% | 50.11% | 11.5783 | 100.3937 | 1.6659 | 0.23105 | 9.6814 | 11.1705 | 0.40587 | 88.8173 | 250 |  | 494 | 250-288F | 221.9396 | 210.3613 | 121.5459 | 110.7355 | 99.1571 | 10.3418 | 0 | 0 | 0 | 111.2042 | 12.5798 | 10.914 | 1.4093 | 12.4962 | 10.8303 | 1.3256 | 0 | 0 | 0 | 0.083678 | 107.9316 | 98.2503 | 19.1144 | 97.8298 | 88.1484 | 9.0125 | 0 | 0 | 0 | 10.1019 | 101.4281 | 101.1971 | 101.0223 | 0.40951 | 0.17846 | 0.0036381 | 0 | 0 | 0 | 101.0186 | 0.0001062 | 4.6e-05 | 1e-06 | 0 | 0 | 0 | 0.000151 | 5000000 | scaled
250-47 | 266.0817 | 196.3835 | 0 | 69.6982 | 73.81% | 0% | 26.19% | 67.499 | 196.382 | 6.9482 | 0.085671 | 60.4651 | 19.6912 | 0.14965 | 176.5412 | 250 |  | 495 | 250-47 | 266.0817 | 198.5827 | 69.6997 | 196.3835 | 128.8845 | 0.0014806 | 0 | 0 | 0 | 69.6982 | 19.7436 | 12.7954 | 0.052446 | 19.6912 | 12.743 | 0 | 0 | 0 | 0 | 0.052446 | 182.8726 | 122.4075 | 6.3314 | 176.5412 | 116.076 | 0 | 0 | 0 | 0 | 6.3314 | 63.4655 | 63.3798 | 63.3158 | 0.15113 | 0.065454 | 0.0014806 | 0 | 0 | 0 | 63.3144 | 0.0001784 | 7.72e-05 | 2e-06 | 0 | 0 | 0 | 0.0001034 | 5000000 | scaled
252-129 | 49485.3293 | 42886.1174 | 3320.5216 | 3278.6903 | 86.66% | 6.71% | 6.626% | 29731.2401 | 45904.2792 | 2433.6274 | 1388.7402 | 25908.8726 | 3742.4673 | 2836.0222 | 39325.7897 | 252 |  | 496 | 252-129 | 49485.3293 | 19754.0891 | 3581.0501 | 42886.1174 | 14636.5734 | 80.448 | 3320.5216 | 1838.8255 | 221.9118 | 3278.6903 | 3754.9726 | 1321.3452 | 12.5053 | 3739.2595 | 1311.5428 | 9.153 | 13.246 | 7.3353 | 0.88524 | 2.4671 | 39736.8184 | 13827.9458 | 411.0287 | 38755.6295 | 13151.6842 | 67.5216 | 683.3504 | 378.4231 | 45.6686 | 297.8385 | 5993.5383 | 4604.7981 | 3157.5161 | 391.2284 | 173.3463 | 3.7735 | 2623.9251 | 1453.067 | 175.358 | 2978.3847 | 0.013344 | 0.0059062 | 0.0001496 | 0.0059444 | 0.0033858 | 0.0005944 | 0.0046216 | 5000000 | scaled
252-132 | 5974.5438 | 0 | 5974.5438 | 0 | 0% | 100% | 0% | 947.6112 | 1981.2408 | 0.86972 | 752.2048 | 194.5367 | 1.8184 | 1572.6901 | 406.7323 | 252 |  | 497 | 252-132 | 5974.5438 | 5026.9326 | 3993.303 | 0 | 0 | 0 | 5974.5438 | 5026.9326 | 3993.303 | 0 | 5.4834 | 4.6137 | 3.665 | 0 | 0 | 0 | 5.4834 | 4.6137 | 3.665 | 0 | 1226.5244 | 1031.9876 | 819.7921 | 0 | 0 | 0 | 1226.5244 | 1031.9876 | 819.7921 | 0 | 4742.536 | 3990.3312 | 3169.8459 | 0 | 0 | 0 | 4742.536 | 3990.3312 | 3169.8459 | 0 | 0 | 0 | 0 | 0.0059316 | 0.0059316 | 0.0059316 | 0 | 5000000 | scaled
252-277F | 3351.0827 | 2176.4848 | 0 | 1174.5979 | 64.95% | 0% | 35.05% | 1020.3362 | 2150.1879 | 100.2536 | 372.5832 | 547.4994 | 218.7886 | 721.3513 | 1210.048 | 252 |  | 498 | 252-277F | 3351.0827 | 2330.7465 | 1200.8948 | 2176.4848 | 1156.1486 | 26.2969 | 0 | 0 | 0 | 1174.5979 | 222.7334 | 122.4797 | 3.9448 | 221.8495 | 121.5959 | 3.0609 | 0 | 0 | 0 | 0.88385 | 1332.4371 | 784.9377 | 122.3891 | 1225.7358 | 678.2364 | 15.6878 | 0 | 0 | 0 | 106.7013 | 1795.9122 | 1423.329 | 1074.5609 | 728.8995 | 356.3163 | 7.5481 | 0 | 0 | 0 | 1067.0127 | 0.0020612 | 0.000992 | 2.5e-05 | 0 | 0 | 0 | 0.0016396 | 5000000 | scaled
255-1080R | 2174.484 | 644.7495 | 0 | 1529.7344 | 29.65% | 0% | 70.35% | 365.5404 | 637.7073 | 0 | 365.5404 | 0 | 0 | 637.7073 | 0 | 255 |  | 499 | 255-1080R | 2174.484 | 1808.9436 | 1536.7766 | 644.7495 | 279.2092 | 7.0422 | 0 | 0 | 0 | 1529.7344 | 1.1511 | 1.1511 | 1.1511 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1511 | 138.9621 | 138.9621 | 138.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 138.9621 | 2034.3708 | 1668.8304 | 1396.6634 | 644.7495 | 279.2092 | 7.0422 | 0 | 0 | 0 | 1389.6212 | 0.0045112 | 0.001954 | 4.96e-05 | 0 | 0 | 0 | 0.0021458 | 5000000 | scaled
255-43AE | 53099.8638 | 41288.7217 | 0 | 11811.1421 | 77.76% | 0% | 22.24% | 23904.1472 | 40738.6813 | 2330.9072 | 12874.2865 | 8698.9536 | 3810.3794 | 22816.3134 | 14111.9885 | 255 |  | 500 | 255-43AE | 53099.8638 | 29195.7166 | 12361.1825 | 41288.7217 | 17384.5745 | 550.0404 | 0 | 0 | 0 | 11811.1421 | 3862.0823 | 1531.1751 | 51.7029 | 3853.1948 | 1522.2876 | 42.8154 | 0 | 0 | 0 | 8.8875 | 15353.4341 | 6654.4805 | 1241.4456 | 14280.5018 | 5581.5483 | 168.5133 | 0 | 0 | 0 | 1072.9322 | 33884.3475 | 21010.061 | 11068.0341 | 23155.0251 | 10280.7386 | 338.7117 | 0 | 0 | 0 | 10729.3224 | 0.031775 | 0.014015 | 0.0003568 | 0 | 0 | 0 | 0.016666 | 5000000 | scaled
256-39AE | 1060.8544 | 203.2472 | 0 | 857.6072 | 19.16% | 0% | 80.84% | 115.2022 | 200.9941 | 0 | 115.2022 | 0 | 0 | 200.9941 | 0 | 256 |  | 501 | 256-39AE | 1060.8544 | 945.6522 | 859.8603 | 203.2472 | 88.045 | 2.2531 | 0 | 0 | 0 | 857.6072 | 0.64532 | 0.64532 | 0.64532 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64532 | 77.9056 | 77.9056 | 77.9056 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9056 | 982.3034 | 867.1012 | 781.3094 | 203.2472 | 88.045 | 2.2531 | 0 | 0 | 0 | 779.0562 | 0.0022404 | 0.0009702 | 2.48e-05 | 0 | 0 | 0 | 0.0011924 | 5000000 | scaled
256-46AE | 5468.3511 | 1614.1227 | 0 | 3854.2284 | 29.52% | 0% | 70.48% | 914.8929 | 1595.9351 | 0 | 914.8929 | 0 | 0 | 1595.9351 | 0 | 256 |  | 502 | 256-46AE | 5468.3511 | 4553.4582 | 3872.416 | 1614.1227 | 699.2299 | 18.1876 | 0 | 0 | 0 | 3854.2284 | 2.9002 | 2.9002 | 2.9002 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9002 | 350.1207 | 350.1207 | 350.1207 | 0 | 0 | 0 | 0 | 0 | 0 | 350.1207 | 5115.3302 | 4200.4373 | 3519.3951 | 1614.1227 | 699.2299 | 18.1876 | 0 | 0 | 0 | 3501.2074 | 0.008937 | 0.0039708 | 0.000102 | 0 | 0 | 0 | 0.005383 | 5000000 | scaled
256-539R | 14306.9467 | 9099.1124 | 0 | 5207.8343 | 63.6% | 0% | 36.4% | 4851.8941 | 8991.289 | 2.12 | 4838.0539 | 11.7202 | 4.6113 | 8960.2111 | 26.4666 | 256 |  | 503 | 256-539R | 14306.9467 | 9455.0526 | 5315.6577 | 9099.1124 | 4247.2182 | 107.8234 | 0 | 0 | 0 | 5207.8343 | 8.5667 | 6.4467 | 3.9554 | 4.648 | 2.5279 | 0.036654 | 0 | 0 | 0 | 3.9187 | 499.7877 | 488.0675 | 473.3211 | 26.7045 | 14.9843 | 0.23789 | 0 | 0 | 0 | 473.0832 | 13798.5923 | 8960.5384 | 4838.3812 | 9067.76 | 4229.706 | 107.5489 | 0 | 0 | 0 | 4730.8323 | 0.012576 | 0.0055826 | 0.0001426 | 0 | 0 | 0 | 0.0072962 | 5000000 | scaled
257-29AE | 2298.3224 | 454.2227 | 0 | 1844.0997 | 19.76% | 0% | 80.24% | 257.5288 | 449.3804 | 0 | 257.5288 | 0 | 0 | 449.3804 | 0 | 257 |  | 504 | 257-29AE | 2298.3224 | 2040.7937 | 1848.9421 | 454.2227 | 196.694 | 4.8424 | 0 | 0 | 0 | 1844.0997 | 1.3876 | 1.3876 | 1.3876 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3876 | 167.5193 | 167.5193 | 167.5193 | 0 | 0 | 0 | 0 | 0 | 0 | 167.5193 | 2129.4155 | 1871.8868 | 1680.0352 | 454.2227 | 196.694 | 4.8424 | 0 | 0 | 0 | 1675.1928 | 0.0043622 | 0.001889 | 4.68e-05 | 0 | 0 | 0 | 0.0026268 | 5000000 | scaled
257-31AE | 5771.887 | 2256.1361 | 0 | 3515.7509 | 39.09% | 0% | 60.91% | 1279.6722 | 2231.6003 | 0 | 1279.6722 | 0 | 0 | 2231.6003 | 0 | 257 |  | 505 | 257-31AE | 5771.887 | 4492.2148 | 3540.2867 | 2256.1361 | 976.4639 | 24.5358 | 0 | 0 | 0 | 3515.7509 | 2.6455 | 2.6455 | 2.6455 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6455 | 319.3732 | 319.3732 | 319.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 319.3732 | 5449.8683 | 4170.1961 | 3218.268 | 2256.1361 | 976.4639 | 24.5358 | 0 | 0 | 0 | 3193.7322 | 0.007657 | 0.0033144 | 8.44e-05 | 0 | 0 | 0 | 0.004964 | 5000000 | scaled
266-485F | 3902.5439 | 3798.96 | 0 | 103.5839 | 97.35% | 0% | 2.654% | 1924.6208 | 3595.2561 | 173.0216 | 1.9059 | 1749.6934 | 326.8139 | 3.3227 | 3265.1195 | 266 |  | 506 | 266-485F | 3902.5439 | 1977.923 | 307.2878 | 3798.96 | 1874.3391 | 203.7039 | 0 | 0 | 0 | 103.5839 | 342.892 | 169.8703 | 16.0781 | 342.814 | 169.7924 | 16.0001 | 0 | 0 | 0 | 0.077944 | 3462.1953 | 1712.5019 | 197.0758 | 3452.7857 | 1703.0923 | 187.6662 | 0 | 0 | 0 | 9.4096 | 97.4566 | 95.5507 | 94.1339 | 3.3603 | 1.4544 | 0.037596 | 0 | 0 | 0 | 94.0963 | 0.0004956 | 0.0002148 | 5.4e-06 | 0 | 0 | 0 | 0.0001504 | 5000000 | scaled
270-177 | 44748.6442 | 0 | 44748.6442 | 0 | 0% | 100% | 0% | 7007.3834 | 14713.6196 | 9.7044 | 6342.6735 | 655.0055 | 20.3766 | 13317.9077 | 1375.3353 | 270 |  | 507 | 270-177 | 44748.6442 | 37741.2608 | 30035.0246 | 0 | 0 | 0 | 44748.6442 | 37741.2608 | 30035.0246 | 0 | 61.9717 | 52.2672 | 41.595 | 0 | 0 | 0 | 61.9717 | 52.2672 | 41.595 | 0 | 4182.8179 | 3527.8124 | 2807.4826 | 0 | 0 | 0 | 4182.8179 | 3527.8124 | 2807.4826 | 0 | 40503.8547 | 34161.1812 | 27185.947 | 0 | 0 | 0 | 40503.8547 | 34161.1812 | 27185.947 | 0 | 0 | 0 | 0 | 0.0074362 | 0.0074362 | 0.0074362 | 0 | 5000000 | scaled
274-23R | 237928.3924 | 11198.6712 | 217061.7274 | 9667.9938 | 4.707% | 91.23% | 4.063% | 103194.8222 | 213674.6657 | 205.4449 | 94724.4949 | 8264.8824 | 402.564 | 196069.8941 | 17202.2076 | 274 |  | 508 | 274-23R | 237928.3924 | 134733.5701 | 24253.7266 | 11198.6712 | 4838.2132 | 105.6096 | 217061.7274 | 120227.3632 | 14480.1232 | 9667.9938 | 428.8795 | 223.4346 | 26.3155 | 136.1798 | 58.0671 | 0 | 285.4249 | 158.0927 | 19.0406 | 7.2749 | 19278.5584 | 11013.676 | 2076.3509 | 440.3497 | 187.6649 | 0 | 17959.9616 | 9947.7639 | 1198.1037 | 878.2472 | 218220.9544 | 123496.4595 | 22151.0603 | 10622.1417 | 4592.4812 | 105.6096 | 198816.3409 | 110121.5065 | 13262.9789 | 8782.4718 | 0.028711 | 0.012431 | 0.0003152 | 0.014252 | 0.0081206 | 0.0014252 | 0.013607 | 5000000 | scaled
274-38AE | 25862.5762 | 0 | 25862.5762 | 0 | 0% | 100% | 0% | 4117.7556 | 8615.1446 | 5.8544 | 3264.9443 | 846.9569 | 12.2485 | 6830.8977 | 1771.9984 | 274 |  | 509 | 274-38AE | 25862.5762 | 21744.8207 | 17247.4316 | 0 | 0 | 0 | 25862.5762 | 21744.8207 | 17247.4316 | 0 | 36.77 | 30.9156 | 24.5214 | 0 | 0 | 0 | 36.77 | 30.9156 | 24.5214 | 0 | 5319.5211 | 4472.5642 | 3547.5227 | 0 | 0 | 0 | 5319.5211 | 4472.5642 | 3547.5227 | 0 | 20506.2852 | 17241.3409 | 13675.3875 | 0 | 0 | 0 | 20506.2852 | 17241.3409 | 13675.3875 | 0 | 0 | 0 | 0 | 0.014483 | 0.014483 | 0.014483 | 0 | 5000000 | scaled
274-40 | 130226.1581 | 3449.5552 | 120853.7695 | 5922.8334 | 2.649% | 92.8% | 4.548% | 55673.455 | 116206.6624 | 90.5317 | 50766.2672 | 4816.6561 | 189.5271 | 105908.7718 | 10108.3635 | 274 |  | 510 | 274-40 | 130226.1581 | 74552.7031 | 14019.4956 | 3449.5552 | 1509.6455 | 36.6024 | 120853.7695 | 67120.2242 | 8060.0599 | 5922.8334 | 205.4887 | 114.9571 | 15.9617 | 32.5141 | 16.9082 | 0.26604 | 168.5179 | 93.5921 | 11.2389 | 4.4567 | 11358.2305 | 6541.5744 | 1249.867 | 167.6803 | 87.3055 | 1.3881 | 10652.516 | 5916.2347 | 710.4447 | 538.0342 | 118662.4388 | 67896.1716 | 12753.667 | 3249.3607 | 1405.4318 | 34.9483 | 110032.7357 | 61110.3974 | 7338.3763 | 5380.3424 | 0.014408 | 0.0062924 | 0.000158 | 0.01436 | 0.0082034 | 0.001436 | 0.0084272 | 5000000 | scaled
275-45 | 157580.9542 | 671.5644 | 156050.3867 | 859.0031 | 0.4262% | 99.03% | 0.5451% | 69854.5626 | 146309.2996 | 85.2488 | 64082.873 | 5686.4408 | 217.6204 | 134043.7363 | 12047.943 | 275 |  | 511 | 275-45 | 157580.9542 | 87726.3917 | 11271.6546 | 671.5644 | 482.4181 | 3.6131 | 156050.3867 | 86384.9705 | 10409.0384 | 859.0031 | 231.8311 | 146.5823 | 14.2107 | 27.8311 | 33.3653 | 0 | 203.3536 | 112.5706 | 13.5643 | 0.64637 | 12980.4187 | 7293.9779 | 932.4758 | 92.7292 | 124.8906 | 0 | 12809.6571 | 7091.0548 | 854.4433 | 78.0324 | 144368.7044 | 80285.8314 | 10324.9681 | 551.0041 | 324.1621 | 3.6131 | 143037.376 | 79181.345 | 9541.0307 | 780.3243 | 0.0029192 | 0.0012638 | 3.2e-05 | 0.014288 | 0.008137 | 0.0014288 | 0.0012134 | 5000000 | scaled
275-48F | 122148.3024 | 7054.1771 | 113387.9953 | 1706.13 | 5.775% | 92.83% | 1.397% | 54171.5044 | 112804.5696 | 370.6681 | 48370.6374 | 5430.1988 | 749.5746 | 100698.0821 | 11356.9128 | 275 |  | 512 | 275-48F | 122148.3024 | 67976.798 | 9343.7328 | 7054.1771 | 3496.022 | 75.5507 | 113387.9953 | 62774.6461 | 7562.0521 | 1706.13 | 767.582 | 396.9138 | 18.0073 | 625.8106 | 317.8523 | 7.3542 | 140.4875 | 77.7777 | 9.3694 | 1.2838 | 12157.5395 | 6727.3407 | 800.6267 | 2804.4583 | 1480.0416 | 32.203 | 9198.0952 | 5092.3131 | 613.4377 | 154.986 | 109223.1809 | 60852.5435 | 8525.0988 | 3623.9082 | 1698.128 | 35.9936 | 104049.4126 | 57604.5553 | 6939.245 | 1549.8601 | 0.0077536 | 0.0033572 | 8.56e-05 | 0.014311 | 0.0081506 | 0.001431 | 0.002401 | 5000000 | scaled
275-680F | 32517.9038 | 0 | 32517.9038 | 0 | 0% | 100% | 0% | 5168.1663 | 10831.1377 | 6.1634 | 4631.4225 | 530.5804 | 12.9168 | 9706.2618 | 1111.9591 | 275 |  | 513 | 275-680F | 32517.9038 | 27349.7376 | 21686.7662 | 0 | 0 | 0 | 32517.9038 | 27349.7376 | 21686.7662 | 0 | 38.7797 | 32.6163 | 25.8629 | 0 | 0 | 0 | 38.7797 | 32.6163 | 25.8629 | 0 | 3338.3915 | 2807.8111 | 2226.4324 | 0 | 0 | 0 | 3338.3915 | 2807.8111 | 2226.4324 | 0 | 29140.7327 | 24509.3102 | 19434.4709 | 0 | 0 | 0 | 29140.7327 | 24509.3102 | 19434.4709 | 0 | 0 | 0 | 0 | 0.01434 | 0.01434 | 0.01434 | 0 | 5000000 | scaled
275-681F | 22678.5482 | 0 | 22678.5482 | 0 | 0% | 100% | 0% | 3603.5272 | 7554.1358 | 3.849 | 3300.0306 | 299.6476 | 8.0686 | 6917.9107 | 628.1565 | 275 |  | 514 | 275-681F | 22678.5482 | 19075.0209 | 15124.4124 | 0 | 0 | 0 | 22678.5482 | 19075.0209 | 15124.4124 | 0 | 24.2231 | 20.3742 | 16.1545 | 0 | 0 | 0 | 24.2231 | 20.3742 | 16.1545 | 0 | 1885.8116 | 1586.164 | 1257.6551 | 0 | 0 | 0 | 1885.8116 | 1586.164 | 1257.6551 | 0 | 20768.5135 | 17468.4828 | 13850.6028 | 0 | 0 | 0 | 20768.5135 | 17468.4828 | 13850.6028 | 0 | 0 | 0 | 0 | 0.014331 | 0.014331 | 0.014331 | 0 | 5000000 | scaled
276-158R | 188059.4775 | 8834.2035 | 167614.4884 | 11610.7856 | 4.698% | 89.13% | 6.174% | 79528.3934 | 165194.6274 | 219.1518 | 72874.9904 | 6434.2512 | 429.591 | 151353.3452 | 13411.6912 | 276 |  | 515 | 276-158R | 188059.4775 | 108531.0841 | 22864.8501 | 8834.2035 | 3933.0575 | 70.742 | 167614.4884 | 92987.241 | 11183.3225 | 11610.7856 | 452.3899 | 233.2381 | 22.7989 | 232.8907 | 107.577 | 0 | 210.7624 | 116.9244 | 14.0622 | 8.7367 | 15382.3918 | 8948.1406 | 1970.7007 | 599.2118 | 277.298 | 0 | 13728.4484 | 7616.1109 | 915.9689 | 1054.7317 | 172224.6958 | 99349.7054 | 20871.3506 | 8002.101 | 3548.1825 | 70.742 | 153675.2777 | 85254.2057 | 10253.2914 | 10547.3171 | 0.029868 | 0.012933 | 0.0003276 | 0.014118 | 0.008056 | 0.0014118 | 0.016323 | 5000000 | scaled
276-228 | 290991.4091 | 33914.6868 | 244428.7908 | 12647.9314 | 11.65% | 84% | 4.346% | 127092.9972 | 262060.3602 | 907.5109 | 113229.8442 | 12955.6422 | 1649.5846 | 234287.0832 | 26123.6924 | 276 |  | 516 | 276-228 | 290991.4091 | 163898.4119 | 28931.0489 | 33914.6868 | 15860.3031 | 415.2864 | 244428.7908 | 135390.1773 | 15867.8311 | 12647.9314 | 1697.8475 | 790.3366 | 48.2628 | 1361.8782 | 599.7628 | 17.0663 | 326.4521 | 181.0566 | 21.6793 | 9.5172 | 28815.3501 | 15859.7079 | 2691.6577 | 5396.7648 | 2361.3888 | 67.5575 | 22269.6385 | 12349.3724 | 1475.1534 | 1148.9468 | 260478.2116 | 147248.3674 | 26191.1284 | 27156.0438 | 12899.1516 | 330.6625 | 221832.7003 | 122859.7483 | 14370.9983 | 11489.4675 | 0.033692 | 0.014877 | 0.0003792 | 0.014047 | 0.0080158 | 0.0014046 | 0.017895 | 5000000 | scaled
277-456F | 118446.9891 | 0 | 118446.9891 | 0 | 0% | 100% | 0% | 18845.396 | 39453.371 | 22.3184 | 17154.4745 | 1668.603 | 46.7242 | 35913.379 | 3493.2678 | 277 |  | 517 | 277-456F | 118446.9891 | 99601.5931 | 78993.618 | 0 | 0 | 0 | 118446.9891 | 99601.5931 | 78993.618 | 0 | 140.2756 | 117.9572 | 93.5513 | 0 | 0 | 0 | 140.2756 | 117.9572 | 93.5513 | 0 | 10487.4954 | 8818.8924 | 6994.2277 | 0 | 0 | 0 | 10487.4954 | 8818.8924 | 6994.2277 | 0 | 107819.2181 | 90664.7435 | 71905.839 | 0 | 0 | 0 | 107819.2181 | 90664.7435 | 71905.839 | 0 | 0 | 0 | 0 | 0.014179 | 0.014179 | 0.014179 | 0 | 5000000 | scaled
277-458F | 2237.5813 | 0 | 2237.5813 | 0 | 0% | 100% | 0% | 355.822 | 745.3496 | 0.83195 | 284.2522 | 70.7378 | 1.7427 | 595.4305 | 148.1764 | 277 |  | 518 | 277-458F | 2237.5813 | 1881.7593 | 1492.2317 | 0 | 0 | 0 | 2237.5813 | 1881.7593 | 1492.2317 | 0 | 5.2317 | 4.3997 | 3.489 | 0 | 0 | 0 | 5.2317 | 4.3997 | 3.489 | 0 | 444.8338 | 374.096 | 296.6575 | 0 | 0 | 0 | 444.8338 | 374.096 | 296.6575 | 0 | 1787.5158 | 1503.2636 | 1192.0853 | 0 | 0 | 0 | 1787.5158 | 1503.2636 | 1192.0853 | 0 | 0 | 0 | 0 | 0.014308 | 0.014308 | 0.014308 | 0 | 5000000 | scaled
277-459F | 196344.7376 | 15553.8641 | 174091.2914 | 6699.5821 | 7.922% | 88.67% | 3.412% | 86634.4202 | 177903.4987 | 284.7304 | 79036.5796 | 7313.1102 | 511.8495 | 162526.6757 | 14864.9735 | 277 |  | 519 | 277-459F | 196344.7376 | 109710.3174 | 18441.2389 | 15553.8641 | 6497.3125 | 128.1788 | 174091.2914 | 96513.4227 | 11613.478 | 6699.5821 | 532.8758 | 248.1453 | 21.0263 | 312.7776 | 123.88 | 1.6388 | 215.0569 | 119.2241 | 14.3463 | 5.0412 | 16427.3116 | 9114.2014 | 1562.3381 | 1648.136 | 649.6637 | 8.4364 | 14170.5809 | 7855.943 | 945.3071 | 608.5946 | 179384.5502 | 100347.9706 | 16857.8745 | 13592.9505 | 5723.7688 | 118.1036 | 159705.6535 | 88538.2556 | 10653.8246 | 6085.9462 | 0.019412 | 0.008406 | 0.0002142 | 0.014131 | 0.0080586 | 0.001413 | 0.0093166 | 5000000 | scaled
277-48 | 230021.8708 | 13476.6107 | 209832.6151 | 6712.645 | 5.859% | 91.22% | 2.918% | 100917.4889 | 209265.8525 | 630.755 | 90362.8335 | 9923.9004 | 1215.0264 | 187657.7691 | 20393.0571 | 277 |  | 520 | 277-48 | 230021.8708 | 129104.3819 | 20756.0183 | 13476.6107 | 6010.9181 | 45.3865 | 209832.6151 | 116380.8188 | 13997.9868 | 6712.645 | 1238.1106 | 607.3556 | 23.0842 | 965.0248 | 453.6427 | 0.1525 | 268.0348 | 148.6619 | 17.8807 | 5.051 | 22184.9719 | 12261.0715 | 1791.9148 | 3862.4109 | 1827.1367 | 0.50952 | 17712.7797 | 9824.1535 | 1181.624 | 609.7813 | 206598.7883 | 116235.9548 | 18941.0192 | 8649.1751 | 3730.1387 | 44.7245 | 191851.8006 | 106408.0035 | 12798.4821 | 6097.8127 | 0.020132 | 0.0087178 | 0.0002216 | 0.014072 | 0.008028 | 0.0014072 | 0.0095078 | 5000000 | scaled
278-22R | 285166.5473 | 15713.5191 | 259256.7122 | 10196.3159 | 5.51% | 90.91% | 3.576% | 124568.2405 | 258270.1388 | 397.643 | 113748.6588 | 10421.9387 | 734.3297 | 235986.3212 | 21549.4879 | 278 |  | 521 | 278-22R | 285166.5473 | 160598.3068 | 26896.4085 | 15713.5191 | 6751.5958 | 185.3492 | 259256.7122 | 143650.3951 | 16514.7433 | 10196.3159 | 770.3464 | 372.7034 | 36.0167 | 440.5563 | 186.158 | 7.0082 | 322.1177 | 178.873 | 21.3361 | 7.6724 | 23920.0604 | 13498.1217 | 2370.5725 | 1458.346 | 615.9036 | 23.6006 | 21535.4742 | 11955.9778 | 1420.7316 | 926.2403 | 260476.1404 | 146727.4816 | 24489.8192 | 13814.6168 | 5949.5341 | 154.7404 | 237399.1204 | 131515.5443 | 15072.6756 | 9262.4032 | 0.030153 | 0.013057 | 0.0003314 | 0.014037 | 0.0080206 | 0.0014036 | 0.014344 | 5000000 | scaled
278-630 | 273714.2345 | 15641.7794 | 251466.9765 | 6605.4786 | 5.715% | 91.87% | 2.413% | 120838.4224 | 250771.791 | 259.4469 | 111325.2419 | 9253.7336 | 527.9291 | 230872.7813 | 19371.0806 | 278 |  | 522 | 278-630 | 273714.2345 | 152875.812 | 22942.4435 | 15641.7794 | 6914.6233 | 164.3878 | 251466.9765 | 139355.7102 | 16172.5772 | 6605.4786 | 554.9938 | 295.5469 | 27.0647 | 246.8512 | 122.2713 | 1.9788 | 303.1722 | 168.3052 | 20.1155 | 4.9704 | 21295.9539 | 12042.2203 | 1924.8734 | 760.3297 | 376.8925 | 6.0644 | 19935.5781 | 11065.2816 | 1318.7628 | 600.0462 | 251863.2868 | 140538.0449 | 20990.5054 | 14634.5986 | 6415.4595 | 156.3445 | 231228.2262 | 128122.1234 | 14833.6989 | 6000.462 | 0.021421 | 0.0092764 | 0.0002356 | 0.014034 | 0.008016 | 0.0014034 | 0.0093144 | 5000000 | scaled
279-10AE | 166571.4259 | 9846.5178 | 146782.4285 | 9942.4795 | 5.911% | 88.12% | 5.969% | 70434.3776 | 146725.0995 | 286.9255 | 63995.1445 | 6152.3076 | 551.6503 | 133481.4901 | 12691.959 | 279 |  | 523 | 279-10AE | 166571.4259 | 96137.0482 | 19846.3264 | 9846.5178 | 4803.9511 | 115.9998 | 146782.4285 | 81390.6176 | 9787.8471 | 9942.4795 | 574.0173 | 287.0917 | 22.3669 | 388.6204 | 180.9565 | 3.0216 | 177.9155 | 98.6539 | 11.8639 | 7.4814 | 14402.5934 | 8250.2858 | 1710.6344 | 1563.3453 | 728.5747 | 11.5237 | 11936.0664 | 6618.5294 | 795.929 | 903.1816 | 151594.8152 | 87599.6707 | 18113.325 | 7894.5521 | 3894.4199 | 101.4544 | 134668.4466 | 74673.4344 | 8980.0542 | 9031.8165 | 0.026271 | 0.011845 | 0.0003262 | 0.014147 | 0.0080692 | 0.0014146 | 0.013996 | 5000000 | scaled
279-11AE | 201506.0077 | 6211.1266 | 185605.543 | 9689.3381 | 3.082% | 92.11% | 4.808% | 85870.056 | 179367.6331 | 110.1453 | 78533.6811 | 7226.2296 | 243.2496 | 163928.0121 | 15196.3713 | 279 |  | 524 | 279-11AE | 201506.0077 | 115635.9517 | 22138.3746 | 6211.1266 | 3067.5912 | 69.3667 | 185605.543 | 102879.0224 | 12379.6698 | 9689.3381 | 266.2337 | 156.0884 | 22.984 | 26.3422 | 19.8696 | 0.17893 | 232.6005 | 128.9278 | 15.5142 | 7.2909 | 17153.9191 | 9927.6895 | 1957.5478 | 134.7827 | 101.8685 | 0.91284 | 16138.9503 | 8945.6349 | 1076.4489 | 880.1861 | 184085.8549 | 105552.1738 | 20157.8428 | 6050.0017 | 2945.853 | 68.2749 | 169233.9921 | 93804.4597 | 11287.7068 | 8801.8611 | 0.027589 | 0.012047 | 0.000307 | 0.014101 | 0.0080404 | 0.0014102 | 0.013533 | 5000000 | scaled
280-23AE | 38657.0939 | 0 | 38657.0939 | 0 | 0% | 100% | 0% | 4576.3407 | 9505.7121 | 5.4586 | 4155.0431 | 415.839 | 11.3383 | 8630.6169 | 863.7569 | 280 |  | 525 | 280-23AE | 38657.0939 | 34080.7532 | 29151.3818 | 0 | 0 | 0 | 38657.0939 | 34080.7532 | 29151.3818 | 0 | 46.1098 | 40.6512 | 34.7715 | 0 | 0 | 0 | 46.1098 | 40.6512 | 34.7715 | 0 | 3512.6595 | 3096.8205 | 2648.9027 | 0 | 0 | 0 | 3512.6595 | 3096.8205 | 2648.9027 | 0 | 35098.3245 | 30943.2814 | 26467.7076 | 0 | 0 | 0 | 35098.3245 | 30943.2814 | 26467.7076 | 0 | 0 | 0 | 0 | 0.030355 | 0.030355 | 0.030355 | 0 | 5000000 | scaled
280-24AE | 365788.5423 | 11503.142 | 352682.9576 | 1602.4428 | 3.145% | 96.42% | 0.4381% | 161739.8718 | 337527.904 | 458.9045 | 147032.8374 | 14248.1299 | 1094.3845 | 305648.5104 | 30785.0091 | 280 |  | 526 | 280-24AE | 365788.5423 | 204048.6705 | 28260.6383 | 11503.142 | 6573.9933 | 114.7577 | 352682.9576 | 195872.2344 | 26543.4378 | 1602.4428 | 1138.0161 | 679.1116 | 43.6316 | 679.8814 | 424.1377 | 8.0367 | 456.9289 | 253.7681 | 34.3891 | 1.2058 | 33183.3848 | 18935.2549 | 2398.3757 | 3636.9287 | 2461.0911 | 40.0546 | 29400.8891 | 16328.5969 | 2212.7541 | 145.567 | 331467.1414 | 184434.304 | 25818.631 | 7186.3318 | 3688.7646 | 66.6665 | 322825.1396 | 179289.8694 | 24296.2945 | 1455.67 | 0.0050284 | 0.0021772 | 5.52e-05 | 0.029833 | 0.016933 | 0.0029834 | 0.0022314 | 5000000 | scaled
280-382AE | 117950.1754 | 11405.7555 | 103537.7125 | 3006.7075 | 9.67% | 87.78% | 2.549% | 54089.199 | 107084.3434 | 761.9792 | 43449.3412 | 9877.8786 | 1111.605 | 89599.1476 | 16373.5907 | 280 |  | 527 | 280-382AE | 117950.1754 | 63860.9764 | 10865.8321 | 11405.7555 | 3373.7891 | 61.1195 | 103537.7125 | 57480.4798 | 7798.0052 | 3006.7075 | 1130.4724 | 368.4932 | 18.8674 | 974.4204 | 280.8522 | 5.0222 | 153.7896 | 85.3785 | 11.5828 | 2.2625 | 17397.1145 | 7519.2359 | 1023.5237 | 7578.0793 | 1946.556 | 31.4369 | 9545.9038 | 5299.5485 | 718.9555 | 273.1314 | 99422.5886 | 55973.2473 | 9823.441 | 2853.2557 | 1146.3809 | 24.6604 | 93838.0192 | 52095.5528 | 7067.4669 | 2731.3137 | 0.0095686 | 0.0041866 | 0.000107 | 0.030367 | 0.017231 | 0.0030368 | 0.0042386 | 5000000 | scaled
282-563F | 27943.6221 | 6353.0054 | 21389.7462 | 200.8706 | 22.74% | 76.55% | 0.7188% | 12134.154 | 26076.1276 | 258.1086 | 7599.976 | 4276.0694 | 619.489 | 15838.5884 | 9618.0502 | 282 |  | 528 | 282-563F | 27943.6221 | 15809.4681 | 1867.4945 | 6353.0054 | 3729.2792 | 58.9383 | 21389.7462 | 11879.3183 | 1607.6857 | 200.8706 | 627.6045 | 369.4959 | 8.1155 | 609.8964 | 359.5941 | 6.6447 | 17.5569 | 9.7506 | 1.3196 | 0.15115 | 10018.1471 | 5742.0777 | 400.0969 | 5583.9709 | 3271.3364 | 49.9418 | 4415.929 | 2452.4941 | 331.9079 | 18.2472 | 17297.8705 | 9697.8945 | 1459.2821 | 159.138 | 98.3487 | 2.3518 | 16956.2603 | 9417.0736 | 1274.4582 | 182.4722 | 0.0010466 | 0.0006128 | 1.58e-05 | 0.030192 | 0.017139 | 0.0030192 | 0.0002934 | 5000000 | scaled
282-565F | 89977.8 | 373.7239 | 88914.7259 | 689.3502 | 0.4154% | 98.82% | 0.7661% | 39622.0534 | 82610.239 | 69.5625 | 32333.6583 | 7218.8326 | 159.0785 | 67296.0086 | 15155.1519 | 282 |  | 529 | 282-565F | 89977.8 | 50355.7466 | 7367.561 | 373.7239 | 261.5842 | 0.20618 | 88914.7259 | 49404.8123 | 6678.0047 | 689.3502 | 168.7993 | 99.2368 | 9.7208 | 45.7585 | 30.6396 | 0 | 122.5221 | 68.0785 | 9.2021 | 0.51871 | 16423.6164 | 9204.7838 | 1268.4644 | 305.7152 | 221.1646 | 0 | 16055.2801 | 8920.9981 | 1205.8434 | 62.621 | 73385.3844 | 41051.726 | 6089.3758 | 22.2502 | 9.7799 | 0.20618 | 72736.9237 | 40415.7357 | 5462.9592 | 626.2104 | 0.0017488 | 0.000757 | 1.92e-05 | 0.029982 | 0.017025 | 0.0029982 | 0.0009526 | 5000000 | scaled
283-1357AE | 1309.6636 | 0 | 1309.6636 | 0 | 0% | 100% | 0% | 39.1868 | 81.6898 | 0.50838 | 30.6867 | 7.9918 | 1.0598 | 63.9702 | 16.6598 | 283 |  | 530 | 283-1357AE | 1309.6636 | 1270.4768 | 1227.9738 | 0 | 0 | 0 | 1309.6636 | 1270.4768 | 1227.9738 | 0 | 16.9905 | 16.4822 | 15.9308 | 0 | 0 | 0 | 16.9905 | 16.4822 | 15.9308 | 0 | 267.0925 | 259.1008 | 250.4327 | 0 | 0 | 0 | 267.0925 | 259.1008 | 250.4327 | 0 | 1025.5805 | 994.8938 | 961.6103 | 0 | 0 | 0 | 1025.5805 | 994.8938 | 961.6103 | 0 | 0 | 0 | 0 | 0.17318 | 0.17318 | 0.17318 | 0 | 5000000 | scaled
283-1358AE | 1307.7045 | 0 | 1307.7045 | 0 | 0% | 100% | 0% | 39.2102 | 81.8245 | 0.50868 | 30.705 | 7.9965 | 1.0615 | 64.0757 | 16.6873 | 283 |  | 531 | 283-1358AE | 1307.7045 | 1268.4943 | 1225.88 | 0 | 0 | 0 | 1307.7045 | 1268.4943 | 1225.88 | 0 | 16.9651 | 16.4564 | 15.9036 | 0 | 0 | 0 | 16.9651 | 16.4564 | 15.9036 | 0 | 266.693 | 258.6965 | 250.0057 | 0 | 0 | 0 | 266.693 | 258.6965 | 250.0057 | 0 | 1024.0464 | 993.3414 | 959.9707 | 0 | 0 | 0 | 1024.0464 | 993.3414 | 959.9707 | 0 | 0 | 0 | 0 | 0.17289 | 0.17289 | 0.17289 | 0 | 5000000 | scaled
283-55R | 5299634.3657 | 5223022.4858 | 72583.4736 | 4028.4062 | 98.55% | 1.37% | 0.07601% | 2113986.7922 | 5160611.6247 | 126416.7262 | 29131.0918 | 1958438.9742 | 310512.2603 | 64292.8515 | 4785806.5128 | 283 |  | 532 | 283-55R | 5299634.3657 | 3185647.5734 | 139022.741 | 5223022.4858 | 3140571.3235 | 128193.0113 | 72583.4736 | 41047.8438 | 6801.3234 | 4028.4062 | 318195.8343 | 191779.1081 | 7683.574 | 317892.7039 | 191606.363 | 7652.4224 | 300.0991 | 169.7139 | 28.1203 | 3.0312 | 4907432.5843 | 2948993.61 | 121626.0714 | 4897878.8454 | 2943431.7292 | 120399.1999 | 9187.7957 | 5195.9376 | 860.9283 | 365.9432 | 74005.9471 | 44874.8553 | 9713.0956 | 7250.9365 | 5533.2313 | 141.389 | 63095.5788 | 35682.1923 | 5912.2747 | 3659.4318 | 0.024145 | 0.01499 | 0.0003842 | 0.17173 | 0.09764 | 0.017173 | 0.0056924 | 5000000 | scaled
283-71F | 2013590.1284 | 1767950.8361 | 242238.6417 | 3400.6506 | 87.8% | 12.03% | 0.1689% | 943016.176 | 1971569.0669 | 49887.72 | 94403.8977 | 798724.5583 | 105060.5053 | 198185.8749 | 1668322.6866 | 283 |  | 533 | 283-71F | 2013590.1284 | 1070573.9524 | 42021.0615 | 1767950.8361 | 930161.9721 | 15936.934 | 242238.6417 | 137011.3296 | 22683.477 | 3400.6506 | 106082.3316 | 56194.6116 | 1021.8262 | 105366.9713 | 55788.8888 | 952.5199 | 712.8014 | 403.1639 | 66.7475 | 2.5589 | 1685986.0688 | 887261.5104 | 17663.3822 | 1659785.1509 | 872307.9542 | 14929.9111 | 25892.0004 | 14644.6388 | 2424.5537 | 308.9174 | 221521.7281 | 127117.8303 | 23335.8531 | 2798.7139 | 2065.129 | 54.503 | 215633.8399 | 121963.527 | 20192.1758 | 3089.1743 | 0.015405 | 0.0080156 | 0.0002038 | 0.16992 | 0.096631 | 0.016992 | 0.0047852 | 5000000 | scaled
283-78F | 3886.4275 | 0 | 3886.4275 | 0 | 0% | 100% | 0% | 117.8731 | 246.0734 | 1.5292 | 92.3049 | 24.039 | 3.1924 | 192.6968 | 50.1842 | 283 |  | 534 | 283-78F | 3886.4275 | 3768.5543 | 3640.3541 | 0 | 0 | 0 | 3886.4275 | 3768.5543 | 3640.3541 | 0 | 50.4194 | 48.8903 | 47.2271 | 0 | 0 | 0 | 50.4194 | 48.8903 | 47.2271 | 0 | 792.5973 | 768.5583 | 742.4131 | 0 | 0 | 0 | 792.5973 | 768.5583 | 742.4131 | 0 | 3043.4108 | 2951.1058 | 2850.7139 | 0 | 0 | 0 | 3043.4108 | 2951.1058 | 2850.7139 | 0 | 0 | 0 | 0 | 0.17113 | 0.17113 | 0.17113 | 0 | 5000000 | scaled
283-80F | 22684.3181 | 11406.2619 | 11242.2302 | 35.826 | 50.28% | 49.56% | 0.1579% | 1360.8886 | 12121.1096 | 66.6036 | 277.5638 | 1016.7212 | 666.8536 | 579.0675 | 10875.1885 | 283 |  | 535 | 283-80F | 22684.3181 | 21323.4295 | 10563.2085 | 11406.2619 | 10388.0807 | 0.0029612 | 11242.2302 | 10899.5228 | 10527.3795 | 35.826 | 778.2935 | 711.6899 | 111.4399 | 659.2882 | 596.3116 | 0 | 118.9783 | 115.3514 | 111.4129 | 0.026958 | 12769.647 | 11752.9258 | 1894.4584 | 10746.7683 | 9791.6132 | 0 | 2019.6242 | 1958.0581 | 1891.204 | 3.2545 | 9136.3777 | 8858.8138 | 8557.3102 | 0.20539 | 0.15598 | 0.0029612 | 9103.6277 | 8826.1133 | 8524.7626 | 32.5446 | 8.54e-05 | 6.48e-05 | 1.6e-06 | 0.17059 | 0.17059 | 0.17059 | 4.94e-05 | 5000000 | scaled
283-81 | 1288.0416 | 0 | 1288.0416 | 0 | 0% | 100% | 0% | 39.3364 | 82.1464 | 0.51032 | 30.8038 | 8.0223 | 1.0657 | 64.3278 | 16.7529 | 283 |  | 536 | 283-81 | 1288.0416 | 1248.7052 | 1205.8952 | 0 | 0 | 0 | 1288.0416 | 1248.7052 | 1205.8952 | 0 | 16.71 | 16.1997 | 15.6443 | 0 | 0 | 0 | 16.71 | 16.1997 | 15.6443 | 0 | 262.683 | 254.6607 | 245.93 | 0 | 0 | 0 | 262.683 | 254.6607 | 245.93 | 0 | 1008.6486 | 977.8448 | 944.3208 | 0 | 0 | 0 | 1008.6486 | 977.8448 | 944.3208 | 0 | 0 | 0 | 0 | 0.17007 | 0.17007 | 0.17007 | 0 | 5000000 | scaled
283-83F | 1280.3933 | 0 | 1280.3933 | 0 | 0% | 100% | 0% | 39.3747 | 82.2315 | 0.51082 | 30.8338 | 8.0301 | 1.0668 | 64.3944 | 16.7703 | 283 |  | 537 | 283-83F | 1280.3933 | 1241.0186 | 1198.1618 | 0 | 0 | 0 | 1280.3933 | 1241.0186 | 1198.1618 | 0 | 16.6108 | 16.1 | 15.544 | 0 | 0 | 0 | 16.6108 | 16.1 | 15.544 | 0 | 261.1232 | 253.0931 | 244.3529 | 0 | 0 | 0 | 261.1232 | 253.0931 | 244.3529 | 0 | 1002.6593 | 971.8255 | 938.2649 | 0 | 0 | 0 | 1002.6593 | 971.8255 | 938.2649 | 0 | 0 | 0 | 0 | 0.16898 | 0.16898 | 0.16898 | 0 | 5000000 | scaled
283-85F | 1276.0703 | 0 | 1276.0703 | 0 | 0% | 100% | 0% | 39.3804 | 82.3003 | 0.51089 | 30.8383 | 8.0312 | 1.0677 | 64.4483 | 16.7843 | 283 |  | 538 | 283-85F | 1276.0703 | 1236.6899 | 1193.77 | 0 | 0 | 0 | 1276.0703 | 1236.6899 | 1193.77 | 0 | 16.5547 | 16.0438 | 15.487 | 0 | 0 | 0 | 16.5547 | 16.0438 | 15.487 | 0 | 260.2415 | 252.2103 | 243.4572 | 0 | 0 | 0 | 260.2415 | 252.2103 | 243.4572 | 0 | 999.274 | 968.4358 | 934.8258 | 0 | 0 | 0 | 999.274 | 968.4358 | 934.8258 | 0 | 0 | 0 | 0 | 0.16836 | 0.16836 | 0.16836 | 0 | 5000000 | scaled
284-660R | 67711.0615 | 25335.0003 | 42167.087 | 208.9742 | 37.42% | 62.28% | 0.3086% | 34164.2323 | 64359.3944 | 1280.2146 | 17025.8119 | 15858.2059 | 2096.7135 | 35596.5199 | 26666.161 | 284 |  | 539 | 284-660R | 67711.0615 | 33546.8291 | 3351.6671 | 25335.0003 | 9967.4702 | 321.6099 | 42167.087 | 23370.3848 | 2821.083 | 208.9742 | 2127.8419 | 847.6273 | 31.1284 | 2074.8265 | 818.1744 | 27.4348 | 52.8581 | 29.2957 | 3.5363 | 0.15725 | 27258.4102 | 11400.2043 | 592.2492 | 23030.5561 | 9048.5265 | 291.682 | 4208.8708 | 2332.6944 | 281.5839 | 18.9834 | 38324.8094 | 21298.9975 | 2728.2895 | 229.6177 | 100.7693 | 2.4932 | 37905.3582 | 21008.3947 | 2535.9627 | 189.8336 | 0.0006862 | 0.0002972 | 7.6e-06 | 0.0058802 | 0.003352 | 0.000588 | 0.0003012 | 5000000 | scaled
286-1053R | 76516.3244 | 14918.8305 | 55121.6765 | 6475.8173 | 19.5% | 72.04% | 8.463% | 32814.6917 | 66152.4925 | 205.0761 | 29568.2602 | 3041.3554 | 401.8365 | 59528.6197 | 6222.0363 | 286 |  | 540 | 286-1053R | 76516.3244 | 43701.6327 | 10363.8319 | 14918.8305 | 6716.4216 | 196.674 | 55121.6765 | 30509.3938 | 3691.3405 | 6475.8173 | 419.1774 | 214.1013 | 17.341 | 343.8286 | 170.2206 | 7.7486 | 70.476 | 39.0079 | 4.7196 | 4.8728 | 7172.7255 | 4131.3701 | 950.6892 | 1781.917 | 884.9356 | 40.8091 | 4802.5408 | 2658.1668 | 321.6124 | 588.2677 | 68924.4215 | 39356.1613 | 9395.8018 | 12793.085 | 5661.2654 | 148.1164 | 50248.6597 | 27812.2191 | 3365.0086 | 5882.6768 | 0.018602 | 0.0082122 | 0.0003268 | 0.0058576 | 0.0033346 | 0.0005858 | 0.0091596 | 5000000 | scaled
286-989AE | 139871.578 | 5630.2462 | 126676.0413 | 7565.2905 | 4.025% | 90.57% | 5.409% | 60048.2944 | 124521.3034 | 218.5379 | 54797.2057 | 5032.5508 | 415.4422 | 113748.2147 | 10357.6465 | 286 |  | 541 | 286-989AE | 139871.578 | 79823.2836 | 15350.2746 | 5630.2462 | 2552.4716 | 55.6239 | 126676.0413 | 69705.5215 | 7729.3601 | 7565.2905 | 432.0378 | 213.4999 | 16.5956 | 295.438 | 135.4416 | 2.2306 | 130.9072 | 72.3656 | 8.6724 | 5.6926 | 11704.4854 | 6671.9346 | 1346.839 | 1101.697 | 506.0532 | 8.2504 | 9915.5523 | 5478.6452 | 651.3524 | 687.2362 | 127735.0548 | 72937.8491 | 13986.84 | 4233.1113 | 1910.9768 | 45.1429 | 116629.5818 | 64154.5106 | 7069.3354 | 6872.3617 | 0.020288 | 0.0088672 | 0.0002246 | 0.0058102 | 0.0033054 | 0.000581 | 0.010591 | 5000000 | scaled
286-990AE | 50012.4149 | 2667.7601 | 44215.4182 | 3129.2366 | 5.334% | 88.41% | 6.257% | 21263.3431 | 43895.2728 | 25.6474 | 19185.4179 | 2052.2777 | 54.1651 | 39552.5399 | 4288.5678 | 286 |  | 542 | 286-990AE | 50012.4149 | 28749.0718 | 6117.142 | 2667.7601 | 1162.5145 | 29.7324 | 44215.4182 | 24457.3207 | 2958.1731 | 3129.2366 | 60.0036 | 34.3563 | 5.8385 | 8.8864 | 5.0291 | 0.2215 | 48.7626 | 26.9726 | 3.2624 | 2.3546 | 4878.2414 | 2825.9637 | 589.6736 | 46.2805 | 26.1871 | 1.1539 | 4547.6989 | 2515.5146 | 304.2577 | 284.262 | 45074.1698 | 25888.7518 | 5521.6299 | 2612.5932 | 1131.2984 | 28.3569 | 39618.9567 | 21914.8335 | 2650.653 | 2842.6199 | 0.0083226 | 0.0036044 | 9.1e-05 | 0.0058512 | 0.0033292 | 0.0005852 | 0.0043728 | 5000000 | scaled
286-991 | 4531.5386 | 0 | 4531.5386 | 0 | 0% | 100% | 0% | 719.1152 | 1502.9394 | 0.84097 | 650.9967 | 67.2776 | 1.7576 | 1360.5728 | 140.609 | 286 |  | 543 | 286-991 | 4531.5386 | 3812.4234 | 3028.5991 | 0 | 0 | 0 | 4531.5386 | 3812.4234 | 3028.5991 | 0 | 5.2994 | 4.4584 | 3.5418 | 0 | 0 | 0 | 5.2994 | 4.4584 | 3.5418 | 0 | 423.9527 | 356.6752 | 283.3437 | 0 | 0 | 0 | 423.9527 | 356.6752 | 283.3437 | 0 | 4102.2864 | 3451.2898 | 2741.7137 | 0 | 0 | 0 | 4102.2864 | 3451.2898 | 2741.7137 | 0 | 0 | 0 | 0 | 0.0058638 | 0.0058638 | 0.0058638 | 0 | 5000000 | scaled
287-1118 | 43578.3828 | 32224.9154 | 11001.52 | 351.9474 | 73.95% | 25.25% | 0.8076% | 22080.6101 | 41818.2113 | 1229.989 | 4570.8208 | 16279.8003 | 2224.1745 | 9518.8322 | 30075.2046 | 287 |  | 544 | 287-1118 | 43578.3828 | 21497.7727 | 1760.1714 | 32224.9154 | 15063.3264 | 672.6836 | 11001.52 | 6082.4988 | 735.5405 | 351.9474 | 2273.4661 | 1043.4771 | 49.2916 | 2260.2436 | 1036.0483 | 48.1604 | 12.9576 | 7.164 | 0.86632 | 0.26483 | 30790.7866 | 14510.9863 | 715.582 | 29857.7365 | 13980.8284 | 623.3664 | 901.0789 | 498.1868 | 60.2444 | 31.9711 | 10514.1301 | 5943.3093 | 995.2979 | 106.9352 | 46.4498 | 1.1567 | 10087.4834 | 5577.1481 | 674.4298 | 319.7114 | 0.0008682 | 0.0003758 | 9.6e-06 | 0.0058512 | 0.0033278 | 0.0005852 | 0.0004892 | 5000000 | scaled
287-20 | 45559.3901 | 2796.1965 | 42301.7244 | 461.4692 | 6.137% | 92.85% | 1.013% | 20206.8256 | 42268.1186 | 169.4124 | 17319.3206 | 2718.0926 | 355.868 | 36189.8424 | 5722.4082 | 287 |  | 545 | 287-20 | 45559.3901 | 25352.5645 | 3291.2715 | 2796.1965 | 1478.4449 | 0.080324 | 42301.7244 | 23412.6505 | 2829.722 | 461.4692 | 359.7263 | 190.3139 | 3.8583 | 306.8916 | 160.9165 | 0 | 52.4874 | 29.0501 | 3.5111 | 0.34724 | 5996.8001 | 3278.7075 | 274.3919 | 2479.6435 | 1313.3552 | 0 | 3475.2364 | 1923.4321 | 232.4717 | 41.9202 | 39202.8638 | 21883.5432 | 3013.0213 | 9.6615 | 4.1732 | 0.080324 | 38774.0006 | 21460.1683 | 2593.7393 | 419.2017 | 0.0016908 | 0.000732 | 1.86e-05 | 0.0058122 | 0.0033086 | 0.0005812 | 0.0006352 | 5000000 | scaled
287-23AE | 31156.8198 | 0 | 31156.8198 | 0 | 0% | 100% | 0% | 4942.0175 | 10333.3745 | 6.2136 | 4532.9739 | 402.8301 | 12.9921 | 9478.096 | 842.2863 | 287 |  | 546 | 287-23AE | 31156.8198 | 26214.8022 | 20823.4453 | 0 | 0 | 0 | 31156.8198 | 26214.8022 | 20823.4453 | 0 | 39.1734 | 32.9598 | 26.1813 | 0 | 0 | 0 | 39.1734 | 32.9598 | 26.1813 | 0 | 2539.6315 | 2136.8014 | 1697.3452 | 0 | 0 | 0 | 2539.6315 | 2136.8014 | 1697.3452 | 0 | 28578.0149 | 24045.041 | 19099.9189 | 0 | 0 | 0 | 28578.0149 | 24045.041 | 19099.9189 | 0 | 0 | 0 | 0 | 0.005806 | 0.005806 | 0.005806 | 0 | 5000000 | scaled
287-24AE | 44837.9199 | 0 | 44837.9199 | 0 | 0% | 100% | 0% | 7090.3259 | 14868.5116 | 8.5312 | 6502.732 | 579.0628 | 17.89 | 13636.319 | 1214.3026 | 287 |  | 547 | 287-24AE | 44837.9199 | 37747.594 | 29969.4083 | 0 | 0 | 0 | 44837.9199 | 37747.594 | 29969.4083 | 0 | 53.9497 | 45.4185 | 36.0597 | 0 | 0 | 0 | 53.9497 | 45.4185 | 36.0597 | 0 | 3661.8866 | 3082.8238 | 2447.584 | 0 | 0 | 0 | 3661.8866 | 3082.8238 | 2447.584 | 0 | 41122.0837 | 34619.3517 | 27485.7647 | 0 | 0 | 0 | 41122.0837 | 34619.3517 | 27485.7647 | 0 | 0 | 0 | 0 | 0.0057884 | 0.0057884 | 0.0057884 | 0 | 5000000 | scaled
287-27AE | 66801.3686 | 0 | 66801.3686 | 0 | 0% | 100% | 0% | 10602.7305 | 22151.3894 | 13.1019 | 9690.1378 | 899.4909 | 27.3726 | 20244.7865 | 1879.2303 | 287 |  | 548 | 287-27AE | 66801.3686 | 56198.6381 | 44649.9792 | 0 | 0 | 0 | 66801.3686 | 56198.6381 | 44649.9792 | 0 | 82.5469 | 69.445 | 55.1743 | 0 | 0 | 0 | 82.5469 | 69.445 | 55.1743 | 0 | 5667.1458 | 4767.655 | 3787.9156 | 0 | 0 | 0 | 5667.1458 | 4767.655 | 3787.9156 | 0 | 61051.6758 | 51361.538 | 40806.8894 | 0 | 0 | 0 | 61051.6758 | 51361.538 | 40806.8894 | 0 | 0 | 0 | 0 | 0.005772 | 0.005772 | 0.005772 | 0 | 5000000 | scaled
287-28 | 61.8369 | 0 | 61.8369 | 0 | 0% | 100% | 0% | 9.8173 | 20.5088 | 0.12736 | 7.6878 | 2.0021 | 0.26606 | 16.0602 | 4.1826 | 287 |  | 549 | 287-28 | 61.8369 | 52.0196 | 41.3281 | 0 | 0 | 0 | 61.8369 | 52.0196 | 41.3281 | 0 | 0.80222 | 0.67486 | 0.53616 | 0 | 0 | 0 | 0.80222 | 0.67486 | 0.53616 | 0 | 12.611 | 10.6089 | 8.4284 | 0 | 0 | 0 | 12.611 | 10.6089 | 8.4284 | 0 | 48.4236 | 40.7359 | 32.3635 | 0 | 0 | 0 | 48.4236 | 40.7359 | 32.3635 | 0 | 0 | 0 | 0 | 0.0058142 | 0.0058142 | 0.0058142 | 0 | 5000000 | scaled
287-30 | 61.8241 | 0 | 61.8241 | 0 | 0% | 100% | 0% | 9.857 | 20.5123 | 0.12788 | 7.7189 | 2.0102 | 0.26611 | 16.0629 | 4.1833 | 287 |  | 550 | 287-30 | 61.8241 | 51.9671 | 41.3118 | 0 | 0 | 0 | 61.8241 | 51.9671 | 41.3118 | 0 | 0.80206 | 0.67418 | 0.53595 | 0 | 0 | 0 | 0.80206 | 0.67418 | 0.53595 | 0 | 12.6084 | 10.5982 | 8.4251 | 0 | 0 | 0 | 12.6084 | 10.5982 | 8.4251 | 0 | 48.4137 | 40.6948 | 32.3507 | 0 | 0 | 0 | 48.4137 | 40.6948 | 32.3507 | 0 | 0 | 0 | 0 | 0.005813 | 0.005813 | 0.005813 | 0 | 5000000 | scaled
288-149R | 481284.3353 | 453892.174 | 23823.7737 | 3568.3875 | 94.31% | 4.95% | 0.7414% | 243374.5446 | 474320.7052 | 15528.0514 | 12067.4537 | 215779.0394 | 30260.2585 | 25007.4493 | 419052.9973 | 288 |  | 551 | 288-149R | 481284.3353 | 237909.7907 | 6963.6301 | 453892.174 | 221188.9518 | 1801.5627 | 23823.7737 | 13152.4514 | 1593.6799 | 3568.3875 | 30406.4955 | 14878.4441 | 146.237 | 30371.6376 | 14857.9973 | 141.3997 | 32.1728 | 17.7617 | 2.1522 | 2.6851 | 421105.6747 | 205326.6353 | 2052.6774 | 418750.1054 | 203880.9923 | 1592.6321 | 2031.4145 | 1121.4882 | 135.8905 | 324.1548 | 29772.165 | 17704.7113 | 4764.7157 | 4770.431 | 2449.9622 | 67.5308 | 21760.1863 | 12013.2014 | 1455.6372 | 3241.5477 | 0.010423 | 0.0046954 | 0.0001192 | 0.0057932 | 0.0032904 | 0.0005794 | 0.0050232 | 5000000 | scaled
288-18 | 1717867.0948 | 1651247.1688 | 62685.8201 | 3934.1058 | 96.12% | 3.649% | 0.229% | 923750.2529 | 1691566.2432 | 62765.3369 | 26942.1353 | 834042.7807 | 114346.7656 | 55304.3324 | 1521915.1453 | 288 |  | 552 | 288-18 | 1717867.0948 | 794116.8418 | 26300.8515 | 1651247.1688 | 755570.4653 | 18173.301 | 62685.8201 | 34612.2707 | 4193.4447 | 3934.1058 | 115634.7225 | 52869.3856 | 1287.957 | 115540.4031 | 52815.9809 | 1278.8851 | 91.3591 | 50.4444 | 6.1116 | 2.9603 | 1539642.3145 | 705599.5338 | 17727.1692 | 1531477.3506 | 700931.161 | 16847.4943 | 7807.5871 | 4310.996 | 522.2981 | 357.3769 | 62590.0577 | 35647.9224 | 7285.7253 | 4229.4151 | 1823.3234 | 46.9217 | 54786.8739 | 30250.8304 | 3665.035 | 3573.7687 | 0.014844 | 0.0064276 | 0.000163 | 0.0057502 | 0.003266 | 0.000575 | 0.005543 | 5000000 | scaled
288-2375R | 41801.3993 | 41062.2068 | 523.848 | 215.3444 | 98.23% | 1.253% | 0.5152% | 14732.3422 | 41546.2889 | 971.1382 | 325.2592 | 13435.9449 | 2713.4573 | 865.5261 | 37967.3054 | 288 |  | 553 | 288-2375R | 41801.3993 | 27069.057 | 255.1104 | 41062.2068 | 26564.4835 | 4.7824 | 523.848 | 289.2291 | 34.9836 | 215.3444 | 2713.646 | 1742.5078 | 0.18868 | 2713.085 | 1742.1255 | 0 | 0.39896 | 0.22027 | 0.026643 | 0.16204 | 37989.6597 | 24553.7148 | 22.3543 | 37928.2866 | 24511.0679 | 0 | 41.8111 | 23.0849 | 2.7922 | 19.562 | 1098.0936 | 772.8344 | 232.5674 | 420.8353 | 311.2902 | 4.7824 | 481.638 | 265.9239 | 32.1647 | 195.6203 | 0.00063 | 0.000371 | 9.4e-06 | 0.005783 | 0.0032848 | 0.0005782 | 0.0002986 | 5000000 | scaled
288-2378F | 10859.6376 | 0 | 10859.6376 | 0 | 0% | 100% | 0% | 1730.8969 | 3605.1765 | 2.4073 | 1583.094 | 145.3956 | 5.014 | 3297.3272 | 302.8353 | 288 |  | 554 | 288-2378F | 10859.6376 | 9128.7407 | 7254.4611 | 0 | 0 | 0 | 10859.6376 | 9128.7407 | 7254.4611 | 0 | 15.1033 | 12.696 | 10.0893 | 0 | 0 | 0 | 15.1033 | 12.696 | 10.0893 | 0 | 912.2111 | 766.8155 | 609.3758 | 0 | 0 | 0 | 912.2111 | 766.8155 | 609.3758 | 0 | 9932.3232 | 8349.2292 | 6634.996 | 0 | 0 | 0 | 9932.3232 | 8349.2292 | 6634.996 | 0 | 0 | 0 | 0 | 0.0057612 | 0.0057612 | 0.0057612 | 0 | 5000000 | scaled
288-2379F | 1002.9641 | 0 | 1002.9641 | 0 | 0% | 100% | 0% | 160.0419 | 333.0123 | 0.31769 | 145.7407 | 13.9835 | 0.66105 | 303.2545 | 29.0967 | 288 |  | 555 | 288-2379F | 1002.9641 | 842.9221 | 669.9518 | 0 | 0 | 0 | 1002.9641 | 842.9221 | 669.9518 | 0 | 1.9909 | 1.6732 | 1.3299 | 0 | 0 | 0 | 1.9909 | 1.6732 | 1.3299 | 0 | 87.6332 | 73.6497 | 58.5365 | 0 | 0 | 0 | 87.6332 | 73.6497 | 58.5365 | 0 | 913.3399 | 767.5992 | 610.0853 | 0 | 0 | 0 | 913.3399 | 767.5992 | 610.0853 | 0 | 0 | 0 | 0 | 0.0057718 | 0.0057718 | 0.0057718 | 0 | 5000000 | scaled
288-2380F | 550610.0211 | 511419.522 | 38159.8215 | 1030.6775 | 92.88% | 6.93% | 0.1872% | 242301.0623 | 534997.5548 | 13846.5059 | 15925.4601 | 212529.0963 | 30633.7634 | 33045.6224 | 471318.169 | 288 |  | 556 | 288-2380F | 550610.0211 | 308308.9587 | 15612.4663 | 511419.522 | 286122.8812 | 11840.2065 | 38159.8215 | 21155.4 | 2741.5822 | 1030.6775 | 31367.7842 | 17521.2783 | 734.0208 | 31311.8801 | 17489.94 | 729.2845 | 55.1286 | 30.5627 | 3.9607 | 0.77555 | 482752.4104 | 270223.3141 | 11434.2413 | 479343.2856 | 268291.6101 | 11102.4129 | 3315.4973 | 1838.0765 | 238.201 | 93.6275 | 36489.8265 | 20564.3664 | 3444.2041 | 764.3564 | 341.3311 | 8.5091 | 34789.1956 | 19286.7608 | 2499.4205 | 936.2745 | 0.0043964 | 0.0022422 | 5.68e-05 | 0.024461 | 0.013894 | 0.0024462 | 0.0014864 | 5000000 | scaled
289-1559 | 4416.9519 | 138.6593 | 3919.5264 | 358.7662 | 3.139% | 88.74% | 8.122% | 1817.9339 | 3795.7949 | 8.2672 | 1633.2908 | 176.3759 | 18.628 | 3401.6297 | 375.5372 | 289 |  | 557 | 289-1559 | 4416.9519 | 2599.018 | 621.157 | 138.6593 | 72.0447 | 0.50785 | 3919.5264 | 2168.2071 | 261.8829 | 358.7662 | 19.1791 | 10.9119 | 0.55116 | 14.7005 | 8.3138 | 0 | 4.2086 | 2.3281 | 0.2812 | 0.26996 | 429.5351 | 253.1592 | 53.9979 | 76.5468 | 43.3308 | 0 | 320.3977 | 177.2379 | 21.4074 | 32.5906 | 3968.2376 | 2334.9468 | 566.6079 | 47.412 | 20.4001 | 0.50785 | 3594.92 | 1988.641 | 240.1944 | 325.9057 | 0.000989 | 0.0004466 | 1.14e-05 | 0.0057552 | 0.0032754 | 0.0005756 | 0.0005094 | 5000000 | scaled
289-905AE | 40945.235 | 6730.4249 | 31084.3447 | 3130.4654 | 16.44% | 75.92% | 7.645% | 17707.4165 | 35668.5759 | 67.0046 | 15873.6081 | 1766.8038 | 122.9139 | 31943.4495 | 3602.2125 | 289 |  | 558 | 289-905AE | 40945.235 | 23237.8185 | 5276.6591 | 6730.4249 | 2912.8598 | 69.3419 | 31084.3447 | 17194.4933 | 2076.8518 | 3130.4654 | 127.9629 | 60.9582 | 5.049 | 91.9663 | 39.9939 | 0.44576 | 33.641 | 18.6087 | 2.2477 | 2.3556 | 4113.0823 | 2346.2785 | 510.8697 | 472.7759 | 205.5504 | 2.2747 | 3355.9328 | 1856.3545 | 224.2214 | 284.3736 | 36704.1899 | 20830.5818 | 4760.7404 | 6165.6827 | 2667.3155 | 66.6215 | 27694.771 | 15319.5301 | 1850.3827 | 2843.7362 | 0.0086756 | 0.0037568 | 9.64e-05 | 0.0057234 | 0.0032568 | 0.0005724 | 0.0044014 | 5000000 | scaled
289-906AE | 60632.2016 | 3654.4768 | 53878.7608 | 3098.9639 | 6.027% | 88.86% | 5.111% | 26157.2459 | 53895.1841 | 123.9258 | 22653.9236 | 3379.3965 | 214.5015 | 46846.8136 | 6833.869 | 289 |  | 559 | 289-906AE | 60632.2016 | 34474.9557 | 6737.0175 | 3654.4768 | 1533.5824 | 33.4488 | 53878.7608 | 29842.4094 | 3604.6048 | 3098.9639 | 221.7593 | 97.8335 | 7.2579 | 161.0765 | 63.1822 | 1.0222 | 58.351 | 32.3195 | 3.9038 | 2.3319 | 7550.8087 | 4171.4122 | 716.9397 | 839.85 | 328.7533 | 5.2839 | 6429.4467 | 3561.1469 | 430.1438 | 281.512 | 52859.6336 | 30205.71 | 6012.8199 | 2653.5504 | 1141.6469 | 27.1427 | 47390.9632 | 26248.9431 | 3170.5572 | 2815.12 | 0.0070966 | 0.0030964 | 7.9e-05 | 0.0057188 | 0.0032582 | 0.0005718 | 0.0043336 | 5000000 | scaled
289-907 | 40108.7304 | 1030.9681 | 36169.1273 | 2908.635 | 2.57% | 90.18% | 7.252% | 16686.6944 | 34769.6537 | 48.8804 | 14958.5131 | 1679.301 | 95.5098 | 31191.9641 | 3482.1798 | 289 |  | 560 | 289-907 | 40108.7304 | 23422.036 | 5339.0767 | 1030.9681 | 457.9176 | 14.8695 | 36169.1273 | 20055.4835 | 2415.5721 | 2908.635 | 102.1269 | 53.2466 | 6.6171 | 49.0389 | 22.8346 | 1.0291 | 50.8994 | 28.2233 | 3.3993 | 2.1887 | 3983.2038 | 2303.9028 | 501.024 | 255.2181 | 119.0522 | 5.4725 | 3463.7633 | 1920.6282 | 231.3291 | 264.2224 | 36023.3997 | 21064.8867 | 4831.4356 | 726.7111 | 316.0308 | 8.3679 | 32654.4646 | 18106.6319 | 2180.8437 | 2642.224 | 0.0075686 | 0.0032772 | 8.34e-05 | 0.0057238 | 0.0032642 | 0.0005724 | 0.0040986 | 5000000 | scaled
292-317F | 133935.9634 | 0 | 133935.9634 | 0 | 0% | 100% | 0% | 12845.1814 | 26697.2096 | 17.3928 | 11748.0898 | 1079.6987 | 36.1488 | 24417.033 | 2244.0278 | 292 |  | 561 | 292-317F | 133935.9634 | 121090.7821 | 107238.7538 | 0 | 0 | 0 | 133935.9634 | 121090.7821 | 107238.7538 | 0 | 181.3534 | 163.9607 | 145.2046 | 0 | 0 | 0 | 181.3534 | 163.9607 | 145.2046 | 0 | 11257.9564 | 10178.2577 | 9013.9287 | 0 | 0 | 0 | 11257.9564 | 10178.2577 | 9013.9287 | 0 | 122496.6535 | 110748.5637 | 98079.6206 | 0 | 0 | 0 | 122496.6535 | 110748.5637 | 98079.6206 | 0 | 0 | 0 | 0 | 0.043158 | 0.043158 | 0.043158 | 0 | 5000000 | scaled
295-1201F | 616.1921 | 477.6017 | 0 | 138.5904 | 77.51% | 0% | 22.49% | 199.241 | 477.5499 | 23.7865 | 3.1204 | 172.3342 | 53.0136 | 5.5197 | 419.0166 | 295 |  | 562 | 295-1201F | 616.1921 | 416.9511 | 138.6422 | 477.6017 | 278.3607 | 0.051822 | 0 | 0 | 0 | 138.5904 | 53.1179 | 29.3314 | 0.10428 | 53.0136 | 29.2271 | 0 | 0 | 0 | 0 | 0.10428 | 431.6063 | 259.2721 | 12.5896 | 419.0166 | 246.6825 | 0 | 0 | 0 | 0 | 12.5896 | 131.4679 | 128.3476 | 125.9483 | 5.5715 | 2.4511 | 0.051822 | 0 | 0 | 0 | 125.8965 | 0.000452 | 0.0001958 | 5e-06 | 0 | 0 | 0 | 0.0002024 | 5000000 | scaled
295-1203F | 804.4752 | 486.659 | 0 | 317.8162 | 60.49% | 0% | 39.51% | 204.8142 | 486.3603 | 33.6287 | 21.8156 | 149.3699 | 81.7292 | 37.2269 | 367.4042 | 295 |  | 563 | 295-1203F | 804.4752 | 599.661 | 318.1149 | 486.659 | 281.8448 | 0.29872 | 0 | 0 | 0 | 317.8162 | 81.9683 | 48.3397 | 0.23915 | 81.7292 | 48.1005 | 0 | 0 | 0 | 0 | 0.23915 | 396.2749 | 246.905 | 28.8706 | 367.4042 | 218.0343 | 0 | 0 | 0 | 0 | 28.8706 | 326.232 | 304.4164 | 289.0051 | 37.5256 | 15.71 | 0.29872 | 0 | 0 | 0 | 288.7064 | 0.0008828 | 0.0003822 | 9.6e-06 | 0 | 0 | 0 | 0.0004534 | 5000000 | scaled
296-66F | 2283.986 | 2068.8061 | 0 | 215.1799 | 90.58% | 0% | 9.421% | 1592.874 | 2047.6609 | 262.9372 | 1.8268 | 1328.11 | 338.9649 | 3.1884 | 1705.5076 | 296 |  | 564 | 296-66F | 2283.986 | 691.112 | 236.3251 | 2068.8061 | 475.9321 | 21.1452 | 0 | 0 | 0 | 215.1799 | 343.3871 | 80.4499 | 4.4222 | 343.2252 | 80.288 | 4.2603 | 0 | 0 | 0 | 0.16192 | 1741.9083 | 413.7983 | 36.4006 | 1722.3612 | 394.2512 | 16.8536 | 0 | 0 | 0 | 19.5471 | 198.6906 | 196.8638 | 195.5023 | 3.2197 | 1.3929 | 0.031363 | 0 | 0 | 0 | 195.4709 | 0.0003162 | 0.000137 | 3.4e-06 | 0 | 0 | 0 | 0.0003016 | 5000000 | scaled
296-68F | 3230.058 | 2550.7142 | 0 | 679.3438 | 78.97% | 0% | 21.03% | 1207.8883 | 2542.7388 | 222.3153 | 141.7828 | 843.7902 | 452.0449 | 346.1367 | 1744.5572 | 296 |  | 565 | 296-68F | 3230.058 | 2022.1697 | 687.3193 | 2550.7142 | 1342.8259 | 7.9754 | 0 | 0 | 0 | 679.3438 | 453.7396 | 231.4243 | 1.6948 | 453.2285 | 230.9131 | 1.1836 | 0 | 0 | 0 | 0.51118 | 1809.7916 | 966.0014 | 65.2343 | 1748.0795 | 904.2893 | 3.5223 | 0 | 0 | 0 | 61.7121 | 966.5268 | 824.7441 | 620.3902 | 349.4062 | 207.6234 | 3.2696 | 0 | 0 | 0 | 617.1206 | 0.0017566 | 0.000843 | 2.16e-05 | 0 | 0 | 0 | 0.000958 | 5000000 | scaled
297-828AE | 51977.572 | 50793.3898 | 0 | 1184.1822 | 97.72% | 0% | 2.278% | 30324.0845 | 50124.9836 | 3964.4854 | 212.7221 | 26146.877 | 6572.931 | 371.2607 | 43180.7919 | 297 |  | 566 | 297-828AE | 51977.572 | 21653.4875 | 1852.5884 | 50793.3898 | 20469.3053 | 668.4062 | 0 | 0 | 0 | 1184.1822 | 6656.1836 | 2691.6982 | 83.2526 | 6655.2925 | 2690.8072 | 82.3615 | 0 | 0 | 0 | 0.89106 | 43870.0934 | 17723.2163 | 689.3015 | 43762.5214 | 17615.6444 | 581.7295 | 0 | 0 | 0 | 107.5719 | 1451.2951 | 1238.573 | 1080.0344 | 375.5758 | 162.8537 | 4.3151 | 0 | 0 | 0 | 1075.7193 | 0.0046362 | 0.0020076 | 5.16e-05 | 0 | 0 | 0 | 0.0016492 | 5000000 | scaled
298-384 | 146.6996 | 110.7252 | 0 | 35.9744 | 75.48% | 0% | 24.52% | 25.5743 | 107.5761 | 1.8995 | 12.7873 | 10.8875 | 8.5031 | 50.4945 | 48.5785 | 298 |  | 567 | 298-384 | 146.6996 | 121.1253 | 39.1235 | 110.7252 | 85.1509 | 3.1491 | 0 | 0 | 0 | 35.9744 | 8.9262 | 7.0268 | 0.42317 | 8.8992 | 6.9997 | 0.3961 | 0 | 0 | 0 | 0.02707 | 53.8833 | 42.9958 | 5.3047 | 50.6153 | 39.7278 | 2.0368 | 0 | 0 | 0 | 3.2679 | 83.8901 | 71.1028 | 33.3956 | 51.2107 | 38.4234 | 0.71625 | 0 | 0 | 0 | 32.6794 | 5.42e-05 | 4.12e-05 | 1e-06 | 0 | 0 | 0 | 4.92e-05 | 5000000 | scaled
298-42R | 3826.2634 | 2433.245 | 0 | 1393.0184 | 63.59% | 0% | 36.41% | 1301.348 | 2422.827 | 111.1067 | 514.33 | 675.9112 | 207.3979 | 975.0016 | 1240.4275 | 298 |  | 568 | 298-42R | 3826.2634 | 2524.9154 | 1403.4365 | 2433.245 | 1131.8971 | 10.4181 | 0 | 0 | 0 | 1393.0184 | 208.7224 | 97.6156 | 1.3245 | 207.6742 | 96.5674 | 0.27628 | 0 | 0 | 0 | 1.0482 | 1368.4011 | 692.4899 | 127.9736 | 1241.8584 | 565.9472 | 1.4309 | 0 | 0 | 0 | 126.5427 | 2249.1399 | 1734.8099 | 1274.1383 | 983.7125 | 469.3824 | 8.7109 | 0 | 0 | 0 | 1265.4274 | 0.0044022 | 0.0021048 | 5.36e-05 | 0 | 0 | 0 | 0.0019492 | 5000000 | scaled
299-1010AE | 300.8992 | 47.9966 | 0 | 252.9026 | 15.95% | 0% | 84.05% | 27.6676 | 47.4821 | 0.18012 | 26.5702 | 0.91734 | 0.18012 | 46.3846 | 0.91734 | 299 |  | 569 | 299-1010AE | 300.8992 | 273.2316 | 253.4171 | 47.9966 | 20.329 | 0.51452 | 0 | 0 | 0 | 252.9026 | 0.37042 | 0.1903 | 0.1903 | 0.18012 | 0 | 0 | 0 | 0 | 0 | 0.1903 | 23.8912 | 22.9738 | 22.9738 | 0.91734 | 0 | 0 | 0 | 0 | 0 | 22.9738 | 276.6376 | 250.0674 | 230.253 | 46.8992 | 20.329 | 0.51452 | 0 | 0 | 0 | 229.7385 | 0.0008278 | 0.0003588 | 9e-06 | 0 | 0 | 0 | 0.0003542 | 5000000 | scaled
299-1011 | 54999.0743 | 51753.9666 | 0 | 3245.1078 | 94.1% | 0% | 5.9% | 25956.8025 | 51366.8748 | 1830.6416 | 9603.2346 | 14522.9264 | 3689.2616 | 17638.5577 | 30039.0555 | 299 |  | 570 | 299-1011 | 54999.0743 | 29042.2719 | 3632.1996 | 51753.9666 | 25797.1641 | 387.0918 | 0 | 0 | 0 | 3245.1078 | 3721.6142 | 1890.9727 | 32.3527 | 3719.1724 | 1888.5308 | 29.9108 | 0 | 0 | 0 | 2.4418 | 30535.4782 | 16012.5518 | 496.4227 | 30240.6904 | 15717.764 | 201.6349 | 0 | 0 | 0 | 294.7878 | 20741.9819 | 11138.7474 | 3103.4242 | 17794.1038 | 8190.8692 | 155.5461 | 0 | 0 | 0 | 2947.8781 | 0.008609 | 0.0039818 | 0.0001004 | 0 | 0 | 0 | 0.0045848 | 5000000 | scaled
299-1153F | 12694.3607 | 12299.9867 | 0 | 394.374 | 96.89% | 0% | 3.107% | 5055.8267 | 12251.9812 | 385.1801 | 1180.1664 | 3490.4801 | 899.1803 | 2888.9014 | 8463.8994 | 299 |  | 571 | 299-1153F | 12694.3607 | 7638.534 | 442.3795 | 12299.9867 | 7244.16 | 48.0055 | 0 | 0 | 0 | 394.374 | 902.7075 | 517.5274 | 3.5272 | 902.4108 | 517.2307 | 3.2305 | 0 | 0 | 0 | 0.29675 | 8518.9306 | 5028.4505 | 55.0312 | 8483.1054 | 4992.6253 | 19.206 | 0 | 0 | 0 | 35.8252 | 3272.7225 | 2092.5561 | 383.8211 | 2914.4705 | 1734.3041 | 25.5691 | 0 | 0 | 0 | 358.252 | 0.0007872 | 0.000417 | 1.06e-05 | 0 | 0 | 0 | 0.0005502 | 5000000 | scaled
299-814AE | 92055.4865 | 90045.9657 | 0 | 2009.5208 | 97.82% | 0% | 2.183% | 45893.7223 | 89913.4121 | 5293.9117 | 677.3357 | 39922.4749 | 10291.5643 | 1176.7142 | 78445.1336 | 299 |  | 572 | 299-814AE | 92055.4865 | 46161.7643 | 2142.0745 | 90045.9657 | 44152.2434 | 132.5536 | 0 | 0 | 0 | 2009.5208 | 10312.5599 | 5018.6482 | 20.9956 | 10311.0478 | 5017.1361 | 19.4835 | 0 | 0 | 0 | 1.5121 | 78728.3308 | 38805.856 | 283.1973 | 78545.7846 | 38623.3097 | 100.651 | 0 | 0 | 0 | 182.5462 | 3014.5958 | 2337.2601 | 1837.8816 | 1189.1333 | 511.7976 | 12.4191 | 0 | 0 | 0 | 1825.4625 | 0.0061788 | 0.0027386 | 6.98e-05 | 0 | 0 | 0 | 0.0028148 | 5000000 | scaled
299-815 | 28225.5574 | 25831.5465 | 0 | 2394.0109 | 91.52% | 0% | 8.482% | 15379.8802 | 25727.2494 | 1247.0516 | 1644.9774 | 12487.8513 | 2087.8433 | 4054.4551 | 19584.951 | 299 |  | 573 | 299-815 | 28225.5574 | 12845.6772 | 2498.308 | 25831.5465 | 10451.6663 | 104.2971 | 0 | 0 | 0 | 2394.0109 | 2096.9855 | 849.934 | 9.1422 | 2095.1841 | 848.1325 | 7.3408 | 0 | 0 | 0 | 1.8014 | 19849.1757 | 7361.3244 | 264.2247 | 19631.7021 | 7143.8508 | 46.7511 | 0 | 0 | 0 | 217.4736 | 6279.3962 | 4634.4188 | 2224.9411 | 4104.6603 | 2459.6829 | 50.2052 | 0 | 0 | 0 | 2174.7359 | 0.0068236 | 0.0034148 | 8.58e-05 | 0 | 0 | 0 | 0.0033296 | 5000000 | scaled
300-483F | 458782.0524 | 456399.3169 | 0 | 2382.7354 | 99.48% | 0% | 0.5194% | 109071.8686 | 448352.7755 | 9353.9366 | 0 | 99717.932 | 38489.0514 | 0 | 409863.7241 | 300 |  | 574 | 300-483F | 458782.0524 | 349710.1838 | 10429.2769 | 456399.3169 | 347327.4483 | 8046.5414 | 0 | 0 | 0 | 2382.7354 | 39168.1137 | 29814.177 | 679.0623 | 39166.3207 | 29812.3841 | 677.2694 | 0 | 0 | 0 | 1.7929 | 417449.4455 | 317731.5135 | 7585.7214 | 417232.9962 | 317515.0642 | 7369.272 | 0 | 0 | 0 | 216.4493 | 2164.4932 | 2164.4932 | 2164.4932 | 0 | 0 | 0 | 0 | 0 | 0 | 2164.4932 | 0.015035 | 0.011344 | 0.0002886 | 0 | 0 | 0 | 0.003362 | 5000000 | scaled
300-484F | 754132.3013 | 696898.4187 | 51897.5748 | 5336.3078 | 92.41% | 6.882% | 0.7076% | 306026.74 | 735294.4423 | 19391.0954 | 36413.9112 | 250221.7334 | 46779.7755 | 75607.9352 | 612906.7316 | 300 |  | 575 | 300-484F | 754132.3013 | 448105.5613 | 18837.859 | 696898.4187 | 413930.705 | 10010.7049 | 51897.5748 | 28838.5485 | 3490.8462 | 5336.3078 | 47484.6683 | 28093.5729 | 704.8929 | 47430.567 | 28061.7257 | 697.5085 | 50.0859 | 27.8318 | 3.369 | 4.0154 | 622627.7046 | 372405.9712 | 9720.973 | 617178.5323 | 369162.5794 | 8902.2918 | 4964.4185 | 2758.638 | 333.9274 | 484.7539 | 84019.9283 | 47606.0172 | 8411.9931 | 32289.3194 | 16706.3999 | 410.9047 | 46883.0704 | 26052.0786 | 3153.5498 | 4847.5386 | 0.026751 | 0.015216 | 0.0003856 | 0.0056236 | 0.003213 | 0.0005624 | 0.0075476 | 5000000 | scaled
303-188 | 1835.331 | 0 | 1835.331 | 0 | 0% | 100% | 0% | 291.2822 | 606.7089 | 1.1528 | 255.6121 | 34.5174 | 2.4011 | 532.4119 | 71.8959 | 303 |  | 576 | 303-188 | 1835.331 | 1544.0487 | 1228.622 | 0 | 0 | 0 | 1835.331 | 1544.0487 | 1228.622 | 0 | 7.2634 | 6.1107 | 4.8624 | 0 | 0 | 0 | 7.2634 | 6.1107 | 4.8624 | 0 | 217.4894 | 182.972 | 145.5935 | 0 | 0 | 0 | 217.4894 | 182.972 | 145.5935 | 0 | 1610.5781 | 1354.966 | 1078.1662 | 0 | 0 | 0 | 1610.5781 | 1354.966 | 1078.1662 | 0 | 0 | 0 | 0 | 0.010743 | 0.010743 | 0.010743 | 0 | 5000000 | scaled
303-189AE | 171003.4457 | 5809.1931 | 160414.7073 | 4779.5452 | 3.397% | 93.81% | 2.795% | 74907.0807 | 155376.0186 | 181.6455 | 68309.778 | 6415.6572 | 352.1074 | 141800.1726 | 13223.7386 | 303 |  | 577 | 303-189AE | 171003.4457 | 96096.365 | 15627.4271 | 5809.1931 | 2763.1026 | 58.8032 | 160414.7073 | 88553.7172 | 10789.0787 | 4779.5452 | 370.7171 | 189.0716 | 18.6097 | 148.6702 | 64.8839 | 0.32082 | 218.4504 | 120.5912 | 14.6924 | 3.5965 | 14558.1369 | 8142.4797 | 1334.3983 | 763.5444 | 332.9536 | 1.6342 | 13360.4153 | 7375.3489 | 898.587 | 434.1772 | 156074.5917 | 87764.8137 | 14274.4191 | 4896.9785 | 2365.265 | 56.8482 | 146835.8416 | 81057.7771 | 9875.7992 | 4341.7716 | 0.015223 | 0.006762 | 0.0001716 | 0.010608 | 0.0060222 | 0.0010608 | 0.0068364 | 5000000 | scaled
303-487AE | 106350.1307 | 5298.298 | 99768.9125 | 1282.9203 | 4.982% | 93.81% | 1.206% | 47560.8962 | 98317.4805 | 197.3579 | 42928.2225 | 4435.3158 | 353.5152 | 89042.2832 | 8921.6821 | 303 |  | 578 | 303-487AE | 106350.1307 | 58789.2345 | 8032.6502 | 5298.298 | 2411.1957 | 43.2585 | 99768.9125 | 55095.1185 | 6706.4715 | 1282.9203 | 363.6079 | 166.25 | 10.0927 | 238.7726 | 96.8802 | 0.80077 | 123.8699 | 68.4044 | 8.3265 | 0.96536 | 9593.5436 | 5158.2278 | 671.8615 | 1276.8635 | 513.3458 | 4.1064 | 8200.1388 | 4528.3406 | 551.2138 | 116.5414 | 96392.9793 | 53464.7568 | 7350.696 | 3782.6619 | 1800.9696 | 38.3513 | 91444.9038 | 50498.3736 | 6146.9312 | 1165.4135 | 0.00358 | 0.0016374 | 4.12e-05 | 0.01065 | 0.0060492 | 0.001065 | 0.0018084 | 5000000 | scaled
305-32R | 4233866.5476 | 4103697.3678 | 124613.0467 | 5556.133 | 96.93% | 2.943% | 0.1312% | 2361584.1974 | 4179988.9172 | 131776.5814 | 49404.0856 | 2180403.5304 | 232206.5305 | 102912.4444 | 3844869.9423 | 305 |  | 579 | 305-32R | 4233866.5476 | 1872282.3501 | 53877.6304 | 4103697.3678 | 1796962.4706 | 38098.4145 | 124613.0467 | 69763.7465 | 10223.0829 | 5556.133 | 234384.6887 | 102608.1073 | 2178.1582 | 234223.8377 | 102516.2158 | 2161.1244 | 156.6701 | 87.7107 | 12.853 | 4.1808 | 3882435.8052 | 1702032.2748 | 37565.8629 | 3868009.8756 | 1693733.8612 | 35919.0633 | 13921.2067 | 7793.6906 | 1142.0766 | 504.7229 | 117046.0537 | 67641.9681 | 14133.6093 | 1463.6545 | 712.3936 | 18.2268 | 110535.1699 | 61882.3452 | 9068.1532 | 5047.2293 | 0.020612 | 0.0090704 | 0.0002304 | 0.051829 | 0.029467 | 0.0051828 | 0.0077926 | 5000000 | scaled
305-35R | 2371785.9811 | 2317507.7248 | 49995.5032 | 4282.7531 | 97.71% | 2.108% | 0.1806% | 1345796.328 | 2337227.407 | 78217.8857 | 21115.1112 | 1246463.3311 | 135576.1611 | 43607.6156 | 2158043.6303 | 305 |  | 580 | 305-35R | 2371785.9811 | 1025989.6531 | 34558.5741 | 2317507.7248 | 993723.6866 | 26169.7795 | 49995.5032 | 27983.2134 | 4106.0415 | 4282.7531 | 137111.1209 | 58893.2352 | 1534.9598 | 137047.6245 | 58856.2765 | 1526.787 | 60.2738 | 33.7361 | 4.9502 | 3.2226 | 2183440.1987 | 936976.8676 | 25396.5684 | 2178328.9433 | 933944.7311 | 24619.6937 | 4722.2072 | 2643.0884 | 387.8265 | 389.0482 | 51234.6615 | 30119.5503 | 7627.0459 | 2131.157 | 922.679 | 23.2988 | 45213.0222 | 25306.389 | 3713.2649 | 3890.4823 | 0.015845 | 0.0068604 | 0.0001734 | 0.052229 | 0.029689 | 0.0052228 | 0.0060642 | 5000000 | scaled
306-961 | 44898.8737 | 16794.6621 | 27934.3957 | 169.8159 | 37.41% | 62.22% | 0.3782% | 20060.9413 | 42424.565 | 539.2381 | 12037.5378 | 7484.1654 | 1072.4527 | 25060.288 | 16291.8243 | 306 |  | 581 | 306-961 | 44898.8737 | 24837.9324 | 2474.3087 | 16794.6621 | 9001.186 | 9.5771 | 27934.3957 | 15666.9305 | 2294.9157 | 169.8159 | 1075.4062 | 536.1682 | 2.9535 | 1040.883 | 516.7498 | 0 | 34.3954 | 19.2906 | 2.8257 | 0.12778 | 16633.5023 | 9149.3369 | 341.678 | 12646.8419 | 6906.6548 | 0 | 3971.2341 | 2227.256 | 326.2518 | 15.4262 | 27189.9651 | 15152.4273 | 2129.6772 | 3106.9371 | 1577.7814 | 9.5771 | 23928.7661 | 13420.3839 | 1965.8381 | 154.262 | 0.0007012 | 0.0003036 | 7.8e-06 | 0.052043 | 0.029641 | 0.0052042 | 0.0002382 | 5000000 | scaled
307-1492R | 744313.2583 | 688944.1383 | 54550.7998 | 818.3202 | 92.56% | 7.329% | 0.1099% | 410168.3837 | 738463.593 | 21788.5409 | 22038.5532 | 366341.2896 | 38750.6016 | 46129.3246 | 653583.6669 | 307 |  | 582 | 307-1492R | 744313.2583 | 334144.8746 | 5849.6653 | 688944.1383 | 302744.7442 | 549.5488 | 54550.7998 | 30581.8102 | 4481.7962 | 818.3202 | 38798.2114 | 17009.6705 | 47.6098 | 38720.0613 | 16965.5881 | 40.624 | 77.5343 | 43.4666 | 6.3701 | 0.61576 | 654555.8124 | 288214.5228 | 972.1456 | 649624.4275 | 285417.2686 | 498.7624 | 4857.0482 | 2722.9175 | 399.0464 | 74.3368 | 50959.2345 | 28920.6813 | 4829.9099 | 599.6495 | 361.8875 | 10.1625 | 49616.2173 | 27815.4261 | 4076.3798 | 743.3677 | 0.0038958 | 0.0017384 | 4.46e-05 | 0.052048 | 0.029632 | 0.0052048 | 0.0011712 | 5000000 | scaled
307-1538F | 2407233.1842 | 2192285.3193 | 213353.479 | 1594.386 | 91.07% | 8.863% | 0.06623% | 1358172.7843 | 2375909.2597 | 67527.5056 | 84035.046 | 1206610.2326 | 116646.0214 | 174855.5008 | 2084407.7376 | 307 |  | 583 | 307-1538F | 2407233.1842 | 1049060.3999 | 31323.9244 | 2192285.3193 | 927566.234 | 10869.2449 | 213353.479 | 119899.78 | 18860.2936 | 1594.386 | 117307.5512 | 49780.0456 | 661.5298 | 116990.851 | 49601.5418 | 632.4401 | 315.5005 | 177.3041 | 27.89 | 1.1997 | 2096682.6461 | 890072.4135 | 12274.9085 | 2075095.9205 | 877877.7259 | 10234.6258 | 21441.8905 | 12049.8525 | 1895.4476 | 144.8351 | 193242.9869 | 109207.9409 | 18387.4861 | 198.5478 | 86.9663 | 2.179 | 191596.088 | 107672.6234 | 16936.9559 | 1448.3511 | 0.0068496 | 0.0030482 | 7.7e-05 | 0.091866 | 0.052154 | 0.0091866 | 0.0022626 | 5000000 | scaled
307-1684R | 2117857.3694 | 2065519.6984 | 49338.8766 | 2998.7944 | 97.53% | 2.33% | 0.1416% | 1154979.9078 | 2086416.4462 | 64193.8894 | 20120.6586 | 1070665.3599 | 115121.4565 | 41872.7833 | 1929422.2064 | 307 |  | 584 | 307-1684R | 2117857.3694 | 962877.4615 | 31440.9232 | 2065519.6984 | 932217.125 | 24388.2881 | 49338.8766 | 27661.5421 | 4053.8407 | 2998.7944 | 116523.2118 | 52329.3224 | 1401.7553 | 116473.3955 | 52300.4018 | 1395.5911 | 47.5598 | 26.6641 | 3.9077 | 2.2565 | 1953052.7126 | 882387.3527 | 23630.5062 | 1948224.1087 | 879560.5391 | 22983.7424 | 4556.1914 | 2554.4011 | 374.3513 | 272.4125 | 48281.445 | 28160.7864 | 6408.6617 | 822.1942 | 356.1841 | 8.9546 | 44735.1254 | 25080.4769 | 3675.5817 | 2724.1254 | 0.011162 | 0.0048332 | 0.0001222 | 0.052098 | 0.029663 | 0.0052098 | 0.0041824 | 5000000 | scaled
307-234R | 4762848.0442 | 4550698.7421 | 208808.1126 | 3341.1895 | 95.55% | 4.384% | 0.07015% | 2014068.0618 | 4671033.2147 | 103945.9332 | 84688.1693 | 1825433.9592 | 242180.4579 | 177498.0069 | 4251354.75 | 307 |  | 585 | 307-234R | 4762848.0442 | 2748779.9824 | 91814.8294 | 4550698.7421 | 2627936.7181 | 70014.8249 | 208808.1126 | 117502.0748 | 18458.8151 | 3341.1895 | 245939.3238 | 141993.3906 | 3758.8659 | 245687.3561 | 141850.502 | 3734.2998 | 249.4536 | 140.3744 | 22.0519 | 2.5141 | 4319539.7344 | 2494105.7752 | 68184.9844 | 4300268.8496 | 2483128.7985 | 66204.7369 | 18967.3688 | 10673.4607 | 1676.7316 | 303.5159 | 197368.986 | 112680.8167 | 19870.9792 | 4742.5364 | 2957.4176 | 75.7881 | 189591.2902 | 106688.2397 | 16760.0316 | 3035.1594 | 0.01324 | 0.0074136 | 0.0001886 | 0.092019 | 0.052308 | 0.009202 | 0.0047476 | 5000000 | scaled
308-464 | 187214.6683 | 9916.229 | 175118.4103 | 2180.029 | 5.297% | 93.54% | 1.164% | 83464.6338 | 171831.6386 | 336.1248 | 75053.3888 | 8075.1203 | 624.204 | 154738.2018 | 16469.2328 | 308 |  | 586 | 308-464 | 187214.6683 | 103750.0345 | 15383.0297 | 9916.229 | 4306.3874 | 61.9249 | 175118.4103 | 97263.6182 | 13141.0758 | 2180.029 | 645.9752 | 309.8504 | 21.7711 | 376.0722 | 159.2126 | 0 | 268.2626 | 148.9974 | 20.1307 | 1.6404 | 17868.7098 | 9793.5895 | 1399.477 | 1660.2229 | 703.0886 | 0 | 16010.4515 | 8892.4656 | 1201.4417 | 198.0353 | 168699.9834 | 93646.5946 | 13961.7816 | 7879.9339 | 3444.0862 | 61.9249 | 158839.6962 | 88222.1551 | 11919.5034 | 1980.3533 | 0.0072068 | 0.0031208 | 7.9e-05 | 0.029804 | 0.016923 | 0.0029804 | 0.0030798 | 5000000 | scaled
308-484AE | 121718.5902 | 10533.5588 | 108033.2691 | 3151.7622 | 8.654% | 88.76% | 2.589% | 53930.2403 | 110403.7557 | 704.9982 | 45415.1508 | 7810.0913 | 1311.188 | 93840.8077 | 15251.76 | 308 |  | 587 | 308-484AE | 121718.5902 | 67788.3499 | 11314.8344 | 10533.5588 | 4710.8027 | 56.6575 | 108033.2691 | 59925.785 | 8106.4148 | 3151.7622 | 1331.2517 | 626.2535 | 20.0636 | 1180.2503 | 541.4373 | 6.5394 | 148.6298 | 82.4446 | 11.1526 | 2.3716 | 16234.5954 | 8424.5042 | 982.8354 | 7083.1607 | 3220.7323 | 31.3211 | 8865.1265 | 4917.4636 | 665.2061 | 286.3082 | 104152.7431 | 58737.5923 | 10311.9353 | 2270.1479 | 948.6331 | 18.797 | 99019.5128 | 54925.8769 | 7430.056 | 2863.0824 | 0.0089962 | 0.0039206 | 9.96e-05 | 0.02992 | 0.016967 | 0.002992 | 0.0044484 | 5000000 | scaled
308-485AE | 157977.2573 | 4383.756 | 152608.2129 | 985.2884 | 2.775% | 96.6% | 0.6237% | 70299.2718 | 145515.195 | 315.6864 | 63045.6083 | 6937.9771 | 611.1594 | 130704.2407 | 14199.795 | 308 |  | 588 | 308-485AE | 157977.2573 | 87677.9856 | 12462.0623 | 4383.756 | 2036.681 | 32.8349 | 152608.2129 | 84656.0161 | 11443.939 | 985.2884 | 630.0857 | 314.3993 | 18.9263 | 429.9416 | 203.0437 | 3.2319 | 199.4027 | 110.6142 | 14.953 | 0.7414 | 15258.3335 | 8320.3564 | 1058.5386 | 2465.2975 | 1183.8501 | 16.409 | 12703.5317 | 7047.002 | 952.6253 | 89.5043 | 142088.8381 | 79043.2298 | 11384.5974 | 1488.517 | 649.7872 | 13.194 | 139705.2784 | 77498.3998 | 10476.3607 | 895.0427 | 0.003508 | 0.0015594 | 3.96e-05 | 0.02984 | 0.016925 | 0.002984 | 0.0013904 | 5000000 | scaled
308-486AE | 164677.8024 | 3924.9147 | 158415.7965 | 2337.0912 | 2.383% | 96.2% | 1.419% | 72868.4421 | 150449.385 | 310.2087 | 65660.0498 | 6898.1836 | 548.2114 | 136060.4661 | 13840.7075 | 308 |  | 589 | 308-486AE | 164677.8024 | 91809.3602 | 14228.4174 | 3924.9147 | 1584.5443 | 18.407 | 158415.7965 | 87887.7247 | 11872.9192 | 2337.0912 | 567.057 | 256.8483 | 18.8456 | 352.9443 | 137.2775 | 1.1716 | 212.3541 | 117.8122 | 15.9155 | 1.7586 | 15041.7975 | 8143.6139 | 1201.09 | 1698.9638 | 646.6051 | 4.6823 | 13130.5307 | 7284.7058 | 984.1047 | 212.303 | 149068.9478 | 83408.898 | 13008.4817 | 1873.0066 | 800.6617 | 12.5531 | 145072.9116 | 80485.2067 | 10872.899 | 2123.0296 | 0.0071828 | 0.0031438 | 7.94e-05 | 0.029791 | 0.016895 | 0.002979 | 0.0033052 | 5000000 | scaled
308-563AE | 95526.3419 | 18507.6595 | 76322.3117 | 696.3706 | 19.37% | 79.9% | 0.729% | 44079.0384 | 88504.5317 | 1463.1673 | 31199.3238 | 11416.5473 | 2599.701 | 64795.4694 | 21109.3613 | 308 |  | 590 | 308-563AE | 95526.3419 | 51447.3035 | 7021.8102 | 18507.6595 | 8393.6412 | 601.8577 | 76322.3117 | 42357.2917 | 5723.5819 | 696.3706 | 2695.2555 | 1232.0882 | 95.5545 | 2585.6414 | 1171.0214 | 86.8495 | 109.0901 | 60.5427 | 8.1809 | 0.524 | 22170.273 | 10753.7257 | 1060.9117 | 15629.1286 | 7095.3754 | 511.8617 | 6477.8857 | 3595.0915 | 485.7912 | 63.2588 | 70660.8134 | 39461.4896 | 5865.344 | 292.8896 | 127.2444 | 3.1464 | 69735.336 | 38701.6574 | 5229.6097 | 632.5878 | 0.0021958 | 0.001002 | 3.82e-05 | 0.029979 | 0.017011 | 0.002998 | 0.0009844 | 5000000 | scaled
309-15F | 10194.9475 | 5403.5256 | 0 | 4791.4219 | 53% | 0% | 47% | 3068.4064 | 5356.8488 | 63.7861 | 2673.479 | 331.1413 | 110.3794 | 4673.6503 | 572.8191 | 309 |  | 591 | 309-15F | 10194.9475 | 7126.5411 | 4838.0987 | 5403.5256 | 2335.1192 | 46.6768 | 0 | 0 | 0 | 4791.4219 | 114.0943 | 50.3082 | 3.715 | 110.4889 | 46.7028 | 0.10957 | 0 | 0 | 0 | 3.6054 | 1008.6357 | 677.4945 | 435.8166 | 573.3797 | 242.2384 | 0.56056 | 0 | 0 | 0 | 435.256 | 9072.2175 | 6398.7384 | 4398.5672 | 4719.657 | 2046.178 | 46.0067 | 0 | 0 | 0 | 4352.5605 | 0.017214 | 0.0074532 | 0.000188 | 0 | 0 | 0 | 0.0067802 | 5000000 | scaled
310-1192F | 284941.6726 | 5320.1357 | 272715.3833 | 6906.1536 | 1.867% | 95.71% | 2.424% | 125482.1044 | 260015.7926 | 139.8487 | 114395.2988 | 10946.9569 | 289.8872 | 236959.6038 | 22766.3017 | 310 |  | 592 | 310-1192F | 284941.6726 | 159459.5682 | 24925.8799 | 5320.1357 | 2305.6291 | 57.8521 | 272715.3833 | 150247.7855 | 17961.8743 | 6906.1536 | 315.2527 | 175.404 | 25.3655 | 7.3674 | 3.3343 | 0 | 302.6886 | 166.873 | 20.1688 | 5.1967 | 25014.0719 | 14067.115 | 2247.7703 | 37.619 | 17.0126 | 0 | 24349.0932 | 13422.7427 | 1620.4106 | 627.3597 | 259612.3479 | 145217.0491 | 22652.7442 | 5275.1493 | 2285.2822 | 57.8521 | 248063.6014 | 136658.1698 | 16321.2949 | 6273.5972 | 0.016381 | 0.0070938 | 0.000178 | 0.016349 | 0.009275 | 0.0016348 | 0.00978 | 5000000 | scaled
310-1194F | 286.7451 | 83.3551 | 0 | 203.39 | 29.07% | 0% | 70.93% | 46.0535 | 82.577 | 0.6712 | 41.7977 | 3.5846 | 1.5142 | 72.993 | 8.0698 | 310 |  | 593 | 310-1194F | 286.7451 | 240.6916 | 204.1681 | 83.3551 | 37.3016 | 0.77807 | 0 | 0 | 0 | 203.39 | 1.6673 | 0.99608 | 0.15304 | 1.5142 | 0.84304 | 0 | 0 | 0 | 0 | 0.15304 | 26.5459 | 22.9613 | 18.4761 | 8.0698 | 4.4852 | 0 | 0 | 0 | 0 | 18.4761 | 258.5319 | 216.7342 | 185.5389 | 73.771 | 31.9734 | 0.77807 | 0 | 0 | 0 | 184.7609 | 0.0004014 | 0.0001738 | 4.4e-06 | 0 | 0 | 0 | 0.0002906 | 5000000 | scaled
310-718F | 818.0206 | 741.9213 | 0 | 76.0993 | 90.7% | 0% | 9.303% | 421.1382 | 734.1214 | 0.15923 | 420.1277 | 0.85129 | 0.17342 | 733.0225 | 0.92545 | 310 |  | 594 | 310-718F | 818.0206 | 396.8825 | 83.8992 | 741.9213 | 320.7832 | 7.7999 | 0 | 0 | 0 | 76.0993 | 0.23068 | 0.071451 | 0.057262 | 0.17342 | 0.014189 | 0 | 0 | 0 | 0 | 0.057262 | 7.8384 | 6.9871 | 6.9129 | 0.92545 | 0.074162 | 0 | 0 | 0 | 0 | 6.9129 | 809.9516 | 389.824 | 76.9291 | 740.8225 | 320.6948 | 7.7999 | 0 | 0 | 0 | 69.1291 | 0.000152 | 6.58e-05 | 1.6e-06 | 0 | 0 | 0 | 0.000102 | 5000000 | scaled
310-719F | 124514.6895 | 2817.8482 | 119524.2441 | 2172.5971 | 2.263% | 95.99% | 1.745% | 55233.6459 | 114333.357 | 80.2085 | 50508.8418 | 4644.5956 | 158.169 | 104559.1663 | 9616.0217 | 310 |  | 595 | 310-719F | 124514.6895 | 69281.0436 | 10181.3324 | 2817.8482 | 1211.0057 | 28.1844 | 119524.2441 | 65897.4408 | 7980.5509 | 2172.5971 | 168.8946 | 88.6861 | 10.7256 | 31.1079 | 11.9865 | 0 | 136.1518 | 75.0648 | 9.0908 | 1.6348 | 10489.8906 | 5845.295 | 873.8689 | 160.4992 | 61.8302 | 0 | 10132.0311 | 5586.1045 | 676.5087 | 197.3602 | 113855.9043 | 63347.0625 | 9296.738 | 2626.241 | 1137.1889 | 28.1844 | 109256.0611 | 60236.2715 | 7294.9514 | 1973.6021 | 0.0059446 | 0.002574 | 6.54e-05 | 0.016588 | 0.0094106 | 0.0016588 | 0.0030992 | 5000000 | scaled
310-9R | 7880.5398 | 6733.5913 | 0 | 1146.9486 | 85.45% | 0% | 14.55% | 3329.4439 | 6647.417 | 1.247 | 3321.6759 | 6.521 | 3.2756 | 6627.035 | 17.1064 | 310 |  | 596 | 310-9R | 7880.5398 | 4551.0959 | 1233.1228 | 6733.5913 | 3404.1473 | 86.1742 | 0 | 0 | 0 | 1146.9486 | 4.1386 | 2.8916 | 0.86304 | 3.2756 | 2.0286 | 0 | 0 | 0 | 0 | 0.86304 | 121.296 | 114.775 | 104.1896 | 17.1064 | 10.5854 | 0 | 0 | 0 | 0 | 104.1896 | 7755.1052 | 4433.4293 | 1128.0702 | 6713.2093 | 3391.5333 | 86.1742 | 0 | 0 | 0 | 1041.896 | 0.0028414 | 0.0013366 | 3.4e-05 | 0 | 0 | 0 | 0.001637 | 5000000 | scaled
311-1163F | 46195.0999 | 39123.9482 | 6818.2707 | 252.881 | 84.69% | 14.76% | 0.5474% | 19358.9267 | 45054.1888 | 973.6069 | 11286.2328 | 7099.0869 | 2492.4818 | 23222.485 | 19339.222 | 311 |  | 597 | 311-1163F | 46195.0999 | 26836.1732 | 1140.9111 | 39123.9482 | 22820.6402 | 433.1402 | 6818.2707 | 3762.652 | 454.8899 | 252.881 | 2520.4157 | 1546.8087 | 27.9338 | 2507.292 | 1539.4812 | 26.8807 | 12.9333 | 7.1372 | 0.86286 | 0.19028 | 19605.3782 | 12506.2912 | 266.1562 | 18771.575 | 12035.8634 | 189.0886 | 810.8313 | 447.456 | 54.0957 | 22.9719 | 24069.306 | 12783.0732 | 846.8211 | 17845.0812 | 9245.2956 | 217.1709 | 5994.5061 | 3308.0588 | 399.9314 | 229.7188 | 0.0015204 | 0.0007742 | 2e-05 | 0.016742 | 0.0095068 | 0.0016742 | 0.00036 | 5000000 | scaled
311-1199 | 15605.6232 | 7706.5535 | 7504.4728 | 394.5969 | 49.38% | 48.09% | 2.529% | 8163.5726 | 14678.5752 | 392.1556 | 4197.1281 | 3574.2888 | 629.2047 | 8325.5061 | 5723.8644 | 311 |  | 598 | 311-1199 | 15605.6232 | 7442.0506 | 927.048 | 7706.5535 | 2909.4274 | 31.8171 | 7504.4728 | 4138.0263 | 500.634 | 394.5969 | 632.7434 | 240.5877 | 3.5386 | 620.0579 | 233.4596 | 2.4153 | 12.3886 | 6.8312 | 0.82646 | 0.29692 | 5817.2176 | 2242.9287 | 93.3532 | 5138.2745 | 1852.4741 | 14.6058 | 643.0976 | 354.6091 | 42.902 | 35.8455 | 9155.6623 | 4958.5342 | 830.1562 | 1948.2211 | 823.4936 | 14.796 | 6848.9867 | 3776.586 | 456.9056 | 358.4545 | 0.0010032 | 0.0004344 | 1.12e-05 | 0.016787 | 0.0095248 | 0.0016786 | 0.0005458 | 5000000 | scaled
311-14R | 278651.9529 | 45363.8342 | 232869.7624 | 418.3563 | 16.28% | 83.57% | 0.1501% | 128627.0103 | 262163.4452 | 1719.136 | 105968.9753 | 20938.899 | 3214.8865 | 218048.1458 | 40900.4128 | 311 |  | 599 | 311-14R | 278651.9529 | 150024.9426 | 16488.5077 | 45363.8342 | 21029.9291 | 517.9014 | 232869.7624 | 128576.6571 | 15552.25 | 418.3563 | 3268.616 | 1549.48 | 53.7295 | 2973.8349 | 1386.5787 | 33.7487 | 294.4663 | 162.5865 | 19.666 | 0.3148 | 42500.4546 | 21561.5556 | 1600.0417 | 22961.0979 | 10756.0793 | 259.6365 | 19501.3529 | 10767.4725 | 1302.4015 | 38.0038 | 232882.8823 | 126913.907 | 14834.7365 | 19428.9014 | 8887.2712 | 224.5161 | 213073.9432 | 117646.5981 | 14230.1826 | 380.0377 | 0.0017894 | 0.0008134 | 2.08e-05 | 0.016542 | 0.0093966 | 0.0016542 | 0.0006042 | 5000000 | scaled
311-43 | 159858.0503 | 3739.0789 | 153156.7623 | 2962.2091 | 2.339% | 95.81% | 1.853% | 70739.2938 | 146647.0157 | 163.6215 | 63391.9429 | 7183.7294 | 308.6811 | 131551.9614 | 14786.3732 | 311 |  | 600 | 311-43 | 159858.0503 | 89118.7565 | 13211.0346 | 3739.0789 | 1601.5189 | 22.7306 | 153156.7623 | 84555.0285 | 10226.0949 | 2962.2091 | 323.6006 | 159.9791 | 14.9195 | 132.3317 | 53.3846 | 0.068578 | 189.04 | 104.3655 | 12.622 | 2.229 | 16061.6158 | 8877.8864 | 1275.2426 | 728.5507 | 292.2535 | 0.34974 | 15063.976 | 8316.5438 | 1005.8038 | 269.0891 | 143472.8339 | 80080.891 | 11920.8725 | 2878.1965 | 1255.8808 | 22.3123 | 137903.7463 | 76134.1192 | 9207.6692 | 2690.891 | 0.0070966 | 0.0031524 | 8.04e-05 | 0.016713 | 0.0094928 | 0.0016712 | 0.004128 | 5000000 | scaled
312-14F | 202123.6211 | 305.923 | 201292.1779 | 525.5203 | 0.1514% | 99.59% | 0.26% | 90440.0663 | 188154.941 | 126.9101 | 81501.2547 | 8811.9014 | 253.8489 | 169607.8127 | 18293.2794 | 312 |  | 601 | 312-14F | 202123.6211 | 111683.5548 | 13968.6801 | 305.923 | 73.5942 | 1.9289 | 201292.1779 | 111084.4404 | 13441.231 | 525.5203 | 271.7133 | 144.8031 | 17.8644 | 9.7075 | 0.03626 | 0 | 261.6104 | 144.3714 | 17.469 | 0.39544 | 19646.1668 | 10834.2654 | 1352.8874 | 52.8794 | 0.18442 | 0 | 19545.5488 | 10786.3424 | 1305.1488 | 47.7386 | 182205.741 | 100704.4863 | 12597.9283 | 243.3361 | 73.3735 | 1.9289 | 181485.0188 | 100153.7266 | 12118.6132 | 477.3862 | 0.001414 | 0.000612 | 1.56e-05 | 0.016702 | 0.009483 | 0.0016702 | 0.000752 | 5000000 | scaled
312-40F | 9416.2866 | 7.1797 | 9331.4831 | 77.6238 | 0.07625% | 99.1% | 0.8244% | 4183.1807 | 8715.6246 | 7.5831 | 3790.6016 | 384.996 | 15.7421 | 7897.9407 | 801.9418 | 312 |  | 602 | 312-40F | 9416.2866 | 5233.1059 | 700.662 | 7.1797 | 3.1932 | 0.04738 | 9331.4831 | 5152.2888 | 622.9907 | 77.6238 | 16.892 | 9.3089 | 1.1499 | 0.48517 | 0.22386 | 0 | 16.3484 | 9.0266 | 1.0915 | 0.058409 | 866.1859 | 481.1899 | 64.2441 | 2.4725 | 1.1408 | 0 | 856.662 | 472.9977 | 57.1927 | 7.0514 | 8533.2087 | 4742.6071 | 635.268 | 4.222 | 1.8286 | 0.04738 | 8458.4726 | 4670.2645 | 564.7066 | 70.514 | 0.0001432 | 6.2e-05 | 1.6e-06 | 0.016931 | 0.0096186 | 0.001693 | 9.84e-05 | 5000000 | scaled
312-41F | 540.9913 | 0 | 540.9913 | 0 | 0% | 100% | 0% | 86.4665 | 179.9057 | 1.1217 | 67.7108 | 17.634 | 2.334 | 140.8818 | 36.6899 | 312 |  | 603 | 312-41F | 540.9913 | 454.5247 | 361.0856 | 0 | 0 | 0 | 540.9913 | 454.5247 | 361.0856 | 0 | 7.0184 | 5.8966 | 4.6844 | 0 | 0 | 0 | 7.0184 | 5.8966 | 4.6844 | 0 | 110.3297 | 92.6957 | 73.6397 | 0 | 0 | 0 | 110.3297 | 92.6957 | 73.6397 | 0 | 423.6432 | 355.9324 | 282.7614 | 0 | 0 | 0 | 423.6432 | 355.9324 | 282.7614 | 0 | 0 | 0 | 0 | 0.016959 | 0.016959 | 0.016959 | 0 | 5000000 | scaled
313-548AE | 14293.5479 | 1320.3495 | 12870.4475 | 102.7509 | 9.237% | 90.04% | 0.7189% | 6064.3307 | 13331.8393 | 40.1381 | 4576.0947 | 1448.0979 | 148.2293 | 9527.8484 | 3655.7615 | 313 |  | 604 | 313-548AE | 14293.5479 | 8229.2171 | 961.7086 | 1320.3495 | 1023.5843 | 0.10031 | 12870.4475 | 7102.8819 | 858.8574 | 102.7509 | 149.5591 | 109.421 | 1.3298 | 130.713 | 98.9857 | 0 | 18.7688 | 10.358 | 1.2525 | 0.077317 | 3842.2941 | 2394.1962 | 186.5326 | 1177.5419 | 919.4026 | 0 | 2655.4182 | 1465.4597 | 177.1986 | 9.334 | 10301.6946 | 5725.5999 | 773.8462 | 12.0945 | 5.1961 | 0.10031 | 10196.2605 | 5627.0642 | 680.4063 | 93.3396 | 0.0002144 | 9.3e-05 | 2.2e-06 | 0.017008 | 0.0096574 | 0.0017008 | 0.000145 | 5000000 | scaled
313-549AE | 1261.9352 | 0 | 1261.9352 | 0 | 0% | 100% | 0% | 201.3067 | 419.5721 | 1.5565 | 158.4778 | 41.2725 | 3.2442 | 330.3061 | 86.0218 | 313 |  | 605 | 313-549AE | 1261.9352 | 1060.6285 | 842.3631 | 0 | 0 | 0 | 1261.9352 | 1060.6285 | 842.3631 | 0 | 9.7574 | 8.2009 | 6.5132 | 0 | 0 | 0 | 9.7574 | 8.2009 | 6.5132 | 0 | 258.7254 | 217.453 | 172.7036 | 0 | 0 | 0 | 258.7254 | 217.453 | 172.7036 | 0 | 993.4524 | 834.9747 | 663.1463 | 0 | 0 | 0 | 993.4524 | 834.9747 | 663.1463 | 0 | 0 | 0 | 0 | 0.017045 | 0.017045 | 0.017045 | 0 | 5000000 | scaled
313-550AE | 63029.281 | 22186.3268 | 39827.3336 | 1015.6206 | 35.2% | 63.19% | 1.611% | 31292.8862 | 59173.2165 | 1108.8909 | 14824.8963 | 15359.099 | 1840.1531 | 30818.7559 | 26514.3075 | 313 |  | 606 | 313-550AE | 63029.281 | 31736.3948 | 3856.0645 | 22186.3268 | 8741.3549 | 183.0711 | 39827.3336 | 21979.4193 | 2657.3728 | 1015.6206 | 1861.3864 | 752.4955 | 21.2333 | 1817.9202 | 728.1654 | 17.6199 | 42.702 | 23.5658 | 2.8492 | 0.76422 | 27240.7062 | 11881.6073 | 726.3988 | 20079.1261 | 7888.0179 | 162.4575 | 7069.3205 | 3901.3297 | 471.6816 | 92.2597 | 33927.1884 | 19102.292 | 3108.4325 | 289.2806 | 125.1716 | 2.9937 | 32715.3111 | 18054.5238 | 2182.842 | 922.5967 | 0.002596 | 0.001124 | 2.88e-05 | 0.017009 | 0.0096586 | 0.0017008 | 0.0014292 | 5000000 | scaled
313-920F | 25989.7712 | 644.0418 | 24674.485 | 671.2444 | 2.478% | 94.94% | 2.583% | 11415.9239 | 23670.2963 | 48.6626 | 9153.0642 | 2214.1971 | 88.4937 | 19058.1904 | 4523.6122 | 313 |  | 607 | 313-920F | 25989.7712 | 14573.8472 | 2319.4749 | 644.0418 | 274.9395 | 1.2034 | 24674.485 | 13627.6633 | 1647.0271 | 671.2444 | 91.0694 | 42.4068 | 2.5757 | 60.264 | 25.1669 | 0.048084 | 30.3004 | 16.7348 | 2.0226 | 0.50509 | 4876.4903 | 2662.2931 | 352.878 | 446.1346 | 188.1183 | 0.24475 | 4369.3794 | 2413.1986 | 291.657 | 60.9763 | 21022.2115 | 11869.1473 | 1964.0211 | 137.6433 | 61.6544 | 0.91058 | 20274.8052 | 11197.7299 | 1353.3475 | 609.763 | 0.001383 | 0.0005988 | 1.54e-05 | 0.017028 | 0.009676 | 0.0017028 | 0.0009414 | 5000000 | scaled
313-921F | 17816.1718 | 3462.2824 | 14182.9051 | 170.9843 | 19.43% | 79.61% | 0.9597% | 8347.7732 | 16698.0735 | 212.5391 | 5028.7913 | 3106.4429 | 373.3085 | 10490.4651 | 5834.2999 | 313 |  | 608 | 313-921F | 17816.1718 | 9468.3986 | 1118.0983 | 3462.2824 | 1460.003 | 0.062556 | 14182.9051 | 7837.4113 | 947.0514 | 170.9843 | 374.806 | 162.267 | 1.4975 | 354.1776 | 150.8102 | 0 | 20.4997 | 11.3281 | 1.3689 | 0.12866 | 6045.2295 | 2938.7866 | 210.9296 | 3103.4562 | 1306.2263 | 0 | 2926.241 | 1617.028 | 195.3973 | 15.5323 | 11396.1363 | 6367.3451 | 905.6712 | 4.6486 | 2.9665 | 0.062556 | 11236.1644 | 6209.0553 | 750.2853 | 155.3233 | 0.0006832 | 0.000368 | 9.2e-06 | 0.017082 | 0.0097114 | 0.0017082 | 0.0002414 | 5000000 | scaled
313-922F | 7544.4249 | 0 | 7544.4249 | 0 | 0% | 100% | 0% | 1199.7819 | 2507.7655 | 1.3689 | 950.7965 | 247.6165 | 2.8612 | 1987.3401 | 517.5642 | 313 |  | 609 | 313-922F | 7544.4249 | 6344.643 | 5036.6594 | 0 | 0 | 0 | 7544.4249 | 6344.643 | 5036.6594 | 0 | 8.6078 | 7.2389 | 5.7466 | 0 | 0 | 0 | 8.6078 | 7.2389 | 5.7466 | 0 | 1557.0531 | 1309.4366 | 1039.4889 | 0 | 0 | 0 | 1557.0531 | 1309.4366 | 1039.4889 | 0 | 5978.7641 | 5027.9675 | 3991.4239 | 0 | 0 | 0 | 5978.7641 | 5027.9675 | 3991.4239 | 0 | 0 | 0 | 0 | 0.017097 | 0.017097 | 0.017097 | 0 | 5000000 | scaled
313-923F | 37779.6956 | 7496.0209 | 28515.1048 | 1768.57 | 19.84% | 75.48% | 4.681% | 15931.1575 | 33865.697 | 359.045 | 11352.8922 | 4219.2204 | 779.6526 | 23709.1381 | 9376.9062 | 313 |  | 610 | 313-923F | 37779.6956 | 21848.5381 | 3913.9986 | 7496.0209 | 4295.613 | 241.3005 | 28515.1048 | 15784.355 | 1904.1281 | 1768.57 | 809.7404 | 450.6953 | 30.0877 | 718.1701 | 399.4131 | 22.7311 | 90.2395 | 49.9515 | 6.0258 | 1.3308 | 10012.5383 | 5793.3179 | 635.6321 | 5856.9466 | 3421.2897 | 208.2078 | 3994.9336 | 2211.3701 | 266.7662 | 160.6581 | 26957.4169 | 15604.5248 | 3248.2788 | 920.9042 | 474.9103 | 10.3616 | 24429.9316 | 13523.0334 | 1631.3361 | 1606.5811 | 0.0051508 | 0.0024342 | 6.18e-05 | 0.017059 | 0.0097144 | 0.0017058 | 0.002505 | 5000000 | scaled
314-13F | 74540.7705 | 56747.5225 | 17488.1011 | 305.1468 | 76.13% | 23.46% | 0.4094% | 33850.8987 | 72581.5153 | 1926.8931 | 7169.0674 | 24754.9382 | 4093.9563 | 14958.0452 | 53529.5138 | 314 |  | 611 | 314-13F | 74540.7705 | 40689.8718 | 1959.2552 | 56747.5225 | 30717.7774 | 486.8941 | 17488.1011 | 9666.9475 | 1167.2143 | 305.1468 | 4132.9785 | 2206.0854 | 39.0222 | 4104.0816 | 2190.0093 | 36.8792 | 28.6672 | 15.8465 | 1.9133 | 0.22961 | 54106.9662 | 29352.0279 | 577.4523 | 52570.8944 | 28490.5321 | 449.0601 | 1508.352 | 833.776 | 100.6724 | 27.7197 | 16300.8259 | 9131.7585 | 1342.7807 | 72.5465 | 37.236 | 0.95476 | 15951.0819 | 8817.325 | 1064.6285 | 277.1975 | 0.0015898 | 0.0008138 | 2.1e-05 | 0.017105 | 0.0097282 | 0.0017104 | 0.0004346 | 5000000 | scaled
315-1192F | 14668.0984 | 14389.5416 | 0 | 278.5568 | 98.1% | 0% | 1.899% | 1372.8582 | 14389.338 | 861.6322 | 4.2867 | 506.9393 | 9077.8456 | 17.5925 | 5293.8999 | 315 |  | 612 | 315-1192F | 14668.0984 | 13295.2402 | 278.7604 | 14389.5416 | 13016.6834 | 0.20359 | 0 | 0 | 0 | 278.5568 | 9078.0552 | 8216.4229 | 0.20961 | 9077.8456 | 8216.2133 | 0 | 0 | 0 | 0 | 0.20961 | 5319.2042 | 4812.265 | 25.3043 | 5293.8999 | 4786.9607 | 0 | 0 | 0 | 0 | 25.3043 | 270.839 | 266.5524 | 253.2465 | 17.7961 | 13.5094 | 0.20359 | 0 | 0 | 0 | 253.0429 | 0.0011306 | 0.000859 | 2.2e-05 | 0 | 0 | 0 | 0.0003978 | 5000000 | scaled
315-485AE | 209855.9254 | 208810.8548 | 0 | 1045.0706 | 99.5% | 0% | 0.498% | 97441.3195 | 207543.0912 | 27247.7621 | 72.9868 | 70120.5706 | 57834.254 | 255.2769 | 149453.5603 | 315 |  | 613 | 315-485AE | 209855.9254 | 112414.6059 | 2312.8342 | 208810.8548 | 111369.5353 | 1267.7636 | 0 | 0 | 0 | 1045.0706 | 58198.28 | 30950.5179 | 364.026 | 58197.4936 | 30949.7315 | 363.2396 | 0 | 0 | 0 | 0.78638 | 150448.3492 | 80327.7786 | 994.7889 | 150353.4143 | 80232.8436 | 899.854 | 0 | 0 | 0 | 94.9349 | 1209.2962 | 1136.3095 | 954.0193 | 259.9469 | 186.9602 | 4.67 | 0 | 0 | 0 | 949.3493 | 0.0048876 | 0.0026414 | 6.76e-05 | 0 | 0 | 0 | 0.0014824 | 5000000 | scaled
320-1414 | 2934.8264 | 619.5534 | 0 | 2315.273 | 21.11% | 0% | 78.89% | 362.1178 | 613.4461 | 7.3431 | 317.2871 | 37.4876 | 9.8323 | 553.4213 | 50.1926 | 320 |  | 614 | 320-1414 | 2934.8264 | 2572.7086 | 2321.3802 | 619.5534 | 257.4356 | 6.1072 | 0 | 0 | 0 | 2315.273 | 11.5745 | 4.2314 | 1.7422 | 9.8323 | 2.4893 | 0 | 0 | 0 | 0 | 1.7422 | 260.5135 | 223.026 | 210.321 | 50.1926 | 12.705 | 0 | 0 | 0 | 0 | 210.321 | 2662.7383 | 2345.4512 | 2109.3171 | 559.5285 | 242.2413 | 6.1072 | 0 | 0 | 0 | 2103.2099 | 0.0066132 | 0.0028634 | 7.26e-05 | 0 | 0 | 0 | 0.0032618 | 5000000 | scaled
321-1332R | 9616.2978 | 6563.8121 | 0 | 3052.4857 | 68.26% | 0% | 31.74% | 3382.8392 | 6485.894 | 21.4983 | 3251.2477 | 110.0932 | 39.9688 | 6241.1507 | 204.7744 | 321 |  | 615 | 321-1332R | 9616.2978 | 6233.4586 | 3130.4039 | 6563.8121 | 3180.9729 | 77.9181 | 0 | 0 | 0 | 3052.4857 | 42.2976 | 20.7993 | 2.3288 | 40.0007 | 18.5024 | 0.031924 | 0 | 0 | 0 | 2.2969 | 482.2292 | 372.136 | 277.4548 | 204.9393 | 94.8461 | 0.16487 | 0 | 0 | 0 | 277.2899 | 9091.771 | 5840.5233 | 2850.6203 | 6318.8721 | 3067.6244 | 77.7213 | 0 | 0 | 0 | 2772.8989 | 0.0090582 | 0.0040644 | 0.0001034 | 0 | 0 | 0 | 0.0043338 | 5000000 | scaled
321-646 | 2127.4066 | 681.1536 | 0 | 1446.253 | 32.02% | 0% | 67.98% | 401.4835 | 673.2476 | 26.0345 | 239.6954 | 135.7536 | 40.7241 | 420.0754 | 212.4481 | 321 |  | 616 | 321-646 | 2127.4066 | 1725.9231 | 1454.159 | 681.1536 | 279.6701 | 7.906 | 0 | 0 | 0 | 1446.253 | 42.3484 | 16.3139 | 1.6243 | 41.2601 | 15.2256 | 0.53601 | 0 | 0 | 0 | 1.0883 | 346.6061 | 210.8524 | 134.1579 | 215.2274 | 79.4738 | 2.7793 | 0 | 0 | 0 | 131.3786 | 1738.4522 | 1498.7568 | 1318.3768 | 424.6661 | 184.9707 | 4.5907 | 0 | 0 | 0 | 1313.7861 | 0.0037864 | 0.0016396 | 4.22e-05 | 0 | 0 | 0 | 0.0020042 | 5000000 | scaled
321-740AE | 5604.3599 | 1388.3716 | 0 | 4215.9883 | 24.77% | 0% | 75.23% | 790.3343 | 1370.7748 | 6.1031 | 752.7722 | 31.459 | 9.3763 | 1313.0484 | 48.3501 | 321 |  | 617 | 321-740AE | 5604.3599 | 4814.0256 | 4233.5851 | 1388.3716 | 598.0373 | 17.5968 | 0 | 0 | 0 | 4215.9883 | 13.076 | 6.973 | 3.6997 | 9.9036 | 3.8006 | 0.52734 | 0 | 0 | 0 | 3.1724 | 434.0685 | 402.6095 | 385.7184 | 51.0853 | 19.6262 | 2.7352 | 0 | 0 | 0 | 382.9833 | 5157.2153 | 4404.4431 | 3844.1669 | 1327.3827 | 574.6105 | 14.3343 | 0 | 0 | 0 | 3829.8326 | 0.01041 | 0.0045372 | 0.0001138 | 0 | 0 | 0 | 0.005873 | 5000000 | scaled
321-741 | 1210.8213 | 206.9236 | 0 | 1003.8977 | 17.09% | 0% | 82.91% | 117.3458 | 204.6875 | 0 | 117.3458 | 0 | 0 | 204.6875 | 0 | 321 |  | 618 | 321-741 | 1210.8213 | 1093.4755 | 1006.1338 | 206.9236 | 89.5778 | 2.2361 | 0 | 0 | 0 | 1003.8977 | 0.7554 | 0.7554 | 0.7554 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7554 | 91.1948 | 91.1948 | 91.1948 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1948 | 1118.8711 | 1001.5253 | 914.1836 | 206.9236 | 89.5778 | 2.2361 | 0 | 0 | 0 | 911.9475 | 0.002825 | 0.001223 | 3.08e-05 | 0 | 0 | 0 | 0.0013932 | 5000000 | scaled
322-32R | 502.6597 | 393.1656 | 0 | 109.4941 | 78.22% | 0% | 21.78% | 221.7228 | 388.7459 | 0 | 221.7228 | 0 | 0.21046 | 387.4625 | 1.073 | 322 |  | 619 | 322-32R | 502.6597 | 280.9369 | 113.9138 | 393.1656 | 171.4428 | 4.4197 | 0 | 0 | 0 | 109.4941 | 0.29285 | 0.29285 | 0.082391 | 0.21046 | 0.21046 | 0 | 0 | 0 | 0 | 0.082391 | 11.0195 | 11.0195 | 9.9465 | 1.073 | 1.073 | 0 | 0 | 0 | 0 | 9.9465 | 491.3474 | 269.6245 | 103.8849 | 391.8821 | 170.1593 | 4.4197 | 0 | 0 | 0 | 99.4652 | 0.000157 | 6.82e-05 | 1.8e-06 | 0 | 0 | 0 | 0.0001502 | 5000000 | scaled
322-821F | 18510.6685 | 10475.5756 | 0 | 8035.0929 | 56.59% | 0% | 43.41% | 5221.1803 | 10336.2836 | 155.4731 | 4254.157 | 811.5501 | 344.0834 | 8123.0039 | 1869.1963 | 322 |  | 620 | 322-821F | 18510.6685 | 13289.4882 | 8174.3849 | 10475.5756 | 5254.3953 | 139.292 | 0 | 0 | 0 | 8035.0929 | 355.7833 | 200.3103 | 11.7 | 349.7372 | 194.2641 | 5.6538 | 0 | 0 | 0 | 6.0461 | 2631.1575 | 1819.6074 | 761.9612 | 1901.2442 | 1089.6941 | 32.0479 | 0 | 0 | 0 | 729.9133 | 15523.7276 | 11269.5706 | 7400.7238 | 8224.5942 | 3970.4371 | 101.5903 | 0 | 0 | 0 | 7299.1334 | 0.021791 | 0.0094634 | 0.0002406 | 0 | 0 | 0 | 0.011281 | 5000000 | scaled
322-822F | 869.6793 | 207.8409 | 0 | 661.8384 | 23.9% | 0% | 76.1% | 155.8133 | 206.8085 | 9.5684 | 91.7331 | 54.5118 | 11.3599 | 131.7444 | 63.7042 | 322 |  | 621 | 322-822F | 869.6793 | 713.866 | 662.8708 | 207.8409 | 52.0276 | 1.0324 | 0 | 0 | 0 | 661.8384 | 11.8579 | 2.2896 | 0.49801 | 11.3599 | 1.7915 | 0 | 0 | 0 | 0 | 0.49801 | 123.826 | 69.3142 | 60.1219 | 63.7042 | 9.1924 | 0 | 0 | 0 | 0 | 60.1219 | 733.9953 | 642.2623 | 602.2509 | 132.7768 | 41.0437 | 1.0324 | 0 | 0 | 0 | 601.2186 | 0.0019008 | 0.0008226 | 2.1e-05 | 0 | 0 | 0 | 0.0009298 | 5000000 | scaled
323-1134F | 1800.5999 | 1099.0741 | 0 | 701.5258 | 61.04% | 0% | 38.96% | 543.3921 | 1098.2919 | 69.1177 | 46.455 | 427.8194 | 138.886 | 81.4666 | 877.9394 | 323 |  | 622 | 323-1134F | 1800.5999 | 1257.2078 | 702.308 | 1099.0741 | 555.6819 | 0.78214 | 0 | 0 | 0 | 701.5258 | 139.4138 | 70.2961 | 0.52788 | 138.886 | 69.7683 | 0 | 0 | 0 | 0 | 0.52788 | 941.6665 | 513.847 | 63.7271 | 877.9394 | 450.12 | 0 | 0 | 0 | 0 | 63.7271 | 719.5196 | 673.0646 | 638.053 | 82.2487 | 35.7937 | 0.78214 | 0 | 0 | 0 | 637.2709 | 0.0027264 | 0.0011808 | 3e-05 | 0 | 0 | 0 | 0.0009944 | 5000000 | scaled
323-471 | 28359.9249 | 21392.9363 | 0 | 6966.9886 | 75.43% | 0% | 24.57% | 11422.9512 | 20957.7572 | 1762.3669 | 2833.8687 | 6826.7156 | 3241.0353 | 5207.5363 | 12509.1856 | 323 |  | 623 | 323-471 | 28359.9249 | 16936.9737 | 7402.1677 | 21392.9363 | 9969.9851 | 435.1791 | 0 | 0 | 0 | 6966.9886 | 3320.9262 | 1558.5593 | 79.8909 | 3315.6838 | 1553.3168 | 74.6484 | 0 | 0 | 0 | 5.2424 | 13445.5639 | 6618.8484 | 936.3783 | 12812.6779 | 5985.9623 | 303.4923 | 0 | 0 | 0 | 632.886 | 11593.4348 | 8759.5661 | 6385.8985 | 5264.5746 | 2430.7059 | 57.0383 | 0 | 0 | 0 | 6328.8602 | 0.020413 | 0.0088946 | 0.0002264 | 0 | 0 | 0 | 0.0099162 | 5000000 | scaled
323-472AE | 8330.9337 | 6700.3621 | 0 | 1630.5716 | 80.43% | 0% | 19.57% | 3932.1966 | 6609.8235 | 431.6619 | 189.1212 | 3311.4135 | 726.2383 | 330.7189 | 5552.8663 | 323 |  | 624 | 323-472AE | 8330.9337 | 4398.7371 | 1721.1102 | 6700.3621 | 2768.1655 | 90.5386 | 0 | 0 | 0 | 1630.5716 | 737.5261 | 305.8643 | 11.2878 | 736.2992 | 304.6373 | 10.0609 | 0 | 0 | 0 | 1.227 | 5777.8971 | 2466.4836 | 225.0309 | 5629.7749 | 2318.3613 | 76.9086 | 0 | 0 | 0 | 148.1222 | 1815.5104 | 1626.3892 | 1484.7915 | 334.288 | 145.1668 | 3.5691 | 0 | 0 | 0 | 1481.2224 | 0.0041966 | 0.001818 | 4.6e-05 | 0 | 0 | 0 | 0.0022756 | 5000000 | scaled
325-1220R | 37708.5774 | 22451.3592 | 0 | 15257.2182 | 59.54% | 0% | 40.46% | 12708.9826 | 22209.268 | 63.8905 | 12316.9504 | 328.1416 | 109.0988 | 21539.7742 | 560.395 | 325 |  | 625 | 325-1220R | 37708.5774 | 24999.5949 | 15499.3094 | 22451.3592 | 9742.3766 | 242.0912 | 0 | 0 | 0 | 15257.2182 | 121.6943 | 57.8037 | 12.5954 | 110.2137 | 46.3231 | 1.1149 | 0 | 0 | 0 | 11.4806 | 1952.1053 | 1623.9636 | 1391.7102 | 566.1291 | 237.9875 | 5.7341 | 0 | 0 | 0 | 1385.9762 | 35634.7779 | 23317.8275 | 14095.0037 | 21775.0164 | 9458.066 | 235.2422 | 0 | 0 | 0 | 13859.7615 | 0.038558 | 0.016696 | 0.0004226 | 0 | 0 | 0 | 0.021465 | 5000000 | scaled
325-1227F | 7449.1852 | 7236.3788 | 0 | 212.8064 | 97.14% | 0% | 2.857% | 3471.2621 | 7067.6273 | 318.4976 | 1.4003 | 3151.3643 | 643.8915 | 2.7135 | 6421.0224 | 325 |  | 626 | 325-1227F | 7449.1852 | 3977.9231 | 381.5579 | 7236.3788 | 3765.1167 | 168.7515 | 0 | 0 | 0 | 212.8064 | 659.2016 | 340.7041 | 15.3102 | 659.0415 | 340.5439 | 15.15 | 0 | 0 | 0 | 0.16013 | 6593.921 | 3442.5567 | 172.8986 | 6574.5895 | 3423.2252 | 153.5671 | 0 | 0 | 0 | 19.3315 | 196.0626 | 194.6623 | 193.3492 | 2.7478 | 1.3475 | 0.034365 | 0 | 0 | 0 | 193.3148 | 0.000609 | 0.0002982 | 7.6e-06 | 0 | 0 | 0 | 0.000299 | 5000000 | scaled
325-1229F | 10049.8517 | 9206.548 | 0 | 843.3037 | 91.61% | 0% | 8.391% | 5207.3282 | 9122.6612 | 138.9418 | 4597.182 | 471.2044 | 248.3234 | 8032.1749 | 842.163 | 325 |  | 627 | 325-1229F | 10049.8517 | 4842.5235 | 927.1904 | 9206.548 | 3999.2198 | 83.8868 | 0 | 0 | 0 | 843.3037 | 250.2185 | 111.2767 | 1.8952 | 249.584 | 110.6421 | 1.2606 | 0 | 0 | 0 | 0.63456 | 922.9959 | 451.7915 | 80.8329 | 846.3896 | 375.1852 | 4.2266 | 0 | 0 | 0 | 76.6063 | 8876.6373 | 4279.4553 | 844.4624 | 8110.5744 | 3513.3925 | 78.3995 | 0 | 0 | 0 | 766.0628 | 0.0026012 | 0.0011266 | 2.78e-05 | 0 | 0 | 0 | 0.0012204 | 5000000 | scaled
325-22R | 13831.2362 | 7759.0733 | 0 | 6072.1629 | 56.1% | 0% | 43.9% | 3994.0986 | 7709.3703 | 245.5549 | 2849.633 | 898.9107 | 499.5689 | 5369.3681 | 1840.4333 | 325 |  | 628 | 325-22R | 13831.2362 | 9837.1376 | 6121.8659 | 7759.0733 | 3764.9748 | 49.703 | 0 | 0 | 0 | 6072.1629 | 505.2693 | 259.7144 | 5.7004 | 500.7002 | 255.1453 | 1.1313 | 0 | 0 | 0 | 4.5691 | 2395.9328 | 1497.0222 | 555.4995 | 1844.3334 | 945.4227 | 3.9001 | 0 | 0 | 0 | 551.5994 | 10930.0341 | 8080.4011 | 5560.6659 | 5414.0397 | 2564.4068 | 44.6716 | 0 | 0 | 0 | 5515.9943 | 0.015611 | 0.0069526 | 0.000177 | 0 | 0 | 0 | 0.0085416 | 5000000 | scaled
325-25 | 8361.1532 | 7360.9654 | 0 | 1000.1878 | 88.04% | 0% | 11.96% | 4179.5007 | 7281.3995 | 2.6718 | 4163.2094 | 13.6195 | 2.8078 | 7264.2744 | 14.3173 | 325 |  | 629 | 325-25 | 8361.1532 | 4181.6524 | 1079.7537 | 7360.9654 | 3181.4647 | 79.5659 | 0 | 0 | 0 | 1000.1878 | 3.6688 | 0.99697 | 0.86099 | 2.9162 | 0.24436 | 0.10838 | 0 | 0 | 0 | 0.75261 | 105.7282 | 92.1087 | 91.4109 | 14.8705 | 1.251 | 0.55315 | 0 | 0 | 0 | 90.8577 | 8251.7562 | 4088.5468 | 987.4818 | 7343.1788 | 3179.9693 | 78.9043 | 0 | 0 | 0 | 908.5774 | 0.0023982 | 0.0010386 | 2.62e-05 | 0 | 0 | 0 | 0.0013672 | 5000000 | scaled
326-26 | 1950.0665 | 1768.4026 | 0 | 181.6639 | 90.68% | 0% | 9.316% | 618.915 | 1740.1001 | 1.1229 | 612.0329 | 5.7592 | 3.0383 | 1721.4921 | 15.5697 | 326 |  | 630 | 326-26 | 1950.0665 | 1331.1515 | 209.9664 | 1768.4026 | 1149.4876 | 28.3025 | 0 | 0 | 0 | 181.6639 | 3.175 | 2.0522 | 0.1367 | 3.0383 | 1.9155 | 0 | 0 | 0 | 0 | 0.1367 | 32.0721 | 26.3129 | 16.5025 | 15.5697 | 9.8104 | 0 | 0 | 0 | 0 | 16.5025 | 1914.8193 | 1302.7864 | 193.3272 | 1749.7946 | 1137.7617 | 28.3025 | 0 | 0 | 0 | 165.0247 | 0.0006686 | 0.0004104 | 1.02e-05 | 0 | 0 | 0 | 0.0002502 | 5000000 | scaled
326-35R | 586182.605 | 109665.2191 | 468246.1805 | 8271.2055 | 18.71% | 79.88% | 1.411% | 267824.6065 | 540798.9676 | 9122.7649 | 202823.0354 | 55878.8062 | 16757.8527 | 417923.6395 | 106117.4754 | 326 |  | 631 | 326-35R | 586182.605 | 318357.9985 | 45383.6374 | 109665.2191 | 50254.0405 | 791.0669 | 468246.1805 | 259832.7525 | 36321.3651 | 8271.2055 | 16911.166 | 7788.4011 | 153.3132 | 16207.2388 | 7395.0173 | 92.9693 | 697.7034 | 387.16 | 54.1201 | 6.2238 | 110447.4044 | 54568.5982 | 4329.929 | 68183.9386 | 30781.9085 | 358.5167 | 41512.1039 | 23035.3277 | 3220.0504 | 751.362 | 458824.0346 | 256000.9992 | 40900.3952 | 25274.0417 | 12077.1147 | 339.5809 | 426036.3732 | 236410.2649 | 33047.1946 | 7513.6197 | 0.028331 | 0.012592 | 0.0003214 | 0.034978 | 0.019794 | 0.0034978 | 0.011661 | 5000000 | scaled
329-13F | 183.911 | 0 | 183.911 | 0 | 0% | 100% | 0% | 29.3412 | 61.1073 | 0.38065 | 22.9767 | 5.9838 | 0.79276 | 47.8523 | 12.4622 | 329 |  | 632 | 329-13F | 183.911 | 154.5698 | 122.8038 | 0 | 0 | 0 | 183.911 | 154.5698 | 122.8038 | 0 | 2.3859 | 2.0053 | 1.5932 | 0 | 0 | 0 | 2.3859 | 2.0053 | 1.5932 | 0 | 37.5068 | 31.5229 | 25.0446 | 0 | 0 | 0 | 37.5068 | 31.5229 | 25.0446 | 0 | 144.0183 | 121.0416 | 96.166 | 0 | 0 | 0 | 144.0183 | 121.0416 | 96.166 | 0 | 0 | 0 | 0 | 0.017298 | 0.017298 | 0.017298 | 0 | 5000000 | scaled
329-215F | 64924.7945 | 1158.5882 | 62337.7743 | 1428.432 | 1.785% | 96.02% | 2.2% | 28461.0604 | 59240.1068 | 107.6655 | 22714.2274 | 5639.1675 | 213.4437 | 47322.6142 | 11704.0489 | 329 |  | 633 | 329-215F | 64924.7945 | 36463.7341 | 5684.6878 | 1158.5882 | 608.3422 | 90.2787 | 62337.7743 | 34426.9598 | 4165.977 | 1428.432 | 229.5588 | 121.8933 | 16.1151 | 125.421 | 63.9004 | 8.1526 | 103.063 | 56.918 | 6.8876 | 1.0748 | 12692.3622 | 7053.1946 | 988.3133 | 927.8353 | 497.9623 | 81.0126 | 11634.7671 | 6425.4726 | 777.541 | 129.7597 | 52002.8736 | 29288.6462 | 4680.2594 | 105.3319 | 46.4795 | 1.1135 | 50599.9443 | 27944.5692 | 3381.5485 | 1297.5974 | 0.0024882 | 0.0010772 | 2.74e-05 | 0.017217 | 0.0097832 | 0.0017216 | 0.0019978 | 5000000 | scaled
329-793F | 8622.2123 | 2355.2291 | 5722.2324 | 544.7508 | 27.32% | 66.37% | 6.318% | 3882.5972 | 7663.1404 | 109.4382 | 2694.8826 | 1078.2764 | 196.3654 | 5402.9034 | 2063.8716 | 329 |  | 634 | 329-793F | 8622.2123 | 4739.6151 | 959.0719 | 2355.2291 | 1036.4925 | 32.0865 | 5722.2324 | 3158.3717 | 382.2346 | 544.7508 | 201.3504 | 91.9122 | 4.985 | 180.8031 | 80.3875 | 3.2299 | 20.1374 | 11.1148 | 1.3451 | 0.40991 | 2205.21 | 1126.9336 | 141.3384 | 1056.815 | 470.9078 | 18.4477 | 1098.9095 | 606.5403 | 73.4051 | 49.4855 | 6215.6519 | 3520.7693 | 812.7485 | 1117.611 | 485.1973 | 10.4088 | 4603.1855 | 2540.7166 | 307.4843 | 494.8554 | 0.0011988 | 0.0005194 | 1.3e-05 | 0.017278 | 0.0098126 | 0.0017278 | 0.000769 | 5000000 | scaled
330-44R | 135.2482 | 20.8035 | 0 | 114.4446 | 15.38% | 0% | 84.62% | 12.0441 | 20.8035 | 0 | 12.0441 | 0 | 0 | 20.8035 | 0 | 330 |  | 635 | 330-44R | 135.2482 | 123.204 | 114.4446 | 20.8035 | 8.7594 | 0 | 0 | 0 | 0 | 114.4446 | 0.086116 | 0.086116 | 0.086116 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086116 | 10.3962 | 10.3962 | 10.3962 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3962 | 124.7658 | 112.7217 | 103.9623 | 20.8035 | 8.7594 | 0 | 0 | 0 | 0 | 103.9623 | 9.2e-06 | 4e-06 | 0 | 0 | 0 | 0 | 0.0001546 | 5000000 | scaled
330-810R | 235355.6121 | 11155.0598 | 221620.2056 | 2580.3467 | 4.74% | 94.16% | 1.096% | 104844.1358 | 217807.0196 | 107.6946 | 94700.7507 | 10035.6905 | 224.6459 | 196639.5656 | 20942.8082 | 330 |  | 636 | 330-810R | 235355.6121 | 130511.4764 | 17548.5925 | 11155.0598 | 5403.9727 | 144.4068 | 221620.2056 | 122527.157 | 14823.839 | 2580.3467 | 242.4422 | 134.7476 | 17.7963 | 3.4687 | 1.7582 | 0 | 237.0319 | 131.0478 | 15.8547 | 1.9416 | 22677.1662 | 12641.4757 | 1734.358 | 18.014 | 9.1034 | 0 | 22424.7517 | 12397.9719 | 1499.9576 | 234.4005 | 212436.0037 | 117735.253 | 15796.4381 | 11133.5771 | 5393.1111 | 144.4068 | 198958.4221 | 109998.1373 | 13308.0267 | 2344.0046 | 0.0053776 | 0.0024814 | 0.0001738 | 0.017057 | 0.0097014 | 0.0017058 | 0.0036222 | 5000000 | scaled
330-8R | 217250.5641 | 25140.2889 | 184805.9785 | 7304.2967 | 11.57% | 85.07% | 3.362% | 93984.9054 | 197239.1382 | 108.0196 | 86212.8952 | 7663.9906 | 222.2446 | 181067.1985 | 15949.6952 | 330 |  | 637 | 330-8R | 217250.5641 | 123265.6587 | 20011.4258 | 25140.2889 | 13946.2315 | 353.4474 | 184805.9785 | 102015.1305 | 12353.6818 | 7304.2967 | 242.1052 | 134.0856 | 19.8606 | 25.6566 | 12.1411 | 0.26288 | 210.9524 | 116.4483 | 14.1015 | 5.4962 | 17747.7621 | 10083.7715 | 1798.067 | 132.3663 | 62.6082 | 1.3621 | 16951.8685 | 9357.636 | 1133.1776 | 663.5273 | 199260.6967 | 113047.8015 | 18193.4982 | 24982.266 | 13871.4821 | 351.8224 | 167643.1576 | 92541.0463 | 11206.4027 | 6635.2732 | 0.017574 | 0.0080094 | 0.0003152 | 0.017108 | 0.0097164 | 0.0017108 | 0.010258 | 5000000 | scaled
331-246R | 26193.6923 | 0 | 26193.6923 | 0 | 0% | 100% | 0% | 4168.7954 | 8701.929 | 6.1362 | 3302.5692 | 860.0901 | 12.8087 | 6893.7713 | 1795.349 | 331 |  | 638 | 331-246R | 26193.6923 | 22024.8969 | 17491.7633 | 0 | 0 | 0 | 26193.6923 | 22024.8969 | 17491.7633 | 0 | 38.5554 | 32.4192 | 25.7468 | 0 | 0 | 0 | 38.5554 | 32.4192 | 25.7468 | 0 | 5404.1832 | 4544.0932 | 3608.8343 | 0 | 0 | 0 | 5404.1832 | 4544.0932 | 3608.8343 | 0 | 20750.9536 | 17448.3845 | 13857.1823 | 0 | 0 | 0 | 20750.9536 | 17448.3845 | 13857.1823 | 0 | 0 | 0 | 0 | 0.017309 | 0.017309 | 0.017309 | 0 | 5000000 | scaled
331-40AE | 217394.1123 | 0 | 217394.1123 | 0 | 0% | 100% | 0% | 34724.9145 | 72210.2843 | 39.6978 | 31805.7385 | 2879.4783 | 82.5513 | 66139.8724 | 5987.8606 | 331 |  | 639 | 331-40AE | 217394.1123 | 182669.1977 | 145183.828 | 0 | 0 | 0 | 217394.1123 | 182669.1977 | 145183.828 | 0 | 248.5264 | 208.8286 | 165.9751 | 0 | 0 | 0 | 248.5264 | 208.8286 | 165.9751 | 0 | 18026.8732 | 15147.3949 | 12039.0126 | 0 | 0 | 0 | 18026.8732 | 15147.3949 | 12039.0126 | 0 | 199118.7127 | 167312.9742 | 132978.8403 | 0 | 0 | 0 | 199118.7127 | 167312.9742 | 132978.8403 | 0 | 0 | 0 | 0 | 0.017096 | 0.017096 | 0.017096 | 0 | 5000000 | scaled
331-42AE | 143891.3323 | 0 | 143891.3323 | 0 | 0% | 100% | 0% | 22911.5411 | 47796.7042 | 25.7703 | 21014.0514 | 1871.7195 | 53.7604 | 43838.2732 | 3904.6706 | 331 |  | 640 | 331-42AE | 143891.3323 | 120979.7912 | 96094.6281 | 0 | 0 | 0 | 143891.3323 | 120979.7912 | 96094.6281 | 0 | 161.845 | 136.0748 | 108.0846 | 0 | 0 | 0 | 161.845 | 136.0748 | 108.0846 | 0 | 11754.9582 | 9883.2387 | 7850.2875 | 0 | 0 | 0 | 11754.9582 | 9883.2387 | 7850.2875 | 0 | 131974.5291 | 110960.4778 | 88136.256 | 0 | 0 | 0 | 131974.5291 | 110960.4778 | 88136.256 | 0 | 0 | 0 | 0 | 0.017193 | 0.017193 | 0.017193 | 0 | 5000000 | scaled
334-21 | 378214.4953 | 336942.3665 | 35993.0586 | 5279.0701 | 89.09% | 9.517% | 1.396% | 193187.033 | 365128.8476 | 16942.9756 | 13328.4351 | 162915.6222 | 31577.7458 | 27641.5695 | 305909.5323 | 334 |  | 641 | 334-21 | 378214.4953 | 185027.4623 | 13085.6477 | 336942.3665 | 159540.9173 | 4640.8928 | 35993.0586 | 20207.4749 | 3165.6847 | 5279.0701 | 32033.3381 | 15090.3625 | 455.5923 | 31779.8957 | 14946.3309 | 429.6784 | 249.47 | 140.0592 | 21.9415 | 3.9723 | 311127.5568 | 148211.9346 | 5218.0245 | 304573.5192 | 144322.0013 | 4204.2033 | 6074.4833 | 3410.3789 | 534.2669 | 479.5543 | 35053.6004 | 21725.1652 | 7412.0309 | 588.9517 | 272.585 | 7.0111 | 29669.1053 | 16657.0368 | 2609.4763 | 4795.5435 | 0.018621 | 0.008313 | 0.000212 | 0.088667 | 0.0503 | 0.0088666 | 0.007451 | 5000000 | scaled
334-44F | 717.1972 | 0 | 717.1972 | 0 | 0% | 100% | 0% | 41.5834 | 86.2638 | 0.53947 | 32.5634 | 8.4805 | 1.1191 | 67.552 | 17.5926 | 334 |  | 642 | 334-44F | 717.1972 | 675.6139 | 630.9335 | 0 | 0 | 0 | 717.1972 | 675.6139 | 630.9335 | 0 | 9.3044 | 8.7649 | 8.1852 | 0 | 0 | 0 | 9.3044 | 8.7649 | 8.1852 | 0 | 146.2651 | 137.7846 | 128.6725 | 0 | 0 | 0 | 146.2651 | 137.7846 | 128.6725 | 0 | 561.6278 | 529.0644 | 494.0758 | 0 | 0 | 0 | 561.6278 | 529.0644 | 494.0758 | 0 | 0 | 0 | 0 | 0.088978 | 0.088978 | 0.088978 | 0 | 5000000 | scaled
334-45F | 1673.6743 | 1310.9059 | 0 | 362.7684 | 78.33% | 0% | 21.67% | 783.0973 | 1297.5622 | 67.7657 | 314.7197 | 400.612 | 111.7543 | 533.5117 | 652.2962 | 334 |  | 643 | 334-45F | 1673.6743 | 890.577 | 376.1121 | 1310.9059 | 527.8086 | 13.3437 | 0 | 0 | 0 | 362.7684 | 113.347 | 45.5813 | 1.5927 | 113.074 | 45.3083 | 1.3197 | 0 | 0 | 0 | 0.27297 | 692.4008 | 291.7888 | 40.1046 | 659.4467 | 258.8347 | 7.1505 | 0 | 0 | 0 | 32.9541 | 867.9265 | 553.2069 | 334.4148 | 538.3852 | 223.6655 | 4.8735 | 0 | 0 | 0 | 329.5413 | 0.0009726 | 0.000421 | 1.06e-05 | 0 | 0 | 0 | 0.0005044 | 5000000 | scaled
334-46F | 529890.7405 | 0 | 529890.7405 | 0 | 0% | 100% | 0% | 31038.7379 | 64394.0466 | 40.9 | 28496.0729 | 2501.765 | 84.8526 | 59118.9452 | 5190.2489 | 334 |  | 644 | 334-46F | 529890.7405 | 498852.0026 | 465496.6939 | 0 | 0 | 0 | 529890.7405 | 498852.0026 | 465496.6939 | 0 | 698.2413 | 657.3413 | 613.3888 | 0 | 0 | 0 | 698.2413 | 657.3413 | 613.3888 | 0 | 42709.9237 | 40208.1587 | 37519.6749 | 0 | 0 | 0 | 42709.9237 | 40208.1587 | 37519.6749 | 0 | 486482.5755 | 457986.5026 | 427363.6303 | 0 | 0 | 0 | 486482.5755 | 457986.5026 | 427363.6303 | 0 | 0 | 0 | 0 | 0.087161 | 0.087161 | 0.087161 | 0 | 5000000 | scaled
340-376F | 34927.5947 | 33468.2796 | 0 | 1459.3151 | 95.82% | 0% | 4.178% | 11304.4042 | 32951.9247 | 451.234 | 9166.8073 | 1686.3629 | 1375.4807 | 26355.4545 | 5220.9895 | 340 |  | 645 | 340-376F | 34927.5947 | 23623.1905 | 1975.67 | 33468.2796 | 22163.8753 | 516.3548 | 0 | 0 | 0 | 1459.3151 | 1402.6204 | 951.3865 | 27.1398 | 1401.5223 | 950.2884 | 26.0417 | 0 | 0 | 0 | 1.0981 | 5451.0415 | 3764.6786 | 230.052 | 5318.4763 | 3632.1134 | 97.4868 | 0 | 0 | 0 | 132.5652 | 28073.9328 | 18907.1254 | 1718.4782 | 26748.2809 | 17581.4736 | 392.8264 | 0 | 0 | 0 | 1325.6518 | 0.0053008 | 0.002914 | 7.48e-05 | 0 | 0 | 0 | 0.0020474 | 5000000 | scaled
340-378F | 393785.0691 | 388138.9599 | 0 | 5646.1093 | 98.57% | 0% | 1.434% | 215196.4802 | 382332.0584 | 25123.4509 | 1985.8738 | 188087.1555 | 44581.4625 | 3461.2783 | 334289.3177 | 340 |  | 646 | 340-378F | 393785.0691 | 178588.5889 | 11453.0107 | 388138.9599 | 172942.4796 | 5806.9015 | 0 | 0 | 0 | 5646.1093 | 45246.9109 | 20123.46 | 665.4484 | 45242.6624 | 20119.2115 | 661.1999 | 0 | 0 | 0 | 4.2485 | 339909.5957 | 151822.4402 | 5620.278 | 339396.6992 | 151309.5437 | 5107.3816 | 0 | 0 | 0 | 512.8964 | 8628.5625 | 6642.6887 | 5167.2843 | 3499.5982 | 1513.7244 | 38.32 | 0 | 0 | 0 | 5128.9643 | 0.01957 | 0.0084746 | 0.000216 | 0 | 0 | 0 | 0.0079598 | 5000000 | scaled
341-1155F | 374361.3305 | 371520.3518 | 0 | 2840.9786 | 99.24% | 0% | 0.7589% | 214201.7673 | 367814.0757 | 18090.73 | 164.0739 | 195946.9634 | 31039.9277 | 286.4856 | 336487.6625 | 341 |  | 647 | 341-1155F | 374361.3305 | 160159.5631 | 6547.2547 | 371520.3518 | 157318.5845 | 3706.2761 | 0 | 0 | 0 | 2840.9786 | 31356.0636 | 13265.3336 | 316.1359 | 31353.9259 | 13263.1959 | 313.9982 | 0 | 0 | 0 | 2.1377 | 340134.8579 | 144187.8945 | 3647.1954 | 339876.7814 | 143929.818 | 3389.119 | 0 | 0 | 0 | 258.0764 | 2870.409 | 2706.3351 | 2583.9234 | 289.6445 | 125.5707 | 3.159 | 0 | 0 | 0 | 2580.7644 | 0.011468 | 0.0049666 | 0.0001256 | 0 | 0 | 0 | 0.004009 | 5000000 | scaled
341-1157F | 34426.7281 | 33265.9478 | 0 | 1160.7803 | 96.63% | 0% | 3.372% | 19180.0843 | 33260.361 | 1965.3276 | 518.4486 | 16696.3082 | 3370.8055 | 935.6729 | 28953.8827 | 341 |  | 648 | 341-1157F | 34426.7281 | 15246.6438 | 1166.3671 | 33265.9478 | 14085.8635 | 5.5868 | 0 | 0 | 0 | 1160.7803 | 3371.679 | 1406.3514 | 0.87345 | 3370.8055 | 1405.478 | 0 | 0 | 0 | 0 | 0.87345 | 29059.3287 | 12363.0206 | 105.4461 | 28953.8827 | 12257.5745 | 0 | 0 | 0 | 0 | 105.4461 | 1995.7204 | 1477.2718 | 1060.0476 | 941.2596 | 422.811 | 5.5868 | 0 | 0 | 0 | 1054.4608 | 0.0050508 | 0.0021872 | 5.58e-05 | 0 | 0 | 0 | 0.0016258 | 5000000 | scaled
341-1179 | 16522.9432 | 15980.3411 | 0 | 542.6022 | 96.72% | 0% | 3.284% | 7057.6667 | 15617.2225 | 793.7654 | 15.9848 | 6247.9164 | 1758.2743 | 37.1109 | 13821.8373 | 341 |  | 649 | 341-1179 | 16522.9432 | 9465.2765 | 905.7208 | 15980.3411 | 8922.6744 | 363.1186 | 0 | 0 | 0 | 542.6022 | 1798.6737 | 1004.9083 | 40.3995 | 1798.2654 | 1004.5 | 39.9912 | 0 | 0 | 0 | 0.40829 | 14193.7059 | 7945.7895 | 371.8687 | 14144.4156 | 7896.4992 | 322.5783 | 0 | 0 | 0 | 49.2904 | 530.5635 | 514.5787 | 493.4526 | 37.66 | 21.6752 | 0.54908 | 0 | 0 | 0 | 492.9035 | 0.0020296 | 0.0010698 | 2.7e-05 | 0 | 0 | 0 | 0.0007544 | 5000000 | scaled
341-920 | 161885.9737 | 154106.2838 | 0 | 7779.69 | 95.19% | 0% | 4.806% | 87890.6523 | 153483.7263 | 10679.9566 | 5662.5964 | 71548.0993 | 18606.1127 | 9934.9547 | 124942.6589 | 341 |  | 650 | 341-920 | 161885.9737 | 73995.3214 | 8402.2474 | 154106.2838 | 66215.6314 | 622.5574 | 0 | 0 | 0 | 7779.69 | 18690.4666 | 8010.51 | 84.3538 | 18684.6126 | 8004.656 | 78.4999 | 0 | 0 | 0 | 5.854 | 126081.841 | 54533.7417 | 1139.1821 | 125375.1286 | 53827.0293 | 432.4697 | 0 | 0 | 0 | 706.7124 | 17113.6661 | 11451.0698 | 7178.7115 | 10046.5425 | 4383.9461 | 111.5878 | 0 | 0 | 0 | 7067.1236 | 0.024972 | 0.010813 | 0.000274 | 0 | 0 | 0 | 0.010955 | 5000000 | scaled
342-514F | 4638.2513 | 1320.2121 | 0 | 3318.0392 | 28.46% | 0% | 71.54% | 803.2629 | 1310.5327 | 37.2142 | 571.1974 | 194.8513 | 54.9513 | 969.0837 | 286.4977 | 342 |  | 651 | 342-514F | 4638.2513 | 3834.9884 | 3327.7186 | 1320.2121 | 516.9492 | 9.6794 | 0 | 0 | 0 | 3318.0392 | 57.4516 | 20.2374 | 2.5003 | 54.9549 | 17.7407 | 0.0035471 | 0 | 0 | 0 | 2.4967 | 587.9292 | 393.0778 | 301.4314 | 286.5162 | 91.6649 | 0.01847 | 0 | 0 | 0 | 301.413 | 3992.8706 | 3421.6732 | 3023.7869 | 978.7411 | 407.5437 | 9.6574 | 0 | 0 | 0 | 3014.1295 | 0.008589 | 0.0037178 | 9.48e-05 | 0 | 0 | 0 | 0.0046472 | 5000000 | scaled
342-521AE | 2959.0165 | 908.5739 | 0 | 2050.4427 | 30.71% | 0% | 69.29% | 449.4728 | 896.6212 | 11.0778 | 381.2992 | 57.0958 | 25.4824 | 739.9591 | 131.1797 | 342 |  | 652 | 342-521AE | 2959.0165 | 2509.5437 | 2062.3954 | 908.5739 | 459.101 | 11.9527 | 0 | 0 | 0 | 2050.4427 | 27.4616 | 16.3838 | 1.9792 | 25.9187 | 14.8409 | 0.4363 | 0 | 0 | 0 | 1.5429 | 319.6929 | 262.597 | 188.5131 | 133.4292 | 76.3334 | 2.2495 | 0 | 0 | 0 | 186.2636 | 2611.8621 | 2230.5629 | 1871.903 | 749.2259 | 367.9267 | 9.2669 | 0 | 0 | 0 | 1862.6362 | 0.0044254 | 0.0019794 | 5.04e-05 | 0 | 0 | 0 | 0.002949 | 5000000 | scaled
343-20 | 6021.6801 | 2909.013 | 0 | 3112.6671 | 48.31% | 0% | 51.69% | 1651.3191 | 2884.6164 | 63.5766 | 1261.8012 | 325.9412 | 108.0896 | 2222.3574 | 554.1694 | 343 |  | 653 | 343-20 | 6021.6801 | 4370.361 | 3137.0637 | 2909.013 | 1257.6939 | 24.3966 | 0 | 0 | 0 | 3112.6671 | 110.4318 | 46.8552 | 2.3422 | 108.0896 | 44.513 | 0 | 0 | 0 | 0 | 2.3422 | 836.9262 | 510.9849 | 282.7568 | 554.1694 | 228.2281 | 0 | 0 | 0 | 0 | 282.7568 | 5074.3221 | 3812.5208 | 2851.9647 | 2246.754 | 984.9528 | 24.3966 | 0 | 0 | 0 | 2827.5681 | 0.007971 | 0.003486 | 8.86e-05 | 0 | 0 | 0 | 0.0044146 | 5000000 | scaled
35-2 | 55557.1191 | 3369.0821 | 51755.7585 | 432.2785 | 6.064% | 93.16% | 0.7781% | 24925.1212 | 51633.6016 | 209.0339 | 20640.4096 | 4075.6777 | 382.9128 | 43155.2246 | 8095.4642 | 35 |  | 654 | 35-2 | 55557.1191 | 30631.9979 | 3923.5175 | 3369.0821 | 1510.6771 | 34.0548 | 51755.7585 | 28689.0423 | 3457.1841 | 432.2785 | 391.051 | 182.017 | 8.1381 | 329.3705 | 147.6816 | 3.7145 | 61.3553 | 34.0102 | 4.0984 | 0.32528 | 8548.3677 | 4472.69 | 452.9035 | 2724.0997 | 1226.7041 | 27.2083 | 5784.9995 | 3206.7175 | 386.4267 | 39.2685 | 46617.7004 | 25977.2908 | 3462.4758 | 315.6119 | 136.2914 | 3.132 | 45909.4037 | 25448.3146 | 3066.659 | 392.6848 | 0.001247 | 0.00054 | 1.38e-05 | 0.0056828 | 0.00324 | 0.0005682 | 0.0005898 | 5000000 | scaled
35-297AE | 10279.2877 | 2082.2009 | 7854.0294 | 343.0574 | 20.26% | 76.41% | 3.337% | 4416.0841 | 9398.0327 | 102.742 | 2868.5752 | 1444.7668 | 219.9494 | 5983.1802 | 3194.9031 | 35 |  | 655 | 35-297AE | 10279.2877 | 5863.2037 | 881.255 | 2082.2009 | 1160.9891 | 13.5122 | 7854.0294 | 4359.1571 | 524.6853 | 343.0574 | 222.5058 | 119.7638 | 2.5563 | 211.1129 | 113.3256 | 1.5543 | 11.1347 | 6.18 | 0.74385 | 0.25814 | 3344.5802 | 1899.8134 | 149.6771 | 1692.9151 | 969.2362 | 10.2566 | 1620.5015 | 899.4136 | 108.257 | 31.1636 | 6712.2018 | 3843.6265 | 729.0215 | 178.1729 | 78.4273 | 1.7013 | 6222.3931 | 3453.5635 | 415.6845 | 311.6357 | 0.0009236 | 0.0004 | 1.02e-05 | 0.0057032 | 0.0032558 | 0.0005704 | 0.000479 | 5000000 | scaled
350-2073 | 558.2059 | 0 | 558.2059 | 0 | 0% | 100% | 0% | 40.3243 | 83.8392 | 0.026483 | 31.9715 | 8.3264 | 0.055062 | 66.4727 | 17.3115 | 350 |  | 656 | 350-2073 | 558.2059 | 517.8816 | 474.3667 | 0 | 0 | 0 | 558.2059 | 517.8816 | 474.3667 | 0 | 0.3666 | 0.34012 | 0.31154 | 0 | 0 | 0 | 0.3666 | 0.34012 | 0.31154 | 0 | 115.2609 | 106.9346 | 97.9494 | 0 | 0 | 0 | 115.2609 | 106.9346 | 97.9494 | 0 | 442.5784 | 410.6069 | 376.1057 | 0 | 0 | 0 | 442.5784 | 410.6069 | 376.1057 | 0 | 0 | 0 | 0 | 0.067729 | 0.067729 | 0.067729 | 0 | 5000000 | scaled
350-2182R | 302428.0161 | 300219.1158 | 1999.5562 | 209.3441 | 99.27% | 0.6612% | 0.06922% | 84786.4348 | 292637.5225 | 4504.061 | 778.7121 | 79503.6617 | 15790.0571 | 1624.0249 | 275223.4406 | 350 |  | 657 | 350-2182R | 302428.0161 | 217641.5813 | 9790.4935 | 300219.1158 | 216311.672 | 9411.2494 | 1999.5562 | 1120.5653 | 169.9001 | 209.3441 | 16268.4889 | 11764.4279 | 478.4319 | 16266.867 | 11763.4497 | 478.1499 | 1.4644 | 0.82066 | 0.12443 | 0.15752 | 284194.9902 | 204691.3286 | 8971.5497 | 283945.7675 | 204543.3027 | 8932.9724 | 230.2058 | 129.0089 | 19.5603 | 19.017 | 1964.5369 | 1185.8248 | 340.512 | 6.4813 | 4.9196 | 0.12715 | 1767.886 | 990.7357 | 150.2153 | 190.1696 | 0.0010728 | 0.0008146 | 2.08e-05 | 0.067627 | 0.038401 | 0.0067626 | 0.0002912 | 5000000 | scaled
350-2188R | 3602011.8741 | 3439370.2131 | 147102.2415 | 15539.4195 | 95.48% | 4.084% | 0.4314% | 1677168.8664 | 3529530.4107 | 101836.7388 | 59860.7856 | 1515471.342 | 212575.3162 | 124078.7819 | 3192876.3126 | 350 |  | 658 | 350-2188R | 3602011.8741 | 1924843.0078 | 72481.4634 | 3439370.2131 | 1826882.5919 | 44452.3134 | 147102.2415 | 82420.9964 | 12489.7306 | 15539.4195 | 215327.922 | 113491.1832 | 2752.6057 | 215086.1579 | 113350.582 | 2721.3786 | 230.0712 | 128.9083 | 19.5342 | 11.6929 | 3237382.2348 | 1721910.8928 | 44505.9221 | 3219184.0883 | 1711093.8302 | 41669.0482 | 16786.535 | 9405.4511 | 1425.2624 | 1411.6115 | 149301.7174 | 89440.9318 | 25222.9355 | 5099.967 | 2438.1797 | 61.8866 | 130085.6354 | 72886.6371 | 11044.9339 | 14116.115 | 0.062025 | 0.031166 | 0.0007932 | 0.067198 | 0.038151 | 0.0067198 | 0.021987 | 5000000 | scaled
350-2192R | 13871622.229 | 13613237.5993 | 235593.9222 | 22790.7076 | 98.14% | 1.698% | 0.1643% | 6424048.5356 | 13702460.8986 | 415101.6861 | 100059.3613 | 5908887.4882 | 883228.7006 | 211747.1757 | 12607485.0223 | 350 |  | 659 | 350-2192R | 13871622.229 | 7447573.6934 | 169161.3304 | 13613237.5993 | 7292736.0376 | 126377.6032 | 235593.9222 | 132046.9483 | 19993.0196 | 22790.7076 | 891832.9502 | 476731.2641 | 8604.2496 | 891456.6553 | 476512.8189 | 8556.6225 | 359.1457 | 201.2959 | 30.4779 | 17.1493 | 12729190.5725 | 6820303.0843 | 121705.5502 | 12702116.3574 | 6804218.4452 | 117513.3413 | 25003.8916 | 14014.3156 | 2121.8854 | 2070.3235 | 250598.7063 | 150539.345 | 38851.5306 | 19664.5866 | 12004.7734 | 307.6394 | 210230.8849 | 117831.3368 | 17840.6564 | 20703.2348 | 0.090414 | 0.047047 | 0.0011992 | 0.066794 | 0.037937 | 0.0066794 | 0.032069 | 5000000 | scaled
350-2196R | 5570685.7117 | 5402874.7346 | 144206.9831 | 23603.994 | 96.99% | 2.589% | 0.4237% | 1629330.109 | 5426621.0756 | 105301.114 | 57816.8548 | 1466212.1403 | 356933.7594 | 123837.1015 | 4945850.2147 | 350 |  | 660 | 350-2196R | 5570685.7117 | 3941355.6027 | 144064.6361 | 5402874.7346 | 3836951.9056 | 108220.2169 | 144206.9831 | 80799.7031 | 12240.4251 | 23603.994 | 364070.8282 | 258769.7143 | 7137.0688 | 363769.1567 | 258592.8771 | 7095.209 | 283.9103 | 159.076 | 24.0986 | 17.7612 | 5050400.3092 | 3584188.1689 | 104550.0945 | 5031438.6685 | 3572621.0937 | 100978.4115 | 16817.4377 | 9422.8722 | 1427.48 | 2144.203 | 156214.5743 | 98397.7195 | 32377.4728 | 7666.9093 | 5737.9348 | 146.5964 | 127105.6351 | 71217.7549 | 10788.8465 | 21442.0298 | 0.098833 | 0.069959 | 0.0017786 | 0.066999 | 0.038038 | 0.0067 | 0.033314 | 5000000 | scaled
350-2201R | 13521745.4458 | 13424968.4125 | 87426.2339 | 9350.7993 | 99.28% | 0.6466% | 0.06915% | 4853748.0417 | 13300028.3697 | 346827.529 | 35152.1034 | 4471768.4093 | 953175.4051 | 74713.1188 | 12272139.8457 | 350 |  | 661 | 350-2201R | 13521745.4458 | 8667997.404 | 221717.0761 | 13424968.4125 | 8609657.8412 | 204944.5857 | 87426.2339 | 48988.7635 | 7421.691 | 9350.7993 | 968067.2939 | 621239.7649 | 14891.8888 | 967956.7601 | 621174.7344 | 14876.0666 | 103.4976 | 57.9943 | 8.786 | 7.0362 | 12463781.9201 | 7992013.5107 | 191642.0743 | 12453646.277 | 7985960.6058 | 190004.3266 | 9286.2101 | 5203.4719 | 788.3147 | 849.433 | 89896.2318 | 54744.1285 | 15183.113 | 3365.3754 | 2522.5009 | 64.1925 | 78036.5263 | 43727.2974 | 6624.5904 | 8494.3301 | 0.043861 | 0.028511 | 0.000726 | 0.067022 | 0.038055 | 0.0067022 | 0.013221 | 5000000 | scaled
350-41R | 11201388.8952 | 11075404.026 | 114551.2268 | 11433.6424 | 98.88% | 1.023% | 0.1021% | 5367093.2587 | 11055231.497 | 426835.0138 | 55874.122 | 4884384.1228 | 879636.5805 | 125457.2051 | 10050137.7114 | 350 |  | 662 | 350-41R | 11201388.8952 | 5834295.6366 | 146157.3982 | 11075404.026 | 5758692.0024 | 125001.2985 | 114551.2268 | 64169.9917 | 9722.4573 | 11433.6424 | 889778.083 | 462943.0692 | 10141.5025 | 889587.9025 | 462832.7488 | 10117.4878 | 181.5771 | 101.7169 | 15.4112 | 8.6034 | 10166427.7358 | 5282043.613 | 116290.0244 | 10154715.9413 | 5275026.0214 | 114345.5078 | 10673.1547 | 5978.9516 | 905.8767 | 1038.6399 | 145183.0764 | 89308.9544 | 19725.8713 | 31100.1822 | 20833.2322 | 538.3029 | 103696.4951 | 58089.3232 | 8801.1694 | 10386.3991 | 0.046008 | 0.023363 | 0.0005938 | 0.066869 | 0.037962 | 0.0066868 | 0.016086 | 5000000 | scaled
351-819R | 23517427.5477 | 23341044.154 | 168384.291 | 7999.1026 | 99.25% | 0.716% | 0.03401% | 11148524.1451 | 23213062.5812 | 1134171.8958 | 68925.3235 | 9945426.9257 | 2360762.8464 | 143947.4738 | 20708352.261 | 351 |  | 663 | 351-819R | 23517427.5477 | 12368903.4026 | 304364.9665 | 23341044.154 | 12266133.3799 | 281399.8433 | 168384.291 | 94770.9201 | 14966.0206 | 7999.1026 | 2389799.4827 | 1255627.5868 | 29036.6363 | 2389560.2739 | 1255490.3227 | 29009.8913 | 233.1897 | 131.245 | 20.7259 | 6.0191 | 20962855.1918 | 11017428.2661 | 254502.9308 | 20945609.0339 | 11007404.0237 | 252308.03 | 16519.5139 | 9297.5985 | 1468.2568 | 726.644 | 164772.8732 | 95847.5497 | 20825.3994 | 5874.8463 | 3239.0335 | 81.922 | 151631.5873 | 85342.0765 | 13477.0378 | 7266.4396 | 0.035805 | 0.018551 | 0.0004712 | 0.096696 | 0.054946 | 0.0096696 | 0.011257 | 5000000 | scaled
351-871R | 9144312.3619 | 9119653.5616 | 21681.8052 | 2976.995 | 99.73% | 0.2371% | 0.03256% | 4272679.0672 | 9032812.5709 | 211078.295 | 8591.1593 | 4053009.6129 | 447394.7355 | 17897.8379 | 8567519.9976 | 351 |  | 664 | 351-871R | 9144312.3619 | 4871633.2947 | 111499.791 | 9119653.5616 | 4856455.6779 | 106594.8191 | 21681.8052 | 12200.6218 | 1927.9768 | 2976.995 | 452748.8762 | 241670.5813 | 5354.1408 | 452712.9314 | 241649.3751 | 5348.9036 | 33.7047 | 18.9661 | 2.9971 | 2.2401 | 8669230.6644 | 4616221.0515 | 101710.6668 | 8666745.9718 | 4614704.6274 | 101243.3394 | 2214.2604 | 1245.9919 | 196.8952 | 270.4323 | 22332.8212 | 13741.662 | 4434.9833 | 194.6584 | 101.6755 | 2.5761 | 19433.8401 | 10935.6638 | 1728.0846 | 2704.3227 | 0.013276 | 0.0073064 | 0.0001854 | 0.097253 | 0.055253 | 0.0097254 | 0.004152 | 5000000 | scaled
352-27R | 18614182.3412 | 18495148.8145 | 110352.5408 | 8680.986 | 99.36% | 0.5928% | 0.04664% | 7975764.9922 | 18294212.3636 | 646955.4307 | 44786.1418 | 7284023.4197 | 1483729.3881 | 93659.6392 | 16716823.3364 | 352 |  | 665 | 352-27R | 18614182.3412 | 10638417.349 | 319969.9776 | 18495148.8145 | 10567908.8479 | 301925.4324 | 110352.5408 | 61827.5151 | 9363.5592 | 8680.986 | 1508474.057 | 861518.6262 | 24744.6689 | 1508291.127 | 861413.2632 | 24723.1692 | 176.3978 | 98.8309 | 14.9676 | 6.5322 | 16995664.9351 | 9711641.5154 | 278841.5988 | 16984399.36 | 9704982.9582 | 277164.0257 | 10476.9884 | 5869.9705 | 888.9863 | 788.5867 | 110043.3492 | 65257.2074 | 16383.71 | 2458.3275 | 1512.6265 | 38.2376 | 99699.1546 | 55858.7138 | 8459.6053 | 7885.8671 | 0.039108 | 0.022043 | 0.00056 | 0.066819 | 0.037935 | 0.0066818 | 0.012208 | 5000000 | scaled
353-1429R | 9221802.1839 | 8990135.5043 | 226573.8474 | 5092.8322 | 97.49% | 2.457% | 0.05523% | 4350562.0602 | 9107599.5274 | 403720.5864 | 93179.9398 | 3853661.534 | 844938.7091 | 194911.8629 | 8067748.9554 | 353 |  | 666 | 353-1429R | 9221802.1839 | 4871240.1237 | 114202.6565 | 8990135.5043 | 4738654.2781 | 88971.9095 | 226573.8474 | 127493.0135 | 20137.9148 | 5092.8322 | 853606.1717 | 449885.5854 | 8667.4627 | 853268.427 | 449693.8607 | 8633.9523 | 333.9125 | 187.8924 | 29.6782 | 3.8322 | 8150118.7751 | 4296457.2412 | 82369.8197 | 8131006.5421 | 4285500.4842 | 80249.6046 | 18649.5966 | 10494.1206 | 1657.5787 | 462.6364 | 218077.237 | 124897.2972 | 23165.3741 | 5860.5351 | 3459.9331 | 88.3526 | 207590.3382 | 116811.0005 | 18450.6579 | 4626.3637 | 0.017677 | 0.0093004 | 0.0002358 | 0.096588 | 0.054879 | 0.0096588 | 0.0071466 | 5000000 | scaled
353-593F | 2519059.1295 | 2498439.9602 | 19146.1021 | 1473.0673 | 99.18% | 0.76% | 0.05848% | 1167213.9016 | 2482474.2317 | 60141.7025 | 7470.9151 | 1099601.2839 | 127161.9008 | 15593.8574 | 2339718.4735 | 353 |  | 667 | 353-593F | 2519059.1295 | 1351845.228 | 36584.8978 | 2498439.9602 | 1339592.9451 | 33409.0811 | 19146.1021 | 10779.2156 | 1702.7495 | 1473.0673 | 128904.8864 | 68763.1839 | 1742.9856 | 128878.1127 | 68747.626 | 1739.5946 | 25.6653 | 14.4495 | 2.2825 | 1.1084 | 2371707.8472 | 1272106.5633 | 31989.3737 | 2369464.4402 | 1270785.0526 | 31667.9436 | 2109.5925 | 1187.6962 | 187.6156 | 133.8144 | 18446.3959 | 10975.4808 | 2852.5385 | 97.4073 | 60.2666 | 1.5428 | 17010.8443 | 9577.0699 | 1512.8513 | 1338.1444 | 0.0060066 | 0.0030884 | 7.88e-05 | 0.097304 | 0.055309 | 0.0097304 | 0.0020622 | 5000000 | scaled
353-594F | 2215649.7528 | 2214151.4104 | 660.9115 | 837.4309 | 99.93% | 0.02983% | 0.0378% | 1141347.7261 | 2206933.6753 | 57949.5677 | 266.5309 | 1083131.6275 | 112338.9561 | 555.7683 | 2094038.9509 | 353 |  | 668 | 353-594F | 2215649.7528 | 1074302.0267 | 8716.0775 | 2214151.4104 | 1073092.3789 | 7819.8744 | 660.9115 | 372.2168 | 58.7722 | 837.4309 | 112745.566 | 54795.9982 | 406.6099 | 112744.4325 | 54795.0846 | 405.935 | 0.50335 | 0.28348 | 0.04476 | 0.63014 | 2101533.6271 | 1018401.9996 | 7494.6762 | 2101404.8035 | 1018296.2182 | 7413.9125 | 52.7509 | 29.7086 | 4.6909 | 76.0728 | 1370.5597 | 1104.0288 | 814.7915 | 2.1744 | 1.076 | 0.026969 | 607.6573 | 342.2248 | 54.0365 | 760.728 | 0.0036578 | 0.0018432 | 4.7e-05 | 0.097316 | 0.055337 | 0.0097316 | 0.0011824 | 5000000 | scaled
353-900F | 1991358.192 | 1766219.9618 | 224452.8332 | 685.397 | 88.69% | 11.27% | 0.03442% | 1056776.9553 | 1923520.1335 | 48565.7252 | 89711.5208 | 918499.7093 | 87070.1043 | 186953.3091 | 1649496.72 | 353 |  | 669 | 353-900F | 1991358.192 | 934581.2367 | 67838.0585 | 1766219.9618 | 807574.8221 | 47202.4873 | 224452.8332 | 126321.0175 | 19950.1742 | 685.397 | 89416.8516 | 40851.1264 | 2346.7473 | 89078.9619 | 40660.7381 | 2316.2446 | 337.374 | 189.8725 | 29.987 | 0.51574 | 1696130.1624 | 777630.4531 | 46633.4424 | 1677106.096 | 766896.5753 | 44885.7871 | 18961.8044 | 10671.6159 | 1685.3933 | 62.2619 | 205811.178 | 116099.6572 | 18857.8689 | 34.9039 | 17.5087 | 0.45562 | 205153.6548 | 115459.5291 | 18234.7939 | 622.6193 | 0.0033072 | 0.0015398 | 3.98e-05 | 0.096586 | 0.054879 | 0.0096586 | 0.0009594 | 5000000 | scaled
353-901F | 4555618.8657 | 4296048.7024 | 257665.2243 | 1904.9389 | 94.3% | 5.656% | 0.04182% | 2443516.225 | 4522205.5957 | 172157.7333 | 102721.427 | 2168637.0647 | 317542.1294 | 214100.5741 | 3990562.8922 | 353 |  | 670 | 353-901F | 4555618.8657 | 2112102.6407 | 33413.27 | 4296048.7024 | 1965164.7377 | 8601.2608 | 257665.2243 | 145032.964 | 22907.0703 | 1904.9389 | 318260.588 | 146102.8547 | 718.4586 | 317881.4619 | 145888.8281 | 683.4474 | 377.6927 | 212.5933 | 33.5778 | 1.4334 | 4000664.562 | 1832027.4973 | 10101.6698 | 3977820.6598 | 1819093.6238 | 7913.1291 | 22670.8562 | 12760.8275 | 2015.4947 | 173.046 | 236693.7157 | 133972.2887 | 22593.1416 | 346.5807 | 182.2858 | 4.6842 | 234616.6754 | 132059.5433 | 20857.9978 | 1730.4596 | 0.0069132 | 0.0033306 | 8.52e-05 | 0.09656 | 0.054873 | 0.009656 | 0.0027098 | 5000000 | scaled
353-902F | 465100.6078 | 292268.0514 | 172496.6985 | 335.858 | 62.84% | 37.09% | 0.07221% | 206976.8618 | 445133.8203 | 6826.4839 | 68708.6503 | 131441.7275 | 14862.7869 | 143252.0451 | 287018.9882 | 353 |  | 671 | 353-902F | 465100.6078 | 258123.7461 | 19966.7876 | 292268.0514 | 160669.2078 | 4292.1915 | 172496.6985 | 97118.6803 | 15338.7381 | 335.858 | 15126.0487 | 8299.5647 | 263.2618 | 14869.8301 | 8155.1987 | 240.2481 | 255.9659 | 144.1133 | 22.761 | 0.25272 | 292436.4246 | 160994.6971 | 5417.4364 | 277392.1229 | 152511.158 | 4051.8715 | 15013.7922 | 8453.0295 | 1335.0553 | 30.5096 | 157538.1346 | 88829.4843 | 14286.0894 | 6.0984 | 2.8511 | 0.071888 | 157226.9405 | 88521.5375 | 13980.9218 | 305.0957 | 0.0015218 | 0.0007442 | 1.9e-05 | 0.096839 | 0.055044 | 0.0096838 | 0.0004932 | 5000000 | scaled
353-904R | 13534406.6532 | 13457602.2771 | 71457.012 | 5347.3641 | 99.43% | 0.528% | 0.03951% | 5711670.4386 | 13357676.5918 | 359246.5322 | 47861.0753 | 5304562.8312 | 839922.6159 | 108235.8908 | 12409518.085 | 353 |  | 672 | 353-904R | 13534406.6532 | 7822736.2146 | 176730.0614 | 13457602.2771 | 7777185.7018 | 165025.3927 | 71457.012 | 40203.1487 | 6357.3046 | 5347.3641 | 850492.3608 | 491245.8286 | 10569.7448 | 850389.3854 | 491186.1327 | 10556.9177 | 98.9516 | 55.6722 | 8.8034 | 4.0237 | 12564263.4911 | 7259700.66 | 154745.4061 | 12557302.9547 | 7255572.0617 | 153683.6073 | 6474.7782 | 3642.8401 | 576.0406 | 485.7582 | 119650.8013 | 71789.726 | 11414.9104 | 49909.9369 | 30427.5074 | 784.8677 | 64883.2822 | 36504.6364 | 5772.4606 | 4857.5821 | 0.021143 | 0.011967 | 0.0003042 | 0.097148 | 0.05518 | 0.0097148 | 0.0074806 | 5000000 | scaled
354-1706R | 20510259.2469 | 20339348.0468 | 158498.2239 | 12412.9762 | 99.17% | 0.7728% | 0.06052% | 8846905.5704 | 20200258.7955 | 702406.3031 | 72838.2245 | 8071661.0427 | 1607234.1533 | 164546.6096 | 18428478.0325 | 354 |  | 673 | 354-1706R | 20510259.2469 | 11663353.6765 | 310000.4514 | 20339348.0468 | 11562161.8479 | 284144.2606 | 158498.2239 | 88778.8524 | 13443.2146 | 12412.9762 | 1630229.857 | 927823.5539 | 22995.7037 | 1630018.0097 | 927700.7843 | 22969.1874 | 202.507 | 113.4293 | 17.1759 | 9.3404 | 18691468.778 | 10619807.7353 | 262990.7455 | 18674982.0533 | 10610077.1007 | 260560.4401 | 15359.1215 | 8603.0313 | 1302.7021 | 1127.6033 | 188560.6119 | 115722.3873 | 24014.0022 | 34347.9838 | 24383.9629 | 614.6331 | 142936.5954 | 80062.3919 | 12123.3366 | 11276.0326 | 0.055314 | 0.031461 | 0.0007996 | 0.06656 | 0.037784 | 0.006656 | 0.017515 | 5000000 | scaled
354-24AE | 3653653.987 | 3234791.8728 | 416154.1266 | 2707.9876 | 88.54% | 11.39% | 0.07412% | 1625263.8186 | 3579738.1497 | 76158.4941 | 168248.0374 | 1380857.287 | 170124.7873 | 353571.3749 | 3056041.9876 | 354 |  | 674 | 354-24AE | 3653653.987 | 2028390.1684 | 73915.8372 | 3234791.8728 | 1792630.7309 | 35938.6817 | 416154.1266 | 233051.45 | 35269.168 | 2707.9876 | 172081.2118 | 95922.7177 | 1956.4246 | 171575.4025 | 95638.5617 | 1911.6921 | 503.7717 | 282.1184 | 42.6948 | 2.0377 | 3093588.3447 | 1712731.0578 | 37546.3571 | 3052349.9527 | 1689528.814 | 33826.2457 | 40992.3966 | 22956.2483 | 3474.116 | 245.9954 | 387984.4304 | 219736.393 | 34413.0556 | 10866.5177 | 7463.3552 | 200.7439 | 374657.9583 | 209813.0833 | 31752.3571 | 2459.9545 | 0.010941 | 0.0062876 | 0.0001592 | 0.065871 | 0.03738 | 0.006587 | 0.0037426 | 5000000 | scaled
355-41R | 7500586.088 | 7388136.9365 | 107958.6016 | 4490.5499 | 98.5% | 1.439% | 0.05987% | 3789605.0642 | 7389914.6066 | 199998.1395 | 43643.0304 | 3545963.8943 | 389026.8414 | 90366.7178 | 6910521.0474 | 355 |  | 675 | 355-41R | 7500586.088 | 3710981.0238 | 110671.4814 | 7388136.9365 | 3646125.8439 | 96994.9743 | 107958.6016 | 60364.63 | 9185.9572 | 4490.5499 | 394199.0888 | 194200.9493 | 5172.2474 | 393961.1513 | 194066.4178 | 5148.9104 | 234.5585 | 131.1525 | 19.9581 | 3.379 | 7003632.5318 | 3457668.6374 | 93111.4844 | 6992991.7895 | 3451539.0728 | 91832.8721 | 10232.8177 | 5721.64 | 870.6877 | 407.9246 | 102754.4674 | 59111.437 | 12387.7496 | 1183.9957 | 520.3532 | 13.1918 | 97491.2254 | 54511.8375 | 8295.3115 | 4079.2463 | 0.018028 | 0.008914 | 0.0002264 | 0.067904 | 0.038456 | 0.0067904 | 0.0063218 | 5000000 | scaled
355-65R | 66.9898 | 30.8862 | 0 | 36.1036 | 46.11% | 0% | 53.89% | 30.8862 | 30.8862 | 3.3549 | 0 | 27.5313 | 3.3549 | 0 | 27.5313 | 355 |  | 676 | 355-65R | 66.9898 | 36.1036 | 36.1036 | 30.8862 | 0 | 0 | 0 | 0 | 0 | 36.1036 | 3.3821 | 0.027167 | 0.027167 | 3.3549 | 0 | 0 | 0 | 0 | 0 | 0.027167 | 30.811 | 3.2797 | 3.2797 | 27.5313 | 0 | 0 | 0 | 0 | 0 | 3.2797 | 32.7968 | 32.7968 | 32.7968 | 0 | 0 | 0 | 0 | 0 | 0 | 32.7968 | 1.86e-05 | 1.42e-05 | 4e-07 | 0 | 0 | 0 | 5.16e-05 | 5000000 | scaled
355-6R | 1698709.6728 | 1357931.9014 | 339549.8847 | 1227.8867 | 79.94% | 19.99% | 0.07228% | 754737.2154 | 1654472.7808 | 32357.2232 | 137762.8673 | 584617.1249 | 71163.9725 | 286773.7382 | 1296535.0701 | 355 |  | 677 | 355-6R | 1698709.6728 | 943972.4573 | 44236.892 | 1357931.9014 | 752783.0836 | 14150.5822 | 339549.8847 | 189961.487 | 28858.423 | 1227.8867 | 71986.6414 | 39629.4182 | 822.6689 | 71571.3904 | 39396.6986 | 786.5312 | 414.327 | 231.7956 | 35.2138 | 0.92395 | 1312390.3578 | 727773.2329 | 15855.2877 | 1283788.1073 | 711722.5385 | 13322.3137 | 28490.7084 | 15939.1523 | 2421.4319 | 111.5421 | 314332.6736 | 176569.8063 | 27558.9354 | 2572.4037 | 1663.8466 | 41.7373 | 310644.8492 | 173790.5391 | 26401.7774 | 1115.4207 | 0.0054326 | 0.003246 | 8.28e-05 | 0.067158 | 0.038057 | 0.0067158 | 0.0017428 | 5000000 | scaled
356-16R | 5437437.5172 | 5336373.2739 | 96850.0673 | 4214.176 | 98.14% | 1.781% | 0.0775% | 2402463.414 | 5362678.2347 | 183770.3608 | 50501.6763 | 2168191.3769 | 410499.2312 | 111105.5465 | 4841073.4571 | 356 |  | 678 | 356-16R | 5437437.5172 | 3034974.1031 | 74759.2824 | 5336373.2739 | 2976555.7758 | 62304.6673 | 96850.0673 | 54204.1514 | 8240.4391 | 4214.176 | 415427.2778 | 231656.917 | 4928.0466 | 415262.5742 | 231563.3409 | 4911.1316 | 161.5325 | 90.405 | 13.7439 | 3.171 | 4899060.1392 | 2730868.7623 | 57986.6822 | 4890386.5061 | 2725845.8172 | 56898.4438 | 8290.8145 | 4640.1265 | 705.4198 | 382.8186 | 122950.1002 | 72448.4238 | 11844.5537 | 30724.1936 | 19146.6177 | 495.0919 | 88397.7202 | 49473.6198 | 7521.2755 | 3828.1863 | 0.016717 | 0.0092284 | 0.0002332 | 0.068062 | 0.038577 | 0.0068062 | 0.0059742 | 5000000 | scaled
356-19R | 16012786.3517 | 15654557.522 | 343518.1164 | 14710.7133 | 97.76% | 2.145% | 0.09187% | 7825949.9818 | 15684700.4717 | 541187.7115 | 142709.8288 | 7142052.4415 | 1082261.0661 | 298758.0366 | 14303681.3691 | 356 |  | 679 | 356-19R | 16012786.3517 | 8186836.3699 | 328085.88 | 15654557.522 | 7979371.2347 | 283431.1097 | 343518.1164 | 192754.4219 | 29944.057 | 14710.7133 | 1101704.3041 | 560516.5927 | 19443.2381 | 1101171.6181 | 560212.8345 | 19386.7001 | 521.6167 | 292.6889 | 45.4687 | 11.0693 | 14571649.0267 | 7429596.5852 | 267967.6576 | 14538010.2498 | 7410134.7492 | 263815.5614 | 32302.4456 | 18125.5047 | 2815.765 | 1336.3313 | 339433.0209 | 196723.1921 | 40674.9843 | 15375.6541 | 9023.6511 | 228.8483 | 310694.0541 | 174336.2283 | 27082.8234 | 13363.3127 | 0.06528 | 0.032185 | 0.000816 | 0.081694 | 0.046349 | 0.0081694 | 0.02078 | 5000000 | scaled
356-30AE | 9294675.1195 | 8868205.8361 | 412482.4657 | 13986.8177 | 95.41% | 4.438% | 0.1505% | 4539184.4481 | 9153326.9985 | 331158.8756 | 169829.1771 | 4038196.3954 | 665035.6154 | 353479.4989 | 8134811.8842 | 356 |  | 680 | 356-30AE | 9294675.1195 | 4755490.6714 | 141348.121 | 8868205.8361 | 4510783.5774 | 92310.8254 | 412482.4657 | 230720.2763 | 35050.4779 | 13986.8177 | 672191.0939 | 341032.2183 | 7155.4785 | 671493.8385 | 340637.5738 | 7086.5993 | 686.7308 | 384.1199 | 58.3546 | 10.5246 | 8224212.4816 | 4186016.0862 | 89400.5974 | 8187109.2111 | 4164702.6498 | 85085.1608 | 35832.6984 | 20042.8643 | 3044.8645 | 1270.5721 | 398271.544 | 228442.3668 | 44792.0451 | 9602.7865 | 5443.3538 | 139.0653 | 375963.0365 | 210293.2921 | 31947.2588 | 12705.721 | 0.054258 | 0.026918 | 0.0006832 | 0.067045 | 0.037982 | 0.0067046 | 0.019755 | 5000000 | scaled
357-1147R | 1251175.7701 | 1239445.5619 | 10953.1743 | 777.034 | 99.06% | 0.8754% | 0.0621% | 637811.4376 | 1234544.6886 | 32400.3193 | 4397.1609 | 601013.9574 | 62800.6433 | 9150.12 | 1162593.9253 | 357 |  | 681 | 357-1147R | 1251175.7701 | 613364.3325 | 16631.0815 | 1239445.5619 | 606410.3616 | 14841.0315 | 10953.1743 | 6176.9369 | 1013.016 | 777.034 | 63625.3844 | 31225.0651 | 824.7411 | 63608.1286 | 31215.0789 | 822.6146 | 16.671 | 9.4015 | 1.5418 | 0.58469 | 1176763.4941 | 575749.5367 | 14169.5688 | 1175819.3422 | 575186.3115 | 14018.1898 | 873.5656 | 492.6389 | 80.7926 | 70.5863 | 10786.8916 | 6389.7307 | 1636.7716 | 18.091 | 8.9712 | 0.2271 | 10062.9376 | 5674.8965 | 930.6815 | 705.863 | 0.0020868 | 0.0010182 | 2.6e-05 | 0.13968 | 0.07928 | 0.013968 | 0.0011046 | 5000000 | scaled
357-1299R | 5098732.7905 | 5082456.8734 | 14745.3624 | 1530.5548 | 99.68% | 0.2892% | 0.03002% | 2505093.0813 | 5079792.1571 | 171659.3173 | 5877.0061 | 2327556.758 | 347484.0455 | 12233.938 | 4720074.1737 | 357 |  | 682 | 357-1299R | 5098732.7905 | 2593639.7092 | 18940.6334 | 5082456.8734 | 2583765.2039 | 16010.2386 | 14745.3624 | 8343.9505 | 1399.84 | 1530.5548 | 348664.5661 | 177005.2488 | 1180.5206 | 348639.1185 | 176990.3488 | 1177.0624 | 24.2959 | 13.7483 | 2.3065 | 1.1517 | 4735176.2437 | 2407619.4857 | 15102.07 | 4733648.3599 | 2406694.5429 | 14831.1842 | 1388.8471 | 785.9062 | 131.8492 | 139.0366 | 14891.9808 | 9014.9747 | 2658.0428 | 169.395 | 80.3123 | 1.992 | 13332.2194 | 7544.296 | 1265.6843 | 1390.3664 | 0.010791 | 0.0054706 | 0.0001388 | 0.22795 | 0.12954 | 0.022795 | 0.002167 | 5000000 | scaled
357-2047F | 878930.3773 | 839250.3564 | 39397.5938 | 282.4272 | 95.49% | 4.482% | 0.03213% | 465095.5097 | 874657.5494 | 23279.1802 | 15736.2952 | 426080.0343 | 43526.7573 | 32747.7441 | 798383.048 | 357 |  | 683 | 357-2047F | 878930.3773 | 413834.8676 | 4272.8279 | 839250.3564 | 391334.5745 | 346.5653 | 39397.5938 | 22217.8659 | 3643.8355 | 282.4272 | 43557.4696 | 20278.2894 | 30.7122 | 43510.6978 | 20251.8203 | 26.1935 | 46.5592 | 26.2566 | 4.3062 | 0.21252 | 799032.0734 | 372952.0391 | 649.0254 | 795729.1887 | 371078.2239 | 320.2626 | 3277.2289 | 1848.1594 | 303.1069 | 25.6559 | 36340.8344 | 20604.5391 | 3593.0903 | 10.4699 | 4.5304 | 0.10914 | 36073.8057 | 20343.4499 | 3336.4223 | 256.5588 | 0.001136 | 0.0004918 | 1.24e-05 | 0.13974 | 0.079313 | 0.013974 | 0.0004076 | 5000000 | scaled
357-2048F | 41154.2263 | 0 | 41154.2263 | 0 | 0% | 100% | 0% | 1519.8977 | 3159.6853 | 2.5305 | 1391.3339 | 126.0334 | 5.2606 | 2892.4165 | 262.0083 | 357 |  | 684 | 357-2048F | 41154.2263 | 39634.3286 | 37994.541 | 0 | 0 | 0 | 41154.2263 | 39634.3286 | 37994.541 | 0 | 68.5177 | 65.9872 | 63.2571 | 0 | 0 | 0 | 68.5177 | 65.9872 | 63.2571 | 0 | 3412.6016 | 3286.5683 | 3150.5934 | 0 | 0 | 0 | 3412.6016 | 3286.5683 | 3150.5934 | 0 | 37673.107 | 36281.7731 | 34780.6905 | 0 | 0 | 0 | 37673.107 | 36281.7731 | 34780.6905 | 0 | 0 | 0 | 0 | 0.13617 | 0.13617 | 0.13617 | 0 | 5000000 | scaled
357-2049F | 16869708.0077 | 16664984.6208 | 199776.3295 | 4947.0574 | 98.79% | 1.184% | 0.02933% | 8450803.594 | 16548268.3424 | 566269.0664 | 80011.2889 | 7804523.2388 | 1109636.8878 | 166686.0188 | 15271945.4358 | 357 |  | 685 | 357-2049F | 16869708.0077 | 8418904.4137 | 321439.6653 | 16664984.6208 | 8301069.3498 | 297877.2473 | 199776.3295 | 112888.0065 | 18615.3605 | 4947.0574 | 1129545.989 | 563276.9226 | 19909.1011 | 1129267.5032 | 563117.9391 | 19879.7759 | 274.7632 | 155.261 | 25.6027 | 3.7225 | 15551959.5739 | 7747436.3352 | 280014.1381 | 15534538.6382 | 7737396.7984 | 277983.3186 | 16971.5416 | 9590.1426 | 1581.4254 | 449.3941 | 188202.4448 | 108191.156 | 21516.426 | 1178.4793 | 554.6123 | 14.1528 | 182530.0247 | 103142.6028 | 17008.3324 | 4493.9408 | 0.020362 | 0.010305 | 0.0002606 | 0.15549 | 0.088375 | 0.015549 | 0.0070088 | 5000000 | scaled
357-45R | 17696752.5099 | 17249773.4593 | 438470.3008 | 8508.7498 | 97.47% | 2.478% | 0.04808% | 8836376.3508 | 17417976.0319 | 710092.9733 | 182134.0638 | 7944149.3138 | 1398303.4842 | 380372.5861 | 15639299.9616 | 357 |  | 686 | 357-45R | 17696752.5099 | 8860376.1591 | 278776.4779 | 17249773.4593 | 8604552.5277 | 229820.5176 | 438470.3008 | 247314.8816 | 40447.2106 | 8508.7498 | 1417172.8068 | 707079.8335 | 18869.3226 | 1416454.0894 | 706671.6568 | 18797.2117 | 712.3148 | 401.7742 | 65.7083 | 6.4026 | 15854385.7789 | 7910236.4651 | 215085.8172 | 15815166.9124 | 7887778.4763 | 210766.3868 | 38445.9258 | 21685.0482 | 3546.4898 | 772.9407 | 425193.9242 | 243059.8604 | 44821.3381 | 18152.4575 | 10102.3946 | 256.9191 | 399312.0602 | 225228.0593 | 36835.0125 | 7729.4066 | 0.039295 | 0.019475 | 0.000496 | 0.13401 | 0.076102 | 0.013401 | 0.01207 | 5000000 | scaled
357-50R | 10432488.7437 | 10123494.7451 | 300831.8477 | 8162.1509 | 97.04% | 2.884% | 0.07824% | 5173501.4597 | 10235655.5704 | 379559.4003 | 122064.9783 | 4671877.0811 | 750376.206 | 254697.102 | 9230582.2624 | 357 |  | 687 | 357-50R | 10432488.7437 | 5258987.284 | 196833.1733 | 10123494.7451 | 5081338.645 | 161619.6666 | 300831.8477 | 169486.4881 | 27051.3559 | 8162.1509 | 762470.4721 | 382911.0718 | 12094.266 | 761987.8497 | 382636.4843 | 12045.2783 | 476.4806 | 268.4457 | 42.846 | 6.1418 | 9383112.6101 | 4711235.529 | 152530.3477 | 9357039.1706 | 4696222.2169 | 149510.9935 | 25331.9841 | 14271.8567 | 2277.8988 | 741.4554 | 286905.6615 | 164840.6832 | 32208.5595 | 4467.7248 | 2479.9438 | 63.3948 | 275023.383 | 154946.1856 | 24730.611 | 7414.5538 | 0.033132 | 0.01682 | 0.0004382 | 0.10455 | 0.059405 | 0.010455 | 0.011445 | 5000000 | scaled
357-750R | 11757625.4162 | 11499648.1899 | 251929.878 | 6047.3483 | 97.81% | 2.143% | 0.05143% | 5797306.3526 | 11614891.5758 | 462436.1107 | 101981.9843 | 5232888.2575 | 925421.8107 | 211715.6012 | 10477754.164 | 357 |  | 688 | 357-750R | 11757625.4162 | 5960319.0636 | 142733.8404 | 11499648.1899 | 5812232.8648 | 113433.6653 | 251929.878 | 142038.8505 | 23252.8268 | 6047.3483 | 934847.6846 | 472411.5738 | 9425.8739 | 934408.8338 | 472162.1635 | 9381.2381 | 434.3003 | 244.8599 | 40.0854 | 4.5504 | 10584339.5263 | 5351451.2687 | 106585.3623 | 10561880.846 | 5338549.3721 | 104013.8116 | 21909.3351 | 12352.5514 | 2022.2055 | 549.3453 | 238438.2054 | 136456.221 | 26722.6042 | 3358.5101 | 1521.3292 | 38.6157 | 229586.2426 | 129441.4392 | 21190.5359 | 5493.4526 | 0.027182 | 0.013263 | 0.0003442 | 0.13533 | 0.076811 | 0.013533 | 0.0084898 | 5000000 | scaled
358-1175F | 599583.3935 | 582831.823 | 16465.7029 | 285.8675 | 97.21% | 2.746% | 0.04768% | 344835.8796 | 582192.8468 | 17628.0959 | 6611.7621 | 320596.0216 | 29583.2421 | 13758.4039 | 538851.2008 | 358 |  | 689 | 358-1175F | 599583.3935 | 254747.5139 | 17390.5467 | 582831.823 | 245173.9798 | 15581.3861 | 16465.7029 | 9287.6665 | 1523.293 | 285.8675 | 30369.3575 | 12741.2616 | 786.1154 | 30348.2527 | 12729.2635 | 783.9677 | 20.8897 | 11.7831 | 1.9326 | 0.21511 | 553795.8048 | 233199.7832 | 14944.604 | 552456.2883 | 232432.8931 | 14797.1152 | 1313.5481 | 740.9217 | 121.5204 | 25.9684 | 15418.2312 | 8806.469 | 1659.8273 | 27.282 | 11.8233 | 0.30318 | 15131.2651 | 8534.9617 | 1399.8401 | 259.684 | 0.0014874 | 0.0006442 | 1.64e-05 | 0.14006 | 0.079513 | 0.014006 | 0.000398 | 5000000 | scaled
358-1240F | 3541.2933 | 0 | 3541.2933 | 0 | 0% | 100% | 0% | 41.2368 | 86.2258 | 0.027082 | 32.695 | 8.5148 | 0.056629 | 68.3649 | 17.8043 | 358 |  | 690 | 358-1240F | 3541.2933 | 3500.0565 | 3455.0675 | 0 | 0 | 0 | 3541.2933 | 3500.0565 | 3455.0675 | 0 | 2.3258 | 2.2987 | 2.2691 | 0 | 0 | 0 | 2.3258 | 2.2987 | 2.2691 | 0 | 731.2227 | 722.7079 | 713.4184 | 0 | 0 | 0 | 731.2227 | 722.7079 | 713.4184 | 0 | 2807.7449 | 2775.0499 | 2739.38 | 0 | 0 | 0 | 2807.7449 | 2775.0499 | 2739.38 | 0 | 0 | 0 | 0 | 0.49336 | 0.49336 | 0.49336 | 0 | 5000000 | scaled
358-33 | 1344643.6099 | 1340076.1645 | 4140.6168 | 426.8286 | 99.66% | 0.3079% | 0.03174% | 444702.2866 | 1329655.5092 | 33854.9209 | 1844.0222 | 409003.3435 | 101353.2983 | 4038.6435 | 1224263.5675 | 358 |  | 691 | 358-33 | 1344643.6099 | 899941.3233 | 14988.1006 | 1340076.1645 | 897178.4537 | 14178.1228 | 4140.6168 | 2336.041 | 383.1492 | 426.8286 | 102422.2717 | 68567.3508 | 1068.9734 | 102389.7929 | 68548.887 | 1065.6766 | 32.1577 | 18.1426 | 2.9757 | 0.32117 | 1237466.0417 | 828462.6982 | 13202.4742 | 1236694.6293 | 828010.5867 | 13095.9066 | 732.639 | 413.3381 | 67.7943 | 38.7734 | 4755.2964 | 2911.2743 | 716.653 | 991.7423 | 618.98 | 16.5397 | 3375.8201 | 1904.5603 | 312.3793 | 387.734 | 0.0017168 | 0.0010358 | 2.64e-05 | 0.14065 | 0.079859 | 0.014065 | 0.0006096 | 5000000 | scaled
358-663F | 1082.8298 | 0 | 1082.8298 | 0 | 0% | 100% | 0% | 38.6834 | 80.5653 | 0.50185 | 30.2925 | 7.8891 | 1.0452 | 63.0896 | 16.4305 | 358 |  | 692 | 358-663F | 1082.8298 | 1044.1464 | 1002.2646 | 0 | 0 | 0 | 1082.8298 | 1044.1464 | 1002.2646 | 0 | 14.0478 | 13.5459 | 13.0026 | 0 | 0 | 0 | 14.0478 | 13.5459 | 13.0026 | 0 | 220.8321 | 212.943 | 204.4016 | 0 | 0 | 0 | 220.8321 | 212.943 | 204.4016 | 0 | 847.9499 | 817.6575 | 784.8603 | 0 | 0 | 0 | 847.9499 | 817.6575 | 784.8603 | 0 | 0 | 0 | 0 | 0.14135 | 0.14135 | 0.14135 | 0 | 5000000 | scaled
358-665F | 1083.7268 | 0 | 1083.7268 | 0 | 0% | 100% | 0% | 38.716 | 80.6376 | 0.50227 | 30.318 | 7.8957 | 1.0461 | 63.1462 | 16.4452 | 358 |  | 693 | 358-665F | 1083.7268 | 1045.0107 | 1003.0892 | 0 | 0 | 0 | 1083.7268 | 1045.0107 | 1003.0892 | 0 | 14.0594 | 13.5571 | 13.0133 | 0 | 0 | 0 | 14.0594 | 13.5571 | 13.0133 | 0 | 221.015 | 213.1193 | 204.5698 | 0 | 0 | 0 | 221.015 | 213.1193 | 204.5698 | 0 | 848.6523 | 818.3343 | 785.5061 | 0 | 0 | 0 | 848.6523 | 818.3343 | 785.5061 | 0 | 0 | 0 | 0 | 0.14147 | 0.14147 | 0.14147 | 0 | 5000000 | scaled
358-666F | 1084.5712 | 0 | 1084.5712 | 0 | 0% | 100% | 0% | 38.7571 | 80.7397 | 0.5028 | 30.3502 | 7.9041 | 1.0475 | 63.2262 | 16.466 | 358 |  | 694 | 358-666F | 1084.5712 | 1045.8141 | 1003.8315 | 0 | 0 | 0 | 1084.5712 | 1045.8141 | 1003.8315 | 0 | 14.0704 | 13.5676 | 13.0229 | 0 | 0 | 0 | 14.0704 | 13.5676 | 13.0229 | 0 | 221.1872 | 213.2831 | 204.7212 | 0 | 0 | 0 | 221.1872 | 213.2831 | 204.7212 | 0 | 849.3136 | 818.9634 | 786.0874 | 0 | 0 | 0 | 849.3136 | 818.9634 | 786.0874 | 0 | 0 | 0 | 0 | 0.14157 | 0.14157 | 0.14157 | 0 | 5000000 | scaled
358-681F | 59326.7645 | 0 | 59326.7645 | 0 | 0% | 100% | 0% | 2124.0161 | 4422.8489 | 19.065 | 1670.0254 | 434.9257 | 39.6992 | 3477.5018 | 905.6479 | 358 |  | 695 | 358-681F | 59326.7645 | 57202.7483 | 54903.9156 | 0 | 0 | 0 | 59326.7645 | 57202.7483 | 54903.9156 | 0 | 532.5127 | 513.4477 | 492.8135 | 0 | 0 | 0 | 532.5127 | 513.4477 | 492.8135 | 0 | 12148.0882 | 11713.1625 | 11242.4403 | 0 | 0 | 0 | 12148.0882 | 11713.1625 | 11242.4403 | 0 | 46646.1636 | 44976.1382 | 43168.6617 | 0 | 0 | 0 | 46646.1636 | 44976.1382 | 43168.6617 | 0 | 0 | 0 | 0 | 0.14136 | 0.14136 | 0.14136 | 0 | 5000000 | scaled
358-682F | 37602118.365 | 37073060.587 | 521206.7954 | 7850.9826 | 98.59% | 1.386% | 0.02088% | 15994892.9689 | 37025293.9783 | 940322.9486 | 204498.7303 | 14850071.2901 | 2182320.6925 | 426406.6691 | 34416566.6167 | 358 |  | 696 | 358-682F | 37602118.365 | 21607225.396 | 576824.3866 | 37073060.587 | 21304026.2151 | 518153.8928 | 521206.7954 | 295348.1984 | 50819.5113 | 7850.9826 | 2213490.8138 | 1273167.8653 | 31170.1213 | 2212473.7313 | 1272588.963 | 31065.6205 | 1011.1749 | 572.9946 | 98.5931 | 5.9076 | 34909159.7269 | 20059088.4368 | 492593.1102 | 34859024.8017 | 20030369.8173 | 487061.1269 | 49421.7366 | 28005.4308 | 4818.7946 | 713.1886 | 479467.8243 | 274969.094 | 53061.1552 | 1562.0541 | 1067.4348 | 27.1454 | 470773.8839 | 266769.7729 | 45902.1235 | 7131.8863 | 0.050627 | 0.029383 | 0.000747 | 0.48064 | 0.27291 | 0.048064 | 0.011152 | 5000000 | scaled
361-45R | 74922.6332 | 3550.2602 | 68786.5166 | 2585.8564 | 4.739% | 91.81% | 3.451% | 32484.3006 | 67660.87 | 63.599 | 29387.8111 | 3032.8905 | 122.5268 | 61248.2154 | 6290.1278 | 361 |  | 697 | 361-45R | 74922.6332 | 42438.3325 | 7261.7632 | 3550.2602 | 1741.4889 | 74.0491 | 68786.5166 | 38110.9871 | 4601.8576 | 2585.8564 | 133.1247 | 69.5257 | 10.5979 | 51.058 | 23.1891 | 3.292 | 80.1209 | 44.3908 | 5.3601 | 1.9458 | 6976.6761 | 3943.7856 | 686.5484 | 262.6818 | 119.1602 | 18.1923 | 6479.0934 | 3589.7245 | 433.4551 | 234.901 | 67812.8323 | 38425.0212 | 6564.6169 | 3236.5203 | 1599.1396 | 52.5648 | 62227.3023 | 34476.8719 | 4163.0424 | 2349.0097 | 0.0056688 | 0.0026592 | 6.68e-05 | 0.0056432 | 0.0032158 | 0.0005644 | 0.0035582 | 5000000 | scaled
361-684F | 700.0449 | 242.2341 | 103.1801 | 354.6307 | 34.6% | 14.74% | 50.66% | 155.0122 | 338.503 | 11.6193 | 44.0638 | 99.3292 | 25.8937 | 91.5989 | 221.0104 | 361 |  | 698 | 361-684F | 700.0449 | 545.0327 | 361.5419 | 242.2341 | 133.2144 | 0.029612 | 103.1801 | 57.1876 | 6.8816 | 354.6307 | 26.1762 | 14.5569 | 0.28255 | 25.674 | 14.1596 | 0 | 0.23539 | 0.13046 | 0.015699 | 0.26685 | 253.7737 | 154.4446 | 32.7633 | 213.336 | 117.6722 | 0 | 8.2228 | 4.5575 | 0.54842 | 32.2149 | 420.095 | 376.0312 | 328.4961 | 3.2241 | 1.3826 | 0.029612 | 94.7219 | 52.4996 | 6.3175 | 322.149 | 0.0007914 | 0.0003426 | 8.8e-06 | 0.0056866 | 0.0032422 | 0.0005686 | 0.0005056 | 5000000 | scaled
361-686F | 90674.3969 | 3250.9415 | 84709.1853 | 2714.2701 | 3.585% | 93.42% | 2.993% | 39529.4686 | 82189.5866 | 80.4595 | 36074.7388 | 3374.2703 | 158.4981 | 75028.6273 | 7002.4612 | 361 |  | 699 | 361-686F | 90674.3969 | 51144.9283 | 8484.8103 | 3250.9415 | 1476.6156 | 112.1624 | 84709.1853 | 46954.0426 | 5658.3778 | 2714.2701 | 176.0292 | 95.5697 | 17.5311 | 76.6828 | 39.592 | 8.9891 | 97.304 | 53.9353 | 6.4997 | 2.0424 | 7785.6955 | 4411.4252 | 783.2343 | 400.8723 | 208.145 | 59.8491 | 7138.2571 | 3956.7141 | 476.8191 | 246.5662 | 82712.6721 | 46637.9333 | 7684.0449 | 2773.3864 | 1228.8786 | 43.3242 | 77473.6242 | 42943.3932 | 5175.0591 | 2465.6616 | 0.0072464 | 0.0031376 | 7.96e-05 | 0.005597 | 0.0031912 | 0.0005596 | 0.003824 | 5000000 | scaled
362-40F | 13028.4098 | 151.1817 | 12236.2153 | 641.0128 | 1.16% | 93.92% | 4.92% | 5523.4812 | 11556.6344 | 8.4869 | 4978.1413 | 536.853 | 21.335 | 10392.9243 | 1142.3751 | 362 |  | 700 | 362-40F | 13028.4098 | 7504.9286 | 1471.7754 | 151.1817 | 89.8622 | 13.6537 | 12236.2153 | 6774.0536 | 817.1088 | 641.0128 | 24.5766 | 16.0897 | 3.2416 | 7.3822 | 6.3554 | 1.6432 | 16.712 | 9.2519 | 1.116 | 0.48234 | 1291.1293 | 754.2764 | 148.7542 | 39.4831 | 35.3628 | 10.8303 | 1193.4162 | 660.6835 | 79.6938 | 58.23 | 11712.7039 | 6734.5626 | 1319.7796 | 104.3164 | 48.1439 | 1.1802 | 11026.087 | 6104.1182 | 736.299 | 582.3004 | 0.0019284 | 0.0008352 | 2.16e-05 | 0.0056336 | 0.0032084 | 0.0005634 | 0.00092 | 5000000 | scaled
362-45F | 4596.8195 | 0 | 4596.8195 | 0 | 0% | 100% | 0% | 732.9304 | 1528.8981 | 1.1394 | 627.9567 | 103.8344 | 2.3768 | 1309.9221 | 216.5992 | 362 |  | 701 | 362-45F | 4596.8195 | 3863.8891 | 3067.9214 | 0 | 0 | 0 | 4596.8195 | 3863.8891 | 3067.9214 | 0 | 7.1461 | 6.0067 | 4.7693 | 0 | 0 | 0 | 7.1461 | 6.0067 | 4.7693 | 0 | 651.2321 | 547.3978 | 434.6329 | 0 | 0 | 0 | 651.2321 | 547.3978 | 434.6329 | 0 | 3938.4412 | 3310.4846 | 2628.5192 | 0 | 0 | 0 | 3938.4412 | 3310.4846 | 2628.5192 | 0 | 0 | 0 | 0 | 0.0056296 | 0.0056296 | 0.0056296 | 0 | 5000000 | scaled
362-47F | 174272.616 | 63604.2409 | 100045.3053 | 10623.0698 | 36.5% | 57.41% | 6.096% | 75745.4548 | 156501.1629 | 4819.7546 | 46448.8857 | 24476.8145 | 9860.5465 | 96242.5384 | 50398.0779 | 362 |  | 702 | 362-47F | 174272.616 | 98527.1612 | 17771.4531 | 63604.2409 | 32684.9269 | 713.0102 | 100045.3053 | 55219.1645 | 6435.3731 | 10623.0698 | 9986.4612 | 5166.7067 | 125.9147 | 9860.0038 | 5093.2079 | 110.0514 | 118.4639 | 65.5053 | 7.8698 | 7.9935 | 52375.8488 | 27899.0342 | 1977.7708 | 43219.2978 | 22405.3102 | 470.3341 | 8191.544 | 4528.7171 | 542.4298 | 965.0069 | 111910.306 | 65461.4203 | 15667.7676 | 10524.9392 | 5186.4088 | 132.6247 | 91735.2974 | 50624.9421 | 5885.0735 | 9650.0694 | 0.02867 | 0.013142 | 0.0003354 | 0.0055546 | 0.0031606 | 0.0005554 | 0.014891 | 5000000 | scaled
362-48F | 472.875 | 0 | 472.875 | 0 | 0% | 100% | 0% | 75.2833 | 157.3328 | 0.28341 | 59.5033 | 15.4965 | 0.59229 | 124.3547 | 32.3858 | 362 |  | 703 | 362-48F | 472.875 | 397.5918 | 315.5423 | 0 | 0 | 0 | 472.875 | 397.5918 | 315.5423 | 0 | 1.7802 | 1.4968 | 1.1879 | 0 | 0 | 0 | 1.7802 | 1.4968 | 1.1879 | 0 | 97.3378 | 81.8413 | 64.952 | 0 | 0 | 0 | 97.3378 | 81.8413 | 64.952 | 0 | 373.7571 | 314.2537 | 249.4024 | 0 | 0 | 0 | 373.7571 | 314.2537 | 249.4024 | 0 | 0 | 0 | 0 | 0.0056096 | 0.0056096 | 0.0056096 | 0 | 5000000 | scaled
363-25 | 16229.7747 | 39.3472 | 15905.813 | 284.6145 | 0.2424% | 98% | 1.754% | 7137.6541 | 14884.1221 | 10.0511 | 6234.7754 | 892.8276 | 20.9702 | 13000.3843 | 1862.7676 | 363 |  | 704 | 363-25 | 16229.7747 | 9092.1206 | 1345.6526 | 39.3472 | 17.0213 | 0.42235 | 15905.813 | 8790.4848 | 1060.6157 | 284.6145 | 22.6826 | 12.6315 | 1.7124 | 0 | 0 | 0 | 22.4684 | 12.4174 | 1.4982 | 0.21416 | 2021.7076 | 1128.88 | 158.9401 | 0 | 0 | 0 | 1995.8531 | 1103.0254 | 133.0855 | 25.8546 | 14185.3844 | 7950.6091 | 1185.0001 | 39.3472 | 17.0213 | 0.42235 | 13887.4914 | 7675.042 | 926.032 | 258.5458 | 0.0007526 | 0.0003258 | 8e-06 | 0.0055768 | 0.003171 | 0.0005576 | 0.0004044 | 5000000 | scaled
364-36 | 171186.9421 | 3465.8079 | 161856.1205 | 5865.0136 | 2.025% | 94.55% | 3.426% | 75252.1029 | 156338.6129 | 85.3185 | 69559.7719 | 5607.0125 | 175.4986 | 144481.2962 | 11681.8181 | 364 |  | 705 | 364-36 | 171186.9421 | 95934.8392 | 14848.3292 | 3465.8079 | 1545.2559 | 37.5272 | 161856.1205 | 88524.5697 | 8945.7884 | 5865.0136 | 190.7982 | 105.4798 | 15.2997 | 18.6363 | 8.5236 | 0 | 167.7487 | 92.5429 | 10.8864 | 4.4132 | 13003.1607 | 7396.1482 | 1321.3426 | 96.3364 | 44.0393 | 0 | 12374.0425 | 6819.327 | 788.5607 | 532.7819 | 157992.9831 | 88433.2112 | 13511.687 | 3350.8353 | 1492.6929 | 37.5272 | 149314.3293 | 81612.6998 | 8146.3413 | 5327.8185 | 0.01354 | 0.0059188 | 0.000149 | 0.005463 | 0.003105 | 0.0005462 | 0.0083066 | 5000000 | scaled
364-49R | 138166.7587 | 19819.3203 | 111052.1631 | 7295.2752 | 14.34% | 80.38% | 5.28% | 61199.9089 | 123782.8952 | 157.6717 | 56641.717 | 4400.5201 | 292.524 | 114433.8047 | 9056.5666 | 364 |  | 706 | 364-49R | 138166.7587 | 76966.8498 | 14383.8634 | 19819.3203 | 8535.9345 | 209.4589 | 111052.1631 | 61135.64 | 6879.1293 | 7295.2752 | 307.8043 | 150.1326 | 15.2803 | 169.4413 | 71.2317 | 1.0177 | 132.8735 | 73.4115 | 8.7731 | 5.4895 | 10317.2702 | 5916.7501 | 1260.7036 | 592.4379 | 249.2242 | 3.636 | 9062.1245 | 5004.818 | 594.3599 | 662.7078 | 127541.6842 | 70899.9671 | 13107.8795 | 19057.441 | 8215.4786 | 204.8052 | 101857.1651 | 56057.4105 | 6275.9963 | 6627.078 | 0.019642 | 0.008504 | 0.000216 | 0.00548 | 0.0031168 | 0.000548 | 0.010407 | 5000000 | scaled
365-28AE | 5748.6084 | 2997.7973 | 2217.2648 | 533.5463 | 52.15% | 38.57% | 9.281% | 2610.1554 | 5028.4016 | 162.9646 | 946.0727 | 1501.1182 | 300.6006 | 1952.101 | 2775.7 | 365 |  | 707 | 365-28AE | 5748.6084 | 3138.453 | 720.2068 | 2997.7973 | 1379.848 | 38.7681 | 2217.2648 | 1225.0587 | 147.8924 | 533.5463 | 306.037 | 143.0724 | 5.4363 | 299.1808 | 139.1047 | 4.6043 | 6.4547 | 3.5663 | 0.43053 | 0.40148 | 2872.5621 | 1371.4439 | 96.8621 | 2595.942 | 1196.92 | 33.1765 | 228.1523 | 126.0562 | 15.2178 | 48.4677 | 2570.0093 | 1623.9367 | 617.9084 | 102.6744 | 43.8234 | 0.98725 | 1982.6578 | 1095.4362 | 132.244 | 484.6771 | 0.0020144 | 0.000922 | 2.34e-05 | 0.0055362 | 0.0031472 | 0.0005536 | 0.0007662 | 5000000 | scaled
365-34R | 103073.8764 | 4917.6341 | 94789.5099 | 3366.7324 | 4.771% | 91.96% | 3.266% | 45288.7544 | 93493.2387 | 56.2599 | 41579.4877 | 3653.0068 | 109.4726 | 85801.0129 | 7582.7533 | 365 |  | 708 | 365-34R | 103073.8764 | 57785.122 | 9580.6377 | 4917.6341 | 2095.5417 | 52.3245 | 94789.5099 | 52322.848 | 6161.5808 | 3366.7324 | 118.893 | 62.6331 | 9.4204 | 12.805 | 2.8639 | 0 | 103.5546 | 57.2359 | 6.8871 | 2.5334 | 8422.753 | 4769.7462 | 839.9997 | 66.2162 | 14.7988 | 0 | 8050.7005 | 4449.1111 | 534.1635 | 305.8363 | 94532.2304 | 52952.7427 | 8731.2175 | 4838.6129 | 2077.879 | 52.3245 | 86635.2548 | 47816.501 | 5620.5302 | 3058.3627 | 0.0076178 | 0.0032982 | 8.36e-05 | 0.0054484 | 0.0030986 | 0.0005448 | 0.004736 | 5000000 | scaled
365-648R | 37113.6899 | 7519.3761 | 27124.9068 | 2469.407 | 20.26% | 73.09% | 6.654% | 16416.1836 | 32712.652 | 39.761 | 15232.7385 | 1143.6841 | 69.4352 | 30328.0907 | 2315.1262 | 365 |  | 709 | 365-648R | 37113.6899 | 20697.5063 | 4401.0379 | 7519.3761 | 3237.6212 | 120.2129 | 27124.9068 | 14990.4781 | 1811.4179 | 2469.407 | 76.7355 | 36.9745 | 7.3003 | 41.9068 | 16.8953 | 3.2403 | 32.9705 | 18.221 | 2.2018 | 1.8581 | 2708.1537 | 1564.4696 | 393.0275 | 217.3909 | 87.6073 | 17.3506 | 2266.4402 | 1252.5397 | 151.3543 | 224.3226 | 34328.8008 | 19096.0623 | 4000.7101 | 7260.0784 | 3133.1186 | 99.622 | 24825.4961 | 13719.7174 | 1657.8619 | 2243.2262 | 0.0065108 | 0.0028194 | 7.22e-05 | 0.0054996 | 0.0031272 | 0.00055 | 0.0035146 | 5000000 | scaled
366-48 | 85177.9907 | 1535.4342 | 81274.1035 | 2368.453 | 1.803% | 95.42% | 2.781% | 37130.8402 | 77362.5262 | 43.7832 | 33753.8002 | 3333.2567 | 91.5662 | 70299.9445 | 6971.0156 | 366 |  | 710 | 366-48 | 85177.9907 | 48047.1505 | 7815.4644 | 1535.4342 | 670.2581 | 17.2041 | 81274.1035 | 45008.4394 | 5429.8073 | 2368.453 | 99.9037 | 56.1205 | 8.3375 | 0 | 0 | 0 | 98.1215 | 54.3383 | 6.5554 | 1.7822 | 7685.233 | 4351.9763 | 714.2174 | 0 | 0 | 0 | 7470.0811 | 4136.8244 | 499.0655 | 215.1519 | 77392.854 | 43639.0537 | 7092.9095 | 1535.4342 | 670.2581 | 17.2041 | 73705.9008 | 40817.2767 | 4924.1864 | 2151.5189 | 0.0047812 | 0.0021422 | 5.44e-05 | 0.0054494 | 0.0031042 | 0.000545 | 0.00334 | 5000000 | scaled
366-559 | 36973.6855 | 179.9285 | 35994.9221 | 798.8349 | 0.4866% | 97.35% | 2.161% | 16189.9408 | 33767.0239 | 21.6772 | 14719.5437 | 1448.7199 | 45.2585 | 30697.0648 | 3024.7006 | 366 |  | 711 | 366-559 | 36973.6855 | 20783.7447 | 3206.6617 | 179.9285 | 77.9271 | 2.0055 | 35994.9221 | 19906.9826 | 2405.8212 | 798.8349 | 49.1013 | 27.4241 | 3.8427 | 0 | 0 | 0 | 48.5002 | 26.823 | 3.2416 | 0.6011 | 3313.9116 | 1865.1917 | 289.2111 | 0 | 0 | 0 | 3241.3449 | 1792.625 | 216.6443 | 72.5667 | 33610.6726 | 18891.1289 | 2913.6079 | 179.9285 | 77.9271 | 2.0055 | 32705.077 | 18087.5347 | 2185.9352 | 725.6671 | 0.0017674 | 0.0007654 | 1.96e-05 | 0.005454 | 0.0031032 | 0.0005454 | 0.0011184 | 5000000 | scaled
368-1054F | 80990.9593 | 159.3874 | 80484.305 | 347.2669 | 0.1968% | 99.37% | 0.4288% | 36025.9751 | 75266.2405 | 44.1995 | 32468.3499 | 3513.4257 | 92.3808 | 67830.4948 | 7343.365 | 368 |  | 712 | 368-1054F | 80990.9593 | 44964.9841 | 5724.7188 | 159.3874 | 69.0371 | 1.7242 | 80484.305 | 44548.6801 | 5375.7277 | 347.2669 | 99.2541 | 55.0545 | 6.8733 | 0 | 0 | 0 | 98.9927 | 54.7932 | 6.6119 | 0.26131 | 7900.4958 | 4387.07 | 557.1308 | 0 | 0 | 0 | 7868.9498 | 4355.5241 | 525.5848 | 31.546 | 72991.2095 | 40522.8595 | 5160.7147 | 159.3874 | 69.0371 | 1.7242 | 72516.3624 | 40138.3628 | 4843.5309 | 315.4596 | 0.00082 | 0.0003552 | 8.8e-06 | 0.0054148 | 0.003083 | 0.0005414 | 0.0005024 | 5000000 | scaled
368-1057F | 9344.984 | 5802.276 | 2576.2932 | 966.4148 | 62.09% | 27.57% | 10.34% | 4248.1824 | 8144.6549 | 181.7501 | 2947.9563 | 1118.476 | 363.6371 | 5511.7791 | 2269.2386 | 368 |  | 713 | 368-1057F | 9344.984 | 5096.8016 | 1200.3291 | 5802.276 | 2702.6623 | 61.9981 | 2576.2932 | 1427.7245 | 171.9162 | 966.4148 | 369.0879 | 187.3378 | 5.4508 | 365.6448 | 185.1055 | 4.5423 | 2.7159 | 1.5051 | 0.18123 | 0.7272 | 2396.0292 | 1277.5532 | 126.7907 | 2102.6721 | 1075.8425 | 25.2834 | 205.5674 | 113.9209 | 13.7175 | 87.7898 | 6579.8668 | 3631.9106 | 1068.0877 | 3333.9592 | 1441.7143 | 32.1724 | 2368.0099 | 1312.2985 | 158.0175 | 877.8978 | 0.0033916 | 0.0015962 | 4.08e-05 | 0.0054678 | 0.0031168 | 0.0005468 | 0.0013706 | 5000000 | scaled
368-21AE | 50816.3193 | 4021.0171 | 44060.1656 | 2735.1366 | 7.913% | 86.7% | 5.382% | 21958.1934 | 45100.0261 | 23.8275 | 20186.4731 | 1747.8928 | 53.0624 | 41380.9011 | 3666.0626 | 368 |  | 714 | 368-21AE | 50816.3193 | 28858.1259 | 5716.2932 | 4021.0171 | 1760.8383 | 43.054 | 44060.1656 | 24362.151 | 2938.1026 | 2735.1366 | 58.5213 | 34.6938 | 5.4589 | 5.4646 | 4.4371 | 0 | 50.9986 | 28.1986 | 3.4008 | 2.0581 | 4174.4403 | 2426.5476 | 508.3778 | 28.2434 | 22.9144 | 0 | 3897.7352 | 2155.1715 | 259.9161 | 248.4617 | 46583.3576 | 26396.8845 | 5202.4565 | 3987.3091 | 1733.4868 | 43.054 | 40111.4317 | 22178.7808 | 2674.7857 | 2484.6168 | 0.0058482 | 0.0025326 | 6.46e-05 | 0.0054236 | 0.0030852 | 0.0005424 | 0.003826 | 5000000 | scaled
368-24 | 131820.2995 | 7180.8367 | 119308.5993 | 5330.8635 | 5.447% | 90.51% | 4.044% | 57896.0994 | 119224.4326 | 56.1509 | 53809.7871 | 4030.1614 | 116.9794 | 110711.4686 | 8395.9845 | 368 |  | 715 | 368-24 | 131820.2995 | 73924.2001 | 12595.8669 | 7180.8367 | 3109.0422 | 80.1769 | 119308.5993 | 65484.2944 | 7184.8265 | 5330.8635 | 129.2306 | 73.0796 | 12.2511 | 0 | 0 | 0 | 125.2193 | 69.0683 | 8.2398 | 4.0113 | 9466.1178 | 5435.9564 | 1070.1332 | 0 | 0 | 0 | 8981.8585 | 4951.6971 | 585.8739 | 484.2593 | 122224.9512 | 68415.1641 | 11513.4825 | 7180.8367 | 3109.0422 | 80.1769 | 110201.5216 | 60463.529 | 6590.7127 | 4842.5929 | 0.012375 | 0.0053574 | 0.0001376 | 0.0053872 | 0.0030596 | 0.0005388 | 0.0074644 | 5000000 | scaled
368-403F | 10478.0521 | 153.5811 | 9921.1182 | 403.3527 | 1.466% | 94.68% | 3.85% | 4533.9486 | 9409.8882 | 4.931 | 4164.4471 | 364.5704 | 10.2661 | 8640.6043 | 759.0178 | 368 |  | 716 | 368-403F | 10478.0521 | 5944.1036 | 1068.1639 | 153.5811 | 66.4416 | 1.732 | 9921.1182 | 5474.3093 | 663.0792 | 403.3527 | 11.3049 | 6.3739 | 1.0388 | 0 | 0 | 0 | 11.0014 | 6.0704 | 0.73528 | 0.30351 | 850.021 | 485.4506 | 91.0032 | 0 | 0 | 0 | 813.3802 | 448.8098 | 54.3624 | 36.6408 | 9616.7262 | 5452.2791 | 976.1219 | 153.5811 | 66.4416 | 1.732 | 9096.7367 | 5019.4291 | 607.9816 | 366.4084 | 0.000752 | 0.0003254 | 8.6e-06 | 0.0054612 | 0.0031006 | 0.0005462 | 0.0005504 | 5000000 | scaled
374-708R | 1730.6333 | 245.9439 | 0 | 1484.6894 | 14.21% | 0% | 85.79% | 138.373 | 243.2103 | 0.0023648 | 138.3581 | 0.012517 | 0.0070943 | 243.1656 | 0.037598 | 374 |  | 717 | 374-708R | 1730.6333 | 1592.2603 | 1487.423 | 245.9439 | 107.5709 | 2.7336 | 0 | 0 | 0 | 1484.6894 | 1.1243 | 1.1219 | 1.1172 | 0.0070943 | 0.0047295 | 0 | 0 | 0 | 0 | 1.1172 | 134.9078 | 134.8953 | 134.8702 | 0.037598 | 0.025081 | 0 | 0 | 0 | 0 | 134.8702 | 1594.6012 | 1456.2431 | 1351.4356 | 245.8992 | 107.5411 | 2.7336 | 0 | 0 | 0 | 1348.702 | 0.0030662 | 0.0013768 | 3.48e-05 | 0 | 0 | 0 | 0.0021408 | 5000000 | scaled
376-491R | 15387.0193 | 13101.6142 | 0 | 2285.4051 | 85.15% | 0% | 14.85% | 5705.5836 | 12924.7535 | 102.7331 | 5136.0368 | 466.8136 | 225.0496 | 11677.724 | 1021.9799 | 376 |  | 718 | 376-491R | 15387.0193 | 9681.4357 | 2462.2658 | 13101.6142 | 7396.0306 | 176.8607 | 0 | 0 | 0 | 2285.4051 | 228.0934 | 125.3603 | 3.0438 | 226.3737 | 123.6406 | 1.3241 | 0 | 0 | 0 | 1.7197 | 1235.5972 | 768.7836 | 213.6173 | 1027.9895 | 561.1758 | 6.0095 | 0 | 0 | 0 | 207.6078 | 13923.3286 | 8787.2918 | 2245.6047 | 11847.251 | 6711.2142 | 169.5271 | 0 | 0 | 0 | 2076.0776 | 0.008556 | 0.0042568 | 0.0001084 | 0 | 0 | 0 | 0.0032234 | 5000000 | scaled
376-527AE | 491.4829 | 383.255 | 0 | 108.2278 | 77.98% | 0% | 22.02% | 92.5611 | 376.154 | 0.564 | 89.0862 | 2.9108 | 1.7495 | 365.3827 | 9.0218 | 376 |  | 719 | 376-527AE | 491.4829 | 398.9218 | 115.3289 | 383.255 | 290.694 | 7.1011 | 0 | 0 | 0 | 108.2278 | 1.831 | 1.267 | 0.081438 | 1.7495 | 1.1855 | 0 | 0 | 0 | 0 | 0.081438 | 18.8533 | 15.9424 | 9.8315 | 9.0218 | 6.1109 | 0 | 0 | 0 | 0 | 9.8315 | 470.7986 | 381.7124 | 105.416 | 372.4837 | 283.3975 | 7.1011 | 0 | 0 | 0 | 98.3149 | 0.0001154 | 8.78e-05 | 2.2e-06 | 0 | 0 | 0 | 0.0001482 | 5000000 | scaled
38-11 | 25705.6833 | 19388.9674 | 0 | 6316.7159 | 75.43% | 0% | 24.57% | 10078.789 | 18987.0918 | 372.5512 | 8635.7675 | 1070.4703 | 682.4492 | 16350.5803 | 1954.0623 | 38 |  | 720 | 38-11 | 25705.6833 | 15626.8943 | 6718.5915 | 19388.9674 | 9310.1785 | 401.8757 | 0 | 0 | 0 | 6316.7159 | 708.8077 | 336.2566 | 26.3586 | 704.0546 | 331.5034 | 21.6054 | 0 | 0 | 0 | 4.7531 | 2594.7692 | 1524.2989 | 640.7069 | 2020.9544 | 950.4841 | 66.8921 | 0 | 0 | 0 | 573.8148 | 22402.1063 | 13766.3388 | 6051.526 | 16663.9584 | 8028.1909 | 313.3781 | 0 | 0 | 0 | 5738.1479 | 0.019648 | 0.0086496 | 0.0002192 | 0 | 0 | 0 | 0.008961 | 5000000 | scaled
380-27 | 22878.0314 | 14504.0417 | 0 | 8373.9897 | 63.4% | 0% | 36.6% | 7330.3473 | 14337.6618 | 224.5547 | 5924.1011 | 1181.6915 | 478.1366 | 11323.5411 | 2535.9841 | 380 |  | 721 | 380-27 | 22878.0314 | 15547.684 | 8540.3696 | 14504.0417 | 7173.6943 | 166.3799 | 0 | 0 | 0 | 8373.9897 | 490.3145 | 265.7598 | 12.1779 | 484.0133 | 259.4586 | 5.8767 | 0 | 0 | 0 | 6.3012 | 3327.5304 | 2145.8389 | 791.5464 | 2566.8315 | 1385.14 | 30.8474 | 0 | 0 | 0 | 760.699 | 19060.1864 | 13136.0853 | 7736.6453 | 11453.1968 | 5529.0957 | 129.6557 | 0 | 0 | 0 | 7606.9896 | 0.026565 | 0.011876 | 0.0003014 | 0 | 0 | 0 | 0.011813 | 5000000 | scaled
381-450F | 501.1327 | 327.8403 | 0 | 173.2924 | 65.42% | 0% | 34.58% | 144.4179 | 327.8252 | 17.9621 | 0.87041 | 125.5854 | 40.7967 | 1.5185 | 285.5099 | 381 |  | 722 | 381-450F | 501.1327 | 356.7148 | 173.3076 | 327.8403 | 183.4224 | 0.015176 | 0 | 0 | 0 | 173.2924 | 40.9271 | 22.965 | 0.1304 | 40.7967 | 22.8346 | 0 | 0 | 0 | 0 | 0.1304 | 301.2519 | 175.6665 | 15.742 | 285.5099 | 159.9245 | 0 | 0 | 0 | 0 | 15.742 | 158.9536 | 158.0832 | 157.4352 | 1.5336 | 0.66323 | 0.015176 | 0 | 0 | 0 | 157.42 | 0.0007406 | 0.0003206 | 8.2e-06 | 0 | 0 | 0 | 0.00025 | 5000000 | scaled
381-451F | 23318.0707 | 20546.0056 | 0 | 2772.0651 | 88.11% | 0% | 11.89% | 11907.5957 | 20159.6283 | 776.4583 | 6045.6 | 5085.5374 | 1282.9188 | 10566.9782 | 8309.7313 | 381 |  | 723 | 381-451F | 23318.0707 | 11410.475 | 3158.4423 | 20546.0056 | 8638.4099 | 386.3773 | 0 | 0 | 0 | 2772.0651 | 1313.5593 | 537.101 | 30.6405 | 1311.4734 | 535.0151 | 28.5546 | 0 | 0 | 0 | 2.0859 | 8780.311 | 3694.7737 | 470.5797 | 8528.4947 | 3442.9574 | 218.7634 | 0 | 0 | 0 | 251.8163 | 13224.2003 | 7178.6003 | 2657.2221 | 10706.0374 | 4660.4374 | 139.0592 | 0 | 0 | 0 | 2518.1629 | 0.01478 | 0.0064378 | 0.000164 | 0 | 0 | 0 | 0.0038794 | 5000000 | scaled
381-48 | 7913.3657 | 6215.881 | 0 | 1697.4847 | 78.55% | 0% | 21.45% | 3164.5336 | 6113.4197 | 331.9177 | 732.4359 | 2100.1801 | 647.7039 | 1268.5396 | 4197.1763 | 381 |  | 724 | 381-48 | 7913.3657 | 4748.8321 | 1799.946 | 6215.881 | 3051.3474 | 102.4613 | 0 | 0 | 0 | 1697.4847 | 661.893 | 329.9753 | 14.1892 | 660.6157 | 328.698 | 12.9119 | 0 | 0 | 0 | 1.2773 | 4430.2301 | 2330.05 | 233.0538 | 4276.0294 | 2175.8494 | 78.8531 | 0 | 0 | 0 | 154.2007 | 2821.2426 | 2088.8067 | 1552.703 | 1279.2359 | 546.8 | 10.6963 | 0 | 0 | 0 | 1542.0067 | 0.0044918 | 0.0019454 | 4.9e-05 | 0 | 0 | 0 | 0.002392 | 5000000 | scaled
381-49 | 29.6657 | 0.036275 | 0 | 29.6295 | 0.1223% | 0% | 99.88% | 0.020729 | 0.035905 | 0 | 0.020729 | 0 | 0 | 0.035905 | 0 | 381 |  | 725 | 381-49 | 29.6657 | 29.645 | 29.6298 | 0.036275 | 0.015547 | 0.00037016 | 0 | 0 | 0 | 29.6295 | 0.022295 | 0.022295 | 0.022295 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022295 | 2.6916 | 2.6916 | 2.6916 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6916 | 26.9519 | 26.9311 | 26.916 | 0.036275 | 0.015547 | 0.00037016 | 0 | 0 | 0 | 26.9156 | 1.96e-05 | 8.4e-06 | 2e-07 | 0 | 0 | 0 | 4.4e-05 | 5000000 | scaled
386-25R | 143656.9906 | 50796.5184 | 91225.2725 | 1635.1996 | 35.36% | 63.5% | 1.138% | 67149.0171 | 135501.6575 | 3215.7149 | 39293.4869 | 24639.8153 | 6121.8719 | 81321.2997 | 48058.486 | 386 |  | 726 | 386-25R | 143656.9906 | 76507.9735 | 8155.333 | 50796.5184 | 24392.9139 | 433.9011 | 91225.2725 | 50479.86 | 6086.2323 | 1635.1996 | 6190.8884 | 2975.1735 | 69.0165 | 6060.711 | 2902.5898 | 59.1832 | 128.947 | 71.3533 | 8.6029 | 1.2304 | 49079.0186 | 24439.2033 | 1020.5326 | 40970.773 | 19886.128 | 340.9463 | 7959.7029 | 4404.5326 | 531.0436 | 148.5427 | 88387.0836 | 49093.5967 | 7065.7839 | 3765.0344 | 1604.1961 | 33.7716 | 83136.6226 | 46003.974 | 5546.5858 | 1485.4266 | 0.0060984 | 0.0026398 | 6.76e-05 | 0.010699 | 0.0060908 | 0.0010698 | 0.0022856 | 5000000 | scaled
387-11 | 2227280.8448 | 1988427.9219 | 229992.2849 | 8860.6381 | 89.28% | 10.33% | 0.3978% | 1233596.2188 | 2181629.9537 | 134410.0434 | 99150.8799 | 1000035.2955 | 233973.6205 | 204466.989 | 1743189.3443 | 387 |  | 727 | 387-11 | 2227280.8448 | 993684.6261 | 45650.8911 | 1988427.9219 | 856468.6302 | 18414.5999 | 229992.2849 | 128355.3578 | 18375.6532 | 8860.6381 | 236236.7227 | 101826.6793 | 2263.1022 | 235845.1408 | 101605.1967 | 2225.6814 | 384.9145 | 214.8152 | 30.7534 | 6.6673 | 1761624.9369 | 761589.6414 | 18435.5926 | 1741189.7152 | 749829.3408 | 16062.2863 | 19630.3153 | 10955.3942 | 1568.3999 | 804.9064 | 229419.1853 | 130268.3054 | 24952.1963 | 11393.0659 | 5034.0927 | 126.6321 | 209977.0551 | 117185.1484 | 16776.4999 | 8049.0643 | 0.034358 | 0.014997 | 0.0003802 | 0.044652 | 0.025353 | 0.0044652 | 0.012486 | 5000000 | scaled
387-15 | 1455052.7826 | 1295208.7698 | 156033.4941 | 3810.5187 | 89.01% | 10.72% | 0.2619% | 488437.1969 | 1426964.0658 | 33736.1387 | 65043.7032 | 389657.3549 | 101628.1098 | 135570.0074 | 1189765.9486 | 387 |  | 728 | 387-15 | 1455052.7826 | 966615.5858 | 28088.7168 | 1295208.7698 | 875633.6873 | 11811.264 | 156033.4941 | 87171.3798 | 12466.9342 | 3810.5187 | 102665.9768 | 68929.8381 | 1037.867 | 102351.5995 | 68752.9392 | 1010.1104 | 311.5101 | 174.0316 | 24.8894 | 2.8673 | 1201964.6081 | 812307.2532 | 12198.6595 | 1187584.5695 | 804120.7773 | 10731.2145 | 14033.8885 | 7840.3258 | 1121.2949 | 346.1501 | 150422.1977 | 85378.4945 | 14852.1903 | 5272.6008 | 2759.9708 | 69.9391 | 141688.0956 | 79157.0224 | 11320.7499 | 3461.5013 | 0.022332 | 0.013524 | 0.0003442 | 0.044888 | 0.025515 | 0.0044888 | 0.0053808 | 5000000 | scaled
390-15 | 260996.2763 | 1649.7191 | 258285.982 | 1060.5752 | 0.6321% | 98.96% | 0.4064% | 114108.7538 | 236861.9736 | 235.8868 | 102798.9974 | 11073.8696 | 478.1009 | 213420.8311 | 22963.0417 | 390 |  | 729 | 390-15 | 260996.2763 | 146887.5225 | 24134.3027 | 1649.7191 | 779.4813 | 34.3909 | 258285.982 | 145047.466 | 23039.3365 | 1060.5752 | 518.1282 | 282.2413 | 40.0273 | 127.356 | 62.4428 | 4.4432 | 389.9741 | 219.0005 | 34.786 | 0.79805 | 25273.3566 | 14199.487 | 2310.315 | 603.9205 | 303.46 | 22.0301 | 24573.0927 | 13799.6836 | 2191.9415 | 96.3434 | 235204.7915 | 132405.7942 | 21783.9604 | 918.4426 | 413.5784 | 7.9175 | 233322.9151 | 131028.7819 | 20812.609 | 963.4338 | 0.003011 | 0.0013036 | 3.36e-05 | 0.095131 | 0.053915 | 0.009513 | 0.0015128 | 5000000 | scaled
390-18 | 318844.9288 | 52868.043 | 263180.4115 | 2796.4743 | 16.58% | 82.54% | 0.8771% | 145660.4606 | 292211.8499 | 4095.625 | 101656.3488 | 39908.4867 | 7147.4787 | 210750.1596 | 74314.2116 | 390 |  | 730 | 390-18 | 318844.9288 | 173184.4682 | 26633.0789 | 52868.043 | 22603.7144 | 367.5605 | 263180.4115 | 147784.2795 | 23469.0441 | 2796.4743 | 7224.1779 | 3128.5528 | 76.6992 | 6914.1264 | 2953.5263 | 47.1338 | 307.9472 | 172.9223 | 27.4611 | 2.1043 | 77884.6214 | 37976.1347 | 3570.4098 | 43718.3084 | 18679.2637 | 292.2576 | 33912.2794 | 19042.8374 | 3024.1186 | 254.0336 | 233736.1295 | 132079.7806 | 22985.9699 | 2235.6082 | 970.9244 | 28.1691 | 228960.1849 | 128568.5198 | 20417.4643 | 2540.3364 | 0.010116 | 0.0043792 | 0.000112 | 0.094768 | 0.053702 | 0.0094768 | 0.0038964 | 5000000 | scaled
390-346AE | 137769.2384 | 42120.5876 | 94470.1108 | 1178.5399 | 30.57% | 68.57% | 0.8554% | 63742.6403 | 127831.8703 | 2030.7818 | 35662.5405 | 26049.318 | 3816.768 | 73988.5545 | 50026.5479 | 390 |  | 731 | 390-346AE | 137769.2384 | 74026.5981 | 9937.3681 | 42120.5876 | 19791.9136 | 330.0754 | 94470.1108 | 53056.1445 | 8428.7527 | 1178.5399 | 3861.1015 | 1830.3197 | 44.3335 | 3747.2187 | 1765.9722 | 33.365 | 112.996 | 63.4606 | 10.0817 | 0.88681 | 51646.6097 | 25597.2917 | 1620.0619 | 37843.983 | 17798.5509 | 291.0652 | 13695.5674 | 7691.6815 | 1221.9373 | 107.0594 | 82261.5272 | 46598.9867 | 8272.9727 | 529.386 | 227.3905 | 5.6452 | 80661.5474 | 45301.0024 | 7196.7338 | 1070.5937 | 0.0046974 | 0.0020334 | 5.18e-05 | 0.095301 | 0.05401 | 0.00953 | 0.00161 | 5000000 | scaled
392-23F | 466525.0162 | 4305.6083 | 460091.3755 | 2128.0323 | 0.9229% | 98.62% | 0.4561% | 203826.1192 | 423365.526 | 724.1381 | 169401.6355 | 33700.3457 | 1372.3844 | 352406.2172 | 69586.9244 | 392 |  | 732 | 392-23F | 466525.0162 | 262698.897 | 43159.4902 | 4305.6083 | 1892.9815 | 81.6152 | 460091.3755 | 258677.8832 | 40949.8427 | 2128.0323 | 1458.6298 | 734.4917 | 86.2454 | 658.6282 | 284.0046 | 13.5836 | 798.4003 | 448.8859 | 71.0606 | 1.6013 | 76388.6989 | 42688.3533 | 6801.7745 | 2561.3755 | 1095.6776 | 54.7619 | 73634.0115 | 41399.3638 | 6553.7007 | 193.3119 | 388677.6874 | 219276.052 | 36271.4702 | 1085.6046 | 513.2993 | 13.2698 | 385658.9637 | 216829.6335 | 34325.0814 | 1933.1191 | 0.0069098 | 0.0030334 | 7.72e-05 | 0.092679 | 0.052589 | 0.0092678 | 0.0030016 | 5000000 | scaled
393-14R | 924804.0867 | 173746.3064 | 749312.1443 | 1745.6359 | 18.79% | 81.02% | 0.1888% | 413606.923 | 855685.1895 | 14022.6082 | 300774.5511 | 98809.7637 | 28221.7581 | 628492.1791 | 198971.2523 | 393 |  | 733 | 393-14R | 924804.0867 | 511197.1636 | 69118.8972 | 173746.3064 | 88257.1835 | 830.9915 | 749312.1443 | 421194.3442 | 66542.2698 | 1745.6359 | 28448.3473 | 14425.7391 | 226.5893 | 27368.9732 | 13818.4391 | 129.5391 | 1078.0606 | 605.9865 | 95.7366 | 1.3135 | 205340.3669 | 106530.6032 | 6369.1146 | 142082.643 | 70903.4925 | 607.0532 | 63099.1491 | 35468.536 | 5603.4867 | 158.5748 | 691015.3724 | 390240.8213 | 62523.1933 | 4294.6902 | 3535.2519 | 94.3992 | 685134.9346 | 385119.8218 | 60843.0465 | 1585.7476 | 0.0081352 | 0.0042842 | 0.0001098 | 0.090185 | 0.051163 | 0.0090184 | 0.002473 | 5000000 | scaled
394-422F | 314150.6013 | 1036.7268 | 312037.9007 | 1075.9737 | 0.33% | 99.33% | 0.3425% | 136947.2738 | 285343.6785 | 226.0445 | 120721.0181 | 16000.2112 | 461.2164 | 251575.2651 | 33307.197 | 394 |  | 734 | 394-422F | 314150.6013 | 177203.3275 | 28806.9228 | 1036.7268 | 456.5324 | 8.2481 | 312037.9007 | 175670.8214 | 27722.7009 | 1075.9737 | 503.1158 | 277.0713 | 41.8994 | 42.0489 | 17.1465 | 0.19864 | 460.2573 | 259.1152 | 40.8911 | 0.80964 | 36632.0418 | 20631.8306 | 3324.8448 | 222.4222 | 91.2598 | 1.0095 | 36311.8774 | 20442.8286 | 3226.0931 | 97.7422 | 277015.4437 | 156294.4256 | 25440.1786 | 772.2558 | 348.1262 | 7.04 | 275265.7661 | 154968.8775 | 24455.7167 | 977.4219 | 0.0030292 | 0.0013114 | 3.34e-05 | 0.090812 | 0.051601 | 0.0090812 | 0.0014702 | 5000000 | scaled
395-33R | 396975.6503 | 552.3261 | 395928.9695 | 494.3547 | 0.1391% | 99.74% | 0.1245% | 173419.2354 | 361324.3136 | 263.7264 | 159207.7547 | 13947.7543 | 548.071 | 331729.6138 | 29046.6288 | 395 |  | 735 | 395-33R | 396975.6503 | 223556.4148 | 35651.3367 | 552.3261 | 335.727 | 8.0779 | 395928.9695 | 222726.3332 | 35148.9041 | 494.3547 | 601.3236 | 337.5972 | 53.2525 | 5.2876 | 2.1397 | 0 | 595.664 | 335.0855 | 52.8805 | 0.37199 | 31918.7737 | 17971.0194 | 2872.1449 | 26.9217 | 10.8955 | 0 | 31846.9445 | 17915.2164 | 2827.2374 | 44.9075 | 364455.553 | 205247.7982 | 32725.9392 | 520.1168 | 322.6918 | 8.0779 | 363486.361 | 204476.0313 | 32268.7861 | 449.0752 | 0.0015924 | 0.000816 | 2.06e-05 | 0.089819 | 0.051003 | 0.0089818 | 0.0006908 | 5000000 | scaled
396-699R | 3136951.6678 | 2766176.8265 | 357592.253 | 13182.5882 | 88.18% | 11.4% | 0.4202% | 1635393.1553 | 3059595.2076 | 138073.0997 | 147522.9424 | 1349797.1132 | 254862.1343 | 305964.5751 | 2498768.4982 | 396 |  | 736 | 396-699R | 3136951.6678 | 1501558.5125 | 77356.4602 | 2766176.8265 | 1287213.8111 | 32432.9653 | 357592.253 | 201162.1132 | 31740.9066 | 13182.5882 | 257940.4392 | 119867.3395 | 3078.3049 | 257372.4178 | 119543.462 | 3018.8467 | 558.1019 | 313.958 | 49.5387 | 9.9195 | 2531928.1097 | 1182130.9965 | 33159.6115 | 2501047.9817 | 1164235.6444 | 29327.3829 | 29682.6127 | 16697.8368 | 2634.7132 | 1197.5153 | 347083.1189 | 199560.1765 | 41118.5438 | 7756.427 | 3434.7048 | 86.7357 | 327351.5384 | 184150.3183 | 29056.6546 | 11975.1534 | 0.048558 | 0.022079 | 0.0005606 | 0.089609 | 0.050884 | 0.008961 | 0.01847 | 5000000 | scaled
397-39R | 3540.0842 | 2580.1918 | 0 | 959.8925 | 72.89% | 0% | 27.11% | 1451.7186 | 2552.1866 | 17.2651 | 1344.5736 | 89.8798 | 33.5334 | 2344.1729 | 174.4803 | 397 |  | 737 | 397-39R | 3540.0842 | 2088.3656 | 987.8976 | 2580.1918 | 1128.4732 | 28.0052 | 0 | 0 | 0 | 959.8925 | 34.5887 | 17.3236 | 1.0553 | 33.8664 | 16.6013 | 0.33304 | 0 | 0 | 0 | 0.72229 | 263.4066 | 173.5268 | 88.9263 | 176.2093 | 86.3295 | 1.729 | 0 | 0 | 0 | 87.1973 | 3242.089 | 1897.5153 | 897.916 | 2370.1161 | 1025.5424 | 25.9431 | 0 | 0 | 0 | 871.9729 | 0.0022316 | 0.0009666 | 2.5e-05 | 0 | 0 | 0 | 0.0013344 | 5000000 | scaled
397-550F | 4541.956 | 1168.7378 | 0 | 3373.2181 | 25.73% | 0% | 74.27% | 667.8542 | 1159.0475 | 29.3477 | 487.1882 | 151.3183 | 50.9436 | 845.824 | 262.2799 | 397 |  | 738 | 397-550F | 4541.956 | 3874.1017 | 3382.9084 | 1168.7378 | 500.8836 | 9.6903 | 0 | 0 | 0 | 3373.2181 | 53.5871 | 24.2394 | 2.6435 | 51.0489 | 21.7012 | 0.10523 | 0 | 0 | 0 | 2.5382 | 569.2438 | 417.9255 | 306.9639 | 262.8184 | 111.5 | 0.53846 | 0 | 0 | 0 | 306.4254 | 3919.125 | 3431.9368 | 3073.3011 | 854.8706 | 367.6824 | 9.0466 | 0 | 0 | 0 | 3064.2544 | 0.0089348 | 0.003869 | 9.78e-05 | 0 | 0 | 0 | 0.0047478 | 5000000 | scaled
400-1019 | 13837.6389 | 6382.6154 | 0 | 7455.0235 | 46.13% | 0% | 53.87% | 3619.9345 | 6313.706 | 14.5449 | 3530.5184 | 74.8712 | 25.0358 | 6159.8341 | 128.8361 | 400 |  | 739 | 400-1019 | 13837.6389 | 10217.7044 | 7523.933 | 6382.6154 | 2762.6809 | 68.9094 | 0 | 0 | 0 | 7455.0235 | 30.7211 | 16.1762 | 5.6853 | 25.1114 | 10.5666 | 0.075672 | 0 | 0 | 0 | 5.6097 | 806.4545 | 731.5832 | 677.6183 | 129.235 | 54.3638 | 0.3989 | 0 | 0 | 0 | 677.2194 | 13000.4634 | 9469.945 | 6840.6293 | 6228.2689 | 2697.7506 | 68.4348 | 0 | 0 | 0 | 6772.1944 | 0.025905 | 0.011218 | 0.0002848 | 0 | 0 | 0 | 0.010572 | 5000000 | scaled
401-39R | 323232.2781 | 10321.3355 | 312572.1312 | 338.8114 | 3.193% | 96.7% | 0.1048% | 143588.935 | 299332.5052 | 788.6767 | 128350.4202 | 14449.8381 | 1763.7828 | 266850.8807 | 30717.8416 | 401 |  | 740 | 401-39R | 323232.2781 | 179643.3431 | 23899.7729 | 10321.3355 | 5843.9423 | 138.1659 | 312572.1312 | 173460.5893 | 23422.7957 | 338.8114 | 1816.8324 | 1028.1557 | 53.0496 | 1374.6066 | 782.6309 | 19.6752 | 441.9709 | 245.2699 | 33.1194 | 0.25494 | 32801.59 | 18351.7519 | 2083.7484 | 6579.9034 | 3786.4394 | 90.3378 | 26190.9088 | 14534.5346 | 1962.6328 | 30.7779 | 288613.8557 | 160263.4355 | 21762.975 | 2366.8255 | 1274.8721 | 28.1528 | 285939.2515 | 158680.7848 | 21427.0435 | 307.7786 | 0.0018622 | 0.0010672 | 2.72e-05 | 0.029517 | 0.016754 | 0.0029518 | 0.0004928 | 5000000 | scaled
401-684R | 1596.1402 | 996.3521 | 567.76 | 32.028 | 62.42% | 35.57% | 2.007% | 757.8564 | 1521.5311 | 102.2147 | 199.3067 | 456.335 | 203.0055 | 414.5604 | 903.9651 | 401 |  | 741 | 401-684R | 1596.1402 | 838.2838 | 74.6091 | 996.3521 | 490.8977 | 0.0066628 | 567.76 | 315.358 | 42.5744 | 32.028 | 203.3214 | 101.1067 | 0.31587 | 199.4063 | 98.9214 | 0 | 3.891 | 2.1612 | 0.29177 | 0.0241 | 915.611 | 459.2761 | 11.6459 | 796.1948 | 391.6538 | 0 | 116.5068 | 64.7128 | 8.7364 | 2.9094 | 477.2077 | 277.901 | 62.6473 | 0.75096 | 0.32249 | 0.0066628 | 447.3623 | 248.484 | 33.5461 | 29.0945 | 0.0001548 | 6.7e-05 | 1.8e-06 | 0.030193 | 0.017151 | 0.0030192 | 4.74e-05 | 5000000 | scaled
402-30AE | 8256.9747 | 5122.3593 | 0 | 3134.6153 | 62.04% | 0% | 37.96% | 2885.731 | 5071.0593 | 184.6866 | 1706.1813 | 994.8631 | 321.0088 | 3015.0247 | 1735.0259 | 402 |  | 742 | 402-30AE | 8256.9747 | 5371.2437 | 3185.9153 | 5122.3593 | 2236.6283 | 51.3 | 0 | 0 | 0 | 3134.6153 | 326.3153 | 141.6286 | 5.3065 | 323.9566 | 139.2699 | 2.9478 | 0 | 0 | 0 | 2.3587 | 2035.4798 | 1040.6167 | 300.4539 | 1750.7292 | 755.8661 | 15.7033 | 0 | 0 | 0 | 284.7506 | 5895.1796 | 4188.9983 | 2880.1549 | 3047.6736 | 1341.4923 | 32.6489 | 0 | 0 | 0 | 2847.506 | 0.0086352 | 0.0037392 | 9.5e-05 | 0 | 0 | 0 | 0.0043738 | 5000000 | scaled
402-819F | 87.2852 | 14.4092 | 0 | 72.876 | 16.51% | 0% | 83.49% | 9.3987 | 14.3337 | 0.87575 | 4.0273 | 4.4957 | 1.1887 | 7.0289 | 6.1161 | 402 |  | 743 | 402-819F | 87.2852 | 77.8865 | 72.9515 | 14.4092 | 5.0105 | 0.075512 | 0 | 0 | 0 | 72.876 | 1.2435 | 0.36777 | 0.054837 | 1.1887 | 0.31294 | 0 | 0 | 0 | 0 | 0.054837 | 12.7362 | 8.2405 | 6.6201 | 6.1161 | 1.6204 | 0 | 0 | 0 | 0 | 6.6201 | 73.3055 | 69.2782 | 66.2766 | 7.1044 | 3.0771 | 0.075512 | 0 | 0 | 0 | 66.2011 | 0.0002258 | 9.78e-05 | 2.4e-06 | 0 | 0 | 0 | 0.0001044 | 5000000 | scaled
402-820F | 12389.5149 | 10944.1422 | 0 | 1445.3726 | 88.33% | 0% | 11.67% | 6195.7003 | 10826.3688 | 17.888 | 6086.64 | 91.1723 | 34.2857 | 10617.3169 | 174.7661 | 402 |  | 744 | 402-820F | 12389.5149 | 6193.8145 | 1563.1461 | 10944.1422 | 4748.4419 | 117.7735 | 0 | 0 | 0 | 1445.3726 | 35.4896 | 17.6016 | 1.2039 | 34.402 | 16.514 | 0.11627 | 0 | 0 | 0 | 1.0876 | 306.6586 | 215.4862 | 131.8924 | 175.3599 | 84.1876 | 0.59381 | 0 | 0 | 0 | 131.2986 | 12047.3667 | 5960.7267 | 1430.0498 | 10734.3803 | 4647.7403 | 117.0634 | 0 | 0 | 0 | 1312.9864 | 0.0040498 | 0.0017532 | 4.44e-05 | 0 | 0 | 0 | 0.0020234 | 5000000 | scaled
403-11F | 136.7359 | 68.0007 | 0 | 68.7352 | 49.73% | 0% | 50.27% | 38.9277 | 67.2974 | 0.46901 | 36.0591 | 2.3995 | 0.71731 | 62.9099 | 3.6702 | 403 |  | 745 | 403-11F | 136.7359 | 97.8082 | 69.4385 | 68.0007 | 29.073 | 0.7033 | 0 | 0 | 0 | 68.7352 | 0.76903 | 0.30002 | 0.051721 | 0.71731 | 0.2483 | 0 | 0 | 0 | 0 | 0.051721 | 9.9141 | 7.5146 | 6.244 | 3.6702 | 1.2707 | 0 | 0 | 0 | 0 | 6.244 | 126.0527 | 89.9936 | 63.1428 | 63.6132 | 27.5541 | 0.7033 | 0 | 0 | 0 | 62.4395 | 0.000181 | 7.84e-05 | 2e-06 | 0 | 0 | 0 | 9.62e-05 | 5000000 | scaled
403-15F | 1608.0745 | 1476.9221 | 0 | 131.1524 | 91.84% | 0% | 8.156% | 391.4543 | 1459.6653 | 45.3614 | 0 | 346.093 | 169.7744 | 0 | 1289.8909 | 403 |  | 746 | 403-15F | 1608.0745 | 1216.6201 | 148.4091 | 1476.9221 | 1085.4677 | 17.2567 | 0 | 0 | 0 | 131.1524 | 171.9373 | 126.576 | 2.1629 | 171.8386 | 126.4773 | 2.0642 | 0 | 0 | 0 | 0.098688 | 1316.9974 | 970.9044 | 27.1065 | 1305.0834 | 958.9905 | 15.1925 | 0 | 0 | 0 | 11.914 | 119.1397 | 119.1397 | 119.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1397 | 0.0008822 | 0.0006704 | 1.7e-05 | 0 | 0 | 0 | 0.0001888 | 5000000 | scaled
403-9F | 451.6457 | 55.2052 | 0 | 396.4405 | 12.22% | 0% | 87.78% | 30.9237 | 54.6152 | 0.18682 | 29.7846 | 0.95228 | 0.4363 | 51.9481 | 2.2308 | 403 |  | 747 | 403-9F | 451.6457 | 420.722 | 397.0305 | 55.2052 | 24.2815 | 0.59003 | 0 | 0 | 0 | 396.4405 | 0.73461 | 0.54779 | 0.29831 | 0.4363 | 0.24948 | 0 | 0 | 0 | 0 | 0.29831 | 38.2437 | 37.2914 | 36.0129 | 2.2308 | 1.2785 | 0 | 0 | 0 | 0 | 36.0129 | 412.6674 | 382.8828 | 360.7193 | 52.5381 | 22.7535 | 0.59003 | 0 | 0 | 0 | 360.1293 | 0.0016134 | 0.0006986 | 1.8e-05 | 0 | 0 | 0 | 0.0005758 | 5000000 | scaled
404-6AE | 2525.4032 | 501.7087 | 0 | 2023.6945 | 19.87% | 0% | 80.13% | 286.722 | 496.4968 | 7.8928 | 238.4916 | 40.3376 | 13.1426 | 416.1792 | 67.175 | 404 |  | 748 | 404-6AE | 2525.4032 | 2238.6812 | 2028.9064 | 501.7087 | 214.9867 | 5.2119 | 0 | 0 | 0 | 2023.6945 | 14.771 | 6.8782 | 1.6284 | 13.2482 | 5.3554 | 0.10563 | 0 | 0 | 0 | 1.5228 | 251.55 | 211.2124 | 184.375 | 67.7162 | 27.3786 | 0.54117 | 0 | 0 | 0 | 183.8338 | 2259.0823 | 2020.5906 | 1842.9031 | 420.7443 | 182.2527 | 4.5651 | 0 | 0 | 0 | 1838.3379 | 0.0047698 | 0.0020658 | 5.2e-05 | 0 | 0 | 0 | 0.002818 | 5000000 | scaled
409-1155R | 15855.0133 | 12580.1449 | 0 | 3274.8684 | 79.34% | 0% | 20.66% | 7023.597 | 12437.247 | 10.5465 | 6959.1153 | 53.9352 | 17.8492 | 12328.1263 | 91.2715 | 409 |  | 749 | 409-1155R | 15855.0133 | 8831.4162 | 3417.7662 | 12580.1449 | 5556.5478 | 142.8978 | 0 | 0 | 0 | 3274.8684 | 20.5744 | 10.0279 | 2.7251 | 18.1101 | 7.5637 | 0.26091 | 0 | 0 | 0 | 2.4642 | 390.097 | 336.1618 | 298.8255 | 92.6058 | 38.6705 | 1.3342 | 0 | 0 | 0 | 297.4913 | 15444.3418 | 8485.2265 | 3116.2156 | 12469.429 | 5510.3136 | 141.3027 | 0 | 0 | 0 | 2974.9129 | 0.0083154 | 0.0036232 | 9.22e-05 | 0 | 0 | 0 | 0.0045708 | 5000000 | scaled
409-38R | 5310.573 | 2996.5168 | 0 | 2314.0562 | 56.43% | 0% | 43.57% | 1699.1737 | 2964.7488 | 7.6417 | 1652.3268 | 39.2052 | 13.3944 | 2882.6216 | 68.7329 | 409 |  | 750 | 409-38R | 5310.573 | 3611.3993 | 2345.8242 | 2996.5168 | 1297.3431 | 31.768 | 0 | 0 | 0 | 2314.0562 | 15.142 | 7.5002 | 1.7476 | 13.4007 | 5.759 | 0.006306 | 0 | 0 | 0 | 1.7413 | 278.977 | 239.7718 | 210.2442 | 68.7666 | 29.5614 | 0.033739 | 0 | 0 | 0 | 210.2105 | 5016.454 | 3364.1273 | 2133.8325 | 2914.3495 | 1262.0228 | 31.7279 | 0 | 0 | 0 | 2102.1045 | 0.0057398 | 0.0024852 | 6.2e-05 | 0 | 0 | 0 | 0.0032462 | 5000000 | scaled
41-43 | 19884.9596 | 9811.7644 | 0 | 10073.1953 | 49.34% | 0% | 50.66% | 5351.4323 | 9698.9093 | 7.4082 | 5322.4712 | 21.5529 | 15.3307 | 9638.9936 | 44.5851 | 41 |  | 751 | 41-43 | 19884.9596 | 14533.5274 | 10186.0503 | 9811.7644 | 4460.3321 | 112.855 | 0 | 0 | 0 | 10073.1953 | 22.9628 | 15.5547 | 7.6322 | 15.3831 | 7.9749 | 0.052411 | 0 | 0 | 0 | 7.5798 | 959.7926 | 938.2397 | 915.2075 | 44.7366 | 23.1837 | 0.1515 | 0 | 0 | 0 | 915.056 | 18902.2042 | 13579.733 | 9263.2107 | 9751.6447 | 4429.1735 | 112.6511 | 0 | 0 | 0 | 9150.5595 | 0.02512 | 0.011163 | 0.0002828 | 0 | 0 | 0 | 0.014143 | 5000000 | scaled
41-44AE | 4071.6593 | 2007.9244 | 0 | 2063.7349 | 49.31% | 0% | 50.69% | 1149.1387 | 1987.0455 | 14.146 | 1061.8964 | 73.0963 | 24.0479 | 1838.6781 | 124.3195 | 41 |  | 752 | 41-44AE | 4071.6593 | 2922.5206 | 2084.6138 | 2007.9244 | 858.7857 | 20.8789 | 0 | 0 | 0 | 2063.7349 | 25.6784 | 11.5325 | 1.6305 | 24.1255 | 9.9796 | 0.077643 | 0 | 0 | 0 | 1.5529 | 312.2047 | 239.1084 | 187.8852 | 124.7336 | 51.6373 | 0.41412 | 0 | 0 | 0 | 187.4711 | 3733.7762 | 2671.8798 | 1895.098 | 1859.0652 | 797.1688 | 20.3871 | 0 | 0 | 0 | 1874.711 | 0.004962 | 0.0021488 | 5.48e-05 | 0 | 0 | 0 | 0.0028796 | 5000000 | scaled
410-50R | 1314332.5587 | 1306248.6177 | 0 | 8083.941 | 99.38% | 0% | 0.6151% | 742928.3162 | 1293069.8804 | 116147.7686 | 4189.3584 | 622591.1893 | 202126.7839 | 7312.0091 | 1083631.0875 | 410 |  | 753 | 410-50R | 1314332.5587 | 571404.2425 | 21262.6783 | 1306248.6177 | 563320.3014 | 13178.7372 | 0 | 0 | 0 | 8083.941 | 204195.3767 | 88047.6081 | 2068.5928 | 204189.2938 | 88041.5252 | 2062.5099 | 0 | 0 | 0 | 6.0829 | 1095400.1841 | 472808.9948 | 11769.0967 | 1094665.8334 | 472074.6441 | 11034.7459 | 0 | 0 | 0 | 734.3507 | 14736.9979 | 10547.6395 | 7424.9888 | 7393.4905 | 3204.1321 | 81.4814 | 0 | 0 | 0 | 7343.5074 | 0.032645 | 0.014249 | 0.0003618 | 0 | 0 | 0 | 0.011393 | 5000000 | scaled
411-1873R | 1857539.278 | 1817298.243 | 33376.1103 | 6864.9247 | 97.83% | 1.797% | 0.3696% | 990625.5094 | 1824662.4778 | 74715.3877 | 21920.3083 | 893989.8134 | 137176.9237 | 44830.1248 | 1642655.4294 | 411 |  | 754 | 411-1873R | 1857539.278 | 866913.7686 | 32876.8001 | 1817298.243 | 841573.3757 | 23786.1415 | 33376.1103 | 18475.4682 | 2225.7339 | 6864.9247 | 138979.7544 | 64264.3667 | 1802.8307 | 138925.0138 | 64231.7587 | 1794.3591 | 49.575 | 27.4424 | 3.306 | 5.1656 | 1665250.0046 | 771260.1912 | 22594.5752 | 1661763.4138 | 769051.7657 | 21780.0391 | 2862.9763 | 1584.811 | 190.9217 | 623.6145 | 53309.5189 | 31389.2107 | 8479.3942 | 16609.8154 | 8289.8513 | 211.7433 | 30463.5589 | 16863.2147 | 2031.5062 | 6236.1446 | 0.026363 | 0.011919 | 0.0003038 | 0.01079 | 0.0061448 | 0.001079 | 0.0096678 | 5000000 | scaled
411-30R | 6370041.441 | 6272317.8666 | 80399.7124 | 17323.8619 | 98.47% | 1.262% | 0.272% | 3453858.0099 | 6268895.6301 | 325999.4333 | 40216.8296 | 3087641.747 | 591516.4083 | 82062.7167 | 5595316.5051 | 411 |  | 755 | 411-30R | 6370041.441 | 2916183.4311 | 101145.8109 | 6272317.8666 | 2854389.0528 | 78458.771 | 80399.7124 | 44470.5165 | 5363.178 | 17323.8619 | 599026.9454 | 273027.5121 | 7510.5372 | 598887.999 | 272944.833 | 7489.1025 | 125.9108 | 69.6435 | 8.3991 | 13.0356 | 5668165.9192 | 2580524.1722 | 72849.414 | 5659594.942 | 2575080.1481 | 70808.9399 | 6997.2657 | 3870.3126 | 466.7626 | 1573.7115 | 102848.5764 | 62631.7468 | 20785.8597 | 13834.9257 | 6364.0717 | 160.7287 | 73276.5359 | 40530.5603 | 4888.0163 | 15737.1148 | 0.067932 | 0.031268 | 0.0007946 | 0.01073 | 0.0061058 | 0.001073 | 0.024431 | 5000000 | scaled
411-47R | 1350406.1737 | 1296038.94 | 45124.2525 | 9242.9812 | 95.97% | 3.342% | 0.6845% | 714338.8208 | 1318272.299 | 68557.9404 | 32004.8883 | 613775.9922 | 126377.8449 | 69448.5742 | 1122445.88 | 411 |  | 756 | 411-47R | 1350406.1737 | 636067.3529 | 32133.8747 | 1296038.94 | 601874.3912 | 19880.8243 | 45124.2525 | 24949.9806 | 3010.0692 | 9242.9812 | 128335.9242 | 59777.9839 | 1958.0793 | 128259.4235 | 59732.5758 | 1946.4852 | 69.5456 | 38.453 | 4.6391 | 6.955 | 1141044.4622 | 527268.47 | 18598.5822 | 1136276.0947 | 524256.5691 | 17496.8727 | 3928.7288 | 2172.2622 | 262.0707 | 839.6387 | 81025.7873 | 49020.899 | 11577.2131 | 31503.4218 | 17885.2462 | 437.4664 | 41125.9781 | 22739.2654 | 2743.3594 | 8396.3874 | 0.039499 | 0.018486 | 0.0004682 | 0.010782 | 0.0061334 | 0.0010782 | 0.012993 | 5000000 | scaled
412-23AE | 36961.8884 | 4524.9695 | 31655.872 | 781.0468 | 12.24% | 85.64% | 2.113% | 16798.8011 | 33995.5622 | 244.9536 | 13307.7116 | 3246.1359 | 422.6508 | 27547.8893 | 6025.0221 | 412 |  | 757 | 412-23AE | 36961.8884 | 20163.0873 | 2966.3262 | 4524.9695 | 1899.166 | 74.2616 | 31655.872 | 17482.8745 | 2111.0177 | 781.0468 | 433.0112 | 188.0576 | 10.3604 | 389.3485 | 163.6804 | 6.9002 | 43.075 | 23.7894 | 2.8725 | 0.58771 | 6363.6076 | 3117.4717 | 338.5855 | 3150.5917 | 1311.2242 | 58.1015 | 3142.065 | 1735.2966 | 209.5332 | 70.9508 | 30165.2696 | 16857.558 | 2617.3804 | 985.0294 | 424.2613 | 9.26 | 28470.732 | 15723.7884 | 1898.612 | 709.5083 | 0.0021462 | 0.0009296 | 2.36e-05 | 0.010784 | 0.006128 | 0.0010784 | 0.0010886 | 5000000 | scaled
415-1237R | 133095.7859 | 16823.0905 | 110534.0887 | 5738.6067 | 12.64% | 83.05% | 4.312% | 58506.3353 | 119800.0954 | 522.5496 | 52319.2021 | 5664.5835 | 918.376 | 107631.1996 | 11250.5197 | 415 |  | 758 | 415-1237R | 133095.7859 | 74589.4506 | 13295.6906 | 16823.0905 | 7845.195 | 185.8058 | 110534.0887 | 61005.6489 | 7371.278 | 5738.6067 | 940.51 | 417.9604 | 22.134 | 786.3878 | 330.9628 | 7.8258 | 149.8041 | 82.6794 | 9.9901 | 4.3181 | 12422.6644 | 6758.0809 | 1172.1447 | 2514.1712 | 1055.8293 | 24.8341 | 9387.1943 | 5180.9526 | 626.0116 | 521.299 | 119732.6115 | 67413.4094 | 12101.4119 | 13522.5315 | 6458.4029 | 153.1459 | 100997.0903 | 55742.0169 | 6735.2763 | 5212.9896 | 0.018944 | 0.0084058 | 0.0002134 | 0.010713 | 0.0060838 | 0.0010712 | 0.0081384 | 5000000 | scaled
415-33 | 139778.6103 | 28191.1433 | 104891.435 | 6696.032 | 20.17% | 75.04% | 4.79% | 63668.8049 | 125801.9551 | 2704.2085 | 46771.7145 | 14192.8819 | 4527.102 | 96060.7093 | 25214.1438 | 415 |  | 759 | 415-33 | 139778.6103 | 76109.8054 | 13976.6552 | 28191.1433 | 11605.406 | 285.3798 | 104891.435 | 57808.3674 | 6995.2434 | 6696.032 | 4587.0039 | 1882.7954 | 59.9019 | 4431.382 | 1794.7665 | 44.8209 | 150.5833 | 82.9903 | 10.0424 | 5.0385 | 26582.6649 | 12389.783 | 1368.5211 | 17123.6013 | 6903.6121 | 169.9869 | 8850.7915 | 4877.8988 | 590.2621 | 608.2721 | 108608.9415 | 61837.227 | 12548.2322 | 6636.16 | 2907.0274 | 70.572 | 95890.0602 | 52847.4783 | 6394.9388 | 6082.7213 | 0.019237 | 0.0083294 | 0.0002118 | 0.01071 | 0.0060742 | 0.001071 | 0.0093408 | 5000000 | scaled
416-21 | 17053.6459 | 15040.6582 | 0 | 2012.9878 | 88.2% | 0% | 11.8% | 7607.9592 | 14854.1848 | 7.8694 | 7559.7443 | 40.3455 | 12.9833 | 14774.5748 | 66.6267 | 416 |  | 760 | 416-21 | 17053.6459 | 9445.6867 | 2199.4612 | 15040.6582 | 7432.6989 | 186.4734 | 0 | 0 | 0 | 2012.9878 | 14.5299 | 6.6605 | 1.5466 | 13.0152 | 5.1458 | 0.031924 | 0 | 0 | 0 | 1.5147 | 249.6534 | 209.3079 | 183.0267 | 66.7922 | 26.4467 | 0.16553 | 0 | 0 | 0 | 182.8612 | 16789.4626 | 9229.7183 | 2014.8878 | 14960.8507 | 7401.1064 | 186.2759 | 0 | 0 | 0 | 1828.6119 | 0.0041084 | 0.001954 | 4.98e-05 | 0 | 0 | 0 | 0.0028434 | 5000000 | scaled
416-29AE | 443.1363 | 58.9724 | 0 | 384.1639 | 13.31% | 0% | 86.69% | 33.1817 | 58.3375 | 0.013006 | 33.0979 | 0.070841 | 0.11154 | 57.6455 | 0.58048 | 416 |  | 761 | 416-29AE | 443.1363 | 409.9545 | 384.7987 | 58.9724 | 25.7906 | 0.63482 | 0 | 0 | 0 | 384.1639 | 0.40061 | 0.3876 | 0.28907 | 0.11154 | 0.098532 | 0 | 0 | 0 | 0 | 0.28907 | 35.4782 | 35.4073 | 34.8977 | 0.58048 | 0.50963 | 0 | 0 | 0 | 0 | 34.8977 | 407.2575 | 374.1596 | 349.6119 | 58.2804 | 25.1825 | 0.63482 | 0 | 0 | 0 | 348.9771 | 0.000683 | 0.0002956 | 7.6e-06 | 0 | 0 | 0 | 0.0005506 | 5000000 | scaled
416-35F | 1295.8021 | 541.6522 | 0 | 754.1499 | 41.8% | 0% | 58.2% | 309.4245 | 535.8555 | 2.3127 | 295.0256 | 12.0861 | 3.4037 | 514.6726 | 17.7792 | 416 |  | 762 | 416-35F | 1295.8021 | 986.3776 | 759.9466 | 541.6522 | 232.2277 | 5.7967 | 0 | 0 | 0 | 754.1499 | 4.0125 | 1.6998 | 0.60886 | 3.4451 | 1.1323 | 0.041383 | 0 | 0 | 0 | 0.56747 | 86.5045 | 74.4184 | 68.7253 | 17.997 | 5.9109 | 0.2178 | 0 | 0 | 0 | 68.5075 | 1205.285 | 910.2594 | 690.6124 | 520.2101 | 225.1845 | 5.5375 | 0 | 0 | 0 | 685.0749 | 0.0018728 | 0.0008108 | 2e-05 | 0 | 0 | 0 | 0.0010946 | 5000000 | scaled
416-37F | 1722.6905 | 802.1881 | 0 | 920.5024 | 46.57% | 0% | 53.43% | 459.1489 | 792.8169 | 3.0852 | 440.1087 | 15.955 | 4.0512 | 767.8139 | 20.9518 | 416 |  | 763 | 416-37F | 1722.6905 | 1263.5416 | 929.8736 | 802.1881 | 343.0391 | 9.3712 | 0 | 0 | 0 | 920.5024 | 4.8345 | 1.7493 | 0.7833 | 4.1419 | 1.0567 | 0.090649 | 0 | 0 | 0 | 0.69265 | 105.0405 | 89.0855 | 84.0888 | 21.4214 | 5.4664 | 0.46968 | 0 | 0 | 0 | 83.6191 | 1612.8154 | 1172.7067 | 845.0015 | 776.6247 | 336.516 | 8.8108 | 0 | 0 | 0 | 836.1907 | 0.0022406 | 0.0009704 | 2.52e-05 | 0 | 0 | 0 | 0.0012602 | 5000000 | scaled
417-21R | 169297.6361 | 63108.7348 | 99825.8143 | 6363.0869 | 37.28% | 58.96% | 3.759% | 81716.3562 | 155729.8326 | 5337.5315 | 55008.8916 | 21369.9332 | 9043.2991 | 109296.4208 | 37390.1127 | 417 |  | 764 | 417-21R | 169297.6361 | 87581.2799 | 13567.8035 | 63108.7348 | 26244.6548 | 545.1907 | 99825.8143 | 54973.5382 | 6659.5258 | 6363.0869 | 9131.2178 | 3793.6864 | 87.9188 | 8990.5531 | 3714.0718 | 74.0662 | 135.8768 | 74.8266 | 9.0645 | 4.788 | 38759.6951 | 17389.7619 | 1369.5824 | 29791.1 | 12191.0942 | 231.8082 | 8390.5678 | 4620.6405 | 559.747 | 578.0272 | 121406.7232 | 66397.8316 | 12110.3024 | 24327.0817 | 10339.4888 | 239.3163 | 91299.3697 | 50278.071 | 6090.7143 | 5780.2718 | 0.019964 | 0.0086444 | 0.0002202 | 0.010716 | 0.006073 | 0.0010716 | 0.0089994 | 5000000 | scaled
417-41 | 622.7237 | 542.6264 | 0 | 80.0973 | 87.14% | 0% | 12.86% | 130.727 | 532.402 | 0 | 130.727 | 0 | 0 | 532.402 | 0 | 417 |  | 765 | 417-41 | 622.7237 | 491.9967 | 90.3217 | 542.6264 | 411.8995 | 10.2245 | 0 | 0 | 0 | 80.0973 | 0.060271 | 0.060271 | 0.060271 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060271 | 7.2761 | 7.2761 | 7.2761 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2761 | 615.3873 | 484.6604 | 82.9854 | 542.6264 | 411.8995 | 10.2245 | 0 | 0 | 0 | 72.7609 | 0.0001486 | 0.0001128 | 2.8e-06 | 0 | 0 | 0 | 0.0001058 | 5000000 | scaled
417-44AE | 68543.974 | 74.6747 | 67939.6043 | 529.695 | 0.1089% | 99.12% | 0.7728% | 30564.2896 | 63482.8646 | 39.2543 | 27765.8448 | 2759.1904 | 81.5369 | 57669.2943 | 5732.0334 | 417 |  | 766 | 417-44AE | 68543.974 | 37979.6845 | 5061.1094 | 74.6747 | 32.7871 | 0.76178 | 67939.6043 | 37417.2024 | 4530.6526 | 529.695 | 87.6934 | 48.4391 | 6.1565 | 0.95142 | 0.48754 | 0 | 86.3434 | 47.5529 | 5.7579 | 0.39858 | 6189.365 | 3430.1746 | 457.3316 | 4.8639 | 2.492 | 0 | 6136.3833 | 3379.5648 | 409.2138 | 48.1179 | 62266.9156 | 34501.0708 | 4597.6213 | 68.8594 | 29.8076 | 0.76178 | 61716.8776 | 33990.0846 | 4115.6809 | 481.1786 | 0.001392 | 0.0006026 | 1.52e-05 | 0.010771 | 0.0061046 | 0.001077 | 0.000737 | 5000000 | scaled
417-791AE | 96251.671 | 1746.7325 | 92749.407 | 1755.5316 | 1.815% | 96.36% | 1.824% | 42654.8473 | 88292.4996 | 58.8225 | 39167.704 | 3428.3209 | 121.073 | 81054.6839 | 7116.7427 | 417 |  | 767 | 417-791AE | 96251.671 | 53596.8237 | 7959.1714 | 1746.7325 | 758.0575 | 18.9657 | 92749.407 | 51083.2346 | 6184.6742 | 1755.5316 | 130.3365 | 71.514 | 9.2635 | 9.9041 | 4.5905 | 0 | 119.1114 | 65.6025 | 7.9425 | 1.321 | 7781.0353 | 4352.7145 | 664.2926 | 50.9676 | 23.6138 | 0 | 7570.594 | 4169.627 | 504.8189 | 159.4737 | 88340.2992 | 49172.5953 | 7285.6153 | 1685.8607 | 729.8533 | 18.9657 | 85059.7016 | 46848.0051 | 5671.9127 | 1594.7369 | 0.0037746 | 0.0016342 | 4.18e-05 | 0.010751 | 0.0060932 | 0.001075 | 0.0024508 | 5000000 | scaled
418-1260 | 2152.9209 | 563.257 | 0 | 1589.6639 | 26.16% | 0% | 73.84% | 283.501 | 555.5395 | 10.5019 | 219.1154 | 53.8837 | 18.0274 | 445.0414 | 92.4708 | 418 |  | 768 | 418-1260 | 2152.9209 | 1869.4198 | 1597.3814 | 563.257 | 279.756 | 7.7175 | 0 | 0 | 0 | 1589.6639 | 19.5322 | 9.0302 | 1.5048 | 18.336 | 7.8341 | 0.3086 | 0 | 0 | 0 | 1.1962 | 238.4625 | 184.5788 | 145.9918 | 94.0564 | 40.1727 | 1.5856 | 0 | 0 | 0 | 144.4062 | 1894.9262 | 1675.8108 | 1449.8848 | 450.8647 | 231.7492 | 5.8233 | 0 | 0 | 0 | 1444.0615 | 0.0045828 | 0.0021148 | 5.32e-05 | 0 | 0 | 0 | 0.0022374 | 5000000 | scaled
418-25R | 6511.1364 | 3454.4774 | 0 | 3056.659 | 53.05% | 0% | 46.95% | 1912.6782 | 3416.4443 | 17.557 | 1804.8886 | 90.2326 | 34.0098 | 3207.6474 | 174.787 | 418 |  | 769 | 418-25R | 6511.1364 | 4598.4582 | 3094.6921 | 3454.4774 | 1541.7992 | 38.0331 | 0 | 0 | 0 | 3056.659 | 36.4454 | 18.8885 | 2.4356 | 34.1454 | 16.5884 | 0.13558 | 0 | 0 | 0 | 2.3 | 453.1506 | 362.918 | 278.3636 | 175.4816 | 85.249 | 0.69458 | 0 | 0 | 0 | 277.669 | 6021.5403 | 4216.6517 | 2813.8929 | 3244.8504 | 1439.9618 | 37.2029 | 0 | 0 | 0 | 2776.69 | 0.007183 | 0.0032118 | 8.2e-05 | 0 | 0 | 0 | 0.004274 | 5000000 | scaled
42-46 | 44005.0028 | 30761.7871 | 0 | 13243.2157 | 69.91% | 0% | 30.09% | 17140.26 | 30451.8073 | 324.178 | 15732.8532 | 1083.2289 | 584.5115 | 27914.3278 | 1952.968 | 42 |  | 770 | 42-46 | 44005.0028 | 26864.7427 | 13553.1955 | 30761.7871 | 13621.5271 | 309.9798 | 0 | 0 | 0 | 13243.2157 | 596.8276 | 272.6496 | 12.3161 | 586.8625 | 262.6846 | 2.351 | 0 | 0 | 0 | 9.9651 | 3163.8167 | 2080.5878 | 1210.8487 | 1960.7939 | 877.5651 | 7.826 | 0 | 0 | 0 | 1203.0228 | 40244.3585 | 24511.5052 | 12330.0306 | 28214.1307 | 12481.2775 | 299.8028 | 0 | 0 | 0 | 12030.2278 | 0.033352 | 0.014634 | 0.000373 | 0 | 0 | 0 | 0.01859 | 5000000 | scaled
43-443 | 256.0063 | 86.3142 | 0 | 169.6921 | 33.72% | 0% | 66.28% | 48.6186 | 85.371 | 0.33422 | 46.5571 | 1.7273 | 0.70431 | 81.0228 | 3.644 | 43 |  | 771 | 43-443 | 256.0063 | 207.3877 | 170.6352 | 86.3142 | 37.6956 | 0.94316 | 0 | 0 | 0 | 169.6921 | 0.83199 | 0.49777 | 0.12769 | 0.70431 | 0.37009 | 0 | 0 | 0 | 0 | 0.12769 | 19.0589 | 17.3317 | 15.4149 | 3.644 | 1.9167 | 0 | 0 | 0 | 0 | 15.4149 | 236.1153 | 189.5582 | 155.0926 | 81.9659 | 35.4088 | 0.94316 | 0 | 0 | 0 | 154.1494 | 0.0002736 | 0.0001182 | 3.2e-06 | 0 | 0 | 0 | 0.0002488 | 5000000 | scaled
43-445 | 17713.7938 | 8876.64 | 0 | 8837.1538 | 50.11% | 0% | 49.89% | 4492.8537 | 8750.4643 | 244.833 | 2952.2163 | 1295.8045 | 467.1838 | 5814.866 | 2468.4145 | 43 |  | 772 | 43-445 | 17713.7938 | 13220.9401 | 8963.3296 | 8876.64 | 4383.7863 | 126.1757 | 0 | 0 | 0 | 8837.1538 | 481.9437 | 237.1108 | 14.7599 | 475.294 | 230.4611 | 8.1102 | 0 | 0 | 0 | 6.6497 | 3314.1484 | 2018.3439 | 845.7339 | 2511.3753 | 1215.5708 | 42.9608 | 0 | 0 | 0 | 802.7731 | 13917.7017 | 10965.4854 | 8102.8358 | 5889.9707 | 2937.7544 | 75.1047 | 0 | 0 | 0 | 8027.731 | 0.021014 | 0.009749 | 0.0002484 | 0 | 0 | 0 | 0.012378 | 5000000 | scaled
43-475F | 37.9274 | 5.2962 | 0 | 32.6312 | 13.96% | 0% | 86.04% | 3.5774 | 5.2595 | 0.27549 | 1.8856 | 1.4163 | 0.32043 | 3.2914 | 1.6477 | 43 |  | 773 | 43-475F | 37.9274 | 34.35 | 32.6679 | 5.2962 | 1.7188 | 0.036645 | 0 | 0 | 0 | 32.6312 | 0.34498 | 0.069484 | 0.024554 | 0.32043 | 0.044931 | 0 | 0 | 0 | 0 | 0.024554 | 4.6119 | 3.1956 | 2.9642 | 1.6477 | 0.23134 | 0 | 0 | 0 | 0 | 2.9642 | 32.9705 | 31.0849 | 29.6791 | 3.3281 | 1.4425 | 0.036645 | 0 | 0 | 0 | 29.6424 | 0.0001998 | 8.66e-05 | 2.2e-06 | 0 | 0 | 0 | 5.1e-05 | 5000000 | scaled
430-321AE | 306.5823 | 48.0259 | 0 | 258.5565 | 15.66% | 0% | 84.34% | 28.869 | 47.6624 | 1.8445 | 17.5391 | 9.4854 | 2.7778 | 30.5908 | 14.2938 | 430 |  | 774 | 430-321AE | 306.5823 | 277.7133 | 258.9199 | 48.0259 | 19.1569 | 0.36349 | 0 | 0 | 0 | 258.5565 | 2.9724 | 1.1278 | 0.19456 | 2.7778 | 0.93329 | 0 | 0 | 0 | 0 | 0.19456 | 37.7812 | 28.2958 | 23.4874 | 14.2938 | 4.8084 | 0 | 0 | 0 | 0 | 23.4874 | 265.8288 | 248.2897 | 235.2379 | 30.9543 | 13.4152 | 0.36349 | 0 | 0 | 0 | 234.8745 | 0.0005998 | 0.0002598 | 6.6e-06 | 0 | 0 | 0 | 0.0003428 | 5000000 | scaled
430-42F | 4680.7711 | 1737.0584 | 0 | 2943.7126 | 37.11% | 0% | 62.89% | 877.6912 | 1702.3116 | 10.0569 | 817.3442 | 50.2901 | 32.8185 | 1501.2404 | 168.2527 | 430 |  | 775 | 430-42F | 4680.7711 | 3803.0798 | 2978.4594 | 1737.0584 | 859.3672 | 34.7468 | 0 | 0 | 0 | 2943.7126 | 37.1658 | 27.1089 | 4.3473 | 34.9508 | 24.8939 | 2.1323 | 0 | 0 | 0 | 2.215 | 447.5695 | 397.2793 | 279.3168 | 180.1606 | 129.8705 | 11.9079 | 0 | 0 | 0 | 267.4089 | 4196.0358 | 3378.6916 | 2694.7954 | 1521.9471 | 704.6029 | 20.7067 | 0 | 0 | 0 | 2674.0887 | 0.0088758 | 0.0038436 | 9.72e-05 | 0 | 0 | 0 | 0.0041246 | 5000000 | scaled
430-639 | 3166.5417 | 956.1138 | 0 | 2210.4279 | 30.19% | 0% | 69.81% | 546.0428 | 949.6445 | 26.4421 | 379.3675 | 140.2332 | 45.331 | 663.9858 | 240.3278 | 430 |  | 776 | 430-639 | 3166.5417 | 2620.4989 | 2216.8971 | 956.1138 | 410.071 | 6.4693 | 0 | 0 | 0 | 2210.4279 | 47.0498 | 20.6077 | 1.7188 | 45.3866 | 18.9444 | 0.055572 | 0 | 0 | 0 | 1.6633 | 441.4073 | 301.1742 | 201.0796 | 240.6106 | 100.3774 | 0.2828 | 0 | 0 | 0 | 200.7968 | 2678.0845 | 2298.717 | 2014.0987 | 670.1167 | 290.7492 | 6.1309 | 0 | 0 | 0 | 2007.9678 | 0.005227 | 0.0022646 | 5.76e-05 | 0 | 0 | 0 | 0.003123 | 5000000 | scaled
431-46AE | 5460.1979 | 1995.8648 | 0 | 3464.333 | 36.55% | 0% | 63.45% | 1131.1607 | 1973.8046 | 0 | 1131.1607 | 0 | 0.026407 | 1973.6414 | 0.13682 | 431 |  | 777 | 431-46AE | 5460.1979 | 4329.0372 | 3486.3932 | 1995.8648 | 864.7041 | 22.0602 | 0 | 0 | 0 | 3464.333 | 2.6332 | 2.6332 | 2.6068 | 0.026407 | 0.026407 | 0 | 0 | 0 | 0 | 2.6068 | 314.8392 | 314.8392 | 314.7024 | 0.13682 | 0.13682 | 0 | 0 | 0 | 0 | 314.7024 | 5142.7255 | 4011.5648 | 3169.0841 | 1995.7016 | 864.5409 | 22.0602 | 0 | 0 | 0 | 3147.0239 | 0.0076008 | 0.0032916 | 8.42e-05 | 0 | 0 | 0 | 0.0048906 | 5000000 | scaled
431-474 | 2429.0008 | 855.1567 | 0 | 1573.8441 | 35.21% | 0% | 64.79% | 484.8358 | 845.5944 | 0 | 484.8358 | 0 | 0 | 845.5944 | 0 | 431 |  | 778 | 431-474 | 2429.0008 | 1944.165 | 1583.4063 | 855.1567 | 370.3209 | 9.5622 | 0 | 0 | 0 | 1573.8441 | 1.1843 | 1.1843 | 1.1843 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1843 | 142.9691 | 142.9691 | 142.9691 | 0 | 0 | 0 | 0 | 0 | 0 | 142.9691 | 2284.8474 | 1800.0116 | 1439.253 | 855.1567 | 370.3209 | 9.5622 | 0 | 0 | 0 | 1429.6907 | 0.0031232 | 0.0013532 | 3.46e-05 | 0 | 0 | 0 | 0.0022024 | 5000000 | scaled
431-478 | 1841.7341 | 520.155 | 0 | 1321.5791 | 28.24% | 0% | 71.76% | 295.1093 | 514.5364 | 0 | 295.1093 | 0 | 0 | 514.5364 | 0 | 431 |  | 779 | 431-478 | 1841.7341 | 1546.6248 | 1327.1977 | 520.155 | 225.0457 | 5.6186 | 0 | 0 | 0 | 1321.5791 | 0.99445 | 0.99445 | 0.99445 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99445 | 120.0531 | 120.0531 | 120.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 120.0531 | 1720.6865 | 1425.5772 | 1206.1501 | 520.155 | 225.0457 | 5.6186 | 0 | 0 | 0 | 1200.5315 | 0.003043 | 0.0013172 | 3.3e-05 | 0 | 0 | 0 | 0.001848 | 5000000 | scaled
431-48AE | 1403.3282 | 435.3177 | 0 | 968.0105 | 31.02% | 0% | 68.98% | 246.6528 | 430.5933 | 0.056754 | 246.2942 | 0.30186 | 0.11903 | 429.8428 | 0.63145 | 431 |  | 780 | 431-48AE | 1403.3282 | 1156.6754 | 972.735 | 435.3177 | 188.6649 | 4.7244 | 0 | 0 | 0 | 968.0105 | 0.84742 | 0.79067 | 0.7284 | 0.11903 | 0.062272 | 0 | 0 | 0 | 0 | 0.7284 | 88.5674 | 88.2655 | 87.936 | 0.63267 | 0.33081 | 0.001222 | 0 | 0 | 0 | 87.9347 | 1313.9134 | 1067.6192 | 884.0706 | 434.566 | 188.2718 | 4.7232 | 0 | 0 | 0 | 879.3474 | 0.002202 | 0.000954 | 2.36e-05 | 0 | 0 | 0 | 0.0013386 | 5000000 | scaled
431-550 | 13133.9263 | 9920.0056 | 0 | 3213.9206 | 75.53% | 0% | 24.47% | 5631.1699 | 9813.6994 | 9.0142 | 5575.8143 | 46.3415 | 14.8583 | 9722.4913 | 76.3498 | 431 |  | 781 | 431-550 | 13133.9263 | 7502.7563 | 3320.2269 | 9920.0056 | 4288.8357 | 106.3062 | 0 | 0 | 0 | 3213.9206 | 17.2845 | 8.2704 | 2.4263 | 14.8662 | 5.852 | 0.0078825 | 0 | 0 | 0 | 2.4184 | 368.3447 | 322.0033 | 291.9949 | 76.39 | 30.0485 | 0.040188 | 0 | 0 | 0 | 291.9548 | 12748.297 | 7172.4827 | 3025.8057 | 9828.7495 | 4252.9352 | 106.2581 | 0 | 0 | 0 | 2919.5475 | 0.0078356 | 0.0033928 | 8.6e-05 | 0 | 0 | 0 | 0.0045088 | 5000000 | scaled
434-301 | 70649.6666 | 70320.4363 | 0 | 329.2303 | 99.53% | 0% | 0.466% | 19320.4969 | 68516.5816 | 1412.9989 | 172.2911 | 17735.2068 | 5080.7274 | 576.9565 | 62858.8977 | 434 |  | 782 | 434-301 | 70649.6666 | 51329.1697 | 2133.085 | 70320.4363 | 50999.9394 | 1803.8547 | 0 | 0 | 0 | 329.2303 | 5208.7496 | 3795.7507 | 128.0221 | 5208.5019 | 3795.5029 | 127.7744 | 0 | 0 | 0 | 0.24774 | 64554.5322 | 46819.3254 | 1695.6345 | 64524.6247 | 46789.4179 | 1665.727 | 0 | 0 | 0 | 29.9075 | 886.3847 | 714.0936 | 309.4283 | 587.3097 | 415.0185 | 10.3532 | 0 | 0 | 0 | 299.0751 | 0.0027146 | 0.0019954 | 5.04e-05 | 0 | 0 | 0 | 0.0004424 | 5000000 | scaled
438-45 | 4537.9204 | 4225.236 | 0 | 312.6843 | 93.11% | 0% | 6.89% | 1320.6675 | 4188.3011 | 162.0851 | 3.7489 | 1154.8335 | 486.5198 | 8.7917 | 3692.9896 | 438 |  | 783 | 438-45 | 4537.9204 | 3217.2529 | 349.6193 | 4225.236 | 2904.5686 | 36.935 | 0 | 0 | 0 | 312.6843 | 491.9193 | 329.8342 | 5.3995 | 491.684 | 329.5989 | 5.1642 | 0 | 0 | 0 | 0.23528 | 3753.0427 | 2598.2092 | 60.0531 | 3724.6382 | 2569.8048 | 31.6486 | 0 | 0 | 0 | 28.4045 | 292.9584 | 289.2095 | 284.1667 | 8.9138 | 5.1649 | 0.12213 | 0 | 0 | 0 | 284.0446 | 0.0012962 | 0.0007458 | 1.9e-05 | 0 | 0 | 0 | 0.0004476 | 5000000 | scaled
439-42F | 6564.2353 | 6499.1849 | 0 | 65.0504 | 99.01% | 0% | 0.991% | 3060.3953 | 6499.1693 | 334.9952 | 1.0309 | 2724.3692 | 681.4181 | 1.8167 | 5815.9346 | 439 |  | 784 | 439-42F | 6564.2353 | 3503.84 | 65.066 | 6499.1849 | 3438.7896 | 0.015547 | 0 | 0 | 0 | 65.0504 | 681.467 | 346.4718 | 0.048948 | 681.4181 | 346.4229 | 0 | 0 | 0 | 0 | 0.048948 | 5821.8438 | 3097.4746 | 5.9092 | 5815.9346 | 3091.5654 | 0 | 0 | 0 | 0 | 5.9092 | 60.9245 | 59.8936 | 59.1078 | 1.8322 | 0.80132 | 0.015547 | 0 | 0 | 0 | 59.0923 | 0.0002666 | 0.0001154 | 3e-06 | 0 | 0 | 0 | 9.52e-05 | 5000000 | scaled
44-1101F | 2700.9999 | 758.051 | 0 | 1942.9489 | 28.07% | 0% | 71.93% | 428.0606 | 745.166 | 7.9268 | 379.7163 | 40.4175 | 13.4196 | 663.3683 | 68.3782 | 44 |  | 785 | 44-1101F | 2700.9999 | 2272.9393 | 1955.8338 | 758.051 | 329.9904 | 12.8849 | 0 | 0 | 0 | 1942.9489 | 15.6772 | 7.7503 | 2.2576 | 14.2152 | 6.2883 | 0.79561 | 0 | 0 | 0 | 1.462 | 249.0341 | 208.6166 | 180.6559 | 72.5353 | 32.1178 | 4.1571 | 0 | 0 | 0 | 176.4988 | 2436.2886 | 2056.5723 | 1772.9203 | 671.3005 | 291.5842 | 7.9322 | 0 | 0 | 0 | 1764.9881 | 0.004182 | 0.0018108 | 4.58e-05 | 0 | 0 | 0 | 0.0027844 | 5000000 | scaled
44-40AE | 1926.6704 | 988.124 | 0 | 938.5464 | 51.29% | 0% | 48.71% | 564.7279 | 987.7972 | 75.2892 | 18.9921 | 470.4466 | 131.1829 | 33.2474 | 823.3669 | 44 |  | 786 | 44-40AE | 1926.6704 | 1361.9425 | 938.8732 | 988.124 | 423.3962 | 0.32685 | 0 | 0 | 0 | 938.5464 | 131.8891 | 56.5999 | 0.70623 | 131.1829 | 55.8937 | 0 | 0 | 0 | 0 | 0.70623 | 908.6251 | 438.1785 | 85.2582 | 823.3669 | 352.9203 | 0 | 0 | 0 | 0 | 85.2582 | 886.1562 | 867.1641 | 852.9088 | 33.5742 | 14.5821 | 0.32685 | 0 | 0 | 0 | 852.5819 | 0.0022354 | 0.0009676 | 2.42e-05 | 0 | 0 | 0 | 0.0013386 | 5000000 | scaled
44-41 | 1096.5322 | 239.1322 | 0 | 857.3999 | 21.81% | 0% | 78.19% | 134.4357 | 236.5926 | 0.24002 | 132.9723 | 1.2233 | 0.74372 | 232.0602 | 3.7887 | 44 |  | 787 | 44-41 | 1096.5322 | 962.0965 | 859.9396 | 239.1322 | 104.6966 | 2.5396 | 0 | 0 | 0 | 857.3999 | 1.3889 | 1.1489 | 0.64517 | 0.74372 | 0.50369 | 0 | 0 | 0 | 0 | 0.64517 | 81.6755 | 80.4522 | 77.8868 | 3.7887 | 2.5654 | 0 | 0 | 0 | 0 | 77.8868 | 1013.4678 | 880.4955 | 781.4076 | 234.5998 | 101.6275 | 2.5396 | 0 | 0 | 0 | 778.868 | 0.002078 | 0.0008998 | 2.24e-05 | 0 | 0 | 0 | 0.0011996 | 5000000 | scaled
44-42 | 2251.8684 | 1182.048 | 0 | 1069.8204 | 52.49% | 0% | 47.51% | 668.1628 | 1169.8873 | 5.0653 | 636.9359 | 26.1616 | 9.1603 | 1113.447 | 47.28 | 44 |  | 788 | 44-42 | 2251.8684 | 1583.7055 | 1081.9811 | 1182.048 | 513.8852 | 12.1607 | 0 | 0 | 0 | 1069.8204 | 9.9653 | 4.9 | 0.80501 | 9.1603 | 4.095 | 0 | 0 | 0 | 0 | 0.80501 | 144.4632 | 118.3016 | 97.1832 | 47.28 | 21.1184 | 0 | 0 | 0 | 0 | 97.1832 | 2097.4399 | 1460.504 | 983.9929 | 1125.6077 | 488.6718 | 12.1607 | 0 | 0 | 0 | 971.8321 | 0.0025018 | 0.0010834 | 2.74e-05 | 0 | 0 | 0 | 0.001497 | 5000000 | scaled
441-23R | 3518020.3842 | 3428404.8814 | 86815.4737 | 2800.029 | 97.45% | 2.468% | 0.07959% | 1098118.2592 | 3447556.5966 | 54353.0093 | 31648.0421 | 1012117.2079 | 172215.9829 | 66935.1492 | 3208405.4645 | 441 |  | 789 | 441-23R | 3518020.3842 | 2419902.1249 | 70463.7875 | 3428404.8814 | 2367901.5531 | 59182.4427 | 86815.4737 | 49200.5428 | 8481.3159 | 2800.029 | 175296.2421 | 120943.2328 | 3080.2592 | 174737.9745 | 120625.9355 | 3023.8189 | 556.1606 | 315.1904 | 54.3333 | 2.1069 | 3266231.5714 | 2254114.3635 | 57826.1069 | 3251018.8874 | 2245382.7413 | 56110.4175 | 14958.3275 | 8477.2656 | 1461.3328 | 254.3566 | 76492.5707 | 44844.5286 | 9557.4215 | 2648.0195 | 1892.8764 | 48.2063 | 71300.9856 | 40408.0868 | 6965.6497 | 2543.5655 | 0.021156 | 0.014905 | 0.0003796 | 0.52271 | 0.29679 | 0.052271 | 0.0039592 | 5000000 | scaled
441-279R | 582163.2988 | 531721.5473 | 48851.0694 | 1590.682 | 91.34% | 8.391% | 0.2732% | 135759.2653 | 568815.6244 | 5753.9079 | 16800.4613 | 113204.8961 | 25687.9194 | 35043.812 | 508083.893 | 441 |  | 790 | 441-279R | 582163.2988 | 446404.0335 | 13347.6744 | 531721.5473 | 417124.3686 | 6984.3522 | 48851.0694 | 27688.9829 | 4772.6401 | 1590.682 | 26089.2326 | 20335.3247 | 401.3131 | 25542.5775 | 20024.9599 | 346.8261 | 545.4581 | 309.1678 | 53.29 | 1.1969 | 515799.058 | 402594.1619 | 7715.165 | 506084.0716 | 397025.0723 | 6635.6511 | 9570.4877 | 5424.591 | 935.0152 | 144.4986 | 40275.0083 | 23474.547 | 5231.1962 | 94.8982 | 74.3365 | 1.8749 | 38735.1236 | 21955.224 | 3784.3348 | 1444.9865 | 0.0087756 | 0.006809 | 0.0001728 | 0.52428 | 0.29772 | 0.052428 | 0.0022194 | 5000000 | scaled
441-27R | 4750126.7754 | 4655243.6145 | 91023.6797 | 3859.4813 | 98% | 1.916% | 0.08125% | 1701087.8363 | 4674789.4267 | 88118.7457 | 34744.9148 | 1578224.1758 | 243096.0863 | 72635.5312 | 4359057.8092 | 441 |  | 791 | 441-27R | 4750126.7754 | 3049038.9391 | 75337.3487 | 4655243.6145 | 2993596.422 | 62586.9276 | 91023.6797 | 51583.0358 | 8890.9398 | 3859.4813 | 246417.8411 | 158299.0954 | 3321.7548 | 246143.4276 | 158142.3271 | 3292.3304 | 271.5094 | 153.8641 | 26.5203 | 2.9041 | 4419766.7177 | 2841542.542 | 60708.9085 | 4408393.2786 | 2834945.31 | 59281.6301 | 11022.8412 | 6246.634 | 1076.6805 | 350.5979 | 83942.2166 | 49197.3018 | 11306.6854 | 706.9083 | 508.7849 | 12.9671 | 79729.329 | 45182.5376 | 7787.7391 | 3505.9792 | 0.032668 | 0.020483 | 0.00052 | 0.51947 | 0.29493 | 0.051947 | 0.005385 | 5000000 | scaled
441-30R | 5348877.3579 | 5272517.0957 | 72976.4139 | 3383.8483 | 98.57% | 1.364% | 0.06326% | 1625389.916 | 5245293.3541 | 83426.2415 | 28241.0028 | 1513722.6717 | 270935.2243 | 59164.0989 | 4915194.031 | 441 |  | 792 | 441-30R | 5348877.3579 | 3723487.4419 | 103584.0037 | 5272517.0957 | 3678748.2872 | 93072.9033 | 72976.4139 | 41355.3064 | 7127.2522 | 3383.8483 | 275854.9973 | 192428.7558 | 4919.773 | 275677.219 | 192326.9066 | 4900.1127 | 175.232 | 99.303 | 17.1141 | 2.5462 | 5004455.5778 | 3490732.9061 | 89261.5468 | 4995986.2316 | 3485800.1829 | 88157.0171 | 8161.9551 | 4625.3322 | 797.1385 | 307.3911 | 68566.7828 | 40325.78 | 9402.6839 | 853.6451 | 621.1978 | 15.7734 | 64639.2268 | 36630.6712 | 6312.9996 | 3073.911 | 0.033649 | 0.023441 | 0.0005956 | 0.5168 | 0.29342 | 0.05168 | 0.0047416 | 5000000 | scaled
442-16R | 1834937.6384 | 1763136.4862 | 64840.8946 | 6960.2576 | 96.09% | 3.534% | 0.3793% | 610830.7575 | 1799071.2087 | 27878.8376 | 23786.0578 | 559165.8621 | 82324.7225 | 49993.1974 | 1666753.2888 | 442 |  | 793 | 442-16R | 1834937.6384 | 1224106.8809 | 35866.4297 | 1763136.4862 | 1180401.9127 | 22609.2603 | 64840.8946 | 36744.7106 | 6296.9118 | 6960.2576 | 83404.9131 | 55526.0755 | 1080.1907 | 83210.2781 | 55413.5084 | 1056.5603 | 189.3976 | 107.3298 | 18.393 | 5.2374 | 1689932.2994 | 1130766.4373 | 23179.0105 | 1678863.9751 | 1124220.1539 | 21533.257 | 10436.0497 | 5914.0088 | 1013.479 | 632.2746 | 61600.4259 | 37814.3681 | 11607.2285 | 1062.2329 | 768.2505 | 19.4431 | 54215.4473 | 30723.372 | 5265.0398 | 6322.7457 | 0.035884 | 0.023457 | 0.000596 | 0.41228 | 0.23418 | 0.041228 | 0.0097596 | 5000000 | scaled
442-28R | 4758.7032 | 0 | 4758.7032 | 0 | 0% | 100% | 0% | 76.2363 | 159.6796 | 0.053769 | 64.9124 | 11.2701 | 0.11262 | 135.9613 | 23.6057 | 442 |  | 794 | 442-28R | 4758.7032 | 4682.4669 | 4599.0236 | 0 | 0 | 0 | 4758.7032 | 4682.4669 | 4599.0236 | 0 | 3.3563 | 3.3025 | 3.2437 | 0 | 0 | 0 | 3.3563 | 3.3025 | 3.2437 | 0 | 703.4857 | 692.2156 | 679.8801 | 0 | 0 | 0 | 703.4857 | 692.2156 | 679.8801 | 0 | 4051.8612 | 3986.9487 | 3915.8998 | 0 | 0 | 0 | 4051.8612 | 3986.9487 | 3915.8998 | 0 | 0 | 0 | 0 | 0.35262 | 0.35262 | 0.35262 | 0 | 5000000 | scaled
442-46R | 88141.0044 | 1537.9427 | 86528.6053 | 74.4565 | 1.745% | 98.17% | 0.08447% | 1859.7612 | 4431.9095 | 29.2306 | 1263.834 | 566.6966 | 88.1453 | 2647.2883 | 1696.4759 | 442 |  | 795 | 442-46R | 88141.0044 | 86281.2432 | 83709.0949 | 1537.9427 | 1069.7495 | 20.4446 | 86528.6053 | 85137.0373 | 83614.1938 | 74.4565 | 171.5602 | 142.3296 | 83.415 | 86.3929 | 58.5311 | 1.1143 | 85.1113 | 83.7425 | 82.2446 | 0.056026 | 9327.8008 | 8761.1041 | 7631.3249 | 1450.7078 | 1010.5832 | 19.3162 | 7870.3293 | 7743.7573 | 7605.245 | 6.7637 | 78641.6435 | 77377.8095 | 75994.3551 | 0.842 | 0.63521 | 0.014101 | 78573.1647 | 77309.5375 | 75926.7042 | 67.6368 | 0.0001902 | 0.0001446 | 3.6e-06 | 0.35062 | 0.35062 | 0.35062 | 0.0001062 | 5000000 | scaled
442-509R | 852926.0641 | 724344.0959 | 125551.1302 | 3030.838 | 84.92% | 14.72% | 0.3553% | 293202.8982 | 829385.3841 | 13422.0511 | 48819.086 | 230961.7611 | 40326.8218 | 102195.8031 | 686862.7593 | 442 |  | 796 | 442-509R | 852926.0641 | 559723.1659 | 23540.68 | 724344.0959 | 485534.3711 | 8379.7953 | 125551.1302 | 71157.9568 | 12130.0467 | 3030.838 | 40828.2499 | 27406.1988 | 501.4281 | 40661.7072 | 27310.8203 | 483.2774 | 164.2621 | 93.0979 | 15.8701 | 2.2806 | 696294.7919 | 465333.0308 | 9432.0327 | 682804.1119 | 457567.7089 | 7879.9156 | 13215.3567 | 7489.9985 | 1276.7937 | 275.3234 | 115803.0223 | 66983.9363 | 13607.2192 | 878.2768 | 655.8419 | 16.6023 | 112171.5115 | 63574.8604 | 10837.3829 | 2753.234 | 0.016721 | 0.011445 | 0.0002898 | 0.34854 | 0.19808 | 0.034854 | 0.0042844 | 5000000 | scaled
442-525 | 526126.3204 | 304903.9024 | 218705.8748 | 2516.5432 | 57.95% | 41.57% | 0.4783% | 212875.0044 | 496670.2402 | 7656.3299 | 84928.5971 | 120290.0774 | 19725.7819 | 177327.9413 | 299616.517 | 442 |  | 797 | 442-525 | 526126.3204 | 313251.3161 | 29456.0803 | 304903.9024 | 186795.5771 | 5818.9658 | 218705.8748 | 123939.1957 | 21120.5712 | 2516.5432 | 20141.1485 | 12484.8187 | 415.3666 | 19533.6269 | 12139.7196 | 354.9871 | 605.628 | 343.2055 | 58.4859 | 1.8936 | 307468.0303 | 187177.953 | 7851.5134 | 284767.5795 | 174214.6994 | 5452.7878 | 22471.8463 | 12734.649 | 2170.1211 | 228.6045 | 198517.1416 | 113588.5444 | 21189.2003 | 602.696 | 441.1581 | 11.191 | 195628.4005 | 110861.3412 | 18891.9642 | 2286.0451 | 0.014328 | 0.008951 | 0.0002274 | 0.34367 | 0.19531 | 0.034367 | 0.0035488 | 5000000 | scaled
442-728R | 11572220.9733 | 10238670.5132 | 1319166.7287 | 14383.7313 | 88.48% | 11.4% | 0.1243% | 3337779.8025 | 11256098.2896 | 221547.5996 | 521232.6512 | 2594999.5517 | 805481.6255 | 1093211.9605 | 9357404.7037 | 442 |  | 798 | 442-728R | 11572220.9733 | 8234441.1708 | 316122.6836 | 10238670.5132 | 7473342.9108 | 175694.5914 | 1319166.7287 | 746714.5286 | 126044.3609 | 14383.7313 | 819763.7327 | 598216.1331 | 14282.1073 | 817396.1215 | 596871.2496 | 14046.0965 | 2356.788 | 1334.0602 | 225.1875 | 10.8233 | 9531905.5424 | 6936905.9907 | 174500.8388 | 9406840.4695 | 6865545.876 | 161369.2808 | 123758.4449 | 70053.4867 | 11824.9299 | 1306.628 | 1220551.6981 | 699319.0469 | 127339.7376 | 14433.9223 | 10925.7852 | 279.214 | 1193051.4958 | 675326.9817 | 113994.2435 | 13066.28 | 0.077879 | 0.057449 | 0.0014604 | 0.25987 | 0.14764 | 0.025987 | 0.020269 | 5000000 | scaled
442-729 | 704609.103 | 680766.2423 | 22071.417 | 1771.4438 | 96.62% | 3.132% | 0.2514% | 155799.3613 | 663668.6866 | 7212.8286 | 7596.6914 | 140989.8413 | 31018.182 | 30308.0779 | 602342.4267 | 442 |  | 799 | 442-729 | 704609.103 | 548809.7417 | 40940.4164 | 680766.2423 | 525325.686 | 17848.6401 | 22071.417 | 21712.612 | 21320.3326 | 1771.4438 | 32016.4113 | 24803.5826 | 998.2292 | 31876.3012 | 24665.7286 | 862.8417 | 138.7771 | 136.5211 | 134.0546 | 1.333 | 622777.9428 | 481788.1015 | 20435.5161 | 618634.7628 | 477709.6593 | 16427.8514 | 3982.2608 | 3917.523 | 3846.7456 | 160.9192 | 49814.749 | 42218.0576 | 19506.6711 | 30255.1784 | 22950.2981 | 557.947 | 17950.379 | 17658.5678 | 17339.5324 | 1609.1916 | 0.011155 | 0.0084736 | 0.0002152 | 0.34698 | 0.34698 | 0.34698 | 0.0024576 | 5000000 | scaled
442-758F | 549982.9482 | 544073.9346 | 5023.2945 | 885.7191 | 98.93% | 0.9134% | 0.161% | 142067.0361 | 531437.8443 | 7124.2042 | 67.4929 | 134875.339 | 26847.3758 | 146.4751 | 504443.9934 | 442 |  | 800 | 442-758F | 549982.9482 | 407915.9121 | 18545.1039 | 544073.9346 | 402088.7433 | 12807.4537 | 5023.2945 | 4941.4497 | 4851.9311 | 885.7191 | 27506.6926 | 20382.4884 | 659.3168 | 27502.7271 | 20378.5766 | 655.4638 | 3.2991 | 3.2453 | 3.1865 | 0.66648 | 517678.082 | 382802.743 | 13234.0886 | 516560.3895 | 381701.9503 | 12151.7801 | 1037.2332 | 1020.3335 | 1001.8492 | 80.4593 | 4798.1735 | 4730.6806 | 4651.6985 | 10.818 | 8.2164 | 0.20985 | 3982.7623 | 3917.8709 | 3846.8953 | 804.5933 | 0.0035648 | 0.0027078 | 6.86e-05 | 0.34641 | 0.34641 | 0.34641 | 0.0012104 | 5000000 | scaled
442-764R | 474737.5516 | 433481.3733 | 39522.8778 | 1733.3006 | 91.31% | 8.325% | 0.3651% | 107601.9202 | 428176.085 | 4697.8672 | 626.0417 | 102278.0113 | 18801.6775 | 1396.3524 | 407978.055 | 442 |  | 801 | 442-764R | 474737.5516 | 367135.6315 | 46561.4667 | 433481.3733 | 326526.1629 | 6661.2279 | 39522.8778 | 38876.168 | 38166.9382 | 1733.3006 | 19176.4185 | 14478.5513 | 374.741 | 19101.2577 | 14404.599 | 302.114 | 73.8565 | 72.648 | 71.3227 | 1.3043 | 418145.4759 | 315867.4646 | 10167.4209 | 414203.9249 | 311987.8325 | 6355.6936 | 3784.0968 | 3722.1779 | 3654.2731 | 157.4542 | 37415.6572 | 36789.6156 | 36019.3048 | 176.1907 | 133.7314 | 3.4203 | 35664.9245 | 35081.3421 | 34441.3424 | 1574.5421 | 0.0074072 | 0.0056266 | 0.0001434 | 0.3446 | 0.3446 | 0.3446 | 0.0024734 | 5000000 | scaled
442-780 | 141384.6246 | 72107.4765 | 68584.3745 | 692.7736 | 51% | 48.51% | 0.49% | 20699.0334 | 72720.1966 | 1394.054 | 1314.702 | 17990.2774 | 4982.1275 | 3386.5542 | 64351.515 | 442 |  | 802 | 442-780 | 141384.6246 | 120685.5912 | 68664.428 | 72107.4765 | 52540.4408 | 1760.2224 | 68584.3745 | 67452.3768 | 66211.432 | 692.7736 | 5197.8265 | 3803.7725 | 215.699 | 5096.5471 | 3704.1561 | 117.9057 | 100.7581 | 99.0951 | 97.272 | 0.52129 | 73431.0602 | 55440.7828 | 9079.5452 | 65703.9754 | 47840.1962 | 1617.6315 | 7664.1528 | 7537.6546 | 7398.9817 | 62.932 | 62755.7379 | 61441.0359 | 59369.1837 | 1306.9541 | 996.0885 | 24.6852 | 60819.4635 | 59815.6271 | 58715.1783 | 629.3203 | 0.0039088 | 0.0029692 | 7.54e-05 | 0.34111 | 0.34111 | 0.34111 | 0.0009836 | 5000000 | scaled
442-784 | 3030.3346 | 0 | 3030.3346 | 0 | 0% | 100% | 0% | 35.5579 | 74.3345 | 0.027081 | 32.6928 | 2.8381 | 0.056613 | 68.3449 | 5.933 | 442 |  | 803 | 442-784 | 3030.3346 | 2994.7767 | 2956 | 0 | 0 | 0 | 3030.3346 | 2994.7767 | 2956 | 0 | 2.3079 | 2.2808 | 2.2513 | 0 | 0 | 0 | 2.3079 | 2.2808 | 2.2513 | 0 | 241.8671 | 239.029 | 235.934 | 0 | 0 | 0 | 241.8671 | 239.029 | 235.934 | 0 | 2786.1596 | 2753.4669 | 2717.8147 | 0 | 0 | 0 | 2786.1596 | 2753.4669 | 2717.8147 | 0 | 0 | 0 | 0 | 0.48948 | 0.48948 | 0.48948 | 0 | 5000000 | scaled
443-218R | 96981.3555 | 93015.4202 | 2874.1861 | 1091.7492 | 95.91% | 2.964% | 1.126% | 40468.852 | 95194.6776 | 3468.3585 | 1002.3588 | 35998.1348 | 8187.6757 | 2087.1593 | 84919.8427 | 443 |  | 804 | 443-218R | 96981.3555 | 56512.5035 | 1786.6779 | 93015.4202 | 53808.7939 | 442.011 | 2874.1861 | 1611.9604 | 252.9176 | 1091.7492 | 8233.093 | 4764.7346 | 45.4174 | 8194.9841 | 4743.0007 | 41.3147 | 37.2874 | 20.9123 | 3.2812 | 0.82151 | 85470.7627 | 49472.628 | 550.9201 | 84785.4265 | 49044.7098 | 400.1649 | 586.161 | 328.7429 | 51.58 | 99.1752 | 3277.4997 | 2275.141 | 1190.3404 | 35.0096 | 21.0834 | 0.5315 | 2250.7377 | 1262.3052 | 198.0565 | 991.7524 | 0.0054822 | 0.0031826 | 8.1e-05 | 0.08917 | 0.050531 | 0.008917 | 0.0015238 | 5000000 | scaled
444-15R | 333846.4836 | 322553.9108 | 7712.9833 | 3579.5895 | 96.62% | 2.31% | 1.072% | 178035.5798 | 324958.1848 | 12082.3792 | 3139.3627 | 162813.8379 | 21905.0259 | 6464.9415 | 296588.2175 | 444 |  | 805 | 444-15R | 333846.4836 | 155810.9038 | 8888.2988 | 322553.9108 | 147901.5927 | 4631.5884 | 7712.9833 | 4329.7215 | 677.1209 | 3579.5895 | 22233.99 | 10151.6108 | 328.9641 | 22197.9118 | 10130.1766 | 323.3398 | 33.3847 | 18.7407 | 2.9308 | 2.6935 | 301309.2951 | 138495.4572 | 4721.0776 | 299929.7108 | 137578.3855 | 4303.3387 | 1054.4119 | 591.8994 | 92.5666 | 325.1724 | 10303.1985 | 7163.8358 | 3838.2571 | 426.2882 | 193.0307 | 4.91 | 6625.1867 | 3719.0815 | 581.6235 | 3251.7236 | 0.056535 | 0.026824 | 0.0006818 | 0.087289 | 0.049519 | 0.008729 | 0.0050368 | 5000000 | scaled
444-43R | 3413813.7465 | 3334274.9115 | 68095.9501 | 11442.8848 | 97.67% | 1.995% | 0.3352% | 1012340.4771 | 3340610.861 | 55650.8773 | 33564.1032 | 923125.4965 | 185878.0033 | 84916.513 | 3069816.3447 | 444 |  | 806 | 444-43R | 3413813.7465 | 2401473.2694 | 73202.8855 | 3334274.9115 | 2351796.6124 | 55782.7213 | 68095.9501 | 38233.7721 | 5977.2794 | 11442.8848 | 189061.0643 | 133410.1869 | 3183.061 | 188822.3865 | 133272.4008 | 3154.2559 | 230.0673 | 129.1757 | 20.1947 | 8.6104 | 3123568.8614 | 2200443.3648 | 53752.5166 | 3114731.5257 | 2195025.63 | 52028.5623 | 7797.8562 | 4378.2553 | 684.4748 | 1039.4795 | 101183.8209 | 67619.7176 | 16267.3079 | 30720.9993 | 23498.5816 | 599.9031 | 60068.0266 | 33726.3411 | 5272.6099 | 10394.7949 | 0.10918 | 0.07692 | 0.0019536 | 0.087106 | 0.049426 | 0.0087106 | 0.01612 | 5000000 | scaled
444-9R | 571237.272 | 403911.3246 | 159549.0562 | 7776.8912 | 70.71% | 27.93% | 1.361% | 245066.4953 | 543818.4063 | 12752.3845 | 66969.889 | 165344.2218 | 28949.5807 | 140543.6854 | 374325.1401 | 444 |  | 807 | 444-9R | 571237.272 | 326170.7767 | 27418.8657 | 403911.3246 | 228790.768 | 5639.9561 | 159549.0562 | 89603.1175 | 14002.0184 | 7776.8912 | 29380.3241 | 16627.9396 | 430.7434 | 29129.5521 | 16484.5401 | 403.3974 | 244.9201 | 137.5477 | 21.4942 | 5.8519 | 381555.3427 | 216211.1209 | 7230.2025 | 364436.7942 | 206287.595 | 5083.42 | 16412.0904 | 9217.0678 | 1440.3244 | 706.4581 | 160301.6052 | 93331.7162 | 19757.9198 | 10344.9783 | 6018.633 | 153.1387 | 142892.0457 | 80248.502 | 12540.1999 | 7064.5812 | 0.050995 | 0.027925 | 0.0007102 | 0.086862 | 0.0493 | 0.0086862 | 0.010941 | 5000000 | scaled
445-1311R | 9632590.7157 | 9146838.7204 | 478216.1764 | 7535.8189 | 94.96% | 4.965% | 0.07823% | 3755362.8723 | 9432241.5342 | 213809.9926 | 188371.3574 | 3353181.5224 | 542992.1972 | 394865.052 | 8494384.285 | 445 |  | 808 | 445-1311R | 9632590.7157 | 5877227.8434 | 200349.1815 | 9146838.7204 | 5598796.3696 | 146239.1589 | 478216.1764 | 270895.6549 | 46574.2038 | 7535.8189 | 551926.5163 | 338116.5237 | 8934.3191 | 551094.8607 | 337642.9565 | 8848.2047 | 825.9851 | 467.8967 | 80.4439 | 5.6705 | 8637016.4162 | 5283834.8939 | 142632.1312 | 8588165.2217 | 5255865.3268 | 137256.5501 | 48166.6356 | 27285.0082 | 4691.0222 | 684.5589 | 443647.7833 | 255276.4259 | 48782.7313 | 7578.638 | 5288.0863 | 134.4042 | 429223.5558 | 243142.75 | 41802.7376 | 6845.5895 | 0.068253 | 0.04142 | 0.0010516 | 0.45906 | 0.2606 | 0.045906 | 0.010607 | 5000000 | scaled
445-1315 | 26249.3638 | 26142.282 | 0 | 107.0818 | 99.59% | 0% | 0.4079% | 5530.5942 | 26128.886 | 316.9112 | 318.2931 | 4895.3898 | 1558.9738 | 1263.2857 | 23306.6265 | 445 |  | 809 | 445-1315 | 26249.3638 | 20718.7696 | 120.4778 | 26142.282 | 20611.6878 | 13.396 | 0 | 0 | 0 | 107.0818 | 1559.0544 | 1242.1431 | 0.080576 | 1558.9738 | 1242.0626 | 0 | 0 | 0 | 0 | 0.080576 | 23316.3539 | 18420.9641 | 9.7274 | 23306.6265 | 18411.2367 | 0 | 0 | 0 | 0 | 9.7274 | 1373.9555 | 1055.6624 | 110.6698 | 1276.6817 | 958.3885 | 13.396 | 0 | 0 | 0 | 97.2739 | 0.0004822 | 0.0003664 | 9.4e-06 | 0 | 0 | 0 | 0.0001538 | 5000000 | scaled
445-1323 | 78543.8978 | 77963.6375 | 412.3474 | 167.9129 | 99.26% | 0.525% | 0.2138% | 23342.4195 | 76992.1878 | 1269.5125 | 51.617 | 22021.2899 | 4206.4188 | 108.3719 | 72677.397 | 445 |  | 810 | 445-1323 | 78543.8978 | 55201.4784 | 1551.71 | 77963.6375 | 54676.9345 | 1087.5906 | 412.3474 | 356.6309 | 296.2065 | 167.9129 | 4264.3632 | 2994.8506 | 57.9443 | 4263.9228 | 2994.4527 | 57.5924 | 0.31404 | 0.27161 | 0.22559 | 0.12635 | 73746.2593 | 51724.9694 | 1068.8623 | 73698.0943 | 51681.2514 | 1029.9671 | 32.9116 | 28.4646 | 23.6418 | 15.2533 | 533.2754 | 481.6584 | 424.9034 | 1.6204 | 1.2304 | 0.031099 | 379.1218 | 327.8947 | 272.3391 | 152.5332 | 0.000695 | 0.0005278 | 1.32e-05 | 0.024519 | 0.024519 | 0.024519 | 0.0002312 | 5000000 | scaled
445-1325F | 7250722.8788 | 6968326.4254 | 275900.7801 | 6495.6733 | 96.11% | 3.805% | 0.08959% | 2228211.9938 | 7090112.0893 | 120257.6385 | 106723.5336 | 2001230.8217 | 390804.1982 | 222875.0076 | 6476432.8835 | 445 |  | 811 | 445-1325F | 7250722.8788 | 5022510.885 | 160610.7895 | 6968326.4254 | 4859669.2605 | 127171.2623 | 275900.7801 | 156345.9513 | 26943.854 | 6495.6733 | 398153.953 | 277896.3145 | 7349.7548 | 397609.3521 | 277585.585 | 7292.1599 | 539.7132 | 305.8417 | 52.7072 | 4.8878 | 6599795.6747 | 4598564.853 | 123362.7913 | 6569275.8311 | 4581014.3413 | 119849.8452 | 29929.7722 | 16960.4403 | 2922.8747 | 590.0714 | 252773.2511 | 146049.7175 | 29898.2434 | 1441.2422 | 1069.3342 | 29.2572 | 245431.2948 | 139079.6693 | 23968.2721 | 5900.7141 | 0.050439 | 0.035595 | 0.0010326 | 0.51389 | 0.29177 | 0.051389 | 0.0092334 | 5000000 | scaled
445-17R | 1603556.2116 | 1422687.9571 | 178893.509 | 1974.7455 | 88.72% | 11.16% | 0.1231% | 486833.8137 | 1557279.257 | 23204.5545 | 69100.0164 | 394529.2427 | 79123.6094 | 144079.0372 | 1334076.6104 | 445 |  | 812 | 445-17R | 1603556.2116 | 1116722.3979 | 46276.9546 | 1422687.9571 | 1013395.598 | 26828.5015 | 178893.509 | 101352.0544 | 17473.7076 | 1974.7455 | 80673.4809 | 57468.9264 | 1549.8715 | 80359.5327 | 57290.415 | 1517.8653 | 312.4623 | 177.0254 | 30.5203 | 1.4859 | 1361456.3057 | 966927.063 | 27379.6953 | 1341833.8654 | 955732.2209 | 25301.1769 | 19443.0531 | 11015.4549 | 1899.1311 | 179.3872 | 161426.425 | 92326.4086 | 17347.3878 | 494.5591 | 372.9621 | 9.4592 | 159137.9936 | 90159.5742 | 15544.0563 | 1793.8723 | 0.013088 | 0.0095288 | 0.0002426 | 0.51842 | 0.29427 | 0.051842 | 0.002754 | 5000000 | scaled
445-18R | 10619796.7202 | 10161861.8372 | 443951.1893 | 13983.6937 | 95.69% | 4.18% | 0.1317% | 4609242.9485 | 10399739.8322 | 255021.1547 | 172445.8477 | 4181775.9461 | 577170.9819 | 360472.0852 | 9462096.7651 | 445 |  | 813 | 445-18R | 10619796.7202 | 6010553.7717 | 220056.8879 | 10161861.8372 | 5745020.6839 | 162787.9252 | 443951.1893 | 251549.3941 | 43285.2691 | 13983.6937 | 586641.5011 | 331620.3464 | 9470.5192 | 585356.6085 | 330887.7468 | 9335.7457 | 1274.3704 | 722.0773 | 124.2512 | 10.5223 | 9621465.1577 | 5439689.2116 | 159368.3926 | 9571715.9697 | 5410950.0526 | 153371.4085 | 48478.8997 | 27468.8707 | 4726.6958 | 1270.2883 | 411690.0613 | 239244.2136 | 51217.9761 | 4789.259 | 3182.8845 | 80.771 | 394197.9192 | 223358.446 | 38434.3221 | 12702.8831 | 0.1044 | 0.057863 | 0.0014684 | 0.4807 | 0.27294 | 0.04807 | 0.019698 | 5000000 | scaled
445-19R | 1766703.6515 | 1496872.4097 | 263270.2283 | 6561.0135 | 84.73% | 14.9% | 0.3714% | 318311.6484 | 1703007.2256 | 11880.0046 | 102604.153 | 203827.4909 | 83493.4122 | 213958.4146 | 1405555.3987 | 445 |  | 814 | 445-19R | 1766703.6515 | 1448392.003 | 63696.4259 | 1496872.4097 | 1292627.7572 | 31427.7541 | 263270.2283 | 149203.2324 | 25707.6583 | 6561.0135 | 85304.269 | 73424.2644 | 1810.8567 | 84939.2481 | 73215.257 | 1770.7585 | 360.0839 | 204.0705 | 35.1613 | 4.937 | 1438392.0474 | 1234564.5565 | 32836.6487 | 1411202.8793 | 1218897.3976 | 29643.8882 | 26593.1611 | 15071.1519 | 2596.7536 | 596.007 | 243007.3351 | 140403.1821 | 29048.9205 | 730.2822 | 515.1026 | 13.1074 | 236316.9833 | 133928.01 | 23075.7435 | 5960.0696 | 0.043013 | 0.037068 | 0.0009418 | 0.51308 | 0.29135 | 0.051308 | 0.0091738 | 5000000 | scaled
445-39R | 3678580.6505 | 3220260.9918 | 453523.9109 | 4795.7478 | 87.54% | 12.33% | 0.1304% | 793472.3686 | 3563877.5035 | 35951.8639 | 185312.8081 | 572207.6967 | 187738.2086 | 403401.4018 | 2972737.8931 | 445 |  | 815 | 445-39R | 3678580.6505 | 2885108.2819 | 114703.147 | 3220260.9918 | 2623197.8715 | 65774.365 | 453523.9109 | 257114.6626 | 44133.0342 | 4795.7478 | 191668.1206 | 155716.2567 | 3929.912 | 190899.9307 | 155279.1868 | 3851.9009 | 764.5813 | 433.4613 | 74.4025 | 3.6086 | 3038856.3046 | 2466648.608 | 66118.4115 | 2992506.8163 | 2440183.1929 | 61214.8238 | 45913.8393 | 26029.766 | 4467.9387 | 435.649 | 448056.2253 | 262743.4172 | 44654.8235 | 36854.2448 | 27735.4918 | 707.6403 | 406845.4903 | 230651.4352 | 39590.693 | 4356.4902 | 0.037532 | 0.030267 | 0.0007668 | 0.44565 | 0.25321 | 0.044565 | 0.006787 | 5000000 | scaled
445-894R | 4421002.3515 | 3895845.1495 | 508789.1916 | 16368.0103 | 88.12% | 11.51% | 0.3702% | 976821.3481 | 4275773.2905 | 39617.4847 | 198417.3238 | 738786.5397 | 194414.5246 | 417276.4517 | 3664082.3142 | 445 |  | 816 | 445-894R | 4421002.3515 | 3444181.0033 | 145229.061 | 3895845.1495 | 3139341.129 | 79199.3588 | 508789.1916 | 288471.864 | 49661.6919 | 16368.0103 | 198551.4363 | 158933.9515 | 4136.9116 | 197496.4858 | 158330.4854 | 4022.8262 | 1042.634 | 591.1497 | 101.769 | 12.3164 | 3745769.3462 | 3006982.8065 | 81687.032 | 3691386.5598 | 2975505.1539 | 75037.1084 | 52895.9051 | 29990.7714 | 5163.0423 | 1486.8813 | 476681.569 | 278264.2453 | 59405.1174 | 6962.1038 | 5505.4897 | 139.4242 | 454850.6525 | 257889.9429 | 44396.8805 | 14868.8127 | 0.1094 | 0.089637 | 0.0022776 | 0.50288 | 0.28569 | 0.050288 | 0.022971 | 5000000 | scaled
445-897R | 1351774.7323 | 1314501.5554 | 36645.0715 | 628.1054 | 97.24% | 2.711% | 0.04647% | 351458.0337 | 1315523.1527 | 19008.5478 | 16467.8927 | 315981.5932 | 72740.8711 | 38164.5369 | 1204617.7447 | 445 |  | 817 | 445-897R | 1351774.7323 | 1000316.6986 | 36251.5796 | 1314501.5554 | 978898.1289 | 32020.7306 | 36645.0715 | 20790.4642 | 3602.7436 | 628.1054 | 74538.3312 | 55529.7834 | 1797.4601 | 74482.0838 | 55497.6671 | 1791.504 | 55.7748 | 31.6436 | 5.4835 | 0.47263 | 1235040.9691 | 919059.3758 | 30423.2244 | 1232061.2999 | 917344.1839 | 30078.8316 | 2922.6116 | 1658.1344 | 287.3352 | 57.0575 | 42195.4321 | 25727.5394 | 4030.8952 | 7958.1717 | 6056.2779 | 150.395 | 33666.6851 | 19100.6862 | 3309.9249 | 570.5753 | 0.010333 | 0.0077794 | 0.0001974 | 0.74516 | 0.42335 | 0.074515 | 0.00088 | 5000000 | scaled
448-1196F | 16695.9819 | 16597.3603 | 0 | 98.6216 | 99.41% | 0% | 0.5907% | 2087.1811 | 16535.1588 | 121.0697 | 17.9001 | 1948.2113 | 901.926 | 69.9924 | 15563.2405 | 448 |  | 818 | 448-1196F | 16695.9819 | 14608.8008 | 160.8231 | 16597.3603 | 14510.1792 | 62.2015 | 0 | 0 | 0 | 98.6216 | 907.3385 | 786.2688 | 5.4126 | 907.2643 | 786.1946 | 5.3384 | 0 | 0 | 0 | 0.07421 | 15627.712 | 13679.5007 | 64.4715 | 15618.7531 | 13670.5419 | 55.5126 | 0 | 0 | 0 | 8.9589 | 160.9314 | 143.0313 | 90.939 | 71.3429 | 53.4428 | 1.3505 | 0 | 0 | 0 | 89.5885 | 9.74e-05 | 7.4e-05 | 2e-06 | 0 | 0 | 0 | 0.0001458 | 5000000 | scaled
448-1202 | 17607.0914 | 0 | 17607.0914 | 0 | 0% | 100% | 0% | 166.2835 | 348.1107 | 0.10921 | 131.8393 | 34.335 | 0.22862 | 276.0025 | 71.8795 | 448 |  | 819 | 448-1202 | 17607.0914 | 17440.808 | 17258.9808 | 0 | 0 | 0 | 17607.0914 | 17440.808 | 17258.9808 | 0 | 11.5635 | 11.4543 | 11.3349 | 0 | 0 | 0 | 11.5635 | 11.4543 | 11.3349 | 0 | 3635.5939 | 3601.259 | 3563.7144 | 0 | 0 | 0 | 3635.5939 | 3601.259 | 3563.7144 | 0 | 13959.934 | 13828.0947 | 13683.9314 | 0 | 0 | 0 | 13959.934 | 13828.0947 | 13683.9314 | 0 | 0 | 0 | 0 | 0.61612 | 0.61612 | 0.61612 | 0 | 5000000 | scaled
448-1203F | 57382.8736 | 0 | 57382.8736 | 0 | 0% | 100% | 0% | 543.2423 | 1137.0933 | 3.1942 | 428.4632 | 111.5849 | 6.686 | 896.8422 | 233.5651 | 448 |  | 820 | 448-1203F | 57382.8736 | 56839.6312 | 56245.7802 | 0 | 0 | 0 | 57382.8736 | 56839.6312 | 56245.7802 | 0 | 337.4056 | 334.2114 | 330.7196 | 0 | 0 | 0 | 337.4056 | 334.2114 | 330.7196 | 0 | 11786.7539 | 11675.169 | 11553.1888 | 0 | 0 | 0 | 11786.7539 | 11675.169 | 11553.1888 | 0 | 45258.7141 | 44830.2509 | 44361.8719 | 0 | 0 | 0 | 45258.7141 | 44830.2509 | 44361.8719 | 0 | 0 | 0 | 0 | 0.61459 | 0.61459 | 0.61459 | 0 | 5000000 | scaled
448-1234R | 1211619.4268 | 1179994.5966 | 29987.3377 | 1637.4925 | 97.39% | 2.475% | 0.1351% | 287.2693 | 1151610.0395 | 0.54633 | 263.8207 | 22.9023 | 61622.0054 | 602.9138 | 1089385.1202 | 448 |  | 821 | 448-1234R | 1211619.4268 | 1211332.1575 | 60009.3873 | 1179994.5966 | 1179994.5966 | 28985.2864 | 29987.3377 | 29700.0684 | 29386.6084 | 1637.4925 | 63213.8318 | 63213.2855 | 1591.8264 | 63155.5694 | 63155.5694 | 1534.7065 | 57.0302 | 56.4839 | 55.8877 | 1.2322 | 1119325.9367 | 1119303.0344 | 29940.8165 | 1116786.4684 | 1116786.4684 | 27449.2409 | 2390.7173 | 2367.815 | 2342.8246 | 148.7509 | 29079.6583 | 28815.8376 | 28476.7445 | 52.5588 | 52.5588 | 1.3391 | 27539.5902 | 27275.7695 | 26987.8961 | 1487.5094 | 0.011189 | 0.011189 | 0.0002848 | 0.60757 | 0.60757 | 0.60757 | 0.0022506 | 5000000 | scaled
448-47R | 2612271.1194 | 2400903.4768 | 205973.7563 | 5393.8864 | 91.91% | 7.885% | 0.2065% | 7737.7424 | 2340300.8846 | 317.3126 | 1808.9177 | 5611.512 | 131917.8615 | 4983.3235 | 2203399.6996 | 448 |  | 822 | 448-47R | 2612271.1194 | 2604533.3771 | 271970.2348 | 2400903.4768 | 2395185.7403 | 64827.0933 | 205973.7563 | 203953.7504 | 201749.2552 | 5393.8864 | 135851.9628 | 135534.6502 | 3934.1013 | 135575.6668 | 135261.0241 | 3663.3889 | 272.2372 | 269.5674 | 266.6537 | 4.0587 | 2285838.5452 | 2280227.0331 | 82438.8455 | 2264096.1816 | 2258693.0939 | 61132.3662 | 21252.3792 | 21043.9549 | 20816.495 | 489.9843 | 190580.6115 | 188771.6938 | 185597.288 | 1231.6283 | 1231.6223 | 31.3382 | 184449.1398 | 182640.2281 | 180666.1065 | 4899.8433 | 0.029615 | 0.02958 | 0.000751 | 0.5916 | 0.5916 | 0.5916 | 0.0076048 | 5000000 | scaled
448-714R | 2119752.047 | 1180661.9166 | 931759.2323 | 7330.8981 | 55.7% | 43.96% | 0.3458% | 493516.6575 | 1997465.4251 | 5741.0835 | 362123.1204 | 125652.4536 | 69007.9629 | 757351.6793 | 1171105.783 | 448 |  | 823 | 448-714R | 2119752.047 | 1626235.3895 | 122286.6219 | 1180661.9166 | 1090769.2607 | 24435.3496 | 931759.2323 | 528135.2307 | 90520.3742 | 7330.8981 | 70593.5351 | 64852.4516 | 1585.5723 | 69013.8033 | 63954.6461 | 1427.121 | 1574.2155 | 892.2892 | 152.935 | 5.5163 | 1204121.6749 | 1078469.2214 | 33015.892 | 1106213.9779 | 1022685.1805 | 22902.9155 | 97241.7532 | 55118.097 | 9447.0326 | 665.9438 | 845036.837 | 482913.7165 | 87685.1577 | 5434.1354 | 4129.434 | 105.3131 | 832943.2635 | 472124.8445 | 80920.4066 | 6659.438 | 0.034232 | 0.030983 | 0.0007882 | 0.41879 | 0.23792 | 0.041879 | 0.010411 | 5000000 | scaled
448-724R | 520638.974 | 396646.0173 | 118589.4581 | 5403.4986 | 76.18% | 22.78% | 1.038% | 86458.5699 | 495501.954 | 1892.6856 | 44694.7106 | 39871.1736 | 19287.6865 | 95950.6665 | 380263.601 | 448 |  | 824 | 448-724R | 520638.974 | 434180.4041 | 25137.02 | 396646.0173 | 361493.0457 | 8150.6003 | 118589.4581 | 67283.8598 | 11582.9212 | 5403.4986 | 19731.7047 | 17839.019 | 444.0182 | 19463.8054 | 17685.2625 | 414.183 | 263.8333 | 149.6906 | 25.7692 | 4.066 | 389893.902 | 350022.7284 | 9630.3011 | 374298.0302 | 340961.7696 | 7664.1 | 15105.0143 | 8570.1013 | 1475.3435 | 490.8575 | 111013.3673 | 66318.6566 | 15062.7007 | 2884.1817 | 2846.0136 | 72.3172 | 103220.6104 | 58564.0679 | 10081.8084 | 4908.5751 | 0.024005 | 0.021805 | 0.0005532 | 0.51879 | 0.2949 | 0.051879 | 0.007558 | 5000000 | scaled
448-735R | 630762.6745 | 499073.4843 | 126725.7606 | 4963.4296 | 79.12% | 20.09% | 0.7869% | 1424.9167 | 491738.9948 | 1.9834 | 1246.3966 | 176.5367 | 28420.0452 | 4246.342 | 459072.6075 | 448 |  | 825 | 448-735R | 630762.6745 | 629337.7577 | 139023.6797 | 499073.4843 | 499073.4843 | 10314.1174 | 126725.7606 | 125300.8439 | 123746.1327 | 4963.4296 | 29207.5396 | 29205.5563 | 787.4944 | 29027.413 | 29027.413 | 611.5152 | 176.3918 | 174.4085 | 172.2444 | 3.7348 | 484514.374 | 484337.8372 | 25441.7664 | 468363.0994 | 468363.0994 | 9659.646 | 15700.3932 | 15523.8564 | 15331.2391 | 450.8813 | 117040.7609 | 115794.3642 | 112794.4188 | 1682.9718 | 1682.9718 | 42.9563 | 110848.9756 | 109602.579 | 108242.6492 | 4508.8134 | 0.02203 | 0.02203 | 0.000559 | 0.51301 | 0.51301 | 0.51301 | 0.0069734 | 5000000 | scaled
448-744R | 9104561.6318 | 8347199.644 | 739812.5409 | 17549.4469 | 91.68% | 8.126% | 0.1928% | 1335201.446 | 8835293.0749 | 59293.1868 | 289742.208 | 986166.0512 | 474191.6789 | 608269.8258 | 7752831.5702 | 448 |  | 826 | 448-744R | 9104561.6318 | 7769360.1857 | 269268.5568 | 8347199.644 | 7332660.2215 | 180058.555 | 739812.5409 | 419150.5173 | 71660.5548 | 17549.4469 | 484758.3102 | 425465.1234 | 10566.6313 | 483701.8876 | 424860.8695 | 10452.3766 | 1043.2172 | 591.0484 | 101.0493 | 13.2054 | 7930792.6443 | 6944626.5931 | 177961.0741 | 7858068.3022 | 6902732.6747 | 169476.9828 | 71130.1383 | 40299.7146 | 6889.8875 | 1594.2038 | 689010.6773 | 399268.4693 | 80740.8515 | 5429.4542 | 5066.6772 | 129.1956 | 667639.1854 | 378259.7543 | 64669.6181 | 15942.0377 | 0.091514 | 0.080387 | 0.0020422 | 0.37815 | 0.21479 | 0.037815 | 0.024753 | 5000000 | scaled
448-9R | 5644810.8618 | 5273684.8346 | 360369.0586 | 10756.9686 | 93.43% | 6.384% | 0.1906% | 967444.3189 | 5483593.0408 | 46419.2573 | 144189.2839 | 776835.7776 | 292813.3438 | 309601.2535 | 4881178.4435 | 448 |  | 827 | 448-9R | 5644810.8618 | 4677366.5429 | 161217.821 | 5273684.8346 | 4462424.7107 | 115336.7608 | 360369.0586 | 204184.8637 | 35124.0916 | 10756.9686 | 299433.064 | 253013.8067 | 6619.7202 | 299040.9078 | 252788.1032 | 6574.1925 | 384.0619 | 217.6092 | 37.4334 | 8.0943 | 4994121.9807 | 4217286.203 | 112943.5372 | 4956639.1168 | 4195624.9315 | 108408.2663 | 36505.6934 | 20684.1011 | 3558.1005 | 977.1704 | 351255.8172 | 207066.5333 | 41654.5637 | 18004.81 | 14011.676 | 354.302 | 323479.3033 | 183283.1534 | 31528.5577 | 9771.7039 | 0.055676 | 0.047361 | 0.001201 | 0.47319 | 0.26866 | 0.047319 | 0.015075 | 5000000 | scaled
449-13R | 6729964.7304 | 6090025.9061 | 628975.8541 | 10962.9702 | 90.49% | 9.346% | 0.1629% | 3474807.1082 | 6580378.3576 | 209197.2723 | 251861.7222 | 3013748.1137 | 392480.0666 | 523529.3069 | 5664368.9841 | 449 |  | 828 | 449-13R | 6729964.7304 | 3255157.6222 | 149586.3728 | 6090025.9061 | 2888444.8642 | 79044.8347 | 628975.8541 | 355749.7877 | 59578.5679 | 10962.9702 | 397736.6458 | 188539.3735 | 5256.5792 | 396782.775 | 187996.2791 | 5158.7576 | 945.6215 | 534.8451 | 89.5722 | 8.2493 | 5744701.915 | 2730953.8013 | 80332.9309 | 5685196.2806 | 2696864.7054 | 73794.8199 | 58509.7507 | 33093.2122 | 5542.2273 | 995.8837 | 587526.1696 | 335664.4474 | 63996.8627 | 8046.8505 | 3583.8797 | 91.2571 | 569520.4819 | 322121.7304 | 53946.7684 | 9958.8372 | 0.049545 | 0.023454 | 0.000612 | 0.21735 | 0.12348 | 0.021735 | 0.015449 | 5000000 | scaled
449-16R | 1495506.4659 | 1450226.1262 | 43776.0814 | 1504.2583 | 96.97% | 2.927% | 0.1006% | 558284.7175 | 1468187.6707 | 32222.9835 | 17394.1917 | 508667.5424 | 85410.7434 | 36324.8721 | 1346452.0552 | 449 |  | 829 | 449-16R | 1495506.4659 | 937221.7483 | 27318.7952 | 1450226.1262 | 910932.8793 | 21658.4408 | 43776.0814 | 24784.6107 | 4156.096 | 1504.2583 | 86720.7106 | 54497.7272 | 1309.9673 | 86677.5806 | 54472.8173 | 1304.8481 | 41.9981 | 23.778 | 3.9873 | 1.1319 | 1367292.4015 | 858624.8591 | 20840.3463 | 1363449.294 | 856389.7329 | 20351.8076 | 3706.4597 | 2098.4784 | 351.8908 | 136.6479 | 41493.3537 | 24099.162 | 5168.4816 | 99.2516 | 70.3291 | 1.7852 | 40027.6236 | 22662.3544 | 3800.2179 | 1366.4786 | 0.0071532 | 0.0046288 | 0.0001172 | 0.22813 | 0.12971 | 0.022813 | 0.0021002 | 5000000 | scaled
449-683 | 625312.9379 | 604656.2756 | 19735.4701 | 921.1921 | 96.7% | 3.156% | 0.1473% | 242057.6099 | 612209.1364 | 12097.8754 | 6772.3336 | 223187.4009 | 30912.9296 | 14140.4217 | 567155.7851 | 449 |  | 830 | 449-683 | 625312.9379 | 383255.3279 | 13103.8015 | 604656.2756 | 371142.9864 | 10277.8581 | 19735.4701 | 11191.1494 | 1904.7513 | 921.1921 | 31460.5516 | 19362.6762 | 547.6219 | 31379.1282 | 19316.2044 | 539.1372 | 80.7302 | 45.7787 | 7.7916 | 0.69317 | 577369.3446 | 354181.9437 | 10213.5595 | 573224.5939 | 351795.4017 | 9737.9273 | 4061.069 | 2302.8603 | 391.9504 | 83.6817 | 16483.0417 | 9710.7081 | 2342.62 | 52.5536 | 31.3804 | 0.79361 | 15593.6709 | 8842.5104 | 1505.0092 | 836.8172 | 0.0056884 | 0.0035234 | 8.92e-05 | 0.33881 | 0.19267 | 0.033881 | 0.0013068 | 5000000 | scaled
449-693R | 5260705.5579 | 5196144.7106 | 60632.213 | 3928.6343 | 98.77% | 1.153% | 0.07468% | 2068747.4752 | 5173469.5961 | 114996.0647 | 23885.3273 | 1929866.0832 | 287386.4381 | 49909.8766 | 4836173.2814 | 449 |  | 831 | 449-693R | 5260705.5579 | 3191958.0827 | 87235.9618 | 5196144.7106 | 3153704.2846 | 77551.3378 | 60632.213 | 34325.1638 | 5755.9897 | 3928.6343 | 291775.2654 | 176779.2008 | 4388.8273 | 291696.1195 | 176733.1119 | 4378.6382 | 76.1898 | 43.1326 | 7.2329 | 2.9562 | 4910256.0751 | 2980389.9919 | 74082.7936 | 4903997.4405 | 2976692.0053 | 73165.6433 | 5901.7547 | 3341.1068 | 560.2705 | 356.8798 | 58674.2174 | 34788.8901 | 8764.3408 | 451.1507 | 279.1674 | 7.0562 | 54654.2684 | 30940.9244 | 5188.4863 | 3568.7983 | 0.02757 | 0.016478 | 0.000418 | 0.2279 | 0.12958 | 0.02279 | 0.005597 | 5000000 | scaled
449-6R | 2320016.1538 | 2216709.8385 | 100168.8011 | 3137.5142 | 95.55% | 4.318% | 0.1352% | 1082343.7471 | 2203693.8438 | 60029.5806 | 43156.5521 | 979157.6144 | 122457.5976 | 91330.4513 | 1989905.7949 | 449 |  | 832 | 449-6R | 2320016.1538 | 1237672.4067 | 116322.31 | 2216709.8385 | 1177835.4574 | 103677.6401 | 100168.8011 | 56699.4352 | 9507.1557 | 3137.5142 | 128453.2163 | 68423.6357 | 5995.6186 | 128330.9504 | 68353.4039 | 5981.8774 | 119.905 | 67.8709 | 11.3803 | 2.3609 | 2088074.4792 | 1108916.8648 | 98168.6843 | 2079373.6391 | 1103868.1661 | 97084.913 | 8415.8262 | 4763.6848 | 798.7574 | 285.0139 | 103488.4584 | 60331.9062 | 12158.0071 | 9005.249 | 5613.8873 | 610.8498 | 91633.0699 | 51867.8795 | 8697.018 | 2850.1394 | 0.016402 | 0.0090308 | 0.0005438 | 0.227 | 0.12904 | 0.0227 | 0.0043882 | 5000000 | scaled
45-15AE | 8755.1054 | 8137.3184 | 0 | 617.7871 | 92.94% | 0% | 7.056% | 3866.1628 | 7997.6703 | 35.9808 | 3645.8099 | 184.3721 | 68.0469 | 7581.3829 | 348.2405 | 45 |  | 833 | 45-15AE | 8755.1054 | 4888.9427 | 757.4351 | 8137.3184 | 4271.1556 | 139.6481 | 0 | 0 | 0 | 617.7871 | 71.5449 | 35.5641 | 3.498 | 71.0801 | 35.0992 | 3.0332 | 0 | 0 | 0 | 0.46486 | 420.1743 | 235.8022 | 71.9338 | 364.0541 | 179.682 | 15.8136 | 0 | 0 | 0 | 56.1202 | 8263.3862 | 4617.5763 | 682.0033 | 7702.1842 | 4056.3743 | 120.8013 | 0 | 0 | 0 | 561.202 | 0.0013822 | 0.0007264 | 1.86e-05 | 0 | 0 | 0 | 0.0008762 | 5000000 | scaled
45-16 | 10660.9368 | 9199.2042 | 0 | 1461.7326 | 86.29% | 0% | 13.71% | 5285.1915 | 9103.6992 | 1122.6671 | 737.4166 | 3425.1077 | 1927.7377 | 1292.7659 | 5883.1956 | 45 |  | 834 | 45-16 | 10660.9368 | 5375.7454 | 1557.2377 | 9199.2042 | 3914.0128 | 95.5051 | 0 | 0 | 0 | 1461.7326 | 1949.4481 | 826.781 | 21.7105 | 1948.3482 | 825.6811 | 20.6105 | 0 | 0 | 0 | 1.0999 | 6077.2164 | 2652.1088 | 194.0208 | 5944.4316 | 2519.324 | 61.236 | 0 | 0 | 0 | 132.7848 | 2634.2723 | 1896.8556 | 1341.5064 | 1306.4244 | 569.0077 | 13.6585 | 0 | 0 | 0 | 1327.8479 | 0.0054512 | 0.0023602 | 5.96e-05 | 0 | 0 | 0 | 0.0021072 | 5000000 | scaled
450-113F | 1498.393 | 1424.8125 | 0 | 73.5805 | 95.09% | 0% | 4.911% | 933.9271 | 1424.8058 | 87.597 | 0.39654 | 845.9335 | 130.4961 | 0.69823 | 1293.6115 | 450 |  | 835 | 450-113F | 1498.393 | 564.4659 | 73.5872 | 1424.8125 | 490.8854 | 0.0066628 | 0 | 0 | 0 | 73.5805 | 130.5515 | 42.9545 | 0.055367 | 130.4961 | 42.8991 | 0 | 0 | 0 | 0 | 0.055367 | 1300.2956 | 454.3621 | 6.6841 | 1293.6115 | 447.678 | 0 | 0 | 0 | 0 | 6.6841 | 67.546 | 67.1494 | 66.8477 | 0.70489 | 0.30835 | 0.0066628 | 0 | 0 | 0 | 66.8411 | 0.0001564 | 6.76e-05 | 1.8e-06 | 0 | 0 | 0 | 0.0001012 | 5000000 | scaled
450-114F | 28614.9665 | 28133.0301 | 0 | 481.9364 | 98.32% | 0% | 1.684% | 13308.258 | 27947.0744 | 1108.9262 | 746.8659 | 11452.466 | 2293.4566 | 1278.3402 | 24375.2775 | 450 |  | 836 | 450-114F | 28614.9665 | 15306.7085 | 667.8921 | 28133.0301 | 14824.7721 | 185.9558 | 0 | 0 | 0 | 481.9364 | 2310.5769 | 1201.6507 | 17.1202 | 2310.2142 | 1201.2881 | 16.7576 | 0 | 0 | 0 | 0.36264 | 24575.1631 | 13122.6972 | 199.8856 | 24531.3837 | 13078.9177 | 156.1062 | 0 | 0 | 0 | 43.7794 | 1729.2265 | 982.3606 | 450.8863 | 1291.4322 | 544.5663 | 13.092 | 0 | 0 | 0 | 437.7943 | 0.0016618 | 0.0007442 | 1.88e-05 | 0 | 0 | 0 | 0.0006818 | 5000000 | scaled
450-17 | 8346.6073 | 0 | 8346.6073 | 0 | 0% | 100% | 0% | 571.6463 | 1190.2512 | 1.2399 | 509.5807 | 60.8256 | 2.5817 | 1061.0217 | 126.6478 | 450 |  | 837 | 450-17 | 8346.6073 | 7774.9611 | 7156.3561 | 0 | 0 | 0 | 8346.6073 | 7774.9611 | 7156.3561 | 0 | 18.1043 | 16.8643 | 15.5225 | 0 | 0 | 0 | 18.1043 | 16.8643 | 15.5225 | 0 | 888.1147 | 827.2891 | 761.4669 | 0 | 0 | 0 | 888.1147 | 827.2891 | 761.4669 | 0 | 7440.3884 | 6930.8077 | 6379.3667 | 0 | 0 | 0 | 7440.3884 | 6930.8077 | 6379.3667 | 0 | 0 | 0 | 0 | 0.071803 | 0.071803 | 0.071803 | 0 | 5000000 | scaled
450-18 | 2022.8514 | 0 | 2022.8514 | 0 | 0% | 100% | 0% | 138.6766 | 288.8713 | 0.31636 | 127.3086 | 11.0517 | 0.659 | 265.191 | 23.0213 | 450 |  | 838 | 450-18 | 2022.8514 | 1884.1748 | 1733.9802 | 0 | 0 | 0 | 2022.8514 | 1884.1748 | 1733.9802 | 0 | 4.6147 | 4.2984 | 3.9557 | 0 | 0 | 0 | 4.6147 | 4.2984 | 3.9557 | 0 | 161.2089 | 150.1573 | 138.1877 | 0 | 0 | 0 | 161.2089 | 150.1573 | 138.1877 | 0 | 1857.0278 | 1729.7192 | 1591.8367 | 0 | 0 | 0 | 1857.0278 | 1729.7192 | 1591.8367 | 0 | 0 | 0 | 0 | 0.071668 | 0.071668 | 0.071668 | 0 | 5000000 | scaled
450-1850 | 296713.7732 | 288152.8007 | 8067.1958 | 493.7767 | 97.11% | 2.719% | 0.1664% | 169792.9335 | 294241.63 | 9355.0729 | 3277.0607 | 157160.7999 | 16046.3664 | 6803.8108 | 271391.4528 | 450 |  | 839 | 450-1850 | 296713.7732 | 126920.8398 | 2472.1432 | 288152.8007 | 121910.3112 | 1287.1347 | 8067.1958 | 4516.7519 | 691.2318 | 493.7767 | 16134.5826 | 6779.5097 | 88.2162 | 16128.0671 | 6775.6982 | 87.3182 | 6.1439 | 3.4399 | 0.52644 | 0.37155 | 272691.06 | 115530.26 | 1299.6072 | 272002.3193 | 115124.8991 | 1199.5813 | 643.8857 | 360.5059 | 55.1709 | 44.855 | 7888.1307 | 4611.07 | 1084.3199 | 22.4143 | 9.7138 | 0.23524 | 7417.1662 | 4152.8061 | 635.5345 | 448.5501 | 0.0014884 | 0.0006442 | 1.62e-05 | 0.071532 | 0.040531 | 0.0071532 | 0.0006918 | 5000000 | scaled
450-1851F | 8274122.4526 | 8210482.2612 | 59308.949 | 4331.2423 | 99.23% | 0.7168% | 0.05235% | 4406197.4224 | 8189935.6121 | 775457.4456 | 23977.47 | 3606762.5069 | 1439822.2938 | 49665.5236 | 6700447.7947 | 450 |  | 840 | 450-1851F | 8274122.4526 | 3867925.0301 | 84186.8405 | 8210482.2612 | 3830368.0603 | 74776.383 | 59308.949 | 33225.7275 | 5079.2152 | 4331.2423 | 1453153.3973 | 677695.9517 | 13331.1035 | 1453080.5198 | 677653.6914 | 13321.8822 | 69.6183 | 39.0012 | 5.9621 | 3.2591 | 6762808.4906 | 3156045.9837 | 62360.6959 | 6756281.5606 | 3152216.4686 | 61441.9722 | 6133.4769 | 3436.0621 | 525.2706 | 393.453 | 58160.5647 | 34183.0947 | 8495.0411 | 1120.1808 | 497.9004 | 12.5285 | 53105.8538 | 29750.6642 | 4547.9825 | 3934.5301 | 0.022058 | 0.010363 | 0.0002634 | 0.071222 | 0.040381 | 0.0071222 | 0.006197 | 5000000 | scaled
450-1853F | 792201.7619 | 734911.7387 | 56544.6979 | 745.3253 | 92.77% | 7.138% | 0.09408% | 414810.8386 | 782183.1923 | 20733.8329 | 22930.3443 | 371146.6614 | 39335.4743 | 47634.6158 | 695213.1022 | 450 |  | 841 | 450-1853F | 792201.7619 | 377390.9233 | 10018.5696 | 734911.7387 | 344948.9434 | 4431.7182 | 56544.6979 | 31696.6546 | 4841.5261 | 745.3253 | 39596.2031 | 18862.3702 | 260.7289 | 39505.8716 | 18811.4876 | 252.4816 | 89.7707 | 50.3218 | 7.6864 | 0.56083 | 699866.7798 | 328720.1184 | 4653.6776 | 694994.9819 | 325959.4342 | 4174.631 | 4804.0921 | 2692.9783 | 411.3407 | 67.7059 | 52738.779 | 29808.4347 | 5104.1632 | 410.8852 | 178.0216 | 4.6056 | 51650.8351 | 28953.3544 | 4422.4989 | 677.0586 | 0.0031252 | 0.0015218 | 3.86e-05 | 0.071109 | 0.040343 | 0.0071108 | 0.0010574 | 5000000 | scaled
450-1854 | 1132288.7455 | 1078517.0446 | 52365.0744 | 1406.6265 | 95.25% | 4.625% | 0.1242% | 545614.5702 | 1099791.0463 | 37481.4144 | 21377.9477 | 486755.2081 | 74685.5642 | 44368.6939 | 980736.7881 | 450 |  | 842 | 450-1854 | 1132288.7455 | 586674.1753 | 32497.6992 | 1078517.0446 | 555923.0029 | 26607.7469 | 52365.0744 | 29344.546 | 4483.3258 | 1406.6265 | 76529.1639 | 39047.7496 | 1843.5997 | 76460.8567 | 39009.006 | 1836.7836 | 67.2488 | 37.6852 | 5.7576 | 1.0584 | 1006000.0735 | 519244.8654 | 25263.2854 | 1001547.5654 | 516693.5778 | 24765.2373 | 4324.7292 | 2423.5087 | 370.2691 | 127.7789 | 49759.508 | 28381.5603 | 5390.8141 | 508.6226 | 220.4191 | 5.7259 | 47973.0964 | 26883.3521 | 4107.2991 | 1277.7891 | 0.0059382 | 0.0026418 | 8.68e-05 | 0.071123 | 0.040334 | 0.0071122 | 0.0020242 | 5000000 | scaled
450-50R | 537070.1579 | 174705.6831 | 362045.482 | 318.9929 | 32.53% | 67.41% | 0.0594% | 271204.6669 | 504750.6599 | 6729.8315 | 145839.6615 | 118635.1739 | 10713.6766 | 303352.2761 | 190684.7072 | 450 |  | 843 | 450-50R | 537070.1579 | 265865.4911 | 32319.498 | 174705.6831 | 62641.6399 | 1045.024 | 362045.482 | 202904.8583 | 30955.4812 | 318.9929 | 10830.0196 | 4100.1881 | 116.343 | 10312.8986 | 3810.2672 | 71.9088 | 516.8809 | 289.6809 | 44.1942 | 0.24003 | 194264.4071 | 75629.2332 | 3579.6999 | 164049.1467 | 58682.648 | 969.7458 | 30186.2828 | 16917.6077 | 2580.9766 | 28.9775 | 331975.7312 | 186136.0697 | 28623.4551 | 343.6377 | 148.7247 | 3.3694 | 331342.3182 | 185697.5697 | 28330.3105 | 289.7753 | 0.0012638 | 0.0006164 | 1.56e-05 | 0.070082 | 0.039756 | 0.0070082 | 0.000455 | 5000000 | scaled
450-88R | 894374.4666 | 384233.6124 | 507079.2379 | 3061.6162 | 42.96% | 56.7% | 0.3423% | 418400.1484 | 842459.2684 | 30291.9685 | 210722.1218 | 177386.0582 | 58491.6962 | 435678.6405 | 348288.9318 | 450 |  | 844 | 450-88R | 894374.4666 | 475974.3181 | 51915.1981 | 384233.6124 | 188821.674 | 5519.128 | 507079.2379 | 284091.028 | 43334.454 | 3061.6162 | 59352.0995 | 29060.131 | 860.4033 | 58610.4919 | 28643.6324 | 794.9194 | 739.3038 | 414.1948 | 63.1801 | 2.3038 | 356837.486 | 179451.4278 | 8548.5542 | 313222.7746 | 154893.9927 | 4566.9357 | 43336.592 | 24279.3159 | 3703.4992 | 278.1193 | 478184.8811 | 267462.7593 | 42506.2406 | 12400.3459 | 5284.0489 | 157.2729 | 463003.3421 | 259397.5173 | 39567.7746 | 2781.1931 | 0.0089648 | 0.004001 | 0.0001024 | 0.069655 | 0.039506 | 0.0069656 | 0.0043344 | 5000000 | scaled
451-38F | 1674.3155 | 756.0344 | 0 | 918.2811 | 45.15% | 0% | 54.85% | 352.5101 | 745.5794 | 0 | 352.5101 | 0 | 0 | 745.5794 | 0 | 451 |  | 845 | 451-38F | 1674.3155 | 1321.8054 | 928.7362 | 756.0344 | 403.5243 | 10.4551 | 0 | 0 | 0 | 918.2811 | 0.69098 | 0.69098 | 0.69098 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69098 | 83.4173 | 83.4173 | 83.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4173 | 1590.2073 | 1237.6972 | 844.6279 | 756.0344 | 403.5243 | 10.4551 | 0 | 0 | 0 | 834.1729 | 0.0028254 | 0.001482 | 3.76e-05 | 0 | 0 | 0 | 0.0012886 | 5000000 | scaled
452-1403 | 137227.0032 | 137083.0943 | 0 | 143.9088 | 99.9% | 0% | 0.1049% | 80169.3569 | 137025.0092 | 4515.923 | 1.1327 | 75652.3011 | 7692.6123 | 2.0262 | 129330.3707 | 452 |  | 846 | 452-1403 | 137227.0032 | 57057.6463 | 201.994 | 137083.0943 | 56913.7375 | 58.0851 | 0 | 0 | 0 | 143.9088 | 7697.8033 | 3181.8802 | 5.1909 | 7697.695 | 3181.7719 | 5.0826 | 0 | 0 | 0 | 0.10829 | 129396.4249 | 53744.1238 | 66.0542 | 129383.3521 | 53731.051 | 52.9814 | 0 | 0 | 0 | 13.0728 | 132.775 | 131.6424 | 130.7489 | 2.0473 | 0.91459 | 0.02108 | 0 | 0 | 0 | 130.7278 | 0.000595 | 0.0002692 | 6.8e-06 | 0 | 0 | 0 | 0.0001988 | 5000000 | scaled
452-1404F | 625542.4811 | 624941.0442 | 0 | 601.4368 | 99.9% | 0% | 0.09615% | 354406.5541 | 621084.0382 | 41020.5312 | 16.0319 | 313369.991 | 71963.5109 | 32.9287 | 549087.5986 | 452 |  | 847 | 452-1404F | 625542.4811 | 271135.927 | 4458.4429 | 624941.0442 | 270534.4902 | 3857.006 | 0 | 0 | 0 | 601.4368 | 72450.4657 | 31429.9345 | 486.9548 | 72450.0131 | 31429.4819 | 486.5022 | 0 | 0 | 0 | 0.45256 | 552512.3063 | 239142.3152 | 3424.7076 | 552457.6713 | 239087.6803 | 3370.0727 | 0 | 0 | 0 | 54.6349 | 579.7091 | 563.6773 | 546.7804 | 33.3598 | 17.328 | 0.43112 | 0 | 0 | 0 | 546.3493 | 0.0027896 | 0.001508 | 3.86e-05 | 0 | 0 | 0 | 0.0008538 | 5000000 | scaled
452-1405 | 181217.3939 | 180925.7126 | 0 | 291.6813 | 99.84% | 0% | 0.161% | 90752.6823 | 171253.7724 | 6987.058 | 4.0959 | 83761.5283 | 13136.7949 | 7.1481 | 158109.8294 | 452 |  | 848 | 452-1405 | 181217.3939 | 90464.7116 | 9963.6215 | 180925.7126 | 90173.0303 | 9671.9402 | 0 | 0 | 0 | 291.6813 | 13811.5181 | 6824.4601 | 674.7231 | 13811.2986 | 6824.2406 | 674.5037 | 0 | 0 | 0 | 0.21948 | 167133.6798 | 83372.1515 | 9023.8504 | 167107.1833 | 83345.655 | 8997.3539 | 0 | 0 | 0 | 26.4965 | 272.196 | 268.1 | 265.0479 | 7.2307 | 3.1348 | 0.082657 | 0 | 0 | 0 | 264.9653 | 0.0011074 | 0.0004794 | 1.24e-05 | 0 | 0 | 0 | 0.0004056 | 5000000 | scaled
452-37AE | 90620.8912 | 90313.6394 | 0 | 307.2518 | 99.66% | 0% | 0.3391% | 38252.2987 | 88419.6588 | 3935.8665 | 3.5558 | 34312.8764 | 9127.0241 | 6.9949 | 79285.6398 | 452 |  | 849 | 452-37AE | 90620.8912 | 52368.5924 | 2201.2324 | 90313.6394 | 52061.3406 | 1893.9806 | 0 | 0 | 0 | 307.2518 | 9309.3178 | 5373.4513 | 182.2937 | 9309.0866 | 5373.2201 | 182.0625 | 0 | 0 | 0 | 0.2312 | 81025.3797 | 46712.5033 | 1739.7399 | 80997.4687 | 46684.5924 | 1711.8289 | 0 | 0 | 0 | 27.911 | 286.1937 | 282.6378 | 279.1988 | 7.0841 | 3.5282 | 0.089203 | 0 | 0 | 0 | 279.1096 | 0.001322 | 0.0006554 | 1.64e-05 | 0 | 0 | 0 | 0.0004618 | 5000000 | scaled
452-38AE | 2823751.4759 | 2821884.1608 | 0 | 1867.3151 | 99.93% | 0% | 0.06613% | 1397105.5354 | 2762724.8524 | 123696.6683 | 72.9305 | 1273335.9366 | 244940.0585 | 135.858 | 2517648.9359 | 452 |  | 850 | 452-38AE | 2823751.4759 | 1426645.9404 | 61026.6235 | 2821884.1608 | 1424778.6253 | 59159.3084 | 0 | 0 | 0 | 1867.3151 | 250073.9811 | 126377.3128 | 5133.9227 | 250072.576 | 126375.9077 | 5132.5176 | 0 | 0 | 0 | 1.4051 | 2571843.7088 | 1298507.7722 | 54194.7729 | 2571674.0806 | 1298338.144 | 54025.1447 | 0 | 0 | 0 | 169.6282 | 1833.7859 | 1760.8554 | 1697.9279 | 137.5041 | 64.5736 | 1.6461 | 0 | 0 | 0 | 1696.2818 | 0.0087492 | 0.0044258 | 0.0001124 | 0 | 0 | 0 | 0.002646 | 5000000 | scaled
452-39AE | 261242.3756 | 260227.6709 | 0 | 1014.7047 | 99.61% | 0% | 0.3884% | 114734.6713 | 255561.6529 | 21919.3961 | 9.9285 | 92805.3468 | 48536.3707 | 19.3289 | 207005.9533 | 452 |  | 851 | 452-39AE | 261242.3756 | 146507.7043 | 5680.7227 | 260227.6709 | 145492.9996 | 4666.018 | 0 | 0 | 0 | 1014.7047 | 49423.5647 | 27504.1686 | 887.194 | 49422.8012 | 27503.405 | 886.4305 | 0 | 0 | 0 | 0.76353 | 210877.4719 | 118072.1251 | 3871.5185 | 210785.2954 | 117979.9486 | 3779.3421 | 0 | 0 | 0 | 92.1765 | 941.3391 | 931.4106 | 922.0102 | 19.5744 | 9.6459 | 0.24545 | 0 | 0 | 0 | 921.7647 | 0.0041144 | 0.0020278 | 5.16e-05 | 0 | 0 | 0 | 0.0014628 | 5000000 | scaled
452-47 | 8959.682 | 7703.0242 | 0 | 1256.6578 | 85.97% | 0% | 14.03% | 3542.2416 | 7596.6043 | 0 | 3542.2416 | 0 | 0 | 7596.6043 | 0 | 452 |  | 852 | 452-47 | 8959.682 | 5417.4404 | 1363.0777 | 7703.0242 | 4160.7826 | 106.4199 | 0 | 0 | 0 | 1256.6578 | 0.94559 | 0.94559 | 0.94559 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94559 | 114.1557 | 114.1557 | 114.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1557 | 8844.5807 | 5302.3391 | 1247.9764 | 7703.0242 | 4160.7826 | 106.4199 | 0 | 0 | 0 | 1141.5565 | 0.0033388 | 0.0016678 | 4.26e-05 | 0 | 0 | 0 | 0.0017774 | 5000000 | scaled
452-717 | 24802.0192 | 24563.7302 | 0 | 238.289 | 99.04% | 0% | 0.9608% | 12089.6089 | 24563.6976 | 3364.0153 | 2.7145 | 8722.8791 | 6806.9913 | 4.7753 | 17751.9311 | 452 |  | 853 | 452-717 | 24802.0192 | 12712.4103 | 238.3216 | 24563.7302 | 12474.1213 | 0.032574 | 0 | 0 | 0 | 238.289 | 6807.1706 | 3443.1553 | 0.1793 | 6806.9913 | 3442.976 | 0 | 0 | 0 | 0 | 0.1793 | 17773.5774 | 9050.6983 | 21.6463 | 17751.9311 | 9029.0519 | 0 | 0 | 0 | 0 | 21.6463 | 221.2712 | 218.5567 | 216.4959 | 4.8079 | 2.0934 | 0.032574 | 0 | 0 | 0 | 216.4634 | 0.00063 | 0.0002728 | 7e-06 | 0 | 0 | 0 | 0.000343 | 5000000 | scaled
453-32R | 2530.5409 | 847.2804 | 0 | 1683.2605 | 33.48% | 0% | 66.52% | 489.5905 | 838.158 | 28.0687 | 318.1227 | 143.3991 | 46.4678 | 554.3094 | 237.3808 | 453 |  | 854 | 453-32R | 2530.5409 | 2040.9504 | 1692.3829 | 847.2804 | 357.6899 | 9.1224 | 0 | 0 | 0 | 1683.2605 | 48.2007 | 20.132 | 1.7329 | 46.9341 | 18.8654 | 0.46625 | 0 | 0 | 0 | 1.2666 | 392.6654 | 249.2663 | 155.2846 | 239.7569 | 96.3578 | 2.3761 | 0 | 0 | 0 | 152.9085 | 2089.6748 | 1771.5521 | 1535.3654 | 560.5895 | 242.4667 | 6.2801 | 0 | 0 | 0 | 1529.0854 | 0.0045762 | 0.0020272 | 5.12e-05 | 0 | 0 | 0 | 0.002386 | 5000000 | scaled
453-41 | 2600.871 | 2313.4148 | 0 | 287.4562 | 88.95% | 0% | 11.05% | 1312.5743 | 2287.5235 | 0 | 1312.5743 | 0 | 0 | 2287.5235 | 0 | 453 |  | 855 | 453-41 | 2600.871 | 1288.2967 | 313.3475 | 2313.4148 | 1000.8405 | 25.8913 | 0 | 0 | 0 | 287.4562 | 0.2163 | 0.2163 | 0.2163 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2163 | 26.1127 | 26.1127 | 26.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 26.1127 | 2574.5419 | 1261.9677 | 287.0185 | 2313.4148 | 1000.8405 | 25.8913 | 0 | 0 | 0 | 261.1271 | 0.0008636 | 0.0003736 | 9.6e-06 | 0 | 0 | 0 | 0.0004022 | 5000000 | scaled
454-1814 | 39026.189 | 37945.461 | 1009.1906 | 71.5375 | 97.23% | 2.586% | 0.1833% | 9315.1031 | 36493.7211 | 553.4802 | 408.5879 | 8353.035 | 2243.5438 | 850.1407 | 33400.0366 | 454 |  | 856 | 454-1814 | 39026.189 | 29711.086 | 2532.4679 | 37945.461 | 29074.1477 | 2374.4588 | 1009.1906 | 565.4008 | 86.4716 | 71.5375 | 2378.8077 | 1825.3275 | 135.2639 | 2377.9853 | 1824.8431 | 135.1442 | 0.76859 | 0.43061 | 0.065856 | 0.05383 | 35652.7193 | 27299.6843 | 2252.6827 | 35565.6719 | 27248.0581 | 2239.2824 | 80.5489 | 45.1276 | 6.9018 | 6.4985 | 994.6621 | 586.0742 | 144.5213 | 1.8038 | 1.2465 | 0.032188 | 927.8731 | 519.8426 | 79.504 | 64.9851 | 0.000375 | 0.0002592 | 6.6e-06 | 0.071591 | 0.040597 | 0.0071592 | 9.98e-05 | 5000000 | scaled
454-45AE | 491785.8254 | 204645.5613 | 284156.3607 | 2983.9034 | 41.61% | 57.78% | 0.6067% | 236462.0434 | 462271.4144 | 21628.1686 | 114380.1699 | 100453.7049 | 39168.8844 | 237500.9235 | 185601.6065 | 454 |  | 857 | 454-45AE | 491785.8254 | 255323.7821 | 29514.411 | 204645.5613 | 93212.2891 | 2211.7757 | 284156.3607 | 159127.5895 | 24318.7319 | 2983.9034 | 39639.7645 | 18011.5958 | 470.88 | 39154.5516 | 17738.8887 | 427.3013 | 482.9676 | 270.4619 | 41.3334 | 2.2453 | 189797.5617 | 89343.8568 | 4195.9552 | 164378.0543 | 74989.6639 | 1772.6354 | 25148.4476 | 14083.1331 | 2152.2599 | 271.0598 | 262348.4993 | 147968.3294 | 24847.5758 | 1112.9554 | 483.7365 | 11.839 | 258524.9455 | 144773.9946 | 22125.1385 | 2710.5983 | 0.0091422 | 0.0039584 | 0.0001008 | 0.070648 | 0.040047 | 0.0070648 | 0.0042144 | 5000000 | scaled
454-47R | 775.2559 | 528.1633 | 0 | 247.0926 | 68.13% | 0% | 31.87% | 299.5867 | 522.6124 | 0 | 299.5867 | 0 | 0 | 522.6124 | 0 | 454 |  | 858 | 454-47R | 775.2559 | 475.6692 | 252.6434 | 528.1633 | 228.5766 | 5.5509 | 0 | 0 | 0 | 247.0926 | 0.18593 | 0.18593 | 0.18593 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18593 | 22.4461 | 22.4461 | 22.4461 | 0 | 0 | 0 | 0 | 0 | 0 | 22.4461 | 752.6239 | 453.0372 | 230.0115 | 528.1633 | 228.5766 | 5.5509 | 0 | 0 | 0 | 224.4606 | 0.000528 | 0.0002454 | 6.2e-06 | 0 | 0 | 0 | 0.0003568 | 5000000 | scaled
454-48F | 3441166.132 | 3430799.5759 | 8747.5191 | 1619.0369 | 99.7% | 0.2542% | 0.04705% | 1152897.1883 | 3364767.1191 | 247716.7123 | 3333.2593 | 901847.2167 | 723192.2082 | 7017.4859 | 2634557.425 | 454 |  | 859 | 454-48F | 3441166.132 | 2288268.9437 | 76399.0128 | 3430799.5759 | 2281748.358 | 74030.1635 | 8747.5191 | 4901.5488 | 749.8124 | 1619.0369 | 739154.786 | 491438.0737 | 15962.5778 | 739131.2442 | 491424.3468 | 15959.446 | 22.3235 | 12.5087 | 1.9135 | 1.2183 | 2692881.8207 | 1791034.604 | 58324.3957 | 2691443.9781 | 1790164.2659 | 58066.6803 | 1290.7682 | 723.2638 | 110.641 | 147.0744 | 9129.5252 | 5796.2659 | 2112.0393 | 224.3537 | 159.7453 | 4.0372 | 7434.4274 | 4165.7764 | 637.258 | 1470.7442 | 0.011469 | 0.007376 | 0.0001874 | 0.071728 | 0.040685 | 0.0071728 | 0.0022904 | 5000000 | scaled
454-49F | 292974.2889 | 222825.7215 | 69106.3106 | 1042.2567 | 76.06% | 23.59% | 0.3558% | 158716.2692 | 282965.6805 | 23834.121 | 27851.2163 | 107030.9319 | 40907.1114 | 57820.3066 | 184238.2626 | 454 |  | 860 | 454-49F | 292974.2889 | 134258.0196 | 10008.6083 | 222825.7215 | 94485.1278 | 3045.1831 | 69106.3106 | 38730.6351 | 5921.1685 | 1042.2567 | 41479.71 | 17645.5891 | 572.5987 | 41369.8455 | 17583.6707 | 562.4682 | 109.0803 | 61.1341 | 9.3462 | 0.78426 | 187357.5978 | 80326.6659 | 3119.3352 | 180862.7948 | 76645.037 | 2476.2803 | 6400.1237 | 3586.9496 | 548.3755 | 94.6793 | 64136.981 | 36285.7647 | 6316.6745 | 593.0812 | 256.4201 | 6.4346 | 62597.1067 | 35082.5514 | 5363.4467 | 946.7931 | 0.0041912 | 0.0018148 | 4.56e-05 | 0.07155 | 0.04059 | 0.007155 | 0.0014618 | 5000000 | scaled
454-53F | 272539.8921 | 1989.9362 | 270099.0899 | 450.866 | 0.7301% | 99.1% | 0.1654% | 119746.8501 | 248939.781 | 241.6125 | 108826.0712 | 10679.1664 | 501.5643 | 226205.7529 | 22232.4638 | 454 |  | 861 | 454-53F | 272539.8921 | 152793.0421 | 23600.1111 | 1989.9362 | 1053.9743 | 14.6 | 270099.0899 | 151288.2017 | 23134.6451 | 450.866 | 535.4464 | 293.8339 | 33.882 | 164.5912 | 85.9608 | 1.8072 | 370.5159 | 207.5338 | 31.7356 | 0.33926 | 24200.7335 | 13521.567 | 1968.2697 | 1805.3948 | 959.449 | 12.6054 | 22354.3817 | 12521.1611 | 1914.7073 | 40.957 | 247803.7123 | 138977.6411 | 21597.9594 | 19.9503 | 8.5645 | 0.18741 | 247374.1923 | 138559.5069 | 21188.2023 | 409.5697 | 0.0013856 | 0.0006 | 1.54e-05 | 0.071054 | 0.040285 | 0.0071054 | 0.0006544 | 5000000 | scaled
456-5 | 584439.1923 | 579147.0238 | 0 | 5292.1684 | 99.09% | 0% | 0.9055% | 328300.9488 | 576947.5506 | 40584.5407 | 3388.0699 | 284328.3382 | 71107.4669 | 6837.6372 | 499002.4464 | 456 |  | 862 | 456-5 | 584439.1923 | 256138.2435 | 7491.6417 | 579147.0238 | 250846.075 | 2199.4733 | 0 | 0 | 0 | 5292.1684 | 71405.1145 | 30820.5737 | 297.6475 | 71401.1323 | 30816.5915 | 293.6654 | 0 | 0 | 0 | 3.9822 | 501291.2135 | 216962.8753 | 2288.767 | 500810.4693 | 216482.1311 | 1808.0228 | 0 | 0 | 0 | 480.7442 | 11742.8643 | 8354.7944 | 4905.2271 | 6935.4223 | 3547.3524 | 97.7851 | 0 | 0 | 0 | 4807.442 | 0.018003 | 0.0080498 | 0.0002038 | 0 | 0 | 0 | 0.0074316 | 5000000 | scaled
458-33F | 7800.208 | 5981.6011 | 0 | 1818.6069 | 76.69% | 0% | 23.31% | 3393.7692 | 5913.5538 | 2.2059 | 3380.1076 | 11.4556 | 3.3481 | 5892.7831 | 17.4226 | 458 |  | 863 | 458-33F | 7800.208 | 4406.4388 | 1886.6542 | 5981.6011 | 2587.8319 | 68.0473 | 0 | 0 | 0 | 1818.6069 | 4.7166 | 2.5106 | 1.3684 | 3.3481 | 1.1422 | 0 | 0 | 0 | 0 | 1.3684 | 182.6261 | 171.1705 | 165.2035 | 17.4226 | 5.967 | 0 | 0 | 0 | 0 | 165.2035 | 7612.8653 | 4232.7577 | 1720.0822 | 5960.8304 | 2580.7227 | 68.0473 | 0 | 0 | 0 | 1652.035 | 0.0033188 | 0.001437 | 3.76e-05 | 0 | 0 | 0 | 0.0025526 | 5000000 | scaled
458-41F | 159.4505 | 14.6234 | 0 | 144.8271 | 9.171% | 0% | 90.83% | 8.2996 | 14.459 | 0 | 8.2996 | 0 | 0 | 14.459 | 0 | 458 |  | 864 | 458-41F | 159.4505 | 151.1509 | 144.9915 | 14.6234 | 6.3237 | 0.16435 | 0 | 0 | 0 | 144.8271 | 0.10898 | 0.10898 | 0.10898 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10898 | 13.1562 | 13.1562 | 13.1562 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1562 | 146.1853 | 137.8857 | 131.7263 | 14.6234 | 6.3237 | 0.16435 | 0 | 0 | 0 | 131.562 | 0.0002064 | 8.92e-05 | 2.4e-06 | 0 | 0 | 0 | 0.000194 | 5000000 | scaled
458-43F | 2268.8669 | 955.7429 | 0 | 1313.1241 | 42.12% | 0% | 57.88% | 538.7666 | 944.2869 | 2.0685 | 526.1287 | 10.5694 | 4.4435 | 917.144 | 22.6994 | 458 |  | 865 | 458-43F | 2268.8669 | 1730.1003 | 1324.58 | 955.7429 | 416.9762 | 11.456 | 0 | 0 | 0 | 1313.1241 | 5.553 | 3.4845 | 1.1095 | 4.5649 | 2.4964 | 0.12139 | 0 | 0 | 0 | 0.98808 | 142.6046 | 132.0352 | 119.9051 | 23.3195 | 12.7501 | 0.62004 | 0 | 0 | 0 | 119.2851 | 2120.7094 | 1594.5807 | 1203.5654 | 927.8585 | 401.7298 | 10.7145 | 0 | 0 | 0 | 1192.8509 | 0.0034298 | 0.0014854 | 3.82e-05 | 0 | 0 | 0 | 0.0018864 | 5000000 | scaled
458-44F | 703.1428 | 430.1947 | 0 | 272.9481 | 61.18% | 0% | 38.82% | 243.8141 | 425.5485 | 0.14622 | 242.881 | 0.78693 | 0.22899 | 424.0717 | 1.2478 | 458 |  | 866 | 458-44F | 703.1428 | 459.3287 | 277.5943 | 430.1947 | 186.3806 | 4.6462 | 0 | 0 | 0 | 272.9481 | 0.43437 | 0.28815 | 0.20538 | 0.22899 | 0.082767 | 0 | 0 | 0 | 0 | 0.20538 | 26.0426 | 25.2557 | 24.7948 | 1.2478 | 0.46089 | 0 | 0 | 0 | 0 | 24.7948 | 676.6658 | 433.7849 | 252.5942 | 428.7179 | 185.8369 | 4.6462 | 0 | 0 | 0 | 247.948 | 0.0004278 | 0.0001854 | 4.8e-06 | 0 | 0 | 0 | 0.0004076 | 5000000 | scaled
461-24F | 4376.3854 | 3937.7134 | 0 | 438.672 | 89.98% | 0% | 10.02% | 2241.7729 | 3923.9036 | 138.3637 | 1156.5334 | 946.8759 | 230.8923 | 2171.3451 | 1521.6662 | 461 |  | 867 | 461-24F | 4376.3854 | 2134.6124 | 452.4818 | 3937.7134 | 1695.9405 | 13.8098 | 0 | 0 | 0 | 438.672 | 231.2224 | 92.8587 | 0.33009 | 230.8923 | 92.5287 | 0 | 0 | 0 | 0 | 0.33009 | 1561.5154 | 614.6396 | 39.8493 | 1521.6662 | 574.7903 | 0 | 0 | 0 | 0 | 39.8493 | 2583.6475 | 1427.1141 | 412.3024 | 2185.1549 | 1028.6215 | 13.8098 | 0 | 0 | 0 | 398.4926 | 0.000945 | 0.0004558 | 1.16e-05 | 0 | 0 | 0 | 0.0006078 | 5000000 | scaled
461-644R | 1969.9209 | 1723.4162 | 0 | 246.5048 | 87.49% | 0% | 12.51% | 847.7329 | 1715.5766 | 27.5584 | 664.627 | 155.5475 | 68.9872 | 1227.01 | 419.5794 | 461 |  | 868 | 461-644R | 1969.9209 | 1122.188 | 254.3443 | 1723.4162 | 875.6832 | 7.8396 | 0 | 0 | 0 | 246.5048 | 69.192 | 41.6336 | 0.2048 | 69.0065 | 41.4481 | 0.019312 | 0 | 0 | 0 | 0.18549 | 442.0709 | 286.5233 | 22.4915 | 419.6782 | 264.1307 | 0.098799 | 0 | 0 | 0 | 22.3927 | 1458.6581 | 794.0311 | 231.6481 | 1234.7315 | 570.1045 | 7.7215 | 0 | 0 | 0 | 223.9266 | 0.0005244 | 0.000227 | 6e-06 | 0 | 0 | 0 | 0.000341 | 5000000 | scaled
462-1034F | 6673.0508 | 5818.851 | 0 | 854.1998 | 87.2% | 0% | 12.8% | 3125.8036 | 5767.0037 | 236.2299 | 1365.5633 | 1524.0103 | 436.5664 | 2452.4489 | 2877.9885 | 462 |  | 869 | 462-1034F | 6673.0508 | 3547.2472 | 906.0471 | 5818.851 | 2693.0474 | 51.8473 | 0 | 0 | 0 | 854.1998 | 440.9199 | 204.6899 | 4.3535 | 440.2771 | 204.0472 | 3.7107 | 0 | 0 | 0 | 0.64276 | 2978.4826 | 1454.4723 | 100.4942 | 2900.8865 | 1376.8762 | 22.8981 | 0 | 0 | 0 | 77.5961 | 3253.6483 | 1888.0849 | 801.1994 | 2477.6873 | 1112.124 | 25.2385 | 0 | 0 | 0 | 775.9609 | 0.002019 | 0.000874 | 2.24e-05 | 0 | 0 | 0 | 0.0012282 | 5000000 | scaled
462-1035F | 247.7909 | 182.2009 | 0 | 65.59 | 73.53% | 0% | 26.47% | 102.9538 | 180.1691 | 0 | 102.9538 | 0 | 0 | 180.1691 | 0 | 462 |  | 870 | 462-1035F | 247.7909 | 144.8371 | 67.6218 | 182.2009 | 79.2471 | 2.0318 | 0 | 0 | 0 | 65.59 | 0.049354 | 0.049354 | 0.049354 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049354 | 5.9582 | 5.9582 | 5.9582 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9582 | 241.7833 | 138.8295 | 61.6142 | 182.2009 | 79.2471 | 2.0318 | 0 | 0 | 0 | 59.5824 | 5.38e-05 | 2.34e-05 | 6e-07 | 0 | 0 | 0 | 9.56e-05 | 5000000 | scaled
462-1521F | 6083.1432 | 5625.9606 | 0 | 457.1825 | 92.48% | 0% | 7.516% | 3032.9132 | 5620.6467 | 243.0218 | 606.9784 | 2182.913 | 443.347 | 1093.9782 | 4083.3214 | 462 |  | 871 | 462-1521F | 6083.1432 | 3050.23 | 462.4965 | 5625.9606 | 2593.0474 | 5.314 | 0 | 0 | 0 | 457.1825 | 443.691 | 200.6693 | 0.34402 | 443.347 | 200.3253 | 0 | 0 | 0 | 0 | 0.34402 | 4124.8522 | 1941.9392 | 41.5308 | 4083.3214 | 1900.4084 | 0 | 0 | 0 | 0 | 41.5308 | 1514.5999 | 907.6215 | 420.6217 | 1099.2921 | 492.3138 | 5.314 | 0 | 0 | 0 | 415.3078 | 0.0010336 | 0.0004472 | 1.12e-05 | 0 | 0 | 0 | 0.0006428 | 5000000 | scaled
462-1523F | 5288.7367 | 4725.2996 | 0 | 563.4371 | 89.35% | 0% | 10.65% | 3317.1016 | 4723.1127 | 259.8644 | 227.5736 | 2829.6636 | 378.8013 | 397.7132 | 3946.5982 | 462 |  | 872 | 462-1523F | 5288.7367 | 1971.6351 | 565.624 | 4725.2996 | 1408.198 | 2.1869 | 0 | 0 | 0 | 563.4371 | 379.2253 | 119.3609 | 0.42397 | 378.8013 | 118.9369 | 0 | 0 | 0 | 0 | 0.42397 | 3997.7812 | 1168.1176 | 51.183 | 3946.5982 | 1116.9346 | 0 | 0 | 0 | 0 | 51.183 | 911.7303 | 684.1566 | 514.017 | 399.9001 | 172.3265 | 2.1869 | 0 | 0 | 0 | 511.8301 | 0.0015396 | 0.0006666 | 1.66e-05 | 0 | 0 | 0 | 0.000797 | 5000000 | scaled
462-868 | 8272.3662 | 6616.4054 | 0 | 1655.9608 | 79.98% | 0% | 20.02% | 3660.1301 | 6557.9536 | 57.249 | 3305.0322 | 297.849 | 94.3018 | 5973.7235 | 489.9283 | 462 |  | 873 | 462-868 | 8272.3662 | 4612.236 | 1714.4126 | 6616.4054 | 2956.2753 | 58.4518 | 0 | 0 | 0 | 1655.9608 | 95.678 | 38.429 | 1.3761 | 94.4319 | 37.1829 | 0.13006 | 0 | 0 | 0 | 1.2461 | 641.0183 | 343.1693 | 151.09 | 490.5897 | 192.7407 | 0.66141 | 0 | 0 | 0 | 150.4286 | 7535.6699 | 4230.6378 | 1561.9465 | 6031.3838 | 2726.3516 | 57.6603 | 0 | 0 | 0 | 1504.2861 | 0.004364 | 0.001953 | 4.9e-05 | 0 | 0 | 0 | 0.0023422 | 5000000 | scaled
463-1136F | 88014.9255 | 85683.6037 | 1965.457 | 365.8649 | 97.35% | 2.233% | 0.4157% | 19656.084 | 81640.3753 | 1226.2551 | 129.4349 | 18300.3939 | 5160.8037 | 276.2232 | 76203.3484 | 463 |  | 874 | 463-1136F | 88014.9255 | 68358.8415 | 6374.5503 | 85683.6037 | 66187.1027 | 4376.6917 | 1965.457 | 1805.8739 | 1631.9937 | 365.8649 | 5427.4257 | 4201.1705 | 266.622 | 5425.8596 | 4199.7092 | 265.2749 | 1.2908 | 1.186 | 1.0718 | 0.2753 | 80684.7471 | 62384.3532 | 4481.3987 | 80245.675 | 61978.2325 | 4111.1817 | 405.8367 | 372.8852 | 336.9816 | 33.2354 | 1902.7528 | 1773.3178 | 1626.5295 | 12.0691 | 9.161 | 0.23512 | 1558.3295 | 1431.8027 | 1293.9402 | 332.3542 | 0.0016834 | 0.0012786 | 3.26e-05 | 0.058246 | 0.058246 | 0.058246 | 0.0005046 | 5000000 | scaled
463-1137F | 11797.5288 | 11692.1294 | 0 | 105.3994 | 99.11% | 0% | 0.8934% | 5311.5367 | 11687.4032 | 592.4064 | 570.5144 | 4148.6159 | 1277.0888 | 995.5325 | 9414.7819 | 463 |  | 875 | 463-1137F | 11797.5288 | 6485.9921 | 110.1256 | 11692.1294 | 6380.5927 | 4.7262 | 0 | 0 | 0 | 105.3994 | 1277.1681 | 684.7617 | 0.07931 | 1277.0888 | 684.6824 | 0 | 0 | 0 | 0 | 0.07931 | 9424.3565 | 5275.7406 | 9.5746 | 9414.7819 | 5266.166 | 0 | 0 | 0 | 0 | 9.5746 | 1096.0042 | 525.4898 | 100.4717 | 1000.2586 | 429.7442 | 4.7262 | 0 | 0 | 0 | 95.7455 | 0.0003522 | 0.0001526 | 3.8e-06 | 0 | 0 | 0 | 0.0001514 | 5000000 | scaled
463-1229 | 1378318.1962 | 1364772.316 | 7911.5218 | 5634.3584 | 99.02% | 0.574% | 0.4088% | 562697.2315 | 1352549.2872 | 65131.5509 | 2809.3594 | 494756.3213 | 156420.7839 | 5890.8126 | 1190237.6908 | 463 |  | 876 | 463-1229 | 1378318.1962 | 815620.9648 | 25768.909 | 1364772.316 | 805548.9627 | 19477.5675 | 7911.5218 | 4437.6436 | 656.9831 | 5634.3584 | 158633.6102 | 93502.0593 | 2212.8263 | 158575.1515 | 93467.4077 | 2204.0842 | 54.219 | 30.4119 | 4.5024 | 4.2397 | 1208155.1369 | 713398.8156 | 17917.4461 | 1206019.8293 | 711976.3629 | 17270.8013 | 1623.4786 | 910.6237 | 134.8158 | 511.829 | 11529.4492 | 8720.0898 | 5638.6366 | 177.3352 | 105.1921 | 2.6819 | 6233.8243 | 3496.608 | 517.6649 | 5118.2898 | 0.030547 | 0.017843 | 0.0004548 | 0.058255 | 0.033142 | 0.0058254 | 0.0079204 | 5000000 | scaled
470-40AE | 5264968.8371 | 5176968.2697 | 84171.1392 | 3829.4282 | 98.33% | 1.599% | 0.07273% | 2639992.5849 | 5188919.9733 | 167350.7472 | 33607.6738 | 2439034.1639 | 328483.4326 | 70073.9284 | 4790362.6122 | 470 |  | 877 | 470-40AE | 5264968.8371 | 2624976.2522 | 76048.8638 | 5176968.2697 | 2573978.4723 | 65084.2299 | 84171.1392 | 47168.3517 | 7135.2058 | 3829.4282 | 332715.3669 | 165364.6197 | 4231.9343 | 332547.5946 | 165269.3357 | 4215.075 | 164.8908 | 92.4025 | 13.9778 | 2.8815 | 4852351.9146 | 2413317.7506 | 61989.3024 | 4842591.9363 | 2407695.4652 | 60843.5678 | 9412.1104 | 5274.4176 | 797.8666 | 347.8679 | 79901.5556 | 46293.8818 | 9827.6272 | 1828.7388 | 1013.6714 | 25.5871 | 74594.138 | 41801.5316 | 6323.3613 | 3478.6788 | 0.019407 | 0.0098564 | 0.0002502 | 0.066207 | 0.037593 | 0.0066206 | 0.00542 | 5000000 | scaled
470-47R | 16740391.1537 | 16634976.6647 | 89813.4696 | 15601.0193 | 99.37% | 0.5365% | 0.09319% | 8659449.9847 | 16513501.0717 | 555563.1129 | 36376.0097 | 8067510.8621 | 1057597.9529 | 75006.3287 | 15380896.7901 | 470 |  | 878 | 470-47R | 16740391.1537 | 8080941.1689 | 226890.0819 | 16634976.6647 | 8015036.9181 | 203676.2916 | 89813.4696 | 50303.2316 | 7612.7711 | 15601.0193 | 1070574.4499 | 515011.337 | 12976.497 | 1070300.1629 | 514852.5485 | 12942.5036 | 262.5477 | 147.0492 | 22.2541 | 11.7393 | 15574178.1719 | 7506667.3098 | 193281.3818 | 15558552.3367 | 7497292.0545 | 190659.8226 | 14208.6279 | 7958.048 | 1204.352 | 1417.2073 | 95638.5319 | 59262.5222 | 20632.2032 | 6124.1651 | 2892.3151 | 73.9654 | 75342.294 | 42198.1344 | 6386.165 | 14172.0728 | 0.074311 | 0.0352 | 0.0008952 | 0.066092 | 0.037511 | 0.0066092 | 0.021852 | 5000000 | scaled
471-36F | 4253667.121 | 4039168.3366 | 211944.4864 | 2554.2981 | 94.96% | 4.983% | 0.06005% | 2236960.1169 | 4219525.7934 | 118198.2396 | 85434.2002 | 2033327.6771 | 221777.9998 | 177253.1043 | 3820494.6893 | 471 |  | 879 | 471-36F | 4253667.121 | 2016707.0041 | 34141.3276 | 4039168.3366 | 1895478.9444 | 13218.4033 | 211944.4864 | 118673.7616 | 18368.6262 | 2554.2981 | 222618.9933 | 104420.7537 | 840.9935 | 222281.4737 | 104230.921 | 809.9862 | 335.5975 | 187.9106 | 29.0853 | 1.922 | 3834726.832 | 1801399.1549 | 14232.1427 | 3816002.0531 | 1790812.5056 | 12397.3949 | 18492.7448 | 10354.6151 | 1602.7136 | 232.0342 | 196321.2957 | 110887.0955 | 19068.1914 | 884.8098 | 435.5178 | 11.0223 | 193116.144 | 108131.2359 | 16736.8273 | 2320.3419 | 0.011797 | 0.0054458 | 0.000138 | 0.077686 | 0.044006 | 0.0077686 | 0.0035954 | 5000000 | scaled
473-36R | 1339206.7008 | 10897.2467 | 1319022.5993 | 9286.8548 | 0.8137% | 98.49% | 0.6935% | 589164.5302 | 1222626.6116 | 786.516 | 535511.4946 | 52866.5195 | 1605.545 | 1111421.1372 | 109599.9294 | 473 |  | 880 | 473-36R | 1339206.7008 | 750042.1707 | 116580.0892 | 10897.2467 | 5597.7701 | 177.9497 | 1319022.5993 | 735157.5457 | 107115.2847 | 9286.8548 | 1753.7825 | 967.2665 | 148.2376 | 141.6911 | 62.3312 | 4.0956 | 1605.1033 | 897.9472 | 137.1539 | 6.9881 | 120573.937 | 67707.4175 | 10974.0075 | 729.7724 | 320.2424 | 21.49 | 119000.5404 | 66543.5508 | 10108.8932 | 843.6243 | 1216878.9813 | 681367.4867 | 105457.8441 | 10025.7832 | 5215.1965 | 152.3641 | 1198416.9556 | 667716.0477 | 96869.2375 | 8436.2425 | 0.027604 | 0.012873 | 0.000328 | 0.074093 | 0.041973 | 0.0074092 | 0.013075 | 5000000 | scaled
474-22AE | 6435983.3722 | 6428609.8395 | 0 | 7373.5326 | 99.89% | 0% | 0.1146% | 2876075.8727 | 6353148.5173 | 190292.431 | 1860.7779 | 2683922.6639 | 421040.5149 | 6143.7289 | 5925964.2736 | 474 |  | 881 | 474-22AE | 6435983.3722 | 3559907.4994 | 82834.8548 | 6428609.8395 | 3552533.9668 | 75461.3222 | 0 | 0 | 0 | 7373.5326 | 426081.5964 | 235789.1654 | 5041.0815 | 426076.048 | 235783.6171 | 5035.5332 | 0 | 0 | 0 | 5.5483 | 5996947.4819 | 3313024.818 | 70983.2083 | 5996277.6652 | 3312355.0013 | 70313.3916 | 0 | 0 | 0 | 669.8168 | 12954.2938 | 11093.5159 | 6810.5649 | 6256.1263 | 4395.3484 | 112.3974 | 0 | 0 | 0 | 6698.1675 | 0.03621 | 0.020616 | 0.0005242 | 0 | 0 | 0 | 0.010425 | 5000000 | scaled
474-29 | 1510730.1835 | 1509132.2699 | 0 | 1597.9136 | 99.89% | 0% | 0.1058% | 824574.0984 | 1480192.1303 | 54000.0434 | 1223.2938 | 769350.7612 | 96977.3516 | 2402.2528 | 1380812.5259 | 474 |  | 882 | 474-29 | 1510730.1835 | 686156.0852 | 30538.0532 | 1509132.2699 | 684558.1716 | 28940.1396 | 0 | 0 | 0 | 1597.9136 | 98833.6544 | 44833.6111 | 1856.3028 | 98832.4521 | 44832.4087 | 1855.1004 | 0 | 0 | 0 | 1.2024 | 1408012.3865 | 638661.6253 | 27199.8606 | 1407867.2309 | 638516.4697 | 27054.705 | 0 | 0 | 0 | 145.1556 | 3884.1426 | 2660.8488 | 1481.8898 | 2432.5869 | 1209.2931 | 30.3341 | 0 | 0 | 0 | 1451.5556 | 0.0085026 | 0.0038726 | 0.0001074 | 0 | 0 | 0 | 0.002252 | 5000000 | scaled
475-763F | 16723.9953 | 14981.4576 | 0 | 1742.5376 | 89.58% | 0% | 10.42% | 7996.9789 | 14875.5228 | 736.1299 | 451.8846 | 6808.9644 | 1358.2242 | 786.8725 | 12730.4261 | 475 |  | 883 | 475-763F | 16723.9953 | 8727.0164 | 1848.4724 | 14981.4576 | 6984.4788 | 105.9348 | 0 | 0 | 0 | 1742.5376 | 1370.5974 | 634.4675 | 12.3732 | 1369.2862 | 633.1563 | 11.062 | 0 | 0 | 0 | 1.3112 | 12975.5333 | 6166.5689 | 245.1072 | 12817.24 | 6008.2756 | 86.8139 | 0 | 0 | 0 | 158.2933 | 2377.8645 | 1925.9799 | 1590.992 | 794.9314 | 343.0468 | 8.0589 | 0 | 0 | 0 | 1582.9331 | 0.0051542 | 0.0022318 | 5.7e-05 | 0 | 0 | 0 | 0.0024526 | 5000000 | scaled
476-6F | 18586.9783 | 992.408 | 17532.7625 | 61.8078 | 5.339% | 94.33% | 0.3325% | 8136.07 | 16894.441 | 69.7585 | 6477.907 | 1588.4046 | 133.4774 | 13518.7861 | 3242.1776 | 476 |  | 884 | 476-6F | 18586.9783 | 10450.9083 | 1692.5373 | 992.408 | 475.872 | 0.036645 | 17532.7625 | 9913.2286 | 1630.6928 | 61.8078 | 137.6854 | 67.9269 | 4.208 | 92.8955 | 42.582 | 0 | 44.7434 | 25.2984 | 4.1615 | 0.046508 | 3488.4144 | 1900.0098 | 246.2368 | 895.6967 | 431.6169 | 0 | 2587.103 | 1462.7782 | 240.6221 | 5.6147 | 14960.8786 | 8482.9716 | 1442.0925 | 3.8158 | 1.6731 | 0.036645 | 14900.9162 | 8425.1519 | 1385.9092 | 56.1466 | 0.0001852 | 8.02e-05 | 2.2e-06 | 0.156 | 0.088725 | 0.0156 | 9.24e-05 | 5000000 | scaled
480-1163R | 3880.1438 | 1279.5948 | 0 | 2600.549 | 32.98% | 0% | 67.02% | 725.5987 | 1265.8972 | 0 | 725.5987 | 0 | 0 | 1265.8972 | 0 | 480 |  | 885 | 480-1163R | 3880.1438 | 3154.5451 | 2614.2466 | 1279.5948 | 553.9961 | 13.6976 | 0 | 0 | 0 | 2600.549 | 1.9568 | 1.9568 | 1.9568 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9568 | 236.2357 | 236.2357 | 236.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 236.2357 | 3641.9513 | 2916.3527 | 2376.0542 | 1279.5948 | 553.9961 | 13.6976 | 0 | 0 | 0 | 2362.3565 | 0.0064414 | 0.0027894 | 7.08e-05 | 0 | 0 | 0 | 0.0036356 | 5000000 | scaled
480-32 | 17281.2335 | 12154.2904 | 0 | 5126.9431 | 70.33% | 0% | 29.67% | 6891.384 | 12020.0514 | 0.006306 | 6891.3453 | 0.032376 | 0.006306 | 12020.0127 | 0.032376 | 480 |  | 886 | 480-32 | 17281.2335 | 10389.8495 | 5261.1821 | 12154.2904 | 5262.9064 | 134.239 | 0 | 0 | 0 | 5126.9431 | 3.8642 | 3.8579 | 3.8579 | 0.006306 | 0 | 0 | 0 | 0 | 0 | 3.8579 | 465.7674 | 465.735 | 465.735 | 0.032376 | 0 | 0 | 0 | 0 | 0 | 465.735 | 16811.6019 | 9920.2566 | 4791.5892 | 12154.2517 | 5262.9064 | 134.239 | 0 | 0 | 0 | 4657.3502 | 0.01239 | 0.0053654 | 0.000137 | 0 | 0 | 0 | 0.0071776 | 5000000 | scaled
480-35 | 19582.7093 | 7678.1578 | 0 | 11904.5515 | 39.21% | 0% | 60.79% | 4031.8619 | 7591.9576 | 298.9411 | 2905.7963 | 827.1245 | 621.2189 | 5227.42 | 1743.3187 | 480 |  | 887 | 480-35 | 19582.7093 | 15550.8473 | 11990.7517 | 7678.1578 | 3646.2959 | 86.2002 | 0 | 0 | 0 | 11904.5515 | 638.2759 | 339.3348 | 17.057 | 629.3182 | 330.377 | 8.0992 | 0 | 0 | 0 | 8.9578 | 2847.3396 | 2020.2151 | 1104.0209 | 1765.922 | 938.7975 | 22.6033 | 0 | 0 | 0 | 1081.4176 | 16097.0937 | 13191.2974 | 10869.6737 | 5282.9176 | 2377.1213 | 55.4977 | 0 | 0 | 0 | 10814.1761 | 0.030427 | 0.013175 | 0.000334 | 0 | 0 | 0 | 0.016703 | 5000000 | scaled
481-30 | 2776.3014 | 680.3197 | 0 | 2095.9818 | 24.5% | 0% | 75.5% | 385.752 | 672.8107 | 0.062272 | 385.3722 | 0.3175 | 0.097744 | 672.214 | 0.49891 | 481 |  | 888 | 481-30 | 2776.3014 | 2390.5494 | 2103.4908 | 680.3197 | 294.5677 | 7.509 | 0 | 0 | 0 | 2095.9818 | 1.6749 | 1.6126 | 1.5772 | 0.097744 | 0.035471 | 0 | 0 | 0 | 0 | 1.5772 | 190.8993 | 190.5818 | 190.4004 | 0.49891 | 0.18141 | 0 | 0 | 0 | 0 | 190.4004 | 2583.7272 | 2198.355 | 1911.5132 | 679.723 | 294.3508 | 7.509 | 0 | 0 | 0 | 1904.0042 | 0.0054492 | 0.0023598 | 6e-05 | 0 | 0 | 0 | 0.0029016 | 5000000 | scaled
482-381F | 1246.9829 | 166.6817 | 0 | 1080.3012 | 13.37% | 0% | 86.63% | 94.479 | 164.8868 | 0 | 94.479 | 0 | 0 | 164.8868 | 0 | 482 |  | 889 | 482-381F | 1246.9829 | 1152.5039 | 1082.0961 | 166.6817 | 72.2027 | 1.7949 | 0 | 0 | 0 | 1080.3012 | 0.81289 | 0.81289 | 0.81289 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81289 | 98.1353 | 98.1353 | 98.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1353 | 1148.0348 | 1053.5557 | 983.1479 | 166.6817 | 72.2027 | 1.7949 | 0 | 0 | 0 | 981.353 | 0.0028718 | 0.0012436 | 3.14e-05 | 0 | 0 | 0 | 0.0015316 | 5000000 | scaled
482-382F | 4259.0257 | 2416.5377 | 0 | 1842.4879 | 56.74% | 0% | 43.26% | 1370.1591 | 2390.0697 | 0 | 1370.1591 | 0 | 0 | 2390.0697 | 0 | 482 |  | 890 | 482-382F | 4259.0257 | 2888.8666 | 1868.956 | 2416.5377 | 1046.3786 | 26.468 | 0 | 0 | 0 | 1842.4879 | 1.3864 | 1.3864 | 1.3864 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3864 | 167.3729 | 167.3729 | 167.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 167.3729 | 4090.2664 | 2720.1073 | 1700.1967 | 2416.5377 | 1046.3786 | 26.468 | 0 | 0 | 0 | 1673.7287 | 0.0048928 | 0.0021186 | 5.4e-05 | 0 | 0 | 0 | 0.0025538 | 5000000 | scaled
486-61R | 415568.1768 | 410126.658 | 0 | 5441.5188 | 98.69% | 0% | 1.309% | 232142.1571 | 406043.9339 | 21157.8966 | 3402.721 | 207581.5395 | 37030.3796 | 6576.0374 | 362437.5169 | 486 |  | 891 | 486-61R | 415568.1768 | 183426.0197 | 9524.2429 | 410126.658 | 177984.5009 | 4082.7241 | 0 | 0 | 0 | 5441.5188 | 37417.4808 | 16259.5842 | 387.1012 | 37413.3862 | 16255.4896 | 383.0066 | 0 | 0 | 0 | 4.0946 | 366549.8063 | 158968.2668 | 4112.2894 | 366055.495 | 158473.9555 | 3617.9781 | 0 | 0 | 0 | 494.3113 | 11600.8898 | 8198.1687 | 5024.8524 | 6657.7768 | 3255.0557 | 81.7394 | 0 | 0 | 0 | 4943.113 | 0.023952 | 0.010691 | 0.0002714 | 0 | 0 | 0 | 0.0077034 | 5000000 | scaled
486-91 | 14792.1014 | 13412.2259 | 0 | 1379.8755 | 90.67% | 0% | 9.328% | 5629.7692 | 12856.0843 | 101.4223 | 4999.4358 | 528.9112 | 203.1778 | 11635.9158 | 1016.9907 | 486 |  | 892 | 486-91 | 14792.1014 | 9162.3322 | 1936.0171 | 13412.2259 | 7782.4567 | 556.1416 | 0 | 0 | 0 | 1379.8755 | 234.4639 | 133.0416 | 31.2861 | 233.4256 | 132.0033 | 30.2478 | 0 | 0 | 0 | 1.0383 | 1347.5257 | 818.6145 | 330.535 | 1222.1768 | 693.2656 | 205.1861 | 0 | 0 | 0 | 125.3488 | 13210.1118 | 8210.6761 | 1574.196 | 11956.6235 | 6957.1877 | 320.7077 | 0 | 0 | 0 | 1253.4884 | 0.0036772 | 0.0018252 | 4.62e-05 | 0 | 0 | 0 | 0.001946 | 5000000 | scaled
488-32R | 3764.3825 | 1623.1831 | 0 | 2141.1994 | 43.12% | 0% | 56.88% | 744.4204 | 1600.8408 | 0 | 744.4204 | 0 | 0 | 1600.8408 | 0 | 488 |  | 893 | 488-32R | 3764.3825 | 3019.9621 | 2163.5417 | 1623.1831 | 878.7627 | 22.3423 | 0 | 0 | 0 | 2141.1994 | 1.6112 | 1.6112 | 1.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6112 | 194.508 | 194.508 | 194.508 | 0 | 0 | 0 | 0 | 0 | 0 | 194.508 | 3568.2633 | 2823.8429 | 1967.4225 | 1623.1831 | 878.7627 | 22.3423 | 0 | 0 | 0 | 1945.0802 | 0.0053654 | 0.0027366 | 6.94e-05 | 0 | 0 | 0 | 0.0029966 | 5000000 | scaled
489-19AE | 9474.7637 | 7508.9402 | 0 | 1965.8235 | 79.25% | 0% | 20.75% | 4487.338 | 7484.9864 | 808.2289 | 1163.7247 | 2515.3844 | 1363.9866 | 1958.0311 | 4162.9686 | 489 |  | 894 | 489-19AE | 9474.7637 | 4987.4257 | 1989.7773 | 7508.9402 | 3021.6022 | 23.9539 | 0 | 0 | 0 | 1965.8235 | 1368.1644 | 559.9355 | 4.1778 | 1366.6851 | 558.4562 | 2.6986 | 0 | 0 | 0 | 1.4792 | 4348.4043 | 1833.0199 | 185.4356 | 4169.8275 | 1654.4431 | 6.8589 | 0 | 0 | 0 | 178.5767 | 3758.1951 | 2594.4704 | 1800.1639 | 1972.4276 | 808.7029 | 14.3964 | 0 | 0 | 0 | 1785.7675 | 0.005468 | 0.0024536 | 6.26e-05 | 0 | 0 | 0 | 0.002751 | 5000000 | scaled
489-33 | 526.5976 | 53.6771 | 0 | 472.9205 | 10.19% | 0% | 89.81% | 30.442 | 53.0897 | 0 | 30.442 | 0 | 0 | 53.0897 | 0 | 489 |  | 895 | 489-33 | 526.5976 | 496.1556 | 473.508 | 53.6771 | 23.2351 | 0.58744 | 0 | 0 | 0 | 472.9205 | 0.35586 | 0.35586 | 0.35586 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35586 | 42.9604 | 42.9604 | 42.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 42.9604 | 483.2813 | 452.8393 | 430.1917 | 53.6771 | 23.2351 | 0.58744 | 0 | 0 | 0 | 429.6042 | 0.0021808 | 0.0009442 | 2.4e-05 | 0 | 0 | 0 | 0.0006656 | 5000000 | scaled
490-23 | 4294.7661 | 4145.4612 | 0 | 149.3049 | 96.52% | 0% | 3.476% | 2538.9558 | 4145.439 | 217.3544 | 1.4853 | 2320.1161 | 356.7919 | 2.5948 | 3786.0522 | 490 |  | 896 | 490-23 | 4294.7661 | 1755.8103 | 149.3271 | 4145.4612 | 1606.5054 | 0.022209 | 0 | 0 | 0 | 149.3049 | 356.9043 | 139.5499 | 0.11235 | 356.7919 | 139.4376 | 0 | 0 | 0 | 0 | 0.11235 | 3799.6152 | 1479.4991 | 13.563 | 3786.0522 | 1465.9361 | 0 | 0 | 0 | 0 | 13.563 | 138.2466 | 136.7613 | 135.6518 | 2.617 | 1.1317 | 0.022209 | 0 | 0 | 0 | 135.6296 | 0.0005052 | 0.0002188 | 5.4e-06 | 0 | 0 | 0 | 0.000208 | 5000000 | scaled
490-36 | 342.0263 | 309.4942 | 0 | 32.5321 | 90.49% | 0% | 9.512% | 201.7202 | 308.1654 | 12.6489 | 115.6297 | 73.4417 | 18.5047 | 184.2634 | 105.3973 | 490 |  | 897 | 490-36 | 342.0263 | 140.3061 | 33.861 | 309.4942 | 107.774 | 1.3289 | 0 | 0 | 0 | 32.5321 | 18.5292 | 5.8803 | 0.024479 | 18.5047 | 5.8559 | 0 | 0 | 0 | 0 | 0.024479 | 108.3525 | 34.9108 | 2.9552 | 105.3973 | 31.9556 | 0 | 0 | 0 | 0 | 2.9552 | 215.1446 | 99.5149 | 30.8813 | 185.5922 | 69.9625 | 1.3289 | 0 | 0 | 0 | 29.5524 | 9.88e-05 | 4.28e-05 | 1e-06 | 0 | 0 | 0 | 5.02e-05 | 5000000 | scaled
492-1090F | 34628.6398 | 1567.3227 | 30642.2133 | 2419.1038 | 4.526% | 88.49% | 6.986% | 14665.4365 | 30153.1529 | 67.2006 | 13021.2396 | 1576.9962 | 106.022 | 26941.6077 | 3105.5232 | 492 |  | 898 | 492-1090F | 34628.6398 | 19963.2033 | 4475.4869 | 1567.3227 | 555.3239 | 12.4844 | 30642.2133 | 16988.7756 | 2043.8987 | 2419.1038 | 111.1385 | 43.9379 | 5.1165 | 66.9504 | 18.6279 | 0.47019 | 42.3678 | 23.4897 | 2.826 | 1.8203 | 3523.7362 | 1946.74 | 418.2131 | 364.5735 | 97.308 | 2.3954 | 2939.4097 | 1629.679 | 196.0647 | 219.753 | 30993.765 | 17972.5254 | 4052.1574 | 1135.7988 | 439.3881 | 9.6189 | 27660.4358 | 15335.6069 | 1845.008 | 2197.5304 | 0.0056794 | 0.0025392 | 6.44e-05 | 0.014315 | 0.0081644 | 0.0014316 | 0.0033804 | 5000000 | scaled
492-1091F | 120639.6247 | 3519.0109 | 112981.4412 | 4139.1725 | 2.917% | 93.65% | 3.431% | 52311.1075 | 108913.9832 | 164.9603 | 47395.143 | 4751.0041 | 303.2705 | 98828.2087 | 9782.504 | 492 |  | 899 | 492-1091F | 120639.6247 | 68328.5172 | 11725.6414 | 3519.0109 | 1493.8458 | 53.0003 | 112981.4412 | 62695.4988 | 7533.4686 | 4139.1725 | 319.3087 | 154.3483 | 16.0382 | 180.2551 | 75.7987 | 3.8593 | 135.939 | 75.4351 | 9.0643 | 3.1146 | 10821.9934 | 6070.9893 | 1039.4893 | 748.8981 | 313.8888 | 16.8936 | 9697.09 | 5381.0952 | 646.5905 | 376.0053 | 109498.3226 | 62103.1796 | 10670.1139 | 2589.8577 | 1104.1584 | 32.2474 | 103148.4122 | 57238.9685 | 6877.8139 | 3760.0527 | 0.011507 | 0.0049826 | 0.0001274 | 0.014268 | 0.0081444 | 0.0014268 | 0.005885 | 5000000 | scaled
492-1092F | 23835.7837 | 0 | 23835.7837 | 0 | 0% | 100% | 0% | 3794.3892 | 7940.4051 | 4.7436 | 3340.5672 | 449.0784 | 9.9269 | 6990.7052 | 939.773 | 492 |  | 900 | 492-1092F | 23835.7837 | 20041.3944 | 15895.3786 | 0 | 0 | 0 | 23835.7837 | 20041.3944 | 15895.3786 | 0 | 29.7988 | 25.0551 | 19.8719 | 0 | 0 | 0 | 29.7988 | 25.0551 | 19.8719 | 0 | 2821.0433 | 2371.9649 | 1881.2703 | 0 | 0 | 0 | 2821.0433 | 2371.9649 | 1881.2703 | 0 | 20984.9416 | 17644.3744 | 13994.2363 | 0 | 0 | 0 | 20984.9416 | 17644.3744 | 13994.2363 | 0 | 0 | 0 | 0 | 0.014398 | 0.014398 | 0.014398 | 0 | 5000000 | scaled
492-14R | 216578.3188 | 7045.9823 | 202388.9966 | 7143.3398 | 3.253% | 93.45% | 3.298% | 94571.1271 | 195864.5353 | 375.8053 | 85349.9984 | 8845.3235 | 672.8399 | 177176.9714 | 18014.724 | 492 |  | 901 | 492-14R | 216578.3188 | 122007.1916 | 20713.7835 | 7045.9823 | 2959.1744 | 69.2826 | 202388.9966 | 111904.6774 | 13501.1611 | 7143.3398 | 699.8922 | 324.087 | 27.0523 | 430.1185 | 172.5209 | 4.0394 | 264.3986 | 146.1909 | 17.6378 | 5.3751 | 19845.7698 | 11000.4463 | 1831.0458 | 1712.0344 | 683.8498 | 15.745 | 17484.8296 | 9667.6907 | 1166.3949 | 648.9059 | 196032.6567 | 110682.6583 | 18855.6853 | 4903.8295 | 2102.8037 | 49.4981 | 184639.7684 | 102090.7958 | 12317.1284 | 6489.0588 | 0.020949 | 0.0091708 | 0.0002338 | 0.014184 | 0.0080688 | 0.0014184 | 0.010074 | 5000000 | scaled
492-343R | 272427.2085 | 101317.294 | 168994.8101 | 2115.1043 | 37.19% | 62.03% | 0.7764% | 134698.0551 | 258366.5288 | 4437.7565 | 94780.338 | 35479.9606 | 7532.9651 | 188757.4962 | 62076.0675 | 492 |  | 902 | 492-343R | 272427.2085 | 137729.1534 | 14060.6797 | 101317.294 | 42129.4388 | 669.9432 | 168994.8101 | 93484.6103 | 11275.6322 | 2115.1043 | 7585.371 | 3147.6145 | 52.4059 | 7393.4854 | 3040.756 | 38.1176 | 190.2941 | 105.2669 | 12.6968 | 1.5915 | 63432.6782 | 27952.7177 | 1356.6107 | 49016.252 | 19891.983 | 215.4035 | 14224.2887 | 7868.5972 | 949.0697 | 192.1375 | 201409.1593 | 106628.8212 | 12651.6631 | 44907.5566 | 19196.6998 | 416.422 | 154580.2274 | 85510.7462 | 10313.8658 | 1921.3753 | 0.0076116 | 0.003296 | 8.4e-05 | 0.014277 | 0.0081252 | 0.0014278 | 0.0029504 | 5000000 | scaled
493-478R | 28207.5301 | 24872.3499 | 0 | 3335.1802 | 88.18% | 0% | 11.82% | 11689.6257 | 24403.2741 | 1284.1524 | 3198.8634 | 7206.6099 | 2717.3987 | 5859.1982 | 15826.6772 | 493 |  | 903 | 493-478R | 28207.5301 | 16517.9044 | 3804.256 | 24872.3499 | 13182.7242 | 469.0758 | 0 | 0 | 0 | 3335.1802 | 2774.019 | 1489.8666 | 56.6202 | 2771.5094 | 1487.357 | 54.1106 | 0 | 0 | 0 | 2.5096 | 16477.5158 | 9270.9059 | 650.8386 | 16174.5458 | 8967.9359 | 347.8686 | 0 | 0 | 0 | 302.9701 | 8955.9953 | 5757.1319 | 3096.7971 | 5926.2947 | 2727.4313 | 67.0966 | 0 | 0 | 0 | 3029.7006 | 0.0099926 | 0.004507 | 0.0001152 | 0 | 0 | 0 | 0.0046716 | 5000000 | scaled
493-480R | 7277.9222 | 7100.9362 | 0 | 176.9861 | 97.57% | 0% | 2.432% | 2732.8777 | 6918.7082 | 247.1272 | 132.1544 | 2353.5961 | 618.0354 | 639.2872 | 5661.3857 | 493 |  | 904 | 493-480R | 7277.9222 | 4545.0445 | 359.214 | 7100.9362 | 4368.0584 | 182.2279 | 0 | 0 | 0 | 176.9861 | 634.553 | 387.4258 | 16.5177 | 634.4198 | 387.2927 | 16.3845 | 0 | 0 | 0 | 0.13318 | 5831.4331 | 3477.837 | 170.0475 | 5815.3556 | 3461.7595 | 153.9699 | 0 | 0 | 0 | 16.0775 | 811.936 | 679.7816 | 172.6488 | 651.1607 | 519.0063 | 11.8735 | 0 | 0 | 0 | 160.7753 | 0.0006202 | 0.0003592 | 9e-06 | 0 | 0 | 0 | 0.0002454 | 5000000 | scaled
493-485F | 12882.572 | 12564.7605 | 0 | 317.8115 | 97.53% | 0% | 2.467% | 6467.9353 | 12435.3064 | 855.1749 | 1009.1227 | 4603.6376 | 1645.0261 | 1990.6202 | 8799.6602 | 493 |  | 905 | 493-485F | 12882.572 | 6414.6367 | 447.2656 | 12564.7605 | 6096.8252 | 129.4541 | 0 | 0 | 0 | 317.8115 | 1661.8664 | 806.6915 | 16.8403 | 1661.6272 | 806.4523 | 16.6011 | 0 | 0 | 0 | 0.23914 | 8914.7094 | 4311.0718 | 115.0493 | 8885.8392 | 4282.2016 | 86.179 | 0 | 0 | 0 | 28.8702 | 2305.9962 | 1296.8735 | 315.376 | 2017.2941 | 1008.1713 | 26.6739 | 0 | 0 | 0 | 288.7021 | 0.0010008 | 0.0004816 | 1.22e-05 | 0 | 0 | 0 | 0.0004526 | 5000000 | scaled
496-21 | 391.8963 | 7.6049 | 0 | 384.2914 | 1.941% | 0% | 98.06% | 4.3123 | 7.5197 | 0 | 4.3123 | 0 | 0 | 7.5197 | 0 | 496 |  | 906 | 496-21 | 391.8963 | 387.584 | 384.3766 | 7.6049 | 3.2925 | 0.085136 | 0 | 0 | 0 | 384.2914 | 0.28917 | 0.28917 | 0.28917 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28917 | 34.9093 | 34.9093 | 34.9093 | 0 | 0 | 0 | 0 | 0 | 0 | 34.9093 | 356.6978 | 352.3855 | 349.1781 | 7.6049 | 3.2925 | 0.085136 | 0 | 0 | 0 | 349.093 | 0.0008218 | 0.0003558 | 9.2e-06 | 0 | 0 | 0 | 0.0005466 | 5000000 | scaled
497-888F | 9808.2547 | 9234.8813 | 0 | 573.3735 | 94.15% | 0% | 5.846% | 2035.8529 | 8749.3512 | 109.7866 | 1317.4092 | 608.6571 | 453.2396 | 5781.4419 | 2514.6697 | 497 |  | 907 | 497-888F | 9808.2547 | 7772.4018 | 1058.9035 | 9234.8813 | 7199.0284 | 485.5301 | 0 | 0 | 0 | 573.3735 | 490.2636 | 380.477 | 37.024 | 489.8321 | 380.0455 | 36.5925 | 0 | 0 | 0 | 0.43145 | 2849.0051 | 2240.3481 | 334.3354 | 2796.9195 | 2188.2624 | 282.2497 | 0 | 0 | 0 | 52.0856 | 6468.9861 | 5151.5768 | 687.5442 | 5948.1297 | 4630.7204 | 166.6878 | 0 | 0 | 0 | 520.8564 | 0.0023952 | 0.0017952 | 4.54e-05 | 0 | 0 | 0 | 0.0007824 | 5000000 | scaled
500-1531 | 800550.3172 | 172929.7025 | 626994.3832 | 626.2314 | 21.6% | 78.32% | 0.07823% | 378173.7228 | 743667.5844 | 6857.0169 | 252148.6109 | 119168.095 | 11630.8932 | 523947.2324 | 208089.4589 | 500 |  | 908 | 500-1531 | 800550.3172 | 422376.5944 | 56882.7328 | 172929.7025 | 70802.4798 | 2866.4677 | 626994.3832 | 350947.8832 | 53390.0337 | 626.2314 | 11907.0117 | 5049.9947 | 276.1185 | 11014.7286 | 4550.3492 | 199.7074 | 891.8118 | 499.1743 | 75.9399 | 0.47122 | 215364.1698 | 96196.0748 | 7274.7109 | 161851.1276 | 66218.1469 | 2665.9074 | 53456.1549 | 29921.0406 | 4551.9162 | 56.8873 | 573279.1357 | 321130.5249 | 49331.9033 | 63.8463 | 33.9837 | 0.85283 | 572646.4166 | 320527.6683 | 48762.1776 | 568.8729 | 0.0028 | 0.0014732 | 3.78e-05 | 0.067498 | 0.038251 | 0.0067498 | 0.0008794 | 5000000 | scaled
501-786 | 204083.5481 | 203332.4458 | 0 | 751.1023 | 99.63% | 0% | 0.368% | 71797.5329 | 200691.7471 | 4864.8498 | 14.6696 | 66918.0135 | 13698.7598 | 44.8871 | 186948.1002 | 501 |  | 909 | 501-786 | 204083.5481 | 132286.0151 | 3391.801 | 203332.4458 | 131534.9128 | 2640.6986 | 0 | 0 | 0 | 751.1023 | 13903.5146 | 9038.6648 | 204.7548 | 13902.9495 | 9038.0996 | 204.1896 | 0 | 0 | 0 | 0.56518 | 189452.0689 | 122534.0554 | 2503.9686 | 189383.8382 | 122465.8247 | 2435.738 | 0 | 0 | 0 | 68.2306 | 727.9646 | 713.295 | 683.0775 | 45.6581 | 30.9885 | 0.77104 | 0 | 0 | 0 | 682.3065 | 0.003972 | 0.0024624 | 6.26e-05 | 0 | 0 | 0 | 0.0010604 | 5000000 | scaled
504-1563 | 1424190.6827 | 1418596.5163 | 0 | 5594.1664 | 99.61% | 0% | 0.3928% | 816521.9128 | 1406691.1836 | 52818.5426 | 8368.202 | 755335.1682 | 91125.4635 | 14742.0076 | 1300823.7125 | 504 |  | 910 | 504-1563 | 1424190.6827 | 607668.77 | 17499.4991 | 1418596.5163 | 602074.6035 | 11905.3327 | 0 | 0 | 0 | 5594.1664 | 91910.0855 | 39091.5429 | 784.6219 | 91905.876 | 39087.3335 | 780.4125 | 0 | 0 | 0 | 4.2094 | 1312282.4779 | 556947.3096 | 11458.7653 | 1311774.3 | 556439.1317 | 10950.5874 | 0 | 0 | 0 | 508.1779 | 19998.1194 | 11629.9174 | 5256.1118 | 14916.3403 | 6548.1383 | 174.3327 | 0 | 0 | 0 | 5081.7791 | 0.020387 | 0.0089062 | 0.0002264 | 0 | 0 | 0 | 0.0079174 | 5000000 | scaled
504-2501R | 733683.4268 | 730075.9662 | 0 | 3607.4605 | 99.51% | 0% | 0.4917% | 371928.8049 | 718793.7616 | 25940.1474 | 9262.3158 | 336726.3417 | 49908.8007 | 18606.0337 | 650278.9272 | 504 |  | 911 | 504-2501R | 733683.4268 | 361754.6218 | 14889.6652 | 730075.9662 | 358147.1613 | 11282.2046 | 0 | 0 | 0 | 3607.4605 | 50685.9235 | 24745.7761 | 777.1229 | 50683.209 | 24743.0616 | 774.4084 | 0 | 0 | 0 | 2.7145 | 660882.6058 | 324156.2641 | 10603.6786 | 660554.9017 | 323828.5599 | 10275.9745 | 0 | 0 | 0 | 327.7042 | 22114.8974 | 12852.5816 | 3508.8637 | 18837.8555 | 9575.5397 | 231.8218 | 0 | 0 | 0 | 3277.0419 | 0.016515 | 0.0078144 | 0.0001988 | 0 | 0 | 0 | 0.0050774 | 5000000 | scaled
504-287R | 501828.3466 | 496494.4799 | 0 | 5333.8667 | 98.94% | 0% | 1.063% | 276618.0598 | 491429.8991 | 21222.1269 | 909.7258 | 254486.2071 | 37637.7514 | 1589.0344 | 452203.1133 | 504 |  | 912 | 504-287R | 501828.3466 | 225210.2869 | 10398.4475 | 496494.4799 | 219876.4201 | 5064.5808 | 0 | 0 | 0 | 5333.8667 | 38024.3915 | 16802.2647 | 386.6402 | 38020.378 | 16798.2511 | 382.6266 | 0 | 0 | 0 | 4.0136 | 457351.6615 | 202865.4544 | 5148.5481 | 456867.1294 | 202380.9223 | 4664.016 | 0 | 0 | 0 | 484.5321 | 6452.2936 | 5542.5678 | 4863.2592 | 1606.9726 | 697.2468 | 17.9382 | 0 | 0 | 0 | 4845.321 | 0.025607 | 0.011236 | 0.0002856 | 0 | 0 | 0 | 0.0075254 | 5000000 | scaled
504-40R | 796376.3327 | 791219.3132 | 0 | 5157.0194 | 99.35% | 0% | 0.6476% | 451716.7498 | 779763.1369 | 32153.1622 | 4292.0129 | 415271.5747 | 55504.0446 | 7499.0728 | 716760.0196 | 504 |  | 913 | 504-40R | 796376.3327 | 344659.5828 | 16613.1957 | 791219.3132 | 339502.5634 | 11456.1763 | 0 | 0 | 0 | 5157.0194 | 56280.9855 | 24127.8233 | 776.941 | 56277.105 | 24123.9428 | 773.0605 | 0 | 0 | 0 | 3.8805 | 727827.56 | 312555.9853 | 11067.5404 | 727359.0928 | 312087.5181 | 10599.0732 | 0 | 0 | 0 | 468.4672 | 12267.7872 | 7975.7742 | 4768.7144 | 7583.1154 | 3291.1025 | 84.0426 | 0 | 0 | 0 | 4684.6718 | 0.018766 | 0.0081688 | 0.0002078 | 0 | 0 | 0 | 0.0071952 | 5000000 | scaled
505-1676F | 126310.9282 | 122916.4647 | 0 | 3394.4635 | 97.31% | 0% | 2.687% | 62905.3978 | 121798.9037 | 5219.6603 | 564.0271 | 57121.7105 | 9986.7293 | 984.6031 | 110827.5713 | 505 |  | 914 | 505-1676F | 126310.9282 | 63405.5304 | 4512.0245 | 122916.4647 | 60011.0669 | 1117.5609 | 0 | 0 | 0 | 3394.4635 | 10086.6998 | 4867.0395 | 99.9705 | 10084.1455 | 4864.4853 | 97.4163 | 0 | 0 | 0 | 2.5542 | 112145.5945 | 55023.884 | 1318.0231 | 111837.2391 | 54715.5286 | 1009.6678 | 0 | 0 | 0 | 308.3554 | 4078.634 | 3514.6069 | 3094.0308 | 995.08 | 431.053 | 10.4769 | 0 | 0 | 0 | 3083.5539 | 0.011369 | 0.0050284 | 0.0001266 | 0 | 0 | 0 | 0.0047498 | 5000000 | scaled
505-635R | 591818.3193 | 576197.9055 | 0 | 15620.4138 | 97.36% | 0% | 2.639% | 319516.4937 | 571532.571 | 24536.2244 | 7306.4914 | 287673.7778 | 44017.2842 | 17022.0587 | 510493.2282 | 505 |  | 915 | 505-635R | 591818.3193 | 272301.8256 | 20285.7483 | 576197.9055 | 256681.4119 | 4665.3345 | 0 | 0 | 0 | 15620.4138 | 44397.7101 | 19861.4857 | 380.426 | 44385.9562 | 19849.7319 | 368.6721 | 0 | 0 | 0 | 11.7539 | 515940.1533 | 228266.3754 | 5446.9251 | 514521.1842 | 226847.4063 | 4027.956 | 0 | 0 | 0 | 1418.9691 | 31480.4559 | 24173.9645 | 14458.3972 | 17290.7651 | 9984.2736 | 268.7064 | 0 | 0 | 0 | 14189.6908 | 0.046632 | 0.021076 | 0.0005362 | 0 | 0 | 0 | 0.021838 | 5000000 | scaled
506-160AE | 283.8696 | 246.2286 | 0 | 37.6409 | 86.74% | 0% | 13.26% | 86.7323 | 245.3969 | 4.3726 | 64.3454 | 18.0142 | 14.964 | 134.4591 | 95.9738 | 506 |  | 916 | 506-160AE | 283.8696 | 197.1373 | 38.4727 | 246.2286 | 159.4963 | 0.83174 | 0 | 0 | 0 | 37.6409 | 14.9923 | 10.6196 | 0.028324 | 14.964 | 10.5913 | 0 | 0 | 0 | 0 | 0.028324 | 99.3932 | 81.379 | 3.4193 | 95.9738 | 77.9596 | 0 | 0 | 0 | 0 | 3.4193 | 169.4841 | 105.1387 | 35.025 | 135.2908 | 70.9454 | 0.83174 | 0 | 0 | 0 | 34.1933 | 0.0001198 | 5.18e-05 | 1.4e-06 | 0 | 0 | 0 | 5.14e-05 | 5000000 | scaled
506-161 | 4720.4269 | 3508.9172 | 0 | 1211.5097 | 74.33% | 0% | 25.67% | 1900.991 | 3453.6357 | 114.0665 | 1182.978 | 603.9465 | 213.8341 | 2102.7884 | 1137.0131 | 506 |  | 917 | 506-161 | 4720.4269 | 2819.4359 | 1266.7912 | 3508.9172 | 1607.9262 | 55.2815 | 0 | 0 | 0 | 1211.5097 | 218.962 | 104.8955 | 5.1278 | 218.0503 | 103.9838 | 4.2162 | 0 | 0 | 0 | 0.91162 | 1270.932 | 666.9855 | 133.9189 | 1160.8776 | 556.9312 | 23.8645 | 0 | 0 | 0 | 110.0544 | 3230.5329 | 2047.5549 | 1127.7445 | 2129.9892 | 947.0112 | 27.2008 | 0 | 0 | 0 | 1100.5437 | 0.0040978 | 0.0019418 | 4.9e-05 | 0 | 0 | 0 | 0.0017204 | 5000000 | scaled
506-844 | 22402.4809 | 17969.77 | 0 | 4432.7108 | 80.21% | 0% | 19.79% | 8850.6089 | 17738.3349 | 11.8365 | 8777.9543 | 60.8181 | 21.2819 | 17607.8049 | 109.2482 | 506 |  | 918 | 506-844 | 22402.4809 | 13551.872 | 4664.1459 | 17969.77 | 9119.1611 | 231.4351 | 0 | 0 | 0 | 4432.7108 | 24.9535 | 13.117 | 3.6717 | 21.6181 | 9.7815 | 0.33619 | 0 | 0 | 0 | 3.3355 | 513.6518 | 452.8337 | 404.4036 | 110.9813 | 50.1632 | 1.7331 | 0 | 0 | 0 | 402.6705 | 21863.8756 | 13085.9213 | 4256.0707 | 17837.1707 | 9059.2164 | 229.3658 | 0 | 0 | 0 | 4026.7049 | 0.015646 | 0.0071236 | 0.000181 | 0 | 0 | 0 | 0.0062392 | 5000000 | scaled
507-1733 | 7249.4282 | 6243.0213 | 0 | 1006.407 | 86.12% | 0% | 13.88% | 3169.1942 | 6186.6741 | 76.2455 | 2697.0984 | 395.8504 | 153.6637 | 5232.1135 | 800.8969 | 507 |  | 919 | 507-1733 | 7249.4282 | 4080.234 | 1062.7541 | 6243.0213 | 3073.827 | 56.3472 | 0 | 0 | 0 | 1006.407 | 154.5416 | 78.2962 | 0.87789 | 153.7843 | 77.5389 | 0.1206 | 0 | 0 | 0 | 0.75729 | 892.9398 | 497.0894 | 92.0429 | 801.5171 | 405.6667 | 0.62022 | 0 | 0 | 0 | 91.4227 | 6201.9468 | 3504.8484 | 969.8333 | 5287.7198 | 2590.6214 | 55.6063 | 0 | 0 | 0 | 914.227 | 0.0024482 | 0.0011176 | 2.86e-05 | 0 | 0 | 0 | 0.0014288 | 5000000 | scaled
508-1027F | 193.1746 | 163.1614 | 0 | 30.0132 | 84.46% | 0% | 15.54% | 100.5233 | 161.2372 | 13.7698 | 0.49331 | 86.2602 | 21.4919 | 0.87326 | 138.872 | 508 |  | 920 | 508-1027F | 193.1746 | 92.6514 | 31.9374 | 163.1614 | 62.6382 | 1.9242 | 0 | 0 | 0 | 30.0132 | 21.8286 | 8.0589 | 0.3367 | 21.806 | 8.0363 | 0.31412 | 0 | 0 | 0 | 0.022584 | 143.1997 | 56.9395 | 4.3276 | 140.4732 | 54.213 | 1.6012 | 0 | 0 | 0 | 2.7264 | 28.1464 | 27.6531 | 27.2731 | 0.88215 | 0.38884 | 0.0088837 | 0 | 0 | 0 | 27.2642 | 0.000145 | 6.28e-05 | 1.6e-06 | 0 | 0 | 0 | 5.04e-05 | 5000000 | scaled
509-1227R | 6817.7515 | 5274.9485 | 0 | 1542.803 | 77.37% | 0% | 22.63% | 2139.5717 | 5192.894 | 127.3938 | 1339.3223 | 672.8557 | 258.464 | 3578.6955 | 1355.7345 | 509 |  | 921 | 509-1227R | 6817.7515 | 4678.1798 | 1624.8575 | 5274.9485 | 3135.3768 | 82.0545 | 0 | 0 | 0 | 1542.803 | 263.5586 | 136.1648 | 5.0946 | 262.3977 | 135.0039 | 3.9337 | 0 | 0 | 0 | 1.1609 | 1516.4518 | 843.5962 | 160.7173 | 1376.3026 | 703.4469 | 20.5681 | 0 | 0 | 0 | 140.1493 | 5037.7411 | 3698.4188 | 1459.0456 | 3636.2483 | 2296.926 | 57.5528 | 0 | 0 | 0 | 1401.4928 | 0.0042238 | 0.002249 | 5.64e-05 | 0 | 0 | 0 | 0.0021456 | 5000000 | scaled
51-861R | 2905.802 | 549.3185 | 0 | 2356.4835 | 18.9% | 0% | 81.1% | 227.1608 | 537.3213 | 0 | 227.1608 | 0 | 0 | 537.3213 | 0 | 51 |  | 922 | 51-861R | 2905.802 | 2678.6412 | 2368.4807 | 549.3185 | 322.1577 | 11.9971 | 0 | 0 | 0 | 2356.4835 | 1.7732 | 1.7732 | 1.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7732 | 214.0646 | 214.0646 | 214.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0646 | 2689.9642 | 2462.8035 | 2152.6429 | 549.3185 | 322.1577 | 11.9971 | 0 | 0 | 0 | 2140.6458 | 0.0059722 | 0.0027528 | 9.94e-05 | 0 | 0 | 0 | 0.0033752 | 5000000 | scaled
510-49R | 240587.3753 | 66687.6025 | 172637.8629 | 1261.9099 | 27.72% | 71.76% | 0.5245% | 103298.2954 | 226588.5971 | 2122.2599 | 86156.5946 | 15019.4409 | 5132.3861 | 187428.3045 | 34027.9065 | 510 |  | 923 | 510-49R | 240587.3753 | 137289.0798 | 13998.7782 | 66687.6025 | 40771.889 | 1190.5278 | 172637.8629 | 95255.2809 | 11546.3405 | 1261.9099 | 5243.6491 | 3121.3892 | 111.263 | 5047.3228 | 3012.601 | 97.1698 | 195.3767 | 107.8387 | 13.1436 | 0.94955 | 35541.6401 | 20522.1992 | 1513.7336 | 20727.0949 | 12294.1943 | 410.7703 | 14699.9124 | 8113.3721 | 988.3305 | 114.6328 | 199802.0861 | 113645.4915 | 12373.7816 | 40913.1848 | 25465.0937 | 682.5877 | 157742.5737 | 87034.0702 | 10544.8663 | 1146.3276 | 0.0059602 | 0.0036836 | 9.32e-05 | 0.010571 | 0.0060014 | 0.001057 | 0.0017448 | 5000000 | scaled
511-831 | 45773.5846 | 5128.6614 | 40510.2029 | 134.7203 | 11.2% | 88.5% | 0.2943% | 20566.131 | 42909.2963 | 119.1253 | 18337.727 | 2109.2787 | 292.3271 | 37806.9827 | 4809.9865 | 511 |  | 924 | 511-831 | 45773.5846 | 25207.4536 | 2864.2883 | 5128.6614 | 2635.1692 | 15.893 | 40510.2029 | 22437.5642 | 2713.675 | 134.7203 | 295.8019 | 176.6766 | 3.4748 | 245.342 | 148.6829 | 0 | 50.3586 | 27.8923 | 3.3734 | 0.10137 | 5051.0419 | 2941.7632 | 241.0554 | 1622.9793 | 1037.5874 | 0 | 3415.8245 | 1891.9377 | 228.8174 | 12.2381 | 40426.7408 | 22089.0138 | 2619.7581 | 3260.3401 | 1448.8988 | 15.893 | 37044.0199 | 20517.7341 | 2481.4842 | 122.3809 | 0.0004426 | 0.0001918 | 4.8e-06 | 0.010641 | 0.0060614 | 0.001064 | 0.0001896 | 5000000 | scaled
512-300F | 82639.3846 | 0 | 82639.3846 | 0 | 0% | 100% | 0% | 13054.7315 | 27306.6149 | 13.9869 | 11870.0121 | 1170.7325 | 29.2565 | 24828.5343 | 2448.8241 | 512 |  | 925 | 512-300F | 82639.3846 | 69584.6531 | 55332.7697 | 0 | 0 | 0 | 82639.3846 | 69584.6531 | 55332.7697 | 0 | 88.5403 | 74.5534 | 59.2838 | 0 | 0 | 0 | 88.5403 | 74.5534 | 59.2838 | 0 | 7410.9999 | 6240.2674 | 4962.1757 | 0 | 0 | 0 | 7410.9999 | 6240.2674 | 4962.1757 | 0 | 75139.8445 | 63269.8324 | 50311.3101 | 0 | 0 | 0 | 75139.8445 | 63269.8324 | 50311.3101 | 0 | 0 | 0 | 0 | 0.010589 | 0.010589 | 0.010589 | 0 | 5000000 | scaled
512-302F | 24615.1122 | 0 | 24615.1122 | 0 | 0% | 100% | 0% | 3882.595 | 8135.4823 | 4.2956 | 3340.7476 | 537.5517 | 9.001 | 7000.1103 | 1126.371 | 512 |  | 926 | 512-302F | 24615.1122 | 20732.5173 | 16479.6299 | 0 | 0 | 0 | 24615.1122 | 20732.5173 | 16479.6299 | 0 | 27.2337 | 22.9381 | 18.2328 | 0 | 0 | 0 | 27.2337 | 22.9381 | 18.2328 | 0 | 3408.0031 | 2870.4514 | 2281.6321 | 0 | 0 | 0 | 3408.0031 | 2870.4514 | 2281.6321 | 0 | 21179.8754 | 17839.1278 | 14179.7651 | 0 | 0 | 0 | 21179.8754 | 17839.1278 | 14179.7651 | 0 | 0 | 0 | 0 | 0.01064 | 0.01064 | 0.01064 | 0 | 5000000 | scaled
512-50AE | 71824.4159 | 543.7654 | 69953.7478 | 1326.9028 | 0.7571% | 97.4% | 1.847% | 31433.9491 | 65800.1038 | 40.2829 | 27832.7708 | 3560.8953 | 80.4183 | 58272.9983 | 7446.6872 | 512 |  | 927 | 512-50AE | 71824.4159 | 40390.4669 | 6024.3122 | 543.7654 | 230.3534 | 5.2185 | 69953.7478 | 38833.2107 | 4692.1909 | 1326.9028 | 86.3203 | 46.0374 | 5.9021 | 12.2157 | 4.4557 | 0 | 73.1062 | 40.5832 | 4.9036 | 0.99845 | 8098.1383 | 4537.243 | 651.4511 | 62.4405 | 22.787 | 0 | 7915.1611 | 4393.9192 | 530.9143 | 120.5368 | 63639.9573 | 35807.1864 | 5366.959 | 469.1092 | 203.1106 | 5.2185 | 61965.4804 | 34398.7082 | 4156.3729 | 1205.3676 | 0.0039262 | 0.0017 | 4.36e-05 | 0.010629 | 0.0060674 | 0.0010628 | 0.0018688 | 5000000 | scaled
513-42F | 92913.745 | 5114.7727 | 87241.8786 | 557.0937 | 5.505% | 93.9% | 0.5996% | 41562.8473 | 84742.4942 | 388.0855 | 34699.1998 | 6475.562 | 655.9817 | 72051.2902 | 12035.2223 | 513 |  | 928 | 513-42F | 92913.745 | 51350.8977 | 8171.2508 | 5114.7727 | 1910.5586 | 48.2009 | 87241.8786 | 48883.2455 | 7565.9562 | 557.0937 | 675.4271 | 287.3416 | 19.4454 | 511.699 | 195.4174 | 4.8634 | 163.3089 | 91.505 | 14.1628 | 0.4192 | 12849.1506 | 6373.5885 | 813.9283 | 4480.6408 | 1662.3062 | 41.9605 | 8317.903 | 4660.6756 | 721.361 | 50.6068 | 79389.1673 | 44689.9675 | 7337.8771 | 122.4329 | 52.8349 | 1.377 | 78760.6667 | 44131.0649 | 6830.4324 | 506.0677 | 0.0019766 | 0.0008558 | 2.14e-05 | 0.078352 | 0.044405 | 0.0078352 | 0.0007886 | 5000000 | scaled
513-45F | 3667.1682 | 3593.8957 | 0 | 73.2725 | 98% | 0% | 1.998% | 2262.1244 | 3577.025 | 149.8446 | 7.897 | 2104.3829 | 237.4383 | 13.8897 | 3325.697 | 513 |  | 929 | 513-45F | 3667.1682 | 1405.0438 | 90.1433 | 3593.8957 | 1331.7712 | 16.8707 | 0 | 0 | 0 | 73.2725 | 239.5312 | 89.6866 | 2.0928 | 239.476 | 89.6315 | 2.0377 | 0 | 0 | 0 | 0.055135 | 3347.0587 | 1242.6759 | 21.3618 | 3340.4026 | 1236.0197 | 14.7056 | 0 | 0 | 0 | 6.6561 | 80.5783 | 72.6813 | 66.6887 | 14.017 | 6.1201 | 0.12738 | 0 | 0 | 0 | 66.5613 | 0.0002384 | 0.0001032 | 2.6e-06 | 0 | 0 | 0 | 0.0001058 | 5000000 | scaled
515-49R | 938.6551 | 472.1806 | 0 | 466.4744 | 50.3% | 0% | 49.7% | 220.5781 | 465.7601 | 1.178 | 213.3758 | 6.0242 | 2.2473 | 452.0148 | 11.498 | 515 |  | 930 | 515-49R | 938.6551 | 718.077 | 472.8949 | 472.1806 | 251.6025 | 6.4205 | 0 | 0 | 0 | 466.4744 | 2.6685 | 1.4904 | 0.42116 | 2.3175 | 1.1394 | 0.070155 | 0 | 0 | 0 | 0.35101 | 54.2312 | 48.2069 | 42.7331 | 11.8563 | 5.8321 | 0.35826 | 0 | 0 | 0 | 42.3749 | 881.7554 | 668.3796 | 429.7407 | 458.0069 | 244.6311 | 5.9921 | 0 | 0 | 0 | 423.7486 | 0.0007894 | 0.0003792 | 9.6e-06 | 0 | 0 | 0 | 0.000647 | 5000000 | scaled
516-5F | 1245.1969 | 236.0323 | 0 | 1009.1646 | 18.96% | 0% | 81.04% | 130.972 | 233.3724 | 0 | 130.972 | 0 | 0 | 233.3724 | 0 | 516 |  | 931 | 516-5F | 1245.1969 | 1114.2249 | 1011.8245 | 236.0323 | 105.0603 | 2.6599 | 0 | 0 | 0 | 1009.1646 | 0.75936 | 0.75936 | 0.75936 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75936 | 91.6732 | 91.6732 | 91.6732 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6732 | 1152.7643 | 1021.7923 | 919.3919 | 236.0323 | 105.0603 | 2.6599 | 0 | 0 | 0 | 916.732 | 0.0022722 | 0.0010206 | 2.6e-05 | 0 | 0 | 0 | 0.001438 | 5000000 | scaled
516-7F | 353.406 | 40.9245 | 0 | 312.4816 | 11.58% | 0% | 88.42% | 23.1966 | 40.4644 | 0 | 23.1966 | 0 | 0 | 40.4644 | 0 | 516 |  | 932 | 516-7F | 353.406 | 330.2094 | 312.9417 | 40.9245 | 17.7279 | 0.4601 | 0 | 0 | 0 | 312.4816 | 0.23513 | 0.23513 | 0.23513 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23513 | 28.386 | 28.386 | 28.386 | 0 | 0 | 0 | 0 | 0 | 0 | 28.386 | 324.7848 | 301.5883 | 284.3205 | 40.9245 | 17.7279 | 0.4601 | 0 | 0 | 0 | 283.8604 | 0.0005526 | 0.0002392 | 6e-06 | 0 | 0 | 0 | 0.000437 | 5000000 | scaled
518-39 | 1403.0335 | 952.5434 | 0 | 450.4901 | 67.89% | 0% | 32.11% | 540.6133 | 941.7733 | 2.522 | 525.2417 | 12.8496 | 4.1182 | 916.6759 | 20.9791 | 518 |  | 933 | 518-39 | 1403.0335 | 862.4202 | 461.2602 | 952.5434 | 411.9301 | 10.7701 | 0 | 0 | 0 | 450.4901 | 4.5916 | 2.0696 | 0.47338 | 4.2526 | 1.7306 | 0.1344 | 0 | 0 | 0 | 0.33898 | 62.5864 | 49.7368 | 41.6073 | 21.6636 | 8.814 | 0.68444 | 0 | 0 | 0 | 40.9228 | 1335.8555 | 810.6138 | 419.1796 | 926.6272 | 401.3855 | 9.9513 | 0 | 0 | 0 | 409.2283 | 0.0014574 | 0.000663 | 1.64e-05 | 0 | 0 | 0 | 0.0006316 | 5000000 | scaled
518-41 | 181.2908 | 110.5372 | 0 | 70.7536 | 60.97% | 0% | 39.03% | 62.8821 | 109.5536 | 0 | 62.8821 | 0 | 0 | 109.5536 | 0 | 518 |  | 934 | 518-41 | 181.2908 | 118.4087 | 71.7371 | 110.5372 | 47.655 | 0.98351 | 0 | 0 | 0 | 70.7536 | 0.05324 | 0.05324 | 0.05324 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05324 | 6.4273 | 6.4273 | 6.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4273 | 174.8102 | 111.9281 | 65.2566 | 110.5372 | 47.655 | 0.98351 | 0 | 0 | 0 | 64.2731 | 0.0001382 | 5.98e-05 | 1.4e-06 | 0 | 0 | 0 | 9.48e-05 | 5000000 | scaled
518-42AE | 344.3142 | 101.0173 | 0 | 243.2969 | 29.34% | 0% | 70.66% | 57.6349 | 99.8458 | 0.18169 | 56.5199 | 0.93328 | 0.20652 | 98.5778 | 1.0615 | 518 |  | 935 | 518-42AE | 344.3142 | 286.6793 | 244.4684 | 101.0173 | 43.3825 | 1.1715 | 0 | 0 | 0 | 243.2969 | 0.3896 | 0.2079 | 0.18307 | 0.20652 | 0.02483 | 0 | 0 | 0 | 0 | 0.18307 | 23.1627 | 22.2295 | 22.1013 | 1.0615 | 0.12821 | 0 | 0 | 0 | 0 | 22.1013 | 320.7619 | 264.242 | 222.1841 | 99.7493 | 43.2294 | 1.1715 | 0 | 0 | 0 | 221.0125 | 0.0004696 | 0.0002036 | 5.2e-06 | 0 | 0 | 0 | 0.0003502 | 5000000 | scaled
519-46R | 7592.4505 | 4127.822 | 0 | 3464.6285 | 54.37% | 0% | 45.63% | 1861.6943 | 4069.8989 | 0 | 1861.6943 | 0 | 0 | 4069.8989 | 0 | 519 |  | 936 | 519-46R | 7592.4505 | 5730.7562 | 3522.5516 | 4127.822 | 2266.1277 | 57.9232 | 0 | 0 | 0 | 3464.6285 | 2.607 | 2.607 | 2.607 | 0 | 0 | 0 | 0 | 0 | 0 | 2.607 | 314.7292 | 314.7292 | 314.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 314.7292 | 7275.1143 | 5413.4199 | 3205.2154 | 4127.822 | 2266.1277 | 57.9232 | 0 | 0 | 0 | 3147.2922 | 0.0089606 | 0.0042068 | 0.0001064 | 0 | 0 | 0 | 0.0048942 | 5000000 | scaled
52-16F | 647.5006 | 75.3956 | 0 | 572.105 | 11.64% | 0% | 88.36% | 42.8661 | 74.5939 | 0.042172 | 42.5913 | 0.23261 | 0.043354 | 74.3118 | 0.23871 | 52 |  | 937 | 52-16F | 647.5006 | 604.6346 | 572.9068 | 75.3956 | 32.5296 | 0.80176 | 0 | 0 | 0 | 572.105 | 0.47384 | 0.43167 | 0.43049 | 0.043354 | 0.0011824 | 0 | 0 | 0 | 0 | 0.43049 | 52.2091 | 51.9765 | 51.9704 | 0.23871 | 0.006094 | 0 | 0 | 0 | 0 | 51.9704 | 594.8177 | 552.2264 | 520.5059 | 75.1136 | 32.5223 | 0.80176 | 0 | 0 | 0 | 519.7041 | 0.001122 | 0.0004858 | 1.18e-05 | 0 | 0 | 0 | 0.0008 | 5000000 | scaled
52-17F | 2009.8379 | 876.5069 | 0 | 1133.3309 | 43.61% | 0% | 56.39% | 496.8051 | 867.0628 | 0 | 496.8051 | 0 | 0 | 867.0628 | 0 | 52 |  | 938 | 52-17F | 2009.8379 | 1513.0327 | 1142.7751 | 876.5069 | 379.7018 | 9.4442 | 0 | 0 | 0 | 1133.3309 | 0.8528 | 0.8528 | 0.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8528 | 102.9526 | 102.9526 | 102.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9526 | 1906.0325 | 1409.2274 | 1038.9697 | 876.5069 | 379.7018 | 9.4442 | 0 | 0 | 0 | 1029.5256 | 0.0027094 | 0.0011732 | 2.96e-05 | 0 | 0 | 0 | 0.0016266 | 5000000 | scaled
52-18F | 11618.3539 | 7907.1835 | 0 | 3711.1704 | 68.06% | 0% | 31.94% | 4184.7943 | 7811.7987 | 0 | 4184.7943 | 0 | 0 | 7811.7987 | 0 | 52 |  | 939 | 52-18F | 11618.3539 | 7433.5596 | 3806.5552 | 7907.1835 | 3722.3892 | 95.3848 | 0 | 0 | 0 | 3711.1704 | 2.7925 | 2.7925 | 2.7925 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7925 | 337.1253 | 337.1253 | 337.1253 | 0 | 0 | 0 | 0 | 0 | 0 | 337.1253 | 11278.4361 | 7093.6418 | 3466.6374 | 7907.1835 | 3722.3892 | 95.3848 | 0 | 0 | 0 | 3371.2526 | 0.0073846 | 0.0032762 | 8.3e-05 | 0 | 0 | 0 | 0.0052096 | 5000000 | scaled
52-20R | 5958.3686 | 2880.1765 | 0 | 3078.1921 | 48.34% | 0% | 51.66% | 1632.9477 | 2847.9773 | 0.080402 | 1632.4495 | 0.41778 | 0.13085 | 2847.1634 | 0.68308 | 52 |  | 940 | 52-20R | 5958.3686 | 4325.4209 | 3110.3913 | 2880.1765 | 1247.2287 | 32.1991 | 0 | 0 | 0 | 3078.1921 | 2.4471 | 2.3667 | 2.3162 | 0.13085 | 0.050448 | 0 | 0 | 0 | 0 | 2.3162 | 280.3082 | 279.8904 | 279.6251 | 0.68308 | 0.26531 | 0 | 0 | 0 | 0 | 279.6251 | 5675.6133 | 4043.1638 | 2828.4499 | 2879.3625 | 1246.913 | 32.1991 | 0 | 0 | 0 | 2796.2508 | 0.0070072 | 0.0030338 | 7.76e-05 | 0 | 0 | 0 | 0.0043194 | 5000000 | scaled
520-1045R | 2978813.9644 | 2899717.5924 | 73616.8404 | 5479.5316 | 97.34% | 2.471% | 0.184% | 886717.5218 | 2917325.6317 | 46925.4838 | 27598.8962 | 812193.1418 | 157182.4632 | 58306.6534 | 2701836.5151 | 520 |  | 941 | 520-1045R | 2978813.9644 | 2092096.4426 | 61488.3327 | 2899717.5924 | 2044959.8717 | 49012.5006 | 73616.8404 | 41657.0393 | 6996.3005 | 5479.5316 | 159970.6639 | 113045.1801 | 2788.2007 | 159884.177 | 112994.4503 | 2776.2499 | 82.3637 | 46.6066 | 7.8276 | 4.1232 | 2749572.9518 | 1937379.81 | 47736.4367 | 2738196.8104 | 1930726.3756 | 46204.8274 | 10878.377 | 6155.67 | 1033.8449 | 497.7644 | 69270.3487 | 41671.4525 | 10963.6953 | 1636.605 | 1239.0458 | 31.4233 | 62656.0997 | 35454.7627 | 5954.628 | 4977.644 | 0.027405 | 0.01976 | 0.0005016 | 0.23313 | 0.13248 | 0.023313 | 0.007699 | 5000000 | scaled
520-10R | 1478744.639 | 1448788.0509 | 26017.2587 | 3939.3293 | 97.97% | 1.759% | 0.2664% | 710773.357 | 1453446.2002 | 75051.8036 | 14410.5369 | 621311.0165 | 153524.7819 | 31142.5099 | 1268778.9084 | 520 |  | 942 | 520-10R | 1478744.639 | 767971.282 | 25298.4389 | 1448788.0509 | 749578.0387 | 19490.7069 | 26017.2587 | 14453.914 | 1868.4026 | 3939.3293 | 155640.5385 | 80588.7349 | 2115.7566 | 155606.2058 | 80568.3439 | 2110.5397 | 31.3685 | 17.4268 | 2.2527 | 2.9642 | 1286546.059 | 665235.0425 | 17767.1506 | 1283870.5675 | 663589.6238 | 17242.8603 | 2317.6401 | 1287.5673 | 166.4389 | 357.8514 | 36558.0415 | 22147.5046 | 5415.5316 | 9311.2776 | 5420.071 | 137.3068 | 23668.2501 | 13148.9199 | 1699.711 | 3578.5137 | 0.016027 | 0.0080356 | 0.000204 | 0.024483 | 0.013935 | 0.0024484 | 0.005533 | 5000000 | scaled
520-1489R | 2637933.8386 | 2552367.6877 | 73796.5863 | 11769.5647 | 96.76% | 2.798% | 0.4462% | 784901.368 | 2580464.6677 | 42154.468 | 28931.9207 | 713814.9793 | 139034.2565 | 62149.3277 | 2379281.0835 | 520 |  | 943 | 520-1489R | 2637933.8386 | 1853032.4706 | 57469.1709 | 2552367.6877 | 1799944.4493 | 39436.6811 | 73796.5863 | 41318.4566 | 6262.9251 | 11769.5647 | 141247.1189 | 99092.6508 | 2212.8624 | 141128.8819 | 99022.5527 | 2194.7233 | 109.3807 | 61.2419 | 9.2829 | 8.8562 | 2418384.5531 | 1704569.5737 | 39103.4695 | 2407028.9283 | 1697741.0593 | 37161.3282 | 10286.4694 | 5759.3591 | 872.986 | 1069.1553 | 78302.1667 | 49370.246 | 16152.839 | 4209.8774 | 3180.8373 | 80.6296 | 63400.7361 | 35497.8556 | 5380.6562 | 10691.5531 | 0.054807 | 0.039363 | 0.0010044 | 0.066817 | 0.037911 | 0.0066816 | 0.016593 | 5000000 | scaled
520-1509R | 3413911.7889 | 3165391.0031 | 238763.1895 | 9757.5962 | 92.72% | 6.994% | 0.2858% | 1334939.0942 | 3331236.7966 | 73211.5774 | 92866.5125 | 1168861.0042 | 185903.8219 | 194413.6984 | 2950919.2764 | 520 |  | 944 | 520-1509R | 3413911.7889 | 2078972.6947 | 82674.9922 | 3165391.0031 | 1934107.7774 | 50247.221 | 238763.1895 | 135107.3211 | 22670.175 | 9757.5962 | 188988.6435 | 115777.0661 | 3084.8216 | 188652.4205 | 115583.6223 | 3046.2526 | 328.8808 | 186.1016 | 31.2267 | 7.3423 | 3001426.0229 | 1832565.0187 | 50506.7465 | 2974660.4792 | 1817034.5674 | 47163.1761 | 25879.157 | 14644.0646 | 2457.1837 | 886.3867 | 223497.1224 | 130630.6099 | 29083.4241 | 2078.1035 | 1489.5877 | 37.7922 | 212555.1517 | 120277.155 | 20181.7646 | 8863.8672 | 0.043215 | 0.026412 | 0.0006708 | 0.22859 | 0.12991 | 0.022859 | 0.013805 | 5000000 | scaled
520-1525R | 1632803.2803 | 1604824.3239 | 23442.3442 | 4536.6122 | 98.29% | 1.436% | 0.2778% | 683675.0152 | 1596428.0083 | 69850.1304 | 13443.4781 | 600381.4067 | 162698.8211 | 29480.0354 | 1404249.1518 | 520 |  | 945 | 520-1525R | 1632803.2803 | 949128.2651 | 36375.272 | 1604824.3239 | 931459.1011 | 29849.6075 | 23442.3442 | 13132.5518 | 1989.0523 | 4536.6122 | 165691.5844 | 95841.454 | 2992.7633 | 165660.9861 | 95822.8113 | 2987.0431 | 27.1847 | 15.2291 | 2.3066 | 3.4137 | 1431605.4595 | 831224.0528 | 27356.3076 | 1428344.3799 | 829215.9322 | 26702.4673 | 2848.9707 | 1596.0117 | 241.7314 | 412.109 | 35506.2364 | 22062.7583 | 6026.201 | 10818.9579 | 6420.3576 | 160.0972 | 20566.1888 | 11521.3111 | 1745.0142 | 4121.0896 | 0.025799 | 0.015453 | 0.000393 | 0.066858 | 0.037957 | 0.0066858 | 0.0063858 | 5000000 | scaled
520-1527R | 6763000.618 | 6541015.7388 | 214761.3737 | 7223.5055 | 96.72% | 3.176% | 0.1068% | 3328607.1842 | 6659390.4164 | 241789.4308 | 85294.9426 | 3001522.8108 | 483700.5136 | 180117.9444 | 5995571.9584 | 520 |  | 946 | 520-1527R | 6763000.618 | 3434393.4338 | 103610.2017 | 6541015.7388 | 3305686.077 | 76002.5512 | 214761.3737 | 121483.8513 | 20384.145 | 7223.5055 | 489458.6042 | 247669.1733 | 5758.0906 | 489099.5805 | 247463.724 | 5719.0942 | 353.5882 | 200.0139 | 33.5609 | 5.4355 | 6068454.9573 | 3066932.1466 | 72882.999 | 6046211.5049 | 3054064.7122 | 70177.8486 | 21587.2643 | 12211.2462 | 2048.9621 | 656.1882 | 205087.0565 | 119792.1139 | 24969.1121 | 5704.6534 | 4157.6408 | 105.6084 | 192820.5212 | 109072.5912 | 18301.6219 | 6561.8819 | 0.033612 | 0.017343 | 0.0004396 | 0.22731 | 0.12914 | 0.022731 | 0.010119 | 5000000 | scaled
520-1902R | 748333.0035 | 578740.6593 | 162393.6024 | 7198.7418 | 77.34% | 21.7% | 0.962% | 384280.6898 | 723866.683 | 34898.9778 | 68247.3683 | 281134.3437 | 64212.0342 | 141339.4705 | 518315.1783 | 520 |  | 947 | 520-1902R | 748333.0035 | 364052.3137 | 24466.3205 | 578740.6593 | 266680.17 | 5614.3607 | 162393.6024 | 90173.4019 | 11653.218 | 7198.7418 | 64856.0347 | 29957.0569 | 644.0005 | 64607.1836 | 29816.4667 | 621.1151 | 243.4343 | 135.1734 | 17.4686 | 5.4168 | 525074.7667 | 243940.423 | 6759.5884 | 507896.7348 | 234111.0386 | 4919.8958 | 16524.0933 | 9175.4458 | 1185.754 | 653.9386 | 158402.2021 | 90154.8338 | 17062.7316 | 6236.7408 | 2752.6647 | 73.3499 | 145626.0749 | 80862.7827 | 10449.9954 | 6539.3864 | 0.024573 | 0.010961 | 0.000301 | 0.024276 | 0.013808 | 0.0024276 | 0.010083 | 5000000 | scaled
520-1904 | 2084535.8949 | 2011216.826 | 68063.2114 | 5255.8575 | 96.48% | 3.265% | 0.2521% | 1154598.7581 | 2049614.0244 | 76977.3897 | 28691.7506 | 1048929.6178 | 136253.6122 | 59619.7778 | 1853740.6345 | 520 |  | 948 | 520-1904 | 2084535.8949 | 929937.1368 | 34921.8705 | 2011216.826 | 886831.0156 | 24781.6177 | 68063.2114 | 37850.2638 | 4884.3952 | 5255.8575 | 137931.1372 | 60953.7476 | 1677.525 | 137837.3185 | 60899.819 | 1667.1213 | 89.8639 | 49.9737 | 6.4489 | 3.9549 | 1877727.1119 | 828797.494 | 23986.4774 | 1871457.8963 | 825099.2186 | 23093.3991 | 5791.7698 | 3220.8298 | 415.6326 | 477.4457 | 68877.6458 | 40185.8952 | 9257.868 | 1921.6112 | 831.978 | 21.0974 | 62181.5776 | 34579.4603 | 4462.3137 | 4774.4569 | 0.020946 | 0.0092068 | 0.0002346 | 0.024423 | 0.013913 | 0.0024422 | 0.007411 | 5000000 | scaled
520-1936 | 63711.1322 | 63565.9402 | 0 | 145.192 | 99.77% | 0% | 0.2279% | 28767.427 | 61630.4668 | 1657.4258 | 0 | 27110.0013 | 3480.5331 | 0 | 58149.9337 | 520 |  | 949 | 520-1936 | 63711.1322 | 34943.7052 | 2080.6654 | 63565.9402 | 34798.5132 | 1935.4734 | 0 | 0 | 0 | 145.192 | 3586.5149 | 1929.0891 | 105.9817 | 3586.4056 | 1928.9799 | 105.8725 | 0 | 0 | 0 | 0.10925 | 59992.724 | 32882.7227 | 1842.7903 | 59979.5346 | 32869.5334 | 1829.6009 | 0 | 0 | 0 | 13.1893 | 131.8934 | 131.8934 | 131.8934 | 0 | 0 | 0 | 0 | 0 | 0 | 131.8934 | 0.0004712 | 0.000204 | 5.2e-06 | 0 | 0 | 0 | 0.0001956 | 5000000 | scaled
520-22R | 258296.0488 | 193006.7992 | 63350.6437 | 1938.6059 | 74.72% | 24.53% | 0.7505% | 127604.6457 | 247048.1806 | 15391.1456 | 36149.4497 | 76064.0503 | 28310.9684 | 81717.361 | 137019.8511 | 520 |  | 950 | 520-22R | 258296.0488 | 130691.4031 | 11247.8682 | 193006.7992 | 93532.6039 | 4764.4933 | 63350.6437 | 35220.1933 | 4544.769 | 1938.6059 | 29067.1936 | 13676.048 | 756.2252 | 28999.4522 | 13637.739 | 750.0113 | 66.2827 | 36.8503 | 4.7551 | 1.4587 | 141385.7908 | 65321.7405 | 4365.9397 | 133162.9631 | 60672.0091 | 3612.5643 | 8046.7235 | 4473.6271 | 577.2712 | 176.1043 | 87843.0643 | 51693.6146 | 6125.7033 | 30844.3839 | 19222.8558 | 401.9177 | 55237.6376 | 30709.716 | 3962.7427 | 1761.0428 | 0.0088126 | 0.0044532 | 0.0001136 | 0.024437 | 0.013917 | 0.0024438 | 0.0027606 | 5000000 | scaled
520-35R | 4997794.2437 | 4822590.9181 | 165559.9169 | 9643.4087 | 96.49% | 3.313% | 0.193% | 1699357.9455 | 4875660.9853 | 102951.625 | 63998.7377 | 1532407.5827 | 297111.6062 | 136520.6549 | 4442028.7241 | 520 |  | 951 | 520-35R | 4997794.2437 | 3298436.2982 | 122133.2584 | 4822590.9181 | 3195130.2279 | 96776.4643 | 165559.9169 | 93662.6617 | 15713.3854 | 9643.4087 | 303224.098 | 200272.4729 | 6112.4917 | 302995.4121 | 200139.9467 | 6084.2194 | 221.4295 | 125.2699 | 21.016 | 7.2564 | 4535529.9457 | 3003122.363 | 93501.2216 | 4512948.8989 | 2989967.1019 | 90565.1708 | 21705.033 | 12279.2473 | 2060.037 | 876.0138 | 159040.2 | 95041.4623 | 22519.5451 | 6646.607 | 5023.1793 | 127.0742 | 143633.4545 | 81258.1445 | 13632.3324 | 8760.1385 | 0.044456 | 0.028772 | 0.0007304 | 0.22732 | 0.12915 | 0.022732 | 0.013661 | 5000000 | scaled
520-45 | 2044646.2599 | 1994999.328 | 43554.5192 | 6092.4127 | 97.57% | 2.13% | 0.298% | 557837.4903 | 1998245.4924 | 27794.8152 | 16500.0798 | 513542.5953 | 100731.8743 | 34698.343 | 1862815.2751 | 520 |  | 952 | 520-45 | 2044646.2599 | 1486808.7697 | 46400.7675 | 1994999.328 | 1456326.8782 | 36614.6606 | 43554.5192 | 24389.4788 | 3693.6942 | 6092.4127 | 102630.326 | 74835.5108 | 1898.4517 | 102587.4733 | 74809.4971 | 1890.622 | 38.2684 | 21.4294 | 3.2454 | 4.5843 | 1898625.8566 | 1385083.2613 | 35810.5815 | 1891602.5709 | 1380906.8645 | 34708.4593 | 6469.8468 | 3622.9579 | 548.6833 | 553.4389 | 43390.0773 | 26889.9975 | 8691.7343 | 809.2839 | 610.5167 | 15.5794 | 37046.404 | 20745.0914 | 3141.7655 | 5534.3894 | 0.029243 | 0.021168 | 0.0005374 | 0.066565 | 0.037766 | 0.0066566 | 0.0086532 | 5000000 | scaled
521-14R | 11350287.4351 | 10974724.5582 | 366912.4365 | 8650.4405 | 96.69% | 3.233% | 0.07621% | 5913309.0249 | 11157608.7627 | 321228.2719 | 146617.9457 | 5445462.8073 | 602968.4566 | 305129.571 | 10249510.7351 | 521 |  | 953 | 521-14R | 11350287.4351 | 5436978.4102 | 192678.6725 | 10974724.5582 | 5220798.1947 | 149259.4381 | 366912.4365 | 207529.7751 | 34768.7939 | 8650.4405 | 611249.562 | 290021.29 | 8281.1054 | 610759.8289 | 289741.464 | 8228.8057 | 483.2239 | 273.3169 | 45.7905 | 6.5092 | 10394345.0438 | 4948882.2365 | 144834.3086 | 10361403.7425 | 4929908.9204 | 141001.4275 | 32155.4893 | 18187.5042 | 3047.0692 | 785.8119 | 344692.8294 | 198074.8837 | 39563.2584 | 2560.9868 | 1147.8103 | 29.2049 | 334273.7233 | 189068.9541 | 31675.9341 | 7858.1194 | 0.038563 | 0.018126 | 0.0004602 | 0.22026 | 0.12513 | 0.022026 | 0.012147 | 5000000 | scaled
521-1819R | 810999.5818 | 724333.0113 | 83051.8447 | 3614.7258 | 89.31% | 10.24% | 0.4457% | 393355.9288 | 789289.394 | 44782.4065 | 36373.3104 | 312200.212 | 89495.1458 | 76797.1007 | 622997.1475 | 521 |  | 954 | 521-1819R | 810999.5818 | 417643.653 | 21710.1878 | 724333.0113 | 367859.4016 | 12136.6553 | 83051.8447 | 46169.5255 | 5958.8067 | 3614.7258 | 91012.9643 | 46230.5578 | 1517.8185 | 90902.7204 | 46168.064 | 1507.3839 | 107.5239 | 59.7738 | 7.7146 | 2.72 | 634364.0284 | 322163.8164 | 11366.8808 | 627048.1752 | 317951.0225 | 10537.1781 | 6987.489 | 3884.4297 | 501.3386 | 328.3642 | 85622.5892 | 49249.2788 | 8825.4885 | 6382.1157 | 3740.3151 | 92.0933 | 75956.8318 | 42225.322 | 5449.7535 | 3283.6417 | 0.014197 | 0.0069358 | 0.0001758 | 0.024406 | 0.013899 | 0.0024406 | 0.0050642 | 5000000 | scaled
521-1856R | 8477861.6937 | 8290637.7323 | 178342.4023 | 8881.5591 | 97.79% | 2.104% | 0.1048% | 4554944.3134 | 8357638.8249 | 250406.3001 | 71403.1615 | 4233134.8519 | 458896.2731 | 148162.1785 | 7750580.3733 | 521 |  | 955 | 521-1856R | 8477861.6937 | 3922917.3803 | 120222.8688 | 8290637.7323 | 3813605.4595 | 95310.3822 | 178342.4023 | 100430.3617 | 16030.9274 | 8881.5591 | 464240.5315 | 213834.2314 | 5344.2584 | 463894.6547 | 213636.5374 | 5307.0857 | 339.1937 | 191.0109 | 30.4896 | 6.6831 | 7843179.7736 | 3610044.9217 | 92599.4002 | 7821813.9028 | 3597660.6425 | 89944.5703 | 20559.0638 | 11577.4723 | 1848.023 | 806.8069 | 170441.3887 | 99038.2272 | 22279.2102 | 4929.1748 | 2308.2796 | 58.7262 | 157444.1448 | 88661.8785 | 14152.4148 | 8068.0691 | 0.034618 | 0.016333 | 0.0004146 | 0.10709 | 0.06082 | 0.010709 | 0.012402 | 5000000 | scaled
521-18R | 8713017.2766 | 8657405.5156 | 47262.4022 | 8349.3587 | 99.36% | 0.5424% | 0.09583% | 4389847.9817 | 8592680.1329 | 247446.2306 | 21010.2329 | 4121391.5182 | 485295.927 | 44350.3472 | 8063033.8586 | 521 |  | 956 | 521-18R | 8713017.2766 | 4323169.2949 | 120337.1437 | 8657405.5156 | 4288554.6273 | 108597.1669 | 47262.4022 | 26265.3089 | 3390.6181 | 8349.3587 | 491469.7953 | 244023.5647 | 6173.8683 | 491365.2766 | 243962.689 | 6160.5382 | 98.2361 | 54.5931 | 7.0475 | 6.2826 | 8166506.4956 | 4045114.9774 | 103472.6369 | 8160830.6847 | 4041623.7792 | 102361.4034 | 4917.3494 | 2732.7367 | 352.772 | 758.4615 | 55040.9857 | 34030.7528 | 10690.6385 | 5209.5543 | 2968.1591 | 75.2253 | 42246.8168 | 23477.9791 | 3030.7986 | 7584.6146 | 0.035045 | 0.017251 | 0.0004368 | 0.024471 | 0.013933 | 0.0024472 | 0.011805 | 5000000 | scaled
521-27R | 5618622.9164 | 5550019.8098 | 61335.2906 | 7267.816 | 98.78% | 1.092% | 0.1294% | 3016283.1701 | 5528758.3545 | 218345.0884 | 30324.3208 | 2767613.7609 | 398972.9287 | 61670.8757 | 5068114.5501 | 521 |  | 957 | 521-27R | 5618622.9164 | 2602339.7463 | 89864.5619 | 5550019.8098 | 2560999.9264 | 78197.6545 | 61335.2906 | 34072.0039 | 4399.0913 | 7267.816 | 404655.8297 | 186310.7413 | 5682.901 | 404561.2767 | 186255.7859 | 5671.0429 | 89.0842 | 49.4866 | 6.3893 | 5.4688 | 5141598.5438 | 2373984.7828 | 73483.9936 | 5135169.0381 | 2370119.7041 | 72409.9949 | 5769.2923 | 3204.8654 | 413.7853 | 660.2134 | 72368.5429 | 42044.2222 | 10697.6672 | 10289.495 | 4624.4365 | 116.6167 | 55476.9141 | 30817.6519 | 3978.9167 | 6602.1338 | 0.029051 | 0.013285 | 0.0003376 | 0.024453 | 0.013917 | 0.0024454 | 0.010163 | 5000000 | scaled
521-32R | 12241713.4625 | 12165680.2675 | 69068.987 | 6964.2079 | 99.38% | 0.5642% | 0.05689% | 5829357.3671 | 12062873.6618 | 362468.2226 | 27411.4642 | 5439477.6803 | 749916.2107 | 57134.4287 | 11255823.0224 | 521 |  | 958 | 521-32R | 12241713.4625 | 6412356.0954 | 178839.8007 | 12165680.2675 | 6366487.1655 | 165665.8696 | 69068.987 | 38904.722 | 6209.7232 | 6964.2079 | 760329.9374 | 397861.7148 | 10413.7266 | 760201.719 | 397787.2042 | 10397.4298 | 122.978 | 69.2702 | 11.0565 | 5.2403 | 11412366.8363 | 5972889.156 | 156543.8139 | 11404427.0816 | 5968140.6157 | 155254.2257 | 7307.1213 | 4115.9069 | 656.9548 | 632.6334 | 69016.6888 | 41605.2246 | 11882.2601 | 1051.4669 | 559.3456 | 14.2141 | 61638.8877 | 34719.5448 | 5541.7119 | 6326.3341 | 0.031334 | 0.016436 | 0.0004172 | 0.10731 | 0.060959 | 0.010731 | 0.0097964 | 5000000 | scaled
521-700R | 9012544.5994 | 8927133.7418 | 75930.6611 | 9480.1965 | 99.05% | 0.8425% | 0.1052% | 4798276.536 | 8914353.5891 | 354749.1254 | 36637.8863 | 4406889.5243 | 659501.8963 | 79504.3672 | 8175347.3256 | 521 |  | 959 | 521-700R | 9012544.5994 | 4214268.0634 | 98191.0103 | 8927133.7418 | 4162575.9373 | 83266.1297 | 75930.6611 | 42211.9297 | 5444.6841 | 9480.1965 | 665739.0936 | 310989.9682 | 6237.1972 | 665629.9713 | 310926.1363 | 6222.7505 | 101.9887 | 56.6983 | 7.3132 | 7.1335 | 8253492.9625 | 3846603.4382 | 78145.6369 | 8245730.1745 | 3841905.4624 | 76789.5632 | 6901.6004 | 3836.7883 | 494.8862 | 861.1875 | 93312.5433 | 56674.657 | 13808.1761 | 15773.596 | 9744.3385 | 253.816 | 68927.0719 | 38318.443 | 4942.4847 | 8611.8754 | 0.036793 | 0.017612 | 0.0004464 | 0.024382 | 0.013887 | 0.0024382 | 0.013245 | 5000000 | scaled
522-34 | 112711.73 | 48493.7178 | 62905.26 | 1312.7522 | 43.02% | 55.81% | 1.165% | 52373.2043 | 105556.1356 | 1916.5846 | 28706.8696 | 21749.7501 | 3678.5114 | 60485.5033 | 41392.1209 | 522 |  | 960 | 522-34 | 112711.73 | 60338.5257 | 7155.5944 | 48493.7178 | 24041.0033 | 1333.0064 | 62905.26 | 34984.7702 | 4509.8358 | 1312.7522 | 3789.4316 | 1872.8469 | 110.9201 | 3713.4044 | 1830.126 | 104.5526 | 75.0393 | 41.7331 | 5.3798 | 0.9878 | 43026.7553 | 21277.0051 | 1634.6344 | 37828.5688 | 18333.1032 | 1151.2615 | 5078.9352 | 2824.6506 | 364.1216 | 119.2513 | 65895.5432 | 37188.6736 | 5410.0399 | 6951.7447 | 3877.774 | 77.1924 | 57751.2854 | 32118.3865 | 4140.3344 | 1192.5131 | 0.0037922 | 0.0018788 | 4.78e-05 | 0.024364 | 0.013884 | 0.0024364 | 0.0018524 | 5000000 | scaled
522-36 | 116957.6872 | 26354.7042 | 89088.0048 | 1514.9782 | 22.53% | 76.17% | 1.295% | 53962.354 | 109035.0707 | 1121.2421 | 36580.0468 | 16261.0651 | 2099.3437 | 76139.2025 | 30796.5244 | 522 |  | 961 | 522-36 | 116957.6872 | 62995.3332 | 7922.6165 | 26354.7042 | 11960.08 | 22.056 | 89088.0048 | 49520.275 | 6385.5823 | 1514.9782 | 2109.2194 | 987.9773 | 9.8757 | 2009.0781 | 931.8067 | 1.6396 | 99.0013 | 55.0307 | 7.0961 | 1.14 | 31552.1131 | 15291.048 | 755.5886 | 22921.077 | 10432.2944 | 9.1825 | 8493.4144 | 4721.1319 | 608.7845 | 137.6217 | 83296.3547 | 46716.3079 | 7157.1522 | 1424.5491 | 595.9789 | 11.2339 | 80495.589 | 44744.1124 | 5769.7017 | 1376.2166 | 0.0046342 | 0.0021524 | 5.44e-05 | 0.024328 | 0.013858 | 0.0024328 | 0.0021292 | 5000000 | scaled
522-38R | 5639841.4319 | 5439139.6424 | 188304.5448 | 12397.2448 | 96.44% | 3.339% | 0.2198% | 2892813.793 | 5544012.3981 | 351274.5471 | 80410.4103 | 2461128.8356 | 672533.535 | 169422.6885 | 4702056.1746 | 522 |  | 962 | 522-38R | 5639841.4319 | 2747027.639 | 95829.0339 | 5439139.6424 | 2630068.0134 | 69939.9589 | 188304.5448 | 104562.3808 | 13491.8302 | 12397.2448 | 681322.9005 | 330048.3534 | 8789.3655 | 681048.3722 | 329891.7638 | 8761.0357 | 265.1997 | 147.261 | 19.0013 | 9.3285 | 4765353.8601 | 2304225.0246 | 63297.6855 | 4748278.4455 | 2294242.5025 | 61028.7644 | 15949.2405 | 8856.3479 | 1142.747 | 1126.1742 | 193164.6714 | 112754.261 | 23741.9828 | 9812.8247 | 5933.7471 | 150.1588 | 172090.1046 | 95558.7719 | 12330.082 | 11261.742 | 0.046787 | 0.022805 | 0.0005792 | 0.024207 | 0.013776 | 0.0024208 | 0.017607 | 5000000 | scaled
523-31AE | 305199.014 | 35697.5026 | 266158.9754 | 3342.536 | 11.7% | 87.21% | 1.095% | 140011.3115 | 282547.5699 | 2834.4396 | 107733.1867 | 29443.6851 | 4779.352 | 224252.3478 | 53515.8701 | 523 |  | 963 | 523-31AE | 305199.014 | 165187.7025 | 22651.444 | 35697.5026 | 14070.1485 | 247.366 | 266158.9754 | 147775.018 | 19061.542 | 3342.536 | 4841.445 | 2007.0054 | 62.093 | 4509.395 | 1821.5281 | 35.9776 | 329.5348 | 182.9621 | 23.6003 | 2.5152 | 55959.9854 | 26516.3003 | 2444.1153 | 28336.0854 | 11044.0878 | 183.8783 | 27320.2618 | 15168.5742 | 1956.5987 | 303.6383 | 244397.5836 | 136664.3968 | 20145.2357 | 2852.0222 | 1204.5326 | 27.5102 | 238509.1788 | 132423.4816 | 17081.3429 | 3036.3826 | 0.0086164 | 0.0038144 | 9.76e-05 | 0.024081 | 0.013701 | 0.0024082 | 0.0047218 | 5000000 | scaled
524-1782F | 5468134.4802 | 5455868.3357 | 6254.5388 | 6011.6057 | 99.78% | 0.1144% | 0.1099% | 2982557.5203 | 5399865.3117 | 234216.9155 | 6240.0499 | 2742100.5549 | 424290.8209 | 12568.6626 | 4963005.8281 | 524 |  | 964 | 524-1782F | 5468134.4802 | 2485576.9598 | 68269.1685 | 5455868.3357 | 2476080.2643 | 61839.4707 | 6254.5388 | 3485.0898 | 418.0921 | 6011.6057 | 429154.7392 | 194937.8237 | 4863.9183 | 429143.0782 | 194929.3231 | 4858.9176 | 7.1375 | 3.9771 | 0.47712 | 4.5235 | 5020479.2827 | 2278378.7279 | 57473.4546 | 5019358.0762 | 2277512.1736 | 56888.9124 | 575.1082 | 320.4559 | 38.4438 | 546.0984 | 18500.4582 | 12260.4083 | 5931.7956 | 7367.1813 | 3638.7676 | 91.6406 | 5672.293 | 3160.6568 | 379.1712 | 5460.9838 | 0.026739 | 0.012444 | 0.0003162 | 0.005199 | 0.0029786 | 0.0005198 | 0.0084658 | 5000000 | scaled
524-27R | 11317694.2402 | 11291558.1537 | 16005.7023 | 10130.3841 | 99.77% | 0.1414% | 0.08951% | 5618050.5459 | 11171635.9377 | 448770.3429 | 16810.0122 | 5152470.1909 | 893536.0169 | 40150.8159 | 10237949.1049 | 524 |  | 965 | 524-27R | 11317694.2402 | 5699643.6943 | 146058.3025 | 11291558.1537 | 5680600.9529 | 134858.6495 | 16005.7023 | 8912.3573 | 1069.2689 | 10130.3841 | 904328.4614 | 455558.1186 | 10792.4445 | 904296.2945 | 455536.829 | 10783.182 | 24.5442 | 13.6668 | 1.6397 | 7.6228 | 10362607.6462 | 5210137.4553 | 124658.5413 | 10360348.7799 | 5208471.8313 | 123648.8634 | 1338.6153 | 745.3729 | 89.4269 | 920.251 | 50758.1326 | 33948.1205 | 10607.3167 | 26913.0794 | 16592.2926 | 426.604 | 14642.5429 | 8153.3175 | 978.2024 | 9202.5103 | 0.040777 | 0.02092 | 0.0005324 | 0.0051862 | 0.0029694 | 0.0005186 | 0.014244 | 5000000 | scaled
524-46R | 13710953.333 | 13572074.1792 | 131033.6277 | 7845.5261 | 98.99% | 0.9557% | 0.05722% | 6716986.8655 | 13545645.7149 | 501075.1842 | 56643.1035 | 6159268.5779 | 1010322.1987 | 116069.7812 | 12419253.735 | 524 |  | 966 | 524-46R | 13710953.333 | 6993966.4675 | 165307.6181 | 13572074.1792 | 6912243.5753 | 145337.0589 | 131033.6277 | 73877.366 | 12125.033 | 7845.5261 | 1021368.5784 | 520293.3942 | 11046.3796 | 1021177.025 | 520182.8204 | 11023.2972 | 185.6498 | 104.6702 | 17.1789 | 5.9035 | 12555405.131 | 6396136.5531 | 136151.396 | 12541403.4923 | 6387931.491 | 134209.027 | 13288.9457 | 7492.3691 | 1229.676 | 712.693 | 134179.6237 | 77536.5202 | 18109.8425 | 9493.6619 | 4129.2639 | 104.7346 | 117559.0321 | 66280.3267 | 10878.1782 | 7126.9297 | 0.037121 | 0.018823 | 0.0004774 | 0.14094 | 0.079966 | 0.014094 | 0.011096 | 5000000 | scaled
524-50R | 8801876.9717 | 8643494.7957 | 151173.6186 | 7208.5574 | 98.2% | 1.718% | 0.0819% | 4440495.2479 | 8633930.1542 | 269941.2367 | 60257.3233 | 4110296.6878 | 524126.7451 | 125231.5181 | 7984571.8911 | 524 |  | 967 | 524-50R | 8801876.9717 | 4361381.7238 | 167946.8175 | 8643494.7957 | 4268932.0967 | 146750.3967 | 151173.6186 | 85241.0697 | 13987.8634 | 7208.5574 | 533165.0997 | 263223.863 | 9038.3547 | 532922.8625 | 263084.9089 | 9011.0185 | 236.813 | 133.5299 | 21.9119 | 5.4242 | 8124311.1075 | 4014014.4197 | 139739.2165 | 8108897.5737 | 4005037.7163 | 137718.786 | 14758.7035 | 8321.8732 | 1365.6002 | 654.8303 | 144400.7644 | 84143.4411 | 19169.2463 | 1674.3595 | 809.4715 | 20.5922 | 136178.102 | 76785.6667 | 12600.3512 | 6548.3029 | 0.032024 | 0.015766 | 0.0004008 | 0.14094 | 0.079971 | 0.014094 | 0.010167 | 5000000 | scaled
524-69R | 40375330.9497 | 39985024.927 | 367710.4494 | 22595.5733 | 99.03% | 0.9107% | 0.05596% | 20740870.2781 | 39800013.51 | 1144075.007 | 151387.4032 | 19445407.868 | 2192448.9403 | 313077.0943 | 37294487.4754 | 524 |  | 968 | 524-69R | 40375330.9497 | 19634460.6715 | 575317.4397 | 39985024.927 | 19404480.0505 | 518713.2191 | 367710.4494 | 207385.0477 | 34008.6472 | 22595.5733 | 2221303.4449 | 1077228.438 | 28854.5047 | 2220820.296 | 1076948.5335 | 28794.3895 | 466.1465 | 262.902 | 43.1128 | 17.0024 | 37789507.7421 | 18344099.8742 | 495020.2667 | 37753163.8349 | 18322707.318 | 489796.1493 | 34291.3099 | 19339.9588 | 3171.52 | 2052.5974 | 364519.7626 | 213132.3594 | 51442.6683 | 11040.7961 | 4824.1989 | 122.6804 | 332952.993 | 187782.1869 | 30794.0144 | 20525.9735 | 0.10118 | 0.04929 | 0.0012598 | 0.13969 | 0.07929 | 0.013969 | 0.031761 | 5000000 | scaled
525-41F | 35461.1498 | 0 | 35461.1498 | 0 | 0% | 100% | 0% | 5591.0184 | 11751.3358 | 7.5186 | 5125.5816 | 457.9183 | 15.8027 | 10773.0695 | 962.4635 | 525 |  | 969 | 525-41F | 35461.1498 | 29870.1314 | 23709.814 | 0 | 0 | 0 | 35461.1498 | 29870.1314 | 23709.814 | 0 | 47.6867 | 40.1681 | 31.884 | 0 | 0 | 0 | 47.6867 | 40.1681 | 31.884 | 0 | 2904.3561 | 2446.4378 | 1941.8925 | 0 | 0 | 0 | 2904.3561 | 2446.4378 | 1941.8925 | 0 | 32509.1071 | 27383.5255 | 21736.0375 | 0 | 0 | 0 | 32509.1071 | 27383.5255 | 21736.0375 | 0 | 0 | 0 | 0 | 0.00517 | 0.00517 | 0.00517 | 0 | 5000000 | scaled
53-49 | 1795.2575 | 285.8872 | 0 | 1509.3703 | 15.92% | 0% | 84.08% | 162.074 | 282.7038 | 0 | 162.074 | 0 | 0 | 282.7038 | 0 | 53 |  | 970 | 53-49 | 1795.2575 | 1633.1835 | 1512.5537 | 285.8872 | 123.8132 | 3.1833 | 0 | 0 | 0 | 1509.3703 | 1.1358 | 1.1358 | 1.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1358 | 137.1122 | 137.1122 | 137.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 137.1122 | 1657.0095 | 1494.9355 | 1374.3057 | 285.8872 | 123.8132 | 3.1833 | 0 | 0 | 0 | 1371.1224 | 0.004035 | 0.0017472 | 4.5e-05 | 0 | 0 | 0 | 0.0021528 | 5000000 | scaled
531-36AE | 9705.9894 | 5931.6076 | 0 | 3774.3818 | 61.11% | 0% | 38.89% | 2991.3515 | 5860.2108 | 14.7386 | 2900.7886 | 75.8243 | 29.0956 | 5681.36 | 149.7551 | 531 |  | 971 | 531-36AE | 9705.9894 | 6714.6379 | 3845.7786 | 5931.6076 | 2940.2561 | 71.3968 | 0 | 0 | 0 | 3774.3818 | 31.9357 | 17.1971 | 2.8401 | 29.0956 | 14.357 | 0 | 0 | 0 | 0 | 2.8401 | 492.6225 | 416.7983 | 342.8674 | 149.7551 | 73.9309 | 0 | 0 | 0 | 0 | 342.8674 | 9181.4311 | 6280.6425 | 3500.0711 | 5752.7569 | 2851.9683 | 71.3968 | 0 | 0 | 0 | 3428.6743 | 0.010665 | 0.0048142 | 0.0001214 | 0 | 0 | 0 | 0.0053352 | 5000000 | scaled
532-1293F | 1336.6341 | 743.2112 | 0 | 593.4229 | 55.6% | 0% | 44.4% | 417.0279 | 740.0234 | 35.6443 | 185.7484 | 195.6352 | 62.5119 | 333.9454 | 343.5661 | 532 |  | 972 | 532-1293F | 1336.6341 | 919.6063 | 596.6107 | 743.2112 | 326.1833 | 3.1878 | 0 | 0 | 0 | 593.4229 | 62.9584 | 27.3141 | 0.44653 | 62.5119 | 26.8676 | 0 | 0 | 0 | 0 | 0.44653 | 397.473 | 201.8379 | 53.9069 | 343.5661 | 147.9309 | 0 | 0 | 0 | 0 | 53.9069 | 876.2027 | 690.4543 | 542.2572 | 337.1332 | 151.3848 | 3.1878 | 0 | 0 | 0 | 539.0695 | 0.0014704 | 0.0006688 | 1.72e-05 | 0 | 0 | 0 | 0.0008418 | 5000000 | scaled
532-762 | 908.0556 | 798.7294 | 0 | 109.3262 | 87.96% | 0% | 12.04% | 407.522 | 789.99 | 5.526 | 373.5956 | 28.4003 | 10.9422 | 722.8285 | 56.2193 | 532 |  | 973 | 532-762 | 908.0556 | 500.5336 | 118.0656 | 798.7294 | 391.2074 | 8.7394 | 0 | 0 | 0 | 109.3262 | 11.0245 | 5.4985 | 0.082264 | 10.9422 | 5.4162 | 0 | 0 | 0 | 0 | 0.082264 | 66.1506 | 37.7502 | 9.9313 | 56.2193 | 27.819 | 0 | 0 | 0 | 0 | 9.9313 | 830.8805 | 457.2849 | 108.052 | 731.5679 | 357.9723 | 8.7394 | 0 | 0 | 0 | 99.3126 | 0.0002292 | 0.0001116 | 2.8e-06 | 0 | 0 | 0 | 0.0001484 | 5000000 | scaled
532-763 | 872935.3105 | 192670.4343 | 676183.7628 | 4081.1134 | 22.07% | 77.46% | 0.4675% | 397652.2431 | 806717.3825 | 8698.8554 | 271327.4701 | 117625.9176 | 16393.0813 | 563583.6922 | 226740.6089 | 532 |  | 974 | 532-763 | 872935.3105 | 475283.0674 | 66217.9281 | 192670.4343 | 91933.2007 | 2734.2711 | 676183.7628 | 379268.7533 | 59402.5436 | 4081.1134 | 16702.0165 | 8003.1611 | 308.9351 | 15743.1336 | 7463.9791 | 221.8964 | 955.8119 | 536.1111 | 83.9678 | 3.0709 | 234683.1365 | 117057.2189 | 7942.5276 | 176691.0706 | 84366.9128 | 2509.7792 | 57621.3347 | 32319.5749 | 5062.0172 | 370.7311 | 621550.1575 | 350222.6874 | 57966.4654 | 236.23 | 102.3088 | 2.5954 | 617606.6162 | 346413.0673 | 54256.5586 | 3707.3114 | 0.015537 | 0.0067272 | 0.0001714 | 0.086928 | 0.049277 | 0.0086928 | 0.0057242 | 5000000 | scaled
533-7AE | 45746.435 | 5186.6293 | 38848.245 | 1711.5606 | 11.34% | 84.92% | 3.741% | 19123.2423 | 40790.1677 | 227.0865 | 13577.4862 | 5318.6695 | 548.732 | 28443.8814 | 11797.5543 | 533 |  | 975 | 533-7AE | 45746.435 | 26623.1927 | 4956.2673 | 5186.6293 | 3124.3778 | 18.0106 | 38848.245 | 21787.2543 | 3226.6961 | 1711.5606 | 555.1887 | 328.1022 | 6.4567 | 516.1265 | 305.6293 | 2.0313 | 37.7743 | 21.1849 | 3.1375 | 1.2879 | 12631.7857 | 7313.1162 | 834.2314 | 4457.2738 | 2660.3242 | 12.6993 | 8019.0326 | 4497.3126 | 666.0528 | 155.4793 | 32559.4606 | 18981.9743 | 4115.5792 | 213.2291 | 158.4242 | 3.28 | 30791.4381 | 17268.7567 | 2557.5058 | 1554.7934 | 0.0053606 | 0.0032578 | 8.28e-05 | 0.058284 | 0.033153 | 0.0058284 | 0.0024522 | 5000000 | scaled
534-1079F | 3457.3197 | 0 | 3457.3197 | 0 | 0% | 100% | 0% | 280.6325 | 585.9319 | 0.68335 | 222.1059 | 57.8432 | 1.4268 | 463.7345 | 120.7706 | 534 |  | 976 | 534-1079F | 3457.3197 | 3176.6872 | 2871.3878 | 0 | 0 | 0 | 3457.3197 | 3176.6872 | 2871.3878 | 0 | 8.4187 | 7.7353 | 6.9919 | 0 | 0 | 0 | 8.4187 | 7.7353 | 6.9919 | 0 | 712.6131 | 654.7699 | 591.8424 | 0 | 0 | 0 | 712.6131 | 654.7699 | 591.8424 | 0 | 2736.2879 | 2514.182 | 2272.5534 | 0 | 0 | 0 | 2736.2879 | 2514.182 | 2272.5534 | 0 | 0 | 0 | 0 | 0.058455 | 0.058455 | 0.058455 | 0 | 5000000 | scaled
534-1080F | 45876.5355 | 0 | 45876.5355 | 0 | 0% | 100% | 0% | 3724.3064 | 7774.4473 | 6.935 | 2949.2869 | 768.0845 | 14.4767 | 6156.6028 | 1603.3677 | 534 |  | 977 | 534-1080F | 45876.5355 | 42152.229 | 38102.0882 | 0 | 0 | 0 | 45876.5355 | 42152.229 | 38102.0882 | 0 | 85.4261 | 78.4911 | 70.9494 | 0 | 0 | 0 | 85.4261 | 78.4911 | 70.9494 | 0 | 9461.3745 | 8693.29 | 7858.0068 | 0 | 0 | 0 | 9461.3745 | 8693.29 | 7858.0068 | 0 | 36329.7348 | 33380.4479 | 30173.132 | 0 | 0 | 0 | 36329.7348 | 33380.4479 | 30173.132 | 0 | 0 | 0 | 0 | 0.058418 | 0.058418 | 0.058418 | 0 | 5000000 | scaled
534-1081F | 10294.7805 | 0 | 10294.7805 | 0 | 0% | 100% | 0% | 835.6501 | 1742.5667 | 0.55244 | 666.9241 | 168.1736 | 1.152 | 1390.7253 | 350.6894 | 534 |  | 978 | 534-1081F | 10294.7805 | 9459.1304 | 8552.2138 | 0 | 0 | 0 | 10294.7805 | 9459.1304 | 8552.2138 | 0 | 6.8058 | 6.2533 | 5.6538 | 0 | 0 | 0 | 6.8058 | 6.2533 | 5.6538 | 0 | 2071.8119 | 1903.6384 | 1721.1225 | 0 | 0 | 0 | 2071.8119 | 1903.6384 | 1721.1225 | 0 | 8216.1628 | 7549.2387 | 6825.4375 | 0 | 0 | 0 | 8216.1628 | 7549.2387 | 6825.4375 | 0 | 0 | 0 | 0 | 0.058522 | 0.058522 | 0.058522 | 0 | 5000000 | scaled
534-346 | 12300.9538 | 0 | 12300.9538 | 0 | 0% | 100% | 0% | 998.4931 | 2082.4093 | 3.1572 | 794.0545 | 201.2815 | 6.5845 | 1656.0418 | 419.7831 | 534 |  | 979 | 534-346 | 12300.9538 | 11302.4606 | 10218.5445 | 0 | 0 | 0 | 12300.9538 | 11302.4606 | 10218.5445 | 0 | 38.8949 | 35.7377 | 32.3104 | 0 | 0 | 0 | 38.8949 | 35.7377 | 32.3104 | 0 | 2479.6911 | 2278.4096 | 2059.9081 | 0 | 0 | 0 | 2479.6911 | 2278.4096 | 2059.9081 | 0 | 9782.3678 | 8988.3133 | 8126.3259 | 0 | 0 | 0 | 9782.3678 | 8988.3133 | 8126.3259 | 0 | 0 | 0 | 0 | 0.058529 | 0.058529 | 0.058529 | 0 | 5000000 | scaled
535-1118 | 2983.4136 | 0 | 2983.4136 | 0 | 0% | 100% | 0% | 241.9145 | 504.4695 | 1.1603 | 191.0095 | 49.7447 | 2.4196 | 398.3162 | 103.7337 | 535 |  | 980 | 535-1118 | 2983.4136 | 2741.4991 | 2478.9441 | 0 | 0 | 0 | 2983.4136 | 2741.4991 | 2478.9441 | 0 | 14.3092 | 13.1489 | 11.8896 | 0 | 0 | 0 | 14.3092 | 13.1489 | 11.8896 | 0 | 613.4774 | 563.7326 | 509.7436 | 0 | 0 | 0 | 613.4774 | 563.7326 | 509.7436 | 0 | 2355.627 | 2164.6176 | 1957.3108 | 0 | 0 | 0 | 2355.627 | 2164.6176 | 1957.3108 | 0 | 0 | 0 | 0 | 0.058739 | 0.058739 | 0.058739 | 0 | 5000000 | scaled
535-1119 | 3978.9088 | 0 | 3978.9088 | 0 | 0% | 100% | 0% | 323.1249 | 673.2501 | 1.7162 | 254.9991 | 66.4096 | 3.5758 | 531.3059 | 138.3683 | 535 |  | 981 | 535-1119 | 3978.9088 | 3655.7839 | 3305.6588 | 0 | 0 | 0 | 3978.9088 | 3655.7839 | 3305.6588 | 0 | 21.1331 | 19.4169 | 17.5573 | 0 | 0 | 0 | 21.1331 | 19.4169 | 17.5573 | 0 | 817.757 | 751.3474 | 679.3886 | 0 | 0 | 0 | 817.757 | 751.3474 | 679.3886 | 0 | 3140.0188 | 2885.0196 | 2608.7128 | 0 | 0 | 0 | 3140.0188 | 2885.0196 | 2608.7128 | 0 | 0 | 0 | 0 | 0.058716 | 0.058716 | 0.058716 | 0 | 5000000 | scaled
535-1120AE | 1978.5973 | 0 | 1978.5973 | 0 | 0% | 100% | 0% | 160.4738 | 334.7322 | 0.10539 | 127.2331 | 33.1354 | 0.21984 | 265.3953 | 69.1171 | 535 |  | 982 | 535-1120AE | 1978.5973 | 1818.1235 | 1643.8651 | 0 | 0 | 0 | 1978.5973 | 1818.1235 | 1643.8651 | 0 | 1.2995 | 1.1941 | 1.0796 | 0 | 0 | 0 | 1.2995 | 1.1941 | 1.0796 | 0 | 408.5499 | 375.4146 | 339.4329 | 0 | 0 | 0 | 408.5499 | 375.4146 | 339.4329 | 0 | 1568.7479 | 1441.5148 | 1303.3526 | 0 | 0 | 0 | 1568.7479 | 1441.5148 | 1303.3526 | 0 | 0 | 0 | 0 | 0.058671 | 0.058671 | 0.058671 | 0 | 5000000 | scaled
536-363F | 990.4765 | 0 | 990.4765 | 0 | 0% | 100% | 0% | 80.3812 | 167.5202 | 0.052791 | 63.7309 | 16.5975 | 0.11002 | 132.8198 | 34.5903 | 536 |  | 983 | 536-363F | 990.4765 | 910.0954 | 822.9564 | 0 | 0 | 0 | 990.4765 | 910.0954 | 822.9564 | 0 | 0.6505 | 0.59771 | 0.54048 | 0 | 0 | 0 | 0.6505 | 0.59771 | 0.54048 | 0 | 204.5182 | 187.9207 | 169.9278 | 0 | 0 | 0 | 204.5182 | 187.9207 | 169.9278 | 0 | 785.3078 | 721.5769 | 652.488 | 0 | 0 | 0 | 785.3078 | 721.5769 | 652.488 | 0 | 0 | 0 | 0 | 0.058745 | 0.058745 | 0.058745 | 0 | 5000000 | scaled
536-377F | 495.4974 | 0 | 495.4974 | 0 | 0% | 100% | 0% | 40.1997 | 83.7825 | 0.026401 | 31.8727 | 8.3006 | 0.055025 | 66.4277 | 17.2998 | 536 |  | 984 | 536-377F | 495.4974 | 455.2977 | 411.7149 | 0 | 0 | 0 | 495.4974 | 455.2977 | 411.7149 | 0 | 0.32542 | 0.29902 | 0.2704 | 0 | 0 | 0 | 0.32542 | 0.29902 | 0.2704 | 0 | 102.3126 | 94.012 | 85.0128 | 0 | 0 | 0 | 102.3126 | 94.012 | 85.0128 | 0 | 392.8594 | 360.9867 | 326.4317 | 0 | 0 | 0 | 392.8594 | 360.9867 | 326.4317 | 0 | 0 | 0 | 0 | 0.05878 | 0.05878 | 0.05878 | 0 | 5000000 | scaled
536-378F | 495.358 | 0 | 495.358 | 0 | 0% | 100% | 0% | 40.2018 | 83.7167 | 0.026403 | 31.8743 | 8.3011 | 0.054981 | 66.3755 | 17.2862 | 536 |  | 985 | 536-378F | 495.358 | 455.1562 | 411.6413 | 0 | 0 | 0 | 495.358 | 455.1562 | 411.6413 | 0 | 0.32533 | 0.29893 | 0.27035 | 0 | 0 | 0 | 0.32533 | 0.29893 | 0.27035 | 0 | 102.2838 | 93.9828 | 84.9976 | 0 | 0 | 0 | 102.2838 | 93.9828 | 84.9976 | 0 | 392.7489 | 360.8745 | 326.3734 | 0 | 0 | 0 | 392.7489 | 360.8745 | 326.3734 | 0 | 0 | 0 | 0 | 0.058769 | 0.058769 | 0.058769 | 0 | 5000000 | scaled
536-379F | 495.3083 | 0 | 495.3083 | 0 | 0% | 100% | 0% | 40.185 | 83.7412 | 0.026392 | 31.861 | 8.2976 | 0.054997 | 66.3949 | 17.2913 | 536 |  | 986 | 536-379F | 495.3083 | 455.1233 | 411.5671 | 0 | 0 | 0 | 495.3083 | 455.1233 | 411.5671 | 0 | 0.3253 | 0.2989 | 0.2703 | 0 | 0 | 0 | 0.3253 | 0.2989 | 0.2703 | 0 | 102.2736 | 93.976 | 84.9823 | 0 | 0 | 0 | 102.2736 | 93.976 | 84.9823 | 0 | 392.7094 | 360.8484 | 326.3145 | 0 | 0 | 0 | 392.7094 | 360.8484 | 326.3145 | 0 | 0 | 0 | 0 | 0.058759 | 0.058759 | 0.058759 | 0 | 5000000 | scaled
540-241R | 833630.8112 | 564789.9456 | 268204.205 | 636.6605 | 67.75% | 32.17% | 0.07637% | 165141.5104 | 613474.2214 | 8453.2871 | 26759.4721 | 129928.7513 | 34069.361 | 61800.7491 | 517604.1114 | 540 |  | 987 | 540-241R | 833630.8112 | 668489.3007 | 220156.5897 | 564789.9456 | 425438.9425 | 4923.8204 | 268204.205 | 242413.6977 | 214596.1088 | 636.6605 | 34683.2994 | 26230.0124 | 613.9385 | 34320.0455 | 25901.6428 | 323.1952 | 362.7749 | 327.8905 | 290.2642 | 0.47907 | 539587.8527 | 409659.1014 | 21983.7413 | 517516.3044 | 389704.391 | 4312.2481 | 22013.7136 | 19896.8757 | 17613.6585 | 57.8347 | 259359.6591 | 232600.187 | 197558.91 | 12953.5958 | 9832.9087 | 288.3772 | 245827.7165 | 222188.9316 | 196692.1861 | 578.3468 | 0.0040788 | 0.0030986 | 7.84e-05 | 0.04296 | 0.04296 | 0.04296 | 0.0009026 | 5000000 | scaled
540-39AE | 765.902 | 0 | 765.902 | 0 | 0% | 100% | 0% | 73.4637 | 152.7454 | 0.048248 | 58.2463 | 15.1691 | 0.10032 | 121.1055 | 31.5396 | 540 |  | 988 | 540-39AE | 765.902 | 692.4383 | 613.1566 | 0 | 0 | 0 | 765.902 | 692.4383 | 613.1566 | 0 | 0.50301 | 0.45476 | 0.40269 | 0 | 0 | 0 | 0.50301 | 0.45476 | 0.40269 | 0 | 158.147 | 142.9779 | 126.6074 | 0 | 0 | 0 | 158.147 | 142.9779 | 126.6074 | 0 | 607.252 | 549.0057 | 486.1465 | 0 | 0 | 0 | 607.252 | 549.0057 | 486.1465 | 0 | 0 | 0 | 0 | 0.043745 | 0.043745 | 0.043745 | 0 | 5000000 | scaled
545-47F | 110979.2884 | 1509.1981 | 106814.1461 | 2655.9443 | 1.36% | 96.25% | 2.393% | 48384.64 | 101148.7903 | 56.8748 | 44110.6718 | 4217.0934 | 119.7563 | 92185.7618 | 8843.2722 | 545 |  | 989 | 545-47F | 110979.2884 | 62594.6484 | 9830.4981 | 1509.1981 | 661.41 | 15.2719 | 106814.1461 | 59277.2941 | 7159.282 | 2655.9443 | 129.8224 | 72.9476 | 10.0661 | 7.4575 | 4.1509 | 0 | 120.3664 | 66.7982 | 8.0676 | 1.9985 | 9717.1193 | 5500.0259 | 873.8471 | 37.9751 | 21.1393 | 0 | 9437.8764 | 5237.6188 | 632.5793 | 241.2678 | 101132.3467 | 57021.6749 | 8946.5849 | 1463.7655 | 636.1198 | 15.2719 | 97255.9033 | 53972.8771 | 6518.635 | 2412.6779 | 0.0047204 | 0.0020432 | 5.04e-05 | 0.010587 | 0.0060416 | 0.0010586 | 0.0037476 | 5000000 | scaled
545-50F | 135826.4027 | 1446.1693 | 131701.9147 | 2678.3187 | 1.065% | 96.96% | 1.972% | 59477.8887 | 124302.5853 | 64.8068 | 54017.823 | 5395.259 | 135.8593 | 112864.6745 | 11302.0515 | 545 |  | 990 | 545-50F | 135826.4027 | 76348.514 | 11523.8174 | 1446.1693 | 626.7125 | 15.8934 | 131701.9147 | 73043.4828 | 8829.6053 | 2678.3187 | 147.6141 | 82.8073 | 11.7548 | 0.32594 | 0.22189 | 0 | 145.2728 | 80.57 | 9.7394 | 2.0153 | 12357.3977 | 6962.1387 | 1055.3461 | 1.6657 | 1.1365 | 0 | 12112.4317 | 6717.7019 | 812.0458 | 243.3003 | 123321.391 | 69303.568 | 10456.7165 | 1444.1777 | 625.3541 | 15.8934 | 119444.2102 | 66245.2109 | 8007.8201 | 2433.003 | 0.0051944 | 0.0022492 | 5.72e-05 | 0.010576 | 0.0060322 | 0.0010576 | 0.003736 | 5000000 | scaled
545-874R | 149860.7637 | 8964.8518 | 138235.5138 | 2660.3981 | 5.982% | 92.24% | 1.775% | 66646.6315 | 137833.683 | 68.7182 | 61521.4699 | 5056.4433 | 143.5599 | 127123.4811 | 10566.642 | 545 |  | 991 | 545-874R | 149860.7637 | 83214.1322 | 12027.0807 | 8964.8518 | 4033.2124 | 102.3275 | 138235.5138 | 76520.5216 | 9264.3551 | 2660.3981 | 155.8629 | 87.1446 | 12.303 | 0.15607 | 0.059119 | 0 | 153.7049 | 85.0836 | 10.3011 | 2.0019 | 11567.2836 | 6510.8402 | 1000.6416 | 0.86137 | 0.33187 | 0 | 11324.7498 | 6268.836 | 758.9692 | 241.6724 | 138137.6172 | 76616.1473 | 11014.1361 | 8963.8343 | 4032.8214 | 102.3275 | 126757.0591 | 70166.602 | 8495.0848 | 2416.7239 | 0.006251 | 0.0027262 | 6.9e-05 | 0.010569 | 0.0060176 | 0.001057 | 0.0037636 | 5000000 | scaled
545-885R | 32725.6192 | 90.2427 | 32178.775 | 456.6015 | 0.2758% | 98.33% | 1.395% | 14454.6739 | 30115.8612 | 16.2306 | 13206.7027 | 1231.7406 | 33.8355 | 27514.251 | 2567.7747 | 545 |  | 992 | 545-885R | 32725.6192 | 18270.9453 | 2609.758 | 90.2427 | 39.0622 | 0.94279 | 32178.775 | 17775.2816 | 2152.2138 | 456.6015 | 36.6043 | 20.3737 | 2.7688 | 0 | 0 | 0 | 36.2607 | 20.0301 | 2.4252 | 0.34358 | 2793.3031 | 1561.5625 | 225.5283 | 0.00047 | 0 | 0 | 2751.8246 | 1520.0845 | 184.0504 | 41.478 | 29895.7119 | 16689.0091 | 2381.4609 | 90.2422 | 39.0622 | 0.94279 | 29390.6897 | 16235.167 | 1965.7382 | 414.7799 | 0.0009056 | 0.000392 | 9.8e-06 | 0.010661 | 0.0060588 | 0.0010662 | 0.0006458 | 5000000 | scaled
546-12 | 14414.2795 | 55.8621 | 13936.3243 | 422.0931 | 0.3875% | 96.68% | 2.928% | 6273.833 | 13059.699 | 10.8394 | 5600.0547 | 662.9389 | 22.582 | 11655.9996 | 1381.1174 | 546 |  | 993 | 546-12 | 14414.2795 | 8140.4465 | 1354.5805 | 55.8621 | 24.1967 | 0.62816 | 13936.3243 | 7694.1567 | 931.8593 | 422.0931 | 24.5177 | 13.6784 | 1.9358 | 0 | 0 | 0 | 24.2001 | 13.3607 | 1.6182 | 0.31761 | 1518.4272 | 855.4882 | 137.3098 | 0 | 0 | 0 | 1480.084 | 817.145 | 98.9666 | 38.3432 | 12871.3346 | 7271.2799 | 1215.335 | 55.8621 | 24.1967 | 0.62816 | 12432.0402 | 6863.651 | 831.2746 | 383.4322 | 0.0013062 | 0.0005658 | 1.46e-05 | 0.010662 | 0.0060564 | 0.0010662 | 0.000592 | 5000000 | scaled
546-14R | 227212.7305 | 3293.7817 | 221378.3357 | 2540.6131 | 1.45% | 97.43% | 1.118% | 101396.9793 | 211001.6818 | 105.0715 | 93553.9663 | 7737.9415 | 219.1072 | 194645.9331 | 16136.6415 | 546 |  | 994 | 546-14R | 227212.7305 | 125815.7512 | 16211.0487 | 3293.7817 | 1522.8376 | 39.2618 | 221378.3357 | 121752.3006 | 13631.1737 | 2540.6131 | 236.5654 | 131.4939 | 17.4581 | 0.13913 | 0.067396 | 0 | 234.5145 | 129.5148 | 15.5464 | 1.9117 | 17503.9379 | 9765.9963 | 1367.2964 | 0.7593 | 0.36437 | 0.00047 | 17272.3875 | 9534.8409 | 1136.5049 | 230.791 | 209472.2273 | 115918.261 | 14826.2941 | 3292.8833 | 1522.4058 | 39.2614 | 203871.4337 | 112087.9449 | 12479.1224 | 2307.9103 | 0.0065712 | 0.002952 | 7.54e-05 | 0.010495 | 0.0059654 | 0.0010494 | 0.0036134 | 5000000 | scaled
546-525R | 53673.9906 | 3999.1278 | 47842.5971 | 1832.2658 | 7.451% | 89.14% | 3.414% | 23551.8263 | 48592.4209 | 28.9112 | 21704.0953 | 1818.8199 | 60.1868 | 44745.7946 | 3786.4395 | 546 |  | 995 | 546-525R | 53673.9906 | 30122.1643 | 5081.5697 | 3999.1278 | 1890.6984 | 47.876 | 47842.5971 | 26399.2002 | 3201.428 | 1832.2658 | 65.8716 | 36.9605 | 5.6848 | 0.14189 | 0.073308 | 0 | 64.351 | 35.5084 | 4.3061 | 1.3787 | 4224.3739 | 2405.5541 | 437.9344 | 0.74186 | 0.38281 | 0 | 4057.1878 | 2238.727 | 271.4902 | 166.4443 | 49383.7451 | 27679.6498 | 4637.9505 | 3998.244 | 1890.2422 | 47.876 | 43721.0582 | 24124.9648 | 2925.6317 | 1664.4428 | 0.0056068 | 0.0024594 | 6.24e-05 | 0.010648 | 0.006045 | 0.0010648 | 0.0025874 | 5000000 | scaled
547-22R | 7854.4142 | 5386.8824 | 0 | 2467.5317 | 68.58% | 0% | 31.42% | 3004.5224 | 5331.5905 | 55.6628 | 2660.7628 | 288.0968 | 104.9407 | 4683.2662 | 543.3836 | 547 |  | 996 | 547-22R | 7854.4142 | 4849.8917 | 2522.8237 | 5386.8824 | 2382.36 | 55.2919 | 0 | 0 | 0 | 2467.5317 | 107.4524 | 51.7896 | 2.5117 | 105.5957 | 49.9329 | 0.65499 | 0 | 0 | 0 | 1.8567 | 770.9327 | 482.8358 | 227.5491 | 546.7804 | 258.6836 | 3.3968 | 0 | 0 | 0 | 224.1523 | 6976.0291 | 4315.2663 | 2292.7629 | 4734.5063 | 2073.7436 | 51.2402 | 0 | 0 | 0 | 2241.5227 | 0.007005 | 0.0030334 | 7.76e-05 | 0 | 0 | 0 | 0.0034832 | 5000000 | scaled
548-12F | 217.0274 | 40.947 | 0 | 176.0804 | 18.87% | 0% | 81.13% | 9.7603 | 40.7938 | 0.14135 | 10.7064 | -1.0874 | 3.1072 | 19.5641 | 18.1224 | 548 |  | 997 | 548-12F | 217.0274 | 207.2671 | 176.2336 | 40.947 | 31.1867 | 0.15324 | 0 | 0 | 0 | 176.0804 | 3.2397 | 3.0983 | 0.13249 | 3.1072 | 2.9658 | 0 | 0 | 0 | 0 | 0.13249 | 34.1177 | 35.2051 | 15.9953 | 18.1224 | 19.2099 | 0 | 0 | 0 | 0 | 15.9953 | 179.67 | 168.9636 | 160.1059 | 19.7174 | 9.011 | 0.15324 | 0 | 0 | 0 | 159.9526 | 0.0005056 | 0.0002192 | 5.6e-06 | 0 | 0 | 0 | 0.0002538 | 5000000 | scaled
548-14F | 907.0948 | 435.7563 | 0 | 471.3385 | 48.04% | 0% | 51.96% | 244.4293 | 430.6917 | 1.3097 | 236.3884 | 6.7312 | 3.0115 | 412.2022 | 15.4779 | 548 |  | 998 | 548-14F | 907.0948 | 662.6655 | 476.4031 | 435.7563 | 191.327 | 5.0646 | 0 | 0 | 0 | 471.3385 | 3.4115 | 2.1018 | 0.39999 | 3.0569 | 1.7472 | 0.045325 | 0 | 0 | 0 | 0.35467 | 58.5263 | 51.7951 | 43.0484 | 15.7096 | 8.9784 | 0.23164 | 0 | 0 | 0 | 42.8167 | 845.157 | 608.7685 | 432.9547 | 416.9898 | 180.6014 | 4.7876 | 0 | 0 | 0 | 428.1671 | 0.0013406 | 0.0005806 | 1.52e-05 | 0 | 0 | 0 | 0.0006468 | 5000000 | scaled
548-15F | 14761.9794 | 13467.6233 | 0 | 1294.3561 | 91.23% | 0% | 8.768% | 7620.4449 | 13464.0435 | 624.493 | 297.9841 | 6697.9678 | 1091.5709 | 530.0333 | 11842.4392 | 548 |  | 999 | 548-15F | 14761.9794 | 7141.5345 | 1297.9359 | 13467.6233 | 5847.1784 | 3.5798 | 0 | 0 | 0 | 1294.3561 | 1092.5449 | 468.0519 | 0.97396 | 1091.5709 | 467.0779 | 0 | 0 | 0 | 0 | 0.97396 | 11960.0194 | 5262.0516 | 117.5802 | 11842.4392 | 5144.4714 | 0 | 0 | 0 | 0 | 117.5802 | 1709.4151 | 1411.431 | 1179.3817 | 533.6131 | 235.629 | 3.5798 | 0 | 0 | 0 | 1175.8019 | 0.003594 | 0.0015562 | 3.96e-05 | 0 | 0 | 0 | 0.001851 | 5000000 | scaled
548-17F | 104211.8394 | 102230.5088 | 0 | 1981.3306 | 98.1% | 0% | 1.901% | 59755.6083 | 101033.5628 | 7093.7903 | 473.8786 | 52187.9395 | 12089.7572 | 823.2683 | 88120.5374 | 548 |  | 1000 | 548-17F | 104211.8394 | 44456.2311 | 3178.2766 | 102230.5088 | 42474.9005 | 1196.946 | 0 | 0 | 0 | 1981.3306 | 12238.6701 | 5144.8798 | 148.9129 | 12237.1792 | 5143.3889 | 147.422 | 0 | 0 | 0 | 1.4909 | 89341.2491 | 37153.3096 | 1220.7117 | 89161.2637 | 36973.3242 | 1040.7263 | 0 | 0 | 0 | 179.9854 | 2631.9203 | 2158.0417 | 1808.652 | 832.0659 | 358.1874 | 8.7977 | 0 | 0 | 0 | 1799.8543 | 0.008137 | 0.0035232 | 8.96e-05 | 0 | 0 | 0 | 0.0027974 | 5000000 | scaled
548-18F | 1167.6459 | 606.855 | 0 | 560.7908 | 51.97% | 0% | 48.03% | 343.1733 | 600.2618 | 0.50212 | 340.0892 | 2.5821 | 1.1532 | 593.1901 | 5.9185 | 548 |  | 1001 | 548-18F | 1167.6459 | 824.4725 | 567.3841 | 606.855 | 263.6817 | 6.5932 | 0 | 0 | 0 | 560.7908 | 1.5752 | 1.0731 | 0.42198 | 1.1532 | 0.6511 | 0 | 0 | 0 | 0 | 0.42198 | 56.8611 | 54.279 | 50.9426 | 5.9185 | 3.3364 | 0 | 0 | 0 | 0 | 50.9426 | 1109.2096 | 769.1204 | 516.0195 | 599.7833 | 259.6942 | 6.5932 | 0 | 0 | 0 | 509.4262 | 0.0019546 | 0.0008462 | 2.18e-05 | 0 | 0 | 0 | 0.000762 | 5000000 | scaled
549-33F | 3627.3624 | 3411.5511 | 0 | 215.8114 | 94.05% | 0% | 5.95% | 1884.5844 | 3410.189 | 256.116 | 2.1025 | 1626.3659 | 458.6623 | 3.6915 | 2947.8352 | 549 |  | 1002 | 549-33F | 3627.3624 | 1742.7781 | 217.1734 | 3411.5511 | 1526.9667 | 1.362 | 0 | 0 | 0 | 215.8114 | 459.0892 | 202.9732 | 0.4269 | 458.9268 | 202.8108 | 0.26451 | 0 | 0 | 0 | 0.16239 | 2968.5038 | 1342.1379 | 20.6687 | 2948.8994 | 1322.5335 | 1.0642 | 0 | 0 | 0 | 19.6045 | 199.7694 | 197.6669 | 196.0778 | 3.7249 | 1.6224 | 0.033314 | 0 | 0 | 0 | 196.0445 | 0.0004922 | 0.0002132 | 5.4e-06 | 0 | 0 | 0 | 0.0003006 | 5000000 | scaled
549-36F | 1209.4947 | 630.2183 | 0 | 579.2764 | 52.11% | 0% | 47.89% | 434.6089 | 626.8768 | 57.8863 | 25.6159 | 351.1067 | 83.654 | 44.2267 | 498.9961 | 549 |  | 1003 | 549-36F | 1209.4947 | 774.8859 | 582.6179 | 630.2183 | 195.6095 | 3.3415 | 0 | 0 | 0 | 579.2764 | 84.5597 | 26.6734 | 0.90569 | 84.1238 | 26.2375 | 0.4698 | 0 | 0 | 0 | 0.43589 | 554.0526 | 202.9459 | 55.0564 | 501.4307 | 150.324 | 2.4346 | 0 | 0 | 0 | 52.6219 | 570.8825 | 545.2665 | 526.6558 | 44.6638 | 19.0479 | 0.43715 | 0 | 0 | 0 | 526.2186 | 0.0016368 | 0.000709 | 1.78e-05 | 0 | 0 | 0 | 0.0008312 | 5000000 | scaled
55-479F | 1223.9196 | 448.3962 | 0 | 775.5234 | 36.64% | 0% | 63.36% | 257.8558 | 443.8203 | 3.747 | 234.8841 | 19.2247 | 5.569 | 409.6508 | 28.6005 | 55 |  | 1004 | 55-479F | 1223.9196 | 966.0638 | 780.0993 | 448.3962 | 190.5404 | 4.5759 | 0 | 0 | 0 | 775.5234 | 6.1526 | 2.4056 | 0.58356 | 5.569 | 1.8221 | 0 | 0 | 0 | 0 | 0.58356 | 99.0496 | 79.8249 | 70.4491 | 28.6005 | 9.3758 | 0 | 0 | 0 | 0 | 70.4491 | 1118.7174 | 883.8333 | 709.0667 | 414.2266 | 179.3425 | 4.5759 | 0 | 0 | 0 | 704.4908 | 0.0014278 | 0.0006182 | 1.58e-05 | 0 | 0 | 0 | 0.0011092 | 5000000 | scaled
55-483F | 9286.064 | 6609.8689 | 0 | 2676.195 | 71.18% | 0% | 28.82% | 3743.0511 | 6537.235 | 4.3252 | 3716.0966 | 22.6293 | 8.7697 | 6482.7079 | 45.7575 | 55 |  | 1005 | 55-483F | 9286.064 | 5543.0129 | 2748.8289 | 6609.8689 | 2866.8179 | 72.6339 | 0 | 0 | 0 | 2676.195 | 10.7835 | 6.4583 | 2.0138 | 8.7697 | 4.4446 | 0 | 0 | 0 | 0 | 2.0138 | 288.8648 | 266.2355 | 243.1074 | 45.7575 | 23.1281 | 0 | 0 | 0 | 0 | 243.1074 | 8986.4156 | 5270.3191 | 2503.7078 | 6555.3418 | 2839.2452 | 72.6339 | 0 | 0 | 0 | 2431.0739 | 0.005768 | 0.0024968 | 6.38e-05 | 0 | 0 | 0 | 0.003734 | 5000000 | scaled
55-484F | 440.1286 | 48.0748 | 0 | 392.0539 | 10.92% | 0% | 89.08% | 27.2509 | 47.5303 | 0 | 27.2509 | 0 | 0 | 47.5303 | 0 | 55 |  | 1006 | 55-484F | 440.1286 | 412.8777 | 392.5984 | 48.0748 | 20.8239 | 0.5445 | 0 | 0 | 0 | 392.0539 | 0.29501 | 0.29501 | 0.29501 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29501 | 35.6144 | 35.6144 | 35.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6144 | 404.2192 | 376.9683 | 356.6889 | 48.0748 | 20.8239 | 0.5445 | 0 | 0 | 0 | 356.1444 | 0.001033 | 0.0004472 | 1.16e-05 | 0 | 0 | 0 | 0.0005556 | 5000000 | scaled
550-665R | 7297.2642 | 4519.5553 | 0 | 2777.7089 | 61.93% | 0% | 38.07% | 2432.6669 | 4438.1509 | 175.1246 | 1447.5384 | 810.0038 | 333.3073 | 2550.5969 | 1554.2467 | 550 |  | 1007 | 550-665R | 7297.2642 | 4864.5973 | 2859.1133 | 4519.5553 | 2086.8884 | 81.4044 | 0 | 0 | 0 | 2777.7089 | 344.1842 | 169.0596 | 10.8769 | 342.0941 | 166.9695 | 8.7868 | 0 | 0 | 0 | 2.0901 | 1850.4555 | 1040.4517 | 296.2088 | 1598.1266 | 788.1227 | 43.8799 | 0 | 0 | 0 | 252.329 | 5102.6244 | 3655.086 | 2552.0276 | 2579.3346 | 1131.7962 | 28.7378 | 0 | 0 | 0 | 2523.2898 | 0.009563 | 0.0041394 | 0.0001048 | 0 | 0 | 0 | 0.0039268 | 5000000 | scaled
551-19 | 15234.9718 | 10417.9789 | 0 | 4816.9929 | 68.38% | 0% | 31.62% | 5898.2932 | 10308.0393 | 34.3348 | 5687.9923 | 175.9661 | 61.3046 | 9932.5835 | 314.1512 | 551 |  | 1008 | 551-19 | 15234.9718 | 9336.6785 | 4926.9325 | 10417.9789 | 4519.6856 | 109.9396 | 0 | 0 | 0 | 4816.9929 | 65.1314 | 30.7966 | 3.8268 | 61.5068 | 27.172 | 0.20219 | 0 | 0 | 0 | 3.6246 | 752.7726 | 576.8065 | 438.6214 | 315.1937 | 139.2276 | 1.0425 | 0 | 0 | 0 | 437.5789 | 14417.0677 | 8729.0754 | 4484.4842 | 10041.2784 | 4353.286 | 108.6949 | 0 | 0 | 0 | 4375.7893 | 0.012296 | 0.005429 | 0.0001372 | 0 | 0 | 0 | 0.0066946 | 5000000 | scaled
553-27R | 504265.159 | 493342.0025 | 0 | 10923.1565 | 97.83% | 0% | 2.166% | 274706.5151 | 488900.3104 | 33401.5613 | 7014.7416 | 234290.2122 | 59387.7064 | 12321.5945 | 417191.0095 | 553 |  | 1009 | 553-27R | 504265.159 | 229558.6439 | 15364.8486 | 493342.0025 | 218635.4874 | 4441.6921 | 0 | 0 | 0 | 10923.1565 | 59946.6142 | 26545.0529 | 558.9078 | 59938.3949 | 26536.8336 | 550.6884 | 0 | 0 | 0 | 8.2193 | 421936.9009 | 187646.6887 | 4745.8914 | 420944.6339 | 186654.4217 | 3753.6244 | 0 | 0 | 0 | 992.267 | 22381.6439 | 15366.9024 | 10060.0495 | 12458.9738 | 5444.2322 | 137.3793 | 0 | 0 | 0 | 9922.6702 | 0.039299 | 0.017341 | 0.0004364 | 0 | 0 | 0 | 0.015423 | 5000000 | scaled
555-21F | 453.3723 | 379.8697 | 0 | 73.5026 | 83.79% | 0% | 16.21% | 56.7535 | 373.2071 | 3.1914 | 38.5085 | 15.0535 | 30.4031 | 168.6822 | 174.1219 | 555 |  | 1010 | 555-21F | 453.3723 | 396.6189 | 80.1652 | 379.8697 | 323.1163 | 6.6626 | 0 | 0 | 0 | 73.5026 | 31.0922 | 27.9008 | 0.6891 | 31.0369 | 27.8454 | 0.63379 | 0 | 0 | 0 | 0.055308 | 184.1489 | 169.0954 | 10.0271 | 177.4719 | 162.4184 | 3.3501 | 0 | 0 | 0 | 6.677 | 238.1312 | 199.6227 | 69.449 | 171.3609 | 132.8524 | 2.6788 | 0 | 0 | 0 | 66.7703 | 0.0001336 | 0.0001014 | 2.6e-06 | 0 | 0 | 0 | 0.0001058 | 5000000 | scaled
555-24F | 4406.0671 | 2344.3429 | 0 | 2061.7243 | 53.21% | 0% | 46.79% | 1211.9738 | 2326.5959 | 101.0912 | 564.8258 | 546.0567 | 181.0696 | 1166.0216 | 979.5047 | 555 |  | 1011 | 555-24F | 4406.0671 | 3194.0933 | 2079.4712 | 2344.3429 | 1132.3691 | 17.747 | 0 | 0 | 0 | 2061.7243 | 183.3129 | 82.2217 | 2.2433 | 181.7615 | 80.6703 | 0.69189 | 0 | 0 | 0 | 1.5514 | 1170.3862 | 624.3294 | 190.8815 | 983.0977 | 437.041 | 3.593 | 0 | 0 | 0 | 187.2884 | 3052.3681 | 2487.5422 | 1886.3465 | 1179.4836 | 614.6578 | 13.4621 | 0 | 0 | 0 | 1872.8844 | 0.0051842 | 0.0025112 | 6.38e-05 | 0 | 0 | 0 | 0.0029768 | 5000000 | scaled
555-2F | 847.6538 | 327.4282 | 0 | 520.2256 | 38.63% | 0% | 61.37% | 148.1895 | 327.2664 | 19.7662 | 6.2223 | 122.2011 | 41.9975 | 13.9504 | 271.3185 | 555 |  | 1012 | 555-2F | 847.6538 | 699.4643 | 520.3874 | 327.4282 | 179.2386 | 0.16176 | 0 | 0 | 0 | 520.2256 | 42.389 | 22.6228 | 0.39145 | 41.9975 | 22.2313 | 0 | 0 | 0 | 0 | 0.39145 | 318.5762 | 196.3751 | 47.2577 | 271.3185 | 149.1174 | 0 | 0 | 0 | 0 | 47.2577 | 486.6887 | 480.4664 | 472.7383 | 14.1122 | 7.8899 | 0.16176 | 0 | 0 | 0 | 472.5765 | 0.0008442 | 0.0003878 | 9.4e-06 | 0 | 0 | 0 | 0.000747 | 5000000 | scaled
558-301R | 286655.1288 | 284793.9235 | 0 | 1861.2052 | 99.35% | 0% | 0.6493% | 139757.326 | 281564.8086 | 19579.7885 | 95.671 | 120081.8664 | 39397.9657 | 260.4921 | 241906.3508 | 558 |  | 1013 | 558-301R | 286655.1288 | 146897.8028 | 5090.3201 | 284793.9235 | 145036.5976 | 3229.1149 | 0 | 0 | 0 | 1861.2052 | 39847.7299 | 20267.9414 | 449.7642 | 39846.3295 | 20266.5409 | 448.3637 | 0 | 0 | 0 | 1.4005 | 244851.8861 | 124770.0197 | 2945.5353 | 244682.8129 | 124600.9465 | 2776.4621 | 0 | 0 | 0 | 169.0732 | 1955.5127 | 1859.8417 | 1695.0206 | 264.7811 | 169.1101 | 4.289 | 0 | 0 | 0 | 1690.7316 | 0.0077256 | 0.004014 | 0.000102 | 0 | 0 | 0 | 0.0026438 | 5000000 | scaled
56-669F | 107607.9926 | 107.4939 | 106992.8767 | 507.622 | 0.09989% | 99.43% | 0.4717% | 48089.2241 | 99935.9165 | 56.0982 | 43795.8927 | 4237.2332 | 116.6301 | 91011.8103 | 8807.4761 | 56 |  | 1014 | 56-669F | 107607.9926 | 59518.7685 | 7672.0761 | 107.4939 | 46.5958 | 1.1967 | 106992.8767 | 58964.5507 | 7163.2574 | 507.622 | 125.3789 | 69.2807 | 8.7488 | 0.026801 | 0.026801 | 0 | 124.9702 | 68.872 | 8.3669 | 0.38197 | 9485.5573 | 5248.3241 | 678.0813 | 0.14474 | 0.14474 | 0 | 9439.2999 | 5202.0667 | 631.9686 | 46.1127 | 97997.0563 | 54201.1636 | 6985.246 | 107.3223 | 46.4243 | 1.1967 | 97428.6067 | 53693.6121 | 6522.922 | 461.1273 | 0.0010118 | 0.000438 | 1.14e-05 | 0.010606 | 0.0060132 | 0.0010606 | 0.0006968 | 5000000 | scaled
56-670F | 49225.0548 | 291.5931 | 47946.324 | 987.1376 | 0.5924% | 97.4% | 2.005% | 21645.6712 | 45028.9368 | 24.2075 | 19169.1962 | 2452.2675 | 50.5163 | 39870.2789 | 5108.1416 | 56 |  | 1015 | 56-670F | 49225.0548 | 27579.3835 | 4196.118 | 291.5931 | 126.6318 | 3.1589 | 47946.324 | 26465.6141 | 3205.8214 | 987.1376 | 54.8693 | 30.6618 | 4.353 | 0.13164 | 0.11469 | 0 | 53.9949 | 29.8043 | 3.6102 | 0.74279 | 5563.7811 | 3111.5136 | 455.6395 | 0.69634 | 0.60404 | 0 | 5473.4125 | 3021.2373 | 365.9672 | 89.6723 | 43606.4043 | 24437.2081 | 3736.1255 | 290.7651 | 125.9131 | 3.1589 | 42418.9166 | 23414.5725 | 2836.244 | 896.7226 | 0.002107 | 0.0009124 | 2.28e-05 | 0.010678 | 0.0060642 | 0.0010678 | 0.0014234 | 5000000 | scaled
560-46F | 21179.1014 | 20872.8669 | 0 | 306.2344 | 98.55% | 0% | 1.446% | 9478.2688 | 20845.0571 | 1524.916 | 1883.2413 | 6070.1115 | 3221.9354 | 4938.4025 | 12684.7192 | 560 |  | 1016 | 560-46F | 21179.1014 | 11700.8326 | 334.0443 | 20872.8669 | 11394.5981 | 27.8098 | 0 | 0 | 0 | 306.2344 | 3222.1658 | 1697.2498 | 0.23043 | 3221.9354 | 1697.0194 | 0 | 0 | 0 | 0 | 0.23043 | 12712.5377 | 6642.4262 | 27.8185 | 12684.7192 | 6614.6077 | 0 | 0 | 0 | 0 | 27.8185 | 5244.3978 | 3361.1565 | 305.9953 | 4966.2124 | 3082.9711 | 27.8098 | 0 | 0 | 0 | 278.1855 | 0.0011628 | 0.0006206 | 1.58e-05 | 0 | 0 | 0 | 0.0004426 | 5000000 | scaled
57-1291F | 33008.6809 | 234.5849 | 31331.6035 | 1442.4926 | 0.7107% | 94.92% | 4.37% | 14206.4688 | 29469.5033 | 17.4505 | 12842.7859 | 1346.2324 | 36.2499 | 26636.4875 | 2796.7658 | 57 |  | 1017 | 57-1291F | 33008.6809 | 18802.2121 | 3539.1776 | 234.5849 | 101.599 | 2.5937 | 31331.6035 | 17258.1206 | 2094.0914 | 1442.4926 | 39.9315 | 22.4809 | 3.6815 | 0.003153 | 0 | 0 | 38.8429 | 21.3955 | 2.5961 | 1.0854 | 3128.1157 | 1781.8833 | 331.3498 | 0.016376 | 0 | 0 | 2997.0623 | 1650.8463 | 200.3128 | 131.037 | 29840.6338 | 16997.8479 | 3204.1462 | 234.5654 | 101.599 | 2.5937 | 28295.6983 | 15585.8788 | 1891.1824 | 1310.3701 | 0.0033092 | 0.0014334 | 3.7e-05 | 0.010684 | 0.0060552 | 0.0010684 | 0.0020564 | 5000000 | scaled
57-1292F | 21043.8713 | 56.3144 | 20448.601 | 538.9559 | 0.2676% | 97.17% | 2.561% | 9229.1845 | 19137.4417 | 10.4952 | 8408.0283 | 810.661 | 21.7836 | 17433.7202 | 1681.938 | 57 |  | 1018 | 57-1292F | 21043.8713 | 11814.6868 | 1906.4296 | 56.3144 | 24.426 | 0.64037 | 20448.601 | 11251.3049 | 1366.8333 | 538.9559 | 23.7482 | 13.253 | 1.9646 | 0.018918 | 0.014189 | 0 | 23.3237 | 12.8332 | 1.559 | 0.40555 | 1851.3677 | 1040.7067 | 169.4298 | 0.099478 | 0.074397 | 0 | 1802.3091 | 991.6732 | 120.4706 | 48.9591 | 19168.7554 | 10760.7271 | 1735.0352 | 56.196 | 24.3374 | 0.64037 | 18622.9682 | 10246.7985 | 1244.8037 | 489.5912 | 0.0011736 | 0.0005082 | 1.32e-05 | 0.010699 | 0.0060576 | 0.0010698 | 0.0007518 | 5000000 | scaled
57-1295F | 5778.4916 | 1081.6408 | 3717.4291 | 979.4217 | 18.72% | 64.33% | 16.95% | 2286.3683 | 4538.7553 | 1.795 | 2138.2639 | 146.3095 | 3.7219 | 4231.6527 | 303.3806 | 57 |  | 1019 | 57-1295F | 5778.4916 | 3492.1233 | 1239.7364 | 1081.6408 | 468.258 | 11.912 | 3717.4291 | 2044.4437 | 248.4027 | 979.4217 | 4.7254 | 2.9305 | 1.0035 | 0 | 0 | 0 | 3.9885 | 2.1935 | 0.26651 | 0.73698 | 414.0758 | 267.7663 | 110.6952 | 0 | 0 | 0 | 325.1045 | 178.795 | 21.7238 | 88.9713 | 5359.6904 | 3221.4265 | 1128.0377 | 1081.6408 | 468.258 | 11.912 | 3388.3362 | 1863.4551 | 226.4123 | 889.7134 | 0.0017552 | 0.0007598 | 1.94e-05 | 0.010706 | 0.0060592 | 0.0010706 | 0.001355 | 5000000 | scaled
57-1296F | 54256.1032 | 44708.2228 | 6434.7401 | 3113.1403 | 82.4% | 11.86% | 5.738% | 24080.323 | 50467.6527 | 2150.0235 | 3059.4205 | 18870.879 | 4473.1748 | 6282.5091 | 39711.9689 | 57 |  | 1020 | 57-1296F | 54256.1032 | 30175.7802 | 3788.4505 | 44708.2228 | 23526.9425 | 245.398 | 6434.7401 | 3535.6974 | 429.9122 | 3113.1403 | 4503.2824 | 2353.259 | 30.1077 | 4493.4057 | 2346.7766 | 27.2618 | 7.5342 | 4.1398 | 0.50337 | 2.3425 | 40239.293 | 21368.414 | 527.3242 | 39414.6221 | 20787.8722 | 208.3214 | 541.8711 | 297.742 | 36.203 | 282.7998 | 9513.5278 | 6454.1073 | 3231.0187 | 800.195 | 392.2937 | 9.8149 | 5885.3348 | 3233.8156 | 393.2058 | 2827.998 | 0.011173 | 0.0054922 | 0.0002388 | 0.010707 | 0.0060546 | 0.0010706 | 0.0044174 | 5000000 | scaled
57-463AE | 80982.9831 | 2569.1772 | 74262.7224 | 4151.0836 | 3.172% | 91.7% | 5.126% | 34883.254 | 71835.2819 | 48.1045 | 32029.6119 | 2805.5376 | 100.3609 | 65918.1808 | 5816.7402 | 57 |  | 1021 | 57-463AE | 80982.9831 | 46099.7291 | 9147.7012 | 2569.1772 | 1117.9839 | 27.8809 | 74262.7224 | 40830.6616 | 4968.7367 | 4151.0836 | 109.6636 | 61.559 | 9.3026 | 14.2327 | 7.6837 | 0.0030337 | 92.3073 | 50.7518 | 6.1761 | 3.1236 | 6608.2018 | 3802.6642 | 791.4616 | 38.0082 | 20.5222 | 0.008799 | 6193.1064 | 3405.0547 | 414.3656 | 377.0873 | 74265.1177 | 42235.5058 | 8346.9369 | 2516.9363 | 1089.778 | 27.8691 | 67977.3087 | 37374.8551 | 4548.1951 | 3770.8727 | 0.0097828 | 0.0042358 | 0.0001076 | 0.010628 | 0.0060126 | 0.0010628 | 0.0058278 | 5000000 | scaled
57-736 | 116892.4029 | 572.338 | 114985.2145 | 1334.8504 | 0.4896% | 98.37% | 1.142% | 52108.671 | 107859.0307 | 56.6946 | 47386.4476 | 4665.5287 | 117.4451 | 98075.0806 | 9666.5051 | 57 |  | 1022 | 57-736 | 116892.4029 | 64783.7319 | 9033.3721 | 572.338 | 247.9192 | 6.3659 | 114985.2145 | 63200.9623 | 7692.1558 | 1334.8504 | 126.8617 | 70.1671 | 9.4166 | 0.10878 | 0.045719 | 0 | 125.7485 | 69.1169 | 8.4122 | 1.0044 | 10480.7433 | 5815.2146 | 814.2382 | 0.56845 | 0.23717 | 0 | 10358.9161 | 5693.7187 | 692.9795 | 121.2587 | 106284.7979 | 58898.3502 | 8209.7173 | 571.6607 | 247.6363 | 6.3659 | 104500.5499 | 57438.1266 | 6990.7641 | 1212.5873 | 0.0026816 | 0.0011618 | 2.92e-05 | 0.010597 | 0.0059938 | 0.0010598 | 0.0018864 | 5000000 | scaled
570-489F | 36.0461 | 2.3616 | 0 | 33.6845 | 6.552% | 0% | 93.45% | 1.3396 | 2.3372 | 0 | 1.3396 | 0 | 0 | 2.3372 | 0 | 570 |  | 1023 | 570-489F | 36.0461 | 34.7065 | 33.709 | 2.3616 | 1.022 | 0.02443 | 0 | 0 | 0 | 33.6845 | 0.025347 | 0.025347 | 0.025347 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025347 | 3.0599 | 3.0599 | 3.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0599 | 32.9608 | 31.6213 | 30.6237 | 2.3616 | 1.022 | 0.02443 | 0 | 0 | 0 | 30.5993 | 0.000116 | 5.02e-05 | 1.2e-06 | 0 | 0 | 0 | 4.56e-05 | 5000000 | scaled
570-490F | 15986.9058 | 918.4463 | 14636.9018 | 431.5577 | 5.745% | 91.56% | 2.699% | 7346.4525 | 14571.3117 | 88.3137 | 5994.0473 | 1264.0915 | 100.7259 | 12587.132 | 1883.4538 | 570 |  | 1024 | 570-490F | 15986.9058 | 8640.4533 | 1415.594 | 918.4463 | 56.0035 | 1.4 | 14636.9018 | 8152.8921 | 982.6362 | 431.5577 | 102.4407 | 14.127 | 1.7147 | 83.3719 | 3.3617 | 0.13164 | 18.744 | 10.4406 | 1.2584 | 0.32473 | 2005.7084 | 741.617 | 122.2546 | 739.4396 | 18.9268 | 0.67355 | 1227.0658 | 683.4872 | 82.378 | 39.203 | 13878.7567 | 7884.7093 | 1291.6247 | 95.6347 | 33.7151 | 0.59484 | 13391.092 | 7458.9643 | 898.9998 | 392.03 | 0.001404 | 0.0006078 | 1.52e-05 | 0.0074438 | 0.004262 | 0.0007444 | 0.0006252 | 5000000 | scaled
570-491F | 500.5521 | 38.5149 | 0 | 462.0372 | 7.694% | 0% | 92.31% | 21.7931 | 38.1004 | 0.094985 | 21.2137 | 0.48444 | 0.17736 | 37.019 | 0.90404 | 570 |  | 1025 | 570-491F | 500.5521 | 478.759 | 462.4517 | 38.5149 | 16.7218 | 0.41457 | 0 | 0 | 0 | 462.0372 | 0.52503 | 0.43004 | 0.34767 | 0.17736 | 0.082373 | 0 | 0 | 0 | 0 | 0.34767 | 42.8758 | 42.3914 | 41.9718 | 0.90404 | 0.4196 | 0 | 0 | 0 | 0 | 41.9718 | 457.1512 | 435.9376 | 420.1323 | 37.4335 | 16.2199 | 0.41457 | 0 | 0 | 0 | 419.7177 | 0.0012562 | 0.0005442 | 1.4e-05 | 0 | 0 | 0 | 0.0006518 | 5000000 | scaled
571-33 | 41772.9836 | 7025.3258 | 30998.4669 | 3749.1909 | 16.82% | 74.21% | 8.975% | 17909.0962 | 35875.6652 | 21.1114 | 16687.2378 | 1200.7471 | 42.8689 | 33343.8191 | 2488.9771 | 571 |  | 1026 | 571-33 | 41772.9836 | 23863.8873 | 5897.3184 | 7025.3258 | 3043.4307 | 76.8759 | 30998.4669 | 17071.2658 | 2071.2516 | 3749.1909 | 48.0854 | 26.974 | 5.2164 | 9.4166 | 4.4111 | 0 | 35.8476 | 19.7418 | 2.3953 | 2.8211 | 3004.294 | 1803.547 | 515.3169 | 48.579 | 22.7779 | 0 | 2615.136 | 1440.19 | 174.7378 | 340.5791 | 38720.6042 | 22033.3663 | 5376.7851 | 6967.3302 | 3016.2416 | 76.8759 | 28347.4833 | 15611.334 | 1894.1185 | 3405.7907 | 0.0087296 | 0.0037964 | 9.68e-05 | 0.01067 | 0.0060462 | 0.001067 | 0.005318 | 5000000 | scaled
571-49F | 14893.7028 | 11287.3044 | 0 | 3606.3984 | 75.79% | 0% | 24.21% | 6387.6409 | 11169.4667 | 40.877 | 6191.2732 | 155.4907 | 75.661 | 10805.9897 | 287.816 | 571 |  | 1027 | 571-49F | 14893.7028 | 8506.0619 | 3724.2361 | 11287.3044 | 4899.6635 | 117.8377 | 0 | 0 | 0 | 3606.3984 | 78.3747 | 37.4976 | 2.7137 | 75.661 | 34.7839 | 0 | 0 | 0 | 0 | 2.7137 | 615.4237 | 459.933 | 327.6077 | 287.816 | 132.3253 | 0 | 0 | 0 | 0 | 327.6077 | 14199.9045 | 8008.6313 | 3393.9147 | 10923.8275 | 4732.5543 | 117.8377 | 0 | 0 | 0 | 3276.077 | 0.008028 | 0.003477 | 8.76e-05 | 0 | 0 | 0 | 0.0050594 | 5000000 | scaled
572-493F | 123.3645 | 2.5607 | 0 | 120.8038 | 2.076% | 0% | 97.92% | 1.4543 | 2.5308 | 0 | 1.4543 | 0 | 0 | 2.5308 | 0 | 572 |  | 1028 | 572-493F | 123.3645 | 121.9102 | 120.8338 | 2.5607 | 1.1064 | 0.029983 | 0 | 0 | 0 | 120.8038 | 0.090901 | 0.090901 | 0.090901 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090901 | 10.9739 | 10.9739 | 10.9739 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9739 | 112.2997 | 110.8454 | 109.769 | 2.5607 | 1.1064 | 0.029983 | 0 | 0 | 0 | 109.739 | 0.000352 | 0.0001522 | 3.8e-06 | 0 | 0 | 0 | 0.00019 | 5000000 | scaled
576-201F | 1160460.4644 | 0 | 1160460.4644 | 0 | 0% | 100% | 0% | 41989.9504 | 87609.4085 | 54.2074 | 38487.5446 | 3448.1983 | 113.1003 | 80301.8578 | 7194.4504 | 576 |  | 1029 | 576-201F | 1160460.4644 | 1118470.5141 | 1072851.0559 | 0 | 0 | 0 | 1160460.4644 | 1118470.5141 | 1072851.0559 | 0 | 1498.1093 | 1443.9019 | 1385.009 | 0 | 0 | 0 | 1498.1093 | 1443.9019 | 1385.009 | 0 | 95296.5597 | 91848.3614 | 88102.1093 | 0 | 0 | 0 | 95296.5597 | 91848.3614 | 88102.1093 | 0 | 1063665.7954 | 1025178.2508 | 983363.9376 | 0 | 0 | 0 | 1063665.7954 | 1025178.2508 | 983363.9376 | 0 | 0 | 0 | 0 | 0.1419 | 0.1419 | 0.1419 | 0 | 5000000 | scaled
578-227AE | 226195.4158 | 7248.9577 | 213373.7946 | 5572.6635 | 3.205% | 94.33% | 2.464% | 100424.8774 | 207248.7828 | 209.9929 | 91861.2494 | 8353.635 | 439.3887 | 189469.6741 | 17339.72 | 578 |  | 1030 | 578-227AE | 226195.4158 | 125770.5383 | 18946.633 | 7248.9577 | 3323.9485 | 125.4496 | 213373.7946 | 116873.9264 | 13248.52 | 5572.6635 | 460.5794 | 250.5864 | 21.1907 | 228.8772 | 121.3234 | 1.943 | 227.5089 | 125.0698 | 15.0545 | 4.1932 | 19019.8854 | 10666.2503 | 1680.1654 | 747.2275 | 397.09 | 6.3193 | 17766.4333 | 9762.9358 | 1167.6215 | 506.2246 | 206714.951 | 114853.7016 | 17245.277 | 6272.853 | 2805.5351 | 117.1873 | 195379.8523 | 106985.9208 | 12065.844 | 5062.2456 | 0.013935 | 0.0060484 | 0.0001798 | 0.010509 | 0.0059486 | 0.0010508 | 0.0078216 | 5000000 | scaled
578-242F | 101249.3334 | 1131.6861 | 98172.2468 | 1945.4004 | 1.118% | 96.96% | 1.921% | 44773.3829 | 92715.2863 | 83.5308 | 40131.2428 | 4558.6093 | 160.4738 | 83156.1976 | 9398.6149 | 578 |  | 1031 | 578-242F | 101249.3334 | 56475.9504 | 8534.047 | 1131.6861 | 471.8579 | 20.4052 | 98172.2468 | 54058.6921 | 6568.2414 | 1945.4004 | 172.4744 | 88.9436 | 12.0005 | 36.4598 | 13.3892 | 1.5345 | 134.5507 | 74.0906 | 9.0022 | 1.4639 | 10244.4592 | 5685.8499 | 845.8443 | 188.6085 | 69.1714 | 8.1569 | 9879.1291 | 5439.957 | 660.9659 | 176.7215 | 90832.3998 | 50701.157 | 7676.2022 | 906.6178 | 389.2973 | 10.7137 | 88158.5669 | 48544.6446 | 5898.2734 | 1767.2151 | 0.0046836 | 0.0020286 | 5.18e-05 | 0.010617 | 0.0060154 | 0.0010616 | 0.0026888 | 5000000 | scaled
579-32AE | 11299.8128 | 0 | 11299.8128 | 0 | 0% | 100% | 0% | 1801.4667 | 3764.275 | 2.1929 | 1584.5532 | 214.7206 | 4.5822 | 3311.0209 | 448.6718 | 579 |  | 1032 | 579-32AE | 11299.8128 | 9498.3461 | 7535.5378 | 0 | 0 | 0 | 11299.8128 | 9498.3461 | 7535.5378 | 0 | 13.7552 | 11.5623 | 9.173 | 0 | 0 | 0 | 13.7552 | 11.5623 | 9.173 | 0 | 1346.8484 | 1132.1278 | 898.1765 | 0 | 0 | 0 | 1346.8484 | 1132.1278 | 898.1765 | 0 | 9939.2092 | 8354.656 | 6628.1883 | 0 | 0 | 0 | 9939.2092 | 8354.656 | 6628.1883 | 0 | 0 | 0 | 0 | 0.014554 | 0.014554 | 0.014554 | 0 | 5000000 | scaled
579-350F | 142767.3362 | 3184.3886 | 138850.1196 | 732.828 | 2.23% | 97.26% | 0.5133% | 63675.9825 | 132742.8888 | 114.1859 | 57944.2791 | 5617.5176 | 226.3098 | 120813.1187 | 11703.4603 | 579 |  | 1033 | 579-350F | 142767.3362 | 79091.3536 | 10024.4474 | 3184.3886 | 1352.5242 | 29.0262 | 138850.1196 | 77006.0015 | 9262.5932 | 732.828 | 240.4362 | 126.2503 | 14.1264 | 36.3899 | 12.841 | 0 | 203.4949 | 112.8579 | 13.575 | 0.55143 | 12593.0954 | 6975.5779 | 889.6351 | 188.4454 | 66.3328 | 0 | 12338.0794 | 6842.6744 | 823.0645 | 66.5706 | 129933.8045 | 71989.5254 | 9120.6858 | 2959.5533 | 1273.3503 | 29.0262 | 126308.5452 | 70050.4692 | 8425.9537 | 665.706 | 0.0013832 | 0.0005984 | 1.48e-05 | 0.014389 | 0.0082086 | 0.0014388 | 0.0010216 | 5000000 | scaled
58-110F | 93515.1008 | 10852.8184 | 78368.0467 | 4294.2357 | 11.61% | 83.8% | 4.592% | 41222.8478 | 83918.2508 | 590.833 | 34991.9209 | 5640.094 | 1020.4806 | 72204.2096 | 10693.5606 | 58 |  | 1034 | 58-110F | 93515.1008 | 52292.253 | 9596.85 | 10852.8184 | 4583.576 | 75.6274 | 78368.0467 | 43414.4413 | 5226.9869 | 4294.2357 | 1035.7229 | 444.8899 | 15.2423 | 935.3717 | 387.856 | 5.5333 | 97.1199 | 53.8026 | 6.4777 | 3.2313 | 11536.8449 | 5896.7509 | 843.2843 | 4721.1658 | 1947.0034 | 24.6196 | 6425.5877 | 3559.6562 | 428.5734 | 390.0913 | 80942.533 | 45950.6121 | 8738.3234 | 5196.2809 | 2248.7166 | 45.4746 | 71845.339 | 39800.9825 | 4791.9357 | 3900.9131 | 0.012614 | 0.0054622 | 0.000139 | 0.014498 | 0.0082624 | 0.0014498 | 0.0059916 | 5000000 | scaled
58-522 | 27740.6174 | 3193.1069 | 23928.413 | 619.0975 | 11.51% | 86.26% | 2.232% | 12556.0056 | 25492.3264 | 45.9818 | 11421.278 | 1088.7458 | 91.1715 | 23161.4867 | 2239.6682 | 58 |  | 1035 | 58-522 | 27740.6174 | 15184.6118 | 2248.291 | 3193.1069 | 1407.1428 | 31.018 | 23928.413 | 13158.3715 | 1598.1755 | 619.0975 | 93.8392 | 47.8574 | 2.6677 | 60.4071 | 29.2632 | 0 | 32.9663 | 18.1283 | 2.2018 | 0.46585 | 2437.6692 | 1348.9234 | 198.001 | 258.9255 | 125.5068 | 0 | 2122.5044 | 1167.1774 | 141.7618 | 56.2392 | 25209.109 | 13787.831 | 2047.6223 | 2873.7743 | 1252.3728 | 31.018 | 21772.9423 | 11973.0658 | 1454.2119 | 562.3924 | 0.0014036 | 0.0006542 | 1.72e-05 | 0.010714 | 0.006063 | 0.0010714 | 0.0008652 | 5000000 | scaled
58-729F | 155.2101 | 0 | 155.2101 | 0 | 0% | 100% | 0% | 24.6623 | 51.7027 | 0.31995 | 19.3127 | 5.0296 | 0.67075 | 40.4877 | 10.5442 | 58 |  | 1036 | 58-729F | 155.2101 | 130.5478 | 103.5074 | 0 | 0 | 0 | 155.2101 | 130.5478 | 103.5074 | 0 | 2.0136 | 1.6936 | 1.3428 | 0 | 0 | 0 | 2.0136 | 1.6936 | 1.3428 | 0 | 31.6535 | 26.6239 | 21.1093 | 0 | 0 | 0 | 31.6535 | 26.6239 | 21.1093 | 0 | 121.543 | 102.2303 | 81.0553 | 0 | 0 | 0 | 121.543 | 102.2303 | 81.0553 | 0 | 0 | 0 | 0 | 0.014594 | 0.014594 | 0.014594 | 0 | 5000000 | scaled
58-753F | 17678.9362 | 24.8682 | 17509.44 | 144.628 | 0.1407% | 99.04% | 0.8181% | 7902.7389 | 16365.0232 | 10.0307 | 7230.8272 | 661.881 | 20.7775 | 14973.2355 | 1371.0102 | 58 |  | 1037 | 58-753F | 17678.9362 | 9776.1973 | 1313.9131 | 24.8682 | 10.7771 | 0.27021 | 17509.44 | 9620.7922 | 1169.0148 | 144.628 | 22.3727 | 12.342 | 1.5953 | 0 | 0 | 0 | 22.2639 | 12.2332 | 1.4864 | 0.10883 | 1482.2322 | 820.3512 | 111.2219 | 0 | 0 | 0 | 1469.0941 | 807.2131 | 98.0838 | 13.1381 | 16174.3313 | 8943.5041 | 1201.0959 | 24.8682 | 10.7771 | 0.27021 | 16018.082 | 8801.3459 | 1069.4446 | 131.3811 | 0.000388 | 0.000205 | 5.2e-06 | 0.010866 | 0.0061446 | 0.0010866 | 0.0002066 | 5000000 | scaled
58-754F | 111560.8824 | 12109.0604 | 97617.4227 | 1834.3993 | 10.85% | 87.5% | 1.644% | 50818.4624 | 103067.8143 | 50.1597 | 47118.5264 | 3649.7763 | 103.8964 | 95400.3398 | 7563.578 | 58 |  | 1038 | 58-754F | 111560.8824 | 60742.42 | 8493.0681 | 12109.0604 | 5245.161 | 133.5884 | 97617.4227 | 53662.8597 | 6525.0804 | 1834.3993 | 112.7375 | 62.5778 | 8.8411 | 0.23726 | 0.11193 | 0.033107 | 111.1199 | 61.0855 | 7.4276 | 1.3803 | 8272.1006 | 4622.3243 | 708.5226 | 1.2488 | 0.58722 | 0.17134 | 8104.2137 | 4455.099 | 541.7132 | 166.6381 | 103176.0443 | 56057.5179 | 7775.7044 | 12107.5743 | 5244.4619 | 133.3839 | 89402.0891 | 49146.6751 | 5975.9396 | 1666.3809 | 0.0044078 | 0.0019088 | 4.84e-05 | 0.010788 | 0.0061034 | 0.0010788 | 0.0026322 | 5000000 | scaled
58-756F | 14736.2098 | 190.0002 | 14224.3122 | 321.8973 | 1.289% | 96.53% | 2.184% | 6516.1212 | 13461.405 | 16.6737 | 5855.7517 | 643.6958 | 35.0041 | 12091.1245 | 1335.2764 | 58 |  | 1039 | 58-756F | 14736.2098 | 8220.0885 | 1274.8048 | 190.0002 | 84.511 | 2.2472 | 14224.3122 | 7813.6802 | 950.6602 | 321.8973 | 37.6472 | 20.9736 | 2.6431 | 1.482 | 0.99819 | 0 | 35.923 | 19.7332 | 2.4009 | 0.24222 | 1459.5941 | 815.8983 | 124.3177 | 7.7672 | 5.2041 | 0 | 1422.5855 | 781.4528 | 95.0763 | 29.2414 | 13238.9685 | 7383.2167 | 1147.844 | 180.7509 | 78.3087 | 2.2472 | 12765.8038 | 7012.4943 | 853.183 | 292.4137 | 0.000741 | 0.000321 | 8e-06 | 0.010871 | 0.0061456 | 0.001087 | 0.0004452 | 5000000 | scaled
580-690AE | 500.0602 | 431.0102 | 0 | 69.05 | 86.19% | 0% | 13.81% | 318.289 | 430.164 | 27.5337 | 93.8784 | 196.877 | 34.9762 | 152.998 | 242.1898 | 580 |  | 1040 | 580-690AE | 500.0602 | 181.7712 | 69.8962 | 431.0102 | 112.7212 | 0.84618 | 0 | 0 | 0 | 69.05 | 35.0282 | 7.4945 | 0.051958 | 34.9762 | 7.4425 | 0 | 0 | 0 | 0 | 0.051958 | 248.4624 | 51.5854 | 6.2726 | 242.1898 | 45.3128 | 0 | 0 | 0 | 0 | 6.2726 | 216.5697 | 122.6913 | 63.5717 | 153.8442 | 59.9658 | 0.84618 | 0 | 0 | 0 | 62.7255 | 0.0001784 | 7.72e-05 | 1.8e-06 | 0 | 0 | 0 | 0.0001028 | 5000000 | scaled
581-49 | 15957.5638 | 13541.8893 | 0 | 2415.6744 | 84.86% | 0% | 15.14% | 7563.5766 | 13422.9104 | 149.9108 | 6643.8937 | 769.7721 | 283.0212 | 11684.9262 | 1454.963 | 581 |  | 1041 | 581-49 | 15957.5638 | 8393.9872 | 2534.6534 | 13541.8893 | 5978.3127 | 118.9789 | 0 | 0 | 0 | 2415.6744 | 284.8389 | 134.9281 | 1.8177 | 283.0212 | 133.1104 | 0 | 0 | 0 | 0 | 1.8177 | 1674.4045 | 904.6324 | 219.4415 | 1454.963 | 685.1909 | 0 | 0 | 0 | 0 | 219.4415 | 13998.3204 | 7354.4267 | 2313.3941 | 11803.9052 | 5160.0115 | 118.9789 | 0 | 0 | 0 | 2194.4152 | 0.0055902 | 0.0024208 | 6.1e-05 | 0 | 0 | 0 | 0.00339 | 5000000 | scaled
583-318F | 153560.7783 | 152693.8995 | 0 | 866.8788 | 99.44% | 0% | 0.5645% | 65350.0482 | 151342.3919 | 8305.1596 | 0 | 57044.8887 | 19333.2375 | 0 | 132009.1544 | 583 |  | 1042 | 583-318F | 153560.7783 | 88210.7301 | 2218.3865 | 152693.8995 | 87343.8513 | 1351.5076 | 0 | 0 | 0 | 866.8788 | 19528.0954 | 11222.9359 | 194.858 | 19527.4431 | 11222.2836 | 194.2057 | 0 | 0 | 0 | 0.6523 | 133245.2042 | 76200.3156 | 1236.0498 | 133166.4563 | 76121.5677 | 1157.3019 | 0 | 0 | 0 | 78.7479 | 787.4787 | 787.4787 | 787.4787 | 0 | 0 | 0 | 0 | 0 | 0 | 787.4787 | 0.0064722 | 0.0034976 | 8.86e-05 | 0 | 0 | 0 | 0.0012262 | 5000000 | scaled
586-3 | 516808.3995 | 454434.1815 | 59650.6416 | 2723.5764 | 87.93% | 11.54% | 0.527% | 276808.6603 | 505554.5454 | 21700.2404 | 23950.6506 | 231157.7693 | 39170.6244 | 49143.7956 | 417240.1253 | 586 |  | 1043 | 586-3 | 516808.3995 | 239999.7392 | 11253.8541 | 454434.1815 | 204518.284 | 4543.3642 | 59650.6416 | 32757.8788 | 3986.9135 | 2723.5764 | 39586.1995 | 17885.9591 | 415.575 | 39491.0947 | 17832.8072 | 407.306 | 93.0553 | 51.1025 | 6.2196 | 2.0494 | 422220.3529 | 191062.5836 | 4980.2276 | 412675.0201 | 185709.1049 | 4111.3641 | 9297.9213 | 5106.0671 | 621.452 | 247.4115 | 55001.8472 | 31051.1966 | 5858.0515 | 2268.0667 | 976.3719 | 24.6942 | 50259.665 | 27600.7093 | 3359.2419 | 2474.1155 | 0.013428 | 0.0058144 | 0.0001482 | 0.010834 | 0.006123 | 0.0010834 | 0.003827 | 5000000 | scaled
59-1189F | 9345.5195 | 0 | 9345.5195 | 0 | 0% | 100% | 0% | 1499.5614 | 3101.5034 | 3.6054 | 1339.2562 | 156.6997 | 7.457 | 2769.9484 | 324.098 | 59 |  | 1044 | 59-1189F | 9345.5195 | 7845.9582 | 6244.0162 | 0 | 0 | 0 | 9345.5195 | 7845.9582 | 6244.0162 | 0 | 22.4695 | 18.8641 | 15.0125 | 0 | 0 | 0 | 22.4695 | 18.8641 | 15.0125 | 0 | 976.5792 | 819.8795 | 652.4813 | 0 | 0 | 0 | 976.5792 | 819.8795 | 652.4813 | 0 | 8346.4708 | 7007.2146 | 5576.5223 | 0 | 0 | 0 | 8346.4708 | 7007.2146 | 5576.5223 | 0 | 0 | 0 | 0 | 0.010893 | 0.010893 | 0.010893 | 0 | 5000000 | scaled
59-1190F | 22661.0277 | 0 | 22661.0277 | 0 | 0% | 100% | 0% | 3544.6474 | 7450.8646 | 4.4283 | 3248.174 | 292.0451 | 9.3082 | 6827.6762 | 613.8802 | 59 |  | 1045 | 59-1190F | 22661.0277 | 19116.3803 | 15210.1631 | 0 | 0 | 0 | 22661.0277 | 19116.3803 | 15210.1631 | 0 | 28.31 | 23.8817 | 19.0017 | 0 | 0 | 0 | 28.31 | 23.8817 | 19.0017 | 0 | 1867.0526 | 1575.0075 | 1253.1724 | 0 | 0 | 0 | 1867.0526 | 1575.0075 | 1253.1724 | 0 | 20765.6651 | 17517.4911 | 13937.9889 | 0 | 0 | 0 | 20765.6651 | 17517.4911 | 13937.9889 | 0 | 0 | 0 | 0 | 0.0074206 | 0.0074206 | 0.0074206 | 0 | 5000000 | scaled
59-1196 | 2572.8921 | 0 | 2572.8921 | 0 | 0% | 100% | 0% | 402.4172 | 845.87 | 2.7905 | 339.7895 | 59.8372 | 5.8655 | 714.2284 | 125.7761 | 59 |  | 1046 | 59-1196 | 2572.8921 | 2170.475 | 1727.0221 | 0 | 0 | 0 | 2572.8921 | 2170.475 | 1727.0221 | 0 | 17.8412 | 15.0507 | 11.9757 | 0 | 0 | 0 | 17.8412 | 15.0507 | 11.9757 | 0 | 382.5746 | 322.7374 | 256.7985 | 0 | 0 | 0 | 382.5746 | 322.7374 | 256.7985 | 0 | 2172.4764 | 1832.6868 | 1458.2479 | 0 | 0 | 0 | 2172.4764 | 1832.6868 | 1458.2479 | 0 | 0 | 0 | 0 | 0.0074528 | 0.0074528 | 0.0074528 | 0 | 5000000 | scaled
59-24R | 38168.689 | 0 | 38168.689 | 0 | 0% | 100% | 0% | 5977.609 | 12547.427 | 7.4524 | 5432.9465 | 537.2101 | 15.6431 | 11404.1416 | 1127.6423 | 59 |  | 1047 | 59-24R | 38168.689 | 32191.0799 | 25621.262 | 0 | 0 | 0 | 38168.689 | 32191.0799 | 25621.262 | 0 | 47.5856 | 40.1332 | 31.9425 | 0 | 0 | 0 | 47.5856 | 40.1332 | 31.9425 | 0 | 3430.2353 | 2893.0252 | 2302.593 | 0 | 0 | 0 | 3430.2353 | 2893.0252 | 2302.593 | 0 | 34690.8681 | 29257.9215 | 23286.7264 | 0 | 0 | 0 | 34690.8681 | 29257.9215 | 23286.7264 | 0 | 0 | 0 | 0 | 0.0074248 | 0.0074248 | 0.0074248 | 0 | 5000000 | scaled
59-464AE | 7434.4636 | 1910.8447 | 4774.7256 | 748.8932 | 25.7% | 64.22% | 10.07% | 3267.8637 | 6298.0271 | 133.8134 | 2263.8211 | 870.2293 | 220.7669 | 4583.0043 | 1494.2559 | 59 |  | 1048 | 59-464AE | 7434.4636 | 4166.5998 | 1136.4365 | 1910.8447 | 795.432 | 68.7437 | 4774.7256 | 2622.2746 | 318.7995 | 748.8932 | 231.3795 | 97.5662 | 10.6127 | 226.6021 | 94.6884 | 9.7678 | 4.2139 | 2.3143 | 0.28135 | 0.56352 | 1644.1441 | 773.9148 | 149.8882 | 1166.0395 | 480.6722 | 54.4783 | 410.0746 | 225.2126 | 27.3799 | 68.03 | 5558.94 | 3295.1189 | 975.9356 | 518.2031 | 220.0714 | 4.4977 | 4360.4371 | 2394.7477 | 291.1382 | 680.2998 | 0.0021414 | 0.000927 | 2.32e-05 | 0.010907 | 0.0061656 | 0.0010908 | 0.0010424 | 5000000 | scaled
59-465 | 77379.0475 | 49897.8647 | 21754.2923 | 5726.8904 | 64.48% | 28.11% | 7.401% | 33939.4855 | 69904.5092 | 3605.323 | 10942.5032 | 19391.6594 | 7466.7831 | 22410.0743 | 40027.6518 | 59 |  | 1049 | 59-465 | 77379.0475 | 43439.562 | 7474.5384 | 49897.8647 | 25749.6411 | 295.0988 | 21754.2923 | 11963.0305 | 1452.5491 | 5726.8904 | 7518.7639 | 3913.4409 | 51.9808 | 7487.2457 | 3894.169 | 45.8547 | 27.2089 | 14.9626 | 1.8168 | 4.3093 | 40869.1431 | 21477.4837 | 841.4913 | 38584.4414 | 19986.9406 | 203.442 | 1764.467 | 970.3084 | 117.8147 | 520.2346 | 28991.1406 | 18048.6374 | 6581.0663 | 3826.1777 | 1868.5315 | 45.8021 | 19962.6164 | 10977.7594 | 1332.9177 | 5202.3465 | 0.01718 | 0.0082428 | 0.0002106 | 0.010895 | 0.0061656 | 0.0010894 | 0.008052 | 5000000 | scaled
59-467 | 21641.0292 | 0 | 21641.0292 | 0 | 0% | 100% | 0% | 3472.0519 | 7181.8142 | 4.6623 | 3178.7808 | 288.6089 | 9.6438 | 6575.1934 | 596.9771 | 59 |  | 1050 | 59-467 | 21641.0292 | 18168.9773 | 14459.215 | 0 | 0 | 0 | 21641.0292 | 18168.9773 | 14459.215 | 0 | 29.0597 | 24.3974 | 19.4159 | 0 | 0 | 0 | 29.0597 | 24.3974 | 19.4159 | 0 | 1798.8766 | 1510.2678 | 1201.8996 | 0 | 0 | 0 | 1798.8766 | 1510.2678 | 1201.8996 | 0 | 19813.0929 | 16634.3121 | 13237.8995 | 0 | 0 | 0 | 19813.0929 | 16634.3121 | 13237.8995 | 0 | 0 | 0 | 0 | 0.010913 | 0.010913 | 0.010913 | 0 | 5000000 | scaled
59-803F | 5949.9229 | 0 | 5949.9229 | 0 | 0% | 100% | 0% | 930.7243 | 1956.287 | 1.9797 | 845.2476 | 83.497 | 4.1612 | 1776.6237 | 175.502 | 59 |  | 1051 | 59-803F | 5949.9229 | 5019.1986 | 3993.636 | 0 | 0 | 0 | 5949.9229 | 5019.1986 | 3993.636 | 0 | 12.656 | 10.6763 | 8.4948 | 0 | 0 | 0 | 12.656 | 10.6763 | 8.4948 | 0 | 533.7783 | 450.2814 | 358.2763 | 0 | 0 | 0 | 533.7783 | 450.2814 | 358.2763 | 0 | 5403.4886 | 4558.241 | 3626.8648 | 0 | 0 | 0 | 5403.4886 | 4558.241 | 3626.8648 | 0 | 0 | 0 | 0 | 0.0074574 | 0.0074574 | 0.0074574 | 0 | 5000000 | scaled
59-814F | 25190.3438 | 0 | 25190.3438 | 0 | 0% | 100% | 0% | 4024.5019 | 8360.3431 | 4.8758 | 3691.5885 | 328.0376 | 10.1287 | 7668.7618 | 681.4526 | 59 |  | 1052 | 59-814F | 25190.3438 | 21165.8419 | 16830.0008 | 0 | 0 | 0 | 25190.3438 | 21165.8419 | 16830.0008 | 0 | 30.5186 | 25.6428 | 20.3899 | 0 | 0 | 0 | 30.5186 | 25.6428 | 20.3899 | 0 | 2053.2679 | 1725.2303 | 1371.8154 | 0 | 0 | 0 | 2053.2679 | 1725.2303 | 1371.8154 | 0 | 23106.5573 | 19414.9688 | 15437.7956 | 0 | 0 | 0 | 23106.5573 | 19414.9688 | 15437.7956 | 0 | 0 | 0 | 0 | 0.010923 | 0.010923 | 0.010923 | 0 | 5000000 | scaled
59-816F | 52162.6394 | 0 | 52162.6394 | 0 | 0% | 100% | 0% | 8325.7871 | 17313.0864 | 9.8854 | 7637.7941 | 678.1075 | 20.5563 | 15882.4372 | 1410.0929 | 59 |  | 1053 | 59-816F | 52162.6394 | 43836.8523 | 34849.553 | 0 | 0 | 0 | 52162.6394 | 43836.8523 | 34849.553 | 0 | 61.9341 | 52.0487 | 41.3778 | 0 | 0 | 0 | 61.9341 | 52.0487 | 41.3778 | 0 | 4248.4724 | 3570.3649 | 2838.3794 | 0 | 0 | 0 | 4248.4724 | 3570.3649 | 2838.3794 | 0 | 47852.233 | 40214.4388 | 31969.7958 | 0 | 0 | 0 | 47852.233 | 40214.4388 | 31969.7958 | 0 | 0 | 0 | 0 | 0.010882 | 0.010882 | 0.010882 | 0 | 5000000 | scaled
591-1116F | 328.297 | 0 | 328.297 | 0 | 0% | 100% | 0% | 35.3935 | 73.3757 | 0.45917 | 27.7162 | 7.2181 | 0.95192 | 57.4595 | 14.9642 | 591 |  | 1054 | 591-1116F | 328.297 | 292.9035 | 254.9214 | 0 | 0 | 0 | 328.297 | 292.9035 | 254.9214 | 0 | 4.2591 | 3.7999 | 3.3071 | 0 | 0 | 0 | 4.2591 | 3.7999 | 3.3071 | 0 | 66.9528 | 59.7347 | 51.9886 | 0 | 0 | 0 | 66.9528 | 59.7347 | 51.9886 | 0 | 257.0851 | 229.369 | 199.6256 | 0 | 0 | 0 | 257.0851 | 229.369 | 199.6256 | 0 | 0 | 0 | 0 | 0.03593 | 0.03593 | 0.03593 | 0 | 5000000 | scaled
591-1594R | 519957.128 | 500848.0457 | 17004.5766 | 2104.5057 | 96.32% | 3.27% | 0.4047% | 218344.1675 | 514934.5187 | 18622.9782 | 6895.9283 | 192825.2609 | 43825.6876 | 14308.768 | 456800.0631 | 591 |  | 1055 | 591-1594R | 519957.128 | 301612.9605 | 5022.6093 | 500848.0457 | 290062.3413 | 1598.2104 | 17004.5766 | 9446.1135 | 1319.8932 | 2104.5057 | 44000.8441 | 25377.8659 | 175.1565 | 43965.411 | 25357.4788 | 170.9455 | 33.8496 | 18.8036 | 2.6274 | 1.5836 | 458554.6158 | 265729.3549 | 1754.5527 | 456556.2494 | 264534.2776 | 1423.1039 | 1807.1917 | 1003.9026 | 140.274 | 191.1747 | 17401.668 | 10505.7397 | 3092.9001 | 326.3853 | 170.5849 | 4.1609 | 15163.5353 | 8423.4074 | 1176.9918 | 1911.7474 | 0.0083374 | 0.0044816 | 0.0001144 | 0.035903 | 0.020335 | 0.0035902 | 0.0029558 | 5000000 | scaled
591-39AE | 863681.7299 | 263802.9416 | 593970.8583 | 5907.9299 | 30.54% | 68.77% | 0.684% | 415530.9909 | 809112.7681 | 15755.7404 | 248409.2522 | 151365.9983 | 27288.3539 | 514193.8998 | 267630.5144 | 591 |  | 1056 | 591-39AE | 863681.7299 | 448150.739 | 54568.9617 | 263802.9416 | 113245.1189 | 5079.624 | 593970.8583 | 328997.6901 | 43581.4078 | 5907.9299 | 27836.7638 | 12081.0233 | 548.4098 | 27016.4717 | 11623.343 | 481.3546 | 815.8465 | 453.2349 | 62.6097 | 4.4455 | 276416.4666 | 125050.4684 | 8785.9522 | 226561.2995 | 97123.9944 | 4482.0306 | 49318.4868 | 27389.7936 | 3767.2413 | 536.6804 | 559428.4994 | 311019.2473 | 45234.5997 | 10225.1704 | 4497.7816 | 116.2388 | 543836.525 | 301154.6617 | 39751.5568 | 5366.804 | 0.018082 | 0.0079168 | 0.0002004 | 0.034615 | 0.019619 | 0.0034614 | 0.0083956 | 5000000 | scaled
594-1379F | 49429.3275 | 49137.8432 | 0 | 291.4843 | 99.41% | 0% | 0.5897% | 32594.9364 | 49108.6895 | 6180.7207 | 5.1729 | 26409.0428 | 9363.9295 | 8.9812 | 39735.7789 | 594 |  | 1057 | 594-1379F | 49429.3275 | 16834.3911 | 320.638 | 49137.8432 | 16542.9068 | 29.1537 | 0 | 0 | 0 | 291.4843 | 9370.8775 | 3190.1568 | 6.948 | 9370.6582 | 3189.9375 | 6.7287 | 0 | 0 | 0 | 0.21933 | 39784.5983 | 13375.5555 | 48.8194 | 39758.1196 | 13349.0769 | 22.3408 | 0 | 0 | 0 | 26.4786 | 273.8517 | 268.6788 | 264.8705 | 9.0654 | 3.8925 | 0.084213 | 0 | 0 | 0 | 264.7863 | 0.0017846 | 0.0007726 | 1.94e-05 | 0 | 0 | 0 | 0.0003976 | 5000000 | scaled
595-1454F | 124924.5765 | 104029.5755 | 19982.2779 | 912.723 | 83.27% | 16% | 0.7306% | 66229.8203 | 119259.8929 | 9590.8713 | 8206.4472 | 48432.5017 | 16809.5482 | 17111.3706 | 85338.9741 | 595 |  | 1058 | 595-1454F | 124924.5765 | 58694.7562 | 5664.6836 | 104029.5755 | 46725.7471 | 3419.4321 | 19982.2779 | 11056.2861 | 1332.5285 | 912.723 | 17393.0418 | 7802.1705 | 583.4937 | 17355.0727 | 7780.8552 | 580.3207 | 37.2823 | 20.6285 | 2.4862 | 0.68679 | 88361.858 | 39929.3563 | 3022.8839 | 86478.7681 | 38850.3975 | 2819.9257 | 1800.1775 | 996.0464 | 120.0458 | 82.9124 | 19169.6767 | 10963.2294 | 2058.3061 | 195.7346 | 94.4944 | 19.1856 | 18144.8182 | 10039.6111 | 1209.9966 | 829.1239 | 0.0033358 | 0.001528 | 0.0001834 | 0.014147 | 0.0080532 | 0.0014146 | 0.0012934 | 5000000 | scaled
595-500 | 238236.4394 | 71012.7975 | 165556.4857 | 1667.1562 | 29.81% | 69.49% | 0.6998% | 106785.256 | 225345.2472 | 9558.3299 | 69348.2265 | 27878.6996 | 20340.0102 | 146026.2406 | 58978.9964 | 595 |  | 1059 | 595-500 | 238236.4394 | 131451.1834 | 12891.1922 | 71012.7975 | 38308.4178 | 180.6251 | 165556.4857 | 91475.6094 | 11043.4109 | 1667.1562 | 20384.4309 | 10826.101 | 44.4207 | 20188.0379 | 10717.0258 | 30.1495 | 195.1385 | 107.8207 | 13.0167 | 1.2545 | 60520.8695 | 32642.1699 | 1541.8731 | 40293.0406 | 21397.8372 | 51.2365 | 20076.3833 | 11092.8871 | 1339.191 | 151.4456 | 157331.139 | 87982.9125 | 11304.8984 | 10531.719 | 6193.5547 | 99.2391 | 145284.9639 | 80274.9017 | 9691.2033 | 1514.4561 | 0.0056032 | 0.002763 | 7e-05 | 0.013989 | 0.0079528 | 0.0013988 | 0.0023038 | 5000000 | scaled
597-595 | 18774393.9857 | 17938778.6421 | 823747.1843 | 11868.1593 | 95.55% | 4.388% | 0.06321% | 9223529.4561 | 18519477.3752 | 929454.0227 | 332335.0287 | 7961740.4047 | 1862919.5577 | 690955.1888 | 15965602.6287 | 597 |  | 1060 | 597-595 | 18774393.9857 | 9550864.5296 | 254916.6105 | 17938778.6421 | 9076070.2973 | 170178.8621 | 823747.1843 | 462926.073 | 72869.589 | 11868.1593 | 1881048.3724 | 951594.3496 | 18128.8147 | 1879752.146 | 950861.9899 | 18006.0086 | 1287.296 | 723.4293 | 113.8756 | 8.9304 | 16125401.2896 | 8163660.8849 | 159798.6609 | 16048856.7166 | 8120172.44 | 152044.7024 | 75466.4613 | 42410.3332 | 6675.8468 | 1078.1117 | 767944.3237 | 435609.295 | 76989.1349 | 10169.7795 | 5035.8673 | 128.1511 | 746993.427 | 419792.3104 | 66079.8665 | 10781.1172 | 0.050052 | 0.02517 | 0.0006388 | 0.086229 | 0.048924 | 0.008623 | 0.016785 | 5000000 | scaled
599-19R | 25743456.0826 | 25588004.7565 | 135218.1509 | 20233.1752 | 99.4% | 0.5253% | 0.0786% | 12784620.3718 | 25367798.4688 | 680030.7935 | 54532.6901 | 12050056.8881 | 1350337.0566 | 114761.2699 | 23902700.1423 | 599 |  | 1061 | 599-19R | 25743456.0826 | 12958835.7109 | 375657.6138 | 25588004.7565 | 12863093.4566 | 344640.1963 | 135218.1509 | 75509.079 | 10784.2423 | 20233.1752 | 1368799.2522 | 688768.4587 | 18462.1956 | 1368545.7813 | 688620.1915 | 18427.9696 | 238.2461 | 133.0424 | 19.0012 | 15.2248 | 24232018.8846 | 12181961.9965 | 329318.7423 | 24213028.2934 | 12170545.5776 | 326112.7519 | 17152.5957 | 9578.4234 | 1367.995 | 1837.9955 | 142637.9458 | 88105.2556 | 27876.6759 | 6430.6818 | 3927.6876 | 99.4748 | 117827.3091 | 65797.6132 | 9397.2461 | 18379.9549 | 0.079701 | 0.040121 | 0.0010206 | 0.043361 | 0.024643 | 0.004336 | 0.028552 | 5000000 | scaled
60-574 | 8531.1128 | 6139.3442 | 0 | 2391.7686 | 71.96% | 0% | 28.04% | 3279.9991 | 6077.8692 | 70.9993 | 2840.0529 | 368.9469 | 121.6568 | 5325.7131 | 630.4993 | 60 |  | 1062 | 60-574 | 8531.1128 | 5251.1137 | 2453.2436 | 6139.3442 | 2859.3451 | 61.475 | 0 | 0 | 0 | 2391.7686 | 124.0174 | 53.0181 | 2.3606 | 122.2177 | 51.2184 | 0.56084 | 0 | 0 | 0 | 1.7997 | 850.6414 | 481.6945 | 220.1421 | 633.3715 | 264.4246 | 2.8722 | 0 | 0 | 0 | 217.2699 | 7556.454 | 4716.4011 | 2230.7409 | 5383.7551 | 2543.7021 | 58.042 | 0 | 0 | 0 | 2172.6989 | 0.0060132 | 0.002702 | 6.84e-05 | 0 | 0 | 0 | 0.0033362 | 5000000 | scaled
60-576F | 2637.5357 | 1523.0699 | 0 | 1114.4658 | 57.75% | 0% | 42.25% | 877.0584 | 1506.602 | 2.9549 | 858.9211 | 15.1824 | 3.2718 | 1486.5309 | 16.7993 | 60 |  | 1063 | 60-576F | 2637.5357 | 1760.4772 | 1130.9336 | 1523.0699 | 646.0115 | 16.4679 | 0 | 0 | 0 | 1114.4658 | 4.1104 | 1.1555 | 0.8386 | 3.2718 | 0.31688 | 0 | 0 | 0 | 0 | 0.8386 | 118.0381 | 102.8557 | 101.2388 | 16.7993 | 1.6169 | 0 | 0 | 0 | 0 | 101.2388 | 2515.3871 | 1656.466 | 1028.8562 | 1502.9988 | 644.0777 | 16.4679 | 0 | 0 | 0 | 1012.3883 | 0.0043286 | 0.0018744 | 4.8e-05 | 0 | 0 | 0 | 0.001582 | 5000000 | scaled
60-603F | 169513.4667 | 15338.6149 | 150192.0133 | 3982.8384 | 9.049% | 88.6% | 2.35% | 75433.685 | 155440.3711 | 445.3157 | 68305.6358 | 6682.7335 | 860.1099 | 140814.0194 | 13766.2418 | 60 |  | 1064 | 60-603F | 169513.4667 | 94079.7817 | 14073.0956 | 15338.6149 | 6821.6429 | 72.1967 | 150192.0133 | 83275.3004 | 10018.0604 | 3982.8384 | 875.7701 | 430.4544 | 15.6601 | 682.9251 | 322.1945 | 0 | 189.848 | 105.2629 | 12.6632 | 2.997 | 14946.4984 | 8263.7649 | 1180.2565 | 2314.3484 | 1098.5583 | 0 | 12270.3462 | 6803.4028 | 818.4528 | 361.8038 | 153691.1983 | 85385.5625 | 12877.1789 | 12341.3415 | 5400.8901 | 72.1967 | 137731.8191 | 76366.6347 | 9186.9445 | 3618.0377 | 0.012716 | 0.0055072 | 0.0001394 | 0.014468 | 0.0082522 | 0.0014468 | 0.0055096 | 5000000 | scaled
61-13F | 66913.567 | 736.2799 | 64672.6014 | 1504.6858 | 1.1% | 96.65% | 2.249% | 29490.9512 | 61078.4018 | 34.8272 | 27020.4582 | 2435.6659 | 70.6873 | 55959.5614 | 5048.153 | 61 |  | 1065 | 61-13F | 66913.567 | 37422.6158 | 5835.1652 | 736.2799 | 315.7637 | 7.7707 | 64672.6014 | 35602.1664 | 4322.7088 | 1504.6858 | 76.6392 | 41.8121 | 5.9519 | 3.399 | 0.98453 | 0 | 72.108 | 39.6953 | 4.8197 | 1.1322 | 5545.1797 | 3109.5139 | 497.0267 | 17.3997 | 5.0387 | 0 | 5391.0933 | 2967.7885 | 360.34 | 136.6867 | 61291.748 | 34271.2898 | 5332.1866 | 715.4811 | 309.7404 | 7.7707 | 59209.4001 | 32594.6826 | 3957.5491 | 1366.8669 | 0.003164 | 0.0013704 | 3.46e-05 | 0.010854 | 0.0061478 | 0.0010854 | 0.0020736 | 5000000 | scaled
61-21F | 113445.3538 | 7576.1923 | 104486.1286 | 1383.0329 | 6.678% | 92.1% | 1.219% | 51414.3172 | 105002.3755 | 315.9158 | 45416.0929 | 5682.3086 | 538.6043 | 93366.99 | 11096.7813 | 61 |  | 1066 | 61-21F | 113445.3538 | 62031.0366 | 8442.9783 | 7576.1923 | 3110.3022 | 59.7637 | 104486.1286 | 57537.7015 | 7000.1817 | 1383.0329 | 552.5577 | 236.642 | 13.9535 | 410.6904 | 158.0519 | 3.4779 | 140.8266 | 77.5494 | 9.4349 | 1.0407 | 11867.4624 | 6185.1538 | 770.6811 | 2386.8439 | 907.9806 | 18.2964 | 9354.9829 | 5151.5375 | 626.749 | 125.6357 | 101025.3337 | 55609.2409 | 7658.3438 | 4778.658 | 2044.2698 | 37.9894 | 94990.3191 | 52308.6145 | 6363.9978 | 1256.3566 | 0.0041476 | 0.0017962 | 4.52e-05 | 0.010801 | 0.00612 | 0.00108 | 0.001926 | 5000000 | scaled
61-23F | 42473.6336 | 2.2924 | 42368.8763 | 102.4649 | 0.005397% | 99.75% | 0.2412% | 19000.2634 | 39536.9687 | 23.2482 | 17416.0195 | 1560.9958 | 48.3768 | 36240.3356 | 3248.2562 | 61 |  | 1067 | 61-23F | 42473.6336 | 23473.3702 | 2936.665 | 2.2924 | 0.99128 | 0.02295 | 42368.8763 | 23369.914 | 2834.1771 | 102.4649 | 51.922 | 28.6738 | 3.5452 | 0 | 0 | 0 | 51.8449 | 28.5967 | 3.4681 | 0.077102 | 3490.4263 | 1929.4306 | 242.1701 | 0 | 0 | 0 | 3481.1183 | 1920.1226 | 232.8621 | 9.308 | 38931.2853 | 21515.2658 | 2690.9497 | 2.2924 | 0.99128 | 0.02295 | 38835.9131 | 21421.1947 | 2597.8469 | 93.0799 | 0.000253 | 0.0001094 | 2.6e-06 | 0.010844 | 0.0061542 | 0.0010844 | 0.0001376 | 5000000 | scaled
62-22AE | 149850.5521 | 18549.1625 | 125344.6952 | 5956.6945 | 12.38% | 83.65% | 3.975% | 65983.9309 | 135423.3537 | 1019.6499 | 54441.6729 | 10522.6082 | 2038.2597 | 111698.7607 | 21686.3332 | 62 |  | 1068 | 62-22AE | 149850.5521 | 83866.6212 | 14427.1984 | 18549.1625 | 8843.0132 | 76.688 | 125344.6952 | 69066.9134 | 8393.816 | 5956.6945 | 2058.754 | 1039.1042 | 20.4943 | 1887.713 | 942.8454 | 4.8583 | 166.5588 | 91.7765 | 11.1538 | 4.4822 | 23188.4872 | 12665.879 | 1502.154 | 8561.893 | 4363.4439 | 17.7972 | 14085.484 | 7761.3249 | 943.2466 | 541.1102 | 124603.3109 | 70161.638 | 12904.5502 | 8099.5564 | 3536.7239 | 54.0325 | 111092.6524 | 61213.812 | 7439.4156 | 5411.1021 | 0.016592 | 0.0071842 | 0.0001834 | 0.01074 | 0.0060882 | 0.001074 | 0.0083812 | 5000000 | scaled
63-35AE | 256467.5251 | 195478.8589 | 60168.1744 | 820.4918 | 76.22% | 23.46% | 0.3199% | 137440.0609 | 250736.4976 | 10457.1735 | 26905.4448 | 100077.4425 | 18661.8423 | 57594.392 | 174480.2633 | 63 |  | 1069 | 63-35AE | 256467.5251 | 119027.4642 | 5731.0276 | 195478.8589 | 85035.1813 | 888.7786 | 60168.1744 | 33171.7911 | 4021.7571 | 820.4918 | 18759.8424 | 8302.6688 | 98.0001 | 18678.2161 | 8257.3898 | 91.9679 | 81.0089 | 44.6617 | 5.4148 | 0.61739 | 175579.9389 | 75502.4964 | 1099.6756 | 170389.6716 | 72607.5671 | 683.1961 | 5115.7333 | 2820.3953 | 341.9455 | 74.534 | 62127.7438 | 35222.299 | 4533.3518 | 6410.9712 | 4170.2244 | 113.6146 | 54971.4322 | 30306.7341 | 3674.3968 | 745.3404 | 0.0050124 | 0.002901 | 7.36e-05 | 0.010803 | 0.0061276 | 0.0010802 | 0.0011402 | 5000000 | scaled
63-797R | 1294920.7081 | 1241111.1907 | 51084.6541 | 2724.8633 | 95.84% | 3.945% | 0.2104% | 711407.7103 | 1277950.9902 | 72217.2303 | 22895.3963 | 616295.0836 | 128836.5756 | 47074.9834 | 1102039.4312 | 63 |  | 1070 | 63-797R | 1294920.7081 | 583512.9978 | 16969.7179 | 1241111.1907 | 552635.8313 | 10828.0497 | 51084.6541 | 28152.3031 | 3416.8049 | 2724.8633 | 129998.5923 | 57781.3619 | 1162.0167 | 129927.985 | 57741.5305 | 1155.3809 | 68.5569 | 37.7811 | 4.5854 | 2.0504 | 1112217.7268 | 495922.6432 | 10178.2956 | 1107464.0841 | 493191.8348 | 9629.375 | 4506.1143 | 2483.2799 | 301.3921 | 247.5285 | 52704.389 | 29808.9926 | 5629.4056 | 3719.1215 | 1702.466 | 43.2937 | 46509.9829 | 25631.2421 | 3110.8273 | 2475.2845 | 0.010809 | 0.0047488 | 0.0001206 | 0.010802 | 0.0061248 | 0.0010802 | 0.0038798 | 5000000 | scaled
64-13F | 5341.0304 | 1716.8168 | 3516.6556 | 107.558 | 32.14% | 65.84% | 2.014% | 2464.8325 | 4997.0414 | 151.5226 | 1244.1732 | 1069.1366 | 289.2831 | 2613.3173 | 2094.4411 | 64 |  | 1071 | 64-13F | 5341.0304 | 2876.1979 | 343.9891 | 1716.8168 | 812.0315 | 0.11475 | 3516.6556 | 1956.6084 | 236.3163 | 107.558 | 289.6122 | 138.0896 | 0.32916 | 285.8374 | 135.9534 | 0 | 3.6939 | 2.0552 | 0.24823 | 0.080934 | 2152.9882 | 1083.8515 | 58.5471 | 1417.3682 | 670.2304 | 0 | 725.8493 | 403.8504 | 48.7765 | 9.7706 | 2898.43 | 1654.2568 | 285.1128 | 13.6112 | 5.8476 | 0.11475 | 2787.1124 | 1550.7028 | 187.2916 | 97.7064 | 0.0003138 | 0.0001358 | 3.4e-06 | 0.0074366 | 0.0042536 | 0.0007436 | 0.0001478 | 5000000 | scaled
64-14F | 111705.1457 | 5085.4893 | 102021.0938 | 4598.5626 | 4.553% | 91.33% | 4.117% | 48637.804 | 100172.3009 | 160.6851 | 44223.3407 | 4253.7782 | 250.068 | 91456.6687 | 8465.5642 | 64 |  | 1072 | 64-14F | 111705.1457 | 63067.3417 | 11532.8448 | 5085.4893 | 1628.8387 | 31.5033 | 102021.0938 | 56839.9405 | 6902.779 | 4598.5626 | 262.1366 | 101.4516 | 12.0686 | 131.7504 | 27.2759 | 0.020495 | 126.926 | 70.7154 | 8.5879 | 3.4603 | 9446.0018 | 5192.2236 | 980.4376 | 713.2464 | 141.8649 | 0.10428 | 8315.0188 | 4632.6221 | 562.5968 | 417.7366 | 101997.0072 | 57773.6666 | 10540.3386 | 4240.4926 | 1459.6979 | 31.3785 | 93579.1489 | 52136.6029 | 6331.5944 | 4177.3657 | 0.016976 | 0.0073502 | 0.0001868 | 0.0073534 | 0.0042096 | 0.0007354 | 0.006436 | 5000000 | scaled
64-15F | 6195.9048 | 0 | 6195.9048 | 0 | 0% | 100% | 0% | 971.3148 | 2037.2877 | 2.1138 | 834.4339 | 134.7672 | 4.4335 | 1750.1862 | 282.6679 | 64 |  | 1073 | 64-15F | 6195.9048 | 5224.5899 | 4158.6171 | 0 | 0 | 0 | 6195.9048 | 5224.5899 | 4158.6171 | 0 | 13.4835 | 11.3697 | 9.0499 | 0 | 0 | 0 | 13.4835 | 11.3697 | 9.0499 | 0 | 859.6644 | 724.8972 | 576.9964 | 0 | 0 | 0 | 859.6644 | 724.8972 | 576.9964 | 0 | 5322.7569 | 4488.3231 | 3572.5707 | 0 | 0 | 0 | 5322.7569 | 4488.3231 | 3572.5707 | 0 | 0 | 0 | 0 | 0.0074314 | 0.0074314 | 0.0074314 | 0 | 5000000 | scaled
65-1086 | 90215.7695 | 0 | 90215.7695 | 0 | 0% | 100% | 0% | 14175.5486 | 29658.8922 | 16.2377 | 12952.9899 | 1206.3211 | 33.9734 | 27100.9851 | 2523.9338 | 65 |  | 1074 | 65-1086 | 90215.7695 | 76040.2209 | 60556.8773 | 0 | 0 | 0 | 90215.7695 | 76040.2209 | 60556.8773 | 0 | 103.3394 | 87.1018 | 69.3661 | 0 | 0 | 0 | 103.3394 | 87.1018 | 69.3661 | 0 | 7677.2466 | 6470.9256 | 5153.3128 | 0 | 0 | 0 | 7677.2466 | 6470.9256 | 5153.3128 | 0 | 82435.1834 | 69482.1935 | 55334.1984 | 0 | 0 | 0 | 82435.1834 | 69482.1935 | 55334.1984 | 0 | 0 | 0 | 0 | 0.0073536 | 0.0073536 | 0.0073536 | 0 | 5000000 | scaled
65-38AE | 94199.1014 | 0 | 94199.1014 | 0 | 0% | 100% | 0% | 14794.9363 | 30965.4102 | 16.0064 | 13567.7453 | 1211.1846 | 33.5009 | 28396.9319 | 2534.9774 | 65 |  | 1075 | 65-38AE | 94199.1014 | 79404.1651 | 63233.6912 | 0 | 0 | 0 | 94199.1014 | 79404.1651 | 63233.6912 | 0 | 101.9122 | 85.9059 | 68.4113 | 0 | 0 | 0 | 101.9122 | 85.9059 | 68.4113 | 0 | 7711.5915 | 6500.4068 | 5176.6141 | 0 | 0 | 0 | 7711.5915 | 6500.4068 | 5176.6141 | 0 | 86385.5978 | 72817.8524 | 57988.6659 | 0 | 0 | 0 | 86385.5978 | 72817.8524 | 57988.6659 | 0 | 0 | 0 | 0 | 0.0073458 | 0.0073458 | 0.0073458 | 0 | 5000000 | scaled
66-1213R | 5312267.5909 | 5193771.752 | 106206.9301 | 12288.9088 | 97.77% | 1.999% | 0.2313% | 2926883.1102 | 5236471.8799 | 223125.664 | 50978.3903 | 2652779.0558 | 397989.7766 | 104813.7124 | 4733668.3908 | 66 |  | 1076 | 66-1213R | 5312267.5909 | 2385384.4807 | 75795.711 | 5193771.752 | 2314523.3983 | 56402.3019 | 106206.9301 | 58572.1736 | 7104.5003 | 12288.9088 | 402368.9901 | 179243.3261 | 4379.2134 | 402230.5237 | 179162.8157 | 4361.3225 | 129.2194 | 71.2633 | 8.6439 | 9.247 | 4787289.2807 | 2134510.2249 | 53620.8899 | 4776444.5432 | 2128028.7637 | 51853.7948 | 9728.4046 | 5365.1283 | 650.7622 | 1116.3329 | 122609.3201 | 71630.9297 | 17795.6077 | 15096.685 | 7331.8188 | 187.1846 | 96349.3061 | 53135.782 | 6445.0942 | 11163.3289 | 0.047062 | 0.020833 | 0.0005288 | 0.010722 | 0.006083 | 0.0010722 | 0.017361 | 5000000 | scaled
67-24R | 2610800.0114 | 2443585.0538 | 158335.2051 | 8879.7525 | 93.6% | 6.065% | 0.3401% | 1296024.0652 | 2545123.2751 | 73763.6668 | 62758.3007 | 1159502.0977 | 144306.9141 | 130583.8039 | 2270232.5571 | 67 |  | 1077 | 67-24R | 2610800.0114 | 1314775.9462 | 65676.7362 | 2443585.0538 | 1216428.6003 | 41979.9129 | 158335.2051 | 89467.5934 | 14817.0709 | 8879.7525 | 146776.0609 | 73012.3941 | 2469.1468 | 146550.5424 | 72882.0582 | 2441.9862 | 218.8368 | 123.6541 | 20.4788 | 6.6817 | 2312023.0186 | 1152520.9209 | 41790.4614 | 2295583.3274 | 1142880.7958 | 39520.8718 | 15633.0484 | 8833.4822 | 1462.9468 | 806.6428 | 152000.9319 | 89242.6313 | 21417.1281 | 1451.1841 | 665.7463 | 17.0549 | 142483.3199 | 80510.4571 | 13333.6452 | 8066.4279 | 0.040152 | 0.019923 | 0.0005058 | 0.16676 | 0.094747 | 0.016676 | 0.012494 | 5000000 | scaled
67-34R | 4180137.3859 | 3921083.9191 | 245326.3777 | 13727.0891 | 93.8% | 5.869% | 0.3284% | 2147100.7248 | 4097365.8059 | 138508.6187 | 102918.3867 | 1905673.7194 | 263098.6992 | 212446.3665 | 3621820.7402 | 67 |  | 1078 | 67-34R | 4180137.3859 | 2033036.6611 | 82771.58 | 3921083.9191 | 1880694.3899 | 46087.4779 | 245326.3777 | 138615.1821 | 22957.013 | 13727.0891 | 266224.9424 | 127716.3237 | 3126.2432 | 265820.7709 | 127483.4644 | 3079.0593 | 393.8423 | 222.5302 | 36.8547 | 10.3292 | 3668142.4557 | 1762468.7363 | 46321.7155 | 3643383.3983 | 1747936.8795 | 42874.5373 | 23512.0792 | 13284.8786 | 2200.2001 | 1246.9782 | 245769.9878 | 142851.6011 | 33323.6213 | 11879.7498 | 5274.0461 | 133.8814 | 221420.4562 | 125107.7733 | 20719.9582 | 12469.7817 | 0.061507 | 0.029534 | 0.0007494 | 0.16659 | 0.094642 | 0.016659 | 0.01934 | 5000000 | scaled
67-37R | 622304.2119 | 542523.2142 | 74570.4603 | 5210.5374 | 87.18% | 11.98% | 0.8373% | 304550.524 | 602838.9323 | 16205.2512 | 29519.5963 | 258825.6766 | 31828.9506 | 61536.8987 | 509473.0829 | 67 |  | 1079 | 67-37R | 622304.2119 | 317753.6878 | 19465.2796 | 542523.2142 | 270411.0171 | 7273.8813 | 74570.4603 | 42132.1334 | 6980.8609 | 5210.5374 | 32269.79 | 16064.5389 | 440.8394 | 32123.139 | 15979.9758 | 423.557 | 142.7303 | 80.6423 | 13.3616 | 3.9208 | 517502.6407 | 258676.9641 | 8029.5578 | 509334.0542 | 253855.8329 | 6835.8429 | 7695.2577 | 4347.8024 | 720.3861 | 473.3288 | 72531.7812 | 43012.1849 | 10994.8825 | 1066.021 | 575.2083 | 14.4814 | 66732.4723 | 37703.6887 | 6247.1132 | 4733.2879 | 0.025731 | 0.012529 | 0.0003188 | 0.16792 | 0.095387 | 0.016792 | 0.0072982 | 5000000 | scaled
67-45R | 1627950.76 | 1510503.3948 | 110849.533 | 6597.8321 | 92.79% | 6.809% | 0.4053% | 838191.7393 | 1593435.5042 | 53645.1744 | 43779.9939 | 740766.571 | 101535.9847 | 91097.0221 | 1400802.4975 | 67 |  | 1080 | 67-45R | 1627950.76 | 789759.0207 | 34515.2557 | 1510503.3948 | 720526.0466 | 17541.5319 | 110849.533 | 62635.1419 | 10375.8918 | 6597.8321 | 102738.313 | 49093.1386 | 1202.3283 | 102579.2702 | 49001.1127 | 1182.9414 | 154.0781 | 87.0613 | 14.4222 | 4.9647 | 1418800.1494 | 678033.5784 | 17997.6519 | 1406975.2901 | 671091.2928 | 16347.5548 | 11225.5077 | 6342.9339 | 1050.7455 | 599.3516 | 106412.2976 | 62632.3037 | 15315.2755 | 948.8345 | 433.6411 | 11.0356 | 99469.9472 | 56205.1467 | 9310.724 | 5993.5159 | 0.032002 | 0.016004 | 0.0004066 | 0.16768 | 0.095266 | 0.016768 | 0.0091878 | 5000000 | scaled
68-1356AE | 83350.3104 | 0 | 83350.3104 | 0 | 0% | 100% | 0% | 13305.9059 | 27656.3681 | 15.1503 | 12179.0783 | 1111.6773 | 31.4899 | 25314.2533 | 2310.6249 | 68 |  | 1081 | 68-1356AE | 83350.3104 | 70044.4046 | 55693.9423 | 0 | 0 | 0 | 83350.3104 | 70044.4046 | 55693.9423 | 0 | 94.9038 | 79.7535 | 63.4139 | 0 | 0 | 0 | 94.9038 | 79.7535 | 63.4139 | 0 | 6963.7236 | 5852.0463 | 4653.0987 | 0 | 0 | 0 | 6963.7236 | 5852.0463 | 4653.0987 | 0 | 76291.683 | 64112.6048 | 50977.4297 | 0 | 0 | 0 | 76291.683 | 64112.6048 | 50977.4297 | 0 | 0 | 0 | 0 | 0.010714 | 0.010714 | 0.010714 | 0 | 5000000 | scaled
68-1358 | 4228.5637 | 0 | 4228.5637 | 0 | 0% | 100% | 0% | 676.0373 | 1403.2662 | 1.4494 | 602.3748 | 72.2131 | 3.0085 | 1250.3632 | 149.8945 | 68 |  | 1082 | 68-1358 | 4228.5637 | 3552.5263 | 2825.2974 | 0 | 0 | 0 | 4228.5637 | 3552.5263 | 2825.2974 | 0 | 9.0658 | 7.6164 | 6.0573 | 0 | 0 | 0 | 9.0658 | 7.6164 | 6.0573 | 0 | 451.6879 | 379.4747 | 301.7934 | 0 | 0 | 0 | 451.6879 | 379.4747 | 301.7934 | 0 | 3767.81 | 3165.4352 | 2517.4468 | 0 | 0 | 0 | 3767.81 | 3165.4352 | 2517.4468 | 0 | 0 | 0 | 0 | 0.010771 | 0.010771 | 0.010771 | 0 | 5000000 | scaled
68-18 | 7282.0005 | 0 | 7282.0005 | 0 | 0% | 100% | 0% | 1167.8842 | 2416.4867 | 1.5213 | 1061.7379 | 104.625 | 3.1477 | 2196.8578 | 216.4812 | 68 |  | 1083 | 68-18 | 7282.0005 | 6114.1163 | 4865.5138 | 0 | 0 | 0 | 7282.0005 | 6114.1163 | 4865.5138 | 0 | 9.4854 | 7.9641 | 6.3377 | 0 | 0 | 0 | 9.4854 | 7.9641 | 6.3377 | 0 | 652.3589 | 547.7338 | 435.8776 | 0 | 0 | 0 | 652.3589 | 547.7338 | 435.8776 | 0 | 6620.1563 | 5558.4184 | 4423.2985 | 0 | 0 | 0 | 6620.1563 | 5558.4184 | 4423.2985 | 0 | 0 | 0 | 0 | 0.010742 | 0.010742 | 0.010742 | 0 | 5000000 | scaled
68-27 | 64463.8319 | 61936.825 | 1879.8308 | 647.176 | 96.08% | 2.916% | 1.004% | 37023.53 | 63511.5706 | 5582.4049 | 743.0639 | 30698.0613 | 9515.4511 | 1533.1695 | 52462.95 | 68 |  | 1084 | 68-27 | 64463.8319 | 27440.3018 | 952.2613 | 61936.825 | 25760.6941 | 179.4558 | 1879.8308 | 1032.4318 | 125.6294 | 647.176 | 9548.605 | 3966.2001 | 33.1539 | 9546.4844 | 3964.8159 | 32.5578 | 1.6336 | 0.89722 | 0.10918 | 0.48698 | 52686.0444 | 21987.9831 | 223.0944 | 52362.6637 | 21783.8758 | 146.6218 | 264.5908 | 145.3173 | 17.6827 | 58.7899 | 2229.1825 | 1486.1186 | 696.0129 | 27.677 | 12.0023 | 0.2762 | 1613.6064 | 886.2172 | 107.8376 | 587.8991 | 0.002492 | 0.0010794 | 2.76e-05 | 0.010764 | 0.0060842 | 0.0010764 | 0.000951 | 5000000 | scaled
68-42 | 327449.0396 | 265995.1408 | 60448.4767 | 1005.4221 | 81.23% | 18.46% | 0.307% | 192668.1262 | 320130.4953 | 20841.2247 | 24547.05 | 147279.8515 | 33511.6158 | 50850.419 | 235768.4606 | 68 |  | 1085 | 68-42 | 327449.0396 | 134780.9134 | 7318.5443 | 265995.1408 | 100549.3467 | 2271.3917 | 60448.4767 | 33226.1445 | 4041.7305 | 1005.4221 | 33807.9247 | 12966.7 | 296.3089 | 33726.6002 | 12921.6584 | 290.1654 | 80.5679 | 44.285 | 5.387 | 0.75655 | 238237.8371 | 90957.9856 | 2469.3766 | 232200.4453 | 87598.3384 | 1980.4755 | 5946.0586 | 3268.314 | 397.5678 | 91.3332 | 55403.2778 | 30856.2278 | 4552.8589 | 68.0953 | 29.3499 | 0.75077 | 54421.8501 | 29913.5455 | 3638.7757 | 913.3324 | 0.0036074 | 0.0015624 | 3.98e-05 | 0.010695 | 0.0060496 | 0.0010694 | 0.0014342 | 5000000 | scaled
68-43AE | 15601.0764 | 0 | 15601.0764 | 0 | 0% | 100% | 0% | 2491.9657 | 5175.5689 | 2.592 | 2171.8367 | 317.537 | 5.3833 | 4510.6924 | 659.4932 | 68 |  | 1086 | 68-43AE | 15601.0764 | 13109.1107 | 10425.5075 | 0 | 0 | 0 | 15601.0764 | 13109.1107 | 10425.5075 | 0 | 16.2274 | 13.6354 | 10.844 | 0 | 0 | 0 | 16.2274 | 13.6354 | 10.844 | 0 | 1987.9562 | 1670.4192 | 1328.463 | 0 | 0 | 0 | 1987.9562 | 1670.4192 | 1328.463 | 0 | 13596.8929 | 11425.0562 | 9086.2006 | 0 | 0 | 0 | 13596.8929 | 11425.0562 | 9086.2006 | 0 | 0 | 0 | 0 | 0.010741 | 0.010741 | 0.010741 | 0 | 5000000 | scaled
68-775 | 61201.6871 | 0 | 61201.6871 | 0 | 0% | 100% | 0% | 9753.0346 | 20303.8501 | 12.462 | 8853.905 | 886.6676 | 25.9433 | 18432.0437 | 1845.8631 | 68 |  | 1087 | 68-775 | 61201.6871 | 51448.6526 | 40897.8371 | 0 | 0 | 0 | 61201.6871 | 51448.6526 | 40897.8371 | 0 | 78.2007 | 65.7387 | 52.2574 | 0 | 0 | 0 | 78.2007 | 65.7387 | 52.2574 | 0 | 5563.9662 | 4677.2986 | 3718.1031 | 0 | 0 | 0 | 5563.9662 | 4677.2986 | 3718.1031 | 0 | 55559.5202 | 46705.6153 | 37127.4766 | 0 | 0 | 0 | 55559.5202 | 46705.6153 | 37127.4766 | 0 | 0 | 0 | 0 | 0.010674 | 0.010674 | 0.010674 | 0 | 5000000 | scaled
69-45F | 106781.3021 | 2878.3579 | 103720.0487 | 182.8955 | 2.696% | 97.13% | 0.1713% | 47590.2379 | 99599.6274 | 234.0974 | 41138.8112 | 6217.3293 | 483.7711 | 86107.2918 | 13008.5645 | 69 |  | 1088 | 69-45F | 106781.3021 | 59191.0642 | 7181.6746 | 2878.3579 | 1497.7309 | 0.014483 | 103720.0487 | 57510.4379 | 6998.7647 | 182.8955 | 492.6774 | 258.58 | 8.9063 | 362.5899 | 186.3881 | 0 | 129.9499 | 72.0543 | 8.7687 | 0.13762 | 13784.5549 | 7567.2256 | 775.9904 | 2514.1664 | 1310.6463 | 4.7e-05 | 11253.7741 | 6239.965 | 759.376 | 16.6143 | 92504.0698 | 51365.2585 | 6396.7779 | 1.6016 | 0.69651 | 0.014436 | 92336.3247 | 51198.4185 | 6230.62 | 166.1435 | 0.0007042 | 0.000305 | 7.8e-06 | 0.007318 | 0.0041712 | 0.0007318 | 0.0002418 | 5000000 | scaled
700-255 | 16403.111 | 14789.9227 | 640.575 | 972.6134 | 90.17% | 3.905% | 5.929% | 3601.0565 | 15129.6033 | 317.7017 | 306.2358 | 2977.1191 | 1366.209 | 716.1063 | 13047.288 | 700 |  | 1089 | 700-255 | 16403.111 | 12802.0545 | 1273.5077 | 14789.9227 | 11476.9084 | 258.1312 | 640.575 | 352.5327 | 42.7631 | 972.6134 | 1392.2389 | 1074.5372 | 26.0298 | 1390.4197 | 1073.2069 | 25.2254 | 1.0873 | 0.59837 | 0.072584 | 0.73186 | 13368.7246 | 10391.6055 | 321.4366 | 13229.2919 | 10275.1415 | 229.6738 | 51.0798 | 28.1112 | 3.41 | 88.3529 | 1642.1476 | 1335.9118 | 926.0412 | 170.211 | 128.5599 | 3.2319 | 588.4079 | 323.8232 | 39.2806 | 883.5287 | 0.0034118 | 0.0025634 | 6.54e-05 | 0.0054346 | 0.003078 | 0.0005434 | 0.0013672 | 5000000 | scaled
700-259F | 1780.4813 | 749.7955 | 402.8595 | 627.8262 | 42.11% | 22.63% | 35.26% | 695.6508 | 1125.7285 | 57.5518 | 144.5812 | 493.5178 | 87.129 | 299.8988 | 738.7007 | 700 |  | 1090 | 700-259F | 1780.4813 | 1084.8305 | 654.7528 | 749.7955 | 235.0828 | 0.04849 | 402.8595 | 221.9215 | 26.8781 | 627.8262 | 87.9033 | 30.3515 | 0.77432 | 82.9058 | 27.3864 | 0 | 4.5251 | 2.4927 | 0.3019 | 0.47242 | 801.224 | 307.7062 | 62.5233 | 661.8879 | 205.3356 | 0 | 82.304 | 45.3385 | 5.4912 | 57.0322 | 891.3539 | 746.7727 | 591.4551 | 5.0018 | 2.3607 | 0.04849 | 316.0305 | 174.0904 | 21.085 | 570.3216 | 0.0012334 | 0.0005862 | 1.44e-05 | 0.0054208 | 0.0030728 | 0.000542 | 0.000887 | 5000000 | scaled
701-48AE | 111352.5883 | 1684.0019 | 107340.1179 | 2328.4685 | 1.512% | 96.4% | 2.091% | 49153.9484 | 102374.6464 | 116.2754 | 44951.5674 | 4086.1056 | 210.9434 | 93796.4966 | 8367.2064 | 701 |  | 1091 | 701-48AE | 111352.5883 | 62198.6399 | 8977.9418 | 1684.0019 | 678.9869 | 10.0499 | 107340.1179 | 59191.1845 | 6639.4235 | 2328.4685 | 220.5614 | 104.286 | 9.6179 | 101.8833 | 37.8232 | 0.14898 | 116.926 | 64.7107 | 7.7169 | 1.7521 | 9127.8892 | 5041.7836 | 760.6828 | 553.9453 | 203.9282 | 0.80244 | 8362.4243 | 4626.3358 | 548.3607 | 211.5197 | 102004.1377 | 57052.5702 | 8207.6411 | 1028.1734 | 437.2356 | 9.0984 | 98860.7675 | 54500.1379 | 6083.3459 | 2115.1967 | 0.0055856 | 0.0024176 | 6.12e-05 | 0.0052888 | 0.0030126 | 0.0005288 | 0.0033092 | 5000000 | scaled
701-738 | 852.4133 | 0 | 852.4133 | 0 | 0% | 100% | 0% | 135.9748 | 283.5954 | 1.764 | 106.4801 | 27.7307 | 3.6791 | 222.0798 | 57.8364 | 701 |  | 1092 | 701-738 | 852.4133 | 716.4386 | 568.818 | 0 | 0 | 0 | 852.4133 | 716.4386 | 568.818 | 0 | 11.0585 | 9.2945 | 7.3794 | 0 | 0 | 0 | 11.0585 | 9.2945 | 7.3794 | 0 | 173.841 | 146.1103 | 116.0046 | 0 | 0 | 0 | 173.841 | 146.1103 | 116.0046 | 0 | 667.5138 | 561.0337 | 445.4339 | 0 | 0 | 0 | 667.5138 | 561.0337 | 445.4339 | 0 | 0 | 0 | 0 | 0.0053432 | 0.0053432 | 0.0053432 | 0 | 5000000 | scaled
702-25 | 105790.0134 | 17943.7358 | 87360.445 | 485.8327 | 16.96% | 82.58% | 0.4592% | 48275.4235 | 99296.1561 | 209.5761 | 43924.7993 | 4141.0481 | 409.5524 | 90373.0181 | 8513.5857 | 702 |  | 1093 | 702-25 | 105790.0134 | 57514.5899 | 6493.8573 | 17943.7358 | 8647.1977 | 243.191 | 87360.445 | 48381.5596 | 5764.8336 | 485.8327 | 421.6334 | 212.0574 | 12.0811 | 320.9584 | 156.1025 | 5.0203 | 100.3095 | 55.5893 | 6.6952 | 0.36557 | 9074.1113 | 4933.0632 | 560.5256 | 1684.0522 | 818.2478 | 26.6457 | 7345.9258 | 4070.6821 | 489.7465 | 44.1334 | 96294.2686 | 52369.4693 | 5921.2506 | 15938.7252 | 7672.8474 | 211.525 | 79914.2097 | 44255.2882 | 5268.3919 | 441.3337 | 0.0025672 | 0.001255 | 3.18e-05 | 0.0052416 | 0.0029882 | 0.0005242 | 0.0007024 | 5000000 | scaled
702-27R | 127298.312 | 18549.7043 | 100564.1383 | 8184.4694 | 14.57% | 79% | 6.429% | 54065.1124 | 112576.2742 | 291.6495 | 48973.7766 | 4799.6863 | 621.0179 | 101835.1169 | 10120.1395 | 702 |  | 1094 | 702-27R | 127298.312 | 73233.1996 | 14722.0377 | 18549.7043 | 9497.9377 | 202.037 | 100564.1383 | 55550.7925 | 6335.5313 | 8184.4694 | 636.7066 | 345.0571 | 15.6887 | 498.9617 | 266.0063 | 0.81348 | 131.5863 | 72.8923 | 8.7167 | 6.1585 | 11395.2358 | 6595.5495 | 1275.0963 | 2649.2087 | 1420.3229 | 4.1383 | 8002.5443 | 4431.7438 | 527.4753 | 743.4828 | 115266.3696 | 66292.593 | 13431.2527 | 15401.5339 | 7811.6085 | 197.0852 | 92430.0077 | 51046.1564 | 5799.3394 | 7434.828 | 0.022589 | 0.010251 | 0.0002916 | 0.005224 | 0.0029778 | 0.0005224 | 0.011525 | 5000000 | scaled
702-30 | 100370.2474 | 67725.6842 | 27093.7815 | 5550.7817 | 67.48% | 26.99% | 5.53% | 41122.0992 | 92225.246 | 4536.8704 | 14118.9896 | 22466.2392 | 10478.6949 | 28894.1169 | 52852.4343 | 702 |  | 1095 | 702-30 | 100370.2474 | 59248.1482 | 8145.0013 | 67725.6842 | 38677.9914 | 786.3256 | 27093.7815 | 15019.3752 | 1807.8941 | 5550.7817 | 10610.9414 | 6074.0709 | 132.2465 | 10571.3209 | 6050.2461 | 125.7047 | 35.4436 | 19.6481 | 2.3651 | 4.1768 | 54114.4042 | 31648.1651 | 1261.97 | 51090.5616 | 29747.1906 | 589.6067 | 2519.6058 | 1396.7377 | 168.1264 | 504.2368 | 35644.9018 | 21525.9122 | 6750.7849 | 6063.8017 | 2880.5547 | 71.0142 | 24538.732 | 13602.9894 | 1637.4026 | 5042.3681 | 0.020083 | 0.0092848 | 0.0002362 | 0.0052802 | 0.0030108 | 0.000528 | 0.0078788 | 5000000 | scaled
702-448F | 367.334 | 330.7207 | 0 | 36.6133 | 90.03% | 0% | 9.967% | 187.9256 | 326.9436 | 0.15607 | 186.9652 | 0.80436 | 0.19036 | 325.7726 | 0.98066 | 702 |  | 1096 | 702-448F | 367.334 | 179.4084 | 40.3904 | 330.7207 | 142.7951 | 3.7771 | 0 | 0 | 0 | 36.6133 | 0.21791 | 0.061839 | 0.02755 | 0.19036 | 0.034289 | 0 | 0 | 0 | 0 | 0.02755 | 4.3066 | 3.5023 | 3.326 | 0.98066 | 0.1763 | 0 | 0 | 0 | 0 | 3.326 | 362.8095 | 175.8443 | 37.0368 | 329.5497 | 142.5845 | 3.7771 | 0 | 0 | 0 | 33.2598 | 6.98e-05 | 3.02e-05 | 8e-07 | 0 | 0 | 0 | 5.16e-05 | 5000000 | scaled
703-279R | 201974.1866 | 67108.931 | 128254.1979 | 6611.0576 | 33.23% | 63.5% | 3.273% | 83190.3925 | 186884.6198 | 606.8306 | 76798.7321 | 5784.8298 | 1334.4873 | 173223.7676 | 12326.365 | 703 |  | 1097 | 703-279R | 201974.1866 | 118783.794 | 15089.5667 | 67108.931 | 41378.3068 | 1024.3351 | 128254.1979 | 70794.4297 | 7454.174 | 6611.0576 | 1362.1555 | 755.3249 | 27.6682 | 1224.0885 | 676.4104 | 13.9808 | 133.0924 | 73.9399 | 8.7128 | 4.9746 | 13585.7457 | 7800.9159 | 1259.3808 | 3398.5384 | 1878.1727 | 38.8661 | 9586.6543 | 5322.1902 | 619.9616 | 600.553 | 187026.2853 | 110227.5532 | 13802.5177 | 62486.3041 | 38823.7237 | 971.4882 | 118534.4512 | 65398.2996 | 6825.4995 | 6005.53 | 0.016556 | 0.007929 | 0.0002 | 0.005173 | 0.0029586 | 0.0005172 | 0.009259 | 5000000 | scaled
712-26 | 495.3102 | 348.9736 | 0 | 146.3366 | 70.46% | 0% | 29.54% | 180.3502 | 343.7923 | 23.5477 | 2.3597 | 154.4429 | 43.9752 | 4.1486 | 295.6686 | 712 |  | 1098 | 712-26 | 495.3102 | 314.96 | 151.5178 | 348.9736 | 168.6234 | 5.1813 | 0 | 0 | 0 | 146.3366 | 44.8553 | 21.3076 | 0.88012 | 44.7452 | 21.1975 | 0.77001 | 0 | 0 | 0 | 0.11011 | 313.3298 | 158.8869 | 17.6612 | 300.0365 | 145.5936 | 4.3679 | 0 | 0 | 0 | 13.2933 | 137.1251 | 134.7654 | 132.9765 | 4.1919 | 1.8323 | 0.043355 | 0 | 0 | 0 | 132.9331 | 0.000338 | 0.0001466 | 3.8e-06 | 0 | 0 | 0 | 0.0002058 | 5000000 | scaled
712-311F | 2276.2199 | 1393.3339 | 0 | 882.886 | 61.21% | 0% | 38.79% | 832.8604 | 1388.0127 | 92.6788 | 185.6245 | 554.5571 | 153.9031 | 321.4103 | 912.6993 | 712 |  | 1099 | 712-311F | 2276.2199 | 1443.3595 | 888.2073 | 1393.3339 | 560.4735 | 5.3213 | 0 | 0 | 0 | 882.886 | 154.9667 | 62.2879 | 1.0636 | 154.3023 | 61.6235 | 0.39925 | 0 | 0 | 0 | 0.66434 | 994.9664 | 440.4093 | 82.2671 | 914.7644 | 360.2073 | 2.0652 | 0 | 0 | 0 | 80.202 | 1126.2868 | 940.6623 | 804.8765 | 324.2672 | 138.6426 | 2.8569 | 0 | 0 | 0 | 802.0197 | 0.0015932 | 0.00069 | 1.72e-05 | 0 | 0 | 0 | 0.0012478 | 5000000 | scaled
713-169 | 565.3511 | 137.9522 | 0 | 427.3989 | 24.4% | 0% | 75.6% | 30.2675 | 137.5928 | 2.036 | 20.803 | 7.4285 | 14.4184 | 37.5593 | 85.6151 | 713 |  | 1100 | 713-169 | 565.3511 | 535.0835 | 427.7583 | 137.9522 | 107.6846 | 0.35942 | 0 | 0 | 0 | 427.3989 | 14.74 | 12.7039 | 0.3216 | 14.4184 | 12.3823 | 0 | 0 | 0 | 0 | 0.3216 | 124.4403 | 117.0118 | 38.8252 | 85.6151 | 78.1865 | 0 | 0 | 0 | 0 | 38.8252 | 426.1708 | 405.3678 | 388.6115 | 37.9187 | 17.1158 | 0.35942 | 0 | 0 | 0 | 388.2521 | 0.0008722 | 0.0004334 | 1.1e-05 | 0 | 0 | 0 | 0.0005994 | 5000000 | scaled
714-549F | 53275.0703 | 52245.3331 | 0 | 1029.7372 | 98.07% | 0% | 1.933% | 19383.7818 | 51435.1761 | 2409.5155 | 49.9406 | 16924.3257 | 6151.5709 | 117.9198 | 45165.6854 | 714 |  | 1101 | 714-549F | 53275.0703 | 33891.2884 | 1839.8941 | 52245.3331 | 32861.5512 | 810.1569 | 0 | 0 | 0 | 1029.7372 | 6257.5629 | 3848.0475 | 105.992 | 6256.7881 | 3847.2726 | 105.2172 | 0 | 0 | 0 | 0.77484 | 45962.4802 | 29038.1545 | 796.7948 | 45868.9382 | 28944.6124 | 703.2528 | 0 | 0 | 0 | 93.542 | 1055.0272 | 1005.0865 | 937.1073 | 119.6068 | 69.6662 | 1.687 | 0 | 0 | 0 | 935.4203 | 0.005355 | 0.0032406 | 8.22e-05 | 0 | 0 | 0 | 0.0014298 | 5000000 | scaled
718-483R | 8218.105 | 5648.4085 | 0 | 2569.6966 | 68.73% | 0% | 31.27% | 3082.884 | 5567.6398 | 558.9239 | 534.8872 | 1989.0728 | 996.7145 | 1028.5408 | 3542.3844 | 718 |  | 1102 | 718-483R | 8218.105 | 5135.2211 | 2650.4653 | 5648.4085 | 2565.5245 | 80.7687 | 0 | 0 | 0 | 2569.6966 | 1013.3945 | 454.4705 | 16.68 | 1011.4609 | 452.5369 | 14.7464 | 0 | 0 | 0 | 1.9336 | 3828.932 | 1839.8592 | 286.5475 | 3595.499 | 1606.4262 | 53.1145 | 0 | 0 | 0 | 233.433 | 3375.7786 | 2840.8914 | 2347.2378 | 1041.4487 | 506.5614 | 12.9078 | 0 | 0 | 0 | 2334.33 | 0.0094944 | 0.0043538 | 0.000111 | 0 | 0 | 0 | 0.0036786 | 5000000 | scaled
719-20AE | 256.4267 | 5.9033 | 0 | 250.5235 | 2.302% | 0% | 97.7% | 3.3518 | 5.8425 | 0 | 3.3518 | 0 | 0 | 5.8425 | 0 | 719 |  | 1103 | 719-20AE | 256.4267 | 253.0749 | 250.5842 | 5.9033 | 2.5515 | 0.060706 | 0 | 0 | 0 | 250.5235 | 0.18851 | 0.18851 | 0.18851 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18851 | 22.7577 | 22.7577 | 22.7577 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7577 | 233.4805 | 230.1287 | 227.6379 | 5.9033 | 2.5515 | 0.060706 | 0 | 0 | 0 | 227.5772 | 0.000537 | 0.0002322 | 5.6e-06 | 0 | 0 | 0 | 0.0003492 | 5000000 | scaled
719-21AE | 2756.944 | 1116.1923 | 0 | 1640.7517 | 40.49% | 0% | 59.51% | 632.638 | 1104.0264 | 0 | 632.638 | 0 | 0 | 1104.0264 | 0 | 719 |  | 1104 | 719-21AE | 2756.944 | 2124.306 | 1652.9176 | 1116.1923 | 483.5543 | 12.1659 | 0 | 0 | 0 | 1640.7517 | 1.2346 | 1.2346 | 1.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2346 | 149.047 | 149.047 | 149.047 | 0 | 0 | 0 | 0 | 0 | 0 | 149.047 | 2606.6624 | 1974.0244 | 1502.636 | 1116.1923 | 483.5543 | 12.1659 | 0 | 0 | 0 | 1490.4701 | 0.0041472 | 0.0017964 | 4.56e-05 | 0 | 0 | 0 | 0.0022718 | 5000000 | scaled
719-28 | 191.0096 | 155.5319 | 0 | 35.4777 | 81.43% | 0% | 18.57% | 88.551 | 153.2613 | 0 | 88.551 | 0 | 0 | 153.2613 | 0 | 719 |  | 1105 | 719-28 | 191.0096 | 102.4586 | 37.7483 | 155.5319 | 66.9809 | 2.2705 | 0 | 0 | 0 | 35.4777 | 0.026696 | 0.026696 | 0.026696 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026696 | 3.2228 | 3.2228 | 3.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2228 | 187.7601 | 99.2091 | 34.4987 | 155.5319 | 66.9809 | 2.2705 | 0 | 0 | 0 | 32.2282 | 2.74e-05 | 1.18e-05 | 4e-07 | 0 | 0 | 0 | 4.84e-05 | 5000000 | scaled
719-33 | 4049.8609 | 1028.1292 | 0 | 3021.7317 | 25.39% | 0% | 74.61% | 558.3492 | 1016.252 | 0 | 558.3492 | 0 | 0 | 1016.252 | 0 | 719 |  | 1106 | 719-33 | 4049.8609 | 3491.5118 | 3033.6089 | 1028.1292 | 469.78 | 11.8772 | 0 | 0 | 0 | 3021.7317 | 2.2738 | 2.2738 | 2.2738 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2738 | 274.4962 | 274.4962 | 274.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 274.4962 | 3773.091 | 3214.7418 | 2756.839 | 1028.1292 | 469.78 | 11.8772 | 0 | 0 | 0 | 2744.9618 | 0.0087052 | 0.0038378 | 9.72e-05 | 0 | 0 | 0 | 0.0042502 | 5000000 | scaled
719-856F | 512.6964 | 46.4061 | 0 | 466.2903 | 9.051% | 0% | 90.95% | 26.3385 | 45.8649 | 0 | 26.3385 | 0 | 0 | 45.8649 | 0 | 719 |  | 1107 | 719-856F | 512.6964 | 486.358 | 466.8315 | 46.4061 | 20.0676 | 0.54117 | 0 | 0 | 0 | 466.2903 | 0.35087 | 0.35087 | 0.35087 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35087 | 42.3581 | 42.3581 | 42.3581 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3581 | 469.9874 | 443.649 | 424.1225 | 46.4061 | 20.0676 | 0.54117 | 0 | 0 | 0 | 423.5813 | 0.001246 | 0.0005396 | 1.38e-05 | 0 | 0 | 0 | 0.0006524 | 5000000 | scaled
719-857F | 299.0521 | 55.7829 | 0 | 243.2692 | 18.65% | 0% | 81.35% | 31.6298 | 55.1696 | 0 | 31.6298 | 0 | 0 | 55.1696 | 0 | 719 |  | 1108 | 719-857F | 299.0521 | 267.4222 | 243.8825 | 55.7829 | 24.1531 | 0.61335 | 0 | 0 | 0 | 243.2692 | 0.18305 | 0.18305 | 0.18305 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18305 | 22.0987 | 22.0987 | 22.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0987 | 276.7703 | 245.1404 | 221.6007 | 55.7829 | 24.1531 | 0.61335 | 0 | 0 | 0 | 220.9874 | 0.0006748 | 0.0002922 | 7.4e-06 | 0 | 0 | 0 | 0.0003438 | 5000000 | scaled
72-12F | 358.8798 | 132.4876 | 0 | 226.3923 | 36.92% | 0% | 63.08% | 76.6085 | 131.3771 | 3.5307 | 54.9849 | 18.0929 | 5.8553 | 95.5296 | 29.9922 | 72 |  | 1109 | 72-12F | 358.8798 | 282.2713 | 227.5027 | 132.4876 | 55.8791 | 1.1105 | 0 | 0 | 0 | 226.3923 | 6.0257 | 2.4949 | 0.17035 | 5.8553 | 2.3246 | 0 | 0 | 0 | 0 | 0.17035 | 50.5579 | 32.465 | 20.5656 | 29.9922 | 11.8994 | 0 | 0 | 0 | 0 | 20.5656 | 302.2963 | 247.3114 | 206.7667 | 96.64 | 41.6552 | 1.1105 | 0 | 0 | 0 | 205.6563 | 0.0004242 | 0.0001836 | 4.8e-06 | 0 | 0 | 0 | 0.0002952 | 5000000 | scaled
72-16 | 6344.5295 | 2894.9267 | 0 | 3449.6028 | 45.63% | 0% | 54.37% | 1639.2847 | 2854.5988 | 36.5233 | 1506.4598 | 96.3016 | 61.9829 | 2629.1799 | 163.4359 | 72 |  | 1110 | 72-16 | 6344.5295 | 4705.2448 | 3489.9307 | 2894.9267 | 1255.642 | 40.328 | 0 | 0 | 0 | 3449.6028 | 67.6148 | 31.0915 | 5.6319 | 65.0191 | 28.4958 | 3.0361 | 0 | 0 | 0 | 2.5957 | 484.8126 | 388.511 | 321.3766 | 171.4483 | 75.1467 | 8.0124 | 0 | 0 | 0 | 313.3643 | 5792.1022 | 4285.6424 | 3162.9223 | 2658.4594 | 1151.9996 | 29.2795 | 0 | 0 | 0 | 3133.6428 | 0.0080916 | 0.0035034 | 8.86e-05 | 0 | 0 | 0 | 0.0048538 | 5000000 | scaled
723-377 | 117.6652 | 43.5243 | 0 | 74.1409 | 36.99% | 0% | 63.01% | 25.0076 | 43.0764 | 0.2822 | 23.2847 | 1.4407 | 0.40319 | 40.6146 | 2.0585 | 723 |  | 1111 | 723-377 | 117.6652 | 92.6576 | 74.5888 | 43.5243 | 18.5167 | 0.44789 | 0 | 0 | 0 | 74.1409 | 0.45898 | 0.17679 | 0.055789 | 0.40319 | 0.121 | 0 | 0 | 0 | 0 | 0.055789 | 8.7936 | 7.3529 | 6.735 | 2.0585 | 0.61785 | 0 | 0 | 0 | 0 | 6.735 | 108.4127 | 85.128 | 67.798 | 41.0625 | 17.7779 | 0.44789 | 0 | 0 | 0 | 67.3501 | 0.0001834 | 7.94e-05 | 2e-06 | 0 | 0 | 0 | 9.82e-05 | 5000000 | scaled
723-792F | 194.7415 | 80.0548 | 0 | 114.6867 | 41.11% | 0% | 58.89% | 41.9272 | 79.8956 | 5.2695 | 9.2416 | 27.4161 | 10.0623 | 16.4522 | 53.3811 | 723 |  | 1112 | 723-792F | 194.7415 | 152.8143 | 114.8459 | 80.0548 | 38.1276 | 0.15917 | 0 | 0 | 0 | 114.6867 | 10.1486 | 4.8792 | 0.086298 | 10.0623 | 4.7929 | 0 | 0 | 0 | 0 | 0.086298 | 63.7993 | 36.3832 | 10.4182 | 53.3811 | 25.965 | 0 | 0 | 0 | 0 | 10.4182 | 120.7935 | 111.5519 | 104.3413 | 16.6114 | 7.3697 | 0.15917 | 0 | 0 | 0 | 104.1822 | 0.0004002 | 0.0001732 | 4.2e-06 | 0 | 0 | 0 | 0.000152 | 5000000 | scaled
723-793F | 153.6541 | 81.2529 | 0 | 72.4012 | 52.88% | 0% | 47.12% | 48.2224 | 81.2448 | 7.8242 | 0.41828 | 39.9799 | 13.1796 | 0.72958 | 67.3356 | 723 |  | 1113 | 723-793F | 153.6541 | 105.4317 | 72.4094 | 81.2529 | 33.0305 | 0.0081434 | 0 | 0 | 0 | 72.4012 | 13.2341 | 5.4099 | 0.05448 | 13.1796 | 5.3554 | 0 | 0 | 0 | 0 | 0.05448 | 73.9125 | 33.9327 | 6.577 | 67.3356 | 27.3557 | 0 | 0 | 0 | 0 | 6.577 | 66.5075 | 66.0892 | 65.7779 | 0.73772 | 0.31944 | 0.0081434 | 0 | 0 | 0 | 65.7698 | 0.0003986 | 0.0001726 | 4.4e-06 | 0 | 0 | 0 | 0.0001008 | 5000000 | scaled
728-1570F | 33280.7317 | 33209.7385 | 0 | 70.9931 | 99.79% | 0% | 0.2133% | 21621.3574 | 31919.6675 | 2490.2967 | 0.38425 | 19130.6765 | 3729.0707 | 0.66596 | 28189.9308 | 728 |  | 1114 | 728-1570F | 33280.7317 | 11659.3742 | 1361.0642 | 33209.7385 | 11588.3811 | 1290.0711 | 0 | 0 | 0 | 70.9931 | 3878.6734 | 1388.3767 | 149.6027 | 3878.62 | 1388.3233 | 149.5493 | 0 | 0 | 0 | 0.05342 | 29336.8942 | 10206.2177 | 1146.9634 | 29330.4451 | 10199.7686 | 1140.5143 | 0 | 0 | 0 | 6.4491 | 65.1641 | 64.7798 | 64.4981 | 0.67342 | 0.28917 | 0.0074582 | 0 | 0 | 0 | 64.4906 | 0.0002532 | 0.0001096 | 2.8e-06 | 0 | 0 | 0 | 9.4e-05 | 5000000 | scaled
73-1130R | 6201607.0003 | 6033465.8455 | 161292.1004 | 6849.0543 | 97.29% | 2.601% | 0.1104% | 716357.0504 | 6063895.6923 | 37782.8875 | 64090.2192 | 614483.9437 | 345019.2174 | 134493.2795 | 5584383.1954 | 73 |  | 1115 | 73-1130R | 6201607.0003 | 5485249.9499 | 137711.3079 | 6033465.8455 | 5387214.8782 | 115729.4787 | 161292.1004 | 91186.0173 | 15132.775 | 6849.0543 | 351843.7419 | 314060.8545 | 6824.5245 | 351599.6992 | 313920.6456 | 6796.9578 | 238.889 | 135.0552 | 22.4131 | 5.1537 | 5695241.1291 | 5080757.1854 | 110857.9337 | 5680404.557 | 5072098.9435 | 108902.1351 | 14214.3993 | 8036.0691 | 1333.6258 | 622.1728 | 154522.1292 | 90431.91 | 20028.8497 | 1461.5893 | 1195.2891 | 30.3858 | 146838.8121 | 83014.893 | 13776.7361 | 6221.7278 | 0.030024 | 0.026664 | 0.0006772 | 0.1785 | 0.10145 | 0.01785 | 0.0096778 | 5000000 | scaled
73-1163 | 15337184.9109 | 15116478.9066 | 213658.0418 | 7047.9625 | 98.56% | 1.393% | 0.04595% | 5390936.1337 | 14992746.9593 | 304495.3676 | 89308.9042 | 4997131.8618 | 850115.6637 | 194153.4486 | 13948477.847 | 73 |  | 1116 | 73-1163 | 15337184.9109 | 9946248.7773 | 344437.9516 | 15116478.9066 | 9818415.9495 | 317340.0961 | 213658.0418 | 120784.8653 | 20049.893 | 7047.9625 | 868341.7581 | 563846.3905 | 18226.0944 | 868032.3149 | 563669.1512 | 18192.2503 | 304.1398 | 171.9359 | 28.5408 | 5.3034 | 14249896.1946 | 9252764.3328 | 301418.3476 | 14227975.9135 | 9240094.089 | 298781.1648 | 21280.0393 | 12030.0021 | 1996.941 | 640.2417 | 218946.9583 | 129638.054 | 24793.5096 | 20470.6782 | 14652.7094 | 366.6811 | 192073.8627 | 108582.9273 | 18024.4112 | 6402.4174 | 0.035859 | 0.023139 | 0.0005876 | 0.17934 | 0.10192 | 0.017934 | 0.0098612 | 5000000 | scaled
73-1164 | 2448829.3435 | 2415513.2252 | 32259.2117 | 1056.9066 | 98.64% | 1.317% | 0.04316% | 873945.3149 | 2393282.5751 | 42547.1385 | 12575.3057 | 818822.8708 | 116752.8586 | 26221.5311 | 2250308.1855 | 73 |  | 1117 | 73-1164 | 2448829.3435 | 1574884.0286 | 55546.7684 | 2415513.2252 | 1555594.6386 | 51461.4054 | 32259.2117 | 18232.4833 | 3028.4563 | 1056.9066 | 119275.6291 | 76728.4906 | 2522.7705 | 119151.6543 | 76658.0759 | 2510.4113 | 123.1795 | 69.6194 | 11.5639 | 0.79529 | 2299659.5135 | 1480836.6427 | 49351.328 | 2296312.9681 | 1478903.4727 | 48950.1615 | 3250.5352 | 1837.1599 | 305.1564 | 96.0101 | 29894.2009 | 17318.8952 | 3672.6699 | 48.6027 | 33.09 | 0.83264 | 28885.497 | 16325.704 | 2711.736 | 960.1012 | 0.0038056 | 0.0024444 | 6.18e-05 | 0.18088 | 0.10276 | 0.018088 | 0.0014608 | 5000000 | scaled
73-1165 | 24708.4857 | 0 | 24708.4857 | 0 | 0% | 100% | 0% | 723.7381 | 1509.1281 | 0.96327 | 660.0214 | 62.7534 | 2.0086 | 1376.267 | 130.8525 | 73 |  | 1118 | 73-1165 | 24708.4857 | 23984.7476 | 23199.3576 | 0 | 0 | 0 | 24708.4857 | 23984.7476 | 23199.3576 | 0 | 32.8861 | 31.9229 | 30.8775 | 0 | 0 | 0 | 32.8861 | 31.9229 | 30.8775 | 0 | 2142.4072 | 2079.6538 | 2011.5547 | 0 | 0 | 0 | 2142.4072 | 2079.6538 | 2011.5547 | 0 | 22533.1924 | 21873.171 | 21156.9254 | 0 | 0 | 0 | 22533.1924 | 21873.171 | 21156.9254 | 0 | 0 | 0 | 0 | 0.18144 | 0.18144 | 0.18144 | 0 | 5000000 | scaled
73-1218 | 1359.1976 | 0 | 1359.1976 | 0 | 0% | 100% | 0% | 39.7165 | 82.8084 | 0.026084 | 31.4896 | 8.2008 | 0.054385 | 65.6553 | 17.0987 | 73 |  | 1119 | 73-1218 | 1359.1976 | 1319.4811 | 1276.3892 | 0 | 0 | 0 | 1359.1976 | 1319.4811 | 1276.3892 | 0 | 0.89266 | 0.86658 | 0.83827 | 0 | 0 | 0 | 0.89266 | 0.86658 | 0.83827 | 0 | 280.6534 | 272.4526 | 263.5548 | 0 | 0 | 0 | 280.6534 | 272.4526 | 263.5548 | 0 | 1077.6515 | 1046.1619 | 1011.9961 | 0 | 0 | 0 | 1077.6515 | 1046.1619 | 1011.9961 | 0 | 0 | 0 | 0 | 0.18226 | 0.18226 | 0.18226 | 0 | 5000000 | scaled
73-23R | 5733790.742 | 5642495.3869 | 86266.6494 | 5028.7057 | 98.41% | 1.505% | 0.0877% | 654717.9583 | 5589671.7973 | 38189.1407 | 33830.4661 | 582698.3514 | 340804.6664 | 72448.062 | 5176419.069 | 73 |  | 1120 | 73-23R | 5733790.742 | 5079072.7837 | 144118.9447 | 5642495.3869 | 5025273.1006 | 130991.4193 | 86266.6494 | 48770.9775 | 8098.8197 | 5028.7057 | 348910.2852 | 310721.1444 | 8105.6188 | 348750.1429 | 310628.9631 | 8087.1558 | 156.3583 | 88.3974 | 14.6791 | 3.7839 | 5300644.8059 | 4717946.4545 | 124225.7369 | 5290225.7959 | 4711857.4996 | 122833.6623 | 9962.1989 | 5632.1438 | 935.2635 | 456.8111 | 84235.6509 | 50405.1848 | 11787.5889 | 3519.448 | 2786.6379 | 70.6012 | 76148.0922 | 43050.4363 | 7148.877 | 4568.1107 | 0.025077 | 0.022267 | 0.0005652 | 0.18133 | 0.10305 | 0.018133 | 0.0070806 | 5000000 | scaled
73-678R | 10591376.886 | 10412424.065 | 170038.0398 | 8914.7812 | 98.31% | 1.605% | 0.08417% | 4660778.2205 | 10424434.458 | 283717.1949 | 68281.5005 | 4308779.5251 | 634224.2885 | 145339.3283 | 9644870.8412 | 73 |  | 1121 | 73-678R | 10591376.886 | 5930598.6656 | 166942.428 | 10412424.065 | 5825574.6898 | 142069.9947 | 170038.0398 | 96109.1946 | 15957.6521 | 8914.7812 | 642998.21 | 359281.0152 | 8773.9215 | 642786.9722 | 359158.7024 | 8748.0188 | 204.5298 | 115.6047 | 19.1946 | 6.7081 | 9780465.5233 | 5471685.9983 | 135594.6821 | 9762674.8704 | 5461278.2404 | 133191.2483 | 16980.8281 | 9597.933 | 1593.609 | 809.8248 | 167913.1527 | 99631.6521 | 22573.8244 | 6962.2225 | 5137.7469 | 130.7276 | 152852.6819 | 86395.6569 | 14344.8485 | 8098.2483 | 0.044606 | 0.024902 | 0.0006326 | 0.18066 | 0.10264 | 0.018066 | 0.012491 | 5000000 | scaled
73-683R | 9288032.8798 | 9142043.2186 | 138780.9856 | 7208.6755 | 98.43% | 1.494% | 0.07761% | 3235652.472 | 9129519.2194 | 176734.0017 | 55663.3891 | 3003255.0811 | 501976.5645 | 120402.0591 | 8507140.5959 | 73 |  | 1122 | 73-683R | 9288032.8798 | 6052380.4078 | 158513.6604 | 9142043.2186 | 5966682.3133 | 138278.7645 | 138780.9856 | 78489.419 | 13026.2204 | 7208.6755 | 509758.7852 | 333024.7835 | 7782.2208 | 509513.7687 | 332883.8547 | 7754.3079 | 239.5923 | 135.5046 | 22.4885 | 5.4243 | 8639588.9001 | 5636333.819 | 132448.3043 | 8623589.4375 | 5627000.6246 | 130353.1908 | 15344.6216 | 8678.3534 | 1440.2724 | 654.841 | 138685.1944 | 83021.8053 | 18283.1354 | 8940.0124 | 6797.834 | 171.2657 | 123196.7718 | 69675.5611 | 11563.4594 | 6548.4102 | 0.035917 | 0.023408 | 0.0005936 | 0.18109 | 0.10295 | 0.018109 | 0.010155 | 5000000 | scaled
730-1079 | 24915.2225 | 16729.3145 | 0 | 8185.908 | 67.14% | 0% | 32.86% | 9588.1638 | 16517.7059 | 595.9847 | 6988.5061 | 2003.673 | 869.506 | 12763.5691 | 2884.6309 | 730 |  | 1123 | 730-1079 | 24915.2225 | 15327.0587 | 8397.5166 | 16729.3145 | 7141.1507 | 211.6086 | 0 | 0 | 0 | 8185.908 | 888.5871 | 292.6024 | 19.0811 | 882.4275 | 286.4428 | 12.9215 | 0 | 0 | 0 | 6.1596 | 3670.6606 | 1666.9876 | 786.0297 | 2927.0471 | 923.3741 | 42.4163 | 0 | 0 | 0 | 743.6135 | 20355.9748 | 13367.4687 | 7592.4057 | 12919.8399 | 5931.3338 | 156.2708 | 0 | 0 | 0 | 7436.1349 | 0.027865 | 0.01278 | 0.0003236 | 0 | 0 | 0 | 0.011588 | 5000000 | scaled
730-835 | 55259.9191 | 52123.173 | 0 | 3136.7461 | 94.32% | 0% | 5.676% | 29765.6669 | 51202.8508 | 1689.8479 | 20976.4976 | 7099.3213 | 2889.947 | 36230.4768 | 12082.4271 | 730 |  | 1124 | 730-835 | 55259.9191 | 25494.2522 | 4057.0682 | 52123.173 | 22357.5062 | 920.3222 | 0 | 0 | 0 | 3136.7461 | 2969.7658 | 1279.9179 | 79.8188 | 2967.4055 | 1277.5576 | 77.4585 | 0 | 0 | 0 | 2.3603 | 12730.2976 | 5630.9763 | 647.8705 | 12445.3535 | 5346.0321 | 362.9263 | 0 | 0 | 0 | 284.9442 | 39559.8557 | 18583.3581 | 3329.3789 | 36710.4141 | 15733.9165 | 479.9373 | 0 | 0 | 0 | 2849.4416 | 0.0094356 | 0.0040856 | 0.0001038 | 0 | 0 | 0 | 0.004384 | 5000000 | scaled
730-971R | 26513.6816 | 21180.7332 | 0 | 5332.9485 | 79.89% | 0% | 20.11% | 11464.4183 | 21002.1683 | 421.5375 | 8787.938 | 2254.9428 | 769.2704 | 16119.0689 | 4113.829 | 730 |  | 1125 | 730-971R | 26513.6816 | 15049.2633 | 5511.5133 | 21180.7332 | 9716.3149 | 178.5649 | 0 | 0 | 0 | 5332.9485 | 776.8383 | 355.3008 | 7.5679 | 772.8254 | 351.2879 | 3.555 | 0 | 0 | 0 | 4.0129 | 4616.5345 | 2361.5917 | 502.7055 | 4132.0858 | 1877.143 | 18.2568 | 0 | 0 | 0 | 484.4487 | 21120.3089 | 12332.3709 | 5001.24 | 16275.822 | 7487.884 | 156.7531 | 0 | 0 | 0 | 4844.4869 | 0.014973 | 0.0065556 | 0.0001662 | 0 | 0 | 0 | 0.0075362 | 5000000 | scaled
731-1245F | 1723.0987 | 1401.8197 | 0 | 321.279 | 81.35% | 0% | 18.65% | 617.963 | 1392.1784 | 68.7338 | 8.3329 | 540.8963 | 146.5914 | 14.6729 | 1230.9141 | 731 |  | 1126 | 731-1245F | 1723.0987 | 1105.1357 | 330.9203 | 1401.8197 | 783.8567 | 9.6413 | 0 | 0 | 0 | 321.279 | 148.1136 | 79.3798 | 1.5222 | 147.8718 | 79.138 | 1.2804 | 0 | 0 | 0 | 0.24175 | 1268.3126 | 727.4162 | 37.3985 | 1239.1274 | 698.231 | 8.2133 | 0 | 0 | 0 | 29.1852 | 306.6726 | 298.3397 | 291.9996 | 14.8206 | 6.4876 | 0.14761 | 0 | 0 | 0 | 291.852 | 0.00089 | 0.0003854 | 9.6e-06 | 0 | 0 | 0 | 0.0004512 | 5000000 | scaled
731-1247F | 26881.6091 | 21657.9185 | 0 | 5223.6906 | 80.57% | 0% | 19.43% | 11953.1387 | 21542.8881 | 1056.9331 | 3852.5361 | 7043.6695 | 1875.9084 | 7344.5941 | 12322.3857 | 731 |  | 1127 | 731-1247F | 26881.6091 | 14928.4704 | 5338.721 | 21657.9185 | 9704.7798 | 115.0304 | 0 | 0 | 0 | 5223.6906 | 1886.5081 | 829.575 | 10.5997 | 1882.5774 | 825.6443 | 6.6691 | 0 | 0 | 0 | 3.9307 | 12833.188 | 5789.5185 | 510.8023 | 12358.6644 | 5314.9948 | 36.2787 | 0 | 0 | 0 | 474.5236 | 12161.913 | 8309.3769 | 4817.3189 | 7416.6767 | 3564.1406 | 72.0826 | 0 | 0 | 0 | 4745.2363 | 0.01604 | 0.0070044 | 0.0001766 | 0 | 0 | 0 | 0.0073396 | 5000000 | scaled
731-49F | 102830.3529 | 92258.0974 | 0 | 10572.2555 | 89.72% | 0% | 10.28% | 50431.868 | 90519.3675 | 4280.4514 | 10081.5738 | 36069.8429 | 7707.1265 | 18151.9248 | 64660.3163 | 731 |  | 1128 | 731-49F | 102830.3529 | 52398.4849 | 12310.9854 | 92258.0974 | 41826.2294 | 1738.7299 | 0 | 0 | 0 | 10572.2555 | 7863.0034 | 3582.552 | 155.8769 | 7855.0481 | 3574.5967 | 147.9216 | 0 | 0 | 0 | 7.9553 | 67009.0918 | 30939.249 | 2348.7756 | 66048.7009 | 29978.858 | 1388.3846 | 0 | 0 | 0 | 960.3909 | 27958.2577 | 17876.6839 | 9806.3329 | 18354.3485 | 8272.7746 | 202.4236 | 0 | 0 | 0 | 9603.9093 | 0.031423 | 0.013686 | 0.0003476 | 0 | 0 | 0 | 0.014849 | 5000000 | scaled
732-15R | 342637.313 | 338981.0181 | 0 | 3656.2949 | 98.93% | 0% | 1.067% | 189638.7331 | 335888.4242 | 23764.4896 | 1790.2664 | 164083.977 | 42073.8121 | 3342.0289 | 290472.5831 | 732 |  | 1129 | 732-15R | 342637.313 | 152998.5799 | 6748.8888 | 338981.0181 | 149342.285 | 3092.5939 | 0 | 0 | 0 | 3656.2949 | 42465.6791 | 18701.1894 | 391.8669 | 42462.9278 | 18698.4382 | 389.1157 | 0 | 0 | 0 | 2.7512 | 293467.3586 | 129383.3815 | 2994.7755 | 293135.2183 | 129051.2412 | 2662.6351 | 0 | 0 | 0 | 332.1403 | 6704.2753 | 4914.0089 | 3362.2464 | 3382.872 | 1592.6056 | 40.8431 | 0 | 0 | 0 | 3321.4033 | 0.015834 | 0.0068766 | 0.000174 | 0 | 0 | 0 | 0.005126 | 5000000 | scaled
733-20AE | 39729.3937 | 33799.2644 | 0 | 5930.1294 | 85.07% | 0% | 14.93% | 18519.6554 | 33465.7599 | 2112.6508 | 9507.8485 | 6899.156 | 3624.3009 | 18130.6142 | 11710.8448 | 733 |  | 1130 | 733-20AE | 39729.3937 | 21209.7383 | 6263.6338 | 33799.2644 | 15279.6089 | 333.5044 | 0 | 0 | 0 | 5930.1294 | 3655.0329 | 1542.3821 | 30.732 | 3650.5707 | 1537.9198 | 26.2698 | 0 | 0 | 0 | 4.4622 | 12331.627 | 5432.471 | 620.7822 | 11792.93 | 4893.774 | 82.0852 | 0 | 0 | 0 | 538.697 | 23742.7338 | 14234.8853 | 5612.1196 | 18355.7637 | 8847.9151 | 225.1495 | 0 | 0 | 0 | 5386.9701 | 0.017691 | 0.007796 | 0.0001988 | 0 | 0 | 0 | 0.0083956 | 5000000 | scaled
733-23R | 18173.0076 | 7921.379 | 0 | 10251.6286 | 43.59% | 0% | 56.41% | 4437.6832 | 7839.9858 | 94.8809 | 3856.2232 | 486.5792 | 169.556 | 6800.4469 | 869.9829 | 733 |  | 1131 | 733-23R | 18173.0076 | 13735.3244 | 10333.0218 | 7921.379 | 3483.6958 | 81.3933 | 0 | 0 | 0 | 10251.6286 | 178.3934 | 83.5125 | 8.8374 | 170.6793 | 75.7985 | 1.1234 | 0 | 0 | 0 | 7.714 | 1807.001 | 1320.4218 | 937.0181 | 875.736 | 389.1569 | 5.7531 | 0 | 0 | 0 | 931.265 | 16187.6132 | 12331.3901 | 9387.1663 | 6874.9637 | 3018.7405 | 74.5168 | 0 | 0 | 0 | 9312.6496 | 0.025203 | 0.010942 | 0.0002792 | 0 | 0 | 0 | 0.014483 | 5000000 | scaled
74-24R | 13763.1684 | 8385.2878 | 0 | 5377.8806 | 60.93% | 0% | 39.07% | 4027.2412 | 8274.0208 | 15.7235 | 3930.7794 | 80.7383 | 22.882 | 8133.5973 | 117.5415 | 74 |  | 1132 | 74-24R | 13763.1684 | 9735.9273 | 5489.1476 | 8385.2878 | 4358.0467 | 111.267 | 0 | 0 | 0 | 5377.8806 | 27.2381 | 11.5146 | 4.3561 | 23.1914 | 7.4679 | 0.30939 | 0 | 0 | 0 | 4.0467 | 607.6602 | 526.9219 | 490.1186 | 119.1298 | 38.3915 | 1.5883 | 0 | 0 | 0 | 488.5304 | 13128.2702 | 9197.4908 | 4994.6729 | 8242.9666 | 4312.1872 | 109.3693 | 0 | 0 | 0 | 4885.3036 | 0.015304 | 0.0070004 | 0.000178 | 0 | 0 | 0 | 0.0075712 | 5000000 | scaled
74-35R | 50929.5437 | 49730.0983 | 0 | 1199.4454 | 97.64% | 0% | 2.355% | 22244.1741 | 48082.9014 | 1851.4055 | 239.6098 | 20153.1588 | 3924.2096 | 463.1495 | 43695.5424 | 74 |  | 1133 | 74-35R | 50929.5437 | 28685.3696 | 2846.6423 | 49730.0983 | 27485.9242 | 1647.1969 | 0 | 0 | 0 | 1199.4454 | 4053.5731 | 2202.1676 | 129.3635 | 4052.6706 | 2201.265 | 128.461 | 0 | 0 | 0 | 0.90254 | 45317.6657 | 25164.5068 | 1622.1233 | 45208.7072 | 25055.5484 | 1513.1649 | 0 | 0 | 0 | 108.9584 | 1558.305 | 1318.6952 | 1095.1555 | 468.7206 | 229.1108 | 5.5711 | 0 | 0 | 0 | 1089.5844 | 0.005494 | 0.0026988 | 6.88e-05 | 0 | 0 | 0 | 0.0016164 | 5000000 | scaled
740-856F | 2976.7528 | 1013.6519 | 0 | 1963.1009 | 34.05% | 0% | 65.95% | 588.8785 | 1004.3749 | 19.9995 | 466.8092 | 102.0698 | 31.251 | 813.6586 | 159.4653 | 740 |  | 1134 | 740-856F | 2976.7528 | 2387.8743 | 1972.3779 | 1013.6519 | 424.7733 | 9.277 | 0 | 0 | 0 | 1963.1009 | 32.7515 | 12.7519 | 1.5004 | 31.2743 | 11.2748 | 0.023254 | 0 | 0 | 0 | 1.4772 | 337.9137 | 235.8439 | 178.4484 | 159.5842 | 57.5144 | 0.11899 | 0 | 0 | 0 | 178.3294 | 2606.0877 | 2139.2785 | 1792.429 | 822.7933 | 355.9842 | 9.1347 | 0 | 0 | 0 | 1783.2943 | 0.0050724 | 0.002197 | 5.64e-05 | 0 | 0 | 0 | 0.0027664 | 5000000 | scaled
740-857F | 392.0015 | 79.9534 | 0 | 312.0481 | 20.4% | 0% | 79.6% | 27.7627 | 76.3269 | 3.2209 | 7.7274 | 16.8145 | 10.1305 | 13.4552 | 52.7412 | 740 |  | 1135 | 740-857F | 392.0015 | 364.2388 | 315.6746 | 79.9534 | 52.1907 | 3.6265 | 0 | 0 | 0 | 312.0481 | 10.9198 | 7.6989 | 0.78925 | 10.685 | 7.4641 | 0.55444 | 0 | 0 | 0 | 0.23481 | 84.0059 | 67.1915 | 31.2647 | 55.6593 | 38.8448 | 2.9181 | 0 | 0 | 0 | 28.3467 | 297.0758 | 289.3484 | 283.6206 | 13.6092 | 5.8818 | 0.154 | 0 | 0 | 0 | 283.4666 | 0.0005684 | 0.000246 | 6.4e-06 | 0 | 0 | 0 | 0.0004538 | 5000000 | scaled
741-17 | 863.0723 | 411.7056 | 0 | 451.3667 | 47.7% | 0% | 52.3% | 233.4435 | 407.012 | 0.050054 | 233.124 | 0.26942 | 0.12967 | 406.1939 | 0.68846 | 741 |  | 1136 | 741-17 | 863.0723 | 629.6288 | 456.0603 | 411.7056 | 178.2621 | 4.6936 | 0 | 0 | 0 | 451.3667 | 0.46931 | 0.41925 | 0.33964 | 0.12967 | 0.079614 | 0 | 0 | 0 | 0 | 0.33964 | 41.6909 | 41.4215 | 41.0025 | 0.68846 | 0.41904 | 0 | 0 | 0 | 0 | 41.0025 | 820.9121 | 587.7881 | 414.7182 | 410.8874 | 177.7634 | 4.6936 | 0 | 0 | 0 | 410.0246 | 0.0007054 | 0.0003052 | 8e-06 | 0 | 0 | 0 | 0.000645 | 5000000 | scaled
75-2257F | 17796.9307 | 17679.2181 | 0 | 117.7126 | 99.34% | 0% | 0.6614% | 1212.4521 | 17679.2181 | 70.7233 | 0 | 1141.7288 | 1024.8383 | 0 | 16654.3798 | 75 |  | 1137 | 75-2257F | 17796.9307 | 16584.4786 | 117.7126 | 17679.2181 | 16466.766 | 0 | 0 | 0 | 0 | 117.7126 | 1024.9269 | 954.2036 | 0.088575 | 1024.8383 | 954.1151 | 0 | 0 | 0 | 0 | 0.088575 | 16665.0729 | 15523.344 | 10.6931 | 16654.3798 | 15512.651 | 0 | 0 | 0 | 0 | 10.6931 | 106.9309 | 106.9309 | 106.9309 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9309 | 0.000125 | 9.48e-05 | 2.4e-06 | 0 | 0 | 0 | 0.0001554 | 5000000 | scaled
75-2258F | 4423.0965 | 0 | 4423.0965 | 0 | 0% | 100% | 0% | 1959.6708 | 4127.5081 | 3.2707 | 1763.3864 | 193.0138 | 6.8887 | 3714.0888 | 406.5306 | 75 |  | 1138 | 75-2258F | 4423.0965 | 2463.4256 | 295.5884 | 0 | 0 | 0 | 4423.0965 | 2463.4256 | 295.5884 | 0 | 7.3821 | 4.1114 | 0.49333 | 0 | 0 | 0 | 7.3821 | 4.1114 | 0.49333 | 0 | 435.6439 | 242.6301 | 29.1134 | 0 | 0 | 0 | 435.6439 | 242.6301 | 29.1134 | 0 | 3980.0705 | 2216.6841 | 265.9817 | 0 | 0 | 0 | 3980.0705 | 2216.6841 | 265.9817 | 0 | 0 | 0 | 0 | 0.0051944 | 0.0029748 | 0.0005194 | 0 | 5000000 | scaled
75-2259F | 3135457.623 | 3128270.3011 | 4454.2562 | 2733.0658 | 99.77% | 0.1421% | 0.08717% | 1707356.9502 | 3082665.1549 | 144194.1354 | 1928.5116 | 1561234.3031 | 261684.3071 | 4078.8214 | 2816902.0265 | 75 |  | 1139 | 75-2259F | 3135457.623 | 1428100.6728 | 52792.4681 | 3128270.3011 | 1422891.6117 | 49761.5382 | 4454.2562 | 2475.9954 | 297.8641 | 2733.0658 | 265827.2638 | 121633.1284 | 4142.9567 | 265817.889 | 121627.0038 | 4140.4107 | 7.3183 | 4.068 | 0.48939 | 2.0565 | 2862792.3772 | 1301558.0741 | 45890.3508 | 2862168.1437 | 1301100.815 | 45616.9361 | 375.96 | 208.9856 | 25.1411 | 248.2736 | 6837.982 | 4909.4704 | 2759.1606 | 284.2684 | 163.7929 | 4.1914 | 4070.9779 | 2262.9418 | 272.2336 | 2482.7357 | 0.011275 | 0.0054214 | 0.000138 | 0.0052 | 0.0029728 | 0.00052 | 0.0038622 | 5000000 | scaled
75-32R | 1708385.4565 | 1701118.9818 | 5353.4147 | 1913.06 | 99.57% | 0.3134% | 0.112% | 857314.5639 | 1690838.6509 | 61177.3426 | 2340.2484 | 793796.973 | 121630.682 | 4918.1937 | 1564289.7752 | 75 |  | 1140 | 75-32R | 1708385.4565 | 851070.8926 | 17546.8056 | 1701118.9818 | 846184.0108 | 15275.4646 | 5353.4147 | 2973.8218 | 358.281 | 1913.06 | 122832.6891 | 61655.3466 | 1202.0071 | 122823.3951 | 61649.5439 | 1200.042 | 7.8546 | 4.3632 | 0.52567 | 1.4395 | 1578566.789 | 784769.816 | 14277.0137 | 1577896.8526 | 784320.4195 | 14070.0247 | 496.1527 | 275.6128 | 33.2054 | 173.7837 | 6985.9784 | 4645.73 | 2067.7847 | 398.7341 | 214.0474 | 5.398 | 4849.4075 | 2693.8458 | 324.55 | 1737.8368 | 0.0068564 | 0.003518 | 8.94e-05 | 0.0051988 | 0.0029698 | 0.0005198 | 0.002726 | 5000000 | scaled
75-41 | 1937584.5588 | 1934833.8501 | 873.2268 | 1877.4819 | 99.86% | 0.04507% | 0.0969% | 982357.9885 | 1918019.1614 | 99390.1314 | 1380.4069 | 881587.4502 | 193549.3142 | 2744.7537 | 1721725.0935 | 75 |  | 1141 | 75-41 | 1937584.5588 | 955226.5703 | 19565.3973 | 1934833.8501 | 952864.3055 | 17629.5303 | 873.2268 | 484.7829 | 58.3852 | 1877.4819 | 195314.8381 | 95924.7068 | 1765.5239 | 195310.4463 | 95921.6401 | 1763.912 | 2.9791 | 1.6539 | 0.19919 | 1.4127 | 1737741.0528 | 856153.6026 | 16015.9593 | 1737480.2221 | 855932.9314 | 15839.3714 | 90.279 | 50.1195 | 6.0362 | 170.5517 | 4528.6678 | 3148.2609 | 1783.9141 | 2043.1817 | 1009.734 | 26.2468 | 779.9687 | 433.0095 | 52.1498 | 1705.5174 | 0.008444 | 0.0040634 | 0.0001032 | 0.0052028 | 0.0029704 | 0.0005202 | 0.002653 | 5000000 | scaled
75-996R | 2211137.656 | 2194049.83 | 9535.0691 | 7552.7569 | 99.23% | 0.4312% | 0.3416% | 1046800.9461 | 2175493.769 | 105406.5859 | 7256.6014 | 934137.7588 | 220405.757 | 18570.5383 | 1936517.4737 | 75 |  | 1142 | 75-996R | 2211137.656 | 1164336.71 | 35643.887 | 2194049.83 | 1151504.7133 | 27455.0683 | 9535.0691 | 5279.2397 | 636.0618 | 7552.7569 | 223248.7509 | 117842.165 | 2842.9939 | 223225.6394 | 117826.8324 | 2836.1481 | 17.4283 | 9.6494 | 1.1626 | 5.6832 | 1961706.4615 | 1027568.7028 | 25188.9878 | 1959962.1285 | 1026296.6966 | 24432.2978 | 1058.2354 | 585.9085 | 70.5924 | 686.0976 | 26182.4436 | 18925.8422 | 7611.9053 | 10862.062 | 7381.1844 | 186.6224 | 8459.4054 | 4683.6817 | 564.3068 | 6860.9761 | 0.028153 | 0.016147 | 0.0004094 | 0.0052088 | 0.0029668 | 0.0005208 | 0.010635 | 5000000 | scaled
759-13AE | 22236.5116 | 13273.007 | 0 | 8963.5045 | 59.69% | 0% | 40.31% | 7290.1464 | 13080.0225 | 557.7065 | 3498.8487 | 3233.5913 | 997.0315 | 6245.092 | 5837.899 | 759 |  | 1143 | 759-13AE | 22236.5116 | 14946.3652 | 9156.4891 | 13273.007 | 5982.8606 | 192.9845 | 0 | 0 | 0 | 8963.5045 | 1020.3337 | 462.6272 | 23.3021 | 1013.5889 | 455.8824 | 16.5574 | 0 | 0 | 0 | 6.7447 | 6755.094 | 3521.5027 | 917.1949 | 5940.8431 | 2707.2518 | 102.944 | 0 | 0 | 0 | 814.2509 | 14461.084 | 10962.2353 | 8215.992 | 6318.5751 | 2819.7264 | 73.4831 | 0 | 0 | 0 | 8142.5089 | 0.026686 | 0.011701 | 0.000297 | 0 | 0 | 0 | 0.012625 | 5000000 | scaled
76-266F | 328.7034 | 85.9283 | 0 | 242.7751 | 26.14% | 0% | 73.86% | 49.4451 | 85.4359 | 3.812 | 26.069 | 19.5641 | 6.5102 | 45.517 | 33.4088 | 76 |  | 1144 | 76-266F | 328.7034 | 279.2583 | 243.2675 | 85.9283 | 36.4832 | 0.49231 | 0 | 0 | 0 | 242.7751 | 6.6929 | 2.8809 | 0.18268 | 6.5102 | 2.6982 | 0 | 0 | 0 | 0 | 0.18268 | 55.4626 | 35.8985 | 22.0539 | 33.4088 | 13.8447 | 0 | 0 | 0 | 0 | 22.0539 | 266.5479 | 240.4789 | 221.0309 | 46.0093 | 19.9403 | 0.49231 | 0 | 0 | 0 | 220.5386 | 0.0005022 | 0.0002176 | 5.4e-06 | 0 | 0 | 0 | 0.00034 | 5000000 | scaled
76-272 | 2469.17 | 1381.075 | 0 | 1088.095 | 55.93% | 0% | 44.07% | 783.1134 | 1365.0196 | 1.1051 | 776.3571 | 5.6511 | 1.826 | 1353.8496 | 9.344 | 76 |  | 1145 | 76-272 | 2469.17 | 1686.0566 | 1104.1504 | 1381.075 | 597.9616 | 16.0554 | 0 | 0 | 0 | 1088.095 | 2.7405 | 1.6354 | 0.91453 | 1.9218 | 0.81663 | 0.095773 | 0 | 0 | 0 | 0.81876 | 108.6781 | 103.0269 | 99.3341 | 9.8348 | 4.1836 | 0.49079 | 0 | 0 | 0 | 98.8433 | 2357.7514 | 1581.3943 | 1003.9018 | 1369.3185 | 592.9614 | 15.4688 | 0 | 0 | 0 | 988.4329 | 0.0028112 | 0.0012172 | 3.1e-05 | 0 | 0 | 0 | 0.0015362 | 5000000 | scaled
76-49F | 2584.9093 | 1820.8121 | 0 | 764.0972 | 70.44% | 0% | 29.56% | 1033.1599 | 1800.3903 | 3.2062 | 1013.5351 | 16.4187 | 5.4563 | 1766.9969 | 27.9371 | 76 |  | 1146 | 76-49F | 2584.9093 | 1551.7494 | 784.519 | 1820.8121 | 787.6522 | 20.4218 | 0 | 0 | 0 | 764.0972 | 6.0782 | 2.8719 | 0.62186 | 5.5032 | 2.297 | 0.046901 | 0 | 0 | 0 | 0.57496 | 97.587 | 81.1683 | 69.6499 | 28.1759 | 11.7572 | 0.2388 | 0 | 0 | 0 | 69.4111 | 2481.2441 | 1467.7091 | 714.2472 | 1787.133 | 773.598 | 20.1361 | 0 | 0 | 0 | 694.1111 | 0.001513 | 0.0006548 | 1.68e-05 | 0 | 0 | 0 | 0.001045 | 5000000 | scaled
765-53 | 10279.864 | 10066.418 | 0 | 213.4461 | 97.92% | 0% | 2.076% | 4165.8797 | 9614.0439 | 296.6342 | 2325.8952 | 1543.3503 | 655.4975 | 5669.3293 | 3289.2171 | 765 |  | 1147 | 765-53 | 10279.864 | 6113.9843 | 665.8201 | 10066.418 | 5900.5382 | 452.3741 | 0 | 0 | 0 | 213.4461 | 702.4577 | 405.8235 | 46.9602 | 702.2971 | 405.6629 | 46.7996 | 0 | 0 | 0 | 0.16061 | 3622.1591 | 2078.8088 | 332.942 | 3602.7695 | 2059.4192 | 313.5524 | 0 | 0 | 0 | 19.3896 | 5955.2472 | 3629.352 | 285.9179 | 5761.3514 | 3435.4561 | 92.0221 | 0 | 0 | 0 | 193.8959 | 0.0006118 | 0.0003704 | 9.4e-06 | 0 | 0 | 0 | 0.000301 | 5000000 | scaled
768-20AE | 67304.8837 | 66911.2714 | 0 | 393.6123 | 99.42% | 0% | 0.5848% | 34784.3048 | 66498.0378 | 11337.2115 | 5980.6479 | 17466.4454 | 21831.839 | 10945.2391 | 33720.9597 | 768 |  | 1148 | 768-20AE | 67304.8837 | 32520.5788 | 806.8458 | 66911.2714 | 32126.9666 | 413.2336 | 0 | 0 | 0 | 393.6123 | 21945.0891 | 10607.8776 | 113.2501 | 21944.7929 | 10607.5814 | 112.9539 | 0 | 0 | 0 | 0.29618 | 33925.7794 | 16459.334 | 204.8196 | 33890.0234 | 16423.5779 | 169.0636 | 0 | 0 | 0 | 35.756 | 11434.0152 | 5453.3673 | 488.7761 | 11076.4551 | 5095.8072 | 131.216 | 0 | 0 | 0 | 357.5601 | 0.0022736 | 0.001049 | 2.66e-05 | 0 | 0 | 0 | 0.0005374 | 5000000 | scaled
77-28R | 2255.3819 | 1388.675 | 0 | 866.7069 | 61.57% | 0% | 38.43% | 727.8994 | 1385.1985 | 66.4078 | 262.5258 | 398.9658 | 126.5778 | 475.5084 | 783.1122 | 77 |  | 1149 | 77-28R | 2255.3819 | 1527.4825 | 870.1834 | 1388.675 | 660.7756 | 3.4765 | 0 | 0 | 0 | 866.7069 | 127.23 | 60.8222 | 0.65217 | 126.5778 | 60.1701 | 0 | 0 | 0 | 0 | 0.65217 | 861.8445 | 462.8787 | 78.7323 | 783.1122 | 384.1464 | 0 | 0 | 0 | 0 | 78.7323 | 1266.3074 | 1003.7816 | 790.799 | 478.9849 | 216.4591 | 3.4765 | 0 | 0 | 0 | 787.3225 | 0.002473 | 0.0010708 | 2.68e-05 | 0 | 0 | 0 | 0.00123 | 5000000 | scaled
770-250R | 8274.2415 | 7589.4509 | 0 | 684.7906 | 91.72% | 0% | 8.276% | 3990.6081 | 7479.0781 | 553.2546 | 10.8182 | 3426.5353 | 1019.3035 | 21.8641 | 6437.9105 | 770 |  | 1150 | 770-250R | 8274.2415 | 4283.6334 | 795.1634 | 7589.4509 | 3598.8428 | 110.3728 | 0 | 0 | 0 | 684.7906 | 1037.299 | 484.0444 | 17.9955 | 1036.7837 | 483.5291 | 17.4802 | 0 | 0 | 0 | 0.51528 | 6592.7474 | 3166.2121 | 154.8368 | 6530.5405 | 3104.0052 | 92.63 | 0 | 0 | 0 | 62.2068 | 644.1951 | 633.3769 | 622.3311 | 22.1266 | 11.3084 | 0.26258 | 0 | 0 | 0 | 622.0685 | 0.0022776 | 0.0010636 | 2.66e-05 | 0 | 0 | 0 | 0.0009774 | 5000000 | scaled
770-259R | 42511.347 | 41445.1419 | 219.9827 | 846.2224 | 97.49% | 0.5175% | 1.991% | 21751.354 | 41485.8763 | 2253.1257 | 95.301 | 19402.9273 | 4266.6684 | 193.5013 | 37025.7066 | 770 |  | 1151 | 770-259R | 42511.347 | 20759.993 | 1025.4707 | 41445.1419 | 19791.75 | 164.5636 | 219.9827 | 122.0206 | 14.6846 | 846.2224 | 4288.5944 | 2035.4687 | 21.926 | 4287.1295 | 2034.3726 | 21.234 | 0.82815 | 0.45936 | 0.055282 | 0.63676 | 37248.6077 | 17845.6804 | 222.9011 | 37126.4545 | 17743.692 | 143.007 | 45.2818 | 25.117 | 3.0227 | 76.8714 | 974.1449 | 878.8438 | 780.6435 | 31.5579 | 13.6854 | 0.32269 | 173.8727 | 96.4442 | 11.6066 | 768.7142 | 0.0041816 | 0.0018104 | 4.6e-05 | 0.0052192 | 0.0029778 | 0.000522 | 0.0012044 | 5000000 | scaled
771-274AE | 570.1551 | 349.3841 | 0 | 220.771 | 61.28% | 0% | 38.72% | 143.7897 | 324.2145 | 6.7649 | 104.565 | 32.4598 | 19.355 | 199.9781 | 104.8813 | 771 |  | 1152 | 771-274AE | 570.1551 | 426.3653 | 245.9406 | 349.3841 | 205.5943 | 25.1696 | 0 | 0 | 0 | 220.771 | 22.2574 | 15.4925 | 2.9023 | 22.0912 | 15.3263 | 2.7362 | 0 | 0 | 0 | 0.16612 | 145.1681 | 112.7082 | 40.2868 | 125.1131 | 92.6533 | 20.2318 | 0 | 0 | 0 | 20.055 | 402.7296 | 298.1646 | 202.7515 | 202.1797 | 97.6147 | 2.2016 | 0 | 0 | 0 | 200.5499 | 0.0003292 | 0.0001426 | 3.6e-06 | 0 | 0 | 0 | 0.000292 | 5000000 | scaled
773-271F | 3165.6028 | 2520.1427 | 0 | 645.4601 | 79.61% | 0% | 20.39% | 1839.6115 | 2516.6377 | 171.696 | 101.4546 | 1566.4609 | 241.6465 | 171.7447 | 2103.2465 | 773 |  | 1153 | 773-271F | 3165.6028 | 1325.9913 | 648.9651 | 2520.1427 | 680.5312 | 3.505 | 0 | 0 | 0 | 645.4601 | 242.4719 | 70.7759 | 0.82543 | 241.9862 | 70.2902 | 0.33974 | 0 | 0 | 0 | 0.48569 | 2163.7284 | 597.2676 | 60.4819 | 2105.0944 | 538.6335 | 1.8479 | 0 | 0 | 0 | 58.634 | 759.4025 | 657.9479 | 587.6578 | 173.0621 | 71.6075 | 1.3174 | 0 | 0 | 0 | 586.3404 | 0.001903 | 0.0008238 | 2.1e-05 | 0 | 0 | 0 | 0.0009034 | 5000000 | scaled
775-185 | 2412.4047 | 749.3131 | 0 | 1663.0916 | 31.06% | 0% | 68.94% | 440.1587 | 741.8555 | 37.7532 | 272.3732 | 130.0323 | 61.2811 | 470.3014 | 210.2731 | 775 |  | 1154 | 775-185 | 2412.4047 | 1972.246 | 1670.5492 | 749.3131 | 309.1544 | 7.4575 | 0 | 0 | 0 | 1663.0916 | 63.0665 | 25.3133 | 1.7854 | 61.8151 | 24.0619 | 0.53396 | 0 | 0 | 0 | 1.2514 | 363.1549 | 233.1225 | 152.8818 | 212.0785 | 82.0462 | 1.8054 | 0 | 0 | 0 | 151.0764 | 1986.1834 | 1713.8102 | 1515.882 | 475.4195 | 203.0464 | 5.1181 | 0 | 0 | 0 | 1510.7638 | 0.0041918 | 0.0018144 | 4.6e-05 | 0 | 0 | 0 | 0.0023704 | 5000000 | scaled
775-187AE | 594.7955 | 69.5386 | 0 | 525.2568 | 11.69% | 0% | 88.31% | 39.2226 | 68.4493 | 2.6891 | 22.7909 | 13.7426 | 4.6948 | 39.7666 | 23.9878 | 775 |  | 1155 | 775-187AE | 594.7955 | 555.5728 | 526.3462 | 69.5386 | 30.316 | 1.0894 | 0 | 0 | 0 | 525.2568 | 5.1933 | 2.5042 | 0.4985 | 4.7981 | 2.109 | 0.10326 | 0 | 0 | 0 | 0.39524 | 72.2303 | 58.4877 | 48.2425 | 24.5156 | 10.773 | 0.52785 | 0 | 0 | 0 | 47.7147 | 517.3718 | 494.5809 | 477.6052 | 40.2249 | 17.434 | 0.45825 | 0 | 0 | 0 | 477.1469 | 0.001068 | 0.0004628 | 1.22e-05 | 0 | 0 | 0 | 0.0007464 | 5000000 | scaled
777-10 | 219.4752 | 109.7232 | 0 | 109.7521 | 49.99% | 0% | 50.01% | 67.4312 | 109.7213 | 8.7278 | 0.10379 | 58.5997 | 13.561 | 0.18505 | 95.9753 | 777 |  | 1156 | 777-10 | 219.4752 | 152.044 | 109.7539 | 109.7232 | 42.292 | 0.0018508 | 0 | 0 | 0 | 109.7521 | 13.6436 | 4.9158 | 0.082585 | 13.561 | 4.8332 | 0 | 0 | 0 | 0 | 0.082585 | 105.9453 | 47.3456 | 9.97 | 95.9753 | 37.3756 | 0 | 0 | 0 | 0 | 9.97 | 99.8864 | 99.7826 | 99.7014 | 0.18691 | 0.083111 | 0.0018508 | 0 | 0 | 0 | 99.6995 | 0.0002234 | 0.0001228 | 3.2e-06 | 0 | 0 | 0 | 0.0001472 | 5000000 | scaled
777-101 | 2484.6616 | 2050.1837 | 0 | 434.4779 | 82.51% | 0% | 17.49% | 791.8284 | 2049.5789 | 77.6693 | 21.9987 | 692.1604 | 209.9919 | 51.0368 | 1788.5502 | 777 |  | 1157 | 777-101 | 2484.6616 | 1692.8332 | 435.0827 | 2050.1837 | 1258.3553 | 0.60484 | 0 | 0 | 0 | 434.4779 | 210.3189 | 132.6496 | 0.32693 | 209.9919 | 132.3227 | 0 | 0 | 0 | 0 | 0.32693 | 1828.0184 | 1135.858 | 39.4683 | 1788.5502 | 1096.3898 | 0 | 0 | 0 | 0 | 39.4683 | 446.3243 | 424.3256 | 395.2875 | 51.6416 | 29.6429 | 0.60484 | 0 | 0 | 0 | 394.6827 | 0.0009576 | 0.0005402 | 1.38e-05 | 0 | 0 | 0 | 0.000598 | 5000000 | scaled
777-263F | 1123.1468 | 904.5252 | 0 | 218.6215 | 80.53% | 0% | 19.47% | 446.0424 | 904.4978 | 55.9471 | 1.5371 | 388.5582 | 107.1715 | 2.7232 | 794.6032 | 777 |  | 1158 | 777-263F | 1123.1468 | 677.1044 | 218.6489 | 904.5252 | 458.4829 | 0.027392 | 0 | 0 | 0 | 218.6215 | 107.336 | 51.3889 | 0.16451 | 107.1715 | 51.2244 | 0 | 0 | 0 | 0 | 0.16451 | 814.4629 | 425.9047 | 19.8597 | 794.6032 | 406.045 | 0 | 0 | 0 | 0 | 19.8597 | 201.3479 | 199.8108 | 198.6247 | 2.7506 | 1.2135 | 0.027392 | 0 | 0 | 0 | 198.5973 | 0.0005674 | 0.0002456 | 6.4e-06 | 0 | 0 | 0 | 0.0002964 | 5000000 | scaled
777-268F | 578.8455 | 547.257 | 0 | 31.5885 | 94.54% | 0% | 5.457% | 231.3021 | 547.2526 | 24.1555 | 0.28655 | 206.86 | 55.2773 | 0.50267 | 491.4726 | 777 |  | 1159 | 777-268F | 578.8455 | 347.5433 | 31.5929 | 547.257 | 315.9549 | 0.0044419 | 0 | 0 | 0 | 31.5885 | 55.3011 | 31.1455 | 0.023769 | 55.2773 | 31.1218 | 0 | 0 | 0 | 0 | 0.023769 | 494.3421 | 287.4821 | 2.8695 | 491.4726 | 284.6126 | 0 | 0 | 0 | 0 | 2.8695 | 29.2023 | 28.9157 | 28.6996 | 0.50711 | 0.22056 | 0.0044419 | 0 | 0 | 0 | 28.6952 | 7.72e-05 | 3.34e-05 | 8e-07 | 0 | 0 | 0 | 4.5e-05 | 5000000 | scaled
779-25AE | 3531.7831 | 3417.0421 | 0 | 114.741 | 96.75% | 0% | 3.249% | 1909.5456 | 3396.6504 | 184.1567 | 15.1278 | 1710.2612 | 327.3158 | 26.3979 | 3042.9368 | 779 |  | 1160 | 779-25AE | 3531.7831 | 1622.2375 | 135.1327 | 3417.0421 | 1507.4965 | 20.3917 | 0 | 0 | 0 | 114.741 | 329.757 | 145.6003 | 2.4412 | 329.6707 | 145.514 | 2.3549 | 0 | 0 | 0 | 0.086339 | 3071.1235 | 1360.8624 | 28.1868 | 3060.7004 | 1350.4392 | 17.7636 | 0 | 0 | 0 | 10.4232 | 130.9025 | 115.7748 | 104.5047 | 26.671 | 11.5432 | 0.27314 | 0 | 0 | 0 | 104.2315 | 0.000689 | 0.0002984 | 7.6e-06 | 0 | 0 | 0 | 0.0001556 | 5000000 | scaled
78-26R | 14526726.8022 | 14317113.3624 | 205179.4477 | 4433.9921 | 98.56% | 1.412% | 0.03052% | 3364750.7239 | 14209052.5138 | 165788.7779 | 80834.8685 | 3118127.0775 | 707727.3284 | 169328.9262 | 13331996.2592 | 78 |  | 1161 | 78-26R | 14526726.8022 | 11161976.0783 | 317674.2884 | 14317113.3624 | 11041220.1114 | 293476.6734 | 205179.4477 | 116321.9748 | 19763.6229 | 4433.9921 | 722520.9646 | 556732.1867 | 14793.6363 | 722234.7127 | 556568.4576 | 14763.0484 | 282.9155 | 160.3927 | 27.2514 | 3.3364 | 13612868.5963 | 10494741.5189 | 280872.3371 | 13594034.9298 | 10483889.7502 | 278694.2216 | 18430.8796 | 10448.9818 | 1775.3287 | 402.7869 | 191337.2412 | 110502.3727 | 22008.315 | 843.7199 | 761.9037 | 19.4034 | 186465.6525 | 105712.6003 | 17961.0428 | 4027.8688 | 0.019201 | 0.014723 | 0.0003746 | 0.32027 | 0.18211 | 0.032027 | 0.0062056 | 5000000 | scaled
78-35R | 5696335.8077 | 5695326.8309 | 0 | 1008.9768 | 99.98% | 0% | 0.01771% | 1278676.0522 | 5608252.1349 | 63859.5625 | 63.8956 | 1214752.5941 | 279136.5948 | 260.7505 | 5328854.7896 | 78 |  | 1162 | 78-35R | 5696335.8077 | 4417659.7555 | 88083.6728 | 5695326.8309 | 4416650.7787 | 87074.696 | 0 | 0 | 0 | 1008.9768 | 283505.4986 | 219645.9361 | 4368.9037 | 283504.7394 | 219645.1769 | 4368.1445 | 0 | 0 | 0 | 0.75922 | 5411647.8458 | 4196895.2517 | 82793.0562 | 5411556.1896 | 4196803.5955 | 82701.4 | 0 | 0 | 0 | 91.6561 | 1182.4634 | 1118.5677 | 921.7129 | 265.9019 | 202.0063 | 5.1515 | 0 | 0 | 0 | 916.5614 | 0.0067266 | 0.0051098 | 0.0001302 | 0 | 0 | 0 | 0.0014614 | 5000000 | scaled
78-782R | 7202315.8397 | 7167196.5439 | 33919.1162 | 1200.1796 | 99.51% | 0.4709% | 0.01666% | 2451799.7693 | 7026780.821 | 133535.6896 | 13137.5456 | 2305126.534 | 383079.5328 | 27449.6861 | 6616251.602 | 78 |  | 1163 | 78-782R | 7202315.8397 | 4750516.0705 | 175535.0187 | 7167196.5439 | 4730087.099 | 171064.7067 | 33919.1162 | 19228.7919 | 3270.1324 | 1200.1796 | 392258.2086 | 258722.5189 | 9178.6758 | 392225.959 | 258703.8455 | 9174.7506 | 31.3465 | 17.7704 | 3.0221 | 0.9031 | 6778597.1847 | 4473470.6507 | 162345.5826 | 6774874.5178 | 4471313.0473 | 161888.1673 | 3613.6417 | 2048.5783 | 348.3902 | 109.0251 | 31460.4464 | 18322.9008 | 4010.7603 | 96.0671 | 70.2062 | 1.7888 | 30274.128 | 17162.4432 | 2918.7201 | 1090.2514 | 0.0078748 | 0.0053888 | 0.0001368 | 0.32853 | 0.18679 | 0.032853 | 0.0016716 | 5000000 | scaled
780-468R | 132175.5817 | 2845.0468 | 128520.4786 | 810.0563 | 2.152% | 97.23% | 0.6129% | 58978.5537 | 122724.009 | 163.3629 | 52838.8154 | 5976.3755 | 318.4652 | 110060.8849 | 12344.6589 | 780 |  | 1164 | 780-468R | 132175.5817 | 73197.028 | 9451.5727 | 2845.0468 | 1441.3345 | 32.5435 | 128520.4786 | 70945.6372 | 8608.9729 | 810.0563 | 331.6613 | 168.2984 | 13.1961 | 166.8188 | 77.0293 | 1.5854 | 164.2329 | 90.6596 | 11.0012 | 0.60954 | 13256.1765 | 7279.801 | 911.5175 | 782.8529 | 361.3348 | 7.3323 | 12399.7375 | 6844.8802 | 830.5992 | 73.5861 | 118587.744 | 65748.9286 | 8526.859 | 1895.3751 | 1002.9704 | 23.6258 | 115956.5082 | 64010.0974 | 7767.3725 | 735.8607 | 0.002605 | 0.0011904 | 2.98e-05 | 0.010548 | 0.00599 | 0.0010548 | 0.0011426 | 5000000 | scaled
781-1356R | 45623.8779 | 3648.2759 | 40959.2867 | 1016.3152 | 7.996% | 89.78% | 2.228% | 20244.1311 | 41822.8799 | 26.6777 | 17697.2845 | 2520.169 | 54.4107 | 36537.7717 | 5230.6975 | 781 |  | 1165 | 781-1356R | 45623.8779 | 25379.7468 | 3800.998 | 3648.2759 | 1800.2787 | 45.1228 | 40959.2867 | 22563.1529 | 2739.56 | 1016.3152 | 58.8241 | 32.1464 | 4.4134 | 3.5077 | 1.331 | 0 | 54.5516 | 30.0507 | 3.6487 | 0.76474 | 5696.6668 | 3176.4978 | 465.9692 | 17.9389 | 6.8042 | 0 | 5586.4051 | 3077.3708 | 373.6464 | 92.3228 | 39868.387 | 22171.1025 | 3330.6154 | 3626.8293 | 1792.1434 | 45.1228 | 35318.33 | 19455.7314 | 2362.2649 | 923.2277 | 0.0023874 | 0.0010596 | 2.66e-05 | 0.010628 | 0.0060246 | 0.0010628 | 0.0014168 | 5000000 | scaled
781-1359 | 56465.6296 | 360.7715 | 54953.7016 | 1151.1565 | 0.6389% | 97.32% | 2.039% | 24841.8976 | 51620.4189 | 40.4788 | 22698.7938 | 2102.625 | 79.5565 | 47191.0001 | 4349.8623 | 781 |  | 1166 | 781-1359 | 56465.6296 | 31623.732 | 4845.2108 | 360.7715 | 158.9767 | 19.6682 | 54953.7016 | 30313.5988 | 3674.3861 | 1151.1565 | 87.3665 | 46.8877 | 7.81 | 17.3935 | 7.9008 | 2.3231 | 69.1067 | 38.1207 | 4.6207 | 0.86621 | 4774.689 | 2672.064 | 424.8267 | 89.1153 | 40.5167 | 13.954 | 4581.0019 | 2526.9754 | 306.3009 | 104.5718 | 51603.5741 | 28904.7804 | 4412.5741 | 254.2627 | 110.5593 | 3.3911 | 50303.5929 | 27748.5026 | 3363.4645 | 1045.7185 | 0.0035206 | 0.0015244 | 3.96e-05 | 0.010578 | 0.0060034 | 0.0010578 | 0.001637 | 5000000 | scaled
781-43AE | 1265.0833 | 52.3436 | 1077.3116 | 135.4281 | 4.138% | 85.16% | 10.71% | 516.9896 | 1057.663 | 5.3637 | 439.9399 | 71.6861 | 8.5608 | 914.9738 | 134.1284 | 781 |  | 1167 | 781-43AE | 1265.0833 | 748.0937 | 207.4204 | 52.3436 | 18.2915 | 0.044789 | 1077.3116 | 594.3742 | 71.9475 | 135.4281 | 8.7363 | 3.3726 | 0.17554 | 7.5319 | 2.6624 | 0 | 1.1025 | 0.60828 | 0.073631 | 0.10191 | 153.1184 | 81.4324 | 18.9901 | 40.6772 | 13.8814 | 0 | 100.1388 | 55.2486 | 6.6877 | 12.3024 | 1103.2286 | 663.2887 | 188.2547 | 4.1345 | 1.7476 | 0.044789 | 976.0703 | 538.5173 | 65.1862 | 123.0238 | 0.0002856 | 0.0001534 | 4e-06 | 0.010654 | 0.006048 | 0.0010654 | 0.000195 | 5000000 | scaled
781-44 | 408038.5562 | 39350.8773 | 357807.803 | 10879.8758 | 9.644% | 87.69% | 2.666% | 184122.646 | 376708.5909 | 1528.469 | 164930.7024 | 17663.4746 | 2694.2688 | 338790.7393 | 35223.5829 | 781 |  | 1168 | 781-44 | 408038.5562 | 223915.9102 | 31329.9652 | 39350.8773 | 17445.6122 | 467.3412 | 357807.803 | 195590.4221 | 19982.7482 | 10879.8758 | 2755.2256 | 1226.7565 | 60.9568 | 2380.1696 | 1016.3218 | 28.8337 | 366.8692 | 202.248 | 23.9363 | 8.1868 | 38200.3558 | 20536.8812 | 2976.7729 | 7526.6897 | 3203.3402 | 91.5768 | 29685.3307 | 16345.2056 | 1896.8607 | 988.3354 | 367082.9748 | 202152.2724 | 28292.2356 | 29444.018 | 13225.9502 | 346.9307 | 327755.6031 | 179042.9685 | 18061.9512 | 9883.3537 | 0.031486 | 0.013778 | 0.0003514 | 0.010365 | 0.0058858 | 0.0010364 | 0.015436 | 5000000 | scaled
783-1451F | 122427.988 | 0 | 122427.988 | 0 | 0% | 100% | 0% | 19550.9179 | 40609.2264 | 24.6217 | 17915.3843 | 1610.912 | 51.1417 | 37212.0582 | 3346.0265 | 783 |  | 1169 | 783-1451F | 122427.988 | 102877.0701 | 81818.7617 | 0 | 0 | 0 | 122427.988 | 102877.0701 | 81818.7617 | 0 | 154.1811 | 129.5595 | 103.0394 | 0 | 0 | 0 | 154.1811 | 129.5595 | 103.0394 | 0 | 10087.5423 | 8476.6303 | 6741.5158 | 0 | 0 | 0 | 10087.5423 | 8476.6303 | 6741.5158 | 0 | 112186.2646 | 94270.8804 | 74974.2064 | 0 | 0 | 0 | 112186.2646 | 94270.8804 | 74974.2064 | 0 | 0 | 0 | 0 | 0.010483 | 0.010483 | 0.010483 | 0 | 5000000 | scaled
783-1452F | 31579.0136 | 0 | 31579.0136 | 0 | 0% | 100% | 0% | 5047.8095 | 10474.5879 | 6.1936 | 4618.6654 | 422.9505 | 12.8522 | 9584.0814 | 877.6543 | 783 |  | 1170 | 783-1452F | 31579.0136 | 26531.2041 | 21104.4257 | 0 | 0 | 0 | 31579.0136 | 26531.2041 | 21104.4257 | 0 | 38.7472 | 32.5536 | 25.895 | 0 | 0 | 0 | 38.7472 | 32.5536 | 25.895 | 0 | 2645.9712 | 2223.0207 | 1768.3169 | 0 | 0 | 0 | 2645.9712 | 2223.0207 | 1768.3169 | 0 | 28894.2953 | 24275.6298 | 19310.2139 | 0 | 0 | 0 | 28894.2953 | 24275.6298 | 19310.2139 | 0 | 0 | 0 | 0 | 0.010577 | 0.010577 | 0.010577 | 0 | 5000000 | scaled
783-847F | 68083.8716 | 0 | 68083.8716 | 0 | 0% | 100% | 0% | 10878.279 | 22586.6016 | 12.9916 | 9952.7481 | 912.5394 | 26.9745 | 20664.9189 | 1894.7081 | 783 |  | 1171 | 783-847F | 68083.8716 | 57205.5926 | 45497.2701 | 0 | 0 | 0 | 68083.8716 | 57205.5926 | 45497.2701 | 0 | 81.3107 | 68.319 | 54.3361 | 0 | 0 | 0 | 81.3107 | 68.319 | 54.3361 | 0 | 5711.309 | 4798.7696 | 3816.6009 | 0 | 0 | 0 | 5711.309 | 4798.7696 | 3816.6009 | 0 | 62291.252 | 52338.5039 | 41626.333 | 0 | 0 | 0 | 62291.252 | 52338.5039 | 41626.333 | 0 | 0 | 0 | 0 | 0.010505 | 0.010505 | 0.010505 | 0 | 5000000 | scaled
783-848F | 97081.8891 | 0 | 97081.8891 | 0 | 0% | 100% | 0% | 15519.3228 | 32210.1499 | 19.8352 | 14148.546 | 1350.9416 | 41.1678 | 29365.1206 | 2803.8615 | 783 |  | 1172 | 783-848F | 97081.8891 | 81562.5663 | 64871.7393 | 0 | 0 | 0 | 97081.8891 | 81562.5663 | 64871.7393 | 0 | 124.0803 | 104.245 | 82.9125 | 0 | 0 | 0 | 124.0803 | 104.245 | 82.9125 | 0 | 8450.8818 | 7099.9402 | 5647.0203 | 0 | 0 | 0 | 8450.8818 | 7099.9402 | 5647.0203 | 0 | 88506.927 | 74358.3811 | 59141.8064 | 0 | 0 | 0 | 88506.927 | 74358.3811 | 59141.8064 | 0 | 0 | 0 | 0 | 0.010408 | 0.010408 | 0.010408 | 0 | 5000000 | scaled
783-849F | 24529.1556 | 0 | 24529.1556 | 0 | 0% | 100% | 0% | 3915.2577 | 8140.4812 | 5.8 | 3577.2502 | 332.2075 | 12.0592 | 7437.7066 | 690.7154 | 783 |  | 1173 | 783-849F | 24529.1556 | 20613.8978 | 16388.6744 | 0 | 0 | 0 | 24529.1556 | 20613.8978 | 16388.6744 | 0 | 36.3371 | 30.5371 | 24.2779 | 0 | 0 | 0 | 36.3371 | 30.5371 | 24.2779 | 0 | 2081.2856 | 1749.0781 | 1390.5702 | 0 | 0 | 0 | 2081.2856 | 1749.0781 | 1390.5702 | 0 | 22411.5328 | 18834.2826 | 14973.8262 | 0 | 0 | 0 | 22411.5328 | 18834.2826 | 14973.8262 | 0 | 0 | 0 | 0 | 0.01043 | 0.01043 | 0.01043 | 0 | 5000000 | scaled
783-854F | 81195.3171 | 0 | 81195.3171 | 0 | 0% | 100% | 0% | 12974.612 | 26965.567 | 14.6822 | 11880.8058 | 1079.124 | 30.5146 | 24692.2732 | 2242.7792 | 783 |  | 1174 | 783-854F | 81195.3171 | 68220.705 | 54229.7501 | 0 | 0 | 0 | 81195.3171 | 68220.705 | 54229.7501 | 0 | 91.8817 | 77.1995 | 61.3671 | 0 | 0 | 0 | 91.8817 | 77.1995 | 61.3671 | 0 | 6753.174 | 5674.05 | 4510.3948 | 0 | 0 | 0 | 6753.174 | 5674.05 | 4510.3948 | 0 | 74350.2613 | 62469.4555 | 49657.9882 | 0 | 0 | 0 | 74350.2613 | 62469.4555 | 49657.9882 | 0 | 0 | 0 | 0 | 0.010332 | 0.010332 | 0.010332 | 0 | 5000000 | scaled
788-34R | 9132236.5922 | 8614677.8722 | 506521.4185 | 11037.3015 | 94.33% | 5.547% | 0.1209% | 4485047.0455 | 8952386.1899 | 610748.365 | 216116.6607 | 3658182.0198 | 1214202.0746 | 447981.4395 | 7290202.6758 | 788 |  | 1175 | 788-34R | 9132236.5922 | 4647189.5467 | 179850.4024 | 8614677.8722 | 4352853.0532 | 125960.8884 | 506521.4185 | 283299.192 | 42852.2124 | 11037.3015 | 1232181.963 | 621433.598 | 17979.8884 | 1231473.5096 | 621033.6975 | 17912.3499 | 700.1481 | 391.5953 | 59.2332 | 8.3052 | 7402644.7668 | 3744462.747 | 112442.091 | 7357712.4391 | 3718890.0815 | 107722.9597 | 43929.6917 | 24570.0294 | 3716.4953 | 1002.636 | 497409.8624 | 281293.2017 | 49428.4229 | 25491.9234 | 12929.2742 | 325.5788 | 461891.5787 | 258337.5673 | 39076.4839 | 10026.3603 | 0.043828 | 0.021116 | 0.0005366 | 0.064673 | 0.036654 | 0.0064672 | 0.015543 | 5000000 | scaled
789-15 | 761980.5628 | 761323.2888 | 0 | 657.2739 | 99.91% | 0% | 0.08626% | 512145.5092 | 737959.3019 | 26925.7885 | 45.7061 | 485174.0147 | 39202.3287 | 79.6705 | 698677.3026 | 789 |  | 1176 | 789-15 | 761980.5628 | 249835.0535 | 24021.2609 | 761323.2888 | 249177.7796 | 23363.987 | 0 | 0 | 0 | 657.2739 | 40359.1077 | 13433.3192 | 1156.7789 | 40358.6131 | 13432.8246 | 1156.2843 | 0 | 0 | 0 | 0.49458 | 720943.8184 | 235769.8037 | 22266.5158 | 720884.1112 | 235710.0965 | 22206.8085 | 0 | 0 | 0 | 59.7072 | 677.6367 | 631.9306 | 597.9662 | 80.5646 | 34.8585 | 0.89406 | 0 | 0 | 0 | 597.0721 | 0.0032274 | 0.0013974 | 3.58e-05 | 0 | 0 | 0 | 0.0009388 | 5000000 | scaled
789-4R | 10274005.9159 | 10265348.9348 | 0 | 8656.9811 | 99.92% | 0% | 0.08426% | 5626187.4497 | 10210280.8739 | 358482.1847 | 5313.2524 | 5262392.0126 | 651289.696 | 11144.0293 | 9547847.1486 | 789 |  | 1177 | 789-4R | 10274005.9159 | 4647818.4662 | 63725.0419 | 10265348.9348 | 4639161.4851 | 55068.0609 | 0 | 0 | 0 | 8656.9811 | 655135.595 | 296653.4102 | 3845.899 | 655129.0809 | 296646.8961 | 3839.3849 | 0 | 0 | 0 | 6.5141 | 9599696.2564 | 4337304.2437 | 51849.1077 | 9598909.8503 | 4336517.8377 | 51062.7016 | 0 | 0 | 0 | 786.4061 | 19174.0645 | 13860.8122 | 8030.0352 | 11310.0037 | 5996.7513 | 165.9743 | 0 | 0 | 0 | 7864.0609 | 0.038017 | 0.017293 | 0.0004548 | 0 | 0 | 0 | 0.012263 | 5000000 | scaled
79-1215F | 324126.2707 | 322778.0694 | 1173.0331 | 175.1681 | 99.58% | 0.3619% | 0.05404% | 75286.1555 | 310652.5279 | 3809.1134 | 656.8635 | 70820.1786 | 15557.1511 | 1493.8444 | 293601.5324 | 79 |  | 1178 | 79-1215F | 324126.2707 | 248840.1152 | 13473.7427 | 322778.0694 | 248001.7341 | 13188.434 | 1173.0331 | 663.2129 | 110.1406 | 175.1681 | 16221.9175 | 12412.8042 | 664.7664 | 16220.8924 | 12412.1673 | 664.5507 | 0.89337 | 0.5051 | 0.083882 | 0.13181 | 306141.9788 | 235321.8002 | 12540.4464 | 306032.4404 | 235252.9533 | 12515.7431 | 93.626 | 52.9345 | 8.7909 | 15.9124 | 1762.3743 | 1105.5108 | 268.5299 | 524.7366 | 336.6135 | 8.1401 | 1078.5138 | 609.7733 | 101.2659 | 159.1239 | 0.0004792 | 0.0003378 | 8.6e-06 | 0.18237 | 0.10364 | 0.018237 | 0.000252 | 5000000 | scaled
79-658R | 12321075.9006 | 12230390.8778 | 84071.8795 | 6613.1432 | 99.26% | 0.6823% | 0.05367% | 3536495.1442 | 12040150.3733 | 206326.683 | 34404.3601 | 3295764.1011 | 704977.425 | 76584.7883 | 11258588.16 | 79 |  | 1179 | 79-658R | 12321075.9006 | 8784580.7564 | 280925.5273 | 12230390.8778 | 8730315.936 | 266141.8299 | 84071.8795 | 47651.6772 | 8170.5542 | 6613.1432 | 720625.1021 | 514298.419 | 15647.6771 | 720273.7877 | 514097.1395 | 15609.0419 | 346.3381 | 196.3034 | 33.659 | 4.9762 | 11510807.3547 | 8215043.2536 | 252219.1947 | 11496569.2366 | 8206712.8895 | 250293.0993 | 13637.3757 | 7729.6217 | 1325.353 | 600.7425 | 89643.4438 | 55239.0837 | 13058.6555 | 13547.8535 | 9505.907 | 239.6887 | 70088.1657 | 39725.7521 | 6811.5422 | 6007.4246 | 0.034298 | 0.02435 | 0.0006198 | 0.42302 | 0.24031 | 0.042302 | 0.0092374 | 5000000 | scaled
79-660R | 2087038.5602 | 2034167.1446 | 47227.3245 | 5644.0911 | 97.47% | 2.263% | 0.2704% | 1069354.1079 | 2049644.3234 | 47447.1008 | 20664.5005 | 1001242.5066 | 89234.9238 | 44479.2048 | 1915930.1948 | 79 |  | 1180 | 79-660R | 2087038.5602 | 1017684.4523 | 37394.2367 | 2034167.1446 | 985268.4817 | 27160.3428 | 47227.3245 | 26771.8794 | 4589.8028 | 5644.0911 | 90484.0116 | 43036.9109 | 1249.0878 | 90295.6566 | 42928.2981 | 1226.9482 | 184.108 | 104.3658 | 17.8926 | 4.247 | 1943045.1541 | 941802.6475 | 27114.9593 | 1934143.4817 | 936534.4626 | 25786.9625 | 8388.9594 | 4755.4718 | 815.2837 | 512.7131 | 53509.3944 | 32844.8939 | 9030.1896 | 9728.0063 | 5805.721 | 146.4321 | 38654.2571 | 21912.0418 | 3756.6264 | 5127.131 | 0.026675 | 0.015128 | 0.0003838 | 0.42285 | 0.24025 | 0.042285 | 0.0079424 | 5000000 | scaled
79-668R | 1606906.818 | 1139716.6179 | 460060.899 | 7129.3011 | 70.93% | 28.63% | 0.4437% | 577301.4961 | 1538433.6256 | 22081.61 | 177948.4376 | 377271.4485 | 65191.6797 | 371561.1413 | 1101680.8045 | 79 |  | 1181 | 79-668R | 1606906.818 | 1029605.3219 | 68473.1924 | 1139716.6179 | 761681.8006 | 16701.2156 | 460060.899 | 260794.2203 | 44642.6758 | 7129.3011 | 66232.1592 | 44150.5492 | 1040.4794 | 65413.3152 | 43684.0485 | 956.1777 | 813.4794 | 461.1362 | 78.9371 | 5.3646 | 1122846.5745 | 745575.126 | 21165.77 | 1072716.4226 | 716877.3925 | 15716.5313 | 49482.5213 | 28050.1029 | 4801.6081 | 647.6306 | 417828.0843 | 239879.6468 | 46266.943 | 1586.8801 | 1120.3596 | 28.5066 | 409764.8984 | 232282.9812 | 39762.1305 | 6476.3059 | 0.029807 | 0.01965 | 0.0004998 | 0.40006 | 0.22733 | 0.040006 | 0.010118 | 5000000 | scaled
79-676R | 9714146.4463 | 9547621.9773 | 163732.4612 | 2792.0078 | 98.29% | 1.686% | 0.02874% | 2408865.8841 | 9516027.0204 | 139224.4872 | 66627.5618 | 2203013.8351 | 557299.1825 | 142947.1376 | 8815780.7003 | 79 |  | 1182 | 79-676R | 9714146.4463 | 7305280.5622 | 198119.4259 | 9547621.9773 | 7209689.5214 | 179482.5618 | 163732.4612 | 92799.033 | 15844.8563 | 2792.0078 | 567916.8825 | 428692.3953 | 10617.7001 | 567721.6518 | 428580.8337 | 10596.9094 | 193.1299 | 109.4607 | 18.6897 | 2.1009 | 8986150.336 | 6783136.5009 | 170369.6356 | 8971491.5912 | 6774718.451 | 168721.9836 | 14405.1168 | 8164.422 | 1394.0242 | 253.6279 | 160079.2278 | 93451.666 | 17132.0902 | 8408.7343 | 6390.2367 | 163.6688 | 149134.2145 | 84525.1503 | 14432.1424 | 2536.279 | 0.01407 | 0.010619 | 0.0002696 | 0.36609 | 0.20802 | 0.036609 | 0.003935 | 5000000 | scaled
79-679R | 18448582.7599 | 18245131.6107 | 198973.2731 | 4477.8761 | 98.9% | 1.079% | 0.02427% | 5436472.0338 | 18164820.9004 | 298235.328 | 78780.0411 | 5059456.6647 | 1003215.5755 | 164967.8489 | 16996637.476 | 79 |  | 1183 | 79-679R | 18448582.7599 | 13012110.726 | 283761.8595 | 18245131.6107 | 12894898.1877 | 260034.7547 | 198973.2731 | 112734.6623 | 19249.2286 | 4477.8761 | 1017740.323 | 719504.995 | 14524.7475 | 1017464.913 | 719347.4923 | 14495.0601 | 272.0405 | 154.1332 | 26.318 | 3.3695 | 17244280.1656 | 12184823.5009 | 247642.6896 | 17226009.5482 | 12174295.3962 | 245507.7182 | 17863.8441 | 10121.3314 | 1728.198 | 406.7733 | 186562.2713 | 107782.2301 | 21594.4224 | 1657.1495 | 1255.2992 | 31.9764 | 180837.3885 | 102459.1977 | 17494.7127 | 4067.7333 | 0.025346 | 0.018131 | 0.0004606 | 0.36216 | 0.20572 | 0.036216 | 0.0063992 | 5000000 | scaled
79-685R | 2564752.4487 | 2548703.3542 | 13743.305 | 2305.7895 | 99.37% | 0.5359% | 0.0899% | 595178.848 | 2499048.7556 | 29072.7098 | 193.1498 | 565912.9884 | 122324.9545 | 464.4138 | 2376259.3873 | 79 |  | 1184 | 79-685R | 2564752.4487 | 1969573.6008 | 65703.6931 | 2548703.3542 | 1953713.6403 | 50049.8584 | 13743.305 | 13554.1709 | 13348.0452 | 2305.7895 | 124837.3306 | 95764.6208 | 2512.3761 | 124751.4416 | 95679.8899 | 2428.9073 | 84.154 | 82.9959 | 81.7337 | 1.735 | 2425880.1708 | 1859967.1824 | 49620.7836 | 2423824.7947 | 1857937.2097 | 47618.4963 | 1845.9166 | 1820.5133 | 1792.8277 | 209.4595 | 14034.9473 | 13841.7975 | 13570.5335 | 127.118 | 96.5408 | 2.4548 | 11813.2344 | 11650.6618 | 11473.4837 | 2094.595 | 0.015055 | 0.011436 | 0.0002906 | 0.41327 | 0.41327 | 0.41327 | 0.0032196 | 5000000 | scaled
79-714R | 5536620.5341 | 5332550.5898 | 200312.3058 | 3757.6385 | 96.31% | 3.618% | 0.06787% | 1329890.4985 | 5415731.7353 | 70189.3167 | 78543.6955 | 1181157.4864 | 294738.1572 | 165310.9933 | 4955682.5848 | 79 |  | 1185 | 79-714R | 5536620.5341 | 4206730.0356 | 120888.7988 | 5332550.5898 | 4089526.9688 | 97767.259 | 200312.3058 | 113445.4283 | 19363.9013 | 3757.6385 | 300293.7058 | 230104.3891 | 5555.5486 | 299980.5971 | 229925.8361 | 5522.7267 | 310.2812 | 175.7255 | 29.9944 | 2.8275 | 5050215.2536 | 3869057.7672 | 94532.6688 | 5029020.2194 | 3856906.0852 | 92175.4264 | 20853.6878 | 11810.3355 | 2015.8959 | 341.3465 | 186111.5747 | 107567.8792 | 20800.5814 | 3549.7733 | 2695.0474 | 69.1059 | 179148.3369 | 101459.3673 | 17318.011 | 3413.4645 | 0.01796 | 0.013563 | 0.0003444 | 0.35443 | 0.20126 | 0.035443 | 0.0053262 | 5000000 | scaled
79-782R | 2969.2366 | 0 | 2969.2366 | 0 | 0% | 100% | 0% | 41.246 | 86.3326 | 0.26929 | 32.5101 | 8.4666 | 0.56366 | 68.0473 | 17.7216 | 79 |  | 1186 | 79-782R | 2969.2366 | 2927.9906 | 2882.904 | 0 | 0 | 0 | 2969.2366 | 2927.9906 | 2882.904 | 0 | 19.386 | 19.1167 | 18.8224 | 0 | 0 | 0 | 19.386 | 19.1167 | 18.8224 | 0 | 609.4991 | 601.0325 | 591.7775 | 0 | 0 | 0 | 609.4991 | 601.0325 | 591.7775 | 0 | 2340.3514 | 2307.8414 | 2272.3041 | 0 | 0 | 0 | 2340.3514 | 2307.8414 | 2272.3041 | 0 | 0 | 0 | 0 | 0.40924 | 0.40924 | 0.40924 | 0 | 5000000 | scaled
79-785 | 18780928.5331 | 18244488.231 | 528026.7206 | 8413.5815 | 97.14% | 2.812% | 0.0448% | 6154888.1466 | 18387548.9399 | 403619.2807 | 209010.8911 | 5542257.9748 | 1220630.1537 | 439805.3239 | 16727113.4622 | 79 |  | 1187 | 79-785 | 18780928.5331 | 12626040.3865 | 393379.5932 | 18244488.231 | 12318707.1063 | 334038.677 | 528026.7206 | 298919.6987 | 50927.3347 | 8413.5815 | 1243380.6367 | 839761.356 | 22750.483 | 1242557.3844 | 839292.56 | 22665.3613 | 816.9214 | 462.4651 | 78.7908 | 6.3309 | 17044003.2693 | 11501745.2944 | 316889.807 | 16992002.9454 | 11471975.9173 | 311183.8783 | 51236.0283 | 29005.0817 | 4941.6332 | 764.2955 | 493544.6271 | 284533.7361 | 53739.3032 | 9927.9012 | 7438.629 | 189.4374 | 475973.7708 | 269452.152 | 45906.9107 | 7642.9551 | 0.037654 | 0.02567 | 0.0006522 | 0.33071 | 0.18774 | 0.033071 | 0.011868 | 5000000 | scaled
79-799R | 3034823.4797 | 2947432.5106 | 83523.0373 | 3867.9318 | 97.12% | 2.752% | 0.1275% | 755962.5018 | 2961673.3294 | 31783.1448 | 32232.3394 | 691947.0175 | 126466.1075 | 67483.0697 | 2767724.1523 | 79 |  | 1188 | 79-799R | 3034823.4797 | 2278860.9779 | 73150.1503 | 2947432.5106 | 2227607.0304 | 61071.1613 | 83523.0373 | 47386.0157 | 8211.0571 | 3867.9318 | 129094.2211 | 97311.0762 | 2628.1136 | 129002.6054 | 97257.8397 | 2616.4826 | 88.7052 | 50.3261 | 8.7205 | 2.9105 | 2827431.6412 | 2135484.6236 | 59707.4889 | 2817783.9277 | 2129859.0619 | 58442.2097 | 9296.3479 | 5274.1962 | 913.9136 | 351.3656 | 78297.6175 | 46065.2781 | 10814.5478 | 645.9776 | 490.1288 | 12.4691 | 74137.9842 | 42061.4934 | 7288.423 | 3513.6558 | 0.035948 | 0.026932 | 0.0006848 | 0.72925 | 0.41431 | 0.072925 | 0.00548 | 5000000 | scaled
79-808R | 19978325.502 | 19824672.4607 | 146900.5349 | 6752.5064 | 99.23% | 0.7353% | 0.0338% | 8724258.9907 | 19589807.9425 | 447930.7305 | 57459.5379 | 8218868.7222 | 1007379.3049 | 120451.5661 | 18461977.0715 | 79 |  | 1189 | 79-808R | 19978325.502 | 11254066.5114 | 388517.5596 | 19824672.4607 | 11164066.3271 | 367516.201 | 146900.5349 | 83247.6779 | 14248.8521 | 6752.5064 | 1026341.9577 | 578411.2271 | 18962.6528 | 1026147.8823 | 578299.0441 | 18939.2399 | 188.9943 | 107.102 | 18.3318 | 5.081 | 18812651.4384 | 10593782.7162 | 350674.3669 | 18796349.5685 | 10584278.7506 | 348539.2366 | 15688.4676 | 8890.5633 | 1521.728 | 613.4023 | 139332.1059 | 81872.5681 | 18880.5399 | 2175.0099 | 1488.5323 | 37.7245 | 131023.073 | 74250.0127 | 12708.7923 | 6134.0231 | 0.041448 | 0.023454 | 0.0005962 | 0.39463 | 0.22417 | 0.039463 | 0.0095556 | 5000000 | scaled
791-419F | 3349759.3853 | 3101216.4739 | 244656.6803 | 3886.2311 | 92.58% | 7.304% | 0.116% | 1712174.0228 | 3297600.7234 | 115627.6838 | 97811.6888 | 1498734.6502 | 221126.5901 | 203141.4271 | 2873332.7061 | 791 |  | 1190 | 791-419F | 3349759.3853 | 1637585.3625 | 52158.6619 | 3101216.4739 | 1496370.9859 | 26805.0898 | 244656.6803 | 137328.1455 | 21467.341 | 3886.2311 | 223179.3488 | 107551.6651 | 2052.7587 | 222800.1134 | 107337.5137 | 2016.8151 | 376.3112 | 211.2271 | 33.0193 | 2.9243 | 2900697.1906 | 1401962.5404 | 27364.4844 | 2874433.4761 | 1387065.5951 | 24737.9296 | 25910.6866 | 14543.9174 | 2273.5269 | 353.0279 | 225882.8459 | 128071.1571 | 22741.4188 | 3982.8845 | 1967.8771 | 50.345 | 218369.6825 | 122573.001 | 19160.7948 | 3530.2789 | 0.02105 | 0.0096226 | 0.0002448 | 0.0867 | 0.049185 | 0.00867 | 0.0055036 | 5000000 | scaled
791-424F | 71897.4631 | 0 | 71897.4631 | 0 | 0% | 100% | 0% | 4215.2819 | 8750.5839 | 6.2912 | 3862.4224 | 346.5682 | 13.0601 | 8018.0763 | 719.4475 | 791 |  | 1191 | 791-424F | 71897.4631 | 67682.1813 | 63146.8792 | 0 | 0 | 0 | 71897.4631 | 67682.1813 | 63146.8792 | 0 | 107.3058 | 101.0145 | 94.2457 | 0 | 0 | 0 | 107.3058 | 101.0145 | 94.2457 | 0 | 5911.1996 | 5564.6314 | 5191.7521 | 0 | 0 | 0 | 5911.1996 | 5564.6314 | 5191.7521 | 0 | 65878.9578 | 62016.5353 | 57860.8815 | 0 | 0 | 0 | 65878.9578 | 62016.5353 | 57860.8815 | 0 | 0 | 0 | 0 | 0.087564 | 0.087564 | 0.087564 | 0 | 5000000 | scaled
791-425F | 42428.6564 | 0 | 42428.6564 | 0 | 0% | 100% | 0% | 2483.6303 | 5158.7341 | 3.4946 | 2271.6634 | 208.4723 | 7.2586 | 4718.4588 | 433.0167 | 791 |  | 1192 | 791-425F | 42428.6564 | 39945.0261 | 37269.9223 | 0 | 0 | 0 | 42428.6564 | 39945.0261 | 37269.9223 | 0 | 59.6993 | 56.2047 | 52.4407 | 0 | 0 | 0 | 59.6993 | 56.2047 | 52.4407 | 0 | 3561.3999 | 3352.9275 | 3128.3832 | 0 | 0 | 0 | 3561.3999 | 3352.9275 | 3128.3832 | 0 | 38807.5573 | 36535.8939 | 34089.0985 | 0 | 0 | 0 | 38807.5573 | 36535.8939 | 34089.0985 | 0 | 0 | 0 | 0 | 0.087701 | 0.087701 | 0.087701 | 0 | 5000000 | scaled
792-1172F | 6355.8065 | 2598.8677 | 0 | 3756.9388 | 40.89% | 0% | 59.11% | 1473.6177 | 2569.8395 | 0.70352 | 1469.298 | 3.6162 | 1.0775 | 2563.2206 | 5.5413 | 792 |  | 1193 | 792-1172F | 6355.8065 | 4882.1888 | 3785.967 | 2598.8677 | 1125.25 | 29.0282 | 0 | 0 | 0 | 3756.9388 | 4.0322 | 3.3287 | 2.9547 | 1.2052 | 0.50172 | 0.1277 | 0 | 0 | 0 | 2.827 | 347.4744 | 343.8582 | 341.9331 | 6.1915 | 2.5753 | 0.65016 | 0 | 0 | 0 | 341.2829 | 6004.2999 | 4535.0019 | 3441.0793 | 2591.471 | 1122.1729 | 28.2503 | 0 | 0 | 0 | 3412.8289 | 0.009404 | 0.0040726 | 0.0001036 | 0 | 0 | 0 | 0.0052926 | 5000000 | scaled
792-1173F | 9725.8309 | 4365.3001 | 4900.2874 | 460.2434 | 44.88% | 50.38% | 4.732% | 4295.6841 | 8884.5413 | 42.542 | 3624.2768 | 628.8653 | 74.0007 | 7575.8972 | 1234.6433 | 792 |  | 1194 | 792-1173F | 9725.8309 | 5430.1468 | 841.2896 | 4365.3001 | 2264.1769 | 53.8701 | 4900.2874 | 2705.7264 | 327.1761 | 460.2434 | 75.6261 | 33.0841 | 1.6254 | 60.6973 | 24.686 | 0.30545 | 14.5825 | 8.0518 | 0.97363 | 0.34632 | 1344.1262 | 715.2608 | 109.4828 | 312.7082 | 127.0327 | 1.601 | 989.6091 | 546.4193 | 66.0729 | 41.8088 | 8306.0786 | 4681.8018 | 730.1814 | 3991.8946 | 2112.4583 | 51.9636 | 3896.0957 | 2151.2553 | 260.1295 | 418.0883 | 0.0010132 | 0.0005142 | 1.32e-05 | 0.017332 | 0.009847 | 0.0017332 | 0.0006422 | 5000000 | scaled
792-46 | 104787.7442 | 29197.0214 | 71513.6216 | 4077.1013 | 27.86% | 68.25% | 3.891% | 46434.0871 | 95579.1828 | 123.1482 | 43066.1796 | 3244.7593 | 284.5887 | 88375.8051 | 6918.789 | 792 |  | 1195 | 792-46 | 104787.7442 | 58353.6571 | 9208.5614 | 29197.0214 | 14715.3596 | 353.8084 | 71513.6216 | 39561.1963 | 4777.6518 | 4077.1013 | 295.68 | 172.5318 | 11.0913 | 194.4756 | 115.1749 | 1.4672 | 98.1366 | 54.289 | 6.5563 | 3.0679 | 7720.8258 | 4476.0665 | 802.0367 | 1002.151 | 593.8281 | 7.555 | 6348.3081 | 3511.8717 | 424.1151 | 370.3667 | 96771.2384 | 53705.0589 | 8395.4333 | 28000.3948 | 14006.3565 | 344.7862 | 65067.1769 | 35995.0357 | 4346.9804 | 3703.6667 | 0.010932 | 0.0050834 | 0.000129 | 0.017291 | 0.0098402 | 0.001729 | 0.0057348 | 5000000 | scaled
792-47R | 393985.0443 | 6609.8955 | 381944.7723 | 5430.3765 | 1.678% | 96.94% | 1.378% | 175655.317 | 365537.4314 | 186.9994 | 161482.2147 | 13986.1028 | 390.8875 | 335935.1412 | 29211.4027 | 792 |  | 1196 | 792-47R | 393985.0443 | 218329.7274 | 28447.613 | 6609.8955 | 2868.4337 | 73.0851 | 381944.7723 | 210030.9171 | 22944.1513 | 5430.3765 | 421.8428 | 234.8434 | 30.9554 | 9.3085 | 5.0145 | 0 | 408.4481 | 225.7428 | 26.8692 | 4.0862 | 31736.6031 | 17750.5003 | 2525.2004 | 47.8041 | 25.8218 | 0 | 31195.4999 | 17231.3794 | 2031.9013 | 493.2991 | 361826.5984 | 200344.3836 | 25891.4572 | 6552.7829 | 2837.5974 | 73.0851 | 350340.8243 | 192573.795 | 20885.3808 | 4932.9912 | 0.014386 | 0.0062696 | 0.0001584 | 0.017013 | 0.0096814 | 0.0017012 | 0.00767 | 5000000 | scaled
793-27AE | 59590.5566 | 5424.0882 | 53670.8956 | 495.5728 | 9.102% | 90.07% | 0.8316% | 27229.6727 | 55502.7412 | 321.6538 | 22380.0615 | 4527.9575 | 545.5433 | 46538.8105 | 8418.3874 | 793 |  | 1197 | 793-27AE | 59590.5566 | 32360.8839 | 4087.8154 | 5424.0882 | 2173.488 | 6.9223 | 53670.8956 | 29691.8231 | 3585.3203 | 495.5728 | 551.6721 | 230.0184 | 6.1288 | 465.135 | 181.9777 | 0 | 86.1642 | 47.6678 | 5.7559 | 0.3729 | 8800.2062 | 4272.2487 | 381.8188 | 3713.41 | 1438.0171 | 0 | 5041.778 | 2789.2134 | 336.8006 | 45.0182 | 50238.6783 | 27858.6168 | 3699.8678 | 1245.5432 | 553.4932 | 6.9223 | 48542.9533 | 26854.9419 | 3242.7638 | 450.1818 | 0.0017054 | 0.0007384 | 1.86e-05 | 0.017353 | 0.0098762 | 0.0017352 | 0.0007008 | 5000000 | scaled
793-46F | 23414.1115 | 659.9614 | 22246.9463 | 507.2039 | 2.819% | 95.02% | 2.166% | 10179.2084 | 21418.6753 | 18.1709 | 9335.0984 | 825.9391 | 65.0195 | 19437.6963 | 1915.9595 | 793 |  | 1198 | 793-46F | 23414.1115 | 13234.9031 | 1995.4363 | 659.9614 | 443.3375 | 2.7828 | 22246.9463 | 12284.3617 | 1485.4496 | 507.2039 | 67.2596 | 49.0886 | 2.2401 | 39.0451 | 33.3382 | 0 | 27.8328 | 15.3688 | 1.8584 | 0.38165 | 2082.0827 | 1256.1436 | 166.1232 | 238.0939 | 217.2932 | 0 | 1797.914 | 992.7756 | 120.0484 | 46.0747 | 21264.7693 | 11929.6709 | 1827.073 | 382.8224 | 192.7061 | 2.7828 | 20421.1994 | 11276.2173 | 1363.5427 | 460.7475 | 0.002037 | 0.0009958 | 2.56e-05 | 0.017396 | 0.0098834 | 0.0017396 | 0.0007148 | 5000000 | scaled
794-1002 | 176663.8796 | 10326.8513 | 165489.6883 | 847.34 | 5.845% | 93.67% | 0.4796% | 78901.0737 | 164550.9752 | 277.5531 | 71198.4637 | 7425.0569 | 601.9286 | 148303.9955 | 15645.051 | 794 |  | 1199 | 794-1002 | 176663.8796 | 97762.8059 | 12112.9044 | 10326.8513 | 5355.47 | 206.5617 | 165489.6883 | 91559.9959 | 11059.0027 | 847.34 | 631.8583 | 354.3052 | 29.9297 | 418.73 | 236.1035 | 15.0922 | 212.4907 | 117.5641 | 14.1999 | 0.6376 | 16774.8493 | 9349.7924 | 1129.7982 | 2234.1688 | 1270.5262 | 86.2745 | 14463.7075 | 8002.2932 | 966.5507 | 76.9729 | 159257.1721 | 88058.7084 | 10953.1765 | 7673.9524 | 3848.8402 | 105.1949 | 150813.4901 | 83440.1387 | 10078.2521 | 769.7295 | 0.0026544 | 0.0012632 | 3.24e-05 | 0.017252 | 0.0098194 | 0.0017252 | 0.0011848 | 5000000 | scaled
794-15 | 86374.8457 | 6073.1293 | 77552.2355 | 2749.4809 | 7.031% | 89.79% | 3.183% | 37849.0456 | 78391.8536 | 358.9508 | 31979.8376 | 5510.2572 | 681.7234 | 66570.3824 | 11139.7478 | 794 |  | 1200 | 794-15 | 86374.8457 | 48525.8001 | 7982.9921 | 6073.1293 | 2860.0868 | 53.4881 | 77552.2355 | 42916.2323 | 5180.0231 | 2749.4809 | 695.3685 | 336.4177 | 13.6452 | 586.2997 | 275.1366 | 4.4293 | 107 | 59.2122 | 7.147 | 2.0689 | 11973.4932 | 6463.236 | 833.7454 | 3344.8504 | 1576.727 | 24.322 | 8378.878 | 4636.7442 | 559.6587 | 249.7647 | 73705.984 | 41726.1464 | 7135.6016 | 2141.9792 | 1008.2231 | 24.7368 | 69066.3575 | 38220.276 | 4613.2175 | 2497.6473 | 0.0078574 | 0.0035556 | 9.06e-05 | 0.017355 | 0.0098802 | 0.0017356 | 0.0038976 | 5000000 | scaled
795-725AE | 97545.5952 | 0 | 97545.5952 | 0 | 0% | 100% | 0% | 15507.3235 | 32406.7293 | 19.6297 | 14177.3004 | 1310.3934 | 41.0215 | 29627.2878 | 2738.4201 | 795 |  | 1201 | 795-725AE | 97545.5952 | 82038.2717 | 65138.8659 | 0 | 0 | 0 | 97545.5952 | 82038.2717 | 65138.8659 | 0 | 123.4763 | 103.8467 | 82.4549 | 0 | 0 | 0 | 123.4763 | 103.8467 | 82.4549 | 0 | 8242.7576 | 6932.3641 | 5504.3375 | 0 | 0 | 0 | 8242.7576 | 6932.3641 | 5504.3375 | 0 | 89179.3613 | 75002.0609 | 59552.0735 | 0 | 0 | 0 | 89179.3613 | 75002.0609 | 59552.0735 | 0 | 0 | 0 | 0 | 0.017333 | 0.017333 | 0.017333 | 0 | 5000000 | scaled
795-816R | 228765.4086 | 10880.6181 | 212927.0435 | 4957.747 | 4.756% | 93.08% | 2.167% | 100199.1755 | 209440.5679 | 193.545 | 91673.1873 | 8332.4431 | 410.1661 | 191596.9941 | 17433.4077 | 795 |  | 1202 | 795-816R | 228765.4086 | 128566.2331 | 19324.8407 | 10880.6181 | 5816.0248 | 130.3188 | 212927.0435 | 117792.4613 | 14236.7748 | 4957.747 | 432.6836 | 239.1386 | 22.5174 | 157.9767 | 85.5024 | 0.66882 | 270.9763 | 149.9057 | 18.1181 | 3.7305 | 19078.1129 | 10745.6698 | 1644.7051 | 816.4422 | 441.9883 | 3.4366 | 17811.3055 | 9853.3163 | 1190.9034 | 450.3651 | 209254.6121 | 117581.4248 | 17657.6181 | 9906.1991 | 5288.5342 | 126.2134 | 194844.7617 | 107789.2393 | 13027.7533 | 4503.6514 | 0.012253 | 0.0055374 | 0.0001392 | 0.017234 | 0.0098076 | 0.0017234 | 0.0070032 | 5000000 | scaled
795-817AE | 49516.9014 | 0 | 49516.9014 | 0 | 0% | 100% | 0% | 7879.5362 | 16450.4359 | 8.569 | 7227.5093 | 643.4579 | 17.8898 | 15089.1723 | 1343.3738 | 795 |  | 1203 | 795-817AE | 49516.9014 | 41637.3653 | 33066.4655 | 0 | 0 | 0 | 49516.9014 | 41637.3653 | 33066.4655 | 0 | 53.8496 | 45.2806 | 35.9598 | 0 | 0 | 0 | 53.8496 | 45.2806 | 35.9598 | 0 | 4043.644 | 3400.1861 | 2700.2702 | 0 | 0 | 0 | 4043.644 | 3400.1861 | 2700.2702 | 0 | 45419.4078 | 38191.8985 | 30330.2355 | 0 | 0 | 0 | 45419.4078 | 38191.8985 | 30330.2355 | 0 | 0 | 0 | 0 | 0.01743 | 0.01743 | 0.01743 | 0 | 5000000 | scaled
795-821F | 48074.3435 | 8925.093 | 37234.1444 | 1915.1061 | 18.57% | 77.45% | 3.984% | 20584.0857 | 43552.2107 | 123.4917 | 17609.0664 | 2851.5275 | 257.9474 | 37337.7481 | 5956.5153 | 795 |  | 1204 | 795-821F | 48074.3435 | 27490.2578 | 4522.1328 | 8925.093 | 4978.0377 | 122.0848 | 37234.1444 | 20597.114 | 2484.9419 | 1915.1061 | 267.1702 | 143.6785 | 9.2228 | 184.8071 | 97.4732 | 2.3812 | 80.922 | 44.7643 | 5.4006 | 1.4411 | 6501.0076 | 3649.48 | 544.4923 | 960.1708 | 506.677 | 12.3474 | 5366.8672 | 2968.8335 | 358.1754 | 173.9696 | 41306.1658 | 23697.0993 | 3968.4177 | 7780.115 | 4373.8875 | 107.3563 | 31786.3553 | 17583.5163 | 2121.3659 | 1739.6955 | 0.0045624 | 0.0023512 | 5.96e-05 | 0.017514 | 0.009967 | 0.0017514 | 0.0026874 | 5000000 | scaled
796-45 | 28510.9985 | 27775.8112 | 0 | 735.1873 | 97.42% | 0% | 2.579% | 16043.1555 | 27557.989 | 1359.2374 | 3502.1795 | 11181.7386 | 2244.9474 | 7645.3144 | 17667.7273 | 796 |  | 1205 | 796-45 | 28510.9985 | 12467.843 | 953.0095 | 27775.8112 | 11732.6557 | 217.8221 | 0 | 0 | 0 | 735.1873 | 2259.7515 | 900.5141 | 14.8041 | 2259.1983 | 899.9609 | 14.2509 | 0 | 0 | 0 | 0.5532 | 17830.1364 | 6648.3978 | 162.4091 | 17763.3514 | 6581.6129 | 95.6242 | 0 | 0 | 0 | 66.7849 | 8421.1107 | 4918.9311 | 775.7963 | 7753.2614 | 4251.0819 | 107.9471 | 0 | 0 | 0 | 667.8492 | 0.004067 | 0.0021522 | 5.5e-05 | 0 | 0 | 0 | 0.0010496 | 5000000 | scaled
797-32F | 255489.5984 | 0 | 255489.5984 | 0 | 0% | 100% | 0% | 40553.7013 | 84868.483 | 48.3822 | 37185.8811 | 3319.438 | 101.2516 | 77820.5001 | 6946.7313 | 797 |  | 1206 | 797-32F | 255489.5984 | 214935.8971 | 170621.1153 | 0 | 0 | 0 | 255489.5984 | 214935.8971 | 170621.1153 | 0 | 304.8096 | 256.4274 | 203.558 | 0 | 0 | 0 | 304.8096 | 256.4274 | 203.558 | 0 | 20912.5641 | 17593.1261 | 13965.8328 | 0 | 0 | 0 | 20912.5641 | 17593.1261 | 13965.8328 | 0 | 234272.2247 | 197086.3436 | 156451.7245 | 0 | 0 | 0 | 234272.2247 | 197086.3436 | 156451.7245 | 0 | 0 | 0 | 0 | 0.017307 | 0.017307 | 0.017307 | 0 | 5000000 | scaled
797-40F | 5376.487 | 0 | 5376.487 | 0 | 0% | 100% | 0% | 852.4936 | 1786.1636 | 1.6582 | 675.0355 | 175.7999 | 3.4743 | 1414.3494 | 368.3399 | 797 |  | 1207 | 797-40F | 5376.487 | 4523.9934 | 3590.3234 | 0 | 0 | 0 | 5376.487 | 4523.9934 | 3590.3234 | 0 | 10.4578 | 8.7997 | 6.9836 | 0 | 0 | 0 | 10.4578 | 8.7997 | 6.9836 | 0 | 1108.7308 | 932.9309 | 740.3909 | 0 | 0 | 0 | 1108.7308 | 932.9309 | 740.3909 | 0 | 4257.2984 | 3582.2629 | 2842.949 | 0 | 0 | 0 | 4257.2984 | 3582.2629 | 2842.949 | 0 | 0 | 0 | 0 | 0.017636 | 0.017636 | 0.017636 | 0 | 5000000 | scaled
799-504R | 127406.1655 | 126493.8874 | 0 | 912.2781 | 99.28% | 0% | 0.716% | 54531.6511 | 125735.3604 | 9845.7516 | 2561.6311 | 42124.2683 | 22635.4431 | 5292.8411 | 97807.0762 | 799 |  | 1208 | 799-504R | 127406.1655 | 72874.5144 | 1670.805 | 126493.8874 | 71962.2363 | 758.5269 | 0 | 0 | 0 | 912.2781 | 22774.8407 | 12929.089 | 139.3976 | 22774.1542 | 12928.4026 | 138.7111 | 0 | 0 | 0 | 0.68646 | 98433.7235 | 56309.4551 | 626.6472 | 98350.8515 | 56226.5832 | 543.7753 | 0 | 0 | 0 | 82.872 | 6197.6013 | 3635.9702 | 904.7602 | 5368.8817 | 2807.2505 | 76.0405 | 0 | 0 | 0 | 828.7197 | 0.003417 | 0.001645 | 4.22e-05 | 0 | 0 | 0 | 0.0012794 | 5000000 | scaled
80-564 | 31413.6799 | 24430.4678 | 0 | 6983.2121 | 77.77% | 0% | 22.23% | 12189.4465 | 24070.3006 | 102.6151 | 11557.1174 | 529.714 | 186.2203 | 22922.971 | 961.1092 | 80 |  | 1209 | 80-564 | 31413.6799 | 19224.2334 | 7343.3793 | 24430.4678 | 12241.0213 | 360.1672 | 0 | 0 | 0 | 6983.2121 | 193.4328 | 90.8177 | 7.2125 | 188.1782 | 85.563 | 1.9579 | 0 | 0 | 0 | 5.2546 | 1605.5454 | 1075.8314 | 644.4362 | 971.1857 | 441.4717 | 10.0764 | 0 | 0 | 0 | 634.3598 | 29614.7017 | 18057.5843 | 6691.7306 | 23271.104 | 11713.9866 | 348.133 | 0 | 0 | 0 | 6343.5977 | 0.018245 | 0.0084724 | 0.0003282 | 0 | 0 | 0 | 0.009781 | 5000000 | scaled
80-568F | 8328.291 | 2430.3643 | 0 | 5897.9268 | 29.18% | 0% | 70.82% | 1356.6601 | 2392.8963 | 27.3545 | 1188.6225 | 140.683 | 51.4098 | 2077.2917 | 264.1948 | 80 |  | 1210 | 80-568F | 8328.291 | 6971.631 | 5935.3948 | 2430.3643 | 1073.7042 | 37.468 | 0 | 0 | 0 | 5897.9268 | 58.0059 | 30.6513 | 6.5961 | 53.5679 | 26.2133 | 2.1581 | 0 | 0 | 0 | 4.438 | 811.1393 | 670.4563 | 546.9445 | 275.3676 | 134.6846 | 11.1728 | 0 | 0 | 0 | 535.7717 | 7459.1459 | 6270.5233 | 5381.8542 | 2101.4288 | 912.8063 | 24.1371 | 0 | 0 | 0 | 5357.7171 | 0.016622 | 0.0072624 | 0.0001846 | 0 | 0 | 0 | 0.0083946 | 5000000 | scaled
80-575R | 3360.4319 | 2326.0012 | 0 | 1034.4307 | 69.22% | 0% | 30.78% | 1101.4141 | 2297.5292 | 10.8683 | 1034.0461 | 56.4998 | 21.9878 | 2161.2982 | 114.2432 | 80 |  | 1211 | 80-575R | 3360.4319 | 2259.0178 | 1062.9027 | 2326.0012 | 1224.5871 | 28.472 | 0 | 0 | 0 | 1034.4307 | 22.7661 | 11.8979 | 0.77838 | 21.9878 | 11.1195 | 0 | 0 | 0 | 0 | 0.77838 | 208.2116 | 151.7119 | 93.9684 | 114.2432 | 57.7435 | 0 | 0 | 0 | 0 | 93.9684 | 3129.4541 | 2095.4081 | 968.156 | 2189.7702 | 1155.7242 | 28.472 | 0 | 0 | 0 | 939.6839 | 0.0029996 | 0.0013512 | 3.4e-05 | 0 | 0 | 0 | 0.0014508 | 5000000 | scaled
81-177AE | 235.584 | 13.5958 | 0 | 221.9882 | 5.771% | 0% | 94.23% | 7.7074 | 13.4496 | 0 | 7.7074 | 0 | 0 | 13.4496 | 0 | 81 |  | 1212 | 81-177AE | 235.584 | 227.8766 | 222.1344 | 13.5958 | 5.8884 | 0.14621 | 0 | 0 | 0 | 221.9882 | 0.16704 | 0.16704 | 0.16704 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16704 | 20.1656 | 20.1656 | 20.1656 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1656 | 215.2514 | 207.544 | 201.8018 | 13.5958 | 5.8884 | 0.14621 | 0 | 0 | 0 | 201.6556 | 0.0002578 | 0.0001116 | 2.8e-06 | 0 | 0 | 0 | 0.000303 | 5000000 | scaled
81-193AE | 445.7642 | 65.0938 | 0 | 380.6704 | 14.6% | 0% | 85.4% | 36.7428 | 64.3616 | 0 | 36.7428 | 0 | 0 | 64.3616 | 0 | 81 |  | 1213 | 81-193AE | 445.7642 | 409.0214 | 381.4026 | 65.0938 | 28.351 | 0.73217 | 0 | 0 | 0 | 380.6704 | 0.28644 | 0.28644 | 0.28644 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28644 | 34.5804 | 34.5804 | 34.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5804 | 410.8974 | 374.1546 | 346.5358 | 65.0938 | 28.351 | 0.73217 | 0 | 0 | 0 | 345.8036 | 0.0006056 | 0.0002752 | 7.2e-06 | 0 | 0 | 0 | 0.0005352 | 5000000 | scaled
83-622F | 1563.6113 | 405.6146 | 0 | 1157.9967 | 25.94% | 0% | 74.06% | 237.4302 | 401.6591 | 5.4488 | 204.1652 | 27.8162 | 7.4687 | 356.0558 | 38.1345 | 83 |  | 1214 | 83-622F | 1563.6113 | 1326.1811 | 1161.9522 | 405.6146 | 168.1844 | 3.9555 | 0 | 0 | 0 | 1157.9967 | 8.3401 | 2.8913 | 0.87136 | 7.4687 | 2.0199 | 0 | 0 | 0 | 0 | 0.87136 | 143.3277 | 115.5116 | 105.1932 | 38.1345 | 10.3183 | 0 | 0 | 0 | 0 | 105.1932 | 1411.9435 | 1207.7783 | 1055.8876 | 360.0113 | 155.8461 | 3.9555 | 0 | 0 | 0 | 1051.9321 | 0.005349 | 0.0023158 | 5.92e-05 | 0 | 0 | 0 | 0.001611 | 5000000 | scaled
834-887AE | 70346.7137 | 69393.1127 | 0 | 953.601 | 98.64% | 0% | 1.356% | 40585.8959 | 68885.7027 | 11918.4703 | 168.0227 | 28499.4028 | 20187.9884 | 294.566 | 48403.1483 | 834 |  | 1215 | 834-887AE | 70346.7137 | 29760.8178 | 1461.011 | 69393.1127 | 28807.2168 | 507.41 | 0 | 0 | 0 | 953.601 | 20336.7244 | 8418.2541 | 148.736 | 20336.0068 | 8417.5365 | 148.0185 | 0 | 0 | 0 | 0.71755 | 48845.7937 | 20346.3909 | 442.6454 | 48759.1679 | 20259.7651 | 356.0196 | 0 | 0 | 0 | 86.6258 | 1164.1956 | 996.1729 | 869.6296 | 297.9379 | 129.9152 | 3.3719 | 0 | 0 | 0 | 866.2577 | 0.0037534 | 0.0016252 | 4.14e-05 | 0 | 0 | 0 | 0.0013352 | 5000000 | scaled
835-10F | 12413.6752 | 12268.9784 | 0 | 144.6967 | 98.83% | 0% | 1.166% | 6822.1748 | 11782.9977 | 539.3093 | 6.9318 | 6275.9337 | 931.8065 | 12.0906 | 10839.1006 | 835 |  | 1216 | 835-10F | 12413.6752 | 5591.5004 | 630.6775 | 12268.9784 | 5446.8037 | 485.9807 | 0 | 0 | 0 | 144.6967 | 968.5622 | 429.2529 | 36.7557 | 968.4533 | 429.1441 | 36.6468 | 0 | 0 | 0 | 0.10888 | 11301.446 | 5025.5123 | 462.3455 | 11288.3017 | 5012.368 | 449.2011 | 0 | 0 | 0 | 13.1443 | 143.6669 | 136.7351 | 131.5763 | 12.2235 | 5.2916 | 0.13285 | 0 | 0 | 0 | 131.4435 | 0.0008468 | 0.0003666 | 9.2e-06 | 0 | 0 | 0 | 0.0001978 | 5000000 | scaled
835-11F | 139954.9938 | 139435.1597 | 0 | 519.8341 | 99.63% | 0% | 0.3714% | 76261.9972 | 137637.8256 | 10345.6408 | 8.9188 | 65907.4375 | 18650.2909 | 15.5624 | 118971.9723 | 835 |  | 1217 | 835-11F | 139954.9938 | 63692.9966 | 2317.1682 | 139435.1597 | 63173.1625 | 1797.334 | 0 | 0 | 0 | 519.8341 | 18909.5595 | 8563.9186 | 259.2686 | 18909.1683 | 8563.5275 | 258.8774 | 0 | 0 | 0 | 0.39116 | 120557.4814 | 54650.0439 | 1585.5091 | 120510.2593 | 54602.8218 | 1538.287 | 0 | 0 | 0 | 47.2221 | 487.9529 | 479.0341 | 472.3905 | 15.732 | 6.8132 | 0.16962 | 0 | 0 | 0 | 472.2209 | 0.0034416 | 0.0014902 | 3.82e-05 | 0 | 0 | 0 | 0.000745 | 5000000 | scaled
835-35F | 6715.3103 | 6649.6654 | 0 | 65.6449 | 99.02% | 0% | 0.9775% | 4160.4494 | 6649.6599 | 310.7561 | 0.35211 | 3849.3411 | 500.2174 | 0.6142 | 6148.8283 | 835 |  | 1218 | 835-35F | 6715.3103 | 2554.8609 | 65.6504 | 6649.6654 | 2489.216 | 0.0055523 | 0 | 0 | 0 | 65.6449 | 500.2667 | 189.5106 | 0.049396 | 500.2174 | 189.4612 | 0 | 0 | 0 | 0 | 0.049396 | 6154.7916 | 2305.4504 | 5.9632 | 6148.8283 | 2299.4872 | 0 | 0 | 0 | 0 | 5.9632 | 60.252 | 59.8999 | 59.6378 | 0.61975 | 0.26764 | 0.0055523 | 0 | 0 | 0 | 59.6322 | 0.0002176 | 9.42e-05 | 2.4e-06 | 0 | 0 | 0 | 9.78e-05 | 5000000 | scaled
840-308F | 330348.7959 | 328334.851 | 1503.3671 | 510.5778 | 99.39% | 0.4551% | 0.1546% | 177050.0804 | 328442.3519 | 19100.0883 | 596.7559 | 157353.2362 | 35408.7784 | 1217.192 | 291816.3815 | 840 |  | 1219 | 840-308F | 330348.7959 | 153298.7154 | 1906.444 | 328334.851 | 151946.0109 | 1270.9459 | 1503.3671 | 842.1267 | 124.9202 | 510.5778 | 35563.6812 | 16463.5929 | 154.9028 | 35543.7935 | 16452.2836 | 152.898 | 19.5035 | 10.9251 | 1.6206 | 0.38419 | 293004.8224 | 135651.5863 | 1188.441 | 292651.8448 | 135433.4619 | 1116.5835 | 306.5964 | 171.7432 | 25.4762 | 46.3812 | 1780.2922 | 1183.5363 | 563.1002 | 139.2126 | 60.2654 | 1.4644 | 1177.2672 | 659.4584 | 97.8234 | 463.8124 | 0.0038122 | 0.001651 | 4.18e-05 | 0.058713 | 0.033368 | 0.0058714 | 0.0007238 | 5000000 | scaled
840-374 | 232556.2531 | 224795.3124 | 6501.3828 | 1259.5579 | 96.66% | 2.796% | 0.5416% | 142800.4311 | 229510.9652 | 7821.1453 | 2260.9302 | 132718.3556 | 12523.6626 | 4705.5014 | 212281.8012 | 840 |  | 1220 | 840-374 | 232556.2531 | 89755.822 | 3045.2879 | 224795.3124 | 84855.7985 | 1245.5642 | 6501.3828 | 3640.4656 | 540.1658 | 1259.5579 | 12608.7115 | 4787.5662 | 85.0489 | 12535.6103 | 4746.2159 | 78.1063 | 72.1535 | 40.4025 | 5.9949 | 0.94778 | 213673.7447 | 80955.3891 | 1391.9435 | 212230.9161 | 80097.1238 | 1167.1538 | 1328.4095 | 743.8463 | 110.3706 | 114.4191 | 6273.7969 | 4012.8667 | 1568.2955 | 28.7861 | 12.4589 | 0.30411 | 5100.8198 | 2856.2169 | 423.8003 | 1144.191 | 0.003532 | 0.0015294 | 3.82e-05 | 0.058705 | 0.033355 | 0.0058704 | 0.0017702 | 5000000 | scaled
85-498F | 5104.5367 | 4491.6787 | 0 | 612.858 | 87.99% | 0% | 12.01% | 2360.4791 | 4452.803 | 422.4212 | 22.3078 | 1915.7501 | 774.2957 | 39.6113 | 3638.896 | 85 |  | 1221 | 85-498F | 5104.5367 | 2744.0576 | 651.7337 | 4491.6787 | 2131.1996 | 38.8757 | 0 | 0 | 0 | 612.858 | 781.9483 | 359.5272 | 7.6527 | 781.4872 | 359.066 | 7.1915 | 0 | 0 | 0 | 0.46116 | 3725.8353 | 1810.0852 | 86.9393 | 3670.1629 | 1754.4128 | 31.2669 | 0 | 0 | 0 | 55.6724 | 596.7531 | 574.4452 | 557.1418 | 40.0287 | 17.7208 | 0.41737 | 0 | 0 | 0 | 556.7244 | 0.001963 | 0.0008502 | 2.12e-05 | 0 | 0 | 0 | 0.000845 | 5000000 | scaled
85-500F | 4935.9771 | 3009.4572 | 0 | 1926.52 | 60.97% | 0% | 39.03% | 1900.1114 | 3002.0179 | 137.1957 | 767.4035 | 995.5122 | 220.0185 | 1243.5975 | 1538.4018 | 85 |  | 1222 | 85-500F | 4935.9771 | 3035.8658 | 1933.9593 | 3009.4572 | 1109.3458 | 7.4393 | 0 | 0 | 0 | 1926.52 | 221.5675 | 84.3718 | 1.549 | 220.1179 | 82.9222 | 0.09932 | 0 | 0 | 0 | 1.4496 | 1713.914 | 718.4018 | 175.5122 | 1538.9076 | 543.3954 | 0.50579 | 0 | 0 | 0 | 175.0064 | 3000.4956 | 2233.0922 | 1756.8981 | 1250.4317 | 483.0283 | 6.8342 | 0 | 0 | 0 | 1750.0639 | 0.007054 | 0.0030536 | 7.84e-05 | 0 | 0 | 0 | 0.0027566 | 5000000 | scaled
854-607F | 5480.4819 | 5404.5114 | 0 | 75.9705 | 98.61% | 0% | 1.386% | 3089.3798 | 5404.5051 | 211.6047 | 0.45778 | 2877.3173 | 385.9407 | 0.79581 | 5017.7686 | 854 |  | 1223 | 854-607F | 5480.4819 | 2391.1021 | 75.9768 | 5404.5114 | 2315.1316 | 0.0062927 | 0 | 0 | 0 | 75.9705 | 385.9978 | 174.3931 | 0.057165 | 385.9407 | 174.336 | 0 | 0 | 0 | 0 | 0.057165 | 5024.6698 | 2147.3525 | 6.9012 | 5017.7686 | 2140.4513 | 0 | 0 | 0 | 0 | 6.9012 | 69.8142 | 69.3564 | 69.0184 | 0.8021 | 0.34432 | 0.0062927 | 0 | 0 | 0 | 69.0121 | 0.0001542 | 6.68e-05 | 1.6e-06 | 0 | 0 | 0 | 0.0001078 | 5000000 | scaled
855-45 | 68.8384 | 2.7318 | 0 | 66.1067 | 3.968% | 0% | 96.03% | 1.5491 | 2.7021 | 0 | 1.5491 | 0 | 0 | 2.7021 | 0 | 855 |  | 1224 | 855-45 | 68.8384 | 67.2893 | 66.1363 | 2.7318 | 1.1826 | 0.029612 | 0 | 0 | 0 | 66.1067 | 0.049743 | 0.049743 | 0.049743 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049743 | 6.0052 | 6.0052 | 6.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0052 | 62.7835 | 61.2344 | 60.0814 | 2.7318 | 1.1826 | 0.029612 | 0 | 0 | 0 | 60.0517 | 0.0002952 | 0.0001278 | 3.2e-06 | 0 | 0 | 0 | 9.92e-05 | 5000000 | scaled
855-46AE | 188552.8931 | 188332.0556 | 0 | 220.8376 | 99.88% | 0% | 0.1171% | 76497.8833 | 183578.7519 | 13531.6935 | 3.3514 | 62962.8384 | 32292.1581 | 6.7428 | 151279.851 | 855 |  | 1225 | 855-46AE | 188552.8931 | 112055.0099 | 4974.1412 | 188332.0556 | 111834.1723 | 4753.3037 | 0 | 0 | 0 | 220.8376 | 33109.6649 | 19577.9714 | 817.5068 | 33109.4987 | 19577.8052 | 817.3406 | 0 | 0 | 0 | 0.16617 | 155235.7848 | 92272.9465 | 3955.9338 | 155215.7238 | 92252.8854 | 3935.8728 | 0 | 0 | 0 | 20.061 | 207.4434 | 204.092 | 200.7006 | 6.8331 | 3.4816 | 0.090274 | 0 | 0 | 0 | 200.6104 | 0.0007878 | 0.0003996 | 1.02e-05 | 0 | 0 | 0 | 0.000301 | 5000000 | scaled
856-1141R | 34971.9652 | 32716.6652 | 0 | 2255.3 | 93.55% | 0% | 6.449% | 15434.851 | 31932.5483 | 998.2538 | 5393.7083 | 9042.889 | 2045.0318 | 11762.7968 | 18124.7197 | 856 |  | 1226 | 856-1141R | 34971.9652 | 19537.1142 | 3039.4169 | 32716.6652 | 17281.8142 | 784.1169 | 0 | 0 | 0 | 2255.3 | 2104.7481 | 1106.4943 | 59.7163 | 2103.051 | 1104.7973 | 58.0192 | 0 | 0 | 0 | 1.697 | 18910.25 | 9867.361 | 785.5303 | 18705.377 | 9662.488 | 580.6573 | 0 | 0 | 0 | 204.873 | 13956.9672 | 8563.2589 | 2194.1703 | 11908.2372 | 6514.5289 | 145.4404 | 0 | 0 | 0 | 2048.73 | 0.0063318 | 0.0030382 | 7.66e-05 | 0 | 0 | 0 | 0.0031904 | 5000000 | scaled
857-60 | 13599.2185 | 12943.8188 | 0 | 655.3996 | 95.18% | 0% | 4.819% | 7606.1915 | 12736.0393 | 622.1647 | 322.8254 | 6661.2014 | 1020.7799 | 592.4394 | 11122.82 | 857 |  | 1227 | 857-60 | 13599.2185 | 5993.0269 | 863.1791 | 12943.8188 | 5337.6273 | 207.7795 | 0 | 0 | 0 | 655.3996 | 1038.0137 | 415.849 | 17.2338 | 1037.5205 | 415.3558 | 16.7406 | 0 | 0 | 0 | 0.49317 | 11367.1974 | 4705.9961 | 244.3774 | 11307.6605 | 4646.4591 | 184.8404 | 0 | 0 | 0 | 59.537 | 1194.0073 | 871.1819 | 601.568 | 598.6378 | 275.8124 | 6.1985 | 0 | 0 | 0 | 595.3695 | 0.0019314 | 0.0008368 | 2.14e-05 | 0 | 0 | 0 | 0.0008972 | 5000000 | scaled
858-14 | 411696.4919 | 409680.9346 | 0 | 2015.5573 | 99.51% | 0% | 0.4896% | 199609.4376 | 407247.3343 | 20033.9793 | 315.6416 | 179259.8167 | 40716.4689 | 595.3652 | 365935.5003 | 858 |  | 1228 | 858-14 | 411696.4919 | 212087.0543 | 4449.1576 | 409680.9346 | 210071.497 | 2433.6003 | 0 | 0 | 0 | 2015.5573 | 40968.6058 | 20934.6265 | 252.1369 | 40967.0891 | 20933.1099 | 250.6202 | 0 | 0 | 0 | 1.5166 | 368294.0824 | 189034.2656 | 2358.5821 | 368110.9878 | 188851.171 | 2175.4875 | 0 | 0 | 0 | 183.0946 | 2433.8038 | 2118.1621 | 1838.4386 | 602.8577 | 287.2161 | 7.4925 | 0 | 0 | 0 | 1830.9461 | 0.0072454 | 0.003351 | 8.58e-05 | 0 | 0 | 0 | 0.0027974 | 5000000 | scaled
859-1064 | 40252.1639 | 37655.2664 | 0 | 2596.8975 | 93.55% | 0% | 6.452% | 19697.0851 | 37486.3828 | 1722.0802 | 518.1714 | 17456.8335 | 3268.5479 | 1203.8788 | 33013.9562 | 859 |  | 1229 | 859-1064 | 40252.1639 | 20555.0788 | 2765.7811 | 37655.2664 | 17958.1813 | 168.8836 | 0 | 0 | 0 | 2596.8975 | 3286.403 | 1564.3228 | 17.8551 | 3284.4489 | 1562.3687 | 15.9011 | 0 | 0 | 0 | 1.9541 | 33383.6149 | 15926.7814 | 369.6588 | 33147.711 | 15690.8775 | 133.7548 | 0 | 0 | 0 | 235.9039 | 3582.146 | 3063.9746 | 2378.2672 | 1223.1065 | 704.9352 | 19.2278 | 0 | 0 | 0 | 2359.0395 | 0.007832 | 0.0037134 | 9.44e-05 | 0 | 0 | 0 | 0.003737 | 5000000 | scaled
859-13F | 1153855.6719 | 1146359.5944 | 0 | 7496.0775 | 99.35% | 0% | 0.6497% | 506641.863 | 1120558.5386 | 35201.2956 | 30331.987 | 441108.5804 | 77336.217 | 60017.1431 | 983205.1785 | 859 |  | 1230 | 859-13F | 1153855.6719 | 647213.809 | 33297.1333 | 1146359.5944 | 639717.7315 | 25801.0558 | 0 | 0 | 0 | 7496.0775 | 79068.089 | 43866.7934 | 1731.872 | 79062.4484 | 43861.1528 | 1726.2314 | 0 | 0 | 0 | 5.6406 | 1007273.0808 | 566164.5004 | 24067.9023 | 1006592.132 | 565483.5516 | 23386.9535 | 0 | 0 | 0 | 680.9488 | 67514.5021 | 37182.5152 | 7497.359 | 60705.014 | 30373.027 | 687.8709 | 0 | 0 | 0 | 6809.4881 | 0.025073 | 0.01261 | 0.000322 | 0 | 0 | 0 | 0.010604 | 5000000 | scaled
859-42R | 8606971.6622 | 8594825.5955 | 0 | 12146.0667 | 99.86% | 0% | 0.1411% | 4396338.972 | 8486630.2418 | 257152.7233 | 3773.0756 | 4135413.1731 | 494724.3063 | 7137.0506 | 7984768.8849 | 859 |  | 1231 | 859-42R | 8606971.6622 | 4210632.6902 | 120341.4204 | 8594825.5955 | 4198486.6235 | 108195.3537 | 0 | 0 | 0 | 12146.0667 | 501012.3546 | 243859.6312 | 6288.0483 | 501003.2151 | 243850.4917 | 6278.9087 | 0 | 0 | 0 | 9.1395 | 8087700.9649 | 3952287.7918 | 102932.08 | 8086597.6078 | 3951184.4348 | 101828.723 | 0 | 0 | 0 | 1103.357 | 18258.3427 | 14485.2671 | 11121.2922 | 7224.7726 | 3451.697 | 87.722 | 0 | 0 | 0 | 11033.5702 | 0.050053 | 0.023591 | 0.0005994 | 0 | 0 | 0 | 0.017079 | 5000000 | scaled
86-1055F | 1255.142 | 204.4042 | 0 | 1050.7378 | 16.29% | 0% | 83.71% | 105.8421 | 202.5842 | 4.2956 | 79.7128 | 21.8337 | 10.4404 | 139.0521 | 53.0916 | 86 |  | 1232 | 86-1055F | 1255.142 | 1149.2999 | 1052.5578 | 204.4042 | 98.5621 | 1.82 | 0 | 0 | 0 | 1050.7378 | 11.2744 | 6.9788 | 0.834 | 10.4838 | 6.1882 | 0.043354 | 0 | 0 | 0 | 0.79065 | 148.7619 | 126.9282 | 95.6703 | 53.3121 | 31.4784 | 0.22052 | 0 | 0 | 0 | 95.4497 | 1095.1057 | 1015.3929 | 956.0536 | 140.6083 | 60.8955 | 1.5561 | 0 | 0 | 0 | 954.4974 | 0.0027022 | 0.00117 | 3e-05 | 0 | 0 | 0 | 0.001463 | 5000000 | scaled
86-1058F | 461.7444 | 79.1489 | 0 | 382.5955 | 17.14% | 0% | 82.86% | 48.1979 | 79.013 | 6.3536 | 7.2114 | 34.633 | 10.3265 | 12.5644 | 56.1221 | 86 |  | 1233 | 86-1058F | 461.7444 | 413.5464 | 382.7313 | 79.1489 | 30.9509 | 0.13585 | 0 | 0 | 0 | 382.5955 | 10.6144 | 4.2608 | 0.28789 | 10.3265 | 3.9729 | 0 | 0 | 0 | 0 | 0.28789 | 90.8774 | 56.2444 | 34.7552 | 56.1221 | 21.4891 | 0 | 0 | 0 | 0 | 34.7552 | 360.2526 | 353.0413 | 347.6882 | 12.7003 | 5.4889 | 0.13585 | 0 | 0 | 0 | 347.5524 | 0.0007632 | 0.0003306 | 8.4e-06 | 0 | 0 | 0 | 0.0005362 | 5000000 | scaled
86-552F | 186635.7188 | 173007.8388 | 0 | 13627.88 | 92.7% | 0% | 7.302% | 95344.9181 | 171990.377 | 11148.6516 | 4154.022 | 80042.2445 | 20138.5285 | 7368.5473 | 144483.3012 | 86 |  | 1234 | 86-552F | 186635.7188 | 91290.8007 | 14645.3418 | 173007.8388 | 77662.9207 | 1017.4618 | 0 | 0 | 0 | 13627.88 | 20271.2898 | 9122.6382 | 132.7613 | 20261.0353 | 9112.3837 | 122.5068 | 0 | 0 | 0 | 10.2545 | 146525.3702 | 66483.1257 | 2042.069 | 145287.4042 | 65245.1597 | 804.1031 | 0 | 0 | 0 | 1237.966 | 19839.0588 | 15685.0368 | 12470.5115 | 7459.3993 | 3305.3773 | 90.852 | 0 | 0 | 0 | 12379.6595 | 0.038655 | 0.016862 | 0.0004298 | 0 | 0 | 0 | 0.019321 | 5000000 | scaled
87-41AE | 281.5697 | 75.7 | 0 | 205.8697 | 26.88% | 0% | 73.12% | 50.8741 | 74.9808 | 6.4632 | 8.8773 | 35.5335 | 9.2217 | 15.2722 | 50.487 | 87 |  | 1235 | 87-41AE | 281.5697 | 230.6956 | 206.5889 | 75.7 | 24.8259 | 0.71912 | 0 | 0 | 0 | 205.8697 | 9.4582 | 2.995 | 0.23649 | 9.3033 | 2.8401 | 0.081584 | 0 | 0 | 0 | 0.15491 | 69.6445 | 34.111 | 19.1575 | 50.9432 | 15.4096 | 0.45616 | 0 | 0 | 0 | 18.7013 | 202.467 | 193.5897 | 187.1949 | 15.4535 | 6.5762 | 0.18138 | 0 | 0 | 0 | 187.0135 | 0.0005918 | 0.0002564 | 6.6e-06 | 0 | 0 | 0 | 0.0003068 | 5000000 | scaled
88-27F | 2224.5134 | 2059.3238 | 0 | 165.1896 | 92.57% | 0% | 7.426% | 1369.6755 | 2059.0218 | 146.4946 | 18.7121 | 1204.4687 | 222.4468 | 32.7506 | 1803.8243 | 88 |  | 1236 | 88-27F | 2224.5134 | 854.8379 | 165.4917 | 2059.3238 | 689.6483 | 0.30205 | 0 | 0 | 0 | 165.1896 | 222.5711 | 76.0765 | 0.1243 | 222.4468 | 75.9522 | 0 | 0 | 0 | 0 | 0.1243 | 1818.8303 | 614.3615 | 15.0059 | 1803.8243 | 599.3556 | 0 | 0 | 0 | 0 | 15.0059 | 183.1121 | 164.3999 | 150.3614 | 33.0527 | 14.3405 | 0.30205 | 0 | 0 | 0 | 150.0594 | 0.0005646 | 0.0002446 | 6.2e-06 | 0 | 0 | 0 | 0.000241 | 5000000 | scaled
90-24 | 27778.0233 | 355.4902 | 26774.0357 | 648.4973 | 1.28% | 96.39% | 2.335% | 12134.5565 | 25340.282 | 14.8712 | 10973.426 | 1146.2592 | 31.1415 | 22908.781 | 2400.3594 | 90 |  | 1237 | 90-24 | 27778.0233 | 15643.4668 | 2437.7413 | 355.4902 | 153.9117 | 3.8278 | 26774.0357 | 14841.0578 | 1785.4162 | 648.4973 | 33.8545 | 18.9833 | 2.713 | 0 | 0 | 0 | 33.3666 | 18.4953 | 2.225 | 0.48797 | 2630.7731 | 1484.5138 | 230.4136 | 0 | 0 | 0 | 2571.8631 | 1425.6039 | 171.5037 | 58.9099 | 25113.3957 | 14139.9697 | 2204.6147 | 355.4902 | 153.9117 | 3.8278 | 24168.8061 | 13396.9586 | 1611.6875 | 589.0994 | 0.001091 | 0.0004722 | 1.16e-05 | 0.0052006 | 0.0029654 | 0.00052 | 0.000907 | 5000000 | scaled
90-32 | 76419.3748 | 4659.1594 | 68681.1747 | 3079.0407 | 6.097% | 89.87% | 4.029% | 33118.3136 | 68703.3642 | 47.0293 | 30239.3564 | 2831.9279 | 98.3441 | 62667.1607 | 5937.8595 | 90 |  | 1238 | 90-32 | 76419.3748 | 43301.0612 | 7716.0106 | 4659.1594 | 2099.8645 | 47.9204 | 68681.1747 | 38122.156 | 4589.0495 | 3079.0407 | 105.9308 | 58.9016 | 7.5867 | 24.7434 | 12.8068 | 0 | 78.8705 | 43.7779 | 5.2699 | 2.3169 | 6633.6426 | 3801.7147 | 695.7832 | 126.7398 | 65.544 | 0 | 6227.2007 | 3456.4685 | 416.081 | 279.7022 | 69679.8013 | 39440.4449 | 7012.6406 | 4507.6762 | 2021.5137 | 47.9204 | 62375.1034 | 34621.9096 | 4167.6986 | 2797.0216 | 0.0065356 | 0.0028674 | 7.18e-05 | 0.0051544 | 0.0029428 | 0.0005154 | 0.004326 | 5000000 | scaled
90-44AE | 101370.2827 | 11901.6974 | 86871.4396 | 2597.1457 | 11.74% | 85.7% | 2.562% | 45106.5489 | 92927.4703 | 42.5924 | 41963.328 | 3100.6284 | 89.3858 | 86331.0131 | 6507.0714 | 90 |  | 1239 | 90-44AE | 101370.2827 | 56263.7339 | 8442.8124 | 11901.6974 | 5470.4015 | 138.8226 | 86871.4396 | 48196.1867 | 5706.8441 | 2597.1457 | 97.7233 | 55.1308 | 8.3374 | 0 | 0 | 0 | 95.769 | 53.1766 | 6.3832 | 1.9543 | 7206.9911 | 4106.3627 | 699.9197 | 0 | 0 | 0 | 6971.0646 | 3870.4362 | 463.9932 | 235.9265 | 94065.5684 | 52102.2404 | 7734.5553 | 11901.6974 | 5470.4015 | 138.8226 | 79804.606 | 44272.574 | 5236.4678 | 2359.2649 | 0.0063122 | 0.0027892 | 7.12e-05 | 0.0051548 | 0.0029444 | 0.0005154 | 0.0036324 | 5000000 | scaled
90-49 | 11953.6023 | 46.8832 | 11485.2228 | 421.4963 | 0.3922% | 96.08% | 3.526% | 5137.8129 | 10765.0349 | 6.0768 | 4705.4965 | 426.2396 | 12.7434 | 9858.4408 | 893.8507 | 90 |  | 1240 | 90-49 | 11953.6023 | 6815.7894 | 1188.5674 | 46.8832 | 20.3445 | 0.50526 | 11485.2228 | 6373.9486 | 766.5658 | 421.4963 | 13.972 | 7.8952 | 1.2285 | 0 | 0 | 0 | 13.6548 | 7.578 | 0.91137 | 0.31716 | 996.0652 | 569.8256 | 102.2145 | 0 | 0 | 0 | 957.7762 | 531.5366 | 63.9255 | 38.289 | 10943.5651 | 6238.0686 | 1085.1244 | 46.8832 | 20.3445 | 0.50526 | 10513.7918 | 5834.834 | 701.729 | 382.8901 | 0.0007436 | 0.0003224 | 7.8e-06 | 0.005195 | 0.0029656 | 0.0005194 | 0.0006066 | 5000000 | scaled
90-50F | 23591.4416 | 607.9727 | 22258.4972 | 724.9717 | 2.577% | 94.35% | 3.073% | 10253.1656 | 21373.8766 | 11.1952 | 9393.2277 | 848.7427 | 23.4701 | 19571.063 | 1779.3435 | 90 |  | 1241 | 90-50F | 23591.4416 | 13338.276 | 2217.5651 | 607.9727 | 263.2562 | 6.6273 | 22258.4972 | 12350.0481 | 1485.966 | 724.9717 | 25.6946 | 14.4994 | 2.2245 | 0 | 0 | 0 | 25.1491 | 13.9539 | 1.6789 | 0.54552 | 1972.486 | 1123.7433 | 193.1425 | 0 | 0 | 0 | 1906.6291 | 1057.8864 | 127.2856 | 65.8569 | 21593.261 | 12200.0333 | 2022.1981 | 607.9727 | 263.2562 | 6.6273 | 20326.7191 | 11278.2078 | 1357.0015 | 658.5693 | 0.0015584 | 0.0006748 | 1.72e-05 | 0.0051708 | 0.0029512 | 0.000517 | 0.0010102 | 5000000 | scaled
900-1118F | 3820.8776 | 3634.7172 | 0 | 186.1604 | 95.13% | 0% | 4.872% | 1820.7274 | 3591.8037 | 195.5658 | 6.0418 | 1619.1198 | 375.3886 | 10.5955 | 3205.8196 | 900 |  | 1242 | 900-1118F | 3820.8776 | 2000.1502 | 229.0739 | 3634.7172 | 1813.9898 | 42.9135 | 0 | 0 | 0 | 186.1604 | 380.4331 | 184.8673 | 5.0445 | 380.2931 | 184.7272 | 4.9045 | 0 | 0 | 0 | 0.14008 | 3260.624 | 1641.5042 | 54.8044 | 3243.7131 | 1624.5933 | 37.8935 | 0 | 0 | 0 | 16.9109 | 179.8204 | 173.7786 | 169.2249 | 10.7111 | 4.6693 | 0.11552 | 0 | 0 | 0 | 169.1094 | 0.0008482 | 0.0003672 | 9.4e-06 | 0 | 0 | 0 | 0.000255 | 5000000 | scaled
900-1119F | 3064.5099 | 2960.9553 | 0 | 103.5546 | 96.62% | 0% | 3.379% | 1875.2312 | 2946.1824 | 82.6863 | 1316.8785 | 475.6664 | 120.7862 | 2141.5089 | 683.8873 | 900 |  | 1243 | 900-1119F | 3064.5099 | 1189.2787 | 118.3275 | 2960.9553 | 1085.7241 | 14.7729 | 0 | 0 | 0 | 103.5546 | 120.8641 | 38.1778 | 0.077922 | 120.7862 | 38.0998 | 0 | 0 | 0 | 0 | 0.077922 | 693.2943 | 217.6279 | 9.407 | 683.8873 | 208.2209 | 0 | 0 | 0 | 0 | 9.407 | 2250.3516 | 933.473 | 108.8427 | 2156.2818 | 839.4033 | 14.7729 | 0 | 0 | 0 | 94.0697 | 0.0001838 | 7.96e-05 | 2e-06 | 0 | 0 | 0 | 0.0001502 | 5000000 | scaled
900-1163F | 288.1943 | 121.5237 | 0 | 166.6706 | 42.17% | 0% | 57.83% | 73.9173 | 121.1187 | 8.7216 | 19.8579 | 45.3378 | 14.0483 | 34.3621 | 72.7084 | 900 |  | 1244 | 900-1163F | 288.1943 | 214.277 | 167.0755 | 121.5237 | 47.6064 | 0.40495 | 0 | 0 | 0 | 166.6706 | 14.1737 | 5.4521 | 0.12541 | 14.0483 | 5.3267 | 0 | 0 | 0 | 0 | 0.12541 | 87.8488 | 42.511 | 15.1405 | 72.7084 | 27.3706 | 0 | 0 | 0 | 0 | 15.1405 | 186.1717 | 166.3138 | 151.8097 | 34.767 | 14.9091 | 0.40495 | 0 | 0 | 0 | 151.4047 | 0.0005962 | 0.000258 | 6.6e-06 | 0 | 0 | 0 | 0.000244 | 5000000 | scaled
900-1166F | 30059.1077 | 29287.2172 | 0 | 771.8905 | 97.43% | 0% | 2.568% | 14033.7123 | 28795.326 | 1226.5151 | 1185.1573 | 11622.0399 | 2507.9533 | 2014.1489 | 24273.2238 | 900 |  | 1245 | 900-1166F | 30059.1077 | 16025.3954 | 1263.7817 | 29287.2172 | 15253.5049 | 491.8912 | 0 | 0 | 0 | 771.8905 | 2549.6031 | 1323.088 | 41.6497 | 2549.0222 | 1322.5072 | 41.0689 | 0 | 0 | 0 | 0.58082 | 24772.661 | 13150.6211 | 499.4372 | 24702.5419 | 13080.502 | 429.3182 | 0 | 0 | 0 | 70.1191 | 2736.8436 | 1551.6863 | 722.6947 | 2035.653 | 850.4957 | 21.5041 | 0 | 0 | 0 | 701.1906 | 0.0028668 | 0.0012412 | 3.14e-05 | 0 | 0 | 0 | 0.0010992 | 5000000 | scaled
901-1124 | 225481.3871 | 223882.7468 | 0 | 1598.6403 | 99.29% | 0% | 0.709% | 116210.9319 | 220937.8997 | 8529.7904 | 107.5858 | 107573.5557 | 16199.4443 | 206.5302 | 204531.9252 | 901 |  | 1246 | 901-1124 | 225481.3871 | 109270.4553 | 4543.4874 | 223882.7468 | 107671.8149 | 2944.8471 | 0 | 0 | 0 | 1598.6403 | 16423.7454 | 7893.955 | 224.301 | 16422.5424 | 7892.7521 | 223.0981 | 0 | 0 | 0 | 1.2029 | 207396.3482 | 99822.7925 | 2864.4231 | 207251.1266 | 99677.5709 | 2719.2015 | 0 | 0 | 0 | 145.2216 | 1661.2935 | 1553.7078 | 1454.7633 | 209.0777 | 101.4919 | 2.5475 | 0 | 0 | 0 | 1452.2158 | 0.0064902 | 0.002919 | 7.42e-05 | 0 | 0 | 0 | 0.0022642 | 5000000 | scaled
902-364F | 3003.6457 | 2897.4226 | 0 | 106.223 | 96.46% | 0% | 3.536% | 1505.777 | 2897.4226 | 223.3712 | 0 | 1282.4058 | 426.6922 | 0 | 2470.7304 | 902 |  | 1247 | 902-364F | 3003.6457 | 1497.8687 | 106.223 | 2897.4226 | 1391.6456 | 0 | 0 | 0 | 0 | 106.223 | 426.7721 | 203.4009 | 0.079929 | 426.6922 | 203.321 | 0 | 0 | 0 | 0 | 0.079929 | 2480.3798 | 1197.974 | 9.6494 | 2470.7304 | 1188.3246 | 0 | 0 | 0 | 0 | 9.6494 | 96.4937 | 96.4937 | 96.4937 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4937 | 0.0003096 | 0.000134 | 3.2e-06 | 0 | 0 | 0 | 0.0001492 | 5000000 | scaled
902-48 | 11256.8936 | 9341.6239 | 0 | 1915.2696 | 82.99% | 0% | 17.01% | 4294.1312 | 9231.8497 | 230.1843 | 3298.6775 | 765.2694 | 628.0901 | 6364.1318 | 2239.6277 | 902 |  | 1248 | 902-48 | 11256.8936 | 6962.7623 | 2025.0439 | 9341.6239 | 5047.4927 | 109.7743 | 0 | 0 | 0 | 1915.2696 | 636.8601 | 406.6758 | 8.77 | 635.419 | 405.2346 | 7.3289 | 0 | 0 | 0 | 1.4412 | 2440.0157 | 1674.7463 | 200.388 | 2266.0313 | 1500.7619 | 26.4036 | 0 | 0 | 0 | 173.9844 | 8180.0177 | 4881.3402 | 1815.8859 | 6440.1737 | 3141.4962 | 76.0418 | 0 | 0 | 0 | 1739.8441 | 0.006123 | 0.0029336 | 7.42e-05 | 0 | 0 | 0 | 0.0026862 | 5000000 | scaled
907-1475 | 4281.3573 | 0 | 4281.3573 | 0 | 0% | 100% | 0% | 1909.1124 | 3995.6034 | 2.1632 | 1566.8934 | 340.0558 | 4.5274 | 3279.3692 | 711.7067 | 907 |  | 1249 | 907-1475 | 4281.3573 | 2372.2449 | 285.754 | 0 | 0 | 0 | 4281.3573 | 2372.2449 | 285.754 | 0 | 4.8512 | 2.688 | 0.32378 | 0 | 0 | 0 | 4.8512 | 2.688 | 0.32378 | 0 | 762.6059 | 422.5501 | 50.8992 | 0 | 0 | 0 | 762.6059 | 422.5501 | 50.8992 | 0 | 3513.9002 | 1947.0068 | 234.531 | 0 | 0 | 0 | 3513.9002 | 1947.0068 | 234.531 | 0 | 0 | 0 | 0 | 0.017589 | 0.010025 | 0.0017588 | 0 | 5000000 | scaled
907-1562AE | 8439769.2215 | 8238563.7109 | 198305.696 | 2899.8146 | 97.62% | 2.35% | 0.03436% | 4013180.7227 | 8327696.0564 | 260197.5577 | 79621.2533 | 3673361.9118 | 538937.0192 | 165466.9792 | 7623292.058 | 907 |  | 1250 | 907-1562AE | 8439769.2215 | 4426588.4988 | 112073.1651 | 8238563.7109 | 4313215.5206 | 93423.2435 | 198305.696 | 110473.1636 | 15750.107 | 2899.8146 | 545175.3162 | 284977.7586 | 6238.297 | 544938.6657 | 284844.9576 | 6217.4927 | 234.4685 | 130.6189 | 18.6223 | 2.182 | 7712228.8554 | 4038866.9437 | 88936.7974 | 7693463.2824 | 4028296.248 | 87203.873 | 18502.1519 | 10307.2745 | 1469.5033 | 263.4211 | 182365.0499 | 102743.7965 | 16898.0706 | 161.7628 | 74.315 | 1.8778 | 179569.0756 | 100035.2701 | 14261.9814 | 2634.2114 | 0.010825 | 0.005405 | 0.0001372 | 0.039964 | 0.022651 | 0.0039964 | 0.0040772 | 5000000 | scaled
907-1602 | 257241.9108 | 253809.0484 | 3328.7428 | 104.1196 | 98.67% | 1.294% | 0.04048% | 148074.4684 | 256915.3817 | 7195.4073 | 1177.2363 | 139701.8249 | 12491.1138 | 2464.3073 | 241959.9606 | 907 |  | 1251 | 907-1602 | 257241.9108 | 109167.4424 | 326.5291 | 253809.0484 | 107218.167 | 0.02406 | 3328.7428 | 1845.1557 | 222.3854 | 104.1196 | 12491.4922 | 5296.0849 | 0.37836 | 12486.9232 | 5293.5173 | 0 | 4.4907 | 2.4892 | 0.30001 | 0.078347 | 242015.3062 | 102313.4814 | 55.3457 | 241318.9899 | 101923.2907 | 0 | 686.8581 | 380.7324 | 45.8874 | 9.4583 | 2735.1124 | 1557.8761 | 270.8051 | 3.1354 | 1.359 | 0.02406 | 2637.394 | 1461.9341 | 176.1981 | 94.583 | 0.0003734 | 0.0001618 | 4e-06 | 0.017601 | 0.010036 | 0.0017602 | 0.000156 | 5000000 | scaled
907-1604 | 17843.8974 | 14868.8055 | 2939.958 | 35.1338 | 83.33% | 16.48% | 0.1969% | 4490.0201 | 17611.9015 | 189.166 | 1109.4367 | 3191.4174 | 785.1153 | 2291.415 | 14535.3712 | 907 |  | 1252 | 907-1604 | 17843.8974 | 13353.8772 | 231.9958 | 14868.8055 | 11691.9762 | 0.55597 | 2939.958 | 1626.7672 | 196.306 | 35.1338 | 785.2718 | 596.1058 | 0.15648 | 783.2978 | 595.0017 | 0 | 1.9476 | 1.0777 | 0.13004 | 0.026437 | 14577.7451 | 11386.3277 | 42.3739 | 13987.7428 | 11058.4361 | 0 | 586.8108 | 324.7001 | 39.1824 | 3.1916 | 2480.8804 | 1371.4437 | 189.4654 | 97.765 | 38.5384 | 0.55597 | 2351.1996 | 1300.9895 | 156.9936 | 31.9158 | 3.84e-05 | 1.66e-05 | 4e-07 | 0.017653 | 0.010049 | 0.0017654 | 4.72e-05 | 5000000 | scaled
907-1702R | 9100558.2495 | 9075653.9508 | 21331.0684 | 3573.2304 | 99.73% | 0.2344% | 0.03926% | 4777838.8418 | 9009865.4738 | 314389.3014 | 8886.6092 | 4454562.9312 | 594017.7557 | 18362.3941 | 8397485.3241 | 907 |  | 1253 | 907-1702R | 9100558.2495 | 4322719.4077 | 90692.7757 | 9075653.9508 | 4307262.7847 | 85424.2928 | 21331.0684 | 11883.3926 | 1695.2526 | 3573.2304 | 599845.8196 | 285456.5182 | 5828.0639 | 599811.4234 | 285436.1654 | 5822.8553 | 31.7075 | 17.664 | 2.5199 | 2.6887 | 8477564.7915 | 4023001.8602 | 80079.4674 | 8475221.8088 | 4021552.8354 | 79594.4646 | 2018.3879 | 1124.4301 | 160.4082 | 324.5947 | 23147.6384 | 14261.0292 | 4785.2444 | 620.7185 | 273.7838 | 6.9729 | 19280.973 | 10741.2985 | 1532.3245 | 3245.9469 | 0.015464 | 0.0075954 | 0.0001998 | 0.040564 | 0.022988 | 0.0040564 | 0.0050506 | 5000000 | scaled
907-1716R | 27066455.1952 | 26848173.2279 | 210320.852 | 7961.1153 | 99.19% | 0.7771% | 0.02941% | 12326391.6987 | 26708682.7078 | 1071746.161 | 88488.5899 | 11166156.9478 | 2325062.3326 | 188637.6363 | 24194982.7389 | 907 |  | 1254 | 907-1716R | 27066455.1952 | 14740063.4965 | 357772.4875 | 26848173.2279 | 14614903.3275 | 333128.7078 | 210320.852 | 117199.0536 | 16682.6644 | 7961.1153 | 2354358.4803 | 1282612.3193 | 29296.1478 | 2354045.8757 | 1282435.4714 | 29265.8366 | 306.6141 | 170.8575 | 24.3207 | 5.9905 | 24500846.7949 | 13334689.8472 | 305864.0561 | 24481067.239 | 13323347.6989 | 303629.3109 | 19056.3628 | 10618.9551 | 1511.552 | 723.1932 | 211249.92 | 122761.3301 | 22612.2837 | 13060.1132 | 9120.1573 | 233.5603 | 190957.875 | 106409.2411 | 15146.7917 | 7231.9317 | 0.03686 | 0.020215 | 0.0005132 | 0.039975 | 0.022666 | 0.0039974 | 0.011214 | 5000000 | scaled
907-2820R | 6348475.522 | 6346945.6016 | 509.5288 | 1020.3916 | 99.98% | 0.008026% | 0.01607% | 1358429.8852 | 6193713.8519 | 107929.4098 | 209.5146 | 1250290.9608 | 490561.3513 | 443.0387 | 5702709.4619 | 907 |  | 1255 | 907-2820R | 6348475.522 | 4990045.6367 | 154761.67 | 6346945.6016 | 4988739.9984 | 153697.5735 | 509.5288 | 285.2468 | 43.7049 | 1020.3916 | 502760.1389 | 394830.7291 | 12198.7876 | 502757.4368 | 394828.8784 | 12197.8539 | 1.9344 | 1.0829 | 0.16592 | 0.76781 | 5844305.0373 | 4594014.0765 | 141595.5754 | 5844171.7996 | 4593898.6855 | 141499.4046 | 40.5447 | 22.6979 | 3.4777 | 92.6931 | 1410.3457 | 1200.8311 | 967.307 | 16.3652 | 12.4344 | 0.31502 | 467.0498 | 261.4659 | 40.0613 | 926.9307 | 0.0088778 | 0.006717 | 0.0001704 | 0.072148 | 0.040886 | 0.0072148 | 0.0014532 | 5000000 | scaled
908-1172R | 15766518.7901 | 15502577.8274 | 256475.2349 | 7465.7277 | 98.33% | 1.627% | 0.04735% | 6449163.5477 | 15484271.5554 | 451454.9926 | 103330.8457 | 5894377.7093 | 1085436.1529 | 216743.4872 | 14182091.9153 | 908 |  | 1256 | 908-1172R | 15766518.7901 | 9317355.2424 | 282247.2347 | 15502577.8274 | 9164786.292 | 250811.786 | 256475.2349 | 145103.2227 | 23969.721 | 7465.7277 | 1103160.2976 | 651705.305 | 17724.1447 | 1102824.6641 | 651512.9778 | 17687.6843 | 330.0158 | 186.7095 | 30.8427 | 5.6177 | 14418070.7149 | 8523693.0055 | 235978.7996 | 14392994.1137 | 8509211.1892 | 233020.3757 | 24398.4093 | 13803.6244 | 2280.2321 | 678.1918 | 245287.7776 | 141956.9319 | 28544.2904 | 6759.0497 | 4062.1249 | 103.726 | 231746.8098 | 131112.8888 | 21658.6462 | 6781.9182 | 0.030402 | 0.017682 | 0.0004486 | 0.16599 | 0.094407 | 0.016599 | 0.010535 | 5000000 | scaled
908-1236 | 11763931.114 | 11622998.1269 | 137018.798 | 3914.1891 | 98.8% | 1.165% | 0.03327% | 6333096.3708 | 11600021.2241 | 507127.8197 | 54425.0177 | 5771543.5334 | 927715.2123 | 113522.5392 | 10558783.4727 | 908 |  | 1257 | 908-1236 | 11763931.114 | 5430834.7432 | 163909.8899 | 11622998.1269 | 5349391.584 | 147190.8152 | 137018.798 | 77528.9701 | 12804.8856 | 3914.1891 | 939603.481 | 432475.6614 | 11888.2688 | 939416.4016 | 432368.528 | 11868.1155 | 184.1341 | 104.1881 | 17.208 | 2.9453 | 10695608.2921 | 4924064.7587 | 136824.8194 | 10682902.4246 | 4916721.0548 | 135315.0731 | 12350.2999 | 6988.1363 | 1154.1787 | 355.5676 | 128719.3409 | 74294.3232 | 15196.8017 | 679.3007 | 302.0012 | 7.6266 | 124484.364 | 70436.6457 | 11633.4989 | 3555.6762 | 0.015917 | 0.0075894 | 0.0001922 | 0.16628 | 0.094587 | 0.016628 | 0.005501 | 5000000 | scaled
908-1269 | 1247.3865 | 0 | 1247.3865 | 0 | 0% | 100% | 0% | 38.9644 | 81.6746 | 0.02559 | 30.8932 | 8.0455 | 0.05364 | 64.7564 | 16.8646 | 908 |  | 1258 | 908-1269 | 1247.3865 | 1208.4221 | 1165.7119 | 0 | 0 | 0 | 1247.3865 | 1208.4221 | 1165.7119 | 0 | 0.81923 | 0.79364 | 0.76559 | 0 | 0 | 0 | 0.81923 | 0.79364 | 0.76559 | 0 | 257.5661 | 249.5206 | 240.7016 | 0 | 0 | 0 | 257.5661 | 249.5206 | 240.7016 | 0 | 989.0011 | 958.1079 | 924.2447 | 0 | 0 | 0 | 989.0011 | 958.1079 | 924.2447 | 0 | 0 | 0 | 0 | 0.16645 | 0.16645 | 0.16645 | 0 | 5000000 | scaled
908-1368R | 5570792.9034 | 5361811.1093 | 196688.6844 | 12293.1097 | 96.25% | 3.531% | 0.2207% | 2645951.3172 | 5470060.3056 | 161968.7563 | 77164.5506 | 2406818.0103 | 335935.3135 | 161170.37 | 4972954.6221 | 908 |  | 1259 | 908-1368R | 5570792.9034 | 2924841.5862 | 100732.5977 | 5361811.1093 | 2801316.8513 | 70074.1297 | 196688.6844 | 111231.6252 | 18365.3584 | 12293.1097 | 340557.5482 | 178588.7919 | 4622.2347 | 340279.7987 | 178427.6996 | 4587.914 | 268.4994 | 151.8421 | 25.0705 | 9.2502 | 5041461.7919 | 2634643.7816 | 68507.1698 | 5019664.7102 | 2621831.8806 | 65459.4731 | 20680.3671 | 11695.1865 | 1930.9822 | 1116.7145 | 188773.5633 | 111609.0127 | 27603.1933 | 1866.6004 | 1057.2711 | 26.7426 | 175739.8179 | 99384.5966 | 16409.3057 | 11167.145 | 0.054917 | 0.029845 | 0.0007654 | 0.16418 | 0.093351 | 0.016418 | 0.017342 | 5000000 | scaled
908-1370R | 1466276.1601 | 1346128.9144 | 115909.3001 | 4237.9456 | 91.81% | 7.905% | 0.289% | 726729.0178 | 1436439.0559 | 49092.1251 | 46091.991 | 631544.9018 | 96361.1954 | 96152.4292 | 1243925.4314 | 908 |  | 1260 | 908-1370R | 1466276.1601 | 739547.1422 | 29837.1042 | 1346128.9144 | 669724.3685 | 14777.1777 | 115909.3001 | 65584.8281 | 10821.9809 | 4237.9456 | 97459.5268 | 48367.4017 | 1098.3314 | 97330.3607 | 48292.9313 | 1083.3805 | 125.9771 | 71.2815 | 11.762 | 3.1889 | 1258975.8385 | 627430.9367 | 15050.4071 | 1248096.5979 | 621108.0021 | 13685.6225 | 10494.2627 | 5937.9568 | 979.8067 | 384.9779 | 109840.7948 | 63748.8038 | 13688.3657 | 701.9557 | 323.4351 | 8.1747 | 105289.0603 | 59575.5899 | 9830.4122 | 3849.7788 | 0.017878 | 0.008708 | 0.0002214 | 0.16393 | 0.093257 | 0.016393 | 0.0059986 | 5000000 | scaled
908-1372R | 7960290.3283 | 7828738.2327 | 129010.0921 | 2542.0035 | 98.35% | 1.621% | 0.03193% | 4590307.3503 | 7828879.1675 | 385057.4398 | 51763.0816 | 4153486.8289 | 656826.306 | 107776.4025 | 7064276.459 | 908 |  | 1261 | 908-1372R | 7960290.3283 | 3369982.978 | 131411.1608 | 7828738.2327 | 3294454.3354 | 116830.5953 | 129010.0921 | 72986.6391 | 12038.562 | 2542.0035 | 666702.7483 | 281645.3085 | 9876.4423 | 666543.6225 | 281554.4534 | 9859.8592 | 157.2131 | 88.9423 | 14.6703 | 1.9128 | 7172551.3896 | 3019064.5607 | 108274.9307 | 7160635.9608 | 3012223.2053 | 106953.6745 | 11684.5115 | 6610.4381 | 1090.3389 | 230.9173 | 121036.1903 | 69273.1088 | 13259.7878 | 1558.6494 | 676.6766 | 17.0616 | 117168.3676 | 66287.2588 | 10933.5528 | 2309.1734 | 0.010694 | 0.0048966 | 0.000124 | 0.16274 | 0.092571 | 0.016274 | 0.0035764 | 5000000 | scaled
908-2038R | 41258574.2326 | 40800963.6338 | 444898.9658 | 12711.633 | 98.89% | 1.078% | 0.03081% | 16271216.5211 | 40522238.5415 | 1203869.608 | 177058.8046 | 14890288.1085 | 3007234.6337 | 372483.9887 | 37142519.9191 | 908 |  | 1262 | 908-2038R | 41258574.2326 | 24987357.7115 | 736335.6911 | 40800963.6338 | 24723028.7724 | 682162.3913 | 444898.9658 | 251617.3061 | 41461.6668 | 12711.633 | 3058247.7783 | 1854378.1704 | 51013.1447 | 3057666.8608 | 1854045.4708 | 50950.3333 | 571.3525 | 323.1344 | 53.2463 | 9.5651 | 37778588.0076 | 22888299.8991 | 636068.0884 | 37736334.0634 | 22863901.0732 | 631083.178 | 41099.2108 | 23244.0925 | 3830.177 | 1154.7334 | 421738.4467 | 244679.642 | 49254.458 | 6962.7096 | 5082.2283 | 128.88 | 403228.4026 | 228050.0792 | 37578.2435 | 11547.3345 | 0.053569 | 0.033238 | 0.000845 | 0.15924 | 0.09056 | 0.015924 | 0.017728 | 5000000 | scaled
908-2040 | 3646804.7891 | 3351774.2424 | 291221.4671 | 3809.0796 | 91.91% | 7.986% | 0.1044% | 1896570.4428 | 3584585.3199 | 160039.1164 | 116496.4764 | 1620034.85 | 302010.2555 | 243106.0325 | 3039469.0319 | 908 |  | 1263 | 908-2040 | 3646804.7891 | 1750234.3463 | 62219.4692 | 3351774.2424 | 1581689.2184 | 31269.2611 | 291221.4671 | 164736.0483 | 27141.1285 | 3809.0796 | 304929.824 | 144890.7076 | 2919.5686 | 304415.363 | 144598.4462 | 2869.023 | 511.5948 | 289.3952 | 47.6794 | 2.8662 | 3070642.6651 | 1450607.8151 | 31173.6332 | 3043736.4145 | 1435237.3966 | 28352.2652 | 26560.2312 | 15024.3991 | 2475.3486 | 346.0194 | 271232.3 | 154735.8236 | 28126.2674 | 3622.4649 | 1853.3756 | 47.9729 | 264149.6411 | 149422.254 | 24618.1005 | 3460.194 | 0.014493 | 0.0068036 | 0.0001732 | 0.15948 | 0.090724 | 0.015948 | 0.0053198 | 5000000 | scaled
908-2055F | 22564078.3354 | 22357448.5426 | 198388.4941 | 8241.2987 | 99.08% | 0.8792% | 0.03652% | 10473797.7786 | 22266707.7429 | 730159.2287 | 87025.705 | 9656612.8449 | 1555343.3359 | 181400.4449 | 20529963.9621 | 908 |  | 1264 | 908-2055F | 22564078.3354 | 12090280.5569 | 297370.5926 | 22357448.5426 | 11969795.0317 | 270643.292 | 198388.4941 | 112244.2265 | 18486.0019 | 8241.2987 | 1574568.3684 | 844409.1397 | 19225.0325 | 1574236.4418 | 844218.6496 | 19188.4798 | 325.7252 | 184.2888 | 30.3513 | 6.2013 | 20783955.8144 | 11127342.9695 | 253991.8523 | 20760862.0032 | 11113951.8781 | 251161.0663 | 22345.1659 | 12642.4462 | 2082.1408 | 748.6452 | 205554.1527 | 118528.4477 | 24153.7078 | 22350.0975 | 11624.504 | 293.7459 | 175717.603 | 99417.4915 | 16373.5097 | 7486.4522 | 0.032573 | 0.018146 | 0.0004602 | 0.15939 | 0.09069 | 0.015939 | 0.011582 | 5000000 | scaled
908-2062F | 153311.4846 | 151129.2584 | 2081.3926 | 100.8336 | 98.58% | 1.358% | 0.06577% | 19431.782 | 152145.3979 | 1035.8405 | 917.0359 | 17478.9057 | 7786.9076 | 2083.9665 | 142274.5238 | 908 |  | 1265 | 908-2062F | 153311.4846 | 133879.7026 | 1166.0867 | 151129.2584 | 132600.4003 | 871.2801 | 2081.3926 | 1178.4686 | 193.973 | 100.8336 | 7845.6303 | 6809.7898 | 58.7228 | 7837.6527 | 6805.24 | 57.9105 | 7.9018 | 4.4739 | 0.7364 | 0.075874 | 143105.6002 | 125626.6945 | 831.0764 | 142930.818 | 125523.7606 | 806.4816 | 165.6224 | 93.7742 | 15.435 | 9.1598 | 2360.2541 | 1443.2182 | 276.2876 | 360.7878 | 271.3997 | 6.888 | 1907.8683 | 1080.2205 | 177.8016 | 91.598 | 0.000292 | 0.000222 | 5.8e-06 | 0.16011 | 0.09116 | 0.016011 | 0.0001464 | 5000000 | scaled
908-30 | 847523.9719 | 818047.126 | 28215.9668 | 1260.8791 | 96.52% | 3.329% | 0.1488% | 370713.4533 | 833494.9268 | 20721.9885 | 11694.5121 | 338296.9527 | 46545.6099 | 24519.9118 | 762429.405 | 908 |  | 1266 | 908-30 | 847523.9719 | 476810.5186 | 14029.0451 | 818047.126 | 459573.122 | 10139.7012 | 28215.9668 | 15976.5175 | 2628.4649 | 1260.8791 | 47154.2187 | 26432.2302 | 608.6088 | 47098.2745 | 26400.1418 | 602.5369 | 54.9954 | 31.1397 | 5.1231 | 0.94877 | 772300.3894 | 434003.4367 | 9870.9844 | 769633.422 | 432443.6551 | 9518.6733 | 2552.4283 | 1445.2425 | 237.772 | 114.5391 | 28069.3638 | 16374.8517 | 3549.4519 | 1315.4295 | 729.3252 | 18.491 | 25608.543 | 14500.1353 | 2385.5697 | 1145.3912 | 0.0048142 | 0.0026722 | 6.8e-05 | 0.15912 | 0.090616 | 0.015912 | 0.0017858 | 5000000 | scaled
909-451 | 55252374.6886 | 54850768.6606 | 388366.8417 | 13239.1863 | 99.27% | 0.7029% | 0.02396% | 26028485.4876 | 54506211.8088 | 1449668.9619 | 152060.1856 | 24426756.3401 | 3031840.0722 | 317060.3479 | 51157311.3887 | 909 |  | 1267 | 909-451 | 55252374.6886 | 29223889.201 | 746162.8798 | 54850768.6606 | 28990820.1219 | 696066.3932 | 388366.8417 | 219829.8928 | 36857.3004 | 13239.1863 | 3070975.3735 | 1621306.4116 | 39135.3013 | 3070321.4788 | 1620931.96 | 39064.2278 | 643.9326 | 364.4895 | 61.1113 | 9.9621 | 51819465.4936 | 27392709.1535 | 662154.1049 | 51776041.8001 | 27367607.8396 | 656944.5319 | 42221.0368 | 23898.6571 | 4006.9163 | 1202.6567 | 361933.8215 | 209873.6359 | 44873.4736 | 4405.3818 | 2280.3223 | 57.6334 | 345501.8723 | 195566.7461 | 32789.2727 | 12026.5675 | 0.065456 | 0.033837 | 0.0008576 | 0.22712 | 0.1291 | 0.022712 | 0.018541 | 5000000 | scaled
909-453R | 5703040.2921 | 5701153.2251 | 0 | 1887.067 | 99.97% | 0% | 0.03309% | 2413992.0353 | 5630810.4665 | 120305.0522 | 3128.8881 | 2290558.095 | 280484.709 | 7528.7608 | 5342796.9967 | 909 |  | 1268 | 909-453R | 5703040.2921 | 3289048.2568 | 72229.8256 | 5701153.2251 | 3287161.1899 | 70342.7586 | 0 | 0 | 0 | 1887.067 | 284012.6777 | 163707.6255 | 3527.9687 | 284011.2578 | 163706.2056 | 3526.5488 | 0 | 0 | 0 | 1.42 | 5409668.4593 | 3119110.3644 | 66871.4626 | 5409497.0369 | 3118938.9419 | 66700.0402 | 0 | 0 | 0 | 171.4225 | 9359.155 | 6230.2669 | 1830.3942 | 7644.9305 | 4516.0424 | 116.1697 | 0 | 0 | 0 | 1714.2245 | 0.0071514 | 0.0042492 | 0.0001076 | 0 | 0 | 0 | 0.0026414 | 5000000 | scaled
909-458R | 1603.9455 | 0 | 1603.9455 | 0 | 0% | 100% | 0% | 76.0702 | 158.1586 | 0.049959 | 60.3129 | 15.7073 | 0.10387 | 125.3974 | 32.6573 | 909 |  | 1269 | 909-458R | 1603.9455 | 1527.8753 | 1445.7868 | 0 | 0 | 0 | 1603.9455 | 1527.8753 | 1445.7868 | 0 | 1.0534 | 1.0034 | 0.94953 | 0 | 0 | 0 | 1.0534 | 1.0034 | 0.94953 | 0 | 331.1901 | 315.4828 | 298.5328 | 0 | 0 | 0 | 331.1901 | 315.4828 | 298.5328 | 0 | 1271.702 | 1211.3891 | 1146.3045 | 0 | 0 | 0 | 1271.702 | 1211.3891 | 1146.3045 | 0 | 0 | 0 | 0 | 0.10322 | 0.10322 | 0.10322 | 0 | 5000000 | scaled
909-805R | 32313161.0224 | 32075252.6475 | 228761.1805 | 9147.1943 | 99.26% | 0.708% | 0.02831% | 16303374.9729 | 31858639.8912 | 1430483.5192 | 87995.272 | 14784896.1818 | 2793497.8944 | 183665.1612 | 28881476.8356 | 909 |  | 1270 | 909-805R | 32313161.0224 | 16009786.0494 | 454521.1312 | 32075252.6475 | 15871098.5015 | 423615.7956 | 228761.1805 | 129540.3537 | 21758.1413 | 9147.1943 | 2830695.1999 | 1400211.6808 | 37197.3055 | 2830435.7561 | 1400061.7804 | 37166.4008 | 252.5609 | 143.0174 | 24.0218 | 6.883 | 29271351.7902 | 14486455.6084 | 389874.9546 | 29242969.5547 | 14470023.2264 | 386423.5331 | 27551.2981 | 15601.4446 | 2620.4841 | 830.9374 | 211114.0323 | 123118.7603 | 27448.8711 | 1847.3367 | 1013.4947 | 25.8617 | 200957.3216 | 113795.8916 | 19113.6354 | 8309.3739 | 0.038947 | 0.019128 | 0.0004926 | 0.2374 | 0.13497 | 0.02374 | 0.012868 | 5000000 | scaled
909-812 | 62983.815 | 62909.2092 | 0 | 74.6058 | 99.88% | 0% | 0.1185% | 10202.5758 | 62908.004 | 497.7233 | 22.1728 | 9682.6797 | 3122.432 | 87.3063 | 59698.2657 | 909 |  | 1271 | 909-812 | 62983.815 | 52781.2392 | 75.811 | 62909.2092 | 52706.6334 | 1.2052 | 0 | 0 | 0 | 74.6058 | 3122.4882 | 2624.7648 | 0.056138 | 3122.432 | 2624.7087 | 0 | 0 | 0 | 0 | 0.056138 | 59705.0429 | 50022.3632 | 6.7772 | 59698.2657 | 50015.586 | 0 | 0 | 0 | 0 | 6.7772 | 156.2839 | 134.1111 | 68.9776 | 88.5116 | 66.3388 | 1.2052 | 0 | 0 | 0 | 67.7724 | 7.7e-05 | 5.86e-05 | 1.6e-06 | 0 | 0 | 0 | 0.0001016 | 5000000 | scaled
91-7F | 1295990.6131 | 1243883.9508 | 46695.1161 | 5411.5462 | 95.98% | 3.603% | 0.4176% | 704689.552 | 1276063.3512 | 72278.055 | 21317.8593 | 611093.6377 | 130398.1447 | 44288.3529 | 1101376.8536 | 91 |  | 1272 | 91-7F | 1295990.6131 | 591301.0612 | 19927.2619 | 1243883.9508 | 559933.9225 | 11387.2797 | 46695.1161 | 25955.5925 | 3128.436 | 5411.5462 | 131619.2742 | 59341.2192 | 1221.1295 | 131550.5243 | 59301.1958 | 1212.7243 | 64.6779 | 35.9513 | 4.3332 | 4.072 | 1112265.5459 | 501171.9082 | 10888.6923 | 1107561.3463 | 498338.7297 | 10114.8712 | 4212.611 | 2341.5899 | 282.2326 | 491.5886 | 52105.793 | 30787.9338 | 7817.4401 | 4772.0802 | 2293.9969 | 59.6843 | 42417.8273 | 23578.0512 | 2841.8702 | 4915.8856 | 0.021299 | 0.010032 | 0.0002536 | 0.0051654 | 0.0029522 | 0.0005166 | 0.0075736 | 5000000 | scaled
916-381 | 590912.2199 | 419985.2503 | 169793.7042 | 1133.2654 | 71.07% | 28.73% | 0.1918% | 311603.5595 | 564399.9136 | 23294.2523 | 66033.3983 | 222275.9089 | 40265.5393 | 137604.0169 | 386530.3574 | 916 |  | 1273 | 916-381 | 590912.2199 | 279308.6604 | 26512.3063 | 419985.2503 | 183357.996 | 11843.8255 | 169793.7042 | 94817.3989 | 13535.2154 | 1133.2654 | 41392.9317 | 18098.6794 | 1127.3924 | 41180.5307 | 17979.6923 | 1109.676 | 211.5483 | 118.1343 | 16.8637 | 0.85275 | 398972.9509 | 176697.042 | 12442.5935 | 378717.5141 | 165340.3996 | 10733.178 | 20152.4901 | 11253.6958 | 1606.4688 | 102.9466 | 150546.3373 | 84512.939 | 12942.3204 | 87.2055 | 37.9041 | 0.9715 | 149429.6658 | 83445.5688 | 11911.8828 | 1029.4661 | 0.0049452 | 0.002169 | 5.52e-05 | 0.043307 | 0.024616 | 0.0043306 | 0.0015824 | 5000000 | scaled
92-619F | 202868.905 | 95111.7094 | 105659.8808 | 2097.3149 | 46.88% | 52.08% | 1.034% | 98011.7206 | 193935.0295 | 5247.1639 | 43469.3008 | 49295.2559 | 9814.5596 | 91498.4214 | 92622.0485 | 92 |  | 1274 | 92-619F | 202868.905 | 104857.1845 | 8933.8755 | 95111.7094 | 44141.2295 | 335.1636 | 105659.8808 | 58618.64 | 6501.397 | 2097.3149 | 9864.8107 | 4617.6467 | 50.251 | 9720.5388 | 4536.5995 | 39.2588 | 142.6937 | 79.4691 | 9.4141 | 1.5782 | 93672.0109 | 44376.7551 | 1049.9624 | 84770.8655 | 39337.1523 | 289.0221 | 8710.6238 | 4849.0812 | 570.4188 | 190.5215 | 99332.0834 | 55862.7827 | 7833.6621 | 620.305 | 267.4777 | 6.8827 | 96806.5632 | 53690.0898 | 5921.5641 | 1905.2152 | 0.0075474 | 0.0035034 | 8.84e-05 | 0.0050952 | 0.0029198 | 0.0005096 | 0.002974 | 5000000 | scaled
920-1342R | 3406645.8369 | 3384146.9602 | 18401.7954 | 4097.0813 | 99.34% | 0.5402% | 0.1203% | 1857974.405 | 3342348.0297 | 174092.8131 | 7533.866 | 1676347.7259 | 313068.5531 | 15588.8107 | 3013690.6658 | 920 |  | 1275 | 920-1342R | 3406645.8369 | 1548671.4319 | 64297.8072 | 3384146.9602 | 1534297.8933 | 58733.0828 | 18401.7954 | 10276.4573 | 1467.6431 | 4097.0813 | 318482.3624 | 144389.5493 | 5413.8093 | 318445.5127 | 144367.6093 | 5408.0333 | 33.7668 | 18.857 | 2.6931 | 3.0829 | 3067558.0588 | 1391210.3329 | 53867.393 | 3064941.1308 | 1389584.5757 | 53316.1806 | 2244.7463 | 1253.5755 | 179.0307 | 372.1817 | 20605.4157 | 13071.5497 | 5016.605 | 760.3167 | 345.7083 | 8.869 | 16123.2823 | 9004.0248 | 1285.9193 | 3721.8167 | 0.019161 | 0.0088308 | 0.0002244 | 0.043669 | 0.024817 | 0.0043668 | 0.0057742 | 5000000 | scaled
920-735AE | 1554327.9958 | 1072819.5036 | 475895.1821 | 5613.3101 | 69.02% | 30.62% | 0.3611% | 803332.7844 | 1500918.3455 | 61978.4251 | 193241.5234 | 548112.8359 | 110604.2471 | 403050.2418 | 987263.8566 | 920 |  | 1276 | 920-735AE | 1554327.9958 | 750995.2114 | 53409.6502 | 1072819.5036 | 479251.5907 | 9910.3987 | 475895.1821 | 266130.3105 | 37885.9414 | 5613.3101 | 111719.7324 | 49741.3073 | 1115.4853 | 111087.2836 | 49385.7673 | 1061.2486 | 628.2249 | 351.3162 | 50.0129 | 4.2238 | 999783.7079 | 451670.8719 | 12519.8512 | 959217.4366 | 428760.6231 | 8821.0542 | 40056.3543 | 22400.3319 | 3188.8801 | 509.9169 | 442824.5555 | 249583.0321 | 39774.3137 | 2514.7834 | 1105.2004 | 28.096 | 435210.6028 | 243378.6624 | 34647.0484 | 5099.1693 | 0.018109 | 0.0079322 | 0.0002028 | 0.042651 | 0.024278 | 0.0042652 | 0.0079306 | 5000000 | scaled
920-823 | 458218.8554 | 313174.6394 | 142701.2251 | 2342.9909 | 68.35% | 31.14% | 0.5113% | 244807.5427 | 441923.223 | 11798.3703 | 55734.49 | 177274.6824 | 20159.8133 | 116142.5492 | 305620.8605 | 920 |  | 1277 | 920-823 | 458218.8554 | 213411.3127 | 16295.6324 | 313174.6394 | 131309.3218 | 2580.551 | 142701.2251 | 79759 | 11372.0905 | 2342.9909 | 20353.8058 | 8555.4355 | 193.9925 | 20164.1575 | 8448.6591 | 177.2566 | 187.8853 | 105.0134 | 14.9729 | 1.763 | 309594.6108 | 132319.9285 | 3973.7503 | 292241.342 | 122526.9087 | 2394.963 | 17140.43 | 9580.1809 | 1365.9485 | 212.8389 | 128270.4388 | 72535.9488 | 12127.8896 | 769.1399 | 333.7541 | 8.3315 | 125372.9099 | 70073.8057 | 9991.1692 | 2128.389 | 0.0078276 | 0.003389 | 8.58e-05 | 0.043436 | 0.024706 | 0.0043436 | 0.0033132 | 5000000 | scaled
921-800F | 1991710.705 | 1525774.588 | 461353.2381 | 4582.8788 | 76.61% | 23.16% | 0.2301% | 1002903.6739 | 1932609.2345 | 89116.8719 | 184402.8725 | 729383.9295 | 167505.3705 | 384372.9253 | 1380730.9387 | 921 |  | 1278 | 921-800F | 1991710.705 | 988807.0311 | 59101.4705 | 1525774.588 | 726386.6572 | 17783.7835 | 461353.2381 | 257837.495 | 36734.8082 | 4582.8788 | 169523.4661 | 80406.5942 | 2018.0956 | 168973.5006 | 80097.7125 | 1971.1312 | 546.517 | 305.4332 | 43.5159 | 3.4485 | 1400548.1543 | 671164.2248 | 19817.2156 | 1354783.5438 | 645404.0099 | 15790.0891 | 45348.2987 | 25343.903 | 3610.8147 | 416.3119 | 421639.0846 | 237236.2121 | 37266.1593 | 2017.5437 | 884.9347 | 22.5632 | 415458.4225 | 232188.1589 | 33080.4776 | 4163.1185 | 0.016136 | 0.0072936 | 0.0001848 | 0.04277 | 0.024327 | 0.004277 | 0.0064302 | 5000000 | scaled
922-1143F | 20704.9718 | 18349.4334 | 0 | 2355.5383 | 88.62% | 0% | 11.38% | 10896.8665 | 18324.8167 | 736.8191 | 2116.4944 | 8043.553 | 1227.7395 | 3804.808 | 13292.2692 | 922 |  | 1279 | 922-1143F | 20704.9718 | 9808.1053 | 2380.1551 | 18349.4334 | 7452.5669 | 24.6167 | 0 | 0 | 0 | 2355.5383 | 1230.8284 | 494.0093 | 3.0889 | 1229.0559 | 492.2369 | 1.3164 | 0 | 0 | 0 | 1.7725 | 13513.3066 | 5469.7535 | 221.0374 | 13299.3279 | 5255.7748 | 7.0587 | 0 | 0 | 0 | 213.9787 | 5960.8368 | 3844.3424 | 2156.0288 | 3821.0496 | 1704.5552 | 16.2416 | 0 | 0 | 0 | 2139.7872 | 0.0063826 | 0.0028538 | 7.3e-05 | 0 | 0 | 0 | 0.0032882 | 5000000 | scaled
928-19 | 434883.4222 | 432579.0699 | 1170.2784 | 1134.074 | 99.47% | 0.2691% | 0.2608% | 256561.8644 | 432561.4402 | 25764.0844 | 427.1269 | 230370.653 | 43355.3972 | 882.2546 | 388323.7884 | 928 |  | 1280 | 928-19 | 434883.4222 | 178321.5578 | 2321.982 | 432579.0699 | 176534.1329 | 1094.5178 | 1170.2784 | 653.351 | 93.3902 | 1134.074 | 43482.3048 | 17718.2204 | 126.9076 | 43466.2692 | 17708.891 | 124.8427 | 15.1823 | 8.4761 | 1.2116 | 0.85335 | 389415.1132 | 159044.4601 | 1091.3248 | 389073.4268 | 158808.1958 | 969.2587 | 238.6663 | 133.2443 | 19.046 | 103.0201 | 1986.0042 | 1558.8773 | 1103.7496 | 39.3739 | 17.0461 | 0.41638 | 916.4298 | 511.6306 | 73.1327 | 1030.2006 | 0.0063088 | 0.0027314 | 6.9e-05 | 0.043868 | 0.024921 | 0.0043868 | 0.0015796 | 5000000 | scaled
928-20 | 27174.8805 | 25293.1414 | 1772.3766 | 109.3625 | 93.08% | 6.522% | 0.4024% | 19630.1764 | 26924.0933 | 1122.1246 | 675.5954 | 17832.4563 | 1547.9758 | 1407.5617 | 23968.5558 | 928 |  | 1281 | 928-20 | 27174.8805 | 7544.7041 | 250.7872 | 25293.1414 | 6445.5834 | 0.015917 | 1772.3766 | 989.7583 | 141.4088 | 109.3625 | 1548.5427 | 426.4181 | 0.56689 | 1542.3866 | 422.944 | 0 | 6.0738 | 3.3918 | 0.4846 | 0.082292 | 23997.5351 | 6165.0787 | 28.9793 | 23748.8999 | 6021.8452 | 0 | 238.7006 | 133.2989 | 19.0447 | 9.9346 | 1628.8027 | 953.2073 | 221.241 | 1.8548 | 0.79418 | 0.015917 | 1527.6022 | 853.0675 | 121.8795 | 99.3456 | 0.0003394 | 0.000147 | 3.8e-06 | 0.043873 | 0.02493 | 0.0043874 | 0.0001498 | 5000000 | scaled
93-10R | 302332.107 | 274241.4904 | 22080.6379 | 6009.9786 | 90.71% | 7.303% | 1.988% | 168808.2546 | 290921.0119 | 23780.7437 | 10702.962 | 134324.5489 | 40556.6198 | 21883.4455 | 228480.9467 | 93 |  | 1282 | 93-10R | 302332.107 | 133523.8524 | 11411.0951 | 274241.4904 | 115232.6336 | 3927.2989 | 22080.6379 | 12281.2401 | 1473.8175 | 6009.9786 | 41152.4224 | 17371.6787 | 595.8026 | 41116.4361 | 17349.6561 | 589.1802 | 31.464 | 17.5003 | 2.1001 | 4.5223 | 232455.1171 | 98130.5681 | 3974.1704 | 230072.7109 | 96563.1818 | 3305.6418 | 1836.4556 | 1021.4357 | 122.578 | 545.9506 | 28724.5675 | 18021.6055 | 6841.1221 | 3052.3434 | 1319.7957 | 32.4769 | 20212.7184 | 11242.3042 | 1349.1394 | 5459.5057 | 0.022255 | 0.0097084 | 0.0002456 | 0.0051418 | 0.0029412 | 0.0005142 | 0.0084186 | 5000000 | scaled
93-559R | 194929.5535 | 174931.1644 | 15428.484 | 4569.9051 | 89.74% | 7.915% | 2.344% | 96926.8375 | 187417.4506 | 12378.9243 | 7408.3911 | 77139.522 | 23705.8303 | 15552.9046 | 148158.7158 | 93 |  | 1283 | 93-559R | 194929.5535 | 98002.716 | 7512.1028 | 174931.1644 | 84860.8981 | 1912.7929 | 15428.484 | 8571.9128 | 1029.4048 | 4569.9051 | 23989.0773 | 11610.1529 | 283.247 | 23963.4069 | 11594.3626 | 278.325 | 22.2316 | 12.3517 | 1.4833 | 3.4387 | 150261.9301 | 73122.4081 | 2103.2143 | 148588.8083 | 72008.3488 | 1604.1467 | 1257.9885 | 698.9259 | 83.9343 | 415.1333 | 20678.5461 | 13270.155 | 5125.6415 | 2378.9491 | 1258.1867 | 30.3213 | 14148.2639 | 7860.6352 | 943.9871 | 4151.3331 | 0.015124 | 0.0068938 | 0.0001758 | 0.0051478 | 0.0029416 | 0.0005148 | 0.0063986 | 5000000 | scaled
933-472F | 165868.0735 | 164254.131 | 0 | 1613.9425 | 99.03% | 0% | 0.973% | 92256.8679 | 163389.7404 | 9584.0656 | 283.9919 | 82388.8104 | 16879.987 | 496.5551 | 146013.1982 | 933 |  | 1284 | 933-472F | 165868.0735 | 73611.2056 | 2478.3331 | 164254.131 | 71997.2631 | 864.3906 | 0 | 0 | 0 | 1613.9425 | 16974.2601 | 7390.1945 | 94.273 | 16973.0456 | 7388.98 | 93.0586 | 0 | 0 | 0 | 1.2144 | 146925.4257 | 64536.6153 | 912.2275 | 146778.8141 | 64390.0037 | 765.6158 | 0 | 0 | 0 | 146.6116 | 1968.3877 | 1684.3958 | 1471.8326 | 502.2713 | 218.2794 | 5.7162 | 0 | 0 | 0 | 1466.1164 | 0.0056296 | 0.002438 | 6.24e-05 | 0 | 0 | 0 | 0.0022608 | 5000000 | scaled
936-188 | 105840.3918 | 104307.2955 | 0 | 1533.0964 | 98.55% | 0% | 1.448% | 50227.3663 | 102594.217 | 7956.7997 | 66.7333 | 42203.8333 | 16153.1912 | 159.6425 | 86281.3833 | 936 |  | 1285 | 936-188 | 105840.3918 | 55613.0255 | 3246.1748 | 104307.2955 | 54079.9292 | 1713.0784 | 0 | 0 | 0 | 1533.0964 | 16420.3773 | 8463.5776 | 267.1861 | 16419.2237 | 8462.424 | 266.0325 | 0 | 0 | 0 | 1.1536 | 87865.3238 | 45661.4905 | 1583.9405 | 87726.0563 | 45522.223 | 1444.6729 | 0 | 0 | 0 | 139.2675 | 1554.6907 | 1487.9574 | 1395.0483 | 162.0155 | 95.2822 | 2.373 | 0 | 0 | 0 | 1392.6752 | 0.004989 | 0.002498 | 6.32e-05 | 0 | 0 | 0 | 0.0021378 | 5000000 | scaled
94-16F | 4481.6178 | 2736.7616 | 0 | 1744.8562 | 61.07% | 0% | 38.93% | 1237.2815 | 2670.7217 | 68.5931 | 817.9627 | 350.7258 | 164.2091 | 1578.2066 | 928.306 | 94 |  | 1286 | 94-16F | 4481.6178 | 3244.3363 | 1810.8961 | 2736.7616 | 1499.4801 | 66.0399 | 0 | 0 | 0 | 1744.8562 | 171.9899 | 103.3968 | 7.7808 | 170.677 | 102.0839 | 6.4678 | 0 | 0 | 0 | 1.3129 | 1129.9539 | 779.2281 | 201.6479 | 971.4499 | 620.7241 | 43.1439 | 0 | 0 | 0 | 158.5039 | 3179.6741 | 2361.7114 | 1601.4674 | 1594.6347 | 776.6721 | 16.4281 | 0 | 0 | 0 | 1585.0393 | 0.0051144 | 0.0022826 | 5.76e-05 | 0 | 0 | 0 | 0.0024696 | 5000000 | scaled
94-24F | 46366.9888 | 42508.972 | 0 | 3858.0168 | 91.68% | 0% | 8.321% | 26126.6224 | 42446.1944 | 4091.5579 | 1924.9193 | 20110.1452 | 6657.5764 | 3393.4297 | 32395.1883 | 94 |  | 1287 | 94-24F | 46366.9888 | 20240.3664 | 3920.7944 | 42508.972 | 16382.3496 | 62.7775 | 0 | 0 | 0 | 3858.0168 | 6669.2861 | 2577.7282 | 11.7097 | 6666.3831 | 2574.8252 | 8.8067 | 0 | 0 | 0 | 2.903 | 32774.2438 | 12664.0986 | 379.0555 | 32423.7789 | 12313.6337 | 28.5906 | 0 | 0 | 0 | 350.4649 | 6923.4589 | 4998.5396 | 3530.0292 | 3418.81 | 1493.8906 | 25.3802 | 0 | 0 | 0 | 3504.6489 | 0.015485 | 0.0067058 | 0.0001704 | 0 | 0 | 0 | 0.0054372 | 5000000 | scaled
94-41 | 189671.1123 | 183388.528 | 0 | 6282.5843 | 96.69% | 0% | 3.312% | 97958.8909 | 181121.1379 | 9753.2878 | 45608.4903 | 42597.1129 | 18566.9262 | 80140.1162 | 82414.0955 | 94 |  | 1288 | 94-41 | 189671.1123 | 91712.2214 | 8549.9744 | 183388.528 | 85429.6371 | 2267.39 | 0 | 0 | 0 | 6282.5843 | 18818.1594 | 9064.8716 | 251.2332 | 18813.4319 | 9060.1442 | 246.5057 | 0 | 0 | 0 | 4.7274 | 84111.1321 | 41514.0193 | 1697.0366 | 83540.4178 | 40943.305 | 1126.3223 | 0 | 0 | 0 | 570.7143 | 86741.8208 | 41133.3305 | 6601.7046 | 81034.6782 | 35426.1879 | 894.562 | 0 | 0 | 0 | 5707.1426 | 0.027077 | 0.011781 | 0.0002988 | 0 | 0 | 0 | 0.0089338 | 5000000 | scaled
940-391 | 1110.6279 | 307.1215 | 0 | 803.5064 | 27.65% | 0% | 72.35% | 174.255 | 303.7379 | 0.040989 | 174.0052 | 0.2088 | 0.040989 | 303.4881 | 0.2088 | 940 |  | 1289 | 940-391 | 1110.6279 | 936.3728 | 806.89 | 307.1215 | 132.8665 | 3.3836 | 0 | 0 | 0 | 803.5064 | 0.6456 | 0.60461 | 0.60461 | 0.040989 | 0 | 0 | 0 | 0 | 0 | 0.60461 | 73.1999 | 72.9911 | 72.9911 | 0.2088 | 0 | 0 | 0 | 0 | 0 | 72.9911 | 1036.7824 | 862.7772 | 733.2943 | 306.8717 | 132.8665 | 3.3836 | 0 | 0 | 0 | 729.9107 | 0.0031928 | 0.0013824 | 3.5e-05 | 0 | 0 | 0 | 0.0011462 | 5000000 | scaled
941-33F | 24789.0578 | 17875.3836 | 0 | 6913.6742 | 72.11% | 0% | 27.89% | 9340.1748 | 17738.639 | 456.032 | 7426.5518 | 1457.5909 | 962.989 | 13647.6757 | 3127.9743 | 941 |  | 1290 | 941-33F | 24789.0578 | 15448.883 | 7050.4188 | 17875.3836 | 8535.2089 | 136.7446 | 0 | 0 | 0 | 6913.6742 | 973.1989 | 517.1669 | 10.2099 | 967.9966 | 511.9646 | 5.0076 | 0 | 0 | 0 | 5.2023 | 3771.699 | 2314.108 | 643.7246 | 3143.6561 | 1686.0651 | 15.6817 | 0 | 0 | 0 | 628.0429 | 20044.1599 | 12617.6081 | 6396.4842 | 13763.731 | 6337.1792 | 116.0553 | 0 | 0 | 0 | 6280.429 | 0.018767 | 0.008177 | 0.000207 | 0 | 0 | 0 | 0.0097068 | 5000000 | scaled
946-25F | 394.0743 | 74.0527 | 0 | 320.0216 | 18.79% | 0% | 81.21% | 42.0009 | 73.2324 | 0 | 42.0009 | 0 | 0 | 73.2324 | 0 | 946 |  | 1291 | 946-25F | 394.0743 | 352.0734 | 320.8418 | 74.0527 | 32.0518 | 0.82027 | 0 | 0 | 0 | 320.0216 | 0.24081 | 0.24081 | 0.24081 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24081 | 29.071 | 29.071 | 29.071 | 0 | 0 | 0 | 0 | 0 | 0 | 29.071 | 364.7625 | 322.7616 | 291.5301 | 74.0527 | 32.0518 | 0.82027 | 0 | 0 | 0 | 290.7098 | 0.0011374 | 0.0004924 | 1.26e-05 | 0 | 0 | 0 | 0.0004462 | 5000000 | scaled
948-5R | 3649.3933 | 3290.352 | 0 | 359.0413 | 90.16% | 0% | 9.838% | 1713.7151 | 3181.3392 | 197.9613 | 597.8588 | 917.895 | 340.8031 | 1288.4405 | 1552.0956 | 948 |  | 1292 | 948-5R | 3649.3933 | 1935.6783 | 468.0541 | 3290.352 | 1576.637 | 109.0128 | 0 | 0 | 0 | 359.0413 | 355.774 | 157.8127 | 14.9708 | 355.5038 | 157.5425 | 14.7007 | 0 | 0 | 0 | 0.27017 | 1660.7252 | 742.8302 | 108.6295 | 1628.1096 | 710.2146 | 76.014 | 0 | 0 | 0 | 32.6156 | 1632.8942 | 1035.0354 | 344.4538 | 1306.7386 | 708.8798 | 18.2982 | 0 | 0 | 0 | 326.1556 | 0.001882 | 0.0008856 | 2.26e-05 | 0 | 0 | 0 | 0.0005052 | 5000000 | scaled
949-22R | 9231.6493 | 5175.5844 | 0 | 4056.0649 | 56.06% | 0% | 43.94% | 3008.8827 | 5113.4419 | 210.0755 | 1656.3271 | 1142.4801 | 349.1514 | 2871.2183 | 1893.0722 | 949 |  | 1293 | 949-22R | 9231.6493 | 6222.7666 | 4118.2074 | 5175.5844 | 2166.7017 | 62.1425 | 0 | 0 | 0 | 4056.0649 | 357.325 | 147.2495 | 8.1735 | 354.2729 | 144.1974 | 5.1215 | 0 | 0 | 0 | 3.0521 | 2288.9473 | 1146.4671 | 395.8751 | 1920.4916 | 778.0114 | 27.4194 | 0 | 0 | 0 | 368.4557 | 6585.3771 | 4929.05 | 3714.1587 | 2900.8199 | 1244.4928 | 29.6016 | 0 | 0 | 0 | 3684.5571 | 0.01074 | 0.00465 | 0.0001184 | 0 | 0 | 0 | 0.0056616 | 5000000 | scaled
95-1352F | 35.5662 | 0 | 0 | 35.5662 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 |  | 1294 | 95-1352F | 35.5662 | 35.5662 | 35.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 35.5662 | 0.026762 | 0.026762 | 0.026762 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026762 | 3.2309 | 3.2309 | 3.2309 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2309 | 32.3086 | 32.3086 | 32.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 32.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 5.34e-05 | 5000000 | scaled
95-1353F | 32.887 | 0 | 0 | 32.887 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 |  | 1295 | 95-1353F | 32.887 | 32.887 | 32.887 | 0 | 0 | 0 | 0 | 0 | 0 | 32.887 | 0.024746 | 0.024746 | 0.024746 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024746 | 2.9875 | 2.9875 | 2.9875 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9875 | 29.8748 | 29.8748 | 29.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 29.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 4.94e-05 | 5000000 | scaled
95-29R | 60126.4502 | 15046.6937 | 39192.811 | 5886.9455 | 25.03% | 65.18% | 9.791% | 25972.1938 | 51493.7605 | 426.4249 | 21700.2033 | 3845.5657 | 758.1403 | 43403.3907 | 7332.2295 | 95 |  | 1296 | 95-29R | 60126.4502 | 34154.2564 | 8632.6897 | 15046.6937 | 6464.4771 | 129.1992 | 39192.811 | 21802.8338 | 2616.5451 | 5886.9455 | 771.2828 | 344.8579 | 13.1425 | 710.9807 | 309.3466 | 4.9827 | 55.8723 | 31.0816 | 3.7301 | 4.4297 | 8145.1426 | 4299.577 | 812.9131 | 3833.2574 | 1663.6082 | 25.9758 | 3777.1111 | 2101.1946 | 252.1631 | 534.7742 | 51210.0248 | 29509.8215 | 7806.6341 | 10502.4556 | 4491.5224 | 98.2406 | 35359.8277 | 19670.5576 | 2360.6519 | 5347.7416 | 0.019403 | 0.0084024 | 0.0002126 | 0.0050968 | 0.002916 | 0.0005096 | 0.0083674 | 5000000 | scaled
95-34 | 20435.3114 | 11514.7117 | 7991.4421 | 929.1576 | 56.35% | 39.11% | 4.547% | 9647.3406 | 18917.8271 | 544.897 | 3609.7908 | 5492.6528 | 1017.7228 | 7438.8759 | 10461.2285 | 95 |  | 1297 | 95-34 | 20435.3114 | 10787.9708 | 1517.4843 | 11514.7117 | 5419.7123 | 55.2728 | 7991.4421 | 4439.1009 | 533.0539 | 929.1576 | 1024.4576 | 479.5607 | 6.7349 | 1013.5421 | 473.1865 | 5.3542 | 10.2164 | 5.675 | 0.68147 | 0.69916 | 10636.8202 | 5144.1674 | 175.5918 | 9826.2748 | 4656.4044 | 42.7506 | 726.1401 | 403.3577 | 48.4358 | 84.4053 | 8774.0335 | 5164.2427 | 1335.1577 | 674.8948 | 290.1214 | 7.1679 | 7255.0856 | 4030.0682 | 483.9367 | 844.0531 | 0.0028594 | 0.0012382 | 3.1e-05 | 0.0051242 | 0.0029276 | 0.0005124 | 0.001302 | 5000000 | scaled
95-35F | 19054.7202 | 13174.4202 | 4277.0292 | 1603.2708 | 69.14% | 22.45% | 8.414% | 9783.7277 | 17016.9224 | 743.7831 | 1834.4526 | 7205.492 | 1232.0496 | 3839.7069 | 11945.1659 | 95 |  | 1298 | 95-35F | 19054.7202 | 9270.9925 | 2037.7978 | 13174.4202 | 5292.5208 | 149.1137 | 4277.0292 | 2375.2008 | 285.4132 | 1603.2708 | 1246.2118 | 502.4287 | 14.1622 | 1239.0962 | 497.9407 | 12.5614 | 5.9091 | 3.2816 | 0.39433 | 1.2064 | 12247.8302 | 5042.3381 | 302.6642 | 11761.0274 | 4707.2362 | 134.2558 | 341.1606 | 189.4597 | 22.7662 | 145.6422 | 5560.6783 | 3726.2256 | 1720.9714 | 174.2966 | 87.344 | 2.2965 | 3929.9595 | 2182.4595 | 262.2527 | 1456.4222 | 0.0045428 | 0.0020994 | 5.22e-05 | 0.005129 | 0.0029296 | 0.0005128 | 0.0022696 | 5000000 | scaled
95-36F | 25869.0446 | 14580.1865 | 8757.5911 | 2531.2669 | 56.36% | 33.85% | 9.785% | 12182.5847 | 22524.3269 | 741.6381 | 3912.0947 | 7528.852 | 1286.0508 | 8095.9413 | 13142.3349 | 95 |  | 1299 | 95-36F | 25869.0446 | 13686.4599 | 3344.7177 | 14580.1865 | 6288.3459 | 229.3835 | 8757.5911 | 4866.847 | 584.0672 | 2531.2669 | 1307.5601 | 565.9221 | 21.5094 | 1293.1368 | 557.0604 | 18.7698 | 12.5186 | 6.957 | 0.8349 | 1.9047 | 13624.1011 | 6095.2492 | 481.7663 | 12675.1761 | 5465.7475 | 203.8734 | 718.983 | 399.5597 | 47.9509 | 229.942 | 10937.3833 | 7025.2886 | 2841.442 | 611.8736 | 265.538 | 6.7404 | 8026.0895 | 4460.3304 | 535.2814 | 2299.4202 | 0.0073062 | 0.0031634 | 7.94e-05 | 0.005126 | 0.00293 | 0.0005126 | 0.003635 | 5000000 | scaled
95-37F | 464.3405 | 67.0946 | 325.7591 | 71.4868 | 14.45% | 70.16% | 15.4% | 179.8937 | 370.7224 | 2.5797 | 153.5125 | 23.8014 | 5.1254 | 316.6203 | 48.9767 | 95 |  | 1300 | 95-37F | 464.3405 | 284.4468 | 93.618 | 67.0946 | 32.2802 | 0.3894 | 325.7591 | 180.6798 | 21.7418 | 71.4868 | 5.2052 | 2.6255 | 0.079801 | 4.7617 | 2.3556 | 0 | 0.3897 | 0.21614 | 0.026009 | 0.053792 | 57.2052 | 33.4038 | 8.2285 | 24.722 | 12.4951 | 0 | 25.9892 | 14.4147 | 1.7346 | 6.4939 | 401.93 | 248.4175 | 85.3098 | 37.6108 | 17.4295 | 0.3894 | 299.3801 | 166.0489 | 19.9812 | 64.9391 | 0.0001446 | 6.26e-05 | 1.6e-06 | 0.0051352 | 0.0029296 | 0.0005136 | 9.94e-05 | 5000000 | scaled
957-493 | 2096.1638 | 1725.1551 | 0 | 371.0087 | 82.3% | 0% | 17.7% | 677.4407 | 1711.6833 | 69.3481 | 119.042 | 489.0506 | 167.1651 | 411.3464 | 1133.1718 | 957 |  | 1301 | 957-493 | 2096.1638 | 1418.7231 | 384.4806 | 1725.1551 | 1047.7144 | 13.4719 | 0 | 0 | 0 | 371.0087 | 168.644 | 99.2959 | 1.4789 | 168.3648 | 99.0167 | 1.1998 | 0 | 0 | 0 | 0.27917 | 1173.4125 | 684.3619 | 40.2407 | 1139.7098 | 650.6593 | 6.538 | 0 | 0 | 0 | 33.7027 | 754.1073 | 635.0653 | 342.7609 | 417.0805 | 298.0385 | 5.7341 | 0 | 0 | 0 | 337.0268 | 0.0012228 | 0.0008172 | 2.06e-05 | 0 | 0 | 0 | 0.0005292 | 5000000 | scaled
96-1041F | 5617.479 | 5456.8762 | 100.624 | 59.9787 | 97.14% | 1.791% | 1.068% | 3599.1375 | 5441.357 | 250.03 | 1440.6002 | 1908.5072 | 356.5406 | 2450.3261 | 2634.4903 | 96 |  | 1302 | 96-1041F | 5617.479 | 2018.3415 | 176.122 | 5456.8762 | 1902.6356 | 109.425 | 100.624 | 55.7272 | 6.7182 | 59.9787 | 365.8499 | 115.8198 | 9.3092 | 365.0645 | 115.3647 | 9.2147 | 0.74023 | 0.40995 | 0.049422 | 0.045132 | 2717.5598 | 809.0526 | 83.0695 | 2697.3349 | 795.4207 | 76.6344 | 14.7764 | 8.1834 | 0.98656 | 5.4485 | 2534.0693 | 1093.4691 | 83.7432 | 2394.4768 | 991.8501 | 23.5759 | 85.1074 | 47.1338 | 5.6823 | 54.4851 | 0.0004288 | 0.0001856 | 4.8e-06 | 0.0051094 | 0.002911 | 0.000511 | 9.48e-05 | 5000000 | scaled
96-14 | 160.4906 | 0 | 160.4906 | 0 | 0% | 100% | 0% | 25.5089 | 53.4149 | 0.016753 | 20.225 | 5.2672 | 0.035081 | 42.3505 | 11.0294 | 96 |  | 1303 | 96-14 | 160.4906 | 134.9817 | 107.0757 | 0 | 0 | 0 | 160.4906 | 134.9817 | 107.0757 | 0 | 0.1054 | 0.08865 | 0.070322 | 0 | 0 | 0 | 0.1054 | 0.08865 | 0.070322 | 0 | 33.1388 | 27.8716 | 22.1095 | 0 | 0 | 0 | 33.1388 | 27.8716 | 22.1095 | 0 | 127.2464 | 107.0214 | 84.8959 | 0 | 0 | 0 | 127.2464 | 107.0214 | 84.8959 | 0 | 0 | 0 | 0 | 0.0050928 | 0.0050928 | 0.0050928 | 0 | 5000000 | scaled
96-47R | 553695.3131 | 488904.6047 | 59267.3526 | 5523.3559 | 88.3% | 10.7% | 0.9975% | 317601.145 | 540371.2303 | 31538.5788 | 40334.1624 | 245728.4037 | 52824.9381 | 78786.6296 | 408759.6627 | 96 |  | 1304 | 96-47R | 553695.3131 | 236094.1681 | 13324.0828 | 488904.6047 | 197721.0964 | 3846.5799 | 59267.3526 | 32849.7159 | 3954.147 | 5523.3559 | 53273.6932 | 21735.1143 | 448.7551 | 53178.7099 | 21680.6161 | 438.5392 | 90.8271 | 50.3421 | 6.0597 | 4.1561 | 412697.0043 | 166968.6006 | 3937.3416 | 407174.5158 | 163684.0417 | 3100.6267 | 5020.7431 | 2782.8134 | 334.9695 | 501.7454 | 87724.6157 | 47390.4532 | 8937.9861 | 28551.3789 | 12356.4386 | 307.414 | 54155.7824 | 30016.5604 | 3613.1178 | 5017.4543 | 0.02196 | 0.0095352 | 0.0002436 | 0.0050212 | 0.0028628 | 0.0005022 | 0.0077676 | 5000000 | scaled
963-35 | 30737.649 | 28949.201 | 0 | 1788.448 | 94.18% | 0% | 5.818% | 13045.2057 | 28589.7517 | 1309.3967 | 1360.8383 | 10374.9707 | 2843.3462 | 3728.1286 | 22018.2769 | 963 |  | 1305 | 963-35 | 30737.649 | 17692.4433 | 2147.8974 | 28949.201 | 15903.9953 | 359.4493 | 0 | 0 | 0 | 1788.448 | 2880.5797 | 1571.183 | 37.2335 | 2879.234 | 1569.8373 | 35.8877 | 0 | 0 | 0 | 1.3457 | 22443.0857 | 12068.115 | 424.8088 | 22280.6219 | 11905.6512 | 262.345 | 0 | 0 | 0 | 162.4638 | 5413.9836 | 4053.1453 | 1685.855 | 3789.3452 | 2428.5068 | 61.2166 | 0 | 0 | 0 | 1624.6384 | 0.010361 | 0.0057742 | 0.0001472 | 0 | 0 | 0 | 0.0025358 | 5000000 | scaled
968-476F | 62492.0214 | 60559.3536 | 483.0584 | 1449.6095 | 96.91% | 0.773% | 2.32% | 26361.4532 | 58631.4422 | 4289.9576 | 199.8797 | 21871.6159 | 9697.7135 | 420.5057 | 48513.2229 | 968 |  | 1306 | 968-476F | 62492.0214 | 36130.5683 | 3860.5792 | 60559.3536 | 34413.2141 | 2378.7367 | 483.0584 | 267.7447 | 32.233 | 1449.6095 | 10063.736 | 5773.7784 | 366.0225 | 10059.6655 | 5771.0361 | 364.7328 | 2.9797 | 1.6516 | 0.19883 | 1.0908 | 50664.5652 | 28792.9493 | 2151.3423 | 50433.6877 | 28606.2856 | 2013.0398 | 99.194 | 54.9802 | 6.6189 | 131.6835 | 1763.7202 | 1563.8405 | 1343.2145 | 66.0004 | 35.8924 | 0.96399 | 380.8846 | 211.1129 | 25.4153 | 1316.8352 | 0.008191 | 0.0052134 | 0.0001326 | 0.0050814 | 0.0028972 | 0.0005082 | 0.0020428 | 5000000 | scaled
970-1341R | 12961613.4298 | 12917271.9445 | 41466.4897 | 2874.9955 | 99.66% | 0.3199% | 0.02218% | 5039530.0046 | 12673489.7919 | 507789.5983 | 22831.3135 | 4508909.0928 | 1278354.3341 | 63874.6985 | 11331260.7593 | 970 |  | 1307 | 970-1341R | 12961613.4298 | 7922083.4252 | 288123.6379 | 12917271.9445 | 7895851.3485 | 281520.3573 | 41466.4897 | 23357.0812 | 3728.285 | 2874.9955 | 1306568.5018 | 798778.9035 | 28214.1677 | 1306505.3955 | 798742.4124 | 28206.525 | 60.943 | 34.3278 | 5.4794 | 2.1633 | 11584585.4697 | 7075676.3769 | 253324.7104 | 11580699.3285 | 7073373.3489 | 252737.6195 | 3624.9747 | 2041.8615 | 325.9244 | 261.1666 | 70459.4583 | 47628.1448 | 6584.7597 | 30067.2206 | 23735.5872 | 576.2129 | 37780.572 | 21280.892 | 3396.8812 | 2611.6656 | 0.013534 | 0.008266 | 0.0002094 | 0.10732 | 0.060973 | 0.010732 | 0.0041086 | 5000000 | scaled
970-18AE | 588322.3354 | 0 | 588322.3354 | 0 | 0% | 100% | 0% | 28827.8281 | 60062.3716 | 40.532 | 26345.3817 | 2441.9144 | 84.4478 | 54890.2297 | 5087.6941 | 970 |  | 1308 | 970-18AE | 588322.3354 | 559494.5073 | 528259.9638 | 0 | 0 | 0 | 588322.3354 | 559494.5073 | 528259.9638 | 0 | 827.1821 | 786.6501 | 742.7343 | 0 | 0 | 0 | 827.1821 | 786.6501 | 742.7343 | 0 | 49834.9301 | 47393.0156 | 44747.2359 | 0 | 0 | 0 | 49834.9301 | 47393.0156 | 44747.2359 | 0 | 537660.2233 | 511314.8416 | 482769.9936 | 0 | 0 | 0 | 537660.2233 | 511314.8416 | 482769.9936 | 0 | 0 | 0 | 0 | 0.10513 | 0.10513 | 0.10513 | 0 | 5000000 | scaled
970-4AE | 331307.3164 | 0 | 331307.3164 | 0 | 0% | 100% | 0% | 16172.9682 | 33694.9965 | 23.1382 | 14844.5444 | 1305.2857 | 48.2065 | 30927.3389 | 2719.4511 | 970 |  | 1309 | 970-4AE | 331307.3164 | 315134.3481 | 297612.3198 | 0 | 0 | 0 | 331307.3164 | 315134.3481 | 297612.3198 | 0 | 473.9918 | 450.8536 | 425.7853 | 0 | 0 | 0 | 473.9918 | 450.8536 | 425.7853 | 0 | 26739.1052 | 25433.8195 | 24019.6541 | 0 | 0 | 0 | 26739.1052 | 25433.8195 | 24019.6541 | 0 | 304094.2194 | 289249.675 | 273166.8805 | 0 | 0 | 0 | 304094.2194 | 289249.675 | 273166.8805 | 0 | 0 | 0 | 0 | 0.10579 | 0.10579 | 0.10579 | 0 | 5000000 | scaled
971-1973R | 15148796.1922 | 15005297.4007 | 135833.4004 | 7665.3911 | 99.05% | 0.8967% | 0.0506% | 5280372.0027 | 14887537.4011 | 388639.7108 | 54833.2429 | 4836899.049 | 1098674.3216 | 115125.0708 | 13673738.0087 | 971 |  | 1310 | 971-1973R | 15148796.1922 | 9868424.1895 | 261258.7911 | 15005297.4007 | 9784389.4642 | 241347.1611 | 135833.4004 | 76369.3343 | 12246.2388 | 7665.3911 | 1116693.1465 | 728053.4357 | 18018.8249 | 1116465.5403 | 727922.9441 | 17993.0568 | 221.8383 | 124.7237 | 20.0001 | 5.768 | 13898934.0888 | 9062035.0398 | 225196.0801 | 13884763.4226 | 9053763.0616 | 223284.9541 | 13474.3368 | 7575.6488 | 1214.7966 | 696.3294 | 133168.9569 | 78335.714 | 18043.8861 | 4068.4377 | 2703.4584 | 69.1502 | 122137.2254 | 68668.9618 | 11011.4422 | 6963.2937 | 0.032871 | 0.021309 | 0.0005496 | 0.10329 | 0.058563 | 0.010329 | 0.010883 | 5000000 | scaled
971-2050R | 28484583.8082 | 28174790.2275 | 294674.2035 | 15119.3772 | 98.91% | 1.035% | 0.05308% | 9403495.035 | 28039826.3164 | 658809.1729 | 119805.714 | 8624880.1481 | 1971102.7883 | 254168.496 | 25814555.0322 | 971 |  | 1311 | 971-2050R | 28484583.8082 | 19081088.7732 | 444757.4918 | 28174790.2275 | 18900289.8051 | 403070.5529 | 294674.2035 | 165679.5909 | 26567.5616 | 15119.3772 | 1999798.6535 | 1340989.4807 | 28695.8652 | 1999361.3594 | 1340738.6333 | 28646.0881 | 425.9173 | 239.4706 | 38.4003 | 11.3768 | 26192671.0806 | 17567790.9325 | 378116.0484 | 26163027.9515 | 17550522.9474 | 374193.8254 | 28269.6745 | 15894.5305 | 2548.7685 | 1373.4546 | 292114.0741 | 172308.3601 | 37945.5782 | 12400.9166 | 9028.2244 | 230.6395 | 265978.6118 | 149545.5898 | 23980.3929 | 13734.5458 | 0.060319 | 0.03987 | 0.0010112 | 0.10307 | 0.058443 | 0.010307 | 0.021251 | 5000000 | scaled
971-29R | 8015406.5198 | 7972516.2609 | 40413.2039 | 2477.055 | 99.46% | 0.5042% | 0.0309% | 3584975.9317 | 7897659.5989 | 196419.5679 | 15884.9203 | 3372671.4435 | 433192.7304 | 33134.8918 | 7431331.9767 | 971 |  | 1312 | 971-29R | 8015406.5198 | 4430430.5881 | 117746.9209 | 7972516.2609 | 4405186.535 | 111636.7735 | 40413.2039 | 22766.9981 | 3633.0924 | 2477.055 | 439436.3246 | 243016.7568 | 6243.5942 | 439370.526 | 242978.8749 | 6235.9827 | 63.9347 | 36.018 | 5.7476 | 1.8639 | 7537321.4607 | 4164650.0172 | 105989.484 | 7533030.3974 | 4162134.3707 | 105398.9346 | 4066.0459 | 2290.629 | 365.532 | 225.0174 | 38648.7345 | 22763.8142 | 5513.8427 | 115.3374 | 73.2894 | 1.8562 | 36283.2234 | 20440.3511 | 3261.8127 | 2250.1737 | 0.011408 | 0.0064156 | 0.0001634 | 0.10679 | 0.060684 | 0.010679 | 0.0035084 | 5000000 | scaled
971-371R | 4351506.2421 | 4330446.0988 | 19464.057 | 1596.0863 | 99.52% | 0.4473% | 0.03668% | 1164714.9992 | 4256997.5101 | 62533.4483 | 7537.9792 | 1094643.5717 | 229834.6693 | 15766.7042 | 4011396.1365 | 971 |  | 1313 | 971-371R | 4351506.2421 | 3186791.243 | 94508.7321 | 4330446.0988 | 3174240.2813 | 91162.7011 | 19464.057 | 10954.8754 | 1749.9447 | 1596.0863 | 234743.5657 | 172210.1174 | 4908.8964 | 234725.9671 | 172199.6874 | 4906.2211 | 16.3976 | 9.229 | 1.4743 | 1.201 | 4098000.6142 | 3003357.0425 | 86604.4777 | 4095564.322 | 3001922.4485 | 86253.4851 | 2291.3027 | 1289.6045 | 206.0029 | 144.9896 | 18762.0622 | 11224.083 | 2995.358 | 155.8098 | 118.1454 | 2.9948 | 17156.3568 | 9656.042 | 1542.4675 | 1449.8957 | 0.0076008 | 0.0057314 | 0.000145 | 0.10684 | 0.060649 | 0.010684 | 0.0022372 | 5000000 | scaled
971-381R | 191895.4071 | 191774.6514 | 0 | 120.7557 | 99.94% | 0% | 0.06293% | 24482.8855 | 191774.6514 | 1300.978 | 0 | 23181.9075 | 9680.8467 | 0 | 182093.8047 | 971 |  | 1314 | 971-381R | 191895.4071 | 167412.5216 | 120.7557 | 191774.6514 | 167291.7659 | 0 | 0 | 0 | 0 | 120.7557 | 9680.9376 | 8379.9596 | 0.090865 | 9680.8467 | 8379.8687 | 0 | 0 | 0 | 0 | 0.090865 | 182104.7742 | 158922.8667 | 10.9695 | 182093.8047 | 158911.8972 | 0 | 0 | 0 | 0 | 10.9695 | 109.6953 | 109.6953 | 109.6953 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6953 | 0.0002212 | 0.000168 | 4.4e-06 | 0 | 0 | 0 | 0.000159 | 5000000 | scaled
971-383R | 14770596.2279 | 14538988.9378 | 225764.1919 | 5843.0982 | 98.43% | 1.528% | 0.03956% | 6319095.9207 | 14599902.8442 | 365816.0324 | 93492.3127 | 5859787.5756 | 846020.9029 | 197446.126 | 13556435.8153 | 971 |  | 1315 | 971-383R | 14770596.2279 | 8451500.3072 | 170693.3837 | 14538988.9378 | 8318775.4328 | 144478.3977 | 225764.1919 | 126881.7762 | 20371.8878 | 5843.0982 | 854737.1386 | 488921.1062 | 8716.2357 | 854428.1544 | 488745.5282 | 8684.3544 | 304.5874 | 171.1812 | 27.4845 | 4.3967 | 13694414.5653 | 7834626.9896 | 137978.75 | 13673418.8054 | 7822594.6776 | 135601.2974 | 20464.9689 | 11501.521 | 1846.6615 | 530.791 | 221444.5241 | 127952.2114 | 23998.3981 | 11141.978 | 7435.227 | 192.7459 | 204994.6357 | 115209.074 | 18497.7418 | 5307.9104 | 0.026 | 0.01482 | 0.0003768 | 0.1041 | 0.058992 | 0.01041 | 0.0082674 | 5000000 | scaled
971-388R | 11267961.0269 | 11152745.4958 | 104058.5439 | 11156.9873 | 98.98% | 0.9235% | 0.09902% | 3521100.0093 | 11057004.8075 | 213248.492 | 41484.2811 | 3266367.2362 | 671412.1452 | 87772.3728 | 10297820.2895 | 971 |  | 1316 | 971-388R | 11267961.0269 | 7746861.0176 | 210956.2194 | 11152745.4958 | 7677228.0503 | 190400.0672 | 104058.5439 | 58475.98 | 9399.1649 | 11156.9873 | 683141.1399 | 469892.6479 | 11728.9946 | 682976.1137 | 469796.2335 | 11706.4516 | 156.6309 | 88.0191 | 14.1478 | 8.3953 | 10478480.0307 | 7212112.7945 | 180659.7412 | 10466167.165 | 7204749.5817 | 178625.61 | 11299.3573 | 6349.7044 | 1020.6228 | 1013.5084 | 106339.8564 | 64855.5752 | 18567.4836 | 3602.2171 | 2682.2351 | 68.0057 | 92602.5557 | 52038.2565 | 8364.3943 | 10135.0836 | 0.05522 | 0.037432 | 0.0009496 | 0.10534 | 0.059685 | 0.010534 | 0.015858 | 5000000 | scaled
972-1565F | 2476.1864 | 0 | 2476.1864 | 0 | 0% | 100% | 0% | 114.2103 | 237.5069 | 0.075008 | 90.5526 | 23.5827 | 0.15598 | 188.3094 | 49.0415 | 972 |  | 1317 | 972-1565F | 2476.1864 | 2361.9762 | 2238.6796 | 0 | 0 | 0 | 2476.1864 | 2361.9762 | 2238.6796 | 0 | 1.6262 | 1.5512 | 1.4703 | 0 | 0 | 0 | 1.6262 | 1.5512 | 1.4703 | 0 | 511.2945 | 487.7118 | 462.2529 | 0 | 0 | 0 | 511.2945 | 487.7118 | 462.2529 | 0 | 1963.2657 | 1872.7131 | 1774.9564 | 0 | 0 | 0 | 1963.2657 | 1872.7131 | 1774.9564 | 0 | 0 | 0 | 0 | 0.10655 | 0.10655 | 0.10655 | 0 | 5000000 | scaled
972-1566F | 1670.5006 | 0 | 1670.5006 | 0 | 0% | 100% | 0% | 76.6519 | 159.2948 | 0.52531 | 60.3973 | 15.7293 | 1.0917 | 125.5152 | 32.688 | 972 |  | 1318 | 972-1566F | 1670.5006 | 1593.8487 | 1511.2058 | 0 | 0 | 0 | 1670.5006 | 1593.8487 | 1511.2058 | 0 | 11.4482 | 10.9229 | 10.3565 | 0 | 0 | 0 | 11.4482 | 10.9229 | 10.3565 | 0 | 342.794 | 327.0647 | 310.106 | 0 | 0 | 0 | 342.794 | 327.0647 | 310.106 | 0 | 1316.2584 | 1255.8611 | 1190.7433 | 0 | 0 | 0 | 1316.2584 | 1255.8611 | 1190.7433 | 0 | 0 | 0 | 0 | 0.10722 | 0.10722 | 0.10722 | 0 | 5000000 | scaled
972-1582R | 8019179.1907 | 7901674.2084 | 111015.7019 | 6489.2804 | 98.53% | 1.384% | 0.08092% | 1397569.7924 | 7861692.0639 | 79368.134 | 43755.7024 | 1274445.9561 | 456627.7845 | 92850.5484 | 7312213.731 | 972 |  | 1319 | 972-1582R | 8019179.1907 | 6621609.3983 | 157487.1269 | 7901674.2084 | 6552791.2335 | 140945.2834 | 111015.7019 | 62328.8844 | 10052.563 | 6489.2804 | 464948.4252 | 385580.2913 | 8320.6408 | 464802.3969 | 385496.1633 | 8302.977 | 141.1454 | 79.245 | 12.7808 | 4.883 | 7446576.1108 | 6172130.1547 | 134362.3799 | 7432575.8799 | 6164011.3104 | 132558.5356 | 13410.7402 | 7529.3536 | 1214.3535 | 589.4907 | 107654.6547 | 63898.9523 | 14804.1062 | 4295.9316 | 3283.7598 | 83.7708 | 97463.8163 | 54720.2858 | 8825.4287 | 5894.9067 | 0.033479 | 0.028291 | 0.000719 | 0.10812 | 0.061195 | 0.010812 | 0.0090242 | 5000000 | scaled
972-1590F | 23409153.8603 | 23032887.7606 | 362302.0188 | 13964.0809 | 98.39% | 1.548% | 0.05965% | 12422166.7023 | 23145000.5511 | 1006709.4917 | 152887.9077 | 11262569.3029 | 1873704.096 | 314950.6697 | 20956345.7854 | 972 |  | 1320 | 972-1590F | 23409153.8603 | 10986987.158 | 264153.3092 | 23032887.7606 | 10769593.2375 | 217401.0776 | 362302.0188 | 203429.8396 | 32788.1507 | 13964.0809 | 1891600.8952 | 884891.4035 | 17896.7992 | 1891016.393 | 884558.6023 | 17834.3454 | 573.9947 | 322.2937 | 51.9462 | 10.5075 | 21160518.7481 | 9897949.4452 | 204172.9627 | 21119318.3495 | 9874259.4837 | 199290.6399 | 39931.892 | 22421.4549 | 3613.8162 | 1268.5067 | 357034.217 | 204146.3093 | 42083.5473 | 22553.0181 | 10775.1516 | 276.0923 | 321796.1322 | 180686.091 | 29122.3883 | 12685.0667 | 0.04905 | 0.022779 | 0.000577 | 0.10726 | 0.060716 | 0.010726 | 0.019725 | 5000000 | scaled
972-1640 | 12296.0513 | 0 | 12296.0513 | 0 | 0% | 100% | 0% | 553.0553 | 1147.8087 | 1.4301 | 454.3371 | 97.288 | 2.968 | 942.9294 | 201.9112 | 972 |  | 1321 | 972-1640 | 12296.0513 | 11742.996 | 11148.2426 | 0 | 0 | 0 | 12296.0513 | 11742.996 | 11148.2426 | 0 | 31.7956 | 30.3654 | 28.8275 | 0 | 0 | 0 | 31.7956 | 30.3654 | 28.8275 | 0 | 2163.0003 | 2065.7122 | 1961.0891 | 0 | 0 | 0 | 2163.0003 | 2065.7122 | 1961.0891 | 0 | 10101.2555 | 9646.9183 | 9158.326 | 0 | 0 | 0 | 10101.2555 | 9646.9183 | 9158.326 | 0 | 0 | 0 | 0 | 0.10996 | 0.10996 | 0.10996 | 0 | 5000000 | scaled
972-1641 | 295083.8705 | 0 | 295083.8705 | 0 | 0% | 100% | 0% | 13321.8346 | 27633.0717 | 16.7829 | 12126.3526 | 1178.699 | 34.8123 | 25153.3203 | 2444.9391 | 972 |  | 1322 | 972-1641 | 295083.8705 | 281762.0359 | 267450.7988 | 0 | 0 | 0 | 295083.8705 | 281762.0359 | 267450.7988 | 0 | 371.7488 | 354.9659 | 336.9365 | 0 | 0 | 0 | 371.7488 | 354.9659 | 336.9365 | 0 | 26108.6459 | 24929.9469 | 23663.7068 | 0 | 0 | 0 | 26108.6459 | 24929.9469 | 23663.7068 | 0 | 268603.4758 | 256477.1232 | 243450.1555 | 0 | 0 | 0 | 268603.4758 | 256477.1232 | 243450.1555 | 0 | 0 | 0 | 0 | 0.10934 | 0.10934 | 0.10934 | 0 | 5000000 | scaled
972-1642 | 185301.0758 | 0 | 185223.7811 | 77.2947 | 0% | 99.96% | 0.04171% | 81091.7522 | 168424.1533 | 94.8233 | 73062.3165 | 7934.6124 | 196.944 | 151747.3537 | 16479.8557 | 972 |  | 1323 | 972-1642 | 185301.0758 | 104209.3236 | 16876.9225 | 0 | 0 | 0 | 185223.7811 | 104132.0289 | 16799.6278 | 77.2947 | 216.6465 | 121.8232 | 19.7025 | 0 | 0 | 0 | 216.5883 | 121.765 | 19.6444 | 0.058162 | 18130.6761 | 10196.0637 | 1650.8204 | 0 | 0 | 0 | 18123.6546 | 10189.0422 | 1643.7989 | 7.0215 | 166953.7533 | 93891.4367 | 15206.3996 | 0 | 0 | 0 | 166883.5382 | 93821.2217 | 15136.1845 | 70.2151 | 0 | 0 | 0 | 0.11037 | 0.062547 | 0.011037 | 0.000106 | 5000000 | scaled
972-1644 | 200447.1376 | 0 | 200447.1376 | 0 | 0% | 100% | 0% | 8920.2258 | 18517.4979 | 10.1552 | 8082.3086 | 827.762 | 21.0811 | 16778.0656 | 1718.3512 | 972 |  | 1324 | 972-1644 | 200447.1376 | 191526.9118 | 181929.6396 | 0 | 0 | 0 | 200447.1376 | 191526.9118 | 181929.6396 | 0 | 228.1974 | 218.0423 | 207.1163 | 0 | 0 | 0 | 228.1974 | 218.0423 | 207.1163 | 0 | 18600.7085 | 17772.9465 | 16882.3573 | 0 | 0 | 0 | 18600.7085 | 17772.9465 | 16882.3573 | 0 | 181618.2317 | 173535.9231 | 164840.166 | 0 | 0 | 0 | 181618.2317 | 173535.9231 | 164840.166 | 0 | 0 | 0 | 0 | 0.11119 | 0.11119 | 0.11119 | 0 | 5000000 | scaled
972-32R | 22914328.3826 | 22336491.2466 | 567712.7582 | 10124.3777 | 97.48% | 2.478% | 0.04418% | 11242280.1149 | 22605016.8584 | 645787.68 | 225932.7112 | 10370559.7237 | 1296864.0347 | 468710.9796 | 20839441.8441 | 972 |  | 1325 | 972-32R | 22914328.3826 | 11672048.2677 | 309311.5242 | 22336491.2466 | 11342688.7025 | 247697.5396 | 567712.7582 | 319235.1874 | 51489.6068 | 10124.3777 | 1311519.509 | 665731.829 | 14655.4742 | 1310790.3226 | 665318.4599 | 14582.4122 | 721.5681 | 405.7509 | 65.4438 | 7.6183 | 21078596.4255 | 10708036.7017 | 239154.5814 | 21020567.0475 | 10675003.1909 | 233055.2239 | 57109.6725 | 32113.8054 | 5179.6521 | 919.7054 | 524212.4482 | 298279.737 | 55501.4686 | 5133.8765 | 2367.0517 | 59.9035 | 509881.5175 | 286715.6312 | 46244.511 | 9197.0541 | 0.042044 | 0.020806 | 0.0005268 | 0.10987 | 0.062282 | 0.010987 | 0.014154 | 5000000 | scaled
972-942R | 9149683.626 | 9068839.1214 | 75954.7616 | 4889.7431 | 99.12% | 0.8301% | 0.05344% | 2657644.8828 | 8924766.0029 | 179687.5349 | 29824.501 | 2448132.8469 | 605860.5055 | 62915.6911 | 8255989.8063 | 972 |  | 1326 | 972-942R | 9149683.626 | 6492038.7432 | 224917.6232 | 9068839.1214 | 6444392.4375 | 213128.9441 | 75954.7616 | 42756.5627 | 6898.936 | 4889.7431 | 620180.1402 | 440492.6053 | 14319.6348 | 620034.7286 | 440409.1418 | 14303.0819 | 141.7323 | 79.7841 | 12.8735 | 3.6794 | 8455995.2604 | 6007862.4136 | 200005.4542 | 8447080.3407 | 6002649.8694 | 198791.8739 | 8470.7321 | 4768.3566 | 769.3927 | 444.1876 | 73508.2254 | 43683.7244 | 10592.5342 | 1724.0521 | 1333.4263 | 33.9883 | 67342.2972 | 37908.4219 | 6116.6698 | 4441.8761 | 0.022654 | 0.016221 | 0.0004122 | 0.11241 | 0.063783 | 0.011241 | 0.0068852 | 5000000 | scaled
973-1226R | 5177869.5988 | 5039261.7504 | 133846.6295 | 4761.219 | 97.32% | 2.585% | 0.09195% | 2234941.5028 | 5097839.6601 | 118761.2019 | 53908.3621 | 2062271.9388 | 270440.3524 | 112114.0585 | 4715285.2492 | 973 |  | 1327 | 973-1226R | 5177869.5988 | 2942928.0961 | 80029.9387 | 5039261.7504 | 2862792.6784 | 63236.4291 | 133846.6295 | 75374.1987 | 12032.2906 | 4761.219 | 273954.4994 | 155193.2975 | 3514.1471 | 273705.589 | 155051.5613 | 3488.5104 | 245.3278 | 138.1535 | 22.054 | 3.5827 | 4776587.1327 | 2714315.1939 | 61301.8835 | 4763384.8995 | 2706691.5593 | 59721.4229 | 12769.7209 | 7191.1223 | 1147.9482 | 432.5124 | 127327.9667 | 73419.6046 | 15213.9082 | 2171.2619 | 1049.5578 | 26.4958 | 120831.5808 | 68044.9229 | 10862.2885 | 4325.1239 | 0.026938 | 0.013973 | 0.0003548 | 0.1063 | 0.060384 | 0.01063 | 0.0066614 | 5000000 | scaled
973-1245R | 8620110.617 | 8579827.5741 | 38325.9745 | 1957.0683 | 99.53% | 0.4446% | 0.0227% | 2864904.4318 | 8464013.8572 | 162209.1809 | 18372.6463 | 2684322.6046 | 481503.3571 | 46484.7071 | 7936025.793 | 973 |  | 1328 | 973-1245R | 8620110.617 | 5755206.1851 | 156096.7598 | 8579827.5741 | 5731675.2044 | 150694.317 | 38325.9745 | 21573.9125 | 3445.3745 | 1957.0683 | 490174.7607 | 327965.5798 | 8671.4036 | 490061.4677 | 327901.1628 | 8659.8787 | 111.8204 | 62.9443 | 10.0523 | 1.4726 | 8078339.9145 | 5394017.3099 | 142314.1215 | 8073531.7675 | 5391233.069 | 141720.086 | 4630.3656 | 2606.4595 | 416.2541 | 177.7814 | 51595.9418 | 33223.2955 | 5111.2347 | 16234.339 | 12540.9726 | 314.3523 | 33583.7886 | 18904.5086 | 3019.0682 | 1777.8142 | 0.011048 | 0.0074324 | 0.0001884 | 0.10661 | 0.060532 | 0.010661 | 0.0027324 | 5000000 | scaled
973-530AE | 388006.194 | 25127.9255 | 362848.2118 | 30.0568 | 6.476% | 93.52% | 0.007746% | 22674.9293 | 61884.8639 | 281.8326 | 16253.6229 | 6139.4737 | 1400.3623 | 33814.9189 | 26669.5828 | 973 |  | 1329 | 973-530AE | 388006.194 | 365331.2648 | 326121.3301 | 25127.9255 | 20211.9602 | 163.3634 | 362848.2118 | 345089.2478 | 325927.9099 | 30.0568 | 1882.4281 | 1600.5954 | 482.0658 | 1360.1643 | 1103.8918 | 12.9408 | 522.2411 | 496.681 | 469.1024 | 0.022617 | 54218.7297 | 48079.256 | 27549.1469 | 23715.6862 | 19068.9964 | 149.5519 | 30500.3132 | 29007.5293 | 27396.8646 | 2.7304 | 331905.0363 | 315651.4133 | 298090.1174 | 52.075 | 39.072 | 0.87065 | 331825.6575 | 315585.0375 | 298061.943 | 27.3038 | 0.0001182 | 8.98e-05 | 2.2e-06 | 0.10525 | 0.10525 | 0.10525 | 5.12e-05 | 5000000 | scaled
973-533AE | 153488.9701 | 0 | 153488.9701 | 0 | 0% | 100% | 0% | 7468.9467 | 15535.1749 | 10.1875 | 6786.6316 | 672.1276 | 21.1898 | 14115.9809 | 1398.0042 | 973 |  | 1330 | 973-533AE | 153488.9701 | 146020.0234 | 137953.7952 | 0 | 0 | 0 | 153488.9701 | 146020.0234 | 137953.7952 | 0 | 209.3569 | 199.1694 | 188.1671 | 0 | 0 | 0 | 209.3569 | 199.1694 | 188.1671 | 0 | 13812.4115 | 13140.284 | 12414.4073 | 0 | 0 | 0 | 13812.4115 | 13140.284 | 12414.4073 | 0 | 139467.2017 | 132680.5701 | 125351.2208 | 0 | 0 | 0 | 139467.2017 | 132680.5701 | 125351.2208 | 0 | 0 | 0 | 0 | 0.10598 | 0.10598 | 0.10598 | 0 | 5000000 | scaled
973-534AE | 146186.472 | 0 | 146186.472 | 0 | 0% | 100% | 0% | 7116.6862 | 14801.4773 | 10.6652 | 6533.3282 | 572.6928 | 22.1818 | 13588.1935 | 1191.102 | 973 |  | 1331 | 973-534AE | 146186.472 | 139069.7858 | 131384.9947 | 0 | 0 | 0 | 146186.472 | 139069.7858 | 131384.9947 | 0 | 219.0781 | 208.4128 | 196.8963 | 0 | 0 | 0 | 219.0781 | 208.4128 | 196.8963 | 0 | 11763.8934 | 11191.2006 | 10572.7914 | 0 | 0 | 0 | 11763.8934 | 11191.2006 | 10572.7914 | 0 | 134203.5006 | 127670.1724 | 120615.3071 | 0 | 0 | 0 | 134203.5006 | 127670.1724 | 120615.3071 | 0 | 0 | 0 | 0 | 0.10595 | 0.10595 | 0.10595 | 0 | 5000000 | scaled
973-626R | 6521723.6165 | 6393285.8327 | 121568.7084 | 6869.0753 | 98.03% | 1.864% | 0.1053% | 2944013.8635 | 6421347.9361 | 190547.5293 | 47787.5333 | 2705678.8009 | 416628.9869 | 99973.6355 | 5904745.3136 | 973 |  | 1332 | 973-626R | 6521723.6165 | 3577709.753 | 100375.6804 | 6393285.8327 | 3502372.3371 | 82578.562 | 121568.7084 | 68468.3406 | 10928.0431 | 6869.0753 | 422071.148 | 231523.6187 | 5442.1611 | 421909.7155 | 231430.4412 | 5422.9455 | 156.2637 | 88.0088 | 14.0468 | 5.1688 | 5983747.2334 | 3278068.4324 | 79001.9197 | 5969134.971 | 3269566.1497 | 77120.4959 | 13988.2708 | 7878.2913 | 1257.4323 | 623.9915 | 115905.2351 | 68117.7018 | 15931.5996 | 2241.1462 | 1375.7463 | 35.1207 | 107424.1738 | 60502.0405 | 9656.5639 | 6239.915 | 0.036492 | 0.019784 | 0.0005026 | 0.10603 | 0.060239 | 0.010603 | 0.0097772 | 5000000 | scaled
974-16 | 1678.4492 | 0 | 1678.4492 | 0 | 0% | 100% | 0% | 81.3459 | 169.3298 | 1.0553 | 63.7009 | 16.5897 | 2.1968 | 132.5999 | 34.5331 | 974 |  | 1333 | 974-16 | 1678.4492 | 1597.1033 | 1509.1194 | 0 | 0 | 0 | 1678.4492 | 1597.1033 | 1509.1194 | 0 | 21.7749 | 20.7196 | 19.5781 | 0 | 0 | 0 | 21.7749 | 20.7196 | 19.5781 | 0 | 342.3026 | 325.7129 | 307.7695 | 0 | 0 | 0 | 342.3026 | 325.7129 | 307.7695 | 0 | 1314.3717 | 1250.6708 | 1181.7718 | 0 | 0 | 0 | 1314.3717 | 1250.6708 | 1181.7718 | 0 | 0 | 0 | 0 | 0.10641 | 0.10641 | 0.10641 | 0 | 5000000 | scaled
974-18 | 2513.543 | 0 | 2513.543 | 0 | 0% | 100% | 0% | 121.887 | 253.6862 | 1.5813 | 95.4481 | 24.8576 | 3.2911 | 198.6584 | 51.7367 | 974 |  | 1334 | 974-18 | 2513.543 | 2391.656 | 2259.8568 | 0 | 0 | 0 | 2513.543 | 2391.656 | 2259.8568 | 0 | 32.6087 | 31.0275 | 29.3176 | 0 | 0 | 0 | 32.6087 | 31.0275 | 29.3176 | 0 | 512.6115 | 487.7539 | 460.8748 | 0 | 0 | 0 | 512.6115 | 487.7539 | 460.8748 | 0 | 1968.3228 | 1872.8747 | 1769.6644 | 0 | 0 | 0 | 1968.3228 | 1872.8747 | 1769.6644 | 0 | 0 | 0 | 0 | 0.10623 | 0.10623 | 0.10623 | 0 | 5000000 | scaled
974-23R | 3492862.6133 | 3272567.438 | 210871.8591 | 9423.3161 | 93.69% | 6.037% | 0.2698% | 1359421.7026 | 3416138.5884 | 77982.0205 | 82849.8618 | 1198589.8203 | 198723.6798 | 173810.8537 | 3043604.055 | 974 |  | 1335 | 974-23R | 3492862.6133 | 2133440.9107 | 76724.0248 | 3272567.438 | 2005267.6651 | 48353.6554 | 210871.8591 | 118749.9294 | 18947.0534 | 9423.3161 | 201841.164 | 123859.1435 | 3117.4843 | 201192.4897 | 123490.7527 | 3052.7466 | 641.5836 | 361.3 | 57.6469 | 7.0907 | 3091737.2028 | 1893147.3825 | 48133.1478 | 3068261.0765 | 1879553.1238 | 45244.6875 | 22620.1058 | 12738.2382 | 2032.4398 | 856.0205 | 199284.2465 | 116434.3847 | 25473.3928 | 3113.8719 | 2223.7886 | 56.2212 | 187610.1698 | 105650.3913 | 16856.9667 | 8560.2049 | 0.046051 | 0.027927 | 0.0007096 | 0.1054 | 0.059876 | 0.01054 | 0.013266 | 5000000 | scaled
974-715R | 7107169.6783 | 7075029.5845 | 28293.2944 | 3846.7994 | 99.55% | 0.3981% | 0.05413% | 1893165.6849 | 6889816.6894 | 98203.4274 | 15129.2844 | 1779832.9732 | 358630.9507 | 40129.7166 | 6491056.0221 | 974 |  | 1336 | 974-715R | 7107169.6783 | 5214003.9933 | 217352.9889 | 7075029.5845 | 5194214.9127 | 210963.2992 | 28293.2944 | 15942.2812 | 2542.8902 | 3846.7994 | 369506.4289 | 271303.0015 | 10875.4782 | 369360.3403 | 271219.4221 | 10859.7139 | 143.194 | 80.6848 | 12.8697 | 2.8946 | 6691523.3173 | 4911690.3441 | 200467.2951 | 6687251.6391 | 4909130.8576 | 199765.3344 | 3922.2323 | 2210.0407 | 352.5148 | 349.4459 | 46139.9321 | 31010.6477 | 6010.2155 | 18417.6052 | 13864.633 | 338.2509 | 24227.868 | 13651.5557 | 2177.5057 | 3494.4589 | 0.029264 | 0.021118 | 0.000536 | 0.10598 | 0.060235 | 0.010598 | 0.005442 | 5000000 | scaled
975-22R | 6417038.1128 | 5152704.553 | 1263248.1771 | 1085.3827 | 80.3% | 19.69% | 0.01691% | 1114695.7781 | 5122008.6244 | 109197.97 | 41570.6958 | 963927.1124 | 509933.5687 | 102107.1009 | 4509967.9548 | 975 |  | 1337 | 975-22R | 6417038.1128 | 5302342.3347 | 1295029.4884 | 5152704.553 | 4074282.1721 | 106312.2707 | 1263248.1771 | 1226974.7798 | 1187631.835 | 1085.3827 | 522314.9144 | 413116.9445 | 12381.3457 | 520471.7905 | 411326.7212 | 10648.4998 | 1842.3072 | 1789.4065 | 1732.0292 | 0.81672 | 4702331.3758 | 3738404.2634 | 192363.421 | 4598792.9784 | 3637836.0765 | 95016.7914 | 103439.8005 | 100469.59 | 97248.0327 | 98.5969 | 1192391.8226 | 1150821.1268 | 1090284.7216 | 33439.7842 | 25119.3744 | 646.9795 | 1157966.0693 | 1124715.7833 | 1088651.7731 | 985.9691 | 0.0055708 | 0.0042316 | 0.0001078 | 0.18961 | 0.18961 | 0.18961 | 0.0015124 | 5000000 | scaled
975-7 | 645751.2826 | 0 | 645751.2826 | 0 | 0% | 100% | 0% | 17106.5234 | 35713.114 | 25.8966 | 15680.1387 | 1400.4882 | 54.064 | 32735.2651 | 2923.7849 | 975 |  | 1338 | 975-7 | 645751.2826 | 628644.7591 | 610038.1686 | 0 | 0 | 0 | 645751.2826 | 628644.7591 | 610038.1686 | 0 | 977.5651 | 951.6685 | 923.5011 | 0 | 0 | 0 | 977.5651 | 951.6685 | 923.5011 | 0 | 52866.7944 | 51466.3062 | 49943.0095 | 0 | 0 | 0 | 52866.7944 | 51466.3062 | 49943.0095 | 0 | 591906.9231 | 576226.7844 | 559171.658 | 0 | 0 | 0 | 591906.9231 | 576226.7844 | 559171.658 | 0 | 0 | 0 | 0 | 0.20764 | 0.20764 | 0.20764 | 0 | 5000000 | scaled
990-713 | 85922.3865 | 388.6829 | 85493.9786 | 39.725 | 0.4524% | 99.5% | 0.04623% | 38502.4838 | 80175.2885 | 87.0856 | 33458.8704 | 4956.5278 | 159.624 | 69861.3911 | 10154.2733 | 990 |  | 1339 | 990-713 | 85922.3865 | 47419.9027 | 5747.0981 | 388.6829 | 98.5265 | 0.0040717 | 85493.9786 | 47281.6513 | 5707.369 | 39.725 | 168.0946 | 81.009 | 8.4706 | 41.6266 | 11.0537 | 0 | 126.4381 | 69.9254 | 8.4407 | 0.029892 | 10859.4528 | 5902.9251 | 705.1795 | 346.6089 | 87.2814 | 0 | 10509.2353 | 5812.035 | 701.5709 | 3.6086 | 74894.8391 | 41435.9687 | 5033.448 | 0.44744 | 0.1914 | 0.0040717 | 74858.3052 | 41399.6908 | 4997.3574 | 36.0864 | 0.0002068 | 8.96e-05 | 2.2e-06 | 0.017565 | 0.0099938 | 0.0017564 | 5.1e-05 | 5000000 | scaled
991-1 | 626861.7505 | 412906.0205 | 212996.3684 | 959.3616 | 65.87% | 33.98% | 0.153% | 303791.5275 | 606395.4715 | 40714.5044 | 86042.9486 | 177034.0745 | 79887.3408 | 178870.6119 | 347637.5189 | 991 |  | 1340 | 991-1 | 626861.7505 | 323070.223 | 20466.279 | 412906.0205 | 203905.0669 | 3557.7378 | 212996.3684 | 118205.7945 | 15949.1796 | 959.3616 | 80606.1948 | 39891.6904 | 718.854 | 80362.4695 | 39756.1098 | 699.936 | 243.0035 | 134.8587 | 18.1961 | 0.72189 | 352043.3261 | 175009.2516 | 4405.8072 | 332425.1881 | 164083.063 | 2856.1767 | 19530.989 | 10839.0396 | 1462.4815 | 87.1491 | 194212.2296 | 108169.281 | 15341.6177 | 118.363 | 65.8941 | 1.6252 | 193222.3759 | 107231.8962 | 14468.5019 | 871.4906 | 0.0036662 | 0.0019176 | 4.86e-05 | 0.02973 | 0.016873 | 0.002973 | 0.001376 | 5000000 | scaled
991-1206R | 4576791.095 | 4566681.8556 | 4519.9221 | 5589.3174 | 99.78% | 0.09876% | 0.1221% | 1657176.2382 | 4510532.8941 | 196871.357 | 1716.3437 | 1458588.5376 | 537133.2622 | 3716.9365 | 3969682.6954 | 991 |  | 1341 | 991-1206R | 4576791.095 | 2919614.8568 | 66258.2009 | 4566681.8556 | 2911516.3589 | 60330.0705 | 4519.9221 | 2509.1806 | 338.8131 | 5589.3174 | 544326.3532 | 347454.9962 | 7193.091 | 544301.6336 | 347439.4024 | 7187.3475 | 20.5138 | 11.388 | 1.5377 | 4.2058 | 4023395.3956 | 2564806.858 | 53712.7002 | 4021957.9889 | 2563783.0259 | 53135.2749 | 929.6693 | 516.0948 | 69.6879 | 507.7374 | 9069.3462 | 7353.0026 | 5352.4097 | 422.233 | 293.9306 | 7.4481 | 3569.739 | 1981.6978 | 267.5874 | 5077.3742 | 0.025819 | 0.016642 | 0.0004222 | 0.030104 | 0.017087 | 0.0030104 | 0.0078618 | 5000000 | scaled
CB 100 | 5517.2567 | 2920.5837 | 0 | 2596.673 | 52.94% | 0% | 47.06% | 1023.9353 | 2871.4767 | 95.9741 | 373.5264 | 554.4348 | 275.8056 | 1012.166 | 1583.5051 | 100 |  | 1342 | CB 100 | 5517.2567 | 4493.3214 | 2645.7799 | 2920.5837 | 1896.6484 | 49.107 | 0 | 0 | 0 | 2596.673 | 283.0014 | 187.0273 | 7.1958 | 281.0475 | 185.0734 | 5.2419 | 0 | 0 | 0 | 1.9539 | 1848.2234 | 1293.7886 | 264.7183 | 1612.3398 | 1057.9051 | 28.8347 | 0 | 0 | 0 | 235.8836 | 3386.0319 | 3012.5055 | 2373.8659 | 1027.1963 | 653.6699 | 15.0304 | 0 | 0 | 0 | 2358.8355 | 0.007432 | 0.0045372 | 0.0001152 | 0 | 0 | 0 | 0.003691 | 5000000 | scaled
CB 1007 | 183251.9699 | 182883.0134 | 0 | 368.9566 | 99.8% | 0% | 0.2013% | 43810.8032 | 181827.1029 | 2726.7282 | 4169.8517 | 36914.2233 | 11096.1223 | 16414.6335 | 154316.347 | 1007 |  | 1343 | CB 1007 | 183251.9699 | 139441.1667 | 1424.8671 | 182883.0134 | 139072.2102 | 1055.9105 | 0 | 0 | 0 | 368.9566 | 11174.6896 | 8447.9614 | 78.5673 | 11174.412 | 8447.6838 | 78.2897 | 0 | 0 | 0 | 0.27763 | 155079.3118 | 118165.0885 | 762.9648 | 155045.7956 | 118131.5723 | 729.4486 | 0 | 0 | 0 | 33.5163 | 16997.9685 | 12828.1167 | 583.3349 | 16662.8058 | 12492.9541 | 248.1722 | 0 | 0 | 0 | 335.1627 | 0.0018646 | 0.0013912 | 3.52e-05 | 0 | 0 | 0 | 0.000506 | 5000000 | scaled
CB 1023 | 3332738.6224 | 3326464.9375 | 3614.8923 | 2658.7926 | 99.81% | 0.1085% | 0.07978% | 966440.4732 | 3252198.1038 | 52093.6904 | 13187.574 | 901159.2089 | 175785.3701 | 49467.765 | 3026944.9688 | 1023 |  | 1344 | CB 1023 | 3332738.6224 | 2366298.1492 | 80540.5186 | 3326464.9375 | 2361616.2309 | 77575.2038 | 3614.8923 | 2023.1257 | 306.5222 | 2658.7926 | 179951.0896 | 127857.3992 | 4165.7195 | 179945.1259 | 127853.1806 | 4163.3828 | 3.963 | 2.218 | 0.33604 | 2.0007 | 3099811.2075 | 2198651.9986 | 72866.2387 | 3099003.324 | 2198093.5024 | 72576.6884 | 566.357 | 316.9697 | 48.0238 | 241.5265 | 52976.3254 | 39788.7514 | 3508.5604 | 47516.4876 | 35669.5479 | 835.1327 | 3044.5723 | 1703.938 | 258.1623 | 2415.2654 | 0.012075 | 0.0086898 | 0.0002204 | 0.066411 | 0.03766 | 0.0066412 | 0.003781 | 5000000 | scaled
CB 103 | 251307.8778 | 10163.2996 | 233490.8504 | 7653.7279 | 4.044% | 92.91% | 3.046% | 110017.4003 | 228039.696 | 237.3484 | 98159.0113 | 11621.0406 | 463.5071 | 203417.2507 | 24158.9382 | 103 |  | 1345 | CB 103 | 251307.8778 | 141290.4776 | 23268.1818 | 10163.2996 | 4322.4382 | 113.4597 | 233490.8504 | 129314.3115 | 15500.9942 | 7653.7279 | 495.7747 | 258.4264 | 32.2676 | 116.0422 | 45.4995 | 1.5767 | 373.9733 | 207.1677 | 24.9317 | 5.7592 | 26547.4484 | 14926.4079 | 2388.5102 | 552.7231 | 216.6093 | 7.5452 | 25299.4554 | 14014.5287 | 1685.6952 | 695.2699 | 224264.6547 | 126105.6433 | 20847.404 | 9494.5342 | 4060.3295 | 104.3379 | 207817.4216 | 115092.6151 | 13790.3673 | 6952.6988 | 0.019596 | 0.0084854 | 0.0002164 | 0.014383 | 0.0081966 | 0.0014382 | 0.010875 | 5000000 | scaled
CB 1039 | 89253.9647 | 59286.2897 | 29209.2377 | 758.4373 | 66.42% | 32.73% | 0.8498% | 48181.1187 | 85860.8224 | 2382.2733 | 22435.6887 | 23363.1568 | 3964.7913 | 43084.5221 | 38811.5091 | 1039 |  | 1346 | CB 1039 | 89253.9647 | 41072.846 | 3393.1423 | 59286.2897 | 24025.4734 | 303.832 | 29209.2377 | 16288.9353 | 2330.8729 | 758.4373 | 3989.0989 | 1606.8256 | 24.3076 | 3938.6908 | 1578.4624 | 19.7599 | 49.8373 | 27.7925 | 3.977 | 0.5707 | 39226.027 | 15862.8702 | 414.518 | 36532.2492 | 14330.1722 | 136.1577 | 2624.8809 | 1463.8011 | 209.4633 | 68.897 | 46038.8388 | 23603.1501 | 2954.3167 | 18815.3497 | 8116.8388 | 147.9145 | 26534.5195 | 14797.3417 | 2117.4326 | 688.9696 | 0.0018782 | 0.0008134 | 2.08e-05 | 0.044308 | 0.025142 | 0.0044308 | 0.0010548 | 5000000 | scaled
CB 1049 | 5615.9508 | 1375.915 | 0 | 4240.0358 | 24.5% | 0% | 75.5% | 766.3522 | 1359.1602 | 7.008 | 723.5252 | 35.819 | 15.44 | 1264.8379 | 78.8824 | 1049 |  | 1347 | CB 1049 | 5615.9508 | 4849.5986 | 4256.7906 | 1375.915 | 609.5628 | 16.7548 | 0 | 0 | 0 | 4240.0358 | 19.0888 | 12.0808 | 3.6489 | 15.8983 | 8.8903 | 0.45837 | 0 | 0 | 0 | 3.1905 | 466.3854 | 430.5664 | 387.503 | 81.2176 | 45.3986 | 2.3353 | 0 | 0 | 0 | 385.1678 | 5130.4766 | 4406.9514 | 3865.6387 | 1278.799 | 555.2739 | 13.9612 | 0 | 0 | 0 | 3851.6776 | 0.010452 | 0.004557 | 0.0001152 | 0 | 0 | 0 | 0.0060232 | 5000000 | scaled
CB 107 | 5641.2766 | 4171.6485 | 0 | 1469.6281 | 73.95% | 0% | 26.05% | 2233.4146 | 4121.6674 | 7.8948 | 2195.6171 | 29.9027 | 15.9071 | 4045.3408 | 60.4196 | 107 |  | 1348 | CB 107 | 5641.2766 | 3407.862 | 1519.6092 | 4171.6485 | 1938.2339 | 49.9811 | 0 | 0 | 0 | 1469.6281 | 17.0129 | 9.1181 | 1.1058 | 15.9071 | 8.0123 | 0 | 0 | 0 | 0 | 1.1058 | 193.9216 | 164.0189 | 133.502 | 60.4196 | 30.5169 | 0 | 0 | 0 | 0 | 133.502 | 5430.3421 | 3234.7249 | 1385.0013 | 4095.3218 | 1899.7047 | 49.9811 | 0 | 0 | 0 | 1335.0202 | 0.0034994 | 0.0016036 | 4.2e-05 | 0 | 0 | 0 | 0.0020876 | 5000000 | scaled
CB 1073 | 166060.2067 | 10150.6084 | 152344.3473 | 3565.251 | 6.113% | 91.74% | 2.147% | 73193.6653 | 152202.5944 | 249.1951 | 65528.1863 | 7416.2839 | 491.196 | 136369.9234 | 15341.475 | 1073 |  | 1349 | CB 1073 | 166060.2067 | 92866.5415 | 13857.6124 | 10150.6084 | 4978.0029 | 112.6031 | 152344.3473 | 84323.2875 | 10179.7582 | 3565.251 | 508.7074 | 259.5123 | 17.5115 | 325.5258 | 156.9226 | 2.7677 | 180.4989 | 99.907 | 12.0611 | 2.6827 | 16656.8636 | 9240.5797 | 1315.3886 | 1708.8901 | 822.2021 | 14.3257 | 14624.1036 | 8094.5077 | 977.1931 | 323.8698 | 148894.6357 | 83366.4495 | 12524.7123 | 8116.1926 | 3998.8782 | 95.5098 | 137539.7447 | 76128.8728 | 9190.5041 | 3238.6985 | 0.011226 | 0.0049718 | 0.0001264 | 0.017522 | 0.0099772 | 0.0017522 | 0.0049938 | 5000000 | scaled
CB 1076 | 20778.7215 | 17779.1252 | 0 | 2999.5963 | 85.56% | 0% | 14.44% | 9168.7615 | 17559.8351 | 7.0159 | 9124.94 | 36.8056 | 13.8603 | 17473.3234 | 72.6514 | 1076 |  | 1350 | CB 1076 | 20778.7215 | 11609.96 | 3218.8864 | 17779.1252 | 8610.3637 | 219.29 | 0 | 0 | 0 | 2999.5963 | 16.2767 | 9.2608 | 2.4163 | 14.0196 | 7.0037 | 0.15923 | 0 | 0 | 0 | 2.2571 | 345.9669 | 309.1613 | 273.3155 | 73.4815 | 36.6759 | 0.83009 | 0 | 0 | 0 | 272.4854 | 20416.478 | 11291.538 | 2943.1546 | 17691.6242 | 8566.6841 | 218.3007 | 0 | 0 | 0 | 2724.8538 | 0.0073198 | 0.0033296 | 8.44e-05 | 0 | 0 | 0 | 0.0042256 | 5000000 | scaled
CB 1077 | 27170.962 | 21372.8943 | 0 | 5798.0677 | 78.66% | 0% | 21.34% | 12593.4427 | 21342.9723 | 1489.0652 | 3515.9456 | 7588.432 | 2508.3478 | 6155.8253 | 12678.7993 | 1077 |  | 1351 | CB 1077 | 27170.962 | 14577.5193 | 5827.9897 | 21372.8943 | 8779.4515 | 29.9219 | 0 | 0 | 0 | 5798.0677 | 2512.7106 | 1023.6455 | 4.3629 | 2508.3478 | 1019.2826 | 0 | 0 | 0 | 0 | 4.3629 | 13205.4997 | 5617.0677 | 526.7004 | 12678.7993 | 5090.3673 | 0 | 0 | 0 | 0 | 526.7004 | 11452.7516 | 7936.8061 | 5296.9264 | 6185.7472 | 2669.8016 | 29.9219 | 0 | 0 | 0 | 5267.0044 | 0.014901 | 0.0064512 | 0.000164 | 0 | 0 | 0 | 0.0082062 | 5000000 | scaled
CB 1079 | 15973.6482 | 14386.2163 | 0 | 1587.432 | 90.06% | 0% | 9.938% | 4549.7934 | 14133.9216 | 137.9024 | 4047.4473 | 364.4438 | 728.2702 | 11234.6648 | 2170.9867 | 1079 |  | 1352 | CB 1079 | 15973.6482 | 11423.8548 | 1839.7266 | 14386.2163 | 9836.4228 | 252.2946 | 0 | 0 | 0 | 1587.432 | 744.0398 | 606.1374 | 15.7696 | 742.8453 | 604.9429 | 14.5751 | 0 | 0 | 0 | 1.1945 | 2359.8338 | 1995.39 | 188.8471 | 2215.6304 | 1851.1866 | 44.6437 | 0 | 0 | 0 | 144.2034 | 12869.7747 | 8822.3274 | 1635.1099 | 11427.7406 | 7380.2933 | 193.0758 | 0 | 0 | 0 | 1442.0341 | 0.004961 | 0.0025118 | 6.4e-05 | 0 | 0 | 0 | 0.0022538 | 5000000 | scaled
CB 1081 | 237950.4647 | 71179.2619 | 160695.6239 | 6075.5789 | 29.91% | 67.53% | 2.553% | 108866.6534 | 220202.6356 | 1927.6629 | 97036.0698 | 9902.9206 | 3378.4864 | 197271.0378 | 19553.1114 | 1081 |  | 1353 | CB 1081 | 237950.4647 | 129083.8113 | 17747.829 | 71179.2619 | 34382.2182 | 928.3678 | 160695.6239 | 88626.0141 | 10743.8823 | 6075.5789 | 3443.8131 | 1516.1502 | 65.3267 | 3240.2767 | 1401.8465 | 47.4525 | 198.9647 | 109.732 | 13.3025 | 4.5717 | 21206.8359 | 11303.9153 | 1653.7245 | 5348.4957 | 2310.2827 | 78.4484 | 15306.4304 | 8441.7228 | 1023.3663 | 551.9098 | 213299.8156 | 116263.7458 | 16028.7778 | 62590.4894 | 30670.089 | 802.4668 | 145190.2287 | 80074.5593 | 9707.2135 | 5519.0975 | 0.018152 | 0.008367 | 0.0002122 | 0.010213 | 0.005795 | 0.0010212 | 0.0085934 | 5000000 | scaled
CB 1082 | 15792.6851 | 9713.8953 | 5331.4002 | 747.3896 | 61.51% | 33.76% | 4.733% | 5261.3041 | 14386.9103 | 291.5503 | 1967.3111 | 3002.4427 | 952.3276 | 4147.9225 | 9286.6602 | 1082 |  | 1354 | CB 1082 | 15792.6851 | 10531.381 | 1405.7748 | 9713.8953 | 6844.8188 | 302.354 | 5331.4002 | 2939.1726 | 356.0312 | 747.3896 | 981.195 | 689.6447 | 28.8674 | 971.7095 | 684.1631 | 27.7091 | 8.9231 | 4.9193 | 0.59589 | 0.56239 | 9699.0736 | 6696.6309 | 412.4134 | 8531.4482 | 6022.4611 | 271.0799 | 1099.732 | 606.2764 | 73.4402 | 67.8934 | 5112.4164 | 3145.1053 | 964.4939 | 210.7375 | 138.1946 | 3.5649 | 4222.7451 | 2327.9769 | 281.9952 | 678.9338 | 0.0028188 | 0.0018946 | 4.8e-05 | 0.010347 | 0.0058698 | 0.0010348 | 0.0010558 | 5000000 | scaled
CB 1085 | 121815.0932 | 35728.2937 | 85612.6935 | 474.106 | 29.33% | 70.28% | 0.3892% | 58170.3267 | 115265.6617 | 728.5782 | 50102.6103 | 7339.1383 | 1276.8451 | 100326.606 | 13662.2106 | 1085 |  | 1355 | CB 1085 | 121815.0932 | 63644.7665 | 6549.4315 | 35728.2937 | 15860.1397 | 304.765 | 85612.6935 | 47310.5208 | 5770.5605 | 474.106 | 1291.303 | 562.7248 | 14.4579 | 1189.8267 | 506.4883 | 7.2853 | 101.1195 | 55.8797 | 6.8158 | 0.35675 | 14218.4356 | 6879.2973 | 556.225 | 7149.4287 | 2953.6178 | 39.5869 | 7025.9387 | 3882.6114 | 473.57 | 43.0681 | 106305.3547 | 56202.7444 | 5978.7487 | 27389.0382 | 12400.0336 | 257.8928 | 78485.6353 | 43372.0296 | 5290.1747 | 430.6812 | 0.0012322 | 0.0006072 | 1.54e-05 | 0.0073508 | 0.0041772 | 0.000735 | 0.000659 | 5000000 | scaled
CB 1090 | 1414511.4007 | 1409149.397 | 2373.7606 | 2988.243 | 99.62% | 0.1678% | 0.2113% | 725693.5307 | 1389026.0487 | 41276.426 | 1270.8725 | 683146.2322 | 78944.9699 | 2643.2578 | 1307437.8211 | 1090 |  | 1356 | CB 1090 | 1414511.4007 | 688817.87 | 25485.3519 | 1409149.397 | 684512.7007 | 22338.8083 | 2373.7606 | 1316.9263 | 158.3006 | 2988.243 | 80189.7767 | 38913.3508 | 1244.8069 | 80172.545 | 38902.7898 | 1241.5591 | 14.9832 | 8.3124 | 0.99919 | 2.2486 | 1328818.5618 | 645672.3296 | 21380.7407 | 1328216.9165 | 645217.6905 | 21087.267 | 330.1912 | 183.1851 | 22.0197 | 271.454 | 5503.0622 | 4232.1897 | 2859.8044 | 759.9355 | 392.2204 | 9.9822 | 2028.5863 | 1125.4288 | 135.2817 | 2714.5404 | 0.015841 | 0.0074226 | 0.0001886 | 0.0050744 | 0.0028958 | 0.0005074 | 0.004198 | 5000000 | scaled
CB 1094 | 25268.9149 | 24948.6992 | 0 | 320.2157 | 98.73% | 0% | 1.267% | 9286.7546 | 24768.143 | 651.1635 | 3040.9327 | 5594.6584 | 1728.7301 | 8297.4624 | 14741.9504 | 1094 |  | 1357 | CB 1094 | 25268.9149 | 15982.1603 | 500.7719 | 24948.6992 | 15661.9446 | 180.5562 | 0 | 0 | 0 | 320.2157 | 1738.3374 | 1087.174 | 9.6073 | 1738.0965 | 1086.933 | 9.3664 | 0 | 0 | 0 | 0.24095 | 14832.187 | 9237.5286 | 90.2365 | 14803.0983 | 9208.44 | 61.1479 | 0 | 0 | 0 | 29.0886 | 8698.3905 | 5657.4578 | 400.9281 | 8407.5044 | 5366.5716 | 110.042 | 0 | 0 | 0 | 290.8861 | 0.001006 | 0.0005918 | 1.5e-05 | 0 | 0 | 0 | 0.000442 | 5000000 | scaled
CB 1101 | 1133279.0417 | 1130104.6303 | 1733.1702 | 1441.2411 | 99.72% | 0.1529% | 0.1272% | 394848.759 | 1115233.6782 | 24946.1808 | 14248.3697 | 355654.2085 | 71271.0064 | 42607.1875 | 1001355.4843 | 1101 |  | 1358 | CB 1101 | 1133279.0417 | 738430.2827 | 18045.3634 | 1130104.6303 | 736018.8934 | 16456.1465 | 1733.1702 | 970.1482 | 147.9758 | 1441.2411 | 72350.7152 | 47404.5344 | 1079.7088 | 72327.146 | 47390.864 | 1076.7046 | 22.4848 | 12.5859 | 1.9197 | 1.0845 | 1016160.7192 | 660506.5107 | 14805.2348 | 1015676.3334 | 660177.7355 | 14644.1333 | 353.4624 | 197.8518 | 30.1782 | 130.9233 | 44767.6073 | 30519.2376 | 2160.4198 | 42101.1509 | 28450.2939 | 735.3086 | 1357.2231 | 759.7104 | 115.878 | 1309.2333 | 0.020012 | 0.013542 | 0.0003442 | 0.069561 | 0.039416 | 0.0069562 | 0.002005 | 5000000 | scaled
CB 1106 | 1646983.7054 | 568815.0503 | 1077373.3445 | 795.3106 | 34.54% | 65.41% | 0.04829% | 792476.4463 | 1550380.2018 | 17741.7227 | 434782.1565 | 339952.5671 | 31510.6269 | 904010.8181 | 614858.7568 | 1106 |  | 1359 | CB 1106 | 1646983.7054 | 854507.2591 | 96603.5036 | 568815.0503 | 252530.564 | 8544.6727 | 1077373.3445 | 601181.3845 | 87263.5203 | 795.3106 | 32073.3116 | 14331.5888 | 562.6847 | 30814.8473 | 13627.1479 | 456.0629 | 1257.8659 | 703.8425 | 106.0234 | 0.59845 | 630804.8408 | 290852.2737 | 15946.084 | 537967.8723 | 238888.9397 | 8088.2468 | 92764.7219 | 51891.0874 | 7785.5907 | 72.2466 | 984105.553 | 549323.3966 | 80094.7349 | 32.3307 | 14.4764 | 0.36305 | 983350.7567 | 548586.4545 | 79371.9063 | 722.4656 | 0.003777 | 0.0016992 | 4.26e-05 | 0.065885 | 0.037348 | 0.0065884 | 0.0011122 | 5000000 | scaled
CB 1116 | 9336.3944 | 9205.221 | 0 | 131.1735 | 98.6% | 0% | 1.405% | 6904.8503 | 9198.8537 | 520.7918 | 0.12914 | 6383.9294 | 698.8251 | 0.22475 | 8499.8038 | 1116 |  | 1360 | CB 1116 | 9336.3944 | 2431.5441 | 137.5407 | 9205.221 | 2300.3707 | 6.3672 | 0 | 0 | 0 | 131.1735 | 699.8345 | 179.0427 | 1.0094 | 699.7358 | 178.944 | 0.91066 | 0 | 0 | 0 | 0.098704 | 8517.1743 | 2133.245 | 17.3705 | 8505.2585 | 2121.3291 | 5.4546 | 0 | 0 | 0 | 11.9159 | 119.3856 | 119.2564 | 119.1608 | 0.2267 | 0.097561 | 0.0019564 | 0 | 0 | 0 | 119.1589 | 0.0005116 | 0.0002214 | 5.4e-06 | 0 | 0 | 0 | 0.0001996 | 5000000 | scaled
CB 1138 | 765496.0507 | 574088.3659 | 185839.2915 | 5568.3932 | 75% | 24.28% | 0.7274% | 394577.9969 | 733792.078 | 32583.526 | 79573.3252 | 282421.1457 | 58551.7443 | 164324.4346 | 510915.8991 | 1138 |  | 1361 | CB 1138 | 765496.0507 | 370918.0538 | 31703.9727 | 574088.3659 | 260781.2753 | 9648.1726 | 185839.2915 | 104568.3853 | 16487.4069 | 5568.3932 | 59543.6304 | 26960.1044 | 991.8861 | 59217.448 | 26774.7352 | 959.1294 | 321.9923 | 181.1792 | 28.5667 | 4.19 | 521466.2046 | 239045.0589 | 10550.3055 | 504354.9395 | 229195.65 | 8571.258 | 16605.4285 | 9343.5722 | 1473.2108 | 505.8367 | 184486.2156 | 104912.8905 | 20161.781 | 10515.9784 | 4810.8901 | 117.7851 | 168911.8707 | 95043.6338 | 14985.6294 | 5058.3665 | 0.017 | 0.0075816 | 0.0001924 | 0.089365 | 0.05076 | 0.0089366 | 0.0078124 | 5000000 | scaled
CB 1139 | 1980.9302 | 1753.6082 | 0 | 227.322 | 88.52% | 0% | 11.48% | 831.507 | 1736.2651 | 14.193 | 747.4418 | 69.8723 | 48.6929 | 1428.936 | 258.6361 | 1139 |  | 1362 | CB 1139 | 1980.9302 | 1149.4232 | 244.6651 | 1753.6082 | 922.1012 | 17.3431 | 0 | 0 | 0 | 227.322 | 49.5404 | 35.3475 | 0.8475 | 49.3694 | 35.1764 | 0.67645 | 0 | 0 | 0 | 0.17105 | 282.8183 | 212.946 | 24.1822 | 262.1682 | 192.296 | 3.5321 | 0 | 0 | 0 | 20.6501 | 1648.5715 | 901.1297 | 219.6355 | 1442.0706 | 694.6288 | 13.1346 | 0 | 0 | 0 | 206.5009 | 0.0005468 | 0.0002368 | 5.8e-06 | 0 | 0 | 0 | 0.0003394 | 5000000 | scaled
CB 114 | 43248.0725 | 38417.8853 | 3505.8733 | 1324.3139 | 88.83% | 8.106% | 3.062% | 14966.9941 | 41128.4934 | 722.6842 | 9078.6489 | 5165.6609 | 2033.9882 | 24582.3762 | 14512.1291 | 114 |  | 1363 | CB 114 | 43248.0725 | 28281.0784 | 2119.579 | 38417.8853 | 25018.8674 | 560.1333 | 3505.8733 | 1937.8971 | 235.1318 | 1324.3139 | 2062.8713 | 1340.1871 | 28.8831 | 2053.7473 | 1334.6981 | 27.3416 | 8.1275 | 4.4925 | 0.54509 | 0.9965 | 14850.3711 | 9684.7102 | 338.242 | 14194.3699 | 9268.2967 | 182.0122 | 535.6996 | 296.1119 | 35.9283 | 120.3016 | 26334.8301 | 17256.1811 | 1752.4538 | 22169.768 | 14415.8726 | 350.7796 | 2962.0462 | 1637.2927 | 198.6584 | 1203.0159 | 0.0038922 | 0.002393 | 6.08e-05 | 0.0074094 | 0.0042128 | 0.000741 | 0.001886 | 5000000 | scaled
CB 1140 | 668098.3836 | 195.0348 | 667726.7357 | 176.6131 | 0.02919% | 99.94% | 0.02644% | 292453.6769 | 608851.7082 | 414.9595 | 268056.7422 | 23981.9752 | 862.5779 | 558065.5824 | 49923.548 | 1140 |  | 1364 | CB 1140 | 668098.3836 | 375644.7067 | 59246.6753 | 195.0348 | 83.6948 | 1.9885 | 667726.7357 | 375384.3988 | 59068.0738 | 176.6131 | 945.8161 | 530.8567 | 83.2383 | 6.6312 | 2.805 | 0.035471 | 939.052 | 527.9188 | 83.0699 | 0.1329 | 54781.3929 | 30799.4177 | 4857.8449 | 33.9386 | 14.3235 | 0.18146 | 54731.4106 | 30769.0505 | 4841.6198 | 16.0437 | 612371.1746 | 344314.4324 | 54305.5921 | 154.4649 | 66.5663 | 1.7716 | 612056.2731 | 344087.4295 | 54143.384 | 160.4365 | 0.0006006 | 0.00026 | 6.6e-06 | 0.086295 | 0.048983 | 0.0086294 | 0.0002502 | 5000000 | scaled
CB 1152 | 1260.1284 | 1109.8128 | 0 | 150.3156 | 88.07% | 0% | 11.93% | 175.7404 | 1101.8558 | 20.2566 | 23.133 | 132.3508 | 123.6199 | 95.5632 | 882.6727 | 1152 |  | 1365 | CB 1152 | 1260.1284 | 1084.388 | 158.2726 | 1109.8128 | 934.0724 | 7.957 | 0 | 0 | 0 | 150.3156 | 124.6157 | 104.3591 | 0.99584 | 124.5026 | 104.246 | 0.88273 | 0 | 0 | 0 | 0.11311 | 901.671 | 769.3203 | 18.9983 | 888.0163 | 755.6655 | 5.3435 | 0 | 0 | 0 | 13.6548 | 233.8417 | 210.7087 | 138.2785 | 97.2939 | 74.1609 | 1.7307 | 0 | 0 | 0 | 136.5478 | 0.00075 | 0.0005696 | 1.44e-05 | 0 | 0 | 0 | 0.0002132 | 5000000 | scaled
CB 1153 | 544.4236 | 371.3913 | 0 | 173.0323 | 68.22% | 0% | 31.78% | 131.75 | 371.3913 | 15.295 | 0 | 116.455 | 45.0932 | 0 | 326.2981 | 1153 |  | 1366 | CB 1153 | 544.4236 | 412.6736 | 173.0323 | 371.3913 | 239.6413 | 0 | 0 | 0 | 0 | 173.0323 | 45.2234 | 29.9284 | 0.1302 | 45.0932 | 29.7982 | 0 | 0 | 0 | 0 | 0.1302 | 342.0165 | 225.5615 | 15.7184 | 326.2981 | 209.8431 | 0 | 0 | 0 | 0 | 15.7184 | 157.1838 | 157.1838 | 157.1838 | 0 | 0 | 0 | 0 | 0 | 0 | 157.1838 | 0.000266 | 0.000199 | 5e-06 | 0 | 0 | 0 | 0.0002428 | 5000000 | scaled
CB 116 | 265469.7034 | 125281.5056 | 136188.4478 | 3999.7501 | 47.19% | 51.3% | 1.507% | 111011.0197 | 249645.5397 | 3556.0138 | 87017.359 | 20437.647 | 9611.5629 | 184758.4644 | 55275.5124 | 116 |  | 1367 | CB 116 | 265469.7034 | 154458.6837 | 15824.1637 | 125281.5056 | 75167.5455 | 2741.4284 | 136188.4478 | 75291.3881 | 9082.9852 | 3999.7501 | 9886.644 | 6330.6303 | 275.0811 | 9712.4072 | 6232.9581 | 260.6515 | 171.2272 | 94.6625 | 11.4199 | 3.0097 | 57809.8838 | 37372.2368 | 2534.3714 | 46350.4112 | 30874.4321 | 1430.9832 | 11096.1326 | 6134.4647 | 740.0481 | 363.34 | 197773.1756 | 110755.8166 | 13014.7111 | 69218.6872 | 38060.1553 | 1049.7936 | 124921.088 | 69062.261 | 8331.5172 | 3633.4003 | 0.016879 | 0.0087488 | 0.0002218 | 0.014506 | 0.008251 | 0.0014506 | 0.0056442 | 5000000 | scaled
CB 1160 | 2382.5618 | 215.4308 | 1991.0267 | 176.1044 | 9.042% | 83.57% | 7.391% | 998.7939 | 2038.8625 | 11.4102 | 779.4398 | 207.9439 | 20.5029 | 1602.1023 | 416.2573 | 1160 |  | 1368 | CB 1160 | 2382.5618 | 1383.7679 | 343.6993 | 215.4308 | 92.9564 | 2.1709 | 1991.0267 | 1114.7072 | 165.424 | 176.1044 | 21.801 | 10.3908 | 1.2981 | 8.0236 | 2.619 | 0.031924 | 13.6448 | 7.6393 | 1.1337 | 0.13251 | 466.3743 | 258.4304 | 50.117 | 41.8096 | 13.6903 | 0.17384 | 408.5673 | 228.7427 | 33.9457 | 15.9974 | 1894.3865 | 1114.9467 | 292.2842 | 165.5975 | 76.6471 | 1.9652 | 1568.8145 | 878.3251 | 130.3446 | 159.9744 | 0.0004422 | 0.000202 | 5.2e-06 | 0.058676 | 0.033334 | 0.0058676 | 0.0002502 | 5000000 | scaled
CB 1161 | 18246.5091 | 3077.2862 | 14370.6681 | 798.5549 | 16.87% | 78.76% | 4.376% | 7129.7049 | 15331.1076 | 66.9378 | 5392.7297 | 1670.0374 | 177.1044 | 11533.6263 | 3620.3769 | 1161 |  | 1369 | CB 1161 | 18246.5091 | 11116.8043 | 2915.4015 | 3077.2862 | 2276.5276 | 922.9935 | 14370.6681 | 8041.7218 | 1193.8531 | 798.5549 | 238.2744 | 171.3366 | 61.17 | 209.7211 | 155.0937 | 58.2469 | 27.9525 | 15.642 | 2.3222 | 0.60089 | 4789.8233 | 3119.7859 | 1169.4464 | 1753.7853 | 1388.8933 | 850.7107 | 2963.4967 | 1658.3513 | 246.1945 | 72.5413 | 13218.4114 | 7825.6817 | 1684.7851 | 1113.7798 | 732.5405 | 14.0359 | 11379.2188 | 6367.7284 | 945.3364 | 725.4128 | 0.0019282 | 0.0012536 | 3.22e-05 | 0.058701 | 0.033329 | 0.00587 | 0.0011424 | 5000000 | scaled
CB 1162 | 75200.8278 | 72679.151 | 1485.0404 | 1036.6364 | 96.65% | 1.975% | 1.378% | 26511.5071 | 71800.87 | 1660.9702 | 653.1158 | 24197.4211 | 4555.1181 | 1652.6009 | 65593.1509 | 1162 |  | 1370 | CB 1162 | 75200.8278 | 48689.3207 | 3399.9579 | 72679.151 | 46821.8062 | 2239.9492 | 1485.0404 | 830.8781 | 123.3722 | 1036.6364 | 4687.7452 | 3026.7749 | 132.627 | 4685.9898 | 3025.4492 | 131.766 | 0.97531 | 0.54568 | 0.081025 | 0.78004 | 67809.3365 | 43611.9154 | 2216.1855 | 67408.5297 | 43346.1831 | 2096.5423 | 306.638 | 171.5636 | 25.4745 | 94.1688 | 2703.7462 | 2050.6304 | 1051.1453 | 584.6315 | 450.174 | 11.641 | 1177.4271 | 658.7688 | 97.8167 | 941.6876 | 0.004021 | 0.0023814 | 6.08e-05 | 0.058716 | 0.033337 | 0.0058716 | 0.0014766 | 5000000 | scaled
CB 1166 | 70820.1283 | 70676.1193 | 0 | 144.009 | 99.8% | 0% | 0.2033% | 21943.659 | 70675.1702 | 1189.434 | 16.4139 | 20737.8111 | 3840.9772 | 67.3234 | 66766.8695 | 1166 |  | 1371 | CB 1166 | 70820.1283 | 48876.4693 | 144.9581 | 70676.1193 | 48732.4603 | 0.94908 | 0 | 0 | 0 | 144.009 | 3841.0856 | 2651.6515 | 0.10836 | 3840.9772 | 2651.5432 | 0 | 0 | 0 | 0 | 0.10836 | 66779.9514 | 46042.1403 | 13.0819 | 66766.8695 | 46029.0585 | 0 | 0 | 0 | 0 | 13.0819 | 199.0913 | 182.6774 | 131.7679 | 68.2725 | 51.8586 | 0.94908 | 0 | 0 | 0 | 130.8188 | 0.0003126 | 0.0002374 | 6e-06 | 0 | 0 | 0 | 0.0002016 | 5000000 | scaled
CB 1173 | 2968.1638 | 1758.5407 | 0 | 1209.6231 | 59.25% | 0% | 40.75% | 997.1183 | 1739.5602 | 0 | 997.1183 | 0 | 0 | 1739.5602 | 0 | 1173 |  | 1372 | CB 1173 | 2968.1638 | 1971.0455 | 1228.6036 | 1758.5407 | 761.4224 | 18.9805 | 0 | 0 | 0 | 1209.6231 | 0.9102 | 0.9102 | 0.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9102 | 109.883 | 109.883 | 109.883 | 0 | 0 | 0 | 0 | 0 | 0 | 109.883 | 2857.3706 | 1860.2523 | 1117.8104 | 1758.5407 | 761.4224 | 18.9805 | 0 | 0 | 0 | 1098.8299 | 0.00237 | 0.0010262 | 2.56e-05 | 0 | 0 | 0 | 0.0017136 | 5000000 | scaled
CB 1174 | 340.5002 | 0 | 0 | 340.5002 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 |  | 1373 | CB 1174 | 340.5002 | 340.5002 | 340.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 340.5002 | 0.25622 | 0.25622 | 0.25622 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25622 | 30.9313 | 30.9313 | 30.9313 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9313 | 309.3127 | 309.3127 | 309.3127 | 0 | 0 | 0 | 0 | 0 | 0 | 309.3127 | 0.0006108 | 0.0002646 | 6.8e-06 | 0 | 0 | 0 | 0.0004936 | 5000000 | scaled
CB 1180 | 35233.2979 | 34439.8324 | 0 | 793.4656 | 97.75% | 0% | 2.252% | 17228.7138 | 34011.5311 | 717.0314 | 13808.9738 | 2702.7087 | 1429.077 | 27189.0591 | 5393.3949 | 1180 |  | 1374 | CB 1180 | 35233.2979 | 18004.5841 | 1221.7669 | 34439.8324 | 17211.1185 | 428.3013 | 0 | 0 | 0 | 793.4656 | 1448.9067 | 731.8753 | 19.8297 | 1448.3097 | 731.2783 | 19.2327 | 0 | 0 | 0 | 0.59706 | 5537.9066 | 2835.1979 | 144.5116 | 5465.8276 | 2763.1189 | 72.4327 | 0 | 0 | 0 | 72.079 | 28246.4846 | 14437.5109 | 1057.4255 | 27525.6951 | 13716.7214 | 336.636 | 0 | 0 | 0 | 720.7895 | 0.0028144 | 0.0013992 | 3.56e-05 | 0 | 0 | 0 | 0.0010918 | 5000000 | scaled
CB 120 | 72890.1441 | 34143.679 | 37939.8424 | 806.6228 | 46.84% | 52.05% | 1.107% | 36684.9021 | 69293.4476 | 2108.1339 | 17683.2854 | 16893.4828 | 3633.7048 | 36161.5371 | 29498.2058 | 120 |  | 1375 | CB 120 | 72890.1441 | 36205.242 | 3596.6965 | 34143.679 | 14412.9639 | 240.9949 | 37939.8424 | 20985.6554 | 2549.0789 | 806.6228 | 3663.7465 | 1555.6126 | 30.0417 | 3615.2665 | 1528.5256 | 26.2183 | 47.8731 | 26.48 | 3.2165 | 0.60696 | 29964.4097 | 13070.9269 | 466.2039 | 26638.8039 | 11198.6914 | 174.4141 | 3252.3316 | 1798.9614 | 218.5157 | 73.2742 | 39261.9879 | 21578.7025 | 3100.4509 | 3889.6086 | 1685.7469 | 40.3625 | 34639.6377 | 19160.214 | 2327.3467 | 732.7416 | 0.0021122 | 0.000915 | 2.34e-05 | 0.0073744 | 0.0041946 | 0.0007374 | 0.0011316 | 5000000 | scaled
CB 1215 | 21822.314 | 21747.2499 | 0 | 75.0641 | 99.66% | 0% | 0.344% | 4564.9832 | 21746.7835 | 247.4473 | 7.688 | 4309.8479 | 1168.6976 | 31.4673 | 20546.6185 | 1215 |  | 1376 | CB 1215 | 21822.314 | 17257.3308 | 75.5305 | 21747.2499 | 17182.2667 | 0.4664 | 0 | 0 | 0 | 75.0641 | 1168.7541 | 921.3068 | 0.056483 | 1168.6976 | 921.2503 | 0 | 0 | 0 | 0 | 0.056483 | 20553.4374 | 16243.5895 | 6.8189 | 20546.6185 | 16236.7707 | 0 | 0 | 0 | 0 | 6.8189 | 100.1225 | 92.4345 | 68.6552 | 31.9337 | 24.2457 | 0.4664 | 0 | 0 | 0 | 68.1888 | 0.0001544 | 0.0001174 | 3e-06 | 0 | 0 | 0 | 0.0001032 | 5000000 | scaled
CB 1219 | 344.0997 | 92.5809 | 0 | 251.5187 | 26.91% | 0% | 73.09% | 58.9445 | 90.091 | 8.6757 | 2.858 | 47.4108 | 13.2533 | 4.954 | 71.8836 | 1219 |  | 1377 | CB 1219 | 344.0997 | 285.1552 | 254.0087 | 92.5809 | 33.6364 | 2.4899 | 0 | 0 | 0 | 251.5187 | 13.8363 | 5.1606 | 0.58299 | 13.6471 | 4.9714 | 0.39373 | 0 | 0 | 0 | 0.18926 | 96.7747 | 49.3639 | 24.891 | 73.9265 | 26.5157 | 2.0429 | 0 | 0 | 0 | 22.8481 | 233.4887 | 230.6307 | 228.5347 | 5.0073 | 2.1493 | 0.053302 | 0 | 0 | 0 | 228.4814 | 0.0004564 | 0.0001976 | 5e-06 | 0 | 0 | 0 | 0.000351 | 5000000 | scaled
CB 122 | 8109.9916 | 6303.807 | 0 | 1806.1846 | 77.73% | 0% | 22.27% | 3486.3079 | 6225.7895 | 134.6466 | 2645.7006 | 705.9606 | 244.4767 | 4699.656 | 1281.6568 | 122 |  | 1378 | CB 122 | 8109.9916 | 4623.6837 | 1884.2021 | 6303.807 | 2817.4991 | 78.0175 | 0 | 0 | 0 | 1806.1846 | 249.6165 | 114.9699 | 5.1398 | 248.2574 | 113.6108 | 3.7807 | 0 | 0 | 0 | 1.3591 | 1465.7027 | 759.742 | 184.0458 | 1301.6276 | 595.667 | 19.9708 | 0 | 0 | 0 | 164.075 | 6394.6725 | 3748.9718 | 1695.0164 | 4753.922 | 2108.2213 | 54.2659 | 0 | 0 | 0 | 1640.7505 | 0.0044932 | 0.0020636 | 5.2e-05 | 0 | 0 | 0 | 0.0025762 | 5000000 | scaled
CB 123 | 5385.573 | 4431.1482 | 0 | 954.4249 | 82.28% | 0% | 17.72% | 2508.4568 | 4381.7945 | 0.67672 | 2503.9834 | 3.7967 | 1.6002 | 4371.2486 | 8.9457 | 123 |  | 1379 | CB 123 | 5385.573 | 2877.1162 | 1003.7785 | 4431.1482 | 1922.6913 | 49.3537 | 0 | 0 | 0 | 954.4249 | 2.3183 | 1.6416 | 0.71817 | 1.6002 | 0.92344 | 0 | 0 | 0 | 0 | 0.71817 | 95.6463 | 91.8497 | 86.7006 | 8.9457 | 5.149 | 0 | 0 | 0 | 0 | 86.7006 | 5287.6083 | 2783.6249 | 916.3597 | 4420.6023 | 1916.6188 | 49.3537 | 0 | 0 | 0 | 867.0061 | 0.001329 | 0.0005762 | 1.48e-05 | 0 | 0 | 0 | 0.001354 | 5000000 | scaled
CB 1233 | 761.5476 | 692.3736 | 0 | 69.174 | 90.92% | 0% | 9.083% | 1.5932 | 692.274 | 0.26229 | 2.5732 | -1.2423 | 46.2072 | 9.4688 | 636.5981 | 1233 |  | 1380 | CB 1233 | 761.5476 | 759.9545 | 69.2736 | 692.3736 | 690.7804 | 0.099572 | 0 | 0 | 0 | 69.174 | 46.2592 | 45.997 | 0.052051 | 46.2072 | 45.9449 | 0 | 0 | 0 | 0 | 0.052051 | 642.8819 | 644.1242 | 6.2838 | 636.5981 | 637.8404 | 0 | 0 | 0 | 0 | 6.2838 | 72.4065 | 69.8333 | 62.9377 | 9.5683 | 6.9952 | 0.099572 | 0 | 0 | 0 | 62.8382 | 2.68e-05 | 2.04e-05 | 4e-07 | 0 | 0 | 0 | 9.8e-05 | 5000000 | scaled
CB 1234 | 6311491.8914 | 5319836.9588 | 980490.8067 | 11164.1258 | 84.29% | 15.54% | 0.1769% | 3042369.4474 | 6143754.207 | 160437.9477 | 409288.7981 | 2472642.7015 | 325070.4654 | 890732.0517 | 4927951.6899 | 1234 |  | 1381 | CB 1234 | 6311491.8914 | 3269122.4441 | 167737.6844 | 5319836.9588 | 2711209.2827 | 81908.2371 | 980490.8067 | 546749.0356 | 74665.3215 | 11164.1258 | 330094.3731 | 169656.4253 | 5023.9076 | 328881.6776 | 168973.4517 | 4917.7071 | 1204.2948 | 674.573 | 97.7999 | 8.4006 | 5011131.8267 | 2538489.1252 | 83180.1368 | 4929982.3909 | 2492609.7413 | 75701.9617 | 80135.2789 | 44865.2271 | 6464.0183 | 1014.1568 | 970265.6917 | 560976.8935 | 79533.6399 | 60972.8903 | 49626.0897 | 1288.5682 | 899151.233 | 501209.2355 | 68103.5033 | 10141.5684 | 0.051619 | 0.028788 | 0.0007312 | 0.052174 | 0.029705 | 0.0052174 | 0.015821 | 5000000 | scaled
CB 1235 | 6645571.9566 | 6585223.8253 | 45643.4051 | 14704.7262 | 99.09% | 0.6868% | 0.2213% | 3295726.8414 | 6551052.6241 | 247136.44 | 23747.8571 | 3024842.5443 | 490760.8595 | 52680.0996 | 6007611.6651 | 1235 |  | 1382 | CB 1235 | 6645571.9566 | 3349845.1152 | 94519.3324 | 6585223.8253 | 3309789.4105 | 76741.4173 | 45643.4051 | 25350.9786 | 3073.1889 | 14704.7262 | 496575.0477 | 249438.6077 | 5814.1883 | 496502.1422 | 249393.1957 | 5798.9597 | 61.8407 | 34.3472 | 4.1638 | 11.0648 | 6079925.3211 | 3055082.7768 | 72313.656 | 6074708.3216 | 3051591.3106 | 70716.545 | 3881.2121 | 2155.6789 | 261.3236 | 1335.7874 | 69071.5877 | 45323.7306 | 16391.4881 | 14013.3614 | 8804.9042 | 225.9126 | 41700.3524 | 23160.9525 | 2807.7016 | 13357.8739 | 0.056493 | 0.027903 | 0.0007092 | 0.0056448 | 0.0032228 | 0.0005644 | 0.020687 | 5000000 | scaled
CB 124 | 3292.5047 | 2180.937 | 0 | 1111.5677 | 66.24% | 0% | 33.76% | 642.8151 | 2106.2164 | 40.407 | 424.8679 | 177.5402 | 165.8565 | 1162.0031 | 778.3568 | 124 |  | 1383 | CB 124 | 3292.5047 | 2649.6896 | 1186.2883 | 2180.937 | 1538.1219 | 74.7206 | 0 | 0 | 0 | 1111.5677 | 175.1079 | 134.7009 | 9.2514 | 174.2715 | 133.8645 | 8.4149 | 0 | 0 | 0 | 0.83642 | 924.1843 | 746.6441 | 145.8275 | 823.2087 | 645.6685 | 44.8519 | 0 | 0 | 0 | 100.9756 | 2193.2125 | 1768.3447 | 1031.2094 | 1183.4568 | 758.5889 | 21.4537 | 0 | 0 | 0 | 1009.7557 | 0.0025388 | 0.0016544 | 4.2e-05 | 0 | 0 | 0 | 0.0015598 | 5000000 | scaled
CB 1243 | 1438362.8614 | 1434753.7306 | 0 | 3609.1308 | 99.75% | 0% | 0.2509% | 583154.0586 | 1408790.3194 | 35560.7663 | 430.4796 | 547162.8126 | 86155.2112 | 1203.6195 | 1321431.4887 | 1243 |  | 1384 | CB 1243 | 1438362.8614 | 855208.8028 | 29572.542 | 1434753.7306 | 851599.672 | 25963.4111 | 0 | 0 | 0 | 3609.1308 | 87745.8649 | 52185.0986 | 1590.6537 | 87743.1492 | 52182.3828 | 1587.9379 | 0 | 0 | 0 | 2.7158 | 1346114.7704 | 798951.9578 | 24683.2817 | 1345786.9145 | 798624.1019 | 24355.4258 | 0 | 0 | 0 | 327.8559 | 4502.2261 | 4071.7464 | 3298.6066 | 1223.6669 | 793.1873 | 20.0474 | 0 | 0 | 0 | 3278.5592 | 0.014516 | 0.0085612 | 0.0002174 | 0 | 0 | 0 | 0.0050696 | 5000000 | scaled
CB 1245 | 108099.7267 | 107829.7759 | 0 | 269.9507 | 99.75% | 0% | 0.2497% | 33399.6277 | 103903.9515 | 4937.3527 | 6.299 | 28455.976 | 15112.1823 | 14.279 | 88777.4902 | 1245 |  | 1385 | CB 1245 | 108099.7267 | 74700.099 | 4195.7751 | 107829.7759 | 74430.1482 | 3925.8244 | 0 | 0 | 0 | 269.9507 | 15662.4431 | 10725.0903 | 550.2608 | 15662.2399 | 10724.8872 | 550.0576 | 0 | 0 | 0 | 0.20313 | 92177.5698 | 63721.5938 | 3400.0795 | 92153.0473 | 63697.0713 | 3375.557 | 0 | 0 | 0 | 24.5225 | 259.7138 | 253.4148 | 245.4348 | 14.4887 | 8.1897 | 0.20976 | 0 | 0 | 0 | 245.2251 | 0.0012474 | 0.0006898 | 1.74e-05 | 0 | 0 | 0 | 0.0003896 | 5000000 | scaled
CB 1250 | 4075235.8936 | 4072563.6693 | 1647.3021 | 1024.9222 | 99.93% | 0.04042% | 0.02515% | 1089299.7159 | 3986821.7055 | 56807.9624 | 12640.5113 | 1019851.2422 | 209136.6538 | 51713.2983 | 3725971.7534 | 1250 |  | 1386 | CB 1250 | 4075235.8936 | 2985936.1777 | 88414.1882 | 4072563.6693 | 2983987.6177 | 87246.3641 | 1647.3021 | 923.6378 | 142.9019 | 1024.9222 | 213756.8699 | 156948.9075 | 4620.2161 | 213753.1743 | 156946.4966 | 4619.1912 | 2.9244 | 1.6397 | 0.25369 | 0.77122 | 3807776.1564 | 2787924.9142 | 81804.4031 | 3807551.7053 | 2787758.1639 | 81699.9042 | 131.3465 | 73.6456 | 11.3942 | 93.1046 | 53702.8673 | 41062.356 | 1989.569 | 51258.7898 | 39282.9572 | 927.2686 | 1513.0312 | 848.3525 | 131.2541 | 931.0463 | 0.0084468 | 0.0064166 | 0.0001634 | 0.078795 | 0.044689 | 0.0078794 | 0.0014614 | 5000000 | scaled
CB 128 | 2822.1674 | 146.0504 | 0 | 2676.1169 | 5.175% | 0% | 94.82% | 76.4959 | 144.2989 | 8.4052 | 23.2825 | 44.8083 | 16.3303 | 41.0955 | 86.8731 | 128 |  | 1387 | CB 128 | 2822.1674 | 2745.6714 | 2677.8685 | 146.0504 | 69.5545 | 1.7516 | 0 | 0 | 0 | 2676.1169 | 18.545 | 10.1398 | 2.2147 | 16.5313 | 8.1261 | 0.201 | 0 | 0 | 0 | 2.0137 | 331.0572 | 286.2489 | 244.1841 | 87.9569 | 43.1486 | 1.0838 | 0 | 0 | 0 | 243.1003 | 2472.5652 | 2449.2828 | 2431.4697 | 41.5622 | 18.2798 | 0.46677 | 0 | 0 | 0 | 2431.003 | 0.0069108 | 0.0031426 | 7.98e-05 | 0 | 0 | 0 | 0.0037366 | 5000000 | scaled
CB 1283 | 4601.5198 | 4027.8142 | 0 | 573.7055 | 87.53% | 0% | 12.47% | 2458.4305 | 3958.8696 | 244.1551 | 95.4537 | 2118.8218 | 399.9161 | 220.4191 | 3338.5344 | 1283 |  | 1388 | CB 1283 | 4601.5198 | 2143.0892 | 642.6502 | 4027.8142 | 1569.3837 | 68.9447 | 0 | 0 | 0 | 573.7055 | 407.5069 | 163.3519 | 7.5909 | 407.0752 | 162.9202 | 7.1592 | 0 | 0 | 0 | 0.43169 | 3449.2628 | 1330.441 | 110.7284 | 3397.147 | 1278.3252 | 58.6126 | 0 | 0 | 0 | 52.1158 | 744.75 | 649.2963 | 524.331 | 223.592 | 128.1383 | 3.1729 | 0 | 0 | 0 | 521.158 | 0.0016324 | 0.0009236 | 2.4e-05 | 0 | 0 | 0 | 0.0007926 | 5000000 | scaled
CB 1286 | 2694.6955 | 1548.0016 | 0 | 1146.6938 | 57.45% | 0% | 42.55% | 854.8031 | 1533.8177 | 61.8147 | 450.3081 | 342.6803 | 101.5731 | 875.8686 | 556.3759 | 1286 |  | 1389 | CB 1286 | 2694.6955 | 1839.8923 | 1160.8778 | 1548.0016 | 693.1985 | 14.184 | 0 | 0 | 0 | 1146.6938 | 103.2037 | 41.3891 | 1.6306 | 102.3409 | 40.5262 | 0.76777 | 0 | 0 | 0 | 0.86285 | 664.5348 | 321.8545 | 108.1589 | 560.3684 | 217.6881 | 3.9924 | 0 | 0 | 0 | 104.1665 | 1926.9569 | 1476.6488 | 1051.0883 | 885.2924 | 434.9843 | 9.4238 | 0 | 0 | 0 | 1041.6645 | 0.0026846 | 0.0012588 | 3.24e-05 | 0 | 0 | 0 | 0.0016388 | 5000000 | scaled
CB 129 | 3182.1226 | 752.3356 | 0 | 2429.787 | 23.64% | 0% | 76.36% | 410.5543 | 739.7243 | 40.0946 | 157.4496 | 213.0101 | 67.8154 | 311.9207 | 359.9882 | 129 |  | 1390 | CB 129 | 3182.1226 | 2771.5683 | 2442.3983 | 752.3356 | 341.7813 | 12.6113 | 0 | 0 | 0 | 2429.787 | 70.8748 | 30.7802 | 3.0594 | 69.0465 | 28.9519 | 1.2311 | 0 | 0 | 0 | 1.8283 | 587.5996 | 374.5895 | 227.6114 | 366.8761 | 153.866 | 6.8879 | 0 | 0 | 0 | 220.7235 | 2523.6481 | 2366.1986 | 2211.7274 | 316.413 | 158.9634 | 4.4923 | 0 | 0 | 0 | 2207.2351 | 0.0056558 | 0.0025722 | 6.5e-05 | 0 | 0 | 0 | 0.0034552 | 5000000 | scaled
CB 1297 | 8400.9398 | 3347.9477 | 4734.0588 | 318.9332 | 39.85% | 56.35% | 3.796% | 3717.3541 | 7721.8513 | 2.1575 | 3487.4651 | 227.7315 | 4.5312 | 7239.0286 | 478.2915 | 1297 |  | 1391 | CB 1297 | 8400.9398 | 4683.5857 | 679.0885 | 3347.9477 | 1734.2873 | 44.3643 | 4734.0588 | 2630.3651 | 315.7909 | 318.9332 | 5.0951 | 2.9376 | 0.56385 | 0 | 0 | 0 | 4.8551 | 2.6976 | 0.32386 | 0.23999 | 541.449 | 313.7175 | 63.1575 | 0 | 0 | 0 | 512.4769 | 284.7454 | 34.1854 | 28.9721 | 7854.3957 | 4366.9306 | 615.3672 | 3347.9477 | 1734.2873 | 44.3643 | 4216.7269 | 2342.9222 | 281.2817 | 289.7211 | 0.0006544 | 0.000335 | 8.6e-06 | 0.005063 | 0.0028934 | 0.0005062 | 0.0004534 | 5000000 | scaled
CB 1299 | 41775.6269 | 39301.0331 | 0 | 2474.5938 | 94.08% | 0% | 5.924% | 13829.7536 | 38961.7454 | 1643.5121 | 140.196 | 12046.0455 | 4546.7543 | 542.0089 | 33872.9822 | 1299 |  | 1392 | CB 1299 | 41775.6269 | 27945.8733 | 2813.8815 | 39301.0331 | 25471.2795 | 339.2877 | 0 | 0 | 0 | 2474.5938 | 4592.3742 | 2948.862 | 45.6198 | 4590.5121 | 2947 | 43.7578 | 0 | 0 | 0 | 1.8621 | 34383.3776 | 22337.3321 | 510.3954 | 34158.5838 | 22112.5383 | 285.6016 | 0 | 0 | 0 | 224.7938 | 2799.8752 | 2659.6792 | 2257.8663 | 551.9372 | 411.7412 | 9.9283 | 0 | 0 | 0 | 2247.938 | 0.011521 | 0.0071988 | 0.0001832 | 0 | 0 | 0 | 0.0034764 | 5000000 | scaled
CB 130 | 14256.1662 | 12388.7003 | 0 | 1867.4659 | 86.9% | 0% | 13.1% | 5784.0882 | 12221.6576 | 4.0985 | 5757.2296 | 22.76 | 8.7544 | 12164.6335 | 48.2697 | 130 |  | 1393 | CB 130 | 14256.1662 | 8472.078 | 2034.5087 | 12388.7003 | 6604.6121 | 167.0427 | 0 | 0 | 0 | 1867.4659 | 10.225 | 6.1265 | 1.4706 | 8.8198 | 4.7213 | 0.065425 | 0 | 0 | 0 | 1.4052 | 218.2805 | 195.5205 | 170.0108 | 48.6386 | 25.8786 | 0.36889 | 0 | 0 | 0 | 169.6419 | 14027.6607 | 8270.4311 | 1863.0272 | 12331.2419 | 6574.0123 | 166.6084 | 0 | 0 | 0 | 1696.4188 | 0.0039392 | 0.0018776 | 4.74e-05 | 0 | 0 | 0 | 0.0026812 | 5000000 | scaled
CB 131 | 3958.5934 | 2587.7807 | 0 | 1370.8127 | 65.37% | 0% | 34.63% | 1398.6771 | 2560.6562 | 144.9426 | 446.2135 | 807.5211 | 262.0367 | 836.0158 | 1462.6037 | 131 |  | 1394 | CB 131 | 3958.5934 | 2559.9162 | 1397.9371 | 2587.7807 | 1189.1035 | 27.1244 | 0 | 0 | 0 | 1370.8127 | 265.6546 | 120.712 | 3.6179 | 264.6231 | 119.6805 | 2.5864 | 0 | 0 | 0 | 1.0315 | 1601.4426 | 793.9215 | 138.8389 | 1476.9171 | 669.3959 | 14.3133 | 0 | 0 | 0 | 124.5256 | 2091.4962 | 1645.2827 | 1255.4803 | 846.2405 | 400.0271 | 10.2247 | 0 | 0 | 0 | 1245.2556 | 0.0035178 | 0.0015856 | 4.08e-05 | 0 | 0 | 0 | 0.0019376 | 5000000 | scaled
CB 133 | 8718.3598 | 4339.9106 | 0 | 4378.4492 | 49.78% | 0% | 50.22% | 1627.8532 | 4271.9744 | 15.7488 | 1569.8291 | 42.2753 | 28.9038 | 4165.3122 | 77.7584 | 133 |  | 1395 | CB 133 | 8718.3598 | 7090.5066 | 4446.3854 | 4339.9106 | 2712.0574 | 67.9362 | 0 | 0 | 0 | 4378.4492 | 32.3972 | 16.6483 | 3.4934 | 29.1025 | 13.3537 | 0.19871 | 0 | 0 | 0 | 3.2946 | 476.0313 | 433.756 | 398.2729 | 78.29 | 36.0147 | 0.53157 | 0 | 0 | 0 | 397.7413 | 8209.9314 | 6640.1023 | 4044.6192 | 4232.5181 | 2662.689 | 67.2059 | 0 | 0 | 0 | 3977.4133 | 0.011054 | 0.0054042 | 0.0001362 | 0 | 0 | 0 | 0.0060702 | 5000000 | scaled
CB 135 | 563.1686 | 11.2416 | 0 | 551.9269 | 1.996% | 0% | 98% | 4.7365 | 11.0788 | 0 | 4.7365 | 0 | 0 | 11.0788 | 0 | 135 |  | 1396 | CB 135 | 563.1686 | 558.432 | 552.0898 | 11.2416 | 6.5051 | 0.16287 | 0 | 0 | 0 | 551.9269 | 0.41531 | 0.41531 | 0.41531 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41531 | 50.1374 | 50.1374 | 50.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1374 | 512.6158 | 507.8793 | 501.5371 | 11.2416 | 6.5051 | 0.16287 | 0 | 0 | 0 | 501.3742 | 0.0012492 | 0.000664 | 1.66e-05 | 0 | 0 | 0 | 0.0007814 | 5000000 | scaled
CB 136 | 14746.4878 | 11205.4209 | 0 | 3541.0669 | 75.99% | 0% | 24.01% | 5928.9678 | 11088.677 | 246.3806 | 4334.0396 | 1348.5476 | 471.3755 | 8019.1646 | 2598.1368 | 136 |  | 1397 | CB 136 | 14746.4878 | 8817.52 | 3657.8108 | 11205.4209 | 5276.4531 | 116.7439 | 0 | 0 | 0 | 3541.0669 | 479.3576 | 232.977 | 7.9821 | 476.693 | 230.3125 | 5.3175 | 0 | 0 | 0 | 2.6645 | 2948.4872 | 1599.9396 | 350.3503 | 2626.8142 | 1278.2667 | 28.6774 | 0 | 0 | 0 | 321.6729 | 11318.643 | 6984.6034 | 3299.4784 | 8101.9136 | 3767.874 | 82.749 | 0 | 0 | 0 | 3216.7294 | 0.0078198 | 0.0034716 | 8.78e-05 | 0 | 0 | 0 | 0.0049938 | 5000000 | scaled
CB 137 | 707.6134 | 158.6575 | 0 | 548.956 | 22.42% | 0% | 77.58% | 89.962 | 156.8629 | 0 | 89.962 | 0 | 0 | 156.8629 | 0 | 137 |  | 1398 | CB 137 | 707.6134 | 617.6514 | 550.7505 | 158.6575 | 68.6954 | 1.7945 | 0 | 0 | 0 | 548.956 | 0.41307 | 0.41307 | 0.41307 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41307 | 49.8675 | 49.8675 | 49.8675 | 0 | 0 | 0 | 0 | 0 | 0 | 49.8675 | 657.3328 | 567.3708 | 500.4699 | 158.6575 | 68.6954 | 1.7945 | 0 | 0 | 0 | 498.6753 | 0.0016992 | 0.0007358 | 1.88e-05 | 0 | 0 | 0 | 0.0007504 | 5000000 | scaled
CB 138 | 720.2045 | 305.8656 | 0 | 414.3388 | 42.47% | 0% | 57.53% | 172.5757 | 302.8004 | 0 | 172.5757 | 0 | 0 | 302.8004 | 0 | 138 |  | 1399 | CB 138 | 720.2045 | 547.6288 | 417.4041 | 305.8656 | 133.2899 | 3.0653 | 0 | 0 | 0 | 414.3388 | 0.31178 | 0.31178 | 0.31178 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31178 | 37.6388 | 37.6388 | 37.6388 | 0 | 0 | 0 | 0 | 0 | 0 | 37.6388 | 682.2539 | 509.6782 | 379.4535 | 305.8656 | 133.2899 | 3.0653 | 0 | 0 | 0 | 376.3882 | 0.0004544 | 0.0002368 | 5.8e-06 | 0 | 0 | 0 | 0.000588 | 5000000 | scaled
CB 140 | 74831.2879 | 12781.0461 | 59505.8621 | 2544.3797 | 17.08% | 79.52% | 3.4% | 32506.022 | 68137.8842 | 28.1551 | 30311.7821 | 2166.0848 | 58.8881 | 63548.4958 | 4530.5003 | 140 |  | 1400 | CB 140 | 74831.2879 | 42325.2659 | 6693.4036 | 12781.0461 | 6824.913 | 173.8975 | 59505.8621 | 32955.9732 | 3975.1264 | 2544.3797 | 65.0181 | 36.863 | 6.13 | 0 | 0 | 0 | 63.1035 | 34.9484 | 4.2155 | 1.9146 | 5085.946 | 2919.8613 | 555.4457 | 0 | 0 | 0 | 4854.8128 | 2688.7281 | 324.3125 | 231.1332 | 69680.3237 | 39368.5416 | 6131.8279 | 12781.0461 | 6824.913 | 173.8975 | 54587.9457 | 30232.2966 | 3646.5984 | 2311.332 | 0.0059528 | 0.002779 | 7.04e-05 | 0.0050148 | 0.0028572 | 0.0005014 | 0.003564 | 5000000 | scaled
CB 1406 | 717.8709 | 650.759 | 0 | 67.1119 | 90.65% | 0% | 9.349% | 369.3126 | 643.8945 | 0 | 369.3126 | 0 | 0 | 643.8945 | 0 | 1406 |  | 1401 | CB 1406 | 717.8709 | 348.5583 | 73.9764 | 650.759 | 281.4464 | 6.8645 | 0 | 0 | 0 | 67.1119 | 0.0505 | 0.0505 | 0.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0505 | 6.0965 | 6.0965 | 6.0965 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0965 | 711.7239 | 342.4113 | 67.8294 | 650.759 | 281.4464 | 6.8645 | 0 | 0 | 0 | 60.9649 | 9.48e-05 | 4.1e-05 | 1e-06 | 0 | 0 | 0 | 9.16e-05 | 5000000 | scaled
CB 141 | 7741.3029 | 7180.2874 | 53.6837 | 507.3317 | 92.75% | 0.6935% | 6.554% | 2717.6195 | 7139.1636 | 215.645 | 1056.4367 | 1445.5377 | 579.0781 | 2605.8048 | 3954.2807 | 141 |  | 1402 | CB 141 | 7741.3029 | 5023.6834 | 602.1393 | 7180.2874 | 4486.585 | 91.2255 | 53.6837 | 29.7666 | 3.582 | 507.3317 | 587.4443 | 371.7992 | 8.3662 | 586.3661 | 371.0313 | 7.938 | 0.69645 | 0.38617 | 0.04647 | 0.38175 | 4050.8579 | 2605.3202 | 96.5772 | 3993.8233 | 2553.1632 | 49.7603 | 10.9482 | 6.0706 | 0.73052 | 46.0864 | 3103.0007 | 2046.5639 | 497.1959 | 2600.0981 | 1562.3905 | 33.5273 | 42.039 | 23.3098 | 2.805 | 460.8636 | 0.001944 | 0.001149 | 2.92e-05 | 0.0050476 | 0.002879 | 0.0005048 | 0.0006936 | 5000000 | scaled
CB 1418 | 37453.8898 | 32967.1842 | 0 | 4486.7056 | 88.02% | 0% | 11.98% | 14129.8643 | 32578.7743 | 750.1958 | 9179.275 | 4200.3934 | 1531.6801 | 22594.9488 | 8452.1454 | 1418 |  | 1403 | CB 1418 | 37453.8898 | 23324.0255 | 4875.1155 | 32967.1842 | 18837.3199 | 388.4099 | 0 | 0 | 0 | 4486.7056 | 1548.2403 | 798.0444 | 16.5602 | 1544.8642 | 794.6683 | 13.1841 | 0 | 0 | 0 | 3.3761 | 8928.8427 | 4728.4493 | 476.6973 | 8521.2673 | 4320.8739 | 69.1219 | 0 | 0 | 0 | 407.5754 | 26976.8068 | 17797.5318 | 4381.858 | 22901.0527 | 13721.7777 | 306.1039 | 0 | 0 | 0 | 4075.7541 | 0.015596 | 0.0077004 | 0.0001962 | 0 | 0 | 0 | 0.0063058 | 5000000 | scaled
CB 142 | 108633.1926 | 61940.3161 | 39157.2236 | 7535.6529 | 57.02% | 36.05% | 6.937% | 38300.2505 | 97547.9768 | 1667.7568 | 29385.5513 | 7246.9424 | 4348.6293 | 75286.7012 | 17912.6463 | 142 |  | 1404 | CB 142 | 108633.1926 | 70332.9421 | 11085.2159 | 61940.3161 | 41146.879 | 938.6649 | 39157.2236 | 21650.4102 | 2610.8981 | 7535.6529 | 4420.9367 | 2753.1799 | 72.3075 | 4360.7147 | 2717.3474 | 62.9998 | 54.5517 | 30.1622 | 3.6374 | 5.6703 | 19023.5375 | 11776.5951 | 1110.8912 | 15108.8811 | 9306.0906 | 210.9721 | 3230.1125 | 1785.9607 | 215.3752 | 684.5439 | 85188.7184 | 55803.1671 | 9902.0172 | 42470.7203 | 29123.4411 | 664.693 | 35872.5593 | 19834.2873 | 2391.8855 | 6845.4387 | 0.023628 | 0.011468 | 0.0002918 | 0.0050142 | 0.0028524 | 0.0005014 | 0.010501 | 5000000 | scaled
CB 143 | 145603.874 | 79517.8783 | 64227.4792 | 1858.5165 | 54.61% | 44.11% | 1.276% | 60565.4204 | 138192.6523 | 2480.0927 | 48094.654 | 9990.6738 | 6471.6347 | 106992.7533 | 24728.2643 | 143 |  | 1405 | CB 143 | 145603.874 | 85038.4536 | 7411.2217 | 79517.8783 | 47752.0661 | 1266.9161 | 64227.4792 | 35427.871 | 4285.7891 | 1858.5165 | 6569.2897 | 4089.197 | 97.655 | 6483.0071 | 4040.9765 | 90.5923 | 84.884 | 46.822 | 5.6642 | 1.3985 | 25591.3703 | 15600.6965 | 863.106 | 19067.3075 | 11926.3212 | 270.2032 | 6355.2339 | 3505.5464 | 424.0738 | 168.8289 | 113443.2141 | 65348.5601 | 6450.4607 | 53967.5637 | 31784.7684 | 906.1205 | 57787.3612 | 31875.5026 | 3856.0511 | 1688.2891 | 0.00846 | 0.0047722 | 0.0001212 | 0.0049774 | 0.002825 | 0.0004978 | 0.002605 | 5000000 | scaled
CB 1434 | 5988.159 | 4428.4678 | 0 | 1559.6912 | 73.95% | 0% | 26.05% | 2476.9979 | 4379.9941 | 2.6644 | 2460.6307 | 13.7028 | 6.3885 | 4340.7392 | 32.8665 | 1434 |  | 1406 | CB 1434 | 5988.159 | 3511.1611 | 1608.1648 | 4428.4678 | 1951.4699 | 48.4736 | 0 | 0 | 0 | 1559.6912 | 7.5692 | 4.9048 | 1.1807 | 6.3956 | 3.7312 | 0.0070943 | 0 | 0 | 0 | 1.1736 | 174.5867 | 160.8839 | 141.7202 | 32.9033 | 19.2005 | 0.036799 | 0 | 0 | 0 | 141.6834 | 5806.0031 | 3345.3724 | 1465.2639 | 4389.1689 | 1928.5382 | 48.4298 | 0 | 0 | 0 | 1416.8342 | 0.0038506 | 0.0018114 | 4.56e-05 | 0 | 0 | 0 | 0.002154 | 5000000 | scaled
CB 1436 | 5422.7513 | 5039.1573 | 0 | 383.594 | 92.93% | 0% | 7.074% | 2852.597 | 4983.7168 | 12.5941 | 2773.885 | 66.1178 | 22.5932 | 4842.8552 | 118.2684 | 1436 |  | 1407 | CB 1436 | 5422.7513 | 2570.1544 | 439.0345 | 5039.1573 | 2186.5604 | 55.4405 | 0 | 0 | 0 | 383.594 | 23.2693 | 10.6752 | 0.67607 | 22.9806 | 10.3865 | 0.38743 | 0 | 0 | 0 | 0.28864 | 155.1466 | 89.0288 | 36.8782 | 120.3007 | 54.1829 | 2.0323 | 0 | 0 | 0 | 34.8459 | 5244.3354 | 2470.4504 | 401.4802 | 4895.876 | 2121.991 | 53.0208 | 0 | 0 | 0 | 348.4594 | 0.0012144 | 0.0005256 | 1.32e-05 | 0 | 0 | 0 | 0.0005374 | 5000000 | scaled
CB 1438 | 23516.5256 | 14541.2159 | 0 | 8975.3097 | 61.83% | 0% | 38.17% | 8079.7145 | 14459.5399 | 671.8484 | 4761.8895 | 2645.9765 | 1195.6207 | 8568.4983 | 4695.4209 | 1438 |  | 1408 | CB 1438 | 23516.5256 | 15436.8111 | 9056.9857 | 14541.2159 | 6461.5014 | 81.6759 | 0 | 0 | 0 | 8975.3097 | 1204.2354 | 532.387 | 8.6147 | 1197.4818 | 525.6334 | 1.8611 | 0 | 0 | 0 | 6.7536 | 5517.4389 | 2871.4623 | 822.0179 | 4702.1156 | 2056.1391 | 6.6947 | 0 | 0 | 0 | 815.3233 | 16794.8513 | 12032.9618 | 8226.353 | 8641.6185 | 3879.729 | 73.1202 | 0 | 0 | 0 | 8153.2328 | 0.029643 | 0.013269 | 0.0003368 | 0 | 0 | 0 | 0.012586 | 5000000 | scaled
CB 144 | 116349.2706 | 82256.9702 | 30780.9895 | 3311.3109 | 70.7% | 26.46% | 2.846% | 35113.0983 | 109724.0959 | 714.316 | 29337.2727 | 5061.5096 | 2586.6703 | 90640.5748 | 16496.8508 | 144 |  | 1409 | CB 144 | 116349.2706 | 81236.1723 | 6625.1747 | 82256.9702 | 60898.4177 | 1260.8116 | 30780.9895 | 17026.4437 | 2053.0522 | 3311.3109 | 2621.0523 | 1906.7363 | 34.3821 | 2556.1718 | 1869.7344 | 27.7292 | 62.3889 | 34.5103 | 4.1613 | 2.4917 | 17141.9777 | 12080.4681 | 645.1269 | 13862.6184 | 10132.0831 | 145.6592 | 2978.5576 | 1647.5832 | 198.6659 | 300.8018 | 96586.2406 | 67248.9679 | 5945.6658 | 65838.18 | 48896.6002 | 1087.4233 | 27740.0431 | 15344.3502 | 1850.225 | 3008.0175 | 0.011567 | 0.0076224 | 0.0001932 | 0.0049936 | 0.0028418 | 0.0004994 | 0.0046968 | 5000000 | scaled
CB 1446 | 1778.2382 | 1415.9183 | 0 | 362.3199 | 79.62% | 0% | 20.38% | 362.3939 | 1410.1211 | 45.0028 | 33.6172 | 283.774 | 160.1339 | 81.0966 | 1168.8906 | 1446 |  | 1410 | CB 1446 | 1778.2382 | 1415.8442 | 368.1171 | 1415.9183 | 1053.5243 | 5.7972 | 0 | 0 | 0 | 362.3199 | 161.1223 | 116.1195 | 0.98839 | 160.8497 | 115.8469 | 0.71576 | 0 | 0 | 0 | 0.27263 | 1205.8092 | 922.0352 | 36.9186 | 1172.8958 | 889.1218 | 4.0052 | 0 | 0 | 0 | 32.9134 | 411.3067 | 377.6895 | 330.2101 | 82.1728 | 48.5556 | 1.0762 | 0 | 0 | 0 | 329.1339 | 0.0010696 | 0.000689 | 1.74e-05 | 0 | 0 | 0 | 0.000496 | 5000000 | scaled
CB 1448 | 4201.159 | 3729.5698 | 0 | 471.5892 | 88.77% | 0% | 11.23% | 1964.0932 | 3658.214 | 153.3402 | 809.1587 | 1001.5942 | 258.8098 | 1795.8657 | 1603.5385 | 1448 |  | 1411 | CB 1448 | 4201.159 | 2237.0659 | 542.945 | 3729.5698 | 1765.4767 | 71.3558 | 0 | 0 | 0 | 471.5892 | 264.7964 | 111.4562 | 5.9866 | 264.4416 | 111.1014 | 5.6318 | 0 | 0 | 0 | 0.35486 | 1682.0078 | 680.4135 | 78.4692 | 1639.1683 | 637.574 | 35.6298 | 0 | 0 | 0 | 42.8395 | 2254.3548 | 1445.1961 | 458.4892 | 1825.9599 | 1016.8013 | 30.0943 | 0 | 0 | 0 | 428.3949 | 0.0015846 | 0.0008524 | 2.16e-05 | 0 | 0 | 0 | 0.0006764 | 5000000 | scaled
CB 145 | 50157.9138 | 32328.3845 | 16798.5507 | 1030.9786 | 64.45% | 33.49% | 2.055% | 22808.9275 | 47826.3131 | 806.7645 | 18156.017 | 3846.146 | 1858.8357 | 37197.2359 | 8770.2415 | 145 |  | 1412 | CB 145 | 50157.9138 | 27348.9863 | 2331.6007 | 32328.3845 | 17031.7578 | 179.4199 | 16798.5507 | 9286.2499 | 1121.2022 | 1030.9786 | 1862.7963 | 1056.0318 | 3.9606 | 1814.3037 | 1028.8781 | 0 | 47.7168 | 26.3779 | 3.1848 | 0.77578 | 9036.6939 | 5190.548 | 266.4524 | 6354.0779 | 3665.7137 | 0 | 2588.9612 | 1431.1795 | 172.7976 | 93.6548 | 39258.4236 | 21102.4066 | 2061.1877 | 24160.0029 | 12337.166 | 179.4199 | 14161.8727 | 7828.6926 | 945.2198 | 936.548 | 0.00317 | 0.001518 | 3.84e-05 | 0.0050012 | 0.0028444 | 0.0005002 | 0.0014574 | 5000000 | scaled
CB 146 | 2774.8171 | 2569.5917 | 53.0775 | 152.1479 | 92.6% | 1.913% | 5.483% | 1419.6086 | 2608.0938 | 66.6768 | 1084.689 | 268.2428 | 129.389 | 1952.0359 | 526.6689 | 146 |  | 1413 | CB 146 | 2774.8171 | 1355.2085 | 166.7233 | 2569.5917 | 1173.7271 | 11.0358 | 53.0775 | 29.3334 | 3.5395 | 152.1479 | 129.5494 | 62.8725 | 0.1604 | 128.7463 | 62.3775 | 0 | 0.68859 | 0.38055 | 0.045919 | 0.11449 | 541.212 | 272.9692 | 14.5431 | 516.5662 | 253.1657 | 0 | 10.8246 | 5.9822 | 0.72184 | 13.8212 | 2104.0557 | 1019.3667 | 152.0198 | 1924.2792 | 858.1839 | 11.0358 | 41.5643 | 22.9706 | 2.7717 | 138.2122 | 0.0002078 | 8.98e-05 | 2.2e-06 | 0.0049906 | 0.0028378 | 0.000499 | 0.0002092 | 5000000 | scaled
CB 147 | 56225.7692 | 7470.4175 | 48193.0685 | 562.2831 | 13.29% | 85.71% | 1% | 25548.9767 | 52315.3581 | 232.6481 | 22331.9718 | 2984.3569 | 429.4966 | 45952.5586 | 5933.303 | 147 |  | 1414 | CB 147 | 56225.7692 | 30676.7925 | 3910.4111 | 7470.4175 | 3404.9262 | 134.6089 | 48193.0685 | 26709.5832 | 3213.519 | 562.2831 | 444.6655 | 212.0174 | 15.1689 | 387.9193 | 180.3789 | 10.9902 | 56.3231 | 31.2154 | 3.7556 | 0.4231 | 6320.5512 | 3336.1943 | 387.2482 | 2292.5103 | 1081.0021 | 70.9857 | 3976.9627 | 2204.114 | 265.1843 | 51.0782 | 49460.5525 | 27128.5808 | 3507.994 | 4789.988 | 2143.5451 | 52.6331 | 44159.7827 | 24474.2538 | 2944.5791 | 510.7818 | 0.0014628 | 0.0006332 | 1.62e-05 | 0.00496 | 0.0028278 | 0.000496 | 0.0007728 | 5000000 | scaled
CB 1479 | 5382.7979 | 1145.7365 | 0 | 4237.0614 | 21.29% | 0% | 78.71% | 648.202 | 1133.1579 | 0.68381 | 643.9963 | 3.5219 | 1.5355 | 1123.7213 | 7.901 | 1479 |  | 1415 | CB 1479 | 5382.7979 | 4734.5958 | 4249.64 | 1145.7365 | 497.5345 | 12.5786 | 0 | 0 | 0 | 4237.0614 | 4.7238 | 4.04 | 3.1883 | 1.5355 | 0.85171 | 0 | 0 | 0 | 0 | 3.1883 | 392.7986 | 389.2767 | 384.8976 | 7.901 | 4.3791 | 0 | 0 | 0 | 0 | 384.8976 | 4985.2755 | 4341.2792 | 3861.5542 | 1136.3 | 492.3037 | 12.5786 | 0 | 0 | 0 | 3848.9755 | 0.010816 | 0.00488 | 0.0001242 | 0 | 0 | 0 | 0.0059932 | 5000000 | scaled
CB 1482 | 352.3822 | 287.8472 | 0 | 64.535 | 81.69% | 0% | 18.31% | 162.9576 | 284.5087 | 0 | 162.9576 | 0 | 0 | 284.5087 | 0 | 1482 |  | 1416 | CB 1482 | 352.3822 | 189.4246 | 67.8734 | 287.8472 | 124.8896 | 3.3384 | 0 | 0 | 0 | 64.535 | 0.048561 | 0.048561 | 0.048561 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048561 | 5.8624 | 5.8624 | 5.8624 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8624 | 346.4712 | 183.5136 | 61.9625 | 287.8472 | 124.8896 | 3.3384 | 0 | 0 | 0 | 58.624 | 8.62e-05 | 3.74e-05 | 1e-06 | 0 | 0 | 0 | 9.34e-05 | 5000000 | scaled
CB 149 | 21250.0187 | 20712.3529 | 0 | 537.6658 | 97.47% | 0% | 2.53% | 5106.6623 | 20164.5721 | 627.9758 | 0.22767 | 4478.4588 | 2532.0276 | 0.61748 | 17631.927 | 149 |  | 1417 | CB 149 | 21250.0187 | 16143.3563 | 1085.4466 | 20712.3529 | 15605.6905 | 547.7808 | 0 | 0 | 0 | 537.6658 | 2603.6078 | 1975.632 | 71.5803 | 2603.2033 | 1975.2274 | 71.1757 | 0 | 0 | 0 | 0.40458 | 18157.3642 | 13678.9054 | 525.4372 | 18108.5223 | 13630.0634 | 476.5953 | 0 | 0 | 0 | 48.8419 | 489.0466 | 488.8189 | 488.4291 | 0.62734 | 0.39967 | 0.0098552 | 0 | 0 | 0 | 488.4193 | 0.0028586 | 0.0021396 | 5.46e-05 | 0 | 0 | 0 | 0.0007546 | 5000000 | scaled
CB 151 | 3608.8012 | 1353.6894 | 0 | 2255.1118 | 37.51% | 0% | 62.49% | 587.0156 | 1251.2357 | 50.7437 | 227.3835 | 308.8884 | 113.9936 | 414.8953 | 722.3469 | 151 |  | 1418 | CB 151 | 3608.8012 | 3021.7856 | 2357.5655 | 1353.6894 | 766.6738 | 102.4537 | 0 | 0 | 0 | 2255.1118 | 124.8505 | 74.1069 | 10.8569 | 123.1536 | 72.41 | 9.16 | 0 | 0 | 0 | 1.6969 | 1015.7637 | 706.8753 | 293.4168 | 810.9078 | 502.0194 | 88.5609 | 0 | 0 | 0 | 204.8559 | 2468.187 | 2240.8035 | 2053.2917 | 419.628 | 192.2445 | 4.7327 | 0 | 0 | 0 | 2048.559 | 0.0054368 | 0.0023994 | 6.18e-05 | 0 | 0 | 0 | 0.0031846 | 5000000 | scaled
CB 1525 | 259690.3062 | 92170.6478 | 163916.871 | 3602.7874 | 35.49% | 63.12% | 1.387% | 117434.6972 | 242966.417 | 5432.1762 | 70859.3493 | 41143.1717 | 11096.1145 | 145662.5783 | 86207.7243 | 1525 |  | 1419 | CB 1525 | 259690.3062 | 142255.609 | 16723.8892 | 92170.6478 | 47979.9941 | 860.131 | 163916.871 | 90672.8275 | 12260.9708 | 3602.7874 | 11230.7907 | 5798.6145 | 134.6762 | 10949.2415 | 5641.6604 | 111.1082 | 278.8382 | 154.2431 | 20.8571 | 2.711 | 88237.1091 | 47093.9374 | 2029.3848 | 74202.2299 | 39184.1142 | 676.7776 | 13707.5995 | 7582.5435 | 1025.3275 | 327.2797 | 160222.4064 | 89363.0571 | 14559.8281 | 7019.1764 | 3154.2194 | 72.2452 | 149930.4333 | 82936.0409 | 11214.7862 | 3272.7968 | 0.015611 | 0.0074746 | 0.00019 | 0.029814 | 0.016863 | 0.0029814 | 0.0050872 | 5000000 | scaled
CB 153 | 50615.9463 | 40693.3398 | 0 | 9922.6065 | 80.4% | 0% | 19.6% | 21192.9597 | 40197.7308 | 42.0313 | 21026.4452 | 124.4832 | 79.5342 | 39882.6749 | 235.5217 | 153 |  | 1420 | CB 153 | 50615.9463 | 29422.9867 | 10418.2155 | 40693.3398 | 19500.3802 | 495.609 | 0 | 0 | 0 | 9922.6065 | 88.5453 | 46.514 | 9.0111 | 81.0788 | 39.0475 | 1.5446 | 0 | 0 | 0 | 7.4664 | 1141.4664 | 1016.9832 | 905.9446 | 240.09 | 115.6068 | 4.5683 | 0 | 0 | 0 | 901.3764 | 49385.9347 | 28359.4895 | 9503.2598 | 40372.171 | 19345.7258 | 489.4961 | 0 | 0 | 0 | 9013.7637 | 0.027855 | 0.012447 | 0.000317 | 0 | 0 | 0 | 0.014005 | 5000000 | scaled
CB 154 | 34128.8417 | 28824.0192 | 0 | 5304.8224 | 84.46% | 0% | 15.54% | 15667.8058 | 28485.1438 | 0 | 15667.8058 | 0 | 0 | 28485.1438 | 0 | 154 |  | 1421 | CB 154 | 34128.8417 | 18461.0359 | 5643.6978 | 28824.0192 | 13156.2134 | 338.8754 | 0 | 0 | 0 | 5304.8224 | 3.9917 | 3.9917 | 3.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9917 | 481.8937 | 481.8937 | 481.8937 | 0 | 0 | 0 | 0 | 0 | 0 | 481.8937 | 33642.9563 | 17975.1505 | 5157.8124 | 28824.0192 | 13156.2134 | 338.8754 | 0 | 0 | 0 | 4818.937 | 0.016623 | 0.0072776 | 0.0001848 | 0 | 0 | 0 | 0.0074642 | 5000000 | scaled
CB 155 | 44496.3062 | 42017.2654 | 0 | 2479.0409 | 94.43% | 0% | 5.571% | 22182.977 | 41370.0004 | 141.6652 | 21315.1073 | 726.2045 | 237.9791 | 39912.3187 | 1219.7026 | 155 |  | 1422 | CB 155 | 44496.3062 | 22313.3293 | 3126.3059 | 42017.2654 | 19834.2884 | 647.265 | 0 | 0 | 0 | 2479.0409 | 248.5361 | 106.8708 | 10.557 | 246.6707 | 105.0054 | 8.6916 | 0 | 0 | 0 | 1.8654 | 1489.6126 | 763.4082 | 269.91 | 1264.4149 | 538.2104 | 44.7123 | 0 | 0 | 0 | 225.1978 | 42758.1575 | 21443.0503 | 2845.8388 | 40506.1799 | 19191.0726 | 593.8612 | 0 | 0 | 0 | 2251.9777 | 0.0099568 | 0.0046354 | 0.0001368 | 0 | 0 | 0 | 0.0034946 | 5000000 | scaled
CB 156 | 34440.578 | 31833.7746 | 0 | 2606.8034 | 92.43% | 0% | 7.569% | 19817.5733 | 31442.2419 | 2830.0009 | 9738.9839 | 7248.5885 | 4277.6069 | 16336.3471 | 10828.2878 | 156 |  | 1423 | CB 156 | 34440.578 | 14623.0047 | 2998.3361 | 31833.7746 | 12016.2013 | 391.5327 | 0 | 0 | 0 | 2606.8034 | 4334.2034 | 1504.2025 | 56.5964 | 4332.2418 | 1502.2409 | 54.6349 | 0 | 0 | 0 | 1.9615 | 11206.1655 | 3957.577 | 377.8777 | 10969.3617 | 3720.7732 | 141.0739 | 0 | 0 | 0 | 236.8038 | 18900.2091 | 9161.2252 | 2563.862 | 16532.1711 | 6793.1872 | 195.8239 | 0 | 0 | 0 | 2368.0381 | 0.0086866 | 0.0037618 | 9.56e-05 | 0 | 0 | 0 | 0.0037148 | 5000000 | scaled
CB 157 | 6077.4581 | 6042.9545 | 0 | 34.5036 | 99.43% | 0% | 0.5677% | 4362.4433 | 6041.2203 | 265.4462 | 148.9392 | 3948.058 | 366.7043 | 299.4075 | 5375.1085 | 157 |  | 1424 | CB 157 | 6077.4581 | 1715.0148 | 36.2378 | 6042.9545 | 1680.5112 | 1.7342 | 0 | 0 | 0 | 34.5036 | 366.7302 | 101.2841 | 0.025963 | 366.7043 | 101.2581 | 0 | 0 | 0 | 0 | 0.025963 | 5378.2429 | 1430.1849 | 3.1343 | 5375.1085 | 1427.0506 | 0 | 0 | 0 | 0 | 3.1343 | 332.485 | 183.5458 | 33.0775 | 301.1417 | 152.2025 | 1.7342 | 0 | 0 | 0 | 31.3433 | 8.2e-05 | 3.56e-05 | 1e-06 | 0 | 0 | 0 | 5.14e-05 | 5000000 | scaled
CB 158 | 4505.8 | 1544.5846 | 0 | 2961.2155 | 34.28% | 0% | 65.72% | 881.2482 | 1528.4162 | 5.8704 | 845.0825 | 30.2953 | 9.645 | 1469.0646 | 49.7066 | 158 |  | 1425 | CB 158 | 4505.8 | 3624.5518 | 2977.3839 | 1544.5846 | 663.3364 | 16.1684 | 0 | 0 | 0 | 2961.2155 | 11.8732 | 6.0028 | 2.2282 | 9.645 | 3.7746 | 0 | 0 | 0 | 0 | 2.2282 | 318.7054 | 288.4101 | 268.9988 | 49.7066 | 19.4113 | 0 | 0 | 0 | 0 | 268.9988 | 4175.2214 | 3330.1389 | 2706.1568 | 1485.233 | 640.1505 | 16.1684 | 0 | 0 | 0 | 2689.9884 | 0.008147 | 0.0035278 | 8.94e-05 | 0 | 0 | 0 | 0.0041324 | 5000000 | scaled
CB 159 | 13602.7132 | 13039.7822 | 0 | 562.931 | 95.86% | 0% | 4.138% | 7397.4803 | 12896.5155 | 0.53798 | 7394.2025 | 2.7399 | 0.63257 | 12892.6604 | 3.2225 | 159 |  | 1426 | CB 159 | 13602.7132 | 6205.2328 | 706.1977 | 13039.7822 | 5642.3019 | 143.2667 | 0 | 0 | 0 | 562.931 | 1.0562 | 0.51818 | 0.42359 | 0.63257 | 0.094591 | 0 | 0 | 0 | 0 | 0.42359 | 54.3596 | 51.6197 | 51.137 | 3.2225 | 0.48268 | 0 | 0 | 0 | 0 | 51.137 | 13547.2974 | 6153.095 | 654.6371 | 13035.9271 | 5641.7246 | 143.2667 | 0 | 0 | 0 | 511.3703 | 0.0018688 | 0.000809 | 2.06e-05 | 0 | 0 | 0 | 0.0007832 | 5000000 | scaled
CB 160 | 31549.8952 | 29117.4956 | 0 | 2432.3996 | 92.29% | 0% | 7.71% | 16003.9456 | 28785.5813 | 2.2044 | 15990.3658 | 11.3754 | 4.1604 | 28759.96 | 21.4609 | 160 |  | 1427 | CB 160 | 31549.8952 | 15545.9497 | 2764.3139 | 29117.4956 | 13113.55 | 331.9142 | 0 | 0 | 0 | 2432.3996 | 5.9978 | 3.7935 | 1.8374 | 4.1675 | 1.9631 | 0.0070943 | 0 | 0 | 0 | 1.8303 | 242.4587 | 231.0834 | 220.9978 | 21.4979 | 10.1225 | 0.03694 | 0 | 0 | 0 | 220.9608 | 31301.4387 | 15311.0729 | 2541.4787 | 29091.8302 | 13101.4644 | 331.8702 | 0 | 0 | 0 | 2209.6085 | 0.0068296 | 0.0030412 | 7.76e-05 | 0 | 0 | 0 | 0.0034204 | 5000000 | scaled
CB 161 | 13272.8247 | 12607.9591 | 0 | 664.8655 | 94.99% | 0% | 5.009% | 6823.5361 | 12461.2871 | 4.6968 | 6794.5095 | 24.3298 | 8.5045 | 12408.7426 | 44.04 | 161 |  | 1428 | CB 161 | 13272.8247 | 6449.2886 | 811.5376 | 12607.9591 | 5784.4231 | 146.6721 | 0 | 0 | 0 | 664.8655 | 9.0927 | 4.3958 | 0.58818 | 8.5924 | 3.8956 | 0.08789 | 0 | 0 | 0 | 0.50029 | 104.8967 | 80.5669 | 60.8567 | 44.4998 | 20.17 | 0.45982 | 0 | 0 | 0 | 60.3968 | 13158.8353 | 6364.3259 | 750.0927 | 12554.8669 | 5760.3575 | 146.1243 | 0 | 0 | 0 | 603.9684 | 0.001959 | 0.0008988 | 2.28e-05 | 0 | 0 | 0 | 0.000932 | 5000000 | scaled
CB 162 | 8443.2809 | 7089.2291 | 0 | 1354.0518 | 83.96% | 0% | 16.04% | 3543.9732 | 7001.5968 | 3.6701 | 3521.3907 | 18.9124 | 6.7987 | 6959.782 | 35.0162 | 162 |  | 1429 | CB 162 | 8443.2809 | 4899.3077 | 1441.684 | 7089.2291 | 3545.2559 | 87.6322 | 0 | 0 | 0 | 1354.0518 | 7.8527 | 4.1825 | 1.054 | 6.8338 | 3.1637 | 0.035077 | 0 | 0 | 0 | 1.0189 | 158.2065 | 139.2941 | 123.1903 | 35.2035 | 16.2911 | 0.18735 | 0 | 0 | 0 | 123.003 | 8277.2217 | 4755.831 | 1317.4397 | 7047.1918 | 3525.8011 | 87.4098 | 0 | 0 | 0 | 1230.0299 | 0.0028932 | 0.0014044 | 3.48e-05 | 0 | 0 | 0 | 0.0018636 | 5000000 | scaled
CB 163 | 56872.3751 | 50429.155 | 0 | 6443.2201 | 88.67% | 0% | 11.33% | 25755.6465 | 49796.6673 | 180.4208 | 24650.9907 | 924.235 | 359.4119 | 47596.1714 | 1841.084 | 163 |  | 1430 | CB 163 | 56872.3751 | 31116.7286 | 7075.7078 | 50429.155 | 24673.5085 | 632.4877 | 0 | 0 | 0 | 6443.2201 | 369.4097 | 188.9889 | 9.9978 | 364.5614 | 184.1406 | 5.1494 | 0 | 0 | 0 | 4.8483 | 2452.7377 | 1528.5027 | 611.6537 | 1867.4311 | 943.1961 | 26.3472 | 0 | 0 | 0 | 585.3065 | 54050.2277 | 29399.237 | 6454.0563 | 48197.1625 | 23546.1718 | 600.9911 | 0 | 0 | 0 | 5853.0652 | 0.029172 | 0.012967 | 0.0003298 | 0 | 0 | 0 | 0.009103 | 5000000 | scaled
CB 164 | 5356.2394 | 4257.8089 | 0 | 1098.4305 | 79.49% | 0% | 20.51% | 2293.491 | 4210.2179 | 13.9752 | 2207.0409 | 72.4749 | 23.5335 | 4064.4216 | 122.2629 | 164 |  | 1431 | CB 164 | 5356.2394 | 3062.7484 | 1146.0215 | 4257.8089 | 1964.3179 | 47.591 | 0 | 0 | 0 | 1098.4305 | 24.36 | 10.3848 | 0.82653 | 23.5335 | 9.5583 | 0 | 0 | 0 | 0 | 0.82653 | 222.045 | 149.5701 | 99.7822 | 122.2629 | 49.7879 | 0 | 0 | 0 | 0 | 99.7822 | 5109.8344 | 2902.7935 | 1045.4128 | 4112.0126 | 1904.9717 | 47.591 | 0 | 0 | 0 | 997.8218 | 0.003173 | 0.0014628 | 3.72e-05 | 0 | 0 | 0 | 0.0015674 | 5000000 | scaled
CB 166 | 21656.615 | 17851.3809 | 0 | 3805.2341 | 82.43% | 0% | 17.57% | 10123.0062 | 17654.2094 | 5.7216 | 10087.8687 | 29.416 | 9.6163 | 17595.1695 | 49.4235 | 166 |  | 1432 | CB 166 | 21656.615 | 11533.6088 | 4002.4056 | 17851.3809 | 7728.3746 | 197.1715 | 0 | 0 | 0 | 3805.2341 | 12.4796 | 6.7581 | 2.8633 | 9.6163 | 3.8948 | 0 | 0 | 0 | 0 | 2.8633 | 395.0936 | 365.6776 | 345.6701 | 49.4235 | 20.0076 | 0 | 0 | 0 | 0 | 345.6701 | 21249.0418 | 11161.1731 | 3653.8722 | 17792.341 | 7704.4723 | 197.1715 | 0 | 0 | 0 | 3456.7008 | 0.0097508 | 0.0042224 | 0.0001078 | 0 | 0 | 0 | 0.0053616 | 5000000 | scaled
CB 168 | 32748.5843 | 27172.0315 | 0 | 5576.5528 | 82.97% | 0% | 17.03% | 14593.5383 | 26818.9528 | 104.9461 | 13951.7278 | 536.8644 | 177.2826 | 25734.8544 | 906.8158 | 168 |  | 1433 | CB 168 | 32748.5843 | 18155.046 | 5929.6315 | 27172.0315 | 12578.4932 | 353.0788 | 0 | 0 | 0 | 5576.5528 | 186.6962 | 81.7501 | 9.4136 | 182.5 | 77.5539 | 5.2174 | 0 | 0 | 0 | 4.1962 | 1440.135 | 903.2706 | 533.3192 | 933.5571 | 396.6927 | 26.7413 | 0 | 0 | 0 | 506.5779 | 31121.7532 | 17170.0253 | 5386.8987 | 26055.9744 | 12104.2466 | 321.12 | 0 | 0 | 0 | 5065.7787 | 0.01622 | 0.0071422 | 0.0001818 | 0 | 0 | 0 | 0.007772 | 5000000 | scaled
CB 169 | 473.3045 | 177.92 | 0 | 295.3845 | 37.59% | 0% | 62.41% | 97.8292 | 171.3853 | 5.3288 | 65.1418 | 27.3586 | 9.3544 | 114.1984 | 47.8324 | 169 |  | 1434 | CB 169 | 473.3045 | 375.4752 | 301.9192 | 177.92 | 80.0907 | 6.5347 | 0 | 0 | 0 | 295.3845 | 10.371 | 5.0423 | 1.0166 | 10.1488 | 4.82 | 0.79434 | 0 | 0 | 0 | 0.22227 | 78.9838 | 51.6251 | 31.1514 | 52.1508 | 24.7922 | 4.3184 | 0 | 0 | 0 | 26.8329 | 383.9497 | 318.8078 | 269.7512 | 115.6204 | 50.4785 | 1.4219 | 0 | 0 | 0 | 268.3293 | 0.0003354 | 0.0001452 | 3.8e-06 | 0 | 0 | 0 | 0.0004082 | 5000000 | scaled
CB 171 | 113919.2177 | 38508.568 | 73239.22 | 2171.4297 | 33.8% | 64.29% | 1.906% | 49579.6666 | 105837.0461 | 961.1597 | 40526.3329 | 8092.174 | 2044.0659 | 86884.0666 | 16908.9136 | 171 |  | 1435 | CB 171 | 113919.2177 | 64339.5511 | 8082.1716 | 38508.568 | 21555.5763 | 660.4452 | 73239.22 | 40612.5451 | 5250.2967 | 2171.4297 | 2093.7322 | 1132.5726 | 49.6663 | 1999.6812 | 1079.6916 | 41.4073 | 92.4171 | 51.2471 | 6.6251 | 1.6339 | 17787.8145 | 9695.6405 | 878.9009 | 11385.3654 | 6057.4873 | 236.8153 | 6205.1949 | 3440.899 | 444.8315 | 197.2542 | 94037.6709 | 53511.338 | 7153.6043 | 25123.5214 | 14418.3974 | 382.2226 | 66941.6079 | 37120.399 | 4798.8401 | 1972.5416 | 0.012629 | 0.0070182 | 0.0001782 | 0.024408 | 0.013868 | 0.0024408 | 0.0030206 | 5000000 | scaled
CB 172 | 28309.7511 | 19944.7392 | 5320.4521 | 3044.5597 | 70.45% | 18.79% | 10.75% | 13482.4598 | 24676.4559 | 686.6407 | 8470.1716 | 4325.6476 | 1165.4133 | 16055.9418 | 7455.1008 | 172 |  | 1436 | CB 172 | 28309.7511 | 14827.2913 | 3633.2953 | 19944.7392 | 8833.5383 | 207.2801 | 5320.4521 | 2949.1933 | 381.4554 | 3044.5597 | 1178.9491 | 492.3084 | 13.5359 | 1160.4656 | 481.0418 | 10.084 | 16.1926 | 8.9757 | 1.1609 | 2.2909 | 7855.3256 | 3529.6781 | 400.2248 | 6639.645 | 2732.5473 | 56.3244 | 939.1108 | 520.5609 | 67.3305 | 276.5699 | 19275.4764 | 10805.3048 | 3219.5346 | 12144.6286 | 5619.9492 | 140.8718 | 4365.1488 | 2419.6567 | 312.9639 | 2765.6989 | 0.019483 | 0.0086898 | 0.000221 | 0.024501 | 0.01392 | 0.0024502 | 0.0042764 | 5000000 | scaled
CB 175 | 1236507.4611 | 1040412.879 | 193584.9974 | 2509.5847 | 84.14% | 15.66% | 0.203% | 514966.1898 | 1191010.9155 | 34275.2603 | 96749.203 | 383941.7265 | 80554.9852 | 206421.5452 | 904034.3852 | 175 |  | 1437 | CB 175 | 1236507.4611 | 721541.2713 | 45496.5456 | 1040412.879 | 609649.9183 | 24978.3731 | 193584.9974 | 109381.7683 | 18008.5878 | 2509.5847 | 82501.1909 | 48225.9306 | 1946.2057 | 82175.7595 | 48041.23 | 1914.2192 | 323.543 | 182.8122 | 30.0982 | 1.8884 | 928297.9326 | 544356.2061 | 24263.5474 | 910994.8453 | 534480.2429 | 22447.1322 | 17075.1149 | 9647.9907 | 1588.4429 | 227.9724 | 225708.3376 | 128959.1347 | 19286.7925 | 47242.2742 | 27128.4454 | 617.0217 | 176186.3395 | 99550.9654 | 16390.0468 | 2279.7239 | 0.0075652 | 0.004353 | 0.000111 | 0.15618 | 0.088764 | 0.015618 | 0.0034916 | 5000000 | scaled
CB 176 | 15554.4177 | 720.3462 | 14757.9596 | 76.1119 | 4.631% | 94.88% | 0.4893% | 2268.2934 | 4269.2969 | 36.5857 | 1785.1617 | 446.546 | 43.766 | 3593.2361 | 632.2948 | 176 |  | 1438 | CB 176 | 15554.4177 | 13286.1244 | 11285.1208 | 720.3462 | 168.4449 | 2.3449 | 14757.9596 | 13041.5676 | 11206.6639 | 76.1119 | 54.6907 | 18.105 | 10.9248 | 40.3222 | 5.4009 | 0 | 14.3113 | 12.6469 | 10.8675 | 0.057272 | 1590.9075 | 1144.3616 | 958.6127 | 330.7097 | 29.9242 | 0 | 1253.2838 | 1107.5234 | 951.6986 | 6.9141 | 13908.8195 | 12123.6578 | 10315.5833 | 349.3143 | 133.1199 | 2.3449 | 13490.3645 | 11921.3973 | 10244.0978 | 69.1406 | 0.0001398 | 0.0001282 | 3.4e-06 | 0.032346 | 0.032346 | 0.032346 | 9.9e-05 | 5000000 | scaled
CB 178 | 644514.0314 | 642158.1693 | 0 | 2355.8621 | 99.63% | 0% | 0.3655% | 156838.2861 | 632336.075 | 20201.7955 | 13848.1902 | 122788.3004 | 82220.5058 | 49784.8246 | 500330.7445 | 178 |  | 1439 | CB 178 | 644514.0314 | 487675.7453 | 12177.9564 | 642158.1693 | 485319.8832 | 9822.0943 | 0 | 0 | 0 | 2355.8621 | 83513.1494 | 63311.3539 | 1292.6435 | 83511.3767 | 63309.5812 | 1290.8708 | 0 | 0 | 0 | 1.7727 | 508132.3068 | 385344.0064 | 7801.5623 | 507918.2987 | 385129.9983 | 7587.5541 | 0 | 0 | 0 | 214.0081 | 52868.5752 | 39020.385 | 3083.7506 | 50728.4939 | 36880.3037 | 943.6694 | 0 | 0 | 0 | 2140.0813 | 0.010148 | 0.0075734 | 0.0001914 | 0 | 0 | 0 | 0.0033632 | 5000000 | scaled
CB 180 | 7712.1587 | 7002.464 | 0 | 709.6947 | 90.8% | 0% | 9.202% | 3228.9272 | 6906.2672 | 24.0049 | 3081.3163 | 123.606 | 49.5951 | 6601.031 | 255.641 | 180 |  | 1440 | CB 180 | 7712.1587 | 4483.2315 | 805.8916 | 7002.464 | 3773.5368 | 96.1969 | 0 | 0 | 0 | 709.6947 | 51.094 | 27.0891 | 1.4989 | 50.56 | 26.5551 | 0.96487 | 0 | 0 | 0 | 0.53402 | 325.09 | 201.484 | 69.4489 | 260.6208 | 137.0149 | 4.9798 | 0 | 0 | 0 | 64.4691 | 7335.9747 | 4254.6584 | 734.9437 | 6691.2832 | 3609.9669 | 90.2522 | 0 | 0 | 0 | 644.6915 | 0.0020204 | 0.0010394 | 2.62e-05 | 0 | 0 | 0 | 0.0009968 | 5000000 | scaled
CB 181 | 2833.5148 | 2332.6121 | 0 | 500.9027 | 82.32% | 0% | 17.68% | 1382.3931 | 2309.9021 | 27.5249 | 1212.5004 | 142.3677 | 35.8799 | 2088.4537 | 185.5685 | 181 |  | 1441 | CB 181 | 2833.5148 | 1451.1216 | 523.6127 | 2332.6121 | 950.219 | 22.71 | 0 | 0 | 0 | 500.9027 | 36.3805 | 8.8556 | 0.50067 | 36.0036 | 8.4787 | 0.12376 | 0 | 0 | 0 | 0.37691 | 231.7124 | 89.3447 | 46.1439 | 186.2101 | 43.8423 | 0.64154 | 0 | 0 | 0 | 45.5023 | 2565.4218 | 1352.9214 | 476.9681 | 2110.3984 | 897.898 | 21.9447 | 0 | 0 | 0 | 455.0234 | 0.0017656 | 0.0007646 | 1.92e-05 | 0 | 0 | 0 | 0.000729 | 5000000 | scaled
CB 183 | 128802.1053 | 29181.678 | 97598.2373 | 2022.1901 | 22.66% | 75.77% | 1.57% | 60773.1625 | 120071.4197 | 650.6266 | 51654.6128 | 8467.9231 | 1058.3117 | 103215.912 | 15797.196 | 183 |  | 1442 | CB 183 | 128802.1053 | 68028.9428 | 8730.6855 | 29181.678 | 12027.3476 | 200.6491 | 97598.2373 | 53979.4051 | 6507.8464 | 2022.1901 | 1073.9502 | 423.3236 | 15.6385 | 919.5386 | 337.242 | 3.9222 | 152.89 | 84.56 | 10.1947 | 1.5216 | 16750.8367 | 8282.9136 | 953.6407 | 5326.7096 | 1882.3857 | 20.4322 | 11240.43 | 6216.8307 | 749.5114 | 183.6971 | 110977.3184 | 59322.7056 | 7761.4064 | 22935.4298 | 9807.72 | 176.2948 | 86204.9173 | 47678.0143 | 5748.1403 | 1836.9713 | 0.0054056 | 0.002471 | 6.26e-05 | 0.014044 | 0.0079916 | 0.0014044 | 0.002876 | 5000000 | scaled
CB 184 | 52486.6198 | 379.5662 | 51756.426 | 350.6275 | 0.7232% | 98.61% | 0.668% | 23331.0531 | 48680.1037 | 38.3564 | 18529.5848 | 4763.1119 | 80.5509 | 38644.9003 | 9954.6525 | 184 |  | 1443 | CB 184 | 52486.6198 | 29155.5667 | 3806.5161 | 379.5662 | 166.1438 | 4.0907 | 51756.426 | 28638.7954 | 3451.7979 | 350.6275 | 86.495 | 48.1387 | 5.9442 | 1.0602 | 0.74648 | 0 | 85.171 | 47.1283 | 5.6803 | 0.26384 | 10697.4627 | 5934.3508 | 742.8101 | 5.4659 | 3.8363 | 0.00047 | 10660.1455 | 5898.6632 | 710.9584 | 31.8512 | 41702.6621 | 23173.0773 | 3057.7618 | 373.0401 | 161.561 | 4.0902 | 41011.1095 | 22693.0038 | 2735.1591 | 318.5124 | 0.0012086 | 0.0006172 | 1.58e-05 | 0.014109 | 0.0080322 | 0.001411 | 0.000503 | 5000000 | scaled
CB 185 | 396850.6102 | 317222.1204 | 76572.0643 | 3056.4256 | 79.93% | 19.29% | 0.7702% | 143149.3317 | 383676.637 | 8145.4586 | 31516.7709 | 103487.1022 | 23063.0911 | 65278.7357 | 295334.8102 | 185 |  | 1444 | CB 185 | 396850.6102 | 253701.2784 | 13173.9731 | 317222.1204 | 208288.0494 | 5011.508 | 76572.0643 | 42356.8035 | 5106.0396 | 3056.4256 | 23436.807 | 15291.3485 | 373.7159 | 23342.0335 | 15237.8956 | 365.2497 | 92.4737 | 51.153 | 6.1664 | 2.2999 | 300869.5962 | 197382.4939 | 5534.786 | 290931.1352 | 191760.8454 | 4612.9282 | 9660.8132 | 5344.0007 | 644.2101 | 277.6478 | 72544.207 | 41027.436 | 7265.4712 | 2948.9517 | 1289.3084 | 33.3302 | 66818.7774 | 36961.6497 | 4455.6631 | 2776.4779 | 0.0094568 | 0.0053412 | 0.000136 | 0.014051 | 0.0079962 | 0.001405 | 0.0042894 | 5000000 | scaled
CB 186 | 92389.4366 | 89279.1193 | 0 | 3110.3173 | 96.63% | 0% | 3.367% | 43344.9072 | 88359.6047 | 3085.9453 | 28501.571 | 11757.3908 | 5818.768 | 60744.2357 | 21796.601 | 186 |  | 1445 | CB 186 | 92389.4366 | 49044.5294 | 4029.8319 | 89279.1193 | 45934.2121 | 919.5146 | 0 | 0 | 0 | 3110.3173 | 5870.3899 | 2784.4447 | 51.622 | 5868.0495 | 2782.1042 | 49.2815 | 0 | 0 | 0 | 2.3404 | 22251.0783 | 10493.6874 | 454.4773 | 21968.5349 | 10211.1441 | 171.934 | 0 | 0 | 0 | 282.5434 | 64267.9684 | 35766.3973 | 3523.7326 | 61442.5348 | 32940.9638 | 698.2991 | 0 | 0 | 0 | 2825.4336 | 0.010714 | 0.005594 | 0.0001424 | 0 | 0 | 0 | 0.0043686 | 5000000 | scaled
CB 187 | 43460.5328 | 39336.1542 | 0 | 4124.3786 | 90.51% | 0% | 9.49% | 20237.7912 | 38922.6059 | 1014.1321 | 13728.8343 | 5494.8249 | 1818.4129 | 27390.6164 | 9713.5766 | 187 |  | 1446 | CB 187 | 43460.5328 | 23222.7416 | 4537.9269 | 39336.1542 | 19098.363 | 413.5483 | 0 | 0 | 0 | 4124.3786 | 1836.3139 | 822.1818 | 17.901 | 1833.2104 | 819.0783 | 14.7975 | 0 | 0 | 0 | 3.1035 | 10163.2439 | 4668.419 | 449.6673 | 9788.5825 | 4293.7576 | 75.0059 | 0 | 0 | 0 | 374.6614 | 31460.9751 | 17732.1408 | 4070.3586 | 27714.3613 | 13985.5271 | 323.7449 | 0 | 0 | 0 | 3746.6137 | 0.011605 | 0.0056412 | 0.0001436 | 0 | 0 | 0 | 0.0058646 | 5000000 | scaled
CB 188 | 378367.0116 | 371687.2126 | 0 | 6679.799 | 98.23% | 0% | 1.765% | 191997.6794 | 365429.5228 | 22349.2792 | 23785.124 | 145863.2763 | 42137.313 | 50857.1198 | 272435.09 | 188 |  | 1447 | CB 188 | 378367.0116 | 186369.3322 | 12937.4888 | 371687.2126 | 179689.5332 | 6257.6898 | 0 | 0 | 0 | 6679.799 | 42858.4281 | 20509.149 | 721.1151 | 42853.4018 | 20504.1226 | 716.0888 | 0 | 0 | 0 | 5.0263 | 277896.9237 | 132033.6475 | 5461.8337 | 277290.1262 | 131426.85 | 4855.0362 | 0 | 0 | 0 | 606.7975 | 57611.6597 | 33826.5358 | 6754.54 | 51543.6846 | 27758.5606 | 686.5648 | 0 | 0 | 0 | 6067.9751 | 0.026561 | 0.012837 | 0.0003506 | 0 | 0 | 0 | 0.009432 | 5000000 | scaled
CB 189 | 36550.2685 | 35325.0943 | 0 | 1225.1742 | 96.65% | 0% | 3.352% | 17696.9979 | 34892.2445 | 1125.2096 | 8879.0153 | 7692.773 | 2077.6498 | 18927.0181 | 13887.5766 | 189 |  | 1448 | CB 189 | 36550.2685 | 18853.2706 | 1658.024 | 35325.0943 | 17628.0964 | 432.8498 | 0 | 0 | 0 | 1225.1742 | 2100.8683 | 975.6587 | 23.2185 | 2099.9464 | 974.7368 | 22.2966 | 0 | 0 | 0 | 0.9219 | 14143.2624 | 6450.4895 | 255.6858 | 14031.9668 | 6339.1938 | 144.3902 | 0 | 0 | 0 | 111.2957 | 20306.1378 | 11427.1225 | 1379.1197 | 19193.1812 | 10314.1659 | 266.1631 | 0 | 0 | 0 | 1112.9566 | 0.003564 | 0.0017982 | 4.54e-05 | 0 | 0 | 0 | 0.0017356 | 5000000 | scaled
CB 190 | 50749.6999 | 49708.4733 | 0 | 1041.2266 | 97.95% | 0% | 2.052% | 26393.8954 | 49370.2317 | 1324.3557 | 20855.5735 | 4213.9662 | 2495.2574 | 38912.1928 | 7962.7815 | 190 |  | 1449 | CB 190 | 50749.6999 | 24355.8045 | 1379.4681 | 49708.4733 | 23314.5779 | 338.2416 | 0 | 0 | 0 | 1041.2266 | 2504.3586 | 1180.0029 | 9.1012 | 2503.5751 | 1179.2194 | 8.3177 | 0 | 0 | 0 | 0.78349 | 8082.2476 | 3868.2814 | 119.4661 | 7987.6619 | 3773.6957 | 24.8804 | 0 | 0 | 0 | 94.5857 | 40163.0937 | 19307.5202 | 1250.9008 | 39217.2363 | 18361.6628 | 305.0435 | 0 | 0 | 0 | 945.8573 | 0.0031326 | 0.0014452 | 3.6e-05 | 0 | 0 | 0 | 0.001455 | 5000000 | scaled
CB 191 | 11195.0038 | 8965.4141 | 0 | 2229.5897 | 80.08% | 0% | 19.92% | 5108.6154 | 8914.8707 | 302.0266 | 3548.5558 | 1258.033 | 530.9381 | 6174.9104 | 2209.0222 | 191 |  | 1450 | CB 191 | 11195.0038 | 6086.3884 | 2280.1331 | 8965.4141 | 3856.7986 | 50.5433 | 0 | 0 | 0 | 2229.5897 | 532.9005 | 230.8739 | 1.9624 | 531.2228 | 229.1962 | 0.28468 | 0 | 0 | 0 | 1.6777 | 2412.6664 | 1154.6333 | 203.6442 | 2210.1289 | 952.0959 | 1.1067 | 0 | 0 | 0 | 202.5375 | 8249.4369 | 4700.8811 | 2074.5265 | 6224.0624 | 2675.5066 | 49.1519 | 0 | 0 | 0 | 2025.3746 | 0.0063464 | 0.0027482 | 7.08e-05 | 0 | 0 | 0 | 0.0031356 | 5000000 | scaled
CB 192 | 109581.6433 | 106715.6914 | 0 | 2865.9519 | 97.38% | 0% | 2.615% | 43731.7574 | 105113.8352 | 3278.1851 | 24407.2897 | 16046.2827 | 7173.9033 | 63567.1127 | 34372.8192 | 192 |  | 1451 | CB 192 | 109581.6433 | 65849.8859 | 4467.8081 | 106715.6914 | 62983.9339 | 1601.8562 | 0 | 0 | 0 | 2865.9519 | 7278.4905 | 4000.3054 | 104.5872 | 7276.334 | 3998.1489 | 102.4306 | 0 | 0 | 0 | 2.1565 | 35115.5006 | 19069.2179 | 742.6814 | 34855.1555 | 18808.8729 | 482.3364 | 0 | 0 | 0 | 260.345 | 67187.6522 | 42780.3625 | 3620.5396 | 64584.2018 | 40176.9122 | 1017.0892 | 0 | 0 | 0 | 2603.4504 | 0.011077 | 0.006018 | 0.0001528 | 0 | 0 | 0 | 0.0039492 | 5000000 | scaled
CB 194 | 41364.7637 | 37335.206 | 0 | 4029.5577 | 90.26% | 0% | 9.742% | 19917.8797 | 37162.3257 | 1161.9723 | 11123.4301 | 7632.4773 | 2183.4071 | 20261.2179 | 14717.7007 | 194 |  | 1452 | CB 194 | 41364.7637 | 21446.884 | 4202.438 | 37335.206 | 17417.3263 | 172.8804 | 0 | 0 | 0 | 4029.5577 | 2192.442 | 1030.4697 | 9.035 | 2189.4099 | 1027.4376 | 6.0029 | 0 | 0 | 0 | 3.0321 | 15115.9252 | 7483.448 | 398.2245 | 14749.8775 | 7117.4002 | 32.1768 | 0 | 0 | 0 | 366.0478 | 24056.3964 | 12932.9663 | 3795.1785 | 20395.9186 | 9272.4885 | 134.7007 | 0 | 0 | 0 | 3660.4778 | 0.012374 | 0.0053578 | 0.0001362 | 0 | 0 | 0 | 0.0056698 | 5000000 | scaled
CB 195 | 363249.5827 | 215997.1207 | 145060.2166 | 2192.2454 | 59.46% | 39.93% | 0.6035% | 171849.1241 | 349966.8421 | 8074.4176 | 64639.8949 | 99134.8115 | 16104.4469 | 137142.6428 | 196719.7523 | 195 |  | 1453 | CB 195 | 363249.5827 | 191400.4586 | 13282.7406 | 215997.1207 | 108857.0852 | 1400.0234 | 145060.2166 | 80351.128 | 9690.4718 | 2192.2454 | 16227.7262 | 8153.3086 | 123.2793 | 16051.1203 | 8054.7479 | 109.9421 | 174.9563 | 96.9111 | 11.6876 | 1.6496 | 198839.5953 | 99704.7837 | 2119.8429 | 185855.0132 | 92423.5847 | 1066.5911 | 12785.4369 | 7082.054 | 854.1068 | 199.1451 | 148182.2612 | 83542.3663 | 11039.6184 | 14090.9872 | 8378.7526 | 223.4903 | 132099.8233 | 73172.163 | 8824.6774 | 1991.4507 | 0.0087992 | 0.0043676 | 0.0001108 | 0.017536 | 0.0099922 | 0.0017536 | 0.0030674 | 5000000 | scaled
CB 196 | 134469.9059 | 4225.1868 | 129822.9262 | 421.7929 | 3.142% | 96.54% | 0.3137% | 59053.6434 | 125320.2819 | 145.153 | 51495.3911 | 7413.0994 | 408.329 | 108765.9609 | 16145.992 | 196 |  | 1454 | CB 196 | 134469.9059 | 75416.2625 | 9149.624 | 4225.1868 | 3132.1998 | 57.6687 | 129822.9262 | 71862.2699 | 8670.1624 | 421.7929 | 423.2311 | 278.0781 | 14.9021 | 245.1868 | 179.3817 | 2.7153 | 177.727 | 98.3791 | 11.8694 | 0.31739 | 17253.0654 | 9839.966 | 1107.0734 | 1434.8528 | 1066.8354 | 14.9045 | 15779.8967 | 8734.8146 | 1053.8529 | 38.316 | 116793.6095 | 65298.2184 | 8027.6486 | 2545.1473 | 1885.9827 | 40.0489 | 113865.3026 | 63029.0762 | 7604.4401 | 383.1596 | 0.0012872 | 0.0007592 | 1.94e-05 | 0.017583 | 0.010012 | 0.0017582 | 0.0005944 | 5000000 | scaled
CB 197 | 1919.8274 | 1884.9509 | 0 | 34.8765 | 98.18% | 0% | 1.817% | 353.7626 | 1862.2359 | 9.039 | 299.9987 | 44.7249 | 78.5099 | 1352.6944 | 431.0317 | 197 |  | 1455 | CB 197 | 1919.8274 | 1566.0648 | 57.5915 | 1884.9509 | 1531.1883 | 22.715 | 0 | 0 | 0 | 34.8765 | 79.1201 | 70.0811 | 0.61024 | 79.0939 | 70.0549 | 0.584 | 0 | 0 | 0 | 0.026243 | 437.2117 | 392.4868 | 6.1801 | 434.0435 | 389.3186 | 3.0118 | 0 | 0 | 0 | 3.1682 | 1403.4956 | 1103.4969 | 50.8012 | 1371.8135 | 1071.8148 | 19.1191 | 0 | 0 | 0 | 31.6821 | 0.0002634 | 0.0002 | 5e-06 | 0 | 0 | 0 | 5.06e-05 | 5000000 | scaled
CB 198 | 42398.8576 | 40401.1171 | 0 | 1997.7404 | 95.29% | 0% | 4.712% | 21619.4198 | 39780.3906 | 2262.0138 | 10780.8777 | 8576.5283 | 4315.7947 | 19038.2513 | 16426.3446 | 198 |  | 1456 | CB 198 | 42398.8576 | 20779.4378 | 2618.467 | 40401.1171 | 18781.6973 | 620.7266 | 0 | 0 | 0 | 1997.7404 | 4398.6541 | 2136.6403 | 82.8594 | 4397.1509 | 2135.137 | 81.3562 | 0 | 0 | 0 | 1.5032 | 16934.8123 | 8358.284 | 508.4677 | 16753.3362 | 8176.8079 | 326.9916 | 0 | 0 | 0 | 181.4761 | 21065.3912 | 10284.5135 | 2027.1399 | 19250.6301 | 8469.7524 | 212.3788 | 0 | 0 | 0 | 1814.7611 | 0.0062204 | 0.0028242 | 7.24e-05 | 0 | 0 | 0 | 0.0028738 | 5000000 | scaled
CB 199 | 86249.1877 | 82181.7891 | 0 | 4067.3986 | 95.28% | 0% | 4.716% | 44177.4536 | 81137.4907 | 7046.8582 | 1719.4498 | 35411.1456 | 12914.749 | 3087.7222 | 65135.0195 | 199 |  | 1457 | CB 199 | 86249.1877 | 42071.7341 | 5111.697 | 82181.7891 | 38004.3355 | 1044.2984 | 0 | 0 | 0 | 4067.3986 | 13086.6038 | 6039.7455 | 171.8548 | 13083.5432 | 6036.6849 | 168.7942 | 0 | 0 | 0 | 3.0606 | 66345.2246 | 30934.079 | 1210.2051 | 65975.7393 | 30564.5937 | 840.7198 | 0 | 0 | 0 | 369.4853 | 6817.3593 | 5097.9096 | 3729.6371 | 3122.5066 | 1403.0568 | 34.7844 | 0 | 0 | 0 | 3694.8527 | 0.013788 | 0.0062018 | 0.0001584 | 0 | 0 | 0 | 0.005703 | 5000000 | scaled
CB 200 | 1342655.8504 | 401401.4798 | 931360.3809 | 9893.9897 | 29.9% | 69.37% | 0.7369% | 629662.5128 | 1276751.9505 | 13965.2713 | 463019.8213 | 152677.4201 | 26604.2124 | 953959.9733 | 296187.7647 | 200 |  | 1458 | CB 200 | 1342655.8504 | 712993.3376 | 65903.8998 | 401401.4798 | 192369.6622 | 4320.2954 | 931360.3809 | 510729.6857 | 51689.6147 | 9893.9897 | 26946.0037 | 12980.7324 | 341.7913 | 26123.4232 | 12522.3677 | 281.0722 | 815.1357 | 450.9198 | 53.2742 | 7.4449 | 303516.8133 | 150839.3932 | 7329.0486 | 240813.2415 | 115793.4231 | 2477.3848 | 61804.795 | 34147.1932 | 3952.887 | 898.7768 | 1012193.0333 | 549173.212 | 58233.06 | 134464.8151 | 64053.8713 | 1561.8385 | 868740.4502 | 476131.5726 | 47683.4534 | 8987.768 | 0.029303 | 0.013227 | 0.0003358 | 0.017044 | 0.0097086 | 0.0017044 | 0.013914 | 5000000 | scaled
CB 202 | 133986.1187 | 127451.4982 | 0 | 6534.6205 | 95.12% | 0% | 4.877% | 71349.113 | 125803.5611 | 5814.6596 | 481.507 | 65052.9464 | 10229.7942 | 858.8977 | 114714.8693 | 202 |  | 1459 | CB 202 | 133986.1187 | 62637.0057 | 8182.5576 | 127451.4982 | 56102.3852 | 1647.9371 | 0 | 0 | 0 | 6534.6205 | 10371.4667 | 4556.8071 | 141.6725 | 10366.5496 | 4551.89 | 136.7554 | 0 | 0 | 0 | 4.9171 | 116809.8285 | 51756.8821 | 2094.9593 | 116216.2191 | 51163.2727 | 1501.3499 | 0 | 0 | 0 | 593.6094 | 6804.8235 | 6323.3166 | 5945.9259 | 868.7295 | 387.2225 | 9.8318 | 0 | 0 | 0 | 5936.094 | 0.031671 | 0.01407 | 0.0003576 | 0 | 0 | 0 | 0.0092954 | 5000000 | scaled
CB 203 | 195751.9979 | 18759.6424 | 172711.1656 | 4281.1899 | 9.583% | 88.23% | 2.187% | 87323.0715 | 179672.1155 | 365.0405 | 78736.5465 | 8221.4845 | 673.1727 | 162298.5962 | 16700.3466 | 203 |  | 1460 | CB 203 | 195751.9979 | 108428.9264 | 16079.8824 | 18759.6424 | 8468.599 | 259.7337 | 172711.1656 | 95679.1375 | 11538.9589 | 4281.1899 | 698.4295 | 333.389 | 25.2568 | 491.2762 | 217.1927 | 8.4105 | 203.9319 | 112.9749 | 13.6248 | 3.2215 | 18143.023 | 9921.5385 | 1442.6764 | 2688.0801 | 1186.2964 | 47.1973 | 15066.0367 | 8346.3359 | 1006.5729 | 388.9062 | 176910.5454 | 98173.9988 | 14611.9491 | 15580.2861 | 7065.1099 | 204.1258 | 157441.197 | 87219.8267 | 10518.7611 | 3889.0622 | 0.011784 | 0.0051698 | 0.0001322 | 0.017595 | 0.010027 | 0.0017596 | 0.0060308 | 5000000 | scaled
CB 204 | 1059531.3911 | 856339.2182 | 195075.178 | 8116.995 | 80.82% | 18.41% | 0.7661% | 495310.162 | 1026735.3675 | 30463.3907 | 94318.7267 | 370528.0445 | 63068.1704 | 200781.0765 | 762886.1206 | 204 |  | 1461 | CB 204 | 1059531.3911 | 564221.2291 | 32796.0236 | 856339.2182 | 448022.261 | 11651.2181 | 195075.178 | 108081.9731 | 13027.8105 | 8116.995 | 63955.2641 | 33491.8734 | 887.0937 | 63699.9551 | 33347.6949 | 864.3433 | 249.2012 | 138.0707 | 16.6425 | 6.1078 | 775023.6145 | 404495.57 | 12137.494 | 757391.8941 | 394397.8431 | 10271.875 | 16894.367 | 9360.3735 | 1128.2656 | 737.3534 | 220552.5125 | 126233.7857 | 19771.436 | 35247.3689 | 20276.7229 | 514.9998 | 177931.6097 | 98583.529 | 11882.9024 | 7373.5338 | 0.03949 | 0.020013 | 0.0005082 | 0.01758 | 0.01002 | 0.001758 | 0.011454 | 5000000 | scaled
CB 205 | 38779.159 | 34831.8038 | 0 | 3947.3552 | 89.82% | 0% | 10.18% | 19892.4308 | 34402.9453 | 741.1839 | 15130.0308 | 4021.2161 | 1191.4438 | 26797.8783 | 6413.6232 | 205 |  | 1462 | CB 205 | 38779.159 | 18886.7282 | 4376.2137 | 34831.8038 | 14939.373 | 428.8585 | 0 | 0 | 0 | 3947.3552 | 1209.7601 | 468.5762 | 18.3163 | 1206.7898 | 465.6059 | 15.3461 | 0 | 0 | 0 | 2.9703 | 6855.7871 | 2834.571 | 442.1638 | 6497.2066 | 2475.9905 | 83.5834 | 0 | 0 | 0 | 358.5805 | 30713.6118 | 15583.581 | 3915.7335 | 27127.8073 | 11997.7765 | 329.929 | 0 | 0 | 0 | 3585.8045 | 0.010687 | 0.00471 | 0.0001192 | 0 | 0 | 0 | 0.0055322 | 5000000 | scaled
CB 206 | 15008.3863 | 12960.2699 | 0 | 2048.1163 | 86.35% | 0% | 13.65% | 6623.3398 | 12796.1876 | 68.4419 | 6203.411 | 351.4869 | 125.7051 | 12024.7775 | 645.705 | 206 |  | 1463 | CB 206 | 15008.3863 | 8385.0464 | 2212.1987 | 12960.2699 | 6336.9301 | 164.0823 | 0 | 0 | 0 | 2048.1163 | 129.8471 | 61.4052 | 4.142 | 128.3059 | 59.8641 | 2.6008 | 0 | 0 | 0 | 1.5411 | 845.1484 | 493.6615 | 199.4435 | 659.0962 | 307.6092 | 13.3912 | 0 | 0 | 0 | 186.0523 | 14033.3908 | 7829.9797 | 2008.6132 | 12172.8678 | 5969.4568 | 148.0903 | 0 | 0 | 0 | 1860.5229 | 0.0055436 | 0.0025862 | 6.54e-05 | 0 | 0 | 0 | 0.0028938 | 5000000 | scaled
CB 207 | 36129.9667 | 34171.1952 | 0 | 1958.7715 | 94.58% | 0% | 5.421% | 15713.7387 | 33664.2797 | 290.2932 | 13917.7972 | 1505.6483 | 645.3915 | 29663.6979 | 3355.1903 | 207 |  | 1464 | CB 207 | 36129.9667 | 20416.228 | 2465.687 | 34171.1952 | 18457.4565 | 506.9155 | 0 | 0 | 0 | 1958.7715 | 658.8848 | 368.5915 | 13.4932 | 657.4108 | 367.1176 | 12.0193 | 0 | 0 | 0 | 1.4739 | 3596.2313 | 2090.5831 | 241.0411 | 3418.2952 | 1912.6469 | 63.1049 | 0 | 0 | 0 | 177.9361 | 31874.8506 | 17957.0534 | 2211.1527 | 30095.4892 | 16177.692 | 431.7913 | 0 | 0 | 0 | 1779.3615 | 0.006265 | 0.0031256 | 7.92e-05 | 0 | 0 | 0 | 0.0027476 | 5000000 | scaled
CB 208 | 7991.1701 | 7493.7351 | 0 | 497.4349 | 93.78% | 0% | 6.225% | 3812.321 | 7381.8976 | 37.0696 | 3584.947 | 190.3044 | 71.7036 | 6942.0762 | 368.1179 | 208 |  | 1465 | CB 208 | 7991.1701 | 4178.8491 | 609.2724 | 7493.7351 | 3681.4141 | 111.8375 | 0 | 0 | 0 | 497.4349 | 74.3055 | 37.2358 | 2.6019 | 73.9312 | 36.8615 | 2.2276 | 0 | 0 | 0 | 0.3743 | 424.8516 | 234.5473 | 56.7338 | 379.6643 | 189.36 | 11.5465 | 0 | 0 | 0 | 45.1873 | 7492.0129 | 3907.0659 | 549.9367 | 7040.1396 | 3455.1926 | 98.0634 | 0 | 0 | 0 | 451.8733 | 0.0010132 | 0.0004966 | 1.26e-05 | 0 | 0 | 0 | 0.000698 | 5000000 | scaled
CB 209 | 2997.7049 | 2851.3112 | 0 | 146.3937 | 95.12% | 0% | 4.884% | 1610.1046 | 2820.4772 | 5.1364 | 1578.6919 | 26.2762 | 10.4715 | 2756.4225 | 53.5833 | 209 |  | 1466 | CB 209 | 2997.7049 | 1387.6003 | 177.2277 | 2851.3112 | 1241.2067 | 30.834 | 0 | 0 | 0 | 146.3937 | 10.5816 | 5.4452 | 0.11016 | 10.4715 | 5.335 | 0 | 0 | 0 | 0 | 0.11016 | 66.8818 | 40.6055 | 13.2985 | 53.5833 | 27.307 | 0 | 0 | 0 | 0 | 13.2985 | 2920.2415 | 1341.5496 | 163.819 | 2787.2565 | 1208.5646 | 30.834 | 0 | 0 | 0 | 132.985 | 0.000466 | 0.0002018 | 5.2e-06 | 0 | 0 | 0 | 0.000209 | 5000000 | scaled
CB 210 | 1953.1606 | 1879.1531 | 0 | 74.0074 | 96.21% | 0% | 3.789% | 412.9542 | 1878.7134 | 14.4251 | 31.209 | 367.3201 | 75.0326 | 51.5958 | 1752.085 | 210 |  | 1467 | CB 210 | 1953.1606 | 1540.2064 | 74.4472 | 1879.1531 | 1466.199 | 0.43975 | 0 | 0 | 0 | 74.0074 | 75.0883 | 60.6631 | 0.055688 | 75.0326 | 60.6074 | 0 | 0 | 0 | 0 | 0.055688 | 1758.8079 | 1391.4878 | 6.7229 | 1752.085 | 1384.7649 | 0 | 0 | 0 | 0 | 6.7229 | 119.2644 | 88.0555 | 67.6686 | 52.0356 | 20.8266 | 0.43975 | 0 | 0 | 0 | 67.2289 | 0.0001002 | 4.34e-05 | 1.2e-06 | 0 | 0 | 0 | 0.0001 | 5000000 | scaled
CB 211 | 37.2735 | 0 | 0 | 37.2735 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211 |  | 1468 | CB 211 | 37.2735 | 37.2735 | 37.2735 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2735 | 0.028047 | 0.028047 | 0.028047 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028047 | 3.3859 | 3.3859 | 3.3859 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3859 | 33.8595 | 33.8595 | 33.8595 | 0 | 0 | 0 | 0 | 0 | 0 | 33.8595 | 0 | 0 | 0 | 0 | 0 | 0 | 5.02e-05 | 5000000 | scaled
CB 212 | 22980.8656 | 22772.4589 | 0 | 208.4067 | 99.09% | 0% | 0.9069% | 4085.5972 | 22741.3731 | 166.4086 | 220.4681 | 3698.7204 | 872.2239 | 880.2968 | 20988.8525 | 212 |  | 1469 | CB 212 | 22980.8656 | 18895.2684 | 239.4925 | 22772.4589 | 18686.8617 | 31.0858 | 0 | 0 | 0 | 208.4067 | 872.8399 | 706.4313 | 0.61608 | 872.6831 | 706.2745 | 0.45926 | 0 | 0 | 0 | 0.15682 | 21022.4345 | 17323.714 | 33.5819 | 21003.5026 | 17304.7822 | 14.6501 | 0 | 0 | 0 | 18.9318 | 1085.5912 | 865.1231 | 205.2945 | 896.2732 | 675.805 | 15.9764 | 0 | 0 | 0 | 189.3181 | 0.0008774 | 0.0006664 | 1.68e-05 | 0 | 0 | 0 | 0.0002872 | 5000000 | scaled
CB 214 | 59199.6485 | 59129.2953 | 0 | 70.3532 | 99.88% | 0% | 0.1188% | 20975.3408 | 59126.3303 | 1061.9363 | 57.8549 | 19855.5497 | 3082.3525 | 248.6705 | 55795.3074 | 214 |  | 1470 | CB 214 | 59199.6485 | 38224.3077 | 73.3182 | 59129.2953 | 38153.9544 | 2.965 | 0 | 0 | 0 | 70.3532 | 3082.4054 | 2020.4692 | 0.052939 | 3082.3525 | 2020.4162 | 0 | 0 | 0 | 0 | 0.052939 | 55801.6983 | 35946.1487 | 6.3909 | 55795.3074 | 35939.7577 | 0 | 0 | 0 | 0 | 6.3909 | 315.5448 | 257.6899 | 66.8743 | 251.6354 | 193.7805 | 2.965 | 0 | 0 | 0 | 63.9094 | 0.0001002 | 7.62e-05 | 2e-06 | 0 | 0 | 0 | 0.0001014 | 5000000 | scaled
CB 215 | 133913.2875 | 133771.9109 | 0 | 141.3766 | 99.89% | 0% | 0.1056% | 10943.9797 | 133733.8919 | 683.0405 | 135.4999 | 10125.4393 | 7111.6662 | 526.9868 | 126095.2389 | 215 |  | 1471 | CB 215 | 133913.2875 | 122969.3078 | 179.3956 | 133771.9109 | 122827.9312 | 38.019 | 0 | 0 | 0 | 141.3766 | 7115.126 | 6432.0855 | 3.4598 | 7115.0196 | 6431.9791 | 3.3534 | 0 | 0 | 0 | 0.10638 | 126132.764 | 116007.3247 | 37.5251 | 126119.9212 | 115994.4819 | 24.6823 | 0 | 0 | 0 | 12.8427 | 665.3975 | 529.8976 | 138.4107 | 536.9701 | 401.4702 | 9.9833 | 0 | 0 | 0 | 128.4275 | 0.00036 | 0.0002734 | 6.8e-06 | 0 | 0 | 0 | 0.0001946 | 5000000 | scaled
CB 217 | 26667.8484 | 26590.6344 | 0 | 77.214 | 99.71% | 0% | 0.2895% | 845.6316 | 17468.9984 | 58.1587 | 33.2393 | 754.2337 | 905.447 | 121.9545 | 16441.5968 | 217 |  | 1472 | CB 217 | 26667.8484 | 25822.2168 | 9198.85 | 26590.6344 | 25745.0027 | 9121.636 | 0 | 0 | 0 | 77.214 | 1347.3262 | 1289.1676 | 441.8792 | 1347.2681 | 1289.1095 | 441.8211 | 0 | 0 | 0 | 0.058101 | 25126.6982 | 24372.4645 | 8685.1013 | 25119.684 | 24365.4503 | 8678.0871 | 0 | 0 | 0 | 7.0142 | 193.824 | 160.5847 | 71.8695 | 123.6823 | 90.443 | 1.7277 | 0 | 0 | 0 | 70.1418 | 3.26e-05 | 2.48e-05 | 6e-07 | 0 | 0 | 0 | 0.0001014 | 5000000 | scaled
CB 220 | 33.5352 | 0 | 0 | 33.5352 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 |  | 1473 | CB 220 | 33.5352 | 33.5352 | 33.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 33.5352 | 0.025234 | 0.025234 | 0.025234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025234 | 3.0464 | 3.0464 | 3.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0464 | 30.4636 | 30.4636 | 30.4636 | 0 | 0 | 0 | 0 | 0 | 0 | 30.4636 | 0 | 0 | 0 | 0 | 0 | 0 | 4.74e-05 | 5000000 | scaled
CB 229 | 2744.0458 | 2598.977 | 0 | 145.0688 | 94.71% | 0% | 5.287% | 1153.9372 | 2585.2812 | 34.0105 | 972.7787 | 147.148 | 95.1286 | 2024.7448 | 465.4079 | 229 |  | 1474 | CB 229 | 2744.0458 | 1590.1086 | 158.7646 | 2598.977 | 1445.0398 | 13.6958 | 0 | 0 | 0 | 145.0688 | 95.2377 | 61.2272 | 0.10916 | 95.1286 | 61.1181 | 0 | 0 | 0 | 0 | 0.10916 | 478.586 | 331.438 | 13.1781 | 465.4079 | 318.2598 | 0 | 0 | 0 | 0 | 13.1781 | 2170.222 | 1197.4434 | 145.4773 | 2038.4406 | 1065.6619 | 13.6958 | 0 | 0 | 0 | 131.7815 | 0.0003836 | 0.0001662 | 4e-06 | 0 | 0 | 0 | 0.0002028 | 5000000 | scaled
CB 230 | 212827.4514 | 212430.4059 | 0 | 397.0455 | 99.81% | 0% | 0.1866% | 51332.5402 | 199996.7306 | 3235.1787 | 4052.0755 | 44045.286 | 12662.4569 | 16520.3388 | 170813.9349 | 230 |  | 1475 | CB 230 | 212827.4514 | 161494.9112 | 12830.7208 | 212430.4059 | 161097.8656 | 12433.6753 | 0 | 0 | 0 | 397.0455 | 13417.9121 | 10182.7334 | 755.4552 | 13417.6133 | 10182.4347 | 755.1564 | 0 | 0 | 0 | 0.29876 | 182307.9323 | 138262.6462 | 11493.9974 | 182271.8644 | 138226.5783 | 11457.9295 | 0 | 0 | 0 | 36.0679 | 17101.607 | 13049.5315 | 581.2682 | 16740.9282 | 12688.8526 | 220.5894 | 0 | 0 | 0 | 360.6789 | 0.0020306 | 0.0015424 | 3.9e-05 | 0 | 0 | 0 | 0.0005516 | 5000000 | scaled
CB 231 | 2499973.9976 | 2482126.7106 | 12017.5592 | 5829.7277 | 99.29% | 0.4807% | 0.2332% | 1285897.2605 | 2435435.7877 | 94018.8886 | 10143.8333 | 1181734.5387 | 178596.5457 | 30390.5154 | 2226448.7266 | 231 |  | 1476 | CB 231 | 2499973.9976 | 1214076.7371 | 64538.2099 | 2482126.7106 | 1201573.744 | 57901.6016 | 12017.5592 | 6673.2653 | 806.8805 | 5829.7277 | 182949.6791 | 88930.7905 | 4353.1334 | 182925.6217 | 88915.4809 | 4347.4259 | 19.6707 | 10.923 | 1.3207 | 4.3867 | 2279798.3246 | 1098063.7859 | 53349.598 | 2278129.3935 | 1096901.5339 | 52743.5232 | 1139.3546 | 632.6755 | 76.4983 | 529.5765 | 37225.9939 | 27082.1607 | 6835.4786 | 21071.6953 | 15756.7292 | 810.6524 | 10858.534 | 6029.6668 | 729.0615 | 5295.7646 | 0.023621 | 0.011091 | 0.0004216 | 0.0056686 | 0.0032366 | 0.0005668 | 0.008283 | 5000000 | scaled
CB 232 | 1642597.0694 | 1599467.3918 | 38156.7715 | 4972.9061 | 97.37% | 2.323% | 0.3027% | 740277.2751 | 1604153.4129 | 45203.2082 | 18989.6078 | 676084.4591 | 98035.9925 | 43384.4902 | 1462732.9302 | 232 |  | 1477 | CB 232 | 1642597.0694 | 902319.7943 | 38443.6565 | 1599467.3918 | 876147.9323 | 30902.5019 | 38156.7715 | 21198.9559 | 2568.2486 | 4972.9061 | 99901.266 | 54698.0578 | 1865.2735 | 99841.0565 | 54662.9439 | 1857.7308 | 56.4676 | 31.372 | 3.8007 | 3.742 | 1492288.6453 | 816204.1862 | 29555.7151 | 1488033.4618 | 813639.3463 | 28847.9717 | 3803.4413 | 2113.0976 | 256.0013 | 451.7422 | 50407.1581 | 31417.5503 | 7022.6679 | 11592.8735 | 7845.6421 | 196.7994 | 34296.8627 | 19054.4863 | 2308.4466 | 4517.4219 | 0.01641 | 0.008705 | 0.0002216 | 0.0056566 | 0.003231 | 0.0005656 | 0.006957 | 5000000 | scaled
CB 233 | 4127695.5357 | 4075589.0906 | 38305.5831 | 13800.862 | 98.74% | 0.928% | 0.3343% | 2072627.8666 | 4067083.959 | 154442.1572 | 43268.1264 | 1874917.583 | 303924.9234 | 116839.6551 | 3646319.3805 | 233 |  | 1478 | CB 233 | 4127695.5357 | 2055067.6691 | 60611.5767 | 4075589.0906 | 2019988.7859 | 44233.7214 | 38305.5831 | 21278.0212 | 2576.9933 | 13800.862 | 307360.6181 | 152918.4609 | 3435.6947 | 307295.8558 | 152877.8705 | 3421.6517 | 54.3776 | 30.2057 | 3.6582 | 10.3847 | 3687156.7867 | 1812239.2037 | 40837.4062 | 3681771.1735 | 1808690.3137 | 39305.7522 | 4131.9334 | 2295.2103 | 277.9742 | 1253.6798 | 133178.1309 | 89910.0045 | 16338.4758 | 86522.0612 | 58420.6017 | 1506.3175 | 34119.2721 | 18952.6052 | 2295.3608 | 12536.7976 | 0.050248 | 0.025182 | 0.0006388 | 0.0056584 | 0.0032312 | 0.0005658 | 0.019545 | 5000000 | scaled
CB 234 | 3294852.9726 | 3257846.8436 | 29794.9831 | 7211.1458 | 98.88% | 0.9043% | 0.2189% | 1396180.5488 | 3240829.6384 | 107809.8416 | 15808.6782 | 1272562.029 | 250223.9393 | 40775.4928 | 2949830.2063 | 234 |  | 1479 | CB 234 | 3294852.9726 | 1898672.4237 | 54023.3342 | 3257846.8436 | 1874896.4631 | 44802.4183 | 29794.9831 | 16564.8149 | 2009.7702 | 7211.1458 | 253697.7421 | 145887.9005 | 3473.8028 | 253640.0595 | 145853.4219 | 3464.8518 | 52.2564 | 29.0525 | 3.5249 | 5.4262 | 2991689.0235 | 1719126.9945 | 41858.8172 | 2988402.1284 | 1717008.7374 | 41026.2262 | 2631.8296 | 1463.1916 | 177.5256 | 655.0654 | 49466.207 | 33657.5287 | 8690.7142 | 15804.6557 | 12034.3038 | 311.3403 | 27110.8971 | 15072.5708 | 1828.7197 | 6550.6542 | 0.028907 | 0.01606 | 0.0004088 | 0.0056612 | 0.0032354 | 0.0005662 | 0.010089 | 5000000 | scaled
CB 235 | 443542.7134 | 443368.0057 | 0 | 174.7077 | 99.96% | 0% | 0.03939% | 208823.3677 | 442047.5818 | 10666.1341 | 2018.4971 | 196138.7366 | 22387.9234 | 3667.1075 | 415992.5509 | 235 |  | 1480 | CB 235 | 443542.7134 | 234719.3457 | 1495.1316 | 443368.0057 | 234544.6379 | 1320.4239 | 0 | 0 | 0 | 174.7077 | 22475.7303 | 11809.5963 | 87.8069 | 22475.5989 | 11809.4648 | 87.6754 | 0 | 0 | 0 | 0.13146 | 417201.9944 | 221063.2578 | 1209.4435 | 417186.1238 | 221047.3872 | 1193.5729 | 0 | 0 | 0 | 15.8706 | 3864.9887 | 1846.4916 | 197.8812 | 3706.283 | 1687.7859 | 39.1755 | 0 | 0 | 0 | 158.7057 | 0.0004644 | 0.0002178 | 5.4e-06 | 0 | 0 | 0 | 0.000249 | 5000000 | scaled
CB 236 | 12711187.7649 | 12408602.1726 | 296581.1054 | 6004.487 | 97.62% | 2.333% | 0.04724% | 5374115.6265 | 12505683.1571 | 322322.8182 | 125920.3794 | 4925872.429 | 749616.0045 | 270487.8569 | 11485579.2956 | 236 |  | 1481 | CB 236 | 12711187.7649 | 7337072.1384 | 205504.6078 | 12408602.1726 | 7164204.5522 | 172567.6156 | 296581.1054 | 166863.0992 | 26932.5053 | 6004.487 | 760104.894 | 437782.0758 | 10488.8894 | 759693.8486 | 437548.8364 | 10447.4546 | 406.5272 | 228.7212 | 36.9167 | 4.5182 | 11650959.7207 | 6725087.2917 | 165380.4251 | 11613981.1169 | 6704043.7417 | 161526.4819 | 36433.1521 | 20498.0984 | 3308.4915 | 545.4517 | 300123.1502 | 174202.7709 | 29635.2933 | 34927.207 | 22611.9741 | 593.6791 | 259741.4261 | 146136.2797 | 23587.0971 | 5454.5171 | 0.02168 | 0.011964 | 0.000305 | 0.11179 | 0.063393 | 0.011179 | 0.0084302 | 5000000 | scaled
CB 237 | 2111574.6356 | 2101904.2649 | 8993.1901 | 677.1806 | 99.54% | 0.4259% | 0.03207% | 840745.8257 | 2029643.6785 | 54913.1254 | 4525.771 | 781306.9293 | 132629.8023 | 12048.1058 | 1884965.7705 | 237 |  | 1482 | CB 237 | 2111574.6356 | 1270828.8098 | 81930.957 | 2101904.2649 | 1265088.8307 | 80445.6155 | 8993.1901 | 5062.7986 | 808.1609 | 677.1806 | 137756.3761 | 82843.2507 | 5126.5738 | 137747.1978 | 82837.861 | 5125.2853 | 8.6687 | 4.8801 | 0.779 | 0.50956 | 1960362.791 | 1179055.8617 | 75397.0205 | 1959165.6661 | 1178355.0445 | 75233.455 | 1135.6094 | 639.3017 | 102.05 | 61.5155 | 13455.4685 | 8929.6974 | 1407.3626 | 4991.401 | 3895.9252 | 86.8753 | 7848.912 | 4418.6167 | 705.3319 | 615.1555 | 0.0024198 | 0.0014458 | 3.68e-05 | 0.10585 | 0.060109 | 0.010585 | 0.0009538 | 5000000 | scaled
CB 239 | 10677.6391 | 10638.8448 | 0 | 38.7943 | 99.64% | 0% | 0.3633% | 5948.2482 | 10632.6325 | 318.2222 | 276.1477 | 5353.8783 | 627.3963 | 869.9879 | 9135.2483 | 239 |  | 1483 | CB 239 | 10677.6391 | 4729.3909 | 45.0066 | 10638.8448 | 4690.5966 | 6.2123 | 0 | 0 | 0 | 38.7943 | 627.4254 | 309.2033 | 0.029191 | 627.3963 | 309.1741 | 0 | 0 | 0 | 0 | 0.029191 | 9138.7724 | 3784.8941 | 3.5241 | 9135.2483 | 3781.37 | 0 | 0 | 0 | 0 | 3.5241 | 911.4412 | 635.2936 | 41.4533 | 876.2002 | 600.0526 | 6.2123 | 0 | 0 | 0 | 35.241 | 0.0001316 | 0.0001 | 2.6e-06 | 0 | 0 | 0 | 5.1e-05 | 5000000 | scaled
CB 240 | 1263031.5721 | 1233691.1972 | 24617.434 | 4722.9408 | 97.68% | 1.949% | 0.3739% | 611906.6105 | 1237560.3214 | 60845.7246 | 19842.6638 | 531218.2221 | 123120.5498 | 40662.7149 | 1073777.0566 | 240 |  | 1484 | CB 240 | 1263031.5721 | 651124.9615 | 25471.2507 | 1233691.1972 | 632755.0267 | 18984.6074 | 24617.434 | 13646.994 | 1763.7025 | 4722.9408 | 124982.4495 | 64136.7249 | 1861.8997 | 124921.7307 | 64101.4809 | 1854.2503 | 57.165 | 31.6902 | 4.0956 | 3.5539 | 1091242.7613 | 560024.5392 | 17465.7046 | 1088246.19 | 558172.157 | 16852.7198 | 2567.5361 | 1423.347 | 183.9497 | 429.0352 | 46806.3613 | 26963.6975 | 6143.6463 | 20523.2766 | 10481.3888 | 277.6373 | 21992.7329 | 12191.9569 | 1575.6572 | 4290.3518 | 0.017414 | 0.008491 | 0.0002154 | 0.024459 | 0.013897 | 0.0024458 | 0.0066374 | 5000000 | scaled
CB 241 | 614484.3396 | 32156.9844 | 580381.6411 | 1945.7141 | 5.233% | 94.45% | 0.3166% | 271881.2269 | 560934.5754 | 889.5699 | 246004.8191 | 24986.8379 | 1646.2869 | 508466.3469 | 50821.9415 | 241 |  | 1485 | CB 241 | 614484.3396 | 342603.1127 | 53549.7642 | 32156.9844 | 14586.5449 | 236.9026 | 580381.6411 | 326070.8538 | 51367.1476 | 1945.7141 | 1720.2156 | 830.6457 | 73.9287 | 925.6 | 383.5721 | 2.2661 | 793.1515 | 445.6095 | 70.1985 | 1.4641 | 55461.072 | 30474.2342 | 4639.1305 | 4995.5891 | 2044.1954 | 11.5354 | 50288.7329 | 28253.2887 | 4450.8451 | 176.75 | 557303.052 | 311298.2329 | 48836.705 | 26235.7953 | 12158.7774 | 223.1011 | 529299.7567 | 297371.9555 | 46846.104 | 1767.5 | 0.006987 | 0.0032338 | 8.14e-05 | 0.086618 | 0.049136 | 0.0086618 | 0.0027506 | 5000000 | scaled
CB 242 | 406818.4113 | 261841.2817 | 142457.8125 | 2519.317 | 64.36% | 35.02% | 0.6193% | 215046.1152 | 389171.4312 | 10467.0599 | 86019.4688 | 118559.5865 | 17619.6774 | 174363.6475 | 197188.1064 | 242 |  | 1486 | CB 242 | 406818.4113 | 191772.296 | 17646.98 | 261841.2817 | 109207.0647 | 2487.4095 | 142457.8125 | 80045.9143 | 12640.2535 | 2519.317 | 17804.2663 | 7337.2064 | 184.5889 | 17546.7521 | 7191.6806 | 160.0122 | 255.6185 | 143.63 | 22.681 | 1.8957 | 200230.1124 | 81670.5259 | 3042.0061 | 186146.5785 | 73656.8361 | 1583.8268 | 13854.6774 | 7784.8333 | 1229.3228 | 228.8565 | 188784.0326 | 102764.5638 | 14420.3851 | 58147.9511 | 28358.5479 | 743.5705 | 128347.5166 | 72117.451 | 11388.2497 | 2288.5648 | 0.008669 | 0.0041212 | 0.0001054 | 0.089175 | 0.050586 | 0.0089174 | 0.0035608 | 5000000 | scaled
CB 243 | 284280.8232 | 261821.2333 | 20261.2733 | 2198.3166 | 92.1% | 7.127% | 0.7733% | 101932.1238 | 276073.0408 | 9628.7134 | 20077.5607 | 72225.8497 | 26144.8305 | 53566.1177 | 196362.0926 | 243 |  | 1487 | CB 243 | 284280.8232 | 182348.6994 | 8207.7824 | 261821.2333 | 168926.8904 | 4558.3655 | 20261.2733 | 11223.4925 | 1451.1003 | 2198.3166 | 26621.4777 | 16992.7643 | 476.6472 | 26581.4312 | 16969.8432 | 472.2434 | 38.3923 | 21.267 | 2.7496 | 1.6542 | 200184.8345 | 127958.9848 | 3822.7419 | 198187.7394 | 126763.6406 | 3494.3167 | 1797.3985 | 995.6476 | 128.7286 | 199.6966 | 57474.511 | 37396.9503 | 3908.3932 | 37052.0627 | 25193.4066 | 591.8054 | 18425.4824 | 10206.5779 | 1319.622 | 1996.9658 | 0.011686 | 0.0066602 | 0.0001694 | 0.024497 | 0.01391 | 0.0024496 | 0.0031052 | 5000000 | scaled
CB 244 | 295550.8103 | 110842.2141 | 181440.687 | 3267.9092 | 37.5% | 61.39% | 1.106% | 147288.7127 | 278345.4574 | 3022.8767 | 114350.3091 | 29915.5269 | 5007.249 | 222531.3807 | 50806.8278 | 244 |  | 1488 | CB 244 | 295550.8103 | 148262.0976 | 17205.3529 | 110842.2141 | 44593.9113 | 956.7368 | 181440.687 | 100400.2772 | 12980.7068 | 3267.9092 | 5079.8803 | 2057.0036 | 72.6313 | 4826.7238 | 1915.821 | 52.2368 | 250.6976 | 138.7236 | 17.9355 | 2.459 | 52541.4401 | 22625.9131 | 1734.6123 | 37079.401 | 13937.3956 | 352.7995 | 15165.1799 | 8391.6584 | 1084.9538 | 296.8591 | 237929.4899 | 123579.1809 | 15398.1092 | 68936.0893 | 28740.6946 | 551.7006 | 166024.8095 | 91869.8951 | 11877.8176 | 2968.5911 | 0.011693 | 0.0053192 | 0.0001356 | 0.024275 | 0.013772 | 0.0024276 | 0.0047006 | 5000000 | scaled
CB 245 | 248324.7054 | 75144.5628 | 169218.9876 | 3961.1549 | 30.26% | 68.14% | 1.595% | 114504.4131 | 231845.0576 | 4159.5241 | 83478.9016 | 26865.9875 | 8041.1412 | 170284.2936 | 53519.6227 | 245 |  | 1489 | CB 245 | 248324.7054 | 133820.2923 | 16479.6478 | 75144.5628 | 36130.0232 | 414.9878 | 169218.9876 | 93729.1142 | 12103.5051 | 3961.1549 | 8102.5166 | 3942.9925 | 61.3754 | 7826.8728 | 3788.9858 | 38.8923 | 272.6632 | 151.0261 | 19.5024 | 2.9806 | 55049.9911 | 28184.0036 | 1530.3684 | 40591.2937 | 20014.9161 | 162.1034 | 14098.8634 | 7809.2535 | 1008.431 | 359.834 | 185172.1977 | 101693.2962 | 14887.9041 | 26726.3963 | 12326.1213 | 213.9921 | 154847.4611 | 85768.8346 | 11075.5717 | 3598.3403 | 0.014722 | 0.0064326 | 0.000164 | 0.024349 | 0.013826 | 0.002435 | 0.0055658 | 5000000 | scaled
CB 246 | 1438441.8634 | 1294643.4277 | 136220.2784 | 7578.1573 | 90% | 9.47% | 0.5268% | 612940.6424 | 1397217.6633 | 74374.459 | 64643.0679 | 473923.1155 | 170509.9471 | 158921.5469 | 1067786.1693 | 246 |  | 1490 | CB 246 | 1438441.8634 | 825501.221 | 41224.2 | 1294643.4277 | 742459.6951 | 23901.3896 | 136220.2784 | 75463.3686 | 9744.6531 | 7578.1573 | 173643.9211 | 99269.4621 | 3133.974 | 173432.9308 | 99150.0343 | 3113.5862 | 205.288 | 113.7255 | 14.6855 | 5.7023 | 1089216.5405 | 615293.425 | 21430.3712 | 1076238.9714 | 607797.0636 | 19862.8486 | 12289.1642 | 6807.9565 | 879.1176 | 688.405 | 175581.4017 | 110938.3338 | 16659.8548 | 44971.5255 | 35512.5972 | 924.9547 | 123725.8262 | 68541.6866 | 8850.8501 | 6884.05 | 0.031403 | 0.018473 | 0.0004692 | 0.024445 | 0.013884 | 0.0024444 | 0.010583 | 5000000 | scaled
CB 247 | 379742.3425 | 266881.3984 | 110164.8695 | 2696.0746 | 70.28% | 29.01% | 0.71% | 149661.5969 | 361440.7864 | 11162.9487 | 52737.2459 | 85761.4023 | 28772.9747 | 120280.8663 | 212386.9453 | 247 |  | 1491 | CB 247 | 379742.3425 | 230080.7457 | 18301.5562 | 266881.3984 | 166410.1636 | 7722.3612 | 110164.8695 | 60974.5074 | 7883.1203 | 2696.0746 | 29606.4061 | 18443.4574 | 833.4313 | 29403.0992 | 18330.0245 | 816.9997 | 201.2781 | 111.4043 | 14.403 | 2.0287 | 219736.2877 | 133974.8854 | 7349.3424 | 209918.1777 | 128431.3596 | 6419.3953 | 9573.1967 | 5298.6125 | 685.0338 | 244.9133 | 130399.6488 | 77662.4029 | 10118.7825 | 27560.1215 | 19648.7796 | 485.9663 | 100390.3947 | 55564.4907 | 7183.6836 | 2449.1326 | 0.010281 | 0.0064146 | 0.0001622 | 0.024494 | 0.013899 | 0.0024494 | 0.0037918 | 5000000 | scaled
CB 248 | 962152.7105 | 957350.6463 | 0 | 4802.0642 | 99.5% | 0% | 0.4991% | 319323.2765 | 948391.997 | 21135.7845 | 10.5789 | 298176.9131 | 62377.0726 | 28.5422 | 885986.3823 | 248 |  | 1492 | CB 248 | 962152.7105 | 642829.434 | 13760.7134 | 957350.6463 | 638027.3698 | 8958.6493 | 0 | 0 | 0 | 4802.0642 | 63007.8696 | 41872.0851 | 630.797 | 63004.2562 | 41868.4717 | 627.1836 | 0 | 0 | 0 | 3.6134 | 894753.6077 | 596576.6946 | 8767.2254 | 894317.3849 | 596140.4718 | 8331.0026 | 0 | 0 | 0 | 436.2228 | 4391.2332 | 4380.6543 | 4362.691 | 29.0052 | 18.4263 | 0.46306 | 0 | 0 | 0 | 4362.228 | 0.012069 | 0.007681 | 0.0001948 | 0 | 0 | 0 | 0.0067416 | 5000000 | scaled
CB 249 | 826920.825 | 802439.1199 | 22096.7151 | 2384.99 | 97.04% | 2.672% | 0.2884% | 352875.195 | 812387.6758 | 20482.265 | 12034.3314 | 320358.5986 | 47446.6848 | 28232.2218 | 736708.7691 | 249 |  | 1493 | CB 249 | 826920.825 | 474045.63 | 14533.1492 | 802439.1199 | 459341.5038 | 10384.7763 | 22096.7151 | 12319.1362 | 1763.3829 | 2384.99 | 48119.1674 | 27636.9024 | 672.4826 | 48016.5511 | 27578.8987 | 662.6421 | 100.8217 | 56.2091 | 8.0459 | 1.7946 | 746703.1265 | 426344.5279 | 9994.3574 | 743643.8003 | 424543.0561 | 9550.8497 | 2842.672 | 1584.8176 | 226.8536 | 216.6541 | 32098.5311 | 20064.1997 | 3866.3092 | 10778.7684 | 7219.5489 | 171.2845 | 19153.2214 | 10678.1095 | 1528.4834 | 2166.5413 | 0.011314 | 0.0067512 | 0.000172 | 0.044374 | 0.02517 | 0.0044374 | 0.0033716 | 5000000 | scaled
CB 254 | 875.5669 | 748.9444 | 0 | 126.6226 | 85.54% | 0% | 14.46% | 457.416 | 748.6942 | 50.5405 | 16.1918 | 390.6838 | 83.9042 | 28.1564 | 636.6336 | 254 |  | 1494 | CB 254 | 875.5669 | 418.1509 | 126.8728 | 748.9444 | 291.5283 | 0.25023 | 0 | 0 | 0 | 126.6226 | 83.9995 | 33.459 | 0.095279 | 83.9042 | 33.3638 | 0 | 0 | 0 | 0 | 0.095279 | 648.136 | 257.4523 | 11.5025 | 636.6336 | 245.9498 | 0 | 0 | 0 | 0 | 11.5025 | 143.4314 | 127.2396 | 115.275 | 28.4066 | 12.2148 | 0.25023 | 0 | 0 | 0 | 115.0248 | 0.0004028 | 0.0001746 | 4.4e-06 | 0 | 0 | 0 | 0.0001864 | 5000000 | scaled
CB 255 | 32280.1469 | 28172.8076 | 0 | 4107.3393 | 87.28% | 0% | 12.72% | 14348.7504 | 27817.3638 | 35.5473 | 14132.4836 | 180.7195 | 59.4053 | 27455.9549 | 302.0037 | 255 |  | 1495 | CB 255 | 32280.1469 | 17931.3965 | 4462.783 | 28172.8076 | 13824.0572 | 355.4437 | 0 | 0 | 0 | 4107.3393 | 63.226 | 27.6787 | 3.8208 | 60.1354 | 24.5881 | 0.73014 | 0 | 0 | 0 | 3.0906 | 678.8669 | 498.1474 | 376.8632 | 305.7534 | 125.0339 | 3.7497 | 0 | 0 | 0 | 373.1135 | 31538.0539 | 17405.5704 | 4082.099 | 27806.9188 | 13674.4352 | 350.9639 | 0 | 0 | 0 | 3731.1352 | 0.010991 | 0.0049814 | 0.0001258 | 0 | 0 | 0 | 0.0057564 | 5000000 | scaled
CB 256 | 11439.3068 | 8907.9222 | 0 | 2531.3846 | 77.87% | 0% | 22.13% | 4145.289 | 8798.2586 | 112.3124 | 3514.4001 | 518.5764 | 210.7811 | 7611.4918 | 975.9857 | 256 |  | 1496 | CB 256 | 11439.3068 | 7294.0178 | 2641.0482 | 8907.9222 | 4762.6332 | 109.6636 | 0 | 0 | 0 | 2531.3846 | 213.7268 | 101.4143 | 2.9457 | 211.822 | 99.5095 | 1.0409 | 0 | 0 | 0 | 1.9048 | 1211.0336 | 692.4571 | 235.0479 | 981.0809 | 462.5044 | 5.0952 | 0 | 0 | 0 | 229.9527 | 10014.5465 | 6500.1464 | 2403.0546 | 7715.0193 | 4200.6192 | 103.5275 | 0 | 0 | 0 | 2299.5271 | 0.0080652 | 0.0039328 | 0.0001002 | 0 | 0 | 0 | 0.0035726 | 5000000 | scaled
CB 257 | 24507.9173 | 18853.7915 | 0 | 5654.1258 | 76.93% | 0% | 23.07% | 8960.0079 | 18603.7103 | 16.834 | 8854.1263 | 89.0476 | 25.8446 | 18440.9226 | 136.943 | 257 |  | 1497 | CB 257 | 24507.9173 | 15547.9094 | 5904.207 | 18853.7915 | 9893.7836 | 250.0812 | 0 | 0 | 0 | 5654.1258 | 30.0992 | 13.2651 | 4.2545 | 25.8446 | 9.0106 | 0 | 0 | 0 | 0 | 4.2545 | 650.5677 | 561.5201 | 513.6247 | 136.943 | 47.8955 | 0 | 0 | 0 | 0 | 513.6247 | 23827.2504 | 14973.1241 | 5386.3278 | 18691.0038 | 9836.8775 | 250.0812 | 0 | 0 | 0 | 5136.2466 | 0.013591 | 0.0064862 | 0.0001656 | 0 | 0 | 0 | 0.007944 | 5000000 | scaled
CB 258 | 175.3575 | 0.84879 | 0 | 174.5087 | 0.484% | 0% | 99.52% | 0.59977 | 0.84694 | 0.080008 | 0.11142 | 0.40835 | 0.10681 | 0.1947 | 0.54543 | 258 |  | 1498 | CB 258 | 175.3575 | 174.7577 | 174.5105 | 0.84879 | 0.24902 | 0.0018508 | 0 | 0 | 0 | 174.5087 | 0.23812 | 0.15811 | 0.13131 | 0.10681 | 0.026801 | 0 | 0 | 0 | 0 | 0.13131 | 16.3979 | 15.9896 | 15.8525 | 0.54543 | 0.13708 | 0 | 0 | 0 | 0 | 15.8525 | 158.7214 | 158.61 | 158.5267 | 0.19655 | 0.085136 | 0.0018508 | 0 | 0 | 0 | 158.5249 | 0.0001062 | 4.6e-05 | 1e-06 | 0 | 0 | 0 | 0.0002452 | 5000000 | scaled
CB 261 | 8776.6631 | 7522.9355 | 0 | 1253.7276 | 85.72% | 0% | 14.28% | 3895.1254 | 7473.4877 | 401.8672 | 663.1617 | 2830.0966 | 758.158 | 1259.5299 | 5455.7998 | 261 |  | 1499 | CB 261 | 8776.6631 | 4881.5376 | 1303.1754 | 7522.9355 | 3627.8101 | 49.4478 | 0 | 0 | 0 | 1253.7276 | 764.0447 | 362.1775 | 5.8867 | 763.1013 | 361.2341 | 4.9433 | 0 | 0 | 0 | 0.94339 | 5600.5573 | 2770.4607 | 144.7575 | 5486.6678 | 2656.5712 | 30.868 | 0 | 0 | 0 | 113.8895 | 2412.0611 | 1748.8994 | 1152.5312 | 1273.1664 | 610.0047 | 13.6365 | 0 | 0 | 0 | 1138.8947 | 0.003675 | 0.0016842 | 4.26e-05 | 0 | 0 | 0 | 0.0017602 | 5000000 | scaled
CB 262 | 8112.5271 | 7147.1215 | 0 | 965.4057 | 88.1% | 0% | 11.9% | 2640.8433 | 7082.4959 | 242.6987 | 889.1426 | 1509.002 | 656.1697 | 2291.4926 | 4134.8336 | 262 |  | 1500 | CB 262 | 8112.5271 | 5471.6839 | 1030.0312 | 7147.1215 | 4506.2782 | 64.6255 | 0 | 0 | 0 | 965.4057 | 660.8904 | 418.1917 | 4.7208 | 660.164 | 417.4653 | 3.9943 | 0 | 0 | 0 | 0.72644 | 4246.0927 | 2737.0907 | 111.259 | 4158.3946 | 2649.3926 | 23.5609 | 0 | 0 | 0 | 87.6981 | 3205.544 | 2316.4014 | 914.0514 | 2328.5629 | 1439.4203 | 37.0703 | 0 | 0 | 0 | 876.9811 | 0.0035606 | 0.0022704 | 5.76e-05 | 0 | 0 | 0 | 0.0013574 | 5000000 | scaled
CB 263 | 5064.1935 | 4140.3274 | 0 | 923.8661 | 81.76% | 0% | 18.24% | 1818.4124 | 4063.6754 | 227.8676 | 6.6747 | 1583.8701 | 500.8527 | 12.9058 | 3549.9168 | 263 |  | 1501 | CB 263 | 5064.1935 | 3245.7811 | 1000.5182 | 4140.3274 | 2321.915 | 76.6521 | 0 | 0 | 0 | 923.8661 | 511.1972 | 283.3296 | 10.3445 | 510.502 | 282.6344 | 9.6493 | 0 | 0 | 0 | 0.69518 | 3700.6846 | 2116.8145 | 150.7678 | 3616.76 | 2032.8899 | 66.8431 | 0 | 0 | 0 | 83.9246 | 852.3117 | 845.637 | 839.4059 | 13.0655 | 6.3908 | 0.15966 | 0 | 0 | 0 | 839.2463 | 0.0032754 | 0.0016784 | 4.26e-05 | 0 | 0 | 0 | 0.001275 | 5000000 | scaled
CB 266 | 30627.2919 | 29687.3658 | 0 | 939.9261 | 96.93% | 0% | 3.069% | 11893.656 | 29256.3297 | 238.9798 | 10374.7412 | 1279.9349 | 506.9755 | 26034.9403 | 2714.4138 | 266 |  | 1502 | CB 266 | 30627.2919 | 18733.636 | 1370.9622 | 29687.3658 | 17793.7099 | 431.0361 | 0 | 0 | 0 | 939.9261 | 512.5946 | 273.6147 | 5.619 | 511.8873 | 272.9075 | 4.9118 | 0 | 0 | 0 | 0.70726 | 2826.1431 | 1546.2082 | 111.7293 | 2740.7596 | 1460.8247 | 26.3458 | 0 | 0 | 0 | 85.3835 | 27288.5542 | 16913.813 | 1253.6139 | 26434.7189 | 16059.9777 | 399.7786 | 0 | 0 | 0 | 853.8353 | 0.0039834 | 0.0024304 | 6.22e-05 | 0 | 0 | 0 | 0.0013156 | 5000000 | scaled
CB 270 | 71458.8354 | 11377.2296 | 58823.6324 | 1257.9734 | 15.92% | 82.32% | 1.76% | 32899.6331 | 66038.1844 | 723.2406 | 24464.7576 | 7711.6349 | 1246.8308 | 50893.0547 | 13898.2988 | 270 |  | 1503 | CB 270 | 71458.8354 | 38559.2024 | 5420.651 | 11377.2296 | 4832.5404 | 198.8095 | 58823.6324 | 32468.6885 | 3963.8681 | 1257.9734 | 1273.9634 | 550.7228 | 27.1326 | 1194.5389 | 506.459 | 20.8977 | 78.4779 | 43.3172 | 5.2883 | 0.94658 | 14520.4833 | 6808.8485 | 622.1845 | 9362.1191 | 3910.4039 | 168.0101 | 5044.089 | 2784.1694 | 339.8992 | 114.2752 | 55664.3887 | 31199.6311 | 4771.334 | 820.5715 | 415.6775 | 9.9016 | 53701.0655 | 29641.202 | 3618.6807 | 1142.7517 | 0.005089 | 0.0022738 | 5.76e-05 | 0.0073438 | 0.0041692 | 0.0007344 | 0.0017672 | 5000000 | scaled
CB 274 | 104808.8717 | 292.7475 | 104407.8676 | 108.2566 | 0.2793% | 99.62% | 0.1033% | 46810.7135 | 97733.95 | 65.68 | 42636.6901 | 4108.3435 | 132.6994 | 89041.1148 | 8560.1358 | 274 |  | 1504 | CB 274 | 104808.8717 | 57998.1582 | 7074.9217 | 292.7475 | 120.1397 | 2.5067 | 104407.8676 | 57769.7619 | 6964.1584 | 108.2566 | 141.3954 | 75.7155 | 8.6961 | 12.1624 | 4.1733 | 0 | 129.1516 | 71.4607 | 8.6146 | 0.08146 | 9177.2285 | 5068.885 | 617.0926 | 63.2692 | 21.6609 | 0 | 9104.1252 | 5037.39 | 607.2585 | 9.8341 | 95490.2478 | 52853.5577 | 6449.133 | 217.3159 | 94.3054 | 2.5067 | 95174.5908 | 52660.9112 | 6348.2852 | 98.341 | 0.0002712 | 0.0001176 | 3e-06 | 0.014557 | 0.0082868 | 0.0014558 | 0.0001522 | 5000000 | scaled
CB 275 | 206623.495 | 94736.6978 | 110211.7033 | 1675.0939 | 45.85% | 53.34% | 0.8107% | 80088.5375 | 196215.7331 | 1125.4256 | 67248.7352 | 11714.3767 | 3666.9897 | 159765.0558 | 32783.6875 | 275 |  | 1505 | CB 275 | 206623.495 | 126534.9575 | 10407.762 | 94736.6978 | 63955.4768 | 1383.2066 | 110211.7033 | 60904.3868 | 7349.4614 | 1675.0939 | 3735.655 | 2610.2293 | 68.6652 | 3487.7088 | 2472.6472 | 50.9546 | 246.6857 | 136.3216 | 16.4502 | 1.2605 | 34141.8706 | 22427.4939 | 1358.1831 | 20256.4071 | 14686.133 | 290.2123 | 13733.2968 | 7589.1942 | 915.8041 | 152.1667 | 168745.9695 | 101497.2343 | 8980.9136 | 70992.5818 | 46796.6966 | 1042.0398 | 96231.7208 | 53178.871 | 6417.207 | 1521.6668 | 0.0081454 | 0.0048258 | 0.000134 | 0.014589 | 0.008295 | 0.0014588 | 0.0023188 | 5000000 | scaled
CB 276 | 26079.268 | 14068.1278 | 11056.8005 | 954.3397 | 53.94% | 42.4% | 3.659% | 11773.7556 | 24213.9038 | 109.5223 | 10730.1102 | 934.1231 | 213.5718 | 22126.4045 | 1873.9275 | 276 |  | 1506 | CB 276 | 26079.268 | 14305.5124 | 1865.3642 | 14068.1278 | 7230.6802 | 173.5535 | 11056.8005 | 6120.4925 | 737.4709 | 954.3397 | 217.6765 | 108.1541 | 4.1046 | 206.9158 | 101.877 | 2.7167 | 10.0426 | 5.5591 | 0.66982 | 0.71811 | 2033.4362 | 1099.3131 | 159.5087 | 1064.371 | 524.183 | 13.963 | 882.3723 | 488.4373 | 58.8528 | 86.6929 | 23828.1554 | 13098.0452 | 1701.7509 | 12796.8411 | 6604.6203 | 156.8739 | 10164.3856 | 5626.4962 | 677.9483 | 866.9287 | 0.0034876 | 0.001777 | 4.48e-05 | 0.014704 | 0.0083738 | 0.0014704 | 0.0013486 | 5000000 | scaled
CB 277 | 9242.0774 | 8892.4168 | 0 | 349.6606 | 96.22% | 0% | 3.783% | 5029.8637 | 8798.0529 | 13.6185 | 4946.258 | 69.9872 | 25.9992 | 8638.4255 | 133.6282 | 277 |  | 1507 | CB 277 | 9242.0774 | 4212.2137 | 444.0245 | 8892.4168 | 3862.5531 | 94.3639 | 0 | 0 | 0 | 349.6606 | 26.2623 | 12.6438 | 0.26311 | 25.9992 | 12.3807 | 0 | 0 | 0 | 0 | 0.26311 | 165.3916 | 95.4044 | 31.7634 | 133.6282 | 63.641 | 0 | 0 | 0 | 0 | 31.7634 | 9050.4235 | 4104.1655 | 411.998 | 8732.7895 | 3786.5315 | 94.3639 | 0 | 0 | 0 | 317.634 | 0.00118 | 0.000511 | 1.3e-05 | 0 | 0 | 0 | 0.0004902 | 5000000 | scaled
CB 279 | 90028.008 | 17657.2647 | 69494.9128 | 2875.8305 | 19.61% | 77.19% | 3.194% | 40519.5989 | 82336.922 | 118.9702 | 37462.9664 | 2937.6623 | 225.5315 | 76096.0188 | 6015.3717 | 279 |  | 1508 | CB 279 | 90028.008 | 49508.4091 | 7691.086 | 17657.2647 | 8206.7802 | 180.1193 | 69494.9128 | 38425.7984 | 4635.1361 | 2875.8305 | 234.2774 | 115.3072 | 8.7459 | 135.7176 | 59.8431 | 0.15253 | 96.3958 | 53.3001 | 6.4294 | 2.164 | 6657.5555 | 3719.8932 | 642.1838 | 696.4737 | 307.0405 | 0.7764 | 5699.8393 | 3151.6102 | 380.165 | 261.2424 | 83136.1752 | 45673.2087 | 7040.1564 | 16825.0734 | 7839.8965 | 179.1904 | 63698.6776 | 35220.8881 | 4248.5418 | 2612.4242 | 0.0094576 | 0.0041788 | 0.0001062 | 0.014708 | 0.0083672 | 0.0014708 | 0.0041166 | 5000000 | scaled
CB 280 | 310796.8025 | 50007.0136 | 258225.3736 | 2564.4153 | 16.09% | 83.08% | 0.8251% | 136681.4972 | 286544.076 | 1219.1988 | 119196.0825 | 16266.2159 | 2743.6232 | 247597.4355 | 36203.0173 | 280 |  | 1509 | CB 280 | 310796.8025 | 174115.3053 | 24252.7265 | 50007.0136 | 28723.9676 | 2381.8567 | 258225.3736 | 142826.9224 | 19306.4545 | 2564.4153 | 2931.7708 | 1712.572 | 188.1476 | 2534.4705 | 1491.9591 | 156.6577 | 395.3706 | 218.6833 | 29.5602 | 1.9296 | 39741.471 | 23475.2552 | 3538.4538 | 17575.7037 | 11111.0528 | 1665.6738 | 21932.8141 | 12131.2491 | 1639.8268 | 232.9532 | 268123.5607 | 148927.4782 | 20526.1252 | 29896.8393 | 16120.9557 | 559.5252 | 235897.1889 | 130476.9901 | 17637.0675 | 2329.5324 | 0.0091484 | 0.0044166 | 0.000113 | 0.029662 | 0.016777 | 0.0029662 | 0.0035986 | 5000000 | scaled
CB 281 | 131322.8593 | 1504.0306 | 126538.5243 | 3280.3044 | 1.145% | 96.36% | 2.498% | 57314.9222 | 118560.4965 | 80.1964 | 52660.9144 | 4573.8114 | 166.1298 | 108911.6753 | 9482.6914 | 281 |  | 1510 | CB 281 | 131322.8593 | 74007.9371 | 12762.3628 | 1504.0306 | 652.3956 | 16.1377 | 126538.5243 | 70075.2371 | 9465.9207 | 3280.3044 | 181.8295 | 101.6331 | 15.6997 | 2.487 | 1.2143 | 0 | 176.8742 | 97.9504 | 13.2314 | 2.4683 | 10546.3754 | 5972.5641 | 1063.684 | 12.681 | 6.1885 | 0 | 10235.7093 | 5668.3904 | 765.6989 | 297.9851 | 120594.6543 | 67933.7399 | 11682.9791 | 1488.8627 | 644.9927 | 16.1377 | 116125.9407 | 64308.8962 | 8686.9904 | 2979.851 | 0.012207 | 0.0052858 | 0.0001336 | 0.030002 | 0.016986 | 0.0030002 | 0.0046294 | 5000000 | scaled
CB 282 | 152506.8923 | 7242.3735 | 144094.4419 | 1170.077 | 4.749% | 94.48% | 0.7672% | 68227.2591 | 140492.5631 | 140.1217 | 60332.5627 | 7754.5747 | 279.9461 | 124203.4575 | 16009.1595 | 282 |  | 1511 | CB 282 | 152506.8923 | 84279.6332 | 12014.3293 | 7242.3735 | 3375.8295 | 68.5626 | 144094.4419 | 79733.7267 | 10775.6897 | 1170.077 | 293.7882 | 153.6664 | 13.842 | 119.5832 | 56.878 | 0 | 173.3245 | 95.908 | 12.9616 | 0.88045 | 17359.3025 | 9604.7277 | 1350.143 | 619.9963 | 294.6657 | 0 | 16633.0155 | 9203.7715 | 1243.8524 | 106.2906 | 134853.8017 | 74521.2391 | 10650.3443 | 6502.794 | 3024.2859 | 68.5626 | 127288.1018 | 70434.0472 | 9518.8758 | 1062.9059 | 0.0038878 | 0.0018166 | 4.62e-05 | 0.030046 | 0.016999 | 0.0030046 | 0.0016394 | 5000000 | scaled
CB 283 | 6045.1476 | 6009.7428 | 0 | 35.4048 | 99.41% | 0% | 0.5857% | 922.4918 | 6009.2397 | 55.6183 | 9.6479 | 857.2256 | 330.8543 | 40.7439 | 5637.6416 | 283 |  | 1512 | CB 283 | 6045.1476 | 5122.6557 | 35.9078 | 6009.7428 | 5087.2509 | 0.50304 | 0 | 0 | 0 | 35.4048 | 330.8809 | 275.2626 | 0.026641 | 330.8543 | 275.236 | 0 | 0 | 0 | 0 | 0.026641 | 5640.8578 | 4783.6321 | 3.2162 | 5637.6416 | 4780.4159 | 0 | 0 | 0 | 0 | 3.2162 | 73.4089 | 63.761 | 32.665 | 41.2469 | 31.599 | 0.50304 | 0 | 0 | 0 | 32.1619 | 2.94e-05 | 2.24e-05 | 6e-07 | 0 | 0 | 0 | 4.66e-05 | 5000000 | scaled
CB 284 | 126880.6737 | 60797.6641 | 63880.6967 | 2202.3129 | 47.92% | 50.35% | 1.736% | 56726.9099 | 120033.5691 | 1895.7253 | 37919.5916 | 16911.593 | 3912.0039 | 81122.1336 | 34999.4316 | 284 |  | 1513 | CB 284 | 126880.6737 | 70153.7638 | 6847.1046 | 60797.6641 | 32483.4278 | 382.585 | 63880.6967 | 35468.0231 | 4262.2067 | 2202.3129 | 3939.2208 | 2043.4955 | 27.2169 | 3860.3293 | 1998.9561 | 20.4065 | 77.2344 | 42.8823 | 5.1532 | 1.6572 | 35733.2504 | 18821.6574 | 733.8189 | 29314.4769 | 15168.8257 | 118.8382 | 6218.7139 | 3452.7721 | 414.921 | 200.0596 | 87208.2025 | 49288.6108 | 6086.0689 | 27622.8579 | 15315.646 | 243.3402 | 57584.7484 | 31972.3687 | 3842.1325 | 2000.5961 | 0.0052396 | 0.0027258 | 6.94e-05 | 0.004876 | 0.0027846 | 0.0004876 | 0.0030944 | 5000000 | scaled
CB 286 | 207241.2445 | 136058.0537 | 61220.7604 | 9962.4303 | 65.65% | 29.54% | 4.807% | 106090.5079 | 191435.744 | 7624.9034 | 56881.0038 | 41584.6007 | 12807.4985 | 108478.2048 | 70150.0406 | 286 |  | 1514 | CB 286 | 207241.2445 | 101150.7366 | 15805.5006 | 136058.0537 | 57141.6143 | 1758.0029 | 61220.7604 | 34046.6919 | 4085.0673 | 9962.4303 | 13000.695 | 5375.7916 | 193.1965 | 12916.5424 | 5325.6644 | 180.5851 | 76.6562 | 42.6308 | 5.115 | 7.4964 | 72359.4337 | 30774.833 | 2209.3931 | 65941.2478 | 26803.7885 | 936.5213 | 5513.192 | 3066.0506 | 367.8778 | 904.994 | 121881.1158 | 65000.1119 | 13402.911 | 57200.2636 | 25012.1614 | 640.8966 | 55630.9123 | 30938.0105 | 3712.0744 | 9049.9399 | 0.02699 | 0.011901 | 0.0003152 | 0.0048756 | 0.0027886 | 0.0004876 | 0.013998 | 5000000 | scaled
CB 287 | 114667.6367 | 82479.405 | 29217.7449 | 2970.4868 | 71.93% | 25.48% | 2.591% | 53206.4142 | 108827.0192 | 1080.1082 | 44590.4654 | 7535.8406 | 2151.9385 | 91479.0044 | 15196.0762 | 287 |  | 1515 | CB 287 | 114667.6367 | 61461.2225 | 5840.6175 | 82479.405 | 42256.7947 | 920.9255 | 29217.7449 | 16233.9411 | 1949.2052 | 2970.4868 | 2178.0672 | 1097.959 | 26.1287 | 2142.1945 | 1077.0342 | 21.6494 | 33.6375 | 18.6896 | 2.2441 | 2.2352 | 15834.444 | 8298.6034 | 638.3678 | 11770.9248 | 5920.9218 | 115.4389 | 3793.6782 | 2107.8406 | 253.0879 | 269.8411 | 96655.1255 | 52064.6601 | 5176.121 | 68566.2857 | 35258.8387 | 783.8372 | 25390.4292 | 14107.4109 | 1693.8733 | 2698.4105 | 0.0069378 | 0.0033928 | 8.7e-05 | 0.0048856 | 0.002792 | 0.0004886 | 0.0041424 | 5000000 | scaled
CB 288 | 139689.0353 | 70803.6621 | 62844.0173 | 6041.356 | 50.69% | 44.99% | 4.325% | 63840.2915 | 129108.6771 | 2577.807 | 45200.9094 | 16061.5751 | 5153.8235 | 91136.0325 | 32818.8211 | 288 |  | 1516 | CB 288 | 139689.0353 | 75848.7438 | 10580.3582 | 70803.6621 | 34894.6214 | 346.9799 | 62844.0173 | 34912.7665 | 4192.0223 | 6041.356 | 5175.4693 | 2597.6623 | 21.6458 | 5091.603 | 2549.0502 | 11.8088 | 79.3203 | 44.0661 | 5.2911 | 4.5459 | 33787.5702 | 17725.9952 | 968.7491 | 27735.4313 | 14119.8347 | 52.847 | 5503.3381 | 3057.3595 | 367.1012 | 548.8009 | 100725.9958 | 55525.0864 | 9589.9633 | 37976.6278 | 18225.7364 | 282.3242 | 57261.3589 | 31811.3408 | 3819.63 | 5488.0091 | 0.017749 | 0.0078788 | 0.0001996 | 0.0048452 | 0.0027686 | 0.0004846 | 0.0086276 | 5000000 | scaled
CB 289 | 64738.907 | 25424.3679 | 36010.176 | 3304.3632 | 39.27% | 55.62% | 5.104% | 29106.6563 | 58806.9022 | 477.3608 | 24605.7272 | 4023.5683 | 980.7861 | 49471.1199 | 8354.9962 | 289 |  | 1517 | CB 289 | 64738.907 | 35632.2508 | 5932.0049 | 25424.3679 | 12387.0153 | 225.9768 | 36010.176 | 19940.8723 | 2401.6649 | 3304.3632 | 991.4644 | 514.1036 | 10.6783 | 936.4306 | 482.5187 | 4.6873 | 52.5473 | 29.0984 | 3.5046 | 2.4864 | 8967.999 | 4944.4307 | 613.0028 | 4286.8713 | 2218.2762 | 20.6483 | 4380.957 | 2425.9838 | 292.1838 | 300.1706 | 54779.4437 | 30173.7165 | 5308.3238 | 20201.0659 | 9686.2203 | 200.6412 | 31576.6716 | 17485.79 | 2105.9765 | 3001.7061 | 0.0087182 | 0.0038688 | 9.74e-05 | 0.004867 | 0.0027726 | 0.0004866 | 0.004649 | 5000000 | scaled
CB 292 | 94668.5575 | 62928.3165 | 31170.2759 | 569.9651 | 66.47% | 32.93% | 0.6021% | 38948.0359 | 91296.1961 | 1924.6014 | 12547.9763 | 24475.4582 | 4779.1525 | 26697.7727 | 59819.2709 | 292 |  | 1518 | CB 292 | 94668.5575 | 55720.5216 | 3372.3614 | 62928.3165 | 37782.4271 | 314.1934 | 31170.2759 | 17368.1294 | 2488.2029 | 569.9651 | 4810.7389 | 2886.1376 | 31.5864 | 4760.7137 | 2858.0735 | 27.1984 | 49.5963 | 27.6351 | 3.9591 | 0.42888 | 60611.7411 | 36136.2829 | 792.4702 | 54129.7998 | 32501.6081 | 227.3989 | 6430.1653 | 3582.8988 | 513.2953 | 51.776 | 29246.0775 | 16698.1012 | 2548.3048 | 4037.803 | 2422.7455 | 59.596 | 24690.5142 | 13757.5955 | 1970.9485 | 517.7602 | 0.0029764 | 0.001696 | 4.3e-05 | 0.044343 | 0.025142 | 0.0044342 | 0.0008098 | 5000000 | scaled
CB 295 | 6290.7521 | 6045.4445 | 0 | 245.3076 | 96.1% | 0% | 3.899% | 1672.9856 | 5986.8432 | 74.0264 | 1181.3269 | 417.6323 | 225.4876 | 4514.6531 | 1246.7025 | 295 |  | 1519 | CB 295 | 6290.7521 | 4617.7665 | 303.9089 | 6045.4445 | 4372.4589 | 58.6013 | 0 | 0 | 0 | 245.3076 | 225.6722 | 151.6458 | 0.18459 | 225.4876 | 151.4612 | 0 | 0 | 0 | 0 | 0.18459 | 1268.9864 | 851.3542 | 22.2839 | 1246.7025 | 829.0702 | 0 | 0 | 0 | 0 | 22.2839 | 4796.0935 | 3614.7666 | 281.4404 | 4573.2544 | 3391.9275 | 58.6013 | 0 | 0 | 0 | 222.8391 | 0.0011808 | 0.000757 | 1.92e-05 | 0 | 0 | 0 | 0.000337 | 5000000 | scaled
CB 296 | 39569.8911 | 39259.7779 | 0 | 310.1131 | 99.22% | 0% | 0.7837% | 8649.3211 | 37691.1293 | 588.653 | 3243.5308 | 4817.1373 | 2526.0261 | 13897.7894 | 21267.3139 | 296 |  | 1520 | CB 296 | 39569.8911 | 30920.57 | 1878.7618 | 39259.7779 | 30610.4569 | 1568.6486 | 0 | 0 | 0 | 310.1131 | 2640.1794 | 2051.5264 | 114.1533 | 2639.9461 | 2051.2931 | 113.92 | 0 | 0 | 0 | 0.23335 | 22485.2859 | 17668.1487 | 1217.972 | 22457.115 | 17639.9778 | 1189.8012 | 0 | 0 | 0 | 28.1709 | 14444.4257 | 11200.8949 | 546.6364 | 14162.7168 | 10919.186 | 264.9275 | 0 | 0 | 0 | 281.7089 | 0.0012138 | 0.0008714 | 2.22e-05 | 0 | 0 | 0 | 0.0004444 | 5000000 | scaled
CB 297 | 7428.6087 | 7042.1258 | 0 | 386.4829 | 94.8% | 0% | 5.203% | 1990.0481 | 6963.9048 | 101.0604 | 1274.3535 | 614.6341 | 340.2751 | 4629.2671 | 1994.3627 | 297 |  | 1521 | CB 297 | 7428.6087 | 5438.5606 | 464.7038 | 7042.1258 | 5052.0777 | 78.221 | 0 | 0 | 0 | 386.4829 | 343.1174 | 242.057 | 2.8423 | 342.8266 | 241.7662 | 2.5515 | 0 | 0 | 0 | 0.29082 | 2042.8771 | 1428.2429 | 48.5144 | 2007.7687 | 1393.1346 | 13.406 | 0 | 0 | 0 | 35.1084 | 5042.6142 | 3768.2607 | 413.3471 | 4691.5306 | 3417.177 | 62.2635 | 0 | 0 | 0 | 351.0837 | 0.0014066 | 0.0010684 | 2.68e-05 | 0 | 0 | 0 | 0.0005522 | 5000000 | scaled