## README
Overview: | Appendix G acts as both a source of information for the WMP and a methodological guide to cost-benefit calculations. The intended purpose is to allow the reader to track the calculation methodology of cost-benefit ratios (CBRs) using the formulas within the excel workbook and treat the workbook as a compendium of cost-benefit information. Appendix G contains a README tab, two summary tabs, a tab dedicated to each of the scoped mitigation programs in grid hardening, vegetation management, overhead inspections, system protection, and PSPS categories, and tabs that contain input data for the calculation of cost-benefit ratios. Each mitigation program tab contains measurements, separated by feeder segment and year, of mitigation cost, baseline risk, mitigation risk reduction, and cost-benefit calculations for three separate discount rates. There is also a Likelihood of Risk Event (LoRE) and Cost of Risk Event (CoRE) measurement along with percentage estimations of risk reduction within each feeder segment and total service territory risk reduction. These measurements are summarized for each mitigation program in the CBR Summary By Risk tab. The tabs in the Master Input section contain the raw data used to calculate the measurements and estimations found in the mitigation tabs. This raw data includes output from the WiNGS model, subject matter expert estimations of long-term mitigation costs, historical mitigation costs, and feeder segment mile tracking.
Cost in Cost-Benefit Framework
Lifecycle Costs = One-Time installation costs + Long-term Foundational costs + Long-term Operational Mitigation costs
Term | Units | Definition | Capital / O&M | Inputs | Outputs | Comments
Capital Cost only in Year 0 | M$/mile | This variable represents the upfront investment required to install long-term assets or infrastructure. This cost is assumed to occur entirely at the start of the project (Year 0) and does not recur in future years. | Capital | Cell: K5 | Columns: PV Total Cost, CBR | User-Defined Input Variable to perform sensitivity analysis
Additional Installation Cost (O&M) only in Year 0 | M$/mile | This variable cost is not indicative of ongoing annual O&M activities. Rather, it is a non-capitalizable expense incurred during the installation phase of the mitigation project. As such, it is categorized as an O&M cost and is assumed to be fully realized at the project’s outset (Year 0). Cost estimates for CCC and SUG are based on historical data. | O&M | Cell: K11 | Columns: PV Total Cost, CBR | CCC and SUG estimates are calculated based on historical data
Long-term Foundational costs | M$/mile-year | This cost includes ongoing foundational costs expected over the entire lifespan of the mitigation for programs that support SUG and CCC. For example: weather station maintenance and calibration, Risk methodology and assessment costs. | Capital + O&M | Cell: K8 | Columns: Mitigation Annual Cost, PV Total Cost, CBR | The cost is calculated using forecasted units and cost data from the RAMP tables. It is normalized by HFTD miles and allocated to SUG and CCC based on SME-defined criteria to reflect the relative impact on each potential mitigation.
Long-term Operational Mitigation costs | M$/mile-year | This cost includes ongoing mitigation activities associated with CCC and SUG needed during the lifetime of the asset (i.e., 55 years) For example: Asset inspections, Vegetation activities, EFD and FCP O&M costs | O&M | Tab: SUG&CCC_long_term_ogm_costs | Columns: Mitigation Annual Cost, PV Total Cost, CBR | Feeder-segment-specific mitigation cost estimates are derived from historical cost data and extrapolated to reflect the total cost over the asset’s 55-year lifespan. For modeling purposes, these costs are normalized to a per mile per year ($/mile-year) basis.
Inflation | Dimensionless | Yearly inflation (assumed at 2.5%). | NA | Tab: Inflation_and_Discount | Columns: PV Total Cost, CBR
Discount Rate | Dimensionless | CBR calculations based on the three discount rates as required in the RDF requirements: https://www.sdge.com/sites/default/files/regulatory/Vol1_Ch3_Joint_ERM_Risk_Quantification.pdf | NA | Tab: Inflation_and_Discount | Columns: PV Total Cost, CBR
Equation Definitions
Column |  | Equation |  |  | Output Units | Comments
Mitigation Annual Cost |  | (Long-term Operational Mitigation Costs (K$ / mile-year) + Long-term Foundational Costs (K$ / mile-year)) * Number of Miles (miles) |  |  | K$ / year
PV Total Cost |  | (Number of Miles (miles) * One-time Installation Cost (K$ / mile-year) * Discount Rate) + (Mitigation Annual Cost (K$ / year) * Inflation * Discount Rate) |  |  | K$ / year
CBR Locations |  |  |  | OEIS Table Data Locations
Tab | CBR Column (WACC, HDR, SDR) |  |  | OEIS Table / Column |  | Linked Location in Appendix G
CBR Summary by Risk | K, N, Q |  |  | 6-3 / Cost-Benefit Score - Overall Risk |  | CBR Summary by Risk - Column K
SUG_vs_CCC - SUG | N, Q, T |  |  | 6-3 / Expected % Risk Reduction |  | CBR Summary by Risk - Column V
SUG_vs_CCC - CCC | Z, AC, AF |  |  | 8-1 / % Risk Reduction for 2026 |  | CBR Summary by Risk - Column V
SUG_2028_comp | U, X, AA |  |  | 8-1 / % Risk Reduction for 2027 |  | CBR Summary by Risk - Column V
CCC_2028_comp | U, X, AA |  |  | 8-1 / % Risk Reduction for 2028 |  | CBR Summary by Risk - Column V
SUG | U, X, AA |  |  | 9-2 / % Risk Reduction for 2026 |  | CBR Summary by Risk - Column V
CCC | U, X, AA |  |  | 9-2 / % Risk Reduction for 2027 |  | CBR Summary by Risk - Column V
SPRP | T, W, Z |  |  | 9-2 / % Risk Reduction for 2028 |  | CBR Summary by Risk - Column V
Distribution_Underbuilt | T, W, Z |  |  | 10-1 / % Risk Reduction for all years |  | CBR Summary by Risk - Column V
OH Hardening | T, W, Z
Pole_Clearing | T, W, Z
Fuel_Management | T, W, Z
Trim_and_Removal | T, W, Z
Off_Cycle_Patrol | T, W, Z
Veg_Detail_Inspection | T, W, Z
OH_Patrol | T, W, Z
RIDI | T, W, Z
WoodPole_Intrusive_Primary | T, W, Z
OH_Detail_Inspection | T, W, Z
FCP | U, X, AA
EFD | U, X, AA
Microgrid(Capital) | Z, AC, AF
Service Territory Risk Reduction Locations
Tab | STRR Column
CBR Summary by Risk | V
SUG_vs_CCC - SUG | U
SUG_vs_CCC - CCC | AG
SUG_comp | AM
CCC_comp | AM
SUG | AM
CCC | AM
SPRP | AL
Distribution_Underbuilt | AL
OH Hardening | AL
Pole_Clearing | AL
Fuel_Management | AL
Trim_and_Removal | AL
Off_Cycle_Patrol | AL
Veg_Detail_Inspection | AL
OH_Patrol | AL
RIDI | AL
WoodPole_Intrusive_Primary | AL
OH_Detail_Inspection | AL
FCP | AM
EFD | AM
Microgrid(Capital) | AR

## Index
Summary Tables
README
CBR Summary by Risk
SUG_vs_CCC
Mitigation Workpapers
SUG
CCC
SPRP
Distribution_Underbuilt
OH Hardening
Pole_Clearing
Fuel_Management
Trim_and_Removal
Off_Cycle_Patrol
Veg_Detail_Inspection
OH_Patrol
RIDI
WoodPole_Intrusive_Primary
OH_Detail_Inspection
FCP
EFD
Microgrid(Capital)
WiNGS-Planning
raw_WiNGS_Planning
Inflation_and_Discount
FCP Cost
Microgrid Assumptions
TrancheID
FeederSegment miles
SUG&CCC_long_term_om_costs
Capital_Units&Cost
O&M_Units&Cost

## CBR Summary by Risk
back to index |  |  |  |  | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Link to page | Grid Hardening | Mitigation | YEAR | Mitigation Units | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) | PV Total Cost Capital + O&M (K$) | CBR WACC | PV Risk Reduced (K$) | PV Total Cost Capital + O&M (K$) | CBR HDR | PV Risk Reduced (K$) | PV Total Cost Capital + O&M (K$) | CBR SDR | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigation CoRE | Post-Mitigation CoRE | Service Territory Risk Reduction (%)
Strategic Pole Replacement |  | Strategic Pole Replacement | 2026 | 200 | 98550.2033 | 1326.0872 | 1.346% | 23296.553 | 5259.5998 | 4.4293 | 23296.553 | 5259.5998 | 4.4293 | 58729.9288 | 5540.6275 | 10.5999 | 2.0925 | 2.0604 | 47097.3665 | 47186.4043 | 0.04373%
Strategic Pole Replacement |  | Strategic Pole Replacement | 2027 | 200 | 100008.7722 | 1504.1815 | 1.504% | 25207.9347 | 5017.3009 | 5.0242 | 25207.9347 | 5017.3009 | 5.0242 | 66943.9477 | 5567.7874 | 12.0234 | 1.6876 | 1.6543 | 59262.5261 | 59546.3649 | 0.0496%
Strategic Pole Replacement |  | Strategic Pole Replacement | 2028 | 200 | 81394.9393 | 1107.8034 | 1.361% | 17709.9434 | 4786.1642 | 3.7002 | 17709.9434 | 4786.1642 | 3.7002 | 49544.7312 | 5595.0805 | 8.8551 | 2.0541 | 2.0188 | 39626.1721 | 39769.5393 | 0.03653%
| Total | Strategic Pole Replacement | 2026-2028 | 600 | 279953.9148 | 3938.0722 | 1.407% | 66214.4311 | 15063.0649 | 4.3958 | 66214.4311 | 15063.0649 | 4.3958 | 175218.6077 | 16703.4953 | 10.4899 | 5.8341 | 5.7335 | 47985.7667 | 48141.0117 | 0.1299%
Distribution_Underbuilt |  | Distribution Underbuilt | 2026 | 1.2 | 436.6355 | 14.4962 | 3.32% | 254.6684 | 1002.8739 | 0.25394 | 254.6684 | 1002.8739 | 0.25394 | 642.0115 | 862586.3257 | 0.00074429 | 0.20473 | 0.18432 | 2132.7486 | 2290.2097 | 0.000478%
Distribution_Underbuilt |  | Distribution Underbuilt | 2027 | 7.1 | 1573.1982 | 276.3828 | 17.57% | 4631.7812 | 5660.3187 | 0.81829 | 4631.7812 | 5660.3187 | 0.81829 | 12300.4808 | 5128653.5826 | 0.0023984 | 0.073536 | 0.06018 | 21393.4624 | 21548.8604 | 0.009114%
Distribution_Underbuilt |  | Distribution Underbuilt | 2028 | 3 | 5195.4029 | 83.1538 | 1.601% | 1329.3409 | 2281.504 | 0.58266 | 1329.3409 | 2281.504 | 0.58266 | 3718.9185 | 2177659.4541 | 0.0017078 | 0.42512 | 0.41425 | 12221.0037 | 12340.8614 | 0.002742%
| Total | Distribution Underbuilt | 2026-2028 | 11.3 | 7205.2366 | 374.0328 | 5.191% | 6215.7904 | 8944.6966 | 0.69491 | 6215.7904 | 8944.6966 | 0.69491 | 16661.4108 | 8168899.3623 | 0.0020396 | 0.70339 | 0.65876 | 10243.6422 | 10369.8313 | 0.01233%
Distribution Overhead System Hardening |  | Distribution Overhead System Hardening | 2026 | 6.5934 | 20046.7249 | 812.9708 | 4.055% | 14282.18 | 6550.3476 | 2.1804 | 14282.18 | 6550.3476 | 2.1804 | 36004.9581 | 6902.6224 | 5.2161 | 1.2668 | 1.2027 | 15824.671 | 15992.0559 | 0.02681%
Distribution Overhead System Hardening |  | Distribution Overhead System Hardening | 2027 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
Distribution Overhead System Hardening |  | Distribution Overhead System Hardening | 2028 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Total | Distribution Overhead System Hardening | 2026-2028 | 6.5934 | 20046.7249 | 812.9708 | 4.055% | 14282.18 | 6550.3476 | 2.1804 | 14282.18 | 6550.3476 | 2.1804 | 36004.9581 | 6902.6224 | 5.2161 | 1.2668 | 1.2027 | 15824.671 | 15992.0559 | 0.02681%
Pole_Clearing |  | Pole Clearing | 2026 | 22000 | 2882839.1756 | 139231.1772 | 4.83% | 132817.0839 | 8604.4672 | 15.4358 | 132817.0839 | 8604.4672 | 15.4358 | 139913.683 | 9064.2157 | 15.4358 | 85.8997 | 81.6477 | 33560.5083 | 33603.0002 | 4.591%
Pole_Clearing |  | Pole Clearing | 2027 | 22000 | 2882839.1756 | 139231.1772 | 4.83% | 126698.4746 | 8208.0771 | 15.4358 | 126698.4746 | 8208.0771 | 15.4358 | 140599.5344 | 9108.6481 | 15.4358 | 85.8997 | 81.6477 | 33560.5083 | 33603.0002 | 4.591%
Pole_Clearing |  | Pole Clearing | 2028 | 22000 | 2882839.1756 | 139231.1772 | 4.83% | 120861.7371 | 7829.9479 | 15.4358 | 120861.7371 | 7829.9479 | 15.4358 | 141288.7478 | 9153.2984 | 15.4358 | 85.8997 | 81.6477 | 33560.5083 | 33603.0002 | 4.591%
| Total | Pole Clearing | 2026-2028 | 66000 | 8648517.5267 | 417693.5316 | 4.83% | 380377.2956 | 24642.4923 | 15.4358 | 380377.2956 | 24642.4923 | 15.4358 | 421801.9651 | 27326.1622 | 15.4358 | 257.6992 | 244.9431 | 33560.5083 | 33603.0002 | 13.77%
Fuel_Management |  | Fuel Management | 2026 | 500 | 2126959.604 | 3239.5352 | 0.1523% | 3090.2965 | 5194.1601 | 0.59496 | 3090.2965 | 5194.1601 | 0.59496 | 3255.4153 | 5471.6912 | 0.59496 | 48.9987 | 48.8938 | 43408.4735 | 43435.4019 | 0.1068%
Fuel_Management |  | Fuel Management | 2027 | 500 | 2028961.4705 | 3363.0649 | 0.1658% | 3060.3433 | 4954.8758 | 0.61764 | 3060.3433 | 4954.8758 | 0.61764 | 3396.117 | 5498.5132 | 0.61764 | 48.4724 | 48.3434 | 41858.0701 | 41900.2398 | 0.1109%
Fuel_Management |  | Fuel Management | 2028 | 500 | 2106114.899 | 3270.411 | 0.1553% | 2838.9299 | 4726.6149 | 0.60063 | 2838.9299 | 4726.6149 | 0.60063 | 3318.7414 | 5525.4667 | 0.60063 | 50.7804 | 50.6782 | 41474.9965 | 41494.0974 | 0.1078%
| Total | Fuel Management | 2026-2028 | 1500 | 6262035.9734 | 9873.0111 | 0.1577% | 8989.5697 | 14875.6508 | 0.60431 | 8989.5697 | 14875.6508 | 0.60431 | 9970.2736 | 16495.6711 | 0.60442 | 148.2515 | 147.9153 | 42239.2816 | 42268.5405 | 0.3256%
Trim_and_Removal |  | Trim and Removal | 2026 | 91336 | 2834578.5099 | 136692.5546 | 4.822% | 130395.4104 | 30054.5835 | 4.3386 | 130395.4104 | 30054.5835 | 4.3386 | 137362.6162 | 31660.4412 | 4.3386 | 83.0293 | 78.9194 | 34139.4893 | 34185.3473 | 4.508%
Trim_and_Removal |  | Trim and Removal | 2027 | 91336 | 2834578.5099 | 136692.5546 | 4.822% | 124388.3627 | 28670.0308 | 4.3386 | 124388.3627 | 28670.0308 | 4.3386 | 138035.9623 | 31815.6394 | 4.3386 | 83.0293 | 78.9194 | 34139.4893 | 34185.3473 | 4.508%
Trim_and_Removal |  | Trim and Removal | 2028 | 91336 | 2834578.5099 | 136692.5546 | 4.822% | 118658.0472 | 27349.2616 | 4.3386 | 118658.0472 | 27349.2616 | 4.3386 | 138712.6092 | 31971.5984 | 4.3386 | 83.0293 | 78.9194 | 34139.4893 | 34185.3473 | 4.508%
| Total | Trim and Removal | 2026-2028 | 274008 | 8503735.5297 | 410077.6639 | 4.822% | 373441.8203 | 86073.8759 | 4.3386 | 373441.8203 | 86073.8759 | 4.3386 | 414111.1878 | 95447.679 | 4.3386 | 249.088 | 236.7581 | 34139.4893 | 34185.3473 | 13.52%
Off_Cycle_Patrol |  | Off Cycle Patrol | 2026 | 246834 | 2892488.839 | 139029.6154 | 4.807% | 132624.8076 | 2717.2041 | 48.8093 | 132624.8076 | 2717.2041 | 48.8093 | 139711.1331 | 2862.3881 | 48.8093 | 88.6759 | 84.2864 | 32618.6576 | 32667.8776 | 4.585%
Off_Cycle_Patrol |  | Off Cycle Patrol | 2027 | 246834 | 2892488.839 | 139029.6154 | 4.807% | 126515.0561 | 2592.0281 | 48.8093 | 126515.0561 | 2592.0281 | 48.8093 | 140395.9916 | 2876.4194 | 48.8093 | 88.6759 | 84.2864 | 32618.6576 | 32667.8776 | 4.585%
Off_Cycle_Patrol |  | Off Cycle Patrol | 2028 | 246834 | 2892488.839 | 139029.6154 | 4.807% | 120686.7683 | 2472.6187 | 48.8093 | 120686.7683 | 2472.6187 | 48.8093 | 141084.2073 | 2890.5195 | 48.8093 | 88.6759 | 84.2864 | 32618.6576 | 32667.8776 | 4.585%
| Total | Off Cycle Patrol | 2026-2028 | 740502 | 8677466.5171 | 417088.8462 | 4.807% | 379826.632 | 7781.851 | 48.8093 | 379826.632 | 7781.851 | 48.8093 | 421191.332 | 8629.3269 | 48.8093 | 266.0277 | 252.8593 | 32618.6576 | 32667.8776 | 13.75%
Veg_Detail_Inspection |  | Veg Detail Inspection | 2026 | 485500 | 3016574.4786 | 143144.891 | 4.745% | 136550.501 | 9025.9483 | 15.1287 | 136550.501 | 9025.9483 | 15.1287 | 143846.5817 | 9508.2171 | 15.1287 | 110.1552 | 104.7025 | 27384.7777 | 27443.7596 | 4.72%
Veg_Detail_Inspection |  | Veg Detail Inspection | 2027 | 485500 | 3016574.4786 | 143144.891 | 4.745% | 130259.9009 | 8610.1414 | 15.1287 | 130259.9009 | 8610.1414 | 15.1287 | 144551.712 | 9554.826 | 15.1287 | 110.1552 | 104.7025 | 27384.7777 | 27443.7596 | 4.72%
Veg_Detail_Inspection |  | Veg Detail Inspection | 2028 | 485500 | 3016574.4786 | 143144.891 | 4.745% | 124259.0958 | 8213.49 | 15.1287 | 124259.0958 | 8213.49 | 15.1287 | 145260.2988 | 9601.6633 | 15.1287 | 110.1552 | 104.7025 | 27384.7777 | 27443.7596 | 4.72%
| Total | Veg Detail Inspection | 2026-2028 | 1456500 | 9049723.4358 | 429434.6731 | 4.745% | 391069.4977 | 25849.5796 | 15.1287 | 391069.4977 | 25849.5796 | 15.1287 | 433658.5925 | 28664.7064 | 15.1287 | 330.4655 | 314.1074 | 27384.7777 | 27443.7596 | 14.16%
Distribution Overhead Patrol Inspections |  | Distribution Overhead Patrol Inspections | 2026 | 75135 | 2857247.4849 | 209625.2486 | 7.337% | 199968.2456 | 1047.5537 | 190.8907 | 199968.2456 | 1047.5537 | 190.8907 | 210652.8234 | 1103.5259 | 190.8907 | 87.1263 | 80.3312 | 32794.3111 | 32958.8139 | 6.913%
Distribution Overhead Patrol Inspections |  | Distribution Overhead Patrol Inspections | 2027 | 75135 | 2857247.4849 | 209625.2486 | 7.337% | 190756.1207 | 999.295 | 190.8907 | 190756.1207 | 999.295 | 190.8907 | 211685.4353 | 1108.9354 | 190.8907 | 87.1263 | 80.3312 | 32794.3111 | 32958.8139 | 6.913%
Distribution Overhead Patrol Inspections |  | Distribution Overhead Patrol Inspections | 2028 | 75135 | 2857247.4849 | 209625.2486 | 7.337% | 181968.3795 | 953.2596 | 190.8907 | 181968.3795 | 953.2596 | 190.8907 | 212723.109 | 1114.3713 | 190.8907 | 87.1263 | 80.3312 | 32794.3111 | 32958.8139 | 6.913%
| Total | Distribution Overhead Patrol Inspections | 2026-2028 | 225405 | 8571742.4547 | 628875.7459 | 7.337% | 572692.7457 | 3000.1083 | 190.8907 | 572692.7457 | 3000.1083 | 190.8907 | 635061.3676 | 3326.8326 | 190.8907 | 261.3789 | 240.9937 | 32794.3111 | 32958.8139 | 20.74%
Risk-Informed Drone Inspections |  | Risk-Informed Drone Inspections | 2026 | 9000 | 2645380.3809 | 45262.851 | 1.711% | 43177.6847 | 1004.4905 | 42.9847 | 43177.6847 | 1004.4905 | 42.9847 | 45484.7277 | 1058.1618 | 42.9847 | 71.5245 | 70.0368 | 36985.6553 | 37125.0068 | 1.493%
Risk-Informed Drone Inspections |  | Risk-Informed Drone Inspections | 2027 | 9000 | 2684191.9375 | 57043.7643 | 2.125% | 51909.0485 | 958.2157 | 54.1726 | 51909.0485 | 958.2157 | 54.1726 | 57604.3876 | 1063.3488 | 54.1726 | 74.373 | 72.7504 | 36090.9591 | 36111.8011 | 1.881%
Risk-Informed Drone Inspections |  | Risk-Informed Drone Inspections | 2028 | 9000 | 2741256.7369 | 72415.9785 | 2.642% | 62861.7895 | 914.0726 | 68.7711 | 62861.7895 | 914.0726 | 68.7711 | 73486.1482 | 1068.5613 | 68.7711 | 74.7182 | 72.8916 | 36687.9336 | 36613.855 | 2.388%
| Total | Risk-Informed Drone Inspections | 2026-2028 | 27000 | 8070829.0553 | 174722.5938 | 2.165% | 157948.5227 | 2876.7788 | 54.9046 | 157948.5227 | 2876.7788 | 54.9046 | 176575.2635 | 3190.0719 | 55.3515 | 220.6157 | 215.6788 | 36583.2068 | 36610.4927 | 5.762%
WoodPole_Intrusive_Primary |  | Wood pole Intrusive Primary | 2026 | 1003 | 52450.6146 | 1376.7399 | 2.625% | 1313.3164 | 158.1285 | 8.3054 | 1313.3164 | 158.1285 | 8.3054 | 1383.4887 | 166.5776 | 8.3054 | 1.0153 | 0.97886 | 51661.2513 | 52177.1455 | 0.0454%
WoodPole_Intrusive_Primary |  | Wood pole Intrusive Primary | 2027 | 4906 | 266043.1681 | 10483.3154 | 3.94% | 9539.6742 | 737.8266 | 12.9294 | 9539.6742 | 737.8266 | 12.9294 | 10586.3449 | 818.7792 | 12.9294 | 6.3756 | 6.1076 | 41728.0542 | 41843.1683 | 0.3457%
WoodPole_Intrusive_Primary |  | Wood pole Intrusive Primary | 2028 | 11137 | 889727.5255 | 46524.7302 | 5.229% | 40386.4983 | 1597.7632 | 25.2769 | 40386.4983 | 1597.7632 | 25.2769 | 47212.2767 | 1867.8034 | 25.2769 | 15.3961 | 14.6036 | 57789.0122 | 57739.4053 | 1.534%
| Total | Wood pole Intrusive Primary | 2026-2028 | 17046 | 1208221.3082 | 58384.7855 | 4.832% | 51239.4889 | 2493.7184 | 20.5474 | 51239.4889 | 2493.7184 | 20.5474 | 59182.1103 | 2853.1602 | 20.7427 | 22.7871 | 21.69 | 53022.2574 | 53012.2555 | 1.925%
Distribution Overhead Detailed Inspections |  | Distribution Overhead Detailed Inspections | 2026 | 19874 | 1681774.7952 | 197707.0485 | 11.76% | 188599.0923 | 2624.6339 | 71.8573 | 188599.0923 | 2624.6339 | 71.8573 | 198676.2007 | 2764.8717 | 71.8573 | 34.4047 | 30.2607 | 48882.094 | 49042.7761 | 6.52%
Distribution Overhead Detailed Inspections |  | Distribution Overhead Detailed Inspections | 2027 | 15365 | 887502.8357 | 78280.3388 | 8.82% | 71234.042 | 1935.6795 | 36.8005 | 71234.042 | 1935.6795 | 36.8005 | 79049.6741 | 2148.0578 | 36.8005 | 35.6682 | 31.7581 | 24882.1584 | 25480.8017 | 2.581%
Distribution Overhead Detailed Inspections |  | Distribution Overhead Detailed Inspections | 2028 | 10276 | 605883.9218 | 51400.698 | 8.484% | 44619.1562 | 1234.9303 | 36.1309 | 44619.1562 | 1234.9303 | 36.1309 | 52160.302 | 1443.6475 | 36.1309 | 27.1973 | 23.9105 | 22277.3924 | 23189.9082 | 1.695%
| Total | Distribution Overhead Detailed Inspections | 2026-2028 | 45515 | 3175161.5527 | 327388.0853 | 10.31% | 304452.2905 | 5795.2437 | 52.5349 | 304452.2905 | 5795.2437 | 52.5349 | 329886.1768 | 6356.577 | 51.8968 | 97.2702 | 85.9293 | 32642.69 | 33140.8724 | 10.8%
Advanced Protection |  | Advanced Protection | 2026 | 30 | 73381.4244 | 1277.2735 | 1.741% | 16150.6266 | 3251.1038 | 4.9677 | 16150.6266 | 3251.1038 | 4.9677 | 26902.0471 | 3424.8147 | 7.855 | 0.19291 | 0.18792 | 380386.4977 | 383702.6048 | 0.04212%
Advanced Protection |  | Advanced Protection | 2027 | 30 | 92120.5683 | 1741.3051 | 1.89% | 21003.7956 | 3101.3322 | 6.7725 | 21003.7956 | 3101.3322 | 6.7725 | 36855.3029 | 3441.6031 | 10.7088 | 0.57989 | 0.5694 | 158859.4614 | 158726.9388 | 0.05742%
Advanced Protection |  | Advanced Protection | 2028 | 30 | 115315.796 | 2197.6631 | 1.906% | 25287.2425 | 2958.4602 | 8.5474 | 25287.2425 | 2958.4602 | 8.5474 | 46742.2831 | 3458.4737 | 13.5153 | 0.46088 | 0.4499 | 250206.4431 | 251429.6175 | 0.07247%
| Total | Advanced Protection | 2026-2028 | 90 | 280817.7886 | 5216.2418 | 1.858% | 62441.6647 | 9310.8961 | 6.7063 | 62441.6647 | 9310.8961 | 6.7063 | 110499.6331 | 10324.8915 | 10.7023 | 1.2337 | 1.2072 | 227625.6378 | 228294.8643 | 0.172%
Early Fault Detection |  | Early Fault Detection | 2026 | 46 | 60993.9474 | 9408.507 | 15.43% | 118966.907 | 1734.1304 | 68.6032 | 118966.907 | 1734.1304 | 68.6032 | 198162.7969 | 1826.7873 | 108.4761 | 2.0834 | 1.75 | 29276.7116 | 29477.0087 | 0.3103%
Early Fault Detection |  | Early Fault Detection | 2027 | 37 | 47534.0231 | 7322.3638 | 15.4% | 88323.0808 | 1330.5864 | 66.3791 | 88323.0808 | 1330.5864 | 66.3791 | 154980.2688 | 1476.5752 | 104.9593 | 1.51 | 1.2684 | 31479.6481 | 31702.828 | 0.2415%
Early Fault Detection |  | Early Fault Detection | 2028 | 51 | 88483.8681 | 13931.5964 | 15.74% | 160302.8466 | 1749.5606 | 91.6246 | 160302.8466 | 1749.5606 | 91.6246 | 296312.3025 | 2045.2562 | 144.8778 | 1.3003 | 1.0923 | 68047.9626 | 68254.7095 | 0.4594%
| Total | Early Fault Detection | 2026-2028 | 134 | 197011.8387 | 30662.4671 | 15.56% | 367592.8344 | 4814.2774 | 76.3547 | 367592.8344 | 4814.2774 | 76.3547 | 649455.3682 | 5348.6188 | 121.4249 | 4.8937 | 4.1107 | 40258.5133 | 40467.585 | 1.011%
Microgrid(Capital) |  | Microgrid (Capital) | 2026 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | 0 | 0 | 0%
Microgrid(Capital) |  | Microgrid (Capital) | 2027 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | 0 | 0 | 0%
Microgrid(Capital) |  | Microgrid (Capital) | 2028 | 1 | 6.7611 | 6.7611 | 100% | 0.077796 | 11628.8443 | 6.6899e-06 | 0.070442 | 11628.8443 | 6.0575e-06 | 0.1438 | 20708.581 | 6.9441e-06 | 1 | 1 | 6.7611 | 0 | 0.000223%
| Total | Microgrid (Capital) | 2026-2028 | 1 | 6.7611 | 6.7611 | 100% | 0.077796 | 11628.8443 | 6.6899e-06 | 0.070442 | 11628.8443 | 6.0575e-06 | 0.1438 | 20708.581 | 6.9441e-06 | 1 | 1 | 6.7611 | 0 | 0.000223%
Combined Covered Conductor |  | Combined Covered Conductor | 2026 | 53.5892 | 13538.5148 | 3952.3181 | 29.19% | 75725.4569 | 86275.8703 | 0.87771 | 79732.3062 | 86275.8703 | 0.92416 | 250026.304 | 164653.8273 | 1.5185 | 1.2311 | 0.73539 | 10997.3683 | 13035.4461 | 0.1303%
Combined Covered Conductor |  | Combined Covered Conductor | 2027 | 57.9325 | 30087.8368 | 12025.6972 | 39.97% | 219794.9563 | 108854.2908 | 2.0192 | 231440.5187 | 108854.2908 | 2.1261 | 764482.8889 | 248026.2292 | 3.0823 | 1.8535 | 1.1336 | 16232.608 | 15933.225 | 0.3966%
Combined Covered Conductor |  | Combined Covered Conductor | 2028 | 31.2815 | 16665.9414 | 8303.7228 | 49.82% | 144776.3904 | 49222.5696 | 2.9413 | 152792.0508 | 49222.5696 | 3.1041 | 530461.7082 | 109494.0544 | 4.8447 | 0.93496 | 0.5401 | 17825.2073 | 15482.7859 | 0.2738%
| Total | Combined Covered Conductor | 2026-2028 | 142.8032 | 60292.293 | 24281.738 | 40.27% | 440296.8036 | 244352.7308 | 1.8019 | 463964.8757 | 244352.7308 | 1.8988 | 1544970.9011 | 522174.1109 | 2.9587 | 4.0196 | 2.4091 | 14999.6634 | 14947.6764 | 0.8007%
Strategic Undergrounding |  | Strategic Undergrounding | 2026 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
Strategic Undergrounding |  | Strategic Undergrounding | 2027 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
Strategic Undergrounding |  | Strategic Undergrounding | 2028 | 57.9695 | 126273.2831 | 122742.524 | 97.2% | 2140030.454 | 129745.7641 | 16.494 | 2259197.2581 | 129745.7641 | 17.4125 | 7841086.5684 | 170751.3747 | 45.9211 | 1.8283 | 0.21787 | 69064.896 | 16206.1785 | 4.048%
| Total | Strategic Undergrounding | 2026-2028 | 57.9695 | 126273.2831 | 122742.524 | 97.2% | 2140030.454 | 129745.7641 | 16.494 | 2259197.2581 | 129745.7641 | 17.4125 | 7841086.5684 | 170751.3747 | 45.9211 | 1.8283 | 0.21787 | 69064.896 | 16206.1785 | 4.048%

## SUG_vs_CCC
back to index | [7 empty] | SUG | [12 empty] | CCC
[8 empty] | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
Feeder Segment | SDG&E Grid Hardening Plan | YEAR | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | CCC Units (OH Primary + Secondary miles + Service Drop) | SUG miles (Miles + OH to UG Conversion) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Risk Reduction SUG (K$/year) | Baseline Risk Reduction SUG (%) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Service Territory Risk Reduction (%) | Baseline Risk Reduction CCC (K$) | Baseline Risk Reduction CCC (%) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Service Territory Risk Reduction (%) | Pre-Mitigation LoRE | SUG Post-Mitigation LoRE | CCC Post-Mitigation LoRE
157-204R | SUG/CCC | 2028 | Tier-3 | Tier-3---11 | 5--4 | 13.385 | 16.062 | 3876.1334 | 3750.4331 | 96.76% | 65389.246 | 30039.0823 | 2.1768 | 68518.7732 | 30039.0823 | 2.281 | 239586.6554 | 39723.4864 | 6.0314 | 0.1237% | 1603.6047 | 41.37% | 27959.0379 | 18869.5531 | 1.4817 | 29312.06 | 18869.5531 | 1.5534 | 102442.1106 | 38818.9607 | 2.639 | 0.05288% | 0.32777 | 0.038447 | 0.19112
157-257R | SUG/CCC | 2028 | Tier-3 | Tier-3---14 | 5--4 | 23.2973 | 27.9568 | 2061.1876 | 1955.938 | 94.89% | 34102.0114 | 52227.113 | 0.65296 | 36717.4785 | 52227.113 | 0.70303 | 124950.0085 | 68929.9054 | 1.8127 | 0.0645% | 753.4873 | 36.56% | 13137.1407 | 34549.2225 | 0.38024 | 14266.1197 | 34549.2225 | 0.41292 | 48134.5757 | 73816.2902 | 0.65209 | 0.02485% | 0.36686 | 0.049338 | 0.22343
157-273R | SUG/CCC | 2028 | Tier-3 | Tier-3---14 | 5--4 | 8.5826 | 10.2991 | 1867.403 | 1798.9538 | 96.33% | 31364.972 | 19251.3811 | 1.6292 | 33068.9139 | 19251.3811 | 1.7177 | 114921.4769 | 25434.5374 | 4.5183 | 0.05932% | 686.6124 | 36.77% | 11971.1684 | 12944.5162 | 0.92481 | 12651.0138 | 12944.5162 | 0.97733 | 43862.4448 | 27987.8162 | 1.5672 | 0.02264% | 0.32295 | 0.03672 | 0.18936
73-23R | SUG/CCC | 2028 | Tier-3 | Tier-3---9 | 5--5 | 8.3244 | 9.9893 | 5733.7907 | 5474.9217 | 95.49% | 95455.9086 | 18663.4207 | 5.1146 | 100517.0463 | 18663.4207 | 5.3858 | 349751.1175 | 24637.0073 | 14.1962 | 0.1805% | 908.6137 | 15.85% | 15841.7872 | 12146.5749 | 1.3042 | 16773.9265 | 12146.5749 | 1.381 | 58044.4192 | 25648.9699 | 2.263 | 0.02996% | 0.21349 | 0.02633 | 0.13148
973-1245R | SUG/CCC | 2028 | Tier-3 | Tier-3---6 | 5--5 | 3.3857 | 4.0628 | 8620.1106 | 8345.8684 | 96.82% | 145511.2053 | 7597.8198 | 19.1517 | 153113.3118 | 7597.8198 | 20.1523 | 533154.0753 | 10046.3365 | 53.0695 | 0.2752% | 3422.2157 | 39.7% | 59666.7371 | 5067.4464 | 11.7745 | 62789.1986 | 5067.4464 | 12.3907 | 218619.3426 | 10898.0669 | 20.0604 | 0.1129% | 0.12039 | 0.013736 | 0.069838
973-626R | SUG/CCC | 2028 | Tier-3 | Tier-3---7 | 5--5 | 11.0435 | 13.2521 | 6521.7236 | 6346.8968 | 97.32% | 110658.8987 | 24784.7065 | 4.4648 | 116877.7751 | 24784.7065 | 4.7157 | 405454.9795 | 32776.3948 | 12.3703 | 0.2093% | 3292.8403 | 50.49% | 57411.0606 | 15927.53 | 3.6045 | 60619.6439 | 15927.53 | 3.806 | 210354.5279 | 33343.2865 | 6.3088 | 0.1086% | 0.1523 | 0.021295 | 0.087516
448-9R | SUG/CCC | 2028 | Tier-3 | Tier-3---9 | 5--4 | 18.008 | 21.6096 | 5644.8109 | 5374.1599 | 95.21% | 93699.1146 | 64843.2831 | 1.445 | 99070.8352 | 64843.2831 | 1.5279 | 343314.2119 | 142951.6797 | 2.4016 | 0.1772% | 1153.3377 | 20.43% | 20108.5798 | 45981.2912 | 0.43732 | 21601.4323 | 45981.2912 | 0.46979 | 73677.977 | 127684.633 | 0.57703 | 0.03803% | 0.54394 | 0.064761 | 0.32907
973-1226R | SUG/CCC | 2028 | Tier-3 | Tier-3---10 | 5--5 | 8.59 | 10.3081 | 5177.8696 | 5030.443 | 97.15% | 87706.3707 | 19248.4043 | 4.5566 | 92357.2538 | 19248.4043 | 4.7982 | 321356.7564 | 25384.3653 | 12.6596 | 0.1659% | 2607.7989 | 50.36% | 45467.2823 | 12507.4518 | 3.6352 | 47857.0316 | 12507.4518 | 3.8263 | 166592.4407 | 26369.4843 | 6.3176 | 0.086% | 0.13989 | 0.017936 | 0.079405
1243-45R | SUG/CCC | 2028 | Tier-2 | Tier-2---7 | 4--5 | 4.279 | 5.1348 | 1878.3826 | 1814.2798 | 96.59% | 31632.1838 | 9600.5379 | 3.2948 | 33165.3843 | 9600.5379 | 3.4545 | 115900.543 | 12689.7599 | 9.1334 | 0.05983% | 755.9533 | 40.24% | 13180.1359 | 6223.7894 | 2.1177 | 13822.4469 | 6223.7894 | 2.2209 | 48292.1102 | 13111.3839 | 3.6832 | 0.02493% | 0.087615 | 0.010869 | 0.051647
1243-319R | SUG/CCC | 2028 | Tier-2 | Tier-2---9 | 4--4 | 3.3629 | 4.0354 | 1178.043 | 1155.0932 | 98.05% | 20139.1864 | 7538.1991 | 2.6716 | 21089.8883 | 7538.1991 | 2.7977 | 73790.1199 | 9947.6889 | 7.4178 | 0.03809% | 574.847 | 48.8% | 10022.5264 | 4813.5415 | 2.0822 | 10495.4535 | 4813.5415 | 2.1804 | 36722.6068 | 10019.3973 | 3.6652 | 0.01896% | 0.081051 | 0.0095422 | 0.04611
448-724R | SUG/CCC | 2028 | Tier-3 | Tier-3---18 | 5--2 | 8.8782 | 10.6539 | 520.639 | 486.5346 | 93.45% | 8482.7887 | 19909.2155 | 0.42607 | 9185.6798 | 19909.2155 | 0.46138 | 31080.9972 | 26291.0674 | 1.1822 | 0.01604% | 97.8365 | 18.79% | 1705.7915 | 12884.6814 | 0.13239 | 1963.4137 | 12884.6814 | 0.15238 | 6250.0318 | 27098.842 | 0.23064 | 0.003226% | 0.55035 | 0.060538 | 0.32352
973-530AE | SUG/CCC | 2028 | Tier-3 | Tier-3---17 | 5--3 | 0.034712 | 0.041655 | 388.0062 | 61.835 | 15.94% | 1078.1003 | 76.6529 | 14.0647 | 1273.1428 | 76.6529 | 16.6092 | 3950.1671 | 98.4391 | 40.128 | 0.002039% | 22.6781 | 5.845% | 395.3951 | 39.089 | 10.1153 | 483.3986 | 39.089 | 12.3666 | 1448.7305 | 64.5933 | 22.4285 | 0.0007478% | 0.10542 | 0.1053 | 0.10538
1243-38R | SUG/CCC | 2028 | Tier-2 | Tier-2---16 | 4--3 | 0.35057 | 0.42069 | 158.2514 | 157.6285 | 99.61% | 2748.2713 | 774.1521 | 3.55 | 2879.5915 | 774.1521 | 3.7197 | 10069.6852 | 994.1802 | 10.1286 | 0.005198% | 98.1896 | 62.05% | 1711.9472 | 394.7774 | 4.3365 | 1793.5275 | 394.7774 | 4.5431 | 6272.5865 | 652.3568 | 9.6153 | 0.003238% | 0.072591 | 0.007488 | 0.041133
TM1-10R | SUG/CCC | 2028 | Tier-3 | Tier-3---12 | 5--5 | 3.4326 | 4.1192 | 3782.8568 | 3671.9938 | 97.07% | 64021.6478 | 7689.5664 | 8.3258 | 67077.1122 | 7689.5664 | 8.7231 | 234575.7657 | 10135.6825 | 23.1436 | 0.1211% | 2006.3849 | 53.04% | 34981.5585 | 5965.9762 | 5.8635 | 36647.5843 | 5965.9762 | 6.1428 | 128172.6755 | 14083.8999 | 9.1007 | 0.06616% | 0.093421 | 0.011688 | 0.053413
1233-585R | SUG/CCC | 2028 | Tier-3 | Tier-3---12 | 5--5 | 6.3138 | 7.5766 | 3561.9587 | 3494.4398 | 98.1% | 60925.9719 | 14156.8789 | 4.3036 | 64107.2244 | 14156.8789 | 4.5283 | 223233.1876 | 18690.828 | 11.9435 | 0.1152% | 1825.8875 | 51.26% | 31834.565 | 9785.8264 | 3.2531 | 33489.2825 | 9785.8264 | 3.4222 | 116642.0692 | 21553.4465 | 5.4118 | 0.06021% | 0.12988 | 0.017175 | 0.074306
452-38AE | SUG/CCC | 2028 | Tier-2 | Tier-2---4 | 2--5 | 2.8002 | 3.3602 | 2823.7515 | 2712.086 | 96.05% | 47285.5402 | 6265.284 | 7.5472 | 50241.6776 | 6265.284 | 8.0191 | 173254.5505 | 8240.6768 | 21.0243 | 0.08943% | 1540.3131 | 54.55% | 26855.541 | 4577.4266 | 5.867 | 28534.7596 | 4577.4266 | 6.2338 | 98398.8902 | 10428.8329 | 9.4353 | 0.05079% | 0.011395 | 0.00285 | 0.0065598
1458-1058F | SUG/CCC | 2028 | Tier-3 | Tier-3---13 | 5--5 | 1.4878 | 1.7854 | 2365.6896 | 2245.7625 | 94.93% | 39155.1345 | 3334.8713 | 11.7411 | 42392.3465 | 3334.8713 | 12.7118 | 143464.687 | 4400.3775 | 32.6028 | 0.07406% | 1044.1272 | 44.14% | 18204.482 | 2102.3907 | 8.6589 | 19727.8843 | 2102.3907 | 9.3835 | 66701.3494 | 4333.0504 | 15.3936 | 0.03443% | 0.13833 | 0.014765 | 0.078995
79-660R | SUG/CCC | 2028 | Tier-3 | Tier-3---14 | 5--3 | 7.6593 | 9.1912 | 2087.0386 | 2029.1939 | 97.23% | 35379.2354 | 17186.4671 | 2.0586 | 36994.9265 | 17186.4671 | 2.1526 | 129629.7661 | 22720.5228 | 5.7054 | 0.06692% | 1172.7783 | 56.19% | 20447.5284 | 12093.0825 | 1.6908 | 21374.1071 | 12093.0825 | 1.7675 | 74919.8872 | 26959.4889 | 2.779 | 0.03867% | 0.45747 | 0.050926 | 0.26157
520-45 | SUG/CCC | 2028 | Tier-2 | Tier-2---8 | 5--5 | 9.5877 | 11.5052 | 2044.6463 | 1969.7947 | 96.34% | 34343.6043 | 21495.5658 | 1.5977 | 35856.3763 | 21495.5658 | 1.6681 | 125835.2066 | 28375.1858 | 4.4347 | 0.06496% | 714.2318 | 34.93% | 12452.7155 | 14697.8673 | 0.84725 | 13018.433 | 14697.8673 | 0.88574 | 45626.8368 | 32135.3356 | 1.4198 | 0.02355% | 0.10446 | 0.016293 | 0.065251
358-682F | SUG/CCC | 2028 | Tier-3 | Tier-3---3 | 5--5 | 12.6655 | 15.1986 | 37602.1184 | 36611.5871 | 97.37% | 638327.3605 | 28369.958 | 22.5001 | 673516.5233 | 28369.958 | 23.7405 | 2338835.9184 | 37388.6116 | 62.5548 | 1.207% | 18335.8591 | 48.76% | 319687.8772 | 18413.1227 | 17.362 | 337271.7353 | 18413.1227 | 18.3169 | 1171338.6204 | 38776.2702 | 30.2076 | 0.6046% | 0.54241 | 0.060572 | 0.31006
908-2055F | SUG/CCC | 2028 | Tier-3 | Tier-3---2 | 5--5 | 11.7057 | 14.0468 | 22564.0783 | 21974.0291 | 97.39% | 383119.8017 | 26218.2442 | 14.6127 | 405618.9503 | 26218.2442 | 15.4709 | 1403753.6361 | 34548.7191 | 40.6311 | 0.7246% | 11798.7861 | 52.29% | 205713.2332 | 18267.5492 | 11.2611 | 217757.2542 | 18267.5492 | 11.9204 | 753734.727 | 40417.0471 | 18.6489 | 0.3891% | 0.20355 | 0.028362 | 0.11832
79-679R | SUG/CCC | 2028 | Tier-3 | Tier-3---3 | 5--5 | 7.4635 | 8.9562 | 18448.5828 | 17879.4526 | 96.92% | 311730.3754 | 16713.679 | 18.6512 | 328055.2217 | 16713.679 | 19.6279 | 1142182.2783 | 22017.2373 | 51.8767 | 0.5896% | 6836.2672 | 37.06% | 119191.1292 | 11206.2924 | 10.6361 | 125500.0562 | 11206.2924 | 11.1991 | 436717.1321 | 24153.8281 | 18.0807 | 0.2254% | 0.3939 | 0.043452 | 0.22816
357-2049F | SUG/CCC | 2028 | Tier-3 | Tier-3---8 | 5--5 | 7.9044 | 9.4853 | 16869.708 | 16408.5807 | 97.27% | 286085.5487 | 17670.829 | 16.1897 | 302842.2818 | 17670.829 | 17.138 | 1048219.4537 | 23207.3464 | 45.1676 | 0.5411% | 9446.5244 | 56% | 164701.2719 | 12117.741 | 13.5917 | 174283.4147 | 12117.741 | 14.3825 | 603466.6133 | 26494.7113 | 22.7769 | 0.3115% | 0.18286 | 0.023035 | 0.1045
1030-18R | SUG/CCC | 2028 | Tier-3 | Tier-3---7 | 5--5 | 3.5719 | 4.2863 | 6620.9098 | 6413.7808 | 96.87% | 111825.0284 | 8000.8656 | 13.9766 | 117716.9365 | 8000.8656 | 14.713 | 409727.6869 | 10544.3323 | 38.8576 | 0.2115% | 2335.1221 | 35.27% | 40713.1303 | 5492.8916 | 7.412 | 42892.264 | 5492.8916 | 7.8087 | 149173.1944 | 12035.0146 | 12.3949 | 0.077% | 0.23843 | 0.025777 | 0.1373
CB 236 | SUG/CCC | 2028 | Tier-2 | Tier-2---1 | 5--5 | 9.4868 | 11.3841 | 12711.1878 | 12340.0159 | 97.08% | 215149.6402 | 21193.7367 | 10.1516 | 227530.9438 | 21193.7367 | 10.7358 | 788309.7883 | 27799.7084 | 28.3568 | 0.4069% | 6268.5534 | 49.32% | 109292.9713 | 13834.3784 | 7.9001 | 115549.7954 | 13834.3784 | 8.3524 | 400450.2121 | 29200.1404 | 13.714 | 0.2067% | 0.1419 | 0.020161 | 0.082405
CB 971 | SUG/CCC | 2028 | Tier-2 | Tier-2---3 | 5--5 | 5.1717 | 6.2061 | 11456.6981 | 11115.0778 | 97.02% | 193792.6991 | 11578.4516 | 16.7374 | 203916.4007 | 11578.4516 | 17.6117 | 710057.8066 | 15245.4195 | 46.5752 | 0.3665% | 5569.9585 | 48.62% | 97112.887 | 7607.0884 | 12.7661 | 102174.5382 | 7607.0884 | 13.4315 | 355822.2978 | 16157.6143 | 22.022 | 0.1837% | 0.12528 | 0.016506 | 0.072799

## SUG_vs_CCC_Plot
Note:
Each orange dot represents a Feeder-Segment CBR. Dots below the 1:1 ratio (blue line) indicate that the SUG CBR is greater than the CCC CBR. Conversely, orange dots above the blue line indicate that the CCC CBR is greater than the SUG CBR.

## SUG_comp
SUG - Risk & Cost Benefit
back to index
|  |  | Note: The feeder segments listed below have been selected for detailed scoping and feasibility engineering studies. The total mileage presented here exceeds SDG&E targets because some segments may not be feasible for selected mitigation due to permitting issues, difficult terrain, customer resistance, and other factors not accounted for in the current WiNGS-Planning model. | [5 empty] | Assumptions | Value | Units | Last Update | Comments
[9 empty] | Capital Cost only in Year 0 | 2 | M$/mile | 2025-06-30 | Includes Primary, Secondary for CBR
[9 empty] | Service Drop factor | 1.26% | % | 2025-06-30 | Factor to account for Service drop miles
[9 empty] | OH to UG conversion factor | 20% | % | 2025-06-30 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.003337 | M$/mile-year | 2025-06-30 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 55 | Years | 2025-06-30 | SB 884 end of the expected lifetime (defined as 55 years) of the infrastructure
[9 empty] | Mitigation Effectiveness Estimate (%) | 98% | % | 2025-06-30 | ME value assumption used in WiNGS-Planning
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.022 | M$/mile | 2025-06-30 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[7 empty] | OH miles | SUG miles | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | HFTD Tier | Feeder | Feeder Segment | Tranche ID HTM | Tranche ID Quintile | Total miles in scope | Units (OH Primary + Secondary miles + Service Drop) | SUG miles (Miles + OH to UG Conversion) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2028 | Tier-3 | 157 | 157-204R | Tier-3---11 | 5--4 | 100% | 13.385 | 16.062 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 3750.4331 | 563.1591 | 43.6272 | 3143.6468 | 105.9172 | 65389.246 | 30039.0823 | 2.1768 | 68518.7732 | 30039.0823 | 2.281 | 239586.6554 | 39723.4864 | 6.0314 | 96.76% | 0.32777 | 0.038447 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 3269.4256 | 490.9318 | 38.0319 | 2740.462 | 0.1237%
2028 | Tier-3 | 157 | 157-257R | Tier-3---14 | 5--4 | 100% | 23.2973 | 27.9568 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 1955.938 | 207.1294 | 299.9854 | 1448.8232 | 181.051 | 34102.0114 | 52227.113 | 0.65296 | 36717.4785 | 52227.113 | 0.70303 | 124950.0085 | 68929.9054 | 1.8127 | 94.89% | 0.36686 | 0.049338 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 2133.236 | 225.9049 | 327.1779 | 1580.1532 | 0.0645%
2028 | Tier-3 | 157 | 157-273R | Tier-3---14 | 5--4 | 100% | 8.5826 | 10.2991 | 1867.403 | 95.01% | 4.712% | 0.2778% | 1798.9538 | 249.8856 | 80.4929 | 1468.5752 | 67.3429 | 31364.972 | 19251.3811 | 1.6292 | 33068.9139 | 19251.3811 | 1.7177 | 114921.4769 | 25434.5374 | 4.5183 | 96.33% | 0.32295 | 0.03672 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 1864.0862 | 258.9329 | 83.4072 | 1521.7461 | 0.05932%
2028 | Tier-3 | 73 | 73-23R | Tier-3---9 | 5--5 | 100% | 8.3244 | 9.9893 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 5474.9217 | 909.3557 | 71.9521 | 4493.614 | 64.8097 | 95455.9086 | 18663.4207 | 5.1146 | 100517.0463 | 18663.4207 | 5.3858 | 349751.1175 | 24637.0073 | 14.1962 | 95.49% | 0.21349 | 0.02633 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 9831.8641 | 1633.0208 | 129.2115 | 8069.6318 | 0.1805%
2028 | Tier-3 | 973 | 973-1245R | Tier-3---6 | 5--5 | 100% | 3.3857 | 4.0628 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 8345.8684 | 1430.9439 | 43.0341 | 6871.8904 | 26.7675 | 145511.2053 | 7597.8198 | 19.1517 | 153113.3118 | 7597.8198 | 20.1523 | 533154.0753 | 10046.3365 | 53.0695 | 96.82% | 0.12039 | 0.013736 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 19964.9234 | 3423.0933 | 102.9458 | 16438.8844 | 0.2752%
2028 | Tier-3 | 973 | 973-626R | Tier-3---7 | 5--5 | 100% | 11.0435 | 13.2521 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 6346.8968 | 1106.1577 | 99.6249 | 5141.1143 | 87.4194 | 110658.8987 | 24784.7065 | 4.4648 | 116877.7751 | 24784.7065 | 4.7157 | 405454.9795 | 32776.3948 | 12.3703 | 97.32% | 0.1523 | 0.021295 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 8209.8341 | 1430.8364 | 128.8667 | 6650.1311 | 0.2093%
2028 | Tier-3 | 448 | 448-9R | Tier-3---9 | 5--4 | 100% | 18.008 | 21.6096 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 5374.1599 | 734.9463 | 306.5806 | 4332.633 | 1543.6392 | 93699.1146 | 64843.2831 | 1.445 | 99070.8352 | 64843.2831 | 1.5279 | 343314.2119 | 142951.6797 | 2.4016 | 95.21% | 0.54394 | 0.064761 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 4179.2279 | 571.5327 | 238.4131 | 3369.2821 | 0.1772%
2028 | Tier-3 | 973 | 973-1226R | Tier-3---10 | 5--5 | 100% | 8.59 | 10.3081 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 5030.443 | 790.0049 | 111.7582 | 4128.6799 | 66.2695 | 87706.3707 | 19248.4043 | 4.5566 | 92357.2538 | 19248.4043 | 4.7982 | 321356.7564 | 25384.3653 | 12.6596 | 97.15% | 0.13989 | 0.017936 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 8219.406 | 1290.815 | 182.6054 | 6745.9856 | 0.1659%
2028 | Tier-2 | 1243 | 1243-45R | Tier-2---7 | 4--5 | 100% | 4.279 | 5.1348 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 1814.2798 | 285.3207 | 11.9527 | 1517.0065 | 33.715 | 31632.1838 | 9600.5379 | 3.2948 | 33165.3843 | 9600.5379 | 3.4545 | 115900.543 | 12689.7599 | 9.1334 | 96.59% | 0.087615 | 0.010869 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 5897.8674 | 927.5216 | 38.8557 | 4931.49 | 0.05983%
2028 | Tier-2 | 1243 | 1243-319R | Tier-2---9 | 4--4 | 100% | 3.3629 | 4.0354 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 1155.0932 | 179.5546 | 4.7777 | 970.7609 | 26.1019 | 20139.1864 | 7538.1991 | 2.6716 | 21089.8883 | 7538.1991 | 2.7977 | 73790.1199 | 9947.6889 | 7.4178 | 98.05% | 0.081051 | 0.0095422 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 2405.0921 | 373.8619 | 9.9479 | 2021.2823 | 0.03809%
2028 | Tier-3 | 448 | 448-724R | Tier-3---18 | 5--2 | 100% | 8.8782 | 10.6539 | 520.639 | 76.18% | 22.78% | 1.038% | 486.5346 | 40.7314 | 95.5527 | 350.2505 | 69.3547 | 8482.7887 | 19909.2155 | 0.42607 | 9185.6798 | 19909.2155 | 0.46138 | 31080.9972 | 26291.0674 | 1.1822 | 93.45% | 0.55035 | 0.060538 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 563.3583 | 47.1629 | 110.6404 | 405.555 | 0.01604%
2028 | Tier-3 | 973 | 973-530AE | Tier-3---17 | 5--3 | 100% | 0.034712 | 0.041655 | 388.0062 | 6.476% | 93.52% | 0.007746% | 61.835 | 4.0138 | 33.8032 | 24.0181 | 0.20301 | 1078.1003 | 76.6529 | 14.0647 | 1273.1428 | 76.6529 | 16.6092 | 3950.1671 | 98.4391 | 40.128 | 15.94% | 0.10542 | 0.1053 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3097.4894 | 201.0613 | 1693.2959 | 1203.1322 | 0.002039%
2028 | Tier-2 | 1243 | 1243-38R | Tier-2---16 | 4--3 | 100% | 0.35057 | 0.42069 | 158.2514 | 99.48% | 0.3681% | 0.155% | 157.6285 | 25.0375 | 0.42432 | 132.1667 | 2.0503 | 2748.2713 | 774.1521 | 3.55 | 2879.5915 | 774.1521 | 3.7197 | 10069.6852 | 994.1802 | 10.1286 | 99.61% | 0.072591 | 0.007488 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 83.1851 | 13.213 | 0.22393 | 69.7482 | 0.005198%
2028 | Tier-3 | TM1 | TM1-10R | Tier-3---12 | 5--5 | 100% | 3.4326 | 4.1192 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 3671.9938 | 578.3117 | 14.1146 | 3079.5676 | 26.3558 | 64021.6478 | 7689.5664 | 8.3258 | 67077.1122 | 7689.5664 | 8.7231 | 234575.7657 | 10135.6825 | 23.1436 | 97.07% | 0.093421 | 0.011688 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 9485.1934 | 1493.8473 | 36.4596 | 7954.8865 | 0.1211%
2028 | Tier-3 | 1233 | 1233-585R | Tier-3---12 | 5--5 | 100% | 6.3138 | 7.5766 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 3494.4398 | 573.5003 | 43.315 | 2877.6244 | 49.2241 | 60925.9719 | 14156.8789 | 4.3036 | 64107.2244 | 14156.8789 | 4.5283 | 223233.1876 | 18690.828 | 11.9435 | 98.1% | 0.12988 | 0.017175 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 3931.231 | 645.1856 | 48.7293 | 3237.3161 | 0.1152%
2028 | Tier-2 | 452 | 452-38AE | Tier-2---4 | 2--5 | 100% | 2.8002 | 3.3602 | 2823.7515 | 99.93% | 0% | 0.06613% | 2712.086 | 573.0588 | 0.10887 | 2138.9183 | 21.0684 | 47285.5402 | 6265.284 | 7.5472 | 50241.6776 | 6265.284 | 8.0191 | 173254.5505 | 8240.6768 | 21.0243 | 96.05% | 0.011395 | 0.00285 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 39180.881 | 8278.8482 | 1.5729 | 30900.46 | 0.08943%
2028 | Tier-3 | 1458 | 1458-1058F | Tier-3---13 | 5--5 | 100% | 1.4878 | 1.7854 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 2245.7625 | 347.118 | 280.5475 | 1618.097 | 11.5372 | 39155.1345 | 3334.8713 | 11.7411 | 42392.3465 | 3334.8713 | 12.7118 | 143464.687 | 4400.3775 | 32.6028 | 94.93% | 0.13833 | 0.014765 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 8122.5057 | 1255.4612 | 1014.6881 | 5852.3565 | 0.07406%
2028 | Tier-3 | 79 | 79-660R | Tier-3---14 | 5--3 | 100% | 7.6593 | 9.1912 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 2029.1939 | 270.7004 | 42.5672 | 1715.9263 | 60.444 | 35379.2354 | 17186.4671 | 2.0586 | 36994.9265 | 17186.4671 | 2.1526 | 129629.7661 | 22720.5228 | 5.7054 | 97.23% | 0.45747 | 0.050926 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 1135.8536 | 151.5262 | 23.8272 | 960.5001 | 0.06692%
2028 | Tier-2 | 520 | 520-45 | Tier-2---8 | 5--5 | 100% | 9.5877 | 11.5052 | 2044.6463 | 97.57% | 2.13% | 0.298% | 1969.7947 | 258.7068 | 34.6057 | 1676.4822 | 74.6341 | 34343.6043 | 21495.5658 | 1.5977 | 35856.3763 | 21495.5658 | 1.6681 | 125835.2066 | 28375.1858 | 4.4347 | 96.34% | 0.10446 | 0.016293 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 4593.9796 | 603.3592 | 80.7078 | 3909.9126 | 0.06496%
2028 | Tier-3 | 358 | 358-682F | Tier-3---3 | 5--5 | 100% | 12.6655 | 15.1986 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 36611.5871 | 6396.5945 | 426.2582 | 29788.7344 | 97.0978 | 638327.3605 | 28369.958 | 22.5001 | 673516.5233 | 28369.958 | 23.7405 | 2338835.9184 | 37388.6116 | 62.5548 | 97.37% | 0.54241 | 0.060572 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 16352.9021 | 2857.0978 | 190.3921 | 13305.4122 | 1.207%
2028 | Tier-3 | 908 | 908-2055F | Tier-3---2 | 5--5 | 100% | 11.7057 | 14.0468 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 21974.0291 | 4185.414 | 176.9625 | 17611.6526 | 89.6378 | 383119.8017 | 26218.2442 | 14.6127 | 405618.9503 | 26218.2442 | 15.4709 | 1403753.6361 | 34548.7191 | 40.6311 | 97.39% | 0.20355 | 0.028362 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 20804.365 | 3962.627 | 167.5429 | 16674.1951 | 0.7246%
2028 | Tier-3 | 79 | 79-679R | Tier-3---3 | 5--5 | 100% | 7.4635 | 8.9562 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 17879.4526 | 3000.4003 | 164.8362 | 14714.2162 | 56.9822 | 311730.3754 | 16713.679 | 18.6512 | 328055.2217 | 16713.679 | 19.6279 | 1142182.2783 | 22017.2373 | 51.8767 | 96.92% | 0.3939 | 0.043452 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 13097.8442 | 2197.9854 | 120.7531 | 10779.1058 | 0.5896%
2028 | Tier-3 | 357 | 357-2049F | Tier-3---8 | 5--5 | 100% | 7.9044 | 9.4853 | 16869.708 | 98.79% | 1.184% | 0.02933% | 16408.5807 | 3082.419 | 166.5564 | 13159.6054 | 58.6187 | 286085.5487 | 17670.829 | 16.1897 | 302842.2818 | 17670.829 | 17.138 | 1048219.4537 | 23207.3464 | 45.1676 | 97.27% | 0.18286 | 0.023035 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 20018.5518 | 3760.5668 | 203.1996 | 16054.7854 | 0.5411%
2028 | Tier-3 | 1030 | 1030-18R | Tier-3---7 | 5--5 | 100% | 3.5719 | 4.2863 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 6413.7808 | 1070.6439 | 71.7425 | 5271.3944 | 27.3842 | 111825.0284 | 8000.8656 | 13.9766 | 117716.9365 | 8000.8656 | 14.713 | 409727.6869 | 10544.3323 | 38.8576 | 96.87% | 0.23843 | 0.025777 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 8035.4823 | 1341.3524 | 89.8823 | 6604.2476 | 0.2115%
2028 | Tier-2 | 236 | CB 236 | Tier-2---1 | 5--5 | 100% | 9.4868 | 11.3841 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 12340.0159 | 2139.5164 | 261.1036 | 9939.3959 | 69.5161 | 215149.6402 | 21193.7367 | 10.1516 | 227530.9438 | 21193.7367 | 10.7358 | 788309.7883 | 27799.7084 | 28.3568 | 97.08% | 0.1419 | 0.020161 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 18410.0231 | 3191.9365 | 389.5395 | 14828.5471 | 0.4069%
2028 | Tier-2 | 971 | CB 971 | Tier-2---3 | 5--5 | 100% | 5.1717 | 6.2061 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 11115.0778 | 1897.1782 | 65.7138 | 9152.1859 | 39.3116 | 193792.6991 | 11578.4516 | 16.7374 | 203916.4007 | 11578.4516 | 17.6117 | 710057.8066 | 15245.4195 | 46.5752 | 97.02% | 0.12528 | 0.016506 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 20697.2324 | 3532.7092 | 122.3647 | 17042.1585 | 0.3665%

## CCC_comp
CCC - Risk & Cost Benefit
back to index
|  |  | Note: The feeder segments listed below have been selected for detailed scoping and feasibility engineering studies. The total mileage presented here exceeds SDG&E targets because some segments may not be feasible for selected mitigation due to permitting issues, difficult terrain, customer resistance, and other factors not accounted for in the current WiNGS-Planning model. | [5 empty] | Assumptions | Value | Units | Last Update | Comments
[9 empty] | Capital Cost only in Year 0 | 1 | M$/mile | 2025-06-30 | Includes Primary, Secondary for CBR
[9 empty] | Service Drop factor | 1.26% | % | 2025-06-30 | Factor to account for Service drop miles
[9 empty] | OH to UG conversion factor | 0% | % | 2025-06-30 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.0080298 | M$/mile-year | 2025-06-30 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 55 | Years | 2025-06-30 | End of the expected lifetime (defined as 55 years) of the infrastructure
[9 empty] | Mitigation Effectiveness Estimate (%) | 61.7% | % | 2025-06-30 | ME value assumption used in WiNGS-Planning
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.045872 | M$/mile | 2025-06-30 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[7 empty] | OH miles | OH miles (OH to UG factor = 0%) | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | HFTD Tier | Feeder | Feeder Segment | Tranche ID HTM | Tranche ID Quintile | Total miles in scope | Units (OH Primary + Secondary miles + Service Drop) | OH miles (Miles + OH to UG Conversion) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2028 | Tier-3 | 157 | 157-204R | Tier-3---11 | 5--4 | 100% | 13.385 | 13.385 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 1603.6047 | 239.9351 | 22.4033 | 1341.2662 | 385.288 | 27959.0379 | 18869.5531 | 1.4817 | 29312.06 | 18869.5531 | 1.5534 | 102442.1106 | 38818.9607 | 2.639 | 41.37% | 0.32777 | 0.19112 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11890.2993 | 1779.0549 | 166.1145 | 9945.1299 | 0.05288%
2028 | Tier-3 | 157 | 157-257R | Tier-3---14 | 5--4 | 100% | 23.2973 | 23.2973 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 753.4873 | 75.8163 | 143.0822 | 534.5888 | 768.4468 | 13137.1407 | 34549.2225 | 0.38024 | 14266.1197 | 34549.2225 | 0.41292 | 48134.5757 | 73816.2902 | 0.65209 | 36.56% | 0.36686 | 0.22343 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5852.8779 | 588.92 | 1111.4225 | 4152.5354 | 0.02485%
2028 | Tier-3 | 157 | 157-273R | Tier-3---14 | 5--4 | 100% | 8.5826 | 8.5826 | 1867.403 | 95.01% | 4.712% | 0.2778% | 686.6124 | 94.668 | 37.1477 | 554.7967 | 295.5257 | 11971.1684 | 12944.5162 | 0.92481 | 12651.0138 | 12944.5162 | 0.97733 | 43862.4448 | 27987.8162 | 1.5672 | 36.77% | 0.32295 | 0.18936 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 6235.6919 | 859.7582 | 337.3687 | 5038.5649 | 0.02264%
2028 | Tier-3 | 73 | 73-23R | Tier-3---9 | 5--5 | 100% | 8.3244 | 8.3244 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 908.6137 | 146.7723 | 33.9609 | 727.8805 | 263.2033 | 15841.7872 | 12146.5749 | 1.3042 | 16773.9265 | 12146.5749 | 1.381 | 58044.4192 | 25648.9699 | 2.263 | 15.85% | 0.21349 | 0.13148 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 36698.5525 | 5928.0747 | 1371.6681 | 29398.8097 | 0.02996%
2028 | Tier-3 | 973 | 973-1245R | Tier-3---6 | 5--5 | 100% | 3.3857 | 3.3857 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 3422.2157 | 586.5406 | 18.8757 | 2816.7994 | 114.3472 | 59666.7371 | 5067.4464 | 11.7745 | 62789.1986 | 5067.4464 | 12.3907 | 218619.3426 | 10898.0669 | 20.0604 | 39.7% | 0.12039 | 0.069838 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 74427.8884 | 12756.3499 | 410.5176 | 61261.0209 | 0.1129%
2028 | Tier-3 | 973 | 973-626R | Tier-3---7 | 5--5 | 100% | 11.0435 | 11.0435 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 3292.8403 | 574.3225 | 47.7921 | 2670.7257 | 338.4744 | 57411.0606 | 15927.53 | 3.6045 | 60619.6439 | 15927.53 | 3.806 | 210354.5279 | 33343.2865 | 6.3088 | 50.49% | 0.1523 | 0.087516 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 36894.693 | 6435.0071 | 535.488 | 29924.198 | 0.1086%
2028 | Tier-3 | 448 | 448-9R | Tier-3---9 | 5--4 | 100% | 18.008 | 18.008 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 1153.3377 | 144.8267 | 144.6235 | 863.8874 | 1699.5645 | 20108.5798 | 45981.2912 | 0.43732 | 21601.4323 | 45981.2912 | 0.46979 | 73677.977 | 127684.633 | 0.57703 | 20.43% | 0.54394 | 0.32907 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 13648.9651 | 1713.9258 | 1711.5209 | 10223.5185 | 0.03803%
2028 | Tier-3 | 973 | 973-1226R | Tier-3---10 | 5--5 | 100% | 8.59 | 8.59 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 2607.7989 | 409.5215 | 53.8288 | 2144.4486 | 270.0686 | 45467.2823 | 12507.4518 | 3.6352 | 47857.0316 | 12507.4518 | 3.8263 | 166592.4407 | 26369.4843 | 6.3176 | 50.36% | 0.13989 | 0.079405 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 32366.7739 | 5082.7885 | 668.0972 | 26615.8882 | 0.086%
2028 | Tier-2 | 1243 | 1243-45R | Tier-2---7 | 4--5 | 100% | 4.279 | 4.279 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 755.9533 | 118.8555 | 5.6827 | 631.4152 | 134.1524 | 13180.1359 | 6223.7894 | 2.1177 | 13822.4469 | 6223.7894 | 2.2209 | 48292.1102 | 13111.3839 | 3.6832 | 40.24% | 0.087615 | 0.051647 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21732.8777 | 3416.9726 | 163.3705 | 18152.5345 | 0.02493%
2028 | Tier-2 | 1243 | 1243-319R | Tier-2---9 | 4--4 | 100% | 3.3629 | 3.3629 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 574.847 | 89.3879 | 2.3083 | 483.1509 | 100.9714 | 10022.5264 | 4813.5415 | 2.0822 | 10495.4535 | 4813.5415 | 2.1804 | 36722.6068 | 10019.3973 | 3.6652 | 48.8% | 0.081051 | 0.04611 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 13081.5607 | 2034.1639 | 52.5292 | 10994.8677 | 0.01896%
2028 | Tier-3 | 448 | 448-724R | Tier-3---18 | 5--2 | 100% | 8.8782 | 8.8782 | 520.639 | 76.18% | 22.78% | 1.038% | 97.8365 | 5.2471 | 44.7035 | 47.886 | 276.6977 | 1705.7915 | 12884.6814 | 0.13239 | 1963.4137 | 12884.6814 | 0.15238 | 6250.0318 | 27098.842 | 0.23064 | 18.79% | 0.55035 | 0.32352 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 1306.8868 | 70.0894 | 597.1433 | 639.654 | 0.003226%
2028 | Tier-3 | 973 | 973-530AE | Tier-3---17 | 5--3 | 100% | 0.034712 | 0.034712 | 388.0062 | 6.476% | 93.52% | 0.007746% | 22.6781 | 0.80994 | 16.2531 | 5.615 | 0.43443 | 395.3951 | 39.089 | 10.1153 | 483.3986 | 39.089 | 12.3666 | 1448.7305 | 64.5933 | 22.4285 | 5.845% | 0.10542 | 0.10538 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3466.8676 | 123.8174 | 2484.6633 | 858.3868 | 0.0007478%
2028 | Tier-2 | 1243 | 1243-38R | Tier-2---16 | 4--3 | 100% | 0.35057 | 0.35057 | 158.2514 | 99.48% | 0.3681% | 0.155% | 98.1896 | 15.6134 | 0.20431 | 82.3719 | 4.3875 | 1711.9472 | 394.7774 | 4.3365 | 1793.5275 | 394.7774 | 4.5431 | 6272.5865 | 652.3568 | 9.6153 | 62.05% | 0.072591 | 0.041133 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 1460.1989 | 232.1898 | 3.0383 | 1224.9708 | 0.003238%
2028 | Tier-3 | TM1 | TM1-10R | Tier-3---12 | 5--5 | 100% | 3.4326 | 3.4326 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 2006.3849 | 316.2244 | 6.8025 | 1683.3579 | 163.4372 | 34981.5585 | 5965.9762 | 5.8635 | 36647.5843 | 5965.9762 | 6.1428 | 128172.6755 | 14083.8999 | 9.1007 | 53.04% | 0.093421 | 0.053413 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 33259.2914 | 5241.9654 | 112.7637 | 27904.5622 | 0.06616%
2028 | Tier-3 | 1233 | 1233-585R | Tier-3---12 | 5--5 | 100% | 6.3138 | 6.3138 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 1825.8875 | 299.9406 | 20.8938 | 1505.0531 | 232.496 | 31834.565 | 9785.8264 | 3.2531 | 33489.2825 | 9785.8264 | 3.4222 | 116642.0692 | 21553.4465 | 5.4118 | 51.26% | 0.12988 | 0.074306 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 23363.7459 | 3837.9894 | 267.353 | 19258.4036 | 0.06021%
2028 | Tier-2 | 452 | 452-38AE | Tier-2---4 | 2--5 | 100% | 2.8002 | 2.8002 | 2823.7515 | 99.93% | 0% | 0.06613% | 1540.3131 | 325.5201 | 0.064842 | 1214.7281 | 116.7289 | 26855.541 | 4577.4266 | 5.867 | 28534.7596 | 4577.4266 | 6.2338 | 98398.8902 | 10428.8329 | 9.4353 | 54.55% | 0.011395 | 0.0065598 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 195652.063 | 41347.8784 | 8.2363 | 154295.9483 | 0.05079%
2028 | Tier-3 | 1458 | 1458-1058F | Tier-3---13 | 5--5 | 100% | 1.4878 | 1.4878 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 1044.1272 | 160.4984 | 134.8752 | 748.7536 | 43.1105 | 18204.482 | 2102.3907 | 8.6589 | 19727.8843 | 2102.3907 | 9.3835 | 66701.3494 | 4333.0504 | 15.3936 | 44.14% | 0.13833 | 0.078995 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 16729.6968 | 2571.6109 | 2161.0602 | 11997.0257 | 0.03443%
2028 | Tier-3 | 79 | 79-660R | Tier-3---14 | 5--3 | 100% | 7.6593 | 7.6593 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 1172.7783 | 159.1243 | 20.5307 | 993.1233 | 294.7673 | 20447.5284 | 12093.0825 | 1.6908 | 21374.1071 | 12093.0825 | 1.7675 | 74919.8872 | 26959.4889 | 2.779 | 56.19% | 0.45747 | 0.26157 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 3495.2341 | 474.2386 | 61.1878 | 2959.8078 | 0.03867%
2028 | Tier-2 | 520 | 520-45 | Tier-2---8 | 5--5 | 100% | 9.5877 | 9.5877 | 2044.6463 | 97.57% | 2.13% | 0.298% | 714.2318 | 93.1426 | 16.5447 | 604.5444 | 343.7511 | 12452.7155 | 14697.8673 | 0.84725 | 13018.433 | 14697.8673 | 0.88574 | 45626.8368 | 32135.3356 | 1.4198 | 34.93% | 0.10446 | 0.065251 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 20389.3067 | 2658.9604 | 472.3056 | 17258.0407 | 0.02355%
2028 | Tier-3 | 358 | 358-682F | Tier-3---3 | 5--5 | 100% | 12.6655 | 12.6655 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 18335.8591 | 3204.7735 | 204.5737 | 14926.5119 | 396.5725 | 319687.8772 | 18413.1227 | 17.362 | 337271.7353 | 18413.1227 | 18.3169 | 1171338.6204 | 38776.2702 | 30.2076 | 48.76% | 0.54241 | 0.31006 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 62138.0385 | 10860.5949 | 693.2759 | 50584.1677 | 0.6046%
2028 | Tier-3 | 908 | 908-2055F | Tier-3---2 | 5--5 | 100% | 11.7057 | 11.7057 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 11798.7861 | 2249.1572 | 86.0669 | 9463.562 | 438.2031 | 205713.2332 | 18267.5492 | 11.2611 | 217757.2542 | 18267.5492 | 11.9204 | 753734.727 | 40417.0471 | 18.6489 | 52.29% | 0.20355 | 0.11832 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 90982.3997 | 17343.6248 | 663.6761 | 72975.0988 | 0.3891%
2028 | Tier-3 | 79 | 79-679R | Tier-3---3 | 5--5 | 100% | 7.4635 | 7.4635 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 6836.2672 | 1144.3556 | 78.8869 | 5613.0247 | 254.1013 | 119191.1292 | 11206.2924 | 10.6361 | 125500.0562 | 11206.2924 | 11.1991 | 436717.1321 | 24153.8281 | 18.0807 | 37.06% | 0.3939 | 0.22816 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 50895.9831 | 8519.7227 | 587.313 | 41788.9474 | 0.2254%
2028 | Tier-3 | 357 | 357-2049F | Tier-3---8 | 5--5 | 100% | 7.9044 | 7.9044 | 16869.708 | 98.79% | 1.184% | 0.02933% | 9446.5244 | 1777.8862 | 80.0026 | 7588.6356 | 283.4202 | 164701.2719 | 12117.741 | 13.5917 | 174283.4147 | 12117.741 | 14.3825 | 603466.6133 | 26494.7113 | 22.7769 | 56% | 0.18286 | 0.1045 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 71035.6581 | 13369.2889 | 601.6006 | 57064.7686 | 0.3115%
2028 | Tier-3 | 1030 | 1030-18R | Tier-3---7 | 5--5 | 100% | 3.5719 | 3.5719 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 2335.1221 | 388.1237 | 34.3901 | 1912.6082 | 129.0504 | 40713.1303 | 5492.8916 | 7.412 | 42892.264 | 5492.8916 | 7.8087 | 149173.1944 | 12035.0146 | 12.3949 | 35.27% | 0.23843 | 0.1373 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 31214.8596 | 5188.2628 | 459.7118 | 25566.885 | 0.077%
2028 | Tier-2 | 236 | CB 236 | Tier-2---1 | 5--5 | 100% | 9.4868 | 9.4868 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 6268.5534 | 1088.2289 | 124.9113 | 5055.4131 | 299.4812 | 109292.9713 | 13834.3784 | 7.9001 | 115549.7954 | 13834.3784 | 8.3524 | 400450.2121 | 29200.1404 | 13.714 | 49.32% | 0.1419 | 0.082405 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 78182.1868 | 13572.5282 | 1557.9095 | 63051.749 | 0.2067%
2028 | Tier-2 | 971 | CB 971 | Tier-2---3 | 5--5 | 100% | 5.1717 | 5.1717 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 5569.9585 | 951.1587 | 30.2485 | 4588.5512 | 167.0058 | 97112.887 | 7607.0884 | 12.7661 | 102174.5382 | 7607.0884 | 13.4315 | 355822.2978 | 16157.6143 | 22.022 | 48.62% | 0.12528 | 0.072799 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 80862.4733 | 13808.5495 | 439.1364 | 66614.7874 | 0.1837%

## SUG
SUG - Risk & Cost Benefit
back to index
|  |  | Note: The feeder segments listed below have been selected for detailed scoping and feasibility engineering studies. The total mileage presented here exceeds SDG&E targets because some segments may not be feasible for selected mitigation due to permitting issues, difficult terrain, customer resistance, and other factors not accounted for in the current WiNGS-Planning model. | [5 empty] | Assumptions | Value | Units | Last Update | Comments
[9 empty] | Capital Cost only in Year 0 | 2 | M$/mile | 2025-06-30 | Includes Primary, Secondary for CBR
[9 empty] | Service Drop factor | 1.26% | % | 2025-06-30 | Factor to account for Service drop miles
[9 empty] | OH to UG conversion factor | 20% | % | 2025-06-30 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.003337 | M$/mile-year | 2025-06-30 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 55 | Years | 2025-06-30 | SB 884 end of the expected lifetime (defined as 55 years) of the infrastructure
[9 empty] | Mitigation Effectiveness Estimate (%) | 98% | % | 2025-06-30 | ME value assumption used in WiNGS-Planning
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.022 | M$/mile | 2025-06-30 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[7 empty] | OH miles | SUG miles | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | HFTD Tier | Feeder | Feeder Segment | Tranche ID HTM | Tranche ID Quintile | Total miles in scope | Units (OH Primary + Secondary miles + Service Drop) | SUG miles (Miles + OH to UG Conversion) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2028 | Tier-3 | 358 | 358-682F | Tier-3---3 | 5--5 | 100% | 12.6655 | 15.1986 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 36611.5871 | 6396.5945 | 426.2582 | 29788.7344 | 97.0978 | 638327.3605 | 28369.958 | 22.5001 | 673516.5233 | 28369.958 | 23.7405 | 2338835.9184 | 37388.6116 | 62.5548 | 97.37% | 0.54241 | 0.060572 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 16352.9021 | 2857.0978 | 190.3921 | 13305.4122 | 1.207%
2028 | Tier-3 | 908 | 908-2055F | Tier-3---2 | 5--5 | 100% | 11.7057 | 14.0468 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 21974.0291 | 4185.414 | 176.9625 | 17611.6526 | 89.6378 | 383119.8017 | 26218.2442 | 14.6127 | 405618.9503 | 26218.2442 | 15.4709 | 1403753.6361 | 34548.7191 | 40.6311 | 97.39% | 0.20355 | 0.028362 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 20804.365 | 3962.627 | 167.5429 | 16674.1951 | 0.7246%
2028 | Tier-3 | 79 | 79-679R | Tier-3---3 | 5--5 | 100% | 7.4635 | 8.9562 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 17879.4526 | 3000.4003 | 164.8362 | 14714.2162 | 56.9822 | 311730.3754 | 16713.679 | 18.6512 | 328055.2217 | 16713.679 | 19.6279 | 1142182.2783 | 22017.2373 | 51.8767 | 96.92% | 0.3939 | 0.043452 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 13097.8442 | 2197.9854 | 120.7531 | 10779.1058 | 0.5896%
2028 | Tier-3 | 357 | 357-2049F | Tier-3---8 | 5--5 | 100% | 7.9044 | 9.4853 | 16869.708 | 98.79% | 1.184% | 0.02933% | 16408.5807 | 3082.419 | 166.5564 | 13159.6054 | 58.6187 | 286085.5487 | 17670.829 | 16.1897 | 302842.2818 | 17670.829 | 17.138 | 1048219.4537 | 23207.3464 | 45.1676 | 97.27% | 0.18286 | 0.023035 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 20018.5518 | 3760.5668 | 203.1996 | 16054.7854 | 0.5411%
2028 | Tier-3 | 1030 | 1030-18R | Tier-3---7 | 5--5 | 100% | 3.5719 | 4.2863 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 6413.7808 | 1070.6439 | 71.7425 | 5271.3944 | 27.3842 | 111825.0284 | 8000.8656 | 13.9766 | 117716.9365 | 8000.8656 | 14.713 | 409727.6869 | 10544.3323 | 38.8576 | 96.87% | 0.23843 | 0.025777 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 8035.4823 | 1341.3524 | 89.8823 | 6604.2476 | 0.2115%
2028 | Tier-2 | 236 | CB 236 | Tier-2---1 | 5--5 | 100% | 9.4868 | 11.3841 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 12340.0159 | 2139.5164 | 261.1036 | 9939.3959 | 69.5161 | 215149.6402 | 21193.7367 | 10.1516 | 227530.9438 | 21193.7367 | 10.7358 | 788309.7883 | 27799.7084 | 28.3568 | 97.08% | 0.1419 | 0.020161 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 18410.0231 | 3191.9365 | 389.5395 | 14828.5471 | 0.4069%
2028 | Tier-2 | 971 | CB 971 | Tier-2---3 | 5--5 | 100% | 5.1717 | 6.2061 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 11115.0778 | 1897.1782 | 65.7138 | 9152.1859 | 39.3116 | 193792.6991 | 11578.4516 | 16.7374 | 203916.4007 | 11578.4516 | 17.6117 | 710057.8066 | 15245.4195 | 46.5752 | 97.02% | 0.12528 | 0.016506 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 20697.2324 | 3532.7092 | 122.3647 | 17042.1585 | 0.3665%

## CCC
CCC - Risk & Cost Benefit
back to index
|  |  | Note: The feeder segments listed below have been selected for detailed scoping and feasibility engineering studies. The total mileage presented here exceeds SDG&E targets because some segments may not be feasible for selected mitigation due to permitting issues, difficult terrain, customer resistance, and other factors not accounted for in the current WiNGS-Planning model. | [5 empty] | Assumptions | Value | Units | Last Update | Comments
[9 empty] | Capital Cost only in Year 0 | 1 | M$/mile | 2025-06-30 | Includes Primary, Secondary for CBR
[9 empty] | Service Drop factor | 1.26% | % | 2025-06-30 | Factor to account for Service drop miles
[9 empty] | OH to UG conversion factor | 0% | % | 2025-06-30 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.0080298 | M$/mile-year | 2025-06-30 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 55 | Years | 2025-06-30 | End of the expected lifetime (defined as 55 years) of the infrastructure
[9 empty] | Mitigation Effectiveness Estimate (%) | 61.7% | % | 2025-06-30 | ME value assumption used in WiNGS-Planning
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.045872 | M$/mile | 2025-06-30 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[7 empty] | OH miles | OH miles (OH to UG factor = 0%) | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | HFTD Tier | Feeder | Feeder Segment | Tranche ID HTM | Tranche ID Quintile | Total miles in scope | Units (OH Primary + Secondary miles + Service Drop) | OH miles (Miles + OH to UG Conversion) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | Tier-3 | 157 | 157-204R | Tier-3---11 | 5--4 | 100% | 13.385 | 13.385 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 1603.6047 | 239.9351 | 22.4033 | 1341.2662 | 385.288 | 30724.6774 | 20736.0831 | 1.4817 | 32048.9018 | 20736.0831 | 1.5456 | 101445.113 | 38441.1629 | 2.639 | 41.37% | 0.32777 | 0.19112 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11890.2993 | 1779.0549 | 166.1145 | 9945.1299 | 0.05288%
2026 | Tier-3 | 157 | 157-257R | Tier-3---14 | 5--4 | 100% | 23.2973 | 23.2973 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 753.4873 | 75.8163 | 143.0822 | 534.5888 | 768.4468 | 14436.6345 | 37966.7469 | 0.38024 | 15541.5842 | 37966.7469 | 0.40935 | 47666.1154 | 73097.8877 | 0.65209 | 36.56% | 0.36686 | 0.22343 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5852.8779 | 588.92 | 1111.4225 | 4152.5354 | 0.02485%
2026 | Tier-3 | 157 | 157-273R | Tier-3---14 | 5--4 | 100% | 8.5826 | 8.5826 | 1867.403 | 95.01% | 4.712% | 0.2778% | 686.6124 | 94.668 | 37.1477 | 554.7967 | 295.5257 | 13155.327 | 14224.956 | 0.92481 | 13820.7026 | 14224.956 | 0.97158 | 43435.5622 | 27715.4303 | 1.5672 | 36.77% | 0.32295 | 0.18936 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 6235.6919 | 859.7582 | 337.3687 | 5038.5649 | 0.02264%
2026 | Tier-3 | 73 | 73-23R | Tier-3---9 | 5--5 | 100% | 8.3244 | 8.3244 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 908.6137 | 146.7723 | 33.9609 | 727.8805 | 263.2033 | 17408.8179 | 13348.0843 | 1.3042 | 18321.1176 | 13348.0843 | 1.3726 | 57479.5134 | 25399.3463 | 2.263 | 15.85% | 0.21349 | 0.13148 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 36698.5525 | 5928.0747 | 1371.6681 | 29398.8097 | 0.02996%
2027 | Tier-3 | 973 | 973-1245R | Tier-3---6 | 5--5 | 100% | 3.3857 | 3.3857 | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 3422.2157 | 586.5406 | 18.8757 | 2816.7994 | 114.3472 | 62548.2039 | 5312.167 | 11.7745 | 65641.3087 | 5312.167 | 12.3568 | 217552.9068 | 10844.9056 | 20.0604 | 39.7% | 0.12039 | 0.069838 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 74427.8884 | 12756.3499 | 410.5176 | 61261.0209 | 0.1129%
2027 | Tier-3 | 973 | 973-626R | Tier-3---7 | 5--5 | 100% | 11.0435 | 11.0435 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 3292.8403 | 574.3225 | 47.7921 | 2670.7257 | 338.4744 | 60183.5947 | 16696.7131 | 3.6045 | 63362.0116 | 16696.7131 | 3.7949 | 209328.4083 | 33180.6363 | 6.3088 | 50.49% | 0.1523 | 0.087516 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 36894.693 | 6435.0071 | 535.488 | 29924.198 | 0.1086%
2027 | Tier-3 | 448 | 448-9R | Tier-3---9 | 5--4 | 100% | 18.008 | 18.008 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 1153.3377 | 144.8267 | 144.6235 | 863.8874 | 1699.5645 | 21079.677 | 48201.8512 | 0.43732 | 22558.4941 | 48201.8512 | 0.468 | 73318.5722 | 127061.7812 | 0.57703 | 20.43% | 0.54394 | 0.32907 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 13648.9651 | 1713.9258 | 1711.5209 | 10223.5185 | 0.03803%
2027 | Tier-3 | 973 | 973-1226R | Tier-3---10 | 5--5 | 100% | 8.59 | 8.59 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 2607.7989 | 409.5215 | 53.8288 | 2144.4486 | 270.0686 | 47663.0193 | 13111.4702 | 3.6352 | 50030.3007 | 13111.4702 | 3.8158 | 165779.7947 | 26240.8527 | 6.3176 | 50.36% | 0.13989 | 0.079405 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 32366.7739 | 5082.7885 | 668.0972 | 26615.8882 | 0.086%
2027 | Tier-2 | 1243 | 1243-45R | Tier-2---7 | 4--5 | 100% | 4.279 | 4.279 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 755.9533 | 118.8555 | 5.6827 | 631.4152 | 134.1524 | 13816.64 | 6524.3529 | 2.1177 | 14452.9121 | 6524.3529 | 2.2152 | 48056.5389 | 13047.4259 | 3.6832 | 40.24% | 0.087615 | 0.051647 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21732.8777 | 3416.9726 | 163.3705 | 18152.5345 | 0.02493%
2027 | Tier-2 | 1243 | 1243-319R | Tier-2---9 | 4--4 | 100% | 3.3629 | 3.3629 | 1178.043 | 99.35% | 0.5195% | 0.1323% | 574.847 | 89.3879 | 2.3083 | 483.1509 | 100.9714 | 10506.5411 | 5046.0004 | 2.0822 | 10975.0218 | 5046.0004 | 2.175 | 36543.4721 | 9970.5222 | 3.6652 | 48.8% | 0.081051 | 0.04611 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 13081.5607 | 2034.1639 | 52.5292 | 10994.8677 | 0.01896%
2027 | Tier-3 | 448 | 448-724R | Tier-3---18 | 5--2 | 100% | 8.8782 | 8.8782 | 520.639 | 76.18% | 22.78% | 1.038% | 97.8365 | 5.2471 | 44.7035 | 47.886 | 276.6977 | 1788.1687 | 13506.9172 | 0.13239 | 2043.3688 | 13506.9172 | 0.15128 | 6219.5439 | 26966.6525 | 0.23064 | 18.79% | 0.55035 | 0.32352 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 1306.8868 | 70.0894 | 597.1433 | 639.654 | 0.003226%
2027 | Tier-3 | 973 | 973-530AE | Tier-3---17 | 5--3 | 100% | 0.034712 | 0.034712 | 388.0062 | 6.476% | 93.52% | 0.007746% | 22.6781 | 0.80994 | 16.2531 | 5.615 | 0.43443 | 414.4898 | 40.9767 | 10.1153 | 501.6659 | 40.9767 | 12.2427 | 1441.6635 | 64.2782 | 22.4285 | 5.845% | 0.10542 | 0.10538 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3466.8676 | 123.8174 | 2484.6633 | 858.3868 | 0.0007478%
2027 | Tier-2 | 1243 | 1243-38R | Tier-2---16 | 4--3 | 100% | 0.35057 | 0.35057 | 158.2514 | 99.48% | 0.3681% | 0.155% | 98.1896 | 15.6134 | 0.20431 | 82.3719 | 4.3875 | 1794.6217 | 413.8422 | 4.3365 | 1875.4351 | 413.8422 | 4.5318 | 6241.9885 | 649.1746 | 9.6153 | 62.05% | 0.072591 | 0.041133 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 1460.1989 | 232.1898 | 3.0383 | 1224.9708 | 0.003238%
2028 | Tier-3 | TM1 | TM1-10R | Tier-3---12 | 5--5 | 100% | 3.4326 | 3.4326 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 2006.3849 | 316.2244 | 6.8025 | 1683.3579 | 163.4372 | 34981.5585 | 5965.9762 | 5.8635 | 36647.5843 | 5965.9762 | 6.1428 | 128172.6755 | 14083.8999 | 9.1007 | 53.04% | 0.093421 | 0.053413 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 33259.2914 | 5241.9654 | 112.7637 | 27904.5622 | 0.06616%
2028 | Tier-3 | 1233 | 1233-585R | Tier-3---12 | 5--5 | 100% | 6.3138 | 6.3138 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 1825.8875 | 299.9406 | 20.8938 | 1505.0531 | 232.496 | 31834.565 | 9785.8264 | 3.2531 | 33489.2825 | 9785.8264 | 3.4222 | 116642.0692 | 21553.4465 | 5.4118 | 51.26% | 0.12988 | 0.074306 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 23363.7459 | 3837.9894 | 267.353 | 19258.4036 | 0.06021%
2028 | Tier-2 | 452 | 452-38AE | Tier-2---4 | 2--5 | 100% | 2.8002 | 2.8002 | 2823.7515 | 99.93% | 0% | 0.06613% | 1540.3131 | 325.5201 | 0.064842 | 1214.7281 | 116.7289 | 26855.541 | 4577.4266 | 5.867 | 28534.7596 | 4577.4266 | 6.2338 | 98398.8902 | 10428.8329 | 9.4353 | 54.55% | 0.011395 | 0.0065598 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 195652.063 | 41347.8784 | 8.2363 | 154295.9483 | 0.05079%
2028 | Tier-3 | 1458 | 1458-1058F | Tier-3---13 | 5--5 | 100% | 1.4878 | 1.4878 | 2365.6896 | 85.54% | 14.42% | 0.04244% | 1044.1272 | 160.4984 | 134.8752 | 748.7536 | 43.1105 | 18204.482 | 2102.3907 | 8.6589 | 19727.8843 | 2102.3907 | 9.3835 | 66701.3494 | 4333.0504 | 15.3936 | 44.14% | 0.13833 | 0.078995 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 16729.6968 | 2571.6109 | 2161.0602 | 11997.0257 | 0.03443%
2028 | Tier-3 | 79 | 79-660R | Tier-3---14 | 5--3 | 100% | 7.6593 | 7.6593 | 2087.0386 | 97.47% | 2.263% | 0.2704% | 1172.7783 | 159.1243 | 20.5307 | 993.1233 | 294.7673 | 20447.5284 | 12093.0825 | 1.6908 | 21374.1071 | 12093.0825 | 1.7675 | 74919.8872 | 26959.4889 | 2.779 | 56.19% | 0.45747 | 0.26157 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 3495.2341 | 474.2386 | 61.1878 | 2959.8078 | 0.03867%
2028 | Tier-2 | 520 | 520-45 | Tier-2---8 | 5--5 | 100% | 9.5877 | 9.5877 | 2044.6463 | 97.57% | 2.13% | 0.298% | 714.2318 | 93.1426 | 16.5447 | 604.5444 | 343.7511 | 12452.7155 | 14697.8673 | 0.84725 | 13018.433 | 14697.8673 | 0.88574 | 45626.8368 | 32135.3356 | 1.4198 | 34.93% | 0.10446 | 0.065251 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 20389.3067 | 2658.9604 | 472.3056 | 17258.0407 | 0.02355%

## SPRP
Strategic Pole Replacement - Risk & Cost Benefit | [29 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[30 empty] | Year | Total Units | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%)
back to index | [29 empty] | 2026 | 200 | 98550.2033 | 1326.0872 | 1.346% | 23296.553 | 5259.5998 | 4.4293 | 23296.553 | 5259.5998 | 4.4293 | 58729.9288 | 5540.6275 | 10.5999 | 0.04373%
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [12 empty] | 2027 | 200 | 100008.7722 | 1504.1815 | 1.504% | 25207.9347 | 5017.3009 | 5.0242 | 25207.9347 | 5017.3009 | 5.0242 | 66943.9477 | 5567.7874 | 12.0234 | 0.0496%
[9 empty] | Capital Cost only in Year 0 | 25 | K$/unit | 2025-06-30 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [12 empty] | 2028 | 200 | 81394.9393 | 1107.8034 | 1.361% | 17709.9434 | 4786.1642 | 3.7002 | 17709.9434 | 4786.1642 | 3.7002 | 49544.7312 | 5595.0805 | 8.8551 | 0.03653%
[9 empty] | Service Drop factor | 0% | % | 2025-06-30 | Factor to account for Service drop miles |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [12 empty] | Total 2026-2028 | 600 | 279953.9148 | 3938.0722 | 1.407% | 66214.4311 | 15063.0649 | 4.3958 | 66214.4311 | 15063.0649 | 4.3958 | 175218.6077 | 16703.4953 | 10.4899 | 0.1299%
[9 empty] | OH to UG conversion factor | 0% | % | 2025-06-30 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-06-30 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 40 | Years | 2025-06-30 | Expected lifetime (defined as 40 years) of the infrastructure
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[9 empty] | Mitigation Effectiveness Estimate (%) | 39% | % | 2025-06-30
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 2.568 | K$/unit | 2025-06-30 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized.
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 127 | 4 | 860.3234 | 98.08% | 1.495% | 0.4234% | 10.365 | 0 | 0 | 10.365 | 0 | 182.0907 | 105.192 | 1.731 | 182.0907 | 105.192 | 1.731 | 459.0454 | 110.8125 | 4.1425 | 1.205% | 0.078224 | 0.077263 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11000.8833 | 0 | 0 | 11000.8833 | 0.0003418%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 55 | 2 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 22.1817 | 0 | 0 | 22.1817 | 0 | 389.6857 | 52.596 | 7.409 | 389.6857 | 52.596 | 7.409 | 982.3861 | 55.4063 | 17.7306 | 1.399% | 0.11902 | 0.11733 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13321.2377 | 0 | 0 | 13321.2377 | 0.0007315%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 469 | 34 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 256.9728 | 0 | 0 | 256.9728 | 0 | 4514.4689 | 894.132 | 5.049 | 4514.4689 | 894.132 | 5.049 | 11380.8442 | 941.9067 | 12.0828 | 2.714% | 0.13914 | 0.1352 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68142.3368 | 0 | 0 | 68142.3368 | 0.008474%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 380 | 12 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 45.2649 | 0 | 0 | 45.2649 | 0 | 795.2084 | 315.576 | 2.5199 | 795.2084 | 315.576 | 2.5199 | 2004.6971 | 332.4376 | 6.0303 | 1.199% | 0.12816 | 0.12658 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29455.3135 | 0 | 0 | 29455.3135 | 0.001493%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 119 | 2 | 585.5086 | 87.68% | 11.85% | 0.4758% | 3.3649 | 0 | 0 | 3.3649 | 0 | 59.1141 | 52.596 | 1.1239 | 59.1141 | 52.596 | 1.1239 | 149.025 | 55.4063 | 2.6897 | 0.5747% | 0.083403 | 0.082857 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7025.9084 | 0 | 0 | 7025.9084 | 0.000111%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 103 | 8 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 120.9483 | 0 | 0 | 120.9483 | 0 | 2124.8058 | 210.384 | 10.0997 | 2124.8058 | 210.384 | 10.0997 | 5356.5732 | 221.6251 | 24.1695 | 3.002% | 0.19114 | 0.18535 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21084.5906 | 0 | 0 | 21084.5906 | 0.003988%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 239 | 22 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 153.5351 | 0 | 0 | 153.5351 | 0 | 2697.2879 | 578.556 | 4.6621 | 2697.2879 | 578.556 | 4.6621 | 6799.7839 | 609.469 | 11.1569 | 3.501% | 0.20232 | 0.19506 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21695.2111 | 0 | 0 | 21695.2111 | 0.005063%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 300 | 7 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 50.6076 | 0 | 0 | 50.6076 | 0 | 889.0682 | 184.086 | 4.8296 | 889.0682 | 184.086 | 4.8296 | 2241.3148 | 193.922 | 11.5578 | 0.8814% | 0.20491 | 0.20305 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28027.3969 | 0 | 0 | 28027.3969 | 0.001669%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 52 | 1 | 836.2457 | 79.76% | 20.09% | 0.1547% | 5.0023 | 0 | 0 | 5.0023 | 0 | 87.8803 | 26.298 | 3.3417 | 87.8803 | 26.298 | 3.3417 | 221.5436 | 27.7031 | 7.9971 | 0.5982% | 0.16555 | 0.16431 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5059.0325 | 0 | 0 | 5059.0325 | 0.000165%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 342 | 7 | 1857.5393 | 97.83% | 1.797% | 0.3696% | 14.5065 | 0 | 0 | 14.5065 | 0 | 254.8486 | 184.086 | 1.3844 | 254.8486 | 184.086 | 1.3844 | 642.466 | 193.922 | 3.313 | 0.781% | 0.04682 | 0.046446 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39680.802 | 0 | 0 | 39680.802 | 0.0004784%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 856 | 14 | 6370.0414 | 98.47% | 1.262% | 0.272% | 40.008 | 0 | 0 | 40.008 | 0 | 702.8562 | 368.172 | 1.909 | 702.8562 | 368.172 | 1.909 | 1771.88 | 387.8439 | 4.5685 | 0.6281% | 0.10309 | 0.10244 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61795.4772 | 0 | 0 | 61795.4772 | 0.001319%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 459 | 12 | 1350.4062 | 95.97% | 3.342% | 0.6845% | 13.2145 | 0 | 0 | 13.2145 | 0 | 232.1511 | 315.576 | 0.73564 | 232.1511 | 315.576 | 0.73564 | 585.2462 | 332.4376 | 1.7605 | 0.9786% | 0.063274 | 0.062629 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21350.9806 | 0 | 0 | 21350.9806 | 0.0004358%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 398 | 5 | 18774.394 | 95.55% | 4.388% | 0.06321% | 87.891 | 0 | 0 | 87.891 | 0 | 1544.0593 | 131.49 | 11.7428 | 1544.0593 | 131.49 | 11.7428 | 3892.5284 | 138.5157 | 28.1017 | 0.4681% | 0.15307 | 0.15232 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122682.5864 | 0 | 0 | 122682.5864 | 0.002898%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 753 | 26 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 344.5715 | 0 | 0 | 344.5715 | 0 | 6053.3944 | 683.748 | 8.8533 | 6053.3944 | 683.748 | 8.8533 | 15260.4303 | 720.2816 | 21.1868 | 1.338% | 0.15161 | 0.14957 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169810.7026 | 0 | 0 | 169810.7026 | 0.01136%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 369 | 20 | 4323.2442 | 99.81% | 0% | 0.1903% | 91.2117 | 0 | 0 | 91.2117 | 0 | 1602.3976 | 525.96 | 3.0466 | 1602.3976 | 525.96 | 3.0466 | 4039.5975 | 554.0627 | 7.2909 | 2.11% | 0.043095 | 0.042184 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100323.9818 | 0 | 0 | 100323.9818 | 0.003008%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 804 | 24 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 49.4757 | 0 | 0 | 49.4757 | 0 | 829.1427 | 602.0761 | 1.3771 | 829.1427 | 602.0761 | 1.3771 | 2201.9291 | 668.1345 | 3.2956 | 1.061% | 0.17153 | 0.16953 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27218.997 | 0 | 0 | 27218.997 | 0.001632%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 1069 | 23 | 8462.8018 | 99.74% | 0% | 0.2593% | 70.8274 | 0 | 0 | 70.8274 | 0 | 1186.9667 | 576.9896 | 2.0572 | 1186.9667 | 576.9896 | 2.0572 | 3152.1914 | 640.2955 | 4.923 | 0.8369% | 0.11169 | 0.11076 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75770.2151 | 0 | 0 | 75770.2151 | 0.002336%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 334 | 5 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 28.681 | 0 | 0 | 28.681 | 0 | 480.6524 | 125.4325 | 3.832 | 480.6524 | 125.4325 | 3.832 | 1276.4541 | 139.1947 | 9.1703 | 0.5807% | 0.047931 | 0.047652 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103054.3 | 0 | 0 | 103054.3 | 0.0009458%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 436 | 6 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 17.1863 | 0 | 0 | 17.1863 | 0 | 301.9273 | 157.788 | 1.9135 | 301.9273 | 157.788 | 1.9135 | 761.1499 | 166.2188 | 4.5792 | 0.5074% | 0.070488 | 0.07011 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48064.9586 | 0 | 0 | 48064.9586 | 0.0005667%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 464 | 10 | 3753.23 | 95.85% | 3.876% | 0.273% | 30.2377 | 0 | 0 | 30.2377 | 0 | 531.2126 | 262.98 | 2.02 | 531.2126 | 262.98 | 2.02 | 1339.1715 | 277.0314 | 4.834 | 0.8056% | 0.10094 | 0.10009 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37197.0378 | 0 | 0 | 37197.0378 | 0.0009971%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 359 | 9 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 180.83 | 0 | 0 | 180.83 | 0 | 3030.4527 | 225.7785 | 13.4222 | 3030.4527 | 225.7785 | 13.4222 | 8047.8815 | 250.5504 | 32.1208 | 0.9715% | 0.11814 | 0.11698 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157576.7226 | 0 | 0 | 157576.7226 | 0.005963%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 481 | 40 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 659.6545 | 0 | 0 | 659.6545 | 0 | 11054.8682 | 1003.4602 | 11.0167 | 11054.8682 | 1003.4602 | 11.0167 | 29358.0782 | 1113.5575 | 26.3642 | 3.216% | 0.13939 | 0.13487 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147184.919 | 0 | 0 | 147184.919 | 0.02175%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 89 | 5 | 3653.654 | 88.54% | 11.39% | 0.07412% | 70.8747 | 0 | 0 | 70.8747 | 0 | 1187.758 | 125.4325 | 9.4693 | 1187.758 | 125.4325 | 9.4693 | 3154.2929 | 139.1947 | 22.661 | 1.94% | 0.080555 | 0.07879 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45472.7214 | 0 | 0 | 45472.7214 | 0.002337%
2027 | 450 | 450-114F | Tier-1 | Non-HFTD---7 | 1--4 | 25 | 2 | 28.615 | 98.32% | 0% | 1.684% | 0.87775 | 0 | 0 | 0.87775 | 0 | 14.7098 | 50.173 | 0.29318 | 14.7098 | 50.173 | 0.29318 | 39.0645 | 55.6779 | 0.70162 | 3.067% | 0.0023436 | 0.0022705 | 12209.8338 | 1908.2658 | 365.7567 | 9935.8114 | 12216.4564 | 0 | 0 | 12216.4564 | 2.894e-05%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 209 | 6 | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 91.926 | 0 | 0 | 91.926 | 0 | 1540.5481 | 150.519 | 10.2349 | 1540.5481 | 150.519 | 10.2349 | 4091.1868 | 167.0336 | 24.4932 | 1.111% | 0.099477 | 0.098363 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83183.4801 | 0 | 0 | 83183.4801 | 0.003031%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 44 | 13 | 792.2018 | 92.77% | 7.138% | 0.09408% | 84.6819 | 0 | 0 | 84.6819 | 0 | 1419.1473 | 326.1246 | 4.3516 | 1419.1473 | 326.1246 | 4.3516 | 3768.7865 | 361.9062 | 10.4137 | 10.69% | 0.075291 | 0.066616 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10620.9339 | 0 | 0 | 10620.9339 | 0.002792%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 70 | 18 | 1132.2887 | 95.25% | 4.625% | 0.1242% | 108.1599 | 0 | 0 | 108.1599 | 0 | 1812.6047 | 451.5571 | 4.0141 | 1812.6047 | 451.5571 | 4.0141 | 4813.6794 | 501.1009 | 9.6062 | 9.552% | 0.079085 | 0.071154 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14393.1511 | 0 | 0 | 14393.1511 | 0.003567%
2027 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 143 | 2 | 894.3745 | 42.96% | 56.7% | 0.3423% | 2.0958 | 0 | 0 | 2.0958 | 0 | 35.1229 | 50.173 | 0.70004 | 35.1229 | 50.173 | 0.70004 | 93.2749 | 55.6779 | 1.6753 | 0.2343% | 0.082954 | 0.082502 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 10815.2469 | 0 | 0 | 10815.2469 | 6.911e-05%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 93 | 1 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.11052 | 0 | 0 | 0.11052 | 0 | 1.8522 | 25.0865 | 0.073831 | 1.8522 | 25.0865 | 0.073831 | 4.9187 | 27.8389 | 0.17668 | 0.0945% | 0.031092 | 0.030961 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3773.9851 | 0 | 0 | 3773.9851 | 3.645e-06%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 606 | 6 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 21.0026 | 0 | 0 | 21.0026 | 0 | 351.9739 | 150.519 | 2.3384 | 351.9739 | 150.519 | 2.3384 | 934.7264 | 167.0336 | 5.596 | 0.3724% | 0.088602 | 0.08826 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63662.2953 | 0 | 0 | 63662.2953 | 0.0006926%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 140 | 2 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 17.4289 | 0 | 0 | 17.4289 | 0 | 292.0841 | 50.173 | 5.8215 | 292.0841 | 50.173 | 5.8215 | 775.6788 | 55.6779 | 13.9315 | 0.5559% | 0.020337 | 0.020224 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154173.9795 | 0 | 0 | 154173.9795 | 0.0005747%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 84 | 2 | 1708.3855 | 99.57% | 0.3134% | 0.112% | 15.7961 | 0 | 0 | 15.7961 | 0 | 264.7202 | 50.173 | 5.2761 | 264.7202 | 50.173 | 5.2761 | 703.0093 | 55.6779 | 12.6264 | 0.9246% | 0.014781 | 0.014644 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115582.8731 | 0 | 0 | 115582.8731 | 0.0005209%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 319 | 6 | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 16.0943 | 0 | 0 | 16.0943 | 0 | 269.7172 | 150.519 | 1.7919 | 269.7172 | 150.519 | 1.7919 | 716.2799 | 167.0336 | 4.2882 | 0.7279% | 0.043997 | 0.043674 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50259.1967 | 0 | 0 | 50259.1967 | 0.0005307%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 295 | 1 | 1554.328 | 69.02% | 30.62% | 0.3611% | 1.4183 | 0 | 0 | 1.4183 | 0 | 23.7687 | 25.0865 | 0.94747 | 23.7687 | 25.0865 | 0.94747 | 63.1219 | 27.8389 | 2.2674 | 0.09125% | 0.068691 | 0.0686 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22637.1713 | 0 | 0 | 22637.1713 | 4.677e-05%
2027 | 920 | 920-823 | Tier-2 | Tier-2---11 | 4--4 | 127 | 5 | 458.2189 | 68.35% | 31.14% | 0.5113% | 4.8086 | 0 | 0 | 4.8086 | 0 | 80.5851 | 125.4325 | 0.64246 | 80.5851 | 125.4325 | 0.64246 | 214.0073 | 139.1947 | 1.5375 | 1.049% | 0.054577 | 0.053739 | 8395.8542 | 937.9397 | 2311.5146 | 5146.3999 | 8437.2964 | 0 | 0 | 8437.2964 | 0.0001586%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 291 | 6 | 765.4961 | 75% | 24.28% | 0.7274% | 4.6164 | 0 | 0 | 4.6164 | 0 | 77.3639 | 150.519 | 0.51398 | 77.3639 | 150.519 | 0.51398 | 205.4531 | 167.0336 | 1.23 | 0.6031% | 0.11418 | 0.11326 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6718.0107 | 0 | 0 | 6718.0107 | 0.0001522%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 622 | 12 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 49.548 | 0 | 0 | 49.548 | 0 | 830.3535 | 301.0381 | 2.7583 | 830.3535 | 301.0381 | 2.7583 | 2205.1446 | 334.0672 | 6.6009 | 0.7456% | 0.082825 | 0.082202 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80242.0225 | 0 | 0 | 80242.0225 | 0.001634%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 352 | 3 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 10.8286 | 0 | 0 | 10.8286 | 0 | 181.4725 | 75.2595 | 2.4113 | 181.4725 | 75.2595 | 2.4113 | 481.9311 | 83.5168 | 5.7705 | 0.3287% | 0.044658 | 0.04451 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73782.444 | 0 | 0 | 73782.444 | 0.0003571%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 303 | 6 | 1438.4419 | 90% | 9.47% | 0.5268% | 9.9982 | 0 | 0 | 9.9982 | 0 | 167.5562 | 150.519 | 1.1132 | 167.5562 | 150.519 | 1.1132 | 444.9738 | 167.0336 | 2.664 | 0.6951% | 0.066431 | 0.065918 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21669.8885 | 0 | 0 | 21669.8885 | 0.0003297%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 253 | 3 | 1074.3257 | 89.49% | 10.08% | 0.4258% | 4.4463 | 0 | 0 | 4.4463 | 0 | 74.5136 | 75.2595 | 0.99009 | 74.5136 | 75.2595 | 0.99009 | 197.8834 | 83.5168 | 2.3694 | 0.4139% | 0.049006 | 0.048779 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 21933.1201 | 0 | 0 | 21933.1201 | 0.0001466%
2028 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 104 | 2 | 2758.283 | 96.49% | 3.415% | 0.0991% | 19.9601 | 0 | 0 | 19.9601 | 0 | 319.0928 | 47.8616 | 6.667 | 319.0928 | 47.8616 | 6.667 | 892.683 | 55.9508 | 15.9548 | 0.7236% | 0.10617 | 0.10537 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 25987.6034 | 0 | 0 | 25987.6034 | 0.0006582%
2028 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | 5--4 | 31 | 3 | 1005.6854 | 94.09% | 5.81% | 0.1042% | 35.7115 | 0 | 0 | 35.7115 | 0 | 570.904 | 71.7925 | 7.9521 | 570.904 | 71.7925 | 7.9521 | 1597.1415 | 83.9262 | 19.0303 | 3.551% | 0.097832 | 0.09414 | 10279.6968 | 1573.4563 | 574.8933 | 8131.3471 | 10303.5439 | 0 | 0 | 10303.5439 | 0.001178%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 10 | 2 | 409.0622 | 99.15% | 0.7717% | 0.07851% | 31.6356 | 0 | 0 | 31.6356 | 0 | 505.7436 | 47.8616 | 10.5668 | 505.7436 | 47.8616 | 10.5668 | 1414.8509 | 55.9508 | 25.2874 | 7.734% | 0.094213 | 0.086864 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4345.0186 | 0 | 0 | 4345.0186 | 0.001043%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 146 | 17 | 4222.2471 | 91.41% | 8.486% | 0.103% | 175.2674 | 0 | 0 | 175.2674 | 0 | 2801.9189 | 406.824 | 6.8873 | 2801.9189 | 406.824 | 6.8873 | 7838.5522 | 475.5818 | 16.482 | 4.151% | 0.12846 | 0.12263 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33002.5897 | 0 | 0 | 33002.5897 | 0.00578%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 534 | 20 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 227.1478 | 0 | 0 | 227.1478 | 0 | 3631.3066 | 478.6164 | 7.5871 | 3631.3066 | 478.6164 | 7.5871 | 10158.8191 | 559.508 | 18.1567 | 1.423% | 0.1351 | 0.13313 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118157.8291 | 0 | 0 | 118157.8291 | 0.00749%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 260 | 8 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 19.0174 | 0 | 0 | 19.0174 | 0 | 334.0958 | 210.384 | 1.588 | 334.0958 | 210.384 | 1.588 | 842.2457 | 221.6251 | 3.8003 | 1.103% | 0.048222 | 0.047643 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35786.064 | 0 | 0 | 35786.064 | 0.0006271%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 132 | 5 | 1279.0443 | 99.78% | 0% | 0.2159% | 18.8542 | 0 | 0 | 18.8542 | 0 | 301.4132 | 119.6541 | 2.519 | 301.4132 | 119.6541 | 2.519 | 843.2232 | 139.877 | 6.0283 | 1.474% | 0.014019 | 0.013812 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91239.4422 | 0 | 0 | 91239.4422 | 0.0006217%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 413 | 7 | 2976.5734 | 99.75% | 0% | 0.2502% | 19.6264 | 0 | 0 | 19.6264 | 0 | 313.7587 | 167.5157 | 1.873 | 313.7587 | 167.5157 | 1.873 | 877.7606 | 195.8278 | 4.4823 | 0.6594% | 0.038208 | 0.037955 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77906.1596 | 0 | 0 | 77906.1596 | 0.0006472%
2028 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | 3--5 | 302 | 1 | 1585.8519 | 99.67% | 0% | 0.3254% | 2.0413 | 0 | 0 | 2.0413 | 0 | 32.6332 | 23.9308 | 1.3636 | 32.6332 | 23.9308 | 1.3636 | 91.2935 | 27.9754 | 3.2633 | 0.1287% | 0.026002 | 0.025968 | 60989.6136 | 9907.2213 | 216.3013 | 50866.0909 | 60989.8702 | 0 | 0 | 60989.8702 | 6.731e-05%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 1069 | 77 | 8462.8018 | 99.74% | 0% | 0.2593% | 237.1179 | 0 | 0 | 237.1179 | 0 | 3790.6951 | 1842.6732 | 2.0572 | 3790.6951 | 1842.6732 | 2.0572 | 10604.7188 | 2154.106 | 4.923 | 2.802% | 0.11169 | 0.10856 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75774.2306 | 0 | 0 | 75774.2306 | 0.007819%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 227 | 12 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 25.9459 | 0 | 0 | 25.9459 | 0 | 414.7856 | 287.1699 | 1.4444 | 414.7856 | 287.1699 | 1.4444 | 1160.3899 | 335.7048 | 3.4566 | 1.907% | 0.045228 | 0.044296 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30124.3631 | 0 | 0 | 30124.3631 | 0.0008556%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 9 | 1 | 105.2026 | 98.18% | 1.532% | 0.2854% | 4.4759 | 0 | 0 | 4.4759 | 0 | 71.5548 | 23.9308 | 2.9901 | 71.5548 | 23.9308 | 2.9901 | 200.1792 | 27.9754 | 7.1555 | 4.255% | 0.026216 | 0.02508 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.2786 | 0 | 0 | 4016.2786 | 0.0001476%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 53 | 6 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 96.7915 | 0 | 0 | 96.7915 | 0 | 1547.3606 | 143.5849 | 10.7766 | 1547.3606 | 143.5849 | 10.7766 | 4328.843 | 167.8524 | 25.7896 | 4.021% | 0.10098 | 0.09652 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23937.4606 | 0 | 0 | 23937.4606 | 0.003192%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 109 | 2 | 4762.848 | 95.55% | 4.384% | 0.07015% | 32.5646 | 0 | 0 | 32.5646 | 0 | 520.5958 | 47.8616 | 10.8771 | 520.5958 | 47.8616 | 10.8771 | 1456.401 | 55.9508 | 26.03 | 0.6837% | 0.11001 | 0.10922 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43309.8419 | 0 | 0 | 43309.8419 | 0.001074%
2028 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 523 | 2 | 2227.2808 | 89.28% | 10.33% | 0.3978% | 2.9655 | 0 | 0 | 2.9655 | 0 | 47.4086 | 47.8616 | 0.99053 | 47.4086 | 47.8616 | 0.99053 | 132.6287 | 55.9508 | 2.3705 | 0.1331% | 0.091496 | 0.09136 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24346.8305 | 0 | 0 | 24346.8305 | 9.779e-05%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 140 | 2 | 1455.0528 | 89.01% | 10.72% | 0.2619% | 7.2162 | 0 | 0 | 7.2162 | 0 | 115.3615 | 47.8616 | 2.4103 | 115.3615 | 47.8616 | 2.4103 | 322.7313 | 55.9508 | 5.7681 | 0.4959% | 0.072601 | 0.072197 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20054.0533 | 0 | 0 | 20054.0533 | 0.000238%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 748 | 16 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 23.0761 | 0 | 0 | 23.0761 | 0 | 368.9074 | 382.8931 | 0.96347 | 368.9074 | 382.8931 | 0.96347 | 1032.0428 | 447.6064 | 2.3057 | 0.7356% | 0.15664 | 0.15533 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20046.8011 | 0 | 0 | 20046.8011 | 0.000761%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 20 | 1 | 625.5425 | 99.9% | 0% | 0.09615% | 12.1864 | 0 | 0 | 12.1864 | 0 | 194.8176 | 23.9308 | 8.1409 | 194.8176 | 23.9308 | 8.1409 | 545.015 | 27.9754 | 19.4819 | 1.948% | 0.0036434 | 0.0035724 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171695.2413 | 0 | 0 | 171695.2413 | 0.0004019%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 71 | 3 | 2823.7515 | 99.93% | 0% | 0.06613% | 46.5015 | 0 | 0 | 46.5015 | 0 | 743.3976 | 71.7925 | 10.3548 | 743.3976 | 71.7925 | 10.3548 | 2079.7037 | 83.9262 | 24.7801 | 1.647% | 0.011395 | 0.011207 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247804.5811 | 0 | 0 | 247804.5811 | 0.001533%
2028 | 452 | 452-717 | Tier-2 | Tier-2---19 | 1--5 | 17 | 1 | 24.802 | 99.04% | 0% | 0.9608% | 0.56352 | 0 | 0 | 0.56352 | 0 | 9.0087 | 23.9308 | 0.37645 | 9.0087 | 23.9308 | 0.37645 | 25.2026 | 27.9754 | 0.90088 | 2.272% | 0.000973 | 0.00095068 | 25490.2561 | 9086.828 | 25.5586 | 16377.8695 | 25496.0064 | 0 | 0 | 25496.0064 | 1.858e-05%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 93 | 1 | 116.9577 | 22.53% | 76.17% | 1.295% | 0.11052 | 0 | 0 | 0.11052 | 0 | 1.7668 | 23.9308 | 0.073831 | 1.7668 | 23.9308 | 0.073831 | 4.9428 | 27.9754 | 0.17668 | 0.0945% | 0.031092 | 0.030961 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3773.9851 | 0 | 0 | 3773.9851 | 3.645e-06%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 90 | 2 | 379.7423 | 70.28% | 29.01% | 0.71% | 2.313 | 0 | 0 | 2.313 | 0 | 36.9764 | 47.8616 | 0.77257 | 36.9764 | 47.8616 | 0.77257 | 103.444 | 55.9508 | 1.8488 | 0.6091% | 0.038566 | 0.038232 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9872.0906 | 0 | 0 | 9872.0906 | 7.627e-05%
2028 | 387 | CB 387 | Tier-1 | Non-HFTD---2 | 4--4 | 257 | 3 | 522.65 | 70.14% | 28.94% | 0.9137% | 1.669 | 0 | 0 | 1.669 | 0 | 26.6809 | 71.7925 | 0.37164 | 26.6809 | 71.7925 | 0.37164 | 74.6415 | 83.9262 | 0.88937 | 0.3193% | 0.067633 | 0.067325 | 7727.6908 | 947.907 | 2193.816 | 4585.9679 | 7738.2429 | 0 | 0 | 7738.2429 | 5.504e-05%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 145 | 1 | 669.8148 | 14.34% | 85.25% | 0.4034% | 0.25839 | 0 | 0 | 0.25839 | 0 | 4.1308 | 23.9308 | 0.17262 | 4.1308 | 23.9308 | 0.17262 | 11.5562 | 27.9754 | 0.41309 | 0.03858% | 0.10036 | 0.10009 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6689.5389 | 0 | 0 | 6689.5389 | 8.521e-06%
2028 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 259 | 5 | 305.5692 | 37.2% | 61.32% | 1.484% | 0.85577 | 0 | 0 | 0.85577 | 0 | 13.6809 | 119.6541 | 0.11434 | 13.6809 | 119.6541 | 0.11434 | 38.2731 | 139.877 | 0.27362 | 0.2801% | 0.044603 | 0.044267 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 6883.5047 | 0 | 0 | 6883.5047 | 2.822e-05%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 357 | 3 | 2730.9177 | 98.3% | 1.373% | 0.325% | 8.7981 | 0 | 0 | 8.7981 | 0 | 140.6508 | 71.7925 | 1.9591 | 140.6508 | 71.7925 | 1.9591 | 393.4799 | 83.9262 | 4.6884 | 0.3222% | 0.054655 | 0.054475 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 49969.6313 | 0 | 0 | 49969.6313 | 0.0002901%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 244 | 1 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 6.1021 | 0 | 0 | 6.1021 | 0 | 97.5521 | 23.9308 | 4.0764 | 97.5521 | 23.9308 | 4.0764 | 272.9084 | 27.9754 | 9.7553 | 0.1551% | 0.19925 | 0.19893 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19748.5641 | 0 | 0 | 19748.5641 | 0.0002012%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 344 | 4 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 68.0473 | 0 | 0 | 68.0473 | 0 | 1087.8405 | 95.7233 | 11.3644 | 1087.8405 | 95.7233 | 11.3644 | 3043.3054 | 111.9016 | 27.1963 | 0.4492% | 0.14704 | 0.14637 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103029.307 | 0 | 0 | 103029.307 | 0.002244%

## Distribution_Underbuilt
Distribution Underbuilt - Risk & Cost Benefit | [29 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[30 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%)
back to index | [29 empty] | 2026 | 1.2 | 436.6355 | 14.4962 | 3.32% | 254.6684 | 1002.8739 | 0.25394 | 254.6684 | 1002.8739 | 0.25394 | 642.0115 | 862586.3257 | 0.00074429 | 0.000478%
[9 empty] | Assumptions | Value | Units | Last Update | Comments | [16 empty] | 2027 | 7.1 | 1573.1982 | 276.3828 | 17.57% | 4631.7812 | 5660.3187 | 0.81829 | 4631.7812 | 5660.3187 | 0.81829 | 12300.4808 | 5128653.5826 | 0.0023984 | 0.009114%
[9 empty] | Capital Cost only in Year 0 | 714.81 | K$/unit | 2025-06-30 | [5 empty] | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [11 empty] | 2028 | 3 | 5195.4029 | 83.1538 | 1.601% | 1329.3409 | 2281.504 | 0.58266 | 1329.3409 | 2281.504 | 0.58266 | 3718.9185 | 2177659.4541 | 0.0017078 | 0.002742%
[9 empty] | Service Drop factor | 0% | % | 2025-06-30 | Factor to account for Service drop miles | [16 empty] | Total 2026-2028 | 11.3 | 7205.2366 | 374.0328 | 5.191% | 6215.7904 | 8944.6966 | 0.69491 | 6215.7904 | 8944.6966 | 0.69491 | 16661.4108 | 8168899.3623 | 0.0020396 | 0.01233%
[9 empty] | OH to UG conversion factor | 0% | % | 2025-06-30 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 8.0298 | K$/unit | 2025-06-30 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 40 | Years | 2025-06-30 | Expected lifetime (defined as 40 years) of the infrastructure
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[9 empty] | Mitigation Effectiveness Estimate (%) | 39% | % | 2025-06-30
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | K$/unit | 2025-06-30 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized. | [24 empty] | `
[13 empty] | [1] | [1] | [1]
[6 empty] | OH miles | OH miles | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | HFTD Tier | Feeder | Feeder Segment | Tranche ID HTM | Tranche ID Quintile | Units (OH Primary + Secondary miles + Service Drop) | OH miles in scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | Tier-1 | 963 | 963-35 | Non-HFTD---7 | 2--3 | 3.1555 | 0.28411 | 30.7376 | 94.18% | 0% | 5.818% | 1.0165 | 0 | 0 | 1.0165 | 2.2813 | 17.8584 | 237.4397 | 0.075212 | 17.8584 | 237.4397 | 0.075212 | 45.0204 | 204225.2766 | 0.00022044 | 3.307% | 0.012897 | 0.012444 | 2383.2808 | 325.3782 | 213.264 | 1844.6386 | 2388.3273 | 0 | 0 | 2388.3273 | 3.352e-05%
2026 | Tier-2 | 1162 | 1162-324R | Tier-2---13 | 4--3 | 3.3255 | 0.29785 | 240.2897 | 88.19% | 10.99% | 0.8202% | 7.402 | 0 | 0 | 7.402 | 2.3917 | 130.0368 | 248.924 | 0.5224 | 130.0368 | 248.924 | 0.5224 | 327.8189 | 214103.1619 | 0.0015311 | 3.08% | 0.068658 | 0.06626 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3514.7689 | 0 | 0 | 3514.7689 | 0.0002441%
2026 | Tier-2 | 536 | CB 536 | Tier-2---18 | 4--2 | 1.5002 | 0.49161 | 54.1099 | 76.19% | 21.99% | 1.82% | 5.2691 | 0 | 0 | 5.2691 | 3.9475 | 92.5675 | 410.8539 | 0.22531 | 92.5675 | 410.8539 | 0.22531 | 233.3599 | 353381.3433 | 0.00066036 | 9.738% | 0.063476 | 0.055363 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 882.1884 | 0 | 0 | 882.1884 | 0.0001738%
2026 | Tier-2 | 535 | CB 535 | Tier-2---16 | 4--3 | 0.31174 | 0.12642 | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.80862 | 0 | 0 | 0.80862 | 1.0152 | 14.2058 | 105.6563 | 0.13445 | 14.2058 | 105.6563 | 0.13445 | 35.8124 | 90876.5439 | 0.00039408 | 0.7252% | 0.059698 | 0.050256 | 1867.7052 | 14.9488 | 1426.0626 | 426.6938 | 2202.5112 | 0 | 0 | 2202.5112 | 2.667e-05%
2027 | Tier-2 | 91 | CB 91 | Tier-2---12 | 3--5 | 2.7814 | 2.7814 | 337.7351 | 93.43% | 6.078% | 0.496% | 123.0571 | 0 | 0 | 123.0571 | 22.3341 | 2062.2617 | 2217.4256 | 0.93003 | 2062.2617 | 2217.4256 | 0.93003 | 5476.6859 | 2009146.2104 | 0.0027259 | 36.44% | 0.015476 | 0.0094402 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 22740.7329 | 0 | 0 | 22740.7329 | 0.004058%
2027 | Tier-3 | 524 | CB 524 | Tier-3---17 | 3--5 | 3.4998 | 1.6723 | 481.3309 | 94.25% | 5.298% | 0.4514% | 84.5385 | 0 | 0 | 84.5385 | 13.4278 | 1416.7442 | 1333.1726 | 1.0627 | 1416.7442 | 1333.1726 | 1.0627 | 3762.4047 | 1207949.7679 | 0.0031147 | 17.56% | 0.018139 | 0.014758 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26885.7112 | 0 | 0 | 26885.7112 | 0.002788%
2027 | Tier-2 | 300 | 300-484F | Tier-2---9 | 4--5 | 10.4561 | 2.6463 | 754.1323 | 92.41% | 6.882% | 0.7076% | 68.7872 | 0 | 0 | 68.7872 | 21.2493 | 1152.7752 | 2109.7204 | 0.54641 | 1152.7752 | 2109.7204 | 0.54641 | 3061.3902 | 1911557.6043 | 0.0016015 | 9.121% | 0.039922 | 0.035982 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 19047.1478 | 0 | 0 | 19047.1478 | 0.002268%
2028 | Tier-2 | 522 | 522-34 | Tier-2---16 | 4--3 | 1.8014 | 0.10646 | 112.7117 | 43.02% | 55.81% | 1.165% | 1.1178 | 0 | 0 | 1.1178 | 0.85488 | 17.8693 | 80.9659 | 0.2207 | 17.8693 | 80.9659 | 0.2207 | 49.9906 | 77280.6904 | 0.00064687 | 0.9917% | 0.030009 | 0.029317 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3806.4203 | 0 | 0 | 3806.4203 | 3.686e-05%
2028 | Tier-2 | 231 | 231-1136R | Tier-2---7 | 4--5 | 13.2557 | 0.80491 | 2730.9177 | 98.3% | 1.373% | 0.325% | 63.5744 | 0 | 0 | 63.5744 | 6.4633 | 1016.334 | 612.138 | 1.6603 | 1016.334 | 612.138 | 1.6603 | 2843.2612 | 584275.9888 | 0.0048663 | 2.328% | 0.054655 | 0.05336 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 49987.4233 | 0 | 0 | 49987.4233 | 0.002096%
2028 | Tier-2 | FB1 | CB FB1 | Tier-2---11 | 4--4 | 7.7129 | 0.34893 | 346.5871 | 36.93% | 61.45% | 1.621% | 2.2582 | 0 | 0 | 2.2582 | 2.8018 | 36.1011 | 265.3636 | 0.13604 | 36.1011 | 265.3636 | 0.13604 | 100.9951 | 253285.3396 | 0.00039874 | 0.6516% | 0.04664 | 0.045817 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7515.2933 | 0 | 0 | 7515.2933 | 7.447e-05%
2028 | Tier-2 | 522 | 522-36 | Tier-2---16 | 4--3 | 2.2803 | 0.38579 | 116.9577 | 22.53% | 76.17% | 1.295% | 1.7389 | 0 | 0 | 1.7389 | 3.0978 | 27.7995 | 293.3902 | 0.094753 | 27.7995 | 293.3902 | 0.094753 | 77.7709 | 280036.3479 | 0.00027772 | 1.487% | 0.031092 | 0.02904 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3967.5716 | 0 | 0 | 3967.5716 | 5.734e-05%
2028 | Tier-2 | 212 | 212-1204R | Tier-2---8 | 5--4 | 10.0072 | 0.105 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 6.1031 | 0 | 0 | 6.1031 | 0.84314 | 97.5674 | 79.8538 | 1.2218 | 97.5674 | 79.8538 | 1.2218 | 272.9512 | 76219.1424 | 0.0035811 | 0.3886% | 0.19221 | 0.19142 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8171.9644 | 0 | 0 | 8171.9644 | 0.0002013%
2028 | Tier-2 | 523 | CB 523 | Tier-2---13 | 4--4 | 6.3104 | 1.1676 | 305.5692 | 37.2% | 61.32% | 1.484% | 8.2021 | 0 | 0 | 8.2021 | 9.3755 | 131.123 | 887.9559 | 0.14767 | 131.123 | 887.9559 | 0.14767 | 366.8252 | 847539.8792 | 0.00043281 | 2.684% | 0.044603 | 0.041384 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7185.4833 | 0 | 0 | 7185.4833 | 0.0002705%
2028 | Tier-2 | 521 | CB 521 | Tier-2---20 | 3--1 | 0.41062 | 0.08131 | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1593 | 0 | 0 | 0.1593 | 0.6529 | 2.5466 | 61.8366 | 0.041183 | 2.5466 | 61.8366 | 0.041183 | 7.1244 | 59022.0657 | 0.00012071 | 1.297% | 0.025917 | 0.023915 | 473.952 | 7.4349 | 392.0671 | 74.45 | 506.9562 | 0 | 0 | 506.9562 | 5.253e-06%

## OH Hardening
OH Hardening - Risk & Cost Benefit | [29 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[30 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%)
back to index | [29 empty] | 2026 | 6.5934 | 20046.7249 | 812.9708 | 4.055% | 14282.18 | 6550.3476 | 2.1804 | 14282.18 | 6550.3476 | 2.1804 | 36004.9581 | 6902.6224 | 5.2161 | 0.02681%
[9 empty] | Assumptions | Value | Units | Last Update | Comments | [16 empty] | 2027 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0%
[9 empty] | Capital Cost only in Year 0 | 1 | M$/unit | 2025-06-30 | [5 empty] | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [11 empty] | 2028 | 0 | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0 | 0 | --- | 0%
[9 empty] | Service Drop factor | 0% | % | 2025-06-30 | Factor to account for Service drop miles | [16 empty] | Total 2026-2028 | 6.5934 | 20046.7249 | 812.9708 | 4.055% | 14282.18 | 6550.3476 | 2.1804 | 14282.18 | 6550.3476 | 2.1804 | 36004.9581 | 6902.6224 | 5.2161 | 0.02681%
[9 empty] | OH to UG conversion factor | 0% | % | 2025-06-30 | Factor to account for OH to UG extra miles
[9 empty] | Long-term Ongoing costs | 0.0080298 | $/mile | 2025-06-30 | Includes ongoing foundational costs expected over the entire lifespan.
[9 empty] | Lifetime | 40 | Years | 2025-06-30 | Expected lifetime (defined as 40 years) of the infrastructure
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[9 empty] | Mitigation Effectiveness Estimate (%) | 39% | % | 2025-06-30
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0.041292 | M$/unit | 2025-06-30 | This cost does not represent annual O&M activities; it is incurred during the installation that cannot be capitalized. | [24 empty] | `
[13 empty] | [1] | [1] | [1]
[6 empty] | OH miles | OH miles | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Units (OH Primary + Secondary miles + Service Drop) | OH miles in scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 18.1587 | 0.46231 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 15.1399 | 0 | 0 | 15.1399 | 0.0037122 | 265.9759 | 459.2937 | 0.5791 | 265.9759 | 459.2937 | 0.5791 | 670.5175 | 483.9943 | 1.3854 | 0.8367% | 0.39031 | 0.38643 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4643.4645 | 0 | 0 | 4643.4645 | 0.0004993%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 8.351 | 3.0742 | 333.8465 | 96.62% | 2.31% | 1.072% | 46.3092 | 0 | 0 | 46.3092 | 0.024685 | 813.5553 | 3054.1831 | 0.26637 | 813.5553 | 3054.1831 | 0.26637 | 2050.9492 | 3218.4357 | 0.63725 | 13.87% | 0.14886 | 0.12749 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2255.3896 | 0 | 0 | 2255.3896 | 0.001527%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 8.4553 | 0.97197 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 232.9531 | 0 | 0 | 232.9531 | 0.0078047 | 4092.4938 | 965.6274 | 4.2382 | 4092.4938 | 965.6274 | 4.2382 | 10317.0572 | 1017.5584 | 10.139 | 4.428% | 0.26107 | 0.24937 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20162.0699 | 0 | 0 | 20162.0699 | 0.007682%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 5.3305 | 1.0949 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 177.5723 | 0 | 0 | 177.5723 | 0.0087917 | 3119.571 | 1087.7434 | 2.8679 | 3119.571 | 1087.7434 | 2.8679 | 7864.3472 | 1146.2418 | 6.861 | 7.654% | 0.24779 | 0.22794 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9399.2134 | 0 | 0 | 9399.2134 | 0.005856%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 11.5801 | 0.98996 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 340.9962 | 0 | 0 | 340.9962 | 0.0079491 | 5990.584 | 983.5 | 6.0911 | 5990.584 | 983.5 | 6.0911 | 15102.087 | 1036.3922 | 14.5718 | 3.303% | 0.21878 | 0.21148 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47198.5292 | 0 | 0 | 47198.5292 | 0.01124%
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A
#N/A

## Veg--->
back to index

## Pole_Clearing
Pole Brushing - Risk & Cost Benefit | [30 empty] | Summary Table |  |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[31 empty] | Year | Total Units (Poles) | Total Units (Miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%)
back to index | [30 empty] | 2026 | 22000 | 1500 | 2882839.1756 | 139231.1772 | 4.83% | 132817.0839 | 8604.4672 | 15.4358 | 132817.0839 | 8604.4672 | 15.4358 | 139913.683 | 9064.2157 | 15.4358 | 4.591%
[10 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [12 empty] | 2027 | 22000 | 1500 | 2882839.1756 | 139231.1772 | 4.83% | 126698.4746 | 8208.0771 | 15.4358 | 126698.4746 | 8208.0771 | 15.4358 | 140599.5344 | 9108.6481 | 15.4358 | 4.591%
[10 empty] | Capital Cost only in Year 0 | 0.41 | k$/structure | 2025-06-30 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [12 empty] | 2028 | 22000 | 1500 | 2882839.1756 | 139231.1772 | 4.83% | 120861.7371 | 7829.9479 | 15.4358 | 120861.7371 | 7829.9479 | 15.4358 | 141288.7478 | 9153.2984 | 15.4358 | 4.591%
[10 empty] | Service Drop factor | 0% | % | 2025-06-30 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [12 empty] | Total 2026-2028 | 66000 | 4500 | 8648517.5267 | 417693.5316 | 4.83% | 380377.2956 | 24642.4923 | 15.4358 | 380377.2956 | 24642.4923 | 15.4358 | 421801.9651 | 27326.1622 | 15.4358 | 13.77%
[10 empty] | OH to UG conversion factor | 0% | % | 2025-06-30
[10 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-06-30
[10 empty] | Lifetime | 1 | Years | 2025-06-30
[10 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[10 empty] | Mitigation Effectiveness Estimate (%) | 4.95% | % | 2025-06-30
[10 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-06-30
[14 empty] | [1] | [1] | [1] | [2]
[9 empty] | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Scoped Mileage | Scoped Poles | Poles in the Scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 18.9705 | 264 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1888.0784 | 103.2536 | 18.2858 | 1888.0784 | 103.2536 | 18.2858 | 1988.961 | 108.7706 | 18.2858 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 16.9478 | 243 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 642.8121 | 95.0403 | 6.7636 | 642.8121 | 95.0403 | 6.7636 | 677.1585 | 100.1184 | 6.7636 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 16.4216 | 230 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 255.1218 | 89.9558 | 2.8361 | 255.1218 | 89.9558 | 2.8361 | 268.7533 | 94.7623 | 2.8361 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 16.3387 | 208 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 394.1517 | 81.3513 | 4.8451 | 394.1517 | 81.3513 | 4.8451 | 415.2118 | 85.698 | 4.8451 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 16.241 | 202 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 3060.5719 | 79.0047 | 38.7391 | 3060.5719 | 79.0047 | 38.7391 | 3224.1024 | 83.226 | 38.7391 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 15.1902 | 204 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 858.8326 | 79.7869 | 10.7641 | 858.8326 | 79.7869 | 10.7641 | 904.7212 | 84.05 | 10.7641 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 14.975 | 232 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 765.8108 | 90.738 | 8.4398 | 765.8108 | 90.738 | 8.4398 | 806.7292 | 95.5863 | 8.4398 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 12.4911 | 168 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 185.1522 | 65.7068 | 2.8179 | 185.1522 | 65.7068 | 2.8179 | 195.0451 | 69.2176 | 2.8179 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 12.3702 | 175 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 240.4359 | 68.4446 | 3.5129 | 240.4359 | 68.4446 | 3.5129 | 253.2827 | 72.1017 | 3.5129 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 12.0312 | 165 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 151.314 | 64.5335 | 2.3447 | 151.314 | 64.5335 | 2.3447 | 159.3989 | 67.9816 | 2.3447 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 11.9654 | 158 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 183.9604 | 61.7957 | 2.9769 | 183.9604 | 61.7957 | 2.9769 | 193.7897 | 65.0975 | 2.9769 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 11.4812 | 153 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3711.5659 | 59.8402 | 62.0247 | 3711.5659 | 59.8402 | 62.0247 | 3909.88 | 63.0375 | 62.0247 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 11.2437 | 150 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 79.3622 | 58.6668 | 1.3528 | 79.3622 | 58.6668 | 1.3528 | 83.6027 | 61.8015 | 1.3528 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 11.1024 | 166 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1330.4034 | 64.9246 | 20.4915 | 1330.4034 | 64.9246 | 20.4915 | 1401.4886 | 68.3936 | 20.4915 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 10.8361 | 146 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 71.9999 | 57.1024 | 1.2609 | 71.9999 | 57.1024 | 1.2609 | 75.847 | 60.1534 | 1.2609 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 10.2901 | 149 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1445.8524 | 58.2757 | 24.8106 | 1445.8524 | 58.2757 | 24.8106 | 1523.1063 | 61.3895 | 24.8106 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 10.1733 | 154 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 239.6048 | 60.2313 | 3.9781 | 239.6048 | 60.2313 | 3.9781 | 252.4072 | 63.4495 | 3.9781 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 9.5585 | 147 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 162.4058 | 57.4935 | 2.8248 | 162.4058 | 57.4935 | 2.8248 | 171.0834 | 60.5654 | 2.8248 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 9.4763 | 129 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 120.5219 | 50.4535 | 2.3888 | 120.5219 | 50.4535 | 2.3888 | 126.9615 | 53.1493 | 2.3888 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 9.4722 | 119 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 479.8394 | 46.5423 | 10.3097 | 479.8394 | 46.5423 | 10.3097 | 505.4779 | 49.0292 | 10.3097 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 9.219 | 142 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 739.2025 | 55.5379 | 13.3099 | 739.2025 | 55.5379 | 13.3099 | 778.6991 | 58.5054 | 13.3099 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 9.1274 | 116 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 249.0215 | 45.369 | 5.4888 | 249.0215 | 45.369 | 5.4888 | 262.327 | 47.7931 | 5.4888 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 9.0834 | 125 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1227.409 | 48.889 | 25.106 | 1227.409 | 48.889 | 25.106 | 1292.9912 | 51.5012 | 25.106 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 8.8391 | 106 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 157.4433 | 41.4579 | 3.7977 | 157.4433 | 41.4579 | 3.7977 | 165.8557 | 43.673 | 3.7977 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 8.769 | 159 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 483.4663 | 62.1868 | 7.7744 | 483.4663 | 62.1868 | 7.7744 | 509.2986 | 65.5096 | 7.7744 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2026 | 221 | 221-1251R | Tier-1 | Non-HFTD---2 | 5--4 | 8.6538 | 112 | 100% | 1814.8505 | 87.56% | 11.92% | 0.5209% | 78.6628 | 0 | 0 | 78.6628 | 0 | 75.039 | 43.8046 | 1.713 | 75.039 | 43.8046 | 1.713 | 79.0484 | 46.1451 | 1.713 | 4.334% | 0.27478 | 0.26118 | 6604.7785 | 826.9947 | 747.1453 | 5030.6385 | 6647.5552 | 0 | 0 | 6647.5552 | 0.002594%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 8.5037 | 120 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 960.4166 | 46.9335 | 20.4634 | 960.4166 | 46.9335 | 20.4634 | 1011.733 | 49.4412 | 20.4634 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 8.4854 | 124 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 985.7421 | 48.4979 | 20.3255 | 985.7421 | 48.4979 | 20.3255 | 1038.4116 | 51.0892 | 20.3255 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 8.4423 | 124 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2590.0334 | 48.4979 | 53.4051 | 2590.0334 | 48.4979 | 53.4051 | 2728.4224 | 51.0892 | 53.4051 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 8.4285 | 130 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1926.6067 | 50.8446 | 37.8921 | 1926.6067 | 50.8446 | 37.8921 | 2029.5479 | 53.5613 | 37.8921 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 8.2367 | 113 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1185.2748 | 44.1957 | 26.8188 | 1185.2748 | 44.1957 | 26.8188 | 1248.6056 | 46.5571 | 26.8188 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 8.1575 | 139 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 287.5688 | 54.3646 | 5.2896 | 287.5688 | 54.3646 | 5.2896 | 302.934 | 57.2694 | 5.2896 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 8.072 | 95 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 124.7575 | 37.1557 | 3.3577 | 124.7575 | 37.1557 | 3.3577 | 131.4234 | 39.1409 | 3.3577 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 8.0514 | 112 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 526.6286 | 43.8046 | 12.0222 | 526.6286 | 43.8046 | 12.0222 | 554.7671 | 46.1451 | 12.0222 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 7.8648 | 104 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 602.1374 | 40.6757 | 14.8034 | 602.1374 | 40.6757 | 14.8034 | 634.3104 | 42.849 | 14.8034 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2026 | 221 | 221-1249R | Tier-1 | Non-HFTD---2 | 5--2 | 7.8246 | 94 | 100% | 329.3718 | 60.93% | 35.44% | 3.632% | 9.9343 | 0 | 0 | 9.9343 | 0 | 9.4767 | 36.7645 | 0.25777 | 9.4767 | 36.7645 | 0.25777 | 9.983 | 38.7289 | 0.25777 | 3.016% | 0.32343 | 0.30742 | 1018.3674 | 70.1582 | 373.9946 | 574.2146 | 1039.0867 | 0 | 0 | 1039.0867 | 0.0003276%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 7.7595 | 100 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 633.9221 | 39.1112 | 16.2082 | 633.9221 | 39.1112 | 16.2082 | 667.7935 | 41.201 | 16.2082 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 7.7298 | 114 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 253.1828 | 44.5868 | 5.6784 | 253.1828 | 44.5868 | 5.6784 | 266.7107 | 46.9691 | 5.6784 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 7.7249 | 134 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1208.2563 | 52.409 | 23.0544 | 1208.2563 | 52.409 | 23.0544 | 1272.8151 | 55.2093 | 23.0544 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 7.6943 | 120 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1739.5055 | 46.9335 | 37.0632 | 1739.5055 | 46.9335 | 37.0632 | 1832.4497 | 49.4412 | 37.0632 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 7.5567 | 107 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1087.6046 | 41.849 | 25.9888 | 1087.6046 | 41.849 | 25.9888 | 1145.7168 | 44.085 | 25.9888 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 7.5022 | 112 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1249.9804 | 43.8046 | 28.5354 | 1249.9804 | 43.8046 | 28.5354 | 1316.7686 | 46.1451 | 28.5354 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 7.3384 | 119 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 337.9327 | 46.5423 | 7.2608 | 337.9327 | 46.5423 | 7.2608 | 355.9889 | 49.0292 | 7.2608 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 7.2729 | 117 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 522.9766 | 45.7601 | 11.4287 | 522.9766 | 45.7601 | 11.4287 | 550.9199 | 48.2051 | 11.4287 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 7.1477 | 105 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 115.3852 | 41.0668 | 2.8097 | 115.3852 | 41.0668 | 2.8097 | 121.5504 | 43.261 | 2.8097 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 7.05 | 89 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 154.5294 | 34.809 | 4.4394 | 154.5294 | 34.809 | 4.4394 | 162.7862 | 36.6689 | 4.4394 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 7.0044 | 107 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1320.7925 | 41.849 | 31.5609 | 1320.7925 | 41.849 | 31.5609 | 1391.3643 | 44.085 | 31.5609 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 6.9425 | 118 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 192.4478 | 46.1512 | 4.1699 | 192.4478 | 46.1512 | 4.1699 | 202.7306 | 48.6172 | 4.1699 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 6.9423 | 98 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 491.6709 | 38.329 | 12.8277 | 491.6709 | 38.329 | 12.8277 | 517.9415 | 40.377 | 12.8277 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 6.7285 | 96 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1750.5765 | 37.5468 | 46.6239 | 1750.5765 | 37.5468 | 46.6239 | 1844.1122 | 39.5529 | 46.6239 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 6.7134 | 96 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 227.721 | 37.5468 | 6.065 | 227.721 | 37.5468 | 6.065 | 239.8884 | 39.5529 | 6.065 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 6.6793 | 104 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1643.7869 | 40.6757 | 40.412 | 1643.7869 | 40.6757 | 40.412 | 1731.6167 | 42.849 | 40.412 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 6.6731 | 69 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 482.9506 | 26.9867 | 17.8959 | 482.9506 | 26.9867 | 17.8959 | 508.7553 | 28.4287 | 17.8959 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 6.6185 | 105 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 84.8362 | 41.0668 | 2.0658 | 84.8362 | 41.0668 | 2.0658 | 89.3691 | 43.261 | 2.0658 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 6.5844 | 101 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 169.8732 | 39.5023 | 4.3003 | 169.8732 | 39.5023 | 4.3003 | 178.9497 | 41.613 | 4.3003 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 6.5087 | 101 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 861.4981 | 39.5023 | 21.8088 | 861.4981 | 39.5023 | 21.8088 | 907.5291 | 41.613 | 21.8088 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 6.3857 | 85 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 55.7504 | 33.2445 | 1.677 | 55.7504 | 33.2445 | 1.677 | 58.7292 | 35.0208 | 1.677 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 6.3651 | 74 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 301.8886 | 28.9423 | 10.4307 | 301.8886 | 28.9423 | 10.4307 | 318.019 | 30.4887 | 10.4307 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 6.3399 | 103 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 310.9519 | 40.2846 | 7.7189 | 310.9519 | 40.2846 | 7.7189 | 327.5665 | 42.437 | 7.7189 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 6.3184 | 93 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 391.4809 | 36.3734 | 10.7628 | 391.4809 | 36.3734 | 10.7628 | 412.3983 | 38.3169 | 10.7628 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 6.2953 | 97 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 478.0277 | 37.9379 | 12.6003 | 478.0277 | 37.9379 | 12.6003 | 503.5694 | 39.965 | 12.6003 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 6.2854 | 103 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 533.1833 | 40.2846 | 13.2354 | 533.1833 | 40.2846 | 13.2354 | 561.672 | 42.437 | 13.2354 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 6.2785 | 95 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 167.585 | 37.1557 | 4.5104 | 167.585 | 37.1557 | 4.5104 | 176.5393 | 39.1409 | 4.5104 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 6.2728 | 79 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2122.0228 | 30.8979 | 68.6786 | 2122.0228 | 30.8979 | 68.6786 | 2235.4054 | 32.5488 | 68.6786 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 6.2536 | 72 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 373.1142 | 28.1601 | 13.2498 | 373.1142 | 28.1601 | 13.2498 | 393.0502 | 29.6647 | 13.2498 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 6.2492 | 99 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 205.1652 | 38.7201 | 5.2987 | 205.1652 | 38.7201 | 5.2987 | 216.1274 | 40.789 | 5.2987 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 6.192 | 88 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 262.6012 | 34.4179 | 7.6298 | 262.6012 | 34.4179 | 7.6298 | 276.6324 | 36.2569 | 7.6298 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 6.1782 | 87 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 124.1616 | 34.0268 | 3.6489 | 124.1616 | 34.0268 | 3.6489 | 130.7958 | 35.8449 | 3.6489 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 6.1766 | 109 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 398.5744 | 42.6312 | 9.3494 | 398.5744 | 42.6312 | 9.3494 | 419.8708 | 44.9091 | 9.3494 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 6.1716 | 84 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 431.684 | 32.8534 | 13.1397 | 431.684 | 32.8534 | 13.1397 | 454.7494 | 34.6088 | 13.1397 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 6.1345 | 91 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 251.2008 | 35.5912 | 7.0579 | 251.2008 | 35.5912 | 7.0579 | 264.6228 | 37.4929 | 7.0579 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 6.1235 | 100 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 814.528 | 39.1112 | 20.8259 | 814.528 | 39.1112 | 20.8259 | 858.0494 | 41.201 | 20.8259 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 6.0644 | 82 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 640.8684 | 32.0712 | 19.9827 | 640.8684 | 32.0712 | 19.9827 | 675.1109 | 33.7848 | 19.9827 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 6.0573 | 82 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 497.9891 | 32.0712 | 15.5276 | 497.9891 | 32.0712 | 15.5276 | 524.5974 | 33.7848 | 15.5276 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 6.0221 | 79 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 142.1765 | 30.8979 | 4.6015 | 142.1765 | 30.8979 | 4.6015 | 149.7732 | 32.5488 | 4.6015 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 6.015 | 81 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 78.3562 | 31.6801 | 2.4734 | 78.3562 | 31.6801 | 2.4734 | 82.5429 | 33.3728 | 2.4734 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 5.8678 | 90 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 149.4686 | 35.2001 | 4.2463 | 149.4686 | 35.2001 | 4.2463 | 157.4549 | 37.0809 | 4.2463 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 5.8655 | 70 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 396.1715 | 27.3779 | 14.4705 | 396.1715 | 27.3779 | 14.4705 | 417.3395 | 28.8407 | 14.4705 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 5.8426 | 75 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 81.2969 | 29.3334 | 2.7715 | 81.2969 | 29.3334 | 2.7715 | 85.6408 | 30.9007 | 2.7715 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 5.8078 | 82 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 76.6538 | 32.0712 | 2.3901 | 76.6538 | 32.0712 | 2.3901 | 80.7496 | 33.7848 | 2.3901 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 5.794 | 82 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 113.1467 | 32.0712 | 3.528 | 113.1467 | 32.0712 | 3.528 | 119.1922 | 33.7848 | 3.528 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 5.7925 | 77 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 431.9104 | 30.1156 | 14.3417 | 431.9104 | 30.1156 | 14.3417 | 454.988 | 31.7248 | 14.3417 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 5.7743 | 69 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 68.092 | 26.9867 | 2.5232 | 68.092 | 26.9867 | 2.5232 | 71.7303 | 28.4287 | 2.5232 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 5.7743 | 95 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 429.1796 | 37.1557 | 11.5509 | 429.1796 | 37.1557 | 11.5509 | 452.1112 | 39.1409 | 11.5509 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 5.7334 | 83 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 847.0626 | 32.4623 | 26.0937 | 847.0626 | 32.4623 | 26.0937 | 892.3223 | 34.1968 | 26.0937 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 5.6393 | 85 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1055.7106 | 33.2445 | 31.7559 | 1055.7106 | 33.2445 | 31.7559 | 1112.1187 | 35.0208 | 31.7559 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 5.6107 | 87 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 94.985 | 34.0268 | 2.7915 | 94.985 | 34.0268 | 2.7915 | 100.0601 | 35.8449 | 2.7915 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 5.5928 | 89 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 708.5447 | 34.809 | 20.3552 | 708.5447 | 34.809 | 20.3552 | 746.4032 | 36.6689 | 20.3552 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 5.5142 | 85 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1514.5818 | 33.2445 | 45.5588 | 1514.5818 | 33.2445 | 45.5588 | 1595.508 | 35.0208 | 45.5588 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 5.4426 | 107 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 200.6758 | 41.849 | 4.7952 | 200.6758 | 41.849 | 4.7952 | 211.3982 | 44.085 | 4.7952 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2026 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | 4--5 | 5.4183 | 81 | 100% | 5312.2676 | 97.77% | 1.999% | 0.2313% | 257.0917 | 0 | 0 | 257.0917 | 0 | 245.248 | 31.6801 | 7.7414 | 245.248 | 31.6801 | 7.7414 | 258.352 | 33.3728 | 7.7414 | 4.84% | 0.075145 | 0.071425 | 70693.7485 | 12854.9773 | 1446.2382 | 56392.533 | 70775.8701 | 0 | 0 | 70775.8701 | 0.008478%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 5.3672 | 95 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 336.8429 | 37.1557 | 9.0657 | 336.8429 | 37.1557 | 9.0657 | 354.8409 | 39.1409 | 9.0657 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 5.3558 | 82 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 408.1427 | 32.0712 | 12.7261 | 408.1427 | 32.0712 | 12.7261 | 429.9503 | 33.7848 | 12.7261 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 5.3395 | 81 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 873.3342 | 31.6801 | 27.5673 | 873.3342 | 31.6801 | 27.5673 | 919.9977 | 33.3728 | 27.5673 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 5.3336 | 104 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 296.1766 | 40.6757 | 7.2814 | 296.1766 | 40.6757 | 7.2814 | 312.0017 | 42.849 | 7.2814 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 5.2977 | 65 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 50.6908 | 25.4223 | 1.994 | 50.6908 | 25.4223 | 1.994 | 53.3993 | 26.7806 | 1.994 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 5.2871 | 79 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 408.7995 | 30.8979 | 13.2307 | 408.7995 | 30.8979 | 13.2307 | 430.6423 | 32.5488 | 13.2307 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 5.2523 | 72 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 71.3254 | 28.1601 | 2.5329 | 71.3254 | 28.1601 | 2.5329 | 75.1364 | 29.6647 | 2.5329 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 5.2244 | 59 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 70.4248 | 23.0756 | 3.0519 | 70.4248 | 23.0756 | 3.0519 | 74.1877 | 24.3086 | 3.0519 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 5.212 | 78 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 290.7937 | 30.5067 | 9.5321 | 290.7937 | 30.5067 | 9.5321 | 306.3312 | 32.1368 | 9.5321 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 5.1827 | 76 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 19.0725 | 29.7245 | 0.64164 | 19.0725 | 29.7245 | 0.64164 | 20.0916 | 31.3127 | 0.64164 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 5.1751 | 72 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 94.2031 | 28.1601 | 3.3453 | 94.2031 | 28.1601 | 3.3453 | 99.2365 | 29.6647 | 3.3453 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 5.0888 | 75 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1267.761 | 29.3334 | 43.219 | 1267.761 | 29.3334 | 43.219 | 1335.4992 | 30.9007 | 43.219 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 5.0843 | 94 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 418.7535 | 36.7645 | 11.3901 | 418.7535 | 36.7645 | 11.3901 | 441.128 | 38.7289 | 11.3901 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 5.0636 | 75 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 296.4305 | 29.3334 | 10.1056 | 296.4305 | 29.3334 | 10.1056 | 312.2692 | 30.9007 | 10.1056 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 5.063 | 76 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 732.0261 | 29.7245 | 24.627 | 732.0261 | 29.7245 | 24.627 | 771.1393 | 31.3127 | 24.627 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 5.0508 | 80 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 713.7946 | 31.289 | 22.813 | 713.7946 | 31.289 | 22.813 | 751.9337 | 32.9608 | 22.813 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 5.0233 | 64 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 1047.5713 | 25.0312 | 41.8507 | 1047.5713 | 25.0312 | 41.8507 | 1103.5445 | 26.3686 | 41.8507 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 4.978 | 70 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 173.5489 | 27.3779 | 6.339 | 173.5489 | 27.3779 | 6.339 | 182.8218 | 28.8407 | 6.339 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 4.9753 | 73 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 543.0092 | 28.5512 | 19.0188 | 543.0092 | 28.5512 | 19.0188 | 572.0229 | 30.0767 | 19.0188 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 4.8985 | 74 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 284.8981 | 28.9423 | 9.8437 | 284.8981 | 28.9423 | 9.8437 | 300.1206 | 30.4887 | 9.8437 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 4.8944 | 58 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 23.5661 | 22.6845 | 1.0389 | 23.5661 | 22.6845 | 1.0389 | 24.8252 | 23.8966 | 1.0389 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 4.8617 | 74 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 167.1394 | 28.9423 | 5.7749 | 167.1394 | 28.9423 | 5.7749 | 176.0699 | 30.4887 | 5.7749 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 4.8551 | 85 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 130.6179 | 33.2445 | 3.929 | 130.6179 | 33.2445 | 3.929 | 137.597 | 35.0208 | 3.929 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 4.7692 | 74 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 526.8313 | 28.9423 | 18.2028 | 526.8313 | 28.9423 | 18.2028 | 554.9807 | 30.4887 | 18.2028 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 4.7364 | 81 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 405.8445 | 31.6801 | 12.8107 | 405.8445 | 31.6801 | 12.8107 | 427.5294 | 33.3728 | 12.8107 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 4.7152 | 60 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 18.7295 | 23.4667 | 0.79813 | 18.7295 | 23.4667 | 0.79813 | 19.7302 | 24.7206 | 0.79813 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 4.6872 | 62 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 42.0166 | 24.249 | 1.7327 | 42.0166 | 24.249 | 1.7327 | 44.2616 | 25.5446 | 1.7327 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 4.6403 | 67 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 786.9145 | 26.2045 | 30.0297 | 786.9145 | 26.2045 | 30.0297 | 828.9604 | 27.6047 | 30.0297 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 4.613 | 70 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 163.4677 | 27.3779 | 5.9708 | 163.4677 | 27.3779 | 5.9708 | 172.202 | 28.8407 | 5.9708 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 4.6105 | 71 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 312.9422 | 27.769 | 11.2695 | 312.9422 | 27.769 | 11.2695 | 329.6631 | 29.2527 | 11.2695 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 4.5567 | 59 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 428.2273 | 23.0756 | 18.5576 | 428.2273 | 23.0756 | 18.5576 | 451.1081 | 24.3086 | 18.5576 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 4.5517 | 72 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 277.4933 | 28.1601 | 9.8541 | 277.4933 | 28.1601 | 9.8541 | 292.3202 | 29.6647 | 9.8541 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 4.5471 | 61 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 113.3698 | 23.8578 | 4.7519 | 113.3698 | 23.8578 | 4.7519 | 119.4273 | 25.1326 | 4.7519 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 4.5413 | 78 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 384.6902 | 30.5067 | 12.61 | 384.6902 | 30.5067 | 12.61 | 405.2447 | 32.1368 | 12.61 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 4.5215 | 73 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 201.9487 | 28.5512 | 7.0732 | 201.9487 | 28.5512 | 7.0732 | 212.7391 | 30.0767 | 7.0732 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 4.5105 | 78 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 318.8395 | 30.5067 | 10.4514 | 318.8395 | 30.5067 | 10.4514 | 335.8755 | 32.1368 | 10.4514 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 4.4665 | 60 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 936.1138 | 23.4667 | 39.8911 | 936.1138 | 23.4667 | 39.8911 | 986.1317 | 24.7206 | 39.8911 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 4.4447 | 63 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1325.1737 | 24.6401 | 53.7813 | 1325.1737 | 24.6401 | 53.7813 | 1395.9796 | 25.9566 | 53.7813 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 4.4326 | 62 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 61.735 | 24.249 | 2.5459 | 61.735 | 24.249 | 2.5459 | 65.0335 | 25.5446 | 2.5459 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 4.4294 | 79 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 151.2085 | 30.8979 | 4.8938 | 151.2085 | 30.8979 | 4.8938 | 159.2877 | 32.5488 | 4.8938 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 4.3685 | 55 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 320.0792 | 21.5112 | 14.8797 | 320.0792 | 21.5112 | 14.8797 | 337.1815 | 22.6605 | 14.8797 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 4.3413 | 58 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 70.6818 | 22.6845 | 3.1159 | 70.6818 | 22.6845 | 3.1159 | 74.4584 | 23.8966 | 3.1159 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 4.3085 | 63 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1102.1556 | 24.6401 | 44.7302 | 1102.1556 | 24.6401 | 44.7302 | 1161.0453 | 25.9566 | 44.7302 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 4.292 | 63 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 308.8644 | 24.6401 | 12.535 | 308.8644 | 24.6401 | 12.535 | 325.3674 | 25.9566 | 12.535 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 4.2842 | 53 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 329.0418 | 20.7289 | 15.8735 | 329.0418 | 20.7289 | 15.8735 | 346.623 | 21.8365 | 15.8735 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 4.2597 | 57 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 152.0596 | 22.2934 | 6.8208 | 152.0596 | 22.2934 | 6.8208 | 160.1843 | 23.4846 | 6.8208 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 4.1777 | 71 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 734.3072 | 27.769 | 26.4434 | 734.3072 | 27.769 | 26.4434 | 773.5422 | 29.2527 | 26.4434 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 4.175 | 75 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1264.5743 | 29.3334 | 43.1104 | 1264.5743 | 29.3334 | 43.1104 | 1332.1422 | 30.9007 | 43.1104 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 4.1306 | 59 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 589.092 | 23.0756 | 25.5288 | 589.092 | 23.0756 | 25.5288 | 620.568 | 24.3086 | 25.5288 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 4.1246 | 51 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 58.5338 | 19.9467 | 2.9345 | 58.5338 | 19.9467 | 2.9345 | 61.6614 | 21.0125 | 2.9345 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 4.0797 | 70 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 141.6855 | 27.3779 | 5.1752 | 141.6855 | 27.3779 | 5.1752 | 149.2559 | 28.8407 | 5.1752 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 4.0305 | 55 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 266.4366 | 21.5112 | 12.386 | 266.4366 | 21.5112 | 12.386 | 280.6727 | 22.6605 | 12.386 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 4.0205 | 46 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 473.1787 | 17.9912 | 26.3006 | 473.1787 | 17.9912 | 26.3006 | 498.4613 | 18.9525 | 26.3006 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 4.0063 | 72 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 234.7817 | 28.1601 | 8.3374 | 234.7817 | 28.1601 | 8.3374 | 247.3264 | 29.6647 | 8.3374 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 4.0008 | 67 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 406.782 | 26.2045 | 15.5234 | 406.782 | 26.2045 | 15.5234 | 428.5169 | 27.6047 | 15.5234 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 3.8739 | 51 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 67.9477 | 19.9467 | 3.4065 | 67.9477 | 19.9467 | 3.4065 | 71.5783 | 21.0125 | 3.4065 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 3.8709 | 52 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 156.9652 | 20.3378 | 7.7179 | 156.9652 | 20.3378 | 7.7179 | 165.3521 | 21.4245 | 7.7179 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 3.8679 | 61 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 160.2048 | 23.8578 | 6.715 | 160.2048 | 23.8578 | 6.715 | 168.7647 | 25.1326 | 6.715 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 3.8654 | 52 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 83.7784 | 20.3378 | 4.1193 | 83.7784 | 20.3378 | 4.1193 | 88.2548 | 21.4245 | 4.1193 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 3.8277 | 55 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 676.0489 | 21.5112 | 31.4278 | 676.0489 | 21.5112 | 31.4278 | 712.1711 | 22.6605 | 31.4278 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 3.8071 | 70 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 53.817 | 27.3779 | 1.9657 | 53.817 | 27.3779 | 1.9657 | 56.6925 | 28.8407 | 1.9657 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 3.7897 | 49 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 193.8402 | 19.1645 | 10.1145 | 193.8402 | 19.1645 | 10.1145 | 204.1973 | 20.1885 | 10.1145 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 3.777 | 62 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 89.1348 | 24.249 | 3.6758 | 89.1348 | 24.249 | 3.6758 | 93.8974 | 25.5446 | 3.6758 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 3.7716 | 56 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 135.4211 | 21.9023 | 6.183 | 135.4211 | 21.9023 | 6.183 | 142.6568 | 23.0725 | 6.183 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 3.762 | 57 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 175.0719 | 22.2934 | 7.8531 | 175.0719 | 22.2934 | 7.8531 | 184.4262 | 23.4846 | 7.8531 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 3.7556 | 54 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 136.9236 | 21.1201 | 6.4831 | 136.9236 | 21.1201 | 6.4831 | 144.2396 | 22.2485 | 6.4831 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 3.7382 | 64 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 180.2727 | 25.0312 | 7.2019 | 180.2727 | 25.0312 | 7.2019 | 189.905 | 26.3686 | 7.2019 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 3.729 | 53 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 518.2225 | 20.7289 | 24.9999 | 518.2225 | 20.7289 | 24.9999 | 545.9119 | 21.8365 | 24.9999 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 3.704 | 55 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 453.1135 | 21.5112 | 21.0641 | 453.1135 | 21.5112 | 21.0641 | 477.324 | 22.6605 | 21.0641 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 3.6992 | 49 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 237.9521 | 19.1645 | 12.4163 | 237.9521 | 19.1645 | 12.4163 | 250.6662 | 20.1885 | 12.4163 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 3.6983 | 73 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 142.3168 | 28.5512 | 4.9846 | 142.3168 | 28.5512 | 4.9846 | 149.921 | 30.0767 | 4.9846 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 3.666 | 64 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1054.721 | 25.0312 | 42.1363 | 1054.721 | 25.0312 | 42.1363 | 1111.0762 | 26.3686 | 42.1363 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 3.5829 | 54 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 25.6177 | 21.1201 | 1.213 | 25.6177 | 21.1201 | 1.213 | 26.9865 | 22.2485 | 1.213 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 3.5582 | 64 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 148.7546 | 25.0312 | 5.9428 | 148.7546 | 25.0312 | 5.9428 | 156.7028 | 26.3686 | 5.9428 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 3.5375 | 58 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 657.6222 | 22.6845 | 28.9899 | 657.6222 | 22.6845 | 28.9899 | 692.7598 | 23.8966 | 28.9899 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 3.4803 | 57 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 488.2028 | 22.2934 | 21.899 | 488.2028 | 22.2934 | 21.899 | 514.2881 | 23.4846 | 21.899 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 3.4792 | 59 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 89.723 | 23.0756 | 3.8882 | 89.723 | 23.0756 | 3.8882 | 94.517 | 24.3086 | 3.8882 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 3.4748 | 49 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 228.8419 | 19.1645 | 11.9409 | 228.8419 | 19.1645 | 11.9409 | 241.0693 | 20.1885 | 11.9409 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 3.4634 | 58 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 348.8651 | 22.6845 | 15.379 | 348.8651 | 22.6845 | 15.379 | 367.5055 | 23.8966 | 15.379 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 3.4338 | 51 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 574.459 | 19.9467 | 28.7997 | 574.459 | 19.9467 | 28.7997 | 605.1531 | 21.0125 | 28.7997 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 3.4306 | 44 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 284.1236 | 17.2089 | 16.5102 | 284.1236 | 17.2089 | 16.5102 | 299.3047 | 18.1284 | 16.5102 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 3.3636 | 41 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 748.0666 | 16.0356 | 46.6504 | 748.0666 | 16.0356 | 46.6504 | 788.0369 | 16.8924 | 46.6504 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 3.313 | 51 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 323.2915 | 19.9467 | 16.2078 | 323.2915 | 19.9467 | 16.2078 | 340.5654 | 21.0125 | 16.2078 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 3.2878 | 52 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 861.5285 | 20.3378 | 42.3609 | 861.5285 | 20.3378 | 42.3609 | 907.5611 | 21.4245 | 42.3609 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 3.2754 | 50 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 246.9272 | 19.5556 | 12.6269 | 246.9272 | 19.5556 | 12.6269 | 260.1209 | 20.6005 | 12.6269 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 3.2692 | 43 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 537.4279 | 16.8178 | 31.9559 | 537.4279 | 16.8178 | 31.9559 | 566.1434 | 17.7164 | 31.9559 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 3.2674 | 51 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 257.6241 | 19.9467 | 12.9156 | 257.6241 | 19.9467 | 12.9156 | 271.3893 | 21.0125 | 12.9156 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 3.2566 | 43 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 137.9346 | 16.8178 | 8.2017 | 137.9346 | 16.8178 | 8.2017 | 145.3046 | 17.7164 | 8.2017 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 3.2292 | 52 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 911.0636 | 20.3378 | 44.7965 | 911.0636 | 20.3378 | 44.7965 | 959.743 | 21.4245 | 44.7965 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 3.1944 | 52 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 103.6022 | 20.3378 | 5.0941 | 103.6022 | 20.3378 | 5.0941 | 109.1378 | 21.4245 | 5.0941 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 3.1096 | 46 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 45.5695 | 17.9912 | 2.5329 | 45.5695 | 17.9912 | 2.5329 | 48.0044 | 18.9525 | 2.5329 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 3.1062 | 56 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1099.8308 | 21.9023 | 50.2154 | 1099.8308 | 21.9023 | 50.2154 | 1158.5963 | 23.0725 | 50.2154 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 3.1055 | 42 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 687.0628 | 16.4267 | 41.826 | 687.0628 | 16.4267 | 41.826 | 723.7735 | 17.3044 | 41.826 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 3.1032 | 38 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 382.4036 | 14.8623 | 25.7298 | 382.4036 | 14.8623 | 25.7298 | 402.8359 | 15.6564 | 25.7298 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 3.1032 | 40 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 47.6389 | 15.6445 | 3.0451 | 47.6389 | 15.6445 | 3.0451 | 50.1843 | 16.4804 | 3.0451 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 3.0947 | 37 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 75.7792 | 14.4711 | 5.2366 | 75.7792 | 14.4711 | 5.2366 | 79.8282 | 15.2444 | 5.2366 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2026 | BN2 | CB BN2 | Tier-1 | Non-HFTD---1 | 4--5 | 3.0893 | 50 | 100% | 1098.8312 | 99.36% | 0% | 0.6449% | 54.0413 | 0 | 0 | 54.0413 | 0 | 51.5518 | 19.5556 | 2.6362 | 51.5518 | 19.5556 | 2.6362 | 54.3063 | 20.6005 | 2.6362 | 4.918% | 0.034221 | 0.032527 | 32110.0379 | 7492.6936 | 90.1662 | 24527.178 | 32120.8227 | 0 | 0 | 32120.8227 | 0.001782%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 3.0886 | 43 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 104.6722 | 16.8178 | 6.2239 | 104.6722 | 16.8178 | 6.2239 | 110.265 | 17.7164 | 6.2239 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 3.0856 | 48 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 117.2051 | 18.7734 | 6.2432 | 117.2051 | 18.7734 | 6.2432 | 123.4676 | 19.7765 | 6.2432 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 3.0508 | 41 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 886.2644 | 16.0356 | 55.2686 | 886.2644 | 16.0356 | 55.2686 | 933.6187 | 16.8924 | 55.2686 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 3.0423 | 31 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 246.6292 | 12.1245 | 20.3414 | 246.6292 | 12.1245 | 20.3414 | 259.807 | 12.7723 | 20.3414 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 3.0327 | 45 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 686.5258 | 17.6 | 39.007 | 686.5258 | 17.6 | 39.007 | 723.2078 | 18.5404 | 39.007 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 3.0013 | 33 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 334.0803 | 12.9067 | 25.8843 | 334.0803 | 12.9067 | 25.8843 | 351.9307 | 13.5963 | 25.8843 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 2.931 | 43 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 577.5146 | 16.8178 | 34.3394 | 577.5146 | 16.8178 | 34.3394 | 608.372 | 17.7164 | 34.3394 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 2.8346 | 48 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 277.0305 | 18.7734 | 14.7566 | 277.0305 | 18.7734 | 14.7566 | 291.8326 | 19.7765 | 14.7566 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 2.8213 | 45 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 58.7357 | 17.6 | 3.3372 | 58.7357 | 17.6 | 3.3372 | 61.8741 | 18.5404 | 3.3372 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 2.8166 | 44 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 33.1256 | 17.2089 | 1.9249 | 33.1256 | 17.2089 | 1.9249 | 34.8956 | 18.1284 | 1.9249 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 2.7905 | 43 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 158.2696 | 16.8178 | 9.4108 | 158.2696 | 16.8178 | 9.4108 | 166.7261 | 17.7164 | 9.4108 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 2.7494 | 42 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 550.1247 | 16.4267 | 33.4896 | 550.1247 | 16.4267 | 33.4896 | 579.5186 | 17.3044 | 33.4896 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 2.7478 | 42 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 530.5991 | 16.4267 | 32.301 | 530.5991 | 16.4267 | 32.301 | 558.9498 | 17.3044 | 32.301 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 2.7261 | 42 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 635.4631 | 16.4267 | 38.6847 | 635.4631 | 16.4267 | 38.6847 | 669.4168 | 17.3044 | 38.6847 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 2.678 | 32 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 219.8189 | 12.5156 | 17.5636 | 219.8189 | 12.5156 | 17.5636 | 231.5641 | 13.1843 | 17.5636 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 2.6361 | 42 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 251.8011 | 16.4267 | 15.3288 | 251.8011 | 16.4267 | 15.3288 | 265.2552 | 17.3044 | 15.3288 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 2.6311 | 29 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 40.7779 | 11.3423 | 3.5952 | 40.7779 | 11.3423 | 3.5952 | 42.9567 | 11.9483 | 3.5952 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 2.6281 | 38 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 278.8709 | 14.8623 | 18.7637 | 278.8709 | 14.8623 | 18.7637 | 293.7714 | 15.6564 | 18.7637 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 2.6018 | 32 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 100.0176 | 12.5156 | 7.9914 | 100.0176 | 12.5156 | 7.9914 | 105.3617 | 13.1843 | 7.9914 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 2.5951 | 48 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 251.9816 | 18.7734 | 13.4223 | 251.9816 | 18.7734 | 13.4223 | 265.4453 | 19.7765 | 13.4223 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2026 | 305 | CB 305 | Tier-1 | Non-HFTD---1 | 4--5 | 2.575 | 36 | 100% | 2786.7739 | 97.11% | 2.732% | 0.1605% | 133.9547 | 0 | 0 | 133.9547 | 0 | 127.7837 | 14.08 | 9.0755 | 127.7837 | 14.08 | 9.0755 | 134.6113 | 14.8324 | 9.0755 | 4.807% | 0.073949 | 0.070288 | 37685.1802 | 5958.9331 | 946.9636 | 30779.2836 | 37741.9553 | 0 | 0 | 37741.9553 | 0.004417%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 2.531 | 36 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 83.482 | 14.08 | 5.9291 | 83.482 | 14.08 | 5.9291 | 87.9426 | 14.8324 | 5.9291 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 2.5257 | 32 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 245.3601 | 12.5156 | 19.6044 | 245.3601 | 12.5156 | 19.6044 | 258.47 | 13.1843 | 19.6044 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 2.4981 | 46 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 69.6651 | 17.9912 | 3.8722 | 69.6651 | 17.9912 | 3.8722 | 73.3874 | 18.9525 | 3.8722 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 2.4941 | 35 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 129.6779 | 13.6889 | 9.4732 | 129.6779 | 13.6889 | 9.4732 | 136.6068 | 14.4203 | 9.4732 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 2.4903 | 40 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 200.3313 | 15.6445 | 12.8052 | 200.3313 | 15.6445 | 12.8052 | 211.0352 | 16.4804 | 12.8052 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 2.4751 | 38 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 165.5356 | 14.8623 | 11.138 | 165.5356 | 14.8623 | 11.138 | 174.3804 | 15.6564 | 11.138 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 2.4671 | 37 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 428.5491 | 14.4711 | 29.614 | 428.5491 | 14.4711 | 29.614 | 451.4471 | 15.2444 | 29.614 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 2.4658 | 33 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 237.4956 | 12.9067 | 18.401 | 237.4956 | 12.9067 | 18.401 | 250.1853 | 13.5963 | 18.401 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 2.4649 | 27 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 181.173 | 10.56 | 17.1565 | 181.173 | 10.56 | 17.1565 | 190.8533 | 11.1243 | 17.1565 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 2.4456 | 43 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 424.5109 | 16.8178 | 25.2417 | 424.5109 | 16.8178 | 25.2417 | 447.1931 | 17.7164 | 25.2417 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 2.4106 | 39 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 59.4254 | 15.2534 | 3.8959 | 59.4254 | 15.2534 | 3.8959 | 62.6005 | 16.0684 | 3.8959 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 2.3652 | 54 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 76.8984 | 21.1201 | 3.641 | 76.8984 | 21.1201 | 3.641 | 81.0071 | 22.2485 | 3.641 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 2.3519 | 38 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 63.5637 | 14.8623 | 4.2769 | 63.5637 | 14.8623 | 4.2769 | 66.96 | 15.6564 | 4.2769 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 2.3316 | 32 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 227.6349 | 12.5156 | 18.1881 | 227.6349 | 12.5156 | 18.1881 | 239.7978 | 13.1843 | 18.1881 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 2.3139 | 24 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 15.2309 | 9.3867 | 1.6226 | 15.2309 | 9.3867 | 1.6226 | 16.0447 | 9.8882 | 1.6226 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 2.3096 | 32 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 20.0778 | 12.5156 | 1.6042 | 20.0778 | 12.5156 | 1.6042 | 21.1505 | 13.1843 | 1.6042 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 2.308 | 33 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 231.9683 | 12.9067 | 17.9727 | 231.9683 | 12.9067 | 17.9727 | 244.3627 | 13.5963 | 17.9727 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 2.2931 | 36 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 34.2033 | 14.08 | 2.4292 | 34.2033 | 14.08 | 2.4292 | 36.0308 | 14.8324 | 2.4292 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 2.2137 | 38 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 22.2618 | 14.8623 | 1.4979 | 22.2618 | 14.8623 | 1.4979 | 23.4513 | 15.6564 | 1.4979 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 2.197 | 32 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 461.0302 | 12.5156 | 36.8365 | 461.0302 | 12.5156 | 36.8365 | 485.6637 | 13.1843 | 36.8365 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 2.1724 | 37 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 550.6852 | 14.4711 | 38.054 | 550.6852 | 14.4711 | 38.054 | 580.1091 | 15.2444 | 38.054 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 2.1631 | 32 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 83.2547 | 12.5156 | 6.6521 | 83.2547 | 12.5156 | 6.6521 | 87.7031 | 13.1843 | 6.6521 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 2.1495 | 30 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 248.9663 | 11.7334 | 21.2187 | 248.9663 | 11.7334 | 21.2187 | 262.269 | 12.3603 | 21.2187 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 2.125 | 36 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 103.331 | 14.08 | 7.3388 | 103.331 | 14.08 | 7.3388 | 108.8522 | 14.8324 | 7.3388 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 2.1166 | 37 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 421.536 | 14.4711 | 29.1294 | 421.536 | 14.4711 | 29.1294 | 444.0593 | 15.2444 | 29.1294 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 2.0966 | 30 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 253.85 | 11.7334 | 21.6349 | 253.85 | 11.7334 | 21.6349 | 267.4135 | 12.3603 | 21.6349 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2026 | 859 | 859-13F | Tier-1 | Non-HFTD---1 | 4--5 | 2.0873 | 40 | 100% | 1153.8557 | 99.35% | 0% | 0.6497% | 56.7448 | 0 | 0 | 56.7448 | 0 | 54.1307 | 15.6445 | 3.46 | 54.1307 | 15.6445 | 3.46 | 57.023 | 16.4804 | 3.46 | 4.918% | 0.035677 | 0.033911 | 32341.7236 | 5122.1729 | 819.8446 | 26399.7061 | 32352.6656 | 0 | 0 | 32352.6656 | 0.001871%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 2.0797 | 33 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 438.0272 | 12.9067 | 33.938 | 438.0272 | 12.9067 | 33.938 | 461.4316 | 13.5963 | 33.938 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 2.0717 | 32 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 147.7158 | 12.5156 | 11.8025 | 147.7158 | 12.5156 | 11.8025 | 155.6084 | 13.1843 | 11.8025 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 2.0635 | 28 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 72.5366 | 10.9511 | 6.6237 | 72.5366 | 10.9511 | 6.6237 | 76.4123 | 11.5363 | 6.6237 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 2.0555 | 26 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 39.8446 | 10.1689 | 3.9183 | 39.8446 | 10.1689 | 3.9183 | 41.9736 | 10.7123 | 3.9183 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2026 | 63 | 63-797R | Tier-1 | Non-HFTD---1 | 3--5 | 1.9943 | 28 | 100% | 1294.9207 | 95.84% | 3.945% | 0.2104% | 61.435 | 0 | 0 | 61.435 | 0 | 58.6048 | 10.9511 | 5.3515 | 58.6048 | 10.9511 | 5.3515 | 61.7362 | 11.5363 | 5.3515 | 4.744% | 0.02549 | 0.024229 | 50800.3291 | 10671.1023 | 1938.6345 | 38190.5924 | 50910.264 | 0 | 0 | 50910.264 | 0.002026%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 1.9678 | 26 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 100.8529 | 10.1689 | 9.9178 | 100.8529 | 10.1689 | 9.9178 | 106.2416 | 10.7123 | 9.9178 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2026 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | 4--5 | 1.9662 | 38 | 100% | 4233.8665 | 96.93% | 2.943% | 0.1312% | 203.133 | 0 | 0 | 203.133 | 0 | 193.7751 | 14.8623 | 13.0381 | 193.7751 | 14.8623 | 13.0381 | 204.1288 | 15.6564 | 13.0381 | 4.798% | 0.080233 | 0.076262 | 52769.5087 | 8342.6927 | 1399.583 | 43027.233 | 52853.9991 | 0 | 0 | 52853.9991 | 0.006699%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 1.9529 | 27 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 183.9861 | 10.56 | 17.4229 | 183.9861 | 10.56 | 17.4229 | 193.8167 | 11.1243 | 17.4229 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 1.9524 | 23 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 67.1788 | 8.9956 | 7.468 | 67.1788 | 8.9956 | 7.468 | 70.7683 | 9.4762 | 7.468 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 1.9416 | 22 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 45.2058 | 8.6045 | 5.2538 | 45.2058 | 8.6045 | 5.2538 | 47.6212 | 9.0642 | 5.2538 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 1.9313 | 20 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 476.2228 | 7.8222 | 60.8806 | 476.2228 | 7.8222 | 60.8806 | 501.668 | 8.2402 | 60.8806 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 1.9282 | 3 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 174.1258 | 1.1733 | 148.4023 | 174.1258 | 1.1733 | 148.4023 | 183.4296 | 1.236 | 148.4023 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 1.9167 | 27 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 430.6267 | 10.56 | 40.7789 | 430.6267 | 10.56 | 40.7789 | 453.6357 | 11.1243 | 40.7789 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 1.9116 | 29 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 548.8338 | 11.3423 | 48.3884 | 548.8338 | 11.3423 | 48.3884 | 578.1587 | 11.9483 | 48.3884 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 1.9075 | 26 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 21.1934 | 10.1689 | 2.0841 | 21.1934 | 10.1689 | 2.0841 | 22.3257 | 10.7123 | 2.0841 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 1.8959 | 25 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 17.3347 | 9.7778 | 1.7729 | 17.3347 | 9.7778 | 1.7729 | 18.261 | 10.3002 | 1.7729 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2026 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | 3--5 | 1.8897 | 36 | 100% | 1585.8519 | 99.67% | 0% | 0.3254% | 78.2443 | 0 | 0 | 78.2443 | 0 | 74.6397 | 14.08 | 5.3011 | 74.6397 | 14.08 | 5.3011 | 78.6278 | 14.8324 | 5.3011 | 4.934% | 0.026002 | 0.024715 | 60989.6136 | 9907.2213 | 216.3013 | 50866.0909 | 60999.9476 | 0 | 0 | 60999.9476 | 0.00258%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 1.8872 | 28 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 50.8518 | 10.9511 | 4.6435 | 50.8518 | 10.9511 | 4.6435 | 53.5689 | 11.5363 | 4.6435 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 1.8794 | 27 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.6262 | 10.56 | 0.72218 | 7.6262 | 10.56 | 0.72218 | 8.0337 | 11.1243 | 0.72218 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 1.875 | 19 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 405.1363 | 7.4311 | 54.5188 | 405.1363 | 7.4311 | 54.5188 | 426.7833 | 7.8282 | 54.5188 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 1.8512 | 22 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 58.2545 | 8.6045 | 6.7703 | 58.2545 | 8.6045 | 6.7703 | 61.3671 | 9.0642 | 6.7703 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 1.8462 | 35 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 538.3214 | 13.6889 | 39.3253 | 538.3214 | 13.6889 | 39.3253 | 567.0846 | 14.4203 | 39.3253 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 1.8381 | 33 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 68.4112 | 12.9067 | 5.3004 | 68.4112 | 12.9067 | 5.3004 | 72.0666 | 13.5963 | 5.3004 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 1.8306 | 32 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 238.2603 | 12.5156 | 19.0371 | 238.2603 | 12.5156 | 19.0371 | 250.9909 | 13.1843 | 19.0371 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2026 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | 4--5 | 1.8306 | 28 | 100% | 2371.786 | 97.71% | 2.108% | 0.1806% | 114.7166 | 0 | 0 | 114.7166 | 0 | 109.4319 | 10.9511 | 9.9927 | 109.4319 | 10.9511 | 9.9927 | 115.279 | 11.5363 | 9.9927 | 4.837% | 0.074138 | 0.070468 | 31991.6747 | 5091.6051 | 638.7369 | 26261.3327 | 32029.8024 | 0 | 0 | 32029.8024 | 0.003783%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 1.8025 | 10 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 157.0745 | 3.9111 | 40.161 | 157.0745 | 3.9111 | 40.161 | 165.4672 | 4.1201 | 40.161 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 1.7988 | 27 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 105.2609 | 10.56 | 9.9679 | 105.2609 | 10.56 | 9.9679 | 110.8851 | 11.1243 | 9.9679 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 1.7985 | 30 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 214.8823 | 11.7334 | 18.3138 | 214.8823 | 11.7334 | 18.3138 | 226.3638 | 12.3603 | 18.3138 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 1.7681 | 31 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 61.1326 | 12.1245 | 5.0421 | 61.1326 | 12.1245 | 5.0421 | 64.399 | 12.7723 | 5.0421 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 1.7564 | 23 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 308.4441 | 8.9956 | 34.2884 | 308.4441 | 8.9956 | 34.2884 | 324.9247 | 9.4762 | 34.2884 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2026 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 1.7092 | 24 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 37.8909 | 9.3867 | 4.0367 | 37.8909 | 9.3867 | 4.0367 | 39.9154 | 9.8882 | 4.0367 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 1.6955 | 27 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 106.3059 | 10.56 | 10.0668 | 106.3059 | 10.56 | 10.0668 | 111.9859 | 11.1243 | 10.0668 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 1.6928 | 34 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 389.022 | 13.2978 | 29.2546 | 389.022 | 13.2978 | 29.2546 | 409.808 | 14.0083 | 29.2546 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 1.685 | 34 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 27.1082 | 13.2978 | 2.0385 | 27.1082 | 13.2978 | 2.0385 | 28.5567 | 14.0083 | 2.0385 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 1.6768 | 29 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 61.1985 | 11.3423 | 5.3956 | 61.1985 | 11.3423 | 5.3956 | 64.4684 | 11.9483 | 5.3956 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2026 | 504 | 504-40R | Tier-1 | Non-HFTD---1 | 3--5 | 1.6708 | 33 | 100% | 796.3763 | 99.35% | 0% | 0.6476% | 39.1654 | 0 | 0 | 39.1654 | 0 | 37.3611 | 12.9067 | 2.8947 | 37.3611 | 12.9067 | 2.8947 | 39.3573 | 13.5963 | 2.8947 | 4.918% | 0.025961 | 0.024676 | 30675.6364 | 4949.6837 | 226.8975 | 25499.0552 | 30685.9814 | 0 | 0 | 30685.9814 | 0.001292%
2026 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 1.6678 | 25 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 484.7261 | 9.7778 | 49.5741 | 484.7261 | 9.7778 | 49.5741 | 510.6256 | 10.3002 | 49.5741 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 1.6667 | 31 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 126.7631 | 12.1245 | 10.4551 | 126.7631 | 12.1245 | 10.4551 | 133.5362 | 12.7723 | 10.4551 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 1.6595 | 28 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 387.696 | 10.9511 | 35.4023 | 387.696 | 10.9511 | 35.4023 | 408.4111 | 11.5363 | 35.4023 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2026 | 170 | 170-410R | Tier-1 | Non-HFTD---8 | 5--1 | 1.6575 | 17 | 100% | 29.1667 | 31.01% | 45.41% | 23.57% | 0.44774 | 0 | 0 | 0.44774 | 0 | 0.42711 | 6.6489 | 0.064238 | 0.42711 | 6.6489 | 0.064238 | 0.44993 | 7.0042 | 0.064238 | 1.535% | 0.10336 | 0.098244 | 282.1845 | 8.474 | 122.6089 | 151.1016 | 292.3227 | 0 | 0 | 292.3227 | 1.476e-05%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 1.6502 | 23 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 61.1593 | 8.9956 | 6.7988 | 61.1593 | 8.9956 | 6.7988 | 64.4271 | 9.4762 | 6.7988 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 1.6334 | 26 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 67.7486 | 10.1689 | 6.6623 | 67.7486 | 10.1689 | 6.6623 | 71.3684 | 10.7123 | 6.6623 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 1.633 | 20 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 68.4792 | 7.8222 | 8.7544 | 68.4792 | 7.8222 | 8.7544 | 72.1381 | 8.2402 | 8.7544 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 1.6303 | 18 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 64.4441 | 7.04 | 9.154 | 64.4441 | 7.04 | 9.154 | 67.8874 | 7.4162 | 9.154 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 1.6074 | 28 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 585.9297 | 10.9511 | 53.504 | 585.9297 | 10.9511 | 53.504 | 617.2367 | 11.5363 | 53.504 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 1.5842 | 23 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 170.5666 | 8.9956 | 18.9612 | 170.5666 | 8.9956 | 18.9612 | 179.6802 | 9.4762 | 18.9612 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 1.5812 | 24 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 175.0725 | 9.3867 | 18.6511 | 175.0725 | 9.3867 | 18.6511 | 184.4269 | 9.8882 | 18.6511 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 1.5508 | 21 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 452.3048 | 8.2134 | 55.0694 | 452.3048 | 8.2134 | 55.0694 | 476.4721 | 8.6522 | 55.0694 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 1.5471 | 28 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 376.4593 | 10.9511 | 34.3763 | 376.4593 | 10.9511 | 34.3763 | 396.5741 | 11.5363 | 34.3763 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 1.5464 | 26 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 18.4924 | 10.1689 | 1.8185 | 18.4924 | 10.1689 | 1.8185 | 19.4805 | 10.7123 | 1.8185 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 1.5456 | 31 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 450.8352 | 12.1245 | 37.1839 | 450.8352 | 12.1245 | 37.1839 | 474.924 | 12.7723 | 37.1839 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 1.5412 | 19 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 142.8022 | 7.4311 | 19.2168 | 142.8022 | 7.4311 | 19.2168 | 150.4323 | 7.8282 | 19.2168 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 1.5364 | 22 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 135.4283 | 8.6045 | 15.7393 | 135.4283 | 8.6045 | 15.7393 | 142.6644 | 9.0642 | 15.7393 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 1.5139 | 26 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 14.3975 | 10.1689 | 1.4158 | 14.3975 | 10.1689 | 1.4158 | 15.1667 | 10.7123 | 1.4158 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 1.5062 | 21 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 73.856 | 8.2134 | 8.9922 | 73.856 | 8.2134 | 8.9922 | 77.8022 | 8.6522 | 8.9922 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 1.5037 | 20 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 87.8513 | 7.8222 | 11.231 | 87.8513 | 7.8222 | 11.231 | 92.5454 | 8.2402 | 11.231 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 1.4968 | 22 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 215.6371 | 8.6045 | 25.0611 | 215.6371 | 8.6045 | 25.0611 | 227.1588 | 9.0642 | 25.0611 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 1.4952 | 31 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 85.8122 | 12.1245 | 7.0776 | 85.8122 | 12.1245 | 7.0776 | 90.3972 | 12.7723 | 7.0776 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 1.4812 | 17 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 55.7189 | 6.6489 | 8.3802 | 55.7189 | 6.6489 | 8.3802 | 58.6961 | 7.0042 | 8.3802 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 1.4789 | 19 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 237.7519 | 7.4311 | 31.994 | 237.7519 | 7.4311 | 31.994 | 250.4553 | 7.8282 | 31.994 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 1.4762 | 27 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 75.5263 | 10.56 | 7.1521 | 75.5263 | 10.56 | 7.1521 | 79.5617 | 11.1243 | 7.1521 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2026 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 1.4725 | 22 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 125.6678 | 8.6045 | 14.6049 | 125.6678 | 8.6045 | 14.6049 | 132.3824 | 9.0642 | 14.6049 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 1.4649 | 18 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.6768 | 7.04 | 0.80636 | 5.6768 | 7.04 | 0.80636 | 5.9801 | 7.4162 | 0.80636 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 1.4572 | 19 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 161.888 | 7.4311 | 21.7851 | 161.888 | 7.4311 | 21.7851 | 170.5379 | 7.8282 | 21.7851 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 1.4508 | 26 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 24.2408 | 10.1689 | 2.3838 | 24.2408 | 10.1689 | 2.3838 | 25.536 | 10.7123 | 2.3838 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 1.4439 | 18 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 99.0448 | 7.04 | 14.0688 | 99.0448 | 7.04 | 14.0688 | 104.3369 | 7.4162 | 14.0688 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2026 | 474 | 474-22AE | Tier-1 | Non-HFTD---1 | 4--5 | 1.4235 | 22 | 100% | 6435.9834 | 99.89% | 0% | 0.1146% | 318.2162 | 0 | 0 | 318.2162 | 0 | 303.5566 | 8.6045 | 35.279 | 303.5566 | 8.6045 | 35.279 | 319.7761 | 9.0642 | 35.279 | 4.944% | 0.046635 | 0.044327 | 138007.5774 | 24328.5202 | 121.2373 | 113557.8199 | 138015.8115 | 0 | 0 | 138015.8115 | 0.01049%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 1.4146 | 22 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 54.8903 | 8.6045 | 6.3793 | 54.8903 | 8.6045 | 6.3793 | 57.8231 | 9.0642 | 6.3793 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2026 | 288 | 288-18 | Tier-1 | Non-HFTD---1 | 3--5 | 1.41 | 20 | 100% | 1717.8671 | 96.12% | 3.649% | 0.229% | 81.7367 | 0 | 0 | 81.7367 | 0 | 77.9713 | 7.8222 | 9.9679 | 77.9713 | 7.8222 | 9.9679 | 82.1374 | 8.2402 | 9.9679 | 4.758% | 0.026137 | 0.024843 | 65724.9856 | 11143.2146 | 2230.6061 | 52351.1649 | 65857.7245 | 0 | 0 | 65857.7245 | 0.002695%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 1.3985 | 16 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 64.7607 | 6.2578 | 10.3488 | 64.7607 | 6.2578 | 10.3488 | 68.2209 | 6.5922 | 10.3488 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 1.3827 | 24 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 369.6702 | 9.3867 | 39.3824 | 369.6702 | 9.3867 | 39.3824 | 389.4222 | 9.8882 | 39.3824 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 1.3633 | 22 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 29.9106 | 8.6045 | 3.4762 | 29.9106 | 8.6045 | 3.4762 | 31.5088 | 9.0642 | 3.4762 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 1.3484 | 20 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 609.9489 | 7.8222 | 77.9762 | 609.9489 | 7.8222 | 77.9762 | 642.5393 | 8.2402 | 77.9762 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 1.3358 | 21 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 96.0526 | 8.2134 | 11.6947 | 96.0526 | 8.2134 | 11.6947 | 101.1849 | 8.6522 | 11.6947 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 1.3358 | 23 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 66.5395 | 8.9956 | 7.3969 | 66.5395 | 8.9956 | 7.3969 | 70.0948 | 9.4762 | 7.3969 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 1.3275 | 20 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 327.0901 | 7.8222 | 41.8154 | 327.0901 | 7.8222 | 41.8154 | 344.567 | 8.2402 | 41.8154 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 1.3154 | 22 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 70.7701 | 8.6045 | 8.2248 | 70.7701 | 8.6045 | 8.2248 | 74.5514 | 9.0642 | 8.2248 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 1.3093 | 20 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 61.0795 | 7.8222 | 7.8084 | 61.0795 | 7.8222 | 7.8084 | 64.343 | 8.2402 | 7.8084 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2026 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 1.3038 | 13 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 50.3341 | 5.0845 | 9.8996 | 50.3341 | 5.0845 | 9.8996 | 53.0235 | 5.3561 | 9.8996 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 1.3021 | 20 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 203.6169 | 7.8222 | 26.0305 | 203.6169 | 7.8222 | 26.0305 | 214.4964 | 8.2402 | 26.0305 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 1.2948 | 21 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 312.1007 | 8.2134 | 37.9992 | 312.1007 | 8.2134 | 37.9992 | 328.7766 | 8.6522 | 37.9992 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 1.2618 | 18 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 17.2331 | 7.04 | 2.4479 | 17.2331 | 7.04 | 2.4479 | 18.1539 | 7.4162 | 2.4479 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2026 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 1.2605 | 12 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 22.1263 | 4.6933 | 4.7144 | 22.1263 | 4.6933 | 4.7144 | 23.3085 | 4.9441 | 4.7144 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 1.2591 | 22 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 33.6771 | 8.6045 | 3.9139 | 33.6771 | 8.6045 | 3.9139 | 35.4765 | 9.0642 | 3.9139 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 1.257 | 18 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 139.1767 | 7.04 | 19.7694 | 139.1767 | 7.04 | 19.7694 | 146.6131 | 7.4162 | 19.7694 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2026 | 172 | 172-630R | Tier-1 | Non-HFTD---6 | 4--2 | 1.2534 | 10 | 100% | 66.3107 | 6.519% | 90.48% | 2.997% | 0.21398 | 0 | 0 | 0.21398 | 0 | 0.20413 | 3.9111 | 0.052191 | 0.20413 | 3.9111 | 0.052191 | 0.21503 | 4.1201 | 0.052191 | 0.3227% | 0.053137 | 0.050507 | 1247.9203 | 10.8427 | 1030.4852 | 206.5924 | 1308.6726 | 0 | 0 | 1308.6726 | 7.056e-06%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 1.2484 | 24 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 785.4976 | 9.3867 | 83.682 | 785.4976 | 9.3867 | 83.682 | 827.4678 | 9.8882 | 83.682 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2026 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | 4--5 | 1.2229 | 18 | 100% | 2117.8574 | 97.53% | 2.33% | 0.1416% | 102.2432 | 0 | 0 | 102.2432 | 0 | 97.5331 | 7.04 | 13.8541 | 97.5331 | 7.04 | 13.8541 | 102.7444 | 7.4162 | 13.8541 | 4.828% | 0.067442 | 0.064104 | 31402.4615 | 4988.1224 | 677.5642 | 25736.7748 | 31442.8757 | 0 | 0 | 31442.8757 | 0.003372%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 1.1787 | 15 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 210.4643 | 5.8667 | 35.8745 | 210.4643 | 5.8667 | 35.8745 | 221.7097 | 6.1801 | 35.8745 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2026 | 206 | 206-974 | Tier-1 | Non-HFTD---1 | 4--5 | 1.1741 | 24 | 100% | 1943.6719 | 99.69% | 0% | 0.3117% | 95.9119 | 0 | 0 | 95.9119 | 0 | 91.4934 | 9.3867 | 9.7471 | 91.4934 | 9.3867 | 9.7471 | 96.382 | 9.8882 | 9.7471 | 4.935% | 0.028958 | 0.027525 | 67119.4507 | 10907.8418 | 251.1395 | 55960.4695 | 67130.3452 | 0 | 0 | 67130.3452 | 0.003163%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 1.1689 | 13 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 239.9918 | 5.0845 | 47.2011 | 239.9918 | 5.0845 | 47.2011 | 252.8149 | 5.3561 | 47.2011 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 1.1689 | 22 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 203.7535 | 8.6045 | 23.68 | 203.7535 | 8.6045 | 23.68 | 214.6403 | 9.0642 | 23.68 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 1.1678 | 16 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 65.4226 | 6.2578 | 10.4546 | 65.4226 | 6.2578 | 10.4546 | 68.9182 | 6.5922 | 10.4546 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 1.1572 | 12 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 36.5689 | 4.6933 | 7.7917 | 36.5689 | 4.6933 | 7.7917 | 38.5229 | 4.9441 | 7.7917 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 1.1071 | 22 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 177.6968 | 8.6045 | 20.6517 | 177.6968 | 8.6045 | 20.6517 | 187.1914 | 9.0642 | 20.6517 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 1.0878 | 16 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 242.2939 | 6.2578 | 38.7187 | 242.2939 | 6.2578 | 38.7187 | 255.24 | 6.5922 | 38.7187 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2026 | BN1 | CB BN1 | Tier-1 | Non-HFTD---4 | 4--4 | 1.0878 | 22 | 100% | 173.8031 | 96.37% | 0% | 3.629% | 8.291 | 0 | 0 | 8.291 | 0 | 7.9091 | 8.6045 | 0.91918 | 7.9091 | 8.6045 | 0.91918 | 8.3317 | 9.0642 | 0.91918 | 4.77% | 0.028851 | 0.027423 | 6024.1621 | 939.3966 | 90.5041 | 4994.2615 | 6035.548 | 0 | 0 | 6035.548 | 0.0002734%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 1.0864 | 17 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 20.0009 | 6.6489 | 3.0082 | 20.0009 | 6.6489 | 3.0082 | 21.0696 | 7.0042 | 3.0082 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 1.0771 | 18 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 262.0699 | 7.04 | 37.2257 | 262.0699 | 7.04 | 37.2257 | 276.0727 | 7.4162 | 37.2257 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 1.0615 | 5 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 269.2064 | 1.9556 | 137.662 | 269.2064 | 1.9556 | 137.662 | 283.5905 | 2.06 | 137.662 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 1.0168 | 17 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 118.5279 | 6.6489 | 17.8267 | 118.5279 | 6.6489 | 17.8267 | 124.861 | 7.0042 | 17.8267 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 1.0038 | 17 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 152.7457 | 6.6489 | 22.9731 | 152.7457 | 6.6489 | 22.9731 | 160.9071 | 7.0042 | 22.9731 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 0.9777 | 11 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 12.3641 | 4.3022 | 2.8739 | 12.3641 | 4.3022 | 2.8739 | 13.0247 | 4.5321 | 2.8739 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 0.97273 | 16 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 183.0917 | 6.2578 | 29.2582 | 183.0917 | 6.2578 | 29.2582 | 192.8746 | 6.5922 | 29.2582 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 0.96847 | 13 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 338.4324 | 5.0845 | 66.5621 | 338.4324 | 5.0845 | 66.5621 | 356.5153 | 5.3561 | 66.5621 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 0.96776 | 19 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 198.1694 | 7.4311 | 26.6675 | 198.1694 | 7.4311 | 26.6675 | 208.7579 | 7.8282 | 26.6675 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 0.96758 | 16 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 153.8343 | 6.2578 | 24.5828 | 153.8343 | 6.2578 | 24.5828 | 162.0539 | 6.5922 | 24.5828 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 0.94539 | 16 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 64.1211 | 6.2578 | 10.2466 | 64.1211 | 6.2578 | 10.2466 | 67.5471 | 6.5922 | 10.2466 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 0.93847 | 15 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 204.4821 | 5.8667 | 34.8548 | 204.4821 | 5.8667 | 34.8548 | 215.4079 | 6.1801 | 34.8548 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2026 | 66 | CB 66 | Tier-1 | Non-HFTD---1 | 4--5 | 0.93509 | 16 | 100% | 917.8674 | 93.46% | 5.958% | 0.5799% | 42.4641 | 0 | 0 | 42.4641 | 0 | 40.5079 | 6.2578 | 6.4732 | 40.5079 | 6.2578 | 6.4732 | 42.6723 | 6.5922 | 6.4732 | 4.626% | 0.036366 | 0.034566 | 25239.7123 | 4508.1978 | 1664.2037 | 19067.3107 | 25325.6439 | 0 | 0 | 25325.6439 | 0.0014%
2026 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | 3--5 | 0.93119 | 21 | 100% | 1424.1907 | 99.61% | 0% | 0.3928% | 70.2205 | 0 | 0 | 70.2205 | 0 | 66.9856 | 8.2134 | 8.1557 | 66.9856 | 8.2134 | 8.1557 | 70.5647 | 8.6522 | 8.1557 | 4.931% | 0.028304 | 0.026903 | 50317.6471 | 8145.1206 | 368.3302 | 41804.1963 | 50327.94 | 0 | 0 | 50327.94 | 0.002316%
2026 | 170 | 170-46 | Tier-1 | Non-HFTD---6 | 5--2 | 0.93066 | 12 | 100% | 63.3107 | 39.69% | 47.72% | 12.59% | 1.2437 | 0 | 0 | 1.2437 | 0 | 1.1864 | 4.6933 | 0.25279 | 1.1864 | 4.6933 | 0.25279 | 1.2498 | 4.9441 | 0.25279 | 1.964% | 0.099838 | 0.094896 | 634.1343 | 13.2723 | 434.6906 | 186.1714 | 654.0524 | 0 | 0 | 654.0524 | 4.101e-05%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 0.90864 | 10 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 17.5537 | 3.9111 | 4.4881 | 17.5537 | 3.9111 | 4.4881 | 18.4916 | 4.1201 | 4.4881 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 0.89089 | 13 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 140.2011 | 5.0845 | 27.5744 | 140.2011 | 5.0845 | 27.5744 | 147.6922 | 5.3561 | 27.5744 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 0.88609 | 15 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 244.4546 | 5.8667 | 41.6683 | 244.4546 | 5.8667 | 41.6683 | 257.5161 | 6.1801 | 41.6683 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 0.88361 | 16 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 94.9689 | 6.2578 | 15.1761 | 94.9689 | 6.2578 | 15.1761 | 100.0432 | 6.5922 | 15.1761 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 0.8829 | 16 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 23.6499 | 6.2578 | 3.7793 | 23.6499 | 6.2578 | 3.7793 | 24.9135 | 6.5922 | 3.7793 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2026 | 591 | CB 591 | Tier-1 | Non-HFTD---1 | 4--4 | 0.87881 | 15 | 100% | 1060.5472 | 90.24% | 9.188% | 0.5739% | 47.3724 | 0 | 0 | 47.3724 | 0 | 45.1901 | 5.8667 | 7.7028 | 45.1901 | 5.8667 | 7.7028 | 47.6046 | 6.1801 | 7.7028 | 4.467% | 0.066615 | 0.063317 | 15920.6417 | 3763.87 | 1847.5145 | 10309.2572 | 16001.5783 | 0 | 0 | 16001.5783 | 0.001562%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 0.8568 | 7 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 96.5805 | 2.7378 | 35.2769 | 96.5805 | 2.7378 | 35.2769 | 101.7409 | 2.8841 | 35.2769 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 0.85023 | 11 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 304.239 | 4.3022 | 70.7165 | 304.239 | 4.3022 | 70.7165 | 320.4949 | 4.5321 | 70.7165 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2026 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 0.84757 | 14 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 32.1455 | 5.4756 | 5.8707 | 32.1455 | 5.4756 | 5.8707 | 33.8631 | 5.7681 | 5.8707 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 0.8394 | 13 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 21.4921 | 5.0845 | 4.227 | 21.4921 | 5.0845 | 4.227 | 22.6404 | 5.3561 | 4.227 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 0.83354 | 17 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 80.3262 | 6.6489 | 12.0811 | 80.3262 | 6.6489 | 12.0811 | 84.6182 | 7.0042 | 12.0811 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 0.83088 | 20 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 202.8579 | 7.8222 | 25.9335 | 202.8579 | 7.8222 | 25.9335 | 213.6968 | 8.2402 | 25.9335 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 0.822 | 14 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 114.0597 | 5.4756 | 20.8306 | 114.0597 | 5.4756 | 20.8306 | 120.154 | 5.7681 | 20.8306 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 0.81969 | 14 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 236.5455 | 5.4756 | 43.2002 | 236.5455 | 5.4756 | 43.2002 | 249.1845 | 5.7681 | 43.2002 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 0.81952 | 14 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 21.4215 | 5.4756 | 3.9122 | 21.4215 | 5.4756 | 3.9122 | 22.5661 | 5.7681 | 3.9122 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 0.81472 | 13 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 34.2346 | 5.0845 | 6.7332 | 34.2346 | 5.0845 | 6.7332 | 36.0638 | 5.3561 | 6.7332 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 0.8007 | 11 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 38.6279 | 4.3022 | 8.9786 | 38.6279 | 4.3022 | 8.9786 | 40.6918 | 4.5321 | 8.9786 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2026 | MV1 | CB MV1 | Tier-1 | Non-HFTD---4 | 3--4 | 0.78685 | 16 | 100% | 150.3384 | 97.79% | 0% | 2.21% | 7.2773 | 0 | 0 | 7.2773 | 0 | 6.942 | 6.2578 | 1.1093 | 6.942 | 6.2578 | 1.1093 | 7.3129 | 6.5922 | 1.1093 | 4.841% | 0.014765 | 0.014034 | 10182.3567 | 1618.5344 | 97.4794 | 8466.3429 | 10194.0779 | 0 | 0 | 10194.0779 | 0.00024%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 0.77975 | 14 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 190.7281 | 5.4756 | 34.8325 | 190.7281 | 5.4756 | 34.8325 | 200.9189 | 5.7681 | 34.8325 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 0.75773 | 9 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 9.4254 | 3.52 | 2.6777 | 9.4254 | 3.52 | 2.6777 | 9.929 | 3.7081 | 2.6777 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2026 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 0.74744 | 15 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.9791 | 5.8667 | 2.5533 | 14.9791 | 5.8667 | 2.5533 | 15.7795 | 6.1801 | 2.5533 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2026 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | 5--4 | 0.68938 | 10 | 100% | 1005.6854 | 94.09% | 5.81% | 0.1042% | 46.8371 | 0 | 0 | 46.8371 | 0 | 44.6794 | 3.9111 | 11.4237 | 44.6794 | 3.9111 | 11.4237 | 47.0667 | 4.1201 | 11.4237 | 4.657% | 0.097832 | 0.09299 | 10279.6968 | 1573.4563 | 574.8933 | 8131.3471 | 10311.3601 | 0 | 0 | 10311.3601 | 0.001545%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 0.68654 | 12 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 159.7982 | 4.6933 | 34.0478 | 159.7982 | 4.6933 | 34.0478 | 168.3364 | 4.9441 | 34.0478 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 0.68512 | 8 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.8455 | 3.1289 | 1.5486 | 4.8455 | 3.1289 | 1.5486 | 5.1044 | 3.2961 | 1.5486 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 0.65867 | 14 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 170.7918 | 5.4756 | 31.1916 | 170.7918 | 5.4756 | 31.1916 | 179.9174 | 5.7681 | 31.1916 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 0.63221 | 9 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 36.8826 | 3.52 | 10.478 | 36.8826 | 3.52 | 10.478 | 38.8532 | 3.7081 | 10.478 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 0.63062 | 7 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.981 | 2.7378 | 4.3762 | 11.981 | 2.7378 | 4.3762 | 12.6212 | 2.8841 | 4.3762 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 0.62174 | 9 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 10.0061 | 3.52 | 2.8426 | 10.0061 | 3.52 | 2.8426 | 10.5407 | 3.7081 | 2.8426 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 0.62121 | 10 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 30.0665 | 3.9111 | 7.6874 | 30.0665 | 3.9111 | 7.6874 | 31.673 | 4.1201 | 7.6874 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 0.61091 | 12 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 23.9277 | 4.6933 | 5.0982 | 23.9277 | 4.6933 | 5.0982 | 25.2062 | 4.9441 | 5.0982 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 0.61038 | 14 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 118.0741 | 5.4756 | 21.5638 | 118.0741 | 5.4756 | 21.5638 | 124.383 | 5.7681 | 21.5638 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2026 | 307 | CB 307 | Tier-1 | Non-HFTD---1 | 4--4 | 0.60043 | 8 | 100% | 601.8674 | 89.73% | 10.15% | 0.1197% | 26.7338 | 0 | 0 | 26.7338 | 0 | 25.5023 | 3.1289 | 8.1506 | 25.5023 | 3.1289 | 8.1506 | 26.8649 | 3.2961 | 8.1506 | 4.442% | 0.056404 | 0.053612 | 10670.688 | 1554.5631 | 980.4133 | 8135.7116 | 10727.7391 | 0 | 0 | 10727.7391 | 0.0008816%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 0.59919 | 7 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 182.2481 | 2.7378 | 66.5677 | 182.2481 | 2.7378 | 66.5677 | 191.9859 | 2.8841 | 66.5677 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 0.59493 | 8 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 199.4969 | 3.1289 | 63.7595 | 199.4969 | 3.1289 | 63.7595 | 210.1563 | 3.2961 | 63.7595 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.58517 | 6 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 101.0059 | 2.3467 | 43.0422 | 101.0059 | 2.3467 | 43.0422 | 106.4028 | 2.4721 | 43.0422 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 0.56439 | 8 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 11.4466 | 3.1289 | 3.6583 | 11.4466 | 3.1289 | 3.6583 | 12.0582 | 3.2961 | 3.6583 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.55871 | 8 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 83.4003 | 3.1289 | 26.6548 | 83.4003 | 3.1289 | 26.6548 | 87.8565 | 3.2961 | 26.6548 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.55854 | 7 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 169.657 | 2.7378 | 61.9687 | 169.657 | 2.7378 | 61.9687 | 178.722 | 2.8841 | 61.9687 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 0.55836 | 9 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 117.9754 | 3.52 | 33.5157 | 117.9754 | 3.52 | 33.5157 | 124.279 | 3.7081 | 33.5157 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 0.54487 | 11 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 103.5189 | 4.3022 | 24.0617 | 103.5189 | 4.3022 | 24.0617 | 109.0501 | 4.5321 | 24.0617 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 0.53847 | 11 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 20.4688 | 4.3022 | 4.7577 | 20.4688 | 4.3022 | 4.7577 | 21.5625 | 4.5321 | 4.7577 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 0.53244 | 7 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 28.5516 | 2.7378 | 10.4287 | 28.5516 | 2.7378 | 10.4287 | 30.0772 | 2.8841 | 10.4287 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 0.52285 | 10 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 19.3654 | 3.9111 | 4.9514 | 19.3654 | 3.9111 | 4.9514 | 20.4002 | 4.1201 | 4.9514 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 0.51593 | 8 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.5521 | 3.1289 | 2.4136 | 7.5521 | 3.1289 | 2.4136 | 7.9556 | 3.2961 | 2.4136 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2026 | 455 | CB 455 | Tier-1 | Non-HFTD---1 | 3--5 | 0.50847 | 9 | 100% | 628.6508 | 99.14% | 0% | 0.8628% | 30.8497 | 0 | 0 | 30.8497 | 0 | 29.4285 | 3.52 | 8.3604 | 29.4285 | 3.52 | 8.3604 | 31.001 | 3.7081 | 8.3604 | 4.907% | 0.025428 | 0.024169 | 24722.9716 | 4556.7235 | 179.5676 | 19986.6805 | 24734.0802 | 0 | 0 | 24734.0802 | 0.001017%
2026 | 171 | 171-704R | Tier-1 | Non-HFTD---6 | 4--2 | 0.50261 | 7 | 100% | 80.6143 | 61.35% | 34.31% | 4.34% | 2.4483 | 0 | 0 | 2.4483 | 0 | 2.3355 | 2.7378 | 0.85307 | 2.3355 | 2.7378 | 0.85307 | 2.4603 | 2.8841 | 0.85307 | 3.037% | 0.048088 | 0.045707 | 1676.4044 | 165.028 | 536.4334 | 974.9431 | 1710.1431 | 0 | 0 | 1710.1431 | 8.074e-05%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 0.47847 | 7 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 26.8592 | 2.7378 | 9.8106 | 26.8592 | 2.7378 | 9.8106 | 28.2944 | 2.8841 | 9.8106 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 0.46977 | 8 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 129.2749 | 3.1289 | 41.3164 | 129.2749 | 3.1289 | 41.3164 | 136.1822 | 3.2961 | 41.3164 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2026 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 0.46444 | 7 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.5364 | 2.7378 | 1.6569 | 4.5364 | 2.7378 | 1.6569 | 4.7787 | 2.8841 | 1.6569 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 0.45645 | 4 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 184.1331 | 1.5644 | 117.6984 | 184.1331 | 1.5644 | 117.6984 | 193.9716 | 1.648 | 117.6984 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 0.43976 | 6 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 28.5249 | 2.3467 | 12.1555 | 28.5249 | 2.3467 | 12.1555 | 30.0491 | 2.4721 | 12.1555 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 0.4387 | 7 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 34.4739 | 2.7378 | 12.5919 | 34.4739 | 2.7378 | 12.5919 | 36.3159 | 2.8841 | 12.5919 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.43106 | 10 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 5.0165 | 3.9111 | 1.2826 | 5.0165 | 3.9111 | 1.2826 | 5.2845 | 4.1201 | 1.2826 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.42006 | 4 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.1512 | 1.5644 | 2.0143 | 3.1512 | 1.5644 | 2.0143 | 3.3196 | 1.648 | 2.0143 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.4197 | 2 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 61.292 | 0.78222 | 78.3561 | 61.292 | 0.78222 | 78.3561 | 64.5669 | 0.82402 | 78.3561 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 0.41562 | 7 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 68.9354 | 2.7378 | 25.1793 | 68.9354 | 2.7378 | 25.1793 | 72.6187 | 2.8841 | 25.1793 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 0.41526 | 4 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 120.3488 | 1.5644 | 76.9273 | 120.3488 | 1.5644 | 76.9273 | 126.7793 | 1.648 | 76.9273 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2026 | 412 | CB 412 | Tier-1 | Non-HFTD---1 | 4--5 | 0.41437 | 7 | 100% | 1311.9921 | 88.37% | 10.81% | 0.8215% | 57.392 | 0 | 0 | 57.392 | 0 | 54.7481 | 2.7378 | 19.9972 | 54.7481 | 2.7378 | 19.9972 | 57.6734 | 2.8841 | 19.9972 | 4.374% | 0.071433 | 0.067897 | 18366.6483 | 2615.4927 | 2100.6109 | 13650.5447 | 18477.8687 | 0 | 0 | 18477.8687 | 0.001893%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 0.41331 | 7 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 28.7981 | 2.7378 | 10.5187 | 28.7981 | 2.7378 | 10.5187 | 30.3368 | 2.8841 | 10.5187 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 0.40443 | 7 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 95.5517 | 2.7378 | 34.9011 | 95.5517 | 2.7378 | 34.9011 | 100.6572 | 2.8841 | 34.9011 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 0.39893 | 8 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 19.4973 | 3.1289 | 6.2314 | 19.4973 | 3.1289 | 6.2314 | 20.539 | 3.2961 | 6.2314 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 0.39698 | 6 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 62.0703 | 2.3467 | 26.4503 | 62.0703 | 2.3467 | 26.4503 | 65.3868 | 2.4721 | 26.4503 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 0.38686 | 7 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 60.2656 | 2.7378 | 22.0126 | 60.2656 | 2.7378 | 22.0126 | 63.4857 | 2.8841 | 22.0126 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 0.38437 | 5 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 100.9567 | 1.9556 | 51.6255 | 100.9567 | 1.9556 | 51.6255 | 106.351 | 2.06 | 51.6255 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 0.3826 | 8 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 146.4383 | 3.1289 | 46.8019 | 146.4383 | 3.1289 | 46.8019 | 154.2627 | 3.2961 | 46.8019 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 0.37585 | 7 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 91.3318 | 2.7378 | 33.3597 | 91.3318 | 2.7378 | 33.3597 | 96.2118 | 2.8841 | 33.3597 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 0.35756 | 6 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 25.1077 | 2.3467 | 10.6993 | 25.1077 | 2.3467 | 10.6993 | 26.4492 | 2.4721 | 10.6993 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 0.35561 | 10 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.4049 | 3.9111 | 0.87057 | 3.4049 | 3.9111 | 0.87057 | 3.5868 | 4.1201 | 0.87057 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 0.35525 | 2 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 243.3088 | 0.78222 | 311.0474 | 243.3088 | 0.78222 | 311.0474 | 256.3092 | 0.82402 | 311.0474 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2026 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 0.34957 | 9 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 93.8928 | 3.52 | 26.674 | 93.8928 | 3.52 | 26.674 | 98.9097 | 3.7081 | 26.674 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2026 | 206 | 206-963F | Tier-1 | Non-HFTD---1 | 3--5 | 0.34283 | 6 | 100% | 308.0085 | 98.9% | 0% | 1.099% | 15.0788 | 0 | 0 | 15.0788 | 0 | 14.3842 | 2.3467 | 6.1296 | 14.3842 | 2.3467 | 6.1296 | 15.1527 | 2.4721 | 6.1296 | 4.896% | 0.014856 | 0.014121 | 20732.6556 | 3229.8813 | 785.6991 | 16717.0751 | 20744.5251 | 0 | 0 | 20744.5251 | 0.0004972%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 0.33945 | 7 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.6148 | 2.7378 | 3.8771 | 10.6148 | 2.7378 | 3.8771 | 11.1819 | 2.8841 | 3.8771 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2026 | 553 | 553-27R | Tier-1 | Non-HFTD---1 | 4--4 | 0.33928 | 7 | 100% | 504.2652 | 97.83% | 0% | 2.166% | 24.4204 | 0 | 0 | 24.4204 | 0 | 23.2954 | 2.7378 | 8.5089 | 23.2954 | 2.7378 | 8.5089 | 24.5401 | 2.8841 | 8.5089 | 4.843% | 0.054721 | 0.052013 | 9215.1363 | 1913.347 | 158.4888 | 7143.3005 | 9225.5318 | 0 | 0 | 9225.5318 | 0.0008053%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.33644 | 5 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 65.2006 | 1.9556 | 33.3411 | 65.2006 | 1.9556 | 33.3411 | 68.6844 | 2.06 | 33.3411 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2026 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | 3--5 | 0.33608 | 7 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 13.1668 | 0 | 0 | 13.1668 | 0 | 12.5602 | 2.7378 | 4.5877 | 12.5602 | 2.7378 | 4.5877 | 13.2313 | 2.8841 | 4.5877 | 4.021% | 0.015736 | 0.014957 | 20808.6476 | 4091.2697 | 3467.4094 | 13249.9684 | 21012.0249 | 0 | 0 | 21012.0249 | 0.0004342%
2026 | 471 | CB 471 | Tier-1 | Non-HFTD---1 | 4--5 | 0.33537 | 7 | 100% | 3808.7328 | 99.83% | 0% | 0.1692% | 188.2133 | 0 | 0 | 188.2133 | 0 | 179.5427 | 2.7378 | 65.5795 | 179.5427 | 2.7378 | 65.5795 | 189.1359 | 2.8841 | 65.5795 | 4.942% | 0.030567 | 0.029054 | 124601.1385 | 20145.8945 | 297.3105 | 104157.9336 | 124612.117 | 0 | 0 | 124612.117 | 0.006207%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.33288 | 7 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 58.5262 | 2.7378 | 21.3772 | 58.5262 | 2.7378 | 21.3772 | 61.6533 | 2.8841 | 21.3772 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2026 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.32987 | 5 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 99.2512 | 1.9556 | 50.7533 | 99.2512 | 1.9556 | 50.7533 | 104.5543 | 2.06 | 50.7533 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 0.32365 | 5 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.9468 | 1.9556 | 0.9955 | 1.9468 | 1.9556 | 0.9955 | 2.0508 | 2.06 | 0.9955 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2026 | 170 | 170-3R | Tier-1 | Non-HFTD---3 | 4--3 | 0.32312 | 5 | 100% | 134.6076 | 71.34% | 24.69% | 3.975% | 4.7533 | 0 | 0 | 4.7533 | 0 | 4.5343 | 1.9556 | 2.3187 | 4.5343 | 1.9556 | 2.3187 | 4.7766 | 2.06 | 2.3187 | 3.531% | 0.059016 | 0.056095 | 2280.8503 | 250.0057 | 616.1021 | 1414.7425 | 2314.8955 | 0 | 0 | 2314.8955 | 0.0001567%
2026 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 0.32063 | 5 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 32.5317 | 1.9556 | 16.6355 | 32.5317 | 1.9556 | 16.6355 | 34.2699 | 2.06 | 16.6355 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 0.3114 | 8 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 91.3622 | 3.1289 | 29.1995 | 91.3622 | 3.1289 | 29.1995 | 96.2438 | 3.2961 | 29.1995 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 0.30767 | 4 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 229.1341 | 1.5644 | 146.4632 | 229.1341 | 1.5644 | 146.4632 | 241.3771 | 1.648 | 146.4632 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 0.3027 | 4 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.8993 | 1.5644 | 9.5237 | 14.8993 | 1.5644 | 9.5237 | 15.6954 | 1.648 | 9.5237 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 0.30253 | 4 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 281.9725 | 1.5644 | 180.2376 | 281.9725 | 1.5644 | 180.2376 | 297.0387 | 1.648 | 180.2376 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 0.30111 | 4 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 55.2642 | 1.5644 | 35.325 | 55.2642 | 1.5644 | 35.325 | 58.217 | 1.648 | 35.325 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2026 | 387 | CB 387 | Tier-1 | Non-HFTD---2 | 4--4 | 0.30022 | 6 | 100% | 522.65 | 70.14% | 28.94% | 0.9137% | 18.1467 | 0 | 0 | 18.1467 | 0 | 17.3107 | 2.3467 | 7.3767 | 17.3107 | 2.3467 | 7.3767 | 18.2357 | 2.4721 | 7.3767 | 3.472% | 0.067633 | 0.064286 | 7727.6908 | 947.907 | 2193.816 | 4585.9679 | 7847.8494 | 0 | 0 | 7847.8494 | 0.0005984%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 0.29276 | 6 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 34.7023 | 2.3467 | 14.7879 | 34.7023 | 2.3467 | 14.7879 | 36.5565 | 2.4721 | 14.7879 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 0.29081 | 5 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.4319 | 1.9556 | 1.7549 | 3.4319 | 1.9556 | 1.7549 | 3.6153 | 2.06 | 1.7549 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2026 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 0.283 | 6 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.602 | 2.3467 | 5.3702 | 12.602 | 2.3467 | 5.3702 | 13.2754 | 2.4721 | 5.3702 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 0.26649 | 3 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 27.3279 | 1.1733 | 23.2908 | 27.3279 | 1.1733 | 23.2908 | 28.7881 | 1.236 | 23.2908 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 0.26151 | 5 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 5.2339 | 1.9556 | 2.6764 | 5.2339 | 1.9556 | 2.6764 | 5.5136 | 2.06 | 2.6764 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2026 | 172 | 172-615R | Tier-1 | Non-HFTD---6 | 4--2 | 0.25938 | 5 | 100% | 65.0211 | 31.38% | 63.15% | 5.469% | 1.0101 | 0 | 0 | 1.0101 | 0 | 0.96353 | 1.9556 | 0.49271 | 0.96353 | 1.9556 | 0.49271 | 1.015 | 2.06 | 0.49271 | 1.553% | 0.053579 | 0.050927 | 1213.547 | 17.4537 | 970.9978 | 225.0954 | 1256.9124 | 0 | 0 | 1256.9124 | 3.331e-05%
2026 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.25477 | 2 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 8.0511 | 0.78222 | 10.2925 | 8.0511 | 0.78222 | 10.2925 | 8.4812 | 0.82402 | 10.2925 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.2521 | 4 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.8774 | 1.5644 | 3.1176 | 4.8774 | 1.5644 | 3.1176 | 5.138 | 1.648 | 3.1176 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2026 | 410 | 410-50R | Tier-1 | Non-HFTD---1 | 4--5 | 0.24749 | 4 | 100% | 1314.3326 | 99.38% | 0% | 0.6151% | 64.6593 | 0 | 0 | 64.6593 | 0 | 61.6806 | 1.5644 | 39.4264 | 61.6806 | 1.5644 | 39.4264 | 64.9763 | 1.648 | 39.4264 | 4.92% | 0.044038 | 0.041858 | 29845.69 | 7721.7282 | 133.8501 | 21990.1116 | 29855.2499 | 0 | 0 | 29855.2499 | 0.002132%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.24252 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 5.4171 | 1.9556 | 2.7701 | 5.4171 | 1.9556 | 2.7701 | 5.7065 | 2.06 | 2.7701 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.2379 | 4 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 33.3597 | 1.5644 | 21.3236 | 33.3597 | 1.5644 | 21.3236 | 35.1422 | 1.648 | 21.3236 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2026 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | 4--5 | 0.23648 | 3 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 37.535 | 0 | 0 | 37.535 | 0 | 35.8058 | 1.1733 | 30.5162 | 35.8058 | 1.1733 | 30.5162 | 37.719 | 1.236 | 30.5162 | 3.124% | 0.042337 | 0.040241 | 28377.3086 | 3599.9822 | 10019.8495 | 14757.4769 | 28922.3867 | 0 | 0 | 28922.3867 | 0.001238%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.23417 | 5 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 18.259 | 1.9556 | 9.3369 | 18.259 | 1.9556 | 9.3369 | 19.2346 | 2.06 | 9.3369 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2026 | 306 | CB 306 | Tier-1 | Non-HFTD---1 | 4--4 | 0.234 | 6 | 100% | 737.4997 | 97.09% | 2.802% | 0.1119% | 35.4424 | 0 | 0 | 35.4424 | 0 | 33.8097 | 2.3467 | 14.4075 | 33.8097 | 2.3467 | 14.4075 | 35.6162 | 2.4721 | 14.4075 | 4.806% | 0.057753 | 0.054894 | 12769.9388 | 2020.535 | 320.1958 | 10429.208 | 12789.3181 | 0 | 0 | 12789.3181 | 0.001169%
2026 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 0.23062 | 5 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 23.0859 | 1.9556 | 11.8053 | 23.0859 | 1.9556 | 11.8053 | 24.3194 | 2.06 | 11.8053 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2026 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 0.22654 | 4 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 18.1434 | 1.5644 | 11.5973 | 18.1434 | 1.5644 | 11.5973 | 19.1128 | 1.648 | 11.5973 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2026 | 1007 | CB 1007 | Tier-1 | Non-HFTD---4 | 1--5 | 0.22459 | 1 | 100% | 183.252 | 99.8% | 0% | 0.2013% | 9.0527 | 0 | 0 | 9.0527 | 0 | 8.6357 | 0.39111 | 22.0798 | 8.6357 | 0.39111 | 22.0798 | 9.0971 | 0.41201 | 22.0798 | 4.94% | 0.0023706 | 0.0022533 | 77301.9362 | 12237.1432 | 2369.9057 | 62694.8873 | 77310.0415 | 0 | 0 | 77310.0415 | 0.0002985%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.22086 | 3 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 14.1762 | 1.1733 | 12.082 | 14.1762 | 1.1733 | 12.082 | 14.9337 | 1.236 | 12.082 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.21127 | 4 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.8535 | 1.5644 | 3.7416 | 5.8535 | 1.5644 | 3.7416 | 6.1663 | 1.648 | 3.7416 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.20097 | 3 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 27.5211 | 1.1733 | 23.4554 | 27.5211 | 1.1733 | 23.4554 | 28.9916 | 1.236 | 23.4554 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2026 | HW1 | CB HW1 | Tier-1 | Non-HFTD---4 | 1--5 | 0.2008 | 5 | 100% | 122.4382 | 99.35% | 0% | 0.6452% | 6.0216 | 0 | 0 | 6.0216 | 0 | 5.7442 | 1.9556 | 2.9374 | 5.7442 | 1.9556 | 2.9374 | 6.0511 | 2.06 | 2.9374 | 4.918% | 0.0031138 | 0.0029597 | 39321.1613 | 6393.1555 | 36.0556 | 32891.9501 | 39334.373 | 0 | 0 | 39334.373 | 0.0001986%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 0.19973 | 5 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 50.9272 | 1.9556 | 26.0422 | 50.9272 | 1.9556 | 26.0422 | 53.6483 | 2.06 | 26.0422 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2026 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.19192 | 2 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 5.3951 | 0.78222 | 6.8971 | 5.3951 | 0.78222 | 6.8971 | 5.6834 | 0.82402 | 6.8971 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2026 | 172 | 172-569R | Tier-1 | Non-HFTD---3 | 5--2 | 0.19139 | 2 | 100% | 174.5806 | 70.22% | 23.82% | 5.957% | 6.0684 | 0 | 0 | 6.0684 | 0 | 5.7888 | 0.78222 | 7.4005 | 5.7888 | 0.78222 | 7.4005 | 6.0981 | 0.82402 | 7.4005 | 3.476% | 0.12865 | 0.12229 | 1356.9713 | 139.4703 | 376.51 | 840.9911 | 1378.015 | 0 | 0 | 1378.015 | 0.0002001%
2026 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.18961 | 1 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 10.0309 | 0.39111 | 25.6471 | 10.0309 | 0.39111 | 25.6471 | 10.5669 | 0.41201 | 25.6471 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.18908 | 4 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 39.6291 | 1.5644 | 25.331 | 39.6291 | 1.5644 | 25.331 | 41.7465 | 1.648 | 25.331 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.18748 | 3 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 5.0917 | 1.1733 | 4.3395 | 5.0917 | 1.1733 | 4.3395 | 5.3637 | 1.236 | 4.3395 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 0.17772 | 3 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 188.5406 | 1.1733 | 160.6876 | 188.5406 | 1.1733 | 160.6876 | 198.6146 | 1.236 | 160.6876 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2026 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.17736 | 2 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 1.0753 | 0.78222 | 1.3747 | 1.0753 | 0.78222 | 1.3747 | 1.1328 | 0.82402 | 1.3747 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 0.17683 | 2 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 299.7005 | 0.78222 | 383.1388 | 299.7005 | 0.78222 | 383.1388 | 315.7139 | 0.82402 | 383.1388 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 0.16671 | 2 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 74.8329 | 0.78222 | 95.6669 | 74.8329 | 0.78222 | 95.6669 | 78.8314 | 0.82402 | 95.6669 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.16405 | 2 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.3203 | 0.78222 | 2.9662 | 2.3203 | 0.78222 | 2.9662 | 2.4442 | 0.82402 | 2.9662 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 0.16103 | 3 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 133.2483 | 1.1733 | 113.5636 | 133.2483 | 1.1733 | 113.5636 | 140.368 | 1.236 | 113.5636 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2026 | 1039 | CB 1039 | Tier-1 | Non-HFTD---6 | 4--3 | 0.15694 | 3 | 100% | 89.254 | 66.42% | 32.73% | 0.8498% | 2.9347 | 0 | 0 | 2.9347 | 0 | 2.7995 | 1.1733 | 2.3859 | 2.7995 | 1.1733 | 2.3859 | 2.9491 | 1.236 | 2.3859 | 3.288% | 0.047241 | 0.044903 | 1889.3167 | 183.5723 | 702.9111 | 1002.8332 | 1922.3524 | 0 | 0 | 1922.3524 | 9.677e-05%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.15446 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.8025 | 0.78222 | 15.0884 | 11.8025 | 0.78222 | 15.0884 | 12.4331 | 0.82402 | 15.0884 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2026 | 856 | 856-1141R | Tier-1 | Non-HFTD---7 | 2--3 | 0.15197 | 3 | 100% | 34.972 | 93.55% | 0% | 6.449% | 1.6195 | 0 | 0 | 1.6195 | 0 | 1.5449 | 1.1733 | 1.3166 | 1.5449 | 1.1733 | 1.3166 | 1.6274 | 1.236 | 1.3166 | 4.631% | 0.0095222 | 0.0090509 | 3672.677 | 493.2945 | 440.7828 | 2738.5997 | 3685.0115 | 0 | 0 | 3685.0115 | 5.34e-05%
2026 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.14789 | 1 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 6.2466 | 0.39111 | 15.9713 | 6.2466 | 0.39111 | 15.9713 | 6.5803 | 0.41201 | 15.9713 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 0.14629 | 3 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 192.305 | 1.1733 | 163.8959 | 192.305 | 1.1733 | 163.8959 | 202.5801 | 1.236 | 163.8959 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2026 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 0.14008 | 3 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 33.9169 | 1.1733 | 28.9063 | 33.9169 | 1.1733 | 28.9063 | 35.7291 | 1.236 | 28.9063 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.14008 | 3 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 63.2779 | 1.1733 | 53.9299 | 63.2779 | 1.1733 | 53.9299 | 66.6589 | 1.236 | 53.9299 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.11345 | 2 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 32.5478 | 0.78222 | 41.6093 | 32.5478 | 0.78222 | 41.6093 | 34.2868 | 0.82402 | 41.6093 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.11025 | 1 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.8008 | 0.39111 | 35.286 | 13.8008 | 0.39111 | 35.286 | 14.5382 | 0.41201 | 35.286 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2026 | 1221 | 1221-2095F | Tier-1 | Non-HFTD---9 | 1--4 | 0.10883 | 2 | 100% | 19.6421 | 98.74% | 0% | 1.261% | 0.96002 | 0 | 0 | 0.96002 | 0 | 0.91579 | 0.78222 | 1.1708 | 0.91579 | 0.78222 | 1.1708 | 0.96473 | 0.82402 | 1.1708 | 4.888% | 0.0016714 | 0.0015887 | 11751.8616 | 4301.6259 | 14.6524 | 7435.5833 | 11759.5801 | 0 | 0 | 11759.5801 | 3.166e-05%
2026 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.10848 | 1 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 15.2415 | 0.39111 | 38.9695 | 15.2415 | 0.39111 | 38.9695 | 16.0558 | 0.41201 | 38.9695 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2026 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.10741 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 6.3024 | 0.39111 | 16.114 | 6.3024 | 0.39111 | 16.114 | 6.6391 | 0.41201 | 16.114 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2026 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.1067 | 2 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.8521 | 0.78222 | 7.4813 | 5.8521 | 0.78222 | 7.4813 | 6.1647 | 0.82402 | 7.4813 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.1035 | 2 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 18.6068 | 0.78222 | 23.7871 | 18.6068 | 0.78222 | 23.7871 | 19.601 | 0.82402 | 23.7871 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.097469 | 2 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.9848 | 0.78222 | 15.3214 | 11.9848 | 0.78222 | 15.3214 | 12.6251 | 0.82402 | 15.3214 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2026 | 93 | 93-10R | Tier-1 | Non-HFTD---2 | 4--4 | 0.095516 | 3 | 100% | 302.3321 | 90.71% | 7.303% | 1.988% | 13.575 | 0 | 0 | 13.575 | 0 | 12.9496 | 1.1733 | 11.0365 | 12.9496 | 1.1733 | 11.0365 | 13.6415 | 1.236 | 11.0365 | 4.49% | 0.035815 | 0.034042 | 8441.494 | 1852.3748 | 638.1878 | 5950.9314 | 8482.34 | 0 | 0 | 8482.34 | 0.0004477%
2026 | 901 | 901-1124 | Tier-1 | Non-HFTD---1 | 2--5 | 0.094983 | 1 | 100% | 225.4814 | 99.29% | 0% | 0.709% | 11.0822 | 0 | 0 | 11.0822 | 0 | 10.5717 | 0.39111 | 27.0297 | 10.5717 | 0.39111 | 27.0297 | 11.1365 | 0.41201 | 27.0297 | 4.915% | 0.0087544 | 0.0083211 | 25756.3496 | 4178.6743 | 36.5656 | 21541.1098 | 25765.8596 | 0 | 0 | 25765.8596 | 0.0003654%
2026 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.09161 | 2 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 4.1171 | 0.78222 | 5.2633 | 4.1171 | 0.78222 | 5.2633 | 4.3371 | 0.82402 | 5.2633 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2026 | 299 | 299-1153F | Tier-1 | Non-HFTD---11 | 1--4 | 0.090722 | 2 | 100% | 12.6944 | 96.89% | 0% | 3.107% | 0.60885 | 0 | 0 | 0.60885 | 0 | 0.5808 | 0.78222 | 0.7425 | 0.5808 | 0.78222 | 0.7425 | 0.61183 | 0.82402 | 0.7425 | 4.796% | 0.0013374 | 0.0012712 | 9491.8205 | 1360.071 | 891.9808 | 7239.7687 | 9507.1772 | 0 | 0 | 9507.1772 | 2.008e-05%
2026 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 0.089302 | 2 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 268.9313 | 0.78222 | 343.8033 | 268.9313 | 0.78222 | 343.8033 | 283.3006 | 0.82402 | 343.8033 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2026 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.088947 | 1 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 6.3167 | 0.39111 | 16.1505 | 6.3167 | 0.39111 | 16.1505 | 6.6542 | 0.41201 | 16.1505 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 0.080425 | 1 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 15.5039 | 0.39111 | 39.6404 | 15.5039 | 0.39111 | 39.6404 | 16.3322 | 0.41201 | 39.6404 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 0.08007 | 2 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 18.2584 | 0.78222 | 23.3417 | 18.2584 | 0.78222 | 23.3417 | 19.234 | 0.82402 | 23.3417 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 0.079715 | 1 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 104.5514 | 0.39111 | 267.3183 | 104.5514 | 0.39111 | 267.3183 | 110.1378 | 0.41201 | 267.3183 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2026 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.077762 | 2 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.6814 | 0.78222 | 4.7063 | 3.6814 | 0.78222 | 4.7063 | 3.8781 | 0.82402 | 4.7063 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2026 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.071015 | 2 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 4.0459 | 0.78222 | 5.1724 | 4.0459 | 0.78222 | 5.1724 | 4.2621 | 0.82402 | 5.1724 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2026 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.069773 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.5515 | 0.39111 | 6.5237 | 2.5515 | 0.39111 | 6.5237 | 2.6878 | 0.41201 | 6.5237 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 0.068352 | 2 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 25.691 | 0.78222 | 32.8435 | 25.691 | 0.78222 | 32.8435 | 27.0637 | 0.82402 | 32.8435 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.068175 | 1 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 7.1363 | 0.39111 | 18.2461 | 7.1363 | 0.39111 | 18.2461 | 7.5176 | 0.41201 | 18.2461 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.061606 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 68.6427 | 0.39111 | 175.5064 | 68.6427 | 0.39111 | 175.5064 | 72.3104 | 0.41201 | 175.5064 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2026 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.060718 | 1 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 15.7754 | 0.39111 | 40.3348 | 15.7754 | 0.39111 | 40.3348 | 16.6183 | 0.41201 | 40.3348 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2026 | 474 | 474-29 | Tier-1 | Non-HFTD---1 | 2--5 | 0.059298 | 2 | 100% | 1510.7302 | 99.89% | 0% | 0.1058% | 74.702 | 0 | 0 | 74.702 | 0 | 71.2607 | 0.78222 | 91.1001 | 71.2607 | 0.78222 | 91.1001 | 75.0682 | 0.82402 | 91.1001 | 4.945% | 0.010755 | 0.010222 | 140472.931 | 24566.9965 | 189.9323 | 115716.0023 | 140480.6687 | 0 | 0 | 140480.6687 | 0.002463%
2026 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.057878 | 1 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.8484 | 0.39111 | 30.2942 | 11.8484 | 0.39111 | 30.2942 | 12.4815 | 0.41201 | 30.2942 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2026 | 171 | 171-34 | Tier-1 | Non-HFTD---6 | 4--3 | 0.056812 | 1 | 100% | 81.2035 | 44.67% | 51.64% | 3.687% | 1.7955 | 0 | 0 | 1.7955 | 0 | 1.7128 | 0.39111 | 4.3793 | 1.7128 | 0.39111 | 4.3793 | 1.8043 | 0.41201 | 4.3793 | 2.211% | 0.043687 | 0.041525 | 1858.7395 | 129.5883 | 851.5868 | 877.5644 | 1912.2988 | 0 | 0 | 1912.2988 | 5.921e-05%
2026 | 1001 | 1001-1232F | Tier-1 | Non-HFTD---15 | 1--4 | 0.056812 | 1 | 100% | 3.7082 | 98.25% | 0% | 1.746% | 0.18035 | 0 | 0 | 0.18035 | 0 | 0.17204 | 0.39111 | 0.43988 | 0.17204 | 0.39111 | 0.43988 | 0.18123 | 0.41201 | 0.43988 | 4.864% | 0.0002536 | 0.00024105 | 14622.1214 | 2186.2186 | 960.6365 | 11475.2662 | 14635.4188 | 0 | 0 | 14635.4188 | 5.947e-06%
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.056635 | 1 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.4787 | 0.39111 | 14.008 | 5.4787 | 0.39111 | 14.008 | 5.7714 | 0.41201 | 14.008 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.053439 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.8232 | 0.39111 | 9.7751 | 3.8232 | 0.39111 | 9.7751 | 4.0275 | 0.41201 | 9.7751 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2026 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.052906 | 1 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.3373 | 0.39111 | 8.5328 | 3.3373 | 0.39111 | 8.5328 | 3.5156 | 0.41201 | 8.5328 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.052551 | 1 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.6787 | 0.39111 | 19.6331 | 7.6787 | 0.39111 | 19.6331 | 8.089 | 0.41201 | 19.6331 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.052196 | 1 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.072621 | 0.39111 | 0.18568 | 0.072621 | 0.39111 | 0.18568 | 0.076501 | 0.41201 | 0.18568 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2026 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.051664 | 1 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.67947 | 0.39111 | 1.7373 | 0.67947 | 0.39111 | 1.7373 | 0.71577 | 0.41201 | 1.7373 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2026 | 591 | 591-39AE | Tier-1 | Non-HFTD---1 | 4--4 | 0.051309 | 2 | 100% | 863.6817 | 30.54% | 68.77% | 0.684% | 13.0582 | 0 | 0 | 13.0582 | 0 | 12.4567 | 0.78222 | 15.9247 | 12.4567 | 0.78222 | 15.9247 | 13.1223 | 0.82402 | 15.9247 | 1.512% | 0.061092 | 0.058068 | 14137.3023 | 873.1637 | 8965.9062 | 4298.2324 | 14648.6655 | 0 | 0 | 14648.6655 | 0.0004306%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.050598 | 1 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 30.6993 | 0.39111 | 78.4924 | 30.6993 | 0.39111 | 78.4924 | 32.3396 | 0.41201 | 78.4924 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2026 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.050421 | 1 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.088733 | 0.39111 | 0.22687 | 0.088733 | 0.39111 | 0.22687 | 0.093474 | 0.41201 | 0.22687 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2026 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.049711 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 1.0269 | 0.39111 | 2.6256 | 1.0269 | 0.39111 | 2.6256 | 1.0818 | 0.41201 | 2.6256 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2026 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.049001 | 1 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.11451 | 0.39111 | 0.29277 | 0.11451 | 0.39111 | 0.29277 | 0.12063 | 0.41201 | 0.29277 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2026 | 472 | CB 472 | Tier-1 | Non-HFTD---6 | 3--3 | 0.04687 | 1 | 100% | 66.0921 | 92.91% | 0% | 7.09% | 3.0396 | 0 | 0 | 3.0396 | 0 | 2.8996 | 0.39111 | 7.4137 | 2.8996 | 0.39111 | 7.4137 | 3.0545 | 0.41201 | 7.4137 | 4.599% | 0.020578 | 0.019559 | 3211.8146 | 441.0584 | 309.4932 | 2461.263 | 3223.674 | 0 | 0 | 3223.674 | 0.0001002%
2026 | 859 | 859-1064 | Tier-1 | Non-HFTD---7 | 2--3 | 0.045272 | 2 | 100% | 40.2522 | 93.55% | 0% | 6.452% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.7781 | 0.78222 | 2.2731 | 1.7781 | 0.78222 | 2.2731 | 1.8731 | 0.82402 | 2.2731 | 4.631% | 0.011569 | 0.010996 | 3479.3123 | 521.49 | 92.9503 | 2864.872 | 3491.0022 | 0 | 0 | 3491.0022 | 6.147e-05%
2026 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.042964 | 1 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 14.647 | 0.39111 | 37.4496 | 14.647 | 0.39111 | 37.4496 | 15.4296 | 0.41201 | 37.4496 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.041366 | 1 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.4335 | 0.39111 | 19.006 | 7.4335 | 0.39111 | 19.006 | 7.8307 | 0.41201 | 19.006 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.040479 | 1 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 37.005 | 0.39111 | 94.6147 | 37.005 | 0.39111 | 94.6147 | 38.9822 | 0.41201 | 94.6147 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.038881 | 1 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 9.0555 | 0.39111 | 23.1533 | 9.0555 | 0.39111 | 23.1533 | 9.5394 | 0.41201 | 23.1533 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 0.038703 | 1 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 26.6692 | 0.39111 | 68.1881 | 26.6692 | 0.39111 | 68.1881 | 28.0941 | 0.41201 | 68.1881 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2026 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.037283 | 1 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.56685 | 0.39111 | 1.4493 | 0.56685 | 0.39111 | 1.4493 | 0.59714 | 0.41201 | 1.4493 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2026 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.036218 | 1 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.78372 | 0.39111 | 2.0038 | 0.78372 | 0.39111 | 2.0038 | 0.8256 | 0.41201 | 2.0038 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2026 | 245 | CB 245 | Tier-1 | Non-HFTD---2 | 4--4 | 0.03462 | 1 | 100% | 248.3247 | 30.26% | 68.14% | 1.595% | 3.7197 | 0 | 0 | 3.7197 | 0 | 3.5483 | 0.39111 | 9.0723 | 3.5483 | 0.39111 | 9.0723 | 3.7379 | 0.41201 | 9.0723 | 1.498% | 0.044637 | 0.042428 | 5563.1534 | 331.3651 | 3704.159 | 1527.6293 | 5765.2004 | 0 | 0 | 5765.2004 | 0.0001227%
2026 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | 2--4 | 0.034265 | 1 | 100% | 92.0555 | 97.82% | 0% | 2.183% | 4.4573 | 0 | 0 | 4.4573 | 0 | 4.2519 | 0.39111 | 10.8714 | 4.2519 | 0.39111 | 10.8714 | 4.4791 | 0.41201 | 10.8714 | 4.842% | 0.0089936 | 0.0085484 | 10235.6661 | 2125.5614 | 107.0953 | 8003.0094 | 10247.3023 | 0 | 0 | 10247.3023 | 0.000147%
2026 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.032134 | 1 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.1865 | 0.39111 | 3.0337 | 1.1865 | 0.39111 | 3.0337 | 1.2499 | 0.41201 | 3.0337 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.032134 | 1 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.7481 | 0.39111 | 7.0263 | 2.7481 | 0.39111 | 7.0263 | 2.8949 | 0.41201 | 7.0263 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2026 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.032134 | 1 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.73012 | 0.39111 | 1.8668 | 0.73012 | 0.39111 | 1.8668 | 0.76913 | 0.41201 | 1.8668 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.031957 | 1 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.3389 | 0.39111 | 13.6506 | 5.3389 | 0.39111 | 13.6506 | 5.6242 | 0.41201 | 13.6506 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2026 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.031424 | 1 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.5386 | 0.39111 | 1.3771 | 0.5386 | 0.39111 | 1.3771 | 0.56738 | 0.41201 | 1.3771 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2026 | 96 | 96-1041F | Tier-1 | Non-HFTD---13 | 2--2 | 0.031424 | 1 | 100% | 5.6175 | 97.14% | 1.791% | 1.068% | 0.27012 | 0 | 0 | 0.27012 | 0 | 0.25767 | 0.39111 | 0.65882 | 0.25767 | 0.39111 | 0.65882 | 0.27144 | 0.41201 | 0.65882 | 4.808% | 0.005633 | 0.0053542 | 997.2446 | 127.463 | 205.2994 | 664.4822 | 998.7294 | 0 | 0 | 998.7294 | 8.907e-06%
2026 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.031247 | 1 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.8387 | 0.39111 | 2.1444 | 0.8387 | 0.39111 | 2.1444 | 0.88351 | 0.41201 | 2.1444 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2026 | 205 | 205-369R | Tier-1 | Non-HFTD---2 | 4--4 | 0.030537 | 1 | 100% | 370.1825 | 97.17% | 0% | 2.827% | 17.8061 | 0 | 0 | 17.8061 | 0 | 16.9858 | 0.39111 | 43.4295 | 16.9858 | 0.39111 | 43.4295 | 17.8934 | 0.41201 | 43.4295 | 4.81% | 0.046634 | 0.044326 | 7938.0395 | 1227.249 | 240.0519 | 6470.7387 | 7949.7244 | 0 | 0 | 7949.7244 | 0.0005872%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.029826 | 1 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1705 | 0.39111 | 2.9928 | 1.1705 | 0.39111 | 2.9928 | 1.2331 | 0.41201 | 2.9928 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2026 | BW1 | CB BW1 | Tier-1 | Non-HFTD---11 | 1--3 | 0.027874 | 1 | 100% | 8.712 | 88.19% | 0% | 11.81% | 0.3803 | 0 | 0 | 0.3803 | 0 | 0.36278 | 0.39111 | 0.92757 | 0.36278 | 0.39111 | 0.92757 | 0.38217 | 0.41201 | 0.92757 | 4.365% | 0.0039232 | 0.003729 | 2220.6335 | 316.4948 | 49.7388 | 1854.3999 | 2234.2939 | 0 | 0 | 2234.2939 | 1.254e-05%
2026 | 93 | 93-559R | Tier-1 | Non-HFTD---2 | 3--4 | 0.026808 | 1 | 100% | 194.9296 | 89.74% | 7.915% | 2.344% | 8.6591 | 0 | 0 | 8.6591 | 0 | 8.2602 | 0.39111 | 21.1197 | 8.2602 | 0.39111 | 21.1197 | 8.7015 | 0.41201 | 21.1197 | 4.442% | 0.02667 | 0.02535 | 7308.8898 | 1504.7135 | 606.7669 | 5197.4095 | 7347.9399 | 0 | 0 | 7347.9399 | 0.0002855%
2026 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.026098 | 1 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.28535 | 0.39111 | 0.72958 | 0.28535 | 0.39111 | 0.72958 | 0.30059 | 0.41201 | 0.72958 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2026 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.025033 | 1 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.4032 | 0.39111 | 3.5878 | 1.4032 | 0.39111 | 3.5878 | 1.4782 | 0.41201 | 3.5878 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2026 | 95 | 95-35F | Tier-1 | Non-HFTD---9 | 2--2 | 0.024145 | 1 | 100% | 19.0547 | 69.14% | 22.45% | 8.414% | 0.65213 | 0 | 0 | 0.65213 | 0 | 0.62209 | 0.39111 | 1.5906 | 0.62209 | 0.39111 | 1.5906 | 0.65533 | 0.41201 | 1.5906 | 3.422% | 0.011941 | 0.01135 | 1595.6856 | 179.3204 | 352.6449 | 1063.7203 | 1621.3303 | 0 | 0 | 1621.3303 | 2.15e-05%
2026 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.022015 | 1 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.9706 | 0.39111 | 7.5951 | 2.9706 | 0.39111 | 7.5951 | 3.1293 | 0.41201 | 7.5951 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2026 | 63 | 63-35AE | Tier-1 | Non-HFTD---1 | 3--4 | 0.019707 | 1 | 100% | 256.4675 | 76.22% | 23.46% | 0.3199% | 9.6762 | 0 | 0 | 9.6762 | 0 | 9.2304 | 0.39111 | 23.6005 | 9.2304 | 0.39111 | 23.6005 | 9.7236 | 0.41201 | 23.6005 | 3.773% | 0.016955 | 0.016116 | 15126.187 | 2259.8593 | 3445.3068 | 9421.0209 | 15313.5135 | 0 | 0 | 15313.5135 | 0.0003191%
2026 | 450 | 450-114F | Tier-1 | Non-HFTD---7 | 1--4 | 0.018642 | 1 | 100% | 28.615 | 98.32% | 0% | 1.684% | 1.3926 | 0 | 0 | 1.3926 | 0 | 1.3284 | 0.39111 | 3.3965 | 1.3284 | 0.39111 | 3.3965 | 1.3994 | 0.41201 | 3.3965 | 4.867% | 0.0023436 | 0.0022276 | 12209.8338 | 1908.2658 | 365.7567 | 9935.8114 | 12220.543 | 0 | 0 | 12220.543 | 4.592e-05%
2026 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.017576 | 1 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.7021 | 0.39111 | 1.7951 | 0.7021 | 0.39111 | 1.7951 | 0.73961 | 0.41201 | 1.7951 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.017399 | 1 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.3625 | 0.39111 | 8.5973 | 3.3625 | 0.39111 | 8.5973 | 3.5422 | 0.41201 | 8.5973 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 0.017044 | 1 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 162.0011 | 0.39111 | 414.2063 | 162.0011 | 0.39111 | 414.2063 | 170.6571 | 0.41201 | 414.2063 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2026 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.016866 | 1 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.36233 | 0.39111 | 0.92642 | 0.36233 | 0.39111 | 0.92642 | 0.38169 | 0.41201 | 0.92642 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 0.015623 | 1 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 256.8342 | 0.39111 | 656.6766 | 256.8342 | 0.39111 | 656.6766 | 270.5572 | 0.41201 | 656.6766 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2026 | 172 | 172-567R | Tier-1 | Non-HFTD---3 | 4--3 | 0.014203 | 1 | 100% | 141.9219 | 62.19% | 32.78% | 5.033% | 4.369 | 0 | 0 | 4.369 | 0 | 4.1678 | 0.39111 | 10.6562 | 4.1678 | 0.39111 | 10.6562 | 4.3904 | 0.41201 | 10.6562 | 3.078% | 0.069555 | 0.066112 | 2040.4331 | 199.3667 | 664.6627 | 1176.4036 | 2080.609 | 0 | 0 | 2080.609 | 0.0001441%
2026 | TM1 | CB TM1 | Tier-1 | Non-HFTD---7 | 1--5 | 0.014026 | 1 | 100% | 38.7396 | 99.8% | 0% | 0.1958% | 1.9139 | 0 | 0 | 1.9139 | 0 | 1.8257 | 0.39111 | 4.6679 | 1.8257 | 0.39111 | 4.6679 | 1.9232 | 0.41201 | 4.6679 | 4.94% | 0.0001408 | 0.00013383 | 275139.3146 | 43811.8165 | 68.1712 | 231259.327 | 275167.3683 | 0 | 0 | 275167.3683 | 6.311e-05%
2026 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.013848 | 1 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.50996 | 0.39111 | 1.3039 | 0.50996 | 0.39111 | 1.3039 | 0.5372 | 0.41201 | 1.3039 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2026 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.01367 | 1 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 3.0016 | 0.39111 | 7.6744 | 3.0016 | 0.39111 | 7.6744 | 3.1619 | 0.41201 | 7.6744 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2026 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011185 | 1 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.39111 | 0 | 0 | 0.39111 | 0 | 0 | 0.41201 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2026 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.01083 | 1 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.1885 | 0.39111 | 3.0387 | 1.1885 | 0.39111 | 3.0387 | 1.252 | 0.41201 | 3.0387 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2026 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.010652 | 1 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.032694 | 0.39111 | 0.083591 | 0.032694 | 0.39111 | 0.083591 | 0.03444 | 0.41201 | 0.083591 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 0.010475 | 1 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 22.199 | 0.39111 | 56.7585 | 22.199 | 0.39111 | 56.7585 | 23.3851 | 0.41201 | 56.7585 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2026 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.0099421 | 1 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.39111 | 0 | 0 | 0.39111 | 0 | 0 | 0.41201 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2026 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.0094095 | 1 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.2556 | 0.39111 | 3.2103 | 1.2556 | 0.39111 | 3.2103 | 1.3227 | 0.41201 | 3.2103 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.0079892 | 1 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 37.3591 | 0.39111 | 95.5202 | 37.3591 | 0.39111 | 95.5202 | 39.3553 | 0.41201 | 95.5202 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2026 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.0079892 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.31849 | 0.39111 | 0.81433 | 0.31849 | 0.39111 | 0.81433 | 0.33551 | 0.41201 | 0.81433 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2026 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.0056812 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.28378 | 0.39111 | 0.72557 | 0.28378 | 0.39111 | 0.72557 | 0.29894 | 0.41201 | 0.72557 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 18.9705 | 264 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1801.0985 | 98.4969 | 18.2858 | 1801.0985 | 98.4969 | 18.2858 | 1998.7108 | 109.3038 | 18.2858 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 16.9478 | 243 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 613.1991 | 90.6619 | 6.7636 | 613.1991 | 90.6619 | 6.7636 | 680.4779 | 100.6092 | 6.7636 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 16.4216 | 230 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 243.3688 | 85.8117 | 2.8361 | 243.3688 | 85.8117 | 2.8361 | 270.0707 | 95.2268 | 2.8361 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 16.3387 | 208 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 375.994 | 77.6036 | 4.8451 | 375.994 | 77.6036 | 4.8451 | 417.2472 | 86.1181 | 4.8451 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 16.241 | 202 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2919.5776 | 75.3651 | 38.7391 | 2919.5776 | 75.3651 | 38.7391 | 3239.9069 | 83.634 | 38.7391 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 15.1902 | 204 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 819.268 | 76.1113 | 10.7641 | 819.268 | 76.1113 | 10.7641 | 909.1561 | 84.462 | 10.7641 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 14.975 | 232 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 730.5315 | 86.5579 | 8.4398 | 730.5315 | 86.5579 | 8.4398 | 810.6837 | 96.0548 | 8.4398 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 12.4911 | 168 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 176.6226 | 62.6799 | 2.8179 | 176.6226 | 62.6799 | 2.8179 | 196.0012 | 69.5569 | 2.8179 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 12.3702 | 175 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 229.3595 | 65.2915 | 3.5129 | 229.3595 | 65.2915 | 3.5129 | 254.5243 | 72.4552 | 3.5129 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 12.0312 | 165 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 144.3433 | 61.5606 | 2.3447 | 144.3433 | 61.5606 | 2.3447 | 160.1803 | 68.3149 | 2.3447 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 11.9654 | 158 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 175.4857 | 58.9489 | 2.9769 | 175.4857 | 58.9489 | 2.9769 | 194.7396 | 65.4167 | 2.9769 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 11.4812 | 153 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3540.5817 | 57.0834 | 62.0247 | 3540.5817 | 57.0834 | 62.0247 | 3929.0461 | 63.3465 | 62.0247 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 11.2437 | 150 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 75.7062 | 55.9642 | 1.3528 | 75.7062 | 55.9642 | 1.3528 | 84.0125 | 62.1044 | 1.3528 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 11.1024 | 166 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1269.1144 | 61.9337 | 20.4915 | 1269.1144 | 61.9337 | 20.4915 | 1408.3587 | 68.7289 | 20.4915 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 10.8361 | 146 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 68.683 | 54.4718 | 1.2609 | 68.683 | 54.4718 | 1.2609 | 76.2188 | 60.4483 | 1.2609 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 10.2901 | 149 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1379.245 | 55.5911 | 24.8106 | 1379.245 | 55.5911 | 24.8106 | 1530.5725 | 61.6904 | 24.8106 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 10.1733 | 154 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 228.5667 | 57.4565 | 3.9781 | 228.5667 | 57.4565 | 3.9781 | 253.6445 | 63.7605 | 3.9781 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 9.5585 | 147 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 154.9241 | 54.8449 | 2.8248 | 154.9241 | 54.8449 | 2.8248 | 171.922 | 60.8623 | 2.8248 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 9.4763 | 129 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 114.9697 | 48.1292 | 2.3888 | 114.9697 | 48.1292 | 2.3888 | 127.5839 | 53.4098 | 2.3888 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 9.4722 | 119 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 457.7342 | 44.3982 | 10.3097 | 457.7342 | 44.3982 | 10.3097 | 507.9557 | 49.2695 | 10.3097 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 9.219 | 142 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 705.149 | 52.9794 | 13.3099 | 705.149 | 52.9794 | 13.3099 | 782.5163 | 58.7922 | 13.3099 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 9.1274 | 116 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 237.5496 | 43.279 | 5.4888 | 237.5496 | 43.279 | 5.4888 | 263.613 | 48.0274 | 5.4888 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 9.0834 | 125 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1170.8648 | 46.6368 | 25.106 | 1170.8648 | 46.6368 | 25.106 | 1299.3294 | 51.7537 | 25.106 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 8.8391 | 106 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 150.1902 | 39.548 | 3.7977 | 150.1902 | 39.548 | 3.7977 | 166.6687 | 43.8871 | 3.7977 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 8.769 | 159 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 461.194 | 59.322 | 7.7744 | 461.194 | 59.322 | 7.7744 | 511.7951 | 65.8307 | 7.7744 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2027 | 221 | 221-1251R | Tier-1 | Non-HFTD---2 | 5--4 | 8.6538 | 112 | 100% | 1814.8505 | 87.56% | 11.92% | 0.5209% | 78.6628 | 0 | 0 | 78.6628 | 0 | 71.5821 | 41.7866 | 1.713 | 71.5821 | 41.7866 | 1.713 | 79.4359 | 46.3713 | 1.713 | 4.334% | 0.27478 | 0.26118 | 6604.7785 | 826.9947 | 747.1453 | 5030.6385 | 6647.5552 | 0 | 0 | 6647.5552 | 0.002594%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 8.5037 | 120 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 916.1722 | 44.7713 | 20.4634 | 916.1722 | 44.7713 | 20.4634 | 1016.6925 | 49.6835 | 20.4634 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 8.4854 | 124 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 940.331 | 46.2637 | 20.3255 | 940.331 | 46.2637 | 20.3255 | 1043.5019 | 51.3397 | 20.3255 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 8.4423 | 124 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2470.7159 | 46.2637 | 53.4051 | 2470.7159 | 46.2637 | 53.4051 | 2741.797 | 51.3397 | 53.4051 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 8.4285 | 130 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1837.8519 | 48.5023 | 37.8921 | 1837.8519 | 48.5023 | 37.8921 | 2039.4967 | 53.8238 | 37.8921 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 8.2367 | 113 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1130.6716 | 42.1597 | 26.8188 | 1130.6716 | 42.1597 | 26.8188 | 1254.7263 | 46.7853 | 26.8188 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 8.1575 | 139 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 274.3211 | 51.8601 | 5.2896 | 274.3211 | 51.8601 | 5.2896 | 304.419 | 57.5501 | 5.2896 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 8.072 | 95 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 119.0101 | 35.444 | 3.3577 | 119.0101 | 35.444 | 3.3577 | 132.0677 | 39.3328 | 3.3577 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 8.0514 | 112 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 502.3679 | 41.7866 | 12.0222 | 502.3679 | 41.7866 | 12.0222 | 557.4865 | 46.3713 | 12.0222 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 7.8648 | 104 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 574.3981 | 38.8018 | 14.8034 | 574.3981 | 38.8018 | 14.8034 | 637.4198 | 43.0591 | 14.8034 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2027 | 221 | 221-1249R | Tier-1 | Non-HFTD---2 | 5--2 | 7.8246 | 94 | 100% | 329.3718 | 60.93% | 35.44% | 3.632% | 9.9343 | 0 | 0 | 9.9343 | 0 | 9.0401 | 35.0709 | 0.25777 | 9.0401 | 35.0709 | 0.25777 | 10.032 | 38.9188 | 0.25777 | 3.016% | 0.32343 | 0.30742 | 1018.3674 | 70.1582 | 373.9946 | 574.2146 | 1039.0867 | 0 | 0 | 1039.0867 | 0.0003276%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 7.7595 | 100 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 604.7186 | 37.3094 | 16.2082 | 604.7186 | 37.3094 | 16.2082 | 671.067 | 41.4029 | 16.2082 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 7.7298 | 114 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 241.5192 | 42.5328 | 5.6784 | 241.5192 | 42.5328 | 5.6784 | 268.0181 | 47.1994 | 5.6784 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 7.7249 | 134 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1152.5944 | 49.9947 | 23.0544 | 1152.5944 | 49.9947 | 23.0544 | 1279.0544 | 55.4799 | 23.0544 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 7.6943 | 120 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1659.3701 | 44.7713 | 37.0632 | 1659.3701 | 44.7713 | 37.0632 | 1841.4323 | 49.6835 | 37.0632 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 7.5567 | 107 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1037.5009 | 39.9211 | 25.9888 | 1037.5009 | 39.9211 | 25.9888 | 1151.3331 | 44.3012 | 25.9888 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 7.5022 | 112 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1192.3964 | 41.7866 | 28.5354 | 1192.3964 | 41.7866 | 28.5354 | 1323.2233 | 46.3713 | 28.5354 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 7.3384 | 119 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 322.3648 | 44.3982 | 7.2608 | 322.3648 | 44.3982 | 7.2608 | 357.7339 | 49.2695 | 7.2608 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 7.2729 | 117 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 498.8841 | 43.652 | 11.4287 | 498.8841 | 43.652 | 11.4287 | 553.6205 | 48.4414 | 11.4287 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 7.1477 | 105 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 110.0696 | 39.1749 | 2.8097 | 110.0696 | 39.1749 | 2.8097 | 122.1462 | 43.4731 | 2.8097 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 7.05 | 89 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 147.4106 | 33.2054 | 4.4394 | 147.4106 | 33.2054 | 4.4394 | 163.5841 | 36.8486 | 4.4394 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 7.0044 | 107 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1259.9464 | 39.9211 | 31.5609 | 1259.9464 | 39.9211 | 31.5609 | 1398.1847 | 44.3012 | 31.5609 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 6.9425 | 118 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 183.5822 | 44.0251 | 4.1699 | 183.5822 | 44.0251 | 4.1699 | 203.7244 | 48.8555 | 4.1699 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 6.9423 | 98 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 469.0206 | 36.5633 | 12.8277 | 469.0206 | 36.5633 | 12.8277 | 520.4805 | 40.5749 | 12.8277 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 6.7285 | 96 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1669.931 | 35.8171 | 46.6239 | 1669.931 | 35.8171 | 46.6239 | 1853.1519 | 39.7468 | 46.6239 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 6.7134 | 96 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 217.2304 | 35.8171 | 6.065 | 217.2304 | 35.8171 | 6.065 | 241.0644 | 39.7468 | 6.065 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 6.6793 | 104 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1568.061 | 38.8018 | 40.412 | 1568.061 | 38.8018 | 40.412 | 1740.105 | 43.0591 | 40.412 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 6.6731 | 69 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 460.7021 | 25.7435 | 17.8959 | 460.7021 | 25.7435 | 17.8959 | 511.2492 | 28.568 | 17.8959 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 6.6185 | 105 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 80.9279 | 39.1749 | 2.0658 | 80.9279 | 39.1749 | 2.0658 | 89.8072 | 43.4731 | 2.0658 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 6.5844 | 101 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 162.0475 | 37.6825 | 4.3003 | 162.0475 | 37.6825 | 4.3003 | 179.8269 | 41.817 | 4.3003 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 6.5087 | 101 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 821.8107 | 37.6825 | 21.8088 | 821.8107 | 37.6825 | 21.8088 | 911.9778 | 41.817 | 21.8088 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 6.3857 | 85 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 53.1821 | 31.713 | 1.677 | 53.1821 | 31.713 | 1.677 | 59.0171 | 35.1925 | 1.677 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 6.3651 | 74 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 287.9812 | 27.609 | 10.4307 | 287.9812 | 27.609 | 10.4307 | 319.5779 | 30.6382 | 10.4307 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 6.3399 | 103 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 296.627 | 38.4287 | 7.7189 | 296.627 | 38.4287 | 7.7189 | 329.1722 | 42.645 | 7.7189 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 6.3184 | 93 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 373.4462 | 34.6978 | 10.7628 | 373.4462 | 34.6978 | 10.7628 | 414.4198 | 38.5047 | 10.7628 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 6.2953 | 97 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 456.006 | 36.1902 | 12.6003 | 456.006 | 36.1902 | 12.6003 | 506.0379 | 40.1609 | 12.6003 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 6.2854 | 103 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 508.6206 | 38.4287 | 13.2354 | 508.6206 | 38.4287 | 13.2354 | 564.4253 | 42.645 | 13.2354 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 6.2785 | 95 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 159.8647 | 35.444 | 4.5104 | 159.8647 | 35.444 | 4.5104 | 177.4047 | 39.3328 | 4.5104 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 6.2728 | 79 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2024.2656 | 29.4745 | 68.6786 | 2024.2656 | 29.4745 | 68.6786 | 2246.3633 | 32.7083 | 68.6786 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 6.2536 | 72 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 355.9256 | 26.8628 | 13.2498 | 355.9256 | 26.8628 | 13.2498 | 394.9769 | 29.8101 | 13.2498 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 6.2492 | 99 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 195.7136 | 36.9363 | 5.2987 | 195.7136 | 36.9363 | 5.2987 | 217.1869 | 40.9889 | 5.2987 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 6.192 | 88 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 250.5037 | 32.8323 | 7.6298 | 250.5037 | 32.8323 | 7.6298 | 277.9884 | 36.4346 | 7.6298 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 6.1782 | 87 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 118.4418 | 32.4592 | 3.6489 | 118.4418 | 32.4592 | 3.6489 | 131.4369 | 36.0206 | 3.6489 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 6.1766 | 109 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 380.2129 | 40.6673 | 9.3494 | 380.2129 | 40.6673 | 9.3494 | 421.929 | 45.1292 | 9.3494 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 6.1716 | 84 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 411.7972 | 31.3399 | 13.1397 | 411.7972 | 31.3399 | 13.1397 | 456.9786 | 34.7785 | 13.1397 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 6.1345 | 91 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 239.6285 | 33.9516 | 7.0579 | 239.6285 | 33.9516 | 7.0579 | 265.9199 | 37.6767 | 7.0579 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 6.1235 | 100 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 777.0044 | 37.3094 | 20.8259 | 777.0044 | 37.3094 | 20.8259 | 862.2555 | 41.4029 | 20.8259 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 6.0644 | 82 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 611.3449 | 30.5937 | 19.9827 | 611.3449 | 30.5937 | 19.9827 | 678.4203 | 33.9504 | 19.9827 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 6.0573 | 82 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 475.0478 | 30.5937 | 15.5276 | 475.0478 | 30.5937 | 15.5276 | 527.1689 | 33.9504 | 15.5276 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 6.0221 | 79 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 135.6268 | 29.4745 | 4.6015 | 135.6268 | 29.4745 | 4.6015 | 150.5074 | 32.7083 | 4.6015 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 6.015 | 81 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 74.7465 | 30.2206 | 2.4734 | 74.7465 | 30.2206 | 2.4734 | 82.9475 | 33.5364 | 2.4734 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 5.8678 | 90 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 142.5829 | 33.5785 | 4.2463 | 142.5829 | 33.5785 | 4.2463 | 158.2268 | 37.2627 | 4.2463 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 5.8655 | 70 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 377.9207 | 26.1166 | 14.4705 | 377.9207 | 26.1166 | 14.4705 | 419.3853 | 28.9821 | 14.4705 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 5.8426 | 75 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 77.5518 | 27.9821 | 2.7715 | 77.5518 | 27.9821 | 2.7715 | 86.0606 | 31.0522 | 2.7715 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 5.8078 | 82 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 73.1226 | 30.5937 | 2.3901 | 73.1226 | 30.5937 | 2.3901 | 81.1454 | 33.9504 | 2.3901 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 5.794 | 82 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 107.9342 | 30.5937 | 3.528 | 107.9342 | 30.5937 | 3.528 | 119.7765 | 33.9504 | 3.528 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 5.7925 | 77 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 412.0132 | 28.7283 | 14.3417 | 412.0132 | 28.7283 | 14.3417 | 457.2183 | 31.8803 | 14.3417 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 5.7743 | 69 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 64.9552 | 25.7435 | 2.5232 | 64.9552 | 25.7435 | 2.5232 | 72.0819 | 28.568 | 2.5232 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 5.7743 | 95 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 409.4082 | 35.444 | 11.5509 | 409.4082 | 35.444 | 11.5509 | 454.3275 | 39.3328 | 11.5509 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 5.7334 | 83 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 808.0402 | 30.9668 | 26.0937 | 808.0402 | 30.9668 | 26.0937 | 896.6965 | 34.3644 | 26.0937 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 5.6393 | 85 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1007.0762 | 31.713 | 31.7559 | 1007.0762 | 31.713 | 31.7559 | 1117.5702 | 35.1925 | 31.7559 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 5.6107 | 87 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 90.6092 | 32.4592 | 2.7915 | 90.6092 | 32.4592 | 2.7915 | 100.5506 | 36.0206 | 2.7915 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 5.5928 | 89 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 675.9035 | 33.2054 | 20.3552 | 675.9035 | 33.2054 | 20.3552 | 750.0621 | 36.8486 | 20.3552 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 5.5142 | 85 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1444.8081 | 31.713 | 45.5588 | 1444.8081 | 31.713 | 45.5588 | 1603.3291 | 35.1925 | 45.5588 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 5.4426 | 107 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 191.4311 | 39.9211 | 4.7952 | 191.4311 | 39.9211 | 4.7952 | 212.4345 | 44.3012 | 4.7952 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2027 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | 4--5 | 5.4183 | 81 | 100% | 5312.2676 | 97.77% | 1.999% | 0.2313% | 257.0917 | 0 | 0 | 257.0917 | 0 | 233.9499 | 30.2206 | 7.7414 | 233.9499 | 30.2206 | 7.7414 | 259.6184 | 33.5364 | 7.7414 | 4.84% | 0.075145 | 0.071425 | 70693.7485 | 12854.9773 | 1446.2382 | 56392.533 | 70775.8701 | 0 | 0 | 70775.8701 | 0.008478%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 5.3672 | 95 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 321.3252 | 35.444 | 9.0657 | 321.3252 | 35.444 | 9.0657 | 356.5803 | 39.3328 | 9.0657 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 5.3558 | 82 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 389.3404 | 30.5937 | 12.7261 | 389.3404 | 30.5937 | 12.7261 | 432.0579 | 33.9504 | 12.7261 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 5.3395 | 81 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 833.1015 | 30.2206 | 27.5673 | 833.1015 | 30.2206 | 27.5673 | 924.5075 | 33.5364 | 27.5673 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 5.3336 | 104 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 282.5323 | 38.8018 | 7.2814 | 282.5323 | 38.8018 | 7.2814 | 313.5311 | 43.0591 | 7.2814 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 5.2977 | 65 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 48.3556 | 24.2511 | 1.994 | 48.3556 | 24.2511 | 1.994 | 53.6611 | 26.9119 | 1.994 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 5.2871 | 79 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 389.967 | 29.4745 | 13.2307 | 389.967 | 29.4745 | 13.2307 | 432.7533 | 32.7083 | 13.2307 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 5.2523 | 72 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 68.0396 | 26.8628 | 2.5329 | 68.0396 | 26.8628 | 2.5329 | 75.5048 | 29.8101 | 2.5329 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 5.2244 | 59 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 67.1805 | 22.0126 | 3.0519 | 67.1805 | 22.0126 | 3.0519 | 74.5514 | 24.4277 | 3.0519 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 5.212 | 78 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 277.3974 | 29.1014 | 9.5321 | 277.3974 | 29.1014 | 9.5321 | 307.8328 | 32.2943 | 9.5321 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 5.1827 | 76 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 18.1939 | 28.3552 | 0.64164 | 18.1939 | 28.3552 | 0.64164 | 20.1901 | 31.4662 | 0.64164 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 5.1751 | 72 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 89.8634 | 26.8628 | 3.3453 | 89.8634 | 26.8628 | 3.3453 | 99.723 | 29.8101 | 3.3453 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 5.0888 | 75 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1209.3579 | 27.9821 | 43.219 | 1209.3579 | 27.9821 | 43.219 | 1342.0458 | 31.0522 | 43.219 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 5.0843 | 94 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 399.4624 | 35.0709 | 11.3901 | 399.4624 | 35.0709 | 11.3901 | 443.2904 | 38.9188 | 11.3901 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 5.0636 | 75 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 282.7746 | 27.9821 | 10.1056 | 282.7746 | 27.9821 | 10.1056 | 313.7999 | 31.0522 | 10.1056 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 5.063 | 76 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 698.3032 | 28.3552 | 24.627 | 698.3032 | 28.3552 | 24.627 | 774.9194 | 31.4662 | 24.627 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 5.0508 | 80 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 680.9116 | 29.8476 | 22.813 | 680.9116 | 29.8476 | 22.813 | 755.6196 | 33.1224 | 22.813 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 5.0233 | 64 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 999.3119 | 23.878 | 41.8507 | 999.3119 | 23.878 | 41.8507 | 1108.954 | 26.4979 | 41.8507 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 4.978 | 70 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 165.5538 | 26.1166 | 6.339 | 165.5538 | 26.1166 | 6.339 | 183.718 | 28.9821 | 6.339 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 4.9753 | 73 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 517.9939 | 27.2359 | 19.0188 | 517.9939 | 27.2359 | 19.0188 | 574.827 | 30.2242 | 19.0188 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 4.8985 | 74 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 271.7734 | 27.609 | 9.8437 | 271.7734 | 27.609 | 9.8437 | 301.5917 | 30.6382 | 9.8437 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 4.8944 | 58 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 22.4804 | 21.6395 | 1.0389 | 22.4804 | 21.6395 | 1.0389 | 24.9469 | 24.0137 | 1.0389 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 4.8617 | 74 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 159.4396 | 27.609 | 5.7749 | 159.4396 | 27.609 | 5.7749 | 176.933 | 30.6382 | 5.7749 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 4.8551 | 85 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 124.6006 | 31.713 | 3.929 | 124.6006 | 31.713 | 3.929 | 138.2715 | 35.1925 | 3.929 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 4.7692 | 74 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 502.5613 | 27.609 | 18.2028 | 502.5613 | 27.609 | 18.2028 | 557.7011 | 30.6382 | 18.2028 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 4.7364 | 81 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 387.1481 | 30.2206 | 12.8107 | 387.1481 | 30.2206 | 12.8107 | 429.6251 | 33.5364 | 12.8107 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 4.7152 | 60 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 17.8667 | 22.3857 | 0.79813 | 17.8667 | 22.3857 | 0.79813 | 19.8269 | 24.8418 | 0.79813 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 4.6872 | 62 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 40.081 | 23.1319 | 1.7327 | 40.081 | 23.1319 | 1.7327 | 44.4786 | 25.6698 | 1.7327 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 4.6403 | 67 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 750.663 | 24.9973 | 30.0297 | 750.663 | 24.9973 | 30.0297 | 833.024 | 27.74 | 30.0297 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 4.613 | 70 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 155.9371 | 26.1166 | 5.9708 | 155.9371 | 26.1166 | 5.9708 | 173.0461 | 28.9821 | 5.9708 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 4.6105 | 71 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 298.5256 | 26.4897 | 11.2695 | 298.5256 | 26.4897 | 11.2695 | 331.2791 | 29.3961 | 11.2695 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 4.5567 | 59 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 408.4997 | 22.0126 | 18.5576 | 408.4997 | 22.0126 | 18.5576 | 453.3194 | 24.4277 | 18.5576 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 4.5517 | 72 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 264.7098 | 26.8628 | 9.8541 | 264.7098 | 26.8628 | 9.8541 | 293.7531 | 29.8101 | 9.8541 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 4.5471 | 61 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 108.1471 | 22.7588 | 4.7519 | 108.1471 | 22.7588 | 4.7519 | 120.0127 | 25.2558 | 4.7519 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 4.5413 | 78 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 366.9683 | 29.1014 | 12.61 | 366.9683 | 29.1014 | 12.61 | 407.2312 | 32.2943 | 12.61 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 4.5215 | 73 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 192.6453 | 27.2359 | 7.0732 | 192.6453 | 27.2359 | 7.0732 | 213.7819 | 30.2242 | 7.0732 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 4.5105 | 78 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 304.1512 | 29.1014 | 10.4514 | 304.1512 | 29.1014 | 10.4514 | 337.522 | 32.2943 | 10.4514 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 4.4665 | 60 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 892.989 | 22.3857 | 39.8911 | 892.989 | 22.3857 | 39.8911 | 990.9657 | 24.8418 | 39.8911 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 4.4447 | 63 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1264.1257 | 23.5049 | 53.7813 | 1264.1257 | 23.5049 | 53.7813 | 1402.8226 | 26.0839 | 53.7813 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 4.4326 | 62 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 58.891 | 23.1319 | 2.5459 | 58.891 | 23.1319 | 2.5459 | 65.3523 | 25.6698 | 2.5459 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 4.4294 | 79 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 144.2426 | 29.4745 | 4.8938 | 144.2426 | 29.4745 | 4.8938 | 160.0686 | 32.7083 | 4.8938 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 4.3685 | 55 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 305.3339 | 20.5202 | 14.8797 | 305.3339 | 20.5202 | 14.8797 | 338.8344 | 22.7716 | 14.8797 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 4.3413 | 58 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 67.4256 | 21.6395 | 3.1159 | 67.4256 | 21.6395 | 3.1159 | 74.8234 | 24.0137 | 3.1159 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 4.3085 | 63 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1051.3816 | 23.5049 | 44.7302 | 1051.3816 | 23.5049 | 44.7302 | 1166.7367 | 26.0839 | 44.7302 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 4.292 | 63 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 294.6356 | 23.5049 | 12.535 | 294.6356 | 23.5049 | 12.535 | 326.9624 | 26.0839 | 12.535 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 4.2842 | 53 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 313.8836 | 19.774 | 15.8735 | 313.8836 | 19.774 | 15.8735 | 348.3221 | 21.9436 | 15.8735 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 4.2597 | 57 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 145.0545 | 21.2664 | 6.8208 | 145.0545 | 21.2664 | 6.8208 | 160.9695 | 23.5997 | 6.8208 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 4.1777 | 71 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 700.4791 | 26.4897 | 26.4434 | 700.4791 | 26.4897 | 26.4434 | 777.3341 | 29.3961 | 26.4434 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 4.175 | 75 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1206.3179 | 27.9821 | 43.1104 | 1206.3179 | 27.9821 | 43.1104 | 1338.6723 | 31.0522 | 43.1104 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 4.1306 | 59 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 561.9538 | 22.0126 | 25.5288 | 561.9538 | 22.0126 | 25.5288 | 623.61 | 24.4277 | 25.5288 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 4.1246 | 51 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 55.8373 | 19.0278 | 2.9345 | 55.8373 | 19.0278 | 2.9345 | 61.9636 | 21.1155 | 2.9345 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 4.0797 | 70 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 135.1583 | 26.1166 | 5.1752 | 135.1583 | 26.1166 | 5.1752 | 149.9876 | 28.9821 | 5.1752 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 4.0305 | 55 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 254.1624 | 20.5202 | 12.386 | 254.1624 | 20.5202 | 12.386 | 282.0485 | 22.7716 | 12.386 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 4.0205 | 46 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 451.3803 | 17.1623 | 26.3006 | 451.3803 | 17.1623 | 26.3006 | 500.9047 | 19.0454 | 26.3006 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 4.0063 | 72 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 223.9657 | 26.8628 | 8.3374 | 223.9657 | 26.8628 | 8.3374 | 248.5387 | 29.8101 | 8.3374 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 4.0008 | 67 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 388.0424 | 24.9973 | 15.5234 | 388.0424 | 24.9973 | 15.5234 | 430.6175 | 27.74 | 15.5234 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 3.8739 | 51 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 64.8175 | 19.0278 | 3.4065 | 64.8175 | 19.0278 | 3.4065 | 71.9292 | 21.1155 | 3.4065 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 3.8709 | 52 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 149.7342 | 19.4009 | 7.7179 | 149.7342 | 19.4009 | 7.7179 | 166.1626 | 21.5295 | 7.7179 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 3.8679 | 61 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 152.8245 | 22.7588 | 6.715 | 152.8245 | 22.7588 | 6.715 | 169.592 | 25.2558 | 6.715 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 3.8654 | 52 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 79.9189 | 19.4009 | 4.1193 | 79.9189 | 19.4009 | 4.1193 | 88.6875 | 21.5295 | 4.1193 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 3.8277 | 55 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 644.9047 | 20.5202 | 31.4278 | 644.9047 | 20.5202 | 31.4278 | 715.6622 | 22.7716 | 31.4278 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 3.8071 | 70 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 51.3378 | 26.1166 | 1.9657 | 51.3378 | 26.1166 | 1.9657 | 56.9704 | 28.9821 | 1.9657 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 3.7897 | 49 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 184.9104 | 18.2816 | 10.1145 | 184.9104 | 18.2816 | 10.1145 | 205.1983 | 20.2874 | 10.1145 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 3.777 | 62 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 85.0286 | 23.1319 | 3.6758 | 85.0286 | 23.1319 | 3.6758 | 94.3577 | 25.6698 | 3.6758 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 3.7716 | 56 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 129.1825 | 20.8933 | 6.183 | 129.1825 | 20.8933 | 6.183 | 143.3561 | 23.1856 | 6.183 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 3.762 | 57 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 167.0067 | 21.2664 | 7.8531 | 167.0067 | 21.2664 | 7.8531 | 185.3303 | 23.5997 | 7.8531 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 3.7556 | 54 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 130.6158 | 20.1471 | 6.4831 | 130.6158 | 20.1471 | 6.4831 | 144.9467 | 22.3576 | 6.4831 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 3.7382 | 64 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 171.9679 | 23.878 | 7.2019 | 171.9679 | 23.878 | 7.2019 | 190.8359 | 26.4979 | 7.2019 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 3.729 | 53 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 494.3491 | 19.774 | 24.9999 | 494.3491 | 19.774 | 24.9999 | 548.5879 | 21.9436 | 24.9999 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 3.704 | 55 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 432.2395 | 20.5202 | 21.0641 | 432.2395 | 20.5202 | 21.0641 | 479.6638 | 22.7716 | 21.0641 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 3.6992 | 49 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 226.9901 | 18.2816 | 12.4163 | 226.9901 | 18.2816 | 12.4163 | 251.895 | 20.2874 | 12.4163 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 3.6983 | 73 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 135.7606 | 27.2359 | 4.9846 | 135.7606 | 27.2359 | 4.9846 | 150.6559 | 30.2242 | 4.9846 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 3.666 | 64 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1006.1322 | 23.878 | 42.1363 | 1006.1322 | 23.878 | 42.1363 | 1116.5227 | 26.4979 | 42.1363 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 3.5829 | 54 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 24.4376 | 20.1471 | 1.213 | 24.4376 | 20.1471 | 1.213 | 27.1188 | 22.3576 | 1.213 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 3.5582 | 64 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 141.9018 | 23.878 | 5.9428 | 141.9018 | 23.878 | 5.9428 | 157.4709 | 26.4979 | 5.9428 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 3.5375 | 58 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 627.3269 | 21.6395 | 28.9899 | 627.3269 | 21.6395 | 28.9899 | 696.1557 | 24.0137 | 28.9899 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 3.4803 | 57 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 465.7123 | 21.2664 | 21.899 | 465.7123 | 21.2664 | 21.899 | 516.8091 | 23.5997 | 21.899 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 3.4792 | 59 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 85.5897 | 22.0126 | 3.8882 | 85.5897 | 22.0126 | 3.8882 | 94.9804 | 24.4277 | 3.8882 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 3.4748 | 49 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 218.2996 | 18.2816 | 11.9409 | 218.2996 | 18.2816 | 11.9409 | 242.251 | 20.2874 | 11.9409 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 3.4634 | 58 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 332.7936 | 21.6395 | 15.379 | 332.7936 | 21.6395 | 15.379 | 369.307 | 24.0137 | 15.379 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 3.4338 | 51 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 547.9949 | 19.0278 | 28.7997 | 547.9949 | 19.0278 | 28.7997 | 608.1196 | 21.1155 | 28.7997 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 3.4306 | 44 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 271.0346 | 16.4162 | 16.5102 | 271.0346 | 16.4162 | 16.5102 | 300.7719 | 18.2173 | 16.5102 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 3.3636 | 41 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 713.6047 | 15.2969 | 46.6504 | 713.6047 | 15.2969 | 46.6504 | 791.8998 | 16.9752 | 46.6504 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 3.313 | 51 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 308.3982 | 19.0278 | 16.2078 | 308.3982 | 19.0278 | 16.2078 | 342.2349 | 21.1155 | 16.2078 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 3.2878 | 52 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 821.8397 | 19.4009 | 42.3609 | 821.8397 | 19.4009 | 42.3609 | 912.01 | 21.5295 | 42.3609 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 3.2754 | 50 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 235.5518 | 18.6547 | 12.6269 | 235.5518 | 18.6547 | 12.6269 | 261.396 | 20.7015 | 12.6269 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 3.2692 | 43 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 512.6697 | 16.0431 | 31.9559 | 512.6697 | 16.0431 | 31.9559 | 568.9186 | 17.8033 | 31.9559 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 3.2674 | 51 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 245.7559 | 19.0278 | 12.9156 | 245.7559 | 19.0278 | 12.9156 | 272.7197 | 21.1155 | 12.9156 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 3.2566 | 43 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 131.5802 | 16.0431 | 8.2017 | 131.5802 | 16.0431 | 8.2017 | 146.0169 | 17.8033 | 8.2017 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 3.2292 | 52 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 869.0928 | 19.4009 | 44.7965 | 869.0928 | 19.4009 | 44.7965 | 964.4476 | 21.5295 | 44.7965 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 3.1944 | 52 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 98.8295 | 19.4009 | 5.0941 | 98.8295 | 19.4009 | 5.0941 | 109.6728 | 21.5295 | 5.0941 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 3.1096 | 46 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 43.4702 | 17.1623 | 2.5329 | 43.4702 | 17.1623 | 2.5329 | 48.2397 | 19.0454 | 2.5329 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 3.1062 | 56 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1049.1639 | 20.8933 | 50.2154 | 1049.1639 | 20.8933 | 50.2154 | 1164.2757 | 23.1856 | 50.2154 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 3.1055 | 42 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 655.4112 | 15.67 | 41.826 | 655.4112 | 15.67 | 41.826 | 727.3214 | 17.3892 | 41.826 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 3.1032 | 38 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 364.787 | 14.1776 | 25.7298 | 364.787 | 14.1776 | 25.7298 | 404.8106 | 15.7331 | 25.7298 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 3.1032 | 40 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 45.4442 | 14.9238 | 3.0451 | 45.4442 | 14.9238 | 3.0451 | 50.4303 | 16.5612 | 3.0451 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 3.0947 | 37 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 72.2882 | 13.8045 | 5.2366 | 72.2882 | 13.8045 | 5.2366 | 80.2195 | 15.3191 | 5.2366 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2027 | BN2 | CB BN2 | Tier-1 | Non-HFTD---1 | 4--5 | 3.0893 | 50 | 100% | 1098.8312 | 99.36% | 0% | 0.6449% | 54.0413 | 0 | 0 | 54.0413 | 0 | 49.1769 | 18.6547 | 2.6362 | 49.1769 | 18.6547 | 2.6362 | 54.5725 | 20.7015 | 2.6362 | 4.918% | 0.034221 | 0.032527 | 32110.0379 | 7492.6936 | 90.1662 | 24527.178 | 32120.8227 | 0 | 0 | 32120.8227 | 0.001782%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 3.0886 | 43 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 99.8502 | 16.0431 | 6.2239 | 99.8502 | 16.0431 | 6.2239 | 110.8055 | 17.8033 | 6.2239 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 3.0856 | 48 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 111.8057 | 17.9085 | 6.2432 | 111.8057 | 17.9085 | 6.2432 | 124.0728 | 19.8734 | 6.2432 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 3.0508 | 41 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 845.436 | 15.2969 | 55.2686 | 845.436 | 15.2969 | 55.2686 | 938.1953 | 16.9752 | 55.2686 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 3.0423 | 31 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 235.2675 | 11.5659 | 20.3414 | 235.2675 | 11.5659 | 20.3414 | 261.0805 | 12.8349 | 20.3414 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 3.0327 | 45 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 654.899 | 16.7892 | 39.007 | 654.899 | 16.7892 | 39.007 | 726.7529 | 18.6313 | 39.007 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 3.0013 | 33 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 318.6899 | 12.3121 | 25.8843 | 318.6899 | 12.3121 | 25.8843 | 353.6559 | 13.663 | 25.8843 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 2.931 | 43 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 550.9097 | 16.0431 | 34.3394 | 550.9097 | 16.0431 | 34.3394 | 611.3542 | 17.8033 | 34.3394 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 2.8346 | 48 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 264.2682 | 17.9085 | 14.7566 | 264.2682 | 17.9085 | 14.7566 | 293.2631 | 19.8734 | 14.7566 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 2.8213 | 45 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 56.0299 | 16.7892 | 3.3372 | 56.0299 | 16.7892 | 3.3372 | 62.1774 | 18.6313 | 3.3372 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 2.8166 | 44 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 31.5996 | 16.4162 | 1.9249 | 31.5996 | 16.4162 | 1.9249 | 35.0666 | 18.2173 | 1.9249 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 2.7905 | 43 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 150.9784 | 16.0431 | 9.4108 | 150.9784 | 16.0431 | 9.4108 | 167.5434 | 17.8033 | 9.4108 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 2.7494 | 42 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 524.7816 | 15.67 | 33.4896 | 524.7816 | 15.67 | 33.4896 | 582.3594 | 17.3892 | 33.4896 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 2.7478 | 42 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 506.1555 | 15.67 | 32.301 | 506.1555 | 15.67 | 32.301 | 561.6897 | 17.3892 | 32.301 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 2.7261 | 42 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 606.1886 | 15.67 | 38.6847 | 606.1886 | 15.67 | 38.6847 | 672.6982 | 17.3892 | 38.6847 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 2.678 | 32 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 209.6923 | 11.939 | 17.5636 | 209.6923 | 11.939 | 17.5636 | 232.6993 | 13.2489 | 17.5636 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 2.6361 | 42 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 240.2011 | 15.67 | 15.3288 | 240.2011 | 15.67 | 15.3288 | 266.5555 | 17.3892 | 15.3288 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 2.6311 | 29 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 38.8993 | 10.8197 | 3.5952 | 38.8993 | 10.8197 | 3.5952 | 43.1673 | 12.0069 | 3.5952 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 2.6281 | 38 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 266.0239 | 14.1776 | 18.7637 | 266.0239 | 14.1776 | 18.7637 | 295.2114 | 15.7331 | 18.7637 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 2.6018 | 32 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 95.41 | 11.939 | 7.9914 | 95.41 | 11.939 | 7.9914 | 105.8782 | 13.2489 | 7.9914 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 2.5951 | 48 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 240.3733 | 17.9085 | 13.4223 | 240.3733 | 17.9085 | 13.4223 | 266.7465 | 19.8734 | 13.4223 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2027 | 305 | CB 305 | Tier-1 | Non-HFTD---1 | 4--5 | 2.575 | 36 | 100% | 2786.7739 | 97.11% | 2.732% | 0.1605% | 133.9547 | 0 | 0 | 133.9547 | 0 | 121.8969 | 13.4314 | 9.0755 | 121.8969 | 13.4314 | 9.0755 | 135.2712 | 14.9051 | 9.0755 | 4.807% | 0.073949 | 0.070288 | 37685.1802 | 5958.9331 | 946.9636 | 30779.2836 | 37741.9553 | 0 | 0 | 37741.9553 | 0.004417%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 2.531 | 36 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 79.6362 | 13.4314 | 5.9291 | 79.6362 | 13.4314 | 5.9291 | 88.3736 | 14.9051 | 5.9291 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 2.5257 | 32 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 234.0568 | 11.939 | 19.6044 | 234.0568 | 11.939 | 19.6044 | 259.737 | 13.2489 | 19.6044 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 2.4981 | 46 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 66.4558 | 17.1623 | 3.8722 | 66.4558 | 17.1623 | 3.8722 | 73.7472 | 19.0454 | 3.8722 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 2.4941 | 35 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 123.7039 | 13.0583 | 9.4732 | 123.7039 | 13.0583 | 9.4732 | 137.2764 | 14.491 | 9.4732 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 2.4903 | 40 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 191.1024 | 14.9238 | 12.8052 | 191.1024 | 14.9238 | 12.8052 | 212.0697 | 16.5612 | 12.8052 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 2.4751 | 38 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 157.9098 | 14.1776 | 11.138 | 157.9098 | 14.1776 | 11.138 | 175.2352 | 15.7331 | 11.138 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 2.4671 | 37 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 408.8067 | 13.8045 | 29.614 | 408.8067 | 13.8045 | 29.614 | 453.66 | 15.3191 | 29.614 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 2.4658 | 33 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 226.5547 | 12.3121 | 18.401 | 226.5547 | 12.3121 | 18.401 | 251.4117 | 13.663 | 18.401 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 2.4649 | 27 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 172.8267 | 10.0735 | 17.1565 | 172.8267 | 10.0735 | 17.1565 | 191.7888 | 11.1788 | 17.1565 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 2.4456 | 43 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 404.9546 | 16.0431 | 25.2417 | 404.9546 | 16.0431 | 25.2417 | 449.3853 | 17.8033 | 25.2417 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 2.4106 | 39 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 56.6878 | 14.5507 | 3.8959 | 56.6878 | 14.5507 | 3.8959 | 62.9074 | 16.1471 | 3.8959 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 2.3652 | 54 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 73.3558 | 20.1471 | 3.641 | 73.3558 | 20.1471 | 3.641 | 81.4042 | 22.3576 | 3.641 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 2.3519 | 38 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 60.6355 | 14.1776 | 4.2769 | 60.6355 | 14.1776 | 4.2769 | 67.2883 | 15.7331 | 4.2769 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 2.3316 | 32 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 217.1483 | 11.939 | 18.1881 | 217.1483 | 11.939 | 18.1881 | 240.9733 | 13.2489 | 18.1881 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 2.3139 | 24 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 14.5292 | 8.9543 | 1.6226 | 14.5292 | 8.9543 | 1.6226 | 16.1233 | 9.9367 | 1.6226 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 2.3096 | 32 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 19.1528 | 11.939 | 1.6042 | 19.1528 | 11.939 | 1.6042 | 21.2542 | 13.2489 | 1.6042 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 2.308 | 33 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 221.282 | 12.3121 | 17.9727 | 221.282 | 12.3121 | 17.9727 | 245.5605 | 13.663 | 17.9727 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 2.2931 | 36 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 32.6276 | 13.4314 | 2.4292 | 32.6276 | 13.4314 | 2.4292 | 36.2074 | 14.9051 | 2.4292 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 2.2137 | 38 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 21.2363 | 14.1776 | 1.4979 | 21.2363 | 14.1776 | 1.4979 | 23.5663 | 15.7331 | 1.4979 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 2.197 | 32 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 439.7915 | 11.939 | 36.8365 | 439.7915 | 11.939 | 36.8365 | 488.0444 | 13.2489 | 36.8365 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 2.1724 | 37 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 525.3163 | 13.8045 | 38.054 | 525.3163 | 13.8045 | 38.054 | 582.9527 | 15.3191 | 38.054 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 2.1631 | 32 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 79.4193 | 11.939 | 6.6521 | 79.4193 | 11.939 | 6.6521 | 88.133 | 13.2489 | 6.6521 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 2.1495 | 30 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 237.497 | 11.1928 | 21.2187 | 237.497 | 11.1928 | 21.2187 | 263.5546 | 12.4209 | 21.2187 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 2.125 | 36 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 98.5708 | 13.4314 | 7.3388 | 98.5708 | 13.4314 | 7.3388 | 109.3858 | 14.9051 | 7.3388 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 2.1166 | 37 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 402.1167 | 13.8045 | 29.1294 | 402.1167 | 13.8045 | 29.1294 | 446.236 | 15.3191 | 29.1294 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 2.0966 | 30 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 242.1556 | 11.1928 | 21.6349 | 242.1556 | 11.1928 | 21.6349 | 268.7244 | 12.4209 | 21.6349 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2027 | 859 | 859-13F | Tier-1 | Non-HFTD---1 | 4--5 | 2.0873 | 40 | 100% | 1153.8557 | 99.35% | 0% | 0.6497% | 56.7448 | 0 | 0 | 56.7448 | 0 | 51.637 | 14.9238 | 3.46 | 51.637 | 14.9238 | 3.46 | 57.3025 | 16.5612 | 3.46 | 4.918% | 0.035677 | 0.033911 | 32341.7236 | 5122.1729 | 819.8446 | 26399.7061 | 32352.6656 | 0 | 0 | 32352.6656 | 0.001871%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 2.0797 | 33 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 417.8482 | 12.3121 | 33.938 | 417.8482 | 12.3121 | 33.938 | 463.6936 | 13.663 | 33.938 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 2.0717 | 32 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 140.9108 | 11.939 | 11.8025 | 140.9108 | 11.939 | 11.8025 | 156.3712 | 13.2489 | 11.8025 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 2.0635 | 28 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 69.195 | 10.4466 | 6.6237 | 69.195 | 10.4466 | 6.6237 | 76.7869 | 11.5928 | 6.6237 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 2.0555 | 26 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 38.0091 | 9.7005 | 3.9183 | 38.0091 | 9.7005 | 3.9183 | 42.1794 | 10.7648 | 3.9183 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2027 | 63 | 63-797R | Tier-1 | Non-HFTD---1 | 3--5 | 1.9943 | 28 | 100% | 1294.9207 | 95.84% | 3.945% | 0.2104% | 61.435 | 0 | 0 | 61.435 | 0 | 55.905 | 10.4466 | 5.3515 | 55.905 | 10.4466 | 5.3515 | 62.0388 | 11.5928 | 5.3515 | 4.744% | 0.02549 | 0.024229 | 50800.3291 | 10671.1023 | 1938.6345 | 38190.5924 | 50910.264 | 0 | 0 | 50910.264 | 0.002026%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 1.9678 | 26 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 96.2068 | 9.7005 | 9.9178 | 96.2068 | 9.7005 | 9.9178 | 106.7624 | 10.7648 | 9.9178 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2027 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | 4--5 | 1.9662 | 38 | 100% | 4233.8665 | 96.93% | 2.943% | 0.1312% | 203.133 | 0 | 0 | 203.133 | 0 | 184.8483 | 14.1776 | 13.0381 | 184.8483 | 14.1776 | 13.0381 | 205.1294 | 15.7331 | 13.0381 | 4.798% | 0.080233 | 0.076262 | 52769.5087 | 8342.6927 | 1399.583 | 43027.233 | 52853.9991 | 0 | 0 | 52853.9991 | 0.006699%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 1.9529 | 27 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 175.5102 | 10.0735 | 17.4229 | 175.5102 | 10.0735 | 17.4229 | 194.7668 | 11.1788 | 17.4229 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 1.9524 | 23 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 64.084 | 8.5812 | 7.468 | 64.084 | 8.5812 | 7.468 | 71.1152 | 9.5227 | 7.468 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 1.9416 | 22 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 43.1232 | 8.2081 | 5.2538 | 43.1232 | 8.2081 | 5.2538 | 47.8546 | 9.1086 | 5.2538 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 1.9313 | 20 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 454.2842 | 7.4619 | 60.8806 | 454.2842 | 7.4619 | 60.8806 | 504.1272 | 8.2806 | 60.8806 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 1.9282 | 3 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 166.1042 | 1.1193 | 148.4023 | 166.1042 | 1.1193 | 148.4023 | 184.3288 | 1.2421 | 148.4023 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 1.9167 | 27 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 410.7886 | 10.0735 | 40.7789 | 410.7886 | 10.0735 | 40.7789 | 455.8594 | 11.1788 | 40.7789 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 1.9116 | 29 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 523.5501 | 10.8197 | 48.3884 | 523.5501 | 10.8197 | 48.3884 | 580.9928 | 12.0069 | 48.3884 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 1.9075 | 26 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 20.217 | 9.7005 | 2.0841 | 20.217 | 9.7005 | 2.0841 | 22.4352 | 10.7648 | 2.0841 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 1.8959 | 25 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 16.5362 | 9.3274 | 1.7729 | 16.5362 | 9.3274 | 1.7729 | 18.3505 | 10.3507 | 1.7729 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2027 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | 3--5 | 1.8897 | 36 | 100% | 1585.8519 | 99.67% | 0% | 0.3254% | 78.2443 | 0 | 0 | 78.2443 | 0 | 71.2012 | 13.4314 | 5.3011 | 71.2012 | 13.4314 | 5.3011 | 79.0132 | 14.9051 | 5.3011 | 4.934% | 0.026002 | 0.024715 | 60989.6136 | 9907.2213 | 216.3013 | 50866.0909 | 60999.9476 | 0 | 0 | 60999.9476 | 0.00258%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 1.8872 | 28 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 48.5092 | 10.4466 | 4.6435 | 48.5092 | 10.4466 | 4.6435 | 53.8315 | 11.5928 | 4.6435 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 1.8794 | 27 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.2749 | 10.0735 | 0.72218 | 7.2749 | 10.0735 | 0.72218 | 8.0731 | 11.1788 | 0.72218 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 1.875 | 19 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 386.4725 | 7.0888 | 54.5188 | 386.4725 | 7.0888 | 54.5188 | 428.8754 | 7.8666 | 54.5188 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 1.8512 | 22 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 55.5708 | 8.2081 | 6.7703 | 55.5708 | 8.2081 | 6.7703 | 61.6679 | 9.1086 | 6.7703 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 1.8462 | 35 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 513.522 | 13.0583 | 39.3253 | 513.522 | 13.0583 | 39.3253 | 569.8644 | 14.491 | 39.3253 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 1.8381 | 33 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 65.2597 | 12.3121 | 5.3004 | 65.2597 | 12.3121 | 5.3004 | 72.4198 | 13.663 | 5.3004 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 1.8306 | 32 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 227.2841 | 11.939 | 19.0371 | 227.2841 | 11.939 | 19.0371 | 252.2212 | 13.2489 | 19.0371 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2027 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | 4--5 | 1.8306 | 28 | 100% | 2371.786 | 97.71% | 2.108% | 0.1806% | 114.7166 | 0 | 0 | 114.7166 | 0 | 104.3906 | 10.4466 | 9.9927 | 104.3906 | 10.4466 | 9.9927 | 115.8441 | 11.5928 | 9.9927 | 4.837% | 0.074138 | 0.070468 | 31991.6747 | 5091.6051 | 638.7369 | 26261.3327 | 32029.8024 | 0 | 0 | 32029.8024 | 0.003783%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 1.8025 | 10 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 149.8384 | 3.7309 | 40.161 | 149.8384 | 3.7309 | 40.161 | 166.2783 | 4.1403 | 40.161 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 1.7988 | 27 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 100.4117 | 10.0735 | 9.9679 | 100.4117 | 10.0735 | 9.9679 | 111.4286 | 11.1788 | 9.9679 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 1.7985 | 30 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 204.9832 | 11.1928 | 18.3138 | 204.9832 | 11.1928 | 18.3138 | 227.4734 | 12.4209 | 18.3138 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 1.7681 | 31 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 58.3163 | 11.5659 | 5.0421 | 58.3163 | 11.5659 | 5.0421 | 64.7147 | 12.8349 | 5.0421 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 1.7564 | 23 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 294.2347 | 8.5812 | 34.2884 | 294.2347 | 8.5812 | 34.2884 | 326.5175 | 9.5227 | 34.2884 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 1.7092 | 24 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 36.1453 | 8.9543 | 4.0367 | 36.1453 | 8.9543 | 4.0367 | 40.1111 | 9.9367 | 4.0367 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 1.6955 | 27 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 101.4086 | 10.0735 | 10.0668 | 101.4086 | 10.0735 | 10.0668 | 112.5349 | 11.1788 | 10.0668 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 1.6928 | 34 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 371.1005 | 12.6852 | 29.2546 | 371.1005 | 12.6852 | 29.2546 | 411.8168 | 14.077 | 29.2546 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 1.685 | 34 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 25.8594 | 12.6852 | 2.0385 | 25.8594 | 12.6852 | 2.0385 | 28.6967 | 14.077 | 2.0385 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 1.6768 | 29 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 58.3792 | 10.8197 | 5.3956 | 58.3792 | 10.8197 | 5.3956 | 64.7844 | 12.0069 | 5.3956 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2027 | 504 | 504-40R | Tier-1 | Non-HFTD---1 | 3--5 | 1.6708 | 33 | 100% | 796.3763 | 99.35% | 0% | 0.6476% | 39.1654 | 0 | 0 | 39.1654 | 0 | 35.6399 | 12.3121 | 2.8947 | 35.6399 | 12.3121 | 2.8947 | 39.5503 | 13.663 | 2.8947 | 4.918% | 0.025961 | 0.024676 | 30675.6364 | 4949.6837 | 226.8975 | 25499.0552 | 30685.9814 | 0 | 0 | 30685.9814 | 0.001292%
2027 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 1.6678 | 25 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 462.3957 | 9.3274 | 49.5741 | 462.3957 | 9.3274 | 49.5741 | 513.1287 | 10.3507 | 49.5741 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 1.6667 | 31 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 120.9234 | 11.5659 | 10.4551 | 120.9234 | 11.5659 | 10.4551 | 134.1908 | 12.8349 | 10.4551 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 1.6595 | 28 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 369.8356 | 10.4466 | 35.4023 | 369.8356 | 10.4466 | 35.4023 | 410.4131 | 11.5928 | 35.4023 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2027 | 170 | 170-410R | Tier-1 | Non-HFTD---8 | 5--1 | 1.6575 | 17 | 100% | 29.1667 | 31.01% | 45.41% | 23.57% | 0.44774 | 0 | 0 | 0.44774 | 0 | 0.40744 | 6.3426 | 0.064238 | 0.40744 | 6.3426 | 0.064238 | 0.45214 | 7.0385 | 0.064238 | 1.535% | 0.10336 | 0.098244 | 282.1845 | 8.474 | 122.6089 | 151.1016 | 292.3227 | 0 | 0 | 292.3227 | 1.476e-05%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 1.6502 | 23 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 58.3418 | 8.5812 | 6.7988 | 58.3418 | 8.5812 | 6.7988 | 64.7429 | 9.5227 | 6.7988 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 1.6334 | 26 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 64.6275 | 9.7005 | 6.6623 | 64.6275 | 9.7005 | 6.6623 | 71.7183 | 10.7648 | 6.6623 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 1.633 | 20 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 65.3245 | 7.4619 | 8.7544 | 65.3245 | 7.4619 | 8.7544 | 72.4917 | 8.2806 | 8.7544 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 1.6303 | 18 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 61.4752 | 6.7157 | 9.154 | 61.4752 | 6.7157 | 9.154 | 68.2202 | 7.4525 | 9.154 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2027 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 1.6074 | 28 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 558.9371 | 10.4466 | 53.504 | 558.9371 | 10.4466 | 53.504 | 620.2624 | 11.5928 | 53.504 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 1.5842 | 23 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 162.7089 | 8.5812 | 18.9612 | 162.7089 | 8.5812 | 18.9612 | 180.561 | 9.5227 | 18.9612 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 1.5812 | 24 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 167.0073 | 8.9543 | 18.6511 | 167.0073 | 8.9543 | 18.6511 | 185.3309 | 9.9367 | 18.6511 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 1.5508 | 21 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 431.4681 | 7.835 | 55.0694 | 431.4681 | 7.835 | 55.0694 | 478.8077 | 8.6946 | 55.0694 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 1.5471 | 28 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 359.1166 | 10.4466 | 34.3763 | 359.1166 | 10.4466 | 34.3763 | 398.5181 | 11.5928 | 34.3763 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 1.5464 | 26 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 17.6405 | 9.7005 | 1.8185 | 17.6405 | 9.7005 | 1.8185 | 19.576 | 10.7648 | 1.8185 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 1.5456 | 31 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 430.0662 | 11.5659 | 37.1839 | 430.0662 | 11.5659 | 37.1839 | 477.252 | 12.8349 | 37.1839 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 1.5412 | 19 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 136.2236 | 7.0888 | 19.2168 | 136.2236 | 7.0888 | 19.2168 | 151.1698 | 7.8666 | 19.2168 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 1.5364 | 22 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 129.1894 | 8.2081 | 15.7393 | 129.1894 | 8.2081 | 15.7393 | 143.3638 | 9.1086 | 15.7393 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 1.5139 | 26 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.7342 | 9.7005 | 1.4158 | 13.7342 | 9.7005 | 1.4158 | 15.2411 | 10.7648 | 1.4158 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 1.5062 | 21 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 70.4536 | 7.835 | 8.9922 | 70.4536 | 7.835 | 8.9922 | 78.1836 | 8.6946 | 8.9922 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 1.5037 | 20 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 83.8042 | 7.4619 | 11.231 | 83.8042 | 7.4619 | 11.231 | 92.999 | 8.2806 | 11.231 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 1.4968 | 22 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 205.7031 | 8.2081 | 25.0611 | 205.7031 | 8.2081 | 25.0611 | 228.2724 | 9.1086 | 25.0611 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 1.4952 | 31 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 81.859 | 11.5659 | 7.0776 | 81.859 | 11.5659 | 7.0776 | 90.8403 | 12.8349 | 7.0776 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 1.4812 | 17 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 53.1521 | 6.3426 | 8.3802 | 53.1521 | 6.3426 | 8.3802 | 58.9838 | 7.0385 | 8.3802 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 1.4789 | 19 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 226.7991 | 7.0888 | 31.994 | 226.7991 | 7.0888 | 31.994 | 251.683 | 7.8666 | 31.994 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 1.4762 | 27 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 72.0469 | 10.0735 | 7.1521 | 72.0469 | 10.0735 | 7.1521 | 79.9518 | 11.1788 | 7.1521 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2027 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 1.4725 | 22 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 119.8785 | 8.2081 | 14.6049 | 119.8785 | 8.2081 | 14.6049 | 133.0313 | 9.1086 | 14.6049 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 1.4649 | 18 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.4153 | 6.7157 | 0.80636 | 5.4153 | 6.7157 | 0.80636 | 6.0094 | 7.4525 | 0.80636 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 1.4572 | 19 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 154.4302 | 7.0888 | 21.7851 | 154.4302 | 7.0888 | 21.7851 | 171.3739 | 7.8666 | 21.7851 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 1.4508 | 26 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 23.1241 | 9.7005 | 2.3838 | 23.1241 | 9.7005 | 2.3838 | 25.6612 | 10.7648 | 2.3838 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 1.4439 | 18 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 94.482 | 6.7157 | 14.0688 | 94.482 | 6.7157 | 14.0688 | 104.8483 | 7.4525 | 14.0688 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2027 | 474 | 474-22AE | Tier-1 | Non-HFTD---1 | 4--5 | 1.4235 | 22 | 100% | 6435.9834 | 99.89% | 0% | 0.1146% | 318.2162 | 0 | 0 | 318.2162 | 0 | 289.5724 | 8.2081 | 35.279 | 289.5724 | 8.2081 | 35.279 | 321.3436 | 9.1086 | 35.279 | 4.944% | 0.046635 | 0.044327 | 138007.5774 | 24328.5202 | 121.2373 | 113557.8199 | 138015.8115 | 0 | 0 | 138015.8115 | 0.01049%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 1.4146 | 22 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 52.3616 | 8.2081 | 6.3793 | 52.3616 | 8.2081 | 6.3793 | 58.1066 | 9.1086 | 6.3793 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2027 | 288 | 288-18 | Tier-1 | Non-HFTD---1 | 3--5 | 1.41 | 20 | 100% | 1717.8671 | 96.12% | 3.649% | 0.229% | 81.7367 | 0 | 0 | 81.7367 | 0 | 74.3793 | 7.4619 | 9.9679 | 74.3793 | 7.4619 | 9.9679 | 82.54 | 8.2806 | 9.9679 | 4.758% | 0.026137 | 0.024843 | 65724.9856 | 11143.2146 | 2230.6061 | 52351.1649 | 65857.7245 | 0 | 0 | 65857.7245 | 0.002695%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 1.3985 | 16 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 61.7773 | 5.9695 | 10.3488 | 61.7773 | 5.9695 | 10.3488 | 68.5553 | 6.6245 | 10.3488 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 1.3827 | 24 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 352.6402 | 8.9543 | 39.3824 | 352.6402 | 8.9543 | 39.3824 | 391.3311 | 9.9367 | 39.3824 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 1.3633 | 22 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 28.5327 | 8.2081 | 3.4762 | 28.5327 | 8.2081 | 3.4762 | 31.6632 | 9.1086 | 3.4762 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 1.3484 | 20 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 581.8498 | 7.4619 | 77.9762 | 581.8498 | 7.4619 | 77.9762 | 645.689 | 8.2806 | 77.9762 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 1.3358 | 21 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 91.6277 | 7.835 | 11.6947 | 91.6277 | 7.835 | 11.6947 | 101.6809 | 8.6946 | 11.6947 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 1.3358 | 23 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 63.4742 | 8.5812 | 7.3969 | 63.4742 | 8.5812 | 7.3969 | 70.4384 | 9.5227 | 7.3969 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 1.3275 | 20 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 312.0217 | 7.4619 | 41.8154 | 312.0217 | 7.4619 | 41.8154 | 346.256 | 8.2806 | 41.8154 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 1.3154 | 22 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 67.5098 | 8.2081 | 8.2248 | 67.5098 | 8.2081 | 8.2248 | 74.9169 | 9.1086 | 8.2248 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 1.3093 | 20 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 58.2657 | 7.4619 | 7.8084 | 58.2657 | 7.4619 | 7.8084 | 64.6584 | 8.2806 | 7.8084 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 1.3038 | 13 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 48.0153 | 4.8502 | 9.8996 | 48.0153 | 4.8502 | 9.8996 | 53.2834 | 5.3824 | 9.8996 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 1.3021 | 20 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 194.2367 | 7.4619 | 26.0305 | 194.2367 | 7.4619 | 26.0305 | 215.5479 | 8.2806 | 26.0305 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 1.2948 | 21 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 297.7228 | 7.835 | 37.9992 | 297.7228 | 7.835 | 37.9992 | 330.3883 | 8.6946 | 37.9992 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 1.2618 | 18 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 16.4392 | 6.7157 | 2.4479 | 16.4392 | 6.7157 | 2.4479 | 18.2429 | 7.4525 | 2.4479 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2027 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 1.2605 | 12 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 21.107 | 4.4771 | 4.7144 | 21.107 | 4.4771 | 4.7144 | 23.4228 | 4.9684 | 4.7144 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 1.2591 | 22 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 32.1257 | 8.2081 | 3.9139 | 32.1257 | 8.2081 | 3.9139 | 35.6504 | 9.1086 | 3.9139 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 1.257 | 18 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 132.7651 | 6.7157 | 19.7694 | 132.7651 | 6.7157 | 19.7694 | 147.3318 | 7.4525 | 19.7694 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2027 | 172 | 172-630R | Tier-1 | Non-HFTD---6 | 4--2 | 1.2534 | 10 | 100% | 66.3107 | 6.519% | 90.48% | 2.997% | 0.21398 | 0 | 0 | 0.21398 | 0 | 0.19472 | 3.7309 | 0.052191 | 0.19472 | 3.7309 | 0.052191 | 0.21609 | 4.1403 | 0.052191 | 0.3227% | 0.053137 | 0.050507 | 1247.9203 | 10.8427 | 1030.4852 | 206.5924 | 1308.6726 | 0 | 0 | 1308.6726 | 7.056e-06%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 1.2484 | 24 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 749.3113 | 8.9543 | 83.682 | 749.3113 | 8.9543 | 83.682 | 831.524 | 9.9367 | 83.682 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2027 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | 4--5 | 1.2229 | 18 | 100% | 2117.8574 | 97.53% | 2.33% | 0.1416% | 102.2432 | 0 | 0 | 102.2432 | 0 | 93.0399 | 6.7157 | 13.8541 | 93.0399 | 6.7157 | 13.8541 | 103.2481 | 7.4525 | 13.8541 | 4.828% | 0.067442 | 0.064104 | 31402.4615 | 4988.1224 | 677.5642 | 25736.7748 | 31442.8757 | 0 | 0 | 31442.8757 | 0.003372%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 1.1787 | 15 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 200.7686 | 5.5964 | 35.8745 | 200.7686 | 5.5964 | 35.8745 | 222.7965 | 6.2104 | 35.8745 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2027 | 206 | 206-974 | Tier-1 | Non-HFTD---1 | 4--5 | 1.1741 | 24 | 100% | 1943.6719 | 99.69% | 0% | 0.3117% | 95.9119 | 0 | 0 | 95.9119 | 0 | 87.2785 | 8.9543 | 9.7471 | 87.2785 | 8.9543 | 9.7471 | 96.8545 | 9.9367 | 9.7471 | 4.935% | 0.028958 | 0.027525 | 67119.4507 | 10907.8418 | 251.1395 | 55960.4695 | 67130.3452 | 0 | 0 | 67130.3452 | 0.003163%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 1.1689 | 13 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 228.9358 | 4.8502 | 47.2011 | 228.9358 | 4.8502 | 47.2011 | 254.0541 | 5.3824 | 47.2011 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 1.1689 | 22 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 194.367 | 8.2081 | 23.68 | 194.367 | 8.2081 | 23.68 | 215.6925 | 9.1086 | 23.68 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 1.1678 | 16 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 62.4087 | 5.9695 | 10.4546 | 62.4087 | 5.9695 | 10.4546 | 69.256 | 6.6245 | 10.4546 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 1.1572 | 12 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 34.8843 | 4.4771 | 7.7917 | 34.8843 | 4.4771 | 7.7917 | 38.7117 | 4.9684 | 7.7917 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 1.1071 | 22 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 169.5107 | 8.2081 | 20.6517 | 169.5107 | 8.2081 | 20.6517 | 188.109 | 9.1086 | 20.6517 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 1.0878 | 16 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 231.132 | 5.9695 | 38.7187 | 231.132 | 5.9695 | 38.7187 | 256.4912 | 6.6245 | 38.7187 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2027 | BN1 | CB BN1 | Tier-1 | Non-HFTD---4 | 4--4 | 1.0878 | 22 | 100% | 173.8031 | 96.37% | 0% | 3.629% | 8.291 | 0 | 0 | 8.291 | 0 | 7.5447 | 8.2081 | 0.91918 | 7.5447 | 8.2081 | 0.91918 | 8.3725 | 9.1086 | 0.91918 | 4.77% | 0.028851 | 0.027423 | 6024.1621 | 939.3966 | 90.5041 | 4994.2615 | 6035.548 | 0 | 0 | 6035.548 | 0.0002734%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 1.0864 | 17 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 19.0795 | 6.3426 | 3.0082 | 19.0795 | 6.3426 | 3.0082 | 21.1729 | 7.0385 | 3.0082 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 1.0771 | 18 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 249.9969 | 6.7157 | 37.2257 | 249.9969 | 6.7157 | 37.2257 | 277.426 | 7.4525 | 37.2257 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 1.0615 | 5 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 256.8046 | 1.8655 | 137.662 | 256.8046 | 1.8655 | 137.662 | 284.9806 | 2.0701 | 137.662 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 1.0168 | 17 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 113.0675 | 6.3426 | 17.8267 | 113.0675 | 6.3426 | 17.8267 | 125.473 | 7.0385 | 17.8267 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 1.0038 | 17 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 145.709 | 6.3426 | 22.9731 | 145.709 | 6.3426 | 22.9731 | 161.6959 | 7.0385 | 22.9731 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 0.9777 | 11 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.7945 | 4.104 | 2.8739 | 11.7945 | 4.104 | 2.8739 | 13.0885 | 4.5543 | 2.8739 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 0.97273 | 16 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 174.6571 | 5.9695 | 29.2582 | 174.6571 | 5.9695 | 29.2582 | 193.82 | 6.6245 | 29.2582 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 0.96847 | 13 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 322.8415 | 4.8502 | 66.5621 | 322.8415 | 4.8502 | 66.5621 | 358.263 | 5.3824 | 66.5621 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 0.96776 | 19 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 189.0401 | 7.0888 | 26.6675 | 189.0401 | 7.0888 | 26.6675 | 209.7812 | 7.8666 | 26.6675 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 0.96758 | 16 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 146.7475 | 5.9695 | 24.5828 | 146.7475 | 5.9695 | 24.5828 | 162.8483 | 6.6245 | 24.5828 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 0.94539 | 16 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 61.1671 | 5.9695 | 10.2466 | 61.1671 | 5.9695 | 10.2466 | 67.8782 | 6.6245 | 10.2466 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 0.93847 | 15 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 195.062 | 5.5964 | 34.8548 | 195.062 | 5.5964 | 34.8548 | 216.4638 | 6.2104 | 34.8548 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2027 | 66 | CB 66 | Tier-1 | Non-HFTD---1 | 4--5 | 0.93509 | 16 | 100% | 917.8674 | 93.46% | 5.958% | 0.5799% | 42.4641 | 0 | 0 | 42.4641 | 0 | 38.6418 | 5.9695 | 6.4732 | 38.6418 | 5.9695 | 6.4732 | 42.8815 | 6.6245 | 6.4732 | 4.626% | 0.036366 | 0.034566 | 25239.7123 | 4508.1978 | 1664.2037 | 19067.3107 | 25325.6439 | 0 | 0 | 25325.6439 | 0.0014%
2027 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | 3--5 | 0.93119 | 21 | 100% | 1424.1907 | 99.61% | 0% | 0.3928% | 70.2205 | 0 | 0 | 70.2205 | 0 | 63.8997 | 7.835 | 8.1557 | 63.8997 | 7.835 | 8.1557 | 70.9107 | 8.6946 | 8.1557 | 4.931% | 0.028304 | 0.026903 | 50317.6471 | 8145.1206 | 368.3302 | 41804.1963 | 50327.94 | 0 | 0 | 50327.94 | 0.002316%
2027 | 170 | 170-46 | Tier-1 | Non-HFTD---6 | 5--2 | 0.93066 | 12 | 100% | 63.3107 | 39.69% | 47.72% | 12.59% | 1.2437 | 0 | 0 | 1.2437 | 0 | 1.1318 | 4.4771 | 0.25279 | 1.1318 | 4.4771 | 0.25279 | 1.2559 | 4.9684 | 0.25279 | 1.964% | 0.099838 | 0.094896 | 634.1343 | 13.2723 | 434.6906 | 186.1714 | 654.0524 | 0 | 0 | 654.0524 | 4.101e-05%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 0.90864 | 10 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 16.745 | 3.7309 | 4.4881 | 16.745 | 3.7309 | 4.4881 | 18.5822 | 4.1403 | 4.4881 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 0.89089 | 13 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 133.7423 | 4.8502 | 27.5744 | 133.7423 | 4.8502 | 27.5744 | 148.4162 | 5.3824 | 27.5744 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 0.88609 | 15 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 233.193 | 5.5964 | 41.6683 | 233.193 | 5.5964 | 41.6683 | 258.7784 | 6.2104 | 41.6683 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 0.88361 | 16 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 90.5939 | 5.9695 | 15.1761 | 90.5939 | 5.9695 | 15.1761 | 100.5337 | 6.6245 | 15.1761 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 0.8829 | 16 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 22.5604 | 5.9695 | 3.7793 | 22.5604 | 5.9695 | 3.7793 | 25.0356 | 6.6245 | 3.7793 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2027 | 591 | CB 591 | Tier-1 | Non-HFTD---1 | 4--4 | 0.87881 | 15 | 100% | 1060.5472 | 90.24% | 9.188% | 0.5739% | 47.3724 | 0 | 0 | 47.3724 | 0 | 43.1082 | 5.5964 | 7.7028 | 43.1082 | 5.5964 | 7.7028 | 47.838 | 6.2104 | 7.7028 | 4.467% | 0.066615 | 0.063317 | 15920.6417 | 3763.87 | 1847.5145 | 10309.2572 | 16001.5783 | 0 | 0 | 16001.5783 | 0.001562%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 0.8568 | 7 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 92.1312 | 2.6117 | 35.2769 | 92.1312 | 2.6117 | 35.2769 | 102.2396 | 2.8982 | 35.2769 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 0.85023 | 11 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 290.2233 | 4.104 | 70.7165 | 290.2233 | 4.104 | 70.7165 | 322.0659 | 4.5543 | 70.7165 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 0.84757 | 14 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 30.6647 | 5.2233 | 5.8707 | 30.6647 | 5.2233 | 5.8707 | 34.0291 | 5.7964 | 5.8707 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 0.8394 | 13 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 20.502 | 4.8502 | 4.227 | 20.502 | 4.8502 | 4.227 | 22.7514 | 5.3824 | 4.227 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 0.83354 | 17 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 76.6258 | 6.3426 | 12.0811 | 76.6258 | 6.3426 | 12.0811 | 85.033 | 7.0385 | 12.0811 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 0.83088 | 20 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 193.5126 | 7.4619 | 25.9335 | 193.5126 | 7.4619 | 25.9335 | 214.7444 | 8.2806 | 25.9335 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 0.822 | 14 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 108.8052 | 5.2233 | 20.8306 | 108.8052 | 5.2233 | 20.8306 | 120.743 | 5.7964 | 20.8306 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 0.81969 | 14 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 225.6484 | 5.2233 | 43.2002 | 225.6484 | 5.2233 | 43.2002 | 250.406 | 5.7964 | 43.2002 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 0.81952 | 14 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 20.4346 | 5.2233 | 3.9122 | 20.4346 | 5.2233 | 3.9122 | 22.6767 | 5.7964 | 3.9122 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 0.81472 | 13 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 32.6575 | 4.8502 | 6.7332 | 32.6575 | 4.8502 | 6.7332 | 36.2406 | 5.3824 | 6.7332 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 0.8007 | 11 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 36.8484 | 4.104 | 8.9786 | 36.8484 | 4.104 | 8.9786 | 40.8913 | 4.5543 | 8.9786 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2027 | MV1 | CB MV1 | Tier-1 | Non-HFTD---4 | 3--4 | 0.78685 | 16 | 100% | 150.3384 | 97.79% | 0% | 2.21% | 7.2773 | 0 | 0 | 7.2773 | 0 | 6.6222 | 5.9695 | 1.1093 | 6.6222 | 5.9695 | 1.1093 | 7.3488 | 6.6245 | 1.1093 | 4.841% | 0.014765 | 0.014034 | 10182.3567 | 1618.5344 | 97.4794 | 8466.3429 | 10194.0779 | 0 | 0 | 10194.0779 | 0.00024%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 0.77975 | 14 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 181.9416 | 5.2233 | 34.8325 | 181.9416 | 5.2233 | 34.8325 | 201.9038 | 5.7964 | 34.8325 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 0.75773 | 9 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.9912 | 3.3578 | 2.6777 | 8.9912 | 3.3578 | 2.6777 | 9.9777 | 3.7263 | 2.6777 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 0.74744 | 15 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.2891 | 5.5964 | 2.5533 | 14.2891 | 5.5964 | 2.5533 | 15.8568 | 6.2104 | 2.5533 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2027 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | 5--4 | 0.68938 | 10 | 100% | 1005.6854 | 94.09% | 5.81% | 0.1042% | 46.8371 | 0 | 0 | 46.8371 | 0 | 42.6211 | 3.7309 | 11.4237 | 42.6211 | 3.7309 | 11.4237 | 47.2974 | 4.1403 | 11.4237 | 4.657% | 0.097832 | 0.09299 | 10279.6968 | 1573.4563 | 574.8933 | 8131.3471 | 10311.3601 | 0 | 0 | 10311.3601 | 0.001545%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 0.68654 | 12 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 152.4366 | 4.4771 | 34.0478 | 152.4366 | 4.4771 | 34.0478 | 169.1616 | 4.9684 | 34.0478 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 0.68512 | 8 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.6223 | 2.9848 | 1.5486 | 4.6223 | 2.9848 | 1.5486 | 5.1294 | 3.3122 | 1.5486 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 0.65867 | 14 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 162.9237 | 5.2233 | 31.1916 | 162.9237 | 5.2233 | 31.1916 | 180.7993 | 5.7964 | 31.1916 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 0.63221 | 9 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 35.1835 | 3.3578 | 10.478 | 35.1835 | 3.3578 | 10.478 | 39.0437 | 3.7263 | 10.478 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 0.63062 | 7 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.4291 | 2.6117 | 4.3762 | 11.4291 | 2.6117 | 4.3762 | 12.683 | 2.8982 | 4.3762 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 0.62174 | 9 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 9.5451 | 3.3578 | 2.8426 | 9.5451 | 3.3578 | 2.8426 | 10.5924 | 3.7263 | 2.8426 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2027 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 0.62121 | 10 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 28.6814 | 3.7309 | 7.6874 | 28.6814 | 3.7309 | 7.6874 | 31.8282 | 4.1403 | 7.6874 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 0.61091 | 12 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 22.8254 | 4.4771 | 5.0982 | 22.8254 | 4.4771 | 5.0982 | 25.3298 | 4.9684 | 5.0982 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 0.61038 | 14 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 112.6347 | 5.2233 | 21.5638 | 112.6347 | 5.2233 | 21.5638 | 124.9927 | 5.7964 | 21.5638 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2027 | 307 | CB 307 | Tier-1 | Non-HFTD---1 | 4--4 | 0.60043 | 8 | 100% | 601.8674 | 89.73% | 10.15% | 0.1197% | 26.7338 | 0 | 0 | 26.7338 | 0 | 24.3274 | 2.9848 | 8.1506 | 24.3274 | 2.9848 | 8.1506 | 26.9966 | 3.3122 | 8.1506 | 4.442% | 0.056404 | 0.053612 | 10670.688 | 1554.5631 | 980.4133 | 8135.7116 | 10727.7391 | 0 | 0 | 10727.7391 | 0.0008816%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 0.59919 | 7 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 173.8523 | 2.6117 | 66.5677 | 173.8523 | 2.6117 | 66.5677 | 192.927 | 2.8982 | 66.5677 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 0.59493 | 8 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 190.3065 | 2.9848 | 63.7595 | 190.3065 | 2.9848 | 63.7595 | 211.1864 | 3.3122 | 63.7595 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.58517 | 6 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 96.3527 | 2.2386 | 43.0422 | 96.3527 | 2.2386 | 43.0422 | 106.9243 | 2.4842 | 43.0422 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 0.56439 | 8 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.9193 | 2.9848 | 3.6583 | 10.9193 | 2.9848 | 3.6583 | 12.1173 | 3.3122 | 3.6583 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.55871 | 8 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 79.5582 | 2.9848 | 26.6548 | 79.5582 | 2.9848 | 26.6548 | 88.2871 | 3.3122 | 26.6548 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.55854 | 7 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 161.8413 | 2.6117 | 61.9687 | 161.8413 | 2.6117 | 61.9687 | 179.5981 | 2.8982 | 61.9687 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 0.55836 | 9 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 112.5405 | 3.3578 | 33.5157 | 112.5405 | 3.3578 | 33.5157 | 124.8882 | 3.7263 | 33.5157 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 0.54487 | 11 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 98.75 | 4.104 | 24.0617 | 98.75 | 4.104 | 24.0617 | 109.5846 | 4.5543 | 24.0617 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 0.53847 | 11 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 19.5259 | 4.104 | 4.7577 | 19.5259 | 4.104 | 4.7577 | 21.6682 | 4.5543 | 4.7577 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 0.53244 | 7 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 27.2363 | 2.6117 | 10.4287 | 27.2363 | 2.6117 | 10.4287 | 30.2246 | 2.8982 | 10.4287 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 0.52285 | 10 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 18.4733 | 3.7309 | 4.9514 | 18.4733 | 3.7309 | 4.9514 | 20.5002 | 4.1403 | 4.9514 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 0.51593 | 8 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.2041 | 2.9848 | 2.4136 | 7.2041 | 2.9848 | 2.4136 | 7.9946 | 3.3122 | 2.4136 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2027 | 455 | CB 455 | Tier-1 | Non-HFTD---1 | 3--5 | 0.50847 | 9 | 100% | 628.6508 | 99.14% | 0% | 0.8628% | 30.8497 | 0 | 0 | 30.8497 | 0 | 28.0728 | 3.3578 | 8.3604 | 28.0728 | 3.3578 | 8.3604 | 31.1529 | 3.7263 | 8.3604 | 4.907% | 0.025428 | 0.024169 | 24722.9716 | 4556.7235 | 179.5676 | 19986.6805 | 24734.0802 | 0 | 0 | 24734.0802 | 0.001017%
2027 | 171 | 171-704R | Tier-1 | Non-HFTD---6 | 4--2 | 0.50261 | 7 | 100% | 80.6143 | 61.35% | 34.31% | 4.34% | 2.4483 | 0 | 0 | 2.4483 | 0 | 2.2279 | 2.6117 | 0.85307 | 2.2279 | 2.6117 | 0.85307 | 2.4724 | 2.8982 | 0.85307 | 3.037% | 0.048088 | 0.045707 | 1676.4044 | 165.028 | 536.4334 | 974.9431 | 1710.1431 | 0 | 0 | 1710.1431 | 8.074e-05%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 0.47847 | 7 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 25.6219 | 2.6117 | 9.8106 | 25.6219 | 2.6117 | 9.8106 | 28.4331 | 2.8982 | 9.8106 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 0.46977 | 8 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 123.3195 | 2.9848 | 41.3164 | 123.3195 | 2.9848 | 41.3164 | 136.8498 | 3.3122 | 41.3164 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 0.46444 | 7 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.3274 | 2.6117 | 1.6569 | 4.3274 | 2.6117 | 1.6569 | 4.8022 | 2.8982 | 1.6569 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2027 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 0.45645 | 4 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 175.6505 | 1.4924 | 117.6984 | 175.6505 | 1.4924 | 117.6984 | 194.9225 | 1.6561 | 117.6984 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 0.43976 | 6 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 27.2109 | 2.2386 | 12.1555 | 27.2109 | 2.2386 | 12.1555 | 30.1964 | 2.4842 | 12.1555 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 0.4387 | 7 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 32.8858 | 2.6117 | 12.5919 | 32.8858 | 2.6117 | 12.5919 | 36.4939 | 2.8982 | 12.5919 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.43106 | 10 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 4.7854 | 3.7309 | 1.2826 | 4.7854 | 3.7309 | 1.2826 | 5.3104 | 4.1403 | 1.2826 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.42006 | 4 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.0061 | 1.4924 | 2.0143 | 3.0061 | 1.4924 | 2.0143 | 3.3359 | 1.6561 | 2.0143 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2027 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.4197 | 2 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 58.4684 | 0.74619 | 78.3561 | 58.4684 | 0.74619 | 78.3561 | 64.8835 | 0.82806 | 78.3561 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 0.41562 | 7 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 65.7597 | 2.6117 | 25.1793 | 65.7597 | 2.6117 | 25.1793 | 72.9747 | 2.8982 | 25.1793 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 0.41526 | 4 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 114.8046 | 1.4924 | 76.9273 | 114.8046 | 1.4924 | 76.9273 | 127.4007 | 1.6561 | 76.9273 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2027 | 412 | CB 412 | Tier-1 | Non-HFTD---1 | 4--5 | 0.41437 | 7 | 100% | 1311.9921 | 88.37% | 10.81% | 0.8215% | 57.392 | 0 | 0 | 57.392 | 0 | 52.226 | 2.6117 | 19.9972 | 52.226 | 2.6117 | 19.9972 | 57.9561 | 2.8982 | 19.9972 | 4.374% | 0.071433 | 0.067897 | 18366.6483 | 2615.4927 | 2100.6109 | 13650.5447 | 18477.8687 | 0 | 0 | 18477.8687 | 0.001893%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 0.41331 | 7 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 27.4714 | 2.6117 | 10.5187 | 27.4714 | 2.6117 | 10.5187 | 30.4855 | 2.8982 | 10.5187 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 0.40443 | 7 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 91.1498 | 2.6117 | 34.9011 | 91.1498 | 2.6117 | 34.9011 | 101.1506 | 2.8982 | 34.9011 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 0.39893 | 8 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 18.5991 | 2.9848 | 6.2314 | 18.5991 | 2.9848 | 6.2314 | 20.6397 | 3.3122 | 6.2314 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 0.39698 | 6 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 59.2108 | 2.2386 | 26.4503 | 59.2108 | 2.2386 | 26.4503 | 65.7073 | 2.4842 | 26.4503 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 0.38686 | 7 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 57.4893 | 2.6117 | 22.0126 | 57.4893 | 2.6117 | 22.0126 | 63.7969 | 2.8982 | 22.0126 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 0.38437 | 5 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 96.3058 | 1.8655 | 51.6255 | 96.3058 | 1.8655 | 51.6255 | 106.8723 | 2.0701 | 51.6255 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 0.3826 | 8 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 139.6922 | 2.9848 | 46.8019 | 139.6922 | 2.9848 | 46.8019 | 155.0189 | 3.3122 | 46.8019 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 0.37585 | 7 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 87.1243 | 2.6117 | 33.3597 | 87.1243 | 2.6117 | 33.3597 | 96.6834 | 2.8982 | 33.3597 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 0.35756 | 6 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 23.951 | 2.2386 | 10.6993 | 23.951 | 2.2386 | 10.6993 | 26.5789 | 2.4842 | 10.6993 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 0.35561 | 10 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.248 | 3.7309 | 0.87057 | 3.248 | 3.7309 | 0.87057 | 3.6044 | 4.1403 | 0.87057 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 0.35525 | 2 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 232.1001 | 0.74619 | 311.0474 | 232.1001 | 0.74619 | 311.0474 | 257.5656 | 0.82806 | 311.0474 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2027 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 0.34957 | 9 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 89.5674 | 3.3578 | 26.674 | 89.5674 | 3.3578 | 26.674 | 99.3945 | 3.7263 | 26.674 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2027 | 206 | 206-963F | Tier-1 | Non-HFTD---1 | 3--5 | 0.34283 | 6 | 100% | 308.0085 | 98.9% | 0% | 1.099% | 15.0788 | 0 | 0 | 15.0788 | 0 | 13.7215 | 2.2386 | 6.1296 | 13.7215 | 2.2386 | 6.1296 | 15.227 | 2.4842 | 6.1296 | 4.896% | 0.014856 | 0.014121 | 20732.6556 | 3229.8813 | 785.6991 | 16717.0751 | 20744.5251 | 0 | 0 | 20744.5251 | 0.0004972%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 0.33945 | 7 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.1258 | 2.6117 | 3.8771 | 10.1258 | 2.6117 | 3.8771 | 11.2367 | 2.8982 | 3.8771 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2027 | 553 | 553-27R | Tier-1 | Non-HFTD---1 | 4--4 | 0.33928 | 7 | 100% | 504.2652 | 97.83% | 0% | 2.166% | 24.4204 | 0 | 0 | 24.4204 | 0 | 22.2223 | 2.6117 | 8.5089 | 22.2223 | 2.6117 | 8.5089 | 24.6604 | 2.8982 | 8.5089 | 4.843% | 0.054721 | 0.052013 | 9215.1363 | 1913.347 | 158.4888 | 7143.3005 | 9225.5318 | 0 | 0 | 9225.5318 | 0.0008053%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.33644 | 5 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 62.197 | 1.8655 | 33.3411 | 62.197 | 1.8655 | 33.3411 | 69.0211 | 2.0701 | 33.3411 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2027 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | 3--5 | 0.33608 | 7 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 13.1668 | 0 | 0 | 13.1668 | 0 | 11.9816 | 2.6117 | 4.5877 | 11.9816 | 2.6117 | 4.5877 | 13.2962 | 2.8982 | 4.5877 | 4.021% | 0.015736 | 0.014957 | 20808.6476 | 4091.2697 | 3467.4094 | 13249.9684 | 21012.0249 | 0 | 0 | 21012.0249 | 0.0004342%
2027 | 471 | CB 471 | Tier-1 | Non-HFTD---1 | 4--5 | 0.33537 | 7 | 100% | 3808.7328 | 99.83% | 0% | 0.1692% | 188.2133 | 0 | 0 | 188.2133 | 0 | 171.2715 | 2.6117 | 65.5795 | 171.2715 | 2.6117 | 65.5795 | 190.0631 | 2.8982 | 65.5795 | 4.942% | 0.030567 | 0.029054 | 124601.1385 | 20145.8945 | 297.3105 | 104157.9336 | 124612.117 | 0 | 0 | 124612.117 | 0.006207%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.33288 | 7 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 55.83 | 2.6117 | 21.3772 | 55.83 | 2.6117 | 21.3772 | 61.9555 | 2.8982 | 21.3772 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2027 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.32987 | 5 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 94.6789 | 1.8655 | 50.7533 | 94.6789 | 1.8655 | 50.7533 | 105.0668 | 2.0701 | 50.7533 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 0.32365 | 5 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.8571 | 1.8655 | 0.9955 | 1.8571 | 1.8655 | 0.9955 | 2.0608 | 2.0701 | 0.9955 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2027 | 170 | 170-3R | Tier-1 | Non-HFTD---3 | 4--3 | 0.32312 | 5 | 100% | 134.6076 | 71.34% | 24.69% | 3.975% | 4.7533 | 0 | 0 | 4.7533 | 0 | 4.3254 | 1.8655 | 2.3187 | 4.3254 | 1.8655 | 2.3187 | 4.8 | 2.0701 | 2.3187 | 3.531% | 0.059016 | 0.056095 | 2280.8503 | 250.0057 | 616.1021 | 1414.7425 | 2314.8955 | 0 | 0 | 2314.8955 | 0.0001567%
2027 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 0.32063 | 5 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 31.033 | 1.8655 | 16.6355 | 31.033 | 1.8655 | 16.6355 | 34.4379 | 2.0701 | 16.6355 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 0.3114 | 8 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 87.1533 | 2.9848 | 29.1995 | 87.1533 | 2.9848 | 29.1995 | 96.7155 | 3.3122 | 29.1995 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 0.30767 | 4 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 218.5784 | 1.4924 | 146.4632 | 218.5784 | 1.4924 | 146.4632 | 242.5603 | 1.6561 | 146.4632 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 0.3027 | 4 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.2129 | 1.4924 | 9.5237 | 14.2129 | 1.4924 | 9.5237 | 15.7723 | 1.6561 | 9.5237 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 0.30253 | 4 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 268.9826 | 1.4924 | 180.2376 | 268.9826 | 1.4924 | 180.2376 | 298.4947 | 1.6561 | 180.2376 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 0.30111 | 4 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 52.7183 | 1.4924 | 35.325 | 52.7183 | 1.4924 | 35.325 | 58.5024 | 1.6561 | 35.325 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2027 | 387 | CB 387 | Tier-1 | Non-HFTD---2 | 4--4 | 0.30022 | 6 | 100% | 522.65 | 70.14% | 28.94% | 0.9137% | 18.1467 | 0 | 0 | 18.1467 | 0 | 16.5133 | 2.2386 | 7.3767 | 16.5133 | 2.2386 | 7.3767 | 18.3251 | 2.4842 | 7.3767 | 3.472% | 0.067633 | 0.064286 | 7727.6908 | 947.907 | 2193.816 | 4585.9679 | 7847.8494 | 0 | 0 | 7847.8494 | 0.0005984%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 0.29276 | 6 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 33.1036 | 2.2386 | 14.7879 | 33.1036 | 2.2386 | 14.7879 | 36.7357 | 2.4842 | 14.7879 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 0.29081 | 5 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.2738 | 1.8655 | 1.7549 | 3.2738 | 1.8655 | 1.7549 | 3.633 | 2.0701 | 1.7549 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 0.283 | 6 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.0215 | 2.2386 | 5.3702 | 12.0215 | 2.2386 | 5.3702 | 13.3405 | 2.4842 | 5.3702 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 0.26649 | 3 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 26.069 | 1.1193 | 23.2908 | 26.069 | 1.1193 | 23.2908 | 28.9292 | 1.2421 | 23.2908 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 0.26151 | 5 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 4.9928 | 1.8655 | 2.6764 | 4.9928 | 1.8655 | 2.6764 | 5.5406 | 2.0701 | 2.6764 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2027 | 172 | 172-615R | Tier-1 | Non-HFTD---6 | 4--2 | 0.25938 | 5 | 100% | 65.0211 | 31.38% | 63.15% | 5.469% | 1.0101 | 0 | 0 | 1.0101 | 0 | 0.91915 | 1.8655 | 0.49271 | 0.91915 | 1.8655 | 0.49271 | 1.02 | 2.0701 | 0.49271 | 1.553% | 0.053579 | 0.050927 | 1213.547 | 17.4537 | 970.9978 | 225.0954 | 1256.9124 | 0 | 0 | 1256.9124 | 3.331e-05%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.25477 | 2 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 7.6802 | 0.74619 | 10.2925 | 7.6802 | 0.74619 | 10.2925 | 8.5228 | 0.82806 | 10.2925 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.2521 | 4 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.6527 | 1.4924 | 3.1176 | 4.6527 | 1.4924 | 3.1176 | 5.1631 | 1.6561 | 3.1176 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2027 | 410 | 410-50R | Tier-1 | Non-HFTD---1 | 4--5 | 0.24749 | 4 | 100% | 1314.3326 | 99.38% | 0% | 0.6151% | 64.6593 | 0 | 0 | 64.6593 | 0 | 58.8391 | 1.4924 | 39.4264 | 58.8391 | 1.4924 | 39.4264 | 65.2948 | 1.6561 | 39.4264 | 4.92% | 0.044038 | 0.041858 | 29845.69 | 7721.7282 | 133.8501 | 21990.1116 | 29855.2499 | 0 | 0 | 29855.2499 | 0.002132%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.24252 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 5.1675 | 1.8655 | 2.7701 | 5.1675 | 1.8655 | 2.7701 | 5.7345 | 2.0701 | 2.7701 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.2379 | 4 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 31.8229 | 1.4924 | 21.3236 | 31.8229 | 1.4924 | 21.3236 | 35.3145 | 1.6561 | 21.3236 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2027 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | 4--5 | 0.23648 | 3 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 37.535 | 0 | 0 | 37.535 | 0 | 34.1563 | 1.1193 | 30.5162 | 34.1563 | 1.1193 | 30.5162 | 37.9039 | 1.2421 | 30.5162 | 3.124% | 0.042337 | 0.040241 | 28377.3086 | 3599.9822 | 10019.8495 | 14757.4769 | 28922.3867 | 0 | 0 | 28922.3867 | 0.001238%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.23417 | 5 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 17.4178 | 1.8655 | 9.3369 | 17.4178 | 1.8655 | 9.3369 | 19.3289 | 2.0701 | 9.3369 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2027 | 306 | CB 306 | Tier-1 | Non-HFTD---1 | 4--4 | 0.234 | 6 | 100% | 737.4997 | 97.09% | 2.802% | 0.1119% | 35.4424 | 0 | 0 | 35.4424 | 0 | 32.2521 | 2.2386 | 14.4075 | 32.2521 | 2.2386 | 14.4075 | 35.7908 | 2.4842 | 14.4075 | 4.806% | 0.057753 | 0.054894 | 12769.9388 | 2020.535 | 320.1958 | 10429.208 | 12789.3181 | 0 | 0 | 12789.3181 | 0.001169%
2027 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 0.23062 | 5 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 22.0224 | 1.8655 | 11.8053 | 22.0224 | 1.8655 | 11.8053 | 24.4386 | 2.0701 | 11.8053 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2027 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 0.22654 | 4 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 17.3075 | 1.4924 | 11.5973 | 17.3075 | 1.4924 | 11.5973 | 19.2065 | 1.6561 | 11.5973 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2027 | 1007 | CB 1007 | Tier-1 | Non-HFTD---4 | 1--5 | 0.22459 | 1 | 100% | 183.252 | 99.8% | 0% | 0.2013% | 9.0527 | 0 | 0 | 9.0527 | 0 | 8.2378 | 0.37309 | 22.0798 | 8.2378 | 0.37309 | 22.0798 | 9.1417 | 0.41403 | 22.0798 | 4.94% | 0.0023706 | 0.0022533 | 77301.9362 | 12237.1432 | 2369.9057 | 62694.8873 | 77310.0415 | 0 | 0 | 77310.0415 | 0.0002985%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.22086 | 3 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 13.5232 | 1.1193 | 12.082 | 13.5232 | 1.1193 | 12.082 | 15.0069 | 1.2421 | 12.082 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.21127 | 4 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.5839 | 1.4924 | 3.7416 | 5.5839 | 1.4924 | 3.7416 | 6.1965 | 1.6561 | 3.7416 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.20097 | 3 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 26.2533 | 1.1193 | 23.4554 | 26.2533 | 1.1193 | 23.4554 | 29.1337 | 1.2421 | 23.4554 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2027 | HW1 | CB HW1 | Tier-1 | Non-HFTD---4 | 1--5 | 0.2008 | 5 | 100% | 122.4382 | 99.35% | 0% | 0.6452% | 6.0216 | 0 | 0 | 6.0216 | 0 | 5.4796 | 1.8655 | 2.9374 | 5.4796 | 1.8655 | 2.9374 | 6.0808 | 2.0701 | 2.9374 | 4.918% | 0.0031138 | 0.0029597 | 39321.1613 | 6393.1555 | 36.0556 | 32891.9501 | 39334.373 | 0 | 0 | 39334.373 | 0.0001986%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 0.19973 | 5 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 48.5811 | 1.8655 | 26.0422 | 48.5811 | 1.8655 | 26.0422 | 53.9113 | 2.0701 | 26.0422 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.19192 | 2 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 5.1466 | 0.74619 | 6.8971 | 5.1466 | 0.74619 | 6.8971 | 5.7112 | 0.82806 | 6.8971 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2027 | 172 | 172-569R | Tier-1 | Non-HFTD---3 | 5--2 | 0.19139 | 2 | 100% | 174.5806 | 70.22% | 23.82% | 5.957% | 6.0684 | 0 | 0 | 6.0684 | 0 | 5.5221 | 0.74619 | 7.4005 | 5.5221 | 0.74619 | 7.4005 | 6.128 | 0.82806 | 7.4005 | 3.476% | 0.12865 | 0.12229 | 1356.9713 | 139.4703 | 376.51 | 840.9911 | 1378.015 | 0 | 0 | 1378.015 | 0.0002001%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.18961 | 1 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 9.5688 | 0.37309 | 25.6471 | 9.5688 | 0.37309 | 25.6471 | 10.6186 | 0.41403 | 25.6471 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.18908 | 4 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 37.8035 | 1.4924 | 25.331 | 37.8035 | 1.4924 | 25.331 | 41.9512 | 1.6561 | 25.331 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.18748 | 3 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 4.8571 | 1.1193 | 4.3395 | 4.8571 | 1.1193 | 4.3395 | 5.39 | 1.2421 | 4.3395 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 0.17772 | 3 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 179.8549 | 1.1193 | 160.6876 | 179.8549 | 1.1193 | 160.6876 | 199.5882 | 1.2421 | 160.6876 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2027 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.17736 | 2 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 1.0258 | 0.74619 | 1.3747 | 1.0258 | 0.74619 | 1.3747 | 1.1383 | 0.82806 | 1.3747 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 0.17683 | 2 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 285.8939 | 0.74619 | 383.1388 | 285.8939 | 0.74619 | 383.1388 | 317.2615 | 0.82806 | 383.1388 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 0.16671 | 2 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 71.3855 | 0.74619 | 95.6669 | 71.3855 | 0.74619 | 95.6669 | 79.2178 | 0.82806 | 95.6669 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.16405 | 2 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.2134 | 0.74619 | 2.9662 | 2.2134 | 0.74619 | 2.9662 | 2.4562 | 0.82806 | 2.9662 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 0.16103 | 3 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 127.1099 | 1.1193 | 113.5636 | 127.1099 | 1.1193 | 113.5636 | 141.0561 | 1.2421 | 113.5636 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2027 | 1039 | CB 1039 | Tier-1 | Non-HFTD---6 | 4--3 | 0.15694 | 3 | 100% | 89.254 | 66.42% | 32.73% | 0.8498% | 2.9347 | 0 | 0 | 2.9347 | 0 | 2.6705 | 1.1193 | 2.3859 | 2.6705 | 1.1193 | 2.3859 | 2.9635 | 1.2421 | 2.3859 | 3.288% | 0.047241 | 0.044903 | 1889.3167 | 183.5723 | 702.9111 | 1002.8332 | 1922.3524 | 0 | 0 | 1922.3524 | 9.677e-05%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.15446 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.2588 | 0.74619 | 15.0884 | 11.2588 | 0.74619 | 15.0884 | 12.4941 | 0.82806 | 15.0884 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2027 | 856 | 856-1141R | Tier-1 | Non-HFTD---7 | 2--3 | 0.15197 | 3 | 100% | 34.972 | 93.55% | 0% | 6.449% | 1.6195 | 0 | 0 | 1.6195 | 0 | 1.4737 | 1.1193 | 1.3166 | 1.4737 | 1.1193 | 1.3166 | 1.6354 | 1.2421 | 1.3166 | 4.631% | 0.0095222 | 0.0090509 | 3672.677 | 493.2945 | 440.7828 | 2738.5997 | 3685.0115 | 0 | 0 | 3685.0115 | 5.34e-05%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.14789 | 1 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.9588 | 0.37309 | 15.9713 | 5.9588 | 0.37309 | 15.9713 | 6.6126 | 0.41403 | 15.9713 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 0.14629 | 3 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 183.4459 | 1.1193 | 163.8959 | 183.4459 | 1.1193 | 163.8959 | 203.5731 | 1.2421 | 163.8959 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2027 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 0.14008 | 3 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 32.3544 | 1.1193 | 28.9063 | 32.3544 | 1.1193 | 28.9063 | 35.9042 | 1.2421 | 28.9063 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.14008 | 3 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 60.3628 | 1.1193 | 53.9299 | 60.3628 | 1.1193 | 53.9299 | 66.9857 | 1.2421 | 53.9299 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.11345 | 2 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 31.0484 | 0.74619 | 41.6093 | 31.0484 | 0.74619 | 41.6093 | 34.4549 | 0.82806 | 41.6093 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.11025 | 1 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.165 | 0.37309 | 35.286 | 13.165 | 0.37309 | 35.286 | 14.6095 | 0.41403 | 35.286 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2027 | 1221 | 1221-2095F | Tier-1 | Non-HFTD---9 | 1--4 | 0.10883 | 2 | 100% | 19.6421 | 98.74% | 0% | 1.261% | 0.96002 | 0 | 0 | 0.96002 | 0 | 0.87361 | 0.74619 | 1.1708 | 0.87361 | 0.74619 | 1.1708 | 0.96946 | 0.82806 | 1.1708 | 4.888% | 0.0016714 | 0.0015887 | 11751.8616 | 4301.6259 | 14.6524 | 7435.5833 | 11759.5801 | 0 | 0 | 11759.5801 | 3.166e-05%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.10848 | 1 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 14.5393 | 0.37309 | 38.9695 | 14.5393 | 0.37309 | 38.9695 | 16.1345 | 0.41403 | 38.9695 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2027 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.10741 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 6.012 | 0.37309 | 16.114 | 6.012 | 0.37309 | 16.114 | 6.6717 | 0.41403 | 16.114 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2027 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.1067 | 2 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.5825 | 0.74619 | 7.4813 | 5.5825 | 0.74619 | 7.4813 | 6.195 | 0.82806 | 7.4813 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.1035 | 2 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 17.7496 | 0.74619 | 23.7871 | 17.7496 | 0.74619 | 23.7871 | 19.6971 | 0.82806 | 23.7871 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.097469 | 2 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.4327 | 0.74619 | 15.3214 | 11.4327 | 0.74619 | 15.3214 | 12.687 | 0.82806 | 15.3214 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2027 | 93 | 93-10R | Tier-1 | Non-HFTD---2 | 4--4 | 0.095516 | 3 | 100% | 302.3321 | 90.71% | 7.303% | 1.988% | 13.575 | 0 | 0 | 13.575 | 0 | 12.353 | 1.1193 | 11.0365 | 12.353 | 1.1193 | 11.0365 | 13.7084 | 1.2421 | 11.0365 | 4.49% | 0.035815 | 0.034042 | 8441.494 | 1852.3748 | 638.1878 | 5950.9314 | 8482.34 | 0 | 0 | 8482.34 | 0.0004477%
2027 | 901 | 901-1124 | Tier-1 | Non-HFTD---1 | 2--5 | 0.094983 | 1 | 100% | 225.4814 | 99.29% | 0% | 0.709% | 11.0822 | 0 | 0 | 11.0822 | 0 | 10.0846 | 0.37309 | 27.0297 | 10.0846 | 0.37309 | 27.0297 | 11.1911 | 0.41403 | 27.0297 | 4.915% | 0.0087544 | 0.0083211 | 25756.3496 | 4178.6743 | 36.5656 | 21541.1098 | 25765.8596 | 0 | 0 | 25765.8596 | 0.0003654%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.09161 | 2 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 3.9274 | 0.74619 | 5.2633 | 3.9274 | 0.74619 | 5.2633 | 4.3584 | 0.82806 | 5.2633 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2027 | 299 | 299-1153F | Tier-1 | Non-HFTD---11 | 1--4 | 0.090722 | 2 | 100% | 12.6944 | 96.89% | 0% | 3.107% | 0.60885 | 0 | 0 | 0.60885 | 0 | 0.55404 | 0.74619 | 0.7425 | 0.55404 | 0.74619 | 0.7425 | 0.61483 | 0.82806 | 0.7425 | 4.796% | 0.0013374 | 0.0012712 | 9491.8205 | 1360.071 | 891.9808 | 7239.7687 | 9507.1772 | 0 | 0 | 9507.1772 | 2.008e-05%
2027 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 0.089302 | 2 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 256.5422 | 0.74619 | 343.8033 | 256.5422 | 0.74619 | 343.8033 | 284.6894 | 0.82806 | 343.8033 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2027 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.088947 | 1 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 6.0257 | 0.37309 | 16.1505 | 6.0257 | 0.37309 | 16.1505 | 6.6868 | 0.41403 | 16.1505 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 0.080425 | 1 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 14.7896 | 0.37309 | 39.6404 | 14.7896 | 0.37309 | 39.6404 | 16.4123 | 0.41403 | 39.6404 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 0.08007 | 2 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 17.4173 | 0.74619 | 23.3417 | 17.4173 | 0.74619 | 23.3417 | 19.3283 | 0.82806 | 23.3417 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 0.079715 | 1 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 99.735 | 0.37309 | 267.3183 | 99.735 | 0.37309 | 267.3183 | 110.6776 | 0.41403 | 267.3183 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2027 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.077762 | 2 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.5118 | 0.74619 | 4.7063 | 3.5118 | 0.74619 | 4.7063 | 3.8971 | 0.82806 | 4.7063 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.071015 | 2 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 3.8596 | 0.74619 | 5.1724 | 3.8596 | 0.74619 | 5.1724 | 4.283 | 0.82806 | 5.1724 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2027 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.069773 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.4339 | 0.37309 | 6.5237 | 2.4339 | 0.37309 | 6.5237 | 2.701 | 0.41403 | 6.5237 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 0.068352 | 2 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 24.5074 | 0.74619 | 32.8435 | 24.5074 | 0.74619 | 32.8435 | 27.1963 | 0.82806 | 32.8435 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.068175 | 1 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 6.8075 | 0.37309 | 18.2461 | 6.8075 | 0.37309 | 18.2461 | 7.5544 | 0.41403 | 18.2461 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.061606 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 65.4805 | 0.37309 | 175.5064 | 65.4805 | 0.37309 | 175.5064 | 72.6648 | 0.41403 | 175.5064 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2027 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.060718 | 1 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 15.0487 | 0.37309 | 40.3348 | 15.0487 | 0.37309 | 40.3348 | 16.6998 | 0.41403 | 40.3348 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2027 | 474 | 474-29 | Tier-1 | Non-HFTD---1 | 2--5 | 0.059298 | 2 | 100% | 1510.7302 | 99.89% | 0% | 0.1058% | 74.702 | 0 | 0 | 74.702 | 0 | 67.9778 | 0.74619 | 91.1001 | 67.9778 | 0.74619 | 91.1001 | 75.4362 | 0.82806 | 91.1001 | 4.945% | 0.010755 | 0.010222 | 140472.931 | 24566.9965 | 189.9323 | 115716.0023 | 140480.6687 | 0 | 0 | 140480.6687 | 0.002463%
2027 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.057878 | 1 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.3026 | 0.37309 | 30.2942 | 11.3026 | 0.37309 | 30.2942 | 12.5427 | 0.41403 | 30.2942 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2027 | 171 | 171-34 | Tier-1 | Non-HFTD---6 | 4--3 | 0.056812 | 1 | 100% | 81.2035 | 44.67% | 51.64% | 3.687% | 1.7955 | 0 | 0 | 1.7955 | 0 | 1.6339 | 0.37309 | 4.3793 | 1.6339 | 0.37309 | 4.3793 | 1.8132 | 0.41403 | 4.3793 | 2.211% | 0.043687 | 0.041525 | 1858.7395 | 129.5883 | 851.5868 | 877.5644 | 1912.2988 | 0 | 0 | 1912.2988 | 5.921e-05%
2027 | 1001 | 1001-1232F | Tier-1 | Non-HFTD---15 | 1--4 | 0.056812 | 1 | 100% | 3.7082 | 98.25% | 0% | 1.746% | 0.18035 | 0 | 0 | 0.18035 | 0 | 0.16412 | 0.37309 | 0.43988 | 0.16412 | 0.37309 | 0.43988 | 0.18212 | 0.41403 | 0.43988 | 4.864% | 0.0002536 | 0.00024105 | 14622.1214 | 2186.2186 | 960.6365 | 11475.2662 | 14635.4188 | 0 | 0 | 14635.4188 | 5.947e-06%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.056635 | 1 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.2263 | 0.37309 | 14.008 | 5.2263 | 0.37309 | 14.008 | 5.7997 | 0.41403 | 14.008 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.053439 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.647 | 0.37309 | 9.7751 | 3.647 | 0.37309 | 9.7751 | 4.0472 | 0.41403 | 9.7751 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2027 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.052906 | 1 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.1836 | 0.37309 | 8.5328 | 3.1836 | 0.37309 | 8.5328 | 3.5329 | 0.41403 | 8.5328 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.052551 | 1 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.325 | 0.37309 | 19.6331 | 7.325 | 0.37309 | 19.6331 | 8.1287 | 0.41403 | 19.6331 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.052196 | 1 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.069276 | 0.37309 | 0.18568 | 0.069276 | 0.37309 | 0.18568 | 0.076876 | 0.41403 | 0.18568 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2027 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.051664 | 1 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.64817 | 0.37309 | 1.7373 | 0.64817 | 0.37309 | 1.7373 | 0.71928 | 0.41403 | 1.7373 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2027 | 591 | 591-39AE | Tier-1 | Non-HFTD---1 | 4--4 | 0.051309 | 2 | 100% | 863.6817 | 30.54% | 68.77% | 0.684% | 13.0582 | 0 | 0 | 13.0582 | 0 | 11.8828 | 0.74619 | 15.9247 | 11.8828 | 0.74619 | 15.9247 | 13.1866 | 0.82806 | 15.9247 | 1.512% | 0.061092 | 0.058068 | 14137.3023 | 873.1637 | 8965.9062 | 4298.2324 | 14648.6655 | 0 | 0 | 14648.6655 | 0.0004306%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.050598 | 1 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 29.2851 | 0.37309 | 78.4924 | 29.2851 | 0.37309 | 78.4924 | 32.4982 | 0.41403 | 78.4924 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2027 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.050421 | 1 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.084645 | 0.37309 | 0.22687 | 0.084645 | 0.37309 | 0.22687 | 0.093932 | 0.41403 | 0.22687 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2027 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.049711 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 0.97959 | 0.37309 | 2.6256 | 0.97959 | 0.37309 | 2.6256 | 1.0871 | 0.41403 | 2.6256 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2027 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.049001 | 1 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.10923 | 0.37309 | 0.29277 | 0.10923 | 0.37309 | 0.29277 | 0.12122 | 0.41403 | 0.29277 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2027 | 472 | CB 472 | Tier-1 | Non-HFTD---6 | 3--3 | 0.04687 | 1 | 100% | 66.0921 | 92.91% | 0% | 7.09% | 3.0396 | 0 | 0 | 3.0396 | 0 | 2.766 | 0.37309 | 7.4137 | 2.766 | 0.37309 | 7.4137 | 3.0695 | 0.41403 | 7.4137 | 4.599% | 0.020578 | 0.019559 | 3211.8146 | 441.0584 | 309.4932 | 2461.263 | 3223.674 | 0 | 0 | 3223.674 | 0.0001002%
2027 | 859 | 859-1064 | Tier-1 | Non-HFTD---7 | 2--3 | 0.045272 | 2 | 100% | 40.2522 | 93.55% | 0% | 6.452% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.6962 | 0.74619 | 2.2731 | 1.6962 | 0.74619 | 2.2731 | 1.8823 | 0.82806 | 2.2731 | 4.631% | 0.011569 | 0.010996 | 3479.3123 | 521.49 | 92.9503 | 2864.872 | 3491.0022 | 0 | 0 | 3491.0022 | 6.147e-05%
2027 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.042964 | 1 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 13.9722 | 0.37309 | 37.4496 | 13.9722 | 0.37309 | 37.4496 | 15.5052 | 0.41403 | 37.4496 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.041366 | 1 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.091 | 0.37309 | 19.006 | 7.091 | 0.37309 | 19.006 | 7.869 | 0.41403 | 19.006 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.040479 | 1 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 35.3002 | 0.37309 | 94.6147 | 35.3002 | 0.37309 | 94.6147 | 39.1733 | 0.41403 | 94.6147 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2027 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.038881 | 1 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 8.6384 | 0.37309 | 23.1533 | 8.6384 | 0.37309 | 23.1533 | 9.5861 | 0.41403 | 23.1533 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 0.038703 | 1 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 25.4406 | 0.37309 | 68.1881 | 25.4406 | 0.37309 | 68.1881 | 28.2319 | 0.41403 | 68.1881 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2027 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.037283 | 1 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.54074 | 0.37309 | 1.4493 | 0.54074 | 0.37309 | 1.4493 | 0.60007 | 0.41403 | 1.4493 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2027 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.036218 | 1 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.74762 | 0.37309 | 2.0038 | 0.74762 | 0.37309 | 2.0038 | 0.82964 | 0.41403 | 2.0038 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2027 | 245 | CB 245 | Tier-1 | Non-HFTD---2 | 4--4 | 0.03462 | 1 | 100% | 248.3247 | 30.26% | 68.14% | 1.595% | 3.7197 | 0 | 0 | 3.7197 | 0 | 3.3848 | 0.37309 | 9.0723 | 3.3848 | 0.37309 | 9.0723 | 3.7562 | 0.41403 | 9.0723 | 1.498% | 0.044637 | 0.042428 | 5563.1534 | 331.3651 | 3704.159 | 1527.6293 | 5765.2004 | 0 | 0 | 5765.2004 | 0.0001227%
2027 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | 2--4 | 0.034265 | 1 | 100% | 92.0555 | 97.82% | 0% | 2.183% | 4.4573 | 0 | 0 | 4.4573 | 0 | 4.0561 | 0.37309 | 10.8714 | 4.0561 | 0.37309 | 10.8714 | 4.5011 | 0.41403 | 10.8714 | 4.842% | 0.0089936 | 0.0085484 | 10235.6661 | 2125.5614 | 107.0953 | 8003.0094 | 10247.3023 | 0 | 0 | 10247.3023 | 0.000147%
2027 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.032134 | 1 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.1319 | 0.37309 | 3.0337 | 1.1319 | 0.37309 | 3.0337 | 1.2561 | 0.41403 | 3.0337 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.032134 | 1 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.6215 | 0.37309 | 7.0263 | 2.6215 | 0.37309 | 7.0263 | 2.9091 | 0.41403 | 7.0263 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2027 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.032134 | 1 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.69648 | 0.37309 | 1.8668 | 0.69648 | 0.37309 | 1.8668 | 0.7729 | 0.41403 | 1.8668 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.031957 | 1 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.093 | 0.37309 | 13.6506 | 5.093 | 0.37309 | 13.6506 | 5.6517 | 0.41403 | 13.6506 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2027 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.031424 | 1 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.51379 | 0.37309 | 1.3771 | 0.51379 | 0.37309 | 1.3771 | 0.57016 | 0.41403 | 1.3771 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2027 | 96 | 96-1041F | Tier-1 | Non-HFTD---13 | 2--2 | 0.031424 | 1 | 100% | 5.6175 | 97.14% | 1.791% | 1.068% | 0.27012 | 0 | 0 | 0.27012 | 0 | 0.2458 | 0.37309 | 0.65882 | 0.2458 | 0.37309 | 0.65882 | 0.27277 | 0.41403 | 0.65882 | 4.808% | 0.005633 | 0.0053542 | 997.2446 | 127.463 | 205.2994 | 664.4822 | 998.7294 | 0 | 0 | 998.7294 | 8.907e-06%
2027 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.031247 | 1 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.80006 | 0.37309 | 2.1444 | 0.80006 | 0.37309 | 2.1444 | 0.88784 | 0.41403 | 2.1444 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2027 | 205 | 205-369R | Tier-1 | Non-HFTD---2 | 4--4 | 0.030537 | 1 | 100% | 370.1825 | 97.17% | 0% | 2.827% | 17.8061 | 0 | 0 | 17.8061 | 0 | 16.2033 | 0.37309 | 43.4295 | 16.2033 | 0.37309 | 43.4295 | 17.9811 | 0.41403 | 43.4295 | 4.81% | 0.046634 | 0.044326 | 7938.0395 | 1227.249 | 240.0519 | 6470.7387 | 7949.7244 | 0 | 0 | 7949.7244 | 0.0005872%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.029826 | 1 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1166 | 0.37309 | 2.9928 | 1.1166 | 0.37309 | 2.9928 | 1.2391 | 0.41403 | 2.9928 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2027 | BW1 | CB BW1 | Tier-1 | Non-HFTD---11 | 1--3 | 0.027874 | 1 | 100% | 8.712 | 88.19% | 0% | 11.81% | 0.3803 | 0 | 0 | 0.3803 | 0 | 0.34607 | 0.37309 | 0.92757 | 0.34607 | 0.37309 | 0.92757 | 0.38404 | 0.41403 | 0.92757 | 4.365% | 0.0039232 | 0.003729 | 2220.6335 | 316.4948 | 49.7388 | 1854.3999 | 2234.2939 | 0 | 0 | 2234.2939 | 1.254e-05%
2027 | 93 | 93-559R | Tier-1 | Non-HFTD---2 | 3--4 | 0.026808 | 1 | 100% | 194.9296 | 89.74% | 7.915% | 2.344% | 8.6591 | 0 | 0 | 8.6591 | 0 | 7.8797 | 0.37309 | 21.1197 | 7.8797 | 0.37309 | 21.1197 | 8.7442 | 0.41403 | 21.1197 | 4.442% | 0.02667 | 0.02535 | 7308.8898 | 1504.7135 | 606.7669 | 5197.4095 | 7347.9399 | 0 | 0 | 7347.9399 | 0.0002855%
2027 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.026098 | 1 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.2722 | 0.37309 | 0.72958 | 0.2722 | 0.37309 | 0.72958 | 0.30207 | 0.41403 | 0.72958 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2027 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.025033 | 1 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.3386 | 0.37309 | 3.5878 | 1.3386 | 0.37309 | 3.5878 | 1.4855 | 0.41403 | 3.5878 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2027 | 95 | 95-35F | Tier-1 | Non-HFTD---9 | 2--2 | 0.024145 | 1 | 100% | 19.0547 | 69.14% | 22.45% | 8.414% | 0.65213 | 0 | 0 | 0.65213 | 0 | 0.59343 | 0.37309 | 1.5906 | 0.59343 | 0.37309 | 1.5906 | 0.65854 | 0.41403 | 1.5906 | 3.422% | 0.011941 | 0.01135 | 1595.6856 | 179.3204 | 352.6449 | 1063.7203 | 1621.3303 | 0 | 0 | 1621.3303 | 2.15e-05%
2027 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.022015 | 1 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.8337 | 0.37309 | 7.5951 | 2.8337 | 0.37309 | 7.5951 | 3.1446 | 0.41403 | 7.5951 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2027 | 63 | 63-35AE | Tier-1 | Non-HFTD---1 | 3--4 | 0.019707 | 1 | 100% | 256.4675 | 76.22% | 23.46% | 0.3199% | 9.6762 | 0 | 0 | 9.6762 | 0 | 8.8052 | 0.37309 | 23.6005 | 8.8052 | 0.37309 | 23.6005 | 9.7713 | 0.41403 | 23.6005 | 3.773% | 0.016955 | 0.016116 | 15126.187 | 2259.8593 | 3445.3068 | 9421.0209 | 15313.5135 | 0 | 0 | 15313.5135 | 0.0003191%
2027 | 450 | 450-114F | Tier-1 | Non-HFTD---7 | 1--4 | 0.018642 | 1 | 100% | 28.615 | 98.32% | 0% | 1.684% | 1.3926 | 0 | 0 | 1.3926 | 0 | 1.2672 | 0.37309 | 3.3965 | 1.2672 | 0.37309 | 3.3965 | 1.4063 | 0.41403 | 3.3965 | 4.867% | 0.0023436 | 0.0022276 | 12209.8338 | 1908.2658 | 365.7567 | 9935.8114 | 12220.543 | 0 | 0 | 12220.543 | 4.592e-05%
2027 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.017576 | 1 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.66976 | 0.37309 | 1.7951 | 0.66976 | 0.37309 | 1.7951 | 0.74324 | 0.41403 | 1.7951 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.017399 | 1 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.2076 | 0.37309 | 8.5973 | 3.2076 | 0.37309 | 8.5973 | 3.5596 | 0.41403 | 8.5973 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 0.017044 | 1 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 154.5381 | 0.37309 | 414.2063 | 154.5381 | 0.37309 | 414.2063 | 171.4936 | 0.41403 | 414.2063 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2027 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.016866 | 1 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.34564 | 0.37309 | 0.92642 | 0.34564 | 0.37309 | 0.92642 | 0.38356 | 0.41403 | 0.92642 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 0.015623 | 1 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 245.0024 | 0.37309 | 656.6766 | 245.0024 | 0.37309 | 656.6766 | 271.8835 | 0.41403 | 656.6766 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2027 | 172 | 172-567R | Tier-1 | Non-HFTD---3 | 4--3 | 0.014203 | 1 | 100% | 141.9219 | 62.19% | 32.78% | 5.033% | 4.369 | 0 | 0 | 4.369 | 0 | 3.9758 | 0.37309 | 10.6562 | 3.9758 | 0.37309 | 10.6562 | 4.412 | 0.41403 | 10.6562 | 3.078% | 0.069555 | 0.066112 | 2040.4331 | 199.3667 | 664.6627 | 1176.4036 | 2080.609 | 0 | 0 | 2080.609 | 0.0001441%
2027 | TM1 | CB TM1 | Tier-1 | Non-HFTD---7 | 1--5 | 0.014026 | 1 | 100% | 38.7396 | 99.8% | 0% | 0.1958% | 1.9139 | 0 | 0 | 1.9139 | 0 | 1.7416 | 0.37309 | 4.6679 | 1.7416 | 0.37309 | 4.6679 | 1.9327 | 0.41403 | 4.6679 | 4.94% | 0.0001408 | 0.00013383 | 275139.3146 | 43811.8165 | 68.1712 | 231259.327 | 275167.3683 | 0 | 0 | 275167.3683 | 6.311e-05%
2027 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.013848 | 1 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.48646 | 0.37309 | 1.3039 | 0.48646 | 0.37309 | 1.3039 | 0.53984 | 0.41403 | 1.3039 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2027 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.01367 | 1 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 2.8633 | 0.37309 | 7.6744 | 2.8633 | 0.37309 | 7.6744 | 3.1774 | 0.41403 | 7.6744 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2027 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011185 | 1 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.37309 | 0 | 0 | 0.37309 | 0 | 0 | 0.41403 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2027 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.01083 | 1 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.1337 | 0.37309 | 3.0387 | 1.1337 | 0.37309 | 3.0387 | 1.2581 | 0.41403 | 3.0387 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2027 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.010652 | 1 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.031188 | 0.37309 | 0.083591 | 0.031188 | 0.37309 | 0.083591 | 0.034609 | 0.41403 | 0.083591 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 0.010475 | 1 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 21.1763 | 0.37309 | 56.7585 | 21.1763 | 0.37309 | 56.7585 | 23.4997 | 0.41403 | 56.7585 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2027 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.0099421 | 1 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.37309 | 0 | 0 | 0.37309 | 0 | 0 | 0.41403 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2027 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.0094095 | 1 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.1978 | 0.37309 | 3.2103 | 1.1978 | 0.37309 | 3.2103 | 1.3292 | 0.41403 | 3.2103 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.0079892 | 1 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 35.6381 | 0.37309 | 95.5202 | 35.6381 | 0.37309 | 95.5202 | 39.5482 | 0.41403 | 95.5202 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.0079892 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.30382 | 0.37309 | 0.81433 | 0.30382 | 0.37309 | 0.81433 | 0.33716 | 0.41403 | 0.81433 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2027 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.0056812 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.2707 | 0.37309 | 0.72557 | 0.2707 | 0.37309 | 0.72557 | 0.30041 | 0.41403 | 0.72557 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 18.9705 | 264 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1718.1256 | 93.9594 | 18.2858 | 1718.1256 | 93.9594 | 18.2858 | 2008.5084 | 109.8396 | 18.2858 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 16.9478 | 243 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 584.9503 | 86.4853 | 6.7636 | 584.9503 | 86.4853 | 6.7636 | 683.8136 | 101.1023 | 6.7636 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 16.4216 | 230 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 232.1573 | 81.8585 | 2.8361 | 232.1573 | 81.8585 | 2.8361 | 271.3946 | 95.6936 | 2.8361 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 16.3387 | 208 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 358.6727 | 74.0286 | 4.8451 | 358.6727 | 74.0286 | 4.8451 | 419.2925 | 86.5403 | 4.8451 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 16.241 | 202 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2785.0787 | 71.8932 | 38.7391 | 2785.0787 | 71.8932 | 38.7391 | 3255.7888 | 84.0439 | 38.7391 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 15.1902 | 204 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 781.526 | 72.605 | 10.7641 | 781.526 | 72.605 | 10.7641 | 913.6128 | 84.876 | 10.7641 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 14.975 | 232 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 696.8774 | 82.5704 | 8.4398 | 696.8774 | 82.5704 | 8.4398 | 814.6577 | 96.5257 | 8.4398 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 12.4911 | 168 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 168.4859 | 59.7923 | 2.8179 | 168.4859 | 59.7923 | 2.8179 | 196.962 | 69.8979 | 2.8179 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 12.3702 | 175 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 218.7933 | 62.2837 | 3.5129 | 218.7933 | 62.2837 | 3.5129 | 255.7719 | 72.8103 | 3.5129 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 12.0312 | 165 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 137.6937 | 58.7246 | 2.3447 | 137.6937 | 58.7246 | 2.3447 | 160.9655 | 68.6497 | 2.3447 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 11.9654 | 158 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 167.4015 | 56.2333 | 2.9769 | 167.4015 | 56.2333 | 2.9769 | 195.6942 | 65.7373 | 2.9769 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 11.4812 | 153 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3377.4744 | 54.4537 | 62.0247 | 3377.4744 | 54.4537 | 62.0247 | 3948.3061 | 63.657 | 62.0247 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 11.2437 | 150 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 72.2185 | 53.386 | 1.3528 | 72.2185 | 53.386 | 1.3528 | 84.4243 | 62.4089 | 1.3528 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 11.1024 | 166 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1210.6489 | 59.0805 | 20.4915 | 1210.6489 | 59.0805 | 20.4915 | 1415.2624 | 69.0658 | 20.4915 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 10.8361 | 146 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 65.5189 | 51.9624 | 1.2609 | 65.5189 | 51.9624 | 1.2609 | 76.5924 | 60.7446 | 1.2609 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 10.2901 | 149 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1315.706 | 53.0301 | 24.8106 | 1315.706 | 53.0301 | 24.8106 | 1538.0753 | 61.9928 | 24.8106 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 10.1733 | 154 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 218.0371 | 54.8096 | 3.9781 | 218.0371 | 54.8096 | 3.9781 | 254.8879 | 64.0731 | 3.9781 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 9.5585 | 147 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 147.7871 | 52.3183 | 2.8248 | 147.7871 | 52.3183 | 2.8248 | 172.7648 | 61.1607 | 2.8248 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 9.4763 | 129 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 109.6733 | 45.912 | 2.3888 | 109.6733 | 45.912 | 2.3888 | 128.2093 | 53.6716 | 2.3888 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 9.4722 | 119 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 436.6473 | 42.3529 | 10.3097 | 436.6473 | 42.3529 | 10.3097 | 510.4457 | 49.511 | 10.3097 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 9.219 | 142 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 672.6642 | 50.5388 | 13.3099 | 672.6642 | 50.5388 | 13.3099 | 786.3521 | 59.0804 | 13.3099 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 9.1274 | 116 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 226.6062 | 41.2852 | 5.4888 | 226.6062 | 41.2852 | 5.4888 | 264.9052 | 48.2628 | 5.4888 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 9.0834 | 125 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1116.9255 | 44.4883 | 25.106 | 1116.9255 | 44.4883 | 25.106 | 1305.6986 | 52.0074 | 25.106 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 8.8391 | 106 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 143.2712 | 37.7261 | 3.7977 | 143.2712 | 37.7261 | 3.7977 | 167.4857 | 44.1023 | 3.7977 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 8.769 | 159 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 439.9478 | 56.5892 | 7.7744 | 439.9478 | 56.5892 | 7.7744 | 514.3039 | 66.1534 | 7.7744 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2028 | 221 | 221-1251R | Tier-1 | Non-HFTD---2 | 5--4 | 8.6538 | 112 | 100% | 1814.8505 | 87.56% | 11.92% | 0.5209% | 78.6628 | 0 | 0 | 78.6628 | 0 | 68.2845 | 39.8616 | 1.713 | 68.2845 | 39.8616 | 1.713 | 79.8253 | 46.5986 | 1.713 | 4.334% | 0.27478 | 0.26118 | 6604.7785 | 826.9947 | 747.1453 | 5030.6385 | 6647.5552 | 0 | 0 | 6647.5552 | 0.002594%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 8.5037 | 120 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 873.9661 | 42.7088 | 20.4634 | 873.9661 | 42.7088 | 20.4634 | 1021.6763 | 49.9271 | 20.4634 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 8.4854 | 124 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 897.0119 | 44.1324 | 20.3255 | 897.0119 | 44.1324 | 20.3255 | 1048.6171 | 51.5913 | 20.3255 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 8.4423 | 124 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2356.8951 | 44.1324 | 53.4051 | 2356.8951 | 44.1324 | 53.4051 | 2755.2372 | 51.5913 | 53.4051 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 8.4285 | 130 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1753.1858 | 46.2679 | 37.8921 | 1753.1858 | 46.2679 | 37.8921 | 2049.4942 | 54.0877 | 37.8921 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 8.2367 | 113 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1078.5839 | 40.2175 | 26.8188 | 1078.5839 | 40.2175 | 26.8188 | 1260.8769 | 47.0147 | 26.8188 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 8.1575 | 139 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 261.6837 | 49.471 | 5.2896 | 261.6837 | 49.471 | 5.2896 | 305.9112 | 57.8322 | 5.2896 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 8.072 | 95 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 113.5276 | 33.8111 | 3.3577 | 113.5276 | 33.8111 | 3.3577 | 132.715 | 39.5256 | 3.3577 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 8.0514 | 112 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 479.2248 | 39.8616 | 12.0222 | 479.2248 | 39.8616 | 12.0222 | 560.2193 | 46.5986 | 12.0222 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 7.8648 | 104 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 547.9368 | 37.0143 | 14.8034 | 547.9368 | 37.0143 | 14.8034 | 640.5444 | 43.2701 | 14.8034 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2028 | 221 | 221-1249R | Tier-1 | Non-HFTD---2 | 5--2 | 7.8246 | 94 | 100% | 329.3718 | 60.93% | 35.44% | 3.632% | 9.9343 | 0 | 0 | 9.9343 | 0 | 8.6237 | 33.4552 | 0.25777 | 8.6237 | 33.4552 | 0.25777 | 10.0811 | 39.1095 | 0.25777 | 3.016% | 0.32343 | 0.30742 | 1018.3674 | 70.1582 | 373.9946 | 574.2146 | 1039.0867 | 0 | 0 | 1039.0867 | 0.0003276%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 7.7595 | 100 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 576.8605 | 35.5907 | 16.2082 | 576.8605 | 35.5907 | 16.2082 | 674.3565 | 41.6059 | 16.2082 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 7.7298 | 114 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 230.3929 | 40.5734 | 5.6784 | 230.3929 | 40.5734 | 5.6784 | 269.3319 | 47.4307 | 5.6784 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 7.7249 | 134 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1099.4968 | 47.6915 | 23.0544 | 1099.4968 | 47.6915 | 23.0544 | 1285.3243 | 55.7519 | 23.0544 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 7.6943 | 120 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1582.9263 | 42.7088 | 37.0632 | 1582.9263 | 42.7088 | 37.0632 | 1850.4589 | 49.9271 | 37.0632 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 7.5567 | 107 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 989.7054 | 38.082 | 25.9888 | 989.7054 | 38.082 | 25.9888 | 1156.9769 | 44.5183 | 25.9888 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 7.5022 | 112 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1137.4651 | 39.8616 | 28.5354 | 1137.4651 | 39.8616 | 28.5354 | 1329.7097 | 46.5986 | 28.5354 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 7.3384 | 119 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 307.5141 | 42.3529 | 7.2608 | 307.5141 | 42.3529 | 7.2608 | 359.4875 | 49.511 | 7.2608 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 7.2729 | 117 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 475.9015 | 41.6411 | 11.4287 | 475.9015 | 41.6411 | 11.4287 | 556.3343 | 48.6789 | 11.4287 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 7.1477 | 105 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 104.999 | 37.3702 | 2.8097 | 104.999 | 37.3702 | 2.8097 | 122.745 | 43.6862 | 2.8097 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 7.05 | 89 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 140.6197 | 31.6757 | 4.4394 | 140.6197 | 31.6757 | 4.4394 | 164.386 | 37.0293 | 4.4394 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 7.0044 | 107 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1201.9032 | 38.082 | 31.5609 | 1201.9032 | 38.082 | 31.5609 | 1405.0386 | 44.5183 | 31.5609 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 6.9425 | 118 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 175.1249 | 41.997 | 4.1699 | 175.1249 | 41.997 | 4.1699 | 204.723 | 49.095 | 4.1699 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 6.9423 | 98 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 447.4138 | 34.8789 | 12.8277 | 447.4138 | 34.8789 | 12.8277 | 523.0318 | 40.7738 | 12.8277 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 6.7285 | 96 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1593.0007 | 34.167 | 46.6239 | 1593.0007 | 34.167 | 46.6239 | 1862.236 | 39.9417 | 46.6239 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 6.7134 | 96 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 207.223 | 34.167 | 6.065 | 207.223 | 34.167 | 6.065 | 242.246 | 39.9417 | 6.065 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 6.6793 | 104 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1495.8237 | 37.0143 | 40.412 | 1495.8237 | 37.0143 | 40.412 | 1748.6349 | 43.2701 | 40.412 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 6.6731 | 69 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 439.4785 | 24.5576 | 17.8959 | 439.4785 | 24.5576 | 17.8959 | 513.7554 | 28.7081 | 17.8959 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 6.6185 | 105 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 77.1998 | 37.3702 | 2.0658 | 77.1998 | 37.3702 | 2.0658 | 90.2474 | 43.6862 | 2.0658 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 6.5844 | 101 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 154.5823 | 35.9466 | 4.3003 | 154.5823 | 35.9466 | 4.3003 | 180.7085 | 42.022 | 4.3003 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 6.5087 | 101 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 783.9515 | 35.9466 | 21.8088 | 783.9515 | 35.9466 | 21.8088 | 916.4483 | 42.022 | 21.8088 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 6.3857 | 85 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 50.7321 | 30.2521 | 1.677 | 50.7321 | 30.2521 | 1.677 | 59.3064 | 35.365 | 1.677 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 6.3651 | 74 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 274.7145 | 26.3371 | 10.4307 | 274.7145 | 26.3371 | 10.4307 | 321.1444 | 30.7884 | 10.4307 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 6.3399 | 103 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 282.962 | 36.6584 | 7.7189 | 282.962 | 36.6584 | 7.7189 | 330.7858 | 42.8541 | 7.7189 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 6.3184 | 93 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 356.2423 | 33.0993 | 10.7628 | 356.2423 | 33.0993 | 10.7628 | 416.4513 | 38.6935 | 10.7628 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 6.2953 | 97 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 434.9987 | 34.523 | 12.6003 | 434.9987 | 34.523 | 12.6003 | 508.5185 | 40.3577 | 12.6003 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 6.2854 | 103 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 485.1895 | 36.6584 | 13.2354 | 485.1895 | 36.6584 | 13.2354 | 567.1921 | 42.8541 | 13.2354 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 6.2785 | 95 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 152.5001 | 33.8111 | 4.5104 | 152.5001 | 33.8111 | 4.5104 | 178.2744 | 39.5256 | 4.5104 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 6.2728 | 79 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 1931.0119 | 28.1166 | 68.6786 | 1931.0119 | 28.1166 | 68.6786 | 2257.3749 | 32.8687 | 68.6786 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 6.2536 | 72 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 339.5288 | 25.6253 | 13.2498 | 339.5288 | 25.6253 | 13.2498 | 396.9131 | 29.9562 | 13.2498 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 6.2492 | 99 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 186.6975 | 35.2348 | 5.2987 | 186.6975 | 35.2348 | 5.2987 | 218.2515 | 41.1898 | 5.2987 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 6.192 | 88 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 238.9635 | 31.3198 | 7.6298 | 238.9635 | 31.3198 | 7.6298 | 279.3511 | 36.6132 | 7.6298 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 6.1782 | 87 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 112.9854 | 30.9639 | 3.6489 | 112.9854 | 30.9639 | 3.6489 | 132.0812 | 36.1971 | 3.6489 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 6.1766 | 109 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 362.6973 | 38.7938 | 9.3494 | 362.6973 | 38.7938 | 9.3494 | 423.9973 | 45.3504 | 9.3494 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 6.1716 | 84 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 392.8265 | 29.8962 | 13.1397 | 392.8265 | 29.8962 | 13.1397 | 459.2187 | 34.949 | 13.1397 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 6.1345 | 91 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 228.5893 | 32.3875 | 7.0579 | 228.5893 | 32.3875 | 7.0579 | 267.2235 | 37.8614 | 7.0579 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 6.1235 | 100 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 741.2094 | 35.5907 | 20.8259 | 741.2094 | 35.5907 | 20.8259 | 866.4823 | 41.6059 | 20.8259 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 6.0644 | 82 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 583.1815 | 29.1844 | 19.9827 | 583.1815 | 29.1844 | 19.9827 | 681.7459 | 34.1168 | 19.9827 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 6.0573 | 82 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 453.1633 | 29.1844 | 15.5276 | 453.1633 | 29.1844 | 15.5276 | 529.7531 | 34.1168 | 15.5276 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 6.0221 | 79 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 129.3787 | 28.1166 | 4.6015 | 129.3787 | 28.1166 | 4.6015 | 151.2452 | 32.8687 | 4.6015 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 6.015 | 81 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 71.3031 | 28.8284 | 2.4734 | 71.3031 | 28.8284 | 2.4734 | 83.3541 | 33.7008 | 2.4734 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 5.8678 | 90 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 136.0144 | 32.0316 | 4.2463 | 136.0144 | 32.0316 | 4.2463 | 159.0024 | 37.4453 | 4.2463 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 5.8655 | 70 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 360.5107 | 24.9135 | 14.4705 | 360.5107 | 24.9135 | 14.4705 | 421.4411 | 29.1241 | 14.4705 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 5.8426 | 75 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 73.9791 | 26.693 | 2.7715 | 73.9791 | 26.693 | 2.7715 | 86.4824 | 31.2044 | 2.7715 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 5.8078 | 82 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 69.754 | 29.1844 | 2.3901 | 69.754 | 29.1844 | 2.3901 | 81.5432 | 34.1168 | 2.3901 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 5.794 | 82 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 102.9619 | 29.1844 | 3.528 | 102.9619 | 29.1844 | 3.528 | 120.3637 | 34.1168 | 3.528 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 5.7925 | 77 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 393.0326 | 27.4048 | 14.3417 | 393.0326 | 27.4048 | 14.3417 | 459.4596 | 32.0365 | 14.3417 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 5.7743 | 69 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 61.9628 | 24.5576 | 2.5232 | 61.9628 | 24.5576 | 2.5232 | 72.4352 | 28.7081 | 2.5232 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 5.7743 | 95 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 390.5476 | 33.8111 | 11.5509 | 390.5476 | 33.8111 | 11.5509 | 456.5546 | 39.5256 | 11.5509 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 5.7334 | 83 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 770.8154 | 29.5403 | 26.0937 | 770.8154 | 29.5403 | 26.0937 | 901.092 | 34.5329 | 26.0937 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 5.6393 | 85 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 960.6823 | 30.2521 | 31.7559 | 960.6823 | 30.2521 | 31.7559 | 1123.0485 | 35.365 | 31.7559 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 5.6107 | 87 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 86.435 | 30.9639 | 2.7915 | 86.435 | 30.9639 | 2.7915 | 101.0435 | 36.1971 | 2.7915 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 5.5928 | 89 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 644.766 | 31.6757 | 20.3552 | 644.766 | 31.6757 | 20.3552 | 753.7388 | 37.0293 | 20.3552 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 5.5142 | 85 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1378.2488 | 30.2521 | 45.5588 | 1378.2488 | 30.2521 | 45.5588 | 1611.1885 | 35.365 | 45.5588 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 5.4426 | 107 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 182.6123 | 38.082 | 4.7952 | 182.6123 | 38.082 | 4.7952 | 213.4758 | 44.5183 | 4.7952 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2028 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | 4--5 | 5.4183 | 81 | 100% | 5312.2676 | 97.77% | 1.999% | 0.2313% | 257.0917 | 0 | 0 | 257.0917 | 0 | 223.1724 | 28.8284 | 7.7414 | 223.1724 | 28.8284 | 7.7414 | 260.891 | 33.7008 | 7.7414 | 4.84% | 0.075145 | 0.071425 | 70693.7485 | 12854.9773 | 1446.2382 | 56392.533 | 70775.8701 | 0 | 0 | 70775.8701 | 0.008478%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 5.3672 | 95 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 306.5225 | 33.8111 | 9.0657 | 306.5225 | 33.8111 | 9.0657 | 358.3282 | 39.5256 | 9.0657 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 5.3558 | 82 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 371.4043 | 29.1844 | 12.7261 | 371.4043 | 29.1844 | 12.7261 | 434.1758 | 34.1168 | 12.7261 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 5.3395 | 81 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 794.7222 | 28.8284 | 27.5673 | 794.7222 | 28.8284 | 27.5673 | 929.0394 | 33.7008 | 27.5673 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 5.3336 | 104 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 269.5166 | 37.0143 | 7.2814 | 269.5166 | 37.0143 | 7.2814 | 315.068 | 43.2701 | 7.2814 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 5.2977 | 65 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 46.128 | 23.1339 | 1.994 | 46.128 | 23.1339 | 1.994 | 53.9241 | 27.0438 | 1.994 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 5.2871 | 79 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 372.002 | 28.1166 | 13.2307 | 372.002 | 28.1166 | 13.2307 | 434.8746 | 32.8687 | 13.2307 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 5.2523 | 72 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 64.9052 | 25.6253 | 2.5329 | 64.9052 | 25.6253 | 2.5329 | 75.8749 | 29.9562 | 2.5329 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 5.2244 | 59 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 64.0856 | 20.9985 | 3.0519 | 64.0856 | 20.9985 | 3.0519 | 74.9168 | 24.5475 | 3.0519 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 5.212 | 78 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 264.6183 | 27.7607 | 9.5321 | 264.6183 | 27.7607 | 9.5321 | 309.3418 | 32.4526 | 9.5321 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 5.1827 | 76 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 17.3558 | 27.0489 | 0.64164 | 17.3558 | 27.0489 | 0.64164 | 20.2891 | 31.6205 | 0.64164 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 5.1751 | 72 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 85.7236 | 25.6253 | 3.3453 | 85.7236 | 25.6253 | 3.3453 | 100.2118 | 29.9562 | 3.3453 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 5.0888 | 75 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1153.6452 | 26.693 | 43.219 | 1153.6452 | 26.693 | 43.219 | 1348.6244 | 31.2044 | 43.219 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 5.0843 | 94 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 381.0599 | 33.4552 | 11.3901 | 381.0599 | 33.4552 | 11.3901 | 445.4634 | 39.1095 | 11.3901 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 5.0636 | 75 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 269.7477 | 26.693 | 10.1056 | 269.7477 | 26.693 | 10.1056 | 315.3382 | 31.2044 | 10.1056 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 5.063 | 76 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 666.1338 | 27.0489 | 24.627 | 666.1338 | 27.0489 | 24.627 | 778.718 | 31.6205 | 24.627 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 5.0508 | 80 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 649.5434 | 28.4725 | 22.813 | 649.5434 | 28.4725 | 22.813 | 759.3236 | 33.2847 | 22.813 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 5.0233 | 64 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 953.2756 | 22.778 | 41.8507 | 953.2756 | 22.778 | 41.8507 | 1114.3901 | 26.6278 | 41.8507 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 4.978 | 70 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 157.9271 | 24.9135 | 6.339 | 157.9271 | 24.9135 | 6.339 | 184.6186 | 29.1241 | 6.339 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 4.9753 | 73 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 494.131 | 25.9812 | 19.0188 | 494.131 | 25.9812 | 19.0188 | 577.6448 | 30.3723 | 19.0188 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 4.8985 | 74 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 259.2534 | 26.3371 | 9.8437 | 259.2534 | 26.3371 | 9.8437 | 303.0701 | 30.7884 | 9.8437 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 4.8944 | 58 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 21.4448 | 20.6426 | 1.0389 | 21.4448 | 20.6426 | 1.0389 | 25.0692 | 24.1314 | 1.0389 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 4.8617 | 74 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 152.0946 | 26.3371 | 5.7749 | 152.0946 | 26.3371 | 5.7749 | 177.8003 | 30.7884 | 5.7749 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 4.8551 | 85 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 118.8605 | 30.2521 | 3.929 | 118.8605 | 30.2521 | 3.929 | 138.9493 | 35.365 | 3.929 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 4.7692 | 74 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 479.4093 | 26.3371 | 18.2028 | 479.4093 | 26.3371 | 18.2028 | 560.435 | 30.7884 | 18.2028 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 4.7364 | 81 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 369.313 | 28.8284 | 12.8107 | 369.313 | 28.8284 | 12.8107 | 431.7311 | 33.7008 | 12.8107 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 4.7152 | 60 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 17.0436 | 21.3544 | 0.79813 | 17.0436 | 21.3544 | 0.79813 | 19.9241 | 24.9635 | 0.79813 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 4.6872 | 62 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 38.2345 | 22.0662 | 1.7327 | 38.2345 | 22.0662 | 1.7327 | 44.6966 | 25.7957 | 1.7327 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 4.6403 | 67 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 716.0815 | 23.8458 | 30.0297 | 716.0815 | 23.8458 | 30.0297 | 837.1074 | 27.876 | 30.0297 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 4.613 | 70 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 148.7534 | 24.9135 | 5.9708 | 148.7534 | 24.9135 | 5.9708 | 173.8944 | 29.1241 | 5.9708 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 4.6105 | 71 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 284.7731 | 25.2694 | 11.2695 | 284.7731 | 25.2694 | 11.2695 | 332.9031 | 29.5402 | 11.2695 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 4.5567 | 59 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 389.681 | 20.9985 | 18.5576 | 389.681 | 20.9985 | 18.5576 | 455.5415 | 24.5475 | 18.5576 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 4.5517 | 72 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 252.5151 | 25.6253 | 9.8541 | 252.5151 | 25.6253 | 9.8541 | 295.1931 | 29.9562 | 9.8541 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 4.5471 | 61 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 103.165 | 21.7103 | 4.7519 | 103.165 | 21.7103 | 4.7519 | 120.601 | 25.3796 | 4.7519 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 4.5413 | 78 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 350.0629 | 27.7607 | 12.61 | 350.0629 | 27.7607 | 12.61 | 409.2275 | 32.4526 | 12.61 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 4.5215 | 73 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 183.7705 | 25.9812 | 7.0732 | 183.7705 | 25.9812 | 7.0732 | 214.8298 | 30.3723 | 7.0732 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 4.5105 | 78 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 290.1396 | 27.7607 | 10.4514 | 290.1396 | 27.7607 | 10.4514 | 339.1765 | 32.4526 | 10.4514 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 4.4665 | 60 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 851.8508 | 21.3544 | 39.8911 | 851.8508 | 21.3544 | 39.8911 | 995.8233 | 24.9635 | 39.8911 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 4.4447 | 63 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1205.8901 | 22.4221 | 53.7813 | 1205.8901 | 22.4221 | 53.7813 | 1409.6992 | 26.2117 | 53.7813 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 4.4326 | 62 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 56.178 | 22.0662 | 2.5459 | 56.178 | 22.0662 | 2.5459 | 65.6727 | 25.7957 | 2.5459 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 4.4294 | 79 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 137.5976 | 28.1166 | 4.8938 | 137.5976 | 28.1166 | 4.8938 | 160.8532 | 32.8687 | 4.8938 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 4.3685 | 55 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 291.2678 | 19.5749 | 14.8797 | 291.2678 | 19.5749 | 14.8797 | 340.4953 | 22.8832 | 14.8797 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 4.3413 | 58 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 64.3194 | 20.6426 | 3.1159 | 64.3194 | 20.6426 | 3.1159 | 75.1902 | 24.1314 | 3.1159 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 4.3085 | 63 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1002.9466 | 22.4221 | 44.7302 | 1002.9466 | 22.4221 | 44.7302 | 1172.456 | 26.2117 | 44.7302 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 4.292 | 63 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 281.0624 | 22.4221 | 12.535 | 281.0624 | 22.4221 | 12.535 | 328.5651 | 26.2117 | 12.535 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 4.2842 | 53 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 299.4236 | 18.8631 | 15.8735 | 299.4236 | 18.8631 | 15.8735 | 350.0296 | 22.0511 | 15.8735 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 4.2597 | 57 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 138.3721 | 20.2867 | 6.8208 | 138.3721 | 20.2867 | 6.8208 | 161.7586 | 23.7154 | 6.8208 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 4.1777 | 71 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 668.2095 | 25.2694 | 26.4434 | 668.2095 | 25.2694 | 26.4434 | 781.1445 | 29.5402 | 26.4434 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 4.175 | 75 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1150.7453 | 26.693 | 43.1104 | 1150.7453 | 26.693 | 43.1104 | 1345.2344 | 31.2044 | 43.1104 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 4.1306 | 59 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 536.0657 | 20.9985 | 25.5288 | 536.0657 | 20.9985 | 25.5288 | 626.6669 | 24.5475 | 25.5288 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 4.1246 | 51 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 53.265 | 18.1512 | 2.9345 | 53.265 | 18.1512 | 2.9345 | 62.2674 | 21.219 | 2.9345 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 4.0797 | 70 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 128.9318 | 24.9135 | 5.1752 | 128.9318 | 24.9135 | 5.1752 | 150.7228 | 29.1241 | 5.1752 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 4.0305 | 55 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 242.4537 | 19.5749 | 12.386 | 242.4537 | 19.5749 | 12.386 | 283.4311 | 22.8832 | 12.386 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 4.0205 | 46 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 430.5862 | 16.3717 | 26.3006 | 430.5862 | 16.3717 | 26.3006 | 503.3602 | 19.1387 | 26.3006 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 4.0063 | 72 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 213.6481 | 25.6253 | 8.3374 | 213.6481 | 25.6253 | 8.3374 | 249.7571 | 29.9562 | 8.3374 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 4.0008 | 67 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 370.166 | 23.8458 | 15.5234 | 370.166 | 23.8458 | 15.5234 | 432.7283 | 27.876 | 15.5234 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 3.8739 | 51 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 61.8315 | 18.1512 | 3.4065 | 61.8315 | 18.1512 | 3.4065 | 72.2817 | 21.219 | 3.4065 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 3.8709 | 52 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 142.8362 | 18.5071 | 7.7179 | 142.8362 | 18.5071 | 7.7179 | 166.9772 | 21.6351 | 7.7179 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 3.8679 | 61 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 145.7841 | 21.7103 | 6.715 | 145.7841 | 21.7103 | 6.715 | 170.4233 | 25.3796 | 6.715 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 3.8654 | 52 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 76.2372 | 18.5071 | 4.1193 | 76.2372 | 18.5071 | 4.1193 | 89.1222 | 21.6351 | 4.1193 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 3.8277 | 55 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 615.1953 | 19.5749 | 31.4278 | 615.1953 | 19.5749 | 31.4278 | 719.1703 | 22.8832 | 31.4278 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 3.8071 | 70 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 48.9727 | 24.9135 | 1.9657 | 48.9727 | 24.9135 | 1.9657 | 57.2497 | 29.1241 | 1.9657 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 3.7897 | 49 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 176.3919 | 17.4394 | 10.1145 | 176.3919 | 17.4394 | 10.1145 | 206.2042 | 20.3869 | 10.1145 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 3.777 | 62 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 81.1115 | 22.0662 | 3.6758 | 81.1115 | 22.0662 | 3.6758 | 94.8202 | 25.7957 | 3.6758 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 3.7716 | 56 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 123.2314 | 19.9308 | 6.183 | 123.2314 | 19.9308 | 6.183 | 144.0589 | 23.2993 | 6.183 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 3.762 | 57 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 159.313 | 20.2867 | 7.8531 | 159.313 | 20.2867 | 7.8531 | 186.2387 | 23.7154 | 7.8531 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 3.7556 | 54 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 124.5986 | 19.219 | 6.4831 | 124.5986 | 19.219 | 6.4831 | 145.6572 | 22.4672 | 6.4831 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 3.7382 | 64 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 164.0457 | 22.778 | 7.2019 | 164.0457 | 22.778 | 7.2019 | 191.7713 | 26.6278 | 7.2019 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 3.729 | 53 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 471.5754 | 18.8631 | 24.9999 | 471.5754 | 18.8631 | 24.9999 | 551.277 | 22.0511 | 24.9999 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 3.704 | 55 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 412.3272 | 19.5749 | 21.0641 | 412.3272 | 19.5749 | 21.0641 | 482.0151 | 22.8832 | 21.0641 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 3.6992 | 49 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 216.5332 | 17.4394 | 12.4163 | 216.5332 | 17.4394 | 12.4163 | 253.1298 | 20.3869 | 12.4163 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 3.6983 | 73 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 129.5064 | 25.9812 | 4.9846 | 129.5064 | 25.9812 | 4.9846 | 151.3944 | 30.3723 | 4.9846 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 3.666 | 64 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 959.7818 | 22.778 | 42.1363 | 959.7818 | 22.778 | 42.1363 | 1121.9958 | 26.6278 | 42.1363 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 3.5829 | 54 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 23.3118 | 19.219 | 1.213 | 23.3118 | 19.219 | 1.213 | 27.2518 | 22.4672 | 1.213 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 3.5582 | 64 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 135.3647 | 22.778 | 5.9428 | 135.3647 | 22.778 | 5.9428 | 158.2428 | 26.6278 | 5.9428 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 3.5375 | 58 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 598.4272 | 20.6426 | 28.9899 | 598.4272 | 20.6426 | 28.9899 | 699.5682 | 24.1314 | 28.9899 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 3.4803 | 57 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 444.2579 | 20.2867 | 21.899 | 444.2579 | 20.2867 | 21.899 | 519.3425 | 23.7154 | 21.899 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 3.4792 | 59 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 81.6467 | 20.9985 | 3.8882 | 81.6467 | 20.9985 | 3.8882 | 95.4459 | 24.5475 | 3.8882 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 3.4748 | 49 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 208.243 | 17.4394 | 11.9409 | 208.243 | 17.4394 | 11.9409 | 243.4385 | 20.3869 | 11.9409 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 3.4634 | 58 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 317.4625 | 20.6426 | 15.379 | 317.4625 | 20.6426 | 15.379 | 371.1173 | 24.1314 | 15.379 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 3.4338 | 51 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 522.7499 | 18.1512 | 28.7997 | 522.7499 | 18.1512 | 28.7997 | 611.1006 | 21.219 | 28.7997 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 3.4306 | 44 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 258.5486 | 15.6599 | 16.5102 | 258.5486 | 15.6599 | 16.5102 | 302.2462 | 18.3066 | 16.5102 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 3.3636 | 41 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 680.7304 | 14.5922 | 46.6504 | 680.7304 | 14.5922 | 46.6504 | 795.7816 | 17.0584 | 46.6504 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 3.313 | 51 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 294.1909 | 18.1512 | 16.2078 | 294.1909 | 18.1512 | 16.2078 | 343.9125 | 21.219 | 16.2078 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 3.2878 | 52 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 783.9792 | 18.5071 | 42.3609 | 783.9792 | 18.5071 | 42.3609 | 916.4806 | 21.6351 | 42.3609 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 3.2754 | 50 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 224.7004 | 17.7953 | 12.6269 | 224.7004 | 17.7953 | 12.6269 | 262.6774 | 20.803 | 12.6269 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 3.2692 | 43 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 489.052 | 15.304 | 31.9559 | 489.052 | 15.304 | 31.9559 | 571.7074 | 17.8905 | 31.9559 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 3.2674 | 51 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 234.4344 | 18.1512 | 12.9156 | 234.4344 | 18.1512 | 12.9156 | 274.0565 | 21.219 | 12.9156 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 3.2566 | 43 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 125.5186 | 15.304 | 8.2017 | 125.5186 | 15.304 | 8.2017 | 146.7327 | 17.8905 | 8.2017 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 3.2292 | 52 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 829.0555 | 18.5071 | 44.7965 | 829.0555 | 18.5071 | 44.7965 | 969.1753 | 21.6351 | 44.7965 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 3.1944 | 52 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 94.2766 | 18.5071 | 5.0941 | 94.2766 | 18.5071 | 5.0941 | 110.2104 | 21.6351 | 5.0941 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 3.1096 | 46 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 41.4677 | 16.3717 | 2.5329 | 41.4677 | 16.3717 | 2.5329 | 48.4762 | 19.1387 | 2.5329 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 3.1062 | 56 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1000.831 | 19.9308 | 50.2154 | 1000.831 | 19.9308 | 50.2154 | 1169.9829 | 23.2993 | 50.2154 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 3.1055 | 42 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 625.2178 | 14.9481 | 41.826 | 625.2178 | 14.9481 | 41.826 | 730.8867 | 17.4745 | 41.826 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 3.1032 | 38 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 347.982 | 13.5245 | 25.7298 | 347.982 | 13.5245 | 25.7298 | 406.795 | 15.8102 | 25.7298 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 3.1032 | 40 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 43.3507 | 14.2363 | 3.0451 | 43.3507 | 14.2363 | 3.0451 | 50.6775 | 16.6424 | 3.0451 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 3.0947 | 37 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 68.9581 | 13.1685 | 5.2366 | 68.9581 | 13.1685 | 5.2366 | 80.6128 | 15.3942 | 5.2366 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2028 | BN2 | CB BN2 | Tier-1 | Non-HFTD---1 | 4--5 | 3.0893 | 50 | 100% | 1098.8312 | 99.36% | 0% | 0.6449% | 54.0413 | 0 | 0 | 54.0413 | 0 | 46.9114 | 17.7953 | 2.6362 | 46.9114 | 17.7953 | 2.6362 | 54.84 | 20.803 | 2.6362 | 4.918% | 0.034221 | 0.032527 | 32110.0379 | 7492.6936 | 90.1662 | 24527.178 | 32120.8227 | 0 | 0 | 32120.8227 | 0.001782%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 3.0886 | 43 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 95.2503 | 15.304 | 6.2239 | 95.2503 | 15.304 | 6.2239 | 111.3487 | 17.8905 | 6.2239 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 3.0856 | 48 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 106.6551 | 17.0835 | 6.2432 | 106.6551 | 17.0835 | 6.2432 | 124.681 | 19.9708 | 6.2432 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 3.0508 | 41 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 806.4885 | 14.5922 | 55.2686 | 806.4885 | 14.5922 | 55.2686 | 942.7942 | 17.0584 | 55.2686 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 3.0423 | 31 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 224.4292 | 11.0331 | 20.3414 | 224.4292 | 11.0331 | 20.3414 | 262.3603 | 12.8978 | 20.3414 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 3.0327 | 45 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 624.7291 | 16.0158 | 39.007 | 624.7291 | 16.0158 | 39.007 | 730.3154 | 18.7227 | 39.007 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 3.0013 | 33 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 304.0085 | 11.7449 | 25.8843 | 304.0085 | 11.7449 | 25.8843 | 355.3895 | 13.7299 | 25.8843 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 2.931 | 43 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 525.5304 | 15.304 | 34.3394 | 525.5304 | 15.304 | 34.3394 | 614.3511 | 17.8905 | 34.3394 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2028 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 2.8346 | 48 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 252.094 | 17.0835 | 14.7566 | 252.094 | 17.0835 | 14.7566 | 294.7007 | 19.9708 | 14.7566 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 2.8213 | 45 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 53.4487 | 16.0158 | 3.3372 | 53.4487 | 16.0158 | 3.3372 | 62.4822 | 18.7227 | 3.3372 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 2.8166 | 44 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 30.1439 | 15.6599 | 1.9249 | 30.1439 | 15.6599 | 1.9249 | 35.2385 | 18.3066 | 1.9249 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 2.7905 | 43 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 144.0231 | 15.304 | 9.4108 | 144.0231 | 15.304 | 9.4108 | 168.3647 | 17.8905 | 9.4108 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 2.7494 | 42 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 500.606 | 14.9481 | 33.4896 | 500.606 | 14.9481 | 33.4896 | 585.2141 | 17.4745 | 33.4896 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 2.7478 | 42 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 482.838 | 14.9481 | 32.301 | 482.838 | 14.9481 | 32.301 | 564.4431 | 17.4745 | 32.301 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 2.7261 | 42 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 578.2628 | 14.9481 | 38.6847 | 578.2628 | 14.9481 | 38.6847 | 675.9958 | 17.4745 | 38.6847 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 2.678 | 32 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 200.0322 | 11.389 | 17.5636 | 200.0322 | 11.389 | 17.5636 | 233.8399 | 13.3139 | 17.5636 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 2.6361 | 42 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 229.1356 | 14.9481 | 15.3288 | 229.1356 | 14.9481 | 15.3288 | 267.8621 | 17.4745 | 15.3288 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 2.6311 | 29 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 37.1073 | 10.3213 | 3.5952 | 37.1073 | 10.3213 | 3.5952 | 43.3789 | 12.0657 | 3.5952 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 2.6281 | 38 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 253.7687 | 13.5245 | 18.7637 | 253.7687 | 13.5245 | 18.7637 | 296.6585 | 15.8102 | 18.7637 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 2.6018 | 32 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 91.0147 | 11.389 | 7.9914 | 91.0147 | 11.389 | 7.9914 | 106.3972 | 13.3139 | 7.9914 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 2.5951 | 48 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 229.2998 | 17.0835 | 13.4223 | 229.2998 | 17.0835 | 13.4223 | 268.0541 | 19.9708 | 13.4223 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2028 | 305 | CB 305 | Tier-1 | Non-HFTD---1 | 4--5 | 2.575 | 36 | 100% | 2786.7739 | 97.11% | 2.732% | 0.1605% | 133.9547 | 0 | 0 | 133.9547 | 0 | 116.2814 | 12.8126 | 9.0755 | 116.2814 | 12.8126 | 9.0755 | 135.9343 | 14.9781 | 9.0755 | 4.807% | 0.073949 | 0.070288 | 37685.1802 | 5958.9331 | 946.9636 | 30779.2836 | 37741.9553 | 0 | 0 | 37741.9553 | 0.004417%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 2.531 | 36 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 75.9675 | 12.8126 | 5.9291 | 75.9675 | 12.8126 | 5.9291 | 88.8068 | 14.9781 | 5.9291 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 2.5257 | 32 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 223.2743 | 11.389 | 19.6044 | 223.2743 | 11.389 | 19.6044 | 261.0102 | 13.3139 | 19.6044 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 2.4981 | 46 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 63.3943 | 16.3717 | 3.8722 | 63.3943 | 16.3717 | 3.8722 | 74.1087 | 19.1387 | 3.8722 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 2.4941 | 35 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 118.0052 | 12.4567 | 9.4732 | 118.0052 | 12.4567 | 9.4732 | 137.9494 | 14.5621 | 9.4732 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 2.4903 | 40 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 182.2987 | 14.2363 | 12.8052 | 182.2987 | 14.2363 | 12.8052 | 213.1093 | 16.6424 | 12.8052 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 2.4751 | 38 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 150.6352 | 13.5245 | 11.138 | 150.6352 | 13.5245 | 11.138 | 176.0942 | 15.8102 | 11.138 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 2.4671 | 37 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 389.9738 | 13.1685 | 29.614 | 389.9738 | 13.1685 | 29.614 | 455.8839 | 15.3942 | 29.614 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 2.4658 | 33 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 216.1178 | 11.7449 | 18.401 | 216.1178 | 11.7449 | 18.401 | 252.6441 | 13.7299 | 18.401 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 2.4649 | 27 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 164.8649 | 9.6095 | 17.1565 | 164.8649 | 9.6095 | 17.1565 | 192.729 | 11.2336 | 17.1565 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 2.4456 | 43 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 386.2992 | 15.304 | 25.2417 | 386.2992 | 15.304 | 25.2417 | 451.5881 | 17.8905 | 25.2417 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 2.4106 | 39 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 54.0763 | 13.8804 | 3.8959 | 54.0763 | 13.8804 | 3.8959 | 63.2158 | 16.2263 | 3.8959 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 2.3652 | 54 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 69.9765 | 19.219 | 3.641 | 69.9765 | 19.219 | 3.641 | 81.8033 | 22.4672 | 3.641 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 2.3519 | 38 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 57.8421 | 13.5245 | 4.2769 | 57.8421 | 13.5245 | 4.2769 | 67.6181 | 15.8102 | 4.2769 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 2.3316 | 32 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 207.1447 | 11.389 | 18.1881 | 207.1447 | 11.389 | 18.1881 | 242.1545 | 13.3139 | 18.1881 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 2.3139 | 24 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 13.8599 | 8.5418 | 1.6226 | 13.8599 | 8.5418 | 1.6226 | 16.2024 | 9.9854 | 1.6226 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 2.3096 | 32 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 18.2705 | 11.389 | 1.6042 | 18.2705 | 11.389 | 1.6042 | 21.3584 | 13.3139 | 1.6042 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 2.308 | 33 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 211.088 | 11.7449 | 17.9727 | 211.088 | 11.7449 | 17.9727 | 246.7643 | 13.7299 | 17.9727 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 2.2931 | 36 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 31.1245 | 12.8126 | 2.4292 | 31.1245 | 12.8126 | 2.4292 | 36.3849 | 14.9781 | 2.4292 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 2.2137 | 38 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 20.258 | 13.5245 | 1.4979 | 20.258 | 13.5245 | 1.4979 | 23.6818 | 15.8102 | 1.4979 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 2.197 | 32 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 419.5312 | 11.389 | 36.8365 | 419.5312 | 11.389 | 36.8365 | 490.4368 | 13.3139 | 36.8365 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 2.1724 | 37 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 501.116 | 13.1685 | 38.054 | 501.116 | 13.1685 | 38.054 | 585.8104 | 15.3942 | 38.054 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 2.1631 | 32 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 75.7606 | 11.389 | 6.6521 | 75.7606 | 11.389 | 6.6521 | 88.565 | 13.3139 | 6.6521 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 2.1495 | 30 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 226.556 | 10.6772 | 21.2187 | 226.556 | 10.6772 | 21.2187 | 264.8465 | 12.4818 | 21.2187 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 2.125 | 36 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 94.0298 | 12.8126 | 7.3388 | 94.0298 | 12.8126 | 7.3388 | 109.922 | 14.9781 | 7.3388 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 2.1166 | 37 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 383.592 | 13.1685 | 29.1294 | 383.592 | 13.1685 | 29.1294 | 448.4235 | 15.3942 | 29.1294 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 2.0966 | 30 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 231 | 10.6772 | 21.6349 | 231 | 10.6772 | 21.6349 | 270.0416 | 12.4818 | 21.6349 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2028 | 859 | 859-13F | Tier-1 | Non-HFTD---1 | 4--5 | 2.0873 | 40 | 100% | 1153.8557 | 99.35% | 0% | 0.6497% | 56.7448 | 0 | 0 | 56.7448 | 0 | 49.2582 | 14.2363 | 3.46 | 49.2582 | 14.2363 | 3.46 | 57.5834 | 16.6424 | 3.46 | 4.918% | 0.035677 | 0.033911 | 32341.7236 | 5122.1729 | 819.8446 | 26399.7061 | 32352.6656 | 0 | 0 | 32352.6656 | 0.001871%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 2.0797 | 33 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 398.5988 | 11.7449 | 33.938 | 398.5988 | 11.7449 | 33.938 | 465.9666 | 13.7299 | 33.938 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 2.0717 | 32 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 134.4194 | 11.389 | 11.8025 | 134.4194 | 11.389 | 11.8025 | 157.1378 | 13.3139 | 11.8025 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 2.0635 | 28 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 66.0073 | 9.9654 | 6.6237 | 66.0073 | 9.9654 | 6.6237 | 77.1633 | 11.6497 | 6.6237 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 2.0555 | 26 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 36.2581 | 9.2536 | 3.9183 | 36.2581 | 9.2536 | 3.9183 | 42.3861 | 10.8175 | 3.9183 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2028 | 63 | 63-797R | Tier-1 | Non-HFTD---1 | 3--5 | 1.9943 | 28 | 100% | 1294.9207 | 95.84% | 3.945% | 0.2104% | 61.435 | 0 | 0 | 61.435 | 0 | 53.3296 | 9.9654 | 5.3515 | 53.3296 | 9.9654 | 5.3515 | 62.3429 | 11.6497 | 5.3515 | 4.744% | 0.02549 | 0.024229 | 50800.3291 | 10671.1023 | 1938.6345 | 38190.5924 | 50910.264 | 0 | 0 | 50910.264 | 0.002026%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 1.9678 | 26 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 91.7748 | 9.2536 | 9.9178 | 91.7748 | 9.2536 | 9.9178 | 107.2858 | 10.8175 | 9.9178 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2028 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | 4--5 | 1.9662 | 38 | 100% | 4233.8665 | 96.93% | 2.943% | 0.1312% | 203.133 | 0 | 0 | 203.133 | 0 | 176.3327 | 13.5245 | 13.0381 | 176.3327 | 13.5245 | 13.0381 | 206.1349 | 15.8102 | 13.0381 | 4.798% | 0.080233 | 0.076262 | 52769.5087 | 8342.6927 | 1399.583 | 43027.233 | 52853.9991 | 0 | 0 | 52853.9991 | 0.006699%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 1.9529 | 27 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 167.4248 | 9.6095 | 17.4229 | 167.4248 | 9.6095 | 17.4229 | 195.7215 | 11.2336 | 17.4229 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 1.9524 | 23 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 61.1318 | 8.1859 | 7.468 | 61.1318 | 8.1859 | 7.468 | 71.4638 | 9.5694 | 7.468 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2028 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 1.9416 | 22 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 41.1366 | 7.8299 | 5.2538 | 41.1366 | 7.8299 | 5.2538 | 48.0892 | 9.1533 | 5.2538 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 1.9313 | 20 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 433.3562 | 7.1181 | 60.8806 | 433.3562 | 7.1181 | 60.8806 | 506.5984 | 8.3212 | 60.8806 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 1.9282 | 3 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 158.4522 | 1.0677 | 148.4023 | 158.4522 | 1.0677 | 148.4023 | 185.2324 | 1.2482 | 148.4023 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 1.9167 | 27 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 391.8645 | 9.6095 | 40.7789 | 391.8645 | 9.6095 | 40.7789 | 458.094 | 11.2336 | 40.7789 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 1.9116 | 29 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 499.4312 | 10.3213 | 48.3884 | 499.4312 | 10.3213 | 48.3884 | 583.8408 | 12.0657 | 48.3884 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 1.9075 | 26 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 19.2857 | 9.2536 | 2.0841 | 19.2857 | 9.2536 | 2.0841 | 22.5452 | 10.8175 | 2.0841 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 1.8959 | 25 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 15.7744 | 8.8977 | 1.7729 | 15.7744 | 8.8977 | 1.7729 | 18.4404 | 10.4015 | 1.7729 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2028 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | 3--5 | 1.8897 | 36 | 100% | 1585.8519 | 99.67% | 0% | 0.3254% | 78.2443 | 0 | 0 | 78.2443 | 0 | 67.9211 | 12.8126 | 5.3011 | 67.9211 | 12.8126 | 5.3011 | 79.4006 | 14.9781 | 5.3011 | 4.934% | 0.026002 | 0.024715 | 60989.6136 | 9907.2213 | 216.3013 | 50866.0909 | 60999.9476 | 0 | 0 | 60999.9476 | 0.00258%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 1.8872 | 28 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 46.2745 | 9.9654 | 4.6435 | 46.2745 | 9.9654 | 4.6435 | 54.0954 | 11.6497 | 4.6435 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 1.8794 | 27 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 6.9398 | 9.6095 | 0.72218 | 6.9398 | 9.6095 | 0.72218 | 8.1127 | 11.2336 | 0.72218 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 1.875 | 19 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 368.6686 | 6.7622 | 54.5188 | 368.6686 | 6.7622 | 54.5188 | 430.9777 | 7.9051 | 54.5188 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 1.8512 | 22 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 53.0108 | 7.8299 | 6.7703 | 53.0108 | 7.8299 | 6.7703 | 61.9702 | 9.1533 | 6.7703 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 1.8462 | 35 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 489.8651 | 12.4567 | 39.3253 | 489.8651 | 12.4567 | 39.3253 | 572.6579 | 14.5621 | 39.3253 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 1.8381 | 33 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 62.2533 | 11.7449 | 5.3004 | 62.2533 | 11.7449 | 5.3004 | 72.7748 | 13.7299 | 5.3004 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 1.8306 | 32 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 216.8136 | 11.389 | 19.0371 | 216.8136 | 11.389 | 19.0371 | 253.4576 | 13.3139 | 19.0371 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2028 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | 4--5 | 1.8306 | 28 | 100% | 2371.786 | 97.71% | 2.108% | 0.1806% | 114.7166 | 0 | 0 | 114.7166 | 0 | 99.5815 | 9.9654 | 9.9927 | 99.5815 | 9.9654 | 9.9927 | 116.4119 | 11.6497 | 9.9927 | 4.837% | 0.074138 | 0.070468 | 31991.6747 | 5091.6051 | 638.7369 | 26261.3327 | 32029.8024 | 0 | 0 | 32029.8024 | 0.003783%
2028 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 1.8025 | 10 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 142.9356 | 3.5591 | 40.161 | 142.9356 | 3.5591 | 40.161 | 167.0934 | 4.1606 | 40.161 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 1.7988 | 27 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 95.786 | 9.6095 | 9.9679 | 95.786 | 9.6095 | 9.9679 | 111.9749 | 11.2336 | 9.9679 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 1.7985 | 30 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 195.54 | 10.6772 | 18.3138 | 195.54 | 10.6772 | 18.3138 | 228.5885 | 12.4818 | 18.3138 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 1.7681 | 31 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 55.6298 | 11.0331 | 5.0421 | 55.6298 | 11.0331 | 5.0421 | 65.0319 | 12.8978 | 5.0421 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 1.7564 | 23 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 280.6799 | 8.1859 | 34.2884 | 280.6799 | 8.1859 | 34.2884 | 328.1181 | 9.5694 | 34.2884 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2028 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 1.7092 | 24 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 34.4802 | 8.5418 | 4.0367 | 34.4802 | 8.5418 | 4.0367 | 40.3077 | 9.9854 | 4.0367 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 1.6955 | 27 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 96.7369 | 9.6095 | 10.0668 | 96.7369 | 9.6095 | 10.0668 | 113.0865 | 11.2336 | 10.0668 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 1.6928 | 34 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 354.0047 | 12.1008 | 29.2546 | 354.0047 | 12.1008 | 29.2546 | 413.8355 | 14.146 | 29.2546 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 1.685 | 34 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 24.6681 | 12.1008 | 2.0385 | 24.6681 | 12.1008 | 2.0385 | 28.8373 | 14.146 | 2.0385 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 1.6768 | 29 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 55.6898 | 10.3213 | 5.3956 | 55.6898 | 10.3213 | 5.3956 | 65.102 | 12.0657 | 5.3956 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2028 | 504 | 504-40R | Tier-1 | Non-HFTD---1 | 3--5 | 1.6708 | 33 | 100% | 796.3763 | 99.35% | 0% | 0.6476% | 39.1654 | 0 | 0 | 39.1654 | 0 | 33.9981 | 11.7449 | 2.8947 | 33.9981 | 11.7449 | 2.8947 | 39.7441 | 13.7299 | 2.8947 | 4.918% | 0.025961 | 0.024676 | 30675.6364 | 4949.6837 | 226.8975 | 25499.0552 | 30685.9814 | 0 | 0 | 30685.9814 | 0.001292%
2028 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 1.6678 | 25 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 441.0941 | 8.8977 | 49.5741 | 441.0941 | 8.8977 | 49.5741 | 515.644 | 10.4015 | 49.5741 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 1.6667 | 31 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 115.3527 | 11.0331 | 10.4551 | 115.3527 | 11.0331 | 10.4551 | 134.8486 | 12.8978 | 10.4551 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 1.6595 | 28 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 352.7981 | 9.9654 | 35.4023 | 352.7981 | 9.9654 | 35.4023 | 412.425 | 11.6497 | 35.4023 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2028 | 170 | 170-410R | Tier-1 | Non-HFTD---8 | 5--1 | 1.6575 | 17 | 100% | 29.1667 | 31.01% | 45.41% | 23.57% | 0.44774 | 0 | 0 | 0.44774 | 0 | 0.38867 | 6.0504 | 0.064238 | 0.38867 | 6.0504 | 0.064238 | 0.45436 | 7.073 | 0.064238 | 1.535% | 0.10336 | 0.098244 | 282.1845 | 8.474 | 122.6089 | 151.1016 | 292.3227 | 0 | 0 | 292.3227 | 1.476e-05%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 1.6502 | 23 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 55.6541 | 8.1859 | 6.7988 | 55.6541 | 8.1859 | 6.7988 | 65.0603 | 9.5694 | 6.7988 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 1.6334 | 26 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 61.6503 | 9.2536 | 6.6623 | 61.6503 | 9.2536 | 6.6623 | 72.0699 | 10.8175 | 6.6623 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 1.633 | 20 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 62.3151 | 7.1181 | 8.7544 | 62.3151 | 7.1181 | 8.7544 | 72.8471 | 8.3212 | 8.7544 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 1.6303 | 18 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 58.6432 | 6.4063 | 9.154 | 58.6432 | 6.4063 | 9.154 | 68.5546 | 7.4891 | 9.154 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 1.6074 | 28 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 533.188 | 9.9654 | 53.504 | 533.188 | 9.9654 | 53.504 | 623.3029 | 11.6497 | 53.504 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 1.5842 | 23 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 155.2133 | 8.1859 | 18.9612 | 155.2133 | 8.1859 | 18.9612 | 181.4461 | 9.5694 | 18.9612 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 1.5812 | 24 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 159.3136 | 8.5418 | 18.6511 | 159.3136 | 8.5418 | 18.6511 | 186.2394 | 9.9854 | 18.6511 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 1.5508 | 21 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 411.5912 | 7.474 | 55.0694 | 411.5912 | 7.474 | 55.0694 | 481.1548 | 8.7372 | 55.0694 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 1.5471 | 28 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 342.5729 | 9.9654 | 34.3763 | 342.5729 | 9.9654 | 34.3763 | 400.4716 | 11.6497 | 34.3763 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 1.5464 | 26 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 16.8278 | 9.2536 | 1.8185 | 16.8278 | 9.2536 | 1.8185 | 19.6719 | 10.8175 | 1.8185 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 1.5456 | 31 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 410.2539 | 11.0331 | 37.1839 | 410.2539 | 11.0331 | 37.1839 | 479.5915 | 12.8978 | 37.1839 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 1.5412 | 19 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 129.9481 | 6.7622 | 19.2168 | 129.9481 | 6.7622 | 19.2168 | 151.9108 | 7.9051 | 19.2168 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 1.5364 | 22 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 123.2379 | 7.8299 | 15.7393 | 123.2379 | 7.8299 | 15.7393 | 144.0665 | 9.1533 | 15.7393 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 1.5139 | 26 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.1015 | 9.2536 | 1.4158 | 13.1015 | 9.2536 | 1.4158 | 15.3158 | 10.8175 | 1.4158 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 1.5062 | 21 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 67.2079 | 7.474 | 8.9922 | 67.2079 | 7.474 | 8.9922 | 78.5668 | 8.7372 | 8.9922 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 1.5037 | 20 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 79.9435 | 7.1181 | 11.231 | 79.9435 | 7.1181 | 11.231 | 93.4549 | 8.3212 | 11.231 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 1.4968 | 22 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 196.2268 | 7.8299 | 25.0611 | 196.2268 | 7.8299 | 25.0611 | 229.3913 | 9.1533 | 25.0611 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 1.4952 | 31 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 78.0879 | 11.0331 | 7.0776 | 78.0879 | 11.0331 | 7.0776 | 91.2856 | 12.8978 | 7.0776 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 1.4812 | 17 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 50.7035 | 6.0504 | 8.3802 | 50.7035 | 6.0504 | 8.3802 | 59.2729 | 7.073 | 8.3802 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 1.4789 | 19 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 216.3509 | 6.7622 | 31.994 | 216.3509 | 6.7622 | 31.994 | 252.9167 | 7.9051 | 31.994 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 1.4762 | 27 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 68.7279 | 9.6095 | 7.1521 | 68.7279 | 9.6095 | 7.1521 | 80.3437 | 11.2336 | 7.1521 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2028 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 1.4725 | 22 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 114.3559 | 7.8299 | 14.6049 | 114.3559 | 7.8299 | 14.6049 | 133.6834 | 9.1533 | 14.6049 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 1.4649 | 18 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.1658 | 6.4063 | 0.80636 | 5.1658 | 6.4063 | 0.80636 | 6.0389 | 7.4891 | 0.80636 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 1.4572 | 19 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 147.3159 | 6.7622 | 21.7851 | 147.3159 | 6.7622 | 21.7851 | 172.214 | 7.9051 | 21.7851 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 1.4508 | 26 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 22.0588 | 9.2536 | 2.3838 | 22.0588 | 9.2536 | 2.3838 | 25.787 | 10.8175 | 2.3838 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 1.4439 | 18 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 90.1294 | 6.4063 | 14.0688 | 90.1294 | 6.4063 | 14.0688 | 105.3623 | 7.4891 | 14.0688 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2028 | 474 | 474-22AE | Tier-1 | Non-HFTD---1 | 4--5 | 1.4235 | 22 | 100% | 6435.9834 | 99.89% | 0% | 0.1146% | 318.2162 | 0 | 0 | 318.2162 | 0 | 276.2324 | 7.8299 | 35.279 | 276.2324 | 7.8299 | 35.279 | 322.9188 | 9.1533 | 35.279 | 4.944% | 0.046635 | 0.044327 | 138007.5774 | 24328.5202 | 121.2373 | 113557.8199 | 138015.8115 | 0 | 0 | 138015.8115 | 0.01049%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 1.4146 | 22 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 49.9494 | 7.8299 | 6.3793 | 49.9494 | 7.8299 | 6.3793 | 58.3914 | 9.1533 | 6.3793 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2028 | 288 | 288-18 | Tier-1 | Non-HFTD---1 | 3--5 | 1.41 | 20 | 100% | 1717.8671 | 96.12% | 3.649% | 0.229% | 81.7367 | 0 | 0 | 81.7367 | 0 | 70.9528 | 7.1181 | 9.9679 | 70.9528 | 7.1181 | 9.9679 | 82.9446 | 8.3212 | 9.9679 | 4.758% | 0.026137 | 0.024843 | 65724.9856 | 11143.2146 | 2230.6061 | 52351.1649 | 65857.7245 | 0 | 0 | 65857.7245 | 0.002695%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 1.3985 | 16 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 58.9313 | 5.6945 | 10.3488 | 58.9313 | 5.6945 | 10.3488 | 68.8914 | 6.6569 | 10.3488 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 1.3827 | 24 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 336.3948 | 8.5418 | 39.3824 | 336.3948 | 8.5418 | 39.3824 | 393.2494 | 9.9854 | 39.3824 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 1.3633 | 22 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 27.2182 | 7.8299 | 3.4762 | 27.2182 | 7.8299 | 3.4762 | 31.8184 | 9.1533 | 3.4762 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 1.3484 | 20 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 555.0452 | 7.1181 | 77.9762 | 555.0452 | 7.1181 | 77.9762 | 648.8541 | 8.3212 | 77.9762 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 1.3358 | 21 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 87.4066 | 7.474 | 11.6947 | 87.4066 | 7.474 | 11.6947 | 102.1793 | 8.7372 | 11.6947 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 1.3358 | 23 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 60.5501 | 8.1859 | 7.3969 | 60.5501 | 8.1859 | 7.3969 | 70.7837 | 9.5694 | 7.3969 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 1.3275 | 20 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 297.6475 | 7.1181 | 41.8154 | 297.6475 | 7.1181 | 41.8154 | 347.9533 | 8.3212 | 41.8154 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 1.3154 | 22 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 64.3998 | 7.8299 | 8.2248 | 64.3998 | 7.8299 | 8.2248 | 75.2841 | 9.1533 | 8.2248 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 1.3093 | 20 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 55.5815 | 7.1181 | 7.8084 | 55.5815 | 7.1181 | 7.8084 | 64.9754 | 8.3212 | 7.8084 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2028 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 1.3038 | 13 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 45.8033 | 4.6268 | 9.8996 | 45.8033 | 4.6268 | 9.8996 | 53.5446 | 5.4088 | 9.8996 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 1.3021 | 20 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 185.2886 | 7.1181 | 26.0305 | 185.2886 | 7.1181 | 26.0305 | 216.6045 | 8.3212 | 26.0305 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 1.2948 | 21 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 284.0073 | 7.474 | 37.9992 | 284.0073 | 7.474 | 37.9992 | 332.0078 | 8.7372 | 37.9992 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 1.2618 | 18 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 15.6819 | 6.4063 | 2.4479 | 15.6819 | 6.4063 | 2.4479 | 18.3323 | 7.4891 | 2.4479 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2028 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 1.2605 | 12 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 20.1346 | 4.2709 | 4.7144 | 20.1346 | 4.2709 | 4.7144 | 23.5376 | 4.9927 | 4.7144 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 1.2591 | 22 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 30.6457 | 7.8299 | 3.9139 | 30.6457 | 7.8299 | 3.9139 | 35.8252 | 9.1533 | 3.9139 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 1.257 | 18 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 126.6489 | 6.4063 | 19.7694 | 126.6489 | 6.4063 | 19.7694 | 148.054 | 7.4891 | 19.7694 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2028 | 172 | 172-630R | Tier-1 | Non-HFTD---6 | 4--2 | 1.2534 | 10 | 100% | 66.3107 | 6.519% | 90.48% | 2.997% | 0.21398 | 0 | 0 | 0.21398 | 0 | 0.18575 | 3.5591 | 0.052191 | 0.18575 | 3.5591 | 0.052191 | 0.21715 | 4.1606 | 0.052191 | 0.3227% | 0.053137 | 0.050507 | 1247.9203 | 10.8427 | 1030.4852 | 206.5924 | 1308.6726 | 0 | 0 | 1308.6726 | 7.056e-06%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 1.2484 | 24 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 714.7921 | 8.5418 | 83.682 | 714.7921 | 8.5418 | 83.682 | 835.6001 | 9.9854 | 83.682 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2028 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | 4--5 | 1.2229 | 18 | 100% | 2117.8574 | 97.53% | 2.33% | 0.1416% | 102.2432 | 0 | 0 | 102.2432 | 0 | 88.7538 | 6.4063 | 13.8541 | 88.7538 | 6.4063 | 13.8541 | 103.7542 | 7.4891 | 13.8541 | 4.828% | 0.067442 | 0.064104 | 31402.4615 | 4988.1224 | 677.5642 | 25736.7748 | 31442.8757 | 0 | 0 | 31442.8757 | 0.003372%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 1.1787 | 15 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 191.5196 | 5.3386 | 35.8745 | 191.5196 | 5.3386 | 35.8745 | 223.8887 | 6.2409 | 35.8745 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2028 | 206 | 206-974 | Tier-1 | Non-HFTD---1 | 4--5 | 1.1741 | 24 | 100% | 1943.6719 | 99.69% | 0% | 0.3117% | 95.9119 | 0 | 0 | 95.9119 | 0 | 83.2578 | 8.5418 | 9.7471 | 83.2578 | 8.5418 | 9.7471 | 97.3293 | 9.9854 | 9.7471 | 4.935% | 0.028958 | 0.027525 | 67119.4507 | 10907.8418 | 251.1395 | 55960.4695 | 67130.3452 | 0 | 0 | 67130.3452 | 0.003163%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 1.1689 | 13 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 218.3892 | 4.6268 | 47.2011 | 218.3892 | 4.6268 | 47.2011 | 255.2995 | 5.4088 | 47.2011 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 1.1689 | 22 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 185.4129 | 7.8299 | 23.68 | 185.4129 | 7.8299 | 23.68 | 216.7498 | 9.1533 | 23.68 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 1.1678 | 16 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 59.5336 | 5.6945 | 10.4546 | 59.5336 | 5.6945 | 10.4546 | 69.5955 | 6.6569 | 10.4546 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 1.1572 | 12 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 33.2772 | 4.2709 | 7.7917 | 33.2772 | 4.2709 | 7.7917 | 38.9015 | 4.9927 | 7.7917 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 1.1071 | 22 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 161.7017 | 7.8299 | 20.6517 | 161.7017 | 7.8299 | 20.6517 | 189.0311 | 9.1533 | 20.6517 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2028 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 1.0878 | 16 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 220.4842 | 5.6945 | 38.7187 | 220.4842 | 5.6945 | 38.7187 | 257.7485 | 6.6569 | 38.7187 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2028 | BN1 | CB BN1 | Tier-1 | Non-HFTD---4 | 4--4 | 1.0878 | 22 | 100% | 173.8031 | 96.37% | 0% | 3.629% | 8.291 | 0 | 0 | 8.291 | 0 | 7.1971 | 7.8299 | 0.91918 | 7.1971 | 7.8299 | 0.91918 | 8.4135 | 9.1533 | 0.91918 | 4.77% | 0.028851 | 0.027423 | 6024.1621 | 939.3966 | 90.5041 | 4994.2615 | 6035.548 | 0 | 0 | 6035.548 | 0.0002734%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 1.0864 | 17 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 18.2006 | 6.0504 | 3.0082 | 18.2006 | 6.0504 | 3.0082 | 21.2767 | 7.073 | 3.0082 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 1.0771 | 18 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 238.4801 | 6.4063 | 37.2257 | 238.4801 | 6.4063 | 37.2257 | 278.7859 | 7.4891 | 37.2257 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 1.0615 | 5 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 244.9741 | 1.7795 | 137.662 | 244.9741 | 1.7795 | 137.662 | 286.3776 | 2.0803 | 137.662 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 1.0168 | 17 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 107.8587 | 6.0504 | 17.8267 | 107.8587 | 6.0504 | 17.8267 | 126.0881 | 7.073 | 17.8267 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 1.0038 | 17 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 138.9965 | 6.0504 | 22.9731 | 138.9965 | 6.0504 | 22.9731 | 162.4885 | 7.073 | 22.9731 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2028 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 0.9777 | 11 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.2511 | 3.915 | 2.8739 | 11.2511 | 3.915 | 2.8739 | 13.1527 | 4.5766 | 2.8739 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 0.97273 | 16 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 166.611 | 5.6945 | 29.2582 | 166.611 | 5.6945 | 29.2582 | 194.7701 | 6.6569 | 29.2582 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 0.96847 | 13 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 307.9689 | 4.6268 | 66.5621 | 307.9689 | 4.6268 | 66.5621 | 360.0191 | 5.4088 | 66.5621 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 0.96776 | 19 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 180.3315 | 6.7622 | 26.6675 | 180.3315 | 6.7622 | 26.6675 | 210.8095 | 7.9051 | 26.6675 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2028 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 0.96758 | 16 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 139.9872 | 5.6945 | 24.5828 | 139.9872 | 5.6945 | 24.5828 | 163.6466 | 6.6569 | 24.5828 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 0.94539 | 16 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 58.3493 | 5.6945 | 10.2466 | 58.3493 | 5.6945 | 10.2466 | 68.211 | 6.6569 | 10.2466 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 0.93847 | 15 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 186.0759 | 5.3386 | 34.8548 | 186.0759 | 5.3386 | 34.8548 | 217.5249 | 6.2409 | 34.8548 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2028 | 66 | CB 66 | Tier-1 | Non-HFTD---1 | 4--5 | 0.93509 | 16 | 100% | 917.8674 | 93.46% | 5.958% | 0.5799% | 42.4641 | 0 | 0 | 42.4641 | 0 | 36.8616 | 5.6945 | 6.4732 | 36.8616 | 5.6945 | 6.4732 | 43.0917 | 6.6569 | 6.4732 | 4.626% | 0.036366 | 0.034566 | 25239.7123 | 4508.1978 | 1664.2037 | 19067.3107 | 25325.6439 | 0 | 0 | 25325.6439 | 0.0014%
2028 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | 3--5 | 0.93119 | 21 | 100% | 1424.1907 | 99.61% | 0% | 0.3928% | 70.2205 | 0 | 0 | 70.2205 | 0 | 60.956 | 7.474 | 8.1557 | 60.956 | 7.474 | 8.1557 | 71.2583 | 8.7372 | 8.1557 | 4.931% | 0.028304 | 0.026903 | 50317.6471 | 8145.1206 | 368.3302 | 41804.1963 | 50327.94 | 0 | 0 | 50327.94 | 0.002316%
2028 | 170 | 170-46 | Tier-1 | Non-HFTD---6 | 5--2 | 0.93066 | 12 | 100% | 63.3107 | 39.69% | 47.72% | 12.59% | 1.2437 | 0 | 0 | 1.2437 | 0 | 1.0796 | 4.2709 | 0.25279 | 1.0796 | 4.2709 | 0.25279 | 1.2621 | 4.9927 | 0.25279 | 1.964% | 0.099838 | 0.094896 | 634.1343 | 13.2723 | 434.6906 | 186.1714 | 654.0524 | 0 | 0 | 654.0524 | 4.101e-05%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 0.90864 | 10 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 15.9736 | 3.5591 | 4.4881 | 15.9736 | 3.5591 | 4.4881 | 18.6733 | 4.1606 | 4.4881 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 0.89089 | 13 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 127.5811 | 4.6268 | 27.5744 | 127.5811 | 4.6268 | 27.5744 | 149.1437 | 5.4088 | 27.5744 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 0.88609 | 15 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 222.4503 | 5.3386 | 41.6683 | 222.4503 | 5.3386 | 41.6683 | 260.047 | 6.2409 | 41.6683 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 0.88361 | 16 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 86.4204 | 5.6945 | 15.1761 | 86.4204 | 5.6945 | 15.1761 | 101.0265 | 6.6569 | 15.1761 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 0.8829 | 16 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 21.5211 | 5.6945 | 3.7793 | 21.5211 | 5.6945 | 3.7793 | 25.1584 | 6.6569 | 3.7793 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2028 | 591 | CB 591 | Tier-1 | Non-HFTD---1 | 4--4 | 0.87881 | 15 | 100% | 1060.5472 | 90.24% | 9.188% | 0.5739% | 47.3724 | 0 | 0 | 47.3724 | 0 | 41.1223 | 5.3386 | 7.7028 | 41.1223 | 5.3386 | 7.7028 | 48.0725 | 6.2409 | 7.7028 | 4.467% | 0.066615 | 0.063317 | 15920.6417 | 3763.87 | 1847.5145 | 10309.2572 | 16001.5783 | 0 | 0 | 16001.5783 | 0.001562%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 0.8568 | 7 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 87.8869 | 2.4913 | 35.2769 | 87.8869 | 2.4913 | 35.2769 | 102.7408 | 2.9124 | 35.2769 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 0.85023 | 11 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 276.8533 | 3.915 | 70.7165 | 276.8533 | 3.915 | 70.7165 | 323.6447 | 4.5766 | 70.7165 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 0.84757 | 14 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 29.252 | 4.9827 | 5.8707 | 29.252 | 4.9827 | 5.8707 | 34.1959 | 5.8248 | 5.8707 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 0.8394 | 13 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 19.5575 | 4.6268 | 4.227 | 19.5575 | 4.6268 | 4.227 | 22.8629 | 5.4088 | 4.227 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 0.83354 | 17 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 73.0958 | 6.0504 | 12.0811 | 73.0958 | 6.0504 | 12.0811 | 85.4498 | 7.073 | 12.0811 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 0.83088 | 20 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 184.5979 | 7.1181 | 25.9335 | 184.5979 | 7.1181 | 25.9335 | 215.797 | 8.3212 | 25.9335 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 0.822 | 14 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 103.7927 | 4.9827 | 20.8306 | 103.7927 | 4.9827 | 20.8306 | 121.3349 | 5.8248 | 20.8306 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 0.81969 | 14 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 215.2532 | 4.9827 | 43.2002 | 215.2532 | 4.9827 | 43.2002 | 251.6334 | 5.8248 | 43.2002 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 0.81952 | 14 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 19.4933 | 4.9827 | 3.9122 | 19.4933 | 4.9827 | 3.9122 | 22.7878 | 5.8248 | 3.9122 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 0.81472 | 13 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 31.153 | 4.6268 | 6.7332 | 31.153 | 4.6268 | 6.7332 | 36.4183 | 5.4088 | 6.7332 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 0.8007 | 11 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 35.1509 | 3.915 | 8.9786 | 35.1509 | 3.915 | 8.9786 | 41.0917 | 4.5766 | 8.9786 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2028 | MV1 | CB MV1 | Tier-1 | Non-HFTD---4 | 3--4 | 0.78685 | 16 | 100% | 150.3384 | 97.79% | 0% | 2.21% | 7.2773 | 0 | 0 | 7.2773 | 0 | 6.3171 | 5.6945 | 1.1093 | 6.3171 | 5.6945 | 1.1093 | 7.3848 | 6.6569 | 1.1093 | 4.841% | 0.014765 | 0.014034 | 10182.3567 | 1618.5344 | 97.4794 | 8466.3429 | 10194.0779 | 0 | 0 | 10194.0779 | 0.00024%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 0.77975 | 14 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 173.5599 | 4.9827 | 34.8325 | 173.5599 | 4.9827 | 34.8325 | 202.8935 | 5.8248 | 34.8325 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 0.75773 | 9 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.577 | 3.2032 | 2.6777 | 8.577 | 3.2032 | 2.6777 | 10.0266 | 3.7445 | 2.6777 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2028 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 0.74744 | 15 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 13.6308 | 5.3386 | 2.5533 | 13.6308 | 5.3386 | 2.5533 | 15.9345 | 6.2409 | 2.5533 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2028 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | 5--4 | 0.68938 | 10 | 100% | 1005.6854 | 94.09% | 5.81% | 0.1042% | 46.8371 | 0 | 0 | 46.8371 | 0 | 40.6576 | 3.5591 | 11.4237 | 40.6576 | 3.5591 | 11.4237 | 47.5292 | 4.1606 | 11.4237 | 4.657% | 0.097832 | 0.09299 | 10279.6968 | 1573.4563 | 574.8933 | 8131.3471 | 10311.3601 | 0 | 0 | 10311.3601 | 0.001545%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 0.68654 | 12 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 145.4142 | 4.2709 | 34.0478 | 145.4142 | 4.2709 | 34.0478 | 169.9908 | 4.9927 | 34.0478 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 0.68512 | 8 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.4094 | 2.8473 | 1.5486 | 4.4094 | 2.8473 | 1.5486 | 5.1546 | 3.3285 | 1.5486 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 0.65867 | 14 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 155.4182 | 4.9827 | 31.1916 | 155.4182 | 4.9827 | 31.1916 | 181.6856 | 5.8248 | 31.1916 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 0.63221 | 9 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 33.5626 | 3.2032 | 10.478 | 33.5626 | 3.2032 | 10.478 | 39.2351 | 3.7445 | 10.478 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 0.63062 | 7 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 10.9026 | 2.4913 | 4.3762 | 10.9026 | 2.4913 | 4.3762 | 12.7452 | 2.9124 | 4.3762 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2028 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 0.62174 | 9 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 9.1054 | 3.2032 | 2.8426 | 9.1054 | 3.2032 | 2.8426 | 10.6443 | 3.7445 | 2.8426 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2028 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 0.62121 | 10 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 27.3601 | 3.5591 | 7.6874 | 27.3601 | 3.5591 | 7.6874 | 31.9842 | 4.1606 | 7.6874 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 0.61091 | 12 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 21.7739 | 4.2709 | 5.0982 | 21.7739 | 4.2709 | 5.0982 | 25.454 | 4.9927 | 5.0982 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 0.61038 | 14 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 107.4458 | 4.9827 | 21.5638 | 107.4458 | 4.9827 | 21.5638 | 125.6054 | 5.8248 | 21.5638 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2028 | 307 | CB 307 | Tier-1 | Non-HFTD---1 | 4--4 | 0.60043 | 8 | 100% | 601.8674 | 89.73% | 10.15% | 0.1197% | 26.7338 | 0 | 0 | 26.7338 | 0 | 23.2067 | 2.8473 | 8.1506 | 23.2067 | 2.8473 | 8.1506 | 27.1289 | 3.3285 | 8.1506 | 4.442% | 0.056404 | 0.053612 | 10670.688 | 1554.5631 | 980.4133 | 8135.7116 | 10727.7391 | 0 | 0 | 10727.7391 | 0.0008816%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 0.59919 | 7 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 165.8433 | 2.4913 | 66.5677 | 165.8433 | 2.4913 | 66.5677 | 193.8727 | 2.9124 | 66.5677 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 0.59493 | 8 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 181.5394 | 2.8473 | 63.7595 | 181.5394 | 2.8473 | 63.7595 | 212.2217 | 3.3285 | 63.7595 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.58517 | 6 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 91.914 | 2.1354 | 43.0422 | 91.914 | 2.1354 | 43.0422 | 107.4485 | 2.4964 | 43.0422 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 0.56439 | 8 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.4162 | 2.8473 | 3.6583 | 10.4162 | 2.8473 | 3.6583 | 12.1767 | 3.3285 | 3.6583 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.55871 | 8 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 75.8931 | 2.8473 | 26.6548 | 75.8931 | 2.8473 | 26.6548 | 88.7199 | 3.3285 | 26.6548 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.55854 | 7 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 154.3856 | 2.4913 | 61.9687 | 154.3856 | 2.4913 | 61.9687 | 180.4785 | 2.9124 | 61.9687 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 0.55836 | 9 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 107.356 | 3.2032 | 33.5157 | 107.356 | 3.2032 | 33.5157 | 125.5004 | 3.7445 | 33.5157 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 0.54487 | 11 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 94.2008 | 3.915 | 24.0617 | 94.2008 | 3.915 | 24.0617 | 110.1218 | 4.5766 | 24.0617 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 0.53847 | 11 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 18.6264 | 3.915 | 4.7577 | 18.6264 | 3.915 | 4.7577 | 21.7744 | 4.5766 | 4.7577 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 0.53244 | 7 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 25.9816 | 2.4913 | 10.4287 | 25.9816 | 2.4913 | 10.4287 | 30.3728 | 2.9124 | 10.4287 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 0.52285 | 10 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 17.6223 | 3.5591 | 4.9514 | 17.6223 | 3.5591 | 4.9514 | 20.6007 | 4.1606 | 4.9514 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 0.51593 | 8 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 6.8723 | 2.8473 | 2.4136 | 6.8723 | 2.8473 | 2.4136 | 8.0338 | 3.3285 | 2.4136 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2028 | 455 | CB 455 | Tier-1 | Non-HFTD---1 | 3--5 | 0.50847 | 9 | 100% | 628.6508 | 99.14% | 0% | 0.8628% | 30.8497 | 0 | 0 | 30.8497 | 0 | 26.7796 | 3.2032 | 8.3604 | 26.7796 | 3.2032 | 8.3604 | 31.3056 | 3.7445 | 8.3604 | 4.907% | 0.025428 | 0.024169 | 24722.9716 | 4556.7235 | 179.5676 | 19986.6805 | 24734.0802 | 0 | 0 | 24734.0802 | 0.001017%
2028 | 171 | 171-704R | Tier-1 | Non-HFTD---6 | 4--2 | 0.50261 | 7 | 100% | 80.6143 | 61.35% | 34.31% | 4.34% | 2.4483 | 0 | 0 | 2.4483 | 0 | 2.1253 | 2.4913 | 0.85307 | 2.1253 | 2.4913 | 0.85307 | 2.4845 | 2.9124 | 0.85307 | 3.037% | 0.048088 | 0.045707 | 1676.4044 | 165.028 | 536.4334 | 974.9431 | 1710.1431 | 0 | 0 | 1710.1431 | 8.074e-05%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 0.47847 | 7 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 24.4415 | 2.4913 | 9.8106 | 24.4415 | 2.4913 | 9.8106 | 28.5724 | 2.9124 | 9.8106 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 0.46977 | 8 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 117.6384 | 2.8473 | 41.3164 | 117.6384 | 2.8473 | 41.3164 | 137.5206 | 3.3285 | 41.3164 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 0.46444 | 7 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.128 | 2.4913 | 1.6569 | 4.128 | 2.4913 | 1.6569 | 4.8257 | 2.9124 | 1.6569 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2028 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 0.45645 | 4 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 167.5586 | 1.4236 | 117.6984 | 167.5586 | 1.4236 | 117.6984 | 195.878 | 1.6642 | 117.6984 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 0.43976 | 6 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 25.9573 | 2.1354 | 12.1555 | 25.9573 | 2.1354 | 12.1555 | 30.3444 | 2.4964 | 12.1555 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 0.4387 | 7 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 31.3708 | 2.4913 | 12.5919 | 31.3708 | 2.4913 | 12.5919 | 36.6728 | 2.9124 | 12.5919 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.43106 | 10 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 4.5649 | 3.5591 | 1.2826 | 4.5649 | 3.5591 | 1.2826 | 5.3364 | 4.1606 | 1.2826 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.42006 | 4 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 2.8676 | 1.4236 | 2.0143 | 2.8676 | 1.4236 | 2.0143 | 3.3522 | 1.6642 | 2.0143 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2028 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.4197 | 2 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 55.7749 | 0.71181 | 78.3561 | 55.7749 | 0.71181 | 78.3561 | 65.2015 | 0.83212 | 78.3561 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 0.41562 | 7 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 62.7303 | 2.4913 | 25.1793 | 62.7303 | 2.4913 | 25.1793 | 73.3324 | 2.9124 | 25.1793 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 0.41526 | 4 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 109.5158 | 1.4236 | 76.9273 | 109.5158 | 1.4236 | 76.9273 | 128.0252 | 1.6642 | 76.9273 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2028 | 412 | CB 412 | Tier-1 | Non-HFTD---1 | 4--5 | 0.41437 | 7 | 100% | 1311.9921 | 88.37% | 10.81% | 0.8215% | 57.392 | 0 | 0 | 57.392 | 0 | 49.82 | 2.4913 | 19.9972 | 49.82 | 2.4913 | 19.9972 | 58.2402 | 2.9124 | 19.9972 | 4.374% | 0.071433 | 0.067897 | 18366.6483 | 2615.4927 | 2100.6109 | 13650.5447 | 18477.8687 | 0 | 0 | 18477.8687 | 0.001893%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 0.41331 | 7 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 26.2058 | 2.4913 | 10.5187 | 26.2058 | 2.4913 | 10.5187 | 30.6349 | 2.9124 | 10.5187 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 0.40443 | 7 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 86.9507 | 2.4913 | 34.9011 | 86.9507 | 2.4913 | 34.9011 | 101.6464 | 2.9124 | 34.9011 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 0.39893 | 8 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 17.7423 | 2.8473 | 6.2314 | 17.7423 | 2.8473 | 6.2314 | 20.7409 | 3.3285 | 6.2314 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 0.39698 | 6 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 56.4831 | 2.1354 | 26.4503 | 56.4831 | 2.1354 | 26.4503 | 66.0294 | 2.4964 | 26.4503 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 0.38686 | 7 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 54.8409 | 2.4913 | 22.0126 | 54.8409 | 2.4913 | 22.0126 | 64.1096 | 2.9124 | 22.0126 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 0.38437 | 5 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 91.8692 | 1.7795 | 51.6255 | 91.8692 | 1.7795 | 51.6255 | 107.3962 | 2.0803 | 51.6255 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 0.3826 | 8 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 133.2569 | 2.8473 | 46.8019 | 133.2569 | 2.8473 | 46.8019 | 155.7788 | 3.3285 | 46.8019 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 0.37585 | 7 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 83.1107 | 2.4913 | 33.3597 | 83.1107 | 2.4913 | 33.3597 | 97.1573 | 2.9124 | 33.3597 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 0.35756 | 6 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 22.8477 | 2.1354 | 10.6993 | 22.8477 | 2.1354 | 10.6993 | 26.7092 | 2.4964 | 10.6993 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 0.35561 | 10 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.0984 | 3.5591 | 0.87057 | 3.0984 | 3.5591 | 0.87057 | 3.6221 | 4.1606 | 0.87057 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 0.35525 | 2 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 221.4077 | 0.71181 | 311.0474 | 221.4077 | 0.71181 | 311.0474 | 258.8282 | 0.83212 | 311.0474 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2028 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 0.34957 | 9 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 85.4412 | 3.2032 | 26.674 | 85.4412 | 3.2032 | 26.674 | 99.8817 | 3.7445 | 26.674 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2028 | 206 | 206-963F | Tier-1 | Non-HFTD---1 | 3--5 | 0.34283 | 6 | 100% | 308.0085 | 98.9% | 0% | 1.099% | 15.0788 | 0 | 0 | 15.0788 | 0 | 13.0894 | 2.1354 | 6.1296 | 13.0894 | 2.1354 | 6.1296 | 15.3016 | 2.4964 | 6.1296 | 4.896% | 0.014856 | 0.014121 | 20732.6556 | 3229.8813 | 785.6991 | 16717.0751 | 20744.5251 | 0 | 0 | 20744.5251 | 0.0004972%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 0.33945 | 7 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 9.6593 | 2.4913 | 3.8771 | 9.6593 | 2.4913 | 3.8771 | 11.2918 | 2.9124 | 3.8771 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2028 | 553 | 553-27R | Tier-1 | Non-HFTD---1 | 4--4 | 0.33928 | 7 | 100% | 504.2652 | 97.83% | 0% | 2.166% | 24.4204 | 0 | 0 | 24.4204 | 0 | 21.1985 | 2.4913 | 8.5089 | 21.1985 | 2.4913 | 8.5089 | 24.7813 | 2.9124 | 8.5089 | 4.843% | 0.054721 | 0.052013 | 9215.1363 | 1913.347 | 158.4888 | 7143.3005 | 9225.5318 | 0 | 0 | 9225.5318 | 0.0008053%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.33644 | 5 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 59.3317 | 1.7795 | 33.3411 | 59.3317 | 1.7795 | 33.3411 | 69.3594 | 2.0803 | 33.3411 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2028 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | 3--5 | 0.33608 | 7 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 13.1668 | 0 | 0 | 13.1668 | 0 | 11.4296 | 2.4913 | 4.5877 | 11.4296 | 2.4913 | 4.5877 | 13.3613 | 2.9124 | 4.5877 | 4.021% | 0.015736 | 0.014957 | 20808.6476 | 4091.2697 | 3467.4094 | 13249.9684 | 21012.0249 | 0 | 0 | 21012.0249 | 0.0004342%
2028 | 471 | CB 471 | Tier-1 | Non-HFTD---1 | 4--5 | 0.33537 | 7 | 100% | 3808.7328 | 99.83% | 0% | 0.1692% | 188.2133 | 0 | 0 | 188.2133 | 0 | 163.3814 | 2.4913 | 65.5795 | 163.3814 | 2.4913 | 65.5795 | 190.9947 | 2.9124 | 65.5795 | 4.942% | 0.030567 | 0.029054 | 124601.1385 | 20145.8945 | 297.3105 | 104157.9336 | 124612.117 | 0 | 0 | 124612.117 | 0.006207%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.33288 | 7 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 53.258 | 2.4913 | 21.3772 | 53.258 | 2.4913 | 21.3772 | 62.2592 | 2.9124 | 21.3772 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2028 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.32987 | 5 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 90.3172 | 1.7795 | 50.7533 | 90.3172 | 1.7795 | 50.7533 | 105.5818 | 2.0803 | 50.7533 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 0.32365 | 5 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.7715 | 1.7795 | 0.9955 | 1.7715 | 1.7795 | 0.9955 | 2.0709 | 2.0803 | 0.9955 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2028 | 170 | 170-3R | Tier-1 | Non-HFTD---3 | 4--3 | 0.32312 | 5 | 100% | 134.6076 | 71.34% | 24.69% | 3.975% | 4.7533 | 0 | 0 | 4.7533 | 0 | 4.1262 | 1.7795 | 2.3187 | 4.1262 | 1.7795 | 2.3187 | 4.8235 | 2.0803 | 2.3187 | 3.531% | 0.059016 | 0.056095 | 2280.8503 | 250.0057 | 616.1021 | 1414.7425 | 2314.8955 | 0 | 0 | 2314.8955 | 0.0001567%
2028 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 0.32063 | 5 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 29.6034 | 1.7795 | 16.6355 | 29.6034 | 1.7795 | 16.6355 | 34.6067 | 2.0803 | 16.6355 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 0.3114 | 8 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 83.1383 | 2.8473 | 29.1995 | 83.1383 | 2.8473 | 29.1995 | 97.1896 | 3.3285 | 29.1995 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 0.30767 | 4 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 208.5089 | 1.4236 | 146.4632 | 208.5089 | 1.4236 | 146.4632 | 243.7493 | 1.6642 | 146.4632 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2028 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 0.3027 | 4 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 13.5581 | 1.4236 | 9.5237 | 13.5581 | 1.4236 | 9.5237 | 15.8496 | 1.6642 | 9.5237 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 0.30253 | 4 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 256.5911 | 1.4236 | 180.2376 | 256.5911 | 1.4236 | 180.2376 | 299.9579 | 1.6642 | 180.2376 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 0.30111 | 4 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 50.2897 | 1.4236 | 35.325 | 50.2897 | 1.4236 | 35.325 | 58.7892 | 1.6642 | 35.325 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2028 | 387 | CB 387 | Tier-1 | Non-HFTD---2 | 4--4 | 0.30022 | 6 | 100% | 522.65 | 70.14% | 28.94% | 0.9137% | 18.1467 | 0 | 0 | 18.1467 | 0 | 15.7525 | 2.1354 | 7.3767 | 15.7525 | 2.1354 | 7.3767 | 18.4149 | 2.4964 | 7.3767 | 3.472% | 0.067633 | 0.064286 | 7727.6908 | 947.907 | 2193.816 | 4585.9679 | 7847.8494 | 0 | 0 | 7847.8494 | 0.0005984%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 0.29276 | 6 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 31.5786 | 2.1354 | 14.7879 | 31.5786 | 2.1354 | 14.7879 | 36.9157 | 2.4964 | 14.7879 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2028 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 0.29081 | 5 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.123 | 1.7795 | 1.7549 | 3.123 | 1.7795 | 1.7549 | 3.6508 | 2.0803 | 1.7549 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 0.283 | 6 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 11.4677 | 2.1354 | 5.3702 | 11.4677 | 2.1354 | 5.3702 | 13.4059 | 2.4964 | 5.3702 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 0.26649 | 3 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 24.868 | 1.0677 | 23.2908 | 24.868 | 1.0677 | 23.2908 | 29.071 | 1.2482 | 23.2908 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2028 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 0.26151 | 5 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 4.7628 | 1.7795 | 2.6764 | 4.7628 | 1.7795 | 2.6764 | 5.5678 | 2.0803 | 2.6764 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2028 | 172 | 172-615R | Tier-1 | Non-HFTD---6 | 4--2 | 0.25938 | 5 | 100% | 65.0211 | 31.38% | 63.15% | 5.469% | 1.0101 | 0 | 0 | 1.0101 | 0 | 0.8768 | 1.7795 | 0.49271 | 0.8768 | 1.7795 | 0.49271 | 1.025 | 2.0803 | 0.49271 | 1.553% | 0.053579 | 0.050927 | 1213.547 | 17.4537 | 970.9978 | 225.0954 | 1256.9124 | 0 | 0 | 1256.9124 | 3.331e-05%
2028 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.25477 | 2 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 7.3264 | 0.71181 | 10.2925 | 7.3264 | 0.71181 | 10.2925 | 8.5646 | 0.83212 | 10.2925 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.2521 | 4 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.4383 | 1.4236 | 3.1176 | 4.4383 | 1.4236 | 3.1176 | 5.1885 | 1.6642 | 3.1176 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2028 | 410 | 410-50R | Tier-1 | Non-HFTD---1 | 4--5 | 0.24749 | 4 | 100% | 1314.3326 | 99.38% | 0% | 0.6151% | 64.6593 | 0 | 0 | 64.6593 | 0 | 56.1285 | 1.4236 | 39.4264 | 56.1285 | 1.4236 | 39.4264 | 65.6148 | 1.6642 | 39.4264 | 4.92% | 0.044038 | 0.041858 | 29845.69 | 7721.7282 | 133.8501 | 21990.1116 | 29855.2499 | 0 | 0 | 29855.2499 | 0.002132%
2028 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.24252 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 4.9295 | 1.7795 | 2.7701 | 4.9295 | 1.7795 | 2.7701 | 5.7626 | 2.0803 | 2.7701 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.2379 | 4 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 30.3569 | 1.4236 | 21.3236 | 30.3569 | 1.4236 | 21.3236 | 35.4876 | 1.6642 | 21.3236 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2028 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | 4--5 | 0.23648 | 3 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 37.535 | 0 | 0 | 37.535 | 0 | 32.5828 | 1.0677 | 30.5162 | 32.5828 | 1.0677 | 30.5162 | 38.0897 | 1.2482 | 30.5162 | 3.124% | 0.042337 | 0.040241 | 28377.3086 | 3599.9822 | 10019.8495 | 14757.4769 | 28922.3867 | 0 | 0 | 28922.3867 | 0.001238%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.23417 | 5 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 16.6154 | 1.7795 | 9.3369 | 16.6154 | 1.7795 | 9.3369 | 19.4236 | 2.0803 | 9.3369 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2028 | 306 | CB 306 | Tier-1 | Non-HFTD---1 | 4--4 | 0.234 | 6 | 100% | 737.4997 | 97.09% | 2.802% | 0.1119% | 35.4424 | 0 | 0 | 35.4424 | 0 | 30.7663 | 2.1354 | 14.4075 | 30.7663 | 2.1354 | 14.4075 | 35.9662 | 2.4964 | 14.4075 | 4.806% | 0.057753 | 0.054894 | 12769.9388 | 2020.535 | 320.1958 | 10429.208 | 12789.3181 | 0 | 0 | 12789.3181 | 0.001169%
2028 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 0.23062 | 5 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 21.0079 | 1.7795 | 11.8053 | 21.0079 | 1.7795 | 11.8053 | 24.5584 | 2.0803 | 11.8053 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2028 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 0.22654 | 4 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 16.5102 | 1.4236 | 11.5973 | 16.5102 | 1.4236 | 11.5973 | 19.3006 | 1.6642 | 11.5973 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2028 | 1007 | CB 1007 | Tier-1 | Non-HFTD---4 | 1--5 | 0.22459 | 1 | 100% | 183.252 | 99.8% | 0% | 0.2013% | 9.0527 | 0 | 0 | 9.0527 | 0 | 7.8583 | 0.35591 | 22.0798 | 7.8583 | 0.35591 | 22.0798 | 9.1865 | 0.41606 | 22.0798 | 4.94% | 0.0023706 | 0.0022533 | 77301.9362 | 12237.1432 | 2369.9057 | 62694.8873 | 77310.0415 | 0 | 0 | 77310.0415 | 0.0002985%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.22086 | 3 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 12.9002 | 1.0677 | 12.082 | 12.9002 | 1.0677 | 12.082 | 15.0805 | 1.2482 | 12.082 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.21127 | 4 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.3266 | 1.4236 | 3.7416 | 5.3266 | 1.4236 | 3.7416 | 6.2269 | 1.6642 | 3.7416 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.20097 | 3 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 25.0438 | 1.0677 | 23.4554 | 25.0438 | 1.0677 | 23.4554 | 29.2765 | 1.2482 | 23.4554 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2028 | HW1 | CB HW1 | Tier-1 | Non-HFTD---4 | 1--5 | 0.2008 | 5 | 100% | 122.4382 | 99.35% | 0% | 0.6452% | 6.0216 | 0 | 0 | 6.0216 | 0 | 5.2271 | 1.7795 | 2.9374 | 5.2271 | 1.7795 | 2.9374 | 6.1106 | 2.0803 | 2.9374 | 4.918% | 0.0031138 | 0.0029597 | 39321.1613 | 6393.1555 | 36.0556 | 32891.9501 | 39334.373 | 0 | 0 | 39334.373 | 0.0001986%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 0.19973 | 5 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 46.343 | 1.7795 | 26.0422 | 46.343 | 1.7795 | 26.0422 | 54.1755 | 2.0803 | 26.0422 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2028 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.19192 | 2 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 4.9095 | 0.71181 | 6.8971 | 4.9095 | 0.71181 | 6.8971 | 5.7392 | 0.83212 | 6.8971 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2028 | 172 | 172-569R | Tier-1 | Non-HFTD---3 | 5--2 | 0.19139 | 2 | 100% | 174.5806 | 70.22% | 23.82% | 5.957% | 6.0684 | 0 | 0 | 6.0684 | 0 | 5.2678 | 0.71181 | 7.4005 | 5.2678 | 0.71181 | 7.4005 | 6.1581 | 0.83212 | 7.4005 | 3.476% | 0.12865 | 0.12229 | 1356.9713 | 139.4703 | 376.51 | 840.9911 | 1378.015 | 0 | 0 | 1378.015 | 0.0002001%
2028 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.18961 | 1 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 9.128 | 0.35591 | 25.6471 | 9.128 | 0.35591 | 25.6471 | 10.6707 | 0.41606 | 25.6471 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.18908 | 4 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 36.0619 | 1.4236 | 25.331 | 36.0619 | 1.4236 | 25.331 | 42.1568 | 1.6642 | 25.331 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.18748 | 3 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 4.6334 | 1.0677 | 4.3395 | 4.6334 | 1.0677 | 4.3395 | 5.4165 | 1.2482 | 4.3395 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 0.17772 | 3 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 171.5694 | 1.0677 | 160.6876 | 171.5694 | 1.0677 | 160.6876 | 200.5666 | 1.2482 | 160.6876 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2028 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.17736 | 2 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 0.97851 | 0.71181 | 1.3747 | 0.97851 | 0.71181 | 1.3747 | 1.1439 | 0.83212 | 1.3747 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 0.17683 | 2 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 272.7233 | 0.71181 | 383.1388 | 272.7233 | 0.71181 | 383.1388 | 318.8167 | 0.83212 | 383.1388 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 0.16671 | 2 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 68.097 | 0.71181 | 95.6669 | 68.097 | 0.71181 | 95.6669 | 79.6061 | 0.83212 | 95.6669 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.16405 | 2 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.1114 | 0.71181 | 2.9662 | 2.1114 | 0.71181 | 2.9662 | 2.4683 | 0.83212 | 2.9662 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 0.16103 | 3 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 121.2542 | 1.0677 | 113.5636 | 121.2542 | 1.0677 | 113.5636 | 141.7475 | 1.2482 | 113.5636 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2028 | 1039 | CB 1039 | Tier-1 | Non-HFTD---6 | 4--3 | 0.15694 | 3 | 100% | 89.254 | 66.42% | 32.73% | 0.8498% | 2.9347 | 0 | 0 | 2.9347 | 0 | 2.5475 | 1.0677 | 2.3859 | 2.5475 | 1.0677 | 2.3859 | 2.978 | 1.2482 | 2.3859 | 3.288% | 0.047241 | 0.044903 | 1889.3167 | 183.5723 | 702.9111 | 1002.8332 | 1922.3524 | 0 | 0 | 1922.3524 | 9.677e-05%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.15446 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 10.7401 | 0.71181 | 15.0884 | 10.7401 | 0.71181 | 15.0884 | 12.5553 | 0.83212 | 15.0884 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2028 | 856 | 856-1141R | Tier-1 | Non-HFTD---7 | 2--3 | 0.15197 | 3 | 100% | 34.972 | 93.55% | 0% | 6.449% | 1.6195 | 0 | 0 | 1.6195 | 0 | 1.4058 | 1.0677 | 1.3166 | 1.4058 | 1.0677 | 1.3166 | 1.6434 | 1.2482 | 1.3166 | 4.631% | 0.0095222 | 0.0090509 | 3672.677 | 493.2945 | 440.7828 | 2738.5997 | 3685.0115 | 0 | 0 | 3685.0115 | 5.34e-05%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.14789 | 1 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.6843 | 0.35591 | 15.9713 | 5.6843 | 0.35591 | 15.9713 | 6.645 | 0.41606 | 15.9713 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2028 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 0.14629 | 3 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 174.9949 | 1.0677 | 163.8959 | 174.9949 | 1.0677 | 163.8959 | 204.571 | 1.2482 | 163.8959 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2028 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 0.14008 | 3 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 30.8639 | 1.0677 | 28.9063 | 30.8639 | 1.0677 | 28.9063 | 36.0802 | 1.2482 | 28.9063 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.14008 | 3 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 57.582 | 1.0677 | 53.9299 | 57.582 | 1.0677 | 53.9299 | 67.3141 | 1.2482 | 53.9299 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.11345 | 2 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 29.618 | 0.71181 | 41.6093 | 29.618 | 0.71181 | 41.6093 | 34.6238 | 0.83212 | 41.6093 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.11025 | 1 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 12.5585 | 0.35591 | 35.286 | 12.5585 | 0.35591 | 35.286 | 14.6811 | 0.41606 | 35.286 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2028 | 1221 | 1221-2095F | Tier-1 | Non-HFTD---9 | 1--4 | 0.10883 | 2 | 100% | 19.6421 | 98.74% | 0% | 1.261% | 0.96002 | 0 | 0 | 0.96002 | 0 | 0.83336 | 0.71181 | 1.1708 | 0.83336 | 0.71181 | 1.1708 | 0.97421 | 0.83212 | 1.1708 | 4.888% | 0.0016714 | 0.0015887 | 11751.8616 | 4301.6259 | 14.6524 | 7435.5833 | 11759.5801 | 0 | 0 | 11759.5801 | 3.166e-05%
2028 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.10848 | 1 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 13.8695 | 0.35591 | 38.9695 | 13.8695 | 0.35591 | 38.9695 | 16.2136 | 0.41606 | 38.9695 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2028 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.10741 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 5.7351 | 0.35591 | 16.114 | 5.7351 | 0.35591 | 16.114 | 6.7044 | 0.41606 | 16.114 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2028 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.1067 | 2 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.3253 | 0.71181 | 7.4813 | 5.3253 | 0.71181 | 7.4813 | 6.2253 | 0.83212 | 7.4813 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.1035 | 2 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 16.9319 | 0.71181 | 23.7871 | 16.9319 | 0.71181 | 23.7871 | 19.7936 | 0.83212 | 23.7871 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.097469 | 2 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 10.906 | 0.71181 | 15.3214 | 10.906 | 0.71181 | 15.3214 | 12.7492 | 0.83212 | 15.3214 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2028 | 93 | 93-10R | Tier-1 | Non-HFTD---2 | 4--4 | 0.095516 | 3 | 100% | 302.3321 | 90.71% | 7.303% | 1.988% | 13.575 | 0 | 0 | 13.575 | 0 | 11.7839 | 1.0677 | 11.0365 | 11.7839 | 1.0677 | 11.0365 | 13.7756 | 1.2482 | 11.0365 | 4.49% | 0.035815 | 0.034042 | 8441.494 | 1852.3748 | 638.1878 | 5950.9314 | 8482.34 | 0 | 0 | 8482.34 | 0.0004477%
2028 | 901 | 901-1124 | Tier-1 | Non-HFTD---1 | 2--5 | 0.094983 | 1 | 100% | 225.4814 | 99.29% | 0% | 0.709% | 11.0822 | 0 | 0 | 11.0822 | 0 | 9.6201 | 0.35591 | 27.0297 | 9.6201 | 0.35591 | 27.0297 | 11.246 | 0.41606 | 27.0297 | 4.915% | 0.0087544 | 0.0083211 | 25756.3496 | 4178.6743 | 36.5656 | 21541.1098 | 25765.8596 | 0 | 0 | 25765.8596 | 0.0003654%
2028 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.09161 | 2 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 3.7465 | 0.71181 | 5.2633 | 3.7465 | 0.71181 | 5.2633 | 4.3797 | 0.83212 | 5.2633 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2028 | 299 | 299-1153F | Tier-1 | Non-HFTD---11 | 1--4 | 0.090722 | 2 | 100% | 12.6944 | 96.89% | 0% | 3.107% | 0.60885 | 0 | 0 | 0.60885 | 0 | 0.52852 | 0.71181 | 0.7425 | 0.52852 | 0.71181 | 0.7425 | 0.61785 | 0.83212 | 0.7425 | 4.796% | 0.0013374 | 0.0012712 | 9491.8205 | 1360.071 | 891.9808 | 7239.7687 | 9507.1772 | 0 | 0 | 9507.1772 | 2.008e-05%
2028 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 0.089302 | 2 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 244.7238 | 0.71181 | 343.8033 | 244.7238 | 0.71181 | 343.8033 | 286.0849 | 0.83212 | 343.8033 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2028 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.088947 | 1 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 5.7481 | 0.35591 | 16.1505 | 5.7481 | 0.35591 | 16.1505 | 6.7196 | 0.41606 | 16.1505 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 0.080425 | 1 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 14.1083 | 0.35591 | 39.6404 | 14.1083 | 0.35591 | 39.6404 | 16.4928 | 0.41606 | 39.6404 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 0.08007 | 2 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 16.6149 | 0.71181 | 23.3417 | 16.6149 | 0.71181 | 23.3417 | 19.423 | 0.83212 | 23.3417 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 0.079715 | 1 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 95.1404 | 0.35591 | 267.3183 | 95.1404 | 0.35591 | 267.3183 | 111.2202 | 0.41606 | 267.3183 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2028 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.077762 | 2 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.35 | 0.71181 | 4.7063 | 3.35 | 0.71181 | 4.7063 | 3.9162 | 0.83212 | 4.7063 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2028 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.071015 | 2 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 3.6818 | 0.71181 | 5.1724 | 3.6818 | 0.71181 | 5.1724 | 4.304 | 0.83212 | 5.1724 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2028 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.069773 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.3218 | 0.35591 | 6.5237 | 2.3218 | 0.35591 | 6.5237 | 2.7142 | 0.41606 | 6.5237 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 0.068352 | 2 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 23.3784 | 0.71181 | 32.8435 | 23.3784 | 0.71181 | 32.8435 | 27.3297 | 0.83212 | 32.8435 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.068175 | 1 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 6.4939 | 0.35591 | 18.2461 | 6.4939 | 0.35591 | 18.2461 | 7.5915 | 0.41606 | 18.2461 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.061606 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 62.4639 | 0.35591 | 175.5064 | 62.4639 | 0.35591 | 175.5064 | 73.021 | 0.41606 | 175.5064 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2028 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.060718 | 1 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 14.3554 | 0.35591 | 40.3348 | 14.3554 | 0.35591 | 40.3348 | 16.7817 | 0.41606 | 40.3348 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2028 | 474 | 474-29 | Tier-1 | Non-HFTD---1 | 2--5 | 0.059298 | 2 | 100% | 1510.7302 | 99.89% | 0% | 0.1058% | 74.702 | 0 | 0 | 74.702 | 0 | 64.8462 | 0.71181 | 91.1001 | 64.8462 | 0.71181 | 91.1001 | 75.806 | 0.83212 | 91.1001 | 4.945% | 0.010755 | 0.010222 | 140472.931 | 24566.9965 | 189.9323 | 115716.0023 | 140480.6687 | 0 | 0 | 140480.6687 | 0.002463%
2028 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.057878 | 1 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 10.7819 | 0.35591 | 30.2942 | 10.7819 | 0.35591 | 30.2942 | 12.6042 | 0.41606 | 30.2942 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2028 | 171 | 171-34 | Tier-1 | Non-HFTD---6 | 4--3 | 0.056812 | 1 | 100% | 81.2035 | 44.67% | 51.64% | 3.687% | 1.7955 | 0 | 0 | 1.7955 | 0 | 1.5586 | 0.35591 | 4.3793 | 1.5586 | 0.35591 | 4.3793 | 1.8221 | 0.41606 | 4.3793 | 2.211% | 0.043687 | 0.041525 | 1858.7395 | 129.5883 | 851.5868 | 877.5644 | 1912.2988 | 0 | 0 | 1912.2988 | 5.921e-05%
2028 | 1001 | 1001-1232F | Tier-1 | Non-HFTD---15 | 1--4 | 0.056812 | 1 | 100% | 3.7082 | 98.25% | 0% | 1.746% | 0.18035 | 0 | 0 | 0.18035 | 0 | 0.15655 | 0.35591 | 0.43988 | 0.15655 | 0.35591 | 0.43988 | 0.18301 | 0.41606 | 0.43988 | 4.864% | 0.0002536 | 0.00024105 | 14622.1214 | 2186.2186 | 960.6365 | 11475.2662 | 14635.4188 | 0 | 0 | 14635.4188 | 5.947e-06%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.056635 | 1 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 4.9855 | 0.35591 | 14.008 | 4.9855 | 0.35591 | 14.008 | 5.8282 | 0.41606 | 14.008 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2028 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.053439 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.479 | 0.35591 | 9.7751 | 3.479 | 0.35591 | 9.7751 | 4.067 | 0.41606 | 9.7751 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2028 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.052906 | 1 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.0369 | 0.35591 | 8.5328 | 3.0369 | 0.35591 | 8.5328 | 3.5502 | 0.41606 | 8.5328 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.052551 | 1 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 6.9875 | 0.35591 | 19.6331 | 6.9875 | 0.35591 | 19.6331 | 8.1685 | 0.41606 | 19.6331 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.052196 | 1 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.066084 | 0.35591 | 0.18568 | 0.066084 | 0.35591 | 0.18568 | 0.077253 | 0.41606 | 0.18568 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2028 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.051664 | 1 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.61831 | 0.35591 | 1.7373 | 0.61831 | 0.35591 | 1.7373 | 0.72281 | 0.41606 | 1.7373 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2028 | 591 | 591-39AE | Tier-1 | Non-HFTD---1 | 4--4 | 0.051309 | 2 | 100% | 863.6817 | 30.54% | 68.77% | 0.684% | 13.0582 | 0 | 0 | 13.0582 | 0 | 11.3354 | 0.71181 | 15.9247 | 11.3354 | 0.71181 | 15.9247 | 13.2512 | 0.83212 | 15.9247 | 1.512% | 0.061092 | 0.058068 | 14137.3023 | 873.1637 | 8965.9062 | 4298.2324 | 14648.6655 | 0 | 0 | 14648.6655 | 0.0004306%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.050598 | 1 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 27.936 | 0.35591 | 78.4924 | 27.936 | 0.35591 | 78.4924 | 32.6575 | 0.41606 | 78.4924 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2028 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.050421 | 1 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.080746 | 0.35591 | 0.22687 | 0.080746 | 0.35591 | 0.22687 | 0.094393 | 0.41606 | 0.22687 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2028 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.049711 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 0.93446 | 0.35591 | 2.6256 | 0.93446 | 0.35591 | 2.6256 | 1.0924 | 0.41606 | 2.6256 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2028 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.049001 | 1 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.1042 | 0.35591 | 0.29277 | 0.1042 | 0.35591 | 0.29277 | 0.12181 | 0.41606 | 0.29277 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2028 | 472 | CB 472 | Tier-1 | Non-HFTD---6 | 3--3 | 0.04687 | 1 | 100% | 66.0921 | 92.91% | 0% | 7.09% | 3.0396 | 0 | 0 | 3.0396 | 0 | 2.6386 | 0.35591 | 7.4137 | 2.6386 | 0.35591 | 7.4137 | 3.0845 | 0.41606 | 7.4137 | 4.599% | 0.020578 | 0.019559 | 3211.8146 | 441.0584 | 309.4932 | 2461.263 | 3223.674 | 0 | 0 | 3223.674 | 0.0001002%
2028 | 859 | 859-1064 | Tier-1 | Non-HFTD---7 | 2--3 | 0.045272 | 2 | 100% | 40.2522 | 93.55% | 0% | 6.452% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.618 | 0.71181 | 2.2731 | 1.618 | 0.71181 | 2.2731 | 1.8915 | 0.83212 | 2.2731 | 4.631% | 0.011569 | 0.010996 | 3479.3123 | 521.49 | 92.9503 | 2864.872 | 3491.0022 | 0 | 0 | 3491.0022 | 6.147e-05%
2028 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.042964 | 1 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 13.3286 | 0.35591 | 37.4496 | 13.3286 | 0.35591 | 37.4496 | 15.5812 | 0.41606 | 37.4496 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.041366 | 1 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 6.7644 | 0.35591 | 19.006 | 6.7644 | 0.35591 | 19.006 | 7.9076 | 0.41606 | 19.006 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.040479 | 1 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 33.674 | 0.35591 | 94.6147 | 33.674 | 0.35591 | 94.6147 | 39.3653 | 0.41606 | 94.6147 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2028 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.038881 | 1 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 8.2404 | 0.35591 | 23.1533 | 8.2404 | 0.35591 | 23.1533 | 9.6331 | 0.41606 | 23.1533 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 0.038703 | 1 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 24.2686 | 0.35591 | 68.1881 | 24.2686 | 0.35591 | 68.1881 | 28.3703 | 0.41606 | 68.1881 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2028 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.037283 | 1 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.51583 | 0.35591 | 1.4493 | 0.51583 | 0.35591 | 1.4493 | 0.60301 | 0.41606 | 1.4493 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2028 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.036218 | 1 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.71318 | 0.35591 | 2.0038 | 0.71318 | 0.35591 | 2.0038 | 0.83371 | 0.41606 | 2.0038 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2028 | 245 | CB 245 | Tier-1 | Non-HFTD---2 | 4--4 | 0.03462 | 1 | 100% | 248.3247 | 30.26% | 68.14% | 1.595% | 3.7197 | 0 | 0 | 3.7197 | 0 | 3.2289 | 0.35591 | 9.0723 | 3.2289 | 0.35591 | 9.0723 | 3.7746 | 0.41606 | 9.0723 | 1.498% | 0.044637 | 0.042428 | 5563.1534 | 331.3651 | 3704.159 | 1527.6293 | 5765.2004 | 0 | 0 | 5765.2004 | 0.0001227%
2028 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | 2--4 | 0.034265 | 1 | 100% | 92.0555 | 97.82% | 0% | 2.183% | 4.4573 | 0 | 0 | 4.4573 | 0 | 3.8692 | 0.35591 | 10.8714 | 3.8692 | 0.35591 | 10.8714 | 4.5231 | 0.41606 | 10.8714 | 4.842% | 0.0089936 | 0.0085484 | 10235.6661 | 2125.5614 | 107.0953 | 8003.0094 | 10247.3023 | 0 | 0 | 10247.3023 | 0.000147%
2028 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.032134 | 1 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.0797 | 0.35591 | 3.0337 | 1.0797 | 0.35591 | 3.0337 | 1.2622 | 0.41606 | 3.0337 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.032134 | 1 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.5007 | 0.35591 | 7.0263 | 2.5007 | 0.35591 | 7.0263 | 2.9233 | 0.41606 | 7.0263 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2028 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.032134 | 1 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.6644 | 0.35591 | 1.8668 | 0.6644 | 0.35591 | 1.8668 | 0.77669 | 0.41606 | 1.8668 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.031957 | 1 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 4.8583 | 0.35591 | 13.6506 | 4.8583 | 0.35591 | 13.6506 | 5.6795 | 0.41606 | 13.6506 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2028 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.031424 | 1 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.49012 | 0.35591 | 1.3771 | 0.49012 | 0.35591 | 1.3771 | 0.57295 | 0.41606 | 1.3771 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2028 | 96 | 96-1041F | Tier-1 | Non-HFTD---13 | 2--2 | 0.031424 | 1 | 100% | 5.6175 | 97.14% | 1.791% | 1.068% | 0.27012 | 0 | 0 | 0.27012 | 0 | 0.23448 | 0.35591 | 0.65882 | 0.23448 | 0.35591 | 0.65882 | 0.27411 | 0.41606 | 0.65882 | 4.808% | 0.005633 | 0.0053542 | 997.2446 | 127.463 | 205.2994 | 664.4822 | 998.7294 | 0 | 0 | 998.7294 | 8.907e-06%
2028 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.031247 | 1 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.7632 | 0.35591 | 2.1444 | 0.7632 | 0.35591 | 2.1444 | 0.89219 | 0.41606 | 2.1444 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2028 | 205 | 205-369R | Tier-1 | Non-HFTD---2 | 4--4 | 0.030537 | 1 | 100% | 370.1825 | 97.17% | 0% | 2.827% | 17.8061 | 0 | 0 | 17.8061 | 0 | 15.4569 | 0.35591 | 43.4295 | 15.4569 | 0.35591 | 43.4295 | 18.0692 | 0.41606 | 43.4295 | 4.81% | 0.046634 | 0.044326 | 7938.0395 | 1227.249 | 240.0519 | 6470.7387 | 7949.7244 | 0 | 0 | 7949.7244 | 0.0005872%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.029826 | 1 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.0652 | 0.35591 | 2.9928 | 1.0652 | 0.35591 | 2.9928 | 1.2452 | 0.41606 | 2.9928 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2028 | BW1 | CB BW1 | Tier-1 | Non-HFTD---11 | 1--3 | 0.027874 | 1 | 100% | 8.712 | 88.19% | 0% | 11.81% | 0.3803 | 0 | 0 | 0.3803 | 0 | 0.33013 | 0.35591 | 0.92757 | 0.33013 | 0.35591 | 0.92757 | 0.38592 | 0.41606 | 0.92757 | 4.365% | 0.0039232 | 0.003729 | 2220.6335 | 316.4948 | 49.7388 | 1854.3999 | 2234.2939 | 0 | 0 | 2234.2939 | 1.254e-05%
2028 | 93 | 93-559R | Tier-1 | Non-HFTD---2 | 3--4 | 0.026808 | 1 | 100% | 194.9296 | 89.74% | 7.915% | 2.344% | 8.6591 | 0 | 0 | 8.6591 | 0 | 7.5167 | 0.35591 | 21.1197 | 7.5167 | 0.35591 | 21.1197 | 8.7871 | 0.41606 | 21.1197 | 4.442% | 0.02667 | 0.02535 | 7308.8898 | 1504.7135 | 606.7669 | 5197.4095 | 7347.9399 | 0 | 0 | 7347.9399 | 0.0002855%
2028 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.026098 | 1 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.25966 | 0.35591 | 0.72958 | 0.25966 | 0.35591 | 0.72958 | 0.30355 | 0.41606 | 0.72958 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2028 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.025033 | 1 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.2769 | 0.35591 | 3.5878 | 1.2769 | 0.35591 | 3.5878 | 1.4927 | 0.41606 | 3.5878 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2028 | 95 | 95-35F | Tier-1 | Non-HFTD---9 | 2--2 | 0.024145 | 1 | 100% | 19.0547 | 69.14% | 22.45% | 8.414% | 0.65213 | 0 | 0 | 0.65213 | 0 | 0.56609 | 0.35591 | 1.5906 | 0.56609 | 0.35591 | 1.5906 | 0.66177 | 0.41606 | 1.5906 | 3.422% | 0.011941 | 0.01135 | 1595.6856 | 179.3204 | 352.6449 | 1063.7203 | 1621.3303 | 0 | 0 | 1621.3303 | 2.15e-05%
2028 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.022015 | 1 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.7032 | 0.35591 | 7.5951 | 2.7032 | 0.35591 | 7.5951 | 3.16 | 0.41606 | 7.5951 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2028 | 63 | 63-35AE | Tier-1 | Non-HFTD---1 | 3--4 | 0.019707 | 1 | 100% | 256.4675 | 76.22% | 23.46% | 0.3199% | 9.6762 | 0 | 0 | 9.6762 | 0 | 8.3996 | 0.35591 | 23.6005 | 8.3996 | 0.35591 | 23.6005 | 9.8192 | 0.41606 | 23.6005 | 3.773% | 0.016955 | 0.016116 | 15126.187 | 2259.8593 | 3445.3068 | 9421.0209 | 15313.5135 | 0 | 0 | 15313.5135 | 0.0003191%
2028 | 450 | 450-114F | Tier-1 | Non-HFTD---7 | 1--4 | 0.018642 | 1 | 100% | 28.615 | 98.32% | 0% | 1.684% | 1.3926 | 0 | 0 | 1.3926 | 0 | 1.2089 | 0.35591 | 3.3965 | 1.2089 | 0.35591 | 3.3965 | 1.4132 | 0.41606 | 3.3965 | 4.867% | 0.0023436 | 0.0022276 | 12209.8338 | 1908.2658 | 365.7567 | 9935.8114 | 12220.543 | 0 | 0 | 12220.543 | 4.592e-05%
2028 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.017576 | 1 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.6389 | 0.35591 | 1.7951 | 0.6389 | 0.35591 | 1.7951 | 0.74688 | 0.41606 | 1.7951 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.017399 | 1 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.0599 | 0.35591 | 8.5973 | 3.0599 | 0.35591 | 8.5973 | 3.577 | 0.41606 | 8.5973 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 0.017044 | 1 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 147.4188 | 0.35591 | 414.2063 | 147.4188 | 0.35591 | 414.2063 | 172.3343 | 0.41606 | 414.2063 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2028 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.016866 | 1 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.32972 | 0.35591 | 0.92642 | 0.32972 | 0.35591 | 0.92642 | 0.38544 | 0.41606 | 0.92642 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 0.015623 | 1 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 233.7156 | 0.35591 | 656.6766 | 233.7156 | 0.35591 | 656.6766 | 273.2162 | 0.41606 | 656.6766 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2028 | 172 | 172-567R | Tier-1 | Non-HFTD---3 | 4--3 | 0.014203 | 1 | 100% | 141.9219 | 62.19% | 32.78% | 5.033% | 4.369 | 0 | 0 | 4.369 | 0 | 3.7926 | 0.35591 | 10.6562 | 3.7926 | 0.35591 | 10.6562 | 4.4336 | 0.41606 | 10.6562 | 3.078% | 0.069555 | 0.066112 | 2040.4331 | 199.3667 | 664.6627 | 1176.4036 | 2080.609 | 0 | 0 | 2080.609 | 0.0001441%
2028 | TM1 | CB TM1 | Tier-1 | Non-HFTD---7 | 1--5 | 0.014026 | 1 | 100% | 38.7396 | 99.8% | 0% | 0.1958% | 1.9139 | 0 | 0 | 1.9139 | 0 | 1.6614 | 0.35591 | 4.6679 | 1.6614 | 0.35591 | 4.6679 | 1.9421 | 0.41606 | 4.6679 | 4.94% | 0.0001408 | 0.00013383 | 275139.3146 | 43811.8165 | 68.1712 | 231259.327 | 275167.3683 | 0 | 0 | 275167.3683 | 6.311e-05%
2028 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.013848 | 1 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.46405 | 0.35591 | 1.3039 | 0.46405 | 0.35591 | 1.3039 | 0.54248 | 0.41606 | 1.3039 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2028 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.01367 | 1 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 2.7314 | 0.35591 | 7.6744 | 2.7314 | 0.35591 | 7.6744 | 3.193 | 0.41606 | 7.6744 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2028 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011185 | 1 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.35591 | 0 | 0 | 0.35591 | 0 | 0 | 0.41606 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2028 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.01083 | 1 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.0815 | 0.35591 | 3.0387 | 1.0815 | 0.35591 | 3.0387 | 1.2643 | 0.41606 | 3.0387 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2028 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.010652 | 1 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.029751 | 0.35591 | 0.083591 | 0.029751 | 0.35591 | 0.083591 | 0.034779 | 0.41606 | 0.083591 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 0.010475 | 1 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 20.2007 | 0.35591 | 56.7585 | 20.2007 | 0.35591 | 56.7585 | 23.6149 | 0.41606 | 56.7585 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2028 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.0099421 | 1 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.35591 | 0 | 0 | 0.35591 | 0 | 0 | 0.41606 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2028 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.0094095 | 1 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.1426 | 0.35591 | 3.2103 | 1.1426 | 0.35591 | 3.2103 | 1.3357 | 0.41606 | 3.2103 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.0079892 | 1 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 33.9963 | 0.35591 | 95.5202 | 33.9963 | 0.35591 | 95.5202 | 39.742 | 0.41606 | 95.5202 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2028 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.0079892 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.28982 | 0.35591 | 0.81433 | 0.28982 | 0.35591 | 0.81433 | 0.33881 | 0.41606 | 0.81433 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2028 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.0056812 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.25823 | 0.35591 | 0.72557 | 0.25823 | 0.35591 | 0.72557 | 0.30188 | 0.41606 | 0.72557 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%

## Fuel_Management
Fuel Management - Risk & Cost Benefit | [29 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[30 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%)
back to index | [29 empty] | 2026 | 500 | 2126959.604 | 3239.5352 | 0.1523% | 3090.2965 | 5194.1601 | 0.59496 | 3090.2965 | 5194.1601 | 0.59496 | 3255.4153 | 5471.6912 | 0.59496 | 0.1068%
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [12 empty] | 2027 | 500 | 2028961.4705 | 3363.0649 | 0.1658% | 3060.3433 | 4954.8758 | 0.61764 | 3060.3433 | 4954.8758 | 0.61764 | 3396.117 | 5498.5132 | 0.61764 | 0.1109%
[9 empty] | Capital Cost only in Year 0 | 10.89 | K$/structure | 2025-06-30 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [12 empty] | 2028 | 500 | 2106114.899 | 3270.411 | 0.1553% | 2838.9299 | 4726.6149 | 0.60063 | 2838.9299 | 4726.6149 | 0.60063 | 3318.7414 | 5525.4667 | 0.60063 | 0.1078%
[9 empty] | Service Drop factor | 0% | % | 2025-06-30 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [12 empty] | Total 2026-2028 | 1500 | 6262035.9734 | 9873.0111 | 0.1577% | 8989.5697 | 14875.6508 | 0.60431 | 8989.5697 | 14875.6508 | 0.60431 | 9970.2736 | 16495.6711 | 0.60442 | 0.3256%
[9 empty] | OH to UG conversion factor | 0% | % | 2025-06-30
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-06-30
[9 empty] | Lifetime | 1 | Years | 2025-06-30
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[9 empty] | Mitigation Effectiveness Estimate (%) | 4.95% | % | 2025-06-30
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-06-30
[13 empty] | [1] | [1] |  | [2]
[8 empty] | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total HFTD Poles | Poles in Scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 112 | 2 | 2610.8 | 93.6% | 6.065% | 0.3401% | 2.16 | 0 | 0 | 2.16 | 0 | 2.0604 | 20.7766 | 0.099171 | 2.0604 | 20.7766 | 0.099171 | 2.1705 | 21.8868 | 0.099171 | 0.08273% | 0.2194 | 0.21921 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11900.2598 | 0 | 0 | 11900.2598 | 7.123e-05%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 188 | 4 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 4.1297 | 0 | 0 | 4.1297 | 0 | 3.9394 | 41.5533 | 0.094804 | 3.9394 | 41.5533 | 0.094804 | 4.1499 | 43.7735 | 0.094804 | 0.09879% | 0.24743 | 0.24717 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16895.0528 | 0 | 0 | 16895.0528 | 0.0001362%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 55 | 1 | 622.3042 | 87.18% | 11.98% | 0.8373% | 0.48827 | 0 | 0 | 0.48827 | 0 | 0.46578 | 10.3883 | 0.044837 | 0.46578 | 10.3883 | 0.044837 | 0.49066 | 10.9434 | 0.044837 | 0.07846% | 0.20095 | 0.20077 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3097.175 | 0 | 0 | 3097.175 | 1.61e-05%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 78 | 2 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 1.9172 | 0 | 0 | 1.9172 | 0 | 1.8289 | 20.7766 | 0.088025 | 1.8289 | 20.7766 | 0.088025 | 1.9266 | 21.8868 | 0.088025 | 0.1178% | 0.20887 | 0.20861 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7794.6365 | 0 | 0 | 7794.6365 | 6.322e-05%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 84 | 4 | 6201.607 | 97.29% | 2.601% | 0.1104% | 14.2217 | 0 | 0 | 14.2217 | 0 | 13.5666 | 41.5533 | 0.32649 | 13.5666 | 41.5533 | 0.32649 | 14.2915 | 43.7735 | 0.32649 | 0.2293% | 0.2182 | 0.21768 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28423.7969 | 0 | 0 | 28423.7969 | 0.000469%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 90 | 3 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 24.9422 | 0 | 0 | 24.9422 | 0 | 23.7932 | 31.165 | 0.76346 | 23.7932 | 31.165 | 0.76346 | 25.0645 | 32.8301 | 0.76346 | 0.1626% | 0.22506 | 0.22469 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68147.5638 | 0 | 0 | 68147.5638 | 0.0008225%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 56 | 1 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 4.9876 | 0 | 0 | 4.9876 | 0 | 4.7578 | 10.3883 | 0.45799 | 4.7578 | 10.3883 | 0.45799 | 5.012 | 10.9434 | 0.45799 | 0.08699% | 0.21349 | 0.2133 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26857.6481 | 0 | 0 | 26857.6481 | 0.0001645%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 93 | 2 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 11.0842 | 0 | 0 | 11.0842 | 0 | 10.5736 | 20.7766 | 0.50892 | 10.5736 | 20.7766 | 0.50892 | 11.1385 | 21.8868 | 0.50892 | 0.1047% | 0.23776 | 0.23751 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44547.4564 | 0 | 0 | 44547.4564 | 0.0003655%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 84 | 5 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 26.9364 | 0 | 0 | 26.9364 | 0 | 25.6955 | 51.9416 | 0.4947 | 25.6955 | 51.9416 | 0.4947 | 27.0684 | 54.7169 | 0.4947 | 0.29% | 0.22716 | 0.22649 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40889.8841 | 0 | 0 | 40889.8841 | 0.0008883%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 60 | 1 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 11.8116 | 0 | 0 | 11.8116 | 0 | 11.2675 | 10.3883 | 1.0846 | 11.2675 | 10.3883 | 1.0846 | 11.8695 | 10.9434 | 1.0846 | 0.08131% | 0.34567 | 0.34539 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42024.7825 | 0 | 0 | 42024.7825 | 0.0003895%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 34 | 1 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 17.806 | 0 | 0 | 17.806 | 0 | 16.9857 | 10.3883 | 1.6351 | 16.9857 | 10.3883 | 1.6351 | 17.8933 | 10.9434 | 1.6351 | 0.1445% | 0.46655 | 0.46587 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26409.0779 | 0 | 0 | 26409.0779 | 0.0005872%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 77 | 1 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 0.73267 | 0 | 0 | 0.73267 | 0 | 0.69892 | 10.3883 | 0.06728 | 0.69892 | 10.3883 | 0.06728 | 0.73627 | 10.9434 | 0.06728 | 0.0456% | 0.43999 | 0.43971 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3652.837 | 0 | 0 | 3652.837 | 2.416e-05%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 28 | 1 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 16.8788 | 0 | 0 | 16.8788 | 0 | 16.1013 | 10.3883 | 1.5499 | 16.1013 | 10.3883 | 1.5499 | 16.9616 | 10.9434 | 1.5499 | 0.1738% | 0.38409 | 0.38341 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25292.0307 | 0 | 0 | 25292.0307 | 0.0005566%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 59 | 2 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 30.6147 | 0 | 0 | 30.6147 | 0 | 29.2044 | 20.7766 | 1.4056 | 29.2044 | 20.7766 | 1.4056 | 30.7648 | 21.8868 | 1.4056 | 0.1659% | 0.3939 | 0.39324 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46836.2841 | 0 | 0 | 46836.2841 | 0.00101%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 50 | 1 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 5.2792 | 0 | 0 | 5.2792 | 0 | 5.036 | 10.3883 | 0.48478 | 5.036 | 10.3883 | 0.48478 | 5.3051 | 10.9434 | 0.48478 | 0.09535% | 0.37772 | 0.37734 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14658.7004 | 0 | 0 | 14658.7004 | 0.0001741%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 107 | 3 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 25.3206 | 0 | 0 | 25.3206 | 0 | 24.1542 | 31.165 | 0.77504 | 24.1542 | 31.165 | 0.77504 | 25.4447 | 32.8301 | 0.77504 | 0.1348% | 0.38023 | 0.3797 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49395.5867 | 0 | 0 | 49395.5867 | 0.000835%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 15 | 1 | 3034.8235 | 97.12% | 2.752% | 0.1275% | 9.7265 | 0 | 0 | 9.7265 | 0 | 9.2784 | 10.3883 | 0.89316 | 9.2784 | 10.3883 | 0.89316 | 9.7742 | 10.9434 | 0.89316 | 0.3205% | 0.77068 | 0.76814 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3938.2199 | 0 | 0 | 3938.2199 | 0.0003207%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 56 | 2 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 35.0472 | 0 | 0 | 35.0472 | 0 | 33.4326 | 20.7766 | 1.6091 | 33.4326 | 20.7766 | 1.6091 | 35.219 | 21.8868 | 1.6091 | 0.1754% | 0.44563 | 0.44484 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44832.2747 | 0 | 0 | 44832.2747 | 0.001156%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 28 | 1 | 1295.9906 | 95.98% | 3.603% | 0.4176% | 2.199 | 0 | 0 | 2.199 | 0 | 2.0977 | 10.3883 | 0.20193 | 2.0977 | 10.3883 | 0.20193 | 2.2098 | 10.9434 | 0.20193 | 0.1697% | 0.034038 | 0.033978 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38077.7516 | 0 | 0 | 38077.7516 | 7.252e-05%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 20 | 3 | 418.5676 | 87.71% | 11.66% | 0.6303% | 2.7258 | 0 | 0 | 2.7258 | 0 | 2.6002 | 31.165 | 0.083434 | 2.6002 | 31.165 | 0.083434 | 2.7391 | 32.8301 | 0.083434 | 0.6512% | 0.28262 | 0.28052 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1482.404 | 0 | 0 | 1482.404 | 8.989e-05%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 177 | 2 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 2.848 | 0 | 0 | 2.848 | 0 | 2.7168 | 20.7766 | 0.13076 | 2.7168 | 20.7766 | 0.13076 | 2.862 | 21.8868 | 0.13076 | 0.05172% | 0.3705 | 0.37029 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14864.5499 | 0 | 0 | 14864.5499 | 9.392e-05%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 20 | 1 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 9.4961 | 0 | 0 | 9.4961 | 0 | 9.0586 | 10.3883 | 0.872 | 9.0586 | 10.3883 | 0.872 | 9.5427 | 10.9434 | 0.872 | 0.245% | 0.32777 | 0.32695 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11826.207 | 0 | 0 | 11826.207 | 0.0003131%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 151 | 5 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 2.7548 | 0 | 0 | 2.7548 | 0 | 2.6279 | 51.9416 | 0.050593 | 2.6279 | 51.9416 | 0.050593 | 2.7683 | 54.7169 | 0.050593 | 0.1337% | 0.36686 | 0.36626 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5620.1549 | 0 | 0 | 5620.1549 | 9.084e-05%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 53 | 1 | 1867.403 | 95.01% | 4.712% | 0.2778% | 1.6571 | 0 | 0 | 1.6571 | 0 | 1.5807 | 10.3883 | 0.15216 | 1.5807 | 10.3883 | 0.15216 | 1.6652 | 10.9434 | 0.15216 | 0.08874% | 0.32295 | 0.32265 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5782.5839 | 0 | 0 | 5782.5839 | 5.464e-05%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 205 | 7 | 18749.5963 | 97% | 2.901% | 0.09453% | 30.7422 | 0 | 0 | 30.7422 | 0 | 29.326 | 72.7182 | 0.40328 | 29.326 | 72.7182 | 0.40328 | 30.8929 | 76.6037 | 0.40328 | 0.164% | 0.38414 | 0.38349 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48812.3636 | 0 | 0 | 48812.3636 | 0.001014%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 19 | 1 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 10.4024 | 0 | 0 | 10.4024 | 0 | 9.9232 | 10.3883 | 0.95523 | 9.9232 | 10.3883 | 0.95523 | 10.4534 | 10.9434 | 0.95523 | 0.2582% | 0.19114 | 0.19064 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21079.1745 | 0 | 0 | 21079.1745 | 0.000343%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 63 | 1 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 3.3603 | 0 | 0 | 3.3603 | 0 | 3.2055 | 10.3883 | 0.30857 | 3.2055 | 10.3883 | 0.30857 | 3.3768 | 10.9434 | 0.30857 | 0.07663% | 0.20232 | 0.20216 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21675.6449 | 0 | 0 | 21675.6449 | 0.0001108%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 113 | 4 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 9.7445 | 0 | 0 | 9.7445 | 0 | 9.2956 | 41.5533 | 0.2237 | 9.2956 | 41.5533 | 0.2237 | 9.7923 | 43.7735 | 0.2237 | 0.1697% | 0.20491 | 0.20455 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28020.8636 | 0 | 0 | 28020.8636 | 0.0003213%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 62 | 2 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 18.1736 | 0 | 0 | 18.1736 | 0 | 17.3364 | 20.7766 | 0.83442 | 17.3364 | 20.7766 | 0.83442 | 18.2627 | 21.8868 | 0.83442 | 0.1577% | 0.22417 | 0.22381 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51405.5548 | 0 | 0 | 51405.5548 | 0.0005993%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 51 | 1 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 3.2264 | 0 | 0 | 3.2264 | 0 | 3.0777 | 10.3883 | 0.29627 | 3.0777 | 10.3883 | 0.29627 | 3.2422 | 10.9434 | 0.29627 | 0.09487% | 0.20978 | 0.20957 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16212.8443 | 0 | 0 | 16212.8443 | 0.0001064%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 44 | 3 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 16.2701 | 0 | 0 | 16.2701 | 0 | 15.5206 | 31.165 | 0.49801 | 15.5206 | 31.165 | 0.49801 | 16.3498 | 32.8301 | 0.49801 | 0.3297% | 0.21542 | 0.21469 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22906.6212 | 0 | 0 | 22906.6212 | 0.0005365%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 115 | 1 | 13172.958 | 96.8% | 3.124% | 0.0728% | 5.4888 | 0 | 0 | 5.4888 | 0 | 5.236 | 10.3883 | 0.50403 | 5.236 | 10.3883 | 0.50403 | 5.5157 | 10.9434 | 0.50403 | 0.04167% | 0.23242 | 0.23232 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56679.044 | 0 | 0 | 56679.044 | 0.000181%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 40 | 1 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 13.9056 | 0 | 0 | 13.9056 | 0 | 13.265 | 10.3883 | 1.2769 | 13.265 | 10.3883 | 1.2769 | 13.9737 | 10.9434 | 1.2769 | 0.1167% | 0.1455 | 0.14532 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 81908.464 | 0 | 0 | 81908.464 | 0.0004586%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 8 | 1 | 1723.9707 | 91.93% | 7.724% | 0.3493% | 9.8059 | 0 | 0 | 9.8059 | 0 | 9.3541 | 10.3883 | 0.90045 | 9.3541 | 10.3883 | 0.90045 | 9.8539 | 10.9434 | 0.90045 | 0.5688% | 0.048222 | 0.047923 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35768.9774 | 0 | 0 | 35768.9774 | 0.0003234%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 1 | 1 | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 60.2656 | 10.3883 | 5.8013 | 60.2656 | 10.3883 | 5.8013 | 63.4857 | 10.9434 | 5.8013 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 19 | 1 | 498.1496 | 90.1% | 9.186% | 0.7154% | 1.1693 | 0 | 0 | 1.1693 | 0 | 1.1154 | 10.3883 | 0.10737 | 1.1154 | 10.3883 | 0.10737 | 1.175 | 10.9434 | 0.10737 | 0.2347% | 0.32588 | 0.32503 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1529.0392 | 0 | 0 | 1529.0392 | 3.856e-05%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 60 | 3 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 2.2023 | 0 | 0 | 2.2023 | 0 | 2.1008 | 31.165 | 0.06741 | 2.1008 | 31.165 | 0.06741 | 2.2131 | 32.8301 | 0.06741 | 0.2122% | 0.34771 | 0.34685 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 2986.0407 | 0 | 0 | 2986.0407 | 7.262e-05%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 38 | 1 | 317.7725 | 50.82% | 48.53% | 0.6462% | 0.21038 | 0 | 0 | 0.21038 | 0 | 0.20069 | 10.3883 | 0.019319 | 0.20069 | 10.3883 | 0.019319 | 0.21141 | 10.9434 | 0.019319 | 0.06621% | 0.31397 | 0.31356 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1012.7634 | 0 | 0 | 1012.7634 | 6.938e-06%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 145 | 2 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 1.0411 | 0 | 0 | 1.0411 | 0 | 0.9931 | 20.7766 | 0.047799 | 0.9931 | 20.7766 | 0.047799 | 1.0462 | 21.8868 | 0.047799 | 0.05753% | 0.39031 | 0.39004 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4636.6469 | 0 | 0 | 4636.6469 | 3.433e-05%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 66 | 2 | 1890.633 | 91.06% | 8.49% | 0.4466% | 2.5825 | 0 | 0 | 2.5825 | 0 | 2.4635 | 20.7766 | 0.11857 | 2.4635 | 20.7766 | 0.11857 | 2.5952 | 21.8868 | 0.11857 | 0.1366% | 0.3743 | 0.37374 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5051.7383 | 0 | 0 | 5051.7383 | 8.516e-05%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 70 | 1 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 1.0547 | 0 | 0 | 1.0547 | 0 | 1.0061 | 10.3883 | 0.096846 | 1.0061 | 10.3883 | 0.096846 | 1.0598 | 10.9434 | 0.096846 | 0.06716% | 0.19221 | 0.19207 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8170.5674 | 0 | 0 | 8170.5674 | 3.478e-05%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 46 | 3 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 15.6452 | 0 | 0 | 15.6452 | 0 | 14.9245 | 31.165 | 0.47889 | 14.9245 | 31.165 | 0.47889 | 15.7219 | 32.8301 | 0.47889 | 0.3201% | 0.13941 | 0.13896 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35062.0196 | 0 | 0 | 35062.0196 | 0.0005159%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 68 | 3 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 3.1491 | 0 | 0 | 3.1491 | 0 | 3.0041 | 31.165 | 0.096392 | 3.0041 | 31.165 | 0.096392 | 3.1646 | 32.8301 | 0.096392 | 0.2124% | 0.1427 | 0.14239 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10389.0618 | 0 | 0 | 10389.0618 | 0.0001038%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 103 | 2 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 2.5395 | 0 | 0 | 2.5395 | 0 | 2.4225 | 20.7766 | 0.1166 | 2.4225 | 20.7766 | 0.1166 | 2.5519 | 21.8868 | 0.1166 | 0.09206% | 0.19881 | 0.19862 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13875.8442 | 0 | 0 | 13875.8442 | 8.374e-05%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 39 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 1.2805 | 0 | 0 | 1.2805 | 0 | 1.2215 | 10.3883 | 0.11758 | 1.2215 | 10.3883 | 0.11758 | 1.2868 | 10.9434 | 0.11758 | 0.1233% | 0.12493 | 0.12477 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8315.3648 | 0 | 0 | 8315.3648 | 4.223e-05%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 45 | 1 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 1.5829 | 0 | 0 | 1.5829 | 0 | 1.5099 | 10.3883 | 0.14535 | 1.5099 | 10.3883 | 0.14535 | 1.5906 | 10.9434 | 0.14535 | 0.1076% | 0.13116 | 0.13101 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11216.3781 | 0 | 0 | 11216.3781 | 5.22e-05%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 127 | 6 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 60.7882 | 0 | 0 | 60.7882 | 0 | 57.9878 | 62.3299 | 0.93034 | 57.9878 | 62.3299 | 0.93034 | 61.0862 | 65.6603 | 0.93034 | 0.2313% | 0.26918 | 0.26855 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97638.139 | 0 | 0 | 97638.139 | 0.002005%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 75 | 2 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 8.7481 | 0 | 0 | 8.7481 | 0 | 8.3451 | 20.7766 | 0.40166 | 8.3451 | 20.7766 | 0.40166 | 8.791 | 21.8868 | 0.40166 | 0.1312% | 0.090777 | 0.090657 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73443.4256 | 0 | 0 | 73443.4256 | 0.0002885%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 30 | 1 | 484.0355 | 97.4% | 1.48% | 1.12% | 0.7779 | 0 | 0 | 0.7779 | 0 | 0.74206 | 10.3883 | 0.071432 | 0.74206 | 10.3883 | 0.071432 | 0.78171 | 10.9434 | 0.071432 | 0.1607% | 0.071957 | 0.071838 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6727.0592 | 0 | 0 | 6727.0592 | 2.565e-05%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 22 | 1 | 400.1895 | 97.86% | 1.359% | 0.7809% | 0.88116 | 0 | 0 | 0.88116 | 0 | 0.84056 | 10.3883 | 0.080914 | 0.84056 | 10.3883 | 0.080914 | 0.88548 | 10.9434 | 0.080914 | 0.2202% | 0.059676 | 0.059541 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6706.4056 | 0 | 0 | 6706.4056 | 2.906e-05%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 32 | 1 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 3.385 | 0 | 0 | 3.385 | 0 | 3.2291 | 10.3883 | 0.31084 | 3.2291 | 10.3883 | 0.31084 | 3.4016 | 10.9434 | 0.31084 | 0.1533% | 0.070413 | 0.070304 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31362.7362 | 0 | 0 | 31362.7362 | 0.0001116%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 58 | 1 | 19489.7064 | 99% | 0.9737% | 0.02962% | 16.4666 | 0 | 0 | 16.4666 | 0 | 15.708 | 10.3883 | 1.5121 | 15.708 | 10.3883 | 1.5121 | 16.5473 | 10.9434 | 1.5121 | 0.08449% | 0.1982 | 0.19804 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98332.0942 | 0 | 0 | 98332.0942 | 0.000543%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 26 | 1 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 10.235 | 0 | 0 | 10.235 | 0 | 9.7635 | 10.3883 | 0.93985 | 9.7635 | 10.3883 | 0.93985 | 10.2851 | 10.9434 | 0.93985 | 0.1883% | 0.12528 | 0.12504 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43382.2458 | 0 | 0 | 43382.2458 | 0.0003375%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 67 | 4 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 41.157 | 0 | 0 | 41.157 | 0 | 39.261 | 41.5533 | 0.94484 | 39.261 | 41.5533 | 0.94484 | 41.3588 | 43.7735 | 0.94484 | 0.2931% | 0.15704 | 0.15658 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89411.9414 | 0 | 0 | 89411.9414 | 0.001357%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 126 | 1 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 0.70582 | 0 | 0 | 0.70582 | 0 | 0.6733 | 10.3883 | 0.064813 | 0.6733 | 10.3883 | 0.064813 | 0.70928 | 10.9434 | 0.064813 | 0.03505% | 0.19664 | 0.19656 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10240.5633 | 0 | 0 | 10240.5633 | 2.328e-05%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 84 | 3 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 4.2361 | 0 | 0 | 4.2361 | 0 | 4.041 | 31.165 | 0.12966 | 4.041 | 31.165 | 0.12966 | 4.2569 | 32.8301 | 0.12966 | 0.1553% | 0.20236 | 0.202 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13481.8255 | 0 | 0 | 13481.8255 | 0.0001397%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 71 | 1 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 7.3527 | 0 | 0 | 7.3527 | 0 | 7.0139 | 10.3883 | 0.67517 | 7.0139 | 10.3883 | 0.67517 | 7.3887 | 10.9434 | 0.67517 | 0.0688% | 0.28412 | 0.28392 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37614.1258 | 0 | 0 | 37614.1258 | 0.0002425%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 68 | 4 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 10.0801 | 0 | 0 | 10.0801 | 0 | 9.6157 | 41.5533 | 0.23141 | 9.6157 | 41.5533 | 0.23141 | 10.1295 | 43.7735 | 0.23141 | 0.2756% | 0.14269 | 0.14228 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25634.0171 | 0 | 0 | 25634.0171 | 0.0003324%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 70 | 1 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 0.92452 | 0 | 0 | 0.92452 | 0 | 0.88193 | 10.3883 | 0.084896 | 0.88193 | 10.3883 | 0.084896 | 0.92905 | 10.9434 | 0.084896 | 0.06426% | 0.18227 | 0.18214 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7893.4873 | 0 | 0 | 7893.4873 | 3.049e-05%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 48 | 1 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 10.334 | 0 | 0 | 10.334 | 0 | 9.8579 | 10.3883 | 0.94894 | 9.8579 | 10.3883 | 0.94894 | 10.3846 | 10.9434 | 0.94894 | 0.1021% | 0.2438 | 0.24354 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41498.2009 | 0 | 0 | 41498.2009 | 0.0003408%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 155 | 7 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 7.1635 | 0 | 0 | 7.1635 | 0 | 6.8335 | 72.7182 | 0.093973 | 6.8335 | 72.7182 | 0.093973 | 7.1987 | 76.6037 | 0.093973 | 0.1998% | 0.50177 | 0.50065 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7147.6994 | 0 | 0 | 7147.6994 | 0.0002362%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 17 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 10.7373 | 0 | 0 | 10.7373 | 0 | 10.2427 | 10.3883 | 0.98598 | 10.2427 | 10.3883 | 0.98598 | 10.79 | 10.9434 | 0.98598 | 0.2909% | 0.035843 | 0.035739 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102975.5205 | 0 | 0 | 102975.5205 | 0.0003541%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 77 | 3 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 5.8126 | 0 | 0 | 5.8126 | 0 | 5.5448 | 31.165 | 0.17792 | 5.5448 | 31.165 | 0.17792 | 5.8411 | 32.8301 | 0.17792 | 0.1777% | 0.19945 | 0.19906 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16398.9745 | 0 | 0 | 16398.9745 | 0.0001917%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 93 | 4 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 5.5982 | 0 | 0 | 5.5982 | 0 | 5.3403 | 41.5533 | 0.12852 | 5.3403 | 41.5533 | 0.12852 | 5.6256 | 43.7735 | 0.12852 | 0.2046% | 0.2115 | 0.21105 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12936.8565 | 0 | 0 | 12936.8565 | 0.0001846%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 72 | 1 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 2.6247 | 0 | 0 | 2.6247 | 0 | 2.5038 | 10.3883 | 0.24102 | 2.5038 | 10.3883 | 0.24102 | 2.6376 | 10.9434 | 0.24102 | 0.06671% | 0.19925 | 0.19912 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19748.0279 | 0 | 0 | 19748.0279 | 8.655e-05%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 18 | 1 | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 26.3415 | 0 | 0 | 26.3415 | 0 | 25.128 | 10.3883 | 2.4189 | 25.128 | 10.3883 | 2.4189 | 26.4707 | 10.9434 | 2.4189 | 0.2739% | 0.37266 | 0.37163 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25809.3861 | 0 | 0 | 25809.3861 | 0.0008686%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 23 | 1 | 1359.3953 | 95.15% | 4.696% | 0.1502% | 2.7839 | 0 | 0 | 2.7839 | 0 | 2.6556 | 10.3883 | 0.25564 | 2.6556 | 10.3883 | 0.25564 | 2.7975 | 10.9434 | 0.25564 | 0.2048% | 0.23465 | 0.23414 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5793.9539 | 0 | 0 | 5793.9539 | 9.18e-05%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 137 | 9 | 7406.689 | 96.62% | 3.25% | 0.1263% | 23.2721 | 0 | 0 | 23.2721 | 0 | 22.2 | 93.4949 | 0.23745 | 22.2 | 93.4949 | 0.23745 | 23.3861 | 98.4904 | 0.23745 | 0.3142% | 0.26901 | 0.26813 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27536.333 | 0 | 0 | 27536.333 | 0.0007674%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 212 | 4 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 73.4115 | 0 | 0 | 73.4115 | 0 | 70.0295 | 41.5533 | 1.6853 | 70.0295 | 41.5533 | 1.6853 | 73.7713 | 43.7735 | 1.6853 | 0.0927% | 0.41507 | 0.41468 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190798.8152 | 0 | 0 | 190798.8152 | 0.002421%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 81 | 2 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 54.926 | 0 | 0 | 54.926 | 0 | 52.3956 | 20.7766 | 2.5219 | 52.3956 | 20.7766 | 2.5219 | 55.1952 | 21.8868 | 2.5219 | 0.1218% | 0.41211 | 0.41161 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109452.985 | 0 | 0 | 109452.985 | 0.001811%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 132 | 2 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 5.3502 | 0 | 0 | 5.3502 | 0 | 5.1037 | 20.7766 | 0.24565 | 5.1037 | 20.7766 | 0.24565 | 5.3764 | 21.8868 | 0.24565 | 0.07204% | 0.27927 | 0.27906 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26594.9041 | 0 | 0 | 26594.9041 | 0.0001764%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 1220 | 8 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 5.2642 | 0 | 0 | 5.2642 | 0 | 5.0217 | 83.1066 | 0.060425 | 5.0217 | 83.1066 | 0.060425 | 5.29 | 87.5471 | 0.060425 | 0.03139% | 0.35117 | 0.35106 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47761.8158 | 0 | 0 | 47761.8158 | 0.0001736%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 52 | 1 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 1.8088 | 0 | 0 | 1.8088 | 0 | 1.7254 | 10.3883 | 0.16609 | 1.7254 | 10.3883 | 0.16609 | 1.8176 | 10.9434 | 0.16609 | 0.09042% | 0.093988 | 0.093899 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21285.2364 | 0 | 0 | 21285.2364 | 5.965e-05%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 84 | 3 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 11.0981 | 0 | 0 | 11.0981 | 0 | 10.5868 | 31.165 | 0.3397 | 10.5868 | 31.165 | 0.3397 | 11.1525 | 32.8301 | 0.3397 | 0.1737% | 0.095565 | 0.095396 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66854.1544 | 0 | 0 | 66854.1544 | 0.000366%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 57 | 3 | 2072.8837 | 91.06% | 8.635% | 0.3% | 4.9179 | 0 | 0 | 4.9179 | 0 | 4.6913 | 31.165 | 0.15053 | 4.6913 | 31.165 | 0.15053 | 4.942 | 32.8301 | 0.15053 | 0.2372% | 0.084625 | 0.084405 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24500.6503 | 0 | 0 | 24500.6503 | 0.0001622%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 17 | 2 | 536.3838 | 78.97% | 20.71% | 0.32% | 2.4667 | 0 | 0 | 2.4667 | 0 | 2.3531 | 20.7766 | 0.11325 | 2.3531 | 20.7766 | 0.11325 | 2.4788 | 21.8868 | 0.11325 | 0.4599% | 0.062818 | 0.062452 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8549.2159 | 0 | 0 | 8549.2159 | 8.134e-05%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 151 | 9 | 5142.095 | 98.68% | 0.901% | 0.4182% | 14.9708 | 0 | 0 | 14.9708 | 0 | 14.2811 | 93.4949 | 0.15275 | 14.2811 | 93.4949 | 0.15275 | 15.0441 | 98.4904 | 0.15275 | 0.2911% | 0.11648 | 0.11613 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44148.5933 | 0 | 0 | 44148.5933 | 0.0004937%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 50 | 1 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 2.4573 | 0 | 0 | 2.4573 | 0 | 2.3441 | 10.3883 | 0.22565 | 2.3441 | 10.3883 | 0.22565 | 2.4694 | 10.9434 | 0.22565 | 0.09829% | 0.037573 | 0.037535 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66537.6281 | 0 | 0 | 66537.6281 | 8.103e-05%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 57 | 2 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 5.2115 | 0 | 0 | 5.2115 | 0 | 4.9714 | 20.7766 | 0.23928 | 4.9714 | 20.7766 | 0.23928 | 5.237 | 21.8868 | 0.23928 | 0.1717% | 0.06125 | 0.061144 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49564.8327 | 0 | 0 | 49564.8327 | 0.0001719%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 47 | 2 | 718.991 | 97.57% | 1.357% | 1.072% | 1.4777 | 0 | 0 | 1.4777 | 0 | 1.4096 | 20.7766 | 0.067845 | 1.4096 | 20.7766 | 0.067845 | 1.4849 | 21.8868 | 0.067845 | 0.2055% | 0.044487 | 0.044393 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16162.6514 | 0 | 0 | 16162.6514 | 4.873e-05%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 79 | 1 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 1.2604 | 0 | 0 | 1.2604 | 0 | 1.2023 | 10.3883 | 0.11574 | 1.2023 | 10.3883 | 0.11574 | 1.2666 | 10.9434 | 0.11574 | 0.05382% | 0.1204 | 0.12032 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19451.4533 | 0 | 0 | 19451.4533 | 4.156e-05%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 102 | 5 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 9.8893 | 0 | 0 | 9.8893 | 0 | 9.4337 | 51.9416 | 0.18162 | 9.4337 | 51.9416 | 0.18162 | 9.9378 | 54.7169 | 0.18162 | 0.2396% | 0.075451 | 0.075268 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54708.504 | 0 | 0 | 54708.504 | 0.0003261%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 17 | 1 | 3294.853 | 98.88% | 0.9043% | 0.2189% | 9.4861 | 0 | 0 | 9.4861 | 0 | 9.0491 | 10.3883 | 0.87108 | 9.0491 | 10.3883 | 0.87108 | 9.5326 | 10.9434 | 0.87108 | 0.2879% | 0.044658 | 0.044528 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73782.1004 | 0 | 0 | 73782.1004 | 0.0003128%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 14 | 1 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 13.7096 | 0 | 0 | 13.7096 | 0 | 13.078 | 10.3883 | 1.2589 | 13.078 | 10.3883 | 1.2589 | 13.7768 | 10.9434 | 1.2589 | 0.3134% | 0.1179 | 0.11748 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37123.0171 | 0 | 0 | 37123.0171 | 0.0004521%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 37 | 1 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 3.6741 | 0 | 0 | 3.6741 | 0 | 3.5048 | 10.3883 | 0.33738 | 3.5048 | 10.3883 | 0.33738 | 3.6921 | 10.9434 | 0.33738 | 0.1301% | 0.17766 | 0.17742 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15894.1147 | 0 | 0 | 15894.1147 | 0.0001212%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 25 | 1 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 4.4138 | 0 | 0 | 4.4138 | 0 | 4.2104 | 10.3883 | 0.4053 | 4.2104 | 10.3883 | 0.4053 | 4.4354 | 10.9434 | 0.4053 | 0.1952% | 0.17215 | 0.17181 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13132.0828 | 0 | 0 | 13132.0828 | 0.0001455%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 51 | 2 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 10.1511 | 0 | 0 | 10.1511 | 0 | 9.6834 | 20.7766 | 0.46607 | 9.6834 | 20.7766 | 0.46607 | 10.2008 | 21.8868 | 0.46607 | 0.1904% | 0.18129 | 0.18094 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29412.6917 | 0 | 0 | 29412.6917 | 0.0003347%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 124 | 4 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 33.3337 | 0 | 0 | 33.3337 | 0 | 31.7981 | 41.5533 | 0.76524 | 31.7981 | 41.5533 | 0.76524 | 33.4971 | 43.7735 | 0.76524 | 0.1571% | 0.21435 | 0.214 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99015.3661 | 0 | 0 | 99015.3661 | 0.001099%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 56 | 1 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 5.9917 | 0 | 0 | 5.9917 | 0 | 5.7157 | 10.3883 | 0.5502 | 5.7157 | 10.3883 | 0.5502 | 6.0211 | 10.9434 | 0.5502 | 0.08649% | 0.18488 | 0.18471 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37473.8225 | 0 | 0 | 37473.8225 | 0.0001976%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 32 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 19.1946 | 0 | 0 | 19.1946 | 0 | 18.3103 | 10.3883 | 1.7626 | 18.3103 | 10.3883 | 1.7626 | 19.2886 | 10.9434 | 1.7626 | 0.151% | 0.1419 | 0.14168 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89583.9404 | 0 | 0 | 89583.9404 | 0.000633%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 16 | 1 | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 11.1752 | 0 | 0 | 11.1752 | 0 | 10.6604 | 10.3883 | 1.0262 | 10.6604 | 10.3883 | 1.0262 | 11.23 | 10.9434 | 1.0262 | 0.3075% | 0.14935 | 0.14889 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24333.1512 | 0 | 0 | 24333.1512 | 0.0003685%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 62 | 2 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 44.8119 | 0 | 0 | 44.8119 | 0 | 42.7475 | 20.7766 | 2.0575 | 42.7475 | 20.7766 | 2.0575 | 45.0316 | 21.8868 | 2.0575 | 0.1586% | 0.25909 | 0.25867 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109035.8326 | 0 | 0 | 109035.8326 | 0.001478%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 71 | 2 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 37.3421 | 0 | 0 | 37.3421 | 0 | 35.6218 | 20.7766 | 1.7145 | 35.6218 | 20.7766 | 1.7145 | 37.5251 | 21.8868 | 1.7145 | 0.1379% | 0.15539 | 0.15517 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174277.5099 | 0 | 0 | 174277.5099 | 0.001231%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 13 | 1 | 2530.2255 | 98.83% | 1.116% | 0.05734% | 9.5212 | 0 | 0 | 9.5212 | 0 | 9.0826 | 10.3883 | 0.87431 | 9.0826 | 10.3883 | 0.87431 | 9.5679 | 10.9434 | 0.87431 | 0.3763% | 0.10804 | 0.10763 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23419.4798 | 0 | 0 | 23419.4798 | 0.000314%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 165 | 1 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 9.1859 | 0 | 0 | 9.1859 | 0 | 8.7627 | 10.3883 | 0.84352 | 8.7627 | 10.3883 | 0.84352 | 9.2309 | 10.9434 | 0.84352 | 0.02973% | 0.18156 | 0.1815 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170161.8204 | 0 | 0 | 170161.8204 | 0.0003029%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 182 | 6 | 65515.492 | 98.93% | 1.038% | 0.03019% | 105.7706 | 0 | 0 | 105.7706 | 0 | 100.898 | 62.3299 | 1.6188 | 100.898 | 62.3299 | 1.6188 | 106.2891 | 65.6603 | 1.6188 | 0.1614% | 0.49249 | 0.49168 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133032.7001 | 0 | 0 | 133032.7001 | 0.003488%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 23 | 1 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 2.3177 | 0 | 0 | 2.3177 | 0 | 2.2109 | 10.3883 | 0.21283 | 2.2109 | 10.3883 | 0.21283 | 2.3291 | 10.9434 | 0.21283 | 0.2076% | 0.1294 | 0.12913 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8628.4088 | 0 | 0 | 8628.4088 | 7.643e-05%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 72 | 1 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 4.2338 | 0 | 0 | 4.2338 | 0 | 4.0388 | 10.3883 | 0.38878 | 4.0388 | 10.3883 | 0.38878 | 4.2546 | 10.9434 | 0.38878 | 0.06754% | 0.15408 | 0.15397 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40686.0315 | 0 | 0 | 40686.0315 | 0.0001396%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 17 | 1 | 376.72 | 96.88% | 2.523% | 0.5996% | 1.0627 | 0 | 0 | 1.0627 | 0 | 1.0137 | 10.3883 | 0.097582 | 1.0137 | 10.3883 | 0.097582 | 1.0679 | 10.9434 | 0.097582 | 0.2821% | 0.037482 | 0.037373 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10051.5548 | 0 | 0 | 10051.5548 | 3.504e-05%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 73 | 1 | 4437.6588 | 97.91% | 1.769% | 0.321% | 2.9462 | 0 | 0 | 2.9462 | 0 | 2.8105 | 10.3883 | 0.27054 | 2.8105 | 10.3883 | 0.27054 | 2.9606 | 10.9434 | 0.27054 | 0.06639% | 0.095775 | 0.09571 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46334.6715 | 0 | 0 | 46334.6715 | 9.716e-05%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 50 | 1 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 3.6705 | 0 | 0 | 3.6705 | 0 | 3.5014 | 10.3883 | 0.33706 | 3.5014 | 10.3883 | 0.33706 | 3.6885 | 10.9434 | 0.33706 | 0.09808% | 0.06999 | 0.069921 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53473.2976 | 0 | 0 | 53473.2976 | 0.000121%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 104 | 3 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 5.0676 | 0 | 0 | 5.0676 | 0 | 4.8342 | 31.165 | 0.15512 | 4.8342 | 31.165 | 0.15512 | 5.0925 | 32.8301 | 0.15512 | 0.1382% | 0.12278 | 0.1226 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29858.2626 | 0 | 0 | 29858.2626 | 0.0001671%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 9 | 1 | 406.8184 | 64.36% | 35.02% | 0.6193% | 1.4401 | 0 | 0 | 1.4401 | 0 | 1.3738 | 10.3883 | 0.13224 | 1.3738 | 10.3883 | 0.13224 | 1.4472 | 10.9434 | 0.13224 | 0.354% | 0.1014 | 0.10085 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4019.7327 | 0 | 0 | 4019.7327 | 4.749e-05%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 71 | 1 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 2.2325 | 0 | 0 | 2.2325 | 0 | 2.1297 | 10.3883 | 0.20501 | 2.1297 | 10.3883 | 0.20501 | 2.2435 | 10.9434 | 0.20501 | 0.06592% | 0.070488 | 0.070439 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48052.6431 | 0 | 0 | 48052.6431 | 7.362e-05%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 24 | 1 | 1438.4419 | 90% | 9.47% | 0.5268% | 2.6702 | 0 | 0 | 2.6702 | 0 | 2.5472 | 10.3883 | 0.2452 | 2.5472 | 10.3883 | 0.2452 | 2.6833 | 10.9434 | 0.2452 | 0.1856% | 0.066431 | 0.066294 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21657.5153 | 0 | 0 | 21657.5153 | 8.805e-05%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 33 | 1 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 1.8877 | 0 | 0 | 1.8877 | 0 | 1.8008 | 10.3883 | 0.17335 | 1.8008 | 10.3883 | 0.17335 | 1.897 | 10.9434 | 0.17335 | 0.1388% | 0.045228 | 0.045161 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30080.3441 | 0 | 0 | 30080.3441 | 6.225e-05%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 30 | 1 | 962.1527 | 99.5% | 0% | 0.4991% | 1.5796 | 0 | 0 | 1.5796 | 0 | 1.5069 | 10.3883 | 0.14505 | 1.5069 | 10.3883 | 0.14505 | 1.5874 | 10.9434 | 0.14505 | 0.1642% | 0.01881 | 0.018779 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51151.0057 | 0 | 0 | 51151.0057 | 5.209e-05%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 99 | 1 | 3753.23 | 95.85% | 3.876% | 0.273% | 1.7988 | 0 | 0 | 1.7988 | 0 | 1.7159 | 10.3883 | 0.16517 | 1.7159 | 10.3883 | 0.16517 | 1.8076 | 10.9434 | 0.16517 | 0.04793% | 0.10094 | 0.10089 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37184.7327 | 0 | 0 | 37184.7327 | 5.932e-05%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 29 | 1 | 5299.6344 | 98.55% | 1.37% | 0.07601% | 8.9152 | 0 | 0 | 8.9152 | 0 | 8.5045 | 10.3883 | 0.81866 | 8.5045 | 10.3883 | 0.81866 | 8.9589 | 10.9434 | 0.81866 | 0.1682% | 0.20157 | 0.20123 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26292.2225 | 0 | 0 | 26292.2225 | 0.000294%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 40 | 3 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 6.5635 | 0 | 0 | 6.5635 | 0 | 6.2611 | 31.165 | 0.2009 | 6.2611 | 31.165 | 0.2009 | 6.5957 | 32.8301 | 0.2009 | 0.326% | 0.19011 | 0.18941 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10596.2691 | 0 | 0 | 10596.2691 | 0.0002164%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 1 | 1 | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 68.6427 | 10.3883 | 6.6077 | 68.6427 | 10.3883 | 6.6077 | 72.3104 | 10.9434 | 6.6077 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 138 | 3 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 3.7011 | 0 | 0 | 3.7011 | 0 | 3.5306 | 31.165 | 0.11329 | 3.5306 | 31.165 | 0.11329 | 3.7192 | 32.8301 | 0.11329 | 0.1027% | 0.15121 | 0.15105 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23822.4131 | 0 | 0 | 23822.4131 | 0.000122%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 245 | 6 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 16.5026 | 0 | 0 | 16.5026 | 0 | 15.7423 | 62.3299 | 0.25256 | 15.7423 | 62.3299 | 0.25256 | 16.5835 | 65.6603 | 0.25256 | 0.119% | 0.18928 | 0.18905 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73289.2277 | 0 | 0 | 73289.2277 | 0.0005442%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 229 | 5 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 5.8394 | 0 | 0 | 5.8394 | 0 | 5.5703 | 51.9416 | 0.10724 | 5.5703 | 51.9416 | 0.10724 | 5.868 | 54.7169 | 0.10724 | 0.1048% | 0.19915 | 0.19893 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 27973.644 | 0 | 0 | 27973.644 | 0.0001926%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 92 | 2 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 14.4464 | 0 | 0 | 14.4464 | 0 | 13.7809 | 20.7766 | 0.66329 | 13.7809 | 20.7766 | 0.66329 | 14.5172 | 21.8868 | 0.66329 | 0.1068% | 0.1241 | 0.12397 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108956.3195 | 0 | 0 | 108956.3195 | 0.0004764%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 107 | 3 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 15.371 | 0 | 0 | 15.371 | 0 | 14.6629 | 31.165 | 0.47049 | 14.6629 | 31.165 | 0.47049 | 15.4464 | 32.8301 | 0.47049 | 0.1372% | 0.12896 | 0.12878 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86858.7423 | 0 | 0 | 86858.7423 | 0.0005069%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 7 | 1 | 2519.0591 | 99.18% | 0.76% | 0.05848% | 17.6675 | 0 | 0 | 17.6675 | 0 | 16.8536 | 10.3883 | 1.6224 | 16.8536 | 10.3883 | 1.6224 | 17.7541 | 10.9434 | 1.6224 | 0.7014% | 0.10537 | 0.10463 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23907.5547 | 0 | 0 | 23907.5547 | 0.0005826%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 7 | 1 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 12.4897 | 0 | 0 | 12.4897 | 0 | 11.9143 | 10.3883 | 1.1469 | 11.9143 | 10.3883 | 1.1469 | 12.5509 | 10.9434 | 1.1469 | 0.6272% | 0.10085 | 0.10014 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19761.1324 | 0 | 0 | 19761.1324 | 0.0004119%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 42 | 1 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 15.8607 | 0 | 0 | 15.8607 | 0 | 15.1301 | 10.3883 | 1.4565 | 15.1301 | 10.3883 | 1.4565 | 15.9385 | 10.9434 | 1.4565 | 0.1172% | 0.12577 | 0.12562 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107612.226 | 0 | 0 | 107612.226 | 0.000523%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 121 | 2 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 16.6413 | 0 | 0 | 16.6413 | 0 | 15.8747 | 20.7766 | 0.76406 | 15.8747 | 20.7766 | 0.76406 | 16.7229 | 21.8868 | 0.76406 | 0.08114% | 0.13939 | 0.13928 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147144.8233 | 0 | 0 | 147144.8233 | 0.0005488%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 83 | 1 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 6.6539 | 0 | 0 | 6.6539 | 0 | 6.3474 | 10.3883 | 0.61101 | 6.3474 | 10.3883 | 0.61101 | 6.6865 | 10.9434 | 0.61101 | 0.05894% | 0.1048 | 0.10474 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107710.5407 | 0 | 0 | 107710.5407 | 0.0002194%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 50 | 1 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 5.283 | 0 | 0 | 5.283 | 0 | 5.0396 | 10.3883 | 0.48512 | 5.0396 | 10.3883 | 0.48512 | 5.3089 | 10.9434 | 0.48512 | 0.09716% | 0.090754 | 0.090664 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59915.1296 | 0 | 0 | 59915.1296 | 0.0001742%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 140 | 2 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 11.07 | 0 | 0 | 11.07 | 0 | 10.56 | 20.7766 | 0.50826 | 10.56 | 20.7766 | 0.50826 | 11.1243 | 21.8868 | 0.50826 | 0.06913% | 0.16775 | 0.16764 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95455.3737 | 0 | 0 | 95455.3737 | 0.000365%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 92 | 2 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 9.543 | 0 | 0 | 9.543 | 0 | 9.1033 | 20.7766 | 0.43815 | 9.1033 | 20.7766 | 0.43815 | 9.5897 | 21.8868 | 0.43815 | 0.1027% | 0.14106 | 0.14091 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 65895.647 | 0 | 0 | 65895.647 | 0.0003147%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 84 | 1 | 16869.708 | 98.79% | 1.184% | 0.02933% | 9.8204 | 0 | 0 | 9.8204 | 0 | 9.368 | 10.3883 | 0.90178 | 9.368 | 10.3883 | 0.90178 | 9.8686 | 10.9434 | 0.90178 | 0.05821% | 0.18286 | 0.18276 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92253.9208 | 0 | 0 | 92253.9208 | 0.0003238%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 116 | 3 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 22.0827 | 0 | 0 | 22.0827 | 0 | 21.0654 | 31.165 | 0.67593 | 21.0654 | 31.165 | 0.67593 | 22.1909 | 32.8301 | 0.67593 | 0.1248% | 0.18538 | 0.18514 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95465.2311 | 0 | 0 | 95465.2311 | 0.0007282%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 116 | 4 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 17.2798 | 0 | 0 | 17.2798 | 0 | 16.4837 | 41.5533 | 0.39669 | 16.4837 | 41.5533 | 0.39669 | 17.3645 | 43.7735 | 0.39669 | 0.1656% | 0.14913 | 0.14887 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 69960.7117 | 0 | 0 | 69960.7117 | 0.0005698%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 94 | 3 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 18.167 | 0 | 0 | 18.167 | 0 | 17.3301 | 31.165 | 0.55608 | 17.3301 | 31.165 | 0.55608 | 18.2561 | 32.8301 | 0.55608 | 0.1545% | 0.171 | 0.17073 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68759.2242 | 0 | 0 | 68759.2242 | 0.0005991%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 53 | 1 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 5.4794 | 0 | 0 | 5.4794 | 0 | 5.227 | 10.3883 | 0.50316 | 5.227 | 10.3883 | 0.50316 | 5.5063 | 10.9434 | 0.50316 | 0.08967% | 0.12773 | 0.12761 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47842.8551 | 0 | 0 | 47842.8551 | 0.0001807%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 99 | 7 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 129.7557 | 0 | 0 | 129.7557 | 0 | 123.7781 | 72.7182 | 1.7022 | 123.7781 | 72.7182 | 1.7022 | 130.3918 | 76.6037 | 1.7022 | 0.3451% | 0.54241 | 0.54052 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69327.0248 | 0 | 0 | 69327.0248 | 0.004279%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 2 | 1 | 924.8041 | 18.79% | 81.02% | 0.1888% | 4.3002 | 0 | 0 | 4.3002 | 0 | 4.1021 | 10.3883 | 0.39488 | 4.1021 | 10.3883 | 0.39488 | 4.3213 | 10.9434 | 0.39488 | 0.465% | 0.10079 | 0.098298 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9364.3855 | 0 | 0 | 9364.3855 | 0.0001418%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 65 | 2 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 4.2131 | 0 | 0 | 4.2131 | 0 | 4.019 | 20.7766 | 0.19344 | 4.019 | 20.7766 | 0.19344 | 4.2338 | 21.8868 | 0.19344 | 0.1343% | 0.15664 | 0.1564 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20030.4988 | 0 | 0 | 20030.4988 | 0.0001389%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 90 | 2 | 6370.0414 | 98.47% | 1.262% | 0.272% | 6.8995 | 0 | 0 | 6.8995 | 0 | 6.5817 | 20.7766 | 0.31678 | 6.5817 | 20.7766 | 0.31678 | 6.9334 | 21.8868 | 0.31678 | 0.1083% | 0.10309 | 0.10298 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61790.4359 | 0 | 0 | 61790.4359 | 0.0002275%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 27 | 1 | 4750.1268 | 98% | 1.916% | 0.08125% | 8.5346 | 0 | 0 | 8.5346 | 0 | 8.1414 | 10.3883 | 0.78371 | 8.1414 | 10.3883 | 0.78371 | 8.5764 | 10.9434 | 0.78371 | 0.1797% | 0.55752 | 0.5565 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8520.3954 | 0 | 0 | 8520.3954 | 0.0002814%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 31 | 1 | 852.9261 | 84.92% | 14.72% | 0.3553% | 1.1566 | 0 | 0 | 1.1566 | 0 | 1.1033 | 10.3883 | 0.10621 | 1.1033 | 10.3883 | 0.10621 | 1.1623 | 10.9434 | 0.10621 | 0.1356% | 0.36954 | 0.36895 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2308.6153 | 0 | 0 | 2308.6153 | 3.814e-05%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 22 | 1 | 526.1263 | 57.95% | 41.57% | 0.4783% | 0.68603 | 0 | 0 | 0.68603 | 0 | 0.65443 | 10.3883 | 0.062997 | 0.65443 | 10.3883 | 0.062997 | 0.6894 | 10.9434 | 0.062997 | 0.1304% | 0.36155 | 0.36074 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1456.5724 | 0 | 0 | 1456.5724 | 2.262e-05%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 161 | 4 | 11572.221 | 88.48% | 11.4% | 0.1243% | 12.5917 | 0 | 0 | 12.5917 | 0 | 12.0116 | 41.5533 | 0.28906 | 12.0116 | 41.5533 | 0.28906 | 12.6534 | 43.7735 | 0.28906 | 0.1088% | 0.35802 | 0.35758 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32327.6009 | 0 | 0 | 32327.6009 | 0.0004152%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 16 | 3 | 141.3846 | 51% | 48.51% | 0.49% | 0.66925 | 0 | 0 | 0.66925 | 0 | 0.63842 | 31.165 | 0.020485 | 0.63842 | 31.165 | 0.020485 | 0.67253 | 32.8301 | 0.020485 | 0.4734% | 0.34601 | 0.34279 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 410.4952 | 0 | 0 | 410.4952 | 2.207e-05%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 13 | 1 | 333.8465 | 96.62% | 2.31% | 1.072% | 1.2282 | 0 | 0 | 1.2282 | 0 | 1.1716 | 10.3883 | 0.11278 | 1.1716 | 10.3883 | 0.11278 | 1.2342 | 10.9434 | 0.11278 | 0.3679% | 0.14886 | 0.14829 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2242.9625 | 0 | 0 | 2242.9625 | 4.05e-05%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 102 | 1 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 1.6181 | 0 | 0 | 1.6181 | 0 | 1.5436 | 10.3883 | 0.14859 | 1.5436 | 10.3883 | 0.14859 | 1.626 | 10.9434 | 0.14859 | 0.0474% | 0.2124 | 0.2123 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16072.5394 | 0 | 0 | 16072.5394 | 5.336e-05%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 85 | 1 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 5.3267 | 0 | 0 | 5.3267 | 0 | 5.0813 | 10.3883 | 0.48914 | 5.0813 | 10.3883 | 0.48914 | 5.3528 | 10.9434 | 0.48914 | 0.0553% | 0.53792 | 0.53761 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17907.5661 | 0 | 0 | 17907.5661 | 0.0001757%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 76 | 1 | 7250.7229 | 96.11% | 3.805% | 0.08959% | 4.5386 | 0 | 0 | 4.5386 | 0 | 4.3295 | 10.3883 | 0.41677 | 4.3295 | 10.3883 | 0.41677 | 4.5608 | 10.9434 | 0.41677 | 0.06259% | 0.57356 | 0.57319 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12641.8974 | 0 | 0 | 12641.8974 | 0.0001497%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 116 | 3 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 13.0089 | 0 | 0 | 13.0089 | 0 | 12.4096 | 31.165 | 0.39819 | 12.4096 | 31.165 | 0.39819 | 13.0727 | 32.8301 | 0.39819 | 0.1225% | 0.6048 | 0.60402 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17560.2976 | 0 | 0 | 17560.2976 | 0.000429%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 65 | 1 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 1.1399 | 0 | 0 | 1.1399 | 0 | 1.0874 | 10.3883 | 0.10468 | 1.0874 | 10.3883 | 0.10468 | 1.1455 | 10.9434 | 0.10468 | 0.06452% | 0.56527 | 0.56484 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3125.7794 | 0 | 0 | 3125.7794 | 3.759e-05%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 9 | 1 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 7.2298 | 0 | 0 | 7.2298 | 0 | 6.8967 | 10.3883 | 0.66389 | 6.8967 | 10.3883 | 0.66389 | 7.2652 | 10.9434 | 0.66389 | 0.5348% | 0.75637 | 0.75221 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1787.4653 | 0 | 0 | 1787.4653 | 0.0002384%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 85 | 2 | 2119.752 | 55.7% | 43.96% | 0.3458% | 1.3751 | 0 | 0 | 1.3751 | 0 | 1.3118 | 20.7766 | 0.063137 | 1.3118 | 20.7766 | 0.063137 | 1.3819 | 21.8868 | 0.063137 | 0.06487% | 0.46343 | 0.46289 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4576.4268 | 0 | 0 | 4576.4268 | 4.535e-05%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 49 | 2 | 520.639 | 76.18% | 22.78% | 1.038% | 0.80139 | 0 | 0 | 0.80139 | 0 | 0.76447 | 20.7766 | 0.036795 | 0.76447 | 20.7766 | 0.036795 | 0.80532 | 21.8868 | 0.036795 | 0.1539% | 0.55035 | 0.54924 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 946.4715 | 0 | 0 | 946.4715 | 2.643e-05%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 224 | 9 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 16.6012 | 0 | 0 | 16.6012 | 0 | 15.8365 | 93.4949 | 0.16938 | 15.8365 | 93.4949 | 0.16938 | 16.6826 | 98.4904 | 0.16938 | 0.1823% | 0.49442 | 0.49343 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18417.7577 | 0 | 0 | 18417.7577 | 0.0005474%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 147 | 8 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 16.4058 | 0 | 0 | 16.4058 | 0 | 15.65 | 83.1066 | 0.18831 | 15.65 | 83.1066 | 0.18831 | 16.4862 | 87.5471 | 0.18831 | 0.2438% | 0.28234 | 0.28158 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23842.4221 | 0 | 0 | 23842.4221 | 0.000541%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 34 | 1 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 7.565 | 0 | 0 | 7.565 | 0 | 7.2165 | 10.3883 | 0.69467 | 7.2165 | 10.3883 | 0.69467 | 7.6021 | 10.9434 | 0.69467 | 0.1438% | 0.26107 | 0.26069 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20150.8236 | 0 | 0 | 20150.8236 | 0.0002495%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 45 | 4 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 9.7535 | 0 | 0 | 9.7535 | 0 | 9.3042 | 41.5533 | 0.22391 | 9.3042 | 41.5533 | 0.22391 | 9.8013 | 43.7735 | 0.22391 | 0.4204% | 0.24779 | 0.2467 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9364.7502 | 0 | 0 | 9364.7502 | 0.0003216%
2026 | 461 | CB 461 | Tier-2 | Tier-2---15 | 2--4 | 2 | 2 | 101.8709 | 98.65% | 0% | 1.347% | 4.9747 | 0 | 0 | 4.9747 | 0 | 4.7455 | 20.7766 | 0.22841 | 4.7455 | 20.7766 | 0.22841 | 4.9991 | 21.8868 | 0.22841 | 4.883% | 0.0097562 | 0.0092733 | 10441.6529 | 2274.299 | 1515.1673 | 6652.1866 | 10448.9777 | 0 | 0 | 10448.9777 | 0.000164%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 20 | 1 | 1378.3182 | 99.02% | 0.574% | 0.4088% | 3.3778 | 0 | 0 | 3.3778 | 0 | 3.2222 | 10.3883 | 0.31018 | 3.2222 | 10.3883 | 0.31018 | 3.3944 | 10.9434 | 0.31018 | 0.2451% | 0.096723 | 0.096483 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14250.5366 | 0 | 0 | 14250.5366 | 0.0001114%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 20 | 3 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 38.439 | 0 | 0 | 38.439 | 0 | 36.6682 | 31.165 | 1.1766 | 36.6682 | 31.165 | 1.1766 | 38.6274 | 32.8301 | 1.1766 | 0.7301% | 0.091034 | 0.090358 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57842.4229 | 0 | 0 | 57842.4229 | 0.001268%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 6 | 1 | 4253.6671 | 94.96% | 4.983% | 0.06005% | 33.3231 | 0 | 0 | 33.3231 | 0 | 31.788 | 10.3883 | 3.06 | 31.788 | 10.3883 | 3.06 | 33.4865 | 10.9434 | 3.06 | 0.7834% | 0.093079 | 0.092311 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45718.8045 | 0 | 0 | 45718.8045 | 0.001099%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 1 | 1 | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 9.6013 | 10.3883 | 0.92424 | 9.6013 | 10.3883 | 0.92424 | 10.1143 | 10.9434 | 0.92424 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 27 | 1 | 1478.7446 | 97.97% | 1.759% | 0.2664% | 2.6561 | 0 | 0 | 2.6561 | 0 | 2.5337 | 10.3883 | 0.2439 | 2.5337 | 10.3883 | 0.2439 | 2.6691 | 10.9434 | 0.2439 | 0.1796% | 0.046043 | 0.045959 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32117.5165 | 0 | 0 | 32117.5165 | 8.759e-05%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 129 | 2 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 1.9588 | 0 | 0 | 1.9588 | 0 | 1.8686 | 20.7766 | 0.089935 | 1.8686 | 20.7766 | 0.089935 | 1.9684 | 21.8868 | 0.089935 | 0.07425% | 0.13822 | 0.13811 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19085.8993 | 0 | 0 | 19085.8993 | 6.459e-05%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 53 | 1 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 6.1091 | 0 | 0 | 6.1091 | 0 | 5.8276 | 10.3883 | 0.56098 | 5.8276 | 10.3883 | 0.56098 | 6.139 | 10.9434 | 0.56098 | 0.09033% | 0.27105 | 0.27079 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24952.2153 | 0 | 0 | 24952.2153 | 0.0002015%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 19 | 1 | 2084.5359 | 96.48% | 3.265% | 0.2521% | 5.2397 | 0 | 0 | 5.2397 | 0 | 4.9984 | 10.3883 | 0.48115 | 4.9984 | 10.3883 | 0.48115 | 5.2654 | 10.9434 | 0.48115 | 0.2514% | 0.05278 | 0.052642 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39498.7345 | 0 | 0 | 39498.7345 | 0.0001728%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 89 | 1 | 4997.7942 | 96.49% | 3.313% | 0.193% | 2.6822 | 0 | 0 | 2.6822 | 0 | 2.5587 | 10.3883 | 0.2463 | 2.5587 | 10.3883 | 0.2463 | 2.6954 | 10.9434 | 0.2463 | 0.05367% | 0.28544 | 0.28528 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17509.3811 | 0 | 0 | 17509.3811 | 8.845e-05%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 74 | 3 | 2044.6463 | 97.57% | 2.13% | 0.298% | 4.0035 | 0 | 0 | 4.0035 | 0 | 3.819 | 31.165 | 0.12254 | 3.819 | 31.165 | 0.12254 | 4.0231 | 32.8301 | 0.12254 | 0.1958% | 0.10446 | 0.10425 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19574.141 | 0 | 0 | 19574.141 | 0.000132%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 49 | 1 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 11.0867 | 0 | 0 | 11.0867 | 0 | 10.576 | 10.3883 | 1.0181 | 10.576 | 10.3883 | 1.0181 | 11.1411 | 10.9434 | 1.0181 | 0.09768% | 0.27097 | 0.27069 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41889.7291 | 0 | 0 | 41889.7291 | 0.0003656%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 87 | 3 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 14.1513 | 0 | 0 | 14.1513 | 0 | 13.4993 | 31.165 | 0.43316 | 13.4993 | 31.165 | 0.43316 | 14.2206 | 32.8301 | 0.43316 | 0.1669% | 0.15411 | 0.15384 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55014.7612 | 0 | 0 | 55014.7612 | 0.0004667%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 73 | 2 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 11.7409 | 0 | 0 | 11.7409 | 0 | 11.2 | 20.7766 | 0.53907 | 11.2 | 20.7766 | 0.53907 | 11.7984 | 21.8868 | 0.53907 | 0.1348% | 0.071321 | 0.071224 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122166.9405 | 0 | 0 | 122166.9405 | 0.0003872%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 42 | 1 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 14.3381 | 0 | 0 | 14.3381 | 0 | 13.6776 | 10.3883 | 1.3166 | 13.6776 | 10.3883 | 1.3166 | 14.4084 | 10.9434 | 1.3166 | 0.1171% | 0.14844 | 0.14826 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82471.1507 | 0 | 0 | 82471.1507 | 0.0004728%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 37 | 1 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 11.9431 | 0 | 0 | 11.9431 | 0 | 11.3929 | 10.3883 | 1.0967 | 11.3929 | 10.3883 | 1.0967 | 12.0016 | 10.9434 | 1.0967 | 0.1325% | 0.074421 | 0.074321 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121104.3584 | 0 | 0 | 121104.3584 | 0.0003938%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 46 | 1 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 5.871 | 0 | 0 | 5.871 | 0 | 5.6005 | 10.3883 | 0.53912 | 5.6005 | 10.3883 | 0.53912 | 5.8998 | 10.9434 | 0.53912 | 0.1074% | 0.040404 | 0.04036 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135337.4607 | 0 | 0 | 135337.4607 | 0.0001936%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 114 | 2 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 9.8058 | 0 | 0 | 9.8058 | 0 | 9.3541 | 20.7766 | 0.45022 | 9.3541 | 20.7766 | 0.45022 | 9.8539 | 21.8868 | 0.45022 | 0.08664% | 0.060207 | 0.060155 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 187979.4602 | 0 | 0 | 187979.4602 | 0.0003234%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 89 | 3 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 22.6455 | 0 | 0 | 22.6455 | 0 | 21.6023 | 31.165 | 0.69316 | 21.6023 | 31.165 | 0.69316 | 22.7565 | 32.8301 | 0.69316 | 0.1652% | 0.18916 | 0.18884 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72486.2016 | 0 | 0 | 72486.2016 | 0.0007468%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 84 | 1 | 8801.877 | 98.2% | 1.718% | 0.0819% | 5.0935 | 0 | 0 | 5.0935 | 0 | 4.8588 | 10.3883 | 0.46772 | 4.8588 | 10.3883 | 0.46772 | 5.1185 | 10.9434 | 0.46772 | 0.05787% | 0.18313 | 0.18303 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48062.9 | 0 | 0 | 48062.9 | 0.000168%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 283 | 5 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 34.9692 | 0 | 0 | 34.9692 | 0 | 33.3583 | 51.9416 | 0.64223 | 33.3583 | 51.9416 | 0.64223 | 35.1407 | 54.7169 | 0.64223 | 0.08661% | 0.27264 | 0.2724 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148093.6949 | 0 | 0 | 148093.6949 | 0.001153%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 92 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 9.6518 | 0 | 0 | 9.6518 | 0 | 9.2072 | 10.3883 | 0.8863 | 9.2072 | 10.3883 | 0.8863 | 9.6992 | 10.9434 | 0.8863 | 0.05141% | 0.15307 | 0.15298 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122658.6463 | 0 | 0 | 122658.6463 | 0.0003183%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 124 | 1 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 10.2146 | 0 | 0 | 10.2146 | 0 | 9.744 | 10.3883 | 0.93798 | 9.744 | 10.3883 | 0.93798 | 10.2646 | 10.9434 | 0.93798 | 0.03968% | 0.15161 | 0.15155 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169797.1166 | 0 | 0 | 169797.1166 | 0.0003368%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 22 | 1 | 4323.2442 | 99.81% | 0% | 0.1903% | 9.7088 | 0 | 0 | 9.7088 | 0 | 9.2615 | 10.3883 | 0.89153 | 9.2615 | 10.3883 | 0.89153 | 9.7564 | 10.9434 | 0.89153 | 0.2246% | 0.043095 | 0.042998 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100320.2895 | 0 | 0 | 100320.2895 | 0.0003202%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 37 | 3 | 9132.2366 | 94.33% | 5.547% | 0.1209% | 34.5751 | 0 | 0 | 34.5751 | 0 | 32.9823 | 31.165 | 1.0583 | 32.9823 | 31.165 | 1.0583 | 34.7446 | 32.8301 | 1.0583 | 0.3786% | 0.12404 | 0.12355 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73637.9966 | 0 | 0 | 73637.9966 | 0.00114%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 41 | 2 | 8606.9717 | 99.86% | 0% | 0.1411% | 20.7534 | 0 | 0 | 20.7534 | 0 | 19.7973 | 20.7766 | 0.95286 | 19.7973 | 20.7766 | 0.95286 | 20.8551 | 21.8868 | 0.95286 | 0.2411% | 0.067132 | 0.06697 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128210.4913 | 0 | 0 | 128210.4913 | 0.0006844%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 37 | 1 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 11.0219 | 0 | 0 | 11.0219 | 0 | 10.5141 | 10.3883 | 1.0121 | 10.5141 | 10.3883 | 1.0121 | 11.0759 | 10.9434 | 1.0121 | 0.1306% | 0.054867 | 0.054793 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 153828.3539 | 0 | 0 | 153828.3539 | 0.0003635%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 35 | 2 | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 25.6711 | 0 | 0 | 25.6711 | 0 | 24.4885 | 20.7766 | 1.1787 | 24.4885 | 20.7766 | 1.1787 | 25.797 | 21.8868 | 1.1787 | 0.2821% | 0.061079 | 0.060906 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 148998.6492 | 0 | 0 | 148998.6492 | 0.0008465%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 8 | 1 | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 16.9397 | 0 | 0 | 16.9397 | 0 | 16.1594 | 10.3883 | 1.5555 | 16.1594 | 10.3883 | 1.5555 | 17.0228 | 10.9434 | 1.5555 | 0.6177% | 0.023668 | 0.023522 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115863.8565 | 0 | 0 | 115863.8565 | 0.0005586%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 76 | 1 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 10.0971 | 0 | 0 | 10.0971 | 0 | 9.6319 | 10.3883 | 0.92719 | 9.6319 | 10.3883 | 0.92719 | 10.1466 | 10.9434 | 0.92719 | 0.06404% | 0.20692 | 0.20679 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76196.1528 | 0 | 0 | 76196.1528 | 0.000333%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 109 | 1 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 2.435 | 0 | 0 | 2.435 | 0 | 2.3228 | 10.3883 | 0.2236 | 2.3228 | 10.3883 | 0.2236 | 2.4469 | 10.9434 | 0.2236 | 0.04371% | 0.23644 | 0.23634 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23561.1501 | 0 | 0 | 23561.1501 | 8.03e-05%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 40 | 1 | 1466.2762 | 91.81% | 7.905% | 0.289% | 1.6658 | 0 | 0 | 1.6658 | 0 | 1.5891 | 10.3883 | 0.15297 | 1.5891 | 10.3883 | 0.15297 | 1.674 | 10.9434 | 0.15297 | 0.1136% | 0.1878 | 0.18757 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7808.257 | 0 | 0 | 7808.257 | 5.493e-05%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 146 | 3 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 41.4996 | 0 | 0 | 41.4996 | 0 | 39.5878 | 31.165 | 1.2703 | 39.5878 | 31.165 | 1.2703 | 41.703 | 32.8301 | 1.2703 | 0.1006% | 0.23053 | 0.2303 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 178972.5373 | 0 | 0 | 178972.5373 | 0.001369%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 95 | 1 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 11.6494 | 0 | 0 | 11.6494 | 0 | 11.1127 | 10.3883 | 1.0697 | 11.1127 | 10.3883 | 1.0697 | 11.7065 | 10.9434 | 1.0697 | 0.05163% | 0.20355 | 0.20344 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110854.5915 | 0 | 0 | 110854.5915 | 0.0003842%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 1 | 1 | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 7.1363 | 10.3883 | 0.68695 | 7.1363 | 10.3883 | 0.68695 | 7.5176 | 10.9434 | 0.68695 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 126 | 2 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 43.097 | 0 | 0 | 43.097 | 0 | 41.1116 | 20.7766 | 1.9787 | 41.1116 | 20.7766 | 1.9787 | 43.3083 | 21.8868 | 1.9787 | 0.078% | 0.31112 | 0.31088 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177591.718 | 0 | 0 | 177591.718 | 0.001421%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 99 | 1 | 32313.161 | 99.26% | 0.708% | 0.02831% | 16.0376 | 0 | 0 | 16.0376 | 0 | 15.2988 | 10.3883 | 1.4727 | 15.2988 | 10.3883 | 1.4727 | 16.1162 | 10.9434 | 1.4727 | 0.04963% | 0.28921 | 0.28907 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111729.3155 | 0 | 0 | 111729.3155 | 0.0005289%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 3 | 1 | 1554.328 | 69.02% | 30.62% | 0.3611% | 17.7015 | 0 | 0 | 17.7015 | 0 | 16.886 | 10.3883 | 1.6255 | 16.886 | 10.3883 | 1.6255 | 17.7883 | 10.9434 | 1.6255 | 1.139% | 0.068691 | 0.067557 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22745.494 | 0 | 0 | 22745.494 | 0.0005837%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 189 | 7 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 51.6538 | 0 | 0 | 51.6538 | 0 | 49.2742 | 72.7182 | 0.6776 | 49.2742 | 72.7182 | 0.6776 | 51.907 | 76.6037 | 0.6776 | 0.1813% | 0.18464 | 0.1843 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154271.8355 | 0 | 0 | 154271.8355 | 0.001703%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 28 | 2 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 28.1885 | 0 | 0 | 28.1885 | 0 | 26.89 | 20.7766 | 1.2942 | 26.89 | 20.7766 | 1.2942 | 28.3267 | 21.8868 | 1.2942 | 0.3517% | 0.12171 | 0.12128 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65858.0647 | 0 | 0 | 65858.0647 | 0.0009296%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 45 | 1 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 15.9929 | 0 | 0 | 15.9929 | 0 | 15.2561 | 10.3883 | 1.4686 | 15.2561 | 10.3883 | 1.4686 | 16.0713 | 10.9434 | 1.4686 | 0.1083% | 0.13837 | 0.13822 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106749.7147 | 0 | 0 | 106749.7147 | 0.0005274%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 103 | 2 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 10.7196 | 0 | 0 | 10.7196 | 0 | 10.2258 | 20.7766 | 0.49218 | 10.2258 | 20.7766 | 0.49218 | 10.7722 | 21.8868 | 0.49218 | 0.09513% | 0.17642 | 0.17625 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63870.7169 | 0 | 0 | 63870.7169 | 0.0003535%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 27 | 1 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 20.9007 | 0 | 0 | 20.9007 | 0 | 19.9378 | 10.3883 | 1.9193 | 19.9378 | 10.3883 | 1.9193 | 21.0031 | 10.9434 | 1.9193 | 0.1824% | 0.12528 | 0.12505 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91452.193 | 0 | 0 | 91452.193 | 0.0006892%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 81 | 2 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 9.6576 | 0 | 0 | 9.6576 | 0 | 9.2127 | 20.7766 | 0.44342 | 9.2127 | 20.7766 | 0.44342 | 9.7049 | 21.8868 | 0.44342 | 0.1204% | 0.15062 | 0.15044 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53240.6013 | 0 | 0 | 53240.6013 | 0.0003185%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 106 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 10.7559 | 0 | 0 | 10.7559 | 0 | 10.2604 | 10.3883 | 0.98769 | 10.2604 | 10.3883 | 0.98769 | 10.8086 | 10.9434 | 0.98769 | 0.04595% | 0.17603 | 0.17595 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 132983.6782 | 0 | 0 | 132983.6782 | 0.0003547%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 54 | 1 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 20.4751 | 0 | 0 | 20.4751 | 0 | 19.5319 | 10.3883 | 1.8802 | 19.5319 | 10.3883 | 1.8802 | 20.5755 | 10.9434 | 1.8802 | 0.08936% | 0.16607 | 0.16592 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 137981.9677 | 0 | 0 | 137981.9677 | 0.0006752%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 59 | 2 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 15.2172 | 0 | 0 | 15.2172 | 0 | 14.5162 | 20.7766 | 0.69868 | 14.5162 | 20.7766 | 0.69868 | 15.2918 | 21.8868 | 0.69868 | 0.1663% | 0.14195 | 0.14171 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64460.3157 | 0 | 0 | 64460.3157 | 0.0005018%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 50 | 2 | 5177.8696 | 97.32% | 2.585% | 0.09195% | 9.9777 | 0 | 0 | 9.9777 | 0 | 9.5181 | 20.7766 | 0.45811 | 9.5181 | 20.7766 | 0.45811 | 10.0266 | 21.8868 | 0.45811 | 0.1927% | 0.13989 | 0.13962 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37014.5608 | 0 | 0 | 37014.5608 | 0.000329%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 82 | 3 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 11.5781 | 0 | 0 | 11.5781 | 0 | 11.0447 | 31.165 | 0.3544 | 11.0447 | 31.165 | 0.3544 | 11.6348 | 32.8301 | 0.3544 | 0.1775% | 0.1523 | 0.15202 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42823.1464 | 0 | 0 | 42823.1464 | 0.0003818%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 104 | 3 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 4.6728 | 0 | 0 | 4.6728 | 0 | 4.4576 | 31.165 | 0.14303 | 4.4576 | 31.165 | 0.14303 | 4.6958 | 32.8301 | 0.14303 | 0.1338% | 0.16472 | 0.16448 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21206.7349 | 0 | 0 | 21206.7349 | 0.0001541%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 29 | 1 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 12.0763 | 0 | 0 | 12.0763 | 0 | 11.52 | 10.3883 | 1.1089 | 11.52 | 10.3883 | 1.1089 | 12.1355 | 10.9434 | 1.1089 | 0.1699% | 0.14069 | 0.14045 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50517.6321 | 0 | 0 | 50517.6321 | 0.0003982%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 95 | 1 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 18.1386 | 0 | 0 | 18.1386 | 0 | 17.303 | 10.3883 | 1.6656 | 17.303 | 10.3883 | 1.6656 | 18.2275 | 10.9434 | 1.6656 | 0.05159% | 0.16564 | 0.16555 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212250.6249 | 0 | 0 | 212250.6249 | 0.0005981%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 17 | 1 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 20.1698 | 0 | 0 | 20.1698 | 0 | 19.2406 | 10.3883 | 1.8521 | 19.2406 | 10.3883 | 1.8521 | 20.2686 | 10.9434 | 1.8521 | 0.2859% | 0.10829 | 0.10798 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65158.4948 | 0 | 0 | 65158.4948 | 0.0006651%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 43 | 1 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 21.6062 | 0 | 0 | 21.6062 | 0 | 20.6108 | 10.3883 | 1.984 | 20.6108 | 10.3883 | 1.984 | 21.7121 | 10.9434 | 1.984 | 0.1148% | 0.12361 | 0.12347 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152300.5996 | 0 | 0 | 152300.5996 | 0.0007125%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 11 | 1 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 22.5426 | 0 | 0 | 22.5426 | 0 | 21.5041 | 10.3883 | 2.07 | 21.5041 | 10.3883 | 2.07 | 22.6531 | 10.9434 | 2.07 | 0.4478% | 0.10909 | 0.1086 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46150.2795 | 0 | 0 | 46150.2795 | 0.0007434%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 33 | 2 | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 29.2906 | 0 | 0 | 29.2906 | 0 | 27.9412 | 20.7766 | 1.3448 | 27.9412 | 20.7766 | 1.3448 | 29.4342 | 21.8868 | 1.3448 | 0.2989% | 0.10945 | 0.10912 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89545.6656 | 0 | 0 | 89545.6656 | 0.0009659%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 80 | 2 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 11.2476 | 0 | 0 | 11.2476 | 0 | 10.7295 | 20.7766 | 0.51642 | 10.7295 | 20.7766 | 0.51642 | 11.3028 | 21.8868 | 0.51642 | 0.1188% | 0.13914 | 0.13896 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68066.0745 | 0 | 0 | 68066.0745 | 0.0003709%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 19 | 1 | 585.5086 | 87.68% | 11.85% | 0.4758% | 1.3374 | 0 | 0 | 1.3374 | 0 | 1.2758 | 10.3883 | 0.12281 | 1.2758 | 10.3883 | 0.12281 | 1.344 | 10.9434 | 0.12281 | 0.2284% | 0.083403 | 0.083186 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7022.4605 | 0 | 0 | 7022.4605 | 4.41e-05%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 22 | 3 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 14.4387 | 0 | 0 | 14.4387 | 0 | 13.7735 | 31.165 | 0.44196 | 13.7735 | 31.165 | 0.44196 | 14.5095 | 32.8301 | 0.44196 | 0.6713% | 0.10605 | 0.10534 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20282.7519 | 0 | 0 | 20282.7519 | 0.0004761%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 85 | 1 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 3.804 | 0 | 0 | 3.804 | 0 | 3.6288 | 10.3883 | 0.34931 | 3.6288 | 10.3883 | 0.34931 | 3.8226 | 10.9434 | 0.34931 | 0.05745% | 0.23843 | 0.23829 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27769.2749 | 0 | 0 | 27769.2749 | 0.0001254%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 124 | 3 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 30.0608 | 0 | 0 | 30.0608 | 0 | 28.676 | 31.165 | 0.92014 | 28.676 | 31.165 | 0.92014 | 30.2082 | 32.8301 | 0.92014 | 0.1187% | 0.28668 | 0.28634 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88317.3864 | 0 | 0 | 88317.3864 | 0.0009913%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 119 | 1 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 11.6351 | 0 | 0 | 11.6351 | 0 | 11.0991 | 10.3883 | 1.0684 | 11.0991 | 10.3883 | 1.0684 | 11.6921 | 10.9434 | 1.0684 | 0.04097% | 0.28228 | 0.28216 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100606.8778 | 0 | 0 | 100606.8778 | 0.0003837%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 103 | 3 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 38.1654 | 0 | 0 | 38.1654 | 0 | 36.4072 | 31.165 | 1.1682 | 36.4072 | 31.165 | 1.1682 | 38.3525 | 32.8301 | 1.1682 | 0.143% | 0.30703 | 0.30658 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86952.164 | 0 | 0 | 86952.164 | 0.001259%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 68 | 4 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 45.2805 | 0 | 0 | 45.2805 | 0 | 43.1945 | 41.5533 | 1.0395 | 43.1945 | 41.5533 | 1.0395 | 45.5025 | 43.7735 | 1.0395 | 0.2838% | 0.1351 | 0.13471 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118122.0335 | 0 | 0 | 118122.0335 | 0.001493%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 81 | 3 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 10.7739 | 0 | 0 | 10.7739 | 0 | 10.2775 | 31.165 | 0.32978 | 10.2775 | 31.165 | 0.32978 | 10.8267 | 32.8301 | 0.32978 | 0.1826% | 0.046754 | 0.046668 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126173.9523 | 0 | 0 | 126173.9523 | 0.0003553%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 63 | 2 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 7.8133 | 0 | 0 | 7.8133 | 0 | 7.4534 | 20.7766 | 0.35874 | 7.4534 | 20.7766 | 0.35874 | 7.8516 | 21.8868 | 0.35874 | 0.1566% | 0.045737 | 0.045665 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109123.7556 | 0 | 0 | 109123.7556 | 0.0002577%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 93 | 2 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 4.524 | 0 | 0 | 4.524 | 0 | 4.3156 | 20.7766 | 0.20771 | 4.3156 | 20.7766 | 0.20771 | 4.5462 | 21.8868 | 0.20771 | 0.097% | 0.17153 | 0.17134 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27193.1367 | 0 | 0 | 27193.1367 | 0.0001492%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 9 | 1 | 240.2897 | 88.19% | 10.99% | 0.8202% | 1.1655 | 0 | 0 | 1.1655 | 0 | 1.1118 | 10.3883 | 0.10702 | 1.1118 | 10.3883 | 0.10702 | 1.1712 | 10.9434 | 0.10702 | 0.485% | 0.068658 | 0.06828 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3502.0919 | 0 | 0 | 3502.0919 | 3.843e-05%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 16 | 1 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 31.2013 | 0 | 0 | 31.2013 | 0 | 29.7639 | 10.3883 | 2.8651 | 29.7639 | 10.3883 | 2.8651 | 31.3542 | 10.9434 | 2.8651 | 0.3087% | 0.21365 | 0.21299 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47313.7427 | 0 | 0 | 47313.7427 | 0.001029%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 73 | 4 | 10322.642 | 99.08% | 0.8619% | 0.05733% | 27.741 | 0 | 0 | 27.741 | 0 | 26.463 | 41.5533 | 0.63685 | 26.463 | 41.5533 | 0.63685 | 27.877 | 43.7735 | 0.63685 | 0.2687% | 0.21878 | 0.21818 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47184.7489 | 0 | 0 | 47184.7489 | 0.0009148%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 43 | 2 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 13.8532 | 0 | 0 | 13.8532 | 0 | 13.215 | 20.7766 | 0.63605 | 13.215 | 20.7766 | 0.63605 | 13.9211 | 21.8868 | 0.63605 | 0.2254% | 0.69907 | 0.69746 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8793.9518 | 0 | 0 | 8793.9518 | 0.0004568%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 64 | 2 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 12.9782 | 0 | 0 | 12.9782 | 0 | 12.3804 | 20.7766 | 0.59588 | 12.3804 | 20.7766 | 0.59588 | 13.0419 | 21.8868 | 0.59588 | 0.1492% | 0.68132 | 0.68027 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12764.855 | 0 | 0 | 12764.855 | 0.000428%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 39 | 1 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 3.7076 | 0 | 0 | 3.7076 | 0 | 3.5368 | 10.3883 | 0.34046 | 3.5368 | 10.3883 | 0.34046 | 3.7258 | 10.9434 | 0.34046 | 0.1243% | 0.13489 | 0.13472 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22120.7035 | 0 | 0 | 22120.7035 | 0.0001223%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 12 | 1 | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 5.6573 | 0 | 0 | 5.6573 | 0 | 5.3967 | 10.3883 | 0.5195 | 5.3967 | 10.3883 | 0.5195 | 5.6851 | 10.9434 | 0.5195 | 0.408% | 0.11751 | 0.11702 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11799.5045 | 0 | 0 | 11799.5045 | 0.0001866%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 79 | 3 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 9.9999 | 0 | 0 | 9.9999 | 0 | 9.5393 | 31.165 | 0.30609 | 9.5393 | 31.165 | 0.30609 | 10.049 | 32.8301 | 0.30609 | 0.1584% | 0.11961 | 0.11939 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 52781.1081 | 0 | 0 | 52781.1081 | 0.0003298%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 92 | 2 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 7.0863 | 0 | 0 | 7.0863 | 0 | 6.7598 | 20.7766 | 0.32536 | 6.7598 | 20.7766 | 0.32536 | 7.121 | 21.8868 | 0.32536 | 0.1066% | 0.082825 | 0.082736 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80237.2836 | 0 | 0 | 80237.2836 | 0.0002337%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 14 | 2 | 456.1931 | 99.77% | 0% | 0.2285% | 3.2186 | 0 | 0 | 3.2186 | 0 | 3.0703 | 20.7766 | 0.14778 | 3.0703 | 20.7766 | 0.14778 | 3.2343 | 21.8868 | 0.14778 | 0.7055% | 0.005996 | 0.0059536 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76084.1518 | 0 | 0 | 76084.1518 | 0.0001061%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 13 | 1 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 13.7723 | 0 | 0 | 13.7723 | 0 | 13.1378 | 10.3883 | 1.2647 | 13.1378 | 10.3883 | 1.2647 | 13.8398 | 10.9434 | 1.2647 | 0.3737% | 0.092289 | 0.091937 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39931.694 | 0 | 0 | 39931.694 | 0.0004542%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 16 | 1 | 427.4478 | 90.46% | 9.431% | 0.1062% | 1.1963 | 0 | 0 | 1.1963 | 0 | 1.1412 | 10.3883 | 0.10985 | 1.1412 | 10.3883 | 0.10985 | 1.2022 | 10.9434 | 0.10985 | 0.2799% | 0.13508 | 0.13466 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3165.4398 | 0 | 0 | 3165.4398 | 3.945e-05%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 51 | 1 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 15.3763 | 0 | 0 | 15.3763 | 0 | 14.668 | 10.3883 | 1.412 | 14.668 | 10.3883 | 1.412 | 15.4517 | 10.9434 | 1.412 | 0.09618% | 0.15941 | 0.15925 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100292.7533 | 0 | 0 | 100292.7533 | 0.0005071%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 127 | 4 | 37077.302 | 99.36% | 0.615% | 0.02874% | 57.4334 | 0 | 0 | 57.4334 | 0 | 54.7876 | 41.5533 | 1.3185 | 54.7876 | 41.5533 | 1.3185 | 57.715 | 43.7735 | 1.3185 | 0.1549% | 0.20421 | 0.20389 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181563.7335 | 0 | 0 | 181563.7335 | 0.001894%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 53 | 1 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 1.521 | 0 | 0 | 1.521 | 0 | 1.4509 | 10.3883 | 0.13967 | 1.4509 | 10.3883 | 0.13967 | 1.5284 | 10.9434 | 0.13967 | 0.07369% | 0.42513 | 0.42473 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4856.0126 | 0 | 0 | 4856.0126 | 5.016e-05%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 90 | 2 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 3.8936 | 0 | 0 | 3.8936 | 0 | 3.7142 | 20.7766 | 0.17877 | 3.7142 | 20.7766 | 0.17877 | 3.9127 | 21.8868 | 0.17877 | 0.1047% | 0.19421 | 0.194 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19152.2582 | 0 | 0 | 19152.2582 | 0.0001284%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 32 | 1 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 7.8052 | 0 | 0 | 7.8052 | 0 | 7.4456 | 10.3883 | 0.71673 | 7.4456 | 10.3883 | 0.71673 | 7.8435 | 10.9434 | 0.71673 | 0.1525% | 0.12647 | 0.12627 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40482.6819 | 0 | 0 | 40482.6819 | 0.0002574%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 109 | 1 | 6915.6819 | 99% | 0.9206% | 0.07911% | 3.1092 | 0 | 0 | 3.1092 | 0 | 2.966 | 10.3883 | 0.28551 | 2.966 | 10.3883 | 0.28551 | 3.1245 | 10.9434 | 0.28551 | 0.04496% | 0.20255 | 0.20246 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34143.3078 | 0 | 0 | 34143.3078 | 0.0001025%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 66 | 3 | 3027.5479 | 94.73% | 5.109% | 0.164% | 6.4528 | 0 | 0 | 6.4528 | 0 | 6.1555 | 31.165 | 0.19751 | 6.1555 | 31.165 | 0.19751 | 6.4844 | 32.8301 | 0.19751 | 0.2131% | 0.24168 | 0.24114 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12528.5519 | 0 | 0 | 12528.5519 | 0.0002128%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 30 | 2 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 30.6121 | 0 | 0 | 30.6121 | 0 | 29.2018 | 20.7766 | 1.4055 | 29.2018 | 20.7766 | 1.4055 | 30.7621 | 21.8868 | 1.4055 | 0.3278% | 0.12948 | 0.12905 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72132.5254 | 0 | 0 | 72132.5254 | 0.001009%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 17 | 1 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 14.9409 | 0 | 0 | 14.9409 | 0 | 14.2526 | 10.3883 | 1.372 | 14.2526 | 10.3883 | 1.372 | 15.0141 | 10.9434 | 1.372 | 0.2857% | 0.12706 | 0.12669 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41163.7366 | 0 | 0 | 41163.7366 | 0.0004927%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 85 | 1 | 6920.124 | 97.57% | 2.306% | 0.1195% | 3.9322 | 0 | 0 | 3.9322 | 0 | 3.7511 | 10.3883 | 0.36108 | 3.7511 | 10.3883 | 0.36108 | 3.9515 | 10.9434 | 0.36108 | 0.05682% | 0.15381 | 0.15372 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 44993.4188 | 0 | 0 | 44993.4188 | 0.0001297%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 27 | 3 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 32.482 | 0 | 0 | 32.482 | 0 | 30.9857 | 31.165 | 0.99425 | 30.9857 | 31.165 | 0.99425 | 32.6413 | 32.8301 | 0.99425 | 0.5462% | 0.15284 | 0.152 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38907.5591 | 0 | 0 | 38907.5591 | 0.001071%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 19 | 1 | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 9.6593 | 0 | 0 | 9.6593 | 0 | 9.2143 | 10.3883 | 0.88699 | 9.2143 | 10.3883 | 0.88699 | 9.7067 | 10.9434 | 0.88699 | 0.2583% | 0.084253 | 0.084034 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44389.4143 | 0 | 0 | 44389.4143 | 0.0003185%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 128 | 1 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 1.2183 | 0 | 0 | 1.2183 | 0 | 1.1621 | 10.3883 | 0.11187 | 1.1621 | 10.3883 | 0.11187 | 1.2242 | 10.9434 | 0.11187 | 0.03624% | 0.19527 | 0.1952 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17215.0881 | 0 | 0 | 17215.0881 | 4.017e-05%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 20 | 1 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 9.3139 | 0 | 0 | 9.3139 | 0 | 8.8848 | 10.3883 | 0.85527 | 8.8848 | 10.3883 | 0.85527 | 9.3596 | 10.9434 | 0.85527 | 0.2462% | 0.093421 | 0.09319 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40493.1831 | 0 | 0 | 40493.1831 | 0.0003071%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 112 | 2 | 2610.8 | 93.6% | 6.065% | 0.3401% | 2.16 | 0 | 0 | 2.16 | 0 | 1.9655 | 19.8195 | 0.099171 | 1.9655 | 19.8195 | 0.099171 | 2.1812 | 21.9941 | 0.099171 | 0.08273% | 0.2194 | 0.21921 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11900.2598 | 0 | 0 | 11900.2598 | 7.123e-05%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 188 | 2 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 2.0648 | 0 | 0 | 2.0648 | 0 | 1.879 | 19.8195 | 0.094804 | 1.879 | 19.8195 | 0.094804 | 2.0851 | 21.9941 | 0.094804 | 0.0494% | 0.24743 | 0.2473 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16894.5007 | 0 | 0 | 16894.5007 | 6.809e-05%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 78 | 1 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 0.95859 | 0 | 0 | 0.95859 | 0 | 0.8723 | 9.9098 | 0.088025 | 0.8723 | 9.9098 | 0.088025 | 0.96801 | 10.997 | 0.088025 | 0.05888% | 0.20887 | 0.20874 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7794.279 | 0 | 0 | 7794.279 | 3.161e-05%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 84 | 3 | 6201.607 | 97.29% | 2.601% | 0.1104% | 10.6663 | 0 | 0 | 10.6663 | 0 | 9.7062 | 29.7293 | 0.32649 | 9.7062 | 29.7293 | 0.32649 | 10.7711 | 32.9911 | 0.32649 | 0.172% | 0.2182 | 0.21781 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28423.3409 | 0 | 0 | 28423.3409 | 0.0003517%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 90 | 3 | 15337.1849 | 98.56% | 1.393% | 0.04595% | 24.9422 | 0 | 0 | 24.9422 | 0 | 22.6971 | 29.7293 | 0.76346 | 22.6971 | 29.7293 | 0.76346 | 25.1873 | 32.9911 | 0.76346 | 0.1626% | 0.22506 | 0.22469 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68147.5638 | 0 | 0 | 68147.5638 | 0.0008225%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 93 | 2 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 11.0842 | 0 | 0 | 11.0842 | 0 | 10.0865 | 19.8195 | 0.50892 | 10.0865 | 19.8195 | 0.50892 | 11.1931 | 21.9941 | 0.50892 | 0.1047% | 0.23776 | 0.23751 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44547.4564 | 0 | 0 | 44547.4564 | 0.0003655%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 84 | 1 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 5.3873 | 0 | 0 | 5.3873 | 0 | 4.9023 | 9.9098 | 0.4947 | 4.9023 | 9.9098 | 0.4947 | 5.4402 | 10.997 | 0.4947 | 0.058% | 0.22716 | 0.22702 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40888.3639 | 0 | 0 | 40888.3639 | 0.0001777%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 32 | 1 | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 4.839 | 0 | 0 | 4.839 | 0 | 4.4035 | 9.9098 | 0.44436 | 4.4035 | 9.9098 | 0.44436 | 4.8866 | 10.997 | 0.44436 | 0.1543% | 0.020337 | 0.020306 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154172.547 | 0 | 0 | 154172.547 | 0.0001596%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 4 | 1 | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 23.9436 | 0 | 0 | 23.9436 | 0 | 21.7883 | 9.9098 | 2.1987 | 21.7883 | 9.9098 | 2.1987 | 24.1789 | 10.997 | 2.1987 | 1.236% | 0.0163 | 0.016098 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118873.7914 | 0 | 0 | 118873.7914 | 0.0007896%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 60 | 2 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 23.6232 | 0 | 0 | 23.6232 | 0 | 21.4968 | 19.8195 | 1.0846 | 21.4968 | 19.8195 | 1.0846 | 23.8554 | 21.9941 | 1.0846 | 0.1626% | 0.34567 | 0.3451 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42025.284 | 0 | 0 | 42025.284 | 0.000779%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 77 | 3 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 2.198 | 0 | 0 | 2.198 | 0 | 2.0002 | 29.7293 | 0.06728 | 2.0002 | 29.7293 | 0.06728 | 2.2196 | 32.9911 | 0.06728 | 0.1368% | 0.43999 | 0.43914 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3654.2057 | 0 | 0 | 3654.2057 | 7.248e-05%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 28 | 2 | 9714.1464 | 98.29% | 1.686% | 0.02874% | 33.7577 | 0 | 0 | 33.7577 | 0 | 30.719 | 19.8195 | 1.5499 | 30.719 | 19.8195 | 1.5499 | 34.0894 | 21.9941 | 1.5499 | 0.3475% | 0.38409 | 0.38273 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25292.8012 | 0 | 0 | 25292.8012 | 0.001113%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 50 | 1 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 5.2792 | 0 | 0 | 5.2792 | 0 | 4.804 | 9.9098 | 0.48478 | 4.804 | 9.9098 | 0.48478 | 5.3311 | 10.997 | 0.48478 | 0.09535% | 0.37772 | 0.37734 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14658.7004 | 0 | 0 | 14658.7004 | 0.0001741%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 107 | 1 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 8.4402 | 0 | 0 | 8.4402 | 0 | 7.6805 | 9.9098 | 0.77504 | 7.6805 | 9.9098 | 0.77504 | 8.5232 | 10.997 | 0.77504 | 0.04494% | 0.38023 | 0.38005 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49394.279 | 0 | 0 | 49394.279 | 0.0002783%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 56 | 2 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 35.0472 | 0 | 0 | 35.0472 | 0 | 31.8925 | 19.8195 | 1.6091 | 31.8925 | 19.8195 | 1.6091 | 35.3916 | 21.9941 | 1.6091 | 0.1754% | 0.44563 | 0.44484 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44832.2747 | 0 | 0 | 44832.2747 | 0.001156%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 20 | 1 | 418.5676 | 87.71% | 11.66% | 0.6303% | 0.90859 | 0 | 0 | 0.90859 | 0 | 0.82681 | 9.9098 | 0.083434 | 0.82681 | 9.9098 | 0.083434 | 0.91752 | 10.997 | 0.083434 | 0.2171% | 0.28262 | 0.28192 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1481.4937 | 0 | 0 | 1481.4937 | 2.996e-05%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 177 | 6 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 8.544 | 0 | 0 | 8.544 | 0 | 7.7749 | 59.4585 | 0.13076 | 7.7749 | 59.4585 | 0.13076 | 8.6279 | 65.9822 | 0.13076 | 0.1551% | 0.3705 | 0.36987 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14865.8062 | 0 | 0 | 14865.8062 | 0.0002817%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 10 | 1 | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 14.9699 | 0 | 0 | 14.9699 | 0 | 13.6224 | 9.9098 | 1.3746 | 13.6224 | 9.9098 | 1.3746 | 15.117 | 10.997 | 1.3746 | 0.4904% | 0.2812 | 0.27981 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10856.2327 | 0 | 0 | 10856.2327 | 0.0004937%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 80 | 1 | 3160.5079 | 95.27% | 4.501% | 0.231% | 1.863 | 0 | 0 | 1.863 | 0 | 1.6953 | 9.9098 | 0.17108 | 1.6953 | 9.9098 | 0.17108 | 1.8813 | 10.997 | 0.17108 | 0.05895% | 0.32167 | 0.32147 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9825.5932 | 0 | 0 | 9825.5932 | 6.144e-05%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 151 | 5 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 2.7548 | 0 | 0 | 2.7548 | 0 | 2.5068 | 49.5488 | 0.050593 | 2.5068 | 49.5488 | 0.050593 | 2.7819 | 54.9851 | 0.050593 | 0.1337% | 0.36686 | 0.36626 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5620.1549 | 0 | 0 | 5620.1549 | 9.084e-05%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 53 | 3 | 1867.403 | 95.01% | 4.712% | 0.2778% | 4.9712 | 0 | 0 | 4.9712 | 0 | 4.5237 | 29.7293 | 0.15216 | 4.5237 | 29.7293 | 0.15216 | 5.02 | 32.9911 | 0.15216 | 0.2662% | 0.32295 | 0.32205 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5783.1249 | 0 | 0 | 5783.1249 | 0.0001639%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 205 | 7 | 18749.5963 | 97% | 2.901% | 0.09453% | 30.7422 | 0 | 0 | 30.7422 | 0 | 27.975 | 69.3683 | 0.40328 | 27.975 | 69.3683 | 0.40328 | 31.0444 | 76.9792 | 0.40328 | 0.164% | 0.38414 | 0.38349 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48812.3636 | 0 | 0 | 48812.3636 | 0.001014%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 63 | 2 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 6.7207 | 0 | 0 | 6.7207 | 0 | 6.1157 | 19.8195 | 0.30857 | 6.1157 | 19.8195 | 0.30857 | 6.7867 | 21.9941 | 0.30857 | 0.1533% | 0.20232 | 0.20201 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21676.0676 | 0 | 0 | 21676.0676 | 0.0002216%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 113 | 2 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 4.8723 | 0 | 0 | 4.8723 | 0 | 4.4337 | 19.8195 | 0.2237 | 4.4337 | 19.8195 | 0.2237 | 4.9201 | 21.9941 | 0.2237 | 0.08486% | 0.20491 | 0.20473 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28020.091 | 0 | 0 | 28020.091 | 0.0001607%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 62 | 2 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 18.1736 | 0 | 0 | 18.1736 | 0 | 16.5377 | 19.8195 | 0.83442 | 16.5377 | 19.8195 | 0.83442 | 18.3522 | 21.9941 | 0.83442 | 0.1577% | 0.22417 | 0.22381 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51405.5548 | 0 | 0 | 51405.5548 | 0.0005993%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 32 | 1 | 10068.5168 | 97.13% | 2.784% | 0.0867% | 15.1277 | 0 | 0 | 15.1277 | 0 | 13.766 | 9.9098 | 1.3891 | 13.766 | 9.9098 | 1.3891 | 15.2764 | 10.997 | 1.3891 | 0.1502% | 0.23205 | 0.23169 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43392.143 | 0 | 0 | 43392.143 | 0.0004989%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 51 | 1 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 3.2264 | 0 | 0 | 3.2264 | 0 | 2.936 | 9.9098 | 0.29627 | 2.936 | 9.9098 | 0.29627 | 3.2581 | 10.997 | 0.29627 | 0.09487% | 0.20978 | 0.20957 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16212.8443 | 0 | 0 | 16212.8443 | 0.0001064%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 115 | 3 | 13172.958 | 96.8% | 3.124% | 0.0728% | 16.4665 | 0 | 0 | 16.4665 | 0 | 14.9843 | 29.7293 | 0.50403 | 14.9843 | 29.7293 | 0.50403 | 16.6283 | 32.9911 | 0.50403 | 0.125% | 0.23242 | 0.23212 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56680.6065 | 0 | 0 | 56680.6065 | 0.000543%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 5 | 1 | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.4529 | 0 | 0 | 14.4529 | 0 | 13.1519 | 9.9098 | 1.3272 | 13.1519 | 9.9098 | 1.3272 | 14.5949 | 10.997 | 1.3272 | 0.8835% | 0.18529 | 0.18346 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8837.9156 | 0 | 0 | 8837.9156 | 0.0004766%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 40 | 2 | 11917.1989 | 94.29% | 5.651% | 0.05821% | 27.8112 | 0 | 0 | 27.8112 | 0 | 25.3078 | 19.8195 | 1.2769 | 25.3078 | 19.8195 | 1.2769 | 28.0845 | 21.9941 | 1.2769 | 0.2334% | 0.1455 | 0.14514 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 81914.272 | 0 | 0 | 81914.272 | 0.0009171%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 51 | 1 | 8462.8018 | 99.74% | 0% | 0.2593% | 8.1926 | 0 | 0 | 8.1926 | 0 | 7.4552 | 9.9098 | 0.7523 | 7.4552 | 9.9098 | 0.7523 | 8.2731 | 10.997 | 0.7523 | 0.09681% | 0.11169 | 0.11158 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75768.7437 | 0 | 0 | 75768.7437 | 0.0002702%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 19 | 1 | 498.1496 | 90.1% | 9.186% | 0.7154% | 1.1693 | 0 | 0 | 1.1693 | 0 | 1.0641 | 9.9098 | 0.10737 | 1.0641 | 9.9098 | 0.10737 | 1.1808 | 10.997 | 0.10737 | 0.2347% | 0.32588 | 0.32503 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1529.0392 | 0 | 0 | 1529.0392 | 3.856e-05%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 18 | 1 | 170.5929 | 70.47% | 28.1% | 1.432% | 0.33061 | 0 | 0 | 0.33061 | 0 | 0.30085 | 9.9098 | 0.030359 | 0.30085 | 9.9098 | 0.030359 | 0.33386 | 10.997 | 0.030359 | 0.1938% | 0.31841 | 0.31754 | 535.7584 | 42.1364 | 121.741 | 371.881 | 536.1946 | 0 | 0 | 536.1946 | 1.09e-05%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 38 | 1 | 317.7725 | 50.82% | 48.53% | 0.6462% | 0.21038 | 0 | 0 | 0.21038 | 0 | 0.19144 | 9.9098 | 0.019319 | 0.19144 | 9.9098 | 0.019319 | 0.21245 | 10.997 | 0.019319 | 0.06621% | 0.31397 | 0.31356 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1012.7634 | 0 | 0 | 1012.7634 | 6.938e-06%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 65 | 1 | 1199.6322 | 89.49% | 9.8% | 0.7134% | 0.81752 | 0 | 0 | 0.81752 | 0 | 0.74393 | 9.9098 | 0.075071 | 0.74393 | 9.9098 | 0.075071 | 0.82555 | 10.997 | 0.075071 | 0.06815% | 0.37314 | 0.37285 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3215.2645 | 0 | 0 | 3215.2645 | 2.696e-05%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 145 | 3 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 1.5616 | 0 | 0 | 1.5616 | 0 | 1.421 | 29.7293 | 0.047799 | 1.421 | 29.7293 | 0.047799 | 1.5769 | 32.9911 | 0.047799 | 0.0863% | 0.39031 | 0.38991 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4636.8964 | 0 | 0 | 4636.8964 | 5.15e-05%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 66 | 1 | 1890.633 | 91.06% | 8.49% | 0.4466% | 1.2913 | 0 | 0 | 1.2913 | 0 | 1.175 | 9.9098 | 0.11857 | 1.175 | 9.9098 | 0.11857 | 1.3039 | 10.997 | 0.11857 | 0.0683% | 0.3743 | 0.37402 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5051.399 | 0 | 0 | 5051.399 | 4.258e-05%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 79 | 1 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 1.0397 | 0 | 0 | 1.0397 | 0 | 0.94616 | 9.9098 | 0.095477 | 0.94616 | 9.9098 | 0.095477 | 1.05 | 10.997 | 0.095477 | 0.05979% | 0.15054 | 0.15044 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11551.8271 | 0 | 0 | 11551.8271 | 3.429e-05%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 70 | 2 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 2.1093 | 0 | 0 | 2.1093 | 0 | 1.9194 | 19.8195 | 0.096846 | 1.9194 | 19.8195 | 0.096846 | 2.13 | 21.9941 | 0.096846 | 0.1343% | 0.19221 | 0.19193 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8170.8584 | 0 | 0 | 8170.8584 | 6.956e-05%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 46 | 2 | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 10.4301 | 0 | 0 | 10.4301 | 0 | 9.4913 | 19.8195 | 0.47889 | 9.4913 | 19.8195 | 0.47889 | 10.5327 | 21.9941 | 0.47889 | 0.2134% | 0.13941 | 0.13911 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35061.6976 | 0 | 0 | 35061.6976 | 0.0003439%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 42 | 1 | 1265.9596 | 97.92% | 1.386% | 0.6959% | 1.461 | 0 | 0 | 1.461 | 0 | 1.3295 | 9.9098 | 0.13416 | 1.3295 | 9.9098 | 0.13416 | 1.4753 | 10.997 | 0.13416 | 0.1154% | 0.17753 | 0.17733 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7130.9361 | 0 | 0 | 7130.9361 | 4.818e-05%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 68 | 3 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 3.1491 | 0 | 0 | 3.1491 | 0 | 2.8657 | 29.7293 | 0.096392 | 2.8657 | 29.7293 | 0.096392 | 3.1801 | 32.9911 | 0.096392 | 0.2124% | 0.1427 | 0.14239 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10389.0618 | 0 | 0 | 10389.0618 | 0.0001038%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 103 | 4 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 5.0789 | 0 | 0 | 5.0789 | 0 | 4.6218 | 39.639 | 0.1166 | 4.6218 | 39.639 | 0.1166 | 5.1288 | 43.9881 | 0.1166 | 0.1841% | 0.19881 | 0.19843 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13876.4091 | 0 | 0 | 13876.4091 | 0.0001675%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 39 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 1.2805 | 0 | 0 | 1.2805 | 0 | 1.1652 | 9.9098 | 0.11758 | 1.1652 | 9.9098 | 0.11758 | 1.2931 | 10.997 | 0.11758 | 0.1233% | 0.12493 | 0.12477 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8315.3648 | 0 | 0 | 8315.3648 | 4.223e-05%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 45 | 1 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 1.5829 | 0 | 0 | 1.5829 | 0 | 1.4404 | 9.9098 | 0.14535 | 1.4404 | 9.9098 | 0.14535 | 1.5984 | 10.997 | 0.14535 | 0.1076% | 0.13116 | 0.13101 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11216.3781 | 0 | 0 | 11216.3781 | 5.22e-05%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 127 | 5 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 50.6568 | 0 | 0 | 50.6568 | 0 | 46.097 | 49.5488 | 0.93034 | 46.097 | 49.5488 | 0.93034 | 51.1547 | 54.9851 | 0.93034 | 0.1927% | 0.26918 | 0.26865 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97637.7208 | 0 | 0 | 97637.7208 | 0.00167%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 75 | 1 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 4.3741 | 0 | 0 | 4.3741 | 0 | 3.9803 | 9.9098 | 0.40166 | 3.9803 | 9.9098 | 0.40166 | 4.4171 | 10.997 | 0.40166 | 0.06561% | 0.090777 | 0.090717 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73443.1375 | 0 | 0 | 73443.1375 | 0.0001442%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 22 | 2 | 400.1895 | 97.86% | 1.359% | 0.7809% | 1.7623 | 0 | 0 | 1.7623 | 0 | 1.6037 | 19.8195 | 0.080914 | 1.6037 | 19.8195 | 0.080914 | 1.7796 | 21.9941 | 0.080914 | 0.4404% | 0.059676 | 0.059407 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6706.7307 | 0 | 0 | 6706.7307 | 5.811e-05%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 9 | 1 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 2.787 | 0 | 0 | 2.787 | 0 | 2.5362 | 9.9098 | 0.25593 | 2.5362 | 9.9098 | 0.25593 | 2.8144 | 10.997 | 0.25593 | 0.5429% | 0.053744 | 0.053448 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9552.1251 | 0 | 0 | 9552.1251 | 9.191e-05%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 73 | 3 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 45.1299 | 0 | 0 | 45.1299 | 0 | 41.0676 | 29.7293 | 1.3814 | 41.0676 | 29.7293 | 1.3814 | 45.5735 | 32.9911 | 1.3814 | 0.2019% | 0.23844 | 0.23795 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93755.362 | 0 | 0 | 93755.362 | 0.001488%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 72 | 2 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 17.1539 | 0 | 0 | 17.1539 | 0 | 15.6098 | 19.8195 | 0.7876 | 15.6098 | 19.8195 | 0.7876 | 17.3225 | 21.9941 | 0.7876 | 0.135% | 0.20291 | 0.20263 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62602.5044 | 0 | 0 | 62602.5044 | 0.0005657%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 26 | 1 | 5434.8155 | 98.92% | 1.009% | 0.07406% | 10.235 | 0 | 0 | 10.235 | 0 | 9.3137 | 9.9098 | 0.93985 | 9.3137 | 9.9098 | 0.93985 | 10.3356 | 10.997 | 0.93985 | 0.1883% | 0.12528 | 0.12504 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43382.2458 | 0 | 0 | 43382.2458 | 0.0003375%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 67 | 1 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 10.2893 | 0 | 0 | 10.2893 | 0 | 9.3631 | 9.9098 | 0.94484 | 9.3631 | 9.9098 | 0.94484 | 10.3904 | 10.997 | 0.94484 | 0.07328% | 0.15704 | 0.15693 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89410.3207 | 0 | 0 | 89410.3207 | 0.0003393%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 126 | 1 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 0.70582 | 0 | 0 | 0.70582 | 0 | 0.64229 | 9.9098 | 0.064813 | 0.64229 | 9.9098 | 0.064813 | 0.71276 | 10.997 | 0.064813 | 0.03505% | 0.19664 | 0.19656 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10240.5633 | 0 | 0 | 10240.5633 | 2.328e-05%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 84 | 1 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 1.412 | 0 | 0 | 1.412 | 0 | 1.2849 | 9.9098 | 0.12966 | 1.2849 | 9.9098 | 0.12966 | 1.4259 | 10.997 | 0.12966 | 0.05177% | 0.20236 | 0.20224 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13479.8908 | 0 | 0 | 13479.8908 | 4.656e-05%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 71 | 1 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 7.3527 | 0 | 0 | 7.3527 | 0 | 6.6908 | 9.9098 | 0.67517 | 6.6908 | 9.9098 | 0.67517 | 7.4249 | 10.997 | 0.67517 | 0.0688% | 0.28412 | 0.28392 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37614.1258 | 0 | 0 | 37614.1258 | 0.0002425%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 68 | 2 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 5.0401 | 0 | 0 | 5.0401 | 0 | 4.5864 | 19.8195 | 0.23141 | 4.5864 | 19.8195 | 0.23141 | 5.0896 | 21.9941 | 0.23141 | 0.1378% | 0.14269 | 0.14248 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25632.0154 | 0 | 0 | 25632.0154 | 0.0001662%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 70 | 1 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 0.92452 | 0 | 0 | 0.92452 | 0 | 0.8413 | 9.9098 | 0.084896 | 0.8413 | 9.9098 | 0.084896 | 0.9336 | 10.997 | 0.084896 | 0.06426% | 0.18227 | 0.18214 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7893.4873 | 0 | 0 | 7893.4873 | 3.049e-05%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 48 | 2 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 20.6679 | 0 | 0 | 20.6679 | 0 | 18.8075 | 19.8195 | 0.94894 | 18.8075 | 19.8195 | 0.94894 | 20.871 | 21.9941 | 0.94894 | 0.2043% | 0.2438 | 0.24329 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41498.6089 | 0 | 0 | 41498.6089 | 0.0006816%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 29 | 1 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 3.6154 | 0 | 0 | 3.6154 | 0 | 3.29 | 9.9098 | 0.332 | 3.29 | 9.9098 | 0.332 | 3.651 | 10.997 | 0.332 | 0.1644% | 0.37523 | 0.37459 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5859.882 | 0 | 0 | 5859.882 | 0.0001192%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 81 | 4 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 3.9682 | 0 | 0 | 3.9682 | 0 | 3.611 | 39.639 | 0.091097 | 3.611 | 39.639 | 0.091097 | 4.0072 | 43.9881 | 0.091097 | 0.206% | 0.44397 | 0.44289 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4339.5164 | 0 | 0 | 4339.5164 | 0.0001309%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 155 | 3 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 3.0701 | 0 | 0 | 3.0701 | 0 | 2.7937 | 29.7293 | 0.093973 | 2.7937 | 29.7293 | 0.093973 | 3.1003 | 32.9911 | 0.093973 | 0.08562% | 0.50177 | 0.50129 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7146.726 | 0 | 0 | 7146.726 | 0.0001012%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 17 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 10.7373 | 0 | 0 | 10.7373 | 0 | 9.7708 | 9.9098 | 0.98598 | 9.7708 | 9.9098 | 0.98598 | 10.8429 | 10.997 | 0.98598 | 0.2909% | 0.035843 | 0.035739 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102975.5205 | 0 | 0 | 102975.5205 | 0.0003541%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 77 | 2 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 3.8751 | 0 | 0 | 3.8751 | 0 | 3.5262 | 19.8195 | 0.17792 | 3.5262 | 19.8195 | 0.17792 | 3.9131 | 21.9941 | 0.17792 | 0.1185% | 0.19945 | 0.19919 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16398.1457 | 0 | 0 | 16398.1457 | 0.0001278%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 93 | 2 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 2.7991 | 0 | 0 | 2.7991 | 0 | 2.5471 | 19.8195 | 0.12852 | 2.5471 | 19.8195 | 0.12852 | 2.8266 | 21.9941 | 0.12852 | 0.1023% | 0.2115 | 0.21128 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12936.3188 | 0 | 0 | 12936.3188 | 9.23e-05%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 72 | 2 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 5.2494 | 0 | 0 | 5.2494 | 0 | 4.7769 | 19.8195 | 0.24102 | 4.7769 | 19.8195 | 0.24102 | 5.301 | 21.9941 | 0.24102 | 0.1334% | 0.19925 | 0.19898 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19748.4325 | 0 | 0 | 19748.4325 | 0.0001731%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 137 | 4 | 7406.689 | 96.62% | 3.25% | 0.1263% | 10.3431 | 0 | 0 | 10.3431 | 0 | 9.4121 | 39.639 | 0.23745 | 9.4121 | 39.639 | 0.23745 | 10.4448 | 43.9881 | 0.23745 | 0.1396% | 0.26901 | 0.26862 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27534.6457 | 0 | 0 | 27534.6457 | 0.0003411%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 212 | 2 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 36.7057 | 0 | 0 | 36.7057 | 0 | 33.4017 | 19.8195 | 1.6853 | 33.4017 | 19.8195 | 1.6853 | 37.0665 | 21.9941 | 1.6853 | 0.04635% | 0.41507 | 0.41488 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190798.148 | 0 | 0 | 190798.148 | 0.00121%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 81 | 4 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 109.8519 | 0 | 0 | 109.8519 | 0 | 99.9637 | 39.639 | 2.5219 | 99.9637 | 39.639 | 2.5219 | 110.9315 | 43.9881 | 2.5219 | 0.2435% | 0.41211 | 0.4111 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109453.4828 | 0 | 0 | 109453.4828 | 0.003623%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 132 | 2 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 5.3502 | 0 | 0 | 5.3502 | 0 | 4.8686 | 19.8195 | 0.24565 | 4.8686 | 19.8195 | 0.24565 | 5.4027 | 21.9941 | 0.24565 | 0.07204% | 0.27927 | 0.27906 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26594.9041 | 0 | 0 | 26594.9041 | 0.0001764%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 1220 | 8 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 5.2642 | 0 | 0 | 5.2642 | 0 | 4.7904 | 79.278 | 0.060425 | 4.7904 | 79.278 | 0.060425 | 5.316 | 87.9762 | 0.060425 | 0.03139% | 0.35117 | 0.35106 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47761.8158 | 0 | 0 | 47761.8158 | 0.0001736%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 52 | 3 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 5.4263 | 0 | 0 | 5.4263 | 0 | 4.9379 | 29.7293 | 0.16609 | 4.9379 | 29.7293 | 0.16609 | 5.4796 | 32.9911 | 0.16609 | 0.2713% | 0.093988 | 0.09372 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21287.2768 | 0 | 0 | 21287.2768 | 0.0001789%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 24 | 1 | 2730.9177 | 98.3% | 1.373% | 0.325% | 5.5369 | 0 | 0 | 5.5369 | 0 | 5.0385 | 9.9098 | 0.50844 | 5.0385 | 9.9098 | 0.50844 | 5.5913 | 10.997 | 0.50844 | 0.2027% | 0.054655 | 0.054542 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 49968.595 | 0 | 0 | 49968.595 | 0.0001826%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 151 | 6 | 5142.095 | 98.68% | 0.901% | 0.4182% | 9.9805 | 0 | 0 | 9.9805 | 0 | 9.0821 | 59.4585 | 0.15275 | 9.0821 | 59.4585 | 0.15275 | 10.0786 | 65.9822 | 0.15275 | 0.1941% | 0.11648 | 0.11625 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44148.0178 | 0 | 0 | 44148.0178 | 0.0003291%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 50 | 2 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 4.9146 | 0 | 0 | 4.9146 | 0 | 4.4722 | 19.8195 | 0.22565 | 4.4722 | 19.8195 | 0.22565 | 4.9629 | 21.9941 | 0.22565 | 0.1966% | 0.037573 | 0.037498 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66538.0997 | 0 | 0 | 66538.0997 | 0.0001621%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 32 | 1 | 447.7794 | 94.96% | 4.349% | 0.694% | 0.65773 | 0 | 0 | 0.65773 | 0 | 0.59853 | 9.9098 | 0.060398 | 0.59853 | 9.9098 | 0.060398 | 0.66419 | 10.997 | 0.060398 | 0.1469% | 0.02204 | 0.022006 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20318.4394 | 0 | 0 | 20318.4394 | 2.169e-05%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 79 | 2 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 2.5208 | 0 | 0 | 2.5208 | 0 | 2.2939 | 19.8195 | 0.11574 | 2.2939 | 19.8195 | 0.11574 | 2.5456 | 21.9941 | 0.11574 | 0.1076% | 0.1204 | 0.12025 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19453.1746 | 0 | 0 | 19453.1746 | 8.313e-05%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 102 | 4 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 7.9114 | 0 | 0 | 7.9114 | 0 | 7.1993 | 39.639 | 0.18162 | 7.1993 | 39.639 | 0.18162 | 7.9892 | 43.9881 | 0.18162 | 0.1917% | 0.075451 | 0.075305 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54708.1674 | 0 | 0 | 54708.1674 | 0.0002609%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 40 | 1 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 6.0793 | 0 | 0 | 6.0793 | 0 | 5.532 | 9.9098 | 0.55824 | 5.532 | 9.9098 | 0.55824 | 6.139 | 10.997 | 0.55824 | 0.1231% | 0.047931 | 0.047872 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103051.7053 | 0 | 0 | 103051.7053 | 0.0002005%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 48 | 1 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 24.0197 | 0 | 0 | 24.0197 | 0 | 21.8576 | 9.9098 | 2.2057 | 21.8576 | 9.9098 | 2.2057 | 24.2557 | 10.997 | 2.2057 | 0.1014% | 0.15496 | 0.1548 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152802.8333 | 0 | 0 | 152802.8333 | 0.0007921%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 48 | 1 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 9.8957 | 0 | 0 | 9.8957 | 0 | 9.005 | 9.9098 | 0.9087 | 9.005 | 9.9098 | 0.9087 | 9.993 | 10.997 | 0.9087 | 0.1018% | 0.12847 | 0.12834 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75652.1609 | 0 | 0 | 75652.1609 | 0.0003263%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 51 | 1 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 5.0755 | 0 | 0 | 5.0755 | 0 | 4.6187 | 9.9098 | 0.46607 | 4.6187 | 9.9098 | 0.46607 | 5.1254 | 10.997 | 0.46607 | 0.09519% | 0.18129 | 0.18111 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29412.1404 | 0 | 0 | 29412.1404 | 0.0001674%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 124 | 1 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 8.3334 | 0 | 0 | 8.3334 | 0 | 7.5833 | 9.9098 | 0.76524 | 7.5833 | 9.9098 | 0.76524 | 8.4153 | 10.997 | 0.76524 | 0.03927% | 0.21435 | 0.21426 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99013.4222 | 0 | 0 | 99013.4222 | 0.0002748%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 56 | 1 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 5.9917 | 0 | 0 | 5.9917 | 0 | 5.4524 | 9.9098 | 0.5502 | 5.4524 | 9.9098 | 0.5502 | 6.0506 | 10.997 | 0.5502 | 0.08649% | 0.18488 | 0.18471 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37473.8225 | 0 | 0 | 37473.8225 | 0.0001976%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 71 | 1 | 27080.7376 | 98.89% | 1.071% | 0.0369% | 18.671 | 0 | 0 | 18.671 | 0 | 16.9904 | 9.9098 | 1.7145 | 16.9904 | 9.9098 | 1.7145 | 18.8545 | 10.997 | 1.7145 | 0.06895% | 0.15539 | 0.15528 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174276.1608 | 0 | 0 | 174276.1608 | 0.0006157%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 165 | 4 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 36.7437 | 0 | 0 | 36.7437 | 0 | 33.4362 | 39.639 | 0.84352 | 33.4362 | 39.639 | 0.84352 | 37.1048 | 43.9881 | 0.84352 | 0.1189% | 0.18156 | 0.18134 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170163.1826 | 0 | 0 | 170163.1826 | 0.001212%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 182 | 9 | 65515.492 | 98.93% | 1.038% | 0.03019% | 158.6559 | 0 | 0 | 158.6559 | 0 | 144.3747 | 89.1878 | 1.6188 | 144.3747 | 89.1878 | 1.6188 | 160.2152 | 98.9732 | 1.6188 | 0.2422% | 0.49249 | 0.49128 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133033.8643 | 0 | 0 | 133033.8643 | 0.005232%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 19 | 2 | 1585.1718 | 98.67% | 1.22% | 0.1095% | 8.1498 | 0 | 0 | 8.1498 | 0 | 7.4162 | 19.8195 | 0.37419 | 7.4162 | 19.8195 | 0.37419 | 8.2298 | 21.9941 | 0.37419 | 0.5141% | 0.11902 | 0.1184 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13319.6176 | 0 | 0 | 13319.6176 | 0.0002687%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 23 | 1 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 2.3177 | 0 | 0 | 2.3177 | 0 | 2.1091 | 9.9098 | 0.21283 | 2.1091 | 9.9098 | 0.21283 | 2.3405 | 10.997 | 0.21283 | 0.2076% | 0.1294 | 0.12913 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8628.4088 | 0 | 0 | 8628.4088 | 7.643e-05%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 72 | 3 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 12.7015 | 0 | 0 | 12.7015 | 0 | 11.5582 | 29.7293 | 0.38878 | 11.5582 | 29.7293 | 0.38878 | 12.8264 | 32.9911 | 0.38878 | 0.2026% | 0.15408 | 0.15376 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40687.0189 | 0 | 0 | 40687.0189 | 0.0004188%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 17 | 1 | 1029.5673 | 69.27% | 30.42% | 0.3032% | 2.0767 | 0 | 0 | 2.0767 | 0 | 1.8897 | 9.9098 | 0.1907 | 1.8897 | 9.9098 | 0.1907 | 2.0971 | 10.997 | 0.1907 | 0.2017% | 0.073205 | 0.072992 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14076.7101 | 0 | 0 | 14076.7101 | 6.848e-05%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 73 | 2 | 4437.6588 | 97.91% | 1.769% | 0.321% | 5.8924 | 0 | 0 | 5.8924 | 0 | 5.362 | 19.8195 | 0.27054 | 5.362 | 19.8195 | 0.27054 | 5.9503 | 21.9941 | 0.27054 | 0.1328% | 0.095775 | 0.095646 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46335.3294 | 0 | 0 | 46335.3294 | 0.0001943%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 50 | 1 | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 3.6705 | 0 | 0 | 3.6705 | 0 | 3.3401 | 9.9098 | 0.33706 | 3.3401 | 9.9098 | 0.33706 | 3.7066 | 10.997 | 0.33706 | 0.09808% | 0.06999 | 0.069921 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53473.2976 | 0 | 0 | 53473.2976 | 0.000121%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 104 | 5 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 8.4461 | 0 | 0 | 8.4461 | 0 | 7.6858 | 49.5488 | 0.15512 | 7.6858 | 49.5488 | 0.15512 | 8.5291 | 54.9851 | 0.15512 | 0.2304% | 0.12278 | 0.12248 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29859.1707 | 0 | 0 | 29859.1707 | 0.0002785%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 71 | 3 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 6.6976 | 0 | 0 | 6.6976 | 0 | 6.0948 | 29.7293 | 0.20501 | 6.0948 | 29.7293 | 0.20501 | 6.7635 | 32.9911 | 0.20501 | 0.1977% | 0.070488 | 0.070341 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48056.3083 | 0 | 0 | 48056.3083 | 0.0002209%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 24 | 2 | 1438.4419 | 90% | 9.47% | 0.5268% | 5.3404 | 0 | 0 | 5.3404 | 0 | 4.8597 | 19.8195 | 0.2452 | 4.8597 | 19.8195 | 0.2452 | 5.3929 | 21.9941 | 0.2452 | 0.3713% | 0.066431 | 0.066157 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21662.0076 | 0 | 0 | 21662.0076 | 0.0001761%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 99 | 5 | 3753.23 | 95.85% | 3.876% | 0.273% | 8.9938 | 0 | 0 | 8.9938 | 0 | 8.1842 | 49.5488 | 0.16517 | 8.1842 | 49.5488 | 0.16517 | 9.0822 | 54.9851 | 0.16517 | 0.2396% | 0.10094 | 0.10068 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37187.8275 | 0 | 0 | 37187.8275 | 0.0002966%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 24 | 4 | 826.9208 | 97.04% | 2.672% | 0.2884% | 6.6201 | 0 | 0 | 6.6201 | 0 | 6.0242 | 39.639 | 0.15198 | 6.0242 | 39.639 | 0.15198 | 6.6852 | 43.9881 | 0.15198 | 0.8006% | 0.05906 | 0.058573 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14004.7694 | 0 | 0 | 14004.7694 | 0.0002183%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 40 | 1 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 2.1878 | 0 | 0 | 2.1878 | 0 | 1.9909 | 9.9098 | 0.2009 | 1.9909 | 9.9098 | 0.2009 | 2.2093 | 10.997 | 0.2009 | 0.1087% | 0.19011 | 0.18988 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10593.0554 | 0 | 0 | 10593.0554 | 7.215e-05%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 7 | 1 | 2407.2332 | 91.07% | 8.863% | 0.06623% | 15.5026 | 0 | 0 | 15.5026 | 0 | 14.1071 | 9.9098 | 1.4236 | 14.1071 | 9.9098 | 1.4236 | 15.6549 | 10.997 | 1.4236 | 0.644% | 0.10098 | 0.10026 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23854.2972 | 0 | 0 | 23854.2972 | 0.0005112%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | 3--3 | 2 | 1 | 46.1951 | 84.69% | 14.76% | 0.5474% | 0.96832 | 0 | 0 | 0.96832 | 0 | 0.88116 | 9.9098 | 0.088918 | 0.88116 | 9.9098 | 0.088918 | 0.97783 | 10.997 | 0.088918 | 2.096% | 0.018623 | 0.018162 | 2480.5668 | 274.9764 | 742.9932 | 1462.5972 | 2490.203 | 0 | 0 | 2490.203 | 3.193e-05%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | 3--4 | 4 | 1 | 278.652 | 16.28% | 83.57% | 0.1501% | 0.56138 | 0 | 0 | 0.56138 | 0 | 0.51085 | 9.9098 | 0.05155 | 0.51085 | 9.9098 | 0.05155 | 0.56689 | 10.997 | 0.05155 | 0.2015% | 0.018935 | 0.018701 | 14715.9264 | 335.1634 | 11691.6167 | 2689.1463 | 14870.2994 | 0 | 0 | 14870.2994 | 1.851e-05%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 138 | 1 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 1.2337 | 0 | 0 | 1.2337 | 0 | 1.1226 | 9.9098 | 0.11329 | 1.1226 | 9.9098 | 0.11329 | 1.2458 | 10.997 | 0.11329 | 0.03425% | 0.15121 | 0.15116 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23821.6403 | 0 | 0 | 23821.6403 | 4.068e-05%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 245 | 5 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 13.7521 | 0 | 0 | 13.7521 | 0 | 12.5143 | 49.5488 | 0.25256 | 12.5143 | 49.5488 | 0.25256 | 13.8873 | 54.9851 | 0.25256 | 0.09914% | 0.18928 | 0.18909 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73288.9513 | 0 | 0 | 73288.9513 | 0.0004535%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 229 | 7 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 8.1751 | 0 | 0 | 8.1751 | 0 | 7.4392 | 69.3683 | 0.10724 | 7.4392 | 69.3683 | 0.10724 | 8.2554 | 76.9792 | 0.10724 | 0.1468% | 0.19915 | 0.19885 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 27974.0092 | 0 | 0 | 27974.0092 | 0.0002696%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 92 | 1 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 7.2232 | 0 | 0 | 7.2232 | 0 | 6.573 | 9.9098 | 0.66329 | 6.573 | 9.9098 | 0.66329 | 7.2942 | 10.997 | 0.66329 | 0.05342% | 0.1241 | 0.12404 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108955.8992 | 0 | 0 | 108955.8992 | 0.0002382%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 107 | 2 | 11201.3889 | 98.88% | 1.023% | 0.1021% | 10.2473 | 0 | 0 | 10.2473 | 0 | 9.3249 | 19.8195 | 0.47049 | 9.3249 | 19.8195 | 0.47049 | 10.348 | 21.9941 | 0.47049 | 0.09148% | 0.12896 | 0.12884 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86858.2893 | 0 | 0 | 86858.2893 | 0.0003379%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 121 | 1 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 8.3206 | 0 | 0 | 8.3206 | 0 | 7.5717 | 9.9098 | 0.76406 | 7.5717 | 9.9098 | 0.76406 | 8.4024 | 10.997 | 0.76406 | 0.04057% | 0.13939 | 0.13933 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147144.321 | 0 | 0 | 147144.321 | 0.0002744%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 64 | 1 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 5.7143 | 0 | 0 | 5.7143 | 0 | 5.1999 | 9.9098 | 0.52473 | 5.1999 | 9.9098 | 0.52473 | 5.7704 | 10.997 | 0.52473 | 0.07618% | 0.092253 | 0.092182 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81305.2894 | 0 | 0 | 81305.2894 | 0.0001884%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 16 | 1 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 4.2011 | 0 | 0 | 4.2011 | 0 | 3.8229 | 9.9098 | 0.38578 | 3.8229 | 9.9098 | 0.38578 | 4.2424 | 10.997 | 0.38578 | 0.2473% | 0.074333 | 0.074103 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 22866.9262 | 0 | 0 | 22866.9262 | 0.0001385%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 83 | 1 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 6.6539 | 0 | 0 | 6.6539 | 0 | 6.055 | 9.9098 | 0.61101 | 6.055 | 9.9098 | 0.61101 | 6.7193 | 10.997 | 0.61101 | 0.05894% | 0.1048 | 0.10474 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107710.5407 | 0 | 0 | 107710.5407 | 0.0002194%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 50 | 1 | 5437.4375 | 98.14% | 1.781% | 0.0775% | 5.283 | 0 | 0 | 5.283 | 0 | 4.8075 | 9.9098 | 0.48512 | 4.8075 | 9.9098 | 0.48512 | 5.3349 | 10.997 | 0.48512 | 0.09716% | 0.090754 | 0.090664 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59915.1296 | 0 | 0 | 59915.1296 | 0.0001742%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 140 | 2 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 11.07 | 0 | 0 | 11.07 | 0 | 10.0736 | 19.8195 | 0.50826 | 10.0736 | 19.8195 | 0.50826 | 11.1788 | 21.9941 | 0.50826 | 0.06913% | 0.16775 | 0.16764 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95455.3737 | 0 | 0 | 95455.3737 | 0.000365%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 92 | 1 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 4.7715 | 0 | 0 | 4.7715 | 0 | 4.342 | 9.9098 | 0.43815 | 4.342 | 9.9098 | 0.43815 | 4.8184 | 10.997 | 0.43815 | 0.05134% | 0.14106 | 0.14098 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 65894.0177 | 0 | 0 | 65894.0177 | 0.0001573%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 11 | 1 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 22.8711 | 0 | 0 | 22.8711 | 0 | 20.8123 | 9.9098 | 2.1002 | 20.8123 | 9.9098 | 2.1002 | 23.0958 | 10.997 | 2.1002 | 0.4486% | 0.2409 | 0.23982 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21165.2687 | 0 | 0 | 21165.2687 | 0.0007542%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 116 | 3 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 22.0827 | 0 | 0 | 22.0827 | 0 | 20.0949 | 29.7293 | 0.67593 | 20.0949 | 29.7293 | 0.67593 | 22.2997 | 32.9911 | 0.67593 | 0.1248% | 0.18538 | 0.18514 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95465.2311 | 0 | 0 | 95465.2311 | 0.0007282%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 116 | 1 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 4.3199 | 0 | 0 | 4.3199 | 0 | 3.9311 | 9.9098 | 0.39669 | 3.9311 | 9.9098 | 0.39669 | 4.3624 | 10.997 | 0.39669 | 0.04141% | 0.14913 | 0.14906 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 69958.0535 | 0 | 0 | 69958.0535 | 0.0001425%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 94 | 3 | 11757.6254 | 97.81% | 2.143% | 0.05143% | 18.167 | 0 | 0 | 18.167 | 0 | 16.5317 | 29.7293 | 0.55608 | 16.5317 | 29.7293 | 0.55608 | 18.3455 | 32.9911 | 0.55608 | 0.1545% | 0.171 | 0.17073 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68759.2242 | 0 | 0 | 68759.2242 | 0.0005991%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 53 | 1 | 6110.8546 | 96.01% | 3.933% | 0.05986% | 5.4794 | 0 | 0 | 5.4794 | 0 | 4.9862 | 9.9098 | 0.50316 | 4.9862 | 9.9098 | 0.50316 | 5.5333 | 10.997 | 0.50316 | 0.08967% | 0.12773 | 0.12761 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47842.8551 | 0 | 0 | 47842.8551 | 0.0001807%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 99 | 2 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 37.0731 | 0 | 0 | 37.0731 | 0 | 33.736 | 19.8195 | 1.7022 | 33.736 | 19.8195 | 1.7022 | 37.4374 | 21.9941 | 1.7022 | 0.09859% | 0.54241 | 0.54187 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69324.5754 | 0 | 0 | 69324.5754 | 0.001223%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 90 | 2 | 6370.0414 | 98.47% | 1.262% | 0.272% | 6.8995 | 0 | 0 | 6.8995 | 0 | 6.2785 | 19.8195 | 0.31678 | 6.2785 | 19.8195 | 0.31678 | 6.9674 | 21.9941 | 0.31678 | 0.1083% | 0.10309 | 0.10298 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61790.4359 | 0 | 0 | 61790.4359 | 0.0002275%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 26 | 1 | 1834.9376 | 96.09% | 3.534% | 0.3793% | 3.3567 | 0 | 0 | 3.3567 | 0 | 3.0546 | 9.9098 | 0.30824 | 3.0546 | 9.9098 | 0.30824 | 3.3897 | 10.997 | 0.30824 | 0.1829% | 0.45792 | 0.45705 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4007.4218 | 0 | 0 | 4007.4218 | 0.0001107%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 1 | 1 | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.069276 | 9.9098 | 0.0069906 | 0.069276 | 9.9098 | 0.0069906 | 0.076876 | 10.997 | 0.0069906 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 161 | 6 | 11572.221 | 88.48% | 11.4% | 0.1243% | 18.8875 | 0 | 0 | 18.8875 | 0 | 17.1874 | 59.4585 | 0.28906 | 17.1874 | 59.4585 | 0.28906 | 19.0731 | 65.9822 | 0.28906 | 0.1632% | 0.35802 | 0.35736 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32329.8984 | 0 | 0 | 32329.8984 | 0.0006228%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 102 | 2 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 3.2362 | 0 | 0 | 3.2362 | 0 | 2.9449 | 19.8195 | 0.14859 | 2.9449 | 19.8195 | 0.14859 | 3.268 | 21.9941 | 0.14859 | 0.0948% | 0.2124 | 0.2122 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16072.7214 | 0 | 0 | 16072.7214 | 0.0001067%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 90 | 2 | 571.2373 | 70.71% | 27.93% | 1.361% | 0.4443 | 0 | 0 | 0.4443 | 0 | 0.40431 | 19.8195 | 0.0204 | 0.40431 | 19.8195 | 0.0204 | 0.44867 | 21.9941 | 0.0204 | 0.07778% | 0.1488 | 0.14863 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3840.2553 | 0 | 0 | 3840.2553 | 1.465e-05%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 3 | 1 | 117.4434 | 97.68% | 1.947% | 0.3705% | 1.8929 | 0 | 0 | 1.8929 | 0 | 1.7225 | 9.9098 | 0.17382 | 1.7225 | 9.9098 | 0.17382 | 1.9115 | 10.997 | 0.17382 | 1.612% | 0.081621 | 0.080274 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1439.4532 | 0 | 0 | 1439.4532 | 6.242e-05%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 85 | 1 | 9632.5907 | 94.96% | 4.965% | 0.07823% | 5.3267 | 0 | 0 | 5.3267 | 0 | 4.8472 | 9.9098 | 0.48914 | 4.8472 | 9.9098 | 0.48914 | 5.379 | 10.997 | 0.48914 | 0.0553% | 0.53792 | 0.53761 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17907.5661 | 0 | 0 | 17907.5661 | 0.0001757%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 43 | 4 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 6.551 | 0 | 0 | 6.551 | 0 | 5.9613 | 39.639 | 0.15039 | 5.9613 | 39.639 | 0.15039 | 6.6154 | 43.9881 | 0.15039 | 0.4085% | 0.53426 | 0.5318 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3002.9908 | 0 | 0 | 3002.9908 | 0.000216%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 116 | 2 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 8.6726 | 0 | 0 | 8.6726 | 0 | 7.892 | 19.8195 | 0.39819 | 7.892 | 19.8195 | 0.39819 | 8.7579 | 21.9941 | 0.39819 | 0.08166% | 0.6048 | 0.60428 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17559.9738 | 0 | 0 | 17559.9738 | 0.000286%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 65 | 1 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 1.1399 | 0 | 0 | 1.1399 | 0 | 1.0373 | 9.9098 | 0.10468 | 1.0373 | 9.9098 | 0.10468 | 1.1511 | 10.997 | 0.10468 | 0.06452% | 0.56527 | 0.56484 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3125.7794 | 0 | 0 | 3125.7794 | 3.759e-05%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 91 | 2 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 3.5034 | 0 | 0 | 3.5034 | 0 | 3.188 | 19.8195 | 0.16085 | 3.188 | 19.8195 | 0.16085 | 3.5378 | 21.9941 | 0.16085 | 0.09524% | 0.48997 | 0.48943 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7508.8441 | 0 | 0 | 7508.8441 | 0.0001155%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 9 | 1 | 1351.7747 | 97.24% | 2.711% | 0.04647% | 7.2298 | 0 | 0 | 7.2298 | 0 | 6.579 | 9.9098 | 0.66389 | 6.579 | 9.9098 | 0.66389 | 7.3008 | 10.997 | 0.66389 | 0.5348% | 0.75637 | 0.75221 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1787.4653 | 0 | 0 | 1787.4653 | 0.0002384%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 9 | 1 | 1211.6194 | 97.39% | 2.475% | 0.1351% | 6.49 | 0 | 0 | 6.49 | 0 | 5.9058 | 9.9098 | 0.59596 | 5.9058 | 9.9098 | 0.59596 | 6.5538 | 10.997 | 0.59596 | 0.5356% | 0.62101 | 0.61759 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1951.3414 | 0 | 0 | 1951.3414 | 0.000214%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 43 | 1 | 2612.2711 | 91.91% | 7.885% | 0.2065% | 2.7638 | 0 | 0 | 2.7638 | 0 | 2.515 | 9.9098 | 0.2538 | 2.515 | 9.9098 | 0.2538 | 2.791 | 10.997 | 0.2538 | 0.1058% | 0.62882 | 0.6281 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4154.6278 | 0 | 0 | 4154.6278 | 9.114e-05%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 85 | 1 | 2119.752 | 55.7% | 43.96% | 0.3458% | 0.68756 | 0 | 0 | 0.68756 | 0 | 0.62567 | 9.9098 | 0.063137 | 0.62567 | 9.9098 | 0.063137 | 0.69432 | 10.997 | 0.063137 | 0.03244% | 0.46343 | 0.46316 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4575.2447 | 0 | 0 | 4575.2447 | 2.267e-05%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 45 | 1 | 630.7627 | 79.12% | 20.09% | 0.7869% | 0.54898 | 0 | 0 | 0.54898 | 0 | 0.49957 | 9.9098 | 0.050411 | 0.49957 | 9.9098 | 0.050411 | 0.55438 | 10.997 | 0.050411 | 0.08703% | 0.54202 | 0.54142 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1164.0028 | 0 | 0 | 1164.0028 | 1.81e-05%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 224 | 10 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 18.4458 | 0 | 0 | 18.4458 | 0 | 16.7854 | 99.0975 | 0.16938 | 16.7854 | 99.0975 | 0.16938 | 18.6271 | 109.9703 | 0.16938 | 0.2026% | 0.49442 | 0.49333 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18418.0976 | 0 | 0 | 18418.0976 | 0.0006083%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 106 | 3 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 7.3881 | 0 | 0 | 7.3881 | 0 | 6.7231 | 29.7293 | 0.22614 | 6.7231 | 29.7293 | 0.22614 | 7.4607 | 32.9911 | 0.22614 | 0.1309% | 0.54394 | 0.54318 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10378.5962 | 0 | 0 | 10378.5962 | 0.0002436%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 22 | 1 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 3.263 | 0 | 0 | 3.263 | 0 | 2.9693 | 9.9098 | 0.29963 | 2.9693 | 9.9098 | 0.29963 | 3.2951 | 10.997 | 0.29963 | 0.2182% | 0.23738 | 0.23685 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6300.4614 | 0 | 0 | 6300.4614 | 0.0001076%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 45 | 2 | 2320.0162 | 95.55% | 4.318% | 0.1352% | 4.8768 | 0 | 0 | 4.8768 | 0 | 4.4378 | 19.8195 | 0.22391 | 4.4378 | 19.8195 | 0.22391 | 4.9247 | 21.9941 | 0.22391 | 0.2102% | 0.24779 | 0.24724 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9363.8269 | 0 | 0 | 9363.8269 | 0.0001608%
2027 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 1 | 1 | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.34564 | 9.9098 | 0.034879 | 0.34564 | 9.9098 | 0.034879 | 0.38356 | 10.997 | 0.034879 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 1 | 1 | 625.5425 | 99.9% | 0% | 0.09615% | 30.9346 | 0 | 0 | 30.9346 | 0 | 28.15 | 9.9098 | 2.8406 | 28.15 | 9.9098 | 2.8406 | 31.2386 | 10.997 | 2.8406 | 4.945% | 0.0036434 | 0.0034631 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171700.5551 | 0 | 0 | 171700.5551 | 0.00102%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 20 | 1 | 5264.9688 | 98.33% | 1.599% | 0.07273% | 12.813 | 0 | 0 | 12.813 | 0 | 11.6597 | 9.9098 | 1.1766 | 11.6597 | 9.9098 | 1.1766 | 12.9389 | 10.997 | 1.1766 | 0.2434% | 0.091034 | 0.090809 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57837.5901 | 0 | 0 | 57837.5901 | 0.0004225%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 53 | 4 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 62.1458 | 0 | 0 | 62.1458 | 0 | 56.5518 | 39.639 | 1.4267 | 56.5518 | 39.639 | 1.4267 | 62.7565 | 43.9881 | 1.4267 | 0.3712% | 0.16225 | 0.16165 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103176.5447 | 0 | 0 | 103176.5447 | 0.002049%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 47 | 1 | 2978.814 | 97.34% | 2.471% | 0.184% | 3.054 | 0 | 0 | 3.054 | 0 | 2.7791 | 9.9098 | 0.28044 | 2.7791 | 9.9098 | 0.28044 | 3.084 | 10.997 | 0.28044 | 0.1025% | 0.26824 | 0.26795 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11105.5174 | 0 | 0 | 11105.5174 | 0.0001007%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 129 | 2 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 1.9588 | 0 | 0 | 1.9588 | 0 | 1.7825 | 19.8195 | 0.089935 | 1.7825 | 19.8195 | 0.089935 | 1.978 | 21.9941 | 0.089935 | 0.07425% | 0.13822 | 0.13811 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19085.8993 | 0 | 0 | 19085.8993 | 6.459e-05%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 84 | 1 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 1.8653 | 0 | 0 | 1.8653 | 0 | 1.6974 | 9.9098 | 0.17129 | 1.6974 | 9.9098 | 0.17129 | 1.8837 | 10.997 | 0.17129 | 0.05464% | 0.28561 | 0.28544 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11953.6927 | 0 | 0 | 11953.6927 | 6.151e-05%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 53 | 1 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 6.1091 | 0 | 0 | 6.1091 | 0 | 5.5592 | 9.9098 | 0.56098 | 5.5592 | 9.9098 | 0.56098 | 6.1691 | 10.997 | 0.56098 | 0.09033% | 0.27105 | 0.27079 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24952.2153 | 0 | 0 | 24952.2153 | 0.0002015%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 74 | 1 | 2044.6463 | 97.57% | 2.13% | 0.298% | 1.3345 | 0 | 0 | 1.3345 | 0 | 1.2144 | 9.9098 | 0.12254 | 1.2144 | 9.9098 | 0.12254 | 1.3476 | 10.997 | 0.12254 | 0.06527% | 0.10446 | 0.10439 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19573.5035 | 0 | 0 | 19573.5035 | 4.401e-05%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 49 | 2 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 22.1734 | 0 | 0 | 22.1734 | 0 | 20.1775 | 19.8195 | 1.0181 | 20.1775 | 19.8195 | 1.0181 | 22.3913 | 21.9941 | 1.0181 | 0.1954% | 0.27097 | 0.27042 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41891.1336 | 0 | 0 | 41891.1336 | 0.0007312%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 87 | 2 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 9.4342 | 0 | 0 | 9.4342 | 0 | 8.585 | 19.8195 | 0.43316 | 8.585 | 19.8195 | 0.43316 | 9.5269 | 21.9941 | 0.43316 | 0.1113% | 0.15411 | 0.15393 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55014.068 | 0 | 0 | 55014.068 | 0.0003111%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 73 | 4 | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 23.4817 | 0 | 0 | 23.4817 | 0 | 21.3681 | 39.639 | 0.53907 | 21.3681 | 39.639 | 0.53907 | 23.7125 | 43.9881 | 0.53907 | 0.2695% | 0.071321 | 0.071128 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122168.0023 | 0 | 0 | 122168.0023 | 0.0007743%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 25 | 2 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 21.9781 | 0 | 0 | 21.9781 | 0 | 19.9998 | 19.8195 | 1.0091 | 19.9998 | 19.8195 | 1.0091 | 22.1941 | 21.9941 | 1.0091 | 0.3912% | 0.063668 | 0.063415 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88253.612 | 0 | 0 | 88253.612 | 0.0007248%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 37 | 1 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 11.9431 | 0 | 0 | 11.9431 | 0 | 10.868 | 9.9098 | 1.0967 | 10.868 | 9.9098 | 1.0967 | 12.0604 | 10.997 | 1.0967 | 0.1325% | 0.074421 | 0.074321 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121104.3584 | 0 | 0 | 121104.3584 | 0.0003938%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 1 | 1 | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 245.0024 | 9.9098 | 24.7234 | 245.0024 | 9.9098 | 24.7234 | 271.8835 | 10.997 | 24.7234 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 46 | 2 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 11.742 | 0 | 0 | 11.742 | 0 | 10.685 | 19.8195 | 0.53912 | 10.685 | 19.8195 | 0.53912 | 11.8574 | 21.9941 | 0.53912 | 0.2147% | 0.040404 | 0.040317 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135337.7884 | 0 | 0 | 135337.7884 | 0.0003872%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 114 | 4 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 19.6117 | 0 | 0 | 19.6117 | 0 | 17.8463 | 39.639 | 0.45022 | 17.8463 | 39.639 | 0.45022 | 19.8044 | 43.9881 | 0.45022 | 0.1733% | 0.060207 | 0.060103 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 187979.8382 | 0 | 0 | 187979.8382 | 0.0006467%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 89 | 3 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 22.6455 | 0 | 0 | 22.6455 | 0 | 20.6071 | 29.7293 | 0.69316 | 20.6071 | 29.7293 | 0.69316 | 22.8681 | 32.9911 | 0.69316 | 0.1652% | 0.18916 | 0.18884 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72486.2016 | 0 | 0 | 72486.2016 | 0.0007468%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 84 | 1 | 8801.877 | 98.2% | 1.718% | 0.0819% | 5.0935 | 0 | 0 | 5.0935 | 0 | 4.635 | 9.9098 | 0.46772 | 4.635 | 9.9098 | 0.46772 | 5.1435 | 10.997 | 0.46772 | 0.05787% | 0.18313 | 0.18303 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48062.9 | 0 | 0 | 48062.9 | 0.000168%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 283 | 7 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 48.9569 | 0 | 0 | 48.9569 | 0 | 44.5501 | 69.3683 | 0.64223 | 44.5501 | 69.3683 | 0.64223 | 49.4381 | 76.9792 | 0.64223 | 0.1213% | 0.27264 | 0.2723 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148094.1967 | 0 | 0 | 148094.1967 | 0.001614%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 92 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 9.6518 | 0 | 0 | 9.6518 | 0 | 8.783 | 9.9098 | 0.8863 | 8.783 | 9.9098 | 0.8863 | 9.7467 | 10.997 | 0.8863 | 0.05141% | 0.15307 | 0.15298 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122658.6463 | 0 | 0 | 122658.6463 | 0.0003183%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 124 | 4 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 40.8583 | 0 | 0 | 40.8583 | 0 | 37.1805 | 39.639 | 0.93798 | 37.1805 | 39.639 | 0.93798 | 41.2598 | 43.9881 | 0.93798 | 0.1587% | 0.15161 | 0.15137 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169798.347 | 0 | 0 | 169798.347 | 0.001347%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 4 | 1 | 55.0677 | 92.66% | 4.028% | 3.312% | 0.63144 | 0 | 0 | 0.63144 | 0 | 0.57461 | 9.9098 | 0.057984 | 0.57461 | 9.9098 | 0.057984 | 0.63765 | 10.997 | 0.057984 | 1.147% | 0.014982 | 0.014796 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3679.0172 | 0 | 0 | 3679.0172 | 2.082e-05%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 1 | 1 | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 6.2808 | 9.9098 | 0.6338 | 6.2808 | 9.9098 | 0.6338 | 6.9699 | 10.997 | 0.6338 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 41 | 2 | 8606.9717 | 99.86% | 0% | 0.1411% | 20.7534 | 0 | 0 | 20.7534 | 0 | 18.8853 | 19.8195 | 0.95286 | 18.8853 | 19.8195 | 0.95286 | 20.9573 | 21.9941 | 0.95286 | 0.2411% | 0.067132 | 0.06697 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128210.4913 | 0 | 0 | 128210.4913 | 0.0006844%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 37 | 2 | 8439.7692 | 97.62% | 2.35% | 0.03436% | 22.0437 | 0 | 0 | 22.0437 | 0 | 20.0595 | 19.8195 | 1.0121 | 20.0595 | 19.8195 | 1.0121 | 22.2604 | 21.9941 | 1.0121 | 0.2612% | 0.054867 | 0.05472 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 153833.2797 | 0 | 0 | 153833.2797 | 0.0007269%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 74 | 2 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 35.9185 | 0 | 0 | 35.9185 | 0 | 32.6853 | 19.8195 | 1.6492 | 32.6853 | 19.8195 | 1.6492 | 36.2715 | 21.9941 | 1.6492 | 0.1327% | 0.088049 | 0.087931 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307404.8102 | 0 | 0 | 307404.8102 | 0.001184%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 76 | 1 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 10.0971 | 0 | 0 | 10.0971 | 0 | 9.1882 | 9.9098 | 0.92719 | 9.1882 | 9.9098 | 0.92719 | 10.1963 | 10.997 | 0.92719 | 0.06404% | 0.20692 | 0.20679 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76196.1528 | 0 | 0 | 76196.1528 | 0.000333%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 109 | 3 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 7.3049 | 0 | 0 | 7.3049 | 0 | 6.6473 | 29.7293 | 0.2236 | 6.6473 | 29.7293 | 0.2236 | 7.3766 | 32.9911 | 0.2236 | 0.1311% | 0.23644 | 0.23612 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23561.9543 | 0 | 0 | 23561.9543 | 0.0002409%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 40 | 1 | 1466.2762 | 91.81% | 7.905% | 0.289% | 1.6658 | 0 | 0 | 1.6658 | 0 | 1.5159 | 9.9098 | 0.15297 | 1.5159 | 9.9098 | 0.15297 | 1.6822 | 10.997 | 0.15297 | 0.1136% | 0.1878 | 0.18757 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7808.257 | 0 | 0 | 7808.257 | 5.493e-05%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 146 | 2 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 27.6664 | 0 | 0 | 27.6664 | 0 | 25.1761 | 19.8195 | 1.2703 | 25.1761 | 19.8195 | 1.2703 | 27.9383 | 21.9941 | 1.2703 | 0.06706% | 0.23053 | 0.23038 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 178971.8632 | 0 | 0 | 178971.8632 | 0.0009123%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 46 | 1 | 3646.8048 | 91.91% | 7.986% | 0.1044% | 3.6068 | 0 | 0 | 3.6068 | 0 | 3.2821 | 9.9098 | 0.3312 | 3.2821 | 9.9098 | 0.3312 | 3.6422 | 10.997 | 0.3312 | 0.0989% | 0.17929 | 0.1791 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20341.6218 | 0 | 0 | 20341.6218 | 0.0001189%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 95 | 1 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 11.6494 | 0 | 0 | 11.6494 | 0 | 10.6008 | 9.9098 | 1.0697 | 10.6008 | 9.9098 | 1.0697 | 11.7639 | 10.997 | 1.0697 | 0.05163% | 0.20355 | 0.20344 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110854.5915 | 0 | 0 | 110854.5915 | 0.0003842%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 10 | 1 | 847.524 | 96.52% | 3.329% | 0.1488% | 4.0493 | 0 | 0 | 4.0493 | 0 | 3.6848 | 9.9098 | 0.37184 | 3.6848 | 9.9098 | 0.37184 | 4.0891 | 10.997 | 0.37184 | 0.4778% | 0.16572 | 0.1649 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5114.9538 | 0 | 0 | 5114.9538 | 0.0001335%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 126 | 3 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 64.6455 | 0 | 0 | 64.6455 | 0 | 58.8266 | 29.7293 | 1.9787 | 58.8266 | 29.7293 | 1.9787 | 65.2809 | 32.9911 | 1.9787 | 0.117% | 0.31112 | 0.31076 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177592.2261 | 0 | 0 | 177592.2261 | 0.002132%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 2 | 1 | 1991.7107 | 76.61% | 23.16% | 0.2301% | 37.7629 | 0 | 0 | 37.7629 | 0 | 34.3637 | 9.9098 | 3.4677 | 34.3637 | 9.9098 | 3.4677 | 38.1341 | 10.997 | 3.4677 | 1.896% | 0.065336 | 0.063719 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30665.0109 | 0 | 0 | 30665.0109 | 0.001245%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 100 | 3 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 22.2829 | 0 | 0 | 22.2829 | 0 | 20.2771 | 29.7293 | 0.68206 | 20.2771 | 29.7293 | 0.68206 | 22.5019 | 32.9911 | 0.68206 | 0.1471% | 0.14704 | 0.14682 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103026.3126 | 0 | 0 | 103026.3126 | 0.0007348%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 189 | 6 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 44.2747 | 0 | 0 | 44.2747 | 0 | 40.2893 | 59.4585 | 0.6776 | 40.2893 | 59.4585 | 0.6776 | 44.7098 | 65.9822 | 0.6776 | 0.1554% | 0.18464 | 0.18435 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154271.3945 | 0 | 0 | 154271.3945 | 0.00146%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 45 | 2 | 14770.5962 | 98.43% | 1.528% | 0.03956% | 31.9858 | 0 | 0 | 31.9858 | 0 | 29.1066 | 19.8195 | 1.4686 | 29.1066 | 19.8195 | 1.4686 | 32.3001 | 21.9941 | 1.4686 | 0.2166% | 0.13837 | 0.13806 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106751.562 | 0 | 0 | 106751.562 | 0.001055%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 103 | 2 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 10.7196 | 0 | 0 | 10.7196 | 0 | 9.7547 | 19.8195 | 0.49218 | 9.7547 | 19.8195 | 0.49218 | 10.825 | 21.9941 | 0.49218 | 0.09513% | 0.17642 | 0.17625 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63870.7169 | 0 | 0 | 63870.7169 | 0.0003535%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 27 | 2 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 41.8014 | 0 | 0 | 41.8014 | 0 | 38.0387 | 19.8195 | 1.9193 | 38.0387 | 19.8195 | 1.9193 | 42.2122 | 21.9941 | 1.9193 | 0.3649% | 0.12528 | 0.12482 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91453.0219 | 0 | 0 | 91453.0219 | 0.001378%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 81 | 2 | 8019.1792 | 98.53% | 1.384% | 0.08092% | 9.6576 | 0 | 0 | 9.6576 | 0 | 8.7883 | 19.8195 | 0.44342 | 8.7883 | 19.8195 | 0.44342 | 9.7525 | 21.9941 | 0.44342 | 0.1204% | 0.15062 | 0.15044 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53240.6013 | 0 | 0 | 53240.6013 | 0.0003185%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 106 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 10.7559 | 0 | 0 | 10.7559 | 0 | 9.7877 | 9.9098 | 0.98769 | 9.7877 | 9.9098 | 0.98769 | 10.8616 | 10.997 | 0.98769 | 0.04595% | 0.17603 | 0.17595 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 132983.6782 | 0 | 0 | 132983.6782 | 0.0003547%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 54 | 1 | 22914.3284 | 97.48% | 2.478% | 0.04418% | 20.4751 | 0 | 0 | 20.4751 | 0 | 18.6321 | 9.9098 | 1.8802 | 18.6321 | 9.9098 | 1.8802 | 20.6763 | 10.997 | 1.8802 | 0.08936% | 0.16607 | 0.16592 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 137981.9677 | 0 | 0 | 137981.9677 | 0.0006752%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 59 | 2 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 15.2172 | 0 | 0 | 15.2172 | 0 | 13.8474 | 19.8195 | 0.69868 | 13.8474 | 19.8195 | 0.69868 | 15.3668 | 21.9941 | 0.69868 | 0.1663% | 0.14195 | 0.14171 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64460.3157 | 0 | 0 | 64460.3157 | 0.0005018%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 82 | 1 | 6521.7236 | 98.03% | 1.864% | 0.1053% | 3.8594 | 0 | 0 | 3.8594 | 0 | 3.512 | 9.9098 | 0.3544 | 3.512 | 9.9098 | 0.3544 | 3.8973 | 10.997 | 0.3544 | 0.05918% | 0.1523 | 0.15221 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42822.1258 | 0 | 0 | 42822.1258 | 0.0001273%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 104 | 2 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 3.1152 | 0 | 0 | 3.1152 | 0 | 2.8348 | 19.8195 | 0.14303 | 2.8348 | 19.8195 | 0.14303 | 3.1458 | 21.9941 | 0.14303 | 0.08919% | 0.16472 | 0.16456 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21206.0969 | 0 | 0 | 21206.0969 | 0.0001027%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 29 | 2 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 24.1527 | 0 | 0 | 24.1527 | 0 | 21.9786 | 19.8195 | 1.1089 | 21.9786 | 19.8195 | 1.1089 | 24.3901 | 21.9941 | 1.1089 | 0.3398% | 0.14069 | 0.14021 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50518.0241 | 0 | 0 | 50518.0241 | 0.0007965%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 95 | 2 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 36.2773 | 0 | 0 | 36.2773 | 0 | 33.0118 | 19.8195 | 1.6656 | 33.0118 | 19.8195 | 1.6656 | 36.6338 | 21.9941 | 1.6656 | 0.1032% | 0.16564 | 0.16546 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212251.7107 | 0 | 0 | 212251.7107 | 0.001196%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 17 | 1 | 7055.7157 | 98.18% | 1.793% | 0.03106% | 20.1698 | 0 | 0 | 20.1698 | 0 | 18.3542 | 9.9098 | 1.8521 | 18.3542 | 9.9098 | 1.8521 | 20.368 | 10.997 | 1.8521 | 0.2859% | 0.10829 | 0.10798 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65158.4948 | 0 | 0 | 65158.4948 | 0.0006651%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 43 | 3 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 64.8185 | 0 | 0 | 64.8185 | 0 | 58.9839 | 29.7293 | 1.984 | 58.9839 | 29.7293 | 1.984 | 65.4555 | 32.9911 | 1.984 | 0.3443% | 0.12361 | 0.12318 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152301.6608 | 0 | 0 | 152301.6608 | 0.002137%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 11 | 1 | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 22.5426 | 0 | 0 | 22.5426 | 0 | 20.5135 | 9.9098 | 2.07 | 20.5135 | 9.9098 | 2.07 | 22.7642 | 10.997 | 2.07 | 0.4478% | 0.10909 | 0.1086 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46150.2795 | 0 | 0 | 46150.2795 | 0.0007434%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 32 | 1 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 7.7802 | 0 | 0 | 7.7802 | 0 | 7.0798 | 9.9098 | 0.71443 | 7.0798 | 9.9098 | 0.71443 | 7.8566 | 10.997 | 0.71443 | 0.1534% | 0.10587 | 0.1057 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47912.2199 | 0 | 0 | 47912.2199 | 0.0002566%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 80 | 3 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 16.8715 | 0 | 0 | 16.8715 | 0 | 15.3528 | 29.7293 | 0.51642 | 15.3528 | 29.7293 | 0.51642 | 17.0373 | 32.9911 | 0.51642 | 0.1782% | 0.13914 | 0.13888 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68067.7736 | 0 | 0 | 68067.7736 | 0.0005564%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 19 | 1 | 585.5086 | 87.68% | 11.85% | 0.4758% | 1.3374 | 0 | 0 | 1.3374 | 0 | 1.2171 | 9.9098 | 0.12281 | 1.2171 | 9.9098 | 0.12281 | 1.3506 | 10.997 | 0.12281 | 0.2284% | 0.083403 | 0.083186 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7022.4605 | 0 | 0 | 7022.4605 | 4.41e-05%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 22 | 1 | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 4.8129 | 0 | 0 | 4.8129 | 0 | 4.3797 | 9.9098 | 0.44196 | 4.3797 | 9.9098 | 0.44196 | 4.8602 | 10.997 | 0.44196 | 0.2238% | 0.10605 | 0.10581 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20282.242 | 0 | 0 | 20282.242 | 0.0001587%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 85 | 2 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 7.608 | 0 | 0 | 7.608 | 0 | 6.9232 | 19.8195 | 0.34931 | 6.9232 | 19.8195 | 0.34931 | 7.6828 | 21.9941 | 0.34931 | 0.1149% | 0.23843 | 0.23815 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27769.4921 | 0 | 0 | 27769.4921 | 0.0002509%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 124 | 6 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 60.1217 | 0 | 0 | 60.1217 | 0 | 54.7099 | 59.4585 | 0.92014 | 54.7099 | 59.4585 | 0.92014 | 60.7126 | 65.9822 | 0.92014 | 0.2375% | 0.28668 | 0.28599 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88318.2968 | 0 | 0 | 88318.2968 | 0.001983%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 119 | 5 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 58.1755 | 0 | 0 | 58.1755 | 0 | 52.9389 | 49.5488 | 1.0684 | 52.9389 | 49.5488 | 1.0684 | 58.7473 | 54.9851 | 1.0684 | 0.2049% | 0.28228 | 0.28169 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100609.4042 | 0 | 0 | 100609.4042 | 0.001918%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 103 | 4 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 50.8872 | 0 | 0 | 50.8872 | 0 | 46.3067 | 39.639 | 1.1682 | 46.3067 | 39.639 | 1.1682 | 51.3873 | 43.9881 | 1.1682 | 0.1906% | 0.30703 | 0.30644 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86952.5168 | 0 | 0 | 86952.5168 | 0.001678%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 68 | 2 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 22.6403 | 0 | 0 | 22.6403 | 0 | 20.6023 | 19.8195 | 1.0395 | 20.6023 | 19.8195 | 1.0395 | 22.8628 | 21.9941 | 1.0395 | 0.1419% | 0.1351 | 0.1349 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118117.636 | 0 | 0 | 118117.636 | 0.0007466%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 24 | 4 | 919.3728 | 93.93% | 5.62% | 0.4487% | 7.1245 | 0 | 0 | 7.1245 | 0 | 6.4832 | 39.639 | 0.16356 | 6.4832 | 39.639 | 0.16356 | 7.1945 | 43.9881 | 0.16356 | 0.7749% | 0.38465 | 0.38147 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2391.3919 | 0 | 0 | 2391.3919 | 0.0002349%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 81 | 3 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 10.7739 | 0 | 0 | 10.7739 | 0 | 9.8041 | 29.7293 | 0.32978 | 9.8041 | 29.7293 | 0.32978 | 10.8797 | 32.9911 | 0.32978 | 0.1826% | 0.046754 | 0.046668 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126173.9523 | 0 | 0 | 126173.9523 | 0.0003553%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 63 | 1 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 3.9067 | 0 | 0 | 3.9067 | 0 | 3.555 | 9.9098 | 0.35874 | 3.555 | 9.9098 | 0.35874 | 3.9451 | 10.997 | 0.35874 | 0.07828% | 0.045737 | 0.045701 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109123.4318 | 0 | 0 | 109123.4318 | 0.0001288%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 16 | 1 | 2514.2831 | 99.84% | 0% | 0.1648% | 7.7657 | 0 | 0 | 7.7657 | 0 | 7.0667 | 9.9098 | 0.71311 | 7.0667 | 9.9098 | 0.71311 | 7.8421 | 10.997 | 0.71311 | 0.3089% | 0.020398 | 0.020334 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123264.3018 | 0 | 0 | 123264.3018 | 0.0002561%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 93 | 2 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 4.524 | 0 | 0 | 4.524 | 0 | 4.1168 | 19.8195 | 0.20771 | 4.1168 | 19.8195 | 0.20771 | 4.5685 | 21.9941 | 0.20771 | 0.097% | 0.17153 | 0.17134 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27193.1367 | 0 | 0 | 27193.1367 | 0.0001492%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 19 | 1 | 765.4961 | 75% | 24.28% | 0.7274% | 1.4957 | 0 | 0 | 1.4957 | 0 | 1.361 | 9.9098 | 0.13734 | 1.361 | 9.9098 | 0.13734 | 1.5104 | 10.997 | 0.13734 | 0.1954% | 0.11418 | 0.11388 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6708.8 | 0 | 0 | 6708.8 | 4.932e-05%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 8 | 1 | 247.9994 | 97.75% | 1.792% | 0.4608% | 1.4999 | 0 | 0 | 1.4999 | 0 | 1.3649 | 9.9098 | 0.13773 | 1.3649 | 9.9098 | 0.13773 | 1.5147 | 10.997 | 0.13773 | 0.6048% | 0.064829 | 0.064428 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3825.9752 | 0 | 0 | 3825.9752 | 4.946e-05%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 3 | 1 | 75.2008 | 96.65% | 1.975% | 1.378% | 1.1992 | 0 | 0 | 1.1992 | 0 | 1.0913 | 9.9098 | 0.11012 | 1.0913 | 9.9098 | 0.11012 | 1.211 | 10.997 | 0.11012 | 1.595% | 0.064214 | 0.063154 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1171.7632 | 0 | 0 | 1171.7632 | 3.955e-05%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 23 | 1 | 3965.2217 | 98.26% | 1.658% | 0.07833% | 8.3857 | 0 | 0 | 8.3857 | 0 | 7.6309 | 9.9098 | 0.77004 | 7.6309 | 9.9098 | 0.77004 | 8.4681 | 10.997 | 0.77004 | 0.2115% | 0.19397 | 0.19355 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20443.6355 | 0 | 0 | 20443.6355 | 0.0002765%
2027 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 2 | 1 | 157.8878 | 78.49% | 21.24% | 0.2654% | 3.0673 | 0 | 0 | 3.0673 | 0 | 2.7912 | 9.9098 | 0.28167 | 2.7912 | 9.9098 | 0.28167 | 3.0975 | 10.997 | 0.28167 | 1.943% | 0.66566 | 0.64918 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 238.4861 | 0 | 0 | 238.4861 | 0.0001011%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 64 | 1 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 6.4891 | 0 | 0 | 6.4891 | 0 | 5.905 | 9.9098 | 0.59588 | 5.905 | 9.9098 | 0.59588 | 6.5529 | 10.997 | 0.59588 | 0.07462% | 0.68132 | 0.6808 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12764.5062 | 0 | 0 | 12764.5062 | 0.000214%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 33 | 2 | 3561.9587 | 98.42% | 1.457% | 0.1235% | 10.517 | 0 | 0 | 10.517 | 0 | 9.5703 | 19.8195 | 0.48287 | 9.5703 | 19.8195 | 0.48287 | 10.6203 | 21.9941 | 0.48287 | 0.2953% | 0.12988 | 0.12949 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27425.7108 | 0 | 0 | 27425.7108 | 0.0003468%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 39 | 1 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 3.7076 | 0 | 0 | 3.7076 | 0 | 3.3739 | 9.9098 | 0.34046 | 3.3739 | 9.9098 | 0.34046 | 3.744 | 10.997 | 0.34046 | 0.1243% | 0.13489 | 0.13472 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22120.7035 | 0 | 0 | 22120.7035 | 0.0001223%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 30 | 2 | 4300.1838 | 98.66% | 1.226% | 0.1146% | 14.0004 | 0 | 0 | 14.0004 | 0 | 12.7402 | 19.8195 | 0.64281 | 12.7402 | 19.8195 | 0.64281 | 14.138 | 21.9941 | 0.64281 | 0.3256% | 0.13142 | 0.13098 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32723.4218 | 0 | 0 | 32723.4218 | 0.0004617%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 79 | 3 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 9.9999 | 0 | 0 | 9.9999 | 0 | 9.0998 | 29.7293 | 0.30609 | 9.0998 | 29.7293 | 0.30609 | 10.0982 | 32.9911 | 0.30609 | 0.1584% | 0.11961 | 0.11939 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 52781.1081 | 0 | 0 | 52781.1081 | 0.0003298%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 92 | 2 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 7.0863 | 0 | 0 | 7.0863 | 0 | 6.4484 | 19.8195 | 0.32536 | 6.4484 | 19.8195 | 0.32536 | 7.1559 | 21.9941 | 0.32536 | 0.1066% | 0.082825 | 0.082736 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80237.2836 | 0 | 0 | 80237.2836 | 0.0002337%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 30 | 1 | 1438.3629 | 99.75% | 0% | 0.2509% | 2.3673 | 0 | 0 | 2.3673 | 0 | 2.1543 | 9.9098 | 0.21739 | 2.1543 | 9.9098 | 0.21739 | 2.3906 | 10.997 | 0.21739 | 0.1646% | 0.019586 | 0.019554 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73438.6208 | 0 | 0 | 73438.6208 | 7.807e-05%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 28 | 1 | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 20.6171 | 0 | 0 | 20.6171 | 0 | 18.7613 | 9.9098 | 1.8932 | 18.7613 | 9.9098 | 1.8932 | 20.8197 | 10.997 | 1.8932 | 0.1755% | 0.11659 | 0.11638 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100776.6194 | 0 | 0 | 100776.6194 | 0.0006799%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 13 | 1 | 3684.9802 | 98.15% | 1.772% | 0.07391% | 13.7723 | 0 | 0 | 13.7723 | 0 | 12.5326 | 9.9098 | 1.2647 | 12.5326 | 9.9098 | 1.2647 | 13.9076 | 10.997 | 1.2647 | 0.3737% | 0.092289 | 0.091937 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39931.694 | 0 | 0 | 39931.694 | 0.0004542%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 16 | 1 | 427.4478 | 90.46% | 9.431% | 0.1062% | 1.1963 | 0 | 0 | 1.1963 | 0 | 1.0886 | 9.9098 | 0.10985 | 1.0886 | 9.9098 | 0.10985 | 1.2081 | 10.997 | 0.10985 | 0.2799% | 0.13508 | 0.13466 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3165.4398 | 0 | 0 | 3165.4398 | 3.945e-05%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 51 | 1 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 15.3763 | 0 | 0 | 15.3763 | 0 | 13.9922 | 9.9098 | 1.412 | 13.9922 | 9.9098 | 1.412 | 15.5274 | 10.997 | 1.412 | 0.09618% | 0.15941 | 0.15925 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100292.7533 | 0 | 0 | 100292.7533 | 0.0005071%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 38 | 3 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 31.6477 | 0 | 0 | 31.6477 | 0 | 28.799 | 29.7293 | 0.96871 | 28.799 | 29.7293 | 0.96871 | 31.9587 | 32.9911 | 0.96871 | 0.3878% | 0.15819 | 0.15757 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51584.4785 | 0 | 0 | 51584.4785 | 0.001044%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 127 | 3 | 37077.302 | 99.36% | 0.615% | 0.02874% | 43.0751 | 0 | 0 | 43.0751 | 0 | 39.1977 | 29.7293 | 1.3185 | 39.1977 | 29.7293 | 1.3185 | 43.4984 | 32.9911 | 1.3185 | 0.1162% | 0.20421 | 0.20397 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181563.2766 | 0 | 0 | 181563.2766 | 0.00142%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 53 | 1 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 1.521 | 0 | 0 | 1.521 | 0 | 1.3841 | 9.9098 | 0.13967 | 1.3841 | 9.9098 | 0.13967 | 1.5359 | 10.997 | 0.13967 | 0.07369% | 0.42513 | 0.42473 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4856.0126 | 0 | 0 | 4856.0126 | 5.016e-05%
2027 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 1 | 1 | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.69648 | 9.9098 | 0.070283 | 0.69648 | 9.9098 | 0.070283 | 0.7729 | 10.997 | 0.070283 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 90 | 6 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 11.6807 | 0 | 0 | 11.6807 | 0 | 10.6293 | 59.4585 | 0.17877 | 10.6293 | 59.4585 | 0.17877 | 11.7955 | 65.9822 | 0.17877 | 0.314% | 0.19421 | 0.19357 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19154.3037 | 0 | 0 | 19154.3037 | 0.0003852%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 29 | 1 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 2.5582 | 0 | 0 | 2.5582 | 0 | 2.3279 | 9.9098 | 0.23491 | 2.3279 | 9.9098 | 0.23491 | 2.5833 | 10.997 | 0.23491 | 0.167% | 0.1808 | 0.1805 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8472.158 | 0 | 0 | 8472.158 | 8.436e-05%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 32 | 1 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 7.8052 | 0 | 0 | 7.8052 | 0 | 7.1026 | 9.9098 | 0.71673 | 7.1026 | 9.9098 | 0.71673 | 7.8819 | 10.997 | 0.71673 | 0.1525% | 0.12647 | 0.12627 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40482.6819 | 0 | 0 | 40482.6819 | 0.0002574%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 109 | 7 | 6915.6819 | 99% | 0.9206% | 0.07911% | 21.7645 | 0 | 0 | 21.7645 | 0 | 19.8054 | 69.3683 | 0.28551 | 19.8054 | 69.3683 | 0.28551 | 21.9784 | 76.9792 | 0.28551 | 0.3147% | 0.20255 | 0.20191 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34144.2412 | 0 | 0 | 34144.2412 | 0.0007177%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 66 | 2 | 3027.5479 | 94.73% | 5.109% | 0.164% | 4.3018 | 0 | 0 | 4.3018 | 0 | 3.9146 | 19.8195 | 0.19751 | 3.9146 | 19.8195 | 0.19751 | 4.3441 | 21.9941 | 0.19751 | 0.1421% | 0.24168 | 0.24132 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12528.0546 | 0 | 0 | 12528.0546 | 0.0001419%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 65 | 3 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 23.6206 | 0 | 0 | 23.6206 | 0 | 21.4944 | 29.7293 | 0.72301 | 21.4944 | 29.7293 | 0.72301 | 23.8527 | 32.9911 | 0.72301 | 0.2246% | 0.14726 | 0.14693 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71420.3169 | 0 | 0 | 71420.3169 | 0.0007789%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 17 | 1 | 5229.9021 | 98.11% | 1.831% | 0.05575% | 14.9409 | 0 | 0 | 14.9409 | 0 | 13.596 | 9.9098 | 1.372 | 13.596 | 9.9098 | 1.372 | 15.0877 | 10.997 | 1.372 | 0.2857% | 0.12706 | 0.12669 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41163.7366 | 0 | 0 | 41163.7366 | 0.0004927%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 85 | 5 | 6920.124 | 97.57% | 2.306% | 0.1195% | 19.661 | 0 | 0 | 19.661 | 0 | 17.8912 | 49.5488 | 0.36108 | 17.8912 | 49.5488 | 0.36108 | 19.8542 | 54.9851 | 0.36108 | 0.2841% | 0.15381 | 0.15336 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 44995.97 | 0 | 0 | 44995.97 | 0.0006483%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 27 | 2 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 21.6547 | 0 | 0 | 21.6547 | 0 | 19.7055 | 19.8195 | 0.99425 | 19.7055 | 19.8195 | 0.99425 | 21.8675 | 21.9941 | 0.99425 | 0.3642% | 0.15284 | 0.15228 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38907.0666 | 0 | 0 | 38907.0666 | 0.0007141%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 128 | 4 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 4.8731 | 0 | 0 | 4.8731 | 0 | 4.4344 | 39.639 | 0.11187 | 4.4344 | 39.639 | 0.11187 | 4.921 | 43.9881 | 0.11187 | 0.145% | 0.19527 | 0.19497 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17216.3459 | 0 | 0 | 17216.3459 | 0.0001607%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 112 | 3 | 2610.8 | 93.6% | 6.065% | 0.3401% | 3.2399 | 0 | 0 | 3.2399 | 0 | 2.8125 | 28.3597 | 0.099171 | 2.8125 | 28.3597 | 0.099171 | 3.2878 | 33.1528 | 0.099171 | 0.1241% | 0.2194 | 0.21911 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11900.5974 | 0 | 0 | 11900.5974 | 0.0001068%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 188 | 5 | 4180.1374 | 93.8% | 5.869% | 0.3284% | 5.1621 | 0 | 0 | 5.1621 | 0 | 4.481 | 47.2661 | 0.094804 | 4.481 | 47.2661 | 0.094804 | 5.2384 | 55.2547 | 0.094804 | 0.1235% | 0.24743 | 0.24711 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16895.3292 | 0 | 0 | 16895.3292 | 0.0001702%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 78 | 2 | 1627.9508 | 92.79% | 6.809% | 0.4053% | 1.9172 | 0 | 0 | 1.9172 | 0 | 1.6642 | 18.9065 | 0.088025 | 1.6642 | 18.9065 | 0.088025 | 1.9455 | 22.1019 | 0.088025 | 0.1178% | 0.20887 | 0.20861 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7794.6365 | 0 | 0 | 7794.6365 | 6.322e-05%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 84 | 2 | 6201.607 | 97.29% | 2.601% | 0.1104% | 7.1109 | 0 | 0 | 7.1109 | 0 | 6.1727 | 18.9065 | 0.32649 | 6.1727 | 18.9065 | 0.32649 | 7.216 | 22.1019 | 0.32649 | 0.1147% | 0.2182 | 0.21794 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28422.8855 | 0 | 0 | 28422.8855 | 0.0002345%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 21 | 2 | 2448.8293 | 98.64% | 1.317% | 0.04316% | 11.3874 | 0 | 0 | 11.3874 | 0 | 9.885 | 18.9065 | 0.52284 | 9.885 | 18.9065 | 0.52284 | 11.5557 | 22.1019 | 0.52284 | 0.465% | 0.18614 | 0.18527 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13156.4968 | 0 | 0 | 13156.4968 | 0.0003755%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 56 | 1 | 5733.7907 | 98.41% | 1.505% | 0.0877% | 4.9876 | 0 | 0 | 4.9876 | 0 | 4.3295 | 9.4532 | 0.45799 | 4.3295 | 9.4532 | 0.45799 | 5.0613 | 11.0509 | 0.45799 | 0.08699% | 0.21349 | 0.2133 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26857.6481 | 0 | 0 | 26857.6481 | 0.0001645%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 93 | 4 | 10591.3769 | 98.31% | 1.605% | 0.08417% | 22.1684 | 0 | 0 | 22.1684 | 0 | 19.2436 | 37.8129 | 0.50892 | 19.2436 | 37.8129 | 0.50892 | 22.496 | 44.2037 | 0.50892 | 0.2093% | 0.23776 | 0.23725 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44548.2602 | 0 | 0 | 44548.2602 | 0.000731%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 84 | 1 | 9288.0329 | 98.43% | 1.494% | 0.07761% | 5.3873 | 0 | 0 | 5.3873 | 0 | 4.6765 | 9.4532 | 0.4947 | 4.6765 | 9.4532 | 0.4947 | 5.4669 | 11.0509 | 0.4947 | 0.058% | 0.22716 | 0.22702 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40888.3639 | 0 | 0 | 40888.3639 | 0.0001777%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 60 | 2 | 14526.7268 | 98.56% | 1.412% | 0.03052% | 23.6232 | 0 | 0 | 23.6232 | 0 | 20.5065 | 18.9065 | 1.0846 | 20.5065 | 18.9065 | 1.0846 | 23.9723 | 22.1019 | 1.0846 | 0.1626% | 0.34567 | 0.3451 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42025.284 | 0 | 0 | 42025.284 | 0.000779%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 13 | 1 | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 27.2905 | 0 | 0 | 27.2905 | 0 | 23.6899 | 9.4532 | 2.506 | 23.6899 | 9.4532 | 2.506 | 27.6938 | 11.0509 | 2.506 | 0.3789% | 0.33808 | 0.33679 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21304.1328 | 0 | 0 | 21304.1328 | 0.0008999%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 34 | 1 | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 17.806 | 0 | 0 | 17.806 | 0 | 15.4568 | 9.4532 | 1.6351 | 15.4568 | 9.4532 | 1.6351 | 18.0691 | 11.0509 | 1.6351 | 0.1445% | 0.46655 | 0.46587 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26409.0779 | 0 | 0 | 26409.0779 | 0.0005872%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 77 | 3 | 1606.9068 | 70.93% | 28.63% | 0.4437% | 2.198 | 0 | 0 | 2.198 | 0 | 1.908 | 28.3597 | 0.06728 | 1.908 | 28.3597 | 0.06728 | 2.2305 | 33.1528 | 0.06728 | 0.1368% | 0.43999 | 0.43914 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3654.2057 | 0 | 0 | 3654.2057 | 7.248e-05%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 59 | 2 | 18448.5828 | 98.9% | 1.079% | 0.02427% | 30.6147 | 0 | 0 | 30.6147 | 0 | 26.5756 | 18.9065 | 1.4056 | 26.5756 | 18.9065 | 1.4056 | 31.0671 | 22.1019 | 1.4056 | 0.1659% | 0.3939 | 0.39324 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46836.2841 | 0 | 0 | 46836.2841 | 0.00101%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 50 | 1 | 5536.6205 | 96.31% | 3.618% | 0.06787% | 5.2792 | 0 | 0 | 5.2792 | 0 | 4.5827 | 9.4532 | 0.48478 | 4.5827 | 9.4532 | 0.48478 | 5.3572 | 11.0509 | 0.48478 | 0.09535% | 0.37772 | 0.37734 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14658.7004 | 0 | 0 | 14658.7004 | 0.0001741%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 107 | 4 | 18780.9285 | 97.14% | 2.812% | 0.0448% | 33.7608 | 0 | 0 | 33.7608 | 0 | 29.3066 | 37.8129 | 0.77504 | 29.3066 | 37.8129 | 0.77504 | 34.2597 | 44.2037 | 0.77504 | 0.1798% | 0.38023 | 0.37953 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49396.2415 | 0 | 0 | 49396.2415 | 0.001113%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 56 | 1 | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 17.5236 | 0 | 0 | 17.5236 | 0 | 15.2116 | 9.4532 | 1.6091 | 15.2116 | 9.4532 | 1.6091 | 17.7826 | 11.0509 | 1.6091 | 0.08771% | 0.44563 | 0.44524 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44831.9691 | 0 | 0 | 44831.9691 | 0.0005779%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 20 | 1 | 418.5676 | 87.71% | 11.66% | 0.6303% | 0.90859 | 0 | 0 | 0.90859 | 0 | 0.78872 | 9.4532 | 0.083434 | 0.78872 | 9.4532 | 0.083434 | 0.92202 | 11.0509 | 0.083434 | 0.2171% | 0.28262 | 0.28192 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1481.4937 | 0 | 0 | 1481.4937 | 2.996e-05%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 177 | 1 | 5507.0239 | 92.46% | 7.234% | 0.3043% | 1.424 | 0 | 0 | 1.424 | 0 | 1.2361 | 9.4532 | 0.13076 | 1.2361 | 9.4532 | 0.13076 | 1.445 | 11.0509 | 0.13076 | 0.02586% | 0.3705 | 0.37039 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14864.2362 | 0 | 0 | 14864.2362 | 4.696e-05%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 20 | 1 | 3876.1334 | 98.99% | 0.834% | 0.1804% | 9.4961 | 0 | 0 | 9.4961 | 0 | 8.2432 | 9.4532 | 0.872 | 8.2432 | 9.4532 | 0.872 | 9.6364 | 11.0509 | 0.872 | 0.245% | 0.32777 | 0.32695 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11826.207 | 0 | 0 | 11826.207 | 0.0003131%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 80 | 1 | 3160.5079 | 95.27% | 4.501% | 0.231% | 1.863 | 0 | 0 | 1.863 | 0 | 1.6172 | 9.4532 | 0.17108 | 1.6172 | 9.4532 | 0.17108 | 1.8906 | 11.0509 | 0.17108 | 0.05895% | 0.32167 | 0.32147 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9825.5932 | 0 | 0 | 9825.5932 | 6.144e-05%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 151 | 1 | 2061.1876 | 81.54% | 17.79% | 0.6678% | 0.55096 | 0 | 0 | 0.55096 | 0 | 0.47827 | 9.4532 | 0.050593 | 0.47827 | 9.4532 | 0.050593 | 0.5591 | 11.0509 | 0.050593 | 0.02673% | 0.36686 | 0.36674 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5618.7923 | 0 | 0 | 5618.7923 | 1.817e-05%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 53 | 2 | 1867.403 | 95.01% | 4.712% | 0.2778% | 3.3141 | 0 | 0 | 3.3141 | 0 | 2.8769 | 18.9065 | 0.15216 | 2.8769 | 18.9065 | 0.15216 | 3.3631 | 22.1019 | 0.15216 | 0.1775% | 0.32295 | 0.32235 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5782.8541 | 0 | 0 | 5782.8541 | 0.0001093%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 205 | 8 | 18749.5963 | 97% | 2.901% | 0.09453% | 35.134 | 0 | 0 | 35.134 | 0 | 30.4986 | 75.6258 | 0.40328 | 30.4986 | 75.6258 | 0.40328 | 35.6532 | 88.4075 | 0.40328 | 0.1874% | 0.38414 | 0.38339 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48812.7179 | 0 | 0 | 48812.7179 | 0.001159%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 19 | 1 | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 10.4024 | 0 | 0 | 10.4024 | 0 | 9.03 | 9.4532 | 0.95523 | 9.03 | 9.4532 | 0.95523 | 10.5561 | 11.0509 | 0.95523 | 0.2582% | 0.19114 | 0.19064 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21079.1745 | 0 | 0 | 21079.1745 | 0.000343%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 63 | 1 | 4385.4004 | 97.52% | 2.308% | 0.1684% | 3.3603 | 0 | 0 | 3.3603 | 0 | 2.917 | 9.4532 | 0.30857 | 2.917 | 9.4532 | 0.30857 | 3.41 | 11.0509 | 0.30857 | 0.07663% | 0.20232 | 0.20216 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21675.6449 | 0 | 0 | 21675.6449 | 0.0001108%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 113 | 1 | 5741.4949 | 96.86% | 2.992% | 0.1472% | 2.4361 | 0 | 0 | 2.4361 | 0 | 2.1147 | 9.4532 | 0.2237 | 2.1147 | 9.4532 | 0.2237 | 2.4721 | 11.0509 | 0.2237 | 0.04243% | 0.20491 | 0.20482 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28019.7052 | 0 | 0 | 28019.7052 | 8.033e-05%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 62 | 1 | 11523.3049 | 98.77% | 1.172% | 0.05875% | 9.0868 | 0 | 0 | 9.0868 | 0 | 7.8879 | 9.4532 | 0.83442 | 7.8879 | 9.4532 | 0.83442 | 9.2211 | 11.0509 | 0.83442 | 0.07886% | 0.22417 | 0.22399 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51405.0484 | 0 | 0 | 51405.0484 | 0.0002996%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 55 | 2 | 4184.7467 | 98.1% | 1.799% | 0.1047% | 7.3891 | 0 | 0 | 7.3891 | 0 | 6.4143 | 18.9065 | 0.33926 | 6.4143 | 18.9065 | 0.33926 | 7.4983 | 22.1019 | 0.33926 | 0.1766% | 0.20727 | 0.2069 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20190.4485 | 0 | 0 | 20190.4485 | 0.0002437%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 51 | 2 | 3401.0234 | 97.74% | 2.113% | 0.1474% | 6.4528 | 0 | 0 | 6.4528 | 0 | 5.6014 | 18.9065 | 0.29627 | 5.6014 | 18.9065 | 0.29627 | 6.5481 | 22.1019 | 0.29627 | 0.1897% | 0.20978 | 0.20937 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16213.2011 | 0 | 0 | 16213.2011 | 0.0002128%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 44 | 2 | 4934.1603 | 97.7% | 2.178% | 0.1196% | 10.8467 | 0 | 0 | 10.8467 | 0 | 9.4157 | 18.9065 | 0.49801 | 9.4157 | 18.9065 | 0.49801 | 11.007 | 22.1019 | 0.49801 | 0.2198% | 0.21542 | 0.21494 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22906.0256 | 0 | 0 | 22906.0256 | 0.0003577%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 115 | 3 | 13172.958 | 96.8% | 3.124% | 0.0728% | 16.4665 | 0 | 0 | 16.4665 | 0 | 14.294 | 28.3597 | 0.50403 | 14.294 | 28.3597 | 0.50403 | 16.7099 | 33.1528 | 0.50403 | 0.125% | 0.23242 | 0.23212 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56680.6065 | 0 | 0 | 56680.6065 | 0.000543%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 5 | 1 | 1635.841 | 89.24% | 10.7% | 0.05535% | 14.4529 | 0 | 0 | 14.4529 | 0 | 12.5461 | 9.4532 | 1.3272 | 12.5461 | 9.4532 | 1.3272 | 14.6665 | 11.0509 | 1.3272 | 0.8835% | 0.18529 | 0.18346 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8837.9156 | 0 | 0 | 8837.9156 | 0.0004766%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 17 | 1 | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 12.22 | 0 | 0 | 12.22 | 0 | 10.6077 | 9.4532 | 1.1221 | 10.6077 | 9.4532 | 1.1221 | 12.4006 | 11.0509 | 1.1221 | 0.2889% | 0.11307 | 0.11274 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37410.4236 | 0 | 0 | 37410.4236 | 0.000403%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 19 | 1 | 498.1496 | 90.1% | 9.186% | 0.7154% | 1.1693 | 0 | 0 | 1.1693 | 0 | 1.015 | 9.4532 | 0.10737 | 1.015 | 9.4532 | 0.10737 | 1.1866 | 11.0509 | 0.10737 | 0.2347% | 0.32588 | 0.32503 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1529.0392 | 0 | 0 | 1529.0392 | 3.856e-05%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 60 | 1 | 1037.8957 | 85.73% | 13.64% | 0.6245% | 0.73409 | 0 | 0 | 0.73409 | 0 | 0.63724 | 9.4532 | 0.06741 | 0.63724 | 9.4532 | 0.06741 | 0.74494 | 11.0509 | 0.06741 | 0.07073% | 0.34771 | 0.34742 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 2985.3356 | 0 | 0 | 2985.3356 | 2.421e-05%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 38 | 1 | 317.7725 | 50.82% | 48.53% | 0.6462% | 0.21038 | 0 | 0 | 0.21038 | 0 | 0.18263 | 9.4532 | 0.019319 | 0.18263 | 9.4532 | 0.019319 | 0.21349 | 11.0509 | 0.019319 | 0.06621% | 0.31397 | 0.31356 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1012.7634 | 0 | 0 | 1012.7634 | 6.938e-06%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 145 | 2 | 1809.5147 | 84.26% | 15.08% | 0.6521% | 1.0411 | 0 | 0 | 1.0411 | 0 | 0.90371 | 18.9065 | 0.047799 | 0.90371 | 18.9065 | 0.047799 | 1.0564 | 22.1019 | 0.047799 | 0.05753% | 0.39031 | 0.39004 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4636.6469 | 0 | 0 | 4636.6469 | 3.433e-05%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 66 | 2 | 1890.633 | 91.06% | 8.49% | 0.4466% | 2.5825 | 0 | 0 | 2.5825 | 0 | 2.2418 | 18.9065 | 0.11857 | 2.2418 | 18.9065 | 0.11857 | 2.6207 | 22.1019 | 0.11857 | 0.1366% | 0.3743 | 0.37374 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5051.7383 | 0 | 0 | 5051.7383 | 8.516e-05%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 79 | 3 | 1738.9252 | 95.43% | 4.096% | 0.4776% | 3.1192 | 0 | 0 | 3.1192 | 0 | 2.7077 | 28.3597 | 0.095477 | 2.7077 | 28.3597 | 0.095477 | 3.1653 | 33.1528 | 0.095477 | 0.1794% | 0.15054 | 0.15025 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11552.4908 | 0 | 0 | 11552.4908 | 0.0001029%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 70 | 1 | 1570.3762 | 94.97% | 4.642% | 0.3849% | 1.0547 | 0 | 0 | 1.0547 | 0 | 0.91551 | 9.4532 | 0.096846 | 0.91551 | 9.4532 | 0.096846 | 1.0702 | 11.0509 | 0.096846 | 0.06716% | 0.19221 | 0.19207 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8170.5674 | 0 | 0 | 8170.5674 | 3.478e-05%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 39 | 2 | 998.7912 | 96.62% | 2.787% | 0.5903% | 2.4498 | 0 | 0 | 2.4498 | 0 | 2.1265 | 18.9065 | 0.11248 | 2.1265 | 18.9065 | 0.11248 | 2.486 | 22.1019 | 0.11248 | 0.2453% | 0.13097 | 0.13064 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7626.7626 | 0 | 0 | 7626.7626 | 8.078e-05%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 6 | 1 | 261.4279 | 97.06% | 2.12% | 0.8249% | 2.0933 | 0 | 0 | 2.0933 | 0 | 1.8171 | 9.4532 | 0.19222 | 1.8171 | 9.4532 | 0.19222 | 2.1242 | 11.0509 | 0.19222 | 0.8007% | 0.11654 | 0.11558 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2243.7106 | 0 | 0 | 2243.7106 | 6.903e-05%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 68 | 1 | 1482.4618 | 97.27% | 2.316% | 0.4117% | 1.0497 | 0 | 0 | 1.0497 | 0 | 0.91122 | 9.4532 | 0.096392 | 0.91122 | 9.4532 | 0.096392 | 1.0652 | 11.0509 | 0.096392 | 0.07081% | 0.1427 | 0.1426 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10388.6481 | 0 | 0 | 10388.6481 | 3.462e-05%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 103 | 3 | 2758.5667 | 95.78% | 3.96% | 0.2633% | 3.8092 | 0 | 0 | 3.8092 | 0 | 3.3066 | 28.3597 | 0.1166 | 3.3066 | 28.3597 | 0.1166 | 3.8655 | 33.1528 | 0.1166 | 0.1381% | 0.19881 | 0.19852 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13876.1265 | 0 | 0 | 13876.1265 | 0.0001256%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 39 | 1 | 1038.8005 | 97.12% | 2.539% | 0.3416% | 1.2805 | 0 | 0 | 1.2805 | 0 | 1.1116 | 9.4532 | 0.11758 | 1.1116 | 9.4532 | 0.11758 | 1.2994 | 11.0509 | 0.11758 | 0.1233% | 0.12493 | 0.12477 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8315.3648 | 0 | 0 | 8315.3648 | 4.223e-05%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 17 | 1 | 2163.5248 | 98.72% | 1.034% | 0.2463% | 6.219 | 0 | 0 | 6.219 | 0 | 5.3985 | 9.4532 | 0.57108 | 5.3985 | 9.4532 | 0.57108 | 6.3109 | 11.0509 | 0.57108 | 0.2874% | 0.18767 | 0.18712 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11528.8268 | 0 | 0 | 11528.8268 | 0.0002051%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 45 | 1 | 1471.0622 | 97.82% | 1.883% | 0.2988% | 1.5829 | 0 | 0 | 1.5829 | 0 | 1.374 | 9.4532 | 0.14535 | 1.374 | 9.4532 | 0.14535 | 1.6063 | 11.0509 | 0.14535 | 0.1076% | 0.13116 | 0.13101 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11216.3781 | 0 | 0 | 11216.3781 | 5.22e-05%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 127 | 2 | 26281.1502 | 98.91% | 1.048% | 0.04591% | 20.2627 | 0 | 0 | 20.2627 | 0 | 17.5894 | 18.9065 | 0.93034 | 17.5894 | 18.9065 | 0.93034 | 20.5622 | 22.1019 | 0.93034 | 0.0771% | 0.26918 | 0.26897 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97636.4684 | 0 | 0 | 97636.4684 | 0.0006682%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 75 | 4 | 6666.9216 | 99.41% | 0.4702% | 0.123% | 17.4963 | 0 | 0 | 17.4963 | 0 | 15.1879 | 37.8129 | 0.40166 | 15.1879 | 37.8129 | 0.40166 | 17.7548 | 44.2037 | 0.40166 | 0.2624% | 0.090777 | 0.090537 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73444.0029 | 0 | 0 | 73444.0029 | 0.000577%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 30 | 3 | 484.0355 | 97.4% | 1.48% | 1.12% | 2.3337 | 0 | 0 | 2.3337 | 0 | 2.0258 | 28.3597 | 0.071432 | 2.0258 | 28.3597 | 0.071432 | 2.3682 | 33.1528 | 0.071432 | 0.4821% | 0.071957 | 0.0716 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6727.6401 | 0 | 0 | 6727.6401 | 7.696e-05%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 9 | 1 | 513.3291 | 98.71% | 0.8845% | 0.4005% | 2.787 | 0 | 0 | 2.787 | 0 | 2.4193 | 9.4532 | 0.25593 | 2.4193 | 9.4532 | 0.25593 | 2.8282 | 11.0509 | 0.25593 | 0.5429% | 0.053744 | 0.053448 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9552.1251 | 0 | 0 | 9552.1251 | 9.191e-05%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 32 | 1 | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 3.385 | 0 | 0 | 3.385 | 0 | 2.9384 | 9.4532 | 0.31084 | 2.9384 | 9.4532 | 0.31084 | 3.4351 | 11.0509 | 0.31084 | 0.1533% | 0.070413 | 0.070304 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31362.7362 | 0 | 0 | 31362.7362 | 0.0001116%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 50 | 1 | 1721.769 | 85.69% | 14.07% | 0.2459% | 1.4606 | 0 | 0 | 1.4606 | 0 | 1.2679 | 9.4532 | 0.13412 | 1.2679 | 9.4532 | 0.13412 | 1.4822 | 11.0509 | 0.13412 | 0.08483% | 0.43289 | 0.43246 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 3977.9666 | 0 | 0 | 3977.9666 | 4.816e-05%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 73 | 1 | 22354.3085 | 99.24% | 0.73% | 0.02701% | 15.0433 | 0 | 0 | 15.0433 | 0 | 13.0586 | 9.4532 | 1.3814 | 13.0586 | 9.4532 | 1.3814 | 15.2656 | 11.0509 | 1.3814 | 0.06729% | 0.23844 | 0.23827 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93754.3968 | 0 | 0 | 93754.3968 | 0.0004961%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 72 | 1 | 12702.4119 | 98.21% | 1.737% | 0.04837% | 8.577 | 0 | 0 | 8.577 | 0 | 7.4454 | 9.4532 | 0.7876 | 7.4454 | 9.4532 | 0.7876 | 8.7037 | 11.0509 | 0.7876 | 0.06752% | 0.20291 | 0.20277 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62601.7342 | 0 | 0 | 62601.7342 | 0.0002828%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 58 | 1 | 19489.7064 | 99% | 0.9737% | 0.02962% | 16.4666 | 0 | 0 | 16.4666 | 0 | 14.2941 | 9.4532 | 1.5121 | 14.2941 | 9.4532 | 1.5121 | 16.7099 | 11.0509 | 1.5121 | 0.08449% | 0.1982 | 0.19804 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98332.0942 | 0 | 0 | 98332.0942 | 0.000543%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 67 | 2 | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 20.5785 | 0 | 0 | 20.5785 | 0 | 17.8635 | 18.9065 | 0.94484 | 17.8635 | 18.9065 | 0.94484 | 20.8826 | 22.1019 | 0.94484 | 0.1466% | 0.15704 | 0.15681 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89410.8602 | 0 | 0 | 89410.8602 | 0.0006786%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 126 | 2 | 2013.5966 | 89.22% | 10.31% | 0.4697% | 1.4116 | 0 | 0 | 1.4116 | 0 | 1.2254 | 18.9065 | 0.064813 | 1.2254 | 18.9065 | 0.064813 | 1.4325 | 22.1019 | 0.064813 | 0.07011% | 0.19664 | 0.19648 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10240.9973 | 0 | 0 | 10240.9973 | 4.655e-05%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 84 | 1 | 2727.5845 | 87.85% | 11.78% | 0.3693% | 1.412 | 0 | 0 | 1.412 | 0 | 1.2257 | 9.4532 | 0.12966 | 1.2257 | 9.4532 | 0.12966 | 1.4329 | 11.0509 | 0.12966 | 0.05177% | 0.20236 | 0.20224 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13479.8908 | 0 | 0 | 13479.8908 | 4.656e-05%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 71 | 2 | 10686.9326 | 98.68% | 1.222% | 0.09479% | 14.7053 | 0 | 0 | 14.7053 | 0 | 12.7652 | 18.9065 | 0.67517 | 12.7652 | 18.9065 | 0.67517 | 14.9226 | 22.1019 | 0.67517 | 0.1376% | 0.28412 | 0.28373 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37614.4718 | 0 | 0 | 37614.4718 | 0.0004849%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 68 | 3 | 3657.1834 | 94.66% | 5.124% | 0.2164% | 7.5601 | 0 | 0 | 7.5601 | 0 | 6.5626 | 28.3597 | 0.23141 | 6.5626 | 28.3597 | 0.23141 | 7.6718 | 33.1528 | 0.23141 | 0.2067% | 0.14269 | 0.14238 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25633.0155 | 0 | 0 | 25633.0155 | 0.0002493%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 70 | 3 | 1438.6594 | 90.88% | 8.66% | 0.4639% | 2.7736 | 0 | 0 | 2.7736 | 0 | 2.4076 | 28.3597 | 0.084896 | 2.4076 | 28.3597 | 0.084896 | 2.8145 | 33.1528 | 0.084896 | 0.1928% | 0.18227 | 0.18188 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7894.5087 | 0 | 0 | 7894.5087 | 9.146e-05%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 48 | 1 | 10116.9629 | 99.05% | 0.91% | 0.0405% | 10.334 | 0 | 0 | 10.334 | 0 | 8.9705 | 9.4532 | 0.94894 | 8.9705 | 9.4532 | 0.94894 | 10.4867 | 11.0509 | 0.94894 | 0.1021% | 0.2438 | 0.24354 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41498.2009 | 0 | 0 | 41498.2009 | 0.0003408%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 29 | 3 | 2198.6799 | 96.34% | 3.473% | 0.1901% | 10.8463 | 0 | 0 | 10.8463 | 0 | 9.4153 | 28.3597 | 0.332 | 9.4153 | 28.3597 | 0.332 | 11.0066 | 33.1528 | 0.332 | 0.4933% | 0.37523 | 0.37331 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5860.6198 | 0 | 0 | 5860.6198 | 0.0003577%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 81 | 1 | 1925.8876 | 84.29% | 15.28% | 0.4298% | 0.99205 | 0 | 0 | 0.99205 | 0 | 0.86116 | 9.4532 | 0.091097 | 0.86116 | 9.4532 | 0.091097 | 1.0067 | 11.0509 | 0.091097 | 0.05151% | 0.44397 | 0.4437 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4338.2633 | 0 | 0 | 4338.2633 | 3.271e-05%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 155 | 7 | 3585.6314 | 89.37% | 10.06% | 0.5685% | 7.1635 | 0 | 0 | 7.1635 | 0 | 6.2184 | 66.1726 | 0.093973 | 6.2184 | 66.1726 | 0.093973 | 7.2694 | 77.3565 | 0.093973 | 0.1998% | 0.50177 | 0.50065 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7147.6994 | 0 | 0 | 7147.6994 | 0.0002362%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 17 | 1 | 3690.9623 | 99.91% | 0% | 0.09183% | 10.7373 | 0 | 0 | 10.7373 | 0 | 9.3207 | 9.4532 | 0.98598 | 9.3207 | 9.4532 | 0.98598 | 10.896 | 11.0509 | 0.98598 | 0.2909% | 0.035843 | 0.035739 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102975.5205 | 0 | 0 | 102975.5205 | 0.0003541%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 77 | 1 | 3270.2376 | 92.16% | 7.656% | 0.1816% | 1.9375 | 0 | 0 | 1.9375 | 0 | 1.6819 | 9.4532 | 0.17792 | 1.6819 | 9.4532 | 0.17792 | 1.9662 | 11.0509 | 0.17792 | 0.05925% | 0.19945 | 0.19932 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16397.318 | 0 | 0 | 16397.318 | 6.389e-05%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 93 | 3 | 2735.9283 | 96.11% | 3.605% | 0.2871% | 4.1986 | 0 | 0 | 4.1986 | 0 | 3.6447 | 28.3597 | 0.12852 | 3.6447 | 28.3597 | 0.12852 | 4.2607 | 33.1528 | 0.12852 | 0.1535% | 0.2115 | 0.21116 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12936.5875 | 0 | 0 | 12936.5875 | 0.0001385%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 72 | 1 | 3934.7733 | 97.03% | 2.838% | 0.1358% | 2.6247 | 0 | 0 | 2.6247 | 0 | 2.2784 | 9.4532 | 0.24102 | 2.2784 | 9.4532 | 0.24102 | 2.6635 | 11.0509 | 0.24102 | 0.06671% | 0.19925 | 0.19912 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19748.0279 | 0 | 0 | 19748.0279 | 8.655e-05%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 4 | 1 | 2055.424 | 99.51% | 0.3331% | 0.1572% | 25.3112 | 0 | 0 | 25.3112 | 0 | 21.9717 | 9.4532 | 2.3243 | 21.9717 | 9.4532 | 2.3243 | 25.6852 | 11.0509 | 2.3243 | 1.231% | 0.22072 | 0.21799 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9312.9148 | 0 | 0 | 9312.9148 | 0.0008347%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 31 | 4 | 2324.2215 | 96.86% | 3.03% | 0.1069% | 14.3793 | 0 | 0 | 14.3793 | 0 | 12.4822 | 37.8129 | 0.3301 | 12.4822 | 37.8129 | 0.3301 | 14.5918 | 44.2037 | 0.3301 | 0.6187% | 0.18396 | 0.18279 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12636.6169 | 0 | 0 | 12636.6169 | 0.0004742%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 137 | 3 | 7406.689 | 96.62% | 3.25% | 0.1263% | 7.7574 | 0 | 0 | 7.7574 | 0 | 6.7339 | 28.3597 | 0.23745 | 6.7339 | 28.3597 | 0.23745 | 7.872 | 33.1528 | 0.23745 | 0.1047% | 0.26901 | 0.26872 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27534.3089 | 0 | 0 | 27534.3089 | 0.0002558%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 212 | 4 | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 73.4115 | 0 | 0 | 73.4115 | 0 | 63.7259 | 37.8129 | 1.6853 | 63.7259 | 37.8129 | 1.6853 | 74.4963 | 44.2037 | 1.6853 | 0.0927% | 0.41507 | 0.41468 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190798.8152 | 0 | 0 | 190798.8152 | 0.002421%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 13 | 1 | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 13.6808 | 0 | 0 | 13.6808 | 0 | 11.8758 | 9.4532 | 1.2563 | 11.8758 | 9.4532 | 1.2563 | 13.883 | 11.0509 | 1.2563 | 0.378% | 0.34461 | 0.3433 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10503.2418 | 0 | 0 | 10503.2418 | 0.0004511%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 81 | 3 | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 82.3889 | 0 | 0 | 82.3889 | 0 | 71.519 | 28.3597 | 2.5219 | 71.519 | 28.3597 | 2.5219 | 83.6065 | 33.1528 | 2.5219 | 0.1827% | 0.41211 | 0.41136 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109453.2338 | 0 | 0 | 109453.2338 | 0.002717%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 132 | 5 | 7426.9759 | 96.05% | 3.813% | 0.1383% | 13.3754 | 0 | 0 | 13.3754 | 0 | 11.6107 | 47.2661 | 0.24565 | 11.6107 | 47.2661 | 0.24565 | 13.573 | 55.2547 | 0.24565 | 0.1801% | 0.27927 | 0.27875 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26596.0893 | 0 | 0 | 26596.0893 | 0.0004411%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 1220 | 9 | 16772.3082 | 96.7% | 3.181% | 0.1236% | 5.9223 | 0 | 0 | 5.9223 | 0 | 5.1409 | 85.0791 | 0.060425 | 5.1409 | 85.0791 | 0.060425 | 6.0098 | 99.4584 | 0.060425 | 0.03531% | 0.35117 | 0.35104 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47761.8798 | 0 | 0 | 47761.8798 | 0.0001953%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 52 | 1 | 2000.4654 | 94.98% | 4.641% | 0.3747% | 1.8088 | 0 | 0 | 1.8088 | 0 | 1.5701 | 9.4532 | 0.16609 | 1.5701 | 9.4532 | 0.16609 | 1.8355 | 11.0509 | 0.16609 | 0.09042% | 0.093988 | 0.093899 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21285.2364 | 0 | 0 | 21285.2364 | 5.965e-05%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 84 | 1 | 6388.6939 | 98.26% | 1.615% | 0.1229% | 3.6994 | 0 | 0 | 3.6994 | 0 | 3.2113 | 9.4532 | 0.3397 | 3.2113 | 9.4532 | 0.3397 | 3.754 | 11.0509 | 0.3397 | 0.0579% | 0.095565 | 0.095508 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66852.7823 | 0 | 0 | 66852.7823 | 0.000122%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 52 | 1 | 3473.4554 | 97.68% | 2.135% | 0.1887% | 3.2296 | 0 | 0 | 3.2296 | 0 | 2.8035 | 9.4532 | 0.29657 | 2.8035 | 9.4532 | 0.29657 | 3.2774 | 11.0509 | 0.29657 | 0.09298% | 0.088414 | 0.08833 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39286.9519 | 0 | 0 | 39286.9519 | 0.0001065%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 24 | 1 | 2730.9177 | 98.3% | 1.373% | 0.325% | 5.5369 | 0 | 0 | 5.5369 | 0 | 4.8064 | 9.4532 | 0.50844 | 4.8064 | 9.4532 | 0.50844 | 5.6187 | 11.0509 | 0.50844 | 0.2027% | 0.054655 | 0.054542 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 49968.595 | 0 | 0 | 49968.595 | 0.0001826%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 151 | 3 | 5142.095 | 98.68% | 0.901% | 0.4182% | 4.9903 | 0 | 0 | 4.9903 | 0 | 4.3319 | 28.3597 | 0.15275 | 4.3319 | 28.3597 | 0.15275 | 5.064 | 33.1528 | 0.15275 | 0.09705% | 0.11648 | 0.11636 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44147.4433 | 0 | 0 | 44147.4433 | 0.0001646%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 50 | 1 | 2499.974 | 99.29% | 0.4807% | 0.2332% | 2.4573 | 0 | 0 | 2.4573 | 0 | 2.1331 | 9.4532 | 0.22565 | 2.1331 | 9.4532 | 0.22565 | 2.4936 | 11.0509 | 0.22565 | 0.09829% | 0.037573 | 0.037535 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66537.6281 | 0 | 0 | 66537.6281 | 8.103e-05%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 23 | 1 | 1642.5971 | 97.37% | 2.323% | 0.3027% | 3.4423 | 0 | 0 | 3.4423 | 0 | 2.9882 | 9.4532 | 0.3161 | 2.9882 | 9.4532 | 0.3161 | 3.4932 | 11.0509 | 0.3161 | 0.2096% | 0.029023 | 0.028961 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56598.8165 | 0 | 0 | 56598.8165 | 0.0001135%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 57 | 6 | 3035.8045 | 98.84% | 0.8219% | 0.339% | 15.6345 | 0 | 0 | 15.6345 | 0 | 13.5718 | 56.7194 | 0.23928 | 13.5718 | 56.7194 | 0.23928 | 15.8656 | 66.3056 | 0.23928 | 0.515% | 0.06125 | 0.060931 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49566.8454 | 0 | 0 | 49566.8454 | 0.0005156%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 32 | 1 | 447.7794 | 94.96% | 4.349% | 0.694% | 0.65773 | 0 | 0 | 0.65773 | 0 | 0.57095 | 9.4532 | 0.060398 | 0.57095 | 9.4532 | 0.060398 | 0.66745 | 11.0509 | 0.060398 | 0.1469% | 0.02204 | 0.022006 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20318.4394 | 0 | 0 | 20318.4394 | 2.169e-05%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 79 | 2 | 2341.6741 | 85.9% | 13.6% | 0.4998% | 2.5208 | 0 | 0 | 2.5208 | 0 | 2.1882 | 18.9065 | 0.11574 | 2.1882 | 18.9065 | 0.11574 | 2.5581 | 22.1019 | 0.11574 | 0.1076% | 0.1204 | 0.12025 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19453.1746 | 0 | 0 | 19453.1746 | 8.313e-05%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 102 | 3 | 4127.6955 | 98.74% | 0.928% | 0.3343% | 5.9336 | 0 | 0 | 5.9336 | 0 | 5.1507 | 28.3597 | 0.18162 | 5.1507 | 28.3597 | 0.18162 | 6.0213 | 33.1528 | 0.18162 | 0.1438% | 0.075451 | 0.075341 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54707.8311 | 0 | 0 | 54707.8311 | 0.0001957%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 40 | 3 | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 18.2378 | 0 | 0 | 18.2378 | 0 | 15.8316 | 28.3597 | 0.55824 | 15.8316 | 28.3597 | 0.55824 | 18.5073 | 33.1528 | 0.55824 | 0.3692% | 0.047931 | 0.047753 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103053.0981 | 0 | 0 | 103053.0981 | 0.0006014%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 14 | 1 | 4375.0381 | 88.63% | 11.27% | 0.1058% | 13.7096 | 0 | 0 | 13.7096 | 0 | 11.9008 | 9.4532 | 1.2589 | 11.9008 | 9.4532 | 1.2589 | 13.9122 | 11.0509 | 1.2589 | 0.3134% | 0.1179 | 0.11748 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37123.0171 | 0 | 0 | 37123.0171 | 0.0004521%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 48 | 1 | 23678.6611 | 98.37% | 1.593% | 0.04039% | 24.0197 | 0 | 0 | 24.0197 | 0 | 20.8506 | 9.4532 | 2.2057 | 20.8506 | 9.4532 | 2.2057 | 24.3746 | 11.0509 | 2.2057 | 0.1014% | 0.15496 | 0.1548 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152802.8333 | 0 | 0 | 152802.8333 | 0.0007921%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 48 | 2 | 9719.0421 | 98.73% | 1.209% | 0.05836% | 19.7915 | 0 | 0 | 19.7915 | 0 | 17.1803 | 18.9065 | 0.9087 | 17.1803 | 18.9065 | 0.9087 | 20.084 | 22.1019 | 0.9087 | 0.2036% | 0.12847 | 0.12821 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75653.1527 | 0 | 0 | 75653.1527 | 0.0006526%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 37 | 1 | 2823.5781 | 97.26% | 2.617% | 0.1213% | 3.6741 | 0 | 0 | 3.6741 | 0 | 3.1893 | 9.4532 | 0.33738 | 3.1893 | 9.4532 | 0.33738 | 3.7284 | 11.0509 | 0.33738 | 0.1301% | 0.17766 | 0.17742 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15894.1147 | 0 | 0 | 15894.1147 | 0.0001212%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 25 | 1 | 2260.6624 | 98.61% | 1.288% | 0.1052% | 4.4138 | 0 | 0 | 4.4138 | 0 | 3.8314 | 9.4532 | 0.4053 | 3.8314 | 9.4532 | 0.4053 | 4.479 | 11.0509 | 0.4053 | 0.1952% | 0.17215 | 0.17181 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13132.0828 | 0 | 0 | 13132.0828 | 0.0001455%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 51 | 4 | 5332.0037 | 98.07% | 1.841% | 0.0848% | 20.3021 | 0 | 0 | 20.3021 | 0 | 17.6236 | 37.8129 | 0.46607 | 17.6236 | 37.8129 | 0.46607 | 20.6021 | 44.2037 | 0.46607 | 0.3808% | 0.18129 | 0.18059 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29413.7975 | 0 | 0 | 29413.7975 | 0.0006695%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 124 | 3 | 21222.9131 | 98.36% | 1.585% | 0.05121% | 25.0003 | 0 | 0 | 25.0003 | 0 | 21.7019 | 28.3597 | 0.76524 | 21.7019 | 28.3597 | 0.76524 | 25.3698 | 33.1528 | 0.76524 | 0.1178% | 0.21435 | 0.21409 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99014.7176 | 0 | 0 | 99014.7176 | 0.0008244%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 56 | 2 | 6927.8558 | 97.84% | 2.089% | 0.06679% | 11.9835 | 0 | 0 | 11.9835 | 0 | 10.4024 | 18.9065 | 0.5502 | 10.4024 | 18.9065 | 0.5502 | 12.1605 | 22.1019 | 0.5502 | 0.173% | 0.18488 | 0.18455 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37474.5384 | 0 | 0 | 37474.5384 | 0.0003952%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 32 | 1 | 12711.1878 | 97.62% | 2.333% | 0.04724% | 19.1946 | 0 | 0 | 19.1946 | 0 | 16.6621 | 9.4532 | 1.7626 | 16.6621 | 9.4532 | 1.7626 | 19.4782 | 11.0509 | 1.7626 | 0.151% | 0.1419 | 0.14168 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89583.9404 | 0 | 0 | 89583.9404 | 0.000633%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 62 | 1 | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 22.406 | 0 | 0 | 22.406 | 0 | 19.4498 | 9.4532 | 2.0575 | 19.4498 | 9.4532 | 2.0575 | 22.7371 | 11.0509 | 2.0575 | 0.07932% | 0.25909 | 0.25888 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109035.2605 | 0 | 0 | 109035.2605 | 0.0007389%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 165 | 2 | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 18.3718 | 0 | 0 | 18.3718 | 0 | 15.948 | 18.9065 | 0.84352 | 15.948 | 18.9065 | 0.84352 | 18.6433 | 22.1019 | 0.84352 | 0.05947% | 0.18156 | 0.18145 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170162.2742 | 0 | 0 | 170162.2742 | 0.0006058%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 182 | 8 | 65515.492 | 98.93% | 1.038% | 0.03019% | 141.0275 | 0 | 0 | 141.0275 | 0 | 122.421 | 75.6258 | 1.6188 | 122.421 | 75.6258 | 1.6188 | 143.1116 | 88.4075 | 1.6188 | 0.2153% | 0.49249 | 0.49141 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133033.476 | 0 | 0 | 133033.476 | 0.004651%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 23 | 1 | 1116.4705 | 96.46% | 3.23% | 0.3121% | 2.3177 | 0 | 0 | 2.3177 | 0 | 2.0119 | 9.4532 | 0.21283 | 2.0119 | 9.4532 | 0.21283 | 2.352 | 11.0509 | 0.21283 | 0.2076% | 0.1294 | 0.12913 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8628.4088 | 0 | 0 | 8628.4088 | 7.643e-05%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 72 | 2 | 6268.6569 | 98.24% | 1.63% | 0.1302% | 8.4677 | 0 | 0 | 8.4677 | 0 | 7.3505 | 18.9065 | 0.38878 | 7.3505 | 18.9065 | 0.38878 | 8.5928 | 22.1019 | 0.38878 | 0.1351% | 0.15408 | 0.15386 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40686.5249 | 0 | 0 | 40686.5249 | 0.0002792%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 18 | 2 | 376.4251 | 98.76% | 0.8388% | 0.4045% | 2.0446 | 0 | 0 | 2.0446 | 0 | 1.7748 | 18.9065 | 0.093875 | 1.7748 | 18.9065 | 0.093875 | 2.0748 | 22.1019 | 0.093875 | 0.5432% | 0.064786 | 0.064429 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5810.7028 | 0 | 0 | 5810.7028 | 6.742e-05%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 73 | 2 | 4437.6588 | 97.91% | 1.769% | 0.321% | 5.8924 | 0 | 0 | 5.8924 | 0 | 5.115 | 18.9065 | 0.27054 | 5.115 | 18.9065 | 0.27054 | 5.9795 | 22.1019 | 0.27054 | 0.1328% | 0.095775 | 0.095646 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46335.3294 | 0 | 0 | 46335.3294 | 0.0001943%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 104 | 4 | 3665.7351 | 96.82% | 2.929% | 0.2538% | 6.7569 | 0 | 0 | 6.7569 | 0 | 5.8654 | 37.8129 | 0.15512 | 5.8654 | 37.8129 | 0.15512 | 6.8567 | 44.2037 | 0.15512 | 0.1843% | 0.12278 | 0.12254 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29858.7164 | 0 | 0 | 29858.7164 | 0.0002228%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 71 | 2 | 3387.0058 | 94.54% | 5.197% | 0.2577% | 4.4651 | 0 | 0 | 4.4651 | 0 | 3.876 | 18.9065 | 0.20501 | 3.876 | 18.9065 | 0.20501 | 4.5311 | 22.1019 | 0.20501 | 0.1318% | 0.070488 | 0.07039 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48054.4744 | 0 | 0 | 48054.4744 | 0.0001472%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 24 | 2 | 1438.4419 | 90% | 9.47% | 0.5268% | 5.3404 | 0 | 0 | 5.3404 | 0 | 4.6358 | 18.9065 | 0.2452 | 4.6358 | 18.9065 | 0.2452 | 5.4193 | 22.1019 | 0.2452 | 0.3713% | 0.066431 | 0.066157 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21662.0076 | 0 | 0 | 21662.0076 | 0.0001761%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 33 | 3 | 1360.3328 | 92.51% | 7.186% | 0.3009% | 5.6632 | 0 | 0 | 5.6632 | 0 | 4.916 | 28.3597 | 0.17335 | 4.916 | 28.3597 | 0.17335 | 5.7469 | 33.1528 | 0.17335 | 0.4163% | 0.045228 | 0.045025 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30087.1402 | 0 | 0 | 30087.1402 | 0.0001868%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 99 | 4 | 3753.23 | 95.85% | 3.876% | 0.273% | 7.195 | 0 | 0 | 7.195 | 0 | 6.2457 | 37.8129 | 0.16517 | 6.2457 | 37.8129 | 0.16517 | 7.3014 | 44.2037 | 0.16517 | 0.1917% | 0.10094 | 0.10073 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37187.0526 | 0 | 0 | 37187.0526 | 0.0002373%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 40 | 3 | 2013.5901 | 87.8% | 12.03% | 0.1689% | 6.5635 | 0 | 0 | 6.5635 | 0 | 5.6976 | 28.3597 | 0.2009 | 5.6976 | 28.3597 | 0.2009 | 6.6605 | 33.1528 | 0.2009 | 0.326% | 0.19011 | 0.18941 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10596.2691 | 0 | 0 | 10596.2691 | 0.0002164%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 26 | 1 | 4762.848 | 95.55% | 4.384% | 0.07015% | 8.6638 | 0 | 0 | 8.6638 | 0 | 7.5208 | 9.4532 | 0.79558 | 7.5208 | 9.4532 | 0.79558 | 8.7919 | 11.0509 | 0.79558 | 0.1819% | 0.11001 | 0.1098 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43299.6207 | 0 | 0 | 43299.6207 | 0.0002857%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 138 | 1 | 3602.0119 | 95.48% | 4.084% | 0.4314% | 1.2337 | 0 | 0 | 1.2337 | 0 | 1.0709 | 9.4532 | 0.11329 | 1.0709 | 9.4532 | 0.11329 | 1.2519 | 11.0509 | 0.11329 | 0.03425% | 0.15121 | 0.15116 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23821.6403 | 0 | 0 | 23821.6403 | 4.068e-05%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 245 | 6 | 13871.6222 | 98.14% | 1.698% | 0.1643% | 16.5026 | 0 | 0 | 16.5026 | 0 | 14.3253 | 56.7194 | 0.25256 | 14.3253 | 56.7194 | 0.25256 | 16.7465 | 66.3056 | 0.25256 | 0.119% | 0.18928 | 0.18905 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73289.2277 | 0 | 0 | 73289.2277 | 0.0005442%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 229 | 6 | 5570.6857 | 96.99% | 2.589% | 0.4237% | 7.0072 | 0 | 0 | 7.0072 | 0 | 6.0827 | 56.7194 | 0.10724 | 6.0827 | 56.7194 | 0.10724 | 7.1108 | 66.3056 | 0.10724 | 0.1258% | 0.19915 | 0.19889 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 27973.8265 | 0 | 0 | 27973.8265 | 0.0002311%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 92 | 3 | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 21.6697 | 0 | 0 | 21.6697 | 0 | 18.8107 | 28.3597 | 0.66329 | 18.8107 | 28.3597 | 0.66329 | 21.9899 | 33.1528 | 0.66329 | 0.1603% | 0.1241 | 0.1239 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108956.7402 | 0 | 0 | 108956.7402 | 0.0007146%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 58 | 1 | 23517.4275 | 99.25% | 0.716% | 0.03401% | 19.9204 | 0 | 0 | 19.9204 | 0 | 17.2922 | 9.4532 | 1.8292 | 17.2922 | 9.4532 | 1.8292 | 20.2148 | 11.0509 | 1.8292 | 0.0847% | 0.14376 | 0.14364 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163590.7571 | 0 | 0 | 163590.7571 | 0.0006569%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 76 | 2 | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 24.0924 | 0 | 0 | 24.0924 | 0 | 20.9137 | 18.9065 | 1.1062 | 20.9137 | 18.9065 | 1.1062 | 24.4484 | 22.1019 | 1.1062 | 0.1294% | 0.11814 | 0.11798 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157568.0881 | 0 | 0 | 157568.0881 | 0.0007945%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 7 | 1 | 1991.3582 | 88.69% | 11.27% | 0.03442% | 12.4897 | 0 | 0 | 12.4897 | 0 | 10.8419 | 9.4532 | 1.1469 | 10.8419 | 9.4532 | 1.1469 | 12.6743 | 11.0509 | 1.1469 | 0.6272% | 0.10085 | 0.10014 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19761.1324 | 0 | 0 | 19761.1324 | 0.0004119%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 42 | 2 | 13534.4067 | 99.43% | 0.528% | 0.03951% | 31.7215 | 0 | 0 | 31.7215 | 0 | 27.5363 | 18.9065 | 1.4565 | 27.5363 | 18.9065 | 1.4565 | 32.1903 | 22.1019 | 1.4565 | 0.2344% | 0.12577 | 0.12547 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107612.9483 | 0 | 0 | 107612.9483 | 0.001046%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 121 | 4 | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 33.2826 | 0 | 0 | 33.2826 | 0 | 28.8914 | 37.8129 | 0.76406 | 28.8914 | 37.8129 | 0.76406 | 33.7744 | 44.2037 | 0.76406 | 0.1623% | 0.13939 | 0.13916 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147145.8289 | 0 | 0 | 147145.8289 | 0.001098%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 15 | 1 | 3653.654 | 88.54% | 11.39% | 0.07412% | 10.6748 | 0 | 0 | 10.6748 | 0 | 9.2664 | 9.4532 | 0.98024 | 9.2664 | 9.4532 | 0.98024 | 10.8326 | 11.0509 | 0.98024 | 0.2922% | 0.080555 | 0.080289 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45373.4586 | 0 | 0 | 45373.4586 | 0.000352%
2028 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 1 | 1 | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.51583 | 9.4532 | 0.054566 | 0.51583 | 9.4532 | 0.054566 | 0.60301 | 11.0509 | 0.054566 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 64 | 2 | 7500.5861 | 98.5% | 1.439% | 0.05987% | 11.4285 | 0 | 0 | 11.4285 | 0 | 9.9207 | 18.9065 | 0.52473 | 9.9207 | 18.9065 | 0.52473 | 11.5974 | 22.1019 | 0.52473 | 0.1524% | 0.092253 | 0.09211 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81306.2344 | 0 | 0 | 81306.2344 | 0.0003769%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 16 | 1 | 1698.7097 | 79.94% | 19.99% | 0.07228% | 4.2011 | 0 | 0 | 4.2011 | 0 | 3.6468 | 9.4532 | 0.38578 | 3.6468 | 9.4532 | 0.38578 | 4.2632 | 11.0509 | 0.38578 | 0.2473% | 0.074333 | 0.074103 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 22866.9262 | 0 | 0 | 22866.9262 | 0.0001385%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 83 | 6 | 11288.3525 | 98.84% | 1.109% | 0.05403% | 39.9234 | 0 | 0 | 39.9234 | 0 | 34.6561 | 56.7194 | 0.61101 | 34.6561 | 56.7194 | 0.61101 | 40.5134 | 66.3056 | 0.61101 | 0.3537% | 0.1048 | 0.10443 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107714.2925 | 0 | 0 | 107714.2925 | 0.001317%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 140 | 4 | 16012.7864 | 97.76% | 2.145% | 0.09187% | 22.14 | 0 | 0 | 22.14 | 0 | 19.219 | 37.8129 | 0.50826 | 19.219 | 37.8129 | 0.50826 | 22.4672 | 44.2037 | 0.50826 | 0.1383% | 0.16775 | 0.16752 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95456.887 | 0 | 0 | 95456.887 | 0.0007301%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 92 | 4 | 9294.6751 | 95.41% | 4.438% | 0.1505% | 19.0859 | 0 | 0 | 19.0859 | 0 | 16.5678 | 37.8129 | 0.43815 | 16.5678 | 37.8129 | 0.43815 | 19.368 | 44.2037 | 0.43815 | 0.2053% | 0.14106 | 0.14075 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 65898.9109 | 0 | 0 | 65898.9109 | 0.0006294%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 11 | 2 | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 45.7421 | 0 | 0 | 45.7421 | 0 | 39.7071 | 18.9065 | 2.1002 | 39.7071 | 18.9065 | 2.1002 | 46.4181 | 22.1019 | 2.1002 | 0.8971% | 0.2409 | 0.23874 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21165.5769 | 0 | 0 | 21165.5769 | 0.001508%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 3 | 1 | 878.9304 | 95.49% | 4.482% | 0.03213% | 13.8476 | 0 | 0 | 13.8476 | 0 | 12.0206 | 9.4532 | 1.2716 | 12.0206 | 9.4532 | 1.2716 | 14.0523 | 11.0509 | 1.2716 | 1.576% | 0.14128 | 0.13895 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6225.7479 | 0 | 0 | 6225.7479 | 0.0004566%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 84 | 2 | 16869.708 | 98.79% | 1.184% | 0.02933% | 19.6409 | 0 | 0 | 19.6409 | 0 | 17.0496 | 18.9065 | 0.90178 | 17.0496 | 18.9065 | 0.90178 | 19.9311 | 22.1019 | 0.90178 | 0.1164% | 0.18286 | 0.18265 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92254.5817 | 0 | 0 | 92254.5817 | 0.0006477%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 116 | 2 | 17696.7525 | 97.47% | 2.478% | 0.04808% | 14.7218 | 0 | 0 | 14.7218 | 0 | 12.7795 | 18.9065 | 0.67593 | 12.7795 | 18.9065 | 0.67593 | 14.9393 | 22.1019 | 0.67593 | 0.08319% | 0.18538 | 0.18522 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95464.2 | 0 | 0 | 95464.2 | 0.0004855%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 116 | 2 | 10432.4887 | 97.04% | 2.884% | 0.07824% | 8.6399 | 0 | 0 | 8.6399 | 0 | 7.5 | 18.9065 | 0.39669 | 7.5 | 18.9065 | 0.39669 | 8.7676 | 22.1019 | 0.39669 | 0.08282% | 0.14913 | 0.149 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 69958.9388 | 0 | 0 | 69958.9388 | 0.0002849%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 99 | 1 | 37602.1184 | 98.59% | 1.386% | 0.02088% | 18.5365 | 0 | 0 | 18.5365 | 0 | 16.0909 | 9.4532 | 1.7022 | 16.0909 | 9.4532 | 1.7022 | 18.8105 | 11.0509 | 1.7022 | 0.0493% | 0.54241 | 0.54214 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69324.0869 | 0 | 0 | 69324.0869 | 0.0006113%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 65 | 2 | 3136.9517 | 88.18% | 11.4% | 0.4202% | 4.2131 | 0 | 0 | 4.2131 | 0 | 3.6572 | 18.9065 | 0.19344 | 3.6572 | 18.9065 | 0.19344 | 4.2754 | 22.1019 | 0.19344 | 0.1343% | 0.15664 | 0.1564 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20030.4988 | 0 | 0 | 20030.4988 | 0.0001389%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 90 | 1 | 6370.0414 | 98.47% | 1.262% | 0.272% | 3.4498 | 0 | 0 | 3.4498 | 0 | 2.9946 | 9.4532 | 0.31678 | 2.9946 | 9.4532 | 0.31678 | 3.5008 | 11.0509 | 0.31678 | 0.05416% | 0.10309 | 0.10304 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61789.9137 | 0 | 0 | 61789.9137 | 0.0001138%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 15 | 1 | 3518.0204 | 97.45% | 2.468% | 0.07959% | 11.3137 | 0 | 0 | 11.3137 | 0 | 9.8211 | 9.4532 | 1.0389 | 9.8211 | 9.4532 | 1.0389 | 11.4809 | 11.0509 | 1.0389 | 0.3216% | 0.54783 | 0.54602 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6422.2743 | 0 | 0 | 6422.2743 | 0.0003731%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 6 | 1 | 582.1633 | 91.34% | 8.391% | 0.2732% | 4.3867 | 0 | 0 | 4.3867 | 0 | 3.8079 | 9.4532 | 0.40282 | 3.8079 | 9.4532 | 0.40282 | 4.4515 | 11.0509 | 0.40282 | 0.7535% | 0.53527 | 0.53085 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1088.3895 | 0 | 0 | 1088.3895 | 0.0001447%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 27 | 1 | 4750.1268 | 98% | 1.916% | 0.08125% | 8.5346 | 0 | 0 | 8.5346 | 0 | 7.4086 | 9.4532 | 0.78371 | 7.4086 | 9.4532 | 0.78371 | 8.6607 | 11.0509 | 0.78371 | 0.1797% | 0.55752 | 0.5565 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8520.3954 | 0 | 0 | 8520.3954 | 0.0002814%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 26 | 1 | 5348.8774 | 98.57% | 1.364% | 0.06326% | 10.0381 | 0 | 0 | 10.0381 | 0 | 8.7137 | 9.4532 | 0.92177 | 8.7137 | 9.4532 | 0.92177 | 10.1864 | 11.0509 | 0.92177 | 0.1877% | 0.55519 | 0.55414 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9634.5254 | 0 | 0 | 9634.5254 | 0.000331%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 31 | 1 | 852.9261 | 84.92% | 14.72% | 0.3553% | 1.1566 | 0 | 0 | 1.1566 | 0 | 1.004 | 9.4532 | 0.10621 | 1.004 | 9.4532 | 0.10621 | 1.1737 | 11.0509 | 0.10621 | 0.1356% | 0.36954 | 0.36895 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2308.6153 | 0 | 0 | 2308.6153 | 3.814e-05%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 161 | 3 | 11572.221 | 88.48% | 11.4% | 0.1243% | 9.4437 | 0 | 0 | 9.4437 | 0 | 8.1978 | 28.3597 | 0.28906 | 8.1978 | 28.3597 | 0.28906 | 9.5833 | 33.1528 | 0.28906 | 0.08161% | 0.35802 | 0.35769 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32326.4532 | 0 | 0 | 32326.4532 | 0.0003114%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 14 | 1 | 704.6091 | 96.62% | 3.132% | 0.2514% | 2.407 | 0 | 0 | 2.407 | 0 | 2.0894 | 9.4532 | 0.22103 | 2.0894 | 9.4532 | 0.22103 | 2.4426 | 11.0509 | 0.22103 | 0.3416% | 0.36059 | 0.35932 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1954.2645 | 0 | 0 | 1954.2645 | 7.937e-05%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 102 | 1 | 3413.8137 | 97.67% | 1.995% | 0.3352% | 1.6181 | 0 | 0 | 1.6181 | 0 | 1.4046 | 9.4532 | 0.14859 | 1.4046 | 9.4532 | 0.14859 | 1.642 | 11.0509 | 0.14859 | 0.0474% | 0.2124 | 0.2123 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16072.5394 | 0 | 0 | 16072.5394 | 5.336e-05%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 90 | 2 | 571.2373 | 70.71% | 27.93% | 1.361% | 0.4443 | 0 | 0 | 0.4443 | 0 | 0.38568 | 18.9065 | 0.0204 | 0.38568 | 18.9065 | 0.0204 | 0.45087 | 22.1019 | 0.0204 | 0.07778% | 0.1488 | 0.14863 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3840.2553 | 0 | 0 | 3840.2553 | 1.465e-05%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 43 | 1 | 1603.5562 | 88.72% | 11.16% | 0.1231% | 1.6377 | 0 | 0 | 1.6377 | 0 | 1.4217 | 9.4532 | 0.15039 | 1.4217 | 9.4532 | 0.15039 | 1.6619 | 11.0509 | 0.15039 | 0.1021% | 0.53426 | 0.53365 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3001.8149 | 0 | 0 | 3001.8149 | 5.401e-05%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 116 | 4 | 10619.7967 | 95.69% | 4.18% | 0.1317% | 17.3452 | 0 | 0 | 17.3452 | 0 | 15.0568 | 37.8129 | 0.39819 | 15.0568 | 37.8129 | 0.39819 | 17.6016 | 44.2037 | 0.39819 | 0.1633% | 0.6048 | 0.60376 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17560.6217 | 0 | 0 | 17560.6217 | 0.000572%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 65 | 2 | 1766.7037 | 84.73% | 14.9% | 0.3714% | 2.2799 | 0 | 0 | 2.2799 | 0 | 1.9791 | 18.9065 | 0.10468 | 1.9791 | 18.9065 | 0.10468 | 2.3135 | 22.1019 | 0.10468 | 0.129% | 0.56527 | 0.56441 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3126.1437 | 0 | 0 | 3126.1437 | 7.518e-05%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 91 | 3 | 3678.5807 | 87.54% | 12.33% | 0.1304% | 5.255 | 0 | 0 | 5.255 | 0 | 4.5617 | 28.3597 | 0.16085 | 4.5617 | 28.3597 | 0.16085 | 5.3327 | 33.1528 | 0.16085 | 0.1429% | 0.48997 | 0.48917 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7509.3543 | 0 | 0 | 7509.3543 | 0.0001733%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 156 | 2 | 4421.0024 | 88.12% | 11.51% | 0.3702% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.1462 | 18.9065 | 0.11352 | 2.1462 | 18.9065 | 0.11352 | 2.5089 | 22.1019 | 0.11352 | 0.05592% | 0.63526 | 0.63485 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 6959.9189 | 0 | 0 | 6959.9189 | 8.153e-05%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 49 | 5 | 520.639 | 76.18% | 22.78% | 1.038% | 2.0035 | 0 | 0 | 2.0035 | 0 | 1.7391 | 47.2661 | 0.036795 | 1.7391 | 47.2661 | 0.036795 | 2.0331 | 55.2547 | 0.036795 | 0.3848% | 0.55035 | 0.54757 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 947.1591 | 0 | 0 | 947.1591 | 6.607e-05%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 224 | 7 | 9104.5616 | 91.68% | 8.126% | 0.1928% | 12.9121 | 0 | 0 | 12.9121 | 0 | 11.2085 | 66.1726 | 0.16938 | 11.2085 | 66.1726 | 0.16938 | 13.1029 | 77.3565 | 0.16938 | 0.1418% | 0.49442 | 0.49365 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18417.0782 | 0 | 0 | 18417.0782 | 0.0004258%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 106 | 3 | 5644.8109 | 93.43% | 6.384% | 0.1906% | 7.3881 | 0 | 0 | 7.3881 | 0 | 6.4134 | 28.3597 | 0.22614 | 6.4134 | 28.3597 | 0.22614 | 7.4973 | 33.1528 | 0.22614 | 0.1309% | 0.54394 | 0.54318 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10378.5962 | 0 | 0 | 10378.5962 | 0.0002436%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 147 | 7 | 6729.9647 | 90.49% | 9.346% | 0.1629% | 14.3551 | 0 | 0 | 14.3551 | 0 | 12.4611 | 66.1726 | 0.18831 | 12.4611 | 66.1726 | 0.18831 | 14.5672 | 77.3565 | 0.18831 | 0.2133% | 0.28234 | 0.28168 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23841.655 | 0 | 0 | 23841.655 | 0.0004734%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 22 | 3 | 1495.5065 | 96.97% | 2.927% | 0.1006% | 9.789 | 0 | 0 | 9.789 | 0 | 8.4975 | 28.3597 | 0.29963 | 8.4975 | 28.3597 | 0.29963 | 9.9337 | 33.1528 | 0.29963 | 0.6546% | 0.23738 | 0.23578 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6301.3276 | 0 | 0 | 6301.3276 | 0.0003228%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 34 | 1 | 5260.7056 | 98.77% | 1.153% | 0.07468% | 7.565 | 0 | 0 | 7.565 | 0 | 6.5669 | 9.4532 | 0.69467 | 6.5669 | 9.4532 | 0.69467 | 7.6768 | 11.0509 | 0.69467 | 0.1438% | 0.26107 | 0.26069 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20150.8236 | 0 | 0 | 20150.8236 | 0.0002495%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 53 | 2 | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 31.0729 | 0 | 0 | 31.0729 | 0 | 26.9733 | 18.9065 | 1.4267 | 26.9733 | 18.9065 | 1.4267 | 31.5321 | 22.1019 | 1.4267 | 0.1856% | 0.16225 | 0.16195 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103175.3243 | 0 | 0 | 103175.3243 | 0.001025%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 47 | 1 | 2978.814 | 97.34% | 2.471% | 0.184% | 3.054 | 0 | 0 | 3.054 | 0 | 2.651 | 9.4532 | 0.28044 | 2.651 | 9.4532 | 0.28044 | 3.0991 | 11.0509 | 0.28044 | 0.1025% | 0.26824 | 0.26795 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11105.5174 | 0 | 0 | 11105.5174 | 0.0001007%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 129 | 5 | 2637.9338 | 96.76% | 2.798% | 0.4462% | 4.897 | 0 | 0 | 4.897 | 0 | 4.2509 | 47.2661 | 0.089935 | 4.2509 | 47.2661 | 0.089935 | 4.9694 | 55.2547 | 0.089935 | 0.1856% | 0.13822 | 0.13795 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19086.6138 | 0 | 0 | 19086.6138 | 0.0001615%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 84 | 1 | 3413.9118 | 92.72% | 6.994% | 0.2858% | 1.8653 | 0 | 0 | 1.8653 | 0 | 1.6192 | 9.4532 | 0.17129 | 1.6192 | 9.4532 | 0.17129 | 1.8929 | 11.0509 | 0.17129 | 0.05464% | 0.28561 | 0.28544 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11953.6927 | 0 | 0 | 11953.6927 | 6.151e-05%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 53 | 1 | 6763.0006 | 96.72% | 3.176% | 0.1068% | 6.1091 | 0 | 0 | 6.1091 | 0 | 5.3031 | 9.4532 | 0.56098 | 5.3031 | 9.4532 | 0.56098 | 6.1993 | 11.0509 | 0.56098 | 0.09033% | 0.27105 | 0.27079 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24952.2153 | 0 | 0 | 24952.2153 | 0.0002015%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 49 | 2 | 11350.2874 | 96.69% | 3.233% | 0.07621% | 22.1734 | 0 | 0 | 22.1734 | 0 | 19.248 | 18.9065 | 1.0181 | 19.248 | 18.9065 | 1.0181 | 22.5011 | 22.1019 | 1.0181 | 0.1954% | 0.27097 | 0.27042 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41891.1336 | 0 | 0 | 41891.1336 | 0.0007312%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 87 | 3 | 8477.8617 | 97.79% | 2.104% | 0.1048% | 14.1513 | 0 | 0 | 14.1513 | 0 | 12.2842 | 28.3597 | 0.43316 | 12.2842 | 28.3597 | 0.43316 | 14.3604 | 33.1528 | 0.43316 | 0.1669% | 0.15411 | 0.15384 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55014.7612 | 0 | 0 | 55014.7612 | 0.0004667%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 25 | 1 | 5618.6229 | 98.78% | 1.092% | 0.1294% | 10.989 | 0 | 0 | 10.989 | 0 | 9.5392 | 9.4532 | 1.0091 | 9.5392 | 9.4532 | 1.0091 | 11.1514 | 11.0509 | 1.0091 | 0.1956% | 0.063668 | 0.063542 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88251.4657 | 0 | 0 | 88251.4657 | 0.0003624%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 42 | 1 | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 14.3381 | 0 | 0 | 14.3381 | 0 | 12.4464 | 9.4532 | 1.3166 | 12.4464 | 9.4532 | 1.3166 | 14.55 | 11.0509 | 1.3166 | 0.1171% | 0.14844 | 0.14826 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82471.1507 | 0 | 0 | 82471.1507 | 0.0004728%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 37 | 1 | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 11.9431 | 0 | 0 | 11.9431 | 0 | 10.3674 | 9.4532 | 1.0967 | 10.3674 | 9.4532 | 1.0967 | 12.1196 | 11.0509 | 1.0967 | 0.1325% | 0.074421 | 0.074321 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121104.3584 | 0 | 0 | 121104.3584 | 0.0003938%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 46 | 1 | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 5.871 | 0 | 0 | 5.871 | 0 | 5.0964 | 9.4532 | 0.53912 | 5.0964 | 9.4532 | 0.53912 | 5.9578 | 11.0509 | 0.53912 | 0.1074% | 0.040404 | 0.04036 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135337.4607 | 0 | 0 | 135337.4607 | 0.0001936%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 114 | 5 | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 24.5146 | 0 | 0 | 24.5146 | 0 | 21.2802 | 47.2661 | 0.45022 | 21.2802 | 47.2661 | 0.45022 | 24.8768 | 55.2547 | 0.45022 | 0.2166% | 0.060207 | 0.060076 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 187980.0274 | 0 | 0 | 187980.0274 | 0.0008084%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 89 | 3 | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 22.6455 | 0 | 0 | 22.6455 | 0 | 19.6578 | 28.3597 | 0.69316 | 19.6578 | 28.3597 | 0.69316 | 22.9802 | 33.1528 | 0.69316 | 0.1652% | 0.18916 | 0.18884 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72486.2016 | 0 | 0 | 72486.2016 | 0.0007468%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 84 | 2 | 8801.877 | 98.2% | 1.718% | 0.0819% | 10.187 | 0 | 0 | 10.187 | 0 | 8.843 | 18.9065 | 0.46772 | 8.843 | 18.9065 | 0.46772 | 10.3375 | 22.1019 | 0.46772 | 0.1157% | 0.18313 | 0.18292 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48063.4106 | 0 | 0 | 48063.4106 | 0.0003359%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 283 | 4 | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 27.9754 | 0 | 0 | 27.9754 | 0 | 24.2845 | 37.8129 | 0.64223 | 24.2845 | 37.8129 | 0.64223 | 28.3888 | 44.2037 | 0.64223 | 0.06929% | 0.27264 | 0.27245 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148093.4441 | 0 | 0 | 148093.4441 | 0.0009225%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 4 | 1 | 67.245 | 99.24% | 0% | 0.7576% | 0.82585 | 0 | 0 | 0.82585 | 0 | 0.71689 | 9.4532 | 0.075836 | 0.71689 | 9.4532 | 0.075836 | 0.83806 | 11.0509 | 0.075836 | 1.228% | 0.0036022 | 0.0035576 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18669.5346 | 0 | 0 | 18669.5346 | 2.723e-05%
2028 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 3 | 1 | 417.7025 | 78.37% | 21.49% | 0.1463% | 5.4011 | 0 | 0 | 5.4011 | 0 | 4.6885 | 9.4532 | 0.49597 | 4.6885 | 9.4532 | 0.49597 | 5.4809 | 11.0509 | 0.49597 | 1.293% | 0.047237 | 0.046458 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8874.7148 | 0 | 0 | 8874.7148 | 0.0001781%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 92 | 1 | 18774.394 | 95.55% | 4.388% | 0.06321% | 9.6518 | 0 | 0 | 9.6518 | 0 | 8.3784 | 9.4532 | 0.8863 | 8.3784 | 9.4532 | 0.8863 | 9.7945 | 11.0509 | 0.8863 | 0.05141% | 0.15307 | 0.15298 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122658.6463 | 0 | 0 | 122658.6463 | 0.0003183%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 124 | 2 | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 20.4291 | 0 | 0 | 20.4291 | 0 | 17.7338 | 18.9065 | 0.93798 | 17.7338 | 18.9065 | 0.93798 | 20.731 | 22.1019 | 0.93798 | 0.07936% | 0.15161 | 0.15149 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169797.5264 | 0 | 0 | 169797.5264 | 0.0006737%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 74 | 1 | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 17.9593 | 0 | 0 | 17.9593 | 0 | 15.5898 | 9.4532 | 1.6492 | 15.5898 | 9.4532 | 1.6492 | 18.2247 | 11.0509 | 1.6492 | 0.06635% | 0.088049 | 0.08799 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307403.1485 | 0 | 0 | 307403.1485 | 0.0005922%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 2 | 1 | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 157.0869 | 0 | 0 | 157.0869 | 0 | 136.3617 | 9.4532 | 14.4249 | 136.3617 | 9.4532 | 14.4249 | 159.4083 | 11.0509 | 14.4249 | 2.474% | 0.082479 | 0.080437 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.4684 | 0 | 0 | 76971.4684 | 0.00518%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 76 | 1 | 15766.5188 | 98.33% | 1.627% | 0.04735% | 10.0971 | 0 | 0 | 10.0971 | 0 | 8.7649 | 9.4532 | 0.92719 | 8.7649 | 9.4532 | 0.92719 | 10.2463 | 11.0509 | 0.92719 | 0.06404% | 0.20692 | 0.20679 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76196.1528 | 0 | 0 | 76196.1528 | 0.000333%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 28 | 1 | 11763.9311 | 98.8% | 1.165% | 0.03327% | 20.5478 | 0 | 0 | 20.5478 | 0 | 17.8368 | 9.4532 | 1.8869 | 17.8368 | 9.4532 | 1.8869 | 20.8515 | 11.0509 | 1.8869 | 0.1747% | 0.1877 | 0.18737 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62675.3097 | 0 | 0 | 62675.3097 | 0.0006776%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 109 | 1 | 5570.7929 | 96.25% | 3.531% | 0.2207% | 2.435 | 0 | 0 | 2.435 | 0 | 2.1137 | 9.4532 | 0.2236 | 2.1137 | 9.4532 | 0.2236 | 2.4709 | 11.0509 | 0.2236 | 0.04371% | 0.23644 | 0.23634 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23561.1501 | 0 | 0 | 23561.1501 | 8.03e-05%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 146 | 1 | 41258.5742 | 98.89% | 1.078% | 0.03081% | 13.8332 | 0 | 0 | 13.8332 | 0 | 12.0081 | 9.4532 | 1.2703 | 12.0081 | 9.4532 | 1.2703 | 14.0376 | 11.0509 | 1.2703 | 0.03353% | 0.23053 | 0.23045 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 178971.1895 | 0 | 0 | 178971.1895 | 0.0004562%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 95 | 3 | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 34.9482 | 0 | 0 | 34.9482 | 0 | 30.3373 | 28.3597 | 1.0697 | 30.3373 | 28.3597 | 1.0697 | 35.4647 | 33.1528 | 1.0697 | 0.1549% | 0.20355 | 0.20323 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110855.6516 | 0 | 0 | 110855.6516 | 0.001152%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 126 | 3 | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 64.6455 | 0 | 0 | 64.6455 | 0 | 56.1166 | 28.3597 | 1.9787 | 56.1166 | 28.3597 | 1.9787 | 65.6009 | 33.1528 | 1.9787 | 0.117% | 0.31112 | 0.31076 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177592.2261 | 0 | 0 | 177592.2261 | 0.002132%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 11 | 2 | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 116.2554 | 0 | 0 | 116.2554 | 0 | 100.9173 | 18.9065 | 5.3377 | 100.9173 | 18.9065 | 5.3377 | 117.9735 | 22.1019 | 5.3377 | 0.8969% | 0.12497 | 0.12384 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103723.346 | 0 | 0 | 103723.346 | 0.003834%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 100 | 2 | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 14.8552 | 0 | 0 | 14.8552 | 0 | 12.8953 | 18.9065 | 0.68206 | 12.8953 | 18.9065 | 0.68206 | 15.0748 | 22.1019 | 0.68206 | 0.09806% | 0.14704 | 0.14689 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103025.8283 | 0 | 0 | 103025.8283 | 0.0004899%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 189 | 4 | 28484.5838 | 98.91% | 1.035% | 0.05308% | 29.5164 | 0 | 0 | 29.5164 | 0 | 25.6222 | 37.8129 | 0.6776 | 25.6222 | 37.8129 | 0.6776 | 29.9526 | 44.2037 | 0.6776 | 0.1036% | 0.18464 | 0.18445 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154270.5134 | 0 | 0 | 154270.5134 | 0.0009733%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 28 | 1 | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 14.0943 | 0 | 0 | 14.0943 | 0 | 12.2347 | 9.4532 | 1.2942 | 12.2347 | 9.4532 | 1.2942 | 14.3026 | 11.0509 | 1.2942 | 0.1758% | 0.12171 | 0.12149 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65857.4383 | 0 | 0 | 65857.4383 | 0.0004648%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 11 | 1 | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 19.487 | 0 | 0 | 19.487 | 0 | 16.916 | 9.4532 | 1.7894 | 16.916 | 9.4532 | 1.7894 | 19.775 | 11.0509 | 1.7894 | 0.4478% | 0.11668 | 0.11615 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37296.3933 | 0 | 0 | 37296.3933 | 0.0006426%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 103 | 2 | 11267.961 | 98.98% | 0.9235% | 0.09902% | 10.7196 | 0 | 0 | 10.7196 | 0 | 9.3053 | 18.9065 | 0.49218 | 9.3053 | 18.9065 | 0.49218 | 10.878 | 22.1019 | 0.49218 | 0.09513% | 0.17642 | 0.17625 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63870.7169 | 0 | 0 | 63870.7169 | 0.0003535%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 27 | 1 | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 20.9007 | 0 | 0 | 20.9007 | 0 | 18.1432 | 9.4532 | 1.9193 | 18.1432 | 9.4532 | 1.9193 | 21.2096 | 11.0509 | 1.9193 | 0.1824% | 0.12528 | 0.12505 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91452.193 | 0 | 0 | 91452.193 | 0.0006892%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 106 | 1 | 23409.1539 | 98.39% | 1.548% | 0.05965% | 10.7559 | 0 | 0 | 10.7559 | 0 | 9.3368 | 9.4532 | 0.98769 | 9.3368 | 9.4532 | 0.98769 | 10.9149 | 11.0509 | 0.98769 | 0.04595% | 0.17603 | 0.17595 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 132983.6782 | 0 | 0 | 132983.6782 | 0.0003547%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 59 | 1 | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 7.6086 | 0 | 0 | 7.6086 | 0 | 6.6048 | 9.4532 | 0.69868 | 6.6048 | 9.4532 | 0.69868 | 7.721 | 11.0509 | 0.69868 | 0.08316% | 0.14195 | 0.14183 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64459.8366 | 0 | 0 | 64459.8366 | 0.0002509%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 104 | 3 | 3492.8626 | 93.69% | 6.037% | 0.2698% | 4.6728 | 0 | 0 | 4.6728 | 0 | 4.0563 | 28.3597 | 0.14303 | 4.0563 | 28.3597 | 0.14303 | 4.7419 | 33.1528 | 0.14303 | 0.1338% | 0.16472 | 0.16448 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21206.7349 | 0 | 0 | 21206.7349 | 0.0001541%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 29 | 1 | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 12.0763 | 0 | 0 | 12.0763 | 0 | 10.4831 | 9.4532 | 1.1089 | 10.4831 | 9.4532 | 1.1089 | 12.2548 | 11.0509 | 1.1089 | 0.1699% | 0.14069 | 0.14045 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50517.6321 | 0 | 0 | 50517.6321 | 0.0003982%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 9 | 1 | 387.8494 | 99.7% | 0% | 0.3041% | 2.1267 | 0 | 0 | 2.1267 | 0 | 1.8461 | 9.4532 | 0.19529 | 1.8461 | 9.4532 | 0.19529 | 2.1581 | 11.0509 | 0.19529 | 0.5483% | 0.0069124 | 0.0068744 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56110.1728 | 0 | 0 | 56110.1728 | 7.013e-05%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 95 | 2 | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 36.2773 | 0 | 0 | 36.2773 | 0 | 31.491 | 18.9065 | 1.6656 | 31.491 | 18.9065 | 1.6656 | 36.8134 | 22.1019 | 1.6656 | 0.1032% | 0.16564 | 0.16546 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212251.7107 | 0 | 0 | 212251.7107 | 0.001196%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 43 | 3 | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 64.8185 | 0 | 0 | 64.8185 | 0 | 56.2666 | 28.3597 | 1.984 | 56.2666 | 28.3597 | 1.984 | 65.7763 | 33.1528 | 1.984 | 0.3443% | 0.12361 | 0.12318 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152301.6608 | 0 | 0 | 152301.6608 | 0.002137%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 32 | 1 | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 7.7802 | 0 | 0 | 7.7802 | 0 | 6.7537 | 9.4532 | 0.71443 | 6.7537 | 9.4532 | 0.71443 | 7.8951 | 11.0509 | 0.71443 | 0.1534% | 0.10587 | 0.1057 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47912.2199 | 0 | 0 | 47912.2199 | 0.0002566%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 80 | 1 | 9469.9149 | 95.98% | 3.884% | 0.1387% | 5.6238 | 0 | 0 | 5.6238 | 0 | 4.8818 | 9.4532 | 0.51642 | 4.8818 | 9.4532 | 0.51642 | 5.7069 | 11.0509 | 0.51642 | 0.05939% | 0.13914 | 0.13905 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68064.3774 | 0 | 0 | 68064.3774 | 0.0001855%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 64 | 1 | 3773.8473 | 97.39% | 2.337% | 0.2725% | 2.8427 | 0 | 0 | 2.8427 | 0 | 2.4676 | 9.4532 | 0.26103 | 2.4676 | 9.4532 | 0.26103 | 2.8847 | 11.0509 | 0.26103 | 0.07533% | 0.12816 | 0.12806 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29446.3256 | 0 | 0 | 29446.3256 | 9.374e-05%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 21 | 1 | 5124.1587 | 98.26% | 1.711% | 0.02883% | 11.8683 | 0 | 0 | 11.8683 | 0 | 10.3024 | 9.4532 | 1.0898 | 10.3024 | 9.4532 | 1.0898 | 12.0437 | 11.0509 | 1.0898 | 0.2316% | 0.23544 | 0.23488 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21765.0936 | 0 | 0 | 21765.0936 | 0.0003914%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 46 | 4 | 11817.5772 | 98.58% | 1.381% | 0.03413% | 50.1471 | 0 | 0 | 50.1471 | 0 | 43.531 | 37.8129 | 1.1512 | 43.531 | 37.8129 | 1.1512 | 50.8882 | 44.2037 | 1.1512 | 0.4243% | 0.24629 | 0.24523 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 47984.5233 | 0 | 0 | 47984.5233 | 0.001654%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 85 | 5 | 6620.9098 | 98.66% | 1.309% | 0.03186% | 19.02 | 0 | 0 | 19.02 | 0 | 16.5106 | 47.2661 | 0.34931 | 16.5106 | 47.2661 | 0.34931 | 19.3011 | 55.2547 | 0.34931 | 0.2873% | 0.23843 | 0.23773 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27770.1454 | 0 | 0 | 27770.1454 | 0.0006272%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 124 | 3 | 25318.462 | 99.14% | 0.8163% | 0.04139% | 30.0608 | 0 | 0 | 30.0608 | 0 | 26.0948 | 28.3597 | 0.92014 | 26.0948 | 28.3597 | 0.92014 | 30.5051 | 33.1528 | 0.92014 | 0.1187% | 0.28668 | 0.28634 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88317.3864 | 0 | 0 | 88317.3864 | 0.0009913%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 119 | 2 | 28398.7895 | 98.49% | 1.466% | 0.03945% | 23.2702 | 0 | 0 | 23.2702 | 0 | 20.2001 | 18.9065 | 1.0684 | 20.2001 | 18.9065 | 1.0684 | 23.6141 | 22.1019 | 1.0684 | 0.08194% | 0.28228 | 0.28204 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100607.5086 | 0 | 0 | 100607.5086 | 0.0007674%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 103 | 4 | 26696.2161 | 99.16% | 0.796% | 0.04527% | 50.8872 | 0 | 0 | 50.8872 | 0 | 44.1734 | 37.8129 | 1.1682 | 44.1734 | 37.8129 | 1.1682 | 51.6392 | 44.2037 | 1.1682 | 0.1906% | 0.30703 | 0.30644 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86952.5168 | 0 | 0 | 86952.5168 | 0.001678%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 68 | 1 | 15957.1711 | 97.45% | 2.471% | 0.0752% | 11.3201 | 0 | 0 | 11.3201 | 0 | 9.8266 | 9.4532 | 1.0395 | 9.8266 | 9.4532 | 1.0395 | 11.4874 | 11.0509 | 1.0395 | 0.07094% | 0.1351 | 0.135 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118115.4421 | 0 | 0 | 118115.4421 | 0.0003733%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 24 | 1 | 919.3728 | 93.93% | 5.62% | 0.4487% | 1.7811 | 0 | 0 | 1.7811 | 0 | 1.5461 | 9.4532 | 0.16356 | 1.5461 | 9.4532 | 0.16356 | 1.8075 | 11.0509 | 0.16356 | 0.1937% | 0.38465 | 0.38385 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2390.485 | 0 | 0 | 2390.485 | 5.874e-05%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 4 | 1 | 140.8367 | 88.02% | 11.68% | 0.2956% | 1.5341 | 0 | 0 | 1.5341 | 0 | 1.3317 | 9.4532 | 0.14087 | 1.3317 | 9.4532 | 0.14087 | 1.5567 | 11.0509 | 0.14087 | 1.089% | 0.0083 | 0.0081973 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 16993.747 | 0 | 0 | 16993.747 | 5.059e-05%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 81 | 4 | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 14.3651 | 0 | 0 | 14.3651 | 0 | 12.4699 | 37.8129 | 0.32978 | 12.4699 | 37.8129 | 0.32978 | 14.5774 | 44.2037 | 0.32978 | 0.2435% | 0.046754 | 0.046639 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126174.2462 | 0 | 0 | 126174.2462 | 0.0004737%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 63 | 1 | 4990.92 | 99.62% | 0.2191% | 0.1576% | 3.9067 | 0 | 0 | 3.9067 | 0 | 3.3912 | 9.4532 | 0.35874 | 3.3912 | 9.4532 | 0.35874 | 3.9644 | 11.0509 | 0.35874 | 0.07828% | 0.045737 | 0.045701 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109123.4318 | 0 | 0 | 109123.4318 | 0.0001288%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 93 | 1 | 4663.8779 | 91.12% | 8.567% | 0.3106% | 2.262 | 0 | 0 | 2.262 | 0 | 1.9636 | 9.4532 | 0.20771 | 1.9636 | 9.4532 | 0.20771 | 2.2954 | 11.0509 | 0.20771 | 0.0485% | 0.17153 | 0.17143 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27191.8498 | 0 | 0 | 27191.8498 | 7.459e-05%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 16 | 1 | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 31.2013 | 0 | 0 | 31.2013 | 0 | 27.0848 | 9.4532 | 2.8651 | 27.0848 | 9.4532 | 2.8651 | 31.6624 | 11.0509 | 2.8651 | 0.3087% | 0.21365 | 0.21299 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47313.7427 | 0 | 0 | 47313.7427 | 0.001029%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 43 | 1 | 6147.2839 | 97.88% | 2.045% | 0.07292% | 6.9266 | 0 | 0 | 6.9266 | 0 | 6.0128 | 9.4532 | 0.63605 | 6.0128 | 9.4532 | 0.63605 | 7.029 | 11.0509 | 0.63605 | 0.1127% | 0.69907 | 0.69826 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8793.7366 | 0 | 0 | 8793.7366 | 0.0002284%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 64 | 3 | 8696.5042 | 96.48% | 3.447% | 0.07747% | 19.4674 | 0 | 0 | 19.4674 | 0 | 16.8989 | 28.3597 | 0.59588 | 16.8989 | 28.3597 | 0.59588 | 19.7551 | 33.1528 | 0.59588 | 0.2239% | 0.68132 | 0.67974 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12765.2043 | 0 | 0 | 12765.2043 | 0.000642%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 39 | 1 | 2983.7291 | 97.9% | 1.929% | 0.1696% | 3.7076 | 0 | 0 | 3.7076 | 0 | 3.2184 | 9.4532 | 0.34046 | 3.2184 | 9.4532 | 0.34046 | 3.7624 | 11.0509 | 0.34046 | 0.1243% | 0.13489 | 0.13472 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22120.7035 | 0 | 0 | 22120.7035 | 0.0001223%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 79 | 2 | 6311.4919 | 84.29% | 15.54% | 0.1769% | 6.6666 | 0 | 0 | 6.6666 | 0 | 5.7871 | 18.9065 | 0.30609 | 5.7871 | 18.9065 | 0.30609 | 6.7652 | 22.1019 | 0.30609 | 0.1056% | 0.11961 | 0.11946 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 52775.8971 | 0 | 0 | 52775.8971 | 0.0002198%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 92 | 3 | 6645.572 | 99.09% | 0.6868% | 0.2213% | 10.6294 | 0 | 0 | 10.6294 | 0 | 9.227 | 28.3597 | 0.32536 | 9.227 | 28.3597 | 0.32536 | 10.7865 | 33.1528 | 0.32536 | 0.1599% | 0.082825 | 0.082691 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80237.6767 | 0 | 0 | 80237.6767 | 0.0003505%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 16 | 1 | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 5.7559 | 0 | 0 | 5.7559 | 0 | 4.9965 | 9.4532 | 0.52855 | 4.9965 | 9.4532 | 0.52855 | 5.8409 | 11.0509 | 0.52855 | 0.3064% | 0.087615 | 0.087344 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21439.5884 | 0 | 0 | 21439.5884 | 0.0001898%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 30 | 1 | 1438.3629 | 99.75% | 0% | 0.2509% | 2.3673 | 0 | 0 | 2.3673 | 0 | 2.055 | 9.4532 | 0.21739 | 2.055 | 9.4532 | 0.21739 | 2.4023 | 11.0509 | 0.21739 | 0.1646% | 0.019586 | 0.019554 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73438.6208 | 0 | 0 | 73438.6208 | 7.807e-05%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 51 | 1 | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 15.3763 | 0 | 0 | 15.3763 | 0 | 13.3477 | 9.4532 | 1.412 | 13.3477 | 9.4532 | 1.412 | 15.6036 | 11.0509 | 1.412 | 0.09618% | 0.15941 | 0.15925 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100292.7533 | 0 | 0 | 100292.7533 | 0.0005071%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 38 | 2 | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 21.0985 | 0 | 0 | 21.0985 | 0 | 18.3148 | 18.9065 | 0.96871 | 18.3148 | 18.9065 | 0.96871 | 21.4103 | 22.1019 | 0.96871 | 0.2586% | 0.15819 | 0.15778 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51583.9681 | 0 | 0 | 51583.9681 | 0.0006957%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 127 | 4 | 37077.302 | 99.36% | 0.615% | 0.02874% | 57.4334 | 0 | 0 | 57.4334 | 0 | 49.8559 | 37.8129 | 1.3185 | 49.8559 | 37.8129 | 1.3185 | 58.2822 | 44.2037 | 1.3185 | 0.1549% | 0.20421 | 0.20389 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181563.7335 | 0 | 0 | 181563.7335 | 0.001894%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 53 | 2 | 2064.0334 | 78.9% | 20.86% | 0.2358% | 3.042 | 0 | 0 | 3.042 | 0 | 2.6406 | 18.9065 | 0.13967 | 2.6406 | 18.9065 | 0.13967 | 3.0869 | 22.1019 | 0.13967 | 0.1474% | 0.42513 | 0.42434 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4856.9721 | 0 | 0 | 4856.9721 | 0.0001003%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 90 | 4 | 3719.4004 | 95.17% | 4.691% | 0.1427% | 7.7872 | 0 | 0 | 7.7872 | 0 | 6.7598 | 37.8129 | 0.17877 | 6.7598 | 37.8129 | 0.17877 | 7.9022 | 44.2037 | 0.17877 | 0.2094% | 0.19421 | 0.19378 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19153.2798 | 0 | 0 | 19153.2798 | 0.0002568%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 29 | 1 | 1531.7487 | 97.85% | 2.019% | 0.1357% | 2.5582 | 0 | 0 | 2.5582 | 0 | 2.2207 | 9.4532 | 0.23491 | 2.2207 | 9.4532 | 0.23491 | 2.596 | 11.0509 | 0.23491 | 0.167% | 0.1808 | 0.1805 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8472.158 | 0 | 0 | 8472.158 | 8.436e-05%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 32 | 1 | 5119.7141 | 98.56% | 1.393% | 0.05121% | 7.8052 | 0 | 0 | 7.8052 | 0 | 6.7754 | 9.4532 | 0.71673 | 6.7754 | 9.4532 | 0.71673 | 7.9205 | 11.0509 | 0.71673 | 0.1525% | 0.12647 | 0.12627 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40482.6819 | 0 | 0 | 40482.6819 | 0.0002574%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 109 | 1 | 6915.6819 | 99% | 0.9206% | 0.07911% | 3.1092 | 0 | 0 | 3.1092 | 0 | 2.699 | 9.4532 | 0.28551 | 2.699 | 9.4532 | 0.28551 | 3.1552 | 11.0509 | 0.28551 | 0.04496% | 0.20255 | 0.20246 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34143.3078 | 0 | 0 | 34143.3078 | 0.0001025%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 66 | 3 | 3027.5479 | 94.73% | 5.109% | 0.164% | 6.4528 | 0 | 0 | 6.4528 | 0 | 5.6014 | 28.3597 | 0.19751 | 5.6014 | 28.3597 | 0.19751 | 6.5481 | 33.1528 | 0.19751 | 0.2131% | 0.24168 | 0.24114 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12528.5519 | 0 | 0 | 12528.5519 | 0.0002128%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 65 | 1 | 10517.0624 | 98.31% | 1.619% | 0.07383% | 7.8735 | 0 | 0 | 7.8735 | 0 | 6.8347 | 9.4532 | 0.72301 | 6.8347 | 9.4532 | 0.72301 | 7.9899 | 11.0509 | 0.72301 | 0.07486% | 0.14726 | 0.14715 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71418.4694 | 0 | 0 | 71418.4694 | 0.0002596%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 30 | 1 | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 15.306 | 0 | 0 | 15.306 | 0 | 13.2866 | 9.4532 | 1.4055 | 13.2866 | 9.4532 | 1.4055 | 15.5322 | 11.0509 | 1.4055 | 0.1639% | 0.12948 | 0.12926 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72131.7191 | 0 | 0 | 72131.7191 | 0.0005047%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 85 | 3 | 6920.124 | 97.57% | 2.306% | 0.1195% | 11.7966 | 0 | 0 | 11.7966 | 0 | 10.2402 | 28.3597 | 0.36108 | 10.2402 | 28.3597 | 0.36108 | 11.9709 | 33.1528 | 0.36108 | 0.1705% | 0.15381 | 0.15354 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 44994.6929 | 0 | 0 | 44994.6929 | 0.000389%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 27 | 1 | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 10.8273 | 0 | 0 | 10.8273 | 0 | 9.3988 | 9.4532 | 0.99425 | 9.3988 | 9.4532 | 0.99425 | 10.9874 | 11.0509 | 0.99425 | 0.1821% | 0.15284 | 0.15256 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38906.576 | 0 | 0 | 38906.576 | 0.000357%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 128 | 6 | 3361.5705 | 93.71% | 6.129% | 0.1568% | 7.3096 | 0 | 0 | 7.3096 | 0 | 6.3452 | 56.7194 | 0.11187 | 6.3452 | 56.7194 | 0.11187 | 7.4176 | 66.3056 | 0.11187 | 0.2174% | 0.19527 | 0.19482 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17217.1861 | 0 | 0 | 17217.1861 | 0.000241%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 20 | 3 | 3782.8568 | 99.48% | 0.4537% | 0.066% | 27.9417 | 0 | 0 | 27.9417 | 0 | 24.2553 | 28.3597 | 0.85527 | 24.2553 | 28.3597 | 0.85527 | 28.3547 | 33.1528 | 0.85527 | 0.7386% | 0.093421 | 0.092727 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40494.2351 | 0 | 0 | 40494.2351 | 0.0009214%

## Trim_and_Removal
Prune and Removel - Risk & Cost Benefit | [29 empty] | Summary Table |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[30 empty] | Year | Total Units (miles) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%)
back to index | [29 empty] | 2026 | 91336 | 2834578.5099 | 136692.5546 | 4.822% | 130395.4104 | 30054.5835 | 4.3386 | 130395.4104 | 30054.5835 | 4.3386 | 137362.6162 | 31660.4412 | 4.3386 | 4.508%
[9 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [12 empty] | 2027 | 91336 | 2834578.5099 | 136692.5546 | 4.822% | 124388.3627 | 28670.0308 | 4.3386 | 124388.3627 | 28670.0308 | 4.3386 | 138035.9623 | 31815.6394 | 4.3386 | 4.508%
[9 empty] | Capital Cost only in Year 0 | 0.34495 | K$/tree | 2025-06-30 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [12 empty] | 2028 | 91336 | 2834578.5099 | 136692.5546 | 4.822% | 118658.0472 | 27349.2616 | 4.3386 | 118658.0472 | 27349.2616 | 4.3386 | 138712.6092 | 31971.5984 | 4.3386 | 4.508%
[9 empty] | Service Drop factor | 0% | % | 2025-06-30 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [12 empty] | Total 2026-2028 | 274008 | 8503735.5297 | 410077.6639 | 4.822% | 373441.8203 | 86073.8759 | 4.3386 | 373441.8203 | 86073.8759 | 4.3386 | 414111.1878 | 95447.679 | 4.3386 | 13.52%
[9 empty] | OH to UG conversion factor | 0% | % | 2025-06-30
[9 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-06-30
[9 empty] | Lifetime | 1 | Years | 2025-06-30
[9 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[9 empty] | Mitigation Effectiveness Estimate (%) | 4.95% | % | 2025-06-30
[9 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-06-30
[13 empty] | [1] | [1] | [1] | [2]
[8 empty] | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Units | Units (Poles) | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 5 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.4787 | 1.6453 | 3.33 | 5.4787 | 1.6453 | 3.33 | 5.7714 | 1.7332 | 3.33 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 34 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 19.1516 | 11.1879 | 1.7118 | 19.1516 | 11.1879 | 1.7118 | 20.1748 | 11.7857 | 1.7118 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 620 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 182.2481 | 204.0142 | 0.89331 | 182.2481 | 204.0142 | 0.89331 | 191.9859 | 214.915 | 0.89331 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 510 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1643.7869 | 167.8181 | 9.795 | 1643.7869 | 167.8181 | 9.795 | 1731.6167 | 176.7849 | 9.795 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 72 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 327.0901 | 23.692 | 13.8059 | 327.0901 | 23.692 | 13.8059 | 344.567 | 24.9579 | 13.8059 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 230 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 886.2644 | 75.6827 | 11.7103 | 886.2644 | 75.6827 | 11.7103 | 933.6187 | 79.7265 | 11.7103 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 99 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 236.5455 | 32.5765 | 7.2612 | 236.5455 | 32.5765 | 7.2612 | 249.1845 | 34.3171 | 7.2612 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 32 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 65.2006 | 10.5298 | 6.192 | 65.2006 | 10.5298 | 6.192 | 68.6844 | 11.0924 | 6.192 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 20 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 37.3591 | 6.5811 | 5.6767 | 37.3591 | 6.5811 | 5.6767 | 39.3553 | 6.9327 | 5.6767 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 145 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 461.0302 | 47.713 | 9.6626 | 461.0302 | 47.713 | 9.6626 | 485.6637 | 50.2624 | 9.6626 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 5 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 32.5478 | 1.6453 | 19.7826 | 32.5478 | 1.6453 | 19.7826 | 34.2868 | 1.7332 | 19.7826 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 57 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 237.4956 | 18.7561 | 12.6623 | 237.4956 | 18.7561 | 12.6623 | 250.1853 | 19.7583 | 12.6623 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 198 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 135.4283 | 65.1529 | 2.0786 | 135.4283 | 65.1529 | 2.0786 | 142.6644 | 68.6341 | 2.0786 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 886 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 429.1796 | 291.5429 | 1.4721 | 429.1796 | 291.5429 | 1.4721 | 452.1112 | 307.1204 | 1.4721 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 587 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 173.5489 | 193.1554 | 0.89849 | 173.5489 | 193.1554 | 0.89849 | 182.8218 | 203.4759 | 0.89849 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 101 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 24.2408 | 33.2346 | 0.72938 | 24.2408 | 33.2346 | 0.72938 | 25.536 | 35.0103 | 0.72938 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 14 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 237.7519 | 4.6068 | 51.6092 | 237.7519 | 4.6068 | 51.6092 | 250.4553 | 4.8529 | 51.6092 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 117 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 550.1247 | 38.4995 | 14.2892 | 550.1247 | 38.4995 | 14.2892 | 579.5186 | 40.5565 | 14.2892 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 50 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 101.0059 | 16.4528 | 6.1391 | 101.0059 | 16.4528 | 6.1391 | 106.4028 | 17.3319 | 6.1391 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 307 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 308.4441 | 101.0199 | 3.0533 | 308.4441 | 101.0199 | 3.0533 | 324.9247 | 106.4176 | 3.0533 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 298 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1185.2748 | 98.0584 | 12.0874 | 1185.2748 | 98.0584 | 12.0874 | 1248.6056 | 103.2978 | 12.0874 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 474 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1320.7925 | 155.9722 | 8.4681 | 1320.7925 | 155.9722 | 8.4681 | 1391.3643 | 164.306 | 8.4681 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 159 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1249.9804 | 52.3198 | 23.8912 | 1249.9804 | 52.3198 | 23.8912 | 1316.7686 | 55.1153 | 23.8912 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 740 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 734.3072 | 243.5008 | 3.0156 | 734.3072 | 243.5008 | 3.0156 | 773.5422 | 256.5114 | 3.0156 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 49 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.73672 | 16.1237 | 0.045692 | 0.73672 | 16.1237 | 0.045692 | 0.77608 | 16.9852 | 0.045692 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 18 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.16305 | 5.923 | 0.027528 | 0.16305 | 5.923 | 0.027528 | 0.17176 | 6.2395 | 0.027528 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2026 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 2 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.1037 | 0.65811 | 0.15757 | 0.1037 | 0.65811 | 0.15757 | 0.10924 | 0.69327 | 0.15757 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 5 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 34.2346 | 1.6453 | 20.8078 | 34.2346 | 1.6453 | 20.8078 | 36.0638 | 1.7332 | 20.8078 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 72 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 40.7779 | 23.692 | 1.7212 | 40.7779 | 23.692 | 1.7212 | 42.9567 | 24.9579 | 1.7212 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 2 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.8535 | 0.65811 | 8.8944 | 5.8535 | 0.65811 | 8.8944 | 6.1663 | 0.69327 | 8.8944 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 252 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 277.4933 | 82.9219 | 3.3464 | 277.4933 | 82.9219 | 3.3464 | 292.3202 | 87.3525 | 3.3464 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 260 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 234.7817 | 85.5543 | 2.7442 | 234.7817 | 85.5543 | 2.7442 | 247.3264 | 90.1256 | 2.7442 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 214 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 118.5279 | 70.4178 | 1.6832 | 118.5279 | 70.4178 | 1.6832 | 124.861 | 74.1803 | 1.6832 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 47 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.4459 | 15.4656 | 0.28747 | 4.4459 | 15.4656 | 0.28747 | 4.6834 | 16.2919 | 0.28747 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 4 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 100.9567 | 1.3162 | 76.702 | 100.9567 | 1.3162 | 76.702 | 106.351 | 1.3865 | 76.702 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 24 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 199.4969 | 7.8973 | 25.2613 | 199.4969 | 7.8973 | 25.2613 | 210.1563 | 8.3193 | 25.2613 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 17 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 18.6068 | 5.5939 | 3.3262 | 18.6068 | 5.5939 | 3.3262 | 19.601 | 5.8928 | 3.3262 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 60 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 37.005 | 19.7433 | 1.8743 | 37.005 | 19.7433 | 1.8743 | 38.9822 | 20.7982 | 1.8743 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 840 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 200.6758 | 276.4063 | 0.72602 | 200.6758 | 276.4063 | 0.72602 | 211.3982 | 291.1751 | 0.72602 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 10 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 9.4254 | 3.2906 | 2.8644 | 9.4254 | 3.2906 | 2.8644 | 9.929 | 3.4664 | 2.8644 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 2 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 11.4466 | 0.65811 | 17.3931 | 11.4466 | 0.65811 | 17.3931 | 12.0582 | 0.69327 | 17.3931 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 45 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 183.9861 | 14.8075 | 12.4252 | 183.9861 | 14.8075 | 12.4252 | 193.8167 | 15.5987 | 12.4252 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 53 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 476.2228 | 17.4399 | 27.3065 | 476.2228 | 17.4399 | 27.3065 | 501.668 | 18.3718 | 27.3065 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 215 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 482.9506 | 70.7469 | 6.8265 | 482.9506 | 70.7469 | 6.8265 | 508.7553 | 74.527 | 6.8265 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 28 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 284.1236 | 9.2135 | 30.8376 | 284.1236 | 9.2135 | 30.8376 | 299.3047 | 9.7058 | 30.8376 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 21 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 99.0448 | 6.9102 | 14.3332 | 99.0448 | 6.9102 | 14.3332 | 104.3369 | 7.2794 | 14.3332 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 186 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 396.1715 | 61.2043 | 6.4729 | 396.1715 | 61.2043 | 6.4729 | 417.3395 | 64.4745 | 6.4729 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 75 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 72.5366 | 24.6791 | 2.9392 | 72.5366 | 24.6791 | 2.9392 | 76.4123 | 25.9978 | 2.9392 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 117 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 165.5356 | 38.4995 | 4.2997 | 165.5356 | 38.4995 | 4.2997 | 174.3804 | 40.5565 | 4.2997 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 246 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 137.9346 | 80.9476 | 1.704 | 137.9346 | 80.9476 | 1.704 | 145.3046 | 85.2727 | 1.704 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 35 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 64.7607 | 11.5169 | 5.6231 | 64.7607 | 11.5169 | 5.6231 | 68.2209 | 12.1323 | 5.6231 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 94 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 200.3313 | 30.9312 | 6.4767 | 200.3313 | 30.9312 | 6.4767 | 211.0352 | 32.5839 | 6.4767 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 2 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 19.3654 | 0.65811 | 29.4258 | 19.3654 | 0.65811 | 29.4258 | 20.4002 | 0.69327 | 29.4258 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 17 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 21.4921 | 5.5939 | 3.842 | 21.4921 | 5.5939 | 3.842 | 22.6404 | 5.8928 | 3.842 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 55 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 55.2642 | 18.098 | 3.0536 | 55.2642 | 18.098 | 3.0536 | 58.217 | 19.065 | 3.0536 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 9 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.4335 | 2.9615 | 2.51 | 7.4335 | 2.9615 | 2.51 | 7.8307 | 3.1197 | 2.51 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 33 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 87.8513 | 10.8588 | 8.0903 | 87.8513 | 10.8588 | 8.0903 | 92.5454 | 11.439 | 8.0903 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 63 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 281.9725 | 20.7305 | 13.6018 | 281.9725 | 20.7305 | 13.6018 | 297.0387 | 21.8381 | 13.6018 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 25 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 304.239 | 8.2264 | 36.9833 | 304.239 | 8.2264 | 36.9833 | 320.4949 | 8.6659 | 36.9833 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 335 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 550.6852 | 110.2335 | 4.9956 | 550.6852 | 110.2335 | 4.9956 | 580.1091 | 116.1234 | 4.9956 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 91 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 170.7918 | 29.944 | 5.7037 | 170.7918 | 29.944 | 5.7037 | 179.9174 | 31.544 | 5.7037 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 35 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 18.259 | 11.5169 | 1.5854 | 18.259 | 11.5169 | 1.5854 | 19.2346 | 12.1323 | 1.5854 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 8 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 95.5517 | 2.6324 | 36.2977 | 95.5517 | 2.6324 | 36.2977 | 100.6572 | 2.7731 | 36.2977 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 101 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 203.6169 | 33.2346 | 6.1267 | 203.6169 | 33.2346 | 6.1267 | 214.4964 | 35.0103 | 6.1267 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.7481 | 1.3162 | 2.0878 | 2.7481 | 1.3162 | 2.0878 | 2.8949 | 1.3865 | 2.0878 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2026 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | 4--2 | 14 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 4.6068 | 0 | 0 | 4.6068 | 0 | 0 | 4.8529 | 0 | 0% | 0.091242 | 0.086726 | 728.9125 | 1.3917 | 578.9338 | 148.587 | 766.8727 | 0 | 0 | 766.8727 | 0%
2026 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | 4--2 | 8 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2.6324 | 0 | 0 | 2.6324 | 0 | 0 | 2.7731 | 0 | 0% | 0.091116 | 0.086606 | 1530.6137 | 1.9599 | 1384.4341 | 144.2196 | 1610.3248 | 0 | 0 | 1610.3248 | 0%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 58 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 748.0666 | 19.0852 | 39.1962 | 748.0666 | 19.0852 | 39.1962 | 788.0369 | 20.1049 | 39.1962 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 7 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.3585 | 2.3034 | 1.0239 | 2.3585 | 2.3034 | 1.0239 | 2.4845 | 2.4265 | 1.0239 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.8232 | 0.32906 | 11.6186 | 3.8232 | 0.32906 | 11.6186 | 4.0275 | 0.34664 | 11.6186 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 151 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 382.4036 | 49.6873 | 7.6962 | 382.4036 | 49.6873 | 7.6962 | 402.8359 | 52.3422 | 7.6962 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 444 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1739.5055 | 146.1005 | 11.9062 | 1739.5055 | 146.1005 | 11.9062 | 1832.4497 | 153.9068 | 11.9062 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 4 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.34944 | 1.3162 | 0.26548 | 0.34944 | 1.3162 | 0.26548 | 0.36811 | 1.3865 | 0.26548 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 42 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 17.3347 | 13.8203 | 1.2543 | 17.3347 | 13.8203 | 1.2543 | 18.261 | 14.5588 | 1.2543 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 319 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 240.4359 | 104.9686 | 2.2906 | 240.4359 | 104.9686 | 2.2906 | 253.2827 | 110.5772 | 2.2906 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 26 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 142.8022 | 8.5554 | 16.6914 | 142.8022 | 8.5554 | 16.6914 | 150.4323 | 9.0126 | 16.6914 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 61 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 181.173 | 20.0724 | 9.026 | 181.173 | 20.0724 | 9.026 | 190.8533 | 21.1449 | 9.026 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 124 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 142.1765 | 40.8028 | 3.4845 | 142.1765 | 40.8028 | 3.4845 | 149.7732 | 42.983 | 3.4845 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 208 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 79.3622 | 68.4435 | 1.1595 | 79.3622 | 68.4435 | 1.1595 | 83.6027 | 72.1005 | 1.1595 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 114 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 83.7784 | 37.5123 | 2.2334 | 83.7784 | 37.5123 | 2.2334 | 88.2548 | 39.5166 | 2.2334 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 323 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 858.8326 | 106.2848 | 8.0805 | 858.8326 | 106.2848 | 8.0805 | 904.7212 | 111.9638 | 8.0805 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 419 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 188.5406 | 137.8741 | 1.3675 | 188.5406 | 137.8741 | 1.3675 | 198.6146 | 145.2409 | 1.3675 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 53 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 88.4542 | 17.4399 | 5.0719 | 88.4542 | 17.4399 | 5.0719 | 93.1805 | 18.3718 | 5.0719 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 166 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 201.9487 | 54.6232 | 3.6971 | 201.9487 | 54.6232 | 3.6971 | 212.7391 | 57.5417 | 3.6971 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 248 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 262.6012 | 81.6057 | 3.2179 | 262.6012 | 81.6057 | 3.2179 | 276.6324 | 85.966 | 3.2179 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 143 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 31.4944 | 47.0549 | 0.66931 | 31.4944 | 47.0549 | 0.66931 | 33.1772 | 49.5691 | 0.66931 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 96 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 537.4279 | 31.5893 | 17.013 | 537.4279 | 31.5893 | 17.013 | 566.1434 | 33.2772 | 17.013 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 63 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 193.8402 | 20.7305 | 9.3505 | 193.8402 | 20.7305 | 9.3505 | 204.1973 | 21.8381 | 9.3505 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 234 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 461.7857 | 76.9989 | 5.9973 | 461.7857 | 76.9989 | 5.9973 | 486.4596 | 81.1131 | 5.9973 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2026 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 19 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 12.9185 | 6.252 | 2.0663 | 12.9185 | 6.252 | 2.0663 | 13.6088 | 6.5861 | 2.0663 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 62 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 156.9652 | 20.4014 | 7.6938 | 156.9652 | 20.4014 | 7.6938 | 165.3521 | 21.4915 | 7.6938 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 95 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 227.6349 | 31.2602 | 7.2819 | 227.6349 | 31.2602 | 7.2819 | 239.7978 | 32.9305 | 7.2819 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 299 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 602.1374 | 98.3875 | 6.1201 | 602.1374 | 98.3875 | 6.1201 | 634.3104 | 103.6445 | 6.1201 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 68.9354 | 1.6453 | 41.899 | 68.9354 | 1.6453 | 41.899 | 72.6187 | 1.7332 | 41.899 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 11 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 109.4668 | 3.6196 | 30.2427 | 109.4668 | 3.6196 | 30.2427 | 115.3157 | 3.813 | 30.2427 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 1 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 2.0506 | 0.32906 | 6.2317 | 2.0506 | 0.32906 | 6.2317 | 2.1601 | 0.34664 | 6.2317 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 357 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 530.5991 | 117.4727 | 4.5168 | 530.5991 | 117.4727 | 4.5168 | 558.9498 | 123.7494 | 4.5168 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 5 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 91.3318 | 1.6453 | 55.5115 | 91.3318 | 1.6453 | 55.5115 | 96.2118 | 1.7332 | 55.5115 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 208 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 198.1694 | 68.4435 | 2.8954 | 198.1694 | 68.4435 | 2.8954 | 208.7579 | 72.1005 | 2.8954 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 4 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 30.6993 | 1.3162 | 23.3238 | 30.6993 | 1.3162 | 23.3238 | 32.3396 | 1.3865 | 23.3238 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 26 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.8974 | 8.5554 | 1.1569 | 9.8974 | 8.5554 | 1.1569 | 10.4263 | 9.0126 | 1.1569 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 87 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 16.5472 | 28.6278 | 0.57801 | 16.5472 | 28.6278 | 0.57801 | 17.4313 | 30.1574 | 0.57801 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 254 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 74.8329 | 83.58 | 0.89534 | 74.8329 | 83.58 | 0.89534 | 78.8314 | 88.0458 | 0.89534 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 14 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.30123 | 4.6068 | 0.065388 | 0.30123 | 4.6068 | 0.065388 | 0.31732 | 4.8529 | 0.065388 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 21 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 43.8971 | 6.9102 | 6.3525 | 43.8971 | 6.9102 | 6.3525 | 46.2426 | 7.2794 | 6.3525 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 38 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 22.317 | 12.5041 | 1.7848 | 22.317 | 12.5041 | 1.7848 | 23.5094 | 13.1722 | 1.7848 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 35 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 60.2656 | 11.5169 | 5.2328 | 60.2656 | 11.5169 | 5.2328 | 63.4857 | 12.1323 | 5.2328 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 180 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 140.2011 | 59.2299 | 2.3671 | 140.2011 | 59.2299 | 2.3671 | 147.6922 | 62.3947 | 2.3671 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 515 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 398.5744 | 169.4634 | 2.352 | 398.5744 | 169.4634 | 2.352 | 419.8708 | 178.5181 | 2.352 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 55 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 21.1934 | 18.098 | 1.171 | 21.1934 | 18.098 | 1.171 | 22.3257 | 19.065 | 1.171 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 44 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 42.0166 | 14.4784 | 2.902 | 42.0166 | 14.4784 | 2.902 | 44.2616 | 15.252 | 2.902 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 67 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.6768 | 22.0467 | 0.25749 | 5.6768 | 22.0467 | 0.25749 | 5.9801 | 23.2247 | 0.25749 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 15 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.6262 | 4.9358 | 1.5451 | 7.6262 | 4.9358 | 1.5451 | 8.0337 | 5.1996 | 1.5451 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 70 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 50.6908 | 23.0339 | 2.2007 | 50.6908 | 23.0339 | 2.2007 | 53.3993 | 24.2646 | 2.2007 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 129 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 71.9999 | 42.4481 | 1.6962 | 71.9999 | 42.4481 | 1.6962 | 75.847 | 44.7162 | 1.6962 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 264 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 81.2969 | 86.8706 | 0.93584 | 81.2969 | 86.8706 | 0.93584 | 85.6408 | 91.5122 | 0.93584 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 63 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 78.3562 | 20.7305 | 3.7798 | 78.3562 | 20.7305 | 3.7798 | 82.5429 | 21.8381 | 3.7798 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 51 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 70.4248 | 16.7818 | 4.1965 | 70.4248 | 16.7818 | 4.1965 | 74.1877 | 17.6785 | 4.1965 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 5 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 28.5249 | 1.6453 | 17.3375 | 28.5249 | 1.6453 | 17.3375 | 30.0491 | 1.7332 | 17.3375 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 291 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 228.8419 | 95.7551 | 2.3899 | 228.8419 | 95.7551 | 2.3899 | 241.0693 | 100.8714 | 2.3899 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 1 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 58.5338 | 0.32906 | 177.8846 | 58.5338 | 0.32906 | 177.8846 | 61.6614 | 0.34664 | 177.8846 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 68 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 45.5695 | 22.3758 | 2.0366 | 45.5695 | 22.3758 | 2.0366 | 48.0044 | 23.5713 | 2.0366 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 10 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.981 | 3.2906 | 3.641 | 11.981 | 3.2906 | 3.641 | 12.6212 | 3.4664 | 3.641 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 50 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 68.092 | 16.4528 | 4.1386 | 68.092 | 16.4528 | 4.1386 | 71.7303 | 17.3319 | 4.1386 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 81 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 124.7575 | 26.6535 | 4.6807 | 124.7575 | 26.6535 | 4.6807 | 131.4234 | 28.0776 | 4.6807 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 19 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 47.6389 | 6.252 | 7.6197 | 47.6389 | 6.252 | 7.6197 | 50.1843 | 6.5861 | 7.6197 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 7 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.8455 | 2.3034 | 2.1037 | 4.8455 | 2.3034 | 2.1037 | 5.1044 | 2.4265 | 2.1037 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 42 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 100.8529 | 13.8203 | 7.2974 | 100.8529 | 13.8203 | 7.2974 | 106.2416 | 14.5588 | 7.2974 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 59 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 67.9477 | 19.4143 | 3.4999 | 67.9477 | 19.4143 | 3.4999 | 71.5783 | 20.4516 | 3.4999 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 270 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1227.409 | 88.8449 | 13.8152 | 1227.409 | 88.8449 | 13.8152 | 1292.9912 | 93.592 | 13.8152 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 487 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 312.9422 | 160.2499 | 1.9528 | 312.9422 | 160.2499 | 1.9528 | 329.6631 | 168.8122 | 1.9528 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 158 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 22.2618 | 51.9907 | 0.42819 | 22.2618 | 51.9907 | 0.42819 | 23.4513 | 54.7687 | 0.42819 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 69 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 18.4924 | 22.7048 | 0.81447 | 18.4924 | 22.7048 | 0.81447 | 19.4805 | 23.918 | 0.81447 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 105 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 23.9277 | 34.5508 | 0.69254 | 23.9277 | 34.5508 | 0.69254 | 25.2062 | 36.3969 | 0.69254 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 154 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 103.331 | 50.6745 | 2.0391 | 103.331 | 50.6745 | 2.0391 | 108.8522 | 53.3821 | 2.0391 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 534 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 69.6651 | 175.7155 | 0.39647 | 69.6651 | 175.7155 | 0.39647 | 73.3874 | 185.1042 | 0.39647 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 96 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 1047.5713 | 31.5893 | 33.1622 | 1047.5713 | 31.5893 | 33.1622 | 1103.5445 | 33.2772 | 33.1622 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 169 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 589.092 | 55.6103 | 10.5932 | 589.092 | 55.6103 | 10.5932 | 620.568 | 58.5817 | 10.5932 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 153 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 911.0636 | 50.3454 | 18.0962 | 911.0636 | 50.3454 | 18.0962 | 959.743 | 53.0355 | 18.0962 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 46 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 65.4226 | 15.1365 | 4.3222 | 65.4226 | 15.1365 | 4.3222 | 68.9182 | 15.9453 | 4.3222 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 150 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 253.85 | 49.3583 | 5.143 | 253.85 | 49.3583 | 5.143 | 267.4135 | 51.9956 | 5.143 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 111 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 657.6222 | 36.5251 | 18.0047 | 657.6222 | 36.5251 | 18.0047 | 692.7598 | 38.4767 | 18.0047 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 6 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.3625 | 1.9743 | 1.7031 | 3.3625 | 1.9743 | 1.7031 | 3.5422 | 2.0798 | 1.7031 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 502 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 84.8362 | 165.1857 | 0.51358 | 84.8362 | 165.1857 | 0.51358 | 89.3691 | 174.0118 | 0.51358 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 383 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 113.1467 | 126.0281 | 0.89779 | 113.1467 | 126.0281 | 0.89779 | 119.1922 | 132.762 | 0.89779 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 367 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 497.9891 | 120.7632 | 4.1237 | 497.9891 | 120.7632 | 4.1237 | 524.5974 | 127.2158 | 4.1237 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 406 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 163.4677 | 133.5964 | 1.2236 | 163.4677 | 133.5964 | 1.2236 | 172.202 | 140.7346 | 1.2236 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 493 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 61.735 | 162.2242 | 0.38055 | 61.735 | 162.2242 | 0.38055 | 65.0335 | 170.8921 | 0.38055 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 69 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 473.1787 | 22.7048 | 20.8405 | 473.1787 | 22.7048 | 20.8405 | 498.4613 | 23.918 | 20.8405 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 57 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 100.0176 | 18.7561 | 5.3325 | 100.0176 | 18.7561 | 5.3325 | 105.3617 | 19.7583 | 5.3325 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 218 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 76.6538 | 71.734 | 1.0686 | 76.6538 | 71.734 | 1.0686 | 80.7496 | 75.5669 | 1.0686 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 620 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 151.314 | 204.0142 | 0.74168 | 151.314 | 204.0142 | 0.74168 | 159.3989 | 214.915 | 0.74168 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 174.1258 | 5.5939 | 31.1276 | 174.1258 | 5.5939 | 31.1276 | 183.4296 | 5.8928 | 31.1276 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 227 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 142.3168 | 74.6955 | 1.9053 | 142.3168 | 74.6955 | 1.9053 | 149.921 | 78.6866 | 1.9053 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 357 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 124.1616 | 117.4727 | 1.0569 | 124.1616 | 117.4727 | 1.0569 | 130.7958 | 123.7494 | 1.0569 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 33.3597 | 0.98717 | 33.7935 | 33.3597 | 0.98717 | 33.7935 | 35.1422 | 1.0399 | 33.7935 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 384 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 180.2727 | 126.3572 | 1.4267 | 180.2727 | 126.3572 | 1.4267 | 189.905 | 133.1086 | 1.4267 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 29 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 5.0165 | 9.5426 | 0.52569 | 5.0165 | 9.5426 | 0.52569 | 5.2845 | 10.0525 | 0.52569 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 30 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 96.5805 | 9.8717 | 9.7836 | 96.5805 | 9.8717 | 9.7836 | 101.7409 | 10.3991 | 9.7836 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 27 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 28.7981 | 8.8845 | 3.2414 | 28.7981 | 8.8845 | 3.2414 | 30.3368 | 9.3592 | 3.2414 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 56 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 210.4643 | 18.4271 | 11.4215 | 210.4643 | 18.4271 | 11.4215 | 221.7097 | 19.4117 | 11.4215 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 34 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 106.3059 | 11.1879 | 9.5019 | 106.3059 | 11.1879 | 9.5019 | 111.9859 | 11.7857 | 9.5019 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 17 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 452.3048 | 5.5939 | 80.8562 | 452.3048 | 5.5939 | 80.8562 | 476.4721 | 5.8928 | 80.8562 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 120 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 61.0795 | 39.4866 | 1.5468 | 61.0795 | 39.4866 | 1.5468 | 64.343 | 41.5964 | 1.5468 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 822 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 337.9327 | 270.4834 | 1.2494 | 337.9327 | 270.4834 | 1.2494 | 355.9889 | 284.9357 | 1.2494 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 245 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3711.5659 | 80.6185 | 46.0386 | 3711.5659 | 80.6185 | 46.0386 | 3909.88 | 84.9261 | 46.0386 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 169.657 | 2.9615 | 57.2876 | 169.657 | 2.9615 | 57.2876 | 178.722 | 3.1197 | 57.2876 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 107 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2122.0228 | 35.2089 | 60.2695 | 2122.0228 | 35.2089 | 60.2695 | 2235.4054 | 37.0902 | 60.2695 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.8025 | 0.65811 | 17.9339 | 11.8025 | 0.65811 | 17.9339 | 12.4331 | 0.69327 | 17.9339 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 511 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 336.8429 | 168.1472 | 2.0033 | 336.8429 | 168.1472 | 2.0033 | 354.8409 | 177.1315 | 2.0033 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 14 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 229.1341 | 4.6068 | 49.7385 | 229.1341 | 4.6068 | 49.7385 | 241.3771 | 4.8529 | 49.7385 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 600 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 765.8108 | 197.4331 | 3.8788 | 765.8108 | 197.4331 | 3.8788 | 806.7292 | 207.9822 | 3.8788 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2026 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 3 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.80647 | 0.98717 | 0.81696 | 0.80647 | 0.98717 | 0.81696 | 0.84957 | 1.0399 | 0.81696 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 349 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 89.723 | 114.8403 | 0.78129 | 89.723 | 114.8403 | 0.78129 | 94.517 | 120.9763 | 0.78129 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 470 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 296.4305 | 154.6559 | 1.9167 | 296.4305 | 154.6559 | 1.9167 | 312.2692 | 162.9194 | 1.9167 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 585 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 89.1348 | 192.4973 | 0.46304 | 89.1348 | 192.4973 | 0.46304 | 93.8974 | 202.7827 | 0.46304 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 226 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 20.0009 | 74.3665 | 0.26895 | 20.0009 | 74.3665 | 0.26895 | 21.0696 | 78.34 | 0.26895 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 70 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 36.5689 | 23.0339 | 1.5876 | 36.5689 | 23.0339 | 1.5876 | 38.5229 | 24.2646 | 1.5876 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 328 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 160.2048 | 107.9301 | 1.4843 | 160.2048 | 107.9301 | 1.4843 | 168.7647 | 113.697 | 1.4843 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 3 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.3389 | 0.98717 | 5.4083 | 5.3389 | 0.98717 | 5.4083 | 5.6242 | 1.0399 | 5.4083 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 32 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.5521 | 10.5298 | 0.71721 | 7.5521 | 10.5298 | 0.71721 | 7.9556 | 11.0924 | 0.71721 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 364 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 126.7631 | 119.7761 | 1.0583 | 126.7631 | 119.7761 | 1.0583 | 133.5362 | 126.1759 | 1.0583 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 1452 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 239.6048 | 477.7881 | 0.50149 | 239.6048 | 477.7881 | 0.50149 | 252.4072 | 503.317 | 0.50149 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 4 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0024413 | 1.3162 | 0.0018548 | 0.0024413 | 1.3162 | 0.0018548 | 0.0025718 | 1.3865 | 0.0018548 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 743 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 141.6855 | 244.488 | 0.57952 | 141.6855 | 244.488 | 0.57952 | 149.2559 | 257.5513 | 0.57952 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 182 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 33.1256 | 59.888 | 0.55313 | 33.1256 | 59.888 | 0.55313 | 34.8956 | 63.0879 | 0.55313 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 279 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 20.0778 | 91.8064 | 0.2187 | 20.0778 | 91.8064 | 0.2187 | 21.1505 | 96.7117 | 0.2187 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 309 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 94.985 | 101.678 | 0.93417 | 94.985 | 101.678 | 0.93417 | 100.0601 | 107.1108 | 0.93417 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 875 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 231.9683 | 287.9233 | 0.80566 | 231.9683 | 287.9233 | 0.80566 | 244.3627 | 303.3074 | 0.80566 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 106 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 183.0917 | 34.8798 | 5.2492 | 183.0917 | 34.8798 | 5.2492 | 192.8746 | 36.7435 | 5.2492 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 399 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1099.8308 | 131.293 | 8.3769 | 1099.8308 | 131.293 | 8.3769 | 1158.5963 | 138.3082 | 8.3769 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 390 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 453.1135 | 128.3315 | 3.5308 | 453.1135 | 128.3315 | 3.5308 | 477.324 | 135.1884 | 3.5308 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 104 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 129.6779 | 34.2217 | 3.7893 | 129.6779 | 34.2217 | 3.7893 | 136.6068 | 36.0503 | 3.7893 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 19 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 105.2609 | 6.252 | 16.8362 | 105.2609 | 6.252 | 16.8362 | 110.8851 | 6.5861 | 16.8362 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 249 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 246.9272 | 81.9347 | 3.0137 | 246.9272 | 81.9347 | 3.0137 | 260.1209 | 86.3126 | 3.0137 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 365 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 985.7421 | 120.1051 | 8.2073 | 985.7421 | 120.1051 | 8.2073 | 1038.4116 | 126.5225 | 8.2073 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 129 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 320.0792 | 42.4481 | 7.5405 | 320.0792 | 42.4481 | 7.5405 | 337.1815 | 44.7162 | 7.5405 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 48 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 170.5666 | 15.7946 | 10.799 | 170.5666 | 15.7946 | 10.799 | 179.6802 | 16.6386 | 10.799 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 135 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1325.1737 | 44.4224 | 29.8312 | 1325.1737 | 44.4224 | 29.8312 | 1395.9796 | 46.796 | 29.8312 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 345 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1264.5743 | 113.524 | 11.1393 | 1264.5743 | 113.524 | 11.1393 | 1332.1422 | 119.5898 | 11.1393 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 37 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 22.199 | 12.175 | 1.8233 | 22.199 | 12.175 | 1.8233 | 23.3851 | 12.8256 | 1.8233 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 23 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 118.0741 | 7.5683 | 15.6012 | 118.0741 | 7.5683 | 15.6012 | 124.383 | 7.9727 | 15.6012 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 479 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1445.8524 | 157.6174 | 9.1732 | 1445.8524 | 157.6174 | 9.1732 | 1523.1063 | 166.0391 | 9.1732 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 422 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 3060.5719 | 138.8613 | 22.0405 | 3060.5719 | 138.8613 | 22.0405 | 3224.1024 | 146.2808 | 22.0405 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 399 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 39.8446 | 131.293 | 0.30348 | 39.8446 | 131.293 | 0.30348 | 41.9736 | 138.3082 | 0.30348 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 55 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 73.856 | 18.098 | 4.0809 | 73.856 | 18.098 | 4.0809 | 77.8022 | 19.065 | 4.0809 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 233 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 50.8518 | 76.6699 | 0.66326 | 50.8518 | 76.6699 | 0.66326 | 53.5689 | 80.7664 | 0.66326 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 327 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 290.7937 | 107.601 | 2.7025 | 290.7937 | 107.601 | 2.7025 | 306.3312 | 113.3503 | 2.7025 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 303 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 33.6771 | 99.7037 | 0.33777 | 33.6771 | 99.7037 | 0.33777 | 35.4765 | 105.031 | 0.33777 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 31 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 17.5537 | 10.2007 | 1.7208 | 17.5537 | 10.2007 | 1.7208 | 18.4916 | 10.7457 | 1.7208 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 123 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 54.8903 | 40.4738 | 1.3562 | 54.8903 | 40.4738 | 1.3562 | 57.8231 | 42.6364 | 1.3562 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 24 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 36.8826 | 7.8973 | 4.6703 | 36.8826 | 7.8973 | 4.6703 | 38.8532 | 8.3193 | 4.6703 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 21 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 17.2331 | 6.9102 | 2.4939 | 17.2331 | 6.9102 | 2.4939 | 18.1539 | 7.2794 | 2.4939 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 485 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 205.1652 | 159.5918 | 1.2856 | 205.1652 | 159.5918 | 1.2856 | 216.1274 | 168.119 | 1.2856 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 263 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 175.0719 | 86.5415 | 2.023 | 175.0719 | 86.5415 | 2.023 | 184.4262 | 91.1655 | 2.023 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 164 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 167.585 | 53.965 | 3.1054 | 167.585 | 53.965 | 3.1054 | 176.5393 | 56.8485 | 3.1054 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 101 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 29.9106 | 33.2346 | 0.89998 | 29.9106 | 33.2346 | 0.89998 | 31.5088 | 35.0103 | 0.89998 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 389 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 151.2085 | 128.0025 | 1.1813 | 151.2085 | 128.0025 | 1.1813 | 159.2877 | 134.8418 | 1.1813 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 74 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 59.4254 | 24.3501 | 2.4405 | 59.4254 | 24.3501 | 2.4405 | 62.6005 | 25.6511 | 2.4405 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 6 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.8774 | 1.9743 | 2.4704 | 4.8774 | 1.9743 | 2.4704 | 5.138 | 2.0798 | 2.4704 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 299 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 169.8732 | 98.3875 | 1.7266 | 169.8732 | 98.3875 | 1.7266 | 178.9497 | 103.6445 | 1.7266 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 47 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 246.6292 | 15.4656 | 15.947 | 246.6292 | 15.4656 | 15.947 | 259.807 | 16.2919 | 15.947 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 101 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 83.482 | 33.2346 | 2.5119 | 83.482 | 33.2346 | 2.5119 | 87.9426 | 35.0103 | 2.5119 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 21.4326 | 0.32906 | 65.1338 | 21.4326 | 0.32906 | 65.1338 | 22.5778 | 0.34664 | 65.1338 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2026 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 2 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.9389 | 0.65811 | 2.9462 | 1.9389 | 0.65811 | 2.9462 | 2.0425 | 0.69327 | 2.9462 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 215 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 24.149 | 70.7469 | 0.34134 | 24.149 | 70.7469 | 0.34134 | 25.4394 | 74.527 | 0.34134 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 22 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.12044 | 7.2392 | 0.016638 | 0.12044 | 7.2392 | 0.016638 | 0.12688 | 7.626 | 0.016638 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2026 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 2 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 21.551 | 0.65811 | 32.7468 | 21.551 | 0.65811 | 32.7468 | 22.7025 | 0.69327 | 32.7468 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 169 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 32.9073 | 55.6103 | 0.59175 | 32.9073 | 55.6103 | 0.59175 | 34.6656 | 58.5817 | 0.59175 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 110 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 103.5189 | 36.1961 | 2.8599 | 103.5189 | 36.1961 | 2.8599 | 109.0501 | 38.1301 | 2.8599 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 294 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 214.8823 | 96.7422 | 2.2212 | 214.8823 | 96.7422 | 2.2212 | 226.3638 | 101.9113 | 2.2212 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 5 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.87392 | 1.6453 | 0.53117 | 0.87392 | 1.6453 | 0.53117 | 0.92062 | 1.7332 | 0.53117 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2026 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 13 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.3639 | 4.2777 | 0.085069 | 0.3639 | 4.2777 | 0.085069 | 0.38334 | 4.5063 | 0.085069 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 201 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.17656 | 66.1401 | 0.0026695 | 0.17656 | 66.1401 | 0.0026695 | 0.18599 | 69.674 | 0.0026695 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 10 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.014446 | 3.2906 | 0.00439 | 0.014446 | 3.2906 | 0.00439 | 0.015217 | 3.4664 | 0.00439 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2026 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 149 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 9.86 | 49.0292 | 0.2011 | 9.86 | 49.0292 | 0.2011 | 10.3868 | 51.6489 | 0.2011 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 2 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 14.1762 | 0.65811 | 21.5408 | 14.1762 | 0.65811 | 21.5408 | 14.9337 | 0.69327 | 21.5408 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 975 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 162.4058 | 320.8288 | 0.50621 | 162.4058 | 320.8288 | 0.50621 | 171.0834 | 337.9711 | 0.50621 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 827 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 642.8121 | 272.1286 | 2.3622 | 642.8121 | 272.1286 | 2.3622 | 677.1585 | 286.6688 | 2.3622 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 961 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 255.1218 | 316.222 | 0.80678 | 255.1218 | 316.222 | 0.80678 | 268.7533 | 333.1182 | 0.80678 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 397 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 633.9221 | 130.6349 | 4.8526 | 633.9221 | 130.6349 | 4.8526 | 667.7935 | 137.6149 | 4.8526 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 538 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 522.9766 | 177.0317 | 2.9541 | 522.9766 | 177.0317 | 2.9541 | 550.9199 | 186.4907 | 2.9541 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 546 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1102.1556 | 179.6641 | 6.1345 | 1102.1556 | 179.6641 | 6.1345 | 1161.0453 | 189.2638 | 6.1345 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 92 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 430.6267 | 30.2731 | 14.2247 | 430.6267 | 30.2731 | 14.2247 | 453.6357 | 31.8906 | 14.2247 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 488 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 873.3342 | 160.5789 | 5.4387 | 873.3342 | 160.5789 | 5.4387 | 919.9977 | 169.1589 | 5.4387 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 319 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 424.5109 | 104.9686 | 4.0442 | 424.5109 | 104.9686 | 4.0442 | 447.1931 | 110.5772 | 4.0442 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 106 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 117.9754 | 34.8798 | 3.3823 | 117.9754 | 34.8798 | 3.3823 | 124.279 | 36.7435 | 3.3823 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 24 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 104.5514 | 7.8973 | 13.2388 | 104.5514 | 7.8973 | 13.2388 | 110.1378 | 8.3193 | 13.2388 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 55 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 83.4003 | 18.098 | 4.6082 | 83.4003 | 18.098 | 4.6082 | 87.8565 | 19.065 | 4.6082 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 46 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 202.8579 | 15.1365 | 13.4019 | 202.8579 | 15.1365 | 13.4019 | 213.6968 | 15.9453 | 13.4019 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 13 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.8008 | 4.2777 | 3.2262 | 13.8008 | 4.2777 | 3.2262 | 14.5382 | 4.5063 | 3.2262 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 139 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 635.4631 | 45.7387 | 13.8933 | 635.4631 | 45.7387 | 13.8933 | 669.4168 | 48.1825 | 13.8933 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 465 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 960.4166 | 153.0107 | 6.2768 | 960.4166 | 153.0107 | 6.2768 | 1011.733 | 161.1862 | 6.2768 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 102 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 152.7457 | 33.5636 | 4.5509 | 152.7457 | 33.5636 | 4.5509 | 160.9071 | 35.357 | 4.5509 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 276 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 348.8651 | 90.8192 | 3.8413 | 348.8651 | 90.8192 | 3.8413 | 367.5055 | 95.6718 | 3.8413 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 139 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 64.1211 | 45.7387 | 1.4019 | 64.1211 | 45.7387 | 1.4019 | 67.5471 | 48.1825 | 1.4019 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 131 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 251.9816 | 43.1062 | 5.8456 | 251.9816 | 43.1062 | 5.8456 | 265.4453 | 45.4095 | 5.8456 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 704 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 739.2025 | 231.6548 | 3.191 | 739.2025 | 231.6548 | 3.191 | 778.6991 | 244.0325 | 3.191 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 561 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 418.7535 | 184.6 | 2.2684 | 418.7535 | 184.6 | 2.2684 | 441.128 | 194.4634 | 2.2684 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 14 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 58.5262 | 4.6068 | 12.7044 | 58.5262 | 4.6068 | 12.7044 | 61.6533 | 4.8529 | 12.7044 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 7 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 239.9918 | 2.3034 | 104.1908 | 239.9918 | 2.3034 | 104.1908 | 252.8149 | 2.4265 | 104.1908 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 1 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 39.6291 | 0.32906 | 120.433 | 39.6291 | 0.32906 | 120.433 | 41.7465 | 0.34664 | 120.433 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 194 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 786.9145 | 63.8367 | 12.327 | 786.9145 | 63.8367 | 12.327 | 828.9604 | 67.2476 | 12.327 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 329 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 814.528 | 108.2592 | 7.5239 | 814.528 | 108.2592 | 7.5239 | 858.0494 | 114.0436 | 7.5239 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 435 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 478.0277 | 143.139 | 3.3396 | 478.0277 | 143.139 | 3.3396 | 503.5694 | 150.7871 | 3.3396 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 248 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 543.0092 | 81.6057 | 6.6541 | 543.0092 | 81.6057 | 6.6541 | 572.0229 | 85.966 | 6.6541 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 11 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 27.5211 | 3.6196 | 7.6033 | 27.5211 | 3.6196 | 7.6033 | 28.9916 | 3.813 | 7.6033 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 36 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 63.2779 | 11.846 | 5.3417 | 63.2779 | 11.846 | 5.3417 | 66.6589 | 12.4789 | 5.3417 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 252 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1750.5765 | 82.9219 | 21.1111 | 1750.5765 | 82.9219 | 21.1111 | 1844.1122 | 87.3525 | 21.1111 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 14 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 61.1593 | 4.6068 | 13.276 | 61.1593 | 4.6068 | 13.276 | 64.4271 | 4.8529 | 13.276 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 22 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 8.2042 | 7.2392 | 1.1333 | 8.2042 | 7.2392 | 1.1333 | 8.6426 | 7.626 | 1.1333 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 590 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 130.6179 | 194.1426 | 0.67279 | 130.6179 | 194.1426 | 0.67279 | 137.597 | 204.5159 | 0.67279 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 455 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 85.8122 | 149.7201 | 0.57315 | 85.8122 | 149.7201 | 0.57315 | 90.3972 | 157.7199 | 0.57315 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 839 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 296.1766 | 276.0773 | 1.0728 | 296.1766 | 276.0773 | 1.0728 | 312.0017 | 290.8285 | 1.0728 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 3 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 61.1985 | 0.98717 | 61.9942 | 61.1985 | 0.98717 | 61.9942 | 64.4684 | 1.0399 | 61.9942 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2026 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.3205 | 0.32906 | 10.091 | 3.3205 | 0.32906 | 10.091 | 3.4979 | 0.34664 | 10.091 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 91 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 161.888 | 29.944 | 5.4064 | 161.888 | 29.944 | 5.4064 | 170.5379 | 31.544 | 5.4064 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 3 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 25.1077 | 0.98717 | 25.4341 | 25.1077 | 0.98717 | 25.4341 | 26.4492 | 1.0399 | 25.4341 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 68 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 219.8189 | 22.3758 | 9.824 | 219.8189 | 22.3758 | 9.824 | 231.5641 | 23.5713 | 9.824 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 20 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 248.9663 | 6.5811 | 37.8305 | 248.9663 | 6.5811 | 37.8305 | 262.269 | 6.9327 | 37.8305 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 358 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 83.2547 | 117.8018 | 0.70674 | 83.2547 | 117.8018 | 0.70674 | 87.7031 | 124.0961 | 0.70674 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 28 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.072621 | 9.2135 | 0.007882 | 0.072621 | 9.2135 | 0.007882 | 0.076501 | 9.7058 | 0.007882 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 37 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 34.2033 | 12.175 | 2.8093 | 34.2033 | 12.175 | 2.8093 | 36.0308 | 12.8256 | 2.8093 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 17 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 14.3975 | 5.5939 | 2.5738 | 14.3975 | 5.5939 | 2.5738 | 15.1667 | 5.8928 | 2.5738 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 558 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 483.4663 | 183.6128 | 2.6331 | 483.4663 | 183.6128 | 2.6331 | 509.2986 | 193.4235 | 2.6331 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 9 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 25.691 | 2.9615 | 8.675 | 25.691 | 2.9615 | 8.675 | 27.0637 | 3.1197 | 8.675 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 29 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 20.4688 | 9.5426 | 2.145 | 20.4688 | 9.5426 | 2.145 | 21.5625 | 10.0525 | 2.145 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 7 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.4049 | 2.3034 | 1.4782 | 3.4049 | 2.3034 | 1.4782 | 3.5868 | 2.4265 | 1.4782 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 16 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 157.4433 | 5.2649 | 29.9044 | 157.4433 | 5.2649 | 29.9044 | 165.8557 | 5.5462 | 29.9044 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 219 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 19.0725 | 72.0631 | 0.26466 | 19.0725 | 72.0631 | 0.26466 | 20.0916 | 75.9135 | 0.26466 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 202 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 431.9104 | 66.4691 | 6.4979 | 431.9104 | 66.4691 | 6.4979 | 454.988 | 70.0207 | 6.4979 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 55 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 329.0418 | 18.098 | 18.1811 | 329.0418 | 18.098 | 18.1811 | 346.623 | 19.065 | 18.1811 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 33 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 67.1788 | 10.8588 | 6.1866 | 67.1788 | 10.8588 | 6.1866 | 70.7683 | 11.439 | 6.1866 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 211 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 479.8394 | 69.4306 | 6.9111 | 479.8394 | 69.4306 | 6.9111 | 505.4779 | 73.1404 | 6.9111 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 16 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 70.6818 | 5.2649 | 13.4251 | 70.6818 | 5.2649 | 13.4251 | 74.4584 | 5.5462 | 13.4251 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 52 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 152.0596 | 17.1109 | 8.8867 | 152.0596 | 17.1109 | 8.8867 | 160.1843 | 18.0251 | 8.8867 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 29 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 183.9604 | 9.5426 | 19.2778 | 183.9604 | 9.5426 | 19.2778 | 193.7897 | 10.0525 | 19.2778 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 2 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 62.0703 | 0.65811 | 94.3159 | 62.0703 | 0.65811 | 94.3159 | 65.3868 | 0.69327 | 94.3159 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 1 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 55.7189 | 0.32906 | 169.33 | 55.7189 | 0.32906 | 169.33 | 58.6961 | 0.34664 | 169.33 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 56 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 113.3698 | 18.4271 | 6.1523 | 113.3698 | 18.4271 | 6.1523 | 119.4273 | 19.4117 | 6.1523 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 60 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 55.7504 | 19.7433 | 2.8238 | 55.7504 | 19.7433 | 2.8238 | 58.7292 | 20.7982 | 2.8238 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 73 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 18.7295 | 24.021 | 0.77971 | 18.7295 | 24.021 | 0.77971 | 19.7302 | 25.3045 | 0.77971 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 79 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 23.5661 | 25.9954 | 0.90655 | 23.5661 | 25.9954 | 0.90655 | 24.8252 | 27.3843 | 0.90655 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 243 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 394.1517 | 79.9604 | 4.9293 | 394.1517 | 79.9604 | 4.9293 | 415.2118 | 84.2328 | 4.9293 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 119 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 249.0215 | 39.1576 | 6.3595 | 249.0215 | 39.1576 | 6.3595 | 262.327 | 41.2498 | 6.3595 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 495 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 287.5688 | 162.8823 | 1.7655 | 287.5688 | 162.8823 | 1.7655 | 302.934 | 171.5853 | 1.7655 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 14 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 68.4792 | 4.6068 | 14.8649 | 68.4792 | 4.6068 | 14.8649 | 72.1381 | 4.8529 | 14.8649 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 10 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 28.5516 | 3.2906 | 8.6769 | 28.5516 | 3.2906 | 8.6769 | 30.0772 | 3.4664 | 8.6769 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 61 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 245.3601 | 20.0724 | 12.2238 | 245.3601 | 20.0724 | 12.2238 | 258.47 | 21.1449 | 12.2238 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 125 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 104.6722 | 41.1319 | 2.5448 | 104.6722 | 41.1319 | 2.5448 | 110.265 | 43.3296 | 2.5448 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2026 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 49 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 13.6065 | 16.1237 | 0.84388 | 13.6065 | 16.1237 | 0.84388 | 14.3335 | 16.9852 | 0.84388 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 257 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 387.696 | 84.5672 | 4.5845 | 387.696 | 84.5672 | 4.5845 | 408.4111 | 89.0857 | 4.5845 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 62 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 34.7023 | 20.4014 | 1.701 | 34.7023 | 20.4014 | 1.701 | 36.5565 | 21.4915 | 1.701 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 61 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 50.9272 | 20.0724 | 2.5372 | 50.9272 | 20.0724 | 2.5372 | 53.6483 | 21.1449 | 2.5372 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 27 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 6.473 | 8.8845 | 0.72857 | 6.473 | 8.8845 | 0.72857 | 6.8189 | 9.3592 | 0.72857 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 4 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 8.5432 | 1.3162 | 6.4907 | 8.5432 | 1.3162 | 6.4907 | 8.9997 | 1.3865 | 6.4907 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 175 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 133.2483 | 57.5847 | 2.314 | 133.2483 | 57.5847 | 2.314 | 140.368 | 60.6615 | 2.314 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 14 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.7918 | 4.6068 | 0.38894 | 1.7918 | 4.6068 | 0.38894 | 1.8875 | 4.8529 | 0.38894 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 287 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 162.0011 | 94.4388 | 1.7154 | 162.0011 | 94.4388 | 1.7154 | 170.6571 | 99.4848 | 1.7154 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 15 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 64.4441 | 4.9358 | 13.0564 | 64.4441 | 4.9358 | 13.0564 | 67.8874 | 5.1996 | 13.0564 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 213 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 244.4546 | 70.0888 | 3.4878 | 244.4546 | 70.0888 | 3.4878 | 257.5161 | 73.8337 | 3.4878 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 471 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 785.4976 | 154.985 | 5.0682 | 785.4976 | 154.985 | 5.0682 | 827.4678 | 163.266 | 5.0682 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 15 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 190.7281 | 4.9358 | 38.6416 | 190.7281 | 4.9358 | 38.6416 | 200.9189 | 5.1996 | 38.6416 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 90 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 9.6013 | 29.615 | 0.3242 | 9.6013 | 29.615 | 0.3242 | 10.1143 | 31.1973 | 0.3242 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 31 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 34.4739 | 10.2007 | 3.3796 | 34.4739 | 10.2007 | 3.3796 | 36.3159 | 10.7457 | 3.3796 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 779 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 136.9236 | 256.334 | 0.53416 | 136.9236 | 256.334 | 0.53416 | 144.2396 | 270.0303 | 0.53416 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 148 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 68.4112 | 48.7002 | 1.4047 | 68.4112 | 48.7002 | 1.4047 | 72.0666 | 51.3023 | 1.4047 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 400 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 120.5219 | 131.6221 | 0.91567 | 120.5219 | 131.6221 | 0.91567 | 126.9615 | 138.6548 | 0.91567 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 745 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 149.4686 | 245.1461 | 0.60971 | 149.4686 | 245.1461 | 0.60971 | 157.4549 | 258.2446 | 0.60971 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 290 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 75.7792 | 95.426 | 0.79412 | 75.7792 | 95.426 | 0.79412 | 79.8282 | 100.5247 | 0.79412 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 504 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 308.8644 | 165.8438 | 1.8624 | 308.8644 | 165.8438 | 1.8624 | 325.3674 | 174.7051 | 1.8624 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 258 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 27.3279 | 84.8962 | 0.3219 | 27.3279 | 84.8962 | 0.3219 | 28.7881 | 89.4324 | 0.3219 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 221 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 94.9689 | 72.7212 | 1.3059 | 94.9689 | 72.7212 | 1.3059 | 100.0432 | 76.6068 | 1.3059 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 63 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 9.1137 | 20.7305 | 0.43963 | 9.1137 | 20.7305 | 0.43963 | 9.6007 | 21.8381 | 0.43963 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 657 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 227.721 | 216.1893 | 1.0533 | 227.721 | 216.1893 | 1.0533 | 239.8884 | 227.7405 | 1.0533 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 231 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 94.2031 | 76.0117 | 1.2393 | 94.2031 | 76.0117 | 1.2393 | 99.2365 | 80.0732 | 1.2393 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 427 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 518.2225 | 140.5066 | 3.6882 | 518.2225 | 140.5066 | 3.6882 | 545.9119 | 148.014 | 3.6882 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 152 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 34.2027 | 50.0164 | 0.68383 | 34.2027 | 50.0164 | 0.68383 | 36.0302 | 52.6888 | 0.68383 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 356 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 391.4809 | 117.1436 | 3.3419 | 391.4809 | 117.1436 | 3.3419 | 412.3983 | 123.4028 | 3.3419 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 268 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 408.7995 | 88.1868 | 4.6356 | 408.7995 | 88.1868 | 4.6356 | 430.6423 | 92.8987 | 4.6356 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 378 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 262.0699 | 124.3829 | 2.107 | 262.0699 | 124.3829 | 2.107 | 276.0727 | 131.0288 | 2.107 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 262 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 574.459 | 86.2125 | 6.6633 | 574.459 | 86.2125 | 6.6633 | 605.1531 | 90.8189 | 6.6633 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 549 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 421.536 | 180.6513 | 2.3334 | 421.536 | 180.6513 | 2.3334 | 444.0593 | 190.3037 | 2.3334 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 29 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.2899 | 9.5426 | 0.23996 | 2.2899 | 9.5426 | 0.23996 | 2.4122 | 10.0525 | 0.23996 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 39 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.2445 | 12.8332 | 0.096972 | 1.2445 | 12.8332 | 0.096972 | 1.311 | 13.5188 | 0.096972 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 897 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 256.8342 | 295.1625 | 0.87015 | 256.8342 | 295.1625 | 0.87015 | 270.5572 | 310.9334 | 0.87015 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 111 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.6856 | 36.5251 | 0.04615 | 1.6856 | 36.5251 | 0.04615 | 1.7757 | 38.4767 | 0.04615 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 119 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 257.6241 | 39.1576 | 6.5792 | 257.6241 | 39.1576 | 6.5792 | 271.3893 | 41.2498 | 6.5792 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 253 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 533.1833 | 83.251 | 6.4045 | 533.1833 | 83.251 | 6.4045 | 561.672 | 87.6992 | 6.4045 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 241 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 640.8684 | 79.3023 | 8.0813 | 640.8684 | 79.3023 | 8.0813 | 675.1109 | 83.5395 | 8.0813 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 136 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 408.1427 | 44.7515 | 9.1202 | 408.1427 | 44.7515 | 9.1202 | 429.9503 | 47.1426 | 9.1202 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 592 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1888.0784 | 194.8007 | 9.6924 | 1888.0784 | 194.8007 | 9.6924 | 1988.961 | 205.2091 | 9.6924 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 30 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 26.6692 | 9.8717 | 2.7016 | 26.6692 | 9.8717 | 2.7016 | 28.0941 | 10.3991 | 2.7016 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2026 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | 2--5 | 1 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 7.5583 | 0 | 0 | 7.5583 | 0 | 7.2102 | 0.32906 | 21.9117 | 7.2102 | 0.32906 | 21.9117 | 7.5954 | 0.34664 | 21.9117 | 4.922% | 0.0076984 | 0.0073173 | 19947.1031 | 4677.56 | 10.2291 | 15259.3139 | 19952.9673 | 0 | 0 | 19952.9673 | 0.0002492%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 4 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 23.6499 | 1.3162 | 17.968 | 23.6499 | 1.3162 | 17.968 | 24.9135 | 1.3865 | 17.968 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 16 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.3203 | 5.2649 | 0.44071 | 2.3203 | 5.2649 | 0.44071 | 2.4442 | 5.5462 | 0.44071 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 685 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 847.0626 | 225.4028 | 3.758 | 847.0626 | 225.4028 | 3.758 | 892.3223 | 237.4464 | 3.758 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 899 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1208.2563 | 295.8206 | 4.0844 | 1208.2563 | 295.8206 | 4.0844 | 1272.8151 | 311.6267 | 4.0844 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 188 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 115.3852 | 61.8624 | 1.8652 | 115.3852 | 61.8624 | 1.8652 | 121.5504 | 65.1678 | 1.8652 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 406 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 185.1522 | 133.5964 | 1.3859 | 185.1522 | 133.5964 | 1.3859 | 195.0451 | 140.7346 | 1.3859 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 88 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 25.6177 | 28.9569 | 0.88469 | 25.6177 | 28.9569 | 0.88469 | 26.9865 | 30.5041 | 0.88469 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 132 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 71.3254 | 43.4353 | 1.6421 | 71.3254 | 43.4353 | 1.6421 | 75.1364 | 45.7561 | 1.6421 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 54 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 284.8981 | 17.769 | 16.0335 | 284.8981 | 17.769 | 16.0335 | 300.1206 | 18.7184 | 16.0335 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 293 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 713.7946 | 96.4132 | 7.4035 | 713.7946 | 96.4132 | 7.4035 | 751.9337 | 101.5647 | 7.4035 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 134 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 114.0597 | 44.0934 | 2.5868 | 114.0597 | 44.0934 | 2.5868 | 120.154 | 46.4494 | 2.5868 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 32 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 266.4366 | 10.5298 | 25.3032 | 266.4366 | 10.5298 | 25.3032 | 280.6727 | 11.0924 | 25.3032 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 150 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 491.6709 | 49.3583 | 9.9613 | 491.6709 | 49.3583 | 9.9613 | 517.9415 | 51.9956 | 9.9613 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 119 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 431.684 | 39.1576 | 11.0243 | 431.684 | 39.1576 | 11.0243 | 454.7494 | 41.2498 | 11.0243 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.83481 | 0.65811 | 1.2685 | 0.83481 | 0.65811 | 1.2685 | 0.87941 | 0.69327 | 1.2685 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 157 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 147.7158 | 51.6617 | 2.8593 | 147.7158 | 51.6617 | 2.8593 | 155.6084 | 54.422 | 2.8593 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 53 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 80.3262 | 17.4399 | 4.6059 | 80.3262 | 17.4399 | 4.6059 | 84.6182 | 18.3718 | 4.6059 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 25 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 91.3622 | 8.2264 | 11.106 | 91.3622 | 8.2264 | 11.106 | 96.2438 | 8.6659 | 11.106 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 300 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 103.6022 | 98.7166 | 1.0495 | 103.6022 | 98.7166 | 1.0495 | 109.1378 | 103.9911 | 1.0495 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 133 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 676.0489 | 43.7643 | 15.4475 | 676.0489 | 43.7643 | 15.4475 | 712.1711 | 46.1027 | 15.4475 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 9 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 338.4324 | 2.9615 | 114.2775 | 338.4324 | 2.9615 | 114.2775 | 356.5153 | 3.1197 | 114.2775 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 236 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 406.782 | 77.657 | 5.2382 | 406.782 | 77.657 | 5.2382 | 428.5169 | 81.8063 | 5.2382 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2026 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 3 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 15.2415 | 0.98717 | 15.4396 | 15.2415 | 0.98717 | 15.4396 | 16.0558 | 1.0399 | 15.4396 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 43 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 146.4383 | 14.1494 | 10.3495 | 146.4383 | 14.1494 | 10.3495 | 154.2627 | 14.9054 | 10.3495 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 109 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 577.5146 | 35.867 | 16.1016 | 577.5146 | 35.867 | 16.1016 | 608.372 | 37.7834 | 16.1016 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 129 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 96.0526 | 42.4481 | 2.2628 | 96.0526 | 42.4481 | 2.2628 | 101.1849 | 44.7162 | 2.2628 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 99 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 53.817 | 32.5765 | 1.652 | 53.817 | 32.5765 | 1.652 | 56.6925 | 34.3171 | 1.652 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 62 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 450.8352 | 20.4014 | 22.0982 | 450.8352 | 20.4014 | 22.0982 | 474.924 | 21.4915 | 22.0982 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 47 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 861.5285 | 15.4656 | 55.7061 | 861.5285 | 15.4656 | 55.7061 | 907.5611 | 16.2919 | 55.7061 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 9 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 120.3488 | 2.9615 | 40.6378 | 120.3488 | 2.9615 | 40.6378 | 126.7793 | 3.1197 | 40.6378 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 103 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 251.8011 | 33.8927 | 7.4294 | 251.8011 | 33.8927 | 7.4294 | 265.2552 | 35.7036 | 7.4294 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 226 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 861.4981 | 74.3665 | 11.5845 | 861.4981 | 74.3665 | 11.5845 | 907.5291 | 78.34 | 11.5845 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 5 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 139.1767 | 1.6453 | 84.5917 | 139.1767 | 1.6453 | 84.5917 | 146.6131 | 1.7332 | 84.5917 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 210 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 936.1138 | 69.1016 | 13.5469 | 936.1138 | 69.1016 | 13.5469 | 986.1317 | 72.7938 | 13.5469 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 6 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.973 | 1.9743 | 3.0253 | 5.973 | 1.9743 | 3.0253 | 6.2921 | 2.0798 | 3.0253 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 27 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.57934 | 8.8845 | 0.065208 | 0.57934 | 8.8845 | 0.065208 | 0.61029 | 9.3592 | 0.065208 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2026 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 20 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 6.5841 | 6.5811 | 1.0005 | 6.5841 | 6.5811 | 1.0005 | 6.9359 | 6.9327 | 1.0005 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 7 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.31399 | 2.3034 | 0.13632 | 0.31399 | 2.3034 | 0.13632 | 0.33077 | 2.4265 | 0.13632 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 4 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 15.5039 | 1.3162 | 11.7791 | 15.5039 | 1.3162 | 11.7791 | 16.3322 | 1.3865 | 11.7791 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 95 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.6148 | 31.2602 | 0.33956 | 10.6148 | 31.2602 | 0.33956 | 11.1819 | 32.9305 | 0.33956 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 381 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 405.8445 | 125.37 | 3.2372 | 405.8445 | 125.37 | 3.2372 | 427.5294 | 132.0687 | 3.2372 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 124 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 389.022 | 40.8028 | 9.5342 | 389.022 | 40.8028 | 9.5342 | 409.808 | 42.983 | 9.5342 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.9848 | 0.32906 | 36.4218 | 11.9848 | 0.32906 | 36.4218 | 12.6251 | 0.34664 | 36.4218 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 115 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 428.5491 | 37.8413 | 11.3249 | 428.5491 | 37.8413 | 11.3249 | 451.4471 | 39.8633 | 11.3249 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 618 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1267.761 | 203.3561 | 6.2342 | 1267.761 | 203.3561 | 6.2342 | 1335.4992 | 214.2217 | 6.2342 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 53 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 299.7005 | 17.4399 | 17.1847 | 299.7005 | 17.4399 | 17.1847 | 315.7139 | 18.3718 | 17.1847 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 451 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 732.0261 | 148.4039 | 4.9327 | 732.0261 | 148.4039 | 4.9327 | 771.1393 | 156.3333 | 4.9327 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 350 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 548.8338 | 115.1693 | 4.7655 | 548.8338 | 115.1693 | 4.7655 | 578.1587 | 121.323 | 4.7655 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 479 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 253.1828 | 157.6174 | 1.6063 | 253.1828 | 157.6174 | 1.6063 | 266.7107 | 166.0391 | 1.6063 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 302 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 63.5637 | 99.3747 | 0.63964 | 63.5637 | 99.3747 | 0.63964 | 66.96 | 104.6844 | 0.63964 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 118 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 369.6702 | 38.8285 | 9.5206 | 369.6702 | 38.8285 | 9.5206 | 389.4222 | 40.9032 | 9.5206 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 313 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1926.6067 | 102.9943 | 18.706 | 1926.6067 | 102.9943 | 18.706 | 2029.5479 | 108.4974 | 18.706 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 226 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 158.2696 | 74.3665 | 2.1282 | 158.2696 | 74.3665 | 2.1282 | 166.7261 | 78.34 | 2.1282 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 273 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1055.7106 | 89.8321 | 11.752 | 1055.7106 | 89.8321 | 11.752 | 1112.1187 | 94.6319 | 11.752 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 2 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 7.1363 | 0.65811 | 10.8436 | 7.1363 | 0.65811 | 10.8436 | 7.5176 | 0.69327 | 10.8436 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 71 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 38.6279 | 23.3629 | 1.6534 | 38.6279 | 23.3629 | 1.6534 | 40.6918 | 24.6112 | 1.6534 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 434 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2590.0334 | 142.8099 | 18.1362 | 2590.0334 | 142.8099 | 18.1362 | 2728.4224 | 150.4405 | 18.1362 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 1 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 269.2064 | 0.32906 | 818.1193 | 269.2064 | 0.32906 | 818.1193 | 283.5905 | 0.34664 | 818.1193 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 458 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1514.5818 | 150.7073 | 10.0498 | 1514.5818 | 150.7073 | 10.0498 | 1595.508 | 158.7598 | 10.0498 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 136 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 58.7357 | 44.7515 | 1.3125 | 58.7357 | 44.7515 | 1.3125 | 61.8741 | 47.1426 | 1.3125 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 74 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 159.7982 | 24.3501 | 6.5625 | 159.7982 | 24.3501 | 6.5625 | 168.3364 | 25.6511 | 6.5625 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 41 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 50.6581 | 13.4913 | 3.7549 | 50.6581 | 13.4913 | 3.7549 | 53.3649 | 14.2121 | 3.7549 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 93 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 72.0465 | 30.6021 | 2.3543 | 72.0465 | 30.6021 | 2.3543 | 75.8961 | 32.2372 | 2.3543 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 20.4262 | 0.65811 | 31.0377 | 20.4262 | 0.65811 | 31.0377 | 21.5176 | 0.69327 | 31.0377 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 34 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 609.9489 | 11.1879 | 54.5187 | 609.9489 | 11.1879 | 54.5187 | 642.5393 | 11.7857 | 54.5187 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 309 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 708.5447 | 101.678 | 6.9685 | 708.5447 | 101.678 | 6.9685 | 746.4032 | 107.1108 | 6.9685 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 657 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1330.4034 | 216.1893 | 6.1539 | 1330.4034 | 216.1893 | 6.1539 | 1401.4886 | 227.7405 | 6.1539 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 75 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 376.4593 | 24.6791 | 15.2542 | 376.4593 | 24.6791 | 15.2542 | 396.5741 | 25.9978 | 15.2542 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 25 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 204.4821 | 8.2264 | 24.8569 | 204.4821 | 8.2264 | 24.8569 | 215.4079 | 8.6659 | 24.8569 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 123 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 686.5258 | 40.4738 | 16.9622 | 686.5258 | 40.4738 | 16.9622 | 723.2078 | 42.6364 | 16.9622 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 319 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 526.6286 | 104.9686 | 5.017 | 526.6286 | 104.9686 | 5.017 | 554.7671 | 110.5772 | 5.017 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 88 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 373.1142 | 28.9569 | 12.8852 | 373.1142 | 28.9569 | 12.8852 | 393.0502 | 30.5041 | 12.8852 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 704 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1087.6046 | 231.6548 | 4.6949 | 1087.6046 | 231.6548 | 4.6949 | 1145.7168 | 244.0325 | 4.6949 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 407 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1054.721 | 133.9255 | 7.8754 | 1054.721 | 133.9255 | 7.8754 | 1111.0762 | 141.0813 | 7.8754 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 137 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 428.2273 | 45.0806 | 9.4992 | 428.2273 | 45.0806 | 9.4992 | 451.1081 | 47.4893 | 9.4992 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 80 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 237.9521 | 26.3244 | 9.0392 | 237.9521 | 26.3244 | 9.0392 | 250.6662 | 27.731 | 9.0392 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 48 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 405.1363 | 15.7946 | 25.6502 | 405.1363 | 15.7946 | 25.6502 | 426.7833 | 16.6386 | 25.6502 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 42 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 301.8886 | 13.8203 | 21.8438 | 301.8886 | 13.8203 | 21.8438 | 318.019 | 14.5588 | 21.8438 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 138 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 154.5294 | 45.4096 | 3.403 | 154.5294 | 45.4096 | 3.403 | 162.7862 | 47.8359 | 3.403 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 12 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 334.0803 | 3.9487 | 84.606 | 334.0803 | 3.9487 | 84.606 | 351.9307 | 4.1596 | 84.606 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 5 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 243.3088 | 1.6453 | 147.8833 | 243.3088 | 1.6453 | 147.8833 | 256.3092 | 1.7332 | 147.8833 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 17 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 19.4973 | 5.5939 | 3.4854 | 19.4973 | 5.5939 | 3.4854 | 20.539 | 5.8928 | 3.4854 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 107 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 215.6371 | 35.2089 | 6.1245 | 215.6371 | 35.2089 | 6.1245 | 227.1588 | 37.0902 | 6.1245 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 82 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 157.0745 | 26.9825 | 5.8213 | 157.0745 | 26.9825 | 5.8213 | 165.4672 | 28.4242 | 5.8213 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 19 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 66.5395 | 6.252 | 10.6428 | 66.5395 | 6.252 | 10.6428 | 70.0948 | 6.5861 | 10.6428 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2026 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 53.3631 | 0.98717 | 54.0569 | 53.3631 | 0.98717 | 54.0569 | 56.2144 | 1.0399 | 54.0569 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 56 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 26.8592 | 18.4271 | 1.4576 | 26.8592 | 18.4271 | 1.4576 | 28.2944 | 19.4117 | 1.4576 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 80 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 27.1082 | 26.3244 | 1.0298 | 27.1082 | 26.3244 | 1.0298 | 28.5567 | 27.731 | 1.0298 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 571 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 251.2008 | 187.8905 | 1.337 | 251.2008 | 187.8905 | 1.337 | 264.6228 | 197.9298 | 1.337 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 1192 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 310.9519 | 392.2338 | 0.79277 | 310.9519 | 392.2338 | 0.79277 | 327.5665 | 413.1914 | 0.79277 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 132 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 67.7486 | 43.4353 | 1.5598 | 67.7486 | 43.4353 | 1.5598 | 71.3684 | 45.7561 | 1.5598 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 5.0917 | 1.3162 | 3.8684 | 5.0917 | 1.3162 | 3.8684 | 5.3637 | 1.3865 | 3.8684 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 38 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 192.305 | 12.5041 | 15.3794 | 192.305 | 12.5041 | 15.3794 | 202.5801 | 13.1722 | 15.3794 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2026 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 3 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.8558 | 0.98717 | 1.8799 | 1.8558 | 0.98717 | 1.8799 | 1.9549 | 1.0399 | 1.8799 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2026 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 1 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 4.3523 | 0.32906 | 13.2265 | 4.3523 | 0.32906 | 13.2265 | 4.5848 | 0.34664 | 13.2265 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2026 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 1 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.9791 | 0.32906 | 45.5216 | 14.9791 | 0.32906 | 45.5216 | 15.7795 | 0.34664 | 45.5216 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2026 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 58 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 18.954 | 19.0852 | 0.99313 | 18.954 | 19.0852 | 0.99313 | 19.9668 | 20.1049 | 0.99313 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2026 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 22 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 6.0182 | 7.2392 | 0.83134 | 6.0182 | 7.2392 | 0.83134 | 6.3398 | 7.626 | 0.83134 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2026 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 248 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.88582 | 81.6057 | 0.010855 | 0.88582 | 81.6057 | 0.010855 | 0.93315 | 85.966 | 0.010855 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2026 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 89 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 40.436 | 29.2859 | 1.3807 | 40.436 | 29.2859 | 1.3807 | 42.5966 | 30.8507 | 1.3807 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2026 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 36 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 10.0309 | 11.846 | 0.84678 | 10.0309 | 11.846 | 0.84678 | 10.5669 | 12.4789 | 0.84678 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 209 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 117.2051 | 68.7725 | 1.7042 | 117.2051 | 68.7725 | 1.7042 | 123.4676 | 72.4471 | 1.7042 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 277 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 75.5263 | 91.1483 | 0.82861 | 75.5263 | 91.1483 | 0.82861 | 79.5617 | 96.0185 | 0.82861 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 730 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 192.4478 | 240.2103 | 0.80116 | 192.4478 | 240.2103 | 0.80116 | 202.7306 | 253.045 | 0.80116 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 485 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 153.8343 | 159.5918 | 0.96392 | 153.8343 | 159.5918 | 0.96392 | 162.0539 | 168.119 | 0.96392 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 236 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 585.9297 | 77.657 | 7.5451 | 585.9297 | 77.657 | 7.5451 | 617.2367 | 81.8063 | 7.5451 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2026 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 2 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 99.2512 | 0.65811 | 150.8123 | 99.2512 | 0.65811 | 150.8123 | 104.5543 | 0.69327 | 150.8123 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 134 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 58.2545 | 44.0934 | 1.3212 | 58.2545 | 44.0934 | 1.3212 | 61.3671 | 46.4494 | 1.3212 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 18 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 12.3641 | 5.923 | 2.0875 | 12.3641 | 5.923 | 2.0875 | 13.0247 | 6.2395 | 2.0875 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 10 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 5.2339 | 3.2906 | 1.5906 | 5.2339 | 3.2906 | 1.5906 | 5.5136 | 3.4664 | 1.5906 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 167 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 61.1326 | 54.9522 | 1.1125 | 61.1326 | 54.9522 | 1.1125 | 64.399 | 57.8884 | 1.1125 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2026 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 45 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.602 | 14.8075 | 0.85106 | 12.602 | 14.8075 | 0.85106 | 13.2754 | 15.5987 | 0.85106 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 46 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 45.2058 | 15.1365 | 2.9865 | 45.2058 | 15.1365 | 2.9865 | 47.6212 | 15.9453 | 2.9865 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2026 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 79 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 37.8909 | 25.9954 | 1.4576 | 37.8909 | 25.9954 | 1.4576 | 39.9154 | 27.3843 | 1.4576 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2026 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 82 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.9715 | 26.9825 | 0.11013 | 2.9715 | 26.9825 | 0.11013 | 3.1302 | 28.4242 | 0.11013 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2026 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 13 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.49467 | 4.2777 | 0.11564 | 0.49467 | 4.2777 | 0.11564 | 0.5211 | 4.5063 | 0.11564 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 68.6427 | 0.32906 | 208.6054 | 68.6427 | 0.32906 | 208.6054 | 72.3104 | 0.34664 | 208.6054 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2026 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 14 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 9.8433 | 4.6068 | 2.1367 | 9.8433 | 4.6068 | 2.1367 | 10.3692 | 4.8529 | 2.1367 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2026 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 96 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.9569 | 31.5893 | 0.061948 | 1.9569 | 31.5893 | 0.061948 | 2.0615 | 33.2772 | 0.061948 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 211 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 687.0628 | 69.4306 | 9.8957 | 687.0628 | 69.4306 | 9.8957 | 723.7735 | 73.1404 | 9.8957 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2026 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 22 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 4.1171 | 7.2392 | 0.56872 | 4.1171 | 7.2392 | 0.56872 | 4.3371 | 7.626 | 0.56872 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2026 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.35337 | 0.32906 | 1.0739 | 0.35337 | 0.32906 | 1.0739 | 0.37225 | 0.34664 | 1.0739 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 376 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 526.8313 | 123.7247 | 4.2581 | 526.8313 | 123.7247 | 4.2581 | 554.9807 | 130.3355 | 4.2581 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2026 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.31849 | 0.32906 | 0.9679 | 0.31849 | 0.32906 | 0.9679 | 0.33551 | 0.34664 | 0.9679 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 184 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 277.0305 | 60.5462 | 4.5755 | 277.0305 | 60.5462 | 4.5755 | 291.8326 | 63.7812 | 4.5755 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 14 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.6787 | 4.6068 | 1.6668 | 7.6787 | 4.6068 | 1.6668 | 8.089 | 4.8529 | 1.6668 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2026 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 2 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.5364 | 0.65811 | 6.893 | 4.5364 | 0.65811 | 6.893 | 4.7787 | 0.69327 | 6.893 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2026 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 40 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 50.3341 | 13.1622 | 3.8241 | 50.3341 | 13.1622 | 3.8241 | 53.0235 | 13.8655 | 3.8241 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 56 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 312.1007 | 18.4271 | 16.9371 | 312.1007 | 18.4271 | 16.9371 | 328.7766 | 19.4117 | 16.9371 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2026 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.86782 | 0.98717 | 0.8791 | 0.86782 | 0.98717 | 0.8791 | 0.91419 | 1.0399 | 0.8791 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2026 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 1 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.081643 | 0.32906 | 0.24811 | 0.081643 | 0.32906 | 0.24811 | 0.086005 | 0.34664 | 0.24811 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2026 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 11 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.097401 | 3.6196 | 0.026909 | 0.097401 | 3.6196 | 0.026909 | 0.10261 | 3.813 | 0.026909 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2026 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 277 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 45.4 | 91.1483 | 0.49809 | 45.4 | 91.1483 | 0.49809 | 47.8258 | 96.0185 | 0.49809 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2026 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 87 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 5.3672 | 28.6278 | 0.18748 | 5.3672 | 28.6278 | 0.18748 | 5.654 | 30.1574 | 0.18748 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 12 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 21.4215 | 3.9487 | 5.425 | 21.4215 | 3.9487 | 5.425 | 22.5661 | 4.1596 | 5.425 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 8 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.9468 | 2.6324 | 0.73952 | 1.9468 | 2.6324 | 0.73952 | 2.0508 | 2.7731 | 0.73952 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 56 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.1512 | 18.4271 | 0.17101 | 3.1512 | 18.4271 | 0.17101 | 3.3196 | 19.4117 | 0.17101 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2026 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 45 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 42.7961 | 14.8075 | 2.8902 | 42.7961 | 14.8075 | 2.8902 | 45.0828 | 15.5987 | 2.8902 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2026 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 20 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 15.4569 | 6.5811 | 2.3487 | 15.4569 | 6.5811 | 2.3487 | 16.2828 | 6.9327 | 2.3487 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 375 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 203.7535 | 123.3957 | 1.6512 | 203.7535 | 123.3957 | 1.6512 | 214.6403 | 129.9889 | 1.6512 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2026 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 47 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.4094 | 15.4656 | 0.15579 | 2.4094 | 15.4656 | 0.15579 | 2.5382 | 16.2919 | 0.15579 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 23 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 384.6902 | 7.5683 | 50.8294 | 384.6902 | 7.5683 | 50.8294 | 405.2447 | 7.9727 | 50.8294 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2026 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 104 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 2.0022 | 34.2217 | 0.058507 | 2.0022 | 34.2217 | 0.058507 | 2.1092 | 36.0503 | 0.058507 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 26 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 129.2749 | 8.5554 | 15.1103 | 129.2749 | 8.5554 | 15.1103 | 136.1822 | 9.0126 | 15.1103 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 89 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.8993 | 29.2859 | 0.50875 | 14.8993 | 29.2859 | 0.50875 | 15.6954 | 30.8507 | 0.50875 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2026 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 2 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.8484 | 0.65811 | 18.0037 | 11.8484 | 0.65811 | 18.0037 | 12.4815 | 0.69327 | 18.0037 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 34 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 538.3214 | 11.1879 | 48.1165 | 538.3214 | 11.1879 | 48.1165 | 567.0846 | 11.7857 | 48.1165 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 36 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 61.292 | 11.846 | 5.1741 | 61.292 | 11.846 | 5.1741 | 64.5669 | 12.4789 | 5.1741 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 341 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 18.2584 | 112.2078 | 0.16272 | 18.2584 | 112.2078 | 0.16272 | 19.234 | 118.2032 | 0.16272 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2026 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 23 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 6.2466 | 7.5683 | 0.82536 | 6.2466 | 7.5683 | 0.82536 | 6.5803 | 7.9727 | 0.82536 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1705 | 0.65811 | 1.7786 | 1.1705 | 0.65811 | 1.7786 | 1.2331 | 0.69327 | 1.7786 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2026 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 161 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 6.0436 | 52.9779 | 0.11408 | 6.0436 | 52.9779 | 0.11408 | 6.3665 | 55.8086 | 0.11408 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2026 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 154 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 45.8593 | 50.6745 | 0.90498 | 45.8593 | 50.6745 | 0.90498 | 48.3097 | 53.3821 | 0.90498 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 126 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 70.7701 | 41.461 | 1.7069 | 70.7701 | 41.461 | 1.7069 | 74.5514 | 43.6763 | 1.7069 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 97 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 238.2603 | 31.9184 | 7.4647 | 238.2603 | 31.9184 | 7.4647 | 250.9909 | 33.6238 | 7.4647 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2026 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 10 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 29.8334 | 3.2906 | 9.0664 | 29.8334 | 3.2906 | 9.0664 | 31.4275 | 3.4664 | 9.0664 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 593 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 323.2915 | 195.1297 | 1.6568 | 323.2915 | 195.1297 | 1.6568 | 340.5654 | 205.5558 | 1.6568 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 510 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 135.4211 | 167.8181 | 0.80695 | 135.4211 | 167.8181 | 0.80695 | 142.6568 | 176.7849 | 0.80695 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 214 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 488.2028 | 70.4178 | 6.9329 | 488.2028 | 70.4178 | 6.9329 | 514.2881 | 74.1803 | 6.9329 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 170 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 242.2939 | 55.9394 | 4.3314 | 242.2939 | 55.9394 | 4.3314 | 255.24 | 58.9283 | 4.3314 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 44 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 30.0665 | 14.4784 | 2.0766 | 30.0665 | 14.4784 | 2.0766 | 31.673 | 15.252 | 2.0766 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2026 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 3 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.4032 | 0.98717 | 1.4215 | 1.4032 | 0.98717 | 1.4215 | 1.4782 | 1.0399 | 1.4215 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 182 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 175.0725 | 59.888 | 2.9233 | 175.0725 | 59.888 | 2.9233 | 184.4269 | 63.0879 | 2.9233 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 316 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 148.7546 | 103.9814 | 1.4306 | 148.7546 | 103.9814 | 1.4306 | 156.7028 | 109.5373 | 1.4306 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2026 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 22 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.089086 | 7.2392 | 0.012306 | 0.089086 | 7.2392 | 0.012306 | 0.093845 | 7.626 | 0.012306 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 375 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 76.8984 | 123.3957 | 0.62319 | 76.8984 | 123.3957 | 0.62319 | 81.0071 | 129.9889 | 0.62319 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 113 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 167.1394 | 37.1832 | 4.495 | 167.1394 | 37.1832 | 4.495 | 176.0699 | 39.17 | 4.495 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 254 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 438.0272 | 83.58 | 5.2408 | 438.0272 | 83.58 | 5.2408 | 461.4316 | 88.0458 | 5.2408 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 570 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 318.8395 | 187.5615 | 1.6999 | 318.8395 | 187.5615 | 1.6999 | 335.8755 | 197.5831 | 1.6999 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 73 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 278.8709 | 24.021 | 11.6094 | 278.8709 | 24.021 | 11.6094 | 293.7714 | 25.3045 | 11.6094 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 239 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 177.6968 | 78.6442 | 2.2595 | 177.6968 | 78.6442 | 2.2595 | 187.1914 | 82.8463 | 2.2595 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 5 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.2263 | 1.5695 | 3.33 | 5.2263 | 1.5695 | 3.33 | 5.7997 | 1.7417 | 3.33 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 34 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 18.2693 | 10.6725 | 1.7118 | 18.2693 | 10.6725 | 1.7118 | 20.2737 | 11.8434 | 1.7118 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 620 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 173.8523 | 194.6157 | 0.89331 | 173.8523 | 194.6157 | 0.89331 | 192.927 | 215.9685 | 0.89331 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 510 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1568.061 | 160.0871 | 9.795 | 1568.061 | 160.0871 | 9.795 | 1740.105 | 177.6515 | 9.795 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 72 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 312.0217 | 22.6005 | 13.8059 | 312.0217 | 22.6005 | 13.8059 | 346.256 | 25.0802 | 13.8059 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 230 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 845.436 | 72.1961 | 11.7103 | 845.436 | 72.1961 | 11.7103 | 938.1953 | 80.1173 | 11.7103 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 99 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 225.6484 | 31.0757 | 7.2612 | 225.6484 | 31.0757 | 7.2612 | 250.406 | 34.4853 | 7.2612 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 32 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 62.197 | 10.0447 | 6.192 | 62.197 | 10.0447 | 6.192 | 69.0211 | 11.1468 | 6.192 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 20 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 35.6381 | 6.2779 | 5.6767 | 35.6381 | 6.2779 | 5.6767 | 39.5482 | 6.9667 | 5.6767 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 145 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 439.7915 | 45.515 | 9.6626 | 439.7915 | 45.515 | 9.6626 | 488.0444 | 50.5088 | 9.6626 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 5 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 31.0484 | 1.5695 | 19.7826 | 31.0484 | 1.5695 | 19.7826 | 34.4549 | 1.7417 | 19.7826 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 57 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 226.5547 | 17.8921 | 12.6623 | 226.5547 | 17.8921 | 12.6623 | 251.4117 | 19.8552 | 12.6623 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 198 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 129.1894 | 62.1515 | 2.0786 | 129.1894 | 62.1515 | 2.0786 | 143.3638 | 68.9706 | 2.0786 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 886 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 409.4082 | 278.1121 | 1.4721 | 409.4082 | 278.1121 | 1.4721 | 454.3275 | 308.6259 | 1.4721 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 587 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 165.5538 | 184.2571 | 0.89849 | 165.5538 | 184.2571 | 0.89849 | 183.718 | 204.4734 | 0.89849 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 101 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 23.1241 | 31.7035 | 0.72938 | 23.1241 | 31.7035 | 0.72938 | 25.6612 | 35.182 | 0.72938 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 14 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 226.7991 | 4.3945 | 51.6092 | 226.7991 | 4.3945 | 51.6092 | 251.683 | 4.8767 | 51.6092 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 117 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 524.7816 | 36.7259 | 14.2892 | 524.7816 | 36.7259 | 14.2892 | 582.3594 | 40.7553 | 14.2892 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 50 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 96.3527 | 15.6948 | 6.1391 | 96.3527 | 15.6948 | 6.1391 | 106.9243 | 17.4168 | 6.1391 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 307 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 294.2347 | 96.3662 | 3.0533 | 294.2347 | 96.3662 | 3.0533 | 326.5175 | 106.9392 | 3.0533 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 298 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1130.6716 | 93.5411 | 12.0874 | 1130.6716 | 93.5411 | 12.0874 | 1254.7263 | 103.8042 | 12.0874 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 474 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1259.9464 | 148.7868 | 8.4681 | 1259.9464 | 148.7868 | 8.4681 | 1398.1847 | 165.1114 | 8.4681 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 159 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1192.3964 | 49.9095 | 23.8912 | 1192.3964 | 49.9095 | 23.8912 | 1323.2233 | 55.3855 | 23.8912 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 740 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 700.4791 | 232.2832 | 3.0156 | 700.4791 | 232.2832 | 3.0156 | 777.3341 | 257.7688 | 3.0156 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 49 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.70278 | 15.3809 | 0.045692 | 0.70278 | 15.3809 | 0.045692 | 0.77989 | 17.0685 | 0.045692 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 18 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.15554 | 5.6501 | 0.027528 | 0.15554 | 5.6501 | 0.027528 | 0.1726 | 6.2701 | 0.027528 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 2 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.09892 | 0.62779 | 0.15757 | 0.09892 | 0.62779 | 0.15757 | 0.10977 | 0.69667 | 0.15757 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 5 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 32.6575 | 1.5695 | 20.8078 | 32.6575 | 1.5695 | 20.8078 | 36.2406 | 1.7417 | 20.8078 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 72 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 38.8993 | 22.6005 | 1.7212 | 38.8993 | 22.6005 | 1.7212 | 43.1673 | 25.0802 | 1.7212 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 2 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.5839 | 0.62779 | 8.8944 | 5.5839 | 0.62779 | 8.8944 | 6.1965 | 0.69667 | 8.8944 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 252 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 264.7098 | 79.1019 | 3.3464 | 264.7098 | 79.1019 | 3.3464 | 293.7531 | 87.7807 | 3.3464 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 260 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 223.9657 | 81.613 | 2.7442 | 223.9657 | 81.613 | 2.7442 | 248.5387 | 90.5674 | 2.7442 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 214 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 113.0675 | 67.1738 | 1.6832 | 113.0675 | 67.1738 | 1.6832 | 125.473 | 74.544 | 1.6832 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 47 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.2411 | 14.7531 | 0.28747 | 4.2411 | 14.7531 | 0.28747 | 4.7064 | 16.3718 | 0.28747 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 4 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 96.3058 | 1.2556 | 76.702 | 96.3058 | 1.2556 | 76.702 | 106.8723 | 1.3933 | 76.702 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 24 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 190.3065 | 7.5335 | 25.2613 | 190.3065 | 7.5335 | 25.2613 | 211.1864 | 8.3601 | 25.2613 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 17 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 17.7496 | 5.3362 | 3.3262 | 17.7496 | 5.3362 | 3.3262 | 19.6971 | 5.9217 | 3.3262 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 60 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 35.3002 | 18.8338 | 1.8743 | 35.3002 | 18.8338 | 1.8743 | 39.1733 | 20.9002 | 1.8743 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 840 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 191.4311 | 263.6729 | 0.72602 | 191.4311 | 263.6729 | 0.72602 | 212.4345 | 292.6024 | 0.72602 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 10 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.9912 | 3.139 | 2.8644 | 8.9912 | 3.139 | 2.8644 | 9.9777 | 3.4834 | 2.8644 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 2 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.9193 | 0.62779 | 17.3931 | 10.9193 | 0.62779 | 17.3931 | 12.1173 | 0.69667 | 17.3931 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 45 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 175.5102 | 14.1253 | 12.4252 | 175.5102 | 14.1253 | 12.4252 | 194.7668 | 15.6751 | 12.4252 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 53 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 454.2842 | 16.6365 | 27.3065 | 454.2842 | 16.6365 | 27.3065 | 504.1272 | 18.4618 | 27.3065 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 215 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 460.7021 | 67.4877 | 6.8265 | 460.7021 | 67.4877 | 6.8265 | 511.2492 | 74.8923 | 6.8265 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 28 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 271.0346 | 8.7891 | 30.8376 | 271.0346 | 8.7891 | 30.8376 | 300.7719 | 9.7534 | 30.8376 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 21 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 94.482 | 6.5918 | 14.3332 | 94.482 | 6.5918 | 14.3332 | 104.8483 | 7.3151 | 14.3332 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 186 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 377.9207 | 58.3847 | 6.4729 | 377.9207 | 58.3847 | 6.4729 | 419.3853 | 64.7905 | 6.4729 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 75 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 69.195 | 23.5422 | 2.9392 | 69.195 | 23.5422 | 2.9392 | 76.7869 | 26.1252 | 2.9392 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 117 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 157.9098 | 36.7259 | 4.2997 | 157.9098 | 36.7259 | 4.2997 | 175.2352 | 40.7553 | 4.2997 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 246 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 131.5802 | 77.2185 | 1.704 | 131.5802 | 77.2185 | 1.704 | 146.0169 | 85.6907 | 1.704 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 35 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 61.7773 | 10.9864 | 5.6231 | 61.7773 | 10.9864 | 5.6231 | 68.5553 | 12.1918 | 5.6231 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 94 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 191.1024 | 29.5063 | 6.4767 | 191.1024 | 29.5063 | 6.4767 | 212.0697 | 32.7436 | 6.4767 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 2 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 18.4733 | 0.62779 | 29.4258 | 18.4733 | 0.62779 | 29.4258 | 20.5002 | 0.69667 | 29.4258 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 17 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 20.502 | 5.3362 | 3.842 | 20.502 | 5.3362 | 3.842 | 22.7514 | 5.9217 | 3.842 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 55 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 52.7183 | 17.2643 | 3.0536 | 52.7183 | 17.2643 | 3.0536 | 58.5024 | 19.1585 | 3.0536 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 9 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.091 | 2.8251 | 2.51 | 7.091 | 2.8251 | 2.51 | 7.869 | 3.135 | 2.51 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 33 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 83.8042 | 10.3586 | 8.0903 | 83.8042 | 10.3586 | 8.0903 | 92.999 | 11.4951 | 8.0903 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 63 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 268.9826 | 19.7755 | 13.6018 | 268.9826 | 19.7755 | 13.6018 | 298.4947 | 21.9452 | 13.6018 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 25 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 290.2233 | 7.8474 | 36.9833 | 290.2233 | 7.8474 | 36.9833 | 322.0659 | 8.7084 | 36.9833 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 335 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 525.3163 | 105.1553 | 4.9956 | 525.3163 | 105.1553 | 4.9956 | 582.9527 | 116.6926 | 4.9956 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 91 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 162.9237 | 28.5646 | 5.7037 | 162.9237 | 28.5646 | 5.7037 | 180.7993 | 31.6986 | 5.7037 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 35 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 17.4178 | 10.9864 | 1.5854 | 17.4178 | 10.9864 | 1.5854 | 19.3289 | 12.1918 | 1.5854 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 8 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 91.1498 | 2.5112 | 36.2977 | 91.1498 | 2.5112 | 36.2977 | 101.1506 | 2.7867 | 36.2977 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 101 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 194.2367 | 31.7035 | 6.1267 | 194.2367 | 31.7035 | 6.1267 | 215.5479 | 35.182 | 6.1267 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.6215 | 1.2556 | 2.0878 | 2.6215 | 1.2556 | 2.0878 | 2.9091 | 1.3933 | 2.0878 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2027 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | 4--2 | 14 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 4.3945 | 0 | 0 | 4.3945 | 0 | 0 | 4.8767 | 0 | 0% | 0.091242 | 0.086726 | 728.9125 | 1.3917 | 578.9338 | 148.587 | 766.8727 | 0 | 0 | 766.8727 | 0%
2027 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | 4--2 | 8 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2.5112 | 0 | 0 | 2.5112 | 0 | 0 | 2.7867 | 0 | 0% | 0.091116 | 0.086606 | 1530.6137 | 1.9599 | 1384.4341 | 144.2196 | 1610.3248 | 0 | 0 | 1610.3248 | 0%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 58 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 713.6047 | 18.206 | 39.1962 | 713.6047 | 18.206 | 39.1962 | 791.8998 | 20.2035 | 39.1962 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 7 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.2499 | 2.1973 | 1.0239 | 2.2499 | 2.1973 | 1.0239 | 2.4967 | 2.4384 | 1.0239 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.647 | 0.3139 | 11.6186 | 3.647 | 0.3139 | 11.6186 | 4.0472 | 0.34834 | 11.6186 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 151 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 364.787 | 47.3983 | 7.6962 | 364.787 | 47.3983 | 7.6962 | 404.8106 | 52.5988 | 7.6962 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 444 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1659.3701 | 139.3699 | 11.9062 | 1659.3701 | 139.3699 | 11.9062 | 1841.4323 | 154.6613 | 11.9062 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 4 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.33334 | 1.2556 | 0.26548 | 0.33334 | 1.2556 | 0.26548 | 0.36991 | 1.3933 | 0.26548 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 42 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 16.5362 | 13.1836 | 1.2543 | 16.5362 | 13.1836 | 1.2543 | 18.3505 | 14.6301 | 1.2543 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 319 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 229.3595 | 100.1329 | 2.2906 | 229.3595 | 100.1329 | 2.2906 | 254.5243 | 111.1193 | 2.2906 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 26 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 136.2236 | 8.1613 | 16.6914 | 136.2236 | 8.1613 | 16.6914 | 151.1698 | 9.0567 | 16.6914 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 61 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 172.8267 | 19.1477 | 9.026 | 172.8267 | 19.1477 | 9.026 | 191.7888 | 21.2485 | 9.026 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 124 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 135.6268 | 38.9231 | 3.4845 | 135.6268 | 38.9231 | 3.4845 | 150.5074 | 43.1937 | 3.4845 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 208 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 75.7062 | 65.2904 | 1.1595 | 75.7062 | 65.2904 | 1.1595 | 84.0125 | 72.4539 | 1.1595 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 114 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 79.9189 | 35.7842 | 2.2334 | 79.9189 | 35.7842 | 2.2334 | 88.6875 | 39.7103 | 2.2334 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 323 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 819.268 | 101.3885 | 8.0805 | 819.268 | 101.3885 | 8.0805 | 909.1561 | 112.5126 | 8.0805 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 419 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 179.8549 | 131.5225 | 1.3675 | 179.8549 | 131.5225 | 1.3675 | 199.5882 | 145.9529 | 1.3675 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 53 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 84.3793 | 16.6365 | 5.0719 | 84.3793 | 16.6365 | 5.0719 | 93.6372 | 18.4618 | 5.0719 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 166 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 192.6453 | 52.1068 | 3.6971 | 192.6453 | 52.1068 | 3.6971 | 213.7819 | 57.8238 | 3.6971 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 248 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 250.5037 | 77.8463 | 3.2179 | 250.5037 | 77.8463 | 3.2179 | 277.9884 | 86.3874 | 3.2179 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 143 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 30.0435 | 44.8872 | 0.66931 | 30.0435 | 44.8872 | 0.66931 | 33.3398 | 49.8121 | 0.66931 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 96 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 512.6697 | 30.134 | 17.013 | 512.6697 | 30.134 | 17.013 | 568.9186 | 33.4403 | 17.013 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 63 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 184.9104 | 19.7755 | 9.3505 | 184.9104 | 19.7755 | 9.3505 | 205.1983 | 21.9452 | 9.3505 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 234 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 440.5122 | 73.4517 | 5.9973 | 440.5122 | 73.4517 | 5.9973 | 488.8442 | 81.5107 | 5.9973 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 19 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 12.3234 | 5.964 | 2.0663 | 12.3234 | 5.964 | 2.0663 | 13.6755 | 6.6184 | 2.0663 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 62 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 149.7342 | 19.4616 | 7.6938 | 149.7342 | 19.4616 | 7.6938 | 166.1626 | 21.5968 | 7.6938 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 95 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 217.1483 | 29.8201 | 7.2819 | 217.1483 | 29.8201 | 7.2819 | 240.9733 | 33.0919 | 7.2819 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 299 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 574.3981 | 93.855 | 6.1201 | 574.3981 | 93.855 | 6.1201 | 637.4198 | 104.1525 | 6.1201 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 65.7597 | 1.5695 | 41.899 | 65.7597 | 1.5695 | 41.899 | 72.9747 | 1.7417 | 41.899 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 11 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 104.4239 | 3.4529 | 30.2427 | 104.4239 | 3.4529 | 30.2427 | 115.881 | 3.8317 | 30.2427 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 1 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 1.9561 | 0.3139 | 6.2317 | 1.9561 | 0.3139 | 6.2317 | 2.1707 | 0.34834 | 6.2317 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 357 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 506.1555 | 112.061 | 4.5168 | 506.1555 | 112.061 | 4.5168 | 561.6897 | 124.356 | 4.5168 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 5 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 87.1243 | 1.5695 | 55.5115 | 87.1243 | 1.5695 | 55.5115 | 96.6834 | 1.7417 | 55.5115 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 208 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 189.0401 | 65.2904 | 2.8954 | 189.0401 | 65.2904 | 2.8954 | 209.7812 | 72.4539 | 2.8954 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 4 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 29.2851 | 1.2556 | 23.3238 | 29.2851 | 1.2556 | 23.3238 | 32.4982 | 1.3933 | 23.3238 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 26 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.4415 | 8.1613 | 1.1569 | 9.4415 | 8.1613 | 1.1569 | 10.4774 | 9.0567 | 1.1569 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 87 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 15.7849 | 27.309 | 0.57801 | 15.7849 | 27.309 | 0.57801 | 17.5167 | 30.3053 | 0.57801 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 254 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 71.3855 | 79.7297 | 0.89534 | 71.3855 | 79.7297 | 0.89534 | 79.2178 | 88.4774 | 0.89534 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 14 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.28735 | 4.3945 | 0.065388 | 0.28735 | 4.3945 | 0.065388 | 0.31888 | 4.8767 | 0.065388 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 21 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 41.8749 | 6.5918 | 6.3525 | 41.8749 | 6.5918 | 6.3525 | 46.4693 | 7.3151 | 6.3525 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 38 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 21.2889 | 11.9281 | 1.7848 | 21.2889 | 11.9281 | 1.7848 | 23.6247 | 13.2368 | 1.7848 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 35 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 57.4893 | 10.9864 | 5.2328 | 57.4893 | 10.9864 | 5.2328 | 63.7969 | 12.1918 | 5.2328 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 180 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 133.7423 | 56.5013 | 2.3671 | 133.7423 | 56.5013 | 2.3671 | 148.4162 | 62.7005 | 2.3671 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 515 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 380.2129 | 161.6566 | 2.352 | 380.2129 | 161.6566 | 2.352 | 421.929 | 179.3932 | 2.352 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 55 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 20.217 | 17.2643 | 1.171 | 20.217 | 17.2643 | 1.171 | 22.4352 | 19.1585 | 1.171 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 44 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 40.081 | 13.8114 | 2.902 | 40.081 | 13.8114 | 2.902 | 44.4786 | 15.3268 | 2.902 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 67 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.4153 | 21.0311 | 0.25749 | 5.4153 | 21.0311 | 0.25749 | 6.0094 | 23.3385 | 0.25749 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 15 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.2749 | 4.7084 | 1.5451 | 7.2749 | 4.7084 | 1.5451 | 8.0731 | 5.225 | 1.5451 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 70 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 48.3556 | 21.9727 | 2.2007 | 48.3556 | 21.9727 | 2.2007 | 53.6611 | 24.3835 | 2.2007 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 129 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 68.683 | 40.4926 | 1.6962 | 68.683 | 40.4926 | 1.6962 | 76.2188 | 44.9354 | 1.6962 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 264 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 77.5518 | 82.8686 | 0.93584 | 77.5518 | 82.8686 | 0.93584 | 86.0606 | 91.9608 | 0.93584 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 63 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 74.7465 | 19.7755 | 3.7798 | 74.7465 | 19.7755 | 3.7798 | 82.9475 | 21.9452 | 3.7798 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 51 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 67.1805 | 16.0087 | 4.1965 | 67.1805 | 16.0087 | 4.1965 | 74.5514 | 17.7651 | 4.1965 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 5 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 27.2109 | 1.5695 | 17.3375 | 27.2109 | 1.5695 | 17.3375 | 30.1964 | 1.7417 | 17.3375 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 291 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 218.2996 | 91.3438 | 2.3899 | 218.2996 | 91.3438 | 2.3899 | 242.251 | 101.3658 | 2.3899 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 1 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 55.8373 | 0.3139 | 177.8846 | 55.8373 | 0.3139 | 177.8846 | 61.9636 | 0.34834 | 177.8846 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 68 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 43.4702 | 21.3449 | 2.0366 | 43.4702 | 21.3449 | 2.0366 | 48.2397 | 23.6869 | 2.0366 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 10 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.4291 | 3.139 | 3.641 | 11.4291 | 3.139 | 3.641 | 12.683 | 3.4834 | 3.641 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 50 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 64.9552 | 15.6948 | 4.1386 | 64.9552 | 15.6948 | 4.1386 | 72.0819 | 17.4168 | 4.1386 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 81 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 119.0101 | 25.4256 | 4.6807 | 119.0101 | 25.4256 | 4.6807 | 132.0677 | 28.2152 | 4.6807 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 19 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 45.4442 | 5.964 | 7.6197 | 45.4442 | 5.964 | 7.6197 | 50.4303 | 6.6184 | 7.6197 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 7 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.6223 | 2.1973 | 2.1037 | 4.6223 | 2.1973 | 2.1037 | 5.1294 | 2.4384 | 2.1037 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 42 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 96.2068 | 13.1836 | 7.2974 | 96.2068 | 13.1836 | 7.2974 | 106.7624 | 14.6301 | 7.2974 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 59 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 64.8175 | 18.5199 | 3.4999 | 64.8175 | 18.5199 | 3.4999 | 71.9292 | 20.5518 | 3.4999 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 270 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1170.8648 | 84.752 | 13.8152 | 1170.8648 | 84.752 | 13.8152 | 1299.3294 | 94.0508 | 13.8152 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 487 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 298.5256 | 152.8675 | 1.9528 | 298.5256 | 152.8675 | 1.9528 | 331.2791 | 169.6398 | 1.9528 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 158 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 21.2363 | 49.5956 | 0.42819 | 21.2363 | 49.5956 | 0.42819 | 23.5663 | 55.0371 | 0.42819 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 69 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 17.6405 | 21.6588 | 0.81447 | 17.6405 | 21.6588 | 0.81447 | 19.576 | 24.0352 | 0.81447 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 105 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 22.8254 | 32.9591 | 0.69254 | 22.8254 | 32.9591 | 0.69254 | 25.3298 | 36.5753 | 0.69254 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 154 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 98.5708 | 48.34 | 2.0391 | 98.5708 | 48.34 | 2.0391 | 109.3858 | 53.6438 | 2.0391 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 534 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 66.4558 | 167.6206 | 0.39647 | 66.4558 | 167.6206 | 0.39647 | 73.7472 | 186.0116 | 0.39647 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 96 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 999.3119 | 30.134 | 33.1622 | 999.3119 | 30.134 | 33.1622 | 1108.954 | 33.4403 | 33.1622 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 169 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 561.9538 | 53.0485 | 10.5932 | 561.9538 | 53.0485 | 10.5932 | 623.61 | 58.8688 | 10.5932 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 153 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 869.0928 | 48.0261 | 18.0962 | 869.0928 | 48.0261 | 18.0962 | 964.4476 | 53.2954 | 18.0962 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 46 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 62.4087 | 14.4392 | 4.3222 | 62.4087 | 14.4392 | 4.3222 | 69.256 | 16.0235 | 4.3222 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 150 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 242.1556 | 47.0844 | 5.143 | 242.1556 | 47.0844 | 5.143 | 268.7244 | 52.2504 | 5.143 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 111 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 627.3269 | 34.8425 | 18.0047 | 627.3269 | 34.8425 | 18.0047 | 696.1557 | 38.6653 | 18.0047 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 6 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.2076 | 1.8834 | 1.7031 | 3.2076 | 1.8834 | 1.7031 | 3.5596 | 2.09 | 1.7031 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 502 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 80.9279 | 157.5759 | 0.51358 | 80.9279 | 157.5759 | 0.51358 | 89.8072 | 174.8648 | 0.51358 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 383 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 107.9342 | 120.2223 | 0.89779 | 107.9342 | 120.2223 | 0.89779 | 119.7765 | 133.4128 | 0.89779 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 367 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 475.0478 | 115.1999 | 4.1237 | 475.0478 | 115.1999 | 4.1237 | 527.1689 | 127.8394 | 4.1237 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 406 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 155.9371 | 127.4419 | 1.2236 | 155.9371 | 127.4419 | 1.2236 | 173.0461 | 141.4245 | 1.2236 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 493 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 58.891 | 154.7509 | 0.38055 | 58.891 | 154.7509 | 0.38055 | 65.3523 | 171.7298 | 0.38055 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 69 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 451.3803 | 21.6588 | 20.8405 | 451.3803 | 21.6588 | 20.8405 | 500.9047 | 24.0352 | 20.8405 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 57 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 95.41 | 17.8921 | 5.3325 | 95.41 | 17.8921 | 5.3325 | 105.8782 | 19.8552 | 5.3325 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 218 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 73.1226 | 68.4294 | 1.0686 | 73.1226 | 68.4294 | 1.0686 | 81.1454 | 75.9373 | 1.0686 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 620 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 144.3433 | 194.6157 | 0.74168 | 144.3433 | 194.6157 | 0.74168 | 160.1803 | 215.9685 | 0.74168 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 166.1042 | 5.3362 | 31.1276 | 166.1042 | 5.3362 | 31.1276 | 184.3288 | 5.9217 | 31.1276 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 227 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 135.7606 | 71.2545 | 1.9053 | 135.7606 | 71.2545 | 1.9053 | 150.6559 | 79.0723 | 1.9053 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 357 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 118.4418 | 112.061 | 1.0569 | 118.4418 | 112.061 | 1.0569 | 131.4369 | 124.356 | 1.0569 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 31.8229 | 0.94169 | 33.7935 | 31.8229 | 0.94169 | 33.7935 | 35.3145 | 1.045 | 33.7935 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 384 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 171.9679 | 120.5362 | 1.4267 | 171.9679 | 120.5362 | 1.4267 | 190.8359 | 133.7611 | 1.4267 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 29 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 4.7854 | 9.103 | 0.52569 | 4.7854 | 9.103 | 0.52569 | 5.3104 | 10.1018 | 0.52569 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 30 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 92.1312 | 9.4169 | 9.7836 | 92.1312 | 9.4169 | 9.7836 | 102.2396 | 10.4501 | 9.7836 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 27 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 27.4714 | 8.4752 | 3.2414 | 27.4714 | 8.4752 | 3.2414 | 30.4855 | 9.4051 | 3.2414 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 56 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 200.7686 | 17.5782 | 11.4215 | 200.7686 | 17.5782 | 11.4215 | 222.7965 | 19.5068 | 11.4215 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 34 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 101.4086 | 10.6725 | 9.5019 | 101.4086 | 10.6725 | 9.5019 | 112.5349 | 11.8434 | 9.5019 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 17 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 431.4681 | 5.3362 | 80.8562 | 431.4681 | 5.3362 | 80.8562 | 478.8077 | 5.9217 | 80.8562 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 120 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 58.2657 | 37.6676 | 1.5468 | 58.2657 | 37.6676 | 1.5468 | 64.6584 | 41.8003 | 1.5468 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 822 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 322.3648 | 258.0227 | 1.2494 | 322.3648 | 258.0227 | 1.2494 | 357.7339 | 286.3324 | 1.2494 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 245 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3540.5817 | 76.9046 | 46.0386 | 3540.5817 | 76.9046 | 46.0386 | 3929.0461 | 85.3424 | 46.0386 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 161.8413 | 2.8251 | 57.2876 | 161.8413 | 2.8251 | 57.2876 | 179.5981 | 3.135 | 57.2876 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 107 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2024.2656 | 33.5869 | 60.2695 | 2024.2656 | 33.5869 | 60.2695 | 2246.3633 | 37.272 | 60.2695 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.2588 | 0.62779 | 17.9339 | 11.2588 | 0.62779 | 17.9339 | 12.4941 | 0.69667 | 17.9339 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 511 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 321.3252 | 160.401 | 2.0033 | 321.3252 | 160.401 | 2.0033 | 356.5803 | 177.9998 | 2.0033 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 14 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 218.5784 | 4.3945 | 49.7385 | 218.5784 | 4.3945 | 49.7385 | 242.5603 | 4.8767 | 49.7385 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 600 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 730.5315 | 188.3378 | 3.8788 | 730.5315 | 188.3378 | 3.8788 | 810.6837 | 209.0017 | 3.8788 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 3 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.76932 | 0.94169 | 0.81696 | 0.76932 | 0.94169 | 0.81696 | 0.85373 | 1.045 | 0.81696 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 349 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 85.5897 | 109.5498 | 0.78129 | 85.5897 | 109.5498 | 0.78129 | 94.9804 | 121.5694 | 0.78129 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 470 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 282.7746 | 147.5313 | 1.9167 | 282.7746 | 147.5313 | 1.9167 | 313.7999 | 163.718 | 1.9167 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 585 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 85.0286 | 183.6293 | 0.46304 | 85.0286 | 183.6293 | 0.46304 | 94.3577 | 203.7767 | 0.46304 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 226 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 19.0795 | 70.9406 | 0.26895 | 19.0795 | 70.9406 | 0.26895 | 21.1729 | 78.724 | 0.26895 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 70 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 34.8843 | 21.9727 | 1.5876 | 34.8843 | 21.9727 | 1.5876 | 38.7117 | 24.3835 | 1.5876 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 328 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 152.8245 | 102.958 | 1.4843 | 152.8245 | 102.958 | 1.4843 | 169.592 | 114.2543 | 1.4843 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 3 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.093 | 0.94169 | 5.4083 | 5.093 | 0.94169 | 5.4083 | 5.6517 | 1.045 | 5.4083 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 32 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.2041 | 10.0447 | 0.71721 | 7.2041 | 10.0447 | 0.71721 | 7.9946 | 11.1468 | 0.71721 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 364 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 120.9234 | 114.2582 | 1.0583 | 120.9234 | 114.2582 | 1.0583 | 134.1908 | 126.7944 | 1.0583 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 1452 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 228.5667 | 455.7774 | 0.50149 | 228.5667 | 455.7774 | 0.50149 | 253.6445 | 505.7842 | 0.50149 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 4 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0023289 | 1.2556 | 0.0018548 | 0.0023289 | 1.2556 | 0.0018548 | 0.0025844 | 1.3933 | 0.0018548 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 743 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 135.1583 | 233.2249 | 0.57952 | 135.1583 | 233.2249 | 0.57952 | 149.9876 | 258.8138 | 0.57952 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 182 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 31.5996 | 57.1291 | 0.55313 | 31.5996 | 57.1291 | 0.55313 | 35.0666 | 63.3972 | 0.55313 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 279 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 19.1528 | 87.5771 | 0.2187 | 19.1528 | 87.5771 | 0.2187 | 21.2542 | 97.1858 | 0.2187 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 309 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 90.6092 | 96.994 | 0.93417 | 90.6092 | 96.994 | 0.93417 | 100.5506 | 107.6359 | 0.93417 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 875 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 221.282 | 274.6592 | 0.80566 | 221.282 | 274.6592 | 0.80566 | 245.5605 | 304.7942 | 0.80566 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 106 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 174.6571 | 33.273 | 5.2492 | 174.6571 | 33.273 | 5.2492 | 193.82 | 36.9236 | 5.2492 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 399 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1049.1639 | 125.2446 | 8.3769 | 1049.1639 | 125.2446 | 8.3769 | 1164.2757 | 138.9862 | 8.3769 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 390 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 432.2395 | 122.4196 | 3.5308 | 432.2395 | 122.4196 | 3.5308 | 479.6638 | 135.8511 | 3.5308 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 104 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 123.7039 | 32.6452 | 3.7893 | 123.7039 | 32.6452 | 3.7893 | 137.2764 | 36.227 | 3.7893 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 19 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 100.4117 | 5.964 | 16.8362 | 100.4117 | 5.964 | 16.8362 | 111.4286 | 6.6184 | 16.8362 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 249 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 235.5518 | 78.1602 | 3.0137 | 235.5518 | 78.1602 | 3.0137 | 261.396 | 86.7357 | 3.0137 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 365 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 940.331 | 114.5721 | 8.2073 | 940.331 | 114.5721 | 8.2073 | 1043.5019 | 127.1427 | 8.2073 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 129 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 305.3339 | 40.4926 | 7.5405 | 305.3339 | 40.4926 | 7.5405 | 338.8344 | 44.9354 | 7.5405 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 48 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 162.7089 | 15.067 | 10.799 | 162.7089 | 15.067 | 10.799 | 180.561 | 16.7201 | 10.799 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 135 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1264.1257 | 42.376 | 29.8312 | 1264.1257 | 42.376 | 29.8312 | 1402.8226 | 47.0254 | 29.8312 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 345 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1206.3179 | 108.2942 | 11.1393 | 1206.3179 | 108.2942 | 11.1393 | 1338.6723 | 120.176 | 11.1393 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 37 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 21.1763 | 11.6142 | 1.8233 | 21.1763 | 11.6142 | 1.8233 | 23.4997 | 12.8884 | 1.8233 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 23 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 112.6347 | 7.2196 | 15.6012 | 112.6347 | 7.2196 | 15.6012 | 124.9927 | 8.0117 | 15.6012 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 479 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1379.245 | 150.3563 | 9.1732 | 1379.245 | 150.3563 | 9.1732 | 1530.5725 | 166.8531 | 9.1732 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 422 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2919.5776 | 132.4642 | 22.0405 | 2919.5776 | 132.4642 | 22.0405 | 3239.9069 | 146.9979 | 22.0405 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 399 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 38.0091 | 125.2446 | 0.30348 | 38.0091 | 125.2446 | 0.30348 | 42.1794 | 138.9862 | 0.30348 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 55 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 70.4536 | 17.2643 | 4.0809 | 70.4536 | 17.2643 | 4.0809 | 78.1836 | 19.1585 | 4.0809 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 233 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 48.5092 | 73.1378 | 0.66326 | 48.5092 | 73.1378 | 0.66326 | 53.8315 | 81.1623 | 0.66326 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 327 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 277.3974 | 102.6441 | 2.7025 | 277.3974 | 102.6441 | 2.7025 | 307.8328 | 113.906 | 2.7025 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 303 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 32.1257 | 95.1106 | 0.33777 | 32.1257 | 95.1106 | 0.33777 | 35.6504 | 105.5459 | 0.33777 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 31 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 16.745 | 9.7308 | 1.7208 | 16.745 | 9.7308 | 1.7208 | 18.5822 | 10.7984 | 1.7208 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 123 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 52.3616 | 38.6092 | 1.3562 | 52.3616 | 38.6092 | 1.3562 | 58.1066 | 42.8454 | 1.3562 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 24 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 35.1835 | 7.5335 | 4.6703 | 35.1835 | 7.5335 | 4.6703 | 39.0437 | 8.3601 | 4.6703 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 21 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 16.4392 | 6.5918 | 2.4939 | 16.4392 | 6.5918 | 2.4939 | 18.2429 | 7.3151 | 2.4939 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 485 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 195.7136 | 152.2397 | 1.2856 | 195.7136 | 152.2397 | 1.2856 | 217.1869 | 168.9431 | 1.2856 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 263 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 167.0067 | 82.5547 | 2.023 | 167.0067 | 82.5547 | 2.023 | 185.3303 | 91.6124 | 2.023 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 164 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 159.8647 | 51.479 | 3.1054 | 159.8647 | 51.479 | 3.1054 | 177.4047 | 57.1271 | 3.1054 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 101 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 28.5327 | 31.7035 | 0.89998 | 28.5327 | 31.7035 | 0.89998 | 31.6632 | 35.182 | 0.89998 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 389 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 144.2426 | 122.1057 | 1.1813 | 144.2426 | 122.1057 | 1.1813 | 160.0686 | 135.5028 | 1.1813 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 74 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 56.6878 | 23.2283 | 2.4405 | 56.6878 | 23.2283 | 2.4405 | 62.9074 | 25.7769 | 2.4405 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 6 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.6527 | 1.8834 | 2.4704 | 4.6527 | 1.8834 | 2.4704 | 5.1631 | 2.09 | 2.4704 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 299 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 162.0475 | 93.855 | 1.7266 | 162.0475 | 93.855 | 1.7266 | 179.8269 | 104.1525 | 1.7266 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 47 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 235.2675 | 14.7531 | 15.947 | 235.2675 | 14.7531 | 15.947 | 261.0805 | 16.3718 | 15.947 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 101 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 79.6362 | 31.7035 | 2.5119 | 79.6362 | 31.7035 | 2.5119 | 88.3736 | 35.182 | 2.5119 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 20.4453 | 0.3139 | 65.1338 | 20.4453 | 0.3139 | 65.1338 | 22.6885 | 0.34834 | 65.1338 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2027 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 2 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.8496 | 0.62779 | 2.9462 | 1.8496 | 0.62779 | 2.9462 | 2.0526 | 0.69667 | 2.9462 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 215 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 23.0365 | 67.4877 | 0.34134 | 23.0365 | 67.4877 | 0.34134 | 25.5641 | 74.8923 | 0.34134 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 22 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.1149 | 6.9057 | 0.016638 | 0.1149 | 6.9057 | 0.016638 | 0.1275 | 7.6634 | 0.016638 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 2 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 20.5582 | 0.62779 | 32.7468 | 20.5582 | 0.62779 | 32.7468 | 22.8138 | 0.69667 | 32.7468 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 169 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 31.3913 | 53.0485 | 0.59175 | 31.3913 | 53.0485 | 0.59175 | 34.8355 | 58.8688 | 0.59175 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 110 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 98.75 | 34.5286 | 2.8599 | 98.75 | 34.5286 | 2.8599 | 109.5846 | 38.317 | 2.8599 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 294 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 204.9832 | 92.2855 | 2.2212 | 204.9832 | 92.2855 | 2.2212 | 227.4734 | 102.4109 | 2.2212 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 5 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.83367 | 1.5695 | 0.53117 | 0.83367 | 1.5695 | 0.53117 | 0.92513 | 1.7417 | 0.53117 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 13 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.34714 | 4.0807 | 0.085069 | 0.34714 | 4.0807 | 0.085069 | 0.38522 | 4.5284 | 0.085069 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 201 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16842 | 63.0932 | 0.0026695 | 0.16842 | 63.0932 | 0.0026695 | 0.1869 | 70.0156 | 0.0026695 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 10 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.01378 | 3.139 | 0.00439 | 0.01378 | 3.139 | 0.00439 | 0.015292 | 3.4834 | 0.00439 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 149 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 9.4057 | 46.7705 | 0.2011 | 9.4057 | 46.7705 | 0.2011 | 10.4377 | 51.9021 | 0.2011 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 2 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 13.5232 | 0.62779 | 21.5408 | 13.5232 | 0.62779 | 21.5408 | 15.0069 | 0.69667 | 21.5408 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 975 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 154.9241 | 306.0489 | 0.50621 | 154.9241 | 306.0489 | 0.50621 | 171.922 | 339.6278 | 0.50621 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 827 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 613.1991 | 259.5922 | 2.3622 | 613.1991 | 259.5922 | 2.3622 | 680.4779 | 288.0741 | 2.3622 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 961 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 243.3688 | 301.6543 | 0.80678 | 243.3688 | 301.6543 | 0.80678 | 270.0707 | 334.7511 | 0.80678 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 397 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 604.7186 | 124.6168 | 4.8526 | 604.7186 | 124.6168 | 4.8526 | 671.067 | 138.2895 | 4.8526 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 538 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 498.8841 | 168.8762 | 2.9541 | 498.8841 | 168.8762 | 2.9541 | 553.6205 | 187.4049 | 2.9541 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 546 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1051.3816 | 171.3874 | 6.1345 | 1051.3816 | 171.3874 | 6.1345 | 1166.7367 | 190.1916 | 6.1345 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 92 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 410.7886 | 28.8785 | 14.2247 | 410.7886 | 28.8785 | 14.2247 | 455.8594 | 32.0469 | 14.2247 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 488 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 833.1015 | 153.1814 | 5.4387 | 833.1015 | 153.1814 | 5.4387 | 924.5075 | 169.9881 | 5.4387 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 319 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 404.9546 | 100.1329 | 4.0442 | 404.9546 | 100.1329 | 4.0442 | 449.3853 | 111.1193 | 4.0442 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 106 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 112.5405 | 33.273 | 3.3823 | 112.5405 | 33.273 | 3.3823 | 124.8882 | 36.9236 | 3.3823 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 24 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 99.735 | 7.5335 | 13.2388 | 99.735 | 7.5335 | 13.2388 | 110.6776 | 8.3601 | 13.2388 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 55 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 79.5582 | 17.2643 | 4.6082 | 79.5582 | 17.2643 | 4.6082 | 88.2871 | 19.1585 | 4.6082 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 46 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 193.5126 | 14.4392 | 13.4019 | 193.5126 | 14.4392 | 13.4019 | 214.7444 | 16.0235 | 13.4019 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 13 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.165 | 4.0807 | 3.2262 | 13.165 | 4.0807 | 3.2262 | 14.6095 | 4.5284 | 3.2262 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 139 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 606.1886 | 43.6316 | 13.8933 | 606.1886 | 43.6316 | 13.8933 | 672.6982 | 48.4187 | 13.8933 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 465 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 916.1722 | 145.9618 | 6.2768 | 916.1722 | 145.9618 | 6.2768 | 1016.6925 | 161.9764 | 6.2768 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 102 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 145.709 | 32.0174 | 4.5509 | 145.709 | 32.0174 | 4.5509 | 161.6959 | 35.5303 | 4.5509 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 276 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 332.7936 | 86.6354 | 3.8413 | 332.7936 | 86.6354 | 3.8413 | 369.307 | 96.1408 | 3.8413 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 139 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 61.1671 | 43.6316 | 1.4019 | 61.1671 | 43.6316 | 1.4019 | 67.8782 | 48.4187 | 1.4019 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 131 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 240.3733 | 41.1204 | 5.8456 | 240.3733 | 41.1204 | 5.8456 | 266.7465 | 45.632 | 5.8456 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 704 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 705.149 | 220.983 | 3.191 | 705.149 | 220.983 | 3.191 | 782.5163 | 245.2287 | 3.191 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 561 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 399.4624 | 176.0958 | 2.2684 | 399.4624 | 176.0958 | 2.2684 | 443.2904 | 195.4166 | 2.2684 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 14 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 55.83 | 4.3945 | 12.7044 | 55.83 | 4.3945 | 12.7044 | 61.9555 | 4.8767 | 12.7044 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 7 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 228.9358 | 2.1973 | 104.1908 | 228.9358 | 2.1973 | 104.1908 | 254.0541 | 2.4384 | 104.1908 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 1 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 37.8035 | 0.3139 | 120.433 | 37.8035 | 0.3139 | 120.433 | 41.9512 | 0.34834 | 120.433 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 194 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 750.663 | 60.8959 | 12.327 | 750.663 | 60.8959 | 12.327 | 833.024 | 67.5772 | 12.327 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 329 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 777.0044 | 103.2719 | 7.5239 | 777.0044 | 103.2719 | 7.5239 | 862.2555 | 114.6026 | 7.5239 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 435 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 456.006 | 136.5449 | 3.3396 | 456.006 | 136.5449 | 3.3396 | 506.0379 | 151.5263 | 3.3396 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 248 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 517.9939 | 77.8463 | 6.6541 | 517.9939 | 77.8463 | 6.6541 | 574.827 | 86.3874 | 6.6541 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 11 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 26.2533 | 3.4529 | 7.6033 | 26.2533 | 3.4529 | 7.6033 | 29.1337 | 3.8317 | 7.6033 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 36 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 60.3628 | 11.3003 | 5.3417 | 60.3628 | 11.3003 | 5.3417 | 66.9857 | 12.5401 | 5.3417 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 252 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1669.931 | 79.1019 | 21.1111 | 1669.931 | 79.1019 | 21.1111 | 1853.1519 | 87.7807 | 21.1111 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 14 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 58.3418 | 4.3945 | 13.276 | 58.3418 | 4.3945 | 13.276 | 64.7429 | 4.8767 | 13.276 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 22 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 7.8263 | 6.9057 | 1.1333 | 7.8263 | 6.9057 | 1.1333 | 8.685 | 7.6634 | 1.1333 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 590 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 124.6006 | 185.1988 | 0.67279 | 124.6006 | 185.1988 | 0.67279 | 138.2715 | 205.5184 | 0.67279 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 455 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 81.859 | 142.8228 | 0.57315 | 81.859 | 142.8228 | 0.57315 | 90.8403 | 158.493 | 0.57315 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 839 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 282.5323 | 263.359 | 1.0728 | 282.5323 | 263.359 | 1.0728 | 313.5311 | 292.2541 | 1.0728 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 3 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 58.3792 | 0.94169 | 61.9942 | 58.3792 | 0.94169 | 61.9942 | 64.7844 | 1.045 | 61.9942 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2027 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.1675 | 0.3139 | 10.091 | 3.1675 | 0.3139 | 10.091 | 3.5151 | 0.34834 | 10.091 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 91 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 154.4302 | 28.5646 | 5.4064 | 154.4302 | 28.5646 | 5.4064 | 171.3739 | 31.6986 | 5.4064 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 3 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 23.951 | 0.94169 | 25.4341 | 23.951 | 0.94169 | 25.4341 | 26.5789 | 1.045 | 25.4341 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 68 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 209.6923 | 21.3449 | 9.824 | 209.6923 | 21.3449 | 9.824 | 232.6993 | 23.6869 | 9.824 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 20 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 237.497 | 6.2779 | 37.8305 | 237.497 | 6.2779 | 37.8305 | 263.5546 | 6.9667 | 37.8305 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 358 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 79.4193 | 112.3749 | 0.70674 | 79.4193 | 112.3749 | 0.70674 | 88.133 | 124.7044 | 0.70674 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 28 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.069276 | 8.7891 | 0.007882 | 0.069276 | 8.7891 | 0.007882 | 0.076876 | 9.7534 | 0.007882 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 37 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 32.6276 | 11.6142 | 2.8093 | 32.6276 | 11.6142 | 2.8093 | 36.2074 | 12.8884 | 2.8093 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 17 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.7342 | 5.3362 | 2.5738 | 13.7342 | 5.3362 | 2.5738 | 15.2411 | 5.9217 | 2.5738 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 558 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 461.194 | 175.1541 | 2.6331 | 461.194 | 175.1541 | 2.6331 | 511.7951 | 194.3716 | 2.6331 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 9 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 24.5074 | 2.8251 | 8.675 | 24.5074 | 2.8251 | 8.675 | 27.1963 | 3.135 | 8.675 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 29 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 19.5259 | 9.103 | 2.145 | 19.5259 | 9.103 | 2.145 | 21.6682 | 10.1018 | 2.145 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 7 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.248 | 2.1973 | 1.4782 | 3.248 | 2.1973 | 1.4782 | 3.6044 | 2.4384 | 1.4782 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 16 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 150.1902 | 5.0223 | 29.9044 | 150.1902 | 5.0223 | 29.9044 | 166.6687 | 5.5734 | 29.9044 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 219 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 18.1939 | 68.7433 | 0.26466 | 18.1939 | 68.7433 | 0.26466 | 20.1901 | 76.2856 | 0.26466 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 202 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 412.0132 | 63.407 | 6.4979 | 412.0132 | 63.407 | 6.4979 | 457.2183 | 70.3639 | 6.4979 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 55 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 313.8836 | 17.2643 | 18.1811 | 313.8836 | 17.2643 | 18.1811 | 348.3221 | 19.1585 | 18.1811 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 33 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 64.084 | 10.3586 | 6.1866 | 64.084 | 10.3586 | 6.1866 | 71.1152 | 11.4951 | 6.1866 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 211 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 457.7342 | 66.2321 | 6.9111 | 457.7342 | 66.2321 | 6.9111 | 507.9557 | 73.4989 | 6.9111 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 16 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 67.4256 | 5.0223 | 13.4251 | 67.4256 | 5.0223 | 13.4251 | 74.8234 | 5.5734 | 13.4251 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 52 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 145.0545 | 16.3226 | 8.8867 | 145.0545 | 16.3226 | 8.8867 | 160.9695 | 18.1135 | 8.8867 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 29 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 175.4857 | 9.103 | 19.2778 | 175.4857 | 9.103 | 19.2778 | 194.7396 | 10.1018 | 19.2778 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 2 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 59.2108 | 0.62779 | 94.3159 | 59.2108 | 0.62779 | 94.3159 | 65.7073 | 0.69667 | 94.3159 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 1 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 53.1521 | 0.3139 | 169.33 | 53.1521 | 0.3139 | 169.33 | 58.9838 | 0.34834 | 169.33 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 56 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 108.1471 | 17.5782 | 6.1523 | 108.1471 | 17.5782 | 6.1523 | 120.0127 | 19.5068 | 6.1523 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 60 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 53.1821 | 18.8338 | 2.8238 | 53.1821 | 18.8338 | 2.8238 | 59.0171 | 20.9002 | 2.8238 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 73 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 17.8667 | 22.9144 | 0.77971 | 17.8667 | 22.9144 | 0.77971 | 19.8269 | 25.4285 | 0.77971 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 79 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 22.4804 | 24.7978 | 0.90655 | 22.4804 | 24.7978 | 0.90655 | 24.9469 | 27.5186 | 0.90655 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 243 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 375.994 | 76.2768 | 4.9293 | 375.994 | 76.2768 | 4.9293 | 417.2472 | 84.6457 | 4.9293 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 119 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 237.5496 | 37.3537 | 6.3595 | 237.5496 | 37.3537 | 6.3595 | 263.613 | 41.452 | 6.3595 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 495 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 274.3211 | 155.3787 | 1.7655 | 274.3211 | 155.3787 | 1.7655 | 304.419 | 172.4264 | 1.7655 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 14 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 65.3245 | 4.3945 | 14.8649 | 65.3245 | 4.3945 | 14.8649 | 72.4917 | 4.8767 | 14.8649 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 10 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 27.2363 | 3.139 | 8.6769 | 27.2363 | 3.139 | 8.6769 | 30.2246 | 3.4834 | 8.6769 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 61 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 234.0568 | 19.1477 | 12.2238 | 234.0568 | 19.1477 | 12.2238 | 259.737 | 21.2485 | 12.2238 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 125 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 99.8502 | 39.237 | 2.5448 | 99.8502 | 39.237 | 2.5448 | 110.8055 | 43.542 | 2.5448 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 49 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 12.9796 | 15.3809 | 0.84388 | 12.9796 | 15.3809 | 0.84388 | 14.4037 | 17.0685 | 0.84388 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 257 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 369.8356 | 80.6713 | 4.5845 | 369.8356 | 80.6713 | 4.5845 | 410.4131 | 89.5224 | 4.5845 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 62 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 33.1036 | 19.4616 | 1.701 | 33.1036 | 19.4616 | 1.701 | 36.7357 | 21.5968 | 1.701 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 61 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 48.5811 | 19.1477 | 2.5372 | 48.5811 | 19.1477 | 2.5372 | 53.9113 | 21.2485 | 2.5372 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2027 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 27 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 6.1748 | 8.4752 | 0.72857 | 6.1748 | 8.4752 | 0.72857 | 6.8523 | 9.4051 | 0.72857 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2027 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 4 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 8.1497 | 1.2556 | 6.4907 | 8.1497 | 1.2556 | 6.4907 | 9.0438 | 1.3933 | 6.4907 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 175 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 127.1099 | 54.9318 | 2.314 | 127.1099 | 54.9318 | 2.314 | 141.0561 | 60.9588 | 2.314 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2027 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 14 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.7092 | 4.3945 | 0.38894 | 1.7092 | 4.3945 | 0.38894 | 1.8968 | 4.8767 | 0.38894 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 287 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 154.5381 | 90.0882 | 1.7154 | 154.5381 | 90.0882 | 1.7154 | 171.4936 | 99.9725 | 1.7154 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 15 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 61.4752 | 4.7084 | 13.0564 | 61.4752 | 4.7084 | 13.0564 | 68.2202 | 5.225 | 13.0564 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 213 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 233.193 | 66.8599 | 3.4878 | 233.193 | 66.8599 | 3.4878 | 258.7784 | 74.1956 | 3.4878 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 471 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 749.3113 | 147.8451 | 5.0682 | 749.3113 | 147.8451 | 5.0682 | 831.524 | 164.0664 | 5.0682 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 15 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 181.9416 | 4.7084 | 38.6416 | 181.9416 | 4.7084 | 38.6416 | 201.9038 | 5.225 | 38.6416 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 90 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 9.159 | 28.2507 | 0.3242 | 9.159 | 28.2507 | 0.3242 | 10.1639 | 31.3503 | 0.3242 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 31 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 32.8858 | 9.7308 | 3.3796 | 32.8858 | 9.7308 | 3.3796 | 36.4939 | 10.7984 | 3.3796 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 779 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 130.6158 | 244.5252 | 0.53416 | 130.6158 | 244.5252 | 0.53416 | 144.9467 | 271.3539 | 0.53416 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 148 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 65.2597 | 46.4566 | 1.4047 | 65.2597 | 46.4566 | 1.4047 | 72.4198 | 51.5538 | 1.4047 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 400 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 114.9697 | 125.5585 | 0.91567 | 114.9697 | 125.5585 | 0.91567 | 127.5839 | 139.3345 | 0.91567 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 745 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 142.5829 | 233.8527 | 0.60971 | 142.5829 | 233.8527 | 0.60971 | 158.2268 | 259.5105 | 0.60971 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 290 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 72.2882 | 91.0299 | 0.79412 | 72.2882 | 91.0299 | 0.79412 | 80.2195 | 101.0175 | 0.79412 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 504 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 294.6356 | 158.2037 | 1.8624 | 294.6356 | 158.2037 | 1.8624 | 326.9624 | 175.5615 | 1.8624 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 258 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 26.069 | 80.9852 | 0.3219 | 26.069 | 80.9852 | 0.3219 | 28.9292 | 89.8708 | 0.3219 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 221 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 90.5939 | 69.3711 | 1.3059 | 90.5939 | 69.3711 | 1.3059 | 100.5337 | 76.9823 | 1.3059 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 63 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 8.6939 | 19.7755 | 0.43963 | 8.6939 | 19.7755 | 0.43963 | 9.6477 | 21.9452 | 0.43963 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 657 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 217.2304 | 206.2299 | 1.0533 | 217.2304 | 206.2299 | 1.0533 | 241.0644 | 228.8569 | 1.0533 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 231 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 89.8634 | 72.51 | 1.2393 | 89.8634 | 72.51 | 1.2393 | 99.723 | 80.4657 | 1.2393 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 427 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 494.3491 | 134.0337 | 3.6882 | 494.3491 | 134.0337 | 3.6882 | 548.5879 | 148.7396 | 3.6882 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 152 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 32.6271 | 47.7122 | 0.68383 | 32.6271 | 47.7122 | 0.68383 | 36.2069 | 52.9471 | 0.68383 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 356 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 373.4462 | 111.7471 | 3.3419 | 373.4462 | 111.7471 | 3.3419 | 414.4198 | 124.0077 | 3.3419 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 268 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 389.967 | 84.1242 | 4.6356 | 389.967 | 84.1242 | 4.6356 | 432.7533 | 93.3541 | 4.6356 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 378 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 249.9969 | 118.6528 | 2.107 | 249.9969 | 118.6528 | 2.107 | 277.426 | 131.6711 | 2.107 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 262 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 547.9949 | 82.2408 | 6.6633 | 547.9949 | 82.2408 | 6.6633 | 608.1196 | 91.2641 | 6.6633 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 549 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 402.1167 | 172.3291 | 2.3334 | 402.1167 | 172.3291 | 2.3334 | 446.236 | 191.2366 | 2.3334 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 29 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.1844 | 9.103 | 0.23996 | 2.1844 | 9.103 | 0.23996 | 2.424 | 10.1018 | 0.23996 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 39 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.1871 | 12.242 | 0.096972 | 1.1871 | 12.242 | 0.096972 | 1.3174 | 13.5851 | 0.096972 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 897 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 245.0024 | 281.565 | 0.87015 | 245.0024 | 281.565 | 0.87015 | 271.8835 | 312.4576 | 0.87015 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 111 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.608 | 34.8425 | 0.04615 | 1.608 | 34.8425 | 0.04615 | 1.7844 | 38.6653 | 0.04615 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 119 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 245.7559 | 37.3537 | 6.5792 | 245.7559 | 37.3537 | 6.5792 | 272.7197 | 41.452 | 6.5792 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 253 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 508.6206 | 79.4158 | 6.4045 | 508.6206 | 79.4158 | 6.4045 | 564.4253 | 88.1291 | 6.4045 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 241 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 611.3449 | 75.649 | 8.0813 | 611.3449 | 75.649 | 8.0813 | 678.4203 | 83.949 | 8.0813 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 136 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 389.3404 | 42.6899 | 9.1202 | 389.3404 | 42.6899 | 9.1202 | 432.0579 | 47.3737 | 9.1202 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 592 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1801.0985 | 185.8266 | 9.6924 | 1801.0985 | 185.8266 | 9.6924 | 1998.7108 | 206.2151 | 9.6924 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 30 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 25.4406 | 9.4169 | 2.7016 | 25.4406 | 9.4169 | 2.7016 | 28.2319 | 10.4501 | 2.7016 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2027 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | 2--5 | 1 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 7.5583 | 0 | 0 | 7.5583 | 0 | 6.878 | 0.3139 | 21.9117 | 6.878 | 0.3139 | 21.9117 | 7.6326 | 0.34834 | 21.9117 | 4.922% | 0.0076984 | 0.0073173 | 19947.1031 | 4677.56 | 10.2291 | 15259.3139 | 19952.9673 | 0 | 0 | 19952.9673 | 0.0002492%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 4 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 22.5604 | 1.2556 | 17.968 | 22.5604 | 1.2556 | 17.968 | 25.0356 | 1.3933 | 17.968 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 16 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.2134 | 5.0223 | 0.44071 | 2.2134 | 5.0223 | 0.44071 | 2.4562 | 5.5734 | 0.44071 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 685 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 808.0402 | 215.019 | 3.758 | 808.0402 | 215.019 | 3.758 | 896.6965 | 238.6103 | 3.758 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 899 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1152.5944 | 282.1928 | 4.0844 | 1152.5944 | 282.1928 | 4.0844 | 1279.0544 | 313.1543 | 4.0844 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 188 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 110.0696 | 59.0125 | 1.8652 | 110.0696 | 59.0125 | 1.8652 | 122.1462 | 65.4872 | 1.8652 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 406 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 176.6226 | 127.4419 | 1.3859 | 176.6226 | 127.4419 | 1.3859 | 196.0012 | 141.4245 | 1.3859 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 88 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 24.4376 | 27.6229 | 0.88469 | 24.4376 | 27.6229 | 0.88469 | 27.1188 | 30.6536 | 0.88469 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 132 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 68.0396 | 41.4343 | 1.6421 | 68.0396 | 41.4343 | 1.6421 | 75.5048 | 45.9804 | 1.6421 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 54 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 271.7734 | 16.9504 | 16.0335 | 271.7734 | 16.9504 | 16.0335 | 301.5917 | 18.8102 | 16.0335 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 293 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 680.9116 | 91.9716 | 7.4035 | 680.9116 | 91.9716 | 7.4035 | 755.6196 | 102.0625 | 7.4035 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 134 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 108.8052 | 42.0621 | 2.5868 | 108.8052 | 42.0621 | 2.5868 | 120.743 | 46.6771 | 2.5868 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 32 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 254.1624 | 10.0447 | 25.3032 | 254.1624 | 10.0447 | 25.3032 | 282.0485 | 11.1468 | 25.3032 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 150 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 469.0206 | 47.0844 | 9.9613 | 469.0206 | 47.0844 | 9.9613 | 520.4805 | 52.2504 | 9.9613 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 119 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 411.7972 | 37.3537 | 11.0243 | 411.7972 | 37.3537 | 11.0243 | 456.9786 | 41.452 | 11.0243 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2027 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.79635 | 0.62779 | 1.2685 | 0.79635 | 0.62779 | 1.2685 | 0.88372 | 0.69667 | 1.2685 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 157 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 140.9108 | 49.2817 | 2.8593 | 140.9108 | 49.2817 | 2.8593 | 156.3712 | 54.6888 | 2.8593 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 53 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 76.6258 | 16.6365 | 4.6059 | 76.6258 | 16.6365 | 4.6059 | 85.033 | 18.4618 | 4.6059 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 25 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 87.1533 | 7.8474 | 11.106 | 87.1533 | 7.8474 | 11.106 | 96.7155 | 8.7084 | 11.106 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 300 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 98.8295 | 94.1689 | 1.0495 | 98.8295 | 94.1689 | 1.0495 | 109.6728 | 104.5009 | 1.0495 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 133 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 644.9047 | 41.7482 | 15.4475 | 644.9047 | 41.7482 | 15.4475 | 715.6622 | 46.3287 | 15.4475 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 9 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 322.8415 | 2.8251 | 114.2775 | 322.8415 | 2.8251 | 114.2775 | 358.263 | 3.135 | 114.2775 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 236 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 388.0424 | 74.0795 | 5.2382 | 388.0424 | 74.0795 | 5.2382 | 430.6175 | 82.2074 | 5.2382 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 3 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 14.5393 | 0.94169 | 15.4396 | 14.5393 | 0.94169 | 15.4396 | 16.1345 | 1.045 | 15.4396 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 43 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 139.6922 | 13.4975 | 10.3495 | 139.6922 | 13.4975 | 10.3495 | 155.0189 | 14.9785 | 10.3495 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 109 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 550.9097 | 34.2147 | 16.1016 | 550.9097 | 34.2147 | 16.1016 | 611.3542 | 37.9687 | 16.1016 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 129 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 91.6277 | 40.4926 | 2.2628 | 91.6277 | 40.4926 | 2.2628 | 101.6809 | 44.9354 | 2.2628 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 99 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 51.3378 | 31.0757 | 1.652 | 51.3378 | 31.0757 | 1.652 | 56.9704 | 34.4853 | 1.652 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 62 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 430.0662 | 19.4616 | 22.0982 | 430.0662 | 19.4616 | 22.0982 | 477.252 | 21.5968 | 22.0982 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 47 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 821.8397 | 14.7531 | 55.7061 | 821.8397 | 14.7531 | 55.7061 | 912.01 | 16.3718 | 55.7061 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 9 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 114.8046 | 2.8251 | 40.6378 | 114.8046 | 2.8251 | 40.6378 | 127.4007 | 3.135 | 40.6378 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 103 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 240.2011 | 32.3313 | 7.4294 | 240.2011 | 32.3313 | 7.4294 | 266.5555 | 35.8786 | 7.4294 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 226 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 821.8107 | 70.9406 | 11.5845 | 821.8107 | 70.9406 | 11.5845 | 911.9778 | 78.724 | 11.5845 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 5 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 132.7651 | 1.5695 | 84.5917 | 132.7651 | 1.5695 | 84.5917 | 147.3318 | 1.7417 | 84.5917 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 210 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 892.989 | 65.9182 | 13.5469 | 892.989 | 65.9182 | 13.5469 | 990.9657 | 73.1506 | 13.5469 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 6 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.6978 | 1.8834 | 3.0253 | 5.6978 | 1.8834 | 3.0253 | 6.323 | 2.09 | 3.0253 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 27 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.55265 | 8.4752 | 0.065208 | 0.55265 | 8.4752 | 0.065208 | 0.61328 | 9.4051 | 0.065208 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 20 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 6.2808 | 6.2779 | 1.0005 | 6.2808 | 6.2779 | 1.0005 | 6.9699 | 6.9667 | 1.0005 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 7 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.29953 | 2.1973 | 0.13632 | 0.29953 | 2.1973 | 0.13632 | 0.33239 | 2.4384 | 0.13632 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 4 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 14.7896 | 1.2556 | 11.7791 | 14.7896 | 1.2556 | 11.7791 | 16.4123 | 1.3933 | 11.7791 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 95 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.1258 | 29.8201 | 0.33956 | 10.1258 | 29.8201 | 0.33956 | 11.2367 | 33.0919 | 0.33956 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 381 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 387.1481 | 119.5945 | 3.2372 | 387.1481 | 119.5945 | 3.2372 | 429.6251 | 132.7161 | 3.2372 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 124 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 371.1005 | 38.9231 | 9.5342 | 371.1005 | 38.9231 | 9.5342 | 411.8168 | 43.1937 | 9.5342 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.4327 | 0.3139 | 36.4218 | 11.4327 | 0.3139 | 36.4218 | 12.687 | 0.34834 | 36.4218 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 115 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 408.8067 | 36.0981 | 11.3249 | 408.8067 | 36.0981 | 11.3249 | 453.66 | 40.0587 | 11.3249 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 618 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1209.3579 | 193.9879 | 6.2342 | 1209.3579 | 193.9879 | 6.2342 | 1342.0458 | 215.2718 | 6.2342 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 53 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 285.8939 | 16.6365 | 17.1847 | 285.8939 | 16.6365 | 17.1847 | 317.2615 | 18.4618 | 17.1847 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 451 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 698.3032 | 141.5672 | 4.9327 | 698.3032 | 141.5672 | 4.9327 | 774.9194 | 157.0996 | 4.9327 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 350 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 523.5501 | 109.8637 | 4.7655 | 523.5501 | 109.8637 | 4.7655 | 580.9928 | 121.9177 | 4.7655 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 479 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 241.5192 | 150.3563 | 1.6063 | 241.5192 | 150.3563 | 1.6063 | 268.0181 | 166.8531 | 1.6063 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 302 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 60.6355 | 94.7967 | 0.63964 | 60.6355 | 94.7967 | 0.63964 | 67.2883 | 105.1975 | 0.63964 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 118 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 352.6402 | 37.0398 | 9.5206 | 352.6402 | 37.0398 | 9.5206 | 391.3311 | 41.1037 | 9.5206 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 313 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1837.8519 | 98.2495 | 18.706 | 1837.8519 | 98.2495 | 18.706 | 2039.4967 | 109.0292 | 18.706 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 226 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 150.9784 | 70.9406 | 2.1282 | 150.9784 | 70.9406 | 2.1282 | 167.5434 | 78.724 | 2.1282 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 273 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1007.0762 | 85.6937 | 11.752 | 1007.0762 | 85.6937 | 11.752 | 1117.5702 | 95.0958 | 11.752 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 2 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 6.8075 | 0.62779 | 10.8436 | 6.8075 | 0.62779 | 10.8436 | 7.5544 | 0.69667 | 10.8436 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 71 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 36.8484 | 22.2866 | 1.6534 | 36.8484 | 22.2866 | 1.6534 | 40.8913 | 24.7319 | 1.6534 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 434 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2470.7159 | 136.231 | 18.1362 | 2470.7159 | 136.231 | 18.1362 | 2741.797 | 151.1779 | 18.1362 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 1 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 256.8046 | 0.3139 | 818.1193 | 256.8046 | 0.3139 | 818.1193 | 284.9806 | 0.34834 | 818.1193 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 458 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1444.8081 | 143.7645 | 10.0498 | 1444.8081 | 143.7645 | 10.0498 | 1603.3291 | 159.538 | 10.0498 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 136 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 56.0299 | 42.6899 | 1.3125 | 56.0299 | 42.6899 | 1.3125 | 62.1774 | 47.3737 | 1.3125 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 74 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 152.4366 | 23.2283 | 6.5625 | 152.4366 | 23.2283 | 6.5625 | 169.1616 | 25.7769 | 6.5625 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 41 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 48.3244 | 12.8697 | 3.7549 | 48.3244 | 12.8697 | 3.7549 | 53.6265 | 14.2818 | 3.7549 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 93 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 68.7275 | 29.1924 | 2.3543 | 68.7275 | 29.1924 | 2.3543 | 76.2681 | 32.3953 | 2.3543 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 19.4852 | 0.62779 | 31.0377 | 19.4852 | 0.62779 | 31.0377 | 21.6231 | 0.69667 | 31.0377 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 34 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 581.8498 | 10.6725 | 54.5187 | 581.8498 | 10.6725 | 54.5187 | 645.689 | 11.8434 | 54.5187 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 309 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 675.9035 | 96.994 | 6.9685 | 675.9035 | 96.994 | 6.9685 | 750.0621 | 107.6359 | 6.9685 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 657 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1269.1144 | 206.2299 | 6.1539 | 1269.1144 | 206.2299 | 6.1539 | 1408.3587 | 228.8569 | 6.1539 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 75 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 359.1166 | 23.5422 | 15.2542 | 359.1166 | 23.5422 | 15.2542 | 398.5181 | 26.1252 | 15.2542 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 25 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 195.062 | 7.8474 | 24.8569 | 195.062 | 7.8474 | 24.8569 | 216.4638 | 8.7084 | 24.8569 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 123 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 654.899 | 38.6092 | 16.9622 | 654.899 | 38.6092 | 16.9622 | 726.7529 | 42.8454 | 16.9622 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 319 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 502.3679 | 100.1329 | 5.017 | 502.3679 | 100.1329 | 5.017 | 557.4865 | 111.1193 | 5.017 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 88 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 355.9256 | 27.6229 | 12.8852 | 355.9256 | 27.6229 | 12.8852 | 394.9769 | 30.6536 | 12.8852 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 704 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1037.5009 | 220.983 | 4.6949 | 1037.5009 | 220.983 | 4.6949 | 1151.3331 | 245.2287 | 4.6949 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 407 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1006.1322 | 127.7558 | 7.8754 | 1006.1322 | 127.7558 | 7.8754 | 1116.5227 | 141.7729 | 7.8754 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 137 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 408.4997 | 43.0038 | 9.4992 | 408.4997 | 43.0038 | 9.4992 | 453.3194 | 47.7221 | 9.4992 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 80 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 226.9901 | 25.1117 | 9.0392 | 226.9901 | 25.1117 | 9.0392 | 251.895 | 27.8669 | 9.0392 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 48 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 386.4725 | 15.067 | 25.6502 | 386.4725 | 15.067 | 25.6502 | 428.8754 | 16.7201 | 25.6502 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 42 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 287.9812 | 13.1836 | 21.8438 | 287.9812 | 13.1836 | 21.8438 | 319.5779 | 14.6301 | 21.8438 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 138 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 147.4106 | 43.3177 | 3.403 | 147.4106 | 43.3177 | 3.403 | 163.5841 | 48.0704 | 3.403 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 12 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 318.6899 | 3.7668 | 84.606 | 318.6899 | 3.7668 | 84.606 | 353.6559 | 4.18 | 84.606 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 5 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 232.1001 | 1.5695 | 147.8833 | 232.1001 | 1.5695 | 147.8833 | 257.5656 | 1.7417 | 147.8833 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 17 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 18.5991 | 5.3362 | 3.4854 | 18.5991 | 5.3362 | 3.4854 | 20.6397 | 5.9217 | 3.4854 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 107 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 205.7031 | 33.5869 | 6.1245 | 205.7031 | 33.5869 | 6.1245 | 228.2724 | 37.272 | 6.1245 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 82 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 149.8384 | 25.7395 | 5.8213 | 149.8384 | 25.7395 | 5.8213 | 166.2783 | 28.5636 | 5.8213 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 19 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 63.4742 | 5.964 | 10.6428 | 63.4742 | 5.964 | 10.6428 | 70.4384 | 6.6184 | 10.6428 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 50.9048 | 0.94169 | 54.0569 | 50.9048 | 0.94169 | 54.0569 | 56.49 | 1.045 | 54.0569 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 56 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 25.6219 | 17.5782 | 1.4576 | 25.6219 | 17.5782 | 1.4576 | 28.4331 | 19.5068 | 1.4576 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 80 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 25.8594 | 25.1117 | 1.0298 | 25.8594 | 25.1117 | 1.0298 | 28.6967 | 27.8669 | 1.0298 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 571 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 239.6285 | 179.2348 | 1.337 | 239.6285 | 179.2348 | 1.337 | 265.9199 | 198.9 | 1.337 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 1192 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 296.627 | 374.1644 | 0.79277 | 296.627 | 374.1644 | 0.79277 | 329.1722 | 415.2168 | 0.79277 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 132 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 64.6275 | 41.4343 | 1.5598 | 64.6275 | 41.4343 | 1.5598 | 71.7183 | 45.9804 | 1.5598 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 4.8571 | 1.2556 | 3.8684 | 4.8571 | 1.2556 | 3.8684 | 5.39 | 1.3933 | 3.8684 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 38 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 183.4459 | 11.9281 | 15.3794 | 183.4459 | 11.9281 | 15.3794 | 203.5731 | 13.2368 | 15.3794 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2027 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 3 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.7703 | 0.94169 | 1.8799 | 1.7703 | 0.94169 | 1.8799 | 1.9645 | 1.045 | 1.8799 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2027 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 1 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 4.1518 | 0.3139 | 13.2265 | 4.1518 | 0.3139 | 13.2265 | 4.6073 | 0.34834 | 13.2265 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 1 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.2891 | 0.3139 | 45.5216 | 14.2891 | 0.3139 | 45.5216 | 15.8568 | 0.34834 | 45.5216 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 58 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 18.0809 | 18.206 | 0.99313 | 18.0809 | 18.206 | 0.99313 | 20.0646 | 20.2035 | 0.99313 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 22 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 5.741 | 6.9057 | 0.83134 | 5.741 | 6.9057 | 0.83134 | 6.3709 | 7.6634 | 0.83134 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2027 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 248 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.84502 | 77.8463 | 0.010855 | 0.84502 | 77.8463 | 0.010855 | 0.93773 | 86.3874 | 0.010855 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 89 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 38.5732 | 27.9368 | 1.3807 | 38.5732 | 27.9368 | 1.3807 | 42.8054 | 31.0019 | 1.3807 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 36 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 9.5688 | 11.3003 | 0.84678 | 9.5688 | 11.3003 | 0.84678 | 10.6186 | 12.5401 | 0.84678 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 209 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 111.8057 | 65.6043 | 1.7042 | 111.8057 | 65.6043 | 1.7042 | 124.0728 | 72.8023 | 1.7042 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 277 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 72.0469 | 86.9493 | 0.82861 | 72.0469 | 86.9493 | 0.82861 | 79.9518 | 96.4891 | 0.82861 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 730 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 183.5822 | 229.1443 | 0.80116 | 183.5822 | 229.1443 | 0.80116 | 203.7244 | 254.2855 | 0.80116 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 485 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 146.7475 | 152.2397 | 0.96392 | 146.7475 | 152.2397 | 0.96392 | 162.8483 | 168.9431 | 0.96392 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2027 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 236 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 558.9371 | 74.0795 | 7.5451 | 558.9371 | 74.0795 | 7.5451 | 620.2624 | 82.2074 | 7.5451 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2027 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 2 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 94.6789 | 0.62779 | 150.8123 | 94.6789 | 0.62779 | 150.8123 | 105.0668 | 0.69667 | 150.8123 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 134 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 55.5708 | 42.0621 | 1.3212 | 55.5708 | 42.0621 | 1.3212 | 61.6679 | 46.6771 | 1.3212 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 18 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.7945 | 5.6501 | 2.0875 | 11.7945 | 5.6501 | 2.0875 | 13.0885 | 6.2701 | 2.0875 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 10 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 4.9928 | 3.139 | 1.5906 | 4.9928 | 3.139 | 1.5906 | 5.5406 | 3.4834 | 1.5906 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 167 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 58.3163 | 52.4207 | 1.1125 | 58.3163 | 52.4207 | 1.1125 | 64.7147 | 58.1722 | 1.1125 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 45 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.0215 | 14.1253 | 0.85106 | 12.0215 | 14.1253 | 0.85106 | 13.3405 | 15.6751 | 0.85106 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 46 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 43.1232 | 14.4392 | 2.9865 | 43.1232 | 14.4392 | 2.9865 | 47.8546 | 16.0235 | 2.9865 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 79 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 36.1453 | 24.7978 | 1.4576 | 36.1453 | 24.7978 | 1.4576 | 40.1111 | 27.5186 | 1.4576 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2027 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 82 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.8346 | 25.7395 | 0.11013 | 2.8346 | 25.7395 | 0.11013 | 3.1456 | 28.5636 | 0.11013 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2027 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 13 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.47188 | 4.0807 | 0.11564 | 0.47188 | 4.0807 | 0.11564 | 0.52366 | 4.5284 | 0.11564 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 65.4805 | 0.3139 | 208.6054 | 65.4805 | 0.3139 | 208.6054 | 72.6648 | 0.34834 | 208.6054 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2027 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 14 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 9.3898 | 4.3945 | 2.1367 | 9.3898 | 4.3945 | 2.1367 | 10.4201 | 4.8767 | 2.1367 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2027 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 96 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.8667 | 30.134 | 0.061948 | 1.8667 | 30.134 | 0.061948 | 2.0716 | 33.4403 | 0.061948 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 211 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 655.4112 | 66.2321 | 9.8957 | 655.4112 | 66.2321 | 9.8957 | 727.3214 | 73.4989 | 9.8957 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 22 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 3.9274 | 6.9057 | 0.56872 | 3.9274 | 6.9057 | 0.56872 | 4.3584 | 7.6634 | 0.56872 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2027 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.33709 | 0.3139 | 1.0739 | 0.33709 | 0.3139 | 1.0739 | 0.37408 | 0.34834 | 1.0739 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 376 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 502.5613 | 118.025 | 4.2581 | 502.5613 | 118.025 | 4.2581 | 557.7011 | 130.9744 | 4.2581 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.30382 | 0.3139 | 0.9679 | 0.30382 | 0.3139 | 0.9679 | 0.33716 | 0.34834 | 0.9679 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 184 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 264.2682 | 57.7569 | 4.5755 | 264.2682 | 57.7569 | 4.5755 | 293.2631 | 64.0939 | 4.5755 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 14 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.325 | 4.3945 | 1.6668 | 7.325 | 4.3945 | 1.6668 | 8.1287 | 4.8767 | 1.6668 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 2 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.3274 | 0.62779 | 6.893 | 4.3274 | 0.62779 | 6.893 | 4.8022 | 0.69667 | 6.893 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 40 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 48.0153 | 12.5559 | 3.8241 | 48.0153 | 12.5559 | 3.8241 | 53.2834 | 13.9334 | 3.8241 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 56 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 297.7228 | 17.5782 | 16.9371 | 297.7228 | 17.5782 | 16.9371 | 330.3883 | 19.5068 | 16.9371 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2027 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.82784 | 0.94169 | 0.8791 | 0.82784 | 0.94169 | 0.8791 | 0.91867 | 1.045 | 0.8791 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2027 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 1 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.077882 | 0.3139 | 0.24811 | 0.077882 | 0.3139 | 0.24811 | 0.086427 | 0.34834 | 0.24811 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2027 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 11 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.092914 | 3.4529 | 0.026909 | 0.092914 | 3.4529 | 0.026909 | 0.10311 | 3.8317 | 0.026909 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 277 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 43.3085 | 86.9493 | 0.49809 | 43.3085 | 86.9493 | 0.49809 | 48.0602 | 96.4891 | 0.49809 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2027 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 87 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 5.1199 | 27.309 | 0.18748 | 5.1199 | 27.309 | 0.18748 | 5.6817 | 30.3053 | 0.18748 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 12 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 20.4346 | 3.7668 | 5.425 | 20.4346 | 3.7668 | 5.425 | 22.6767 | 4.18 | 5.425 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 8 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.8571 | 2.5112 | 0.73952 | 1.8571 | 2.5112 | 0.73952 | 2.0608 | 2.7867 | 0.73952 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 56 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.0061 | 17.5782 | 0.17101 | 3.0061 | 17.5782 | 0.17101 | 3.3359 | 19.5068 | 0.17101 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 45 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 40.8246 | 14.1253 | 2.8902 | 40.8246 | 14.1253 | 2.8902 | 45.3038 | 15.6751 | 2.8902 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2027 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 20 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 14.7448 | 6.2779 | 2.3487 | 14.7448 | 6.2779 | 2.3487 | 16.3626 | 6.9667 | 2.3487 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 375 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 194.367 | 117.7111 | 1.6512 | 194.367 | 117.7111 | 1.6512 | 215.6925 | 130.6261 | 1.6512 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 47 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.2984 | 14.7531 | 0.15579 | 2.2984 | 14.7531 | 0.15579 | 2.5506 | 16.3718 | 0.15579 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 23 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 366.9683 | 7.2196 | 50.8294 | 366.9683 | 7.2196 | 50.8294 | 407.2312 | 8.0117 | 50.8294 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2027 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 104 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 1.91 | 32.6452 | 0.058507 | 1.91 | 32.6452 | 0.058507 | 2.1195 | 36.227 | 0.058507 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 26 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 123.3195 | 8.1613 | 15.1103 | 123.3195 | 8.1613 | 15.1103 | 136.8498 | 9.0567 | 15.1103 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 89 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.2129 | 27.9368 | 0.50875 | 14.2129 | 27.9368 | 0.50875 | 15.7723 | 31.0019 | 0.50875 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2027 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 2 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.3026 | 0.62779 | 18.0037 | 11.3026 | 0.62779 | 18.0037 | 12.5427 | 0.69667 | 18.0037 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 34 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 513.522 | 10.6725 | 48.1165 | 513.522 | 10.6725 | 48.1165 | 569.8644 | 11.8434 | 48.1165 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2027 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 36 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 58.4684 | 11.3003 | 5.1741 | 58.4684 | 11.3003 | 5.1741 | 64.8835 | 12.5401 | 5.1741 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 341 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 17.4173 | 107.0386 | 0.16272 | 17.4173 | 107.0386 | 0.16272 | 19.3283 | 118.7827 | 0.16272 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 23 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.9588 | 7.2196 | 0.82536 | 5.9588 | 7.2196 | 0.82536 | 6.6126 | 8.0117 | 0.82536 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1166 | 0.62779 | 1.7786 | 1.1166 | 0.62779 | 1.7786 | 1.2391 | 0.69667 | 1.7786 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2027 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 161 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 5.7652 | 50.5373 | 0.11408 | 5.7652 | 50.5373 | 0.11408 | 6.3978 | 56.0821 | 0.11408 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2027 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 154 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 43.7467 | 48.34 | 0.90498 | 43.7467 | 48.34 | 0.90498 | 48.5465 | 53.6438 | 0.90498 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 126 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 67.5098 | 39.5509 | 1.7069 | 67.5098 | 39.5509 | 1.7069 | 74.9169 | 43.8904 | 1.7069 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 97 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 227.2841 | 30.4479 | 7.4647 | 227.2841 | 30.4479 | 7.4647 | 252.2212 | 33.7886 | 7.4647 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2027 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 10 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 28.4591 | 3.139 | 9.0664 | 28.4591 | 3.139 | 9.0664 | 31.5815 | 3.4834 | 9.0664 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 593 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 308.3982 | 186.1405 | 1.6568 | 308.3982 | 186.1405 | 1.6568 | 342.2349 | 206.5634 | 1.6568 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 510 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 129.1825 | 160.0871 | 0.80695 | 129.1825 | 160.0871 | 0.80695 | 143.3561 | 177.6515 | 0.80695 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 214 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 465.7123 | 67.1738 | 6.9329 | 465.7123 | 67.1738 | 6.9329 | 516.8091 | 74.544 | 6.9329 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 170 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 231.132 | 53.3624 | 4.3314 | 231.132 | 53.3624 | 4.3314 | 256.4912 | 59.2172 | 4.3314 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2027 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 44 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 28.6814 | 13.8114 | 2.0766 | 28.6814 | 13.8114 | 2.0766 | 31.8282 | 15.3268 | 2.0766 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2027 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 3 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.3386 | 0.94169 | 1.4215 | 1.3386 | 0.94169 | 1.4215 | 1.4855 | 1.045 | 1.4215 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 182 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 167.0073 | 57.1291 | 2.9233 | 167.0073 | 57.1291 | 2.9233 | 185.3309 | 63.3972 | 2.9233 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 316 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 141.9018 | 99.1912 | 1.4306 | 141.9018 | 99.1912 | 1.4306 | 157.4709 | 110.0743 | 1.4306 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2027 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 22 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.084982 | 6.9057 | 0.012306 | 0.084982 | 6.9057 | 0.012306 | 0.094305 | 7.6634 | 0.012306 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 375 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 73.3558 | 117.7111 | 0.62319 | 73.3558 | 117.7111 | 0.62319 | 81.4042 | 130.6261 | 0.62319 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 113 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 159.4396 | 35.4703 | 4.495 | 159.4396 | 35.4703 | 4.495 | 176.933 | 39.362 | 4.495 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 254 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 417.8482 | 79.7297 | 5.2408 | 417.8482 | 79.7297 | 5.2408 | 463.6936 | 88.4774 | 5.2408 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 570 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 304.1512 | 178.9209 | 1.6999 | 304.1512 | 178.9209 | 1.6999 | 337.522 | 198.5517 | 1.6999 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 73 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 266.0239 | 22.9144 | 11.6094 | 266.0239 | 22.9144 | 11.6094 | 295.2114 | 25.4285 | 11.6094 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 239 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 169.5107 | 75.0212 | 2.2595 | 169.5107 | 75.0212 | 2.2595 | 188.109 | 83.2524 | 2.2595 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 5 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 4.9855 | 1.4972 | 3.33 | 4.9855 | 1.4972 | 3.33 | 5.8282 | 1.7502 | 3.33 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 34 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 17.4277 | 10.1808 | 1.7118 | 17.4277 | 10.1808 | 1.7118 | 20.3731 | 11.9015 | 1.7118 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 620 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 165.8433 | 185.6502 | 0.89331 | 165.8433 | 185.6502 | 0.89331 | 193.8727 | 217.0271 | 0.89331 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 510 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1495.8237 | 152.7122 | 9.795 | 1495.8237 | 152.7122 | 9.795 | 1748.6349 | 178.5223 | 9.795 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 72 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 297.6475 | 21.5594 | 13.8059 | 297.6475 | 21.5594 | 13.8059 | 347.9533 | 25.2032 | 13.8059 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 230 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 806.4885 | 68.8702 | 11.7103 | 806.4885 | 68.8702 | 11.7103 | 942.7942 | 80.5101 | 11.7103 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 99 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 215.2532 | 29.6441 | 7.2612 | 215.2532 | 29.6441 | 7.2612 | 251.6334 | 34.6543 | 7.2612 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 32 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 59.3317 | 9.5819 | 6.192 | 59.3317 | 9.5819 | 6.192 | 69.3594 | 11.2014 | 6.192 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 20 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 33.9963 | 5.9887 | 5.6767 | 33.9963 | 5.9887 | 5.6767 | 39.742 | 7.0009 | 5.6767 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 145 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 419.5312 | 43.4182 | 9.6626 | 419.5312 | 43.4182 | 9.6626 | 490.4368 | 50.7563 | 9.6626 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 5 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 29.618 | 1.4972 | 19.7826 | 29.618 | 1.4972 | 19.7826 | 34.6238 | 1.7502 | 19.7826 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 57 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 216.1178 | 17.0678 | 12.6623 | 216.1178 | 17.0678 | 12.6623 | 252.6441 | 19.9525 | 12.6623 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 198 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 123.2379 | 59.2883 | 2.0786 | 123.2379 | 59.2883 | 2.0786 | 144.0665 | 69.3087 | 2.0786 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 886 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 390.5476 | 265.3001 | 1.4721 | 390.5476 | 265.3001 | 1.4721 | 456.5546 | 310.1388 | 1.4721 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 587 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 157.9271 | 175.7688 | 0.89849 | 157.9271 | 175.7688 | 0.89849 | 184.6186 | 205.4757 | 0.89849 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 101 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 22.0588 | 30.243 | 0.72938 | 22.0588 | 30.243 | 0.72938 | 25.787 | 35.3544 | 0.72938 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 14 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 216.3509 | 4.1921 | 51.6092 | 216.3509 | 4.1921 | 51.6092 | 252.9167 | 4.9006 | 51.6092 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 117 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 500.606 | 35.034 | 14.2892 | 500.606 | 35.034 | 14.2892 | 585.2141 | 40.9551 | 14.2892 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 50 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 91.914 | 14.9718 | 6.1391 | 91.914 | 14.9718 | 6.1391 | 107.4485 | 17.5022 | 6.1391 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 307 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 280.6799 | 91.9268 | 3.0533 | 280.6799 | 91.9268 | 3.0533 | 328.1181 | 107.4634 | 3.0533 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 298 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1078.5839 | 89.2318 | 12.0874 | 1078.5839 | 89.2318 | 12.0874 | 1260.8769 | 104.313 | 12.0874 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 474 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1201.9032 | 141.9325 | 8.4681 | 1201.9032 | 141.9325 | 8.4681 | 1405.0386 | 165.9208 | 8.4681 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 159 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1137.4651 | 47.6103 | 23.8912 | 1137.4651 | 47.6103 | 23.8912 | 1329.7097 | 55.657 | 23.8912 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 740 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 668.2095 | 221.5824 | 3.0156 | 668.2095 | 221.5824 | 3.0156 | 781.1445 | 259.0324 | 3.0156 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2028 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 49 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.6704 | 14.6724 | 0.045692 | 0.6704 | 14.6724 | 0.045692 | 0.78371 | 17.1521 | 0.045692 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2028 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 18 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.14837 | 5.3898 | 0.027528 | 0.14837 | 5.3898 | 0.027528 | 0.17345 | 6.3008 | 0.027528 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2028 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 2 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.094363 | 0.59887 | 0.15757 | 0.094363 | 0.59887 | 0.15757 | 0.11031 | 0.70009 | 0.15757 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 5 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 31.153 | 1.4972 | 20.8078 | 31.153 | 1.4972 | 20.8078 | 36.4183 | 1.7502 | 20.8078 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 72 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 37.1073 | 21.5594 | 1.7212 | 37.1073 | 21.5594 | 1.7212 | 43.3789 | 25.2032 | 1.7212 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 2 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.3266 | 0.59887 | 8.8944 | 5.3266 | 0.59887 | 8.8944 | 6.2269 | 0.70009 | 8.8944 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 252 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 252.5151 | 75.4578 | 3.3464 | 252.5151 | 75.4578 | 3.3464 | 295.1931 | 88.211 | 3.3464 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 260 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 213.6481 | 77.8533 | 2.7442 | 213.6481 | 77.8533 | 2.7442 | 249.7571 | 91.0114 | 2.7442 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 214 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 107.8587 | 64.0792 | 1.6832 | 107.8587 | 64.0792 | 1.6832 | 126.0881 | 74.9094 | 1.6832 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 47 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.0457 | 14.0735 | 0.28747 | 4.0457 | 14.0735 | 0.28747 | 4.7294 | 16.4521 | 0.28747 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 4 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 91.8692 | 1.1977 | 76.702 | 91.8692 | 1.1977 | 76.702 | 107.3962 | 1.4002 | 76.702 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 24 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 181.5394 | 7.1865 | 25.2613 | 181.5394 | 7.1865 | 25.2613 | 212.2217 | 8.4011 | 25.2613 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 17 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 16.9319 | 5.0904 | 3.3262 | 16.9319 | 5.0904 | 3.3262 | 19.7936 | 5.9507 | 3.3262 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 60 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 33.674 | 17.9661 | 1.8743 | 33.674 | 17.9661 | 1.8743 | 39.3653 | 21.0026 | 1.8743 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 840 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 182.6123 | 251.526 | 0.72602 | 182.6123 | 251.526 | 0.72602 | 213.4758 | 294.0368 | 0.72602 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 10 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.577 | 2.9944 | 2.8644 | 8.577 | 2.9944 | 2.8644 | 10.0266 | 3.5004 | 2.8644 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 2 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.4162 | 0.59887 | 17.3931 | 10.4162 | 0.59887 | 17.3931 | 12.1767 | 0.70009 | 17.3931 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 45 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 167.4248 | 13.4746 | 12.4252 | 167.4248 | 13.4746 | 12.4252 | 195.7215 | 15.752 | 12.4252 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 53 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 433.3562 | 15.8701 | 27.3065 | 433.3562 | 15.8701 | 27.3065 | 506.5984 | 18.5523 | 27.3065 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 215 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 439.4785 | 64.3787 | 6.8265 | 439.4785 | 64.3787 | 6.8265 | 513.7554 | 75.2594 | 6.8265 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 28 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 258.5486 | 8.3842 | 30.8376 | 258.5486 | 8.3842 | 30.8376 | 302.2462 | 9.8012 | 30.8376 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 21 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 90.1294 | 6.2882 | 14.3332 | 90.1294 | 6.2882 | 14.3332 | 105.3623 | 7.3509 | 14.3332 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 186 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 360.5107 | 55.695 | 6.4729 | 360.5107 | 55.695 | 6.4729 | 421.4411 | 65.1081 | 6.4729 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 75 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 66.0073 | 22.4577 | 2.9392 | 66.0073 | 22.4577 | 2.9392 | 77.1633 | 26.2533 | 2.9392 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 117 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 150.6352 | 35.034 | 4.2997 | 150.6352 | 35.034 | 4.2997 | 176.0942 | 40.9551 | 4.2997 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 246 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 125.5186 | 73.6612 | 1.704 | 125.5186 | 73.6612 | 1.704 | 146.7327 | 86.1108 | 1.704 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 35 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 58.9313 | 10.4803 | 5.6231 | 58.9313 | 10.4803 | 5.6231 | 68.8914 | 12.2515 | 5.6231 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 94 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 182.2987 | 28.147 | 6.4767 | 182.2987 | 28.147 | 6.4767 | 213.1093 | 32.9041 | 6.4767 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 2 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 17.6223 | 0.59887 | 29.4258 | 17.6223 | 0.59887 | 29.4258 | 20.6007 | 0.70009 | 29.4258 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 17 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 19.5575 | 5.0904 | 3.842 | 19.5575 | 5.0904 | 3.842 | 22.8629 | 5.9507 | 3.842 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 55 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 50.2897 | 16.469 | 3.0536 | 50.2897 | 16.469 | 3.0536 | 58.7892 | 19.2524 | 3.0536 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 9 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 6.7644 | 2.6949 | 2.51 | 6.7644 | 2.6949 | 2.51 | 7.9076 | 3.1504 | 2.51 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 33 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 79.9435 | 9.8814 | 8.0903 | 79.9435 | 9.8814 | 8.0903 | 93.4549 | 11.5514 | 8.0903 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 63 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 256.5911 | 18.8645 | 13.6018 | 256.5911 | 18.8645 | 13.6018 | 299.9579 | 22.0528 | 13.6018 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 25 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 276.8533 | 7.4859 | 36.9833 | 276.8533 | 7.4859 | 36.9833 | 323.6447 | 8.7511 | 36.9833 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 335 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 501.116 | 100.311 | 4.9956 | 501.116 | 100.311 | 4.9956 | 585.8104 | 117.2647 | 4.9956 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 91 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 155.4182 | 27.2487 | 5.7037 | 155.4182 | 27.2487 | 5.7037 | 181.6856 | 31.854 | 5.7037 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 35 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 16.6154 | 10.4803 | 1.5854 | 16.6154 | 10.4803 | 1.5854 | 19.4236 | 12.2515 | 1.5854 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 8 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 86.9507 | 2.3955 | 36.2977 | 86.9507 | 2.3955 | 36.2977 | 101.6464 | 2.8004 | 36.2977 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 101 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 185.2886 | 30.243 | 6.1267 | 185.2886 | 30.243 | 6.1267 | 216.6045 | 35.3544 | 6.1267 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.5007 | 1.1977 | 2.0878 | 2.5007 | 1.1977 | 2.0878 | 2.9233 | 1.4002 | 2.0878 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2028 | 1458 | 1458-1115F | Tier-2 | Tier-2---18 | 4--2 | 14 | 100% | 66.5074 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 4.1921 | 0 | 0 | 4.1921 | 0 | 0 | 4.9006 | 0 | 0% | 0.091242 | 0.086726 | 728.9125 | 1.3917 | 578.9338 | 148.587 | 766.8727 | 0 | 0 | 766.8727 | 0%
2028 | 1458 | 1458-1117F | Tier-2 | Tier-2---16 | 4--2 | 8 | 100% | 139.4631 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 2.3955 | 0 | 0 | 2.3955 | 0 | 0 | 2.8004 | 0 | 0% | 0.091116 | 0.086606 | 1530.6137 | 1.9599 | 1384.4341 | 144.2196 | 1610.3248 | 0 | 0 | 1610.3248 | 0%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 58 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 680.7304 | 17.3673 | 39.1962 | 680.7304 | 17.3673 | 39.1962 | 795.7816 | 20.3025 | 39.1962 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 7 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.1462 | 2.0961 | 1.0239 | 2.1462 | 2.0961 | 1.0239 | 2.509 | 2.4503 | 1.0239 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2028 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 1 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.479 | 0.29944 | 11.6186 | 3.479 | 0.29944 | 11.6186 | 4.067 | 0.35004 | 11.6186 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 151 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 347.982 | 45.2148 | 7.6962 | 347.982 | 45.2148 | 7.6962 | 406.795 | 52.8566 | 7.6962 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 444 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1582.9263 | 132.9495 | 11.9062 | 1582.9263 | 132.9495 | 11.9062 | 1850.4589 | 155.4194 | 11.9062 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 4 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.31798 | 1.1977 | 0.26548 | 0.31798 | 1.1977 | 0.26548 | 0.37173 | 1.4002 | 0.26548 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 42 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 15.7744 | 12.5763 | 1.2543 | 15.7744 | 12.5763 | 1.2543 | 18.4404 | 14.7018 | 1.2543 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 319 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 218.7933 | 95.52 | 2.2906 | 218.7933 | 95.52 | 2.2906 | 255.7719 | 111.664 | 2.2906 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 26 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 129.9481 | 7.7853 | 16.6914 | 129.9481 | 7.7853 | 16.6914 | 151.9108 | 9.1011 | 16.6914 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 61 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 164.8649 | 18.2656 | 9.026 | 164.8649 | 18.2656 | 9.026 | 192.729 | 21.3527 | 9.026 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 124 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 129.3787 | 37.13 | 3.4845 | 129.3787 | 37.13 | 3.4845 | 151.2452 | 43.4054 | 3.4845 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 208 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 72.2185 | 62.2826 | 1.1595 | 72.2185 | 62.2826 | 1.1595 | 84.4243 | 72.8091 | 1.1595 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 114 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 76.2372 | 34.1357 | 2.2334 | 76.2372 | 34.1357 | 2.2334 | 89.1222 | 39.905 | 2.2334 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 323 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 781.526 | 96.7177 | 8.0805 | 781.526 | 96.7177 | 8.0805 | 913.6128 | 113.0641 | 8.0805 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 419 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 171.5694 | 125.4636 | 1.3675 | 171.5694 | 125.4636 | 1.3675 | 200.5666 | 146.6683 | 1.3675 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 53 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 80.4921 | 15.8701 | 5.0719 | 80.4921 | 15.8701 | 5.0719 | 94.0962 | 18.5523 | 5.0719 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 166 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 183.7705 | 49.7063 | 3.6971 | 183.7705 | 49.7063 | 3.6971 | 214.8298 | 58.1073 | 3.6971 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 248 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 238.9635 | 74.2601 | 3.2179 | 238.9635 | 74.2601 | 3.2179 | 279.3511 | 86.8109 | 3.2179 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 143 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 28.6595 | 42.8193 | 0.66931 | 28.6595 | 42.8193 | 0.66931 | 33.5032 | 50.0563 | 0.66931 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 96 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 489.052 | 28.7458 | 17.013 | 489.052 | 28.7458 | 17.013 | 571.7074 | 33.6042 | 17.013 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 63 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 176.3919 | 18.8645 | 9.3505 | 176.3919 | 18.8645 | 9.3505 | 206.2042 | 22.0528 | 9.3505 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 234 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 420.2187 | 70.068 | 5.9973 | 420.2187 | 70.068 | 5.9973 | 491.2405 | 81.9102 | 5.9973 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 19 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 11.7557 | 5.6893 | 2.0663 | 11.7557 | 5.6893 | 2.0663 | 13.7425 | 6.6508 | 2.0663 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 62 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 142.8362 | 18.565 | 7.6938 | 142.8362 | 18.565 | 7.6938 | 166.9772 | 21.7027 | 7.6938 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 95 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 207.1447 | 28.4464 | 7.2819 | 207.1447 | 28.4464 | 7.2819 | 242.1545 | 33.2542 | 7.2819 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 299 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 547.9368 | 89.5313 | 6.1201 | 547.9368 | 89.5313 | 6.1201 | 640.5444 | 104.6631 | 6.1201 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 5 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 62.7303 | 1.4972 | 41.899 | 62.7303 | 1.4972 | 41.899 | 73.3324 | 1.7502 | 41.899 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 11 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 99.6133 | 3.2938 | 30.2427 | 99.6133 | 3.2938 | 30.2427 | 116.449 | 3.8505 | 30.2427 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 1 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 1.866 | 0.29944 | 6.2317 | 1.866 | 0.29944 | 6.2317 | 2.1814 | 0.35004 | 6.2317 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 357 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 482.838 | 106.8986 | 4.5168 | 482.838 | 106.8986 | 4.5168 | 564.4431 | 124.9656 | 4.5168 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 5 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 83.1107 | 1.4972 | 55.5115 | 83.1107 | 1.4972 | 55.5115 | 97.1573 | 1.7502 | 55.5115 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 208 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 180.3315 | 62.2826 | 2.8954 | 180.3315 | 62.2826 | 2.8954 | 210.8095 | 72.8091 | 2.8954 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 4 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 27.936 | 1.1977 | 23.3238 | 27.936 | 1.1977 | 23.3238 | 32.6575 | 1.4002 | 23.3238 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 26 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.0065 | 7.7853 | 1.1569 | 9.0065 | 7.7853 | 1.1569 | 10.5287 | 9.1011 | 1.1569 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 87 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 15.0577 | 26.0509 | 0.57801 | 15.0577 | 26.0509 | 0.57801 | 17.6026 | 30.4538 | 0.57801 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 254 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 68.097 | 76.0567 | 0.89534 | 68.097 | 76.0567 | 0.89534 | 79.6061 | 88.9111 | 0.89534 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 14 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.27411 | 4.1921 | 0.065388 | 0.27411 | 4.1921 | 0.065388 | 0.32044 | 4.9006 | 0.065388 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 21 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 39.9458 | 6.2882 | 6.3525 | 39.9458 | 6.2882 | 6.3525 | 46.6971 | 7.3509 | 6.3525 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 38 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 20.3082 | 11.3786 | 1.7848 | 20.3082 | 11.3786 | 1.7848 | 23.7405 | 13.3017 | 1.7848 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 35 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 54.8409 | 10.4803 | 5.2328 | 54.8409 | 10.4803 | 5.2328 | 64.1096 | 12.2515 | 5.2328 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 180 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 127.5811 | 53.8984 | 2.3671 | 127.5811 | 53.8984 | 2.3671 | 149.1437 | 63.0079 | 2.3671 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 515 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 362.6973 | 154.2094 | 2.352 | 362.6973 | 154.2094 | 2.352 | 423.9973 | 180.2725 | 2.352 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 55 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 19.2857 | 16.469 | 1.171 | 19.2857 | 16.469 | 1.171 | 22.5452 | 19.2524 | 1.171 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 44 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 38.2345 | 13.1752 | 2.902 | 38.2345 | 13.1752 | 2.902 | 44.6966 | 15.4019 | 2.902 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 67 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.1658 | 20.0622 | 0.25749 | 5.1658 | 20.0622 | 0.25749 | 6.0389 | 23.4529 | 0.25749 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 15 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 6.9398 | 4.4915 | 1.5451 | 6.9398 | 4.4915 | 1.5451 | 8.1127 | 5.2507 | 1.5451 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 70 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 46.128 | 20.9605 | 2.2007 | 46.128 | 20.9605 | 2.2007 | 53.9241 | 24.5031 | 2.2007 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 129 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 65.5189 | 38.6272 | 1.6962 | 65.5189 | 38.6272 | 1.6962 | 76.5924 | 45.1556 | 1.6962 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 264 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 73.9791 | 79.051 | 0.93584 | 73.9791 | 79.051 | 0.93584 | 86.4824 | 92.4116 | 0.93584 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 63 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 71.3031 | 18.8645 | 3.7798 | 71.3031 | 18.8645 | 3.7798 | 83.3541 | 22.0528 | 3.7798 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 51 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 64.0856 | 15.2712 | 4.1965 | 64.0856 | 15.2712 | 4.1965 | 74.9168 | 17.8522 | 4.1965 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 5 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 25.9573 | 1.4972 | 17.3375 | 25.9573 | 1.4972 | 17.3375 | 30.3444 | 1.7502 | 17.3375 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 291 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 208.243 | 87.1358 | 2.3899 | 208.243 | 87.1358 | 2.3899 | 243.4385 | 101.8627 | 2.3899 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 1 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 53.265 | 0.29944 | 177.8846 | 53.265 | 0.29944 | 177.8846 | 62.2674 | 0.35004 | 177.8846 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 68 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 41.4677 | 20.3616 | 2.0366 | 41.4677 | 20.3616 | 2.0366 | 48.4762 | 23.803 | 2.0366 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 10 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 10.9026 | 2.9944 | 3.641 | 10.9026 | 2.9944 | 3.641 | 12.7452 | 3.5004 | 3.641 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 50 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 61.9628 | 14.9718 | 4.1386 | 61.9628 | 14.9718 | 4.1386 | 72.4352 | 17.5022 | 4.1386 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 81 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 113.5276 | 24.2543 | 4.6807 | 113.5276 | 24.2543 | 4.6807 | 132.715 | 28.3535 | 4.6807 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 19 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 43.3507 | 5.6893 | 7.6197 | 43.3507 | 5.6893 | 7.6197 | 50.6775 | 6.6508 | 7.6197 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 7 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.4094 | 2.0961 | 2.1037 | 4.4094 | 2.0961 | 2.1037 | 5.1546 | 2.4503 | 2.1037 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 42 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 91.7748 | 12.5763 | 7.2974 | 91.7748 | 12.5763 | 7.2974 | 107.2858 | 14.7018 | 7.2974 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 59 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 61.8315 | 17.6667 | 3.4999 | 61.8315 | 17.6667 | 3.4999 | 72.2817 | 20.6526 | 3.4999 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 270 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1116.9255 | 80.8476 | 13.8152 | 1116.9255 | 80.8476 | 13.8152 | 1305.6986 | 94.5118 | 13.8152 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 487 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 284.7731 | 145.8252 | 1.9528 | 284.7731 | 145.8252 | 1.9528 | 332.9031 | 170.4713 | 1.9528 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 158 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 20.258 | 47.3108 | 0.42819 | 20.258 | 47.3108 | 0.42819 | 23.6818 | 55.3069 | 0.42819 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 69 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 16.8278 | 20.6611 | 0.81447 | 16.8278 | 20.6611 | 0.81447 | 19.6719 | 24.153 | 0.81447 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 105 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 21.7739 | 31.4408 | 0.69254 | 21.7739 | 31.4408 | 0.69254 | 25.454 | 36.7546 | 0.69254 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 154 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 94.0298 | 46.1131 | 2.0391 | 94.0298 | 46.1131 | 2.0391 | 109.922 | 53.9067 | 2.0391 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 534 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 63.3943 | 159.8987 | 0.39647 | 63.3943 | 159.8987 | 0.39647 | 74.1087 | 186.9234 | 0.39647 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 96 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 953.2756 | 28.7458 | 33.1622 | 953.2756 | 28.7458 | 33.1622 | 1114.3901 | 33.6042 | 33.1622 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 169 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 536.0657 | 50.6046 | 10.5932 | 536.0657 | 50.6046 | 10.5932 | 626.6669 | 59.1574 | 10.5932 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 153 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 829.0555 | 45.8137 | 18.0962 | 829.0555 | 45.8137 | 18.0962 | 969.1753 | 53.5567 | 18.0962 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 46 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 59.5336 | 13.774 | 4.3222 | 59.5336 | 13.774 | 4.3222 | 69.5955 | 16.102 | 4.3222 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 150 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 231 | 44.9154 | 5.143 | 231 | 44.9154 | 5.143 | 270.0416 | 52.5066 | 5.143 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 111 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 598.4272 | 33.2374 | 18.0047 | 598.4272 | 33.2374 | 18.0047 | 699.5682 | 38.8549 | 18.0047 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 6 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.0599 | 1.7966 | 1.7031 | 3.0599 | 1.7966 | 1.7031 | 3.577 | 2.1003 | 1.7031 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 502 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 77.1998 | 150.3167 | 0.51358 | 77.1998 | 150.3167 | 0.51358 | 90.2474 | 175.722 | 0.51358 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 383 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 102.9619 | 114.6839 | 0.89779 | 102.9619 | 114.6839 | 0.89779 | 120.3637 | 134.0668 | 0.89779 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 367 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 453.1633 | 109.8929 | 4.1237 | 453.1633 | 109.8929 | 4.1237 | 529.7531 | 128.4661 | 4.1237 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 406 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 148.7534 | 121.5709 | 1.2236 | 148.7534 | 121.5709 | 1.2236 | 173.8944 | 142.1178 | 1.2236 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 493 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 56.178 | 147.6218 | 0.38055 | 56.178 | 147.6218 | 0.38055 | 65.6727 | 172.5716 | 0.38055 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 69 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 430.5862 | 20.6611 | 20.8405 | 430.5862 | 20.6611 | 20.8405 | 503.3602 | 24.153 | 20.8405 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 57 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 91.0147 | 17.0678 | 5.3325 | 91.0147 | 17.0678 | 5.3325 | 106.3972 | 19.9525 | 5.3325 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 218 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 69.754 | 65.277 | 1.0686 | 69.754 | 65.277 | 1.0686 | 81.5432 | 76.3095 | 1.0686 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 620 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 137.6937 | 185.6502 | 0.74168 | 137.6937 | 185.6502 | 0.74168 | 160.9655 | 217.0271 | 0.74168 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 17 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 158.4522 | 5.0904 | 31.1276 | 158.4522 | 5.0904 | 31.1276 | 185.2324 | 5.9507 | 31.1276 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 227 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 129.5064 | 67.9719 | 1.9053 | 129.5064 | 67.9719 | 1.9053 | 151.3944 | 79.4599 | 1.9053 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 357 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 112.9854 | 106.8986 | 1.0569 | 112.9854 | 106.8986 | 1.0569 | 132.0812 | 124.9656 | 1.0569 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 3 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 30.3569 | 0.89831 | 33.7935 | 30.3569 | 0.89831 | 33.7935 | 35.4876 | 1.0501 | 33.7935 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 384 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 164.0457 | 114.9833 | 1.4267 | 164.0457 | 114.9833 | 1.4267 | 191.7713 | 134.4168 | 1.4267 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 29 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 4.5649 | 8.6836 | 0.52569 | 4.5649 | 8.6836 | 0.52569 | 5.3364 | 10.1513 | 0.52569 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 30 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 87.8869 | 8.9831 | 9.7836 | 87.8869 | 8.9831 | 9.7836 | 102.7408 | 10.5013 | 9.7836 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 27 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 26.2058 | 8.0848 | 3.2414 | 26.2058 | 8.0848 | 3.2414 | 30.6349 | 9.4512 | 3.2414 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 56 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 191.5196 | 16.7684 | 11.4215 | 191.5196 | 16.7684 | 11.4215 | 223.8887 | 19.6025 | 11.4215 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 34 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 96.7369 | 10.1808 | 9.5019 | 96.7369 | 10.1808 | 9.5019 | 113.0865 | 11.9015 | 9.5019 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 17 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 411.5912 | 5.0904 | 80.8562 | 411.5912 | 5.0904 | 80.8562 | 481.1548 | 5.9507 | 80.8562 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 120 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 55.5815 | 35.9323 | 1.5468 | 55.5815 | 35.9323 | 1.5468 | 64.9754 | 42.0053 | 1.5468 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 822 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 307.5141 | 246.1362 | 1.2494 | 307.5141 | 246.1362 | 1.2494 | 359.4875 | 287.736 | 1.2494 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 245 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3377.4744 | 73.3618 | 46.0386 | 3377.4744 | 73.3618 | 46.0386 | 3948.3061 | 85.7607 | 46.0386 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 154.3856 | 2.6949 | 57.2876 | 154.3856 | 2.6949 | 57.2876 | 180.4785 | 3.1504 | 57.2876 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 107 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 1931.0119 | 32.0396 | 60.2695 | 1931.0119 | 32.0396 | 60.2695 | 2257.3749 | 37.4547 | 60.2695 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 2 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 10.7401 | 0.59887 | 17.9339 | 10.7401 | 0.59887 | 17.9339 | 12.5553 | 0.70009 | 17.9339 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 511 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 306.5225 | 153.0117 | 2.0033 | 306.5225 | 153.0117 | 2.0033 | 358.3282 | 178.8724 | 2.0033 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 14 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 208.5089 | 4.1921 | 49.7385 | 208.5089 | 4.1921 | 49.7385 | 243.7493 | 4.9006 | 49.7385 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 600 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 696.8774 | 179.6614 | 3.8788 | 696.8774 | 179.6614 | 3.8788 | 814.6577 | 210.0263 | 3.8788 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2028 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 3 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.73388 | 0.89831 | 0.81696 | 0.73388 | 0.89831 | 0.81696 | 0.85792 | 1.0501 | 0.81696 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 349 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 81.6467 | 104.5031 | 0.78129 | 81.6467 | 104.5031 | 0.78129 | 95.4459 | 122.1653 | 0.78129 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 470 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 269.7477 | 140.7348 | 1.9167 | 269.7477 | 140.7348 | 1.9167 | 315.3382 | 164.5206 | 1.9167 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 585 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 81.1115 | 175.1699 | 0.46304 | 81.1115 | 175.1699 | 0.46304 | 94.8202 | 204.7756 | 0.46304 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 226 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 18.2006 | 67.6725 | 0.26895 | 18.2006 | 67.6725 | 0.26895 | 21.2767 | 79.1099 | 0.26895 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 70 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 33.2772 | 20.9605 | 1.5876 | 33.2772 | 20.9605 | 1.5876 | 38.9015 | 24.5031 | 1.5876 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 328 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 145.7841 | 98.2149 | 1.4843 | 145.7841 | 98.2149 | 1.4843 | 170.4233 | 114.8144 | 1.4843 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 3 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 4.8583 | 0.89831 | 5.4083 | 4.8583 | 0.89831 | 5.4083 | 5.6795 | 1.0501 | 5.4083 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 32 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 6.8723 | 9.5819 | 0.71721 | 6.8723 | 9.5819 | 0.71721 | 8.0338 | 11.2014 | 0.71721 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 364 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 115.3527 | 108.9946 | 1.0583 | 115.3527 | 108.9946 | 1.0583 | 134.8486 | 127.4159 | 1.0583 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 1452 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 218.0371 | 434.7807 | 0.50149 | 218.0371 | 434.7807 | 0.50149 | 254.8879 | 508.2636 | 0.50149 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2028 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 4 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0022216 | 1.1977 | 0.0018548 | 0.0022216 | 1.1977 | 0.0018548 | 0.002597 | 1.4002 | 0.0018548 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 743 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 128.9318 | 222.4807 | 0.57952 | 128.9318 | 222.4807 | 0.57952 | 150.7228 | 260.0825 | 0.57952 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 182 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 30.1439 | 54.4973 | 0.55313 | 30.1439 | 54.4973 | 0.55313 | 35.2385 | 63.708 | 0.55313 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 279 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 18.2705 | 83.5426 | 0.2187 | 18.2705 | 83.5426 | 0.2187 | 21.3584 | 97.6622 | 0.2187 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 309 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 86.435 | 92.5256 | 0.93417 | 86.435 | 92.5256 | 0.93417 | 101.0435 | 108.1635 | 0.93417 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 875 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 211.088 | 262.0063 | 0.80566 | 211.088 | 262.0063 | 0.80566 | 246.7643 | 306.2883 | 0.80566 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 106 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 166.611 | 31.7402 | 5.2492 | 166.611 | 31.7402 | 5.2492 | 194.7701 | 37.1046 | 5.2492 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 399 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1000.831 | 119.4749 | 8.3769 | 1000.831 | 119.4749 | 8.3769 | 1169.9829 | 139.6675 | 8.3769 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 390 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 412.3272 | 116.7799 | 3.5308 | 412.3272 | 116.7799 | 3.5308 | 482.0151 | 136.5171 | 3.5308 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 104 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 118.0052 | 31.1413 | 3.7893 | 118.0052 | 31.1413 | 3.7893 | 137.9494 | 36.4046 | 3.7893 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 19 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 95.786 | 5.6893 | 16.8362 | 95.786 | 5.6893 | 16.8362 | 111.9749 | 6.6508 | 16.8362 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 249 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 224.7004 | 74.5595 | 3.0137 | 224.7004 | 74.5595 | 3.0137 | 262.6774 | 87.1609 | 3.0137 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 365 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 897.0119 | 109.294 | 8.2073 | 897.0119 | 109.294 | 8.2073 | 1048.6171 | 127.766 | 8.2073 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 129 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 291.2678 | 38.6272 | 7.5405 | 291.2678 | 38.6272 | 7.5405 | 340.4953 | 45.1556 | 7.5405 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 48 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 155.2133 | 14.3729 | 10.799 | 155.2133 | 14.3729 | 10.799 | 181.4461 | 16.8021 | 10.799 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 135 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1205.8901 | 40.4238 | 29.8312 | 1205.8901 | 40.4238 | 29.8312 | 1409.6992 | 47.2559 | 29.8312 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 345 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1150.7453 | 103.3053 | 11.1393 | 1150.7453 | 103.3053 | 11.1393 | 1345.2344 | 120.7651 | 11.1393 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 37 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 20.2007 | 11.0791 | 1.8233 | 20.2007 | 11.0791 | 1.8233 | 23.6149 | 12.9516 | 1.8233 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 23 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 107.4458 | 6.887 | 15.6012 | 107.4458 | 6.887 | 15.6012 | 125.6054 | 8.051 | 15.6012 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 479 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1315.706 | 143.4297 | 9.1732 | 1315.706 | 143.4297 | 9.1732 | 1538.0753 | 167.671 | 9.1732 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 422 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2785.0787 | 126.3619 | 22.0405 | 2785.0787 | 126.3619 | 22.0405 | 3255.7888 | 147.7185 | 22.0405 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 399 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 36.2581 | 119.4749 | 0.30348 | 36.2581 | 119.4749 | 0.30348 | 42.3861 | 139.6675 | 0.30348 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 55 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 67.2079 | 16.469 | 4.0809 | 67.2079 | 16.469 | 4.0809 | 78.5668 | 19.2524 | 4.0809 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 233 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 46.2745 | 69.7685 | 0.66326 | 46.2745 | 69.7685 | 0.66326 | 54.0954 | 81.5602 | 0.66326 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 327 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 264.6183 | 97.9155 | 2.7025 | 264.6183 | 97.9155 | 2.7025 | 309.3418 | 114.4643 | 2.7025 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 303 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 30.6457 | 90.729 | 0.33777 | 30.6457 | 90.729 | 0.33777 | 35.8252 | 106.0633 | 0.33777 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 31 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 15.9736 | 9.2825 | 1.7208 | 15.9736 | 9.2825 | 1.7208 | 18.6733 | 10.8514 | 1.7208 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 123 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 49.9494 | 36.8306 | 1.3562 | 49.9494 | 36.8306 | 1.3562 | 58.3914 | 43.0554 | 1.3562 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 24 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 33.5626 | 7.1865 | 4.6703 | 33.5626 | 7.1865 | 4.6703 | 39.2351 | 8.4011 | 4.6703 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 21 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 15.6819 | 6.2882 | 2.4939 | 15.6819 | 6.2882 | 2.4939 | 18.3323 | 7.3509 | 2.4939 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 485 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 186.6975 | 145.2263 | 1.2856 | 186.6975 | 145.2263 | 1.2856 | 218.2515 | 169.7712 | 1.2856 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 263 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 159.313 | 78.7516 | 2.023 | 159.313 | 78.7516 | 2.023 | 186.2387 | 92.0615 | 2.023 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 164 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 152.5001 | 49.1075 | 3.1054 | 152.5001 | 49.1075 | 3.1054 | 178.2744 | 57.4072 | 3.1054 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 101 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 27.2182 | 30.243 | 0.89998 | 27.2182 | 30.243 | 0.89998 | 31.8184 | 35.3544 | 0.89998 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 389 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 137.5976 | 116.4805 | 1.1813 | 137.5976 | 116.4805 | 1.1813 | 160.8532 | 136.167 | 1.1813 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 74 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 54.0763 | 22.1582 | 2.4405 | 54.0763 | 22.1582 | 2.4405 | 63.2158 | 25.9032 | 2.4405 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 6 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.4383 | 1.7966 | 2.4704 | 4.4383 | 1.7966 | 2.4704 | 5.1885 | 2.1003 | 2.4704 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 299 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 154.5823 | 89.5313 | 1.7266 | 154.5823 | 89.5313 | 1.7266 | 180.7085 | 104.6631 | 1.7266 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 47 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 224.4292 | 14.0735 | 15.947 | 224.4292 | 14.0735 | 15.947 | 262.3603 | 16.4521 | 15.947 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 101 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 75.9675 | 30.243 | 2.5119 | 75.9675 | 30.243 | 2.5119 | 88.8068 | 35.3544 | 2.5119 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 1 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 19.5034 | 0.29944 | 65.1338 | 19.5034 | 0.29944 | 65.1338 | 22.7997 | 0.35004 | 65.1338 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2028 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 2 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.7644 | 0.59887 | 2.9462 | 1.7644 | 0.59887 | 2.9462 | 2.0626 | 0.70009 | 2.9462 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2028 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 215 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 21.9753 | 64.3787 | 0.34134 | 21.9753 | 64.3787 | 0.34134 | 25.6894 | 75.2594 | 0.34134 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2028 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 22 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.1096 | 6.5876 | 0.016638 | 0.1096 | 6.5876 | 0.016638 | 0.12813 | 7.701 | 0.016638 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 2 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 19.6111 | 0.59887 | 32.7468 | 19.6111 | 0.59887 | 32.7468 | 22.9256 | 0.70009 | 32.7468 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 169 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 29.9452 | 50.6046 | 0.59175 | 29.9452 | 50.6046 | 0.59175 | 35.0063 | 59.1574 | 0.59175 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 110 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 94.2008 | 32.9379 | 2.8599 | 94.2008 | 32.9379 | 2.8599 | 110.1218 | 38.5048 | 2.8599 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 294 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 195.54 | 88.0341 | 2.2212 | 195.54 | 88.0341 | 2.2212 | 228.5885 | 102.9129 | 2.2212 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 5 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.79526 | 1.4972 | 0.53117 | 0.79526 | 1.4972 | 0.53117 | 0.92967 | 1.7502 | 0.53117 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 13 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.33114 | 3.8927 | 0.085069 | 0.33114 | 3.8927 | 0.085069 | 0.38711 | 4.5506 | 0.085069 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 201 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16067 | 60.1866 | 0.0026695 | 0.16067 | 60.1866 | 0.0026695 | 0.18782 | 70.3588 | 0.0026695 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 10 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.013145 | 2.9944 | 0.00439 | 0.013145 | 2.9944 | 0.00439 | 0.015367 | 3.5004 | 0.00439 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 149 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 8.9724 | 44.6159 | 0.2011 | 8.9724 | 44.6159 | 0.2011 | 10.4889 | 52.1565 | 0.2011 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 2 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 12.9002 | 0.59887 | 21.5408 | 12.9002 | 0.59887 | 21.5408 | 15.0805 | 0.70009 | 21.5408 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 975 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 147.7871 | 291.9498 | 0.50621 | 147.7871 | 291.9498 | 0.50621 | 172.7648 | 341.2927 | 0.50621 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 827 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 584.9503 | 247.6333 | 2.3622 | 584.9503 | 247.6333 | 2.3622 | 683.8136 | 289.4862 | 2.3622 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 961 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 232.1573 | 287.7577 | 0.80678 | 232.1573 | 287.7577 | 0.80678 | 271.3946 | 336.3921 | 0.80678 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 397 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 576.8605 | 118.876 | 4.8526 | 576.8605 | 118.876 | 4.8526 | 674.3565 | 138.9674 | 4.8526 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 538 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 475.9015 | 161.0964 | 2.9541 | 475.9015 | 161.0964 | 2.9541 | 556.3343 | 188.3236 | 2.9541 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 546 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1002.9466 | 163.4919 | 6.1345 | 1002.9466 | 163.4919 | 6.1345 | 1172.456 | 191.1239 | 6.1345 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 92 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 391.8645 | 27.5481 | 14.2247 | 391.8645 | 27.5481 | 14.2247 | 458.094 | 32.204 | 14.2247 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 488 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 794.7222 | 146.1246 | 5.4387 | 794.7222 | 146.1246 | 5.4387 | 929.0394 | 170.8214 | 5.4387 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 319 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 386.2992 | 95.52 | 4.0442 | 386.2992 | 95.52 | 4.0442 | 451.5881 | 111.664 | 4.0442 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 106 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 107.356 | 31.7402 | 3.3823 | 107.356 | 31.7402 | 3.3823 | 125.5004 | 37.1046 | 3.3823 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 24 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 95.1404 | 7.1865 | 13.2388 | 95.1404 | 7.1865 | 13.2388 | 111.2202 | 8.4011 | 13.2388 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 55 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 75.8931 | 16.469 | 4.6082 | 75.8931 | 16.469 | 4.6082 | 88.7199 | 19.2524 | 4.6082 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 46 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 184.5979 | 13.774 | 13.4019 | 184.5979 | 13.774 | 13.4019 | 215.797 | 16.102 | 13.4019 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 13 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 12.5585 | 3.8927 | 3.2262 | 12.5585 | 3.8927 | 3.2262 | 14.6811 | 4.5506 | 3.2262 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 139 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 578.2628 | 41.6216 | 13.8933 | 578.2628 | 41.6216 | 13.8933 | 675.9958 | 48.6561 | 13.8933 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 465 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 873.9661 | 139.2376 | 6.2768 | 873.9661 | 139.2376 | 6.2768 | 1021.6763 | 162.7704 | 6.2768 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 102 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 138.9965 | 30.5424 | 4.5509 | 138.9965 | 30.5424 | 4.5509 | 162.4885 | 35.7045 | 4.5509 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 276 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 317.4625 | 82.6443 | 3.8413 | 317.4625 | 82.6443 | 3.8413 | 371.1173 | 96.6121 | 3.8413 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 139 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 58.3493 | 41.6216 | 1.4019 | 58.3493 | 41.6216 | 1.4019 | 68.211 | 48.6561 | 1.4019 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 131 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 229.2998 | 39.2261 | 5.8456 | 229.2998 | 39.2261 | 5.8456 | 268.0541 | 45.8557 | 5.8456 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 704 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 672.6642 | 210.8028 | 3.191 | 672.6642 | 210.8028 | 3.191 | 786.3521 | 246.4308 | 3.191 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 561 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 381.0599 | 167.9834 | 2.2684 | 381.0599 | 167.9834 | 2.2684 | 445.4634 | 196.3746 | 2.2684 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 14 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 53.258 | 4.1921 | 12.7044 | 53.258 | 4.1921 | 12.7044 | 62.2592 | 4.9006 | 12.7044 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 7 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 218.3892 | 2.0961 | 104.1908 | 218.3892 | 2.0961 | 104.1908 | 255.2995 | 2.4503 | 104.1908 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 1 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 36.0619 | 0.29944 | 120.433 | 36.0619 | 0.29944 | 120.433 | 42.1568 | 0.35004 | 120.433 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 194 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 716.0815 | 58.0905 | 12.327 | 716.0815 | 58.0905 | 12.327 | 837.1074 | 67.9085 | 12.327 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 329 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 741.2094 | 98.5144 | 7.5239 | 741.2094 | 98.5144 | 7.5239 | 866.4823 | 115.1644 | 7.5239 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 435 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 434.9987 | 130.2545 | 3.3396 | 434.9987 | 130.2545 | 3.3396 | 508.5185 | 152.269 | 3.3396 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 248 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 494.131 | 74.2601 | 6.6541 | 494.131 | 74.2601 | 6.6541 | 577.6448 | 86.8109 | 6.6541 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 11 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 25.0438 | 3.2938 | 7.6033 | 25.0438 | 3.2938 | 7.6033 | 29.2765 | 3.8505 | 7.6033 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 36 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 57.582 | 10.7797 | 5.3417 | 57.582 | 10.7797 | 5.3417 | 67.3141 | 12.6016 | 5.3417 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 252 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1593.0007 | 75.4578 | 21.1111 | 1593.0007 | 75.4578 | 21.1111 | 1862.236 | 88.211 | 21.1111 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 14 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 55.6541 | 4.1921 | 13.276 | 55.6541 | 4.1921 | 13.276 | 65.0603 | 4.9006 | 13.276 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 22 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 7.4657 | 6.5876 | 1.1333 | 7.4657 | 6.5876 | 1.1333 | 8.7275 | 7.701 | 1.1333 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 590 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 118.8605 | 176.6671 | 0.67279 | 118.8605 | 176.6671 | 0.67279 | 138.9493 | 206.5258 | 0.67279 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 455 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 78.0879 | 136.2433 | 0.57315 | 78.0879 | 136.2433 | 0.57315 | 91.2856 | 159.2699 | 0.57315 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 839 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 269.5166 | 251.2266 | 1.0728 | 269.5166 | 251.2266 | 1.0728 | 315.068 | 293.6867 | 1.0728 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 3 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 55.6898 | 0.89831 | 61.9942 | 55.6898 | 0.89831 | 61.9942 | 65.102 | 1.0501 | 61.9942 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2028 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.0216 | 0.29944 | 10.091 | 3.0216 | 0.29944 | 10.091 | 3.5323 | 0.35004 | 10.091 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 91 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 147.3159 | 27.2487 | 5.4064 | 147.3159 | 27.2487 | 5.4064 | 172.214 | 31.854 | 5.4064 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 3 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 22.8477 | 0.89831 | 25.4341 | 22.8477 | 0.89831 | 25.4341 | 26.7092 | 1.0501 | 25.4341 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 68 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 200.0322 | 20.3616 | 9.824 | 200.0322 | 20.3616 | 9.824 | 233.8399 | 23.803 | 9.824 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 20 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 226.556 | 5.9887 | 37.8305 | 226.556 | 5.9887 | 37.8305 | 264.8465 | 7.0009 | 37.8305 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 358 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 75.7606 | 107.198 | 0.70674 | 75.7606 | 107.198 | 0.70674 | 88.565 | 125.3157 | 0.70674 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 28 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.066084 | 8.3842 | 0.007882 | 0.066084 | 8.3842 | 0.007882 | 0.077253 | 9.8012 | 0.007882 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 37 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 31.1245 | 11.0791 | 2.8093 | 31.1245 | 11.0791 | 2.8093 | 36.3849 | 12.9516 | 2.8093 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 17 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.1015 | 5.0904 | 2.5738 | 13.1015 | 5.0904 | 2.5738 | 15.3158 | 5.9507 | 2.5738 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 558 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 439.9478 | 167.0851 | 2.6331 | 439.9478 | 167.0851 | 2.6331 | 514.3039 | 195.3244 | 2.6331 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 9 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 23.3784 | 2.6949 | 8.675 | 23.3784 | 2.6949 | 8.675 | 27.3297 | 3.1504 | 8.675 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 29 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 18.6264 | 8.6836 | 2.145 | 18.6264 | 8.6836 | 2.145 | 21.7744 | 10.1513 | 2.145 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 7 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.0984 | 2.0961 | 1.4782 | 3.0984 | 2.0961 | 1.4782 | 3.6221 | 2.4503 | 1.4782 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 16 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 143.2712 | 4.791 | 29.9044 | 143.2712 | 4.791 | 29.9044 | 167.4857 | 5.6007 | 29.9044 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 219 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 17.3558 | 65.5764 | 0.26466 | 17.3558 | 65.5764 | 0.26466 | 20.2891 | 76.6596 | 0.26466 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 202 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 393.0326 | 60.486 | 6.4979 | 393.0326 | 60.486 | 6.4979 | 459.4596 | 70.7088 | 6.4979 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 55 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 299.4236 | 16.469 | 18.1811 | 299.4236 | 16.469 | 18.1811 | 350.0296 | 19.2524 | 18.1811 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 33 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 61.1318 | 9.8814 | 6.1866 | 61.1318 | 9.8814 | 6.1866 | 71.4638 | 11.5514 | 6.1866 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 211 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 436.6473 | 63.1809 | 6.9111 | 436.6473 | 63.1809 | 6.9111 | 510.4457 | 73.8592 | 6.9111 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 16 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 64.3194 | 4.791 | 13.4251 | 64.3194 | 4.791 | 13.4251 | 75.1902 | 5.6007 | 13.4251 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 52 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 138.3721 | 15.5707 | 8.8867 | 138.3721 | 15.5707 | 8.8867 | 161.7586 | 18.2023 | 8.8867 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 29 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 167.4015 | 8.6836 | 19.2778 | 167.4015 | 8.6836 | 19.2778 | 195.6942 | 10.1513 | 19.2778 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 2 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 56.4831 | 0.59887 | 94.3159 | 56.4831 | 0.59887 | 94.3159 | 66.0294 | 0.70009 | 94.3159 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 1 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 50.7035 | 0.29944 | 169.33 | 50.7035 | 0.29944 | 169.33 | 59.2729 | 0.35004 | 169.33 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 56 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 103.165 | 16.7684 | 6.1523 | 103.165 | 16.7684 | 6.1523 | 120.601 | 19.6025 | 6.1523 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 60 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 50.7321 | 17.9661 | 2.8238 | 50.7321 | 17.9661 | 2.8238 | 59.3064 | 21.0026 | 2.8238 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 73 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 17.0436 | 21.8588 | 0.77971 | 17.0436 | 21.8588 | 0.77971 | 19.9241 | 25.5532 | 0.77971 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 79 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 21.4448 | 23.6554 | 0.90655 | 21.4448 | 23.6554 | 0.90655 | 25.0692 | 27.6535 | 0.90655 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 243 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 358.6727 | 72.7629 | 4.9293 | 358.6727 | 72.7629 | 4.9293 | 419.2925 | 85.0606 | 4.9293 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 119 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 226.6062 | 35.6329 | 6.3595 | 226.6062 | 35.6329 | 6.3595 | 264.9052 | 41.6552 | 6.3595 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 495 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 261.6837 | 148.2207 | 1.7655 | 261.6837 | 148.2207 | 1.7655 | 305.9112 | 173.2717 | 1.7655 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 14 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 62.3151 | 4.1921 | 14.8649 | 62.3151 | 4.1921 | 14.8649 | 72.8471 | 4.9006 | 14.8649 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 10 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 25.9816 | 2.9944 | 8.6769 | 25.9816 | 2.9944 | 8.6769 | 30.3728 | 3.5004 | 8.6769 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 61 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 223.2743 | 18.2656 | 12.2238 | 223.2743 | 18.2656 | 12.2238 | 261.0102 | 21.3527 | 12.2238 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 125 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 95.2503 | 37.4295 | 2.5448 | 95.2503 | 37.4295 | 2.5448 | 111.3487 | 43.7555 | 2.5448 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 49 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 12.3817 | 14.6724 | 0.84388 | 12.3817 | 14.6724 | 0.84388 | 14.4744 | 17.1521 | 0.84388 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 257 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 352.7981 | 76.955 | 4.5845 | 352.7981 | 76.955 | 4.5845 | 412.425 | 89.9613 | 4.5845 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 62 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 31.5786 | 18.565 | 1.701 | 31.5786 | 18.565 | 1.701 | 36.9157 | 21.7027 | 1.701 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 61 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 46.343 | 18.2656 | 2.5372 | 46.343 | 18.2656 | 2.5372 | 54.1755 | 21.3527 | 2.5372 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 27 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 5.8904 | 8.0848 | 0.72857 | 5.8904 | 8.0848 | 0.72857 | 6.8859 | 9.4512 | 0.72857 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 4 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 7.7742 | 1.1977 | 6.4907 | 7.7742 | 1.1977 | 6.4907 | 9.0882 | 1.4002 | 6.4907 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 175 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 121.2542 | 52.4013 | 2.314 | 121.2542 | 52.4013 | 2.314 | 141.7475 | 61.2577 | 2.314 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 14 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.6305 | 4.1921 | 0.38894 | 1.6305 | 4.1921 | 0.38894 | 1.9061 | 4.9006 | 0.38894 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 287 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 147.4188 | 85.9381 | 1.7154 | 147.4188 | 85.9381 | 1.7154 | 172.3343 | 100.4626 | 1.7154 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 15 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 58.6432 | 4.4915 | 13.0564 | 58.6432 | 4.4915 | 13.0564 | 68.5546 | 5.2507 | 13.0564 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 213 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 222.4503 | 63.7798 | 3.4878 | 222.4503 | 63.7798 | 3.4878 | 260.047 | 74.5593 | 3.4878 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 471 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 714.7921 | 141.0342 | 5.0682 | 714.7921 | 141.0342 | 5.0682 | 835.6001 | 164.8706 | 5.0682 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 15 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 173.5599 | 4.4915 | 38.6416 | 173.5599 | 4.4915 | 38.6416 | 202.8935 | 5.2507 | 38.6416 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 90 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 8.737 | 26.9492 | 0.3242 | 8.737 | 26.9492 | 0.3242 | 10.2137 | 31.5039 | 0.3242 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 31 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 31.3708 | 9.2825 | 3.3796 | 31.3708 | 9.2825 | 3.3796 | 36.6728 | 10.8514 | 3.3796 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 779 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 124.5986 | 233.2604 | 0.53416 | 124.5986 | 233.2604 | 0.53416 | 145.6572 | 272.6841 | 0.53416 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 148 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 62.2533 | 44.3165 | 1.4047 | 62.2533 | 44.3165 | 1.4047 | 72.7748 | 51.8065 | 1.4047 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 400 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 109.6733 | 119.7743 | 0.91567 | 109.6733 | 119.7743 | 0.91567 | 128.2093 | 140.0175 | 0.91567 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 745 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 136.0144 | 223.0796 | 0.60971 | 136.0144 | 223.0796 | 0.60971 | 159.0024 | 260.7826 | 0.60971 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 290 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 68.9581 | 86.8364 | 0.79412 | 68.9581 | 86.8364 | 0.79412 | 80.6128 | 101.5127 | 0.79412 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 504 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 281.0624 | 150.9156 | 1.8624 | 281.0624 | 150.9156 | 1.8624 | 328.5651 | 176.4221 | 1.8624 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 258 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 24.868 | 77.2544 | 0.3219 | 24.868 | 77.2544 | 0.3219 | 29.071 | 90.3113 | 0.3219 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 221 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 86.4204 | 66.1753 | 1.3059 | 86.4204 | 66.1753 | 1.3059 | 101.0265 | 77.3597 | 1.3059 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 63 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 8.2934 | 18.8645 | 0.43963 | 8.2934 | 18.8645 | 0.43963 | 9.695 | 22.0528 | 0.43963 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 657 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 207.223 | 196.7293 | 1.0533 | 207.223 | 196.7293 | 1.0533 | 242.246 | 229.9788 | 1.0533 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 231 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 85.7236 | 69.1697 | 1.2393 | 85.7236 | 69.1697 | 1.2393 | 100.2118 | 80.8601 | 1.2393 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 427 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 471.5754 | 127.8591 | 3.6882 | 471.5754 | 127.8591 | 3.6882 | 551.277 | 149.4687 | 3.6882 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2028 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 152 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 31.124 | 45.5142 | 0.68383 | 31.124 | 45.5142 | 0.68383 | 36.3843 | 53.2067 | 0.68383 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 356 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 356.2423 | 106.5991 | 3.3419 | 356.2423 | 106.5991 | 3.3419 | 416.4513 | 124.6156 | 3.3419 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 268 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 372.002 | 80.2488 | 4.6356 | 372.002 | 80.2488 | 4.6356 | 434.8746 | 93.8117 | 4.6356 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 378 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 238.4801 | 113.1867 | 2.107 | 238.4801 | 113.1867 | 2.107 | 278.7859 | 132.3165 | 2.107 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 262 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 522.7499 | 78.4522 | 6.6633 | 522.7499 | 78.4522 | 6.6633 | 611.1006 | 91.7115 | 6.6633 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 549 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 383.592 | 164.3902 | 2.3334 | 383.592 | 164.3902 | 2.3334 | 448.4235 | 192.174 | 2.3334 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 29 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.0837 | 8.6836 | 0.23996 | 2.0837 | 8.6836 | 0.23996 | 2.4359 | 10.1513 | 0.23996 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 39 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.1324 | 11.678 | 0.096972 | 1.1324 | 11.678 | 0.096972 | 1.3238 | 13.6517 | 0.096972 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 897 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 233.7156 | 268.5938 | 0.87015 | 233.7156 | 268.5938 | 0.87015 | 273.2162 | 313.9893 | 0.87015 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 111 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.5339 | 33.2374 | 0.04615 | 1.5339 | 33.2374 | 0.04615 | 1.7931 | 38.8549 | 0.04615 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 119 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 234.4344 | 35.6329 | 6.5792 | 234.4344 | 35.6329 | 6.5792 | 274.0565 | 41.6552 | 6.5792 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 253 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 485.1895 | 75.7572 | 6.4045 | 485.1895 | 75.7572 | 6.4045 | 567.1921 | 88.5611 | 6.4045 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 241 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 583.1815 | 72.164 | 8.0813 | 583.1815 | 72.164 | 8.0813 | 681.7459 | 84.3606 | 8.0813 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 136 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 371.4043 | 40.7233 | 9.1202 | 371.4043 | 40.7233 | 9.1202 | 434.1758 | 47.606 | 9.1202 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 592 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1718.1256 | 177.266 | 9.6924 | 1718.1256 | 177.266 | 9.6924 | 2008.5084 | 207.2259 | 9.6924 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 30 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 24.2686 | 8.9831 | 2.7016 | 24.2686 | 8.9831 | 2.7016 | 28.3703 | 10.5013 | 2.7016 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2028 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | 2--5 | 1 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 7.5583 | 0 | 0 | 7.5583 | 0 | 6.5611 | 0.29944 | 21.9117 | 6.5611 | 0.29944 | 21.9117 | 7.67 | 0.35004 | 21.9117 | 4.922% | 0.0076984 | 0.0073173 | 19947.1031 | 4677.56 | 10.2291 | 15259.3139 | 19952.9673 | 0 | 0 | 19952.9673 | 0.0002492%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 4 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 21.5211 | 1.1977 | 17.968 | 21.5211 | 1.1977 | 17.968 | 25.1584 | 1.4002 | 17.968 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 16 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.1114 | 4.791 | 0.44071 | 2.1114 | 4.791 | 0.44071 | 2.4683 | 5.6007 | 0.44071 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 685 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 770.8154 | 205.1135 | 3.758 | 770.8154 | 205.1135 | 3.758 | 901.092 | 239.78 | 3.758 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 899 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1099.4968 | 269.1927 | 4.0844 | 1099.4968 | 269.1927 | 4.0844 | 1285.3243 | 314.6894 | 4.0844 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 188 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 104.999 | 56.2939 | 1.8652 | 104.999 | 56.2939 | 1.8652 | 122.745 | 65.8082 | 1.8652 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 406 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 168.4859 | 121.5709 | 1.3859 | 168.4859 | 121.5709 | 1.3859 | 196.962 | 142.1178 | 1.3859 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 88 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 23.3118 | 26.3503 | 0.88469 | 23.3118 | 26.3503 | 0.88469 | 27.2518 | 30.8039 | 0.88469 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 132 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 64.9052 | 39.5255 | 1.6421 | 64.9052 | 39.5255 | 1.6421 | 75.8749 | 46.2058 | 1.6421 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 54 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 259.2534 | 16.1695 | 16.0335 | 259.2534 | 16.1695 | 16.0335 | 303.0701 | 18.9024 | 16.0335 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 293 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 649.5434 | 87.7347 | 7.4035 | 649.5434 | 87.7347 | 7.4035 | 759.3236 | 102.5628 | 7.4035 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 134 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 103.7927 | 40.1244 | 2.5868 | 103.7927 | 40.1244 | 2.5868 | 121.3349 | 46.9059 | 2.5868 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 32 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 242.4537 | 9.5819 | 25.3032 | 242.4537 | 9.5819 | 25.3032 | 283.4311 | 11.2014 | 25.3032 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 150 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 447.4138 | 44.9154 | 9.9613 | 447.4138 | 44.9154 | 9.9613 | 523.0318 | 52.5066 | 9.9613 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 119 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 392.8265 | 35.6329 | 11.0243 | 392.8265 | 35.6329 | 11.0243 | 459.2187 | 41.6552 | 11.0243 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2028 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 2 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.75966 | 0.59887 | 1.2685 | 0.75966 | 0.59887 | 1.2685 | 0.88805 | 0.70009 | 1.2685 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 157 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 134.4194 | 47.0114 | 2.8593 | 134.4194 | 47.0114 | 2.8593 | 157.1378 | 54.9569 | 2.8593 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 53 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 73.0958 | 15.8701 | 4.6059 | 73.0958 | 15.8701 | 4.6059 | 85.4498 | 18.5523 | 4.6059 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 25 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 83.1383 | 7.4859 | 11.106 | 83.1383 | 7.4859 | 11.106 | 97.1896 | 8.7511 | 11.106 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 300 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 94.2766 | 89.8307 | 1.0495 | 94.2766 | 89.8307 | 1.0495 | 110.2104 | 105.0131 | 1.0495 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 133 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 615.1953 | 39.825 | 15.4475 | 615.1953 | 39.825 | 15.4475 | 719.1703 | 46.5558 | 15.4475 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 9 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 307.9689 | 2.6949 | 114.2775 | 307.9689 | 2.6949 | 114.2775 | 360.0191 | 3.1504 | 114.2775 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 236 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 370.166 | 70.6668 | 5.2382 | 370.166 | 70.6668 | 5.2382 | 432.7283 | 82.6103 | 5.2382 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2028 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 3 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 13.8695 | 0.89831 | 15.4396 | 13.8695 | 0.89831 | 15.4396 | 16.2136 | 1.0501 | 15.4396 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 43 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 133.2569 | 12.8757 | 10.3495 | 133.2569 | 12.8757 | 10.3495 | 155.7788 | 15.0519 | 10.3495 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 109 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 525.5304 | 32.6385 | 16.1016 | 525.5304 | 32.6385 | 16.1016 | 614.3511 | 38.1548 | 16.1016 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 129 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 87.4066 | 38.6272 | 2.2628 | 87.4066 | 38.6272 | 2.2628 | 102.1793 | 45.1556 | 2.2628 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 99 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 48.9727 | 29.6441 | 1.652 | 48.9727 | 29.6441 | 1.652 | 57.2497 | 34.6543 | 1.652 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 62 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 410.2539 | 18.565 | 22.0982 | 410.2539 | 18.565 | 22.0982 | 479.5915 | 21.7027 | 22.0982 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 47 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 783.9792 | 14.0735 | 55.7061 | 783.9792 | 14.0735 | 55.7061 | 916.4806 | 16.4521 | 55.7061 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 9 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 109.5158 | 2.6949 | 40.6378 | 109.5158 | 2.6949 | 40.6378 | 128.0252 | 3.1504 | 40.6378 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 103 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 229.1356 | 30.8419 | 7.4294 | 229.1356 | 30.8419 | 7.4294 | 267.8621 | 36.0545 | 7.4294 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 226 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 783.9515 | 67.6725 | 11.5845 | 783.9515 | 67.6725 | 11.5845 | 916.4483 | 79.1099 | 11.5845 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 5 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 126.6489 | 1.4972 | 84.5917 | 126.6489 | 1.4972 | 84.5917 | 148.054 | 1.7502 | 84.5917 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 210 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 851.8508 | 62.8815 | 13.5469 | 851.8508 | 62.8815 | 13.5469 | 995.8233 | 73.5092 | 13.5469 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 6 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.4353 | 1.7966 | 3.0253 | 5.4353 | 1.7966 | 3.0253 | 6.354 | 2.1003 | 3.0253 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2028 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 27 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.52719 | 8.0848 | 0.065208 | 0.52719 | 8.0848 | 0.065208 | 0.61629 | 9.4512 | 0.065208 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2028 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 20 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 5.9914 | 5.9887 | 1.0005 | 5.9914 | 5.9887 | 1.0005 | 7.004 | 7.0009 | 1.0005 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 7 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.28573 | 2.0961 | 0.13632 | 0.28573 | 2.0961 | 0.13632 | 0.33402 | 2.4503 | 0.13632 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 4 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 14.1083 | 1.1977 | 11.7791 | 14.1083 | 1.1977 | 11.7791 | 16.4928 | 1.4002 | 11.7791 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 95 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 9.6593 | 28.4464 | 0.33956 | 9.6593 | 28.4464 | 0.33956 | 11.2918 | 33.2542 | 0.33956 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 381 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 369.313 | 114.085 | 3.2372 | 369.313 | 114.085 | 3.2372 | 431.7311 | 133.3667 | 3.2372 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 124 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 354.0047 | 37.13 | 9.5342 | 354.0047 | 37.13 | 9.5342 | 413.8355 | 43.4054 | 9.5342 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 1 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 10.906 | 0.29944 | 36.4218 | 10.906 | 0.29944 | 36.4218 | 12.7492 | 0.35004 | 36.4218 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 115 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 389.9738 | 34.4351 | 11.3249 | 389.9738 | 34.4351 | 11.3249 | 455.8839 | 40.255 | 11.3249 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 618 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1153.6452 | 185.0513 | 6.2342 | 1153.6452 | 185.0513 | 6.2342 | 1348.6244 | 216.3271 | 6.2342 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 53 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 272.7233 | 15.8701 | 17.1847 | 272.7233 | 15.8701 | 17.1847 | 318.8167 | 18.5523 | 17.1847 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 451 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 666.1338 | 135.0455 | 4.9327 | 666.1338 | 135.0455 | 4.9327 | 778.718 | 157.8697 | 4.9327 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 350 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 499.4312 | 104.8025 | 4.7655 | 499.4312 | 104.8025 | 4.7655 | 583.8408 | 122.5153 | 4.7655 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 479 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 230.3929 | 143.4297 | 1.6063 | 230.3929 | 143.4297 | 1.6063 | 269.3319 | 167.671 | 1.6063 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 302 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 57.8421 | 90.4296 | 0.63964 | 57.8421 | 90.4296 | 0.63964 | 67.6181 | 105.7132 | 0.63964 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 118 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 336.3948 | 35.3334 | 9.5206 | 336.3948 | 35.3334 | 9.5206 | 393.2494 | 41.3052 | 9.5206 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 313 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1753.1858 | 93.7234 | 18.706 | 1753.1858 | 93.7234 | 18.706 | 2049.4942 | 109.5637 | 18.706 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 226 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 144.0231 | 67.6725 | 2.1282 | 144.0231 | 67.6725 | 2.1282 | 168.3647 | 79.1099 | 2.1282 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 273 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 960.6823 | 81.746 | 11.752 | 960.6823 | 81.746 | 11.752 | 1123.0485 | 95.562 | 11.752 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 2 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 6.4939 | 0.59887 | 10.8436 | 6.4939 | 0.59887 | 10.8436 | 7.5915 | 0.70009 | 10.8436 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 71 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 35.1509 | 21.2599 | 1.6534 | 35.1509 | 21.2599 | 1.6534 | 41.0917 | 24.8531 | 1.6534 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 434 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2356.8951 | 129.9551 | 18.1362 | 2356.8951 | 129.9551 | 18.1362 | 2755.2372 | 151.919 | 18.1362 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 1 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 244.9741 | 0.29944 | 818.1193 | 244.9741 | 0.29944 | 818.1193 | 286.3776 | 0.35004 | 818.1193 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 458 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1378.2488 | 137.1416 | 10.0498 | 1378.2488 | 137.1416 | 10.0498 | 1611.1885 | 160.32 | 10.0498 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 136 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 53.4487 | 40.7233 | 1.3125 | 53.4487 | 40.7233 | 1.3125 | 62.4822 | 47.606 | 1.3125 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 74 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 145.4142 | 22.1582 | 6.5625 | 145.4142 | 22.1582 | 6.5625 | 169.9908 | 25.9032 | 6.5625 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 41 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 46.0982 | 12.2769 | 3.7549 | 46.0982 | 12.2769 | 3.7549 | 53.8893 | 14.3518 | 3.7549 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 93 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 65.5614 | 27.8475 | 2.3543 | 65.5614 | 27.8475 | 2.3543 | 76.642 | 32.5541 | 2.3543 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 18.5876 | 0.59887 | 31.0377 | 18.5876 | 0.59887 | 31.0377 | 21.7291 | 0.70009 | 31.0377 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 34 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 555.0452 | 10.1808 | 54.5187 | 555.0452 | 10.1808 | 54.5187 | 648.8541 | 11.9015 | 54.5187 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 309 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 644.766 | 92.5256 | 6.9685 | 644.766 | 92.5256 | 6.9685 | 753.7388 | 108.1635 | 6.9685 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 657 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1210.6489 | 196.7293 | 6.1539 | 1210.6489 | 196.7293 | 6.1539 | 1415.2624 | 229.9788 | 6.1539 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 75 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 342.5729 | 22.4577 | 15.2542 | 342.5729 | 22.4577 | 15.2542 | 400.4716 | 26.2533 | 15.2542 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 25 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 186.0759 | 7.4859 | 24.8569 | 186.0759 | 7.4859 | 24.8569 | 217.5249 | 8.7511 | 24.8569 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 123 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 624.7291 | 36.8306 | 16.9622 | 624.7291 | 36.8306 | 16.9622 | 730.3154 | 43.0554 | 16.9622 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 319 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 479.2248 | 95.52 | 5.017 | 479.2248 | 95.52 | 5.017 | 560.2193 | 111.664 | 5.017 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 88 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 339.5288 | 26.3503 | 12.8852 | 339.5288 | 26.3503 | 12.8852 | 396.9131 | 30.8039 | 12.8852 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 704 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 989.7054 | 210.8028 | 4.6949 | 989.7054 | 210.8028 | 4.6949 | 1156.9769 | 246.4308 | 4.6949 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 407 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 959.7818 | 121.8703 | 7.8754 | 959.7818 | 121.8703 | 7.8754 | 1121.9958 | 142.4678 | 7.8754 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 137 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 389.681 | 41.0227 | 9.4992 | 389.681 | 41.0227 | 9.4992 | 455.5415 | 47.956 | 9.4992 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 80 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 216.5332 | 23.9549 | 9.0392 | 216.5332 | 23.9549 | 9.0392 | 253.1298 | 28.0035 | 9.0392 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 48 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 368.6686 | 14.3729 | 25.6502 | 368.6686 | 14.3729 | 25.6502 | 430.9777 | 16.8021 | 25.6502 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 42 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 274.7145 | 12.5763 | 21.8438 | 274.7145 | 12.5763 | 21.8438 | 321.1444 | 14.7018 | 21.8438 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 138 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 140.6197 | 41.3221 | 3.403 | 140.6197 | 41.3221 | 3.403 | 164.386 | 48.306 | 3.403 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 12 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 304.0085 | 3.5932 | 84.606 | 304.0085 | 3.5932 | 84.606 | 355.3895 | 4.2005 | 84.606 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 5 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 221.4077 | 1.4972 | 147.8833 | 221.4077 | 1.4972 | 147.8833 | 258.8282 | 1.7502 | 147.8833 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 17 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 17.7423 | 5.0904 | 3.4854 | 17.7423 | 5.0904 | 3.4854 | 20.7409 | 5.9507 | 3.4854 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 107 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 196.2268 | 32.0396 | 6.1245 | 196.2268 | 32.0396 | 6.1245 | 229.3913 | 37.4547 | 6.1245 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2028 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 82 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 142.9356 | 24.5537 | 5.8213 | 142.9356 | 24.5537 | 5.8213 | 167.0934 | 28.7036 | 5.8213 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 19 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 60.5501 | 5.6893 | 10.6428 | 60.5501 | 5.6893 | 10.6428 | 70.7837 | 6.6508 | 10.6428 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2028 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 48.5597 | 0.89831 | 54.0569 | 48.5597 | 0.89831 | 54.0569 | 56.7669 | 1.0501 | 54.0569 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 56 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 24.4415 | 16.7684 | 1.4576 | 24.4415 | 16.7684 | 1.4576 | 28.5724 | 19.6025 | 1.4576 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 80 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 24.6681 | 23.9549 | 1.0298 | 24.6681 | 23.9549 | 1.0298 | 28.8373 | 28.0035 | 1.0298 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 571 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 228.5893 | 170.9778 | 1.337 | 228.5893 | 170.9778 | 1.337 | 267.2235 | 199.875 | 1.337 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 1192 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 282.962 | 356.9274 | 0.79277 | 282.962 | 356.9274 | 0.79277 | 330.7858 | 417.2522 | 0.79277 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 132 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 61.6503 | 39.5255 | 1.5598 | 61.6503 | 39.5255 | 1.5598 | 72.0699 | 46.2058 | 1.5598 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 4.6334 | 1.1977 | 3.8684 | 4.6334 | 1.1977 | 3.8684 | 5.4165 | 1.4002 | 3.8684 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2028 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 38 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 174.9949 | 11.3786 | 15.3794 | 174.9949 | 11.3786 | 15.3794 | 204.571 | 13.3017 | 15.3794 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 3 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.6887 | 0.89831 | 1.8799 | 1.6887 | 0.89831 | 1.8799 | 1.9742 | 1.0501 | 1.8799 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2028 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 1 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 3.9605 | 0.29944 | 13.2265 | 3.9605 | 0.29944 | 13.2265 | 4.6299 | 0.35004 | 13.2265 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2028 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 1 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 13.6308 | 0.29944 | 45.5216 | 13.6308 | 0.29944 | 45.5216 | 15.9345 | 0.35004 | 45.5216 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2028 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 58 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 17.2479 | 17.3673 | 0.99313 | 17.2479 | 17.3673 | 0.99313 | 20.163 | 20.3025 | 0.99313 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2028 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 22 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 5.4765 | 6.5876 | 0.83134 | 5.4765 | 6.5876 | 0.83134 | 6.4021 | 7.701 | 0.83134 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2028 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 248 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.80609 | 74.2601 | 0.010855 | 0.80609 | 74.2601 | 0.010855 | 0.94233 | 86.8109 | 0.010855 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 89 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 36.7962 | 26.6498 | 1.3807 | 36.7962 | 26.6498 | 1.3807 | 43.0152 | 31.1539 | 1.3807 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2028 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 36 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 9.128 | 10.7797 | 0.84678 | 9.128 | 10.7797 | 0.84678 | 10.6707 | 12.6016 | 0.84678 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 209 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 106.6551 | 62.5821 | 1.7042 | 106.6551 | 62.5821 | 1.7042 | 124.681 | 73.1591 | 1.7042 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 277 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 68.7279 | 82.9437 | 0.82861 | 68.7279 | 82.9437 | 0.82861 | 80.3437 | 96.9621 | 0.82861 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 730 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 175.1249 | 218.5881 | 0.80116 | 175.1249 | 218.5881 | 0.80116 | 204.723 | 255.532 | 0.80116 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2028 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 485 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 139.9872 | 145.2263 | 0.96392 | 139.9872 | 145.2263 | 0.96392 | 163.6466 | 169.7712 | 0.96392 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 236 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 533.188 | 70.6668 | 7.5451 | 533.188 | 70.6668 | 7.5451 | 623.3029 | 82.6103 | 7.5451 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2028 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 2 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 90.3172 | 0.59887 | 150.8123 | 90.3172 | 0.59887 | 150.8123 | 105.5818 | 0.70009 | 150.8123 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 134 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 53.0108 | 40.1244 | 1.3212 | 53.0108 | 40.1244 | 1.3212 | 61.9702 | 46.9059 | 1.3212 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2028 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 18 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.2511 | 5.3898 | 2.0875 | 11.2511 | 5.3898 | 2.0875 | 13.1527 | 6.3008 | 2.0875 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2028 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 10 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 4.7628 | 2.9944 | 1.5906 | 4.7628 | 2.9944 | 1.5906 | 5.5678 | 3.5004 | 1.5906 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 167 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 55.6298 | 50.0058 | 1.1125 | 55.6298 | 50.0058 | 1.1125 | 65.0319 | 58.4573 | 1.1125 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 45 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 11.4677 | 13.4746 | 0.85106 | 11.4677 | 13.4746 | 0.85106 | 13.4059 | 15.752 | 0.85106 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2028 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 46 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 41.1366 | 13.774 | 2.9865 | 41.1366 | 13.774 | 2.9865 | 48.0892 | 16.102 | 2.9865 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2028 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 79 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 34.4802 | 23.6554 | 1.4576 | 34.4802 | 23.6554 | 1.4576 | 40.3077 | 27.6535 | 1.4576 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2028 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 82 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.704 | 24.5537 | 0.11013 | 2.704 | 24.5537 | 0.11013 | 3.161 | 28.7036 | 0.11013 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2028 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 13 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.45015 | 3.8927 | 0.11564 | 0.45015 | 3.8927 | 0.11564 | 0.52622 | 4.5506 | 0.11564 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 1 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 62.4639 | 0.29944 | 208.6054 | 62.4639 | 0.29944 | 208.6054 | 73.021 | 0.35004 | 208.6054 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2028 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 14 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 8.9573 | 4.1921 | 2.1367 | 8.9573 | 4.1921 | 2.1367 | 10.4711 | 4.9006 | 2.1367 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2028 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 96 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.7807 | 28.7458 | 0.061948 | 1.7807 | 28.7458 | 0.061948 | 2.0817 | 33.6042 | 0.061948 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 211 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 625.2178 | 63.1809 | 9.8957 | 625.2178 | 63.1809 | 9.8957 | 730.8867 | 73.8592 | 9.8957 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2028 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 22 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 3.7465 | 6.5876 | 0.56872 | 3.7465 | 6.5876 | 0.56872 | 4.3797 | 7.701 | 0.56872 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2028 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.32156 | 0.29944 | 1.0739 | 0.32156 | 0.29944 | 1.0739 | 0.37591 | 0.35004 | 1.0739 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 376 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 479.4093 | 112.5878 | 4.2581 | 479.4093 | 112.5878 | 4.2581 | 560.435 | 131.6165 | 4.2581 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2028 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 1 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.28982 | 0.29944 | 0.9679 | 0.28982 | 0.29944 | 0.9679 | 0.33881 | 0.35004 | 0.9679 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2028 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 184 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 252.094 | 55.0962 | 4.5755 | 252.094 | 55.0962 | 4.5755 | 294.7007 | 64.4081 | 4.5755 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 14 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 6.9875 | 4.1921 | 1.6668 | 6.9875 | 4.1921 | 1.6668 | 8.1685 | 4.9006 | 1.6668 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 2 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.128 | 0.59887 | 6.893 | 4.128 | 0.59887 | 6.893 | 4.8257 | 0.70009 | 6.893 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2028 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 40 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 45.8033 | 11.9774 | 3.8241 | 45.8033 | 11.9774 | 3.8241 | 53.5446 | 14.0018 | 3.8241 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 56 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 284.0073 | 16.7684 | 16.9371 | 284.0073 | 16.7684 | 16.9371 | 332.0078 | 19.6025 | 16.9371 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.7897 | 0.89831 | 0.8791 | 0.7897 | 0.89831 | 0.8791 | 0.92317 | 1.0501 | 0.8791 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2028 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 1 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.074294 | 0.29944 | 0.24811 | 0.074294 | 0.29944 | 0.24811 | 0.08685 | 0.35004 | 0.24811 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2028 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 11 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.088634 | 3.2938 | 0.026909 | 0.088634 | 3.2938 | 0.026909 | 0.10361 | 3.8505 | 0.026909 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2028 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 277 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 41.3134 | 82.9437 | 0.49809 | 41.3134 | 82.9437 | 0.49809 | 48.2958 | 96.9621 | 0.49809 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2028 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 87 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 4.8841 | 26.0509 | 0.18748 | 4.8841 | 26.0509 | 0.18748 | 5.7095 | 30.4538 | 0.18748 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 12 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 19.4933 | 3.5932 | 5.425 | 19.4933 | 3.5932 | 5.425 | 22.7878 | 4.2005 | 5.425 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 8 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.7715 | 2.3955 | 0.73952 | 1.7715 | 2.3955 | 0.73952 | 2.0709 | 2.8004 | 0.73952 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 56 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 2.8676 | 16.7684 | 0.17101 | 2.8676 | 16.7684 | 0.17101 | 3.3522 | 19.6025 | 0.17101 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2028 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 45 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 38.9439 | 13.4746 | 2.8902 | 38.9439 | 13.4746 | 2.8902 | 45.5258 | 15.752 | 2.8902 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2028 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 20 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 14.0656 | 5.9887 | 2.3487 | 14.0656 | 5.9887 | 2.3487 | 16.4428 | 7.0009 | 2.3487 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 375 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 185.4129 | 112.2884 | 1.6512 | 185.4129 | 112.2884 | 1.6512 | 216.7498 | 131.2664 | 1.6512 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2028 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 47 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.1925 | 14.0735 | 0.15579 | 2.1925 | 14.0735 | 0.15579 | 2.5631 | 16.4521 | 0.15579 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 23 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 350.0629 | 6.887 | 50.8294 | 350.0629 | 6.887 | 50.8294 | 409.2275 | 8.051 | 50.8294 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2028 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 104 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 1.822 | 31.1413 | 0.058507 | 1.822 | 31.1413 | 0.058507 | 2.1299 | 36.4046 | 0.058507 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 26 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 117.6384 | 7.7853 | 15.1103 | 117.6384 | 7.7853 | 15.1103 | 137.5206 | 9.1011 | 15.1103 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2028 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 89 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 13.5581 | 26.6498 | 0.50875 | 13.5581 | 26.6498 | 0.50875 | 15.8496 | 31.1539 | 0.50875 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2028 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 2 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 10.7819 | 0.59887 | 18.0037 | 10.7819 | 0.59887 | 18.0037 | 12.6042 | 0.70009 | 18.0037 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 34 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 489.8651 | 10.1808 | 48.1165 | 489.8651 | 10.1808 | 48.1165 | 572.6579 | 11.9015 | 48.1165 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2028 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 36 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 55.7749 | 10.7797 | 5.1741 | 55.7749 | 10.7797 | 5.1741 | 65.2015 | 12.6016 | 5.1741 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 341 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 16.6149 | 102.1076 | 0.16272 | 16.6149 | 102.1076 | 0.16272 | 19.423 | 119.3649 | 0.16272 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 23 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.6843 | 6.887 | 0.82536 | 5.6843 | 6.887 | 0.82536 | 6.645 | 8.051 | 0.82536 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 2 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.0652 | 0.59887 | 1.7786 | 1.0652 | 0.59887 | 1.7786 | 1.2452 | 0.70009 | 1.7786 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2028 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 161 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 5.4996 | 48.2092 | 0.11408 | 5.4996 | 48.2092 | 0.11408 | 6.4291 | 56.357 | 0.11408 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2028 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 154 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 41.7314 | 46.1131 | 0.90498 | 41.7314 | 46.1131 | 0.90498 | 48.7844 | 53.9067 | 0.90498 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 126 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 64.3998 | 37.7289 | 1.7069 | 64.3998 | 37.7289 | 1.7069 | 75.2841 | 44.1055 | 1.7069 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 97 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 216.8136 | 29.0453 | 7.4647 | 216.8136 | 29.0453 | 7.4647 | 253.4576 | 33.9542 | 7.4647 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2028 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 10 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 27.148 | 2.9944 | 9.0664 | 27.148 | 2.9944 | 9.0664 | 31.7363 | 3.5004 | 9.0664 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 593 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 294.1909 | 177.5654 | 1.6568 | 294.1909 | 177.5654 | 1.6568 | 343.9125 | 207.576 | 1.6568 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 510 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 123.2314 | 152.7122 | 0.80695 | 123.2314 | 152.7122 | 0.80695 | 144.0589 | 178.5223 | 0.80695 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 214 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 444.2579 | 64.0792 | 6.9329 | 444.2579 | 64.0792 | 6.9329 | 519.3425 | 74.9094 | 6.9329 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2028 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 170 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 220.4842 | 50.9041 | 4.3314 | 220.4842 | 50.9041 | 4.3314 | 257.7485 | 59.5074 | 4.3314 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2028 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 44 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 27.3601 | 13.1752 | 2.0766 | 27.3601 | 13.1752 | 2.0766 | 31.9842 | 15.4019 | 2.0766 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2028 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 3 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.2769 | 0.89831 | 1.4215 | 1.2769 | 0.89831 | 1.4215 | 1.4927 | 1.0501 | 1.4215 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 182 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 159.3136 | 54.4973 | 2.9233 | 159.3136 | 54.4973 | 2.9233 | 186.2394 | 63.708 | 2.9233 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 316 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 135.3647 | 94.6217 | 1.4306 | 135.3647 | 94.6217 | 1.4306 | 158.2428 | 110.6138 | 1.4306 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2028 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 22 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.081067 | 6.5876 | 0.012306 | 0.081067 | 6.5876 | 0.012306 | 0.094768 | 7.701 | 0.012306 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 375 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 69.9765 | 112.2884 | 0.62319 | 69.9765 | 112.2884 | 0.62319 | 81.8033 | 131.2664 | 0.62319 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 113 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 152.0946 | 33.8362 | 4.495 | 152.0946 | 33.8362 | 4.495 | 177.8003 | 39.5549 | 4.495 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 254 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 398.5988 | 76.0567 | 5.2408 | 398.5988 | 76.0567 | 5.2408 | 465.9666 | 88.9111 | 5.2408 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 570 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 290.1396 | 170.6784 | 1.6999 | 290.1396 | 170.6784 | 1.6999 | 339.1765 | 199.525 | 1.6999 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 73 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 253.7687 | 21.8588 | 11.6094 | 253.7687 | 21.8588 | 11.6094 | 296.6585 | 25.5532 | 11.6094 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 239 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 161.7017 | 71.5651 | 2.2595 | 161.7017 | 71.5651 | 2.2595 | 189.0311 | 83.6605 | 2.2595 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%

## Off_Cycle_Patrol
Off Cycle Patrol - Risk & Cost Benefit | [30 empty] | Summary Table |  |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[31 empty] | Year | Total Units (HFTD Miles) | Total Units (Trees) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%) | Transmission Units (Miles)
back to index | [30 empty] | 2026 | 3958.7913 | 246834 | 2892488.839 | 139029.6154 | 4.807% | 132624.8076 | 2717.2041 | 48.8093 | 132624.8076 | 2717.2041 | 48.8093 | 139711.1331 | 2862.3881 | 48.8093 | 4.585% | 891.2087
[10 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [12 empty] | 2027 | 3958.7913 | 246834 | 2892488.839 | 139029.6154 | 4.807% | 126515.0561 | 2592.0281 | 48.8093 | 126515.0561 | 2592.0281 | 48.8093 | 140395.9916 | 2876.4194 | 48.8093 | 4.585% | 891.2087
[10 empty] | Capital Cost only in Year 0 | 0.71952 | K$/mile | 2025-06-30 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [12 empty] | 2028 | 3958.7913 | 246834 | 2892488.839 | 139029.6154 | 4.807% | 120686.7683 | 2472.6187 | 48.8093 | 120686.7683 | 2472.6187 | 48.8093 | 141084.2073 | 2890.5195 | 48.8093 | 4.585% | 891.2087
[10 empty] | Service Drop factor | 0% | % | 2025-06-30 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [12 empty] | Total 2026-2028 | 11876.374 | 740502 | 8677466.5171 | 417088.8462 | 4.807% | 379826.632 | 7781.851 | 48.8093 | 379826.632 | 7781.851 | 48.8093 | 421191.332 | 8629.3269 | 48.8093 | 13.75% | 2673.626
[10 empty] | OH to UG conversion factor | 0% | % | 2025-06-30
[10 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-06-30
[10 empty] | Lifetime | 1 | Years | 2025-06-30
[10 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[10 empty] | Mitigation Effectiveness Estimate (%) | 4.95% | % | 2025-06-30
[10 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-06-30
[14 empty] | [1] | [1] | [1] | [2]
[9 empty] | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total HFTD Circuit Miles | Total Units | %Trees in the Scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 1.5002 | 11 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.9468 | 1.0297 | 1.8907 | 1.9468 | 1.0297 | 1.8907 | 2.0508 | 1.0847 | 1.8907 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 11.503 | 607 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 530.5991 | 7.8954 | 67.204 | 530.5991 | 7.8954 | 67.204 | 558.9498 | 8.3172 | 67.204 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2026 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 2.7701 | 39 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 32.1455 | 1.9013 | 16.9073 | 32.1455 | 1.9013 | 16.9073 | 33.8631 | 2.0029 | 16.9073 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 13.4184 | 1097 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1514.5818 | 9.21 | 164.45 | 1514.5818 | 9.21 | 164.45 | 1595.508 | 9.7021 | 164.45 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 10.907 | 484 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 431.684 | 7.4862 | 57.6637 | 431.684 | 7.4862 | 57.6637 | 454.7494 | 7.8862 | 57.6637 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 6.1667 | 154 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 748.0666 | 4.2326 | 176.7378 | 748.0666 | 4.2326 | 176.7378 | 788.0369 | 4.4588 | 176.7378 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 7.1517 | 253 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 320.0792 | 4.9087 | 65.206 | 320.0792 | 4.9087 | 65.206 | 337.1815 | 5.171 | 65.206 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2026 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 1.4833 | 110 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.602 | 1.0181 | 12.3781 | 12.602 | 1.0181 | 12.3781 | 13.2754 | 1.0725 | 12.3781 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 2.9682 | 235 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 327.0901 | 2.0373 | 160.5509 | 327.0901 | 2.0373 | 160.5509 | 344.567 | 2.1462 | 160.5509 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2026 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.006061 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.28378 | 0.0041601 | 68.2142 | 0.28378 | 0.0041601 | 68.2142 | 0.29894 | 0.0043824 | 68.2142 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2026 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.05303 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 1.0269 | 0.036398 | 28.2128 | 1.0269 | 0.036398 | 28.2128 | 1.0818 | 0.038343 | 28.2128 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 0.91212 | 44 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.12044 | 0.62605 | 0.19239 | 0.12044 | 0.62605 | 0.19239 | 0.12688 | 0.65951 | 0.19239 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 10.9006 | 354 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 142.1765 | 7.4819 | 19.0028 | 142.1765 | 7.4819 | 19.0028 | 149.7732 | 7.8816 | 19.0028 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 2.4656 | 133 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 36.5689 | 1.6923 | 21.609 | 36.5689 | 1.6923 | 21.609 | 38.5229 | 1.7827 | 21.609 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2026 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 3.214 | 0 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 484.7261 | 2.206 | 219.7307 | 484.7261 | 2.206 | 219.7307 | 510.6256 | 2.3239 | 219.7307 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 6.1051 | 1144 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 182.2481 | 4.1904 | 43.4921 | 182.2481 | 4.1904 | 43.4921 | 191.9859 | 4.4143 | 43.4921 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.68239 | 53 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 65.2006 | 0.46837 | 139.2073 | 65.2006 | 0.46837 | 139.2073 | 68.6844 | 0.4934 | 139.2073 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 14.6369 | 996 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1264.5743 | 10.0464 | 125.874 | 1264.5743 | 10.0464 | 125.874 | 1332.1422 | 10.5831 | 125.874 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 19.7983 | 971 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 205.1652 | 13.589 | 15.0979 | 205.1652 | 13.589 | 15.0979 | 216.1274 | 14.3151 | 15.0979 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 11.9253 | 973 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 262.6012 | 8.1852 | 32.0823 | 262.6012 | 8.1852 | 32.0823 | 276.6324 | 8.6226 | 32.0823 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 33.1318 | 3231 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 151.314 | 22.7408 | 6.6539 | 151.314 | 22.7408 | 6.6539 | 159.3989 | 23.9558 | 6.6539 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 16.5267 | 1132 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 173.5489 | 11.3434 | 15.2995 | 173.5489 | 11.3434 | 15.2995 | 182.8218 | 11.9495 | 15.2995 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2026 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 0.5464 | 0 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 32.5317 | 0.37503 | 86.7434 | 32.5317 | 0.37503 | 86.7434 | 34.2699 | 0.39507 | 86.7434 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2026 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 0.4381 | 32 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.3639 | 0.3007 | 1.2102 | 0.3639 | 0.3007 | 1.2102 | 0.38334 | 0.31677 | 1.2102 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 11.0409 | 793 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 405.8445 | 7.5781 | 53.5546 | 405.8445 | 7.5781 | 53.5546 | 427.5294 | 7.9831 | 53.5546 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 27.7167 | 985 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 240.4359 | 19.024 | 12.6386 | 240.4359 | 19.024 | 12.6386 | 253.2827 | 20.0405 | 12.6386 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 4.0256 | 262 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.17656 | 2.7631 | 0.063899 | 0.17656 | 2.7631 | 0.063899 | 0.18599 | 2.9107 | 0.063899 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 5.4265 | 741 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 548.8338 | 3.7246 | 147.3539 | 548.8338 | 3.7246 | 147.3539 | 578.1587 | 3.9236 | 147.3539 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 4.9148 | 635 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 33.6771 | 3.3734 | 9.9832 | 33.6771 | 3.3734 | 9.9832 | 35.4765 | 3.5536 | 9.9832 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2026 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 4.5371 | 0 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 93.8928 | 3.1141 | 30.1505 | 93.8928 | 3.1141 | 30.1505 | 98.9097 | 3.2805 | 30.1505 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 2.7532 | 47 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 239.9918 | 1.8897 | 126.9984 | 239.9918 | 1.8897 | 126.9984 | 252.8149 | 1.9907 | 126.9984 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 9.5078 | 558 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 577.5146 | 6.5259 | 88.4963 | 577.5146 | 6.5259 | 88.4963 | 608.372 | 6.8746 | 88.4963 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2026 | 595 | 595-1454F | Tier-2 | Tier-2---15 | 3--4 | 0.5388 | 0 | 100% | 124.9246 | 83.27% | 16% | 0.7306% | 5.1495 | 0 | 0 | 5.1495 | 0 | 4.9122 | 0.36982 | 13.2829 | 4.9122 | 0.36982 | 13.2829 | 5.1747 | 0.38958 | 13.2829 | 4.122% | 0.018776 | 0.017847 | 6653.3471 | 1471.8841 | 978.4778 | 4202.9852 | 6711.3017 | 0 | 0 | 6711.3017 | 0.0001698%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 10.1674 | 900 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 262.0699 | 6.9786 | 37.5533 | 262.0699 | 6.9786 | 37.5533 | 276.0727 | 7.3515 | 37.5533 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 16.5478 | 1001 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 287.5688 | 11.3579 | 25.3188 | 287.5688 | 11.3579 | 25.3188 | 302.934 | 11.9648 | 25.3188 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 10.9521 | 913 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 708.5447 | 7.5172 | 94.2565 | 708.5447 | 7.5172 | 94.2565 | 746.4032 | 7.9189 | 94.2565 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2026 | 834 | 834-887AE | Tier-2 | Tier-2---17 | 2--4 | 0.2229 | 0 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 3.435 | 0 | 0 | 3.435 | 0 | 3.2767 | 0.15299 | 21.4175 | 3.2767 | 0.15299 | 21.4175 | 3.4518 | 0.16117 | 21.4175 | 4.883% | 0.0050886 | 0.0048367 | 13824.3748 | 4928.7906 | 56.7151 | 8838.8691 | 13834.1342 | 0 | 0 | 13834.1342 | 0.0001133%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 5.0727 | 200 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 30.0665 | 3.4817 | 8.6354 | 30.0665 | 3.4817 | 8.6354 | 31.673 | 3.6678 | 8.6354 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 18.3176 | 1095 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 497.9891 | 12.5727 | 39.6088 | 497.9891 | 12.5727 | 39.6088 | 524.5974 | 13.2445 | 39.6088 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 9.4852 | 908 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 550.6852 | 6.5104 | 84.5854 | 550.6852 | 6.5104 | 84.5854 | 580.1091 | 6.8583 | 84.5854 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 1.2773 | 46 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 26.8592 | 0.87668 | 30.6373 | 26.8592 | 0.87668 | 30.6373 | 28.2944 | 0.92353 | 30.6373 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 5.1553 | 245 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 83.482 | 3.5385 | 23.5927 | 83.482 | 3.5385 | 23.5927 | 87.9426 | 3.7275 | 23.5927 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 4.2257 | 150 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 87.8513 | 2.9004 | 30.2891 | 87.8513 | 2.9004 | 30.2891 | 92.5454 | 3.0554 | 30.2891 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 18.9327 | 1235 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 960.4166 | 12.9949 | 73.9072 | 960.4166 | 12.9949 | 73.9072 | 1011.733 | 13.6892 | 73.9072 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 6.4307 | 308 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 253.85 | 4.4139 | 57.5119 | 253.85 | 4.4139 | 57.5119 | 267.4135 | 4.6497 | 57.5119 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 3.8006 | 169 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 376.4593 | 2.6086 | 144.3148 | 376.4593 | 2.6086 | 144.3148 | 396.5741 | 2.748 | 144.3148 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 7.0653 | 484 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 635.4631 | 4.8494 | 131.0383 | 635.4631 | 4.8494 | 131.0383 | 669.4168 | 5.1086 | 131.0383 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 6.825 | 1960 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 22.2618 | 4.6845 | 4.7522 | 22.2618 | 4.6845 | 4.7522 | 23.4513 | 4.9348 | 4.7522 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2026 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.56254 | 0 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.8521 | 0.38611 | 15.1564 | 5.8521 | 0.38611 | 15.1564 | 6.1647 | 0.40674 | 15.1564 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 2.4665 | 104 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 281.9725 | 1.6929 | 166.5592 | 281.9725 | 1.6929 | 166.5592 | 297.0387 | 1.7834 | 166.5592 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 5.4023 | 504 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 50.8518 | 3.708 | 13.7142 | 50.8518 | 3.708 | 13.7142 | 53.5689 | 3.9061 | 13.7142 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 12.4913 | 384 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 78.3562 | 8.5737 | 9.1392 | 78.3562 | 8.5737 | 9.1392 | 82.5429 | 9.0318 | 9.1392 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2026 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 6.96 | 531 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 45.4 | 4.7772 | 9.5035 | 45.4 | 4.7772 | 9.5035 | 47.8258 | 5.0324 | 9.5035 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 6.5853 | 30 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 61.1985 | 4.5199 | 13.5396 | 61.1985 | 4.5199 | 13.5396 | 64.4684 | 4.7615 | 13.5396 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2026 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3.0366 | 18 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 53.3631 | 2.0842 | 25.6036 | 53.3631 | 2.0842 | 25.6036 | 56.2144 | 2.1956 | 25.6036 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.45755 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 63.2779 | 0.31405 | 201.4889 | 63.2779 | 0.31405 | 201.4889 | 66.6589 | 0.33083 | 201.4889 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2026 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 2.2489 | 0 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 23.0859 | 1.5436 | 14.9561 | 23.0859 | 1.5436 | 14.9561 | 24.3194 | 1.6261 | 14.9561 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 6.4636 | 102 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 384.6902 | 4.4365 | 86.711 | 384.6902 | 4.4365 | 86.711 | 405.2447 | 4.6735 | 86.711 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 10.8632 | 1047 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 478.0277 | 7.4562 | 64.1113 | 478.0277 | 7.4562 | 64.1113 | 503.5694 | 7.8546 | 64.1113 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 2.4735 | 109 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 204.4821 | 1.6978 | 120.4425 | 204.4821 | 1.6978 | 120.4425 | 215.4079 | 1.7885 | 120.4425 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 19.4561 | 1637 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 130.6179 | 13.3541 | 9.7811 | 130.6179 | 13.3541 | 9.7811 | 137.597 | 14.0676 | 9.7811 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 5.3305 | 265 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 104.6722 | 3.6587 | 28.6091 | 104.6722 | 3.6587 | 28.6091 | 110.265 | 3.8542 | 28.6091 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 2.3455 | 217 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 203.6169 | 1.6099 | 126.4793 | 203.6169 | 1.6099 | 126.4793 | 214.4964 | 1.6959 | 126.4793 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 2.4583 | 130 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 299.7005 | 1.6873 | 177.6183 | 299.7005 | 1.6873 | 177.6183 | 315.7139 | 1.7775 | 177.6183 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2026 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.038636 | 0 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.78372 | 0.026519 | 29.5536 | 0.78372 | 0.026519 | 29.5536 | 0.8256 | 0.027936 | 29.5536 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 13.767 | 1095 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 602.1374 | 9.4493 | 63.7229 | 602.1374 | 9.4493 | 63.7229 | 634.3104 | 9.9542 | 63.7229 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 3.6616 | 66 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.981 | 2.5132 | 4.7672 | 11.981 | 2.5132 | 4.7672 | 12.6212 | 2.6475 | 4.7672 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 12.7815 | 1809 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1267.761 | 8.7729 | 144.5095 | 1267.761 | 8.7729 | 144.5095 | 1335.4992 | 9.2416 | 144.5095 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 13.6103 | 587 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 115.3852 | 9.3417 | 12.3516 | 115.3852 | 9.3417 | 12.3516 | 121.5504 | 9.8409 | 12.3516 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.057008 | 0 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.8232 | 0.039129 | 97.7076 | 3.8232 | 0.039129 | 97.7076 | 4.0275 | 0.041219 | 97.7076 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2026 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 0.94167 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.86782 | 0.64633 | 1.3427 | 0.86782 | 0.64633 | 1.3427 | 0.91419 | 0.68087 | 1.3427 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2026 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 5.9186 | 504 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.88582 | 4.0623 | 0.21806 | 0.88582 | 4.0623 | 0.21806 | 0.93315 | 4.2794 | 0.21806 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 6.9741 | 633 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 886.2644 | 4.7868 | 185.1477 | 886.2644 | 4.7868 | 185.1477 | 933.6187 | 5.0426 | 185.1477 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 0.3653 | 62 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.57934 | 0.25073 | 2.3106 | 0.57934 | 0.25073 | 2.3106 | 0.61029 | 0.26413 | 2.3106 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.93788 | 186 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.1512 | 0.64373 | 4.8952 | 3.1512 | 0.64373 | 4.8952 | 3.3196 | 0.67813 | 4.8952 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 1.7432 | 329 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 24.149 | 1.1965 | 20.1834 | 24.149 | 1.1965 | 20.1834 | 25.4394 | 1.2604 | 20.1834 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 1.4693 | 14 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 95.5517 | 1.0085 | 94.7483 | 95.5517 | 1.0085 | 94.7483 | 100.6572 | 1.0624 | 94.7483 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.3089 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.3203 | 0.21202 | 10.9436 | 2.3203 | 0.21202 | 10.9436 | 2.4442 | 0.22335 | 10.9436 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2026 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 2.6153 | 70 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.4094 | 1.7951 | 1.3422 | 2.4094 | 1.7951 | 1.3422 | 2.5382 | 1.891 | 1.3422 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2026 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.62576 | 68 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 10.0309 | 0.4295 | 23.3546 | 10.0309 | 0.4295 | 23.3546 | 10.5669 | 0.45245 | 23.3546 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 6.2526 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 193.8402 | 4.2916 | 45.167 | 193.8402 | 4.2916 | 45.167 | 204.1973 | 4.5209 | 45.167 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2026 | 308 | 308-485AE | Tier-2 | Tier-2---15 | 4--3 | 0.7398 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.217 | 0 | 0 | 0.217 | 0 | 0.207 | 0.50778 | 0.40766 | 0.207 | 0.50778 | 0.40766 | 0.21806 | 0.53491 | 0.40766 | 0.1374% | 0.034738 | 0.033018 | 4547.6785 | 25.2626 | 4047.4864 | 474.9295 | 4777.9399 | 0 | 0 | 4777.9399 | 7.156e-06%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 2.4644 | 81 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 22.199 | 1.6915 | 13.1238 | 22.199 | 1.6915 | 13.1238 | 23.3851 | 1.7819 | 13.1238 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 8.4758 | 325 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 83.7784 | 5.8175 | 14.401 | 83.7784 | 5.8175 | 14.401 | 88.2548 | 6.1284 | 14.401 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 10.6674 | 415 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 936.1138 | 7.3218 | 127.8529 | 936.1138 | 7.3218 | 127.8529 | 986.1317 | 7.713 | 127.8529 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2026 | 94 | 94-24F | Tier-2 | Tier-2---18 | 3--3 | 4.1867 | 0 | 100% | 46.367 | 91.68% | 0% | 8.321% | 2.1042 | 0 | 0 | 2.1042 | 0 | 2.0073 | 2.8736 | 0.69851 | 2.0073 | 2.8736 | 0.69851 | 2.1145 | 3.0272 | 0.69851 | 4.538% | 0.020922 | 0.019886 | 2216.1834 | 511.0324 | 89.3586 | 1615.7924 | 2225.7865 | 0 | 0 | 2225.7865 | 6.939e-05%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 4.8975 | 159 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 66.5395 | 3.3615 | 19.7945 | 66.5395 | 3.3615 | 19.7945 | 70.0948 | 3.5411 | 19.7945 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 2.7176 | 182 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.6262 | 1.8653 | 4.0885 | 7.6262 | 1.8653 | 4.0885 | 8.0337 | 1.9649 | 4.0885 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2026 | 454 | 454-49F | Tier-2 | Tier-2---13 | 4--3 | 0.4782 | 0 | 100% | 292.9743 | 76.06% | 23.59% | 0.3558% | 11.0299 | 0 | 0 | 11.0299 | 0 | 10.5217 | 0.32822 | 32.0567 | 10.5217 | 0.32822 | 32.0567 | 11.0839 | 0.34576 | 32.0567 | 3.765% | 0.077203 | 0.073382 | 3794.8464 | 847.9473 | 816.929 | 2129.9701 | 3842.1656 | 0 | 0 | 3842.1656 | 0.0003637%
2026 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.01875 | 0 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.7021 | 0.012869 | 54.5554 | 0.7021 | 0.012869 | 54.5554 | 0.73961 | 0.013557 | 54.5554 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 0.095455 | 52 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.7918 | 0.065518 | 27.3479 | 1.7918 | 0.065518 | 27.3479 | 1.8875 | 0.069018 | 27.3479 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 7.6085 | 759 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 137.9346 | 5.2223 | 26.4127 | 137.9346 | 5.2223 | 26.4127 | 145.3046 | 5.5013 | 26.4127 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2026 | 205 | 205-1550 | Tier-2 | Tier-2---15 | 2--4 | 0.97858 | 11 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 6.0476 | 0 | 0 | 6.0476 | 0 | 5.769 | 0.67167 | 8.589 | 5.769 | 0.67167 | 8.589 | 6.0772 | 0.70756 | 8.589 | 4.877% | 0.008789 | 0.0083539 | 14109.2738 | 2221.4405 | 309.7116 | 11578.1217 | 14120.1329 | 0 | 0 | 14120.1329 | 0.0001994%
2026 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.47178 | 4 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 5.3951 | 0.32382 | 16.661 | 5.3951 | 0.32382 | 16.661 | 5.6834 | 0.34112 | 16.661 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 6.7553 | 1534 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 135.4211 | 4.6367 | 29.2065 | 135.4211 | 4.6367 | 29.2065 | 142.6568 | 4.8844 | 29.2065 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.10398 | 8 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.9848 | 0.071367 | 167.9317 | 11.9848 | 0.071367 | 167.9317 | 12.6251 | 0.07518 | 167.9317 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 12.5093 | 734 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 408.7995 | 8.586 | 47.6122 | 408.7995 | 8.586 | 47.6122 | 430.6423 | 9.0448 | 47.6122 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 6.6007 | 793 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 148.7546 | 4.5306 | 32.8336 | 148.7546 | 4.5306 | 32.8336 | 156.7028 | 4.7726 | 32.8336 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2026 | 197 | 197-1150F | Tier-2 | Tier-2---15 | 3--4 | 1.3604 | 3 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 9.0248 | 0 | 0 | 9.0248 | 0 | 8.609 | 0.93375 | 9.2198 | 8.609 | 0.93375 | 9.2198 | 9.069 | 0.98364 | 9.2198 | 4.917% | 0.021777 | 0.020699 | 8428.1597 | 1361.8326 | 10.8364 | 7055.4907 | 8431.076 | 0 | 0 | 8431.076 | 0.0002976%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 13.7784 | 951 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 84.8362 | 9.4571 | 8.9706 | 84.8362 | 9.4571 | 8.9706 | 89.3691 | 9.9624 | 8.9706 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 5.0748 | 149 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 183.9861 | 3.4832 | 52.8211 | 183.9861 | 3.4832 | 52.8211 | 193.8167 | 3.6693 | 52.8211 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 3.0297 | 20 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 55.7189 | 2.0795 | 26.7943 | 55.7189 | 2.0795 | 26.7943 | 58.6961 | 2.1906 | 26.7943 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 5.1365 | 315 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 118.5279 | 3.5256 | 33.6194 | 118.5279 | 3.5256 | 33.6194 | 124.861 | 3.714 | 33.6194 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 10.0072 | 260 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 70.4248 | 6.8687 | 10.2531 | 70.4248 | 6.8687 | 10.2531 | 74.1877 | 7.2357 | 10.2531 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 3.7138 | 156 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 105.2609 | 2.5491 | 41.2937 | 105.2609 | 2.5491 | 41.2937 | 110.8851 | 2.6853 | 41.2937 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 3.1481 | 153 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 146.4383 | 2.1607 | 67.7721 | 146.4383 | 2.1607 | 67.7721 | 154.2627 | 2.2762 | 67.7721 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 4.4941 | 222 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 430.6267 | 3.0846 | 139.6036 | 430.6267 | 3.0846 | 139.6036 | 453.6357 | 3.2495 | 139.6036 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2026 | 241 | CB 241 | Tier-2 | Tier-2---11 | 5--4 | 1.5013 | 0 | 100% | 614.4843 | 5.233% | 94.45% | 0.3166% | 1.5918 | 0 | 0 | 1.5918 | 0 | 1.5184 | 1.0305 | 1.4736 | 1.5184 | 1.0305 | 1.4736 | 1.5996 | 1.0855 | 1.4736 | 0.259% | 0.096356 | 0.091586 | 6377.2296 | 31.8975 | 5684.1218 | 661.2103 | 6691.9621 | 0 | 0 | 6691.9621 | 5.249e-05%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 14.1729 | 537 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 491.6709 | 9.7279 | 50.5425 | 491.6709 | 9.7279 | 50.5425 | 517.9415 | 10.2476 | 50.5425 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2026 | 855 | 855-46AE | Tier-2 | Tier-2---15 | 1--5 | 0.25303 | 1 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 9.3224 | 0 | 0 | 9.3224 | 0 | 8.893 | 0.17367 | 51.2053 | 8.893 | 0.17367 | 51.2053 | 9.3681 | 0.18295 | 51.2053 | 4.944% | 0.0010888 | 0.0010349 | 173174.957 | 50966.8705 | 22.9996 | 122185.0869 | 173185.5197 | 0 | 0 | 173185.5197 | 0.0003074%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 3.6236 | 238 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.6768 | 2.4872 | 2.2824 | 5.6768 | 2.4872 | 2.2824 | 5.9801 | 2.6201 | 2.2824 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2026 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.12822 | 0 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 14.647 | 0.088007 | 166.4305 | 14.647 | 0.088007 | 166.4305 | 15.4296 | 0.092709 | 166.4305 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2026 | 928 | CB 928 | Tier-2 | Tier-2---7 | 4--5 | 3.1426 | 3 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 65.3395 | 0 | 0 | 65.3395 | 0 | 62.3294 | 2.157 | 28.8963 | 62.3294 | 2.157 | 28.8963 | 65.6598 | 2.2723 | 28.8963 | 3.948% | 0.057199 | 0.054367 | 28934.4603 | 4597.4585 | 5524.6499 | 18812.3519 | 29239.4879 | 0 | 0 | 29239.4879 | 0.002155%
2026 | 1202 | 1202-9 | Tier-2 | Tier-2---17 | 2--4 | 0.7689 | 0 | 100% | 73.4421 | 96.84% | 0% | 3.16% | 3.5205 | 0 | 0 | 3.5205 | 0 | 3.3583 | 0.52775 | 6.3635 | 3.3583 | 0.52775 | 6.3635 | 3.5378 | 0.55595 | 6.3635 | 4.794% | 0.01182 | 0.011235 | 6213.48 | 1453.8319 | 498.5132 | 4261.1349 | 6223.7055 | 0 | 0 | 6223.7055 | 0.0001161%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 24.8581 | 448 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 479.8394 | 17.0619 | 28.1234 | 479.8394 | 17.0619 | 28.1234 | 505.4779 | 17.9736 | 28.1234 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2026 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 0.42306 | 23 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.49467 | 0.29038 | 1.7036 | 0.49467 | 0.29038 | 1.7036 | 0.5211 | 0.30589 | 1.7036 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 13.0331 | 1531 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 873.3342 | 8.9456 | 97.6275 | 873.3342 | 8.9456 | 97.6275 | 919.9977 | 9.4235 | 97.6275 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 8.4165 | 712 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 543.0092 | 5.7769 | 93.9972 | 543.0092 | 5.7769 | 93.9972 | 572.0229 | 6.0855 | 93.9972 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 11.5724 | 1687 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 124.1616 | 7.943 | 15.6317 | 124.1616 | 7.943 | 15.6317 | 130.7958 | 8.3674 | 15.6317 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 16.5898 | 1991 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 734.3072 | 11.3868 | 64.4877 | 734.3072 | 11.3868 | 64.4877 | 773.5422 | 11.9952 | 64.4877 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 3.9667 | 215 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 88.4542 | 2.7226 | 32.4888 | 88.4542 | 2.7226 | 32.4888 | 93.1805 | 2.8681 | 32.4888 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 4.5633 | 392 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 461.0302 | 3.1321 | 147.1955 | 461.0302 | 3.1321 | 147.1955 | 485.6637 | 3.2994 | 147.1955 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2026 | 178 | 178-982 | Tier-2 | Tier-2---21 | 1--1 | 0.68407 | 9 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0063254 | 0 | 0 | 0.0063254 | 0 | 0.006034 | 0.46953 | 0.012851 | 0.006034 | 0.46953 | 0.012851 | 0.0063564 | 0.49462 | 0.012851 | 0.6625% | 0.0033454 | 0.0031798 | 285.4035 | 0.62363 | 58.6739 | 226.106 | 298.2775 | 0 | 0 | 298.2775 | 2.086e-07%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 4.3521 | 410 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 147.7158 | 2.9871 | 49.4506 | 147.7158 | 2.9871 | 49.4506 | 155.6084 | 3.1467 | 49.4506 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2026 | 189 | 189-750 | Tier-2 | Tier-2---21 | 1--2 | 0.1718 | 0 | 100% | 1.7248 | 88.21% | 0% | 11.79% | 0.075309 | 0 | 0 | 0.075309 | 0 | 0.07184 | 0.11792 | 0.60923 | 0.07184 | 0.11792 | 0.60923 | 0.075679 | 0.12422 | 0.60923 | 4.366% | 0.001013 | 0.00096286 | 1702.705 | 2.2891 | 1507.0729 | 193.3431 | 1713.1637 | 0 | 0 | 1713.1637 | 2.483e-06%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 11.4998 | 49 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 64.4441 | 7.8931 | 8.1646 | 64.4441 | 7.8931 | 8.1646 | 67.8874 | 8.3149 | 8.1646 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 1.5879 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 118.0741 | 1.0899 | 108.3344 | 118.0741 | 1.0899 | 108.3344 | 124.383 | 1.1481 | 108.3344 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 2.2354 | 22 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 100.9567 | 1.5343 | 65.7983 | 100.9567 | 1.5343 | 65.7983 | 106.351 | 1.6163 | 65.7983 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2026 | 790 | CB 790 | Tier-2 | Tier-2---10 | 4--4 | 0.0892 | 0 | 100% | 864.253 | 62.67% | 37.21% | 0.1185% | 26.812 | 0 | 0 | 26.812 | 0 | 25.5768 | 0.061224 | 417.7555 | 25.5768 | 0.061224 | 417.7555 | 26.9434 | 0.064496 | 417.7555 | 3.102% | 0.092624 | 0.088039 | 9330.8076 | 1033.7577 | 3102.9179 | 5194.132 | 9512.1882 | 0 | 0 | 9512.1882 | 0.0008842%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 0.78689 | 20 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.87392 | 0.5401 | 1.6181 | 0.87392 | 0.5401 | 1.6181 | 0.92062 | 0.56895 | 1.6181 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2026 | 454 | 454-53F | Tier-2 | Tier-2---13 | 4--3 | 0.3076 | 0 | 100% | 272.5399 | 0.7301% | 99.1% | 0.1654% | 0.098502 | 0 | 0 | 0.098502 | 0 | 0.093964 | 0.21113 | 0.44506 | 0.093964 | 0.21113 | 0.44506 | 0.098985 | 0.22241 | 0.44506 | 0.03614% | 0.073094 | 0.069476 | 3728.6015 | 9.5009 | 3385.0726 | 334.0281 | 3921.3613 | 0 | 0 | 3921.3613 | 3.248e-06%
2026 | 197 | CB 197 | Tier-2 | Tier-2---21 | 1--4 | 0.097159 | 0 | 100% | 1.9198 | 98.18% | 0% | 1.817% | 0.093305 | 0 | 0 | 0.093305 | 0 | 0.089007 | 0.066687 | 1.3347 | 0.089007 | 0.066687 | 1.3347 | 0.093762 | 0.07025 | 1.3347 | 4.86% | 0.000314 | 0.00029846 | 6114.1 | 461.2612 | 3185.8611 | 2466.9777 | 6119.8844 | 0 | 0 | 6119.8844 | 3.077e-06%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 7.2309 | 81 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 246.6292 | 4.9631 | 49.693 | 246.6292 | 4.9631 | 49.693 | 259.807 | 5.2282 | 49.693 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 7.3388 | 536 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 74.8329 | 5.0372 | 14.8562 | 74.8329 | 5.0372 | 14.8562 | 78.8314 | 5.3063 | 14.8562 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 7.806 | 484 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 786.9145 | 5.3578 | 146.8715 | 786.9145 | 5.3578 | 146.8715 | 828.9604 | 5.6441 | 146.8715 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2026 | 395 | 395-33R | Tier-2 | Tier-2---11 | 4--3 | 0.2491 | 0 | 100% | 396.9757 | 0.1391% | 99.74% | 0.1245% | 0.02734 | 0 | 0 | 0.02734 | 0 | 0.026081 | 0.17098 | 0.15254 | 0.026081 | 0.17098 | 0.15254 | 0.027474 | 0.18011 | 0.15254 | 0.006887% | 0.092102 | 0.087543 | 4310.174 | 6.5289 | 3952.6979 | 350.9472 | 4534.3264 | 0 | 0 | 4534.3264 | 9.016e-07%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 5.2882 | 192 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 27.1082 | 3.6297 | 7.4685 | 27.1082 | 3.6297 | 7.4685 | 28.5567 | 3.8236 | 7.4685 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 11.8401 | 425 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 124.7575 | 8.1267 | 15.3515 | 124.7575 | 8.1267 | 15.3515 | 131.4234 | 8.561 | 15.3515 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 14.3572 | 1385 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 227.721 | 9.8544 | 23.1086 | 227.721 | 9.8544 | 23.1086 | 239.8884 | 10.3809 | 23.1086 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 17.3068 | 1218 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 251.2008 | 11.8789 | 21.1468 | 251.2008 | 11.8789 | 21.1468 | 264.6228 | 12.5136 | 21.1468 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 1.8014 | 93 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.2899 | 1.2364 | 1.852 | 2.2899 | 1.2364 | 1.852 | 2.4122 | 1.3025 | 1.852 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 9.8927 | 661 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 234.7817 | 6.79 | 34.5773 | 234.7817 | 6.79 | 34.5773 | 247.3264 | 7.1528 | 34.5773 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 4.1559 | 590 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 214.8823 | 2.8525 | 75.3311 | 214.8823 | 2.8525 | 75.3311 | 226.3638 | 3.0049 | 75.3311 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 15.3767 | 427 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 50.6908 | 10.5541 | 4.8029 | 50.6908 | 10.5541 | 4.8029 | 53.3993 | 11.1181 | 4.8029 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 18.1587 | 305 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 71.9999 | 12.4636 | 5.7768 | 71.9999 | 12.4636 | 5.7768 | 75.847 | 13.1296 | 5.7768 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2026 | 770 | 770-259R | Tier-2 | Tier-2---17 | 2--3 | 1.3913 | 0 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 2.0515 | 0 | 0 | 2.0515 | 0 | 1.957 | 0.95494 | 2.0494 | 1.957 | 0.95494 | 2.0494 | 2.0616 | 1.006 | 2.0494 | 4.826% | 0.010605 | 0.01008 | 4008.538 | 787.4023 | 25.9222 | 3195.2135 | 4013.7737 | 0 | 0 | 4013.7737 | 6.765e-05%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 22.0576 | 1796 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 162.4058 | 15.1397 | 10.7271 | 162.4058 | 15.1397 | 10.7271 | 171.0834 | 15.9486 | 10.7271 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 8.5739 | 486 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 257.6241 | 5.8849 | 43.7774 | 257.6241 | 5.8849 | 43.7774 | 271.3893 | 6.1993 | 43.7774 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 8.1708 | 346 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 140.2011 | 5.6082 | 24.9991 | 140.2011 | 5.6082 | 24.9991 | 147.6922 | 5.9079 | 24.9991 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2026 | 504 | 504-287R | Tier-2 | Tier-2---12 | 4--4 | 0.7358 | 0 | 100% | 501.8283 | 98.94% | 0% | 1.063% | 24.5765 | 0 | 0 | 24.5765 | 0 | 23.4443 | 0.50503 | 46.4213 | 23.4443 | 0.50503 | 46.4213 | 24.6969 | 0.53202 | 46.4213 | 4.897% | 0.033132 | 0.031492 | 15146.1514 | 2418.4341 | 53.5553 | 12674.162 | 15154.5352 | 0 | 0 | 15154.5352 | 0.0008104%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 1.2528 | 22 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 91.3318 | 0.85992 | 106.2102 | 91.3318 | 0.85992 | 106.2102 | 96.2118 | 0.90586 | 106.2102 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 2.4038 | 61 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 68.4792 | 1.6499 | 41.5052 | 68.4792 | 1.6499 | 41.5052 | 72.1381 | 1.738 | 41.5052 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2026 | 968 | 968-476F | Tier-2 | Tier-2---17 | 3--3 | 1.9167 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 2.9977 | 0 | 0 | 2.9977 | 0 | 2.8596 | 1.3155 | 2.1737 | 2.8596 | 1.3155 | 2.1737 | 3.0124 | 1.3858 | 2.1737 | 4.797% | 0.015315 | 0.014557 | 4080.3921 | 1049.3579 | 36.5623 | 2994.4719 | 4086.964 | 0 | 0 | 4086.964 | 9.885e-05%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 5.9518 | 1034 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 424.5109 | 4.0851 | 103.9164 | 424.5109 | 4.0851 | 103.9164 | 447.1931 | 4.3034 | 103.9164 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 2.2803 | 79 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.2445 | 1.5651 | 0.79512 | 1.2445 | 1.5651 | 0.79512 | 1.311 | 1.6487 | 0.79512 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 7.8388 | 373 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 428.2273 | 5.3803 | 79.5911 | 428.2273 | 5.3803 | 79.5911 | 451.1081 | 5.6678 | 79.5911 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 17.9011 | 1149 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 526.6286 | 12.2868 | 42.8612 | 526.6286 | 12.2868 | 42.8612 | 554.7671 | 12.9433 | 42.8612 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2026 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 11.6007 | 312 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 6.0182 | 7.9624 | 0.75583 | 6.0182 | 7.9624 | 0.75583 | 6.3398 | 8.3879 | 0.75583 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 3.4445 | 84 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 50.6581 | 2.3642 | 21.4269 | 50.6581 | 2.3642 | 21.4269 | 53.3649 | 2.4906 | 21.4269 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2026 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | 4--1 | 0.28182 | 0 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.15233 | 0 | 0 | 0.15233 | 0 | 0.14531 | 0.19343 | 0.75121 | 0.14531 | 0.19343 | 0.75121 | 0.15307 | 0.20377 | 0.75121 | 0.8348% | 0.061771 | 0.058714 | 295.3886 | 6.838 | 193.9385 | 94.612 | 308.1774 | 0 | 0 | 308.1774 | 5.023e-06%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 6.1881 | 443 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 244.4546 | 4.2473 | 57.5546 | 244.4546 | 4.2473 | 57.5546 | 257.5161 | 4.4743 | 57.5546 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2026 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | 2--4 | 1.5301 | 0 | 100% | 70.6534 | 98.66% | 0% | 1.337% | 3.4506 | 0 | 0 | 3.4506 | 0 | 3.2916 | 1.0502 | 3.1342 | 3.2916 | 1.0502 | 3.1342 | 3.4675 | 1.1063 | 3.1342 | 4.884% | 0.0070442 | 0.0066955 | 10030.0143 | 2447.2684 | 423.376 | 7159.37 | 10036.9961 | 0 | 0 | 10036.9961 | 0.0001138%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 16.0076 | 985 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 985.7421 | 10.9871 | 89.7177 | 985.7421 | 10.9871 | 89.7177 | 1038.4116 | 11.5742 | 89.7177 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 12.6949 | 1098 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 318.8395 | 8.7134 | 36.5917 | 318.8395 | 8.7134 | 36.5917 | 335.8755 | 9.179 | 36.5917 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 6.6053 | 250 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 183.0917 | 4.5337 | 40.3845 | 183.0917 | 4.5337 | 40.3845 | 192.8746 | 4.776 | 40.3845 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 1.1019 | 44 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 25.691 | 0.75631 | 33.9689 | 25.691 | 0.75631 | 33.9689 | 27.0637 | 0.79672 | 33.9689 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 4.3966 | 75 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 609.9489 | 3.0177 | 202.1247 | 609.9489 | 3.0177 | 202.1247 | 642.5393 | 3.1789 | 202.1247 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2026 | 312 | 312-40F | Tier-2 | Tier-2---20 | 3--2 | 0.0492 | 0 | 100% | 9.4163 | 0.07625% | 99.1% | 0.8244% | 0.00035539 | 0 | 0 | 0.00035539 | 0 | 0.00033902 | 0.03377 | 0.010039 | 0.00033902 | 0.03377 | 0.010039 | 0.00035713 | 0.035574 | 0.010039 | 0.003774% | 0.017172 | 0.016322 | 548.3384 | 0.98367 | 493.2185 | 54.1362 | 576.8729 | 0 | 0 | 576.8729 | 1.172e-08%
2026 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 0.089364 | 9 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.9389 | 0.061337 | 31.6113 | 1.9389 | 0.061337 | 31.6113 | 2.0425 | 0.064614 | 31.6113 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 14.1159 | 1226 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 81.2969 | 9.6888 | 8.3908 | 81.2969 | 9.6888 | 8.3908 | 85.6408 | 10.2065 | 8.3908 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 1.2536 | 124 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.4459 | 0.86045 | 5.1669 | 4.4459 | 0.86045 | 5.1669 | 4.6834 | 0.90643 | 5.1669 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 2.5449 | 185 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 16.5472 | 1.7468 | 9.473 | 16.5472 | 1.7468 | 9.473 | 17.4313 | 1.8401 | 9.473 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2026 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.03428 | 0 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.1865 | 0.023529 | 50.4288 | 1.1865 | 0.023529 | 50.4288 | 1.2499 | 0.024786 | 50.4288 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2026 | 331 | CB 331 | Tier-2 | Tier-2---14 | 2--5 | 2.8949 | 2 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 12.8498 | 0 | 0 | 12.8498 | 0 | 12.2578 | 1.987 | 6.1691 | 12.2578 | 1.987 | 6.1691 | 12.9128 | 2.0931 | 6.1691 | 4.919% | 0.010352 | 0.0098396 | 25232.8512 | 3536.4388 | 3219.2744 | 18477.138 | 25240.9927 | 0 | 0 | 25240.9927 | 0.0004237%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 16.7242 | 1029 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1445.8524 | 11.479 | 125.9558 | 1445.8524 | 11.479 | 125.9558 | 1523.1063 | 12.0924 | 125.9558 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 2.574 | 82 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 34.4739 | 1.7667 | 19.5129 | 34.4739 | 1.7667 | 19.5129 | 36.3159 | 1.8611 | 19.5129 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 6.3644 | 329 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 278.8709 | 4.3683 | 63.8395 | 278.8709 | 4.3683 | 63.8395 | 293.7714 | 4.6017 | 63.8395 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2026 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 2.267 | 47 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 42.7961 | 1.556 | 27.5033 | 42.7961 | 1.556 | 27.5033 | 45.0828 | 1.6392 | 27.5033 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 5.5445 | 309 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 58.7357 | 3.8056 | 15.434 | 58.7357 | 3.8056 | 15.434 | 61.8741 | 4.0089 | 15.434 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 9.1409 | 791 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 160.2048 | 6.2741 | 25.5344 | 160.2048 | 6.2741 | 25.5344 | 168.7647 | 6.6093 | 25.5344 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 9.5874 | 678 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 45.5695 | 6.5805 | 6.9249 | 45.5695 | 6.5805 | 6.9249 | 48.0044 | 6.9321 | 6.9249 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2026 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.054356 | 0 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.36233 | 0.037308 | 9.7118 | 0.36233 | 0.037308 | 9.7118 | 0.38169 | 0.039302 | 9.7118 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2026 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 0.74429 | 33 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 12.9185 | 0.51086 | 25.2876 | 12.9185 | 0.51086 | 25.2876 | 13.6088 | 0.53816 | 25.2876 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2026 | 196 | CB 196 | Tier-2 | Tier-2---15 | 3--4 | 0.29696 | 0 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.19951 | 0.20382 | 0.97884 | 0.19951 | 0.20382 | 0.97884 | 0.21017 | 0.21472 | 0.97884 | 0.1555% | 0.019464 | 0.018501 | 6908.5051 | 30.9312 | 5935.5679 | 942.006 | 7256.9805 | 0 | 0 | 7256.9805 | 6.897e-06%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 10.0377 | 551 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 406.782 | 6.8896 | 59.043 | 406.782 | 6.8896 | 59.043 | 428.5169 | 7.2577 | 59.043 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2026 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 0.043939 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.35337 | 0.030159 | 11.7171 | 0.35337 | 0.030159 | 11.7171 | 0.37225 | 0.03177 | 11.7171 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 4.4118 | 230 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.6856 | 3.0281 | 0.55666 | 1.6856 | 3.0281 | 0.55666 | 1.7757 | 3.1899 | 0.55666 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.4697 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 5.0917 | 0.32239 | 15.7937 | 5.0917 | 0.32239 | 15.7937 | 5.3637 | 0.33961 | 15.7937 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2026 | 311 | 311-14R | Tier-2 | Tier-2---14 | 3--4 | 0.75338 | 26 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 2.2455 | 0 | 0 | 2.2455 | 0 | 2.1421 | 0.5171 | 4.1425 | 2.1421 | 0.5171 | 4.1425 | 2.2565 | 0.54473 | 4.1425 | 0.8058% | 0.018935 | 0.017998 | 14715.9264 | 335.1634 | 11691.6167 | 2689.1463 | 15357.5365 | 0 | 0 | 15357.5365 | 7.405e-05%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 10.606 | 600 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 277.4933 | 7.2797 | 38.1188 | 277.4933 | 7.2797 | 38.1188 | 292.3202 | 7.6687 | 38.1188 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 2.911 | 8 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 2.0506 | 1.998 | 1.0263 | 2.0506 | 1.998 | 1.0263 | 2.1601 | 2.1048 | 1.0263 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 1.375 | 58 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 129.2749 | 0.94373 | 136.9825 | 129.2749 | 0.94373 | 136.9825 | 136.1822 | 0.99416 | 136.9825 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 3.7273 | 352 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 369.6702 | 2.5583 | 144.4993 | 369.6702 | 2.5583 | 144.4993 | 389.4222 | 2.695 | 144.4993 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 17.3898 | 266 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 22.317 | 11.9359 | 1.8697 | 22.317 | 11.9359 | 1.8697 | 23.5094 | 12.5736 | 1.8697 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 2.6099 | 93 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 91.3622 | 1.7913 | 51.0021 | 91.3622 | 1.7913 | 51.0021 | 96.2438 | 1.8871 | 51.0021 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 22.2475 | 1846 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 483.4663 | 15.2701 | 31.6611 | 483.4663 | 15.2701 | 31.6611 | 509.2986 | 16.086 | 31.6611 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2026 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 0.60374 | 80 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 13.6065 | 0.41439 | 32.8349 | 13.6065 | 0.41439 | 32.8349 | 14.3335 | 0.43653 | 32.8349 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 5.1074 | 161 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 538.3214 | 3.5056 | 153.5625 | 538.3214 | 3.5056 | 153.5625 | 567.0846 | 3.6929 | 153.5625 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 15.5693 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 169.8732 | 10.6863 | 15.8963 | 169.8732 | 10.6863 | 15.8963 | 178.9497 | 11.2573 | 15.8963 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 5.0178 | 495 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 277.0305 | 3.4441 | 80.4371 | 277.0305 | 3.4441 | 80.4371 | 291.8326 | 3.6281 | 80.4371 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 10.1766 | 1320 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 732.0261 | 6.9849 | 104.8011 | 732.0261 | 6.9849 | 104.8011 | 771.1393 | 7.3581 | 104.8011 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2026 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 0.005871 | 7 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.081643 | 0.0040297 | 20.2603 | 0.081643 | 0.0040297 | 20.2603 | 0.086005 | 0.004245 | 20.2603 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 7.3438 | 786 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 323.2915 | 5.0406 | 64.1379 | 323.2915 | 5.0406 | 64.1379 | 340.5654 | 5.3099 | 64.1379 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 1.0739 | 192 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 9.6013 | 0.73708 | 13.026 | 9.6013 | 0.73708 | 13.026 | 10.1143 | 0.77647 | 13.026 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 2.3892 | 150 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 202.8579 | 1.6399 | 123.7014 | 202.8579 | 1.6399 | 123.7014 | 213.6968 | 1.7275 | 123.7014 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 11.1993 | 175 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 70.6818 | 7.6869 | 9.1951 | 70.6818 | 7.6869 | 9.1951 | 74.4584 | 8.0976 | 9.1951 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 12.6807 | 874 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 163.4677 | 8.7037 | 18.7814 | 163.4677 | 8.7037 | 18.7814 | 172.202 | 9.1687 | 18.7814 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2026 | 92 | 92-619F | Tier-2 | Tier-2---14 | 3--4 | 1.454 | 0 | 100% | 202.8689 | 46.88% | 52.08% | 1.034% | 4.708 | 0 | 0 | 4.708 | 0 | 4.4911 | 0.99799 | 4.5002 | 4.4911 | 0.99799 | 4.5002 | 4.7311 | 1.0513 | 4.5002 | 2.321% | 0.015617 | 0.014844 | 12990.5937 | 1279.3739 | 6200.2786 | 5510.9412 | 13349.9397 | 0 | 0 | 13349.9397 | 0.0001553%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 4.1122 | 503 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 389.022 | 2.8225 | 137.8304 | 389.022 | 2.8225 | 137.8304 | 409.808 | 2.9733 | 137.8304 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 12.1511 | 530 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 175.0719 | 8.3402 | 20.9913 | 175.0719 | 8.3402 | 20.9913 | 184.4262 | 8.7858 | 20.9913 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 1.6021 | 37 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 28.5516 | 1.0996 | 25.9649 | 28.5516 | 1.0996 | 25.9649 | 30.0772 | 1.1584 | 25.9649 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 3.7494 | 966 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 18.4924 | 2.5735 | 7.1857 | 18.4924 | 2.5735 | 7.1857 | 19.4805 | 2.711 | 7.1857 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 6.1581 | 318 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 159.7982 | 4.2268 | 37.8063 | 159.7982 | 4.2268 | 37.8063 | 168.3364 | 4.4526 | 37.8063 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 6.9867 | 120 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 67.9477 | 4.7955 | 14.1691 | 67.9477 | 4.7955 | 14.1691 | 71.5783 | 5.0517 | 14.1691 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2026 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 14.6288 | 358 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 40.436 | 10.0408 | 4.0272 | 40.436 | 10.0408 | 4.0272 | 42.5966 | 10.5773 | 4.0272 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 8.4832 | 264 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 237.9521 | 5.8226 | 40.867 | 237.9521 | 5.8226 | 40.867 | 250.6662 | 6.1337 | 40.867 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 8.4771 | 489 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 657.6222 | 5.8185 | 113.0234 | 657.6222 | 5.8185 | 113.0234 | 692.7598 | 6.1294 | 113.0234 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 15.7168 | 1458 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1185.2748 | 10.7876 | 109.874 | 1185.2748 | 10.7876 | 109.874 | 1248.6056 | 11.364 | 109.874 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 2.7396 | 153 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 65.4226 | 1.8804 | 34.7919 | 65.4226 | 1.8804 | 34.7919 | 68.9182 | 1.9809 | 34.7919 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2026 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.011364 | 0 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.032694 | 0.0077999 | 4.1915 | 0.032694 | 0.0077999 | 4.1915 | 0.03444 | 0.0082167 | 4.1915 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2026 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.19716 | 0 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.6814 | 0.13532 | 27.2044 | 3.6814 | 0.13532 | 27.2044 | 3.8781 | 0.14256 | 27.2044 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 7.6936 | 496 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 94.9689 | 5.2807 | 17.9843 | 94.9689 | 5.2807 | 17.9843 | 100.0432 | 5.5628 | 17.9843 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 5.4881 | 1448 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 69.6651 | 3.7669 | 18.4942 | 69.6651 | 3.7669 | 18.4942 | 73.3874 | 3.9681 | 18.4942 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 24.1038 | 1342 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 739.2025 | 16.5442 | 44.6805 | 739.2025 | 16.5442 | 44.6805 | 778.6991 | 17.4282 | 44.6805 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 2.3543 | 108 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.8993 | 1.616 | 9.2201 | 14.8993 | 1.616 | 9.2201 | 15.6954 | 1.7023 | 9.2201 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 19.582 | 1232 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1249.9804 | 13.4405 | 93.0008 | 1249.9804 | 13.4405 | 93.0008 | 1316.7686 | 14.1587 | 93.0008 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2026 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 1.2434 | 1 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.5364 | 0.85344 | 5.3154 | 4.5364 | 0.85344 | 5.3154 | 4.7787 | 0.89904 | 5.3154 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 1.3053 | 37 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 109.4668 | 0.89589 | 122.1873 | 109.4668 | 0.89589 | 122.1873 | 115.3157 | 0.94376 | 122.1873 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.44811 | 19 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.8774 | 0.30757 | 15.8578 | 4.8774 | 0.30757 | 15.8578 | 5.138 | 0.324 | 15.8578 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2026 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 0.1538 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.3205 | 0.10556 | 31.4549 | 3.3205 | 0.10556 | 31.4549 | 3.4979 | 0.1112 | 31.4549 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 4.2055 | 355 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 170.7918 | 2.8865 | 59.1687 | 170.7918 | 2.8865 | 59.1687 | 179.9174 | 3.0408 | 59.1687 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 6.4578 | 333 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 59.4254 | 4.4324 | 13.4069 | 59.4254 | 4.4324 | 13.4069 | 62.6005 | 4.6693 | 13.4069 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 2.7653 | 373 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 133.2483 | 1.8981 | 70.2026 | 133.2483 | 1.8981 | 70.2026 | 140.368 | 1.9995 | 70.2026 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 8.3421 | 316 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1325.1737 | 5.7258 | 231.441 | 1325.1737 | 5.7258 | 231.441 | 1395.9796 | 6.0317 | 231.441 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 1.9394 | 108 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 190.7281 | 1.3312 | 143.2792 | 190.7281 | 1.3312 | 143.2792 | 200.9189 | 1.4023 | 143.2792 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 3.8122 | 341 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 438.0272 | 2.6166 | 167.4054 | 438.0272 | 2.6166 | 167.4054 | 461.4316 | 2.7564 | 167.4054 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 11.0316 | 1032 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 153.8343 | 7.5718 | 20.3167 | 153.8343 | 7.5718 | 20.3167 | 162.0539 | 7.9764 | 20.3167 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 8.4597 | 757 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 589.092 | 5.8065 | 101.454 | 589.092 | 5.8065 | 101.454 | 620.568 | 6.1167 | 101.454 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 4.2816 | 43 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 28.5249 | 2.9388 | 9.7064 | 28.5249 | 2.9388 | 9.7064 | 30.0491 | 3.0958 | 9.7064 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 3.6864 | 236 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 152.7457 | 2.5302 | 60.3681 | 152.7457 | 2.5302 | 60.3681 | 160.9071 | 2.6654 | 60.3681 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2026 | 243 | 243-14R | Tier-2 | Tier-2---11 | 4--4 | 4.9975 | 0 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 5.9029 | 0 | 0 | 5.9029 | 0 | 5.631 | 3.4302 | 1.6416 | 5.631 | 3.4302 | 1.6416 | 5.9318 | 3.6135 | 1.6416 | 1.46% | 0.066445 | 0.063156 | 6084.1314 | 280.7794 | 3933.5085 | 1869.8435 | 6307.5143 | 0 | 0 | 6307.5143 | 0.0001947%
2026 | 916 | 916-381 | Tier-2 | Tier-2---12 | 4--4 | 0.1652 | 0 | 100% | 590.9122 | 71.07% | 28.73% | 0.1918% | 20.7893 | 0 | 0 | 20.7893 | 0 | 19.8316 | 0.11339 | 174.8989 | 19.8316 | 0.11339 | 174.8989 | 20.8912 | 0.11945 | 174.8989 | 3.518% | 0.049834 | 0.047367 | 11857.5641 | 1782.085 | 3001.9836 | 7073.4955 | 12036.1866 | 0 | 0 | 12036.1866 | 0.0006856%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 1.5403 | 211 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 38.6279 | 1.0572 | 36.5368 | 38.6279 | 1.0572 | 36.5368 | 40.6918 | 1.1137 | 36.5368 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 18.6854 | 1020 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 253.1828 | 12.8251 | 19.7412 | 253.1828 | 12.8251 | 19.7412 | 266.7107 | 13.5104 | 19.7412 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 6.8811 | 282 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 473.1787 | 4.723 | 100.1867 | 473.1787 | 4.723 | 100.1867 | 498.4613 | 4.9753 | 100.1867 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 12.6964 | 932 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 518.2225 | 8.7145 | 59.4668 | 518.2225 | 8.7145 | 59.4668 | 545.9119 | 9.1801 | 59.4668 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 20.6608 | 1391 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1087.6046 | 14.181 | 76.6947 | 1087.6046 | 14.181 | 76.6947 | 1145.7168 | 14.9387 | 76.6947 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 3.259 | 164 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 29.9106 | 2.2369 | 13.3713 | 29.9106 | 2.2369 | 13.3713 | 31.5088 | 2.3564 | 13.3713 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2026 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 0.8674 | 0 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 18.1434 | 0.59536 | 30.4747 | 18.1434 | 0.59536 | 30.4747 | 19.1128 | 0.62717 | 30.4747 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 31.8811 | 2181 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 642.8121 | 21.8823 | 29.3759 | 642.8121 | 21.8823 | 29.3759 | 677.1585 | 23.0515 | 29.3759 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 12.0339 | 273 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 284.8981 | 8.2597 | 34.4923 | 284.8981 | 8.2597 | 34.4923 | 300.1206 | 8.7011 | 34.4923 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 2.9135 | 269 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 236.5455 | 1.9997 | 118.2893 | 236.5455 | 1.9997 | 118.2893 | 249.1845 | 2.1066 | 118.2893 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 3.7841 | 209 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 135.4283 | 2.5973 | 52.1423 | 135.4283 | 2.5973 | 52.1423 | 142.6644 | 2.7361 | 52.1423 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 15.005 | 1436 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 141.6855 | 10.299 | 13.7572 | 141.6855 | 10.299 | 13.7572 | 149.2559 | 10.8493 | 13.7572 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 3.0267 | 277 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 162.0011 | 2.0774 | 77.9812 | 162.0011 | 2.0774 | 77.9812 | 170.6571 | 2.1884 | 77.9812 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 3.5275 | 209 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 308.4441 | 2.4212 | 127.3955 | 308.4441 | 2.4212 | 127.3955 | 324.9247 | 2.5505 | 127.3955 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 4.5645 | 642 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 14.3975 | 3.133 | 4.5955 | 14.3975 | 3.133 | 4.5955 | 15.1667 | 3.3004 | 4.5955 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2026 | 334 | CB 334 | Tier-2 | Tier-2---17 | 3--4 | 2.321 | 0 | 100% | 70.5162 | 95.08% | 0% | 4.917% | 3.3189 | 0 | 0 | 3.3189 | 0 | 3.166 | 1.5931 | 1.9874 | 3.166 | 1.5931 | 1.9874 | 3.3352 | 1.6782 | 1.9874 | 4.707% | 0.014478 | 0.013762 | 4870.4444 | 330.0733 | 2622.0959 | 1918.2753 | 4882.9165 | 0 | 0 | 4882.9165 | 0.0001094%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 0.89662 | 14 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 23.6499 | 0.61542 | 38.4291 | 23.6499 | 0.61542 | 38.4291 | 24.9135 | 0.6483 | 38.4291 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 26.8775 | 296 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 183.9604 | 18.4479 | 9.9719 | 183.9604 | 18.4479 | 9.9719 | 193.7897 | 19.4336 | 9.9719 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 9.2899 | 565 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 53.817 | 6.3764 | 8.4401 | 53.817 | 6.3764 | 8.4401 | 56.6925 | 6.717 | 8.4401 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 18.7375 | 1826 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 192.4478 | 12.8609 | 14.9638 | 192.4478 | 12.8609 | 14.9638 | 202.7306 | 13.5481 | 14.9638 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2026 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 1.6445 | 323 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 9.86 | 1.1287 | 8.7355 | 9.86 | 1.1287 | 8.7355 | 10.3868 | 1.189 | 8.7355 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 3.5953 | 283 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 242.2939 | 2.4677 | 98.1865 | 242.2939 | 2.4677 | 98.1865 | 255.24 | 2.5995 | 98.1865 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 20.7013 | 1693 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1330.4034 | 14.2088 | 93.6323 | 1330.4034 | 14.2088 | 93.6323 | 1401.4886 | 14.968 | 93.6323 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 5.4369 | 85 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 43.8971 | 3.7317 | 11.7632 | 43.8971 | 3.7317 | 11.7632 | 46.2426 | 3.9311 | 11.7632 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 0.69072 | 24 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.973 | 0.47409 | 12.5988 | 5.973 | 0.47409 | 12.5988 | 6.2921 | 0.49942 | 12.5988 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 13.5415 | 832 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 461.7857 | 9.2945 | 49.6838 | 461.7857 | 9.2945 | 49.6838 | 486.4596 | 9.7911 | 49.6838 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 8.3178 | 78 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 284.1236 | 5.7091 | 49.7669 | 284.1236 | 5.7091 | 49.7669 | 299.3047 | 6.0141 | 49.7669 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 16.422 | 1620 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 522.9766 | 11.2716 | 46.3978 | 522.9766 | 11.2716 | 46.3978 | 550.9199 | 11.8738 | 46.3978 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 11.56 | 762 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1055.7106 | 7.9345 | 133.0534 | 1055.7106 | 7.9345 | 133.0534 | 1112.1187 | 8.3584 | 133.0534 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2026 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.17383 | 0 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.8387 | 0.11931 | 7.0293 | 0.8387 | 0.11931 | 7.0293 | 0.88351 | 0.12569 | 7.0293 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.77126 | 53 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 37.005 | 0.52937 | 69.9038 | 37.005 | 0.52937 | 69.9038 | 38.9822 | 0.55765 | 69.9038 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 5.0473 | 259 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 67.7486 | 3.4643 | 19.556 | 67.7486 | 3.4643 | 19.556 | 71.3684 | 3.6494 | 19.556 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 13.8096 | 549 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 167.585 | 9.4785 | 17.6805 | 167.585 | 9.4785 | 17.6805 | 176.5393 | 9.985 | 17.6805 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 11.815 | 901 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 814.528 | 8.1095 | 100.4417 | 814.528 | 8.1095 | 100.4417 | 858.0494 | 8.5428 | 100.4417 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 20.6063 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 157.4433 | 14.1436 | 11.1318 | 157.4433 | 14.1436 | 11.1318 | 165.8557 | 14.8993 | 11.1318 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2026 | 476 | CB 476 | Tier-2 | Tier-2---2 | 5--5 | 3.9551 | 0 | 100% | 7260.3217 | 73.64% | 26.17% | 0.1876% | 264.6639 | 0 | 0 | 264.6639 | 0 | 252.4713 | 2.7147 | 93.0026 | 252.4713 | 2.7147 | 93.0026 | 265.9612 | 2.8597 | 93.0026 | 3.645% | 0.20125 | 0.19129 | 36075.4158 | 6663.2216 | 8787.8653 | 20624.3289 | 36570.586 | 0 | 0 | 36570.586 | 0.008728%
2026 | 386 | 386-25R | Tier-2 | Tier-2---15 | 3--4 | 0.7066 | 0 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 2.5144 | 0 | 0 | 2.5144 | 0 | 2.3986 | 0.48499 | 4.9456 | 2.3986 | 0.48499 | 4.9456 | 2.5268 | 0.5109 | 4.9456 | 1.75% | 0.019083 | 0.018138 | 7528.0087 | 552.5881 | 4465.4268 | 2509.9939 | 7781.4266 | 0 | 0 | 7781.4266 | 8.292e-05%
2026 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 0.80794 | 5 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 30.9346 | 0 | 0 | 30.9346 | 0 | 29.5095 | 0.55455 | 53.2135 | 29.5095 | 0.55455 | 53.2135 | 31.0862 | 0.58418 | 53.2135 | 4.945% | 0.0036434 | 0.0034631 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171700.5551 | 0 | 0 | 171700.5551 | 0.00102%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 1.165 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 68.9354 | 0.79963 | 86.2089 | 68.9354 | 0.79963 | 86.2089 | 72.6187 | 0.84236 | 86.2089 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 9.7066 | 442 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 686.5258 | 6.6623 | 103.0456 | 686.5258 | 6.6623 | 103.0456 | 723.2078 | 7.0183 | 103.0456 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 8.2208 | 243 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 266.4366 | 5.6425 | 47.2193 | 266.4366 | 5.6425 | 47.2193 | 280.6727 | 5.944 | 47.2193 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 11.3059 | 892 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 203.7535 | 7.76 | 26.2568 | 203.7535 | 7.76 | 26.2568 | 214.6403 | 8.1747 | 26.2568 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 13.2995 | 353 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 431.9104 | 9.1284 | 47.3151 | 431.9104 | 9.1284 | 47.3151 | 454.988 | 9.6161 | 47.3151 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 8.9197 | 519 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 61.1326 | 6.1222 | 9.9854 | 61.1326 | 6.1222 | 9.9854 | 64.399 | 6.4493 | 9.9854 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 2.6869 | 284 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 20.0009 | 1.8442 | 10.8453 | 20.0009 | 1.8442 | 10.8453 | 21.0696 | 1.9427 | 10.8453 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 0.050947 | 0 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.83481 | 0.034969 | 23.873 | 0.83481 | 0.034969 | 23.873 | 0.87941 | 0.036837 | 23.873 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 1.2638 | 61 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 26.6692 | 0.86745 | 30.7442 | 26.6692 | 0.86745 | 30.7442 | 28.0941 | 0.9138 | 30.7442 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2026 | 308 | 308-486AE | Tier-2 | Tier-2---16 | 4--3 | 1.7369 | 0 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.19428 | 0 | 0 | 0.19428 | 0 | 0.18533 | 1.1922 | 0.15546 | 0.18533 | 1.1922 | 0.15546 | 0.19524 | 1.2559 | 0.15546 | 0.118% | 0.040279 | 0.038285 | 4088.4689 | 19.0997 | 3634.8848 | 434.4844 | 4296.3129 | 0 | 0 | 4296.3129 | 6.407e-06%
2026 | 295 | 295-1203F | Tier-2 | Tier-2---21 | 1--2 | 0.2153 | 0 | 100% | 0.80448 | 60.49% | 0% | 39.51% | 0.02409 | 0 | 0 | 0.02409 | 0 | 0.02298 | 0.14778 | 0.1555 | 0.02298 | 0.14778 | 0.1555 | 0.024208 | 0.15567 | 0.1555 | 2.994% | 0.0013362 | 0.0012701 | 602.062 | 79.8078 | 41.8021 | 480.452 | 614.4487 | 0 | 0 | 614.4487 | 7.944e-07%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 1.3216 | 258 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 114.0597 | 0.90713 | 125.7371 | 114.0597 | 0.90713 | 125.7371 | 120.154 | 0.9556 | 125.7371 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 7.0884 | 586 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 387.696 | 4.8653 | 79.6858 | 387.696 | 4.8653 | 79.6858 | 408.4111 | 5.1253 | 79.6858 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2026 | 450 | 450-50R | Tier-2 | Tier-2---11 | 4--4 | 0.3652 | 6 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 8.6479 | 0 | 0 | 8.6479 | 0 | 8.2495 | 0.25066 | 32.9109 | 8.2495 | 0.25066 | 32.9109 | 8.6903 | 0.26406 | 32.9109 | 1.61% | 0.071801 | 0.068247 | 7480.0024 | 403.5755 | 4618.5943 | 2457.8325 | 7742.8291 | 0 | 0 | 7742.8291 | 0.0002852%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 1.5712 | 63 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 21.4921 | 1.0784 | 19.929 | 21.4921 | 1.0784 | 19.929 | 22.6404 | 1.1361 | 19.929 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 11.7129 | 203 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 329.0418 | 8.0394 | 40.9286 | 329.0418 | 8.0394 | 40.9286 | 346.623 | 8.469 | 40.9286 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.78597 | 36 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.8025 | 0.53947 | 21.878 | 11.8025 | 0.53947 | 21.878 | 12.4331 | 0.56829 | 21.878 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 5.3936 | 448 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 34.2027 | 3.702 | 9.2389 | 34.2027 | 3.702 | 9.2389 | 36.0302 | 3.8998 | 9.2389 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 9.3687 | 504 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 585.9297 | 6.4304 | 91.1183 | 585.9297 | 6.4304 | 91.1183 | 617.2367 | 6.774 | 91.1183 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2026 | 393 | CB 393 | Tier-2 | Tier-2---19 | 1--3 | 0.339 | 0 | 100% | 8.3766 | 93.83% | 0% | 6.171% | 0.38906 | 0 | 0 | 0.38906 | 0 | 0.37113 | 0.23268 | 1.595 | 0.37113 | 0.23268 | 1.595 | 0.39096 | 0.24511 | 1.595 | 4.645% | 0.0030912 | 0.0029382 | 2709.8263 | 11.6903 | 2486.8043 | 211.3317 | 2718.5348 | 0 | 0 | 2718.5348 | 1.283e-05%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 8.4553 | 115 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 245.3601 | 5.8035 | 42.278 | 245.3601 | 5.8035 | 42.278 | 258.47 | 6.1136 | 42.278 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2026 | 443 | CB 443 | Tier-2 | Tier-2---17 | 2--4 | 1.4752 | 0 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 3.2669 | 0 | 0 | 3.2669 | 0 | 3.1164 | 1.0125 | 3.0779 | 3.1164 | 1.0125 | 3.0779 | 3.283 | 1.0666 | 3.0779 | 4.865% | 0.007405 | 0.0070385 | 9067.8323 | 1863.6752 | 20.0371 | 7184.12 | 9075.9094 | 0 | 0 | 9075.9094 | 0.0001077%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 2.5689 | 85 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 192.305 | 1.7632 | 109.0639 | 192.305 | 1.7632 | 109.0639 | 202.5801 | 1.8574 | 109.0639 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 10.4533 | 593 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 27.3279 | 7.1748 | 3.8089 | 27.3279 | 7.1748 | 3.8089 | 28.7881 | 7.5582 | 3.8089 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2026 | 535 | CB 535 | Tier-2 | Tier-2---16 | 4--3 | 0.31174 | 0 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25308 | 0 | 0 | 0.25308 | 0 | 0.24142 | 0.21397 | 1.1283 | 0.24142 | 0.21397 | 1.1283 | 0.25432 | 0.2254 | 1.1283 | 0.227% | 0.059698 | 0.056743 | 1867.7052 | 14.9488 | 1426.0626 | 426.6938 | 1960.5113 | 0 | 0 | 1960.5113 | 8.346e-06%
2026 | 281 | CB 281 | Tier-2 | Tier-2---16 | 4--3 | 3.767 | 0 | 100% | 131.3229 | 1.145% | 96.36% | 2.498% | 0.07445 | 0 | 0 | 0.07445 | 0 | 0.07102 | 2.5856 | 0.027468 | 0.07102 | 2.5856 | 0.027468 | 0.074814 | 2.7237 | 0.027468 | 0.05669% | 0.046838 | 0.04452 | 2803.7555 | 3.8846 | 2517.4341 | 282.4368 | 2948.0968 | 0 | 0 | 2948.0968 | 2.455e-06%
2026 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.023485 | 0 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.9706 | 0.016119 | 184.2836 | 2.9706 | 0.016119 | 184.2836 | 3.1293 | 0.016981 | 184.2836 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 15.3043 | 1286 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 149.4686 | 10.5045 | 14.229 | 149.4686 | 10.5045 | 14.229 | 157.4549 | 11.0657 | 14.229 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 3.3899 | 505 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 177.6968 | 2.3267 | 76.3715 | 177.6968 | 2.3267 | 76.3715 | 187.1914 | 2.4511 | 76.3715 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 14.7171 | 529 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 19.0725 | 10.1014 | 1.8881 | 19.0725 | 10.1014 | 1.8881 | 20.0916 | 10.6411 | 1.8881 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2026 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.87121 | 106 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 6.2466 | 0.59798 | 10.4462 | 6.2466 | 0.59798 | 10.4462 | 6.5803 | 0.62993 | 10.4462 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 5.3095 | 781 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 428.5491 | 3.6443 | 117.5946 | 428.5491 | 3.6443 | 117.5946 | 451.4471 | 3.839 | 117.5946 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 9.9971 | 673 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 574.459 | 6.8617 | 83.7192 | 574.459 | 6.8617 | 83.7192 | 605.1531 | 7.2284 | 83.7192 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2026 | 1139 | 1139-4F | Tier-2 | Tier-2---11 | 5--3 | 2.2023 | 0 | 100% | 472.1771 | 0.2595% | 99.27% | 0.4712% | 0.060646 | 0 | 0 | 0.060646 | 0 | 0.057852 | 1.5116 | 0.038272 | 0.057852 | 1.5116 | 0.038272 | 0.060943 | 1.5924 | 0.038272 | 0.01284% | 0.11231 | 0.10675 | 4204.4022 | 7.5405 | 3803.8802 | 392.9815 | 4422.7903 | 0 | 0 | 4422.7903 | 2e-06%
2026 | 197 | 197-1157F | Tier-2 | Tier-2---18 | 3--3 | 0.1773 | 0 | 100% | 63.1655 | 1.305% | 98.13% | 0.5601% | 0.040803 | 0 | 0 | 0.040803 | 0 | 0.038923 | 0.12169 | 0.31985 | 0.038923 | 0.12169 | 0.31985 | 0.041003 | 0.1282 | 0.31985 | 0.0646% | 0.01787 | 0.016985 | 3534.7635 | 11.6765 | 2974.4275 | 548.6595 | 3716.4442 | 0 | 0 | 3716.4442 | 1.346e-06%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 5.1261 | 334 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 161.888 | 3.5184 | 46.0112 | 161.888 | 3.5184 | 46.0112 | 170.5379 | 3.7064 | 46.0112 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 16.7214 | 1503 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1320.7925 | 11.4771 | 115.0807 | 1320.7925 | 11.4771 | 115.0807 | 1391.3643 | 12.0903 | 115.0807 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 11.1523 | 320 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 373.1142 | 7.6546 | 48.7438 | 373.1142 | 7.6546 | 48.7438 | 393.0502 | 8.0636 | 48.7438 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2026 | 311 | 311-1163F | Tier-2 | Tier-2---18 | 3--3 | 0.65624 | 4 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9366 | 0 | 0 | 1.9366 | 0 | 1.8474 | 0.45043 | 4.1015 | 1.8474 | 0.45043 | 4.1015 | 1.9461 | 0.47449 | 4.1015 | 4.192% | 0.018623 | 0.017701 | 2480.5668 | 274.9764 | 742.9932 | 1462.5972 | 2500.341 | 0 | 0 | 2500.341 | 6.386e-05%
2026 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 3.6983 | 195 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 37.8909 | 2.5384 | 14.927 | 37.8909 | 2.5384 | 14.927 | 39.9154 | 2.674 | 14.927 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2026 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.39659 | 0 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.67947 | 0.27221 | 2.4961 | 0.67947 | 0.27221 | 2.4961 | 0.71577 | 0.28675 | 2.4961 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 1.0854 | 13 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 15.5039 | 0.745 | 20.8105 | 15.5039 | 0.745 | 20.8105 | 16.3322 | 0.78481 | 20.8105 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.31499 | 9 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.6787 | 0.2162 | 35.5163 | 7.6787 | 0.2162 | 35.5163 | 8.089 | 0.22776 | 35.5163 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 17.9266 | 1150 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1926.6067 | 12.3043 | 156.5801 | 1926.6067 | 12.3043 | 156.5801 | 2029.5479 | 12.9617 | 156.5801 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 15.4477 | 756 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1739.5055 | 10.6029 | 164.0594 | 1739.5055 | 10.6029 | 164.0594 | 1832.4497 | 11.1694 | 164.0594 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2026 | 462 | CB 462 | Tier-2 | Tier-2---19 | 2--4 | 0.4439 | 0 | 100% | 42.4238 | 96.69% | 0% | 3.313% | 2.0304 | 0 | 0 | 2.0304 | 0 | 1.9369 | 0.30468 | 6.3571 | 1.9369 | 0.30468 | 6.3571 | 2.0404 | 0.32096 | 6.3571 | 4.786% | 0.0069768 | 0.0066314 | 6080.6996 | 1110.385 | 1800.7984 | 3169.5162 | 6091.1906 | 0 | 0 | 6091.1906 | 6.696e-05%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 17.4555 | 1930 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 847.0626 | 11.981 | 70.7007 | 847.0626 | 11.981 | 70.7007 | 892.3223 | 12.6211 | 70.7007 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 5.0582 | 437 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 68.4112 | 3.4718 | 19.705 | 68.4112 | 3.4718 | 19.705 | 72.0666 | 3.6573 | 19.705 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 0.14415 | 0 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.3585 | 0.098938 | 23.8382 | 2.3585 | 0.098938 | 23.8382 | 2.4845 | 0.10422 | 23.8382 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 5.8553 | 513 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 246.9272 | 4.0189 | 61.4417 | 246.9272 | 4.0189 | 61.4417 | 260.1209 | 4.2336 | 61.4417 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2026 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | 3--3 | 0.27065 | 0 | 100% | 40.9949 | 23.55% | 73.64% | 2.81% | 0.47782 | 0 | 0 | 0.47782 | 0 | 0.45581 | 0.18577 | 2.4536 | 0.45581 | 0.18577 | 2.4536 | 0.48016 | 0.1957 | 2.4536 | 1.166% | 0.021565 | 0.020497 | 1901.027 | 61.7007 | 1198.5032 | 640.8231 | 1976.7168 | 0 | 0 | 1976.7168 | 1.576e-05%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 7.3796 | 121 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 219.8189 | 5.0651 | 43.3983 | 219.8189 | 5.0651 | 43.3983 | 231.5641 | 5.3358 | 43.3983 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.50061 | 50 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 18.259 | 0.3436 | 53.1399 | 18.259 | 0.3436 | 53.1399 | 19.2346 | 0.36196 | 53.1399 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 13.2557 | 1015 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 126.7631 | 9.0983 | 13.9326 | 126.7631 | 9.0983 | 13.9326 | 133.5362 | 9.5845 | 13.9326 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 21.2556 | 676 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3711.5659 | 14.5893 | 254.4035 | 3711.5659 | 14.5893 | 254.4035 | 3909.88 | 15.3688 | 254.4035 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 29.2157 | 713 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 394.1517 | 20.0528 | 19.6557 | 394.1517 | 20.0528 | 19.6557 | 415.2118 | 21.1243 | 19.6557 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 7.4915 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 170.5666 | 5.142 | 33.1715 | 170.5666 | 5.142 | 33.1715 | 179.6802 | 5.4167 | 33.1715 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 15.6835 | 943 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1054.721 | 10.7647 | 97.9792 | 1054.721 | 10.7647 | 97.9792 | 1111.0762 | 11.3399 | 97.9792 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2026 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 2.0208 | 0 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 33.9169 | 1.387 | 24.4526 | 33.9169 | 1.387 | 24.4526 | 35.7291 | 1.4612 | 24.4526 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.1678 | 14 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.3389 | 0.11518 | 46.3547 | 5.3389 | 0.11518 | 46.3547 | 5.6242 | 0.12133 | 46.3547 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 6.2775 | 169 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 452.3048 | 4.3087 | 104.9749 | 452.3048 | 4.3087 | 104.9749 | 476.4721 | 4.5389 | 104.9749 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 8.9137 | 164 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 100.8529 | 6.1181 | 16.4844 | 100.8529 | 6.1181 | 16.4844 | 106.2416 | 6.445 | 16.4844 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 3.55 | 286 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 238.2603 | 2.4366 | 97.7835 | 238.2603 | 2.4366 | 97.7835 | 250.9909 | 2.5668 | 97.7835 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2026 | 500 | 500-1531 | Tier-2 | Tier-2---10 | 4--4 | 0.88746 | 14 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 8.56 | 0 | 0 | 8.56 | 0 | 8.1657 | 0.60913 | 13.4055 | 8.1657 | 0.60913 | 13.4055 | 8.602 | 0.64167 | 13.4055 | 1.069% | 0.071178 | 0.067654 | 11247.1911 | 406.5986 | 8046.836 | 2793.7565 | 11706.3951 | 0 | 0 | 11706.3951 | 0.0002823%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 34.1718 | 1862 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1888.0784 | 23.4546 | 80.4993 | 1888.0784 | 23.4546 | 80.4993 | 1988.961 | 24.7078 | 80.4993 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 1.4237 | 110 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.5521 | 0.97719 | 7.7284 | 7.5521 | 0.97719 | 7.7284 | 7.9556 | 1.0294 | 7.7284 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2026 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 3.4267 | 233 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.9569 | 2.352 | 0.83203 | 1.9569 | 2.352 | 0.83203 | 2.0615 | 2.4776 | 0.83203 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 1.3115 | 241 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.6148 | 0.90019 | 11.7916 | 10.6148 | 0.90019 | 11.7916 | 11.1819 | 0.94829 | 11.7916 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 6.4924 | 205 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 21.1934 | 4.4562 | 4.7559 | 21.1934 | 4.4562 | 4.7559 | 22.3257 | 4.6943 | 4.7559 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 7.8576 | 482 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 75.7792 | 5.3932 | 14.0508 | 75.7792 | 5.3932 | 14.0508 | 79.8282 | 5.6814 | 14.0508 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 17.727 | 1369 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1643.7869 | 12.1674 | 135.0982 | 1643.7869 | 12.1674 | 135.0982 | 1731.6167 | 12.8175 | 135.0982 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 2.3271 | 116 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 72.0465 | 1.5972 | 45.1071 | 72.0465 | 1.5972 | 45.1071 | 75.8961 | 1.6826 | 45.1071 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.49562 | 11 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 39.6291 | 0.34018 | 116.4953 | 39.6291 | 0.34018 | 116.4953 | 41.7465 | 0.35835 | 116.4953 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 2.1594 | 49 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 25.1077 | 1.4822 | 16.9397 | 25.1077 | 1.4822 | 16.9397 | 26.4492 | 1.5614 | 16.9397 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2026 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.010606 | 0 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072797 | 0 | 0 | 0.0072797 | 0 | 0 | 0.0076686 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2026 | 445 | 445-1315 | Tier-2 | Tier-2---19 | 1--5 | 0.080871 | 0 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 1.294 | 0 | 0 | 1.294 | 0 | 1.2344 | 0.055508 | 22.2389 | 1.2344 | 0.055508 | 22.2389 | 1.3004 | 0.058473 | 22.2389 | 4.93% | 0.000636 | 0.00060452 | 41272.5846 | 5558.0973 | 1215.1763 | 34499.311 | 41281.3528 | 0 | 0 | 41281.3528 | 4.267e-05%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.7481 | 0.023529 | 116.7955 | 2.7481 | 0.023529 | 116.7955 | 2.8949 | 0.024786 | 116.7955 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.57917 | 30 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.8008 | 0.39752 | 34.7169 | 13.8008 | 0.39752 | 34.7169 | 14.5382 | 0.41876 | 34.7169 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2026 | 175 | CB 175 | Tier-2 | Tier-2---10 | 5--4 | 0.0828 | 0 | 100% | 1236.5075 | 84.14% | 15.66% | 0.203% | 51.5004 | 0 | 0 | 51.5004 | 0 | 49.1279 | 0.056832 | 864.447 | 49.1279 | 0.056832 | 864.447 | 51.7529 | 0.059868 | 864.447 | 4.165% | 0.16723 | 0.15895 | 7393.9644 | 1133.6762 | 1185.8912 | 5074.397 | 7455.0304 | 0 | 0 | 7455.0304 | 0.001698%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 12.1911 | 327 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 396.1715 | 8.3676 | 47.3459 | 396.1715 | 8.3676 | 47.3459 | 417.3395 | 8.8147 | 47.3459 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 1.8653 | 423 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 18.2584 | 1.2803 | 14.2608 | 18.2584 | 1.2803 | 14.2608 | 19.234 | 1.3487 | 14.2608 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.055682 | 34 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.072621 | 0.038219 | 1.9002 | 0.072621 | 0.038219 | 1.9002 | 0.076501 | 0.040261 | 1.9002 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 24.3072 | 878 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 785.4976 | 16.6838 | 47.0816 | 785.4976 | 16.6838 | 47.0816 | 827.4678 | 17.5752 | 47.0816 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 1.2636 | 41 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 19.4973 | 0.86732 | 22.4798 | 19.4973 | 0.86732 | 22.4798 | 20.539 | 0.91367 | 22.4798 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 10.5112 | 997 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 89.723 | 7.2146 | 12.4364 | 89.723 | 7.2146 | 12.4364 | 94.517 | 7.6001 | 12.4364 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 0.081438 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0024413 | 0.055897 | 0.043676 | 0.0024413 | 0.055897 | 0.043676 | 0.0025718 | 0.058883 | 0.043676 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 7.3706 | 412 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 861.5285 | 5.059 | 170.2962 | 861.5285 | 5.059 | 170.2962 | 907.5611 | 5.3293 | 170.2962 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 22.4647 | 1409 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 398.5744 | 15.4192 | 25.8493 | 398.5744 | 15.4192 | 25.8493 | 419.8708 | 16.243 | 25.8493 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 8.1866 | 140 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 40.7779 | 5.619 | 7.2571 | 40.7779 | 5.619 | 7.2571 | 42.9567 | 5.9193 | 7.2571 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2026 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.016856 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.31849 | 0.011569 | 27.5287 | 0.31849 | 0.011569 | 27.5287 | 0.33551 | 0.012188 | 27.5287 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 8.8214 | 139 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 113.3698 | 6.0547 | 18.7241 | 113.3698 | 6.0547 | 18.7241 | 119.4273 | 6.3783 | 18.7241 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 0.22216 | 19 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.30123 | 0.15248 | 1.9755 | 0.30123 | 0.15248 | 1.9755 | 0.31732 | 0.16063 | 1.9755 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 1.2988 | 31 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 21.4215 | 0.89148 | 24.029 | 21.4215 | 0.89148 | 24.029 | 22.5661 | 0.93912 | 24.029 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 3.321 | 115 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 55.2642 | 2.2795 | 24.2445 | 55.2642 | 2.2795 | 24.2445 | 58.217 | 2.4012 | 24.2445 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 14.5687 | 1091 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 633.9221 | 9.9996 | 63.395 | 633.9221 | 9.9996 | 63.395 | 667.7935 | 10.5339 | 63.395 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 2.3515 | 16 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 269.2064 | 1.614 | 166.7922 | 269.2064 | 1.614 | 166.7922 | 283.5905 | 1.7003 | 166.7922 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.41229 | 18 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 14.1762 | 0.28298 | 50.0961 | 14.1762 | 0.28298 | 50.0961 | 14.9337 | 0.2981 | 50.0961 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 6.2353 | 440 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 165.5356 | 4.2797 | 38.6792 | 165.5356 | 4.2797 | 38.6792 | 174.3804 | 4.5084 | 38.6792 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 2.0774 | 340 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 117.9754 | 1.4259 | 82.7384 | 117.9754 | 1.4259 | 82.7384 | 124.279 | 1.5021 | 82.7384 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2026 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.76383 | 6 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 8.0511 | 0.52427 | 15.3568 | 8.0511 | 0.52427 | 15.3568 | 8.4812 | 0.55228 | 15.3568 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 5.8533 | 585 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 63.5637 | 4.0175 | 15.8217 | 63.5637 | 4.0175 | 15.8217 | 66.96 | 4.2322 | 15.8217 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 4.0824 | 392 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 20.0778 | 2.802 | 7.1655 | 20.0778 | 2.802 | 7.1655 | 21.1505 | 2.9517 | 7.1655 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 15.1559 | 793 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 113.1467 | 10.4026 | 10.8768 | 113.1467 | 10.4026 | 10.8768 | 119.1922 | 10.9584 | 10.8768 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 19.9074 | 1826 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1227.409 | 13.6639 | 89.8289 | 1227.409 | 13.6639 | 89.8289 | 1292.9912 | 14.3939 | 89.8289 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 8.7188 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 334.0803 | 5.9843 | 55.826 | 334.0803 | 5.9843 | 55.826 | 351.9307 | 6.3041 | 55.826 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2026 | 239 | CB 239 | Tier-3 | Tier-3---20 | 1--5 | 0.039773 | 0 | 100% | 10.6776 | 99.64% | 0% | 0.3633% | 0.52662 | 0 | 0 | 0.52662 | 0 | 0.50236 | 0.027299 | 18.4022 | 0.50236 | 0.027299 | 18.4022 | 0.5292 | 0.028758 | 18.4022 | 4.932% | 0.0001826 | 0.00017356 | 58475.5699 | 8842.2618 | 1906.0953 | 47727.2128 | 58486.6341 | 0 | 0 | 58486.6341 | 1.737e-05%
2026 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.84619 | 35 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 99.2512 | 0.5808 | 170.887 | 99.2512 | 0.5808 | 170.887 | 104.5543 | 0.61183 | 170.887 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 3.4333 | 98 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 17.2331 | 2.3565 | 7.3129 | 17.2331 | 2.3565 | 7.3129 | 18.1539 | 2.4824 | 7.3129 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.34621 | 18 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.4335 | 0.23763 | 31.2817 | 7.4335 | 0.23763 | 31.2817 | 7.8307 | 0.25033 | 31.2817 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2026 | 948 | 948-5R | Tier-2 | Tier-2---21 | 1--2 | 0.1373 | 0 | 100% | 3.6494 | 90.16% | 0% | 9.838% | 0.16287 | 0 | 0 | 0.16287 | 0 | 0.15537 | 0.094239 | 1.6487 | 0.15537 | 0.094239 | 1.6487 | 0.16367 | 0.099274 | 1.6487 | 4.463% | 0.0023872 | 0.002269 | 1528.7338 | 203.4062 | 386.7322 | 938.5955 | 1536.5665 | 0 | 0 | 1536.5665 | 5.371e-06%
2026 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 0.81042 | 160 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.9715 | 0.55625 | 5.342 | 2.9715 | 0.55625 | 5.342 | 3.1302 | 0.58597 | 5.342 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2026 | 533 | CB 533 | Tier-2 | Tier-2---20 | 4--1 | 0.027511 | 0 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.01766 | 0 | 0 | 0.01766 | 0 | 0.016847 | 0.018883 | 0.89216 | 0.016847 | 0.018883 | 0.89216 | 0.017747 | 0.019892 | 0.89216 | 0.1665% | 0.06013 | 0.057154 | 176.3723 | 1.2595 | 133.5547 | 41.5581 | 185.2484 | 0 | 0 | 185.2484 | 5.824e-07%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 13.4125 | 992 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 76.6538 | 9.206 | 8.3265 | 76.6538 | 9.206 | 8.3265 | 80.7496 | 9.6979 | 8.3265 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 1.0659 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 62.0703 | 0.73161 | 84.8411 | 62.0703 | 0.73161 | 84.8411 | 65.3868 | 0.7707 | 84.8411 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 14.5985 | 935 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 533.1833 | 10.02 | 53.2118 | 533.1833 | 10.02 | 53.2118 | 561.672 | 10.5554 | 53.2118 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.64526 | 37 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.8535 | 0.44289 | 13.2168 | 5.8535 | 0.44289 | 13.2168 | 6.1663 | 0.46655 | 13.2168 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2026 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 2.803 | 3 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 4.3523 | 1.9239 | 2.2622 | 4.3523 | 1.9239 | 2.2622 | 4.5848 | 2.0267 | 2.2622 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 7.564 | 846 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 96.0526 | 5.1917 | 18.5011 | 96.0526 | 5.1917 | 18.5011 | 101.1849 | 5.4691 | 18.5011 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 24.6051 | 1562 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 296.1766 | 16.8883 | 17.5374 | 296.1766 | 16.8883 | 17.5374 | 312.0017 | 17.7907 | 17.5374 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 5.7333 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 248.9663 | 3.9352 | 63.2667 | 248.9663 | 3.9352 | 63.2667 | 262.269 | 4.1455 | 63.2667 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 10.6382 | 730 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 103.6022 | 7.3018 | 14.1886 | 103.6022 | 7.3018 | 14.1886 | 109.1378 | 7.6919 | 14.1886 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 10.5116 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 408.1427 | 7.2149 | 56.5698 | 408.1427 | 7.2149 | 56.5698 | 429.9503 | 7.6004 | 56.5698 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 1.4734 | 189 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.4049 | 1.0113 | 3.3667 | 3.4049 | 1.0113 | 3.3667 | 3.5868 | 1.0654 | 3.3667 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 20.5957 | 1555 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2590.0334 | 14.1363 | 183.2187 | 2590.0334 | 14.1363 | 183.2187 | 2728.4224 | 14.8916 | 183.2187 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 4.4809 | 263 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 45.2058 | 3.0755 | 14.6985 | 45.2058 | 3.0755 | 14.6985 | 47.6212 | 3.2399 | 14.6985 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 22.8015 | 890 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 79.3622 | 15.6503 | 5.071 | 79.3622 | 15.6503 | 5.071 | 83.6027 | 16.4866 | 5.071 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2026 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.125 | 26 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 4.1171 | 0.085797 | 47.9869 | 4.1171 | 0.085797 | 47.9869 | 4.3371 | 0.090381 | 47.9869 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2026 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.092045 | 7 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.8484 | 0.063177 | 187.5432 | 11.8484 | 0.063177 | 187.5432 | 12.4815 | 0.066553 | 187.5432 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 9.5829 | 976 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 61.735 | 6.5775 | 9.3858 | 61.735 | 6.5775 | 9.3858 | 65.0335 | 6.9289 | 9.3858 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2026 | 728 | 728-1570F | Tier-2 | Tier-2---19 | 1--5 | 0.0015 | 0 | 100% | 33.2807 | 99.79% | 0% | 0.2133% | 1.6439 | 0 | 0 | 1.6439 | 0 | 1.5682 | 0.0010296 | 1523.1308 | 1.5682 | 0.0010296 | 1523.1308 | 1.6519 | 0.0010846 | 1523.1308 | 4.939% | 0.0003472 | 0.00033001 | 95854.6419 | 22304.1965 | 20.1049 | 73530.3404 | 95865.2904 | 0 | 0 | 95865.2904 | 5.421e-05%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 12.1965 | 973 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 391.4809 | 8.3713 | 46.7646 | 391.4809 | 8.3713 | 46.7646 | 412.3983 | 8.8186 | 46.7646 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 20.8132 | 1273 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 418.7535 | 14.2856 | 29.3129 | 418.7535 | 14.2856 | 29.3129 | 441.128 | 15.0489 | 29.3129 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 2.4181 | 206 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 80.3262 | 1.6597 | 48.3969 | 80.3262 | 1.6597 | 48.3969 | 84.6182 | 1.7484 | 48.3969 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 4.0926 | 174 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 312.1007 | 2.8091 | 111.105 | 312.1007 | 2.8091 | 111.105 | 328.7766 | 2.9592 | 111.105 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2026 | 972 | 972-1642 | Tier-2 | Tier-2---16 | 5--2 | 0.038636 | 0 | 100% | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.026519 | 0 | 0 | 0.026519 | 0 | 0 | 0.027936 | 0 | 0% | 0.11047 | 0.105 | 1677.3427 | 1.9611 | 1510.6909 | 164.6906 | 1764.6951 | 0 | 0 | 1764.6951 | 0%
2026 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.2301 | 17 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 15.2415 | 0.15793 | 96.506 | 15.2415 | 0.15793 | 96.506 | 16.0558 | 0.16637 | 96.506 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.38903 | 14 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 32.5478 | 0.26702 | 121.892 | 32.5478 | 0.26702 | 121.892 | 34.2868 | 0.28129 | 121.892 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 12.821 | 921 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 151.2085 | 8.8 | 17.1828 | 151.2085 | 8.8 | 17.1828 | 159.2877 | 9.2702 | 17.1828 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 10.8114 | 889 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 83.2547 | 7.4206 | 11.2193 | 83.2547 | 7.4206 | 11.2193 | 87.7031 | 7.8171 | 11.2193 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 2.6777 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 237.7519 | 1.8379 | 129.3619 | 237.7519 | 1.8379 | 129.3619 | 250.4553 | 1.9361 | 129.3619 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 11.5801 | 469 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 482.9506 | 7.9483 | 60.7618 | 482.9506 | 7.9483 | 60.7618 | 508.7553 | 8.3729 | 60.7618 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2026 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 2.4417 | 29 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 9.8433 | 1.6759 | 5.8735 | 9.8433 | 1.6759 | 5.8735 | 10.3692 | 1.7654 | 5.8735 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2026 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 9.2184 | 137 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 18.954 | 6.3272 | 2.9956 | 18.954 | 6.3272 | 2.9956 | 19.9668 | 6.6653 | 2.9956 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.075568 | 0 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 9.0555 | 0.051868 | 174.5888 | 9.0555 | 0.051868 | 174.5888 | 9.5394 | 0.054639 | 174.5888 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 6.8952 | 725 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 39.8446 | 4.7327 | 8.419 | 39.8446 | 4.7327 | 8.419 | 41.9736 | 4.9856 | 8.419 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 3.5241 | 66 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 61.1593 | 2.4188 | 25.2848 | 61.1593 | 2.4188 | 25.2848 | 64.4271 | 2.5481 | 25.2848 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2026 | 386 | CB 386 | Tier-2 | Tier-2---14 | 4--4 | 2.7822 | 0 | 100% | 266.4482 | 58.89% | 39.19% | 1.927% | 7.7666 | 0 | 0 | 7.7666 | 0 | 7.4088 | 1.9096 | 3.8797 | 7.4088 | 1.9096 | 3.8797 | 7.8047 | 2.0117 | 3.8797 | 2.915% | 0.037437 | 0.035584 | 7117.2424 | 561.1032 | 3326.6838 | 3229.4554 | 7269.6317 | 0 | 0 | 7269.6317 | 0.0002561%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 11.3933 | 245 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 55.7504 | 7.8201 | 7.1292 | 55.7504 | 7.8201 | 7.1292 | 58.7292 | 8.2379 | 7.1292 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 1.2636 | 4 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 21.4326 | 0.8673 | 24.7119 | 21.4326 | 0.8673 | 24.7119 | 22.5778 | 0.91364 | 24.7119 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2026 | 858 | 858-14 | Tier-2 | Tier-2---12 | 2--5 | 1.3439 | 0 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 20.2792 | 0 | 0 | 20.2792 | 0 | 19.345 | 0.92242 | 20.9721 | 19.345 | 0.92242 | 20.9721 | 20.3786 | 0.9717 | 20.9721 | 4.926% | 0.010043 | 0.0095457 | 40994.194 | 8631.9946 | 63.0219 | 32299.1775 | 41004.6459 | 0 | 0 | 41004.6459 | 0.0006687%
2026 | 282 | CB 282 | Tier-2 | Tier-2---15 | 4--3 | 0.221 | 0 | 100% | 152.5069 | 4.749% | 94.48% | 0.7672% | 0.3585 | 0 | 0 | 0.3585 | 0 | 0.34198 | 0.15169 | 2.2545 | 0.34198 | 0.15169 | 2.2545 | 0.36025 | 0.15979 | 2.2545 | 0.2351% | 0.035573 | 0.033812 | 4287.153 | 11.5968 | 3743.6752 | 531.8809 | 4499.8161 | 0 | 0 | 4499.8161 | 1.182e-05%
2026 | 795 | 795-816R | Tier-2 | Tier-2---13 | 4--4 | 2.6195 | 0 | 100% | 228.7654 | 4.756% | 93.08% | 2.167% | 0.53859 | 0 | 0 | 0.53859 | 0 | 0.51378 | 1.798 | 0.28576 | 0.51378 | 1.798 | 0.28576 | 0.54123 | 1.894 | 0.28576 | 0.2354% | 0.036491 | 0.034684 | 6269.16 | 14.3219 | 5608.3339 | 646.5042 | 6580.116 | 0 | 0 | 6580.116 | 1.776e-05%
2026 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 0.64526 | 21 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 15.4569 | 0.44289 | 34.9 | 15.4569 | 0.44289 | 34.9 | 16.2828 | 0.46656 | 34.9 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 3.4282 | 107 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 67.1788 | 2.353 | 28.5503 | 67.1788 | 2.353 | 28.5503 | 70.7683 | 2.4787 | 28.5503 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 11.6815 | 979 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 312.9422 | 8.0178 | 39.0308 | 312.9422 | 8.0178 | 39.0308 | 329.6631 | 8.4462 | 39.0308 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 20.7706 | 2353 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 310.9519 | 14.2564 | 21.8114 | 310.9519 | 14.2564 | 21.8114 | 327.5665 | 15.0181 | 21.8114 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 10.4561 | 129 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 32.9073 | 7.1768 | 4.5853 | 32.9073 | 7.1768 | 4.5853 | 34.6656 | 7.5602 | 4.5853 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 2.8193 | 65 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 17.5537 | 1.9351 | 9.0712 | 17.5537 | 1.9351 | 9.0712 | 18.4916 | 2.0385 | 9.0712 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 13.3513 | 1600 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 421.536 | 9.164 | 45.9993 | 421.536 | 9.164 | 45.9993 | 444.0593 | 9.6536 | 45.9993 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2026 | 928 | 928-20 | Tier-2 | Tier-2---20 | 4--2 | 0.0328 | 0 | 100% | 27.1749 | 93.08% | 6.522% | 0.4024% | 1.252 | 0 | 0 | 1.252 | 0 | 1.1943 | 0.022513 | 53.0508 | 1.1943 | 0.022513 | 53.0508 | 1.2581 | 0.023716 | 53.0508 | 4.607% | 0.044362 | 0.042166 | 612.5656 | 93.209 | 34.6926 | 484.664 | 614.7746 | 0 | 0 | 614.7746 | 4.129e-05%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 4.9693 | 637 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 34.2033 | 3.4108 | 10.0279 | 34.2033 | 3.4108 | 10.0279 | 36.0308 | 3.5931 | 10.0279 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2026 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 5.2678 | 343 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 45.8593 | 3.6157 | 12.6835 | 45.8593 | 3.6157 | 12.6835 | 48.3097 | 3.8089 | 12.6835 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 14.5858 | 738 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1099.8308 | 10.0113 | 109.8593 | 1099.8308 | 10.0113 | 109.8593 | 1158.5963 | 10.5462 | 109.8593 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2026 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 0.049053 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.1037 | 0.033669 | 3.0799 | 0.1037 | 0.033669 | 3.0799 | 0.10924 | 0.035468 | 3.0799 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 0.20947 | 11 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 6.473 | 0.14377 | 45.022 | 6.473 | 0.14377 | 45.022 | 6.8189 | 0.15146 | 45.022 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 9.6756 | 209 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 68.092 | 6.6411 | 10.2532 | 68.092 | 6.6411 | 10.2532 | 71.7303 | 6.9959 | 10.2532 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2026 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 2.7722 | 17 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.8558 | 1.9027 | 0.97532 | 1.8558 | 1.9027 | 0.97532 | 1.9549 | 2.0044 | 0.97532 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 3.6174 | 367 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 210.4643 | 2.4829 | 84.7651 | 210.4643 | 2.4829 | 84.7651 | 221.7097 | 2.6156 | 84.7651 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 9.2129 | 303 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 215.6371 | 6.3235 | 34.101 | 215.6371 | 6.3235 | 34.101 | 227.1588 | 6.6614 | 34.101 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 7.3522 | 285 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 156.9652 | 5.0464 | 31.1046 | 156.9652 | 5.0464 | 31.1046 | 165.3521 | 5.316 | 31.1046 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.32386 | 57 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 18.6068 | 0.22229 | 83.7047 | 18.6068 | 0.22229 | 83.7047 | 19.601 | 0.23417 | 83.7047 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 1.7152 | 34 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 338.4324 | 1.1772 | 287.4814 | 338.4324 | 1.1772 | 287.4814 | 356.5153 | 1.2401 | 287.4814 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 10.7038 | 848 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 308.8644 | 7.3468 | 42.0408 | 308.8644 | 7.3468 | 42.0408 | 325.3674 | 7.7393 | 42.0408 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 1.7237 | 253 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 64.1211 | 1.1831 | 54.1981 | 64.1211 | 1.1831 | 54.1981 | 67.5471 | 1.2463 | 54.1981 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2026 | 243 | CB 243 | Tier-2 | Tier-2---14 | 4--4 | 0.7388 | 0 | 100% | 284.2808 | 92.1% | 7.127% | 0.7733% | 12.9602 | 0 | 0 | 12.9602 | 0 | 12.3631 | 0.50709 | 24.3804 | 12.3631 | 0.50709 | 24.3804 | 13.0237 | 0.53419 | 24.3804 | 4.559% | 0.039288 | 0.037343 | 7235.7813 | 1297.464 | 840.9216 | 5097.3957 | 7265.5523 | 0 | 0 | 7265.5523 | 0.0004274%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 10.906 | 246 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 301.8886 | 7.4856 | 40.3292 | 301.8886 | 7.4856 | 40.3292 | 318.019 | 7.8856 | 40.3292 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2026 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | 4--1 | 0.012311 | 0 | 100% | 2.3826 | 9.042% | 83.57% | 7.391% | 0.010664 | 0 | 0 | 0.010664 | 0 | 0.010173 | 0.0084499 | 1.2039 | 0.010173 | 0.0084499 | 1.2039 | 0.010716 | 0.0089014 | 1.2039 | 0.4476% | 0.059368 | 0.05643 | 40.1318 | 0.36722 | 29.4839 | 10.2807 | 42.0328 | 0 | 0 | 42.0328 | 3.517e-07%
2026 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.11724 | 0 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 15.7754 | 0.080467 | 196.049 | 15.7754 | 0.080467 | 196.049 | 16.6183 | 0.084766 | 196.049 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 33.4712 | 1238 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 3060.5719 | 22.9737 | 133.2208 | 3060.5719 | 22.9737 | 133.2208 | 3224.1024 | 24.2012 | 133.2208 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2026 | 920 | 920-823 | Tier-2 | Tier-2---11 | 4--4 | 0.871 | 0 | 100% | 458.2189 | 68.35% | 31.14% | 0.5113% | 15.5021 | 0 | 0 | 15.5021 | 0 | 14.788 | 0.59783 | 24.7361 | 14.788 | 0.59783 | 24.7361 | 15.5781 | 0.62977 | 24.7361 | 3.383% | 0.054577 | 0.051875 | 8395.8542 | 937.9397 | 2311.5146 | 5146.3999 | 8534.2572 | 0 | 0 | 8534.2572 | 0.0005112%
2026 | 280 | CB 280 | Tier-2 | Tier-2---14 | 4--4 | 2.6745 | 17 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 2.4753 | 0 | 0 | 2.4753 | 0 | 2.3613 | 1.8357 | 1.2863 | 2.3613 | 1.8357 | 1.2863 | 2.4875 | 1.9338 | 1.2863 | 0.7965% | 0.042409 | 0.04031 | 7328.4886 | 170.2669 | 5820.5339 | 1337.6878 | 7648.7329 | 0 | 0 | 7648.7329 | 8.163e-05%
2026 | 355 | 355-65R | Tier-2 | Tier-2---21 | 1--2 | 0.007576 | 0 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.0015289 | 0 | 0 | 0.0015289 | 0 | 0.0014584 | 0.0052 | 0.28047 | 0.0014584 | 0.0052 | 0.28047 | 0.0015364 | 0.0054778 | 0.28047 | 2.282% | 7.02e-05 | 6.6725e-05 | 954.2713 | 72.5365 | 46.719 | 835.0158 | 981.0548 | 0 | 0 | 981.0548 | 5.042e-08%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 6.5815 | 222 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 58.2545 | 4.5173 | 12.8957 | 58.2545 | 4.5173 | 12.8957 | 61.3671 | 4.7587 | 12.8957 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 19.1678 | 1740 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 429.1796 | 13.1563 | 32.6217 | 429.1796 | 13.1563 | 32.6217 | 452.1112 | 13.8592 | 32.6217 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2026 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.033523 | 0 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.5386 | 0.023009 | 23.408 | 0.5386 | 0.023009 | 23.408 | 0.56738 | 0.024239 | 23.408 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2026 | 235 | CB 235 | Tier-2 | Tier-2---12 | 1--5 | 0.15928 | 0 | 100% | 443.5427 | 99.96% | 0% | 0.03939% | 21.9467 | 0 | 0 | 21.9467 | 0 | 20.9357 | 0.10933 | 191.4988 | 20.9357 | 0.10933 | 191.4988 | 22.0543 | 0.11517 | 191.4988 | 4.948% | 0.0007134 | 0.00067809 | 621730.7449 | 100003.5038 | 3209.2492 | 518517.9918 | 621743.4984 | 0 | 0 | 621743.4984 | 0.0007237%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 5.3209 | 577 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 158.2696 | 3.6521 | 43.3365 | 158.2696 | 3.6521 | 43.3365 | 166.7261 | 3.8472 | 43.3365 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 8.1068 | 164 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 23.5661 | 5.5643 | 4.2352 | 23.5661 | 5.5643 | 4.2352 | 24.8252 | 5.8616 | 4.2352 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2026 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 7.7129 | 463 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 6.0436 | 5.2939 | 1.1416 | 6.0436 | 5.2939 | 1.1416 | 6.3665 | 5.5768 | 1.1416 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2026 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.58561 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 4.0459 | 0.40194 | 10.066 | 4.0459 | 0.40194 | 10.066 | 4.2621 | 0.42342 | 10.066 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 7.0273 | 9 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 15.2309 | 4.8233 | 3.1577 | 15.2309 | 4.8233 | 3.1577 | 16.0447 | 5.0811 | 3.1577 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 10.6015 | 361 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 42.0166 | 7.2766 | 5.7742 | 42.0166 | 7.2766 | 5.7742 | 44.2616 | 7.6654 | 5.7742 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 3.3435 | 149 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 405.1363 | 2.2949 | 176.5371 | 405.1363 | 2.2949 | 176.5371 | 426.7833 | 2.4175 | 176.5371 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2026 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 3.5375 | 52 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.089086 | 2.4281 | 0.03669 | 0.089086 | 2.4281 | 0.03669 | 0.093845 | 2.5578 | 0.03669 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2026 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 5.4324 | 4 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 21.551 | 3.7286 | 5.7799 | 21.551 | 3.7286 | 5.7799 | 22.7025 | 3.9279 | 5.7799 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 0.38934 | 15 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 8.5432 | 0.26724 | 31.969 | 8.5432 | 0.26724 | 31.969 | 8.9997 | 0.28151 | 31.969 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2026 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | 3--3 | 2.0388 | 0 | 100% | 117.3021 | 94.99% | 0% | 5.009% | 5.5156 | 0 | 0 | 5.5156 | 0 | 5.2615 | 1.3994 | 3.7599 | 5.2615 | 1.3994 | 3.7599 | 5.5427 | 1.4742 | 3.7599 | 4.702% | 0.027256 | 0.025907 | 4303.7498 | 1020.4795 | 248.6707 | 3034.5996 | 4314.9761 | 0 | 0 | 4314.9761 | 0.0001819%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 7.8127 | 414 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 911.0636 | 5.3624 | 169.8986 | 911.0636 | 5.3624 | 169.8986 | 959.743 | 5.6489 | 169.8986 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 3.1864 | 107 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 142.8022 | 2.187 | 65.2949 | 142.8022 | 2.187 | 65.2949 | 150.4323 | 2.3039 | 65.2949 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 1.1027 | 132 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 34.7023 | 0.75685 | 45.8509 | 34.7023 | 0.75685 | 45.8509 | 36.5565 | 0.79729 | 45.8509 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 7.8693 | 814 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 453.1135 | 5.4013 | 83.8904 | 453.1135 | 5.4013 | 83.8904 | 477.324 | 5.6899 | 83.8904 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2026 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.053788 | 0 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.088733 | 0.036919 | 2.4035 | 0.088733 | 0.036919 | 2.4035 | 0.093474 | 0.038891 | 2.4035 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2026 | 452 | 452-717 | Tier-2 | Tier-2---19 | 1--5 | 0.0871 | 0 | 100% | 24.802 | 99.04% | 0% | 0.9608% | 1.2159 | 0 | 0 | 1.2159 | 0 | 1.1599 | 0.059783 | 19.4017 | 1.1599 | 0.059783 | 19.4017 | 1.2219 | 0.062977 | 19.4017 | 4.902% | 0.000973 | 0.00092484 | 25490.2561 | 9086.828 | 25.5586 | 16377.8695 | 25503.0101 | 0 | 0 | 25503.0101 | 4.01e-05%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 13.2184 | 308 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 181.173 | 9.0728 | 19.9689 | 181.173 | 9.0728 | 19.9689 | 190.8533 | 9.5575 | 19.9689 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2026 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.027841 | 0 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.28535 | 0.019109 | 14.9323 | 0.28535 | 0.019109 | 14.9323 | 0.30059 | 0.02013 | 14.9323 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 6.3703 | 486 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 676.0489 | 4.3724 | 154.6173 | 676.0489 | 4.3724 | 154.6173 | 712.1711 | 4.606 | 154.6173 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 2.6683 | 515 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 23.9277 | 1.8315 | 13.0647 | 23.9277 | 1.8315 | 13.0647 | 25.2062 | 1.9293 | 13.0647 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 11.3506 | 1487 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 296.4305 | 7.7907 | 38.0491 | 296.4305 | 7.7907 | 38.0491 | 312.2692 | 8.207 | 38.0491 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 6.121 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 96.5805 | 4.2013 | 22.9884 | 96.5805 | 4.2013 | 22.9884 | 101.7409 | 4.4258 | 22.9884 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 6.7335 | 641 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 687.0628 | 4.6217 | 148.6608 | 687.0628 | 4.6217 | 148.6608 | 723.7735 | 4.8686 | 148.6608 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 1.5907 | 12 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.4319 | 1.0918 | 3.1433 | 3.4319 | 1.0918 | 3.1433 | 3.6153 | 1.1501 | 3.1433 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2026 | 266 | 266-485F | Tier-2 | Tier-2---21 | 1--4 | 0.047 | 0 | 100% | 3.9025 | 97.35% | 0% | 2.654% | 0.18805 | 0 | 0 | 0.18805 | 0 | 0.17939 | 0.032259 | 5.5607 | 0.17939 | 0.032259 | 5.5607 | 0.18897 | 0.033983 | 5.5607 | 4.819% | 0.000646 | 0.00061402 | 6041.0896 | 954.7948 | 18.9693 | 5067.3254 | 6049.4401 | 0 | 0 | 6049.4401 | 6.201e-06%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 6.8056 | 645 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 75.5263 | 4.6712 | 16.1685 | 75.5263 | 4.6712 | 16.1685 | 79.5617 | 4.9208 | 16.1685 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 11.3022 | 654 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 1047.5713 | 7.7575 | 135.039 | 1047.5713 | 7.7575 | 135.039 | 1103.5445 | 8.172 | 135.039 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 7.9883 | 1090 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 142.3168 | 5.4829 | 25.9563 | 142.3168 | 5.4829 | 25.9563 | 149.921 | 5.7759 | 25.9563 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 6.2962 | 587 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 348.8651 | 4.3216 | 80.7267 | 348.8651 | 4.3216 | 80.7267 | 367.5055 | 4.5525 | 80.7267 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 0.60433 | 297 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 20.4688 | 0.41479 | 49.3469 | 20.4688 | 0.41479 | 49.3469 | 21.5625 | 0.43696 | 49.3469 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 0.61936 | 43 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.73672 | 0.42511 | 1.733 | 0.73672 | 0.42511 | 1.733 | 0.77608 | 0.44783 | 1.733 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 34.4453 | 2656 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 255.1218 | 23.6423 | 10.7909 | 255.1218 | 23.6423 | 10.7909 | 268.7533 | 24.9055 | 10.7909 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 3.289 | 353 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 28.7981 | 2.2575 | 12.7567 | 28.7981 | 2.2575 | 12.7567 | 30.3368 | 2.3781 | 12.7567 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 3.4321 | 23 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 9.4254 | 2.3557 | 4.0011 | 9.4254 | 2.3557 | 4.0011 | 9.929 | 2.4815 | 4.0011 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 2.081 | 79 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 8.2042 | 1.4284 | 5.7438 | 8.2042 | 1.4284 | 5.7438 | 8.6426 | 1.5047 | 5.7438 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 9.6284 | 454 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 488.2028 | 6.6087 | 73.8729 | 488.2028 | 6.6087 | 73.8729 | 514.2881 | 6.9618 | 73.8729 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 4.8606 | 121 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 17.3347 | 3.3362 | 5.196 | 17.3347 | 3.3362 | 5.196 | 18.261 | 3.5144 | 5.196 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2026 | 252 | 252-129 | Tier-2 | Tier-2---18 | 3--3 | 4.2973 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 2.1229 | 0 | 0 | 2.1229 | 0 | 2.0251 | 2.9496 | 0.68657 | 2.0251 | 2.9496 | 0.68657 | 2.1333 | 3.1071 | 0.68657 | 4.29% | 0.02391 | 0.022726 | 2069.6845 | 324.0484 | 134.0961 | 1611.54 | 2084.0584 | 0 | 0 | 2084.0584 | 7e-05%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 4.0623 | 220 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 24.2408 | 2.7883 | 8.6939 | 24.2408 | 2.7883 | 8.6939 | 25.536 | 2.9372 | 8.6939 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 20.3065 | 1265 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 185.1522 | 13.9378 | 13.2842 | 185.1522 | 13.9378 | 13.2842 | 195.0451 | 14.6825 | 13.2842 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 5.9877 | 433 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 251.8011 | 4.1098 | 61.2682 | 251.8011 | 4.1098 | 61.2682 | 265.2552 | 4.3294 | 61.2682 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 12.0589 | 918 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 290.7937 | 8.2769 | 35.1332 | 290.7937 | 8.2769 | 35.1332 | 306.3312 | 8.7191 | 35.1332 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2026 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 6.3104 | 318 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 5.3672 | 4.3313 | 1.2392 | 5.3672 | 4.3313 | 1.2392 | 5.654 | 4.5627 | 1.2392 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2026 | 280 | 280-24AE | Tier-2 | Tier-2---12 | 4--4 | 0.5631 | 0 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.56941 | 0 | 0 | 0.56941 | 0 | 0.54317 | 0.3865 | 1.4054 | 0.54317 | 0.3865 | 1.4054 | 0.5722 | 0.40715 | 1.4054 | 0.1557% | 0.037093 | 0.035257 | 9861.3901 | 49.7133 | 8813.1546 | 998.5222 | 10358.7999 | 0 | 0 | 10358.7999 | 1.878e-05%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 27.9316 | 2562 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1208.2563 | 19.1715 | 63.0236 | 1208.2563 | 19.1715 | 63.0236 | 1272.8151 | 20.1959 | 63.0236 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 5.7761 | 269 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 550.1247 | 3.9646 | 138.7599 | 550.1247 | 3.9646 | 138.7599 | 579.5186 | 4.1764 | 138.7599 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.95666 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 58.5262 | 0.65663 | 89.1317 | 58.5262 | 0.65663 | 89.1317 | 61.6533 | 0.69171 | 89.1317 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 7.5917 | 224 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 476.2228 | 5.2107 | 91.3928 | 476.2228 | 5.2107 | 91.3928 | 501.668 | 5.4891 | 91.3928 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 8.614 | 942 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 89.1348 | 5.9124 | 15.0758 | 89.1348 | 5.9124 | 15.0758 | 93.8974 | 6.2283 | 15.0758 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2.1411 | 3 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 20.4262 | 1.4696 | 13.8995 | 20.4262 | 1.4696 | 13.8995 | 21.5176 | 1.5481 | 13.8995 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 1.8381 | 85 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 60.2656 | 1.2616 | 47.7682 | 60.2656 | 1.2616 | 47.7682 | 63.4857 | 1.329 | 47.7682 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2026 | 308 | CB 308 | Tier-2 | Tier-2---18 | 4--3 | 0.8729 | 0 | 100% | 77.7948 | 18.36% | 79.79% | 1.851% | 0.70708 | 0 | 0 | 0.70708 | 0 | 0.6745 | 0.59913 | 1.1258 | 0.6745 | 0.59913 | 1.1258 | 0.71054 | 0.63115 | 1.1258 | 0.9089% | 0.037941 | 0.036063 | 2050.437 | 12.1248 | 1817.8081 | 220.5041 | 2137.6123 | 0 | 0 | 2137.6123 | 2.332e-05%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 3.0796 | 188 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 9.1137 | 2.1137 | 4.3116 | 9.1137 | 2.1137 | 4.3116 | 9.6007 | 2.2267 | 4.3116 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 10.0146 | 475 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 33.1256 | 6.8737 | 4.8192 | 33.1256 | 6.8737 | 4.8192 | 34.8956 | 7.241 | 4.8192 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2026 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 1.532 | 0 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 268.9313 | 1.0515 | 255.7529 | 268.9313 | 1.0515 | 255.7529 | 283.3006 | 1.1077 | 255.7529 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2026 | 401 | 401-39R | Tier-2 | Tier-2---14 | 4--4 | 0.0585 | 0 | 100% | 323.2323 | 3.193% | 96.7% | 0.1048% | 0.51091 | 0 | 0 | 0.51091 | 0 | 0.48737 | 0.040153 | 12.1379 | 0.48737 | 0.040153 | 12.1379 | 0.51341 | 0.042298 | 12.1379 | 0.1581% | 0.031872 | 0.030295 | 10141.4477 | 77.0794 | 9013.6522 | 1050.7162 | 10652.728 | 0 | 0 | 10652.728 | 1.685e-05%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 0.63484 | 10 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.34944 | 0.43574 | 0.80194 | 0.34944 | 0.43574 | 0.80194 | 0.36811 | 0.45902 | 0.80194 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 8.7678 | 225 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 18.7295 | 6.018 | 3.1123 | 18.7295 | 6.018 | 3.1123 | 19.7302 | 6.3395 | 3.1123 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.87727 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 68.6427 | 0.60214 | 113.9987 | 68.6427 | 0.60214 | 113.9987 | 72.3104 | 0.63431 | 113.9987 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2026 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011932 | 0 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081898 | 0 | 0 | 0.0081898 | 0 | 0 | 0.0086274 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 3.06 | 54 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 99.0448 | 2.1003 | 47.1574 | 99.0448 | 2.1003 | 47.1574 | 104.3369 | 2.2125 | 47.1574 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 1.6544 | 24 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 243.3088 | 1.1355 | 214.2739 | 243.3088 | 1.1355 | 214.2739 | 256.3092 | 1.1962 | 214.2739 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 0.11231 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.16305 | 0.077087 | 2.1151 | 0.16305 | 0.077087 | 2.1151 | 0.17176 | 0.081206 | 2.1151 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 3.4226 | 424 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 198.1694 | 2.3492 | 84.3577 | 198.1694 | 2.3492 | 84.3577 | 208.7579 | 2.4747 | 84.3577 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 2.6673 | 417 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 70.7701 | 1.8307 | 38.6568 | 70.7701 | 1.8307 | 38.6568 | 74.5514 | 1.9285 | 38.6568 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2026 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 0 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.73012 | 0.023529 | 31.0308 | 0.73012 | 0.023529 | 31.0308 | 0.76913 | 0.024786 | 31.0308 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.87803 | 24 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 30.6993 | 0.60266 | 50.9401 | 30.6993 | 0.60266 | 50.9401 | 32.3396 | 0.63486 | 50.9401 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 17.882 | 25 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 58.5338 | 12.2737 | 4.769 | 58.5338 | 12.2737 | 4.769 | 61.6614 | 12.9295 | 4.769 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.030114 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.4787 | 0.020669 | 265.0633 | 5.4787 | 0.020669 | 265.0633 | 5.7714 | 0.021774 | 265.0633 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 9.9068 | 699 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 85.8122 | 6.7998 | 12.6199 | 85.8122 | 6.7998 | 12.6199 | 90.3972 | 7.1631 | 12.6199 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 2.1343 | 19 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 34.2346 | 1.4649 | 23.3701 | 34.2346 | 1.4649 | 23.3701 | 36.0638 | 1.5432 | 23.3701 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 1.1486 | 101 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.8974 | 0.7884 | 12.5539 | 9.8974 | 0.7884 | 12.5539 | 10.4263 | 0.83052 | 12.5539 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.46834 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 37.3591 | 0.32145 | 116.2189 | 37.3591 | 0.32145 | 116.2189 | 39.3553 | 0.33863 | 116.2189 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2026 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.23902 | 0 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 1.0753 | 0.16405 | 6.5546 | 1.0753 | 0.16405 | 6.5546 | 1.1328 | 0.17282 | 6.5546 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 17.7839 | 336 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 249.0215 | 12.2064 | 20.4009 | 249.0215 | 12.2064 | 20.4009 | 262.327 | 12.8586 | 20.4009 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 27.7907 | 1376 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 858.8326 | 19.0747 | 45.0246 | 858.8326 | 19.0747 | 45.0246 | 904.7212 | 20.0939 | 45.0246 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2026 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 1.0255 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.9791 | 0.70389 | 21.2804 | 14.9791 | 0.70389 | 21.2804 | 15.7795 | 0.7415 | 21.2804 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 1.6259 | 6 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 19.3654 | 1.116 | 17.3525 | 19.3654 | 1.116 | 17.3525 | 20.4002 | 1.1756 | 17.3525 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 9.0746 | 475 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 227.6349 | 6.2285 | 36.5471 | 227.6349 | 6.2285 | 36.5471 | 239.7978 | 6.5613 | 36.5471 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 10.35 | 778 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 201.9487 | 7.104 | 28.4276 | 201.9487 | 7.104 | 28.4276 | 212.7391 | 7.4835 | 28.4276 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 5.1765 | 270 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 129.6779 | 3.553 | 36.4979 | 129.6779 | 3.553 | 36.4979 | 136.6068 | 3.7429 | 36.4979 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.94526 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 169.657 | 0.6488 | 261.4946 | 169.657 | 0.6488 | 261.4946 | 178.722 | 0.68346 | 261.4946 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.47553 | 18 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 27.5211 | 0.32639 | 84.3201 | 27.5211 | 0.32639 | 84.3201 | 28.9916 | 0.34383 | 84.3201 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 2.6021 | 514 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 61.0795 | 1.786 | 34.1985 | 61.0795 | 1.786 | 34.1985 | 64.343 | 1.8815 | 34.1985 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 19.0867 | 1839 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 200.6758 | 13.1006 | 15.3181 | 200.6758 | 13.1006 | 15.3181 | 211.3982 | 13.8006 | 15.3181 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.70208 | 157 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 5.0165 | 0.48189 | 10.41 | 5.0165 | 0.48189 | 10.41 | 5.2845 | 0.50764 | 10.41 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2026 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 4.4396 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 29.8334 | 3.0472 | 9.7904 | 29.8334 | 3.0472 | 9.7904 | 31.4275 | 3.21 | 9.7904 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 7.7195 | 1158 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 180.2727 | 5.2984 | 34.0237 | 180.2727 | 5.2984 | 34.0237 | 189.905 | 5.5815 | 34.0237 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.46496 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 61.292 | 0.31914 | 192.0556 | 61.292 | 0.31914 | 192.0556 | 64.5669 | 0.33619 | 192.0556 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 2.2173 | 249 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 103.5189 | 1.5219 | 68.0203 | 103.5189 | 1.5219 | 68.0203 | 109.0501 | 1.6032 | 68.0203 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 5.5852 | 7 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 184.1331 | 3.8335 | 48.0321 | 184.1331 | 3.8335 | 48.0321 | 193.9716 | 4.0384 | 48.0321 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 2.0289 | 237 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 31.4944 | 1.3926 | 22.6154 | 31.4944 | 1.3926 | 22.6154 | 33.1772 | 1.467 | 22.6154 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 9.4684 | 640 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 94.2031 | 6.4988 | 14.4954 | 94.2031 | 6.4988 | 14.4954 | 99.2365 | 6.8461 | 14.4954 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 2.7573 | 110 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 36.8826 | 1.8926 | 19.4882 | 36.8826 | 1.8926 | 19.4882 | 38.8532 | 1.9937 | 19.4882 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 3.4339 | 102 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 199.4969 | 2.3569 | 84.6429 | 199.4969 | 2.3569 | 84.6429 | 210.1563 | 2.4829 | 84.6429 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2026 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.052273 | 0 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.11451 | 0.035879 | 3.1915 | 0.11451 | 0.035879 | 3.1915 | 0.12063 | 0.037796 | 3.1915 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 3.3255 | 21 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 10.0061 | 2.2826 | 4.3837 | 10.0061 | 2.2826 | 4.3837 | 10.5407 | 2.4045 | 4.3837 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 11.8649 | 1745 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 228.8419 | 8.1438 | 28.1003 | 228.8419 | 8.1438 | 28.1003 | 241.0693 | 8.5789 | 28.1003 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 17.4926 | 1898 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 256.8342 | 12.0064 | 21.3914 | 256.8342 | 12.0064 | 21.3914 | 270.5572 | 12.648 | 21.3914 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 14.2375 | 375 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2122.0228 | 9.7722 | 217.149 | 2122.0228 | 9.7722 | 217.149 | 2235.4054 | 10.2943 | 217.149 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2026 | 534 | CB 534 | Tier-2 | Tier-2---21 | 4--1 | 0.38371 | 0 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11233 | 0 | 0 | 0.11233 | 0 | 0.10716 | 0.26337 | 0.40687 | 0.10716 | 0.26337 | 0.40687 | 0.11288 | 0.27744 | 0.40687 | 1.782% | 0.060541 | 0.057544 | 104.1456 | 5.1049 | 50.6919 | 48.3488 | 107.6172 | 0 | 0 | 107.6172 | 3.704e-06%
2026 | 296 | 296-66F | Tier-2 | Tier-2---21 | 1--3 | 0.0214 | 0 | 100% | 2.284 | 90.58% | 0% | 9.421% | 0.10241 | 0 | 0 | 0.10241 | 0 | 0.097688 | 0.014688 | 6.6507 | 0.097688 | 0.014688 | 6.6507 | 0.10291 | 0.015473 | 6.6507 | 4.484% | 0.0006178 | 0.00058722 | 3696.9667 | 843.8145 | 35.5403 | 2817.6118 | 3715.1054 | 0 | 0 | 3715.1054 | 3.377e-06%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 17.4388 | 870 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 94.985 | 11.9695 | 7.9356 | 94.985 | 11.9695 | 7.9356 | 100.0601 | 12.609 | 7.9356 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 3.8686 | 155 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 174.1258 | 2.6553 | 65.5774 | 174.1258 | 2.6553 | 65.5774 | 183.4296 | 2.7971 | 65.5774 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 3.9246 | 150 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 157.0745 | 2.6938 | 58.3104 | 157.0745 | 2.6938 | 58.3104 | 165.4672 | 2.8377 | 58.3104 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 0.43788 | 86 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 19.1516 | 0.30055 | 63.7221 | 19.1516 | 0.30055 | 63.7221 | 20.1748 | 0.31661 | 63.7221 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 6.1356 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 103.331 | 4.2113 | 24.5366 | 103.331 | 4.2113 | 24.5366 | 108.8522 | 4.4363 | 24.5366 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 13.604 | 933 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 861.4981 | 9.3374 | 92.263 | 861.4981 | 9.3374 | 92.263 | 907.5291 | 9.8363 | 92.263 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 8.2782 | 212 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 25.6177 | 5.6819 | 4.5086 | 25.6177 | 5.6819 | 4.5086 | 26.9865 | 5.9855 | 4.5086 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2026 | 461 | CB 461 | Tier-2 | Tier-2---15 | 2--4 | 2.3375 | 0 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 4.9747 | 0 | 0 | 4.9747 | 0 | 4.7455 | 1.6044 | 2.9578 | 4.7455 | 1.6044 | 2.9578 | 4.9991 | 1.6902 | 2.9578 | 4.883% | 0.0097562 | 0.0092733 | 10441.6529 | 2274.299 | 1515.1673 | 6652.1866 | 10448.9777 | 0 | 0 | 10448.9777 | 0.000164%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 16.0805 | 603 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 154.5294 | 11.0372 | 14.0008 | 154.5294 | 11.0372 | 14.0008 | 162.7862 | 11.6269 | 14.0008 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.11194 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 7.1363 | 0.076832 | 92.8817 | 7.1363 | 0.076832 | 92.8817 | 7.5176 | 0.080937 | 92.8817 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 5.7011 | 315 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 382.4036 | 3.9131 | 97.7242 | 382.4036 | 3.9131 | 97.7242 | 402.8359 | 4.1222 | 97.7242 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 12.622 | 1027 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1102.1556 | 8.6634 | 127.22 | 1102.1556 | 8.6634 | 127.22 | 1161.0453 | 9.1263 | 127.22 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 13.7044 | 1345 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 336.8429 | 9.4063 | 35.8104 | 336.8429 | 9.4063 | 35.8104 | 354.8409 | 9.9089 | 35.8104 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2026 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 4.354 | 0 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 22.1263 | 2.9885 | 7.4039 | 22.1263 | 2.9885 | 7.4039 | 23.3085 | 3.1481 | 7.4039 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2026 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 6.0637 | 134 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 50.3341 | 4.1619 | 12.0939 | 50.3341 | 4.1619 | 12.0939 | 53.0235 | 4.3843 | 12.0939 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 12.4352 | 2343 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 337.9327 | 8.5352 | 39.5929 | 337.9327 | 8.5352 | 39.5929 | 355.9889 | 8.9912 | 39.5929 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 8.4532 | 216 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 152.0596 | 5.8021 | 26.2079 | 152.0596 | 5.8021 | 26.2079 | 160.1843 | 6.1121 | 26.2079 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2026 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.18447 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.5515 | 0.12662 | 20.1516 | 2.5515 | 0.12662 | 20.1516 | 2.6878 | 0.13338 | 20.1516 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 10.2425 | 319 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 71.3254 | 7.0301 | 10.1457 | 71.3254 | 7.0301 | 10.1457 | 75.1364 | 7.4058 | 10.1457 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 7.3926 | 433 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 167.1394 | 5.0741 | 32.9399 | 167.1394 | 5.0741 | 32.9399 | 176.0699 | 5.3452 | 32.9399 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 4.8975 | 133 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 72.5366 | 3.3615 | 21.5786 | 72.5366 | 3.3615 | 21.5786 | 76.4123 | 3.5411 | 21.5786 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 0.074242 | 9 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.31399 | 0.050958 | 6.1619 | 0.31399 | 0.050958 | 6.1619 | 0.33077 | 0.05368 | 6.1619 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2026 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.13314 | 0 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 6.3024 | 0.091386 | 68.964 | 6.3024 | 0.091386 | 68.964 | 6.6391 | 0.096269 | 68.964 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 0.85906 | 38 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.014446 | 0.58964 | 0.024499 | 0.014446 | 0.58964 | 0.024499 | 0.015217 | 0.62114 | 0.024499 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 3.4163 | 163 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 106.3059 | 2.3449 | 45.3358 | 106.3059 | 2.3449 | 45.3358 | 111.9859 | 2.4701 | 45.3358 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 12.5079 | 404 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1750.5765 | 8.5851 | 203.909 | 1750.5765 | 8.5851 | 203.909 | 1844.1122 | 9.0438 | 203.909 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 10.6068 | 689 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 537.4279 | 7.2802 | 73.8203 | 537.4279 | 7.2802 | 73.8203 | 566.1434 | 7.6692 | 73.8203 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 31.2755 | 3380 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 765.8108 | 21.4667 | 35.6744 | 765.8108 | 21.4667 | 35.6744 | 806.7292 | 22.6137 | 35.6744 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 12.3091 | 638 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 640.8684 | 8.4486 | 75.8547 | 640.8684 | 8.4486 | 75.8547 | 675.1109 | 8.9001 | 75.8547 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2026 | 188 | 188-11F | Tier-2 | Tier-2---7 | 3--5 | 1.2193 | 0 | 100% | 2209.344 | 99.86% | 0% | 0.1429% | 109.2062 | 0 | 0 | 109.2062 | 0 | 104.1753 | 0.83689 | 124.4786 | 104.1753 | 0.83689 | 124.4786 | 109.7416 | 0.88161 | 124.4786 | 4.943% | 0.019333 | 0.018376 | 114277.2032 | 24326.824 | 78.3726 | 89872.0066 | 114285.7081 | 0 | 0 | 114285.7081 | 0.003601%
2026 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 0.29224 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.80647 | 0.20058 | 4.0207 | 0.80647 | 0.20058 | 4.0207 | 0.84957 | 0.2113 | 4.0207 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2026 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 0.3025 | 0 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 125.6678 | 0.20763 | 605.2556 | 125.6678 | 0.20763 | 605.2556 | 132.3824 | 0.21872 | 605.2556 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 6.4721 | 550 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 200.3313 | 4.4423 | 45.0965 | 200.3313 | 4.4423 | 45.0965 | 211.0352 | 4.6796 | 45.0965 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 2.8459 | 44 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 12.3641 | 1.9533 | 6.3298 | 12.3641 | 1.9533 | 6.3298 | 13.0247 | 2.0577 | 6.3298 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 6.8671 | 1644 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 76.8984 | 4.7134 | 16.315 | 76.8984 | 4.7134 | 16.315 | 81.0071 | 4.9652 | 16.315 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2026 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.085985 | 0 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.3373 | 0.059018 | 56.5474 | 3.3373 | 0.059018 | 56.5474 | 3.5156 | 0.062171 | 56.5474 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 2.8273 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 5.2339 | 1.9406 | 2.6971 | 5.2339 | 1.9406 | 2.6971 | 5.5136 | 2.0443 | 2.6971 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 1.6392 | 113 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.8455 | 1.1251 | 4.3068 | 4.8455 | 1.1251 | 4.3068 | 5.1044 | 1.1852 | 4.3068 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 6.7626 | 34 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 139.1767 | 4.6416 | 29.9845 | 139.1767 | 4.6416 | 29.9845 | 146.6131 | 4.8896 | 29.9845 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 29.745 | 3357 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 239.6048 | 20.4162 | 11.736 | 239.6048 | 20.4162 | 11.736 | 252.4072 | 21.507 | 11.736 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 3.6661 | 221 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 237.4956 | 2.5163 | 94.3826 | 237.4956 | 2.5163 | 94.3826 | 250.1853 | 2.6508 | 94.3826 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 5.2246 | 108 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 47.6389 | 3.586 | 13.2846 | 47.6389 | 3.586 | 13.2846 | 50.1843 | 3.7776 | 13.2846 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 11.5796 | 1397 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 231.9683 | 7.9479 | 29.1861 | 231.9683 | 7.9479 | 29.1861 | 244.3627 | 8.3726 | 29.1861 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 1.3334 | 164 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 304.239 | 0.91518 | 332.4376 | 304.239 | 0.91518 | 332.4376 | 320.4949 | 0.96408 | 332.4376 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 2.7707 | 131 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 73.856 | 1.9017 | 38.8368 | 73.856 | 1.9017 | 38.8368 | 77.8022 | 2.0033 | 38.8368 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2026 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.14849 | 7 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 6.3167 | 0.10192 | 61.9791 | 6.3167 | 0.10192 | 61.9791 | 6.6542 | 0.10736 | 61.9791 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 8.7312 | 1001 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 136.9236 | 5.9929 | 22.8478 | 136.9236 | 5.9929 | 22.8478 | 144.2396 | 6.3131 | 22.8478 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 3.232 | 330 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 175.0725 | 2.2183 | 78.9208 | 175.0725 | 2.2183 | 78.9208 | 184.4269 | 2.3369 | 78.9208 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2026 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.13579 | 2 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 3.0016 | 0.093206 | 32.2035 | 3.0016 | 0.093206 | 32.2035 | 3.1619 | 0.098186 | 32.2035 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.038118 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1705 | 0.026163 | 44.7399 | 1.1705 | 0.026163 | 44.7399 | 1.2331 | 0.027561 | 44.7399 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 17.8309 | 1143 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 120.5219 | 12.2386 | 9.8476 | 120.5219 | 12.2386 | 9.8476 | 126.9615 | 12.8926 | 9.8476 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 1.6328 | 9 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 11.4466 | 1.1207 | 10.2138 | 11.4466 | 1.1207 | 10.2138 | 12.0582 | 1.1806 | 10.2138 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.43141 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 5.4171 | 0.29611 | 18.2942 | 5.4171 | 0.29611 | 18.2942 | 5.7065 | 0.31193 | 18.2942 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.052462 | 10 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.3625 | 0.036008 | 93.3816 | 3.3625 | 0.036008 | 93.3816 | 3.5422 | 0.037932 | 93.3816 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2026 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 0.41062 | 16 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.097401 | 0.28184 | 0.34559 | 0.097401 | 0.28184 | 0.34559 | 0.10261 | 0.2969 | 0.34559 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 7.3674 | 675 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 188.5406 | 5.0568 | 37.2847 | 188.5406 | 5.0568 | 37.2847 | 198.6146 | 5.327 | 37.2847 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.99152 | 143 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 83.4003 | 0.68055 | 122.5483 | 83.4003 | 0.68055 | 122.5483 | 87.8565 | 0.71691 | 122.5483 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 3.9579 | 66 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 120.3488 | 2.7166 | 44.3011 | 120.3488 | 2.7166 | 44.3011 | 126.7793 | 2.8618 | 44.3011 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 8.6068 | 696 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 117.2051 | 5.9075 | 19.8402 | 117.2051 | 5.9075 | 19.8402 | 123.4676 | 6.2231 | 19.8402 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 4.5924 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 450.8352 | 3.1521 | 143.0277 | 450.8352 | 3.1521 | 143.0277 | 474.924 | 3.3205 | 143.0277 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2026 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 0.49168 | 169 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 2.0022 | 0.33747 | 5.933 | 2.0022 | 0.33747 | 5.933 | 2.1092 | 0.35551 | 5.933 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2026 | 214 | CB 214 | Tier-3 | Tier-3---20 | 1--5 | 0.040909 | 0 | 100% | 59.1996 | 99.88% | 0% | 0.1188% | 2.9269 | 0 | 0 | 2.9269 | 0 | 2.7921 | 0.028079 | 99.4367 | 2.7921 | 0.028079 | 99.4367 | 2.9412 | 0.029579 | 99.4367 | 4.944% | 0.0002016 | 0.00019162 | 293649.0501 | 47091.7983 | 966.5627 | 245590.6891 | 293667.224 | 0 | 0 | 293667.224 | 9.652e-05%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.91593 | 107 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 101.0059 | 0.62867 | 160.6657 | 101.0059 | 0.62867 | 160.6657 | 106.4028 | 0.66226 | 160.6657 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2026 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.036174 | 0 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.1885 | 0.024829 | 47.8669 | 1.1885 | 0.024829 | 47.8669 | 1.252 | 0.026155 | 47.8669 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 11.2661 | 800 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 713.7946 | 7.7327 | 92.308 | 713.7946 | 7.7327 | 92.308 | 751.9337 | 8.1459 | 92.308 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 4.9145 | 192 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 229.1341 | 3.3732 | 67.9278 | 229.1341 | 3.3732 | 67.9278 | 241.3771 | 3.5534 | 67.9278 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2026 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 1.0576 | 36 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 6.5841 | 0.72589 | 9.0703 | 6.5841 | 0.72589 | 9.0703 | 6.9359 | 0.76468 | 9.0703 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2026 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.034091 | 0 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.2556 | 0.023399 | 53.6602 | 1.2556 | 0.023399 | 53.6602 | 1.3227 | 0.024649 | 53.6602 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 7.2415 | 169 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 100.0176 | 4.9704 | 20.1229 | 100.0176 | 4.9704 | 20.1229 | 105.3617 | 5.2359 | 20.1229 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 5.9928 | 403 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 251.9816 | 4.1133 | 61.2603 | 251.9816 | 4.1133 | 61.2603 | 265.4453 | 4.3331 | 61.2603 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 8.9743 | 875 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 526.8313 | 6.1597 | 85.5289 | 526.8313 | 6.1597 | 85.5289 | 554.9807 | 6.4888 | 85.5289 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2026 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.026705 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.4032 | 0.01833 | 76.5562 | 1.4032 | 0.01833 | 76.5562 | 1.4782 | 0.019309 | 76.5562 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 1.221 | 60 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 104.5514 | 0.83808 | 124.7517 | 104.5514 | 0.83808 | 124.7517 | 110.1378 | 0.88286 | 124.7517 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2026 | 401 | 401-684R | Tier-2 | Tier-2---21 | 4--1 | 0.051326 | 0 | 100% | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049319 | 0 | 0 | 0.049319 | 0 | 0.047047 | 0.035229 | 1.3355 | 0.047047 | 0.035229 | 1.3355 | 0.049561 | 0.037111 | 1.3355 | 3.09% | 0.030395 | 0.028891 | 52.5129 | 8.9983 | 14.8334 | 28.6812 | 53.5406 | 0 | 0 | 53.5406 | 1.626e-06%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 2.1386 | 171 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 50.9272 | 1.4679 | 34.6947 | 50.9272 | 1.4679 | 34.6947 | 53.6483 | 1.5463 | 34.6947 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2026 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.057008 | 0 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.56685 | 0.039129 | 14.4868 | 0.56685 | 0.039129 | 14.4868 | 0.59714 | 0.041219 | 14.4868 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 5.5421 | 257 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 54.8903 | 3.8039 | 14.4299 | 54.8903 | 3.8039 | 14.4299 | 57.8231 | 4.0072 | 14.4299 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2026 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.043939 | 0 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.50996 | 0.030159 | 16.9092 | 0.50996 | 0.030159 | 16.9092 | 0.5372 | 0.03177 | 16.9092 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 3.2034 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 64.7607 | 2.1987 | 29.4541 | 64.7607 | 2.1987 | 29.4541 | 68.2209 | 2.3162 | 29.4541 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.64962 | 17 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 33.3597 | 0.44588 | 74.8174 | 33.3597 | 0.44588 | 74.8174 | 35.1422 | 0.46971 | 74.8174 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2026 | 221 | 221-1235F | Tier-3 | Tier-3---18 | 5--2 | 0.0489 | 0 | 100% | 236.1769 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.033564 | 0 | 0 | 0.033564 | 0 | 0 | 0.035357 | 0 | 0% | 0.16409 | 0.15597 | 1439.2989 | 2.105 | 1306.2711 | 130.9227 | 1514.2545 | 0 | 0 | 1514.2545 | 0%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 1.5002 | 11 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.8571 | 0.98223 | 1.8907 | 1.8571 | 0.98223 | 1.8907 | 2.0608 | 1.09 | 1.8907 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 11.503 | 607 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 506.1555 | 7.5316 | 67.204 | 506.1555 | 7.5316 | 67.204 | 561.6897 | 8.358 | 67.204 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 2.7701 | 39 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 30.6647 | 1.8137 | 16.9073 | 30.6647 | 1.8137 | 16.9073 | 34.0291 | 2.0127 | 16.9073 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 13.4184 | 1097 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1444.8081 | 8.7857 | 164.45 | 1444.8081 | 8.7857 | 164.45 | 1603.3291 | 9.7496 | 164.45 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 10.907 | 484 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 411.7972 | 7.1414 | 57.6637 | 411.7972 | 7.1414 | 57.6637 | 456.9786 | 7.9249 | 57.6637 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 6.1667 | 154 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 713.6047 | 4.0376 | 176.7378 | 713.6047 | 4.0376 | 176.7378 | 791.8998 | 4.4806 | 176.7378 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 7.1517 | 253 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 305.3339 | 4.6826 | 65.206 | 305.3339 | 4.6826 | 65.206 | 338.8344 | 5.1964 | 65.206 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 1.4833 | 110 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.0215 | 0.97119 | 12.3781 | 12.0215 | 0.97119 | 12.3781 | 13.3405 | 1.0777 | 12.3781 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 2.9682 | 235 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 312.0217 | 1.9434 | 160.5509 | 312.0217 | 1.9434 | 160.5509 | 346.256 | 2.1567 | 160.5509 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2027 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.006061 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.2707 | 0.0039685 | 68.2142 | 0.2707 | 0.0039685 | 68.2142 | 0.30041 | 0.0044039 | 68.2142 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2027 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.05303 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 0.97959 | 0.034722 | 28.2128 | 0.97959 | 0.034722 | 28.2128 | 1.0871 | 0.038531 | 28.2128 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 0.91212 | 44 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.1149 | 0.59721 | 0.19239 | 0.1149 | 0.59721 | 0.19239 | 0.1275 | 0.66274 | 0.19239 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 10.9006 | 354 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 135.6268 | 7.1372 | 19.0028 | 135.6268 | 7.1372 | 19.0028 | 150.5074 | 7.9203 | 19.0028 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 2.4656 | 133 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 34.8843 | 1.6143 | 21.609 | 34.8843 | 1.6143 | 21.609 | 38.7117 | 1.7915 | 21.609 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2027 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 3.214 | 0 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 462.3957 | 2.1044 | 219.7307 | 462.3957 | 2.1044 | 219.7307 | 513.1287 | 2.3353 | 219.7307 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 6.1051 | 1144 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 173.8523 | 3.9973 | 43.4921 | 173.8523 | 3.9973 | 43.4921 | 192.927 | 4.4359 | 43.4921 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.68239 | 53 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 62.197 | 0.44679 | 139.2073 | 62.197 | 0.44679 | 139.2073 | 69.0211 | 0.49582 | 139.2073 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 14.6369 | 996 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1206.3179 | 9.5835 | 125.874 | 1206.3179 | 9.5835 | 125.874 | 1338.6723 | 10.635 | 125.874 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 19.7983 | 971 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 195.7136 | 12.963 | 15.0979 | 195.7136 | 12.963 | 15.0979 | 217.1869 | 14.3852 | 15.0979 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 11.9253 | 973 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 250.5037 | 7.8082 | 32.0823 | 250.5037 | 7.8082 | 32.0823 | 277.9884 | 8.6648 | 32.0823 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 33.1318 | 3231 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 144.3433 | 21.6931 | 6.6539 | 144.3433 | 21.6931 | 6.6539 | 160.1803 | 24.0733 | 6.6539 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 16.5267 | 1132 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 165.5538 | 10.8209 | 15.2995 | 165.5538 | 10.8209 | 15.2995 | 183.718 | 12.0081 | 15.2995 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2027 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 0.5464 | 0 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 31.033 | 0.35776 | 86.7434 | 31.033 | 0.35776 | 86.7434 | 34.4379 | 0.39701 | 86.7434 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 0.4381 | 32 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.34714 | 0.28685 | 1.2102 | 0.34714 | 0.28685 | 1.2102 | 0.38522 | 0.31832 | 1.2102 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 11.0409 | 793 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 387.1481 | 7.229 | 53.5546 | 387.1481 | 7.229 | 53.5546 | 429.6251 | 8.0222 | 53.5546 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 27.7167 | 985 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 229.3595 | 18.1476 | 12.6386 | 229.3595 | 18.1476 | 12.6386 | 254.5243 | 20.1387 | 12.6386 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 4.0256 | 262 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16842 | 2.6358 | 0.063899 | 0.16842 | 2.6358 | 0.063899 | 0.1869 | 2.925 | 0.063899 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 5.4265 | 741 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 523.5501 | 3.553 | 147.3539 | 523.5501 | 3.553 | 147.3539 | 580.9928 | 3.9428 | 147.3539 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 4.9148 | 635 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 32.1257 | 3.218 | 9.9832 | 32.1257 | 3.218 | 9.9832 | 35.6504 | 3.5711 | 9.9832 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2027 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 4.5371 | 0 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 89.5674 | 2.9707 | 30.1505 | 89.5674 | 2.9707 | 30.1505 | 99.3945 | 3.2966 | 30.1505 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 2.7532 | 47 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 228.9358 | 1.8027 | 126.9984 | 228.9358 | 1.8027 | 126.9984 | 254.0541 | 2.0005 | 126.9984 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 9.5078 | 558 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 550.9097 | 6.2252 | 88.4963 | 550.9097 | 6.2252 | 88.4963 | 611.3542 | 6.9082 | 88.4963 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2027 | 595 | 595-1454F | Tier-2 | Tier-2---15 | 3--4 | 0.5388 | 0 | 100% | 124.9246 | 83.27% | 16% | 0.7306% | 5.1495 | 0 | 0 | 5.1495 | 0 | 4.6859 | 0.35278 | 13.2829 | 4.6859 | 0.35278 | 13.2829 | 5.2001 | 0.39149 | 13.2829 | 4.122% | 0.018776 | 0.017847 | 6653.3471 | 1471.8841 | 978.4778 | 4202.9852 | 6711.3017 | 0 | 0 | 6711.3017 | 0.0001698%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 10.1674 | 900 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 249.9969 | 6.6571 | 37.5533 | 249.9969 | 6.6571 | 37.5533 | 277.426 | 7.3875 | 37.5533 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 16.5478 | 1001 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 274.3211 | 10.8347 | 25.3188 | 274.3211 | 10.8347 | 25.3188 | 304.419 | 12.0234 | 25.3188 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 10.9521 | 913 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 675.9035 | 7.1709 | 94.2565 | 675.9035 | 7.1709 | 94.2565 | 750.0621 | 7.9577 | 94.2565 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2027 | 834 | 834-887AE | Tier-2 | Tier-2---17 | 2--4 | 0.2229 | 0 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 3.435 | 0 | 0 | 3.435 | 0 | 3.1258 | 0.14594 | 21.4175 | 3.1258 | 0.14594 | 21.4175 | 3.4687 | 0.16196 | 21.4175 | 4.883% | 0.0050886 | 0.0048367 | 13824.3748 | 4928.7906 | 56.7151 | 8838.8691 | 13834.1342 | 0 | 0 | 13834.1342 | 0.0001133%
2027 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 5.0727 | 200 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 28.6814 | 3.3214 | 8.6354 | 28.6814 | 3.3214 | 8.6354 | 31.8282 | 3.6858 | 8.6354 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 18.3176 | 1095 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 475.0478 | 11.9935 | 39.6088 | 475.0478 | 11.9935 | 39.6088 | 527.1689 | 13.3094 | 39.6088 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 9.4852 | 908 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 525.3163 | 6.2105 | 84.5854 | 525.3163 | 6.2105 | 84.5854 | 582.9527 | 6.8919 | 84.5854 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 1.2773 | 46 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 25.6219 | 0.8363 | 30.6373 | 25.6219 | 0.8363 | 30.6373 | 28.4331 | 0.92805 | 30.6373 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 5.1553 | 245 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 79.6362 | 3.3755 | 23.5927 | 79.6362 | 3.3755 | 23.5927 | 88.3736 | 3.7458 | 23.5927 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 4.2257 | 150 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 83.8042 | 2.7668 | 30.2891 | 83.8042 | 2.7668 | 30.2891 | 92.999 | 3.0704 | 30.2891 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 18.9327 | 1235 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 916.1722 | 12.3963 | 73.9072 | 916.1722 | 12.3963 | 73.9072 | 1016.6925 | 13.7563 | 73.9072 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 6.4307 | 308 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 242.1556 | 4.2105 | 57.5119 | 242.1556 | 4.2105 | 57.5119 | 268.7244 | 4.6725 | 57.5119 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 3.8006 | 169 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 359.1166 | 2.4884 | 144.3148 | 359.1166 | 2.4884 | 144.3148 | 398.5181 | 2.7614 | 144.3148 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 7.0653 | 484 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 606.1886 | 4.626 | 131.0383 | 606.1886 | 4.626 | 131.0383 | 672.6982 | 5.1336 | 131.0383 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 6.825 | 1960 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 21.2363 | 4.4687 | 4.7522 | 21.2363 | 4.4687 | 4.7522 | 23.5663 | 4.959 | 4.7522 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2027 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.56254 | 0 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.5825 | 0.36833 | 15.1564 | 5.5825 | 0.36833 | 15.1564 | 6.195 | 0.40874 | 15.1564 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 2.4665 | 104 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 268.9826 | 1.6149 | 166.5592 | 268.9826 | 1.6149 | 166.5592 | 298.4947 | 1.7921 | 166.5592 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 5.4023 | 504 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 48.5092 | 3.5371 | 13.7142 | 48.5092 | 3.5371 | 13.7142 | 53.8315 | 3.9252 | 13.7142 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 12.4913 | 384 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 74.7465 | 8.1787 | 9.1392 | 74.7465 | 8.1787 | 9.1392 | 82.9475 | 9.0761 | 9.1392 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 6.96 | 531 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 43.3085 | 4.5571 | 9.5035 | 43.3085 | 4.5571 | 9.5035 | 48.0602 | 5.0571 | 9.5035 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 6.5853 | 30 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 58.3792 | 4.3117 | 13.5396 | 58.3792 | 4.3117 | 13.5396 | 64.7844 | 4.7848 | 13.5396 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3.0366 | 18 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 50.9048 | 1.9882 | 25.6036 | 50.9048 | 1.9882 | 25.6036 | 56.49 | 2.2063 | 25.6036 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.45755 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 60.3628 | 0.29958 | 201.4889 | 60.3628 | 0.29958 | 201.4889 | 66.9857 | 0.33245 | 201.4889 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2027 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 2.2489 | 0 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 22.0224 | 1.4725 | 14.9561 | 22.0224 | 1.4725 | 14.9561 | 24.4386 | 1.634 | 14.9561 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 6.4636 | 102 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 366.9683 | 4.2321 | 86.711 | 366.9683 | 4.2321 | 86.711 | 407.2312 | 4.6964 | 86.711 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 10.8632 | 1047 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 456.006 | 7.1127 | 64.1113 | 456.006 | 7.1127 | 64.1113 | 506.0379 | 7.8931 | 64.1113 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 2.4735 | 109 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 195.062 | 1.6195 | 120.4425 | 195.062 | 1.6195 | 120.4425 | 216.4638 | 1.7972 | 120.4425 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 19.4561 | 1637 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 124.6006 | 12.7389 | 9.7811 | 124.6006 | 12.7389 | 9.7811 | 138.2715 | 14.1366 | 9.7811 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 5.3305 | 265 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 99.8502 | 3.4902 | 28.6091 | 99.8502 | 3.4902 | 28.6091 | 110.8055 | 3.8731 | 28.6091 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 2.3455 | 217 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 194.2367 | 1.5357 | 126.4793 | 194.2367 | 1.5357 | 126.4793 | 215.5479 | 1.7042 | 126.4793 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 2.4583 | 130 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 285.8939 | 1.6096 | 177.6183 | 285.8939 | 1.6096 | 177.6183 | 317.2615 | 1.7862 | 177.6183 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2027 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.038636 | 0 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.74762 | 0.025297 | 29.5536 | 0.74762 | 0.025297 | 29.5536 | 0.82964 | 0.028073 | 29.5536 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 13.767 | 1095 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 574.3981 | 9.014 | 63.7229 | 574.3981 | 9.014 | 63.7229 | 637.4198 | 10.003 | 63.7229 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 3.6616 | 66 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.4291 | 2.3974 | 4.7672 | 11.4291 | 2.3974 | 4.7672 | 12.683 | 2.6605 | 4.7672 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 12.7815 | 1809 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1209.3579 | 8.3687 | 144.5095 | 1209.3579 | 8.3687 | 144.5095 | 1342.0458 | 9.2869 | 144.5095 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 13.6103 | 587 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 110.0696 | 8.9114 | 12.3516 | 110.0696 | 8.9114 | 12.3516 | 122.1462 | 9.8891 | 12.3516 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.057008 | 0 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.647 | 0.037326 | 97.7076 | 3.647 | 0.037326 | 97.7076 | 4.0472 | 0.041421 | 97.7076 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2027 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 0.94167 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.82784 | 0.61656 | 1.3427 | 0.82784 | 0.61656 | 1.3427 | 0.91867 | 0.68421 | 1.3427 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2027 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 5.9186 | 504 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.84502 | 3.8752 | 0.21806 | 0.84502 | 3.8752 | 0.21806 | 0.93773 | 4.3004 | 0.21806 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 6.9741 | 633 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 845.436 | 4.5663 | 185.1477 | 845.436 | 4.5663 | 185.1477 | 938.1953 | 5.0673 | 185.1477 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 0.3653 | 62 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.55265 | 0.23918 | 2.3106 | 0.55265 | 0.23918 | 2.3106 | 0.61328 | 0.26542 | 2.3106 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.93788 | 186 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.0061 | 0.61408 | 4.8952 | 3.0061 | 0.61408 | 4.8952 | 3.3359 | 0.68145 | 4.8952 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 1.7432 | 329 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 23.0365 | 1.1414 | 20.1834 | 23.0365 | 1.1414 | 20.1834 | 25.5641 | 1.2666 | 20.1834 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 1.4693 | 14 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 91.1498 | 0.96202 | 94.7483 | 91.1498 | 0.96202 | 94.7483 | 101.1506 | 1.0676 | 94.7483 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.3089 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.2134 | 0.20225 | 10.9436 | 2.2134 | 0.20225 | 10.9436 | 2.4562 | 0.22445 | 10.9436 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 2.6153 | 70 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.2984 | 1.7124 | 1.3422 | 2.2984 | 1.7124 | 1.3422 | 2.5506 | 1.9003 | 1.3422 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.62576 | 68 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 9.5688 | 0.40972 | 23.3546 | 9.5688 | 0.40972 | 23.3546 | 10.6186 | 0.45467 | 23.3546 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 6.2526 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 184.9104 | 4.0939 | 45.167 | 184.9104 | 4.0939 | 45.167 | 205.1983 | 4.5431 | 45.167 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2027 | 308 | 308-485AE | Tier-2 | Tier-2---15 | 4--3 | 0.7398 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.217 | 0 | 0 | 0.217 | 0 | 0.19746 | 0.48439 | 0.40766 | 0.19746 | 0.48439 | 0.40766 | 0.21913 | 0.53753 | 0.40766 | 0.1374% | 0.034738 | 0.033018 | 4547.6785 | 25.2626 | 4047.4864 | 474.9295 | 4777.9399 | 0 | 0 | 4777.9399 | 7.156e-06%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 2.4644 | 81 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 21.1763 | 1.6136 | 13.1238 | 21.1763 | 1.6136 | 13.1238 | 23.4997 | 1.7906 | 13.1238 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 8.4758 | 325 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 79.9189 | 5.5495 | 14.401 | 79.9189 | 5.5495 | 14.401 | 88.6875 | 6.1584 | 14.401 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 10.6674 | 415 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 892.989 | 6.9845 | 127.8529 | 892.989 | 6.9845 | 127.8529 | 990.9657 | 7.7508 | 127.8529 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2027 | 94 | 94-24F | Tier-2 | Tier-2---18 | 3--3 | 4.1867 | 0 | 100% | 46.367 | 91.68% | 0% | 8.321% | 2.1042 | 0 | 0 | 2.1042 | 0 | 1.9148 | 2.7413 | 0.69851 | 1.9148 | 2.7413 | 0.69851 | 2.1249 | 3.042 | 0.69851 | 4.538% | 0.020922 | 0.019886 | 2216.1834 | 511.0324 | 89.3586 | 1615.7924 | 2225.7865 | 0 | 0 | 2225.7865 | 6.939e-05%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 4.8975 | 159 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 63.4742 | 3.2067 | 19.7945 | 63.4742 | 3.2067 | 19.7945 | 70.4384 | 3.5585 | 19.7945 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 2.7176 | 182 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.2749 | 1.7794 | 4.0885 | 7.2749 | 1.7794 | 4.0885 | 8.0731 | 1.9746 | 4.0885 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2027 | 454 | 454-49F | Tier-2 | Tier-2---13 | 4--3 | 0.4782 | 0 | 100% | 292.9743 | 76.06% | 23.59% | 0.3558% | 11.0299 | 0 | 0 | 11.0299 | 0 | 10.037 | 0.3131 | 32.0567 | 10.037 | 0.3131 | 32.0567 | 11.1383 | 0.34746 | 32.0567 | 3.765% | 0.077203 | 0.073382 | 3794.8464 | 847.9473 | 816.929 | 2129.9701 | 3842.1656 | 0 | 0 | 3842.1656 | 0.0003637%
2027 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.01875 | 0 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.66976 | 0.012277 | 54.5554 | 0.66976 | 0.012277 | 54.5554 | 0.74324 | 0.013624 | 54.5554 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2027 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 0.095455 | 52 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.7092 | 0.062499 | 27.3479 | 1.7092 | 0.062499 | 27.3479 | 1.8968 | 0.069357 | 27.3479 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 7.6085 | 759 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 131.5802 | 4.9817 | 26.4127 | 131.5802 | 4.9817 | 26.4127 | 146.0169 | 5.5283 | 26.4127 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2027 | 205 | 205-1550 | Tier-2 | Tier-2---15 | 2--4 | 0.97858 | 11 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 6.0476 | 0 | 0 | 6.0476 | 0 | 5.5032 | 0.64073 | 8.589 | 5.5032 | 0.64073 | 8.589 | 6.107 | 0.71103 | 8.589 | 4.877% | 0.008789 | 0.0083539 | 14109.2738 | 2221.4405 | 309.7116 | 11578.1217 | 14120.1329 | 0 | 0 | 14120.1329 | 0.0001994%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.47178 | 4 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 5.1466 | 0.3089 | 16.661 | 5.1466 | 0.3089 | 16.661 | 5.7112 | 0.34279 | 16.661 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 6.7553 | 1534 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 129.1825 | 4.4231 | 29.2065 | 129.1825 | 4.4231 | 29.2065 | 143.3561 | 4.9084 | 29.2065 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.10398 | 8 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.4327 | 0.068079 | 167.9317 | 11.4327 | 0.068079 | 167.9317 | 12.687 | 0.075549 | 167.9317 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 12.5093 | 734 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 389.967 | 8.1905 | 47.6122 | 389.967 | 8.1905 | 47.6122 | 432.7533 | 9.0891 | 47.6122 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 6.6007 | 793 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 141.9018 | 4.3218 | 32.8336 | 141.9018 | 4.3218 | 32.8336 | 157.4709 | 4.796 | 32.8336 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2027 | 197 | 197-1150F | Tier-2 | Tier-2---15 | 3--4 | 1.3604 | 3 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 9.0248 | 0 | 0 | 9.0248 | 0 | 8.2124 | 0.89074 | 9.2198 | 8.2124 | 0.89074 | 9.2198 | 9.1135 | 0.98847 | 9.2198 | 4.917% | 0.021777 | 0.020699 | 8428.1597 | 1361.8326 | 10.8364 | 7055.4907 | 8431.076 | 0 | 0 | 8431.076 | 0.0002976%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 13.7784 | 951 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 80.9279 | 9.0215 | 8.9706 | 80.9279 | 9.0215 | 8.9706 | 89.8072 | 10.0113 | 8.9706 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 5.0748 | 149 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 175.5102 | 3.3227 | 52.8211 | 175.5102 | 3.3227 | 52.8211 | 194.7668 | 3.6873 | 52.8211 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 3.0297 | 20 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 53.1521 | 1.9837 | 26.7943 | 53.1521 | 1.9837 | 26.7943 | 58.9838 | 2.2014 | 26.7943 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 5.1365 | 315 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 113.0675 | 3.3632 | 33.6194 | 113.0675 | 3.3632 | 33.6194 | 125.473 | 3.7322 | 33.6194 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 10.0072 | 260 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 67.1805 | 6.5522 | 10.2531 | 67.1805 | 6.5522 | 10.2531 | 74.5514 | 7.2711 | 10.2531 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 3.7138 | 156 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 100.4117 | 2.4316 | 41.2937 | 100.4117 | 2.4316 | 41.2937 | 111.4286 | 2.6984 | 41.2937 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 3.1481 | 153 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 139.6922 | 2.0612 | 67.7721 | 139.6922 | 2.0612 | 67.7721 | 155.0189 | 2.2874 | 67.7721 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 4.4941 | 222 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 410.7886 | 2.9425 | 139.6036 | 410.7886 | 2.9425 | 139.6036 | 455.8594 | 3.2654 | 139.6036 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2027 | 241 | CB 241 | Tier-2 | Tier-2---11 | 5--4 | 1.5013 | 0 | 100% | 614.4843 | 5.233% | 94.45% | 0.3166% | 1.5918 | 0 | 0 | 1.5918 | 0 | 1.4485 | 0.98298 | 1.4736 | 1.4485 | 0.98298 | 1.4736 | 1.6074 | 1.0908 | 1.4736 | 0.259% | 0.096356 | 0.091586 | 6377.2296 | 31.8975 | 5684.1218 | 661.2103 | 6691.9621 | 0 | 0 | 6691.9621 | 5.249e-05%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 14.1729 | 537 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 469.0206 | 9.2797 | 50.5425 | 469.0206 | 9.2797 | 50.5425 | 520.4805 | 10.2979 | 50.5425 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2027 | 855 | 855-46AE | Tier-2 | Tier-2---15 | 1--5 | 0.25303 | 1 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 9.3224 | 0 | 0 | 9.3224 | 0 | 8.4833 | 0.16567 | 51.2053 | 8.4833 | 0.16567 | 51.2053 | 9.4141 | 0.18385 | 51.2053 | 4.944% | 0.0010888 | 0.0010349 | 173174.957 | 50966.8705 | 22.9996 | 122185.0869 | 173185.5197 | 0 | 0 | 173185.5197 | 0.0003074%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 3.6236 | 238 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.4153 | 2.3726 | 2.2824 | 5.4153 | 2.3726 | 2.2824 | 6.0094 | 2.6329 | 2.2824 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2027 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.12822 | 0 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 13.9722 | 0.083952 | 166.4305 | 13.9722 | 0.083952 | 166.4305 | 15.5052 | 0.093163 | 166.4305 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | 4--5 | 3.1426 | 3 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 65.3395 | 0 | 0 | 65.3395 | 0 | 59.4581 | 2.0576 | 28.8963 | 59.4581 | 2.0576 | 28.8963 | 65.9817 | 2.2834 | 28.8963 | 3.948% | 0.057199 | 0.054367 | 28934.4603 | 4597.4585 | 5524.6499 | 18812.3519 | 29239.4879 | 0 | 0 | 29239.4879 | 0.002155%
2027 | 1202 | 1202-9 | Tier-2 | Tier-2---17 | 2--4 | 0.7689 | 0 | 100% | 73.4421 | 96.84% | 0% | 3.16% | 3.5205 | 0 | 0 | 3.5205 | 0 | 3.2036 | 0.50344 | 6.3635 | 3.2036 | 0.50344 | 6.3635 | 3.5551 | 0.55868 | 6.3635 | 4.794% | 0.01182 | 0.011235 | 6213.48 | 1453.8319 | 498.5132 | 4261.1349 | 6223.7055 | 0 | 0 | 6223.7055 | 0.0001161%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 24.8581 | 448 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 457.7342 | 16.2759 | 28.1234 | 457.7342 | 16.2759 | 28.1234 | 507.9557 | 18.0617 | 28.1234 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2027 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 0.42306 | 23 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.47188 | 0.277 | 1.7036 | 0.47188 | 0.277 | 1.7036 | 0.52366 | 0.30739 | 1.7036 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 13.0331 | 1531 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 833.1015 | 8.5335 | 97.6275 | 833.1015 | 8.5335 | 97.6275 | 924.5075 | 9.4697 | 97.6275 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 8.4165 | 712 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 517.9939 | 5.5107 | 93.9972 | 517.9939 | 5.5107 | 93.9972 | 574.827 | 6.1154 | 93.9972 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 11.5724 | 1687 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 118.4418 | 7.577 | 15.6317 | 118.4418 | 7.577 | 15.6317 | 131.4369 | 8.4084 | 15.6317 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 16.5898 | 1991 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 700.4791 | 10.8622 | 64.4877 | 700.4791 | 10.8622 | 64.4877 | 777.3341 | 12.054 | 64.4877 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 3.9667 | 215 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 84.3793 | 2.5972 | 32.4888 | 84.3793 | 2.5972 | 32.4888 | 93.6372 | 2.8821 | 32.4888 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 4.5633 | 392 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 439.7915 | 2.9878 | 147.1955 | 439.7915 | 2.9878 | 147.1955 | 488.0444 | 3.3156 | 147.1955 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2027 | 178 | 178-982 | Tier-2 | Tier-2---21 | 1--1 | 0.68407 | 9 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0063254 | 0 | 0 | 0.0063254 | 0 | 0.005756 | 0.4479 | 0.012851 | 0.005756 | 0.4479 | 0.012851 | 0.0063875 | 0.49704 | 0.012851 | 0.6625% | 0.0033454 | 0.0031798 | 285.4035 | 0.62363 | 58.6739 | 226.106 | 298.2775 | 0 | 0 | 298.2775 | 2.086e-07%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 4.3521 | 410 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 140.9108 | 2.8495 | 49.4506 | 140.9108 | 2.8495 | 49.4506 | 156.3712 | 3.1622 | 49.4506 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2027 | 189 | 189-750 | Tier-2 | Tier-2---21 | 1--2 | 0.1718 | 0 | 100% | 1.7248 | 88.21% | 0% | 11.79% | 0.075309 | 0 | 0 | 0.075309 | 0 | 0.068531 | 0.11249 | 0.60923 | 0.068531 | 0.11249 | 0.60923 | 0.07605 | 0.12483 | 0.60923 | 4.366% | 0.001013 | 0.00096286 | 1702.705 | 2.2891 | 1507.0729 | 193.3431 | 1713.1637 | 0 | 0 | 1713.1637 | 2.483e-06%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 11.4998 | 49 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 61.4752 | 7.5295 | 8.1646 | 61.4752 | 7.5295 | 8.1646 | 68.2202 | 8.3556 | 8.1646 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 1.5879 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 112.6347 | 1.0397 | 108.3344 | 112.6347 | 1.0397 | 108.3344 | 124.9927 | 1.1538 | 108.3344 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 2.2354 | 22 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 96.3058 | 1.4637 | 65.7983 | 96.3058 | 1.4637 | 65.7983 | 106.8723 | 1.6242 | 65.7983 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2027 | 790 | CB 790 | Tier-2 | Tier-2---10 | 4--4 | 0.0892 | 0 | 100% | 864.253 | 62.67% | 37.21% | 0.1185% | 26.812 | 0 | 0 | 26.812 | 0 | 24.3986 | 0.058404 | 417.7555 | 24.3986 | 0.058404 | 417.7555 | 27.0755 | 0.064812 | 417.7555 | 3.102% | 0.092624 | 0.088039 | 9330.8076 | 1033.7577 | 3102.9179 | 5194.132 | 9512.1882 | 0 | 0 | 9512.1882 | 0.0008842%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 0.78689 | 20 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.83367 | 0.51522 | 1.6181 | 0.83367 | 0.51522 | 1.6181 | 0.92513 | 0.57174 | 1.6181 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2027 | 454 | 454-53F | Tier-2 | Tier-2---13 | 4--3 | 0.3076 | 0 | 100% | 272.5399 | 0.7301% | 99.1% | 0.1654% | 0.098502 | 0 | 0 | 0.098502 | 0 | 0.089635 | 0.2014 | 0.44506 | 0.089635 | 0.2014 | 0.44506 | 0.09947 | 0.2235 | 0.44506 | 0.03614% | 0.073094 | 0.069476 | 3728.6015 | 9.5009 | 3385.0726 | 334.0281 | 3921.3613 | 0 | 0 | 3921.3613 | 3.248e-06%
2027 | 197 | CB 197 | Tier-2 | Tier-2---21 | 1--4 | 0.097159 | 0 | 100% | 1.9198 | 98.18% | 0% | 1.817% | 0.093305 | 0 | 0 | 0.093305 | 0 | 0.084906 | 0.063615 | 1.3347 | 0.084906 | 0.063615 | 1.3347 | 0.094222 | 0.070595 | 1.3347 | 4.86% | 0.000314 | 0.00029846 | 6114.1 | 461.2612 | 3185.8611 | 2466.9777 | 6119.8844 | 0 | 0 | 6119.8844 | 3.077e-06%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 7.2309 | 81 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 235.2675 | 4.7344 | 49.693 | 235.2675 | 4.7344 | 49.693 | 261.0805 | 5.2539 | 49.693 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 7.3388 | 536 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 71.3855 | 4.8051 | 14.8562 | 71.3855 | 4.8051 | 14.8562 | 79.2178 | 5.3323 | 14.8562 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 7.806 | 484 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 750.663 | 5.111 | 146.8715 | 750.663 | 5.111 | 146.8715 | 833.024 | 5.6718 | 146.8715 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2027 | 395 | 395-33R | Tier-2 | Tier-2---11 | 4--3 | 0.2491 | 0 | 100% | 396.9757 | 0.1391% | 99.74% | 0.1245% | 0.02734 | 0 | 0 | 0.02734 | 0 | 0.024879 | 0.1631 | 0.15254 | 0.024879 | 0.1631 | 0.15254 | 0.027609 | 0.18099 | 0.15254 | 0.006887% | 0.092102 | 0.087543 | 4310.174 | 6.5289 | 3952.6979 | 350.9472 | 4534.3264 | 0 | 0 | 4534.3264 | 9.016e-07%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 5.2882 | 192 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 25.8594 | 3.4625 | 7.4685 | 25.8594 | 3.4625 | 7.4685 | 28.6967 | 3.8424 | 7.4685 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 11.8401 | 425 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 119.0101 | 7.7523 | 15.3515 | 119.0101 | 7.7523 | 15.3515 | 132.0677 | 8.6029 | 15.3515 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 14.3572 | 1385 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 217.2304 | 9.4004 | 23.1086 | 217.2304 | 9.4004 | 23.1086 | 241.0644 | 10.4318 | 23.1086 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 17.3068 | 1218 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 239.6285 | 11.3317 | 21.1468 | 239.6285 | 11.3317 | 21.1468 | 265.9199 | 12.5749 | 21.1468 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 1.8014 | 93 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.1844 | 1.1794 | 1.852 | 2.1844 | 1.1794 | 1.852 | 2.424 | 1.3088 | 1.852 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 9.8927 | 661 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 223.9657 | 6.4772 | 34.5773 | 223.9657 | 6.4772 | 34.5773 | 248.5387 | 7.1879 | 34.5773 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 4.1559 | 590 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 204.9832 | 2.7211 | 75.3311 | 204.9832 | 2.7211 | 75.3311 | 227.4734 | 3.0196 | 75.3311 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 15.3767 | 427 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 48.3556 | 10.0679 | 4.8029 | 48.3556 | 10.0679 | 4.8029 | 53.6611 | 11.1726 | 4.8029 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 18.1587 | 305 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 68.683 | 11.8894 | 5.7768 | 68.683 | 11.8894 | 5.7768 | 76.2188 | 13.1939 | 5.7768 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2027 | 770 | 770-259R | Tier-2 | Tier-2---17 | 2--3 | 1.3913 | 0 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 2.0515 | 0 | 0 | 2.0515 | 0 | 1.8669 | 0.91095 | 2.0494 | 1.8669 | 0.91095 | 2.0494 | 2.0717 | 1.0109 | 2.0494 | 4.826% | 0.010605 | 0.01008 | 4008.538 | 787.4023 | 25.9222 | 3195.2135 | 4013.7737 | 0 | 0 | 4013.7737 | 6.765e-05%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 22.0576 | 1796 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 154.9241 | 14.4423 | 10.7271 | 154.9241 | 14.4423 | 10.7271 | 171.922 | 16.0268 | 10.7271 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 8.5739 | 486 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 245.7559 | 5.6138 | 43.7774 | 245.7559 | 5.6138 | 43.7774 | 272.7197 | 6.2297 | 43.7774 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 8.1708 | 346 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 133.7423 | 5.3499 | 24.9991 | 133.7423 | 5.3499 | 24.9991 | 148.4162 | 5.9369 | 24.9991 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2027 | 504 | 504-287R | Tier-2 | Tier-2---12 | 4--4 | 0.7358 | 0 | 100% | 501.8283 | 98.94% | 0% | 1.063% | 24.5765 | 0 | 0 | 24.5765 | 0 | 22.3643 | 0.48177 | 46.4213 | 22.3643 | 0.48177 | 46.4213 | 24.818 | 0.53463 | 46.4213 | 4.897% | 0.033132 | 0.031492 | 15146.1514 | 2418.4341 | 53.5553 | 12674.162 | 15154.5352 | 0 | 0 | 15154.5352 | 0.0008104%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 1.2528 | 22 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 87.1243 | 0.8203 | 106.2102 | 87.1243 | 0.8203 | 106.2102 | 96.6834 | 0.9103 | 106.2102 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 2.4038 | 61 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 65.3245 | 1.5739 | 41.5052 | 65.3245 | 1.5739 | 41.5052 | 72.4917 | 1.7466 | 41.5052 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2027 | 968 | 968-476F | Tier-2 | Tier-2---17 | 3--3 | 1.9167 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 2.9977 | 0 | 0 | 2.9977 | 0 | 2.7279 | 1.2549 | 2.1737 | 2.7279 | 1.2549 | 2.1737 | 3.0271 | 1.3926 | 2.1737 | 4.797% | 0.015315 | 0.014557 | 4080.3921 | 1049.3579 | 36.5623 | 2994.4719 | 4086.964 | 0 | 0 | 4086.964 | 9.885e-05%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 5.9518 | 1034 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 404.9546 | 3.8969 | 103.9164 | 404.9546 | 3.8969 | 103.9164 | 449.3853 | 4.3245 | 103.9164 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 2.2803 | 79 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.1871 | 1.493 | 0.79512 | 1.1871 | 1.493 | 0.79512 | 1.3174 | 1.6568 | 0.79512 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 7.8388 | 373 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 408.4997 | 5.1325 | 79.5911 | 408.4997 | 5.1325 | 79.5911 | 453.3194 | 5.6956 | 79.5911 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 17.9011 | 1149 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 502.3679 | 11.7208 | 42.8612 | 502.3679 | 11.7208 | 42.8612 | 557.4865 | 13.0068 | 42.8612 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 11.6007 | 312 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 5.741 | 7.5956 | 0.75583 | 5.741 | 7.5956 | 0.75583 | 6.3709 | 8.429 | 0.75583 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 3.4445 | 84 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 48.3244 | 2.2553 | 21.4269 | 48.3244 | 2.2553 | 21.4269 | 53.6265 | 2.5028 | 21.4269 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2027 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | 4--1 | 0.28182 | 0 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.15233 | 0 | 0 | 0.15233 | 0 | 0.13861 | 0.18452 | 0.75121 | 0.13861 | 0.18452 | 0.75121 | 0.15382 | 0.20477 | 0.75121 | 0.8348% | 0.061771 | 0.058714 | 295.3886 | 6.838 | 193.9385 | 94.612 | 308.1774 | 0 | 0 | 308.1774 | 5.023e-06%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 6.1881 | 443 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 233.193 | 4.0517 | 57.5546 | 233.193 | 4.0517 | 57.5546 | 258.7784 | 4.4962 | 57.5546 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2027 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | 2--4 | 1.5301 | 0 | 100% | 70.6534 | 98.66% | 0% | 1.337% | 3.4506 | 0 | 0 | 3.4506 | 0 | 3.14 | 1.0018 | 3.1342 | 3.14 | 1.0018 | 3.1342 | 3.4845 | 1.1118 | 3.1342 | 4.884% | 0.0070442 | 0.0066955 | 10030.0143 | 2447.2684 | 423.376 | 7159.37 | 10036.9961 | 0 | 0 | 10036.9961 | 0.0001138%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 16.0076 | 985 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 940.331 | 10.481 | 89.7177 | 940.331 | 10.481 | 89.7177 | 1043.5019 | 11.6309 | 89.7177 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 12.6949 | 1098 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 304.1512 | 8.312 | 36.5917 | 304.1512 | 8.312 | 36.5917 | 337.522 | 9.224 | 36.5917 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 6.6053 | 250 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 174.6571 | 4.3249 | 40.3845 | 174.6571 | 4.3249 | 40.3845 | 193.82 | 4.7994 | 40.3845 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 1.1019 | 44 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 24.5074 | 0.72147 | 33.9689 | 24.5074 | 0.72147 | 33.9689 | 27.1963 | 0.80063 | 33.9689 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 4.3966 | 75 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 581.8498 | 2.8787 | 202.1247 | 581.8498 | 2.8787 | 202.1247 | 645.689 | 3.1945 | 202.1247 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2027 | 312 | 312-40F | Tier-2 | Tier-2---20 | 3--2 | 0.0492 | 0 | 100% | 9.4163 | 0.07625% | 99.1% | 0.8244% | 0.00035539 | 0 | 0 | 0.00035539 | 0 | 0.0003234 | 0.032214 | 0.010039 | 0.0003234 | 0.032214 | 0.010039 | 0.00035889 | 0.035748 | 0.010039 | 0.003774% | 0.017172 | 0.016322 | 548.3384 | 0.98367 | 493.2185 | 54.1362 | 576.8729 | 0 | 0 | 576.8729 | 1.172e-08%
2027 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 0.089364 | 9 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.8496 | 0.058511 | 31.6113 | 1.8496 | 0.058511 | 31.6113 | 2.0526 | 0.064931 | 31.6113 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 14.1159 | 1226 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 77.5518 | 9.2424 | 8.3908 | 77.5518 | 9.2424 | 8.3908 | 86.0606 | 10.2565 | 8.3908 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 1.2536 | 124 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.2411 | 0.82081 | 5.1669 | 4.2411 | 0.82081 | 5.1669 | 4.7064 | 0.91087 | 5.1669 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 2.5449 | 185 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 15.7849 | 1.6663 | 9.473 | 15.7849 | 1.6663 | 9.473 | 17.5167 | 1.8491 | 9.473 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2027 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.03428 | 0 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.1319 | 0.022445 | 50.4288 | 1.1319 | 0.022445 | 50.4288 | 1.2561 | 0.024908 | 50.4288 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2027 | 331 | CB 331 | Tier-2 | Tier-2---14 | 2--5 | 2.8949 | 2 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 12.8498 | 0 | 0 | 12.8498 | 0 | 11.6932 | 1.8954 | 6.1691 | 11.6932 | 1.8954 | 6.1691 | 12.9761 | 2.1034 | 6.1691 | 4.919% | 0.010352 | 0.0098396 | 25232.8512 | 3536.4388 | 3219.2744 | 18477.138 | 25240.9927 | 0 | 0 | 25240.9927 | 0.0004237%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 16.7242 | 1029 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1379.245 | 10.9502 | 125.9558 | 1379.245 | 10.9502 | 125.9558 | 1530.5725 | 12.1517 | 125.9558 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 2.574 | 82 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 32.8858 | 1.6853 | 19.5129 | 32.8858 | 1.6853 | 19.5129 | 36.4939 | 1.8702 | 19.5129 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 6.3644 | 329 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 266.0239 | 4.1671 | 63.8395 | 266.0239 | 4.1671 | 63.8395 | 295.2114 | 4.6243 | 63.8395 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 2.267 | 47 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 40.8246 | 1.4844 | 27.5033 | 40.8246 | 1.4844 | 27.5033 | 45.3038 | 1.6472 | 27.5033 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 5.5445 | 309 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 56.0299 | 3.6303 | 15.434 | 56.0299 | 3.6303 | 15.434 | 62.1774 | 4.0286 | 15.434 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 9.1409 | 791 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 152.8245 | 5.985 | 25.5344 | 152.8245 | 5.985 | 25.5344 | 169.592 | 6.6417 | 25.5344 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 9.5874 | 678 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 43.4702 | 6.2773 | 6.9249 | 43.4702 | 6.2773 | 6.9249 | 48.2397 | 6.9661 | 6.9249 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2027 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.054356 | 0 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.34564 | 0.03559 | 9.7118 | 0.34564 | 0.03559 | 9.7118 | 0.38356 | 0.039495 | 9.7118 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 0.74429 | 33 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 12.3234 | 0.48733 | 25.2876 | 12.3234 | 0.48733 | 25.2876 | 13.6755 | 0.5408 | 25.2876 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2027 | 196 | CB 196 | Tier-2 | Tier-2---15 | 3--4 | 0.29696 | 0 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.19032 | 0.19443 | 0.97884 | 0.19032 | 0.19443 | 0.97884 | 0.2112 | 0.21577 | 0.97884 | 0.1555% | 0.019464 | 0.018501 | 6908.5051 | 30.9312 | 5935.5679 | 942.006 | 7256.9805 | 0 | 0 | 7256.9805 | 6.897e-06%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 10.0377 | 551 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 388.0424 | 6.5722 | 59.043 | 388.0424 | 6.5722 | 59.043 | 430.6175 | 7.2933 | 59.043 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2027 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 0.043939 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.33709 | 0.028769 | 11.7171 | 0.33709 | 0.028769 | 11.7171 | 0.37408 | 0.031926 | 11.7171 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 4.4118 | 230 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.608 | 2.8886 | 0.55666 | 1.608 | 2.8886 | 0.55666 | 1.7844 | 3.2056 | 0.55666 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.4697 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 4.8571 | 0.30754 | 15.7937 | 4.8571 | 0.30754 | 15.7937 | 5.39 | 0.34128 | 15.7937 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | 3--4 | 0.75338 | 26 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 2.2455 | 0 | 0 | 2.2455 | 0 | 2.0434 | 0.49328 | 4.1425 | 2.0434 | 0.49328 | 4.1425 | 2.2676 | 0.5474 | 4.1425 | 0.8058% | 0.018935 | 0.017998 | 14715.9264 | 335.1634 | 11691.6167 | 2689.1463 | 15357.5365 | 0 | 0 | 15357.5365 | 7.405e-05%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 10.606 | 600 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 264.7098 | 6.9443 | 38.1188 | 264.7098 | 6.9443 | 38.1188 | 293.7531 | 7.7063 | 38.1188 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 2.911 | 8 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 1.9561 | 1.906 | 1.0263 | 1.9561 | 1.906 | 1.0263 | 2.1707 | 2.1151 | 1.0263 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 1.375 | 58 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 123.3195 | 0.90026 | 136.9825 | 123.3195 | 0.90026 | 136.9825 | 136.8498 | 0.99903 | 136.9825 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 3.7273 | 352 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 352.6402 | 2.4404 | 144.4993 | 352.6402 | 2.4404 | 144.4993 | 391.3311 | 2.7082 | 144.4993 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 17.3898 | 266 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 21.2889 | 11.386 | 1.8697 | 21.2889 | 11.386 | 1.8697 | 23.6247 | 12.6353 | 1.8697 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 2.6099 | 93 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 87.1533 | 1.7088 | 51.0021 | 87.1533 | 1.7088 | 51.0021 | 96.7155 | 1.8963 | 51.0021 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 22.2475 | 1846 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 461.194 | 14.5666 | 31.6611 | 461.194 | 14.5666 | 31.6611 | 511.7951 | 16.1648 | 31.6611 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 0.60374 | 80 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 12.9796 | 0.3953 | 32.8349 | 12.9796 | 0.3953 | 32.8349 | 14.4037 | 0.43867 | 32.8349 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 5.1074 | 161 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 513.522 | 3.3441 | 153.5625 | 513.522 | 3.3441 | 153.5625 | 569.8644 | 3.711 | 153.5625 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 15.5693 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 162.0475 | 10.194 | 15.8963 | 162.0475 | 10.194 | 15.8963 | 179.8269 | 11.3125 | 15.8963 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 5.0178 | 495 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 264.2682 | 3.2854 | 80.4371 | 264.2682 | 3.2854 | 80.4371 | 293.2631 | 3.6459 | 80.4371 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 10.1766 | 1320 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 698.3032 | 6.6631 | 104.8011 | 698.3032 | 6.6631 | 104.8011 | 774.9194 | 7.3942 | 104.8011 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2027 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 0.005871 | 7 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.077882 | 0.0038441 | 20.2603 | 0.077882 | 0.0038441 | 20.2603 | 0.086427 | 0.0042658 | 20.2603 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 7.3438 | 786 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 308.3982 | 4.8084 | 64.1379 | 308.3982 | 4.8084 | 64.1379 | 342.2349 | 5.3359 | 64.1379 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 1.0739 | 192 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 9.159 | 0.70313 | 13.026 | 9.159 | 0.70313 | 13.026 | 10.1639 | 0.78027 | 13.026 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 2.3892 | 150 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 193.5126 | 1.5644 | 123.7014 | 193.5126 | 1.5644 | 123.7014 | 214.7444 | 1.736 | 123.7014 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 11.1993 | 175 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 67.4256 | 7.3327 | 9.1951 | 67.4256 | 7.3327 | 9.1951 | 74.8234 | 8.1373 | 9.1951 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 12.6807 | 874 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 155.9371 | 8.3027 | 18.7814 | 155.9371 | 8.3027 | 18.7814 | 173.0461 | 9.2137 | 18.7814 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2027 | 92 | 92-619F | Tier-2 | Tier-2---14 | 3--4 | 1.454 | 0 | 100% | 202.8689 | 46.88% | 52.08% | 1.034% | 4.708 | 0 | 0 | 4.708 | 0 | 4.2842 | 0.95201 | 4.5002 | 4.2842 | 0.95201 | 4.5002 | 4.7543 | 1.0565 | 4.5002 | 2.321% | 0.015617 | 0.014844 | 12990.5937 | 1279.3739 | 6200.2786 | 5510.9412 | 13349.9397 | 0 | 0 | 13349.9397 | 0.0001553%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 4.1122 | 503 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 371.1005 | 2.6924 | 137.8304 | 371.1005 | 2.6924 | 137.8304 | 411.8168 | 2.9879 | 137.8304 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 12.1511 | 530 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 167.0067 | 7.956 | 20.9913 | 167.0067 | 7.956 | 20.9913 | 185.3303 | 8.8289 | 20.9913 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 1.6021 | 37 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 27.2363 | 1.049 | 25.9649 | 27.2363 | 1.049 | 25.9649 | 30.2246 | 1.1641 | 25.9649 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 3.7494 | 966 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 17.6405 | 2.4549 | 7.1857 | 17.6405 | 2.4549 | 7.1857 | 19.576 | 2.7243 | 7.1857 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 6.1581 | 318 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 152.4366 | 4.032 | 37.8063 | 152.4366 | 4.032 | 37.8063 | 169.1616 | 4.4744 | 37.8063 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 6.9867 | 120 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 64.8175 | 4.5746 | 14.1691 | 64.8175 | 4.5746 | 14.1691 | 71.9292 | 5.0765 | 14.1691 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 14.6288 | 358 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 38.5732 | 9.5782 | 4.0272 | 38.5732 | 9.5782 | 4.0272 | 42.8054 | 10.6291 | 4.0272 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 8.4832 | 264 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 226.9901 | 5.5544 | 40.867 | 226.9901 | 5.5544 | 40.867 | 251.895 | 6.1638 | 40.867 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 8.4771 | 489 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 627.3269 | 5.5504 | 113.0234 | 627.3269 | 5.5504 | 113.0234 | 696.1557 | 6.1594 | 113.0234 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 15.7168 | 1458 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1130.6716 | 10.2906 | 109.874 | 1130.6716 | 10.2906 | 109.874 | 1254.7263 | 11.4197 | 109.874 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 2.7396 | 153 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 62.4087 | 1.7938 | 34.7919 | 62.4087 | 1.7938 | 34.7919 | 69.256 | 1.9906 | 34.7919 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2027 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.011364 | 0 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.031188 | 0.0074406 | 4.1915 | 0.031188 | 0.0074406 | 4.1915 | 0.034609 | 0.008257 | 4.1915 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2027 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.19716 | 0 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.5118 | 0.12909 | 27.2044 | 3.5118 | 0.12909 | 27.2044 | 3.8971 | 0.14325 | 27.2044 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 7.6936 | 496 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 90.5939 | 5.0374 | 17.9843 | 90.5939 | 5.0374 | 17.9843 | 100.5337 | 5.5901 | 17.9843 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 5.4881 | 1448 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 66.4558 | 3.5933 | 18.4942 | 66.4558 | 3.5933 | 18.4942 | 73.7472 | 3.9876 | 18.4942 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 24.1038 | 1342 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 705.149 | 15.782 | 44.6805 | 705.149 | 15.782 | 44.6805 | 782.5163 | 17.5136 | 44.6805 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 2.3543 | 108 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.2129 | 1.5415 | 9.2201 | 14.2129 | 1.5415 | 9.2201 | 15.7723 | 1.7106 | 9.2201 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 19.582 | 1232 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1192.3964 | 12.8214 | 93.0008 | 1192.3964 | 12.8214 | 93.0008 | 1323.2233 | 14.2281 | 93.0008 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 1.2434 | 1 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.3274 | 0.81412 | 5.3154 | 4.3274 | 0.81412 | 5.3154 | 4.8022 | 0.90344 | 5.3154 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 1.3053 | 37 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 104.4239 | 0.85462 | 122.1873 | 104.4239 | 0.85462 | 122.1873 | 115.881 | 0.94839 | 122.1873 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.44811 | 19 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.6527 | 0.2934 | 15.8578 | 4.6527 | 0.2934 | 15.8578 | 5.1631 | 0.32559 | 15.8578 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2027 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 0.1538 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.1675 | 0.1007 | 31.4549 | 3.1675 | 0.1007 | 31.4549 | 3.5151 | 0.11175 | 31.4549 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 4.2055 | 355 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 162.9237 | 2.7535 | 59.1687 | 162.9237 | 2.7535 | 59.1687 | 180.7993 | 3.0557 | 59.1687 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 6.4578 | 333 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 56.6878 | 4.2282 | 13.4069 | 56.6878 | 4.2282 | 13.4069 | 62.9074 | 4.6922 | 13.4069 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 2.7653 | 373 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 127.1099 | 1.8106 | 70.2026 | 127.1099 | 1.8106 | 70.2026 | 141.0561 | 2.0093 | 70.2026 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 8.3421 | 316 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1264.1257 | 5.462 | 231.441 | 1264.1257 | 5.462 | 231.441 | 1402.8226 | 6.0613 | 231.441 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 1.9394 | 108 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 181.9416 | 1.2698 | 143.2792 | 181.9416 | 1.2698 | 143.2792 | 201.9038 | 1.4092 | 143.2792 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 3.8122 | 341 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 417.8482 | 2.496 | 167.4054 | 417.8482 | 2.496 | 167.4054 | 463.6936 | 2.7699 | 167.4054 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 11.0316 | 1032 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 146.7475 | 7.223 | 20.3167 | 146.7475 | 7.223 | 20.3167 | 162.8483 | 8.0155 | 20.3167 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 8.4597 | 757 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 561.9538 | 5.539 | 101.454 | 561.9538 | 5.539 | 101.454 | 623.61 | 6.1467 | 101.454 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 4.2816 | 43 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 27.2109 | 2.8034 | 9.7064 | 27.2109 | 2.8034 | 9.7064 | 30.1964 | 3.111 | 9.7064 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 3.6864 | 236 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 145.709 | 2.4137 | 60.3681 | 145.709 | 2.4137 | 60.3681 | 161.6959 | 2.6785 | 60.3681 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2027 | 243 | 243-14R | Tier-2 | Tier-2---11 | 4--4 | 4.9975 | 0 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 5.9029 | 0 | 0 | 5.9029 | 0 | 5.3716 | 3.2722 | 1.6416 | 5.3716 | 3.2722 | 1.6416 | 5.9609 | 3.6312 | 1.6416 | 1.46% | 0.066445 | 0.063156 | 6084.1314 | 280.7794 | 3933.5085 | 1869.8435 | 6307.5143 | 0 | 0 | 6307.5143 | 0.0001947%
2027 | 916 | 916-381 | Tier-2 | Tier-2---12 | 4--4 | 0.1652 | 0 | 100% | 590.9122 | 71.07% | 28.73% | 0.1918% | 20.7893 | 0 | 0 | 20.7893 | 0 | 18.918 | 0.10817 | 174.8989 | 18.918 | 0.10817 | 174.8989 | 20.9936 | 0.12003 | 174.8989 | 3.518% | 0.049834 | 0.047367 | 11857.5641 | 1782.085 | 3001.9836 | 7073.4955 | 12036.1866 | 0 | 0 | 12036.1866 | 0.0006856%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 1.5403 | 211 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 36.8484 | 1.0085 | 36.5368 | 36.8484 | 1.0085 | 36.5368 | 40.8913 | 1.1192 | 36.5368 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 18.6854 | 1020 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 241.5192 | 12.2343 | 19.7412 | 241.5192 | 12.2343 | 19.7412 | 268.0181 | 13.5766 | 19.7412 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 6.8811 | 282 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 451.3803 | 4.5054 | 100.1867 | 451.3803 | 4.5054 | 100.1867 | 500.9047 | 4.9997 | 100.1867 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 12.6964 | 932 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 494.3491 | 8.313 | 59.4668 | 494.3491 | 8.313 | 59.4668 | 548.5879 | 9.2251 | 59.4668 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 20.6608 | 1391 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1037.5009 | 13.5277 | 76.6947 | 1037.5009 | 13.5277 | 76.6947 | 1151.3331 | 15.0119 | 76.6947 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 3.259 | 164 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 28.5327 | 2.1339 | 13.3713 | 28.5327 | 2.1339 | 13.3713 | 31.6632 | 2.368 | 13.3713 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2027 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 0.8674 | 0 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 17.3075 | 0.56793 | 30.4747 | 17.3075 | 0.56793 | 30.4747 | 19.2065 | 0.63024 | 30.4747 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 31.8811 | 2181 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 613.1991 | 20.8742 | 29.3759 | 613.1991 | 20.8742 | 29.3759 | 680.4779 | 23.1645 | 29.3759 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 12.0339 | 273 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 271.7734 | 7.8792 | 34.4923 | 271.7734 | 7.8792 | 34.4923 | 301.5917 | 8.7437 | 34.4923 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 2.9135 | 269 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 225.6484 | 1.9076 | 118.2893 | 225.6484 | 1.9076 | 118.2893 | 250.406 | 2.1169 | 118.2893 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 3.7841 | 209 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 129.1894 | 2.4776 | 52.1423 | 129.1894 | 2.4776 | 52.1423 | 143.3638 | 2.7495 | 52.1423 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 15.005 | 1436 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 135.1583 | 9.8245 | 13.7572 | 135.1583 | 9.8245 | 13.7572 | 149.9876 | 10.9025 | 13.7572 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 3.0267 | 277 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 154.5381 | 1.9817 | 77.9812 | 154.5381 | 1.9817 | 77.9812 | 171.4936 | 2.1992 | 77.9812 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 3.5275 | 209 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 294.2347 | 2.3096 | 127.3955 | 294.2347 | 2.3096 | 127.3955 | 326.5175 | 2.563 | 127.3955 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 4.5645 | 642 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.7342 | 2.9886 | 4.5955 | 13.7342 | 2.9886 | 4.5955 | 15.2411 | 3.3166 | 4.5955 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2027 | 334 | CB 334 | Tier-2 | Tier-2---17 | 3--4 | 2.321 | 0 | 100% | 70.5162 | 95.08% | 0% | 4.917% | 3.3189 | 0 | 0 | 3.3189 | 0 | 3.0202 | 1.5197 | 1.9874 | 3.0202 | 1.5197 | 1.9874 | 3.3515 | 1.6864 | 1.9874 | 4.707% | 0.014478 | 0.013762 | 4870.4444 | 330.0733 | 2622.0959 | 1918.2753 | 4882.9165 | 0 | 0 | 4882.9165 | 0.0001094%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 0.89662 | 14 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 22.5604 | 0.58706 | 38.4291 | 22.5604 | 0.58706 | 38.4291 | 25.0356 | 0.65148 | 38.4291 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 26.8775 | 296 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 175.4857 | 17.5981 | 9.9719 | 175.4857 | 17.5981 | 9.9719 | 194.7396 | 19.5289 | 9.9719 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 9.2899 | 565 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 51.3378 | 6.0826 | 8.4401 | 51.3378 | 6.0826 | 8.4401 | 56.9704 | 6.75 | 8.4401 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 18.7375 | 1826 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 183.5822 | 12.2684 | 14.9638 | 183.5822 | 12.2684 | 14.9638 | 203.7244 | 13.6145 | 14.9638 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 1.6445 | 323 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 9.4057 | 1.0767 | 8.7355 | 9.4057 | 1.0767 | 8.7355 | 10.4377 | 1.1949 | 8.7355 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 3.5953 | 283 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 231.132 | 2.354 | 98.1865 | 231.132 | 2.354 | 98.1865 | 256.4912 | 2.6123 | 98.1865 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 20.7013 | 1693 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1269.1144 | 13.5542 | 93.6323 | 1269.1144 | 13.5542 | 93.6323 | 1408.3587 | 15.0414 | 93.6323 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 5.4369 | 85 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 41.8749 | 3.5598 | 11.7632 | 41.8749 | 3.5598 | 11.7632 | 46.4693 | 3.9504 | 11.7632 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 0.69072 | 24 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.6978 | 0.45225 | 12.5988 | 5.6978 | 0.45225 | 12.5988 | 6.323 | 0.50187 | 12.5988 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 13.5415 | 832 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 440.5122 | 8.8663 | 49.6838 | 440.5122 | 8.8663 | 49.6838 | 488.8442 | 9.8391 | 49.6838 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 8.3178 | 78 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 271.0346 | 5.4461 | 49.7669 | 271.0346 | 5.4461 | 49.7669 | 300.7719 | 6.0436 | 49.7669 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 16.422 | 1620 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 498.8841 | 10.7523 | 46.3978 | 498.8841 | 10.7523 | 46.3978 | 553.6205 | 11.932 | 46.3978 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 11.56 | 762 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1007.0762 | 7.569 | 133.0534 | 1007.0762 | 7.569 | 133.0534 | 1117.5702 | 8.3994 | 133.0534 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2027 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.17383 | 0 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.80006 | 0.11382 | 7.0293 | 0.80006 | 0.11382 | 7.0293 | 0.88784 | 0.1263 | 7.0293 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.77126 | 53 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 35.3002 | 0.50498 | 69.9038 | 35.3002 | 0.50498 | 69.9038 | 39.1733 | 0.56039 | 69.9038 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 5.0473 | 259 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 64.6275 | 3.3047 | 19.556 | 64.6275 | 3.3047 | 19.556 | 71.7183 | 3.6673 | 19.556 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 13.8096 | 549 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 159.8647 | 9.0419 | 17.6805 | 159.8647 | 9.0419 | 17.6805 | 177.4047 | 10.0339 | 17.6805 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 11.815 | 901 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 777.0044 | 7.7359 | 100.4417 | 777.0044 | 7.7359 | 100.4417 | 862.2555 | 8.5846 | 100.4417 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 20.6063 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 150.1902 | 13.492 | 11.1318 | 150.1902 | 13.492 | 11.1318 | 166.6687 | 14.9723 | 11.1318 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2027 | 476 | CB 476 | Tier-2 | Tier-2---2 | 5--5 | 3.9551 | 0 | 100% | 7260.3217 | 73.64% | 26.17% | 0.1876% | 264.6639 | 0 | 0 | 264.6639 | 0 | 240.8405 | 2.5896 | 93.0026 | 240.8405 | 2.5896 | 93.0026 | 267.265 | 2.8737 | 93.0026 | 3.645% | 0.20125 | 0.19129 | 36075.4158 | 6663.2216 | 8787.8653 | 20624.3289 | 36570.586 | 0 | 0 | 36570.586 | 0.008728%
2027 | 386 | 386-25R | Tier-2 | Tier-2---15 | 3--4 | 0.7066 | 0 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 2.5144 | 0 | 0 | 2.5144 | 0 | 2.2881 | 0.46265 | 4.9456 | 2.2881 | 0.46265 | 4.9456 | 2.5391 | 0.51341 | 4.9456 | 1.75% | 0.019083 | 0.018138 | 7528.0087 | 552.5881 | 4465.4268 | 2509.9939 | 7781.4266 | 0 | 0 | 7781.4266 | 8.292e-05%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 0.80794 | 5 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 30.9346 | 0 | 0 | 30.9346 | 0 | 28.15 | 0.529 | 53.2135 | 28.15 | 0.529 | 53.2135 | 31.2386 | 0.58704 | 53.2135 | 4.945% | 0.0036434 | 0.0034631 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171700.5551 | 0 | 0 | 171700.5551 | 0.00102%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 1.165 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 65.7597 | 0.76279 | 86.2089 | 65.7597 | 0.76279 | 86.2089 | 72.9747 | 0.84649 | 86.2089 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 9.7066 | 442 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 654.899 | 6.3554 | 103.0456 | 654.899 | 6.3554 | 103.0456 | 726.7529 | 7.0527 | 103.0456 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 8.2208 | 243 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 254.1624 | 5.3826 | 47.2193 | 254.1624 | 5.3826 | 47.2193 | 282.0485 | 5.9732 | 47.2193 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 11.3059 | 892 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 194.367 | 7.4025 | 26.2568 | 194.367 | 7.4025 | 26.2568 | 215.6925 | 8.2147 | 26.2568 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 13.2995 | 353 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 412.0132 | 8.7079 | 47.3151 | 412.0132 | 8.7079 | 47.3151 | 457.2183 | 9.6633 | 47.3151 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 8.9197 | 519 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 58.3163 | 5.8402 | 9.9854 | 58.3163 | 5.8402 | 9.9854 | 64.7147 | 6.4809 | 9.9854 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 2.6869 | 284 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 19.0795 | 1.7592 | 10.8453 | 19.0795 | 1.7592 | 10.8453 | 21.1729 | 1.9523 | 10.8453 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2027 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 0.050947 | 0 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.79635 | 0.033358 | 23.873 | 0.79635 | 0.033358 | 23.873 | 0.88372 | 0.037018 | 23.873 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 1.2638 | 61 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 25.4406 | 0.82749 | 30.7442 | 25.4406 | 0.82749 | 30.7442 | 28.2319 | 0.91828 | 30.7442 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2027 | 308 | 308-486AE | Tier-2 | Tier-2---16 | 4--3 | 1.7369 | 0 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.19428 | 0 | 0 | 0.19428 | 0 | 0.1768 | 1.1372 | 0.15546 | 0.1768 | 1.1372 | 0.15546 | 0.19619 | 1.262 | 0.15546 | 0.118% | 0.040279 | 0.038285 | 4088.4689 | 19.0997 | 3634.8848 | 434.4844 | 4296.3129 | 0 | 0 | 4296.3129 | 6.407e-06%
2027 | 295 | 295-1203F | Tier-2 | Tier-2---21 | 1--2 | 0.2153 | 0 | 100% | 0.80448 | 60.49% | 0% | 39.51% | 0.02409 | 0 | 0 | 0.02409 | 0 | 0.021921 | 0.14097 | 0.1555 | 0.021921 | 0.14097 | 0.1555 | 0.024326 | 0.15643 | 0.1555 | 2.994% | 0.0013362 | 0.0012701 | 602.062 | 79.8078 | 41.8021 | 480.452 | 614.4487 | 0 | 0 | 614.4487 | 7.944e-07%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 1.3216 | 258 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 108.8052 | 0.86534 | 125.7371 | 108.8052 | 0.86534 | 125.7371 | 120.743 | 0.96028 | 125.7371 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 7.0884 | 586 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 369.8356 | 4.6412 | 79.6858 | 369.8356 | 4.6412 | 79.6858 | 410.4131 | 5.1504 | 79.6858 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2027 | 450 | 450-50R | Tier-2 | Tier-2---11 | 4--4 | 0.3652 | 6 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 8.6479 | 0 | 0 | 8.6479 | 0 | 7.8695 | 0.23912 | 32.9109 | 7.8695 | 0.23912 | 32.9109 | 8.7329 | 0.26535 | 32.9109 | 1.61% | 0.071801 | 0.068247 | 7480.0024 | 403.5755 | 4618.5943 | 2457.8325 | 7742.8291 | 0 | 0 | 7742.8291 | 0.0002852%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 1.5712 | 63 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 20.502 | 1.0288 | 19.929 | 20.502 | 1.0288 | 19.929 | 22.7514 | 1.1416 | 19.929 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 11.7129 | 203 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 313.8836 | 7.669 | 40.9286 | 313.8836 | 7.669 | 40.9286 | 348.3221 | 8.5105 | 40.9286 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.78597 | 36 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.2588 | 0.51462 | 21.878 | 11.2588 | 0.51462 | 21.878 | 12.4941 | 0.57108 | 21.878 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 5.3936 | 448 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 32.6271 | 3.5315 | 9.2389 | 32.6271 | 3.5315 | 9.2389 | 36.2069 | 3.9189 | 9.2389 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2027 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 9.3687 | 504 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 558.9371 | 6.1342 | 91.1183 | 558.9371 | 6.1342 | 91.1183 | 620.2624 | 6.8072 | 91.1183 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2027 | 393 | CB 393 | Tier-2 | Tier-2---19 | 1--3 | 0.339 | 0 | 100% | 8.3766 | 93.83% | 0% | 6.171% | 0.38906 | 0 | 0 | 0.38906 | 0 | 0.35404 | 0.22196 | 1.595 | 0.35404 | 0.22196 | 1.595 | 0.39288 | 0.24631 | 1.595 | 4.645% | 0.0030912 | 0.0029382 | 2709.8263 | 11.6903 | 2486.8043 | 211.3317 | 2718.5348 | 0 | 0 | 2718.5348 | 1.283e-05%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 8.4553 | 115 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 234.0568 | 5.5361 | 42.278 | 234.0568 | 5.5361 | 42.278 | 259.737 | 6.1435 | 42.278 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2027 | 443 | CB 443 | Tier-2 | Tier-2---17 | 2--4 | 1.4752 | 0 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 3.2669 | 0 | 0 | 3.2669 | 0 | 2.9729 | 0.96588 | 3.0779 | 2.9729 | 0.96588 | 3.0779 | 3.299 | 1.0719 | 3.0779 | 4.865% | 0.007405 | 0.0070385 | 9067.8323 | 1863.6752 | 20.0371 | 7184.12 | 9075.9094 | 0 | 0 | 9075.9094 | 0.0001077%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 2.5689 | 85 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 183.4459 | 1.682 | 109.0639 | 183.4459 | 1.682 | 109.0639 | 203.5731 | 1.8665 | 109.0639 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 10.4533 | 593 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 26.069 | 6.8443 | 3.8089 | 26.069 | 6.8443 | 3.8089 | 28.9292 | 7.5952 | 3.8089 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2027 | 535 | CB 535 | Tier-2 | Tier-2---16 | 4--3 | 0.31174 | 0 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25308 | 0 | 0 | 0.25308 | 0 | 0.2303 | 0.20411 | 1.1283 | 0.2303 | 0.20411 | 1.1283 | 0.25556 | 0.22651 | 1.1283 | 0.227% | 0.059698 | 0.056743 | 1867.7052 | 14.9488 | 1426.0626 | 426.6938 | 1960.5113 | 0 | 0 | 1960.5113 | 8.346e-06%
2027 | 281 | CB 281 | Tier-2 | Tier-2---16 | 4--3 | 3.767 | 0 | 100% | 131.3229 | 1.145% | 96.36% | 2.498% | 0.07445 | 0 | 0 | 0.07445 | 0 | 0.067748 | 2.4665 | 0.027468 | 0.067748 | 2.4665 | 0.027468 | 0.075181 | 2.7371 | 0.027468 | 0.05669% | 0.046838 | 0.04452 | 2803.7555 | 3.8846 | 2517.4341 | 282.4368 | 2948.0968 | 0 | 0 | 2948.0968 | 2.455e-06%
2027 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.023485 | 0 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.8337 | 0.015377 | 184.2836 | 2.8337 | 0.015377 | 184.2836 | 3.1446 | 0.017064 | 184.2836 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 15.3043 | 1286 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 142.5829 | 10.0206 | 14.229 | 142.5829 | 10.0206 | 14.229 | 158.2268 | 11.12 | 14.229 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 3.3899 | 505 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 169.5107 | 2.2196 | 76.3715 | 169.5107 | 2.2196 | 76.3715 | 188.109 | 2.4631 | 76.3715 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 14.7171 | 529 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 18.1939 | 9.636 | 1.8881 | 18.1939 | 9.636 | 1.8881 | 20.1901 | 10.6933 | 1.8881 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.87121 | 106 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.9588 | 0.57043 | 10.4462 | 5.9588 | 0.57043 | 10.4462 | 6.6126 | 0.63301 | 10.4462 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 5.3095 | 781 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 408.8067 | 3.4764 | 117.5946 | 408.8067 | 3.4764 | 117.5946 | 453.66 | 3.8578 | 117.5946 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 9.9971 | 673 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 547.9949 | 6.5456 | 83.7192 | 547.9949 | 6.5456 | 83.7192 | 608.1196 | 7.2638 | 83.7192 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2027 | 1139 | 1139-4F | Tier-2 | Tier-2---11 | 5--3 | 2.2023 | 0 | 100% | 472.1771 | 0.2595% | 99.27% | 0.4712% | 0.060646 | 0 | 0 | 0.060646 | 0 | 0.055187 | 1.442 | 0.038272 | 0.055187 | 1.442 | 0.038272 | 0.061242 | 1.6002 | 0.038272 | 0.01284% | 0.11231 | 0.10675 | 4204.4022 | 7.5405 | 3803.8802 | 392.9815 | 4422.7903 | 0 | 0 | 4422.7903 | 2e-06%
2027 | 197 | 197-1157F | Tier-2 | Tier-2---18 | 3--3 | 0.1773 | 0 | 100% | 63.1655 | 1.305% | 98.13% | 0.5601% | 0.040803 | 0 | 0 | 0.040803 | 0 | 0.03713 | 0.11609 | 0.31985 | 0.03713 | 0.11609 | 0.31985 | 0.041204 | 0.12882 | 0.31985 | 0.0646% | 0.01787 | 0.016985 | 3534.7635 | 11.6765 | 2974.4275 | 548.6595 | 3716.4442 | 0 | 0 | 3716.4442 | 1.346e-06%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 5.1261 | 334 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 154.4302 | 3.3564 | 46.0112 | 154.4302 | 3.3564 | 46.0112 | 171.3739 | 3.7246 | 46.0112 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 16.7214 | 1503 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1259.9464 | 10.9484 | 115.0807 | 1259.9464 | 10.9484 | 115.0807 | 1398.1847 | 12.1496 | 115.0807 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 11.1523 | 320 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 355.9256 | 7.302 | 48.7438 | 355.9256 | 7.302 | 48.7438 | 394.9769 | 8.1031 | 48.7438 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | 3--3 | 0.65624 | 4 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9366 | 0 | 0 | 1.9366 | 0 | 1.7623 | 0.42968 | 4.1015 | 1.7623 | 0.42968 | 4.1015 | 1.9557 | 0.47682 | 4.1015 | 4.192% | 0.018623 | 0.017701 | 2480.5668 | 274.9764 | 742.9932 | 1462.5972 | 2500.341 | 0 | 0 | 2500.341 | 6.386e-05%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 3.6983 | 195 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 36.1453 | 2.4215 | 14.927 | 36.1453 | 2.4215 | 14.927 | 40.1111 | 2.6871 | 14.927 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2027 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.39659 | 0 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.64817 | 0.25967 | 2.4961 | 0.64817 | 0.25967 | 2.4961 | 0.71928 | 0.28816 | 2.4961 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 1.0854 | 13 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 14.7896 | 0.71068 | 20.8105 | 14.7896 | 0.71068 | 20.8105 | 16.4123 | 0.78865 | 20.8105 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.31499 | 9 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.325 | 0.20624 | 35.5163 | 7.325 | 0.20624 | 35.5163 | 8.1287 | 0.22887 | 35.5163 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 17.9266 | 1150 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1837.8519 | 11.7375 | 156.5801 | 1837.8519 | 11.7375 | 156.5801 | 2039.4967 | 13.0253 | 156.5801 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 15.4477 | 756 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1659.3701 | 10.1144 | 164.0594 | 1659.3701 | 10.1144 | 164.0594 | 1841.4323 | 11.2242 | 164.0594 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2027 | 462 | CB 462 | Tier-2 | Tier-2---19 | 2--4 | 0.4439 | 0 | 100% | 42.4238 | 96.69% | 0% | 3.313% | 2.0304 | 0 | 0 | 2.0304 | 0 | 1.8476 | 0.29064 | 6.3571 | 1.8476 | 0.29064 | 6.3571 | 2.0504 | 0.32253 | 6.3571 | 4.786% | 0.0069768 | 0.0066314 | 6080.6996 | 1110.385 | 1800.7984 | 3169.5162 | 6091.1906 | 0 | 0 | 6091.1906 | 6.696e-05%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 17.4555 | 1930 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 808.0402 | 11.429 | 70.7007 | 808.0402 | 11.429 | 70.7007 | 896.6965 | 12.683 | 70.7007 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 5.0582 | 437 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 65.2597 | 3.3118 | 19.705 | 65.2597 | 3.3118 | 19.705 | 72.4198 | 3.6752 | 19.705 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 0.14415 | 0 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.2499 | 0.094381 | 23.8382 | 2.2499 | 0.094381 | 23.8382 | 2.4967 | 0.10474 | 23.8382 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 5.8553 | 513 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 235.5518 | 3.8337 | 61.4417 | 235.5518 | 3.8337 | 61.4417 | 261.396 | 4.2544 | 61.4417 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2027 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | 3--3 | 0.27065 | 0 | 100% | 40.9949 | 23.55% | 73.64% | 2.81% | 0.47782 | 0 | 0 | 0.47782 | 0 | 0.43481 | 0.17721 | 2.4536 | 0.43481 | 0.17721 | 2.4536 | 0.48252 | 0.19666 | 2.4536 | 1.166% | 0.021565 | 0.020497 | 1901.027 | 61.7007 | 1198.5032 | 640.8231 | 1976.7168 | 0 | 0 | 1976.7168 | 1.576e-05%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 7.3796 | 121 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 209.6923 | 4.8318 | 43.3983 | 209.6923 | 4.8318 | 43.3983 | 232.6993 | 5.3619 | 43.3983 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.50061 | 50 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 17.4178 | 0.32777 | 53.1399 | 17.4178 | 0.32777 | 53.1399 | 19.3289 | 0.36374 | 53.1399 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 13.2557 | 1015 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 120.9234 | 8.6792 | 13.9326 | 120.9234 | 8.6792 | 13.9326 | 134.1908 | 9.6314 | 13.9326 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 21.2556 | 676 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3540.5817 | 13.9172 | 254.4035 | 3540.5817 | 13.9172 | 254.4035 | 3929.0461 | 15.4441 | 254.4035 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 29.2157 | 713 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 375.994 | 19.129 | 19.6557 | 375.994 | 19.129 | 19.6557 | 417.2472 | 21.2278 | 19.6557 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 7.4915 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 162.7089 | 4.9051 | 33.1715 | 162.7089 | 4.9051 | 33.1715 | 180.561 | 5.4433 | 33.1715 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 15.6835 | 943 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1006.1322 | 10.2688 | 97.9792 | 1006.1322 | 10.2688 | 97.9792 | 1116.5227 | 11.3955 | 97.9792 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2027 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 2.0208 | 0 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 32.3544 | 1.3231 | 24.4526 | 32.3544 | 1.3231 | 24.4526 | 35.9042 | 1.4683 | 24.4526 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.1678 | 14 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.093 | 0.10987 | 46.3547 | 5.093 | 0.10987 | 46.3547 | 5.6517 | 0.12192 | 46.3547 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 6.2775 | 169 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 431.4681 | 4.1102 | 104.9749 | 431.4681 | 4.1102 | 104.9749 | 478.8077 | 4.5612 | 104.9749 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 8.9137 | 164 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 96.2068 | 5.8362 | 16.4844 | 96.2068 | 5.8362 | 16.4844 | 106.7624 | 6.4766 | 16.4844 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 3.55 | 286 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 227.2841 | 2.3244 | 97.7835 | 227.2841 | 2.3244 | 97.7835 | 252.2212 | 2.5794 | 97.7835 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | 4--4 | 0.88746 | 14 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 8.56 | 0 | 0 | 8.56 | 0 | 7.7895 | 0.58107 | 13.4055 | 7.7895 | 0.58107 | 13.4055 | 8.6441 | 0.64482 | 13.4055 | 1.069% | 0.071178 | 0.067654 | 11247.1911 | 406.5986 | 8046.836 | 2793.7565 | 11706.3951 | 0 | 0 | 11706.3951 | 0.0002823%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 34.1718 | 1862 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1801.0985 | 22.3741 | 80.4993 | 1801.0985 | 22.3741 | 80.4993 | 1998.7108 | 24.8289 | 80.4993 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 1.4237 | 110 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.2041 | 0.93217 | 7.7284 | 7.2041 | 0.93217 | 7.7284 | 7.9946 | 1.0344 | 7.7284 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2027 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 3.4267 | 233 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.8667 | 2.2436 | 0.83203 | 1.8667 | 2.2436 | 0.83203 | 2.0716 | 2.4898 | 0.83203 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 1.3115 | 241 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.1258 | 0.85872 | 11.7916 | 10.1258 | 0.85872 | 11.7916 | 11.2367 | 0.95294 | 11.7916 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 6.4924 | 205 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 20.217 | 4.2509 | 4.7559 | 20.217 | 4.2509 | 4.7559 | 22.4352 | 4.7173 | 4.7559 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 7.8576 | 482 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 72.2882 | 5.1448 | 14.0508 | 72.2882 | 5.1448 | 14.0508 | 80.2195 | 5.7092 | 14.0508 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 17.727 | 1369 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1568.061 | 11.6068 | 135.0982 | 1568.061 | 11.6068 | 135.0982 | 1740.105 | 12.8803 | 135.0982 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 2.3271 | 116 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 68.7275 | 1.5237 | 45.1071 | 68.7275 | 1.5237 | 45.1071 | 76.2681 | 1.6908 | 45.1071 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.49562 | 11 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 37.8035 | 0.32451 | 116.4953 | 37.8035 | 0.32451 | 116.4953 | 41.9512 | 0.36011 | 116.4953 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 2.1594 | 49 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 23.951 | 1.4139 | 16.9397 | 23.951 | 1.4139 | 16.9397 | 26.5789 | 1.569 | 16.9397 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2027 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.010606 | 0 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0069443 | 0 | 0 | 0.0069443 | 0 | 0 | 0.0077062 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2027 | 445 | 445-1315 | Tier-2 | Tier-2---19 | 1--5 | 0.080871 | 0 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 1.294 | 0 | 0 | 1.294 | 0 | 1.1776 | 0.05295 | 22.2389 | 1.1776 | 0.05295 | 22.2389 | 1.3068 | 0.05876 | 22.2389 | 4.93% | 0.000636 | 0.00060452 | 41272.5846 | 5558.0973 | 1215.1763 | 34499.311 | 41281.3528 | 0 | 0 | 41281.3528 | 4.267e-05%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.6215 | 0.022445 | 116.7955 | 2.6215 | 0.022445 | 116.7955 | 2.9091 | 0.024908 | 116.7955 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.57917 | 30 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.165 | 0.37921 | 34.7169 | 13.165 | 0.37921 | 34.7169 | 14.6095 | 0.42082 | 34.7169 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2027 | 175 | CB 175 | Tier-2 | Tier-2---10 | 5--4 | 0.0828 | 0 | 100% | 1236.5075 | 84.14% | 15.66% | 0.203% | 51.5004 | 0 | 0 | 51.5004 | 0 | 46.8647 | 0.054213 | 864.447 | 46.8647 | 0.054213 | 864.447 | 52.0066 | 0.060162 | 864.447 | 4.165% | 0.16723 | 0.15895 | 7393.9644 | 1133.6762 | 1185.8912 | 5074.397 | 7455.0304 | 0 | 0 | 7455.0304 | 0.001698%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 12.1911 | 327 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 377.9207 | 7.9821 | 47.3459 | 377.9207 | 7.9821 | 47.3459 | 419.3853 | 8.8579 | 47.3459 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 1.8653 | 423 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 17.4173 | 1.2213 | 14.2608 | 17.4173 | 1.2213 | 14.2608 | 19.3283 | 1.3553 | 14.2608 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.055682 | 34 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.069276 | 0.036458 | 1.9002 | 0.069276 | 0.036458 | 1.9002 | 0.076876 | 0.040458 | 1.9002 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 24.3072 | 878 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 749.3113 | 15.9152 | 47.0816 | 749.3113 | 15.9152 | 47.0816 | 831.524 | 17.6613 | 47.0816 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 1.2636 | 41 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 18.5991 | 0.82737 | 22.4798 | 18.5991 | 0.82737 | 22.4798 | 20.6397 | 0.91815 | 22.4798 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 10.5112 | 997 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 85.5897 | 6.8822 | 12.4364 | 85.5897 | 6.8822 | 12.4364 | 94.9804 | 7.6373 | 12.4364 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 0.081438 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0023289 | 0.053322 | 0.043676 | 0.0023289 | 0.053322 | 0.043676 | 0.0025844 | 0.059172 | 0.043676 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 7.3706 | 412 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 821.8397 | 4.8259 | 170.2962 | 821.8397 | 4.8259 | 170.2962 | 912.01 | 5.3554 | 170.2962 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 22.4647 | 1409 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 380.2129 | 14.7088 | 25.8493 | 380.2129 | 14.7088 | 25.8493 | 421.929 | 16.3227 | 25.8493 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 8.1866 | 140 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 38.8993 | 5.3602 | 7.2571 | 38.8993 | 5.3602 | 7.2571 | 43.1673 | 5.9483 | 7.2571 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.016856 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.30382 | 0.011037 | 27.5287 | 0.30382 | 0.011037 | 27.5287 | 0.33716 | 0.012247 | 27.5287 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 8.8214 | 139 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 108.1471 | 5.7758 | 18.7241 | 108.1471 | 5.7758 | 18.7241 | 120.0127 | 6.4095 | 18.7241 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 0.22216 | 19 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.28735 | 0.14546 | 1.9755 | 0.28735 | 0.14546 | 1.9755 | 0.31888 | 0.16142 | 1.9755 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 1.2988 | 31 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 20.4346 | 0.85041 | 24.029 | 20.4346 | 0.85041 | 24.029 | 22.6767 | 0.94372 | 24.029 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 3.321 | 115 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 52.7183 | 2.1744 | 24.2445 | 52.7183 | 2.1744 | 24.2445 | 58.5024 | 2.413 | 24.2445 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 14.5687 | 1091 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 604.7186 | 9.5389 | 63.395 | 604.7186 | 9.5389 | 63.395 | 671.067 | 10.5855 | 63.395 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 2.3515 | 16 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 256.8046 | 1.5397 | 166.7922 | 256.8046 | 1.5397 | 166.7922 | 284.9806 | 1.7086 | 166.7922 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.41229 | 18 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 13.5232 | 0.26994 | 50.0961 | 13.5232 | 0.26994 | 50.0961 | 15.0069 | 0.29956 | 50.0961 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 6.2353 | 440 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 157.9098 | 4.0826 | 38.6792 | 157.9098 | 4.0826 | 38.6792 | 175.2352 | 4.5305 | 38.6792 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 2.0774 | 340 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 112.5405 | 1.3602 | 82.7384 | 112.5405 | 1.3602 | 82.7384 | 124.8882 | 1.5094 | 82.7384 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.76383 | 6 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 7.6802 | 0.50012 | 15.3568 | 7.6802 | 0.50012 | 15.3568 | 8.5228 | 0.55499 | 15.3568 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 5.8533 | 585 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 60.6355 | 3.8324 | 15.8217 | 60.6355 | 3.8324 | 15.8217 | 67.2883 | 4.2529 | 15.8217 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 4.0824 | 392 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 19.1528 | 2.6729 | 7.1655 | 19.1528 | 2.6729 | 7.1655 | 21.2542 | 2.9662 | 7.1655 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 15.1559 | 793 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 107.9342 | 9.9233 | 10.8768 | 107.9342 | 9.9233 | 10.8768 | 119.7765 | 11.0121 | 10.8768 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 19.9074 | 1826 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1170.8648 | 13.0344 | 89.8289 | 1170.8648 | 13.0344 | 89.8289 | 1299.3294 | 14.4645 | 89.8289 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 8.7188 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 318.6899 | 5.7086 | 55.826 | 318.6899 | 5.7086 | 55.826 | 353.6559 | 6.335 | 55.826 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2027 | 239 | CB 239 | Tier-3 | Tier-3---20 | 1--5 | 0.039773 | 0 | 100% | 10.6776 | 99.64% | 0% | 0.3633% | 0.52662 | 0 | 0 | 0.52662 | 0 | 0.47922 | 0.026041 | 18.4022 | 0.47922 | 0.026041 | 18.4022 | 0.5318 | 0.028899 | 18.4022 | 4.932% | 0.0001826 | 0.00017356 | 58475.5699 | 8842.2618 | 1906.0953 | 47727.2128 | 58486.6341 | 0 | 0 | 58486.6341 | 1.737e-05%
2027 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.84619 | 35 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 94.6789 | 0.55404 | 170.887 | 94.6789 | 0.55404 | 170.887 | 105.0668 | 0.61483 | 170.887 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 3.4333 | 98 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 16.4392 | 2.248 | 7.3129 | 16.4392 | 2.248 | 7.3129 | 18.2429 | 2.4946 | 7.3129 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.34621 | 18 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.091 | 0.22668 | 31.2817 | 7.091 | 0.22668 | 31.2817 | 7.869 | 0.25155 | 31.2817 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2027 | 948 | 948-5R | Tier-2 | Tier-2---21 | 1--2 | 0.1373 | 0 | 100% | 3.6494 | 90.16% | 0% | 9.838% | 0.16287 | 0 | 0 | 0.16287 | 0 | 0.14821 | 0.089898 | 1.6487 | 0.14821 | 0.089898 | 1.6487 | 0.16447 | 0.099761 | 1.6487 | 4.463% | 0.0023872 | 0.002269 | 1528.7338 | 203.4062 | 386.7322 | 938.5955 | 1536.5665 | 0 | 0 | 1536.5665 | 5.371e-06%
2027 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 0.81042 | 160 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.8346 | 0.53062 | 5.342 | 2.8346 | 0.53062 | 5.342 | 3.1456 | 0.58884 | 5.342 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2027 | 533 | CB 533 | Tier-2 | Tier-2---20 | 4--1 | 0.027511 | 0 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.01766 | 0 | 0 | 0.01766 | 0 | 0.01607 | 0.018013 | 0.89216 | 0.01607 | 0.018013 | 0.89216 | 0.017834 | 0.019989 | 0.89216 | 0.1665% | 0.06013 | 0.057154 | 176.3723 | 1.2595 | 133.5547 | 41.5581 | 185.2484 | 0 | 0 | 185.2484 | 5.824e-07%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 13.4125 | 992 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 73.1226 | 8.7819 | 8.3265 | 73.1226 | 8.7819 | 8.3265 | 81.1454 | 9.7454 | 8.3265 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 1.0659 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 59.2108 | 0.6979 | 84.8411 | 59.2108 | 0.6979 | 84.8411 | 65.7073 | 0.77447 | 84.8411 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 14.5985 | 935 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 508.6206 | 9.5584 | 53.2118 | 508.6206 | 9.5584 | 53.2118 | 564.4253 | 10.6071 | 53.2118 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.64526 | 37 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.5839 | 0.42248 | 13.2168 | 5.5839 | 0.42248 | 13.2168 | 6.1965 | 0.46884 | 13.2168 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2027 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 2.803 | 3 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 4.1518 | 1.8353 | 2.2622 | 4.1518 | 1.8353 | 2.2622 | 4.6073 | 2.0366 | 2.2622 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 7.564 | 846 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 91.6277 | 4.9526 | 18.5011 | 91.6277 | 4.9526 | 18.5011 | 101.6809 | 5.4959 | 18.5011 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 24.6051 | 1562 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 282.5323 | 16.1103 | 17.5374 | 282.5323 | 16.1103 | 17.5374 | 313.5311 | 17.8779 | 17.5374 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 5.7333 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 237.497 | 3.7539 | 63.2667 | 237.497 | 3.7539 | 63.2667 | 263.5546 | 4.1658 | 63.2667 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 10.6382 | 730 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 98.8295 | 6.9654 | 14.1886 | 98.8295 | 6.9654 | 14.1886 | 109.6728 | 7.7296 | 14.1886 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 10.5116 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 389.3404 | 6.8825 | 56.5698 | 389.3404 | 6.8825 | 56.5698 | 432.0579 | 7.6376 | 56.5698 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 1.4734 | 189 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.248 | 0.96474 | 3.3667 | 3.248 | 0.96474 | 3.3667 | 3.6044 | 1.0706 | 3.3667 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 20.5957 | 1555 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2470.7159 | 13.4851 | 183.2187 | 2470.7159 | 13.4851 | 183.2187 | 2741.797 | 14.9646 | 183.2187 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 4.4809 | 263 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 43.1232 | 2.9339 | 14.6985 | 43.1232 | 2.9339 | 14.6985 | 47.8546 | 3.2558 | 14.6985 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 22.8015 | 890 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 75.7062 | 14.9294 | 5.071 | 75.7062 | 14.9294 | 5.071 | 84.0125 | 16.5674 | 5.071 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.125 | 26 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 3.9274 | 0.081844 | 47.9869 | 3.9274 | 0.081844 | 47.9869 | 4.3584 | 0.090824 | 47.9869 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2027 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.092045 | 7 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.3026 | 0.060267 | 187.5432 | 11.3026 | 0.060267 | 187.5432 | 12.5427 | 0.066879 | 187.5432 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 9.5829 | 976 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 58.891 | 6.2745 | 9.3858 | 58.891 | 6.2745 | 9.3858 | 65.3523 | 6.9629 | 9.3858 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2027 | 728 | 728-1570F | Tier-2 | Tier-2---19 | 1--5 | 0.0015 | 0 | 100% | 33.2807 | 99.79% | 0% | 0.2133% | 1.6439 | 0 | 0 | 1.6439 | 0 | 1.4959 | 0.00098213 | 1523.1308 | 1.4959 | 0.00098213 | 1523.1308 | 1.66 | 0.0010899 | 1523.1308 | 4.939% | 0.0003472 | 0.00033001 | 95854.6419 | 22304.1965 | 20.1049 | 73530.3404 | 95865.2904 | 0 | 0 | 95865.2904 | 5.421e-05%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 12.1965 | 973 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 373.4462 | 7.9857 | 46.7646 | 373.4462 | 7.9857 | 46.7646 | 414.4198 | 8.8618 | 46.7646 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 20.8132 | 1273 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 399.4624 | 13.6275 | 29.3129 | 399.4624 | 13.6275 | 29.3129 | 443.2904 | 15.1227 | 29.3129 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 2.4181 | 206 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 76.6258 | 1.5833 | 48.3969 | 76.6258 | 1.5833 | 48.3969 | 85.033 | 1.757 | 48.3969 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 4.0926 | 174 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 297.7228 | 2.6797 | 111.105 | 297.7228 | 2.6797 | 111.105 | 330.3883 | 2.9737 | 111.105 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2027 | 972 | 972-1642 | Tier-2 | Tier-2---16 | 5--2 | 0.038636 | 0 | 100% | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.025297 | 0 | 0 | 0.025297 | 0 | 0 | 0.028073 | 0 | 0% | 0.11047 | 0.105 | 1677.3427 | 1.9611 | 1510.6909 | 164.6906 | 1764.6951 | 0 | 0 | 1764.6951 | 0%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.2301 | 17 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 14.5393 | 0.15066 | 96.506 | 14.5393 | 0.15066 | 96.506 | 16.1345 | 0.16719 | 96.506 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.38903 | 14 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 31.0484 | 0.25472 | 121.892 | 31.0484 | 0.25472 | 121.892 | 34.4549 | 0.28267 | 121.892 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 12.821 | 921 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 144.2426 | 8.3946 | 17.1828 | 144.2426 | 8.3946 | 17.1828 | 160.0686 | 9.3156 | 17.1828 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 10.8114 | 889 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 79.4193 | 7.0788 | 11.2193 | 79.4193 | 7.0788 | 11.2193 | 88.133 | 7.8555 | 11.2193 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 2.6777 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 226.7991 | 1.7532 | 129.3619 | 226.7991 | 1.7532 | 129.3619 | 251.683 | 1.9456 | 129.3619 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 11.5801 | 469 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 460.7021 | 7.5821 | 60.7618 | 460.7021 | 7.5821 | 60.7618 | 511.2492 | 8.414 | 60.7618 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2027 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 2.4417 | 29 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 9.3898 | 1.5987 | 5.8735 | 9.3898 | 1.5987 | 5.8735 | 10.4201 | 1.7741 | 5.8735 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 9.2184 | 137 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 18.0809 | 6.0357 | 2.9956 | 18.0809 | 6.0357 | 2.9956 | 20.0646 | 6.698 | 2.9956 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2027 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.075568 | 0 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 8.6384 | 0.049478 | 174.5888 | 8.6384 | 0.049478 | 174.5888 | 9.5861 | 0.054907 | 174.5888 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 6.8952 | 725 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 38.0091 | 4.5147 | 8.419 | 38.0091 | 4.5147 | 8.419 | 42.1794 | 5.01 | 8.419 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 3.5241 | 66 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 58.3418 | 2.3074 | 25.2848 | 58.3418 | 2.3074 | 25.2848 | 64.7429 | 2.5605 | 25.2848 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2027 | 386 | CB 386 | Tier-2 | Tier-2---14 | 4--4 | 2.7822 | 0 | 100% | 266.4482 | 58.89% | 39.19% | 1.927% | 7.7666 | 0 | 0 | 7.7666 | 0 | 7.0675 | 1.8217 | 3.8797 | 7.0675 | 1.8217 | 3.8797 | 7.8429 | 2.0215 | 3.8797 | 2.915% | 0.037437 | 0.035584 | 7117.2424 | 561.1032 | 3326.6838 | 3229.4554 | 7269.6317 | 0 | 0 | 7269.6317 | 0.0002561%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 11.3933 | 245 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 53.1821 | 7.4598 | 7.1292 | 53.1821 | 7.4598 | 7.1292 | 59.0171 | 8.2783 | 7.1292 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 1.2636 | 4 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 20.4453 | 0.82735 | 24.7119 | 20.4453 | 0.82735 | 24.7119 | 22.6885 | 0.91812 | 24.7119 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2027 | 858 | 858-14 | Tier-2 | Tier-2---12 | 2--5 | 1.3439 | 0 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 20.2792 | 0 | 0 | 20.2792 | 0 | 18.4538 | 0.87992 | 20.9721 | 18.4538 | 0.87992 | 20.9721 | 20.4785 | 0.97646 | 20.9721 | 4.926% | 0.010043 | 0.0095457 | 40994.194 | 8631.9946 | 63.0219 | 32299.1775 | 41004.6459 | 0 | 0 | 41004.6459 | 0.0006687%
2027 | 282 | CB 282 | Tier-2 | Tier-2---15 | 4--3 | 0.221 | 0 | 100% | 152.5069 | 4.749% | 94.48% | 0.7672% | 0.3585 | 0 | 0 | 0.3585 | 0 | 0.32623 | 0.1447 | 2.2545 | 0.32623 | 0.1447 | 2.2545 | 0.36202 | 0.16058 | 2.2545 | 0.2351% | 0.035573 | 0.033812 | 4287.153 | 11.5968 | 3743.6752 | 531.8809 | 4499.8161 | 0 | 0 | 4499.8161 | 1.182e-05%
2027 | 795 | 795-816R | Tier-2 | Tier-2---13 | 4--4 | 2.6195 | 0 | 100% | 228.7654 | 4.756% | 93.08% | 2.167% | 0.53859 | 0 | 0 | 0.53859 | 0 | 0.49011 | 1.7151 | 0.28576 | 0.49011 | 1.7151 | 0.28576 | 0.54388 | 1.9033 | 0.28576 | 0.2354% | 0.036491 | 0.034684 | 6269.16 | 14.3219 | 5608.3339 | 646.5042 | 6580.116 | 0 | 0 | 6580.116 | 1.776e-05%
2027 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 0.64526 | 21 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 14.7448 | 0.42249 | 34.9 | 14.7448 | 0.42249 | 34.9 | 16.3626 | 0.46884 | 34.9 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 3.4282 | 107 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 64.084 | 2.2446 | 28.5503 | 64.084 | 2.2446 | 28.5503 | 71.1152 | 2.4909 | 28.5503 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 11.6815 | 979 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 298.5256 | 7.6485 | 39.0308 | 298.5256 | 7.6485 | 39.0308 | 331.2791 | 8.4876 | 39.0308 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 20.7706 | 2353 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 296.627 | 13.5996 | 21.8114 | 296.627 | 13.5996 | 21.8114 | 329.1722 | 15.0917 | 21.8114 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 10.4561 | 129 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 31.3913 | 6.8461 | 4.5853 | 31.3913 | 6.8461 | 4.5853 | 34.8355 | 7.5973 | 4.5853 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 2.8193 | 65 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 16.745 | 1.8459 | 9.0712 | 16.745 | 1.8459 | 9.0712 | 18.5822 | 2.0485 | 9.0712 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 13.3513 | 1600 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 402.1167 | 8.7418 | 45.9993 | 402.1167 | 8.7418 | 45.9993 | 446.236 | 9.7009 | 45.9993 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2027 | 928 | 928-20 | Tier-2 | Tier-2---20 | 4--2 | 0.0328 | 0 | 100% | 27.1749 | 93.08% | 6.522% | 0.4024% | 1.252 | 0 | 0 | 1.252 | 0 | 1.1393 | 0.021476 | 53.0508 | 1.1393 | 0.021476 | 53.0508 | 1.2643 | 0.023832 | 53.0508 | 4.607% | 0.044362 | 0.042166 | 612.5656 | 93.209 | 34.6926 | 484.664 | 614.7746 | 0 | 0 | 614.7746 | 4.129e-05%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 4.9693 | 637 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 32.6276 | 3.2537 | 10.0279 | 32.6276 | 3.2537 | 10.0279 | 36.2074 | 3.6107 | 10.0279 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2027 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 5.2678 | 343 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 43.7467 | 3.4491 | 12.6835 | 43.7467 | 3.4491 | 12.6835 | 48.5465 | 3.8275 | 12.6835 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 14.5858 | 738 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1049.1639 | 9.5501 | 109.8593 | 1049.1639 | 9.5501 | 109.8593 | 1164.2757 | 10.5979 | 109.8593 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 0.049053 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.09892 | 0.032118 | 3.0799 | 0.09892 | 0.032118 | 3.0799 | 0.10977 | 0.035641 | 3.0799 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2027 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 0.20947 | 11 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 6.1748 | 0.13715 | 45.022 | 6.1748 | 0.13715 | 45.022 | 6.8523 | 0.1522 | 45.022 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 9.6756 | 209 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 64.9552 | 6.3351 | 10.2532 | 64.9552 | 6.3351 | 10.2532 | 72.0819 | 7.0302 | 10.2532 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2027 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 2.7722 | 17 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.7703 | 1.8151 | 0.97532 | 1.7703 | 1.8151 | 0.97532 | 1.9645 | 2.0142 | 0.97532 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 3.6174 | 367 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 200.7686 | 2.3685 | 84.7651 | 200.7686 | 2.3685 | 84.7651 | 222.7965 | 2.6284 | 84.7651 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 9.2129 | 303 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 205.7031 | 6.0322 | 34.101 | 205.7031 | 6.0322 | 34.101 | 228.2724 | 6.694 | 34.101 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 7.3522 | 285 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 149.7342 | 4.8139 | 31.1046 | 149.7342 | 4.8139 | 31.1046 | 166.1626 | 5.3421 | 31.1046 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.32386 | 57 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 17.7496 | 0.21205 | 83.7047 | 17.7496 | 0.21205 | 83.7047 | 19.6971 | 0.23532 | 83.7047 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 1.7152 | 34 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 322.8415 | 1.123 | 287.4814 | 322.8415 | 1.123 | 287.4814 | 358.263 | 1.2462 | 287.4814 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 10.7038 | 848 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 294.6356 | 7.0083 | 42.0408 | 294.6356 | 7.0083 | 42.0408 | 326.9624 | 7.7773 | 42.0408 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 1.7237 | 253 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 61.1671 | 1.1286 | 54.1981 | 61.1671 | 1.1286 | 54.1981 | 67.8782 | 1.2524 | 54.1981 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2027 | 243 | CB 243 | Tier-2 | Tier-2---14 | 4--4 | 0.7388 | 0 | 100% | 284.2808 | 92.1% | 7.127% | 0.7733% | 12.9602 | 0 | 0 | 12.9602 | 0 | 11.7936 | 0.48373 | 24.3804 | 11.7936 | 0.48373 | 24.3804 | 13.0875 | 0.5368 | 24.3804 | 4.559% | 0.039288 | 0.037343 | 7235.7813 | 1297.464 | 840.9216 | 5097.3957 | 7265.5523 | 0 | 0 | 7265.5523 | 0.0004274%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 10.906 | 246 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 287.9812 | 7.1408 | 40.3292 | 287.9812 | 7.1408 | 40.3292 | 319.5779 | 7.9242 | 40.3292 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2027 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | 4--1 | 0.012311 | 0 | 100% | 2.3826 | 9.042% | 83.57% | 7.391% | 0.010664 | 0 | 0 | 0.010664 | 0 | 0.0097039 | 0.0080607 | 1.2039 | 0.0097039 | 0.0080607 | 1.2039 | 0.010769 | 0.0089451 | 1.2039 | 0.4476% | 0.059368 | 0.05643 | 40.1318 | 0.36722 | 29.4839 | 10.2807 | 42.0328 | 0 | 0 | 42.0328 | 3.517e-07%
2027 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.11724 | 0 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 15.0487 | 0.07676 | 196.049 | 15.0487 | 0.07676 | 196.049 | 16.6998 | 0.085182 | 196.049 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 33.4712 | 1238 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2919.5776 | 21.9153 | 133.2208 | 2919.5776 | 21.9153 | 133.2208 | 3239.9069 | 24.3198 | 133.2208 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2027 | 920 | 920-823 | Tier-2 | Tier-2---11 | 4--4 | 0.871 | 0 | 100% | 458.2189 | 68.35% | 31.14% | 0.5113% | 15.5021 | 0 | 0 | 15.5021 | 0 | 14.1067 | 0.57029 | 24.7361 | 14.1067 | 0.57029 | 24.7361 | 15.6545 | 0.63286 | 24.7361 | 3.383% | 0.054577 | 0.051875 | 8395.8542 | 937.9397 | 2311.5146 | 5146.3999 | 8534.2572 | 0 | 0 | 8534.2572 | 0.0005112%
2027 | 280 | CB 280 | Tier-2 | Tier-2---14 | 4--4 | 2.6745 | 17 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 2.4753 | 0 | 0 | 2.4753 | 0 | 2.2525 | 1.7511 | 1.2863 | 2.2525 | 1.7511 | 1.2863 | 2.4997 | 1.9432 | 1.2863 | 0.7965% | 0.042409 | 0.04031 | 7328.4886 | 170.2669 | 5820.5339 | 1337.6878 | 7648.7329 | 0 | 0 | 7648.7329 | 8.163e-05%
2027 | 355 | 355-65R | Tier-2 | Tier-2---21 | 1--2 | 0.007576 | 0 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.0015289 | 0 | 0 | 0.0015289 | 0 | 0.0013913 | 0.0049604 | 0.28047 | 0.0013913 | 0.0049604 | 0.28047 | 0.0015439 | 0.0055046 | 0.28047 | 2.282% | 7.02e-05 | 6.6725e-05 | 954.2713 | 72.5365 | 46.719 | 835.0158 | 981.0548 | 0 | 0 | 981.0548 | 5.042e-08%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 6.5815 | 222 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 55.5708 | 4.3092 | 12.8957 | 55.5708 | 4.3092 | 12.8957 | 61.6679 | 4.782 | 12.8957 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 19.1678 | 1740 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 409.4082 | 12.5502 | 32.6217 | 409.4082 | 12.5502 | 32.6217 | 454.3275 | 13.9272 | 32.6217 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2027 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.033523 | 0 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.51379 | 0.021949 | 23.408 | 0.51379 | 0.021949 | 23.408 | 0.57016 | 0.024357 | 23.408 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2027 | 235 | CB 235 | Tier-2 | Tier-2---12 | 1--5 | 0.15928 | 0 | 100% | 443.5427 | 99.96% | 0% | 0.03939% | 21.9467 | 0 | 0 | 21.9467 | 0 | 19.9712 | 0.10429 | 191.4988 | 19.9712 | 0.10429 | 191.4988 | 22.1624 | 0.11573 | 191.4988 | 4.948% | 0.0007134 | 0.00067809 | 621730.7449 | 100003.5038 | 3209.2492 | 518517.9918 | 621743.4984 | 0 | 0 | 621743.4984 | 0.0007237%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 5.3209 | 577 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 150.9784 | 3.4839 | 43.3365 | 150.9784 | 3.4839 | 43.3365 | 167.5434 | 3.8661 | 43.3365 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 8.1068 | 164 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 22.4804 | 5.308 | 4.2352 | 22.4804 | 5.308 | 4.2352 | 24.9469 | 5.8903 | 4.2352 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2027 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 7.7129 | 463 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 5.7652 | 5.05 | 1.1416 | 5.7652 | 5.05 | 1.1416 | 6.3978 | 5.6041 | 1.1416 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.58561 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 3.8596 | 0.38343 | 10.066 | 3.8596 | 0.38343 | 10.066 | 4.283 | 0.4255 | 10.066 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 7.0273 | 9 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 14.5292 | 4.6011 | 3.1577 | 14.5292 | 4.6011 | 3.1577 | 16.1233 | 5.106 | 3.1577 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 10.6015 | 361 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 40.081 | 6.9414 | 5.7742 | 40.081 | 6.9414 | 5.7742 | 44.4786 | 7.703 | 5.7742 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 3.3435 | 149 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 386.4725 | 2.1892 | 176.5371 | 386.4725 | 2.1892 | 176.5371 | 428.8754 | 2.4294 | 176.5371 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2027 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 3.5375 | 52 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.084982 | 2.3162 | 0.03669 | 0.084982 | 2.3162 | 0.03669 | 0.094305 | 2.5703 | 0.03669 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 5.4324 | 4 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 20.5582 | 3.5569 | 5.7799 | 20.5582 | 3.5569 | 5.7799 | 22.8138 | 3.9471 | 5.7799 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2027 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 0.38934 | 15 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 8.1497 | 0.25492 | 31.969 | 8.1497 | 0.25492 | 31.969 | 9.0438 | 0.28289 | 31.969 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2027 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | 3--3 | 2.0388 | 0 | 100% | 117.3021 | 94.99% | 0% | 5.009% | 5.5156 | 0 | 0 | 5.5156 | 0 | 5.0191 | 1.3349 | 3.7599 | 5.0191 | 1.3349 | 3.7599 | 5.5698 | 1.4814 | 3.7599 | 4.702% | 0.027256 | 0.025907 | 4303.7498 | 1020.4795 | 248.6707 | 3034.5996 | 4314.9761 | 0 | 0 | 4314.9761 | 0.0001819%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 7.8127 | 414 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 869.0928 | 5.1154 | 169.8986 | 869.0928 | 5.1154 | 169.8986 | 964.4476 | 5.6766 | 169.8986 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 3.1864 | 107 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 136.2236 | 2.0863 | 65.2949 | 136.2236 | 2.0863 | 65.2949 | 151.1698 | 2.3152 | 65.2949 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 1.1027 | 132 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 33.1036 | 0.72198 | 45.8509 | 33.1036 | 0.72198 | 45.8509 | 36.7357 | 0.8012 | 45.8509 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 7.8693 | 814 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 432.2395 | 5.1524 | 83.8904 | 432.2395 | 5.1524 | 83.8904 | 479.6638 | 5.7177 | 83.8904 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2027 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.053788 | 0 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.084645 | 0.035218 | 2.4035 | 0.084645 | 0.035218 | 2.4035 | 0.093932 | 0.039082 | 2.4035 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2027 | 452 | 452-717 | Tier-2 | Tier-2---19 | 1--5 | 0.0871 | 0 | 100% | 24.802 | 99.04% | 0% | 0.9608% | 1.2159 | 0 | 0 | 1.2159 | 0 | 1.1065 | 0.057029 | 19.4017 | 1.1065 | 0.057029 | 19.4017 | 1.2279 | 0.063286 | 19.4017 | 4.902% | 0.000973 | 0.00092484 | 25490.2561 | 9086.828 | 25.5586 | 16377.8695 | 25503.0101 | 0 | 0 | 25503.0101 | 4.01e-05%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 13.2184 | 308 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 172.8267 | 8.6548 | 19.9689 | 172.8267 | 8.6548 | 19.9689 | 191.7888 | 9.6044 | 19.9689 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2027 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.027841 | 0 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.2722 | 0.018229 | 14.9323 | 0.2722 | 0.018229 | 14.9323 | 0.30207 | 0.020229 | 14.9323 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 6.3703 | 486 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 644.9047 | 4.171 | 154.6173 | 644.9047 | 4.171 | 154.6173 | 715.6622 | 4.6286 | 154.6173 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 2.6683 | 515 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 22.8254 | 1.7471 | 13.0647 | 22.8254 | 1.7471 | 13.0647 | 25.3298 | 1.9388 | 13.0647 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 11.3506 | 1487 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 282.7746 | 7.4318 | 38.0491 | 282.7746 | 7.4318 | 38.0491 | 313.7999 | 8.2472 | 38.0491 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 6.121 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 92.1312 | 4.0077 | 22.9884 | 92.1312 | 4.0077 | 22.9884 | 102.2396 | 4.4474 | 22.9884 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 6.7335 | 641 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 655.4112 | 4.4088 | 148.6608 | 655.4112 | 4.4088 | 148.6608 | 727.3214 | 4.8925 | 148.6608 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 1.5907 | 12 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.2738 | 1.0415 | 3.1433 | 3.2738 | 1.0415 | 3.1433 | 3.633 | 1.1558 | 3.1433 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2027 | 266 | 266-485F | Tier-2 | Tier-2---21 | 1--4 | 0.047 | 0 | 100% | 3.9025 | 97.35% | 0% | 2.654% | 0.18805 | 0 | 0 | 0.18805 | 0 | 0.17112 | 0.030773 | 5.5607 | 0.17112 | 0.030773 | 5.5607 | 0.1899 | 0.03415 | 5.5607 | 4.819% | 0.000646 | 0.00061402 | 6041.0896 | 954.7948 | 18.9693 | 5067.3254 | 6049.4401 | 0 | 0 | 6049.4401 | 6.201e-06%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 6.8056 | 645 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 72.0469 | 4.456 | 16.1685 | 72.0469 | 4.456 | 16.1685 | 79.9518 | 4.9449 | 16.1685 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 11.3022 | 654 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 999.3119 | 7.4002 | 135.039 | 999.3119 | 7.4002 | 135.039 | 1108.954 | 8.2121 | 135.039 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 7.9883 | 1090 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 135.7606 | 5.2303 | 25.9563 | 135.7606 | 5.2303 | 25.9563 | 150.6559 | 5.8042 | 25.9563 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 6.2962 | 587 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 332.7936 | 4.1225 | 80.7267 | 332.7936 | 4.1225 | 80.7267 | 369.307 | 4.5748 | 80.7267 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 0.60433 | 297 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 19.5259 | 0.39569 | 49.3469 | 19.5259 | 0.39569 | 49.3469 | 21.6682 | 0.4391 | 49.3469 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 0.61936 | 43 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.70278 | 0.40553 | 1.733 | 0.70278 | 0.40553 | 1.733 | 0.77989 | 0.45002 | 1.733 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 34.4453 | 2656 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 243.3688 | 22.5531 | 10.7909 | 243.3688 | 22.5531 | 10.7909 | 270.0707 | 25.0276 | 10.7909 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 3.289 | 353 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 27.4714 | 2.1535 | 12.7567 | 27.4714 | 2.1535 | 12.7567 | 30.4855 | 2.3898 | 12.7567 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 3.4321 | 23 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.9912 | 2.2471 | 4.0011 | 8.9912 | 2.2471 | 4.0011 | 9.9777 | 2.4937 | 4.0011 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 2.081 | 79 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 7.8263 | 1.3626 | 5.7438 | 7.8263 | 1.3626 | 5.7438 | 8.685 | 1.5121 | 5.7438 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 9.6284 | 454 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 465.7123 | 6.3042 | 73.8729 | 465.7123 | 6.3042 | 73.8729 | 516.8091 | 6.9959 | 73.8729 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 4.8606 | 121 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 16.5362 | 3.1825 | 5.196 | 16.5362 | 3.1825 | 5.196 | 18.3505 | 3.5317 | 5.196 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | 3--3 | 4.2973 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 2.1229 | 0 | 0 | 2.1229 | 0 | 1.9318 | 2.8137 | 0.68657 | 1.9318 | 2.8137 | 0.68657 | 2.1437 | 3.1224 | 0.68657 | 4.29% | 0.02391 | 0.022726 | 2069.6845 | 324.0484 | 134.0961 | 1611.54 | 2084.0584 | 0 | 0 | 2084.0584 | 7e-05%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 4.0623 | 220 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 23.1241 | 2.6598 | 8.6939 | 23.1241 | 2.6598 | 8.6939 | 25.6612 | 2.9516 | 8.6939 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 20.3065 | 1265 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 176.6226 | 13.2957 | 13.2842 | 176.6226 | 13.2957 | 13.2842 | 196.0012 | 14.7545 | 13.2842 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 5.9877 | 433 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 240.2011 | 3.9205 | 61.2682 | 240.2011 | 3.9205 | 61.2682 | 266.5555 | 4.3506 | 61.2682 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 12.0589 | 918 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 277.3974 | 7.8956 | 35.1332 | 277.3974 | 7.8956 | 35.1332 | 307.8328 | 8.7619 | 35.1332 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2027 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 6.3104 | 318 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 5.1199 | 4.1317 | 1.2392 | 5.1199 | 4.1317 | 1.2392 | 5.6817 | 4.5851 | 1.2392 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2027 | 280 | 280-24AE | Tier-2 | Tier-2---12 | 4--4 | 0.5631 | 0 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.56941 | 0 | 0 | 0.56941 | 0 | 0.51815 | 0.36869 | 1.4054 | 0.51815 | 0.36869 | 1.4054 | 0.575 | 0.40914 | 1.4054 | 0.1557% | 0.037093 | 0.035257 | 9861.3901 | 49.7133 | 8813.1546 | 998.5222 | 10358.7999 | 0 | 0 | 10358.7999 | 1.878e-05%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 27.9316 | 2562 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1152.5944 | 18.2883 | 63.0236 | 1152.5944 | 18.2883 | 63.0236 | 1279.0544 | 20.2949 | 63.0236 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 5.7761 | 269 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 524.7816 | 3.7819 | 138.7599 | 524.7816 | 3.7819 | 138.7599 | 582.3594 | 4.1969 | 138.7599 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.95666 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 55.83 | 0.62638 | 89.1317 | 55.83 | 0.62638 | 89.1317 | 61.9555 | 0.6951 | 89.1317 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 7.5917 | 224 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 454.2842 | 4.9707 | 91.3928 | 454.2842 | 4.9707 | 91.3928 | 504.1272 | 5.516 | 91.3928 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 8.614 | 942 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 85.0286 | 5.6401 | 15.0758 | 85.0286 | 5.6401 | 15.0758 | 94.3577 | 6.2589 | 15.0758 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2.1411 | 3 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 19.4852 | 1.4019 | 13.8995 | 19.4852 | 1.4019 | 13.8995 | 21.6231 | 1.5557 | 13.8995 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 1.8381 | 85 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 57.4893 | 1.2035 | 47.7682 | 57.4893 | 1.2035 | 47.7682 | 63.7969 | 1.3356 | 47.7682 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2027 | 308 | CB 308 | Tier-2 | Tier-2---18 | 4--3 | 0.8729 | 0 | 100% | 77.7948 | 18.36% | 79.79% | 1.851% | 0.70708 | 0 | 0 | 0.70708 | 0 | 0.64343 | 0.57153 | 1.1258 | 0.64343 | 0.57153 | 1.1258 | 0.71403 | 0.63424 | 1.1258 | 0.9089% | 0.037941 | 0.036063 | 2050.437 | 12.1248 | 1817.8081 | 220.5041 | 2137.6123 | 0 | 0 | 2137.6123 | 2.332e-05%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 3.0796 | 188 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 8.6939 | 2.0164 | 4.3116 | 8.6939 | 2.0164 | 4.3116 | 9.6477 | 2.2376 | 4.3116 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 10.0146 | 475 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 31.5996 | 6.5571 | 4.8192 | 31.5996 | 6.5571 | 4.8192 | 35.0666 | 7.2765 | 4.8192 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2027 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 1.532 | 0 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 256.5422 | 1.0031 | 255.7529 | 256.5422 | 1.0031 | 255.7529 | 284.6894 | 1.1131 | 255.7529 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2027 | 401 | 401-39R | Tier-2 | Tier-2---14 | 4--4 | 0.0585 | 0 | 100% | 323.2323 | 3.193% | 96.7% | 0.1048% | 0.51091 | 0 | 0 | 0.51091 | 0 | 0.46492 | 0.038303 | 12.1379 | 0.46492 | 0.038303 | 12.1379 | 0.51593 | 0.042506 | 12.1379 | 0.1581% | 0.031872 | 0.030295 | 10141.4477 | 77.0794 | 9013.6522 | 1050.7162 | 10652.728 | 0 | 0 | 10652.728 | 1.685e-05%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 0.63484 | 10 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.33334 | 0.41566 | 0.80194 | 0.33334 | 0.41566 | 0.80194 | 0.36991 | 0.46127 | 0.80194 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 8.7678 | 225 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 17.8667 | 5.7407 | 3.1123 | 17.8667 | 5.7407 | 3.1123 | 19.8269 | 6.3706 | 3.1123 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.87727 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 65.4805 | 0.5744 | 113.9987 | 65.4805 | 0.5744 | 113.9987 | 72.6648 | 0.63742 | 113.9987 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2027 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011932 | 0 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078125 | 0 | 0 | 0.0078125 | 0 | 0 | 0.0086697 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 3.06 | 54 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 94.482 | 2.0035 | 47.1574 | 94.482 | 2.0035 | 47.1574 | 104.8483 | 2.2234 | 47.1574 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 1.6544 | 24 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 232.1001 | 1.0832 | 214.2739 | 232.1001 | 1.0832 | 214.2739 | 257.5656 | 1.202 | 214.2739 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 0.11231 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.15554 | 0.073536 | 2.1151 | 0.15554 | 0.073536 | 2.1151 | 0.1726 | 0.081604 | 2.1151 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 3.4226 | 424 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 189.0401 | 2.2409 | 84.3577 | 189.0401 | 2.2409 | 84.3577 | 209.7812 | 2.4868 | 84.3577 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 2.6673 | 417 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 67.5098 | 1.7464 | 38.6568 | 67.5098 | 1.7464 | 38.6568 | 74.9169 | 1.938 | 38.6568 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2027 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 0 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.69648 | 0.022445 | 31.0308 | 0.69648 | 0.022445 | 31.0308 | 0.7729 | 0.024908 | 31.0308 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.87803 | 24 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 29.2851 | 0.57489 | 50.9401 | 29.2851 | 0.57489 | 50.9401 | 32.4982 | 0.63797 | 50.9401 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 17.882 | 25 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 55.8373 | 11.7083 | 4.769 | 55.8373 | 11.7083 | 4.769 | 61.9636 | 12.9929 | 4.769 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.030114 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.2263 | 0.019717 | 265.0633 | 5.2263 | 0.019717 | 265.0633 | 5.7997 | 0.021881 | 265.0633 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 9.9068 | 699 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 81.859 | 6.4865 | 12.6199 | 81.859 | 6.4865 | 12.6199 | 90.8403 | 7.1982 | 12.6199 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 2.1343 | 19 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 32.6575 | 1.3974 | 23.3701 | 32.6575 | 1.3974 | 23.3701 | 36.2406 | 1.5507 | 23.3701 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 1.1486 | 101 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.4415 | 0.75208 | 12.5539 | 9.4415 | 0.75208 | 12.5539 | 10.4774 | 0.83459 | 12.5539 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.46834 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 35.6381 | 0.30665 | 116.2189 | 35.6381 | 0.30665 | 116.2189 | 39.5482 | 0.34029 | 116.2189 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2027 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.23902 | 0 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 1.0258 | 0.1565 | 6.5546 | 1.0258 | 0.1565 | 6.5546 | 1.1383 | 0.17367 | 6.5546 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 17.7839 | 336 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 237.5496 | 11.6441 | 20.4009 | 237.5496 | 11.6441 | 20.4009 | 263.613 | 12.9216 | 20.4009 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 27.7907 | 1376 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 819.268 | 18.196 | 45.0246 | 819.268 | 18.196 | 45.0246 | 909.1561 | 20.1924 | 45.0246 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 1.0255 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.2891 | 0.67146 | 21.2804 | 14.2891 | 0.67146 | 21.2804 | 15.8568 | 0.74514 | 21.2804 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 1.6259 | 6 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 18.4733 | 1.0646 | 17.3525 | 18.4733 | 1.0646 | 17.3525 | 20.5002 | 1.1814 | 17.3525 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 9.0746 | 475 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 217.1483 | 5.9416 | 36.5471 | 217.1483 | 5.9416 | 36.5471 | 240.9733 | 6.5935 | 36.5471 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 10.35 | 778 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 192.6453 | 6.7767 | 28.4276 | 192.6453 | 6.7767 | 28.4276 | 213.7819 | 7.5202 | 28.4276 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 5.1765 | 270 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 123.7039 | 3.3893 | 36.4979 | 123.7039 | 3.3893 | 36.4979 | 137.2764 | 3.7612 | 36.4979 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.94526 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 161.8413 | 0.61891 | 261.4946 | 161.8413 | 0.61891 | 261.4946 | 179.5981 | 0.68681 | 261.4946 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.47553 | 18 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 26.2533 | 0.31135 | 84.3201 | 26.2533 | 0.31135 | 84.3201 | 29.1337 | 0.34551 | 84.3201 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 2.6021 | 514 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 58.2657 | 1.7037 | 34.1985 | 58.2657 | 1.7037 | 34.1985 | 64.6584 | 1.8907 | 34.1985 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 19.0867 | 1839 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 191.4311 | 12.4971 | 15.3181 | 191.4311 | 12.4971 | 15.3181 | 212.4345 | 13.8682 | 15.3181 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.70208 | 157 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 4.7854 | 0.45969 | 10.41 | 4.7854 | 0.45969 | 10.41 | 5.3104 | 0.51013 | 10.41 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2027 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 4.4396 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 28.4591 | 2.9068 | 9.7904 | 28.4591 | 2.9068 | 9.7904 | 31.5815 | 3.2258 | 9.7904 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 7.7195 | 1158 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 171.9679 | 5.0544 | 34.0237 | 171.9679 | 5.0544 | 34.0237 | 190.8359 | 5.6089 | 34.0237 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2027 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.46496 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 58.4684 | 0.30443 | 192.0556 | 58.4684 | 0.30443 | 192.0556 | 64.8835 | 0.33784 | 192.0556 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 2.2173 | 249 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 98.75 | 1.4518 | 68.0203 | 98.75 | 1.4518 | 68.0203 | 109.5846 | 1.6111 | 68.0203 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2027 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 5.5852 | 7 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 175.6505 | 3.6569 | 48.0321 | 175.6505 | 3.6569 | 48.0321 | 194.9225 | 4.0582 | 48.0321 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 2.0289 | 237 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 30.0435 | 1.3285 | 22.6154 | 30.0435 | 1.3285 | 22.6154 | 33.3398 | 1.4742 | 22.6154 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 9.4684 | 640 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 89.8634 | 6.1995 | 14.4954 | 89.8634 | 6.1995 | 14.4954 | 99.723 | 6.8796 | 14.4954 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 2.7573 | 110 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 35.1835 | 1.8054 | 19.4882 | 35.1835 | 1.8054 | 19.4882 | 39.0437 | 2.0035 | 19.4882 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 3.4339 | 102 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 190.3065 | 2.2483 | 84.6429 | 190.3065 | 2.2483 | 84.6429 | 211.1864 | 2.495 | 84.6429 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2027 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.052273 | 0 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.10923 | 0.034226 | 3.1915 | 0.10923 | 0.034226 | 3.1915 | 0.12122 | 0.037981 | 3.1915 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 3.3255 | 21 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 9.5451 | 2.1774 | 4.3837 | 9.5451 | 2.1774 | 4.3837 | 10.5924 | 2.4163 | 4.3837 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 11.8649 | 1745 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 218.2996 | 7.7686 | 28.1003 | 218.2996 | 7.7686 | 28.1003 | 242.251 | 8.6209 | 28.1003 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 17.4926 | 1898 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 245.0024 | 11.4533 | 21.3914 | 245.0024 | 11.4533 | 21.3914 | 271.8835 | 12.71 | 21.3914 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 14.2375 | 375 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2024.2656 | 9.322 | 217.149 | 2024.2656 | 9.322 | 217.149 | 2246.3633 | 10.3448 | 217.149 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2027 | 534 | CB 534 | Tier-2 | Tier-2---21 | 4--1 | 0.38371 | 0 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11233 | 0 | 0 | 0.11233 | 0 | 0.10222 | 0.25124 | 0.40687 | 0.10222 | 0.25124 | 0.40687 | 0.11344 | 0.2788 | 0.40687 | 1.782% | 0.060541 | 0.057544 | 104.1456 | 5.1049 | 50.6919 | 48.3488 | 107.6172 | 0 | 0 | 107.6172 | 3.704e-06%
2027 | 296 | 296-66F | Tier-2 | Tier-2---21 | 1--3 | 0.0214 | 0 | 100% | 2.284 | 90.58% | 0% | 9.421% | 0.10241 | 0 | 0 | 0.10241 | 0 | 0.093188 | 0.014012 | 6.6507 | 0.093188 | 0.014012 | 6.6507 | 0.10341 | 0.015549 | 6.6507 | 4.484% | 0.0006178 | 0.00058722 | 3696.9667 | 843.8145 | 35.5403 | 2817.6118 | 3715.1054 | 0 | 0 | 3715.1054 | 3.377e-06%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 17.4388 | 870 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 90.6092 | 11.4181 | 7.9356 | 90.6092 | 11.4181 | 7.9356 | 100.5506 | 12.6709 | 7.9356 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 3.8686 | 155 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 166.1042 | 2.5329 | 65.5774 | 166.1042 | 2.5329 | 65.5774 | 184.3288 | 2.8109 | 65.5774 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 3.9246 | 150 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 149.8384 | 2.5697 | 58.3104 | 149.8384 | 2.5697 | 58.3104 | 166.2783 | 2.8516 | 58.3104 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 0.43788 | 86 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 18.2693 | 0.2867 | 63.7221 | 18.2693 | 0.2867 | 63.7221 | 20.2737 | 0.31816 | 63.7221 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 6.1356 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 98.5708 | 4.0173 | 24.5366 | 98.5708 | 4.0173 | 24.5366 | 109.3858 | 4.4581 | 24.5366 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 13.604 | 933 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 821.8107 | 8.9073 | 92.263 | 821.8107 | 8.9073 | 92.263 | 911.9778 | 9.8845 | 92.263 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 8.2782 | 212 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 24.4376 | 5.4202 | 4.5086 | 24.4376 | 5.4202 | 4.5086 | 27.1188 | 6.0149 | 4.5086 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2027 | 461 | CB 461 | Tier-2 | Tier-2---15 | 2--4 | 2.3375 | 0 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 4.9747 | 0 | 0 | 4.9747 | 0 | 4.5269 | 1.5305 | 2.9578 | 4.5269 | 1.5305 | 2.9578 | 5.0236 | 1.6984 | 2.9578 | 4.883% | 0.0097562 | 0.0092733 | 10441.6529 | 2274.299 | 1515.1673 | 6652.1866 | 10448.9777 | 0 | 0 | 10448.9777 | 0.000164%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 16.0805 | 603 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 147.4106 | 10.5287 | 14.0008 | 147.4106 | 10.5287 | 14.0008 | 163.5841 | 11.6839 | 14.0008 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.11194 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 6.8075 | 0.073292 | 92.8817 | 6.8075 | 0.073292 | 92.8817 | 7.5544 | 0.081334 | 92.8817 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 5.7011 | 315 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 364.787 | 3.7328 | 97.7242 | 364.787 | 3.7328 | 97.7242 | 404.8106 | 4.1424 | 97.7242 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 12.622 | 1027 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1051.3816 | 8.2643 | 127.22 | 1051.3816 | 8.2643 | 127.22 | 1166.7367 | 9.171 | 127.22 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 13.7044 | 1345 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 321.3252 | 8.973 | 35.8104 | 321.3252 | 8.973 | 35.8104 | 356.5803 | 9.9575 | 35.8104 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2027 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 4.354 | 0 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 21.107 | 2.8508 | 7.4039 | 21.107 | 2.8508 | 7.4039 | 23.4228 | 3.1636 | 7.4039 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 6.0637 | 134 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 48.0153 | 3.9702 | 12.0939 | 48.0153 | 3.9702 | 12.0939 | 53.2834 | 4.4058 | 12.0939 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 12.4352 | 2343 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 322.3648 | 8.142 | 39.5929 | 322.3648 | 8.142 | 39.5929 | 357.7339 | 9.0353 | 39.5929 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 8.4532 | 216 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 145.0545 | 5.5348 | 26.2079 | 145.0545 | 5.5348 | 26.2079 | 160.9695 | 6.142 | 26.2079 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2027 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.18447 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.4339 | 0.12078 | 20.1516 | 2.4339 | 0.12078 | 20.1516 | 2.701 | 0.13403 | 20.1516 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 10.2425 | 319 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 68.0396 | 6.7063 | 10.1457 | 68.0396 | 6.7063 | 10.1457 | 75.5048 | 7.4421 | 10.1457 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 7.3926 | 433 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 159.4396 | 4.8403 | 32.9399 | 159.4396 | 4.8403 | 32.9399 | 176.933 | 5.3714 | 32.9399 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 4.8975 | 133 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 69.195 | 3.2066 | 21.5786 | 69.195 | 3.2066 | 21.5786 | 76.7869 | 3.5585 | 21.5786 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 0.074242 | 9 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.29953 | 0.04861 | 6.1619 | 0.29953 | 0.04861 | 6.1619 | 0.33239 | 0.053944 | 6.1619 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2027 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.13314 | 0 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 6.012 | 0.087176 | 68.964 | 6.012 | 0.087176 | 68.964 | 6.6717 | 0.096741 | 68.964 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 0.85906 | 38 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.01378 | 0.56247 | 0.024499 | 0.01378 | 0.56247 | 0.024499 | 0.015292 | 0.62419 | 0.024499 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 3.4163 | 163 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 101.4086 | 2.2368 | 45.3358 | 101.4086 | 2.2368 | 45.3358 | 112.5349 | 2.4823 | 45.3358 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 12.5079 | 404 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1669.931 | 8.1896 | 203.909 | 1669.931 | 8.1896 | 203.909 | 1853.1519 | 9.0881 | 203.909 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 10.6068 | 689 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 512.6697 | 6.9448 | 73.8203 | 512.6697 | 6.9448 | 73.8203 | 568.9186 | 7.7068 | 73.8203 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 31.2755 | 3380 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 730.5315 | 20.4777 | 35.6744 | 730.5315 | 20.4777 | 35.6744 | 810.6837 | 22.7245 | 35.6744 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 12.3091 | 638 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 611.3449 | 8.0594 | 75.8547 | 611.3449 | 8.0594 | 75.8547 | 678.4203 | 8.9437 | 75.8547 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2027 | 188 | 188-11F | Tier-2 | Tier-2---7 | 3--5 | 1.2193 | 0 | 100% | 2209.344 | 99.86% | 0% | 0.1429% | 109.2062 | 0 | 0 | 109.2062 | 0 | 99.3762 | 0.79834 | 124.4786 | 99.3762 | 0.79834 | 124.4786 | 110.2795 | 0.88593 | 124.4786 | 4.943% | 0.019333 | 0.018376 | 114277.2032 | 24326.824 | 78.3726 | 89872.0066 | 114285.7081 | 0 | 0 | 114285.7081 | 0.003601%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 0.29224 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.76932 | 0.19134 | 4.0207 | 0.76932 | 0.19134 | 4.0207 | 0.85373 | 0.21234 | 4.0207 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2027 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 0.3025 | 0 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 119.8785 | 0.19806 | 605.2556 | 119.8785 | 0.19806 | 605.2556 | 133.0313 | 0.21979 | 605.2556 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 6.4721 | 550 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 191.1024 | 4.2376 | 45.0965 | 191.1024 | 4.2376 | 45.0965 | 212.0697 | 4.7026 | 45.0965 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 2.8459 | 44 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.7945 | 1.8633 | 6.3298 | 11.7945 | 1.8633 | 6.3298 | 13.0885 | 2.0678 | 6.3298 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 6.8671 | 1644 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 73.3558 | 4.4962 | 16.315 | 73.3558 | 4.4962 | 16.315 | 81.4042 | 4.9895 | 16.315 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2027 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.085985 | 0 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.1836 | 0.056299 | 56.5474 | 3.1836 | 0.056299 | 56.5474 | 3.5329 | 0.062476 | 56.5474 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 2.8273 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 4.9928 | 1.8512 | 2.6971 | 4.9928 | 1.8512 | 2.6971 | 5.5406 | 2.0543 | 2.6971 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 1.6392 | 113 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.6223 | 1.0733 | 4.3068 | 4.6223 | 1.0733 | 4.3068 | 5.1294 | 1.191 | 4.3068 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 6.7626 | 34 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 132.7651 | 4.4278 | 29.9845 | 132.7651 | 4.4278 | 29.9845 | 147.3318 | 4.9136 | 29.9845 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 29.745 | 3357 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 228.5667 | 19.4756 | 11.736 | 228.5667 | 19.4756 | 11.736 | 253.6445 | 21.6125 | 11.736 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 3.6661 | 221 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 226.5547 | 2.4004 | 94.3826 | 226.5547 | 2.4004 | 94.3826 | 251.4117 | 2.6638 | 94.3826 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 5.2246 | 108 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 45.4442 | 3.4208 | 13.2846 | 45.4442 | 3.4208 | 13.2846 | 50.4303 | 3.7961 | 13.2846 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 11.5796 | 1397 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 221.282 | 7.5818 | 29.1861 | 221.282 | 7.5818 | 29.1861 | 245.5605 | 8.4136 | 29.1861 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 1.3334 | 164 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 290.2233 | 0.87302 | 332.4376 | 290.2233 | 0.87302 | 332.4376 | 322.0659 | 0.9688 | 332.4376 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 2.7707 | 131 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 70.4536 | 1.8141 | 38.8368 | 70.4536 | 1.8141 | 38.8368 | 78.1836 | 2.0131 | 38.8368 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2027 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.14849 | 7 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 6.0257 | 0.097221 | 61.9791 | 6.0257 | 0.097221 | 61.9791 | 6.6868 | 0.10789 | 61.9791 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 8.7312 | 1001 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 130.6158 | 5.7168 | 22.8478 | 130.6158 | 5.7168 | 22.8478 | 144.9467 | 6.344 | 22.8478 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 3.232 | 330 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 167.0073 | 2.1161 | 78.9208 | 167.0073 | 2.1161 | 78.9208 | 185.3309 | 2.3483 | 78.9208 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2027 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.13579 | 2 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 2.8633 | 0.088912 | 32.2035 | 2.8633 | 0.088912 | 32.2035 | 3.1774 | 0.098667 | 32.2035 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.038118 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1166 | 0.024958 | 44.7399 | 1.1166 | 0.024958 | 44.7399 | 1.2391 | 0.027696 | 44.7399 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 17.8309 | 1143 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 114.9697 | 11.6748 | 9.8476 | 114.9697 | 11.6748 | 9.8476 | 127.5839 | 12.9558 | 9.8476 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 1.6328 | 9 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.9193 | 1.0691 | 10.2138 | 10.9193 | 1.0691 | 10.2138 | 12.1173 | 1.1864 | 10.2138 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.43141 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 5.1675 | 0.28247 | 18.2942 | 5.1675 | 0.28247 | 18.2942 | 5.7345 | 0.31346 | 18.2942 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.052462 | 10 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.2076 | 0.03435 | 93.3816 | 3.2076 | 0.03435 | 93.3816 | 3.5596 | 0.038118 | 93.3816 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2027 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 0.41062 | 16 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.092914 | 0.26885 | 0.34559 | 0.092914 | 0.26885 | 0.34559 | 0.10311 | 0.29835 | 0.34559 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 7.3674 | 675 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 179.8549 | 4.8238 | 37.2847 | 179.8549 | 4.8238 | 37.2847 | 199.5882 | 5.3531 | 37.2847 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.99152 | 143 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 79.5582 | 0.6492 | 122.5483 | 79.5582 | 0.6492 | 122.5483 | 88.2871 | 0.72043 | 122.5483 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 3.9579 | 66 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 114.8046 | 2.5915 | 44.3011 | 114.8046 | 2.5915 | 44.3011 | 127.4007 | 2.8758 | 44.3011 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 8.6068 | 696 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 111.8057 | 5.6353 | 19.8402 | 111.8057 | 5.6353 | 19.8402 | 124.0728 | 6.2536 | 19.8402 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 4.5924 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 430.0662 | 3.0069 | 143.0277 | 430.0662 | 3.0069 | 143.0277 | 477.252 | 3.3368 | 143.0277 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2027 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 0.49168 | 169 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 1.91 | 0.32193 | 5.933 | 1.91 | 0.32193 | 5.933 | 2.1195 | 0.35725 | 5.933 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2027 | 214 | CB 214 | Tier-3 | Tier-3---20 | 1--5 | 0.040909 | 0 | 100% | 59.1996 | 99.88% | 0% | 0.1188% | 2.9269 | 0 | 0 | 2.9269 | 0 | 2.6634 | 0.026785 | 99.4367 | 2.6634 | 0.026785 | 99.4367 | 2.9557 | 0.029724 | 99.4367 | 4.944% | 0.0002016 | 0.00019162 | 293649.0501 | 47091.7983 | 966.5627 | 245590.6891 | 293667.224 | 0 | 0 | 293667.224 | 9.652e-05%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.91593 | 107 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 96.3527 | 0.59971 | 160.6657 | 96.3527 | 0.59971 | 160.6657 | 106.9243 | 0.66551 | 160.6657 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2027 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.036174 | 0 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.1337 | 0.023685 | 47.8669 | 1.1337 | 0.023685 | 47.8669 | 1.2581 | 0.026284 | 47.8669 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 11.2661 | 800 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 680.9116 | 7.3765 | 92.308 | 680.9116 | 7.3765 | 92.308 | 755.6196 | 8.1859 | 92.308 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 4.9145 | 192 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 218.5784 | 3.2178 | 67.9278 | 218.5784 | 3.2178 | 67.9278 | 242.5603 | 3.5709 | 67.9278 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 1.0576 | 36 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 6.2808 | 0.69245 | 9.0703 | 6.2808 | 0.69245 | 9.0703 | 6.9699 | 0.76842 | 9.0703 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2027 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.034091 | 0 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.1978 | 0.022321 | 53.6602 | 1.1978 | 0.022321 | 53.6602 | 1.3292 | 0.02477 | 53.6602 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 7.2415 | 169 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 95.41 | 4.7414 | 20.1229 | 95.41 | 4.7414 | 20.1229 | 105.8782 | 5.2616 | 20.1229 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 5.9928 | 403 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 240.3733 | 3.9238 | 61.2603 | 240.3733 | 3.9238 | 61.2603 | 266.7465 | 4.3543 | 61.2603 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 8.9743 | 875 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 502.5613 | 5.8759 | 85.5289 | 502.5613 | 5.8759 | 85.5289 | 557.7011 | 6.5206 | 85.5289 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2027 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.026705 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.3386 | 0.017485 | 76.5562 | 1.3386 | 0.017485 | 76.5562 | 1.4855 | 0.019404 | 76.5562 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 1.221 | 60 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 99.735 | 0.79947 | 124.7517 | 99.735 | 0.79947 | 124.7517 | 110.6776 | 0.88718 | 124.7517 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2027 | 401 | 401-684R | Tier-2 | Tier-2---21 | 4--1 | 0.051326 | 0 | 100% | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049319 | 0 | 0 | 0.049319 | 0 | 0.04488 | 0.033606 | 1.3355 | 0.04488 | 0.033606 | 1.3355 | 0.049804 | 0.037293 | 1.3355 | 3.09% | 0.030395 | 0.028891 | 52.5129 | 8.9983 | 14.8334 | 28.6812 | 53.5406 | 0 | 0 | 53.5406 | 1.626e-06%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 2.1386 | 171 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 48.5811 | 1.4002 | 34.6947 | 48.5811 | 1.4002 | 34.6947 | 53.9113 | 1.5539 | 34.6947 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2027 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.057008 | 0 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.54074 | 0.037326 | 14.4868 | 0.54074 | 0.037326 | 14.4868 | 0.60007 | 0.041421 | 14.4868 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 5.5421 | 257 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 52.3616 | 3.6287 | 14.4299 | 52.3616 | 3.6287 | 14.4299 | 58.1066 | 4.0268 | 14.4299 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2027 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.043939 | 0 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.48646 | 0.028769 | 16.9092 | 0.48646 | 0.028769 | 16.9092 | 0.53984 | 0.031926 | 16.9092 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 3.2034 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 61.7773 | 2.0974 | 29.4541 | 61.7773 | 2.0974 | 29.4541 | 68.5553 | 2.3275 | 29.4541 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.64962 | 17 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 31.8229 | 0.42534 | 74.8174 | 31.8229 | 0.42534 | 74.8174 | 35.3145 | 0.47201 | 74.8174 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2027 | 221 | 221-1235F | Tier-3 | Tier-3---18 | 5--2 | 0.0489 | 0 | 100% | 236.1769 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.032017 | 0 | 0 | 0.032017 | 0 | 0 | 0.03553 | 0 | 0% | 0.16409 | 0.15597 | 1439.2989 | 2.105 | 1306.2711 | 130.9227 | 1514.2545 | 0 | 0 | 1514.2545 | 0%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 1.5002 | 11 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.7715 | 0.93698 | 1.8907 | 1.7715 | 0.93698 | 1.8907 | 2.0709 | 1.0953 | 1.8907 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 11.503 | 607 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 482.838 | 7.1847 | 67.204 | 482.838 | 7.1847 | 67.204 | 564.4431 | 8.399 | 67.204 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 2.7701 | 39 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 29.252 | 1.7301 | 16.9073 | 29.252 | 1.7301 | 16.9073 | 34.1959 | 2.0226 | 16.9073 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 13.4184 | 1097 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1378.2488 | 8.381 | 164.45 | 1378.2488 | 8.381 | 164.45 | 1611.1885 | 9.7974 | 164.45 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 10.907 | 484 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 392.8265 | 6.8124 | 57.6637 | 392.8265 | 6.8124 | 57.6637 | 459.2187 | 7.9637 | 57.6637 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2028 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 6.1667 | 154 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 680.7304 | 3.8516 | 176.7378 | 680.7304 | 3.8516 | 176.7378 | 795.7816 | 4.5026 | 176.7378 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2028 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 7.1517 | 253 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 291.2678 | 4.4669 | 65.206 | 291.2678 | 4.4669 | 65.206 | 340.4953 | 5.2218 | 65.206 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2028 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 1.4833 | 110 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 11.4677 | 0.92645 | 12.3781 | 11.4677 | 0.92645 | 12.3781 | 13.4059 | 1.083 | 12.3781 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 2.9682 | 235 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 297.6475 | 1.8539 | 160.5509 | 297.6475 | 1.8539 | 160.5509 | 347.9533 | 2.1672 | 160.5509 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2028 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.006061 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.25823 | 0.0037856 | 68.2142 | 0.25823 | 0.0037856 | 68.2142 | 0.30188 | 0.0044255 | 68.2142 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2028 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.05303 | 1 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 0.93446 | 0.033122 | 28.2128 | 0.93446 | 0.033122 | 28.2128 | 1.0924 | 0.03872 | 28.2128 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2028 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 0.91212 | 44 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.1096 | 0.5697 | 0.19239 | 0.1096 | 0.5697 | 0.19239 | 0.12813 | 0.66599 | 0.19239 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2028 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 10.9006 | 354 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 129.3787 | 6.8084 | 19.0028 | 129.3787 | 6.8084 | 19.0028 | 151.2452 | 7.9591 | 19.0028 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2028 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 2.4656 | 133 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 33.2772 | 1.54 | 21.609 | 33.2772 | 1.54 | 21.609 | 38.9015 | 1.8002 | 21.609 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2028 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 3.214 | 0 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 441.0941 | 2.0074 | 219.7307 | 441.0941 | 2.0074 | 219.7307 | 515.644 | 2.3467 | 219.7307 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2028 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 6.1051 | 1144 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 165.8433 | 3.8132 | 43.4921 | 165.8433 | 3.8132 | 43.4921 | 193.8727 | 4.4577 | 43.4921 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2028 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.68239 | 53 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 59.3317 | 0.42621 | 139.2073 | 59.3317 | 0.42621 | 139.2073 | 69.3594 | 0.49825 | 139.2073 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 14.6369 | 996 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1150.7453 | 9.142 | 125.874 | 1150.7453 | 9.142 | 125.874 | 1345.2344 | 10.6872 | 125.874 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 19.7983 | 971 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 186.6975 | 12.3658 | 15.0979 | 186.6975 | 12.3658 | 15.0979 | 218.2515 | 14.4557 | 15.0979 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 11.9253 | 973 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 238.9635 | 7.4484 | 32.0823 | 238.9635 | 7.4484 | 32.0823 | 279.3511 | 8.7073 | 32.0823 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 33.1318 | 3231 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 137.6937 | 20.6938 | 6.6539 | 137.6937 | 20.6938 | 6.6539 | 160.9655 | 24.1913 | 6.6539 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2028 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 16.5267 | 1132 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 157.9271 | 10.3224 | 15.2995 | 157.9271 | 10.3224 | 15.2995 | 184.6186 | 12.067 | 15.2995 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2028 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 0.5464 | 0 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 29.6034 | 0.34128 | 86.7434 | 29.6034 | 0.34128 | 86.7434 | 34.6067 | 0.39896 | 86.7434 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2028 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 0.4381 | 32 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.33114 | 0.27363 | 1.2102 | 0.33114 | 0.27363 | 1.2102 | 0.38711 | 0.31988 | 1.2102 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 11.0409 | 793 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 369.313 | 6.896 | 53.5546 | 369.313 | 6.896 | 53.5546 | 431.7311 | 8.0615 | 53.5546 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2028 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 27.7167 | 985 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 218.7933 | 17.3116 | 12.6386 | 218.7933 | 17.3116 | 12.6386 | 255.7719 | 20.2374 | 12.6386 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 4.0256 | 262 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16067 | 2.5144 | 0.063899 | 0.16067 | 2.5144 | 0.063899 | 0.18782 | 2.9393 | 0.063899 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 5.4265 | 741 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 499.4312 | 3.3893 | 147.3539 | 499.4312 | 3.3893 | 147.3539 | 583.8408 | 3.9622 | 147.3539 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 4.9148 | 635 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 30.6457 | 3.0697 | 9.9832 | 30.6457 | 3.0697 | 9.9832 | 35.8252 | 3.5886 | 9.9832 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2028 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 4.5371 | 0 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 85.4412 | 2.8338 | 30.1505 | 85.4412 | 2.8338 | 30.1505 | 99.8817 | 3.3128 | 30.1505 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2028 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 2.7532 | 47 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 218.3892 | 1.7196 | 126.9984 | 218.3892 | 1.7196 | 126.9984 | 255.2995 | 2.0103 | 126.9984 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 9.5078 | 558 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 525.5304 | 5.9384 | 88.4963 | 525.5304 | 5.9384 | 88.4963 | 614.3511 | 6.9421 | 88.4963 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2028 | 595 | 595-1454F | Tier-2 | Tier-2---15 | 3--4 | 0.5388 | 0 | 100% | 124.9246 | 83.27% | 16% | 0.7306% | 5.1495 | 0 | 0 | 5.1495 | 0 | 4.4701 | 0.33653 | 13.2829 | 4.4701 | 0.33653 | 13.2829 | 5.2256 | 0.39341 | 13.2829 | 4.122% | 0.018776 | 0.017847 | 6653.3471 | 1471.8841 | 978.4778 | 4202.9852 | 6711.3017 | 0 | 0 | 6711.3017 | 0.0001698%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 10.1674 | 900 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 238.4801 | 6.3504 | 37.5533 | 238.4801 | 6.3504 | 37.5533 | 278.7859 | 7.4237 | 37.5533 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2028 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 16.5478 | 1001 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 261.6837 | 10.3356 | 25.3188 | 261.6837 | 10.3356 | 25.3188 | 305.9112 | 12.0824 | 25.3188 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 10.9521 | 913 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 644.766 | 6.8405 | 94.2565 | 644.766 | 6.8405 | 94.2565 | 753.7388 | 7.9967 | 94.2565 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2028 | 834 | 834-887AE | Tier-2 | Tier-2---17 | 2--4 | 0.2229 | 0 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 3.435 | 0 | 0 | 3.435 | 0 | 2.9818 | 0.13922 | 21.4175 | 2.9818 | 0.13922 | 21.4175 | 3.4857 | 0.16275 | 21.4175 | 4.883% | 0.0050886 | 0.0048367 | 13824.3748 | 4928.7906 | 56.7151 | 8838.8691 | 13834.1342 | 0 | 0 | 13834.1342 | 0.0001133%
2028 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 5.0727 | 200 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 27.3601 | 3.1683 | 8.6354 | 27.3601 | 3.1683 | 8.6354 | 31.9842 | 3.7038 | 8.6354 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2028 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 18.3176 | 1095 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 453.1633 | 11.441 | 39.6088 | 453.1633 | 11.441 | 39.6088 | 529.7531 | 13.3746 | 39.6088 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 9.4852 | 908 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 501.116 | 5.9244 | 84.5854 | 501.116 | 5.9244 | 84.5854 | 585.8104 | 6.9257 | 84.5854 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 1.2773 | 46 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 24.4415 | 0.79777 | 30.6373 | 24.4415 | 0.79777 | 30.6373 | 28.5724 | 0.9326 | 30.6373 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2028 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 5.1553 | 245 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 75.9675 | 3.22 | 23.5927 | 75.9675 | 3.22 | 23.5927 | 88.8068 | 3.7642 | 23.5927 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 4.2257 | 150 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 79.9435 | 2.6394 | 30.2891 | 79.9435 | 2.6394 | 30.2891 | 93.4549 | 3.0854 | 30.2891 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 18.9327 | 1235 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 873.9661 | 11.8252 | 73.9072 | 873.9661 | 11.8252 | 73.9072 | 1021.6763 | 13.8238 | 73.9072 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 6.4307 | 308 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 231 | 4.0166 | 57.5119 | 231 | 4.0166 | 57.5119 | 270.0416 | 4.6954 | 57.5119 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2028 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 3.8006 | 169 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 342.5729 | 2.3738 | 144.3148 | 342.5729 | 2.3738 | 144.3148 | 400.4716 | 2.775 | 144.3148 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2028 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 7.0653 | 484 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 578.2628 | 4.4129 | 131.0383 | 578.2628 | 4.4129 | 131.0383 | 675.9958 | 5.1588 | 131.0383 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 6.825 | 1960 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 20.258 | 4.2628 | 4.7522 | 20.258 | 4.2628 | 4.7522 | 23.6818 | 4.9833 | 4.7522 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2028 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.56254 | 0 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.3253 | 0.35136 | 15.1564 | 5.3253 | 0.35136 | 15.1564 | 6.2253 | 0.41074 | 15.1564 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2028 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 2.4665 | 104 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 256.5911 | 1.5405 | 166.5592 | 256.5911 | 1.5405 | 166.5592 | 299.9579 | 1.8009 | 166.5592 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 5.4023 | 504 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 46.2745 | 3.3742 | 13.7142 | 46.2745 | 3.3742 | 13.7142 | 54.0954 | 3.9445 | 13.7142 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2028 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 12.4913 | 384 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 71.3031 | 7.8019 | 9.1392 | 71.3031 | 7.8019 | 9.1392 | 83.3541 | 9.1205 | 9.1392 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2028 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 6.96 | 531 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 41.3134 | 4.3472 | 9.5035 | 41.3134 | 4.3472 | 9.5035 | 48.2958 | 5.0819 | 9.5035 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 6.5853 | 30 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 55.6898 | 4.1131 | 13.5396 | 55.6898 | 4.1131 | 13.5396 | 65.102 | 4.8083 | 13.5396 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2028 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3.0366 | 18 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 48.5597 | 1.8966 | 25.6036 | 48.5597 | 1.8966 | 25.6036 | 56.7669 | 2.2171 | 25.6036 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2028 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.45755 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 57.582 | 0.28578 | 201.4889 | 57.582 | 0.28578 | 201.4889 | 67.3141 | 0.33408 | 201.4889 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2028 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 2.2489 | 0 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 21.0079 | 1.4046 | 14.9561 | 21.0079 | 1.4046 | 14.9561 | 24.5584 | 1.642 | 14.9561 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 6.4636 | 102 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 350.0629 | 4.0371 | 86.711 | 350.0629 | 4.0371 | 86.711 | 409.2275 | 4.7194 | 86.711 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2028 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 10.8632 | 1047 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 434.9987 | 6.7851 | 64.1113 | 434.9987 | 6.7851 | 64.1113 | 508.5185 | 7.9318 | 64.1113 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 2.4735 | 109 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 186.0759 | 1.5449 | 120.4425 | 186.0759 | 1.5449 | 120.4425 | 217.5249 | 1.806 | 120.4425 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 19.4561 | 1637 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 118.8605 | 12.152 | 9.7811 | 118.8605 | 12.152 | 9.7811 | 138.9493 | 14.2059 | 9.7811 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 5.3305 | 265 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 95.2503 | 3.3294 | 28.6091 | 95.2503 | 3.3294 | 28.6091 | 111.3487 | 3.8921 | 28.6091 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 2.3455 | 217 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 185.2886 | 1.465 | 126.4793 | 185.2886 | 1.465 | 126.4793 | 216.6045 | 1.7126 | 126.4793 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 2.4583 | 130 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 272.7233 | 1.5354 | 177.6183 | 272.7233 | 1.5354 | 177.6183 | 318.8167 | 1.795 | 177.6183 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2028 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.038636 | 0 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.71318 | 0.024132 | 29.5536 | 0.71318 | 0.024132 | 29.5536 | 0.83371 | 0.02821 | 29.5536 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 13.767 | 1095 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 547.9368 | 8.5987 | 63.7229 | 547.9368 | 8.5987 | 63.7229 | 640.5444 | 10.052 | 63.7229 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 3.6616 | 66 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 10.9026 | 2.287 | 4.7672 | 10.9026 | 2.287 | 4.7672 | 12.7452 | 2.6735 | 4.7672 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 12.7815 | 1809 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1153.6452 | 7.9832 | 144.5095 | 1153.6452 | 7.9832 | 144.5095 | 1348.6244 | 9.3324 | 144.5095 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 13.6103 | 587 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 104.999 | 8.5008 | 12.3516 | 104.999 | 8.5008 | 12.3516 | 122.745 | 9.9376 | 12.3516 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2028 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.057008 | 0 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.479 | 0.035607 | 97.7076 | 3.479 | 0.035607 | 97.7076 | 4.067 | 0.041625 | 97.7076 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 0.94167 | 3 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.7897 | 0.58816 | 1.3427 | 0.7897 | 0.58816 | 1.3427 | 0.92317 | 0.68756 | 1.3427 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2028 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 5.9186 | 504 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.80609 | 3.6967 | 0.21806 | 0.80609 | 3.6967 | 0.21806 | 0.94233 | 4.3214 | 0.21806 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2028 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 6.9741 | 633 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 806.4885 | 4.3559 | 185.1477 | 806.4885 | 4.3559 | 185.1477 | 942.7942 | 5.0921 | 185.1477 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2028 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 0.3653 | 62 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.52719 | 0.22816 | 2.3106 | 0.52719 | 0.22816 | 2.3106 | 0.61629 | 0.26672 | 2.3106 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2028 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.93788 | 186 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 2.8676 | 0.58579 | 4.8952 | 2.8676 | 0.58579 | 4.8952 | 3.3522 | 0.68479 | 4.8952 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2028 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 1.7432 | 329 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 21.9753 | 1.0888 | 20.1834 | 21.9753 | 1.0888 | 20.1834 | 25.6894 | 1.2728 | 20.1834 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 1.4693 | 14 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 86.9507 | 0.9177 | 94.7483 | 86.9507 | 0.9177 | 94.7483 | 101.6464 | 1.0728 | 94.7483 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2028 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.3089 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.1114 | 0.19294 | 10.9436 | 2.1114 | 0.19294 | 10.9436 | 2.4683 | 0.22555 | 10.9436 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2028 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 2.6153 | 70 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.1925 | 1.6335 | 1.3422 | 2.1925 | 1.6335 | 1.3422 | 2.5631 | 1.9096 | 1.3422 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2028 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.62576 | 68 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 9.128 | 0.39084 | 23.3546 | 9.128 | 0.39084 | 23.3546 | 10.6707 | 0.4569 | 23.3546 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2028 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 6.2526 | 357 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 176.3919 | 3.9053 | 45.167 | 176.3919 | 3.9053 | 45.167 | 206.2042 | 4.5654 | 45.167 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2028 | 308 | 308-485AE | Tier-2 | Tier-2---15 | 4--3 | 0.7398 | 5 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.217 | 0 | 0 | 0.217 | 0 | 0.18837 | 0.46207 | 0.40766 | 0.18837 | 0.46207 | 0.40766 | 0.2202 | 0.54017 | 0.40766 | 0.1374% | 0.034738 | 0.033018 | 4547.6785 | 25.2626 | 4047.4864 | 474.9295 | 4777.9399 | 0 | 0 | 4777.9399 | 7.156e-06%
2028 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 2.4644 | 81 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 20.2007 | 1.5392 | 13.1238 | 20.2007 | 1.5392 | 13.1238 | 23.6149 | 1.7994 | 13.1238 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2028 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 8.4758 | 325 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 76.2372 | 5.2939 | 14.401 | 76.2372 | 5.2939 | 14.401 | 89.1222 | 6.1886 | 14.401 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 10.6674 | 415 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 851.8508 | 6.6627 | 127.8529 | 851.8508 | 6.6627 | 127.8529 | 995.8233 | 7.7888 | 127.8529 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2028 | 94 | 94-24F | Tier-2 | Tier-2---18 | 3--3 | 4.1867 | 0 | 100% | 46.367 | 91.68% | 0% | 8.321% | 2.1042 | 0 | 0 | 2.1042 | 0 | 1.8266 | 2.615 | 0.69851 | 1.8266 | 2.615 | 0.69851 | 2.1353 | 3.0569 | 0.69851 | 4.538% | 0.020922 | 0.019886 | 2216.1834 | 511.0324 | 89.3586 | 1615.7924 | 2225.7865 | 0 | 0 | 2225.7865 | 6.939e-05%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 4.8975 | 159 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 60.5501 | 3.0589 | 19.7945 | 60.5501 | 3.0589 | 19.7945 | 70.7837 | 3.5759 | 19.7945 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2028 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 2.7176 | 182 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 6.9398 | 1.6974 | 4.0885 | 6.9398 | 1.6974 | 4.0885 | 8.1127 | 1.9843 | 4.0885 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2028 | 454 | 454-49F | Tier-2 | Tier-2---13 | 4--3 | 0.4782 | 0 | 100% | 292.9743 | 76.06% | 23.59% | 0.3558% | 11.0299 | 0 | 0 | 11.0299 | 0 | 9.5746 | 0.29868 | 32.0567 | 9.5746 | 0.29868 | 32.0567 | 11.1929 | 0.34916 | 32.0567 | 3.765% | 0.077203 | 0.073382 | 3794.8464 | 847.9473 | 816.929 | 2129.9701 | 3842.1656 | 0 | 0 | 3842.1656 | 0.0003637%
2028 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.01875 | 0 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.6389 | 0.011711 | 54.5554 | 0.6389 | 0.011711 | 54.5554 | 0.74688 | 0.01369 | 54.5554 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 0.095455 | 52 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.6305 | 0.05962 | 27.3479 | 1.6305 | 0.05962 | 27.3479 | 1.9061 | 0.069697 | 27.3479 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 7.6085 | 759 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 125.5186 | 4.7522 | 26.4127 | 125.5186 | 4.7522 | 26.4127 | 146.7327 | 5.5554 | 26.4127 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2028 | 205 | 205-1550 | Tier-2 | Tier-2---15 | 2--4 | 0.97858 | 11 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 6.0476 | 0 | 0 | 6.0476 | 0 | 5.2497 | 0.61121 | 8.589 | 5.2497 | 0.61121 | 8.589 | 6.137 | 0.71451 | 8.589 | 4.877% | 0.008789 | 0.0083539 | 14109.2738 | 2221.4405 | 309.7116 | 11578.1217 | 14120.1329 | 0 | 0 | 14120.1329 | 0.0001994%
2028 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.47178 | 4 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 4.9095 | 0.29467 | 16.661 | 4.9095 | 0.29467 | 16.661 | 5.7392 | 0.34447 | 16.661 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 6.7553 | 1534 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 123.2314 | 4.2193 | 29.2065 | 123.2314 | 4.2193 | 29.2065 | 144.0589 | 4.9324 | 29.2065 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2028 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.10398 | 8 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 10.906 | 0.064943 | 167.9317 | 10.906 | 0.064943 | 167.9317 | 12.7492 | 0.075919 | 167.9317 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 12.5093 | 734 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 372.002 | 7.8132 | 47.6122 | 372.002 | 7.8132 | 47.6122 | 434.8746 | 9.1337 | 47.6122 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2028 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 6.6007 | 793 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 135.3647 | 4.1227 | 32.8336 | 135.3647 | 4.1227 | 32.8336 | 158.2428 | 4.8195 | 32.8336 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2028 | 197 | 197-1150F | Tier-2 | Tier-2---15 | 3--4 | 1.3604 | 3 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 9.0248 | 0 | 0 | 9.0248 | 0 | 7.8341 | 0.8497 | 9.2198 | 7.8341 | 0.8497 | 9.2198 | 9.1582 | 0.99331 | 9.2198 | 4.917% | 0.021777 | 0.020699 | 8428.1597 | 1361.8326 | 10.8364 | 7055.4907 | 8431.076 | 0 | 0 | 8431.076 | 0.0002976%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 13.7784 | 951 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 77.1998 | 8.6059 | 8.9706 | 77.1998 | 8.6059 | 8.9706 | 90.2474 | 10.0603 | 8.9706 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 5.0748 | 149 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 167.4248 | 3.1697 | 52.8211 | 167.4248 | 3.1697 | 52.8211 | 195.7215 | 3.7054 | 52.8211 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2028 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 3.0297 | 20 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 50.7035 | 1.8923 | 26.7943 | 50.7035 | 1.8923 | 26.7943 | 59.2729 | 2.2121 | 26.7943 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2028 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 5.1365 | 315 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 107.8587 | 3.2082 | 33.6194 | 107.8587 | 3.2082 | 33.6194 | 126.0881 | 3.7505 | 33.6194 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 10.0072 | 260 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 64.0856 | 6.2504 | 10.2531 | 64.0856 | 6.2504 | 10.2531 | 74.9168 | 7.3068 | 10.2531 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 3.7138 | 156 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 95.786 | 2.3196 | 41.2937 | 95.786 | 2.3196 | 41.2937 | 111.9749 | 2.7117 | 41.2937 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 3.1481 | 153 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 133.2569 | 1.9662 | 67.7721 | 133.2569 | 1.9662 | 67.7721 | 155.7788 | 2.2986 | 67.7721 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 4.4941 | 222 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 391.8645 | 2.807 | 139.6036 | 391.8645 | 2.807 | 139.6036 | 458.094 | 3.2814 | 139.6036 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2028 | 241 | CB 241 | Tier-2 | Tier-2---11 | 5--4 | 1.5013 | 0 | 100% | 614.4843 | 5.233% | 94.45% | 0.3166% | 1.5918 | 0 | 0 | 1.5918 | 0 | 1.3818 | 0.9377 | 1.4736 | 1.3818 | 0.9377 | 1.4736 | 1.6153 | 1.0962 | 1.4736 | 0.259% | 0.096356 | 0.091586 | 6377.2296 | 31.8975 | 5684.1218 | 661.2103 | 6691.9621 | 0 | 0 | 6691.9621 | 5.249e-05%
2028 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 14.1729 | 537 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 447.4138 | 8.8522 | 50.5425 | 447.4138 | 8.8522 | 50.5425 | 523.0318 | 10.3484 | 50.5425 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2028 | 855 | 855-46AE | Tier-2 | Tier-2---15 | 1--5 | 0.25303 | 1 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 9.3224 | 0 | 0 | 9.3224 | 0 | 8.0925 | 0.15804 | 51.2053 | 8.0925 | 0.15804 | 51.2053 | 9.4602 | 0.18475 | 51.2053 | 4.944% | 0.0010888 | 0.0010349 | 173174.957 | 50966.8705 | 22.9996 | 122185.0869 | 173185.5197 | 0 | 0 | 173185.5197 | 0.0003074%
2028 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 3.6236 | 238 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.1658 | 2.2633 | 2.2824 | 5.1658 | 2.2633 | 2.2824 | 6.0389 | 2.6458 | 2.2824 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2028 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.12822 | 0 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 13.3286 | 0.080085 | 166.4305 | 13.3286 | 0.080085 | 166.4305 | 15.5812 | 0.09362 | 166.4305 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2028 | 928 | CB 928 | Tier-2 | Tier-2---7 | 4--5 | 3.1426 | 3 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 65.3395 | 0 | 0 | 65.3395 | 0 | 56.719 | 1.9628 | 28.8963 | 56.719 | 1.9628 | 28.8963 | 66.3051 | 2.2946 | 28.8963 | 3.948% | 0.057199 | 0.054367 | 28934.4603 | 4597.4585 | 5524.6499 | 18812.3519 | 29239.4879 | 0 | 0 | 29239.4879 | 0.002155%
2028 | 1202 | 1202-9 | Tier-2 | Tier-2---17 | 2--4 | 0.7689 | 0 | 100% | 73.4421 | 96.84% | 0% | 3.16% | 3.5205 | 0 | 0 | 3.5205 | 0 | 3.056 | 0.48025 | 6.3635 | 3.056 | 0.48025 | 6.3635 | 3.5725 | 0.56141 | 6.3635 | 4.794% | 0.01182 | 0.011235 | 6213.48 | 1453.8319 | 498.5132 | 4261.1349 | 6223.7055 | 0 | 0 | 6223.7055 | 0.0001161%
2028 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 24.8581 | 448 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 436.6473 | 15.5261 | 28.1234 | 436.6473 | 15.5261 | 28.1234 | 510.4457 | 18.1502 | 28.1234 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2028 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 0.42306 | 23 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.45015 | 0.26424 | 1.7036 | 0.45015 | 0.26424 | 1.7036 | 0.52622 | 0.3089 | 1.7036 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 13.0331 | 1531 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 794.7222 | 8.1404 | 97.6275 | 794.7222 | 8.1404 | 97.6275 | 929.0394 | 9.5162 | 97.6275 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2028 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 8.4165 | 712 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 494.131 | 5.2569 | 93.9972 | 494.131 | 5.2569 | 93.9972 | 577.6448 | 6.1453 | 93.9972 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 11.5724 | 1687 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 112.9854 | 7.228 | 15.6317 | 112.9854 | 7.228 | 15.6317 | 132.0812 | 8.4496 | 15.6317 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 16.5898 | 1991 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 668.2095 | 10.3618 | 64.4877 | 668.2095 | 10.3618 | 64.4877 | 781.1445 | 12.1131 | 64.4877 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 3.9667 | 215 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 80.4921 | 2.4775 | 32.4888 | 80.4921 | 2.4775 | 32.4888 | 94.0962 | 2.8963 | 32.4888 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2028 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 4.5633 | 392 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 419.5312 | 2.8502 | 147.1955 | 419.5312 | 2.8502 | 147.1955 | 490.4368 | 3.3319 | 147.1955 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2028 | 178 | 178-982 | Tier-2 | Tier-2---21 | 1--1 | 0.68407 | 9 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0063254 | 0 | 0 | 0.0063254 | 0 | 0.0054908 | 0.42727 | 0.012851 | 0.0054908 | 0.42727 | 0.012851 | 0.0064188 | 0.49948 | 0.012851 | 0.6625% | 0.0033454 | 0.0031798 | 285.4035 | 0.62363 | 58.6739 | 226.106 | 298.2775 | 0 | 0 | 298.2775 | 2.086e-07%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 4.3521 | 410 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 134.4194 | 2.7183 | 49.4506 | 134.4194 | 2.7183 | 49.4506 | 157.1378 | 3.1777 | 49.4506 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2028 | 189 | 189-750 | Tier-2 | Tier-2---21 | 1--2 | 0.1718 | 0 | 100% | 1.7248 | 88.21% | 0% | 11.79% | 0.075309 | 0 | 0 | 0.075309 | 0 | 0.065373 | 0.1073 | 0.60923 | 0.065373 | 0.1073 | 0.60923 | 0.076422 | 0.12544 | 0.60923 | 4.366% | 0.001013 | 0.00096286 | 1702.705 | 2.2891 | 1507.0729 | 193.3431 | 1713.1637 | 0 | 0 | 1713.1637 | 2.483e-06%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 11.4998 | 49 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 58.6432 | 7.1826 | 8.1646 | 58.6432 | 7.1826 | 8.1646 | 68.5546 | 8.3966 | 8.1646 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2028 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 1.5879 | 35 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 107.4458 | 0.9918 | 108.3344 | 107.4458 | 0.9918 | 108.3344 | 125.6054 | 1.1594 | 108.3344 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 2.2354 | 22 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 91.8692 | 1.3962 | 65.7983 | 91.8692 | 1.3962 | 65.7983 | 107.3962 | 1.6322 | 65.7983 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2028 | 790 | CB 790 | Tier-2 | Tier-2---10 | 4--4 | 0.0892 | 0 | 100% | 864.253 | 62.67% | 37.21% | 0.1185% | 26.812 | 0 | 0 | 26.812 | 0 | 23.2746 | 0.055713 | 417.7555 | 23.2746 | 0.055713 | 417.7555 | 27.2082 | 0.06513 | 417.7555 | 3.102% | 0.092624 | 0.088039 | 9330.8076 | 1033.7577 | 3102.9179 | 5194.132 | 9512.1882 | 0 | 0 | 9512.1882 | 0.0008842%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 0.78689 | 20 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.79526 | 0.49148 | 1.6181 | 0.79526 | 0.49148 | 1.6181 | 0.92967 | 0.57455 | 1.6181 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2028 | 454 | 454-53F | Tier-2 | Tier-2---13 | 4--3 | 0.3076 | 0 | 100% | 272.5399 | 0.7301% | 99.1% | 0.1654% | 0.098502 | 0 | 0 | 0.098502 | 0 | 0.085506 | 0.19212 | 0.44506 | 0.085506 | 0.19212 | 0.44506 | 0.099958 | 0.22459 | 0.44506 | 0.03614% | 0.073094 | 0.069476 | 3728.6015 | 9.5009 | 3385.0726 | 334.0281 | 3921.3613 | 0 | 0 | 3921.3613 | 3.248e-06%
2028 | 197 | CB 197 | Tier-2 | Tier-2---21 | 1--4 | 0.097159 | 0 | 100% | 1.9198 | 98.18% | 0% | 1.817% | 0.093305 | 0 | 0 | 0.093305 | 0 | 0.080995 | 0.060684 | 1.3347 | 0.080995 | 0.060684 | 1.3347 | 0.094684 | 0.070941 | 1.3347 | 4.86% | 0.000314 | 0.00029846 | 6114.1 | 461.2612 | 3185.8611 | 2466.9777 | 6119.8844 | 0 | 0 | 6119.8844 | 3.077e-06%
2028 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 7.2309 | 81 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 224.4292 | 4.5163 | 49.693 | 224.4292 | 4.5163 | 49.693 | 262.3603 | 5.2796 | 49.693 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 7.3388 | 536 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 68.097 | 4.5837 | 14.8562 | 68.097 | 4.5837 | 14.8562 | 79.6061 | 5.3585 | 14.8562 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 7.806 | 484 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 716.0815 | 4.8756 | 146.8715 | 716.0815 | 4.8756 | 146.8715 | 837.1074 | 5.6996 | 146.8715 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2028 | 395 | 395-33R | Tier-2 | Tier-2---11 | 4--3 | 0.2491 | 0 | 100% | 396.9757 | 0.1391% | 99.74% | 0.1245% | 0.02734 | 0 | 0 | 0.02734 | 0 | 0.023733 | 0.15559 | 0.15254 | 0.023733 | 0.15559 | 0.15254 | 0.027744 | 0.18188 | 0.15254 | 0.006887% | 0.092102 | 0.087543 | 4310.174 | 6.5289 | 3952.6979 | 350.9472 | 4534.3264 | 0 | 0 | 4534.3264 | 9.016e-07%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 5.2882 | 192 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 24.6681 | 3.303 | 7.4685 | 24.6681 | 3.303 | 7.4685 | 28.8373 | 3.8612 | 7.4685 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 11.8401 | 425 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 113.5276 | 7.3952 | 15.3515 | 113.5276 | 7.3952 | 15.3515 | 132.715 | 8.6451 | 15.3515 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 14.3572 | 1385 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 207.223 | 8.9674 | 23.1086 | 207.223 | 8.9674 | 23.1086 | 242.246 | 10.483 | 23.1086 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 17.3068 | 1218 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 228.5893 | 10.8096 | 21.1468 | 228.5893 | 10.8096 | 21.1468 | 267.2235 | 12.6366 | 21.1468 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 1.8014 | 93 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.0837 | 1.1251 | 1.852 | 2.0837 | 1.1251 | 1.852 | 2.4359 | 1.3153 | 1.852 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2028 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 9.8927 | 661 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 213.6481 | 6.1789 | 34.5773 | 213.6481 | 6.1789 | 34.5773 | 249.7571 | 7.2231 | 34.5773 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 4.1559 | 590 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 195.54 | 2.5957 | 75.3311 | 195.54 | 2.5957 | 75.3311 | 228.5885 | 3.0344 | 75.3311 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2028 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 15.3767 | 427 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 46.128 | 9.6041 | 4.8029 | 46.128 | 9.6041 | 4.8029 | 53.9241 | 11.2273 | 4.8029 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 18.1587 | 305 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 65.5189 | 11.3417 | 5.7768 | 65.5189 | 11.3417 | 5.7768 | 76.5924 | 13.2586 | 5.7768 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2028 | 770 | 770-259R | Tier-2 | Tier-2---17 | 2--3 | 1.3913 | 0 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 2.0515 | 0 | 0 | 2.0515 | 0 | 1.7809 | 0.86898 | 2.0494 | 1.7809 | 0.86898 | 2.0494 | 2.0819 | 1.0159 | 2.0494 | 4.826% | 0.010605 | 0.01008 | 4008.538 | 787.4023 | 25.9222 | 3195.2135 | 4013.7737 | 0 | 0 | 4013.7737 | 6.765e-05%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 22.0576 | 1796 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 147.7871 | 13.7769 | 10.7271 | 147.7871 | 13.7769 | 10.7271 | 172.7648 | 16.1054 | 10.7271 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2028 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 8.5739 | 486 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 234.4344 | 5.3551 | 43.7774 | 234.4344 | 5.3551 | 43.7774 | 274.0565 | 6.2602 | 43.7774 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2028 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 8.1708 | 346 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 127.5811 | 5.1034 | 24.9991 | 127.5811 | 5.1034 | 24.9991 | 149.1437 | 5.966 | 24.9991 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2028 | 504 | 504-287R | Tier-2 | Tier-2---12 | 4--4 | 0.7358 | 0 | 100% | 501.8283 | 98.94% | 0% | 1.063% | 24.5765 | 0 | 0 | 24.5765 | 0 | 21.334 | 0.45957 | 46.4213 | 21.334 | 0.45957 | 46.4213 | 24.9397 | 0.53725 | 46.4213 | 4.897% | 0.033132 | 0.031492 | 15146.1514 | 2418.4341 | 53.5553 | 12674.162 | 15154.5352 | 0 | 0 | 15154.5352 | 0.0008104%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 1.2528 | 22 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 83.1107 | 0.78251 | 106.2102 | 83.1107 | 0.78251 | 106.2102 | 97.1573 | 0.91476 | 106.2102 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 2.4038 | 61 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 62.3151 | 1.5014 | 41.5052 | 62.3151 | 1.5014 | 41.5052 | 72.8471 | 1.7551 | 41.5052 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2028 | 968 | 968-476F | Tier-2 | Tier-2---17 | 3--3 | 1.9167 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 2.9977 | 0 | 0 | 2.9977 | 0 | 2.6022 | 1.1971 | 2.1737 | 2.6022 | 1.1971 | 2.1737 | 3.042 | 1.3995 | 2.1737 | 4.797% | 0.015315 | 0.014557 | 4080.3921 | 1049.3579 | 36.5623 | 2994.4719 | 4086.964 | 0 | 0 | 4086.964 | 9.885e-05%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 5.9518 | 1034 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 386.2992 | 3.7174 | 103.9164 | 386.2992 | 3.7174 | 103.9164 | 451.5881 | 4.3457 | 103.9164 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 2.2803 | 79 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.1324 | 1.4242 | 0.79512 | 1.1324 | 1.4242 | 0.79512 | 1.3238 | 1.6649 | 0.79512 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 7.8388 | 373 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 389.681 | 4.896 | 79.5911 | 389.681 | 4.896 | 79.5911 | 455.5415 | 5.7235 | 79.5911 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2028 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 17.9011 | 1149 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 479.2248 | 11.1808 | 42.8612 | 479.2248 | 11.1808 | 42.8612 | 560.2193 | 13.0705 | 42.8612 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2028 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 11.6007 | 312 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 5.4765 | 7.2457 | 0.75583 | 5.4765 | 7.2457 | 0.75583 | 6.4021 | 8.4703 | 0.75583 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 3.4445 | 84 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 46.0982 | 2.1514 | 21.4269 | 46.0982 | 2.1514 | 21.4269 | 53.8893 | 2.515 | 21.4269 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2028 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | 4--1 | 0.28182 | 0 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.15233 | 0 | 0 | 0.15233 | 0 | 0.13223 | 0.17602 | 0.75121 | 0.13223 | 0.17602 | 0.75121 | 0.15458 | 0.20577 | 0.75121 | 0.8348% | 0.061771 | 0.058714 | 295.3886 | 6.838 | 193.9385 | 94.612 | 308.1774 | 0 | 0 | 308.1774 | 5.023e-06%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 6.1881 | 443 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 222.4503 | 3.865 | 57.5546 | 222.4503 | 3.865 | 57.5546 | 260.047 | 4.5183 | 57.5546 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2028 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | 2--4 | 1.5301 | 0 | 100% | 70.6534 | 98.66% | 0% | 1.337% | 3.4506 | 0 | 0 | 3.4506 | 0 | 2.9953 | 0.95569 | 3.1342 | 2.9953 | 0.95569 | 3.1342 | 3.5016 | 1.1172 | 3.1342 | 4.884% | 0.0070442 | 0.0066955 | 10030.0143 | 2447.2684 | 423.376 | 7159.37 | 10036.9961 | 0 | 0 | 10036.9961 | 0.0001138%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 16.0076 | 985 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 897.0119 | 9.9982 | 89.7177 | 897.0119 | 9.9982 | 89.7177 | 1048.6171 | 11.688 | 89.7177 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 12.6949 | 1098 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 290.1396 | 7.9291 | 36.5917 | 290.1396 | 7.9291 | 36.5917 | 339.1765 | 9.2692 | 36.5917 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 6.6053 | 250 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 166.611 | 4.1256 | 40.3845 | 166.611 | 4.1256 | 40.3845 | 194.7701 | 4.8229 | 40.3845 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 1.1019 | 44 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 23.3784 | 0.68823 | 33.9689 | 23.3784 | 0.68823 | 33.9689 | 27.3297 | 0.80455 | 33.9689 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 4.3966 | 75 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 555.0452 | 2.7461 | 202.1247 | 555.0452 | 2.7461 | 202.1247 | 648.8541 | 3.2102 | 202.1247 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2028 | 312 | 312-40F | Tier-2 | Tier-2---20 | 3--2 | 0.0492 | 0 | 100% | 9.4163 | 0.07625% | 99.1% | 0.8244% | 0.00035539 | 0 | 0 | 0.00035539 | 0 | 0.0003085 | 0.03073 | 0.010039 | 0.0003085 | 0.03073 | 0.010039 | 0.00036064 | 0.035923 | 0.010039 | 0.003774% | 0.017172 | 0.016322 | 548.3384 | 0.98367 | 493.2185 | 54.1362 | 576.8729 | 0 | 0 | 576.8729 | 1.172e-08%
2028 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 0.089364 | 9 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.7644 | 0.055816 | 31.6113 | 1.7644 | 0.055816 | 31.6113 | 2.0626 | 0.065249 | 31.6113 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 14.1159 | 1226 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 73.9791 | 8.8167 | 8.3908 | 73.9791 | 8.8167 | 8.3908 | 86.4824 | 10.3068 | 8.3908 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 1.2536 | 124 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.0457 | 0.783 | 5.1669 | 4.0457 | 0.783 | 5.1669 | 4.7294 | 0.91534 | 5.1669 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 2.5449 | 185 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 15.0577 | 1.5895 | 9.473 | 15.0577 | 1.5895 | 9.473 | 17.6026 | 1.8582 | 9.473 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2028 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.03428 | 0 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.0797 | 0.021411 | 50.4288 | 1.0797 | 0.021411 | 50.4288 | 1.2622 | 0.02503 | 50.4288 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2028 | 331 | CB 331 | Tier-2 | Tier-2---14 | 2--5 | 2.8949 | 2 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 12.8498 | 0 | 0 | 12.8498 | 0 | 11.1545 | 1.8081 | 6.1691 | 11.1545 | 1.8081 | 6.1691 | 13.0397 | 2.1137 | 6.1691 | 4.919% | 0.010352 | 0.0098396 | 25232.8512 | 3536.4388 | 3219.2744 | 18477.138 | 25240.9927 | 0 | 0 | 25240.9927 | 0.0004237%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 16.7242 | 1029 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1315.706 | 10.4458 | 125.9558 | 1315.706 | 10.4458 | 125.9558 | 1538.0753 | 12.2112 | 125.9558 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2028 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 2.574 | 82 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 31.3708 | 1.6077 | 19.5129 | 31.3708 | 1.6077 | 19.5129 | 36.6728 | 1.8794 | 19.5129 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 6.3644 | 329 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 253.7687 | 3.9751 | 63.8395 | 253.7687 | 3.9751 | 63.8395 | 296.6585 | 4.6469 | 63.8395 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2028 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 2.267 | 47 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 38.9439 | 1.416 | 27.5033 | 38.9439 | 1.416 | 27.5033 | 45.5258 | 1.6553 | 27.5033 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 5.5445 | 309 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 53.4487 | 3.463 | 15.434 | 53.4487 | 3.463 | 15.434 | 62.4822 | 4.0483 | 15.434 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 9.1409 | 791 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 145.7841 | 5.7093 | 25.5344 | 145.7841 | 5.7093 | 25.5344 | 170.4233 | 6.6743 | 25.5344 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 9.5874 | 678 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 41.4677 | 5.9882 | 6.9249 | 41.4677 | 5.9882 | 6.9249 | 48.4762 | 7.0002 | 6.9249 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2028 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.054356 | 0 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.32972 | 0.03395 | 9.7118 | 0.32972 | 0.03395 | 9.7118 | 0.38544 | 0.039688 | 9.7118 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 0.74429 | 33 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 11.7557 | 0.46488 | 25.2876 | 11.7557 | 0.46488 | 25.2876 | 13.7425 | 0.54345 | 25.2876 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2028 | 196 | CB 196 | Tier-2 | Tier-2---15 | 3--4 | 0.29696 | 0 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.18155 | 0.18548 | 0.97884 | 0.18155 | 0.18548 | 0.97884 | 0.21224 | 0.21683 | 0.97884 | 0.1555% | 0.019464 | 0.018501 | 6908.5051 | 30.9312 | 5935.5679 | 942.006 | 7256.9805 | 0 | 0 | 7256.9805 | 6.897e-06%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 10.0377 | 551 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 370.166 | 6.2694 | 59.043 | 370.166 | 6.2694 | 59.043 | 432.7283 | 7.329 | 59.043 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2028 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 0.043939 | 1 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.32156 | 0.027444 | 11.7171 | 0.32156 | 0.027444 | 11.7171 | 0.37591 | 0.032082 | 11.7171 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 4.4118 | 230 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.5339 | 2.7555 | 0.55666 | 1.5339 | 2.7555 | 0.55666 | 1.7931 | 3.2213 | 0.55666 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2028 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.4697 | 4 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 4.6334 | 0.29337 | 15.7937 | 4.6334 | 0.29337 | 15.7937 | 5.4165 | 0.34295 | 15.7937 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2028 | 311 | 311-14R | Tier-2 | Tier-2---14 | 3--4 | 0.75338 | 26 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 2.2455 | 0 | 0 | 2.2455 | 0 | 1.9492 | 0.47055 | 4.1425 | 1.9492 | 0.47055 | 4.1425 | 2.2787 | 0.55008 | 4.1425 | 0.8058% | 0.018935 | 0.017998 | 14715.9264 | 335.1634 | 11691.6167 | 2689.1463 | 15357.5365 | 0 | 0 | 15357.5365 | 7.405e-05%
2028 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 10.606 | 600 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 252.5151 | 6.6244 | 38.1188 | 252.5151 | 6.6244 | 38.1188 | 295.1931 | 7.744 | 38.1188 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 2.911 | 8 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 1.866 | 1.8182 | 1.0263 | 1.866 | 1.8182 | 1.0263 | 2.1814 | 2.1254 | 1.0263 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 1.375 | 58 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 117.6384 | 0.85878 | 136.9825 | 117.6384 | 0.85878 | 136.9825 | 137.5206 | 1.0039 | 136.9825 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 3.7273 | 352 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 336.3948 | 2.328 | 144.4993 | 336.3948 | 2.328 | 144.4993 | 393.2494 | 2.7215 | 144.4993 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 17.3898 | 266 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 20.3082 | 10.8615 | 1.8697 | 20.3082 | 10.8615 | 1.8697 | 23.7405 | 12.6972 | 1.8697 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 2.6099 | 93 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 83.1383 | 1.6301 | 51.0021 | 83.1383 | 1.6301 | 51.0021 | 97.1896 | 1.9056 | 51.0021 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 22.2475 | 1846 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 439.9478 | 13.8955 | 31.6611 | 439.9478 | 13.8955 | 31.6611 | 514.3039 | 16.244 | 31.6611 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 0.60374 | 80 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 12.3817 | 0.37709 | 32.8349 | 12.3817 | 0.37709 | 32.8349 | 14.4744 | 0.44082 | 32.8349 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 5.1074 | 161 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 489.8651 | 3.19 | 153.5625 | 489.8651 | 3.19 | 153.5625 | 572.6579 | 3.7292 | 153.5625 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 15.5693 | 641 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 154.5823 | 9.7244 | 15.8963 | 154.5823 | 9.7244 | 15.8963 | 180.7085 | 11.3679 | 15.8963 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2028 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 5.0178 | 495 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 252.094 | 3.1341 | 80.4371 | 252.094 | 3.1341 | 80.4371 | 294.7007 | 3.6637 | 80.4371 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2028 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 10.1766 | 1320 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 666.1338 | 6.3562 | 104.8011 | 666.1338 | 6.3562 | 104.8011 | 778.718 | 7.4304 | 104.8011 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2028 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 0.005871 | 7 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.074294 | 0.003667 | 20.2603 | 0.074294 | 0.003667 | 20.2603 | 0.08685 | 0.0042867 | 20.2603 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 7.3438 | 786 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 294.1909 | 4.5868 | 64.1379 | 294.1909 | 4.5868 | 64.1379 | 343.9125 | 5.3621 | 64.1379 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 1.0739 | 192 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 8.737 | 0.67074 | 13.026 | 8.737 | 0.67074 | 13.026 | 10.2137 | 0.7841 | 13.026 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 2.3892 | 150 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 184.5979 | 1.4923 | 123.7014 | 184.5979 | 1.4923 | 123.7014 | 215.797 | 1.7445 | 123.7014 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2028 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 11.1993 | 175 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 64.3194 | 6.9949 | 9.1951 | 64.3194 | 6.9949 | 9.1951 | 75.1902 | 8.1772 | 9.1951 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 12.6807 | 874 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 148.7534 | 7.9202 | 18.7814 | 148.7534 | 7.9202 | 18.7814 | 173.8944 | 9.2589 | 18.7814 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2028 | 92 | 92-619F | Tier-2 | Tier-2---14 | 3--4 | 1.454 | 0 | 100% | 202.8689 | 46.88% | 52.08% | 1.034% | 4.708 | 0 | 0 | 4.708 | 0 | 4.0869 | 0.90815 | 4.5002 | 4.0869 | 0.90815 | 4.5002 | 4.7776 | 1.0616 | 4.5002 | 2.321% | 0.015617 | 0.014844 | 12990.5937 | 1279.3739 | 6200.2786 | 5510.9412 | 13349.9397 | 0 | 0 | 13349.9397 | 0.0001553%
2028 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 4.1122 | 503 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 354.0047 | 2.5684 | 137.8304 | 354.0047 | 2.5684 | 137.8304 | 413.8355 | 3.0025 | 137.8304 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 12.1511 | 530 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 159.313 | 7.5895 | 20.9913 | 159.313 | 7.5895 | 20.9913 | 186.2387 | 8.8722 | 20.9913 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 1.6021 | 37 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 25.9816 | 1.0006 | 25.9649 | 25.9816 | 1.0006 | 25.9649 | 30.3728 | 1.1698 | 25.9649 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2028 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 3.7494 | 966 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 16.8278 | 2.3419 | 7.1857 | 16.8278 | 2.3419 | 7.1857 | 19.6719 | 2.7377 | 7.1857 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 6.1581 | 318 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 145.4142 | 3.8463 | 37.8063 | 145.4142 | 3.8463 | 37.8063 | 169.9908 | 4.4964 | 37.8063 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 6.9867 | 120 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 61.8315 | 4.3638 | 14.1691 | 61.8315 | 4.3638 | 14.1691 | 72.2817 | 5.1014 | 14.1691 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 14.6288 | 358 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 36.7962 | 9.137 | 4.0272 | 36.7962 | 9.137 | 4.0272 | 43.0152 | 10.6812 | 4.0272 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 8.4832 | 264 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 216.5332 | 5.2985 | 40.867 | 216.5332 | 5.2985 | 40.867 | 253.1298 | 6.194 | 40.867 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 8.4771 | 489 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 598.4272 | 5.2947 | 113.0234 | 598.4272 | 5.2947 | 113.0234 | 699.5682 | 6.1896 | 113.0234 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2028 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 15.7168 | 1458 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1078.5839 | 9.8166 | 109.874 | 1078.5839 | 9.8166 | 109.874 | 1260.8769 | 11.4757 | 109.874 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 2.7396 | 153 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 59.5336 | 1.7111 | 34.7919 | 59.5336 | 1.7111 | 34.7919 | 69.5955 | 2.0003 | 34.7919 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2028 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.011364 | 0 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.029751 | 0.0070978 | 4.1915 | 0.029751 | 0.0070978 | 4.1915 | 0.034779 | 0.0082974 | 4.1915 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2028 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.19716 | 0 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.35 | 0.12314 | 27.2044 | 3.35 | 0.12314 | 27.2044 | 3.9162 | 0.14396 | 27.2044 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 7.6936 | 496 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 86.4204 | 4.8053 | 17.9843 | 86.4204 | 4.8053 | 17.9843 | 101.0265 | 5.6175 | 17.9843 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 5.4881 | 1448 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 63.3943 | 3.4278 | 18.4942 | 63.3943 | 3.4278 | 18.4942 | 74.1087 | 4.0071 | 18.4942 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 24.1038 | 1342 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 672.6642 | 15.055 | 44.6805 | 672.6642 | 15.055 | 44.6805 | 786.3521 | 17.5995 | 44.6805 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2028 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 2.3543 | 108 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 13.5581 | 1.4705 | 9.2201 | 13.5581 | 1.4705 | 9.2201 | 15.8496 | 1.719 | 9.2201 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 19.582 | 1232 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1137.4651 | 12.2307 | 93.0008 | 1137.4651 | 12.2307 | 93.0008 | 1329.7097 | 14.2978 | 93.0008 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 1.2434 | 1 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.128 | 0.77661 | 5.3154 | 4.128 | 0.77661 | 5.3154 | 4.8257 | 0.90787 | 5.3154 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 1.3053 | 37 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 99.6133 | 0.81525 | 122.1873 | 99.6133 | 0.81525 | 122.1873 | 116.449 | 0.95304 | 122.1873 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.44811 | 19 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.4383 | 0.27988 | 15.8578 | 4.4383 | 0.27988 | 15.8578 | 5.1885 | 0.32719 | 15.8578 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2028 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 0.1538 | 1 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.0216 | 0.096062 | 31.4549 | 3.0216 | 0.096062 | 31.4549 | 3.5323 | 0.1123 | 31.4549 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 4.2055 | 355 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 155.4182 | 2.6267 | 59.1687 | 155.4182 | 2.6267 | 59.1687 | 181.6856 | 3.0706 | 59.1687 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 6.4578 | 333 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 54.0763 | 4.0335 | 13.4069 | 54.0763 | 4.0335 | 13.4069 | 63.2158 | 4.7152 | 13.4069 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 2.7653 | 373 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 121.2542 | 1.7272 | 70.2026 | 121.2542 | 1.7272 | 70.2026 | 141.7475 | 2.0191 | 70.2026 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 8.3421 | 316 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1205.8901 | 5.2104 | 231.441 | 1205.8901 | 5.2104 | 231.441 | 1409.6992 | 6.091 | 231.441 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 1.9394 | 108 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 173.5599 | 1.2113 | 143.2792 | 173.5599 | 1.2113 | 143.2792 | 202.8935 | 1.4161 | 143.2792 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 3.8122 | 341 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 398.5988 | 2.381 | 167.4054 | 398.5988 | 2.381 | 167.4054 | 465.9666 | 2.7835 | 167.4054 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2028 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 11.0316 | 1032 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 139.9872 | 6.8902 | 20.3167 | 139.9872 | 6.8902 | 20.3167 | 163.6466 | 8.0548 | 20.3167 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2028 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 8.4597 | 757 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 536.0657 | 5.2838 | 101.454 | 536.0657 | 5.2838 | 101.454 | 626.6669 | 6.1769 | 101.454 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2028 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 4.2816 | 43 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 25.9573 | 2.6743 | 9.7064 | 25.9573 | 2.6743 | 9.7064 | 30.3444 | 3.1262 | 9.7064 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 3.6864 | 236 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 138.9965 | 2.3025 | 60.3681 | 138.9965 | 2.3025 | 60.3681 | 162.4885 | 2.6916 | 60.3681 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2028 | 243 | 243-14R | Tier-2 | Tier-2---11 | 4--4 | 4.9975 | 0 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 5.9029 | 0 | 0 | 5.9029 | 0 | 5.1241 | 3.1214 | 1.6416 | 5.1241 | 3.1214 | 1.6416 | 5.9901 | 3.649 | 1.6416 | 1.46% | 0.066445 | 0.063156 | 6084.1314 | 280.7794 | 3933.5085 | 1869.8435 | 6307.5143 | 0 | 0 | 6307.5143 | 0.0001947%
2028 | 916 | 916-381 | Tier-2 | Tier-2---12 | 4--4 | 0.1652 | 0 | 100% | 590.9122 | 71.07% | 28.73% | 0.1918% | 20.7893 | 0 | 0 | 20.7893 | 0 | 18.0464 | 0.10318 | 174.8989 | 18.0464 | 0.10318 | 174.8989 | 21.0965 | 0.12062 | 174.8989 | 3.518% | 0.049834 | 0.047367 | 11857.5641 | 1782.085 | 3001.9836 | 7073.4955 | 12036.1866 | 0 | 0 | 12036.1866 | 0.0006856%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 1.5403 | 211 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 35.1509 | 0.96207 | 36.5368 | 35.1509 | 0.96207 | 36.5368 | 41.0917 | 1.1247 | 36.5368 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 18.6854 | 1020 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 230.3929 | 11.6707 | 19.7412 | 230.3929 | 11.6707 | 19.7412 | 269.3319 | 13.6432 | 19.7412 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 6.8811 | 282 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 430.5862 | 4.2978 | 100.1867 | 430.5862 | 4.2978 | 100.1867 | 503.3602 | 5.0242 | 100.1867 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 12.6964 | 932 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 471.5754 | 7.9301 | 59.4668 | 471.5754 | 7.9301 | 59.4668 | 551.277 | 9.2703 | 59.4668 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 20.6608 | 1391 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 989.7054 | 12.9045 | 76.6947 | 989.7054 | 12.9045 | 76.6947 | 1156.9769 | 15.0855 | 76.6947 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 3.259 | 164 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 27.2182 | 2.0356 | 13.3713 | 27.2182 | 2.0356 | 13.3713 | 31.8184 | 2.3796 | 13.3713 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2028 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 0.8674 | 0 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 16.5102 | 0.54177 | 30.4747 | 16.5102 | 0.54177 | 30.4747 | 19.3006 | 0.63333 | 30.4747 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 31.8811 | 2181 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 584.9503 | 19.9126 | 29.3759 | 584.9503 | 19.9126 | 29.3759 | 683.8136 | 23.278 | 29.3759 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 12.0339 | 273 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 259.2534 | 7.5163 | 34.4923 | 259.2534 | 7.5163 | 34.4923 | 303.0701 | 8.7866 | 34.4923 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 2.9135 | 269 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 215.2532 | 1.8197 | 118.2893 | 215.2532 | 1.8197 | 118.2893 | 251.6334 | 2.1273 | 118.2893 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2028 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 3.7841 | 209 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 123.2379 | 2.3635 | 52.1423 | 123.2379 | 2.3635 | 52.1423 | 144.0665 | 2.7629 | 52.1423 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 15.005 | 1436 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 128.9318 | 9.3719 | 13.7572 | 128.9318 | 9.3719 | 13.7572 | 150.7228 | 10.9559 | 13.7572 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 3.0267 | 277 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 147.4188 | 1.8904 | 77.9812 | 147.4188 | 1.8904 | 77.9812 | 172.3343 | 2.2099 | 77.9812 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2028 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 3.5275 | 209 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 280.6799 | 2.2032 | 127.3955 | 280.6799 | 2.2032 | 127.3955 | 328.1181 | 2.5756 | 127.3955 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 4.5645 | 642 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.1015 | 2.851 | 4.5955 | 13.1015 | 2.851 | 4.5955 | 15.3158 | 3.3328 | 4.5955 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2028 | 334 | CB 334 | Tier-2 | Tier-2---17 | 3--4 | 2.321 | 0 | 100% | 70.5162 | 95.08% | 0% | 4.917% | 3.3189 | 0 | 0 | 3.3189 | 0 | 2.881 | 1.4497 | 1.9874 | 2.881 | 1.4497 | 1.9874 | 3.368 | 1.6947 | 1.9874 | 4.707% | 0.014478 | 0.013762 | 4870.4444 | 330.0733 | 2622.0959 | 1918.2753 | 4882.9165 | 0 | 0 | 4882.9165 | 0.0001094%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 0.89662 | 14 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 21.5211 | 0.56002 | 38.4291 | 21.5211 | 0.56002 | 38.4291 | 25.1584 | 0.65467 | 38.4291 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2028 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 26.8775 | 296 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 167.4015 | 16.7874 | 9.9719 | 167.4015 | 16.7874 | 9.9719 | 195.6942 | 19.6246 | 9.9719 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2028 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 9.2899 | 565 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 48.9727 | 5.8024 | 8.4401 | 48.9727 | 5.8024 | 8.4401 | 57.2497 | 6.7831 | 8.4401 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2028 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 18.7375 | 1826 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 175.1249 | 11.7032 | 14.9638 | 175.1249 | 11.7032 | 14.9638 | 204.723 | 13.6812 | 14.9638 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 1.6445 | 323 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 8.9724 | 1.0271 | 8.7355 | 8.9724 | 1.0271 | 8.7355 | 10.4889 | 1.2007 | 8.7355 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2028 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 3.5953 | 283 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 220.4842 | 2.2456 | 98.1865 | 220.4842 | 2.2456 | 98.1865 | 257.7485 | 2.6251 | 98.1865 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 20.7013 | 1693 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1210.6489 | 12.9298 | 93.6323 | 1210.6489 | 12.9298 | 93.6323 | 1415.2624 | 15.1151 | 93.6323 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 5.4369 | 85 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 39.9458 | 3.3958 | 11.7632 | 39.9458 | 3.3958 | 11.7632 | 46.6971 | 3.9698 | 11.7632 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2028 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 0.69072 | 24 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.4353 | 0.43142 | 12.5988 | 5.4353 | 0.43142 | 12.5988 | 6.354 | 0.50433 | 12.5988 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 13.5415 | 832 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 420.2187 | 8.4579 | 49.6838 | 420.2187 | 8.4579 | 49.6838 | 491.2405 | 9.8873 | 49.6838 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 8.3178 | 78 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 258.5486 | 5.1952 | 49.7669 | 258.5486 | 5.1952 | 49.7669 | 302.2462 | 6.0732 | 49.7669 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 16.422 | 1620 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 475.9015 | 10.257 | 46.3978 | 475.9015 | 10.257 | 46.3978 | 556.3343 | 11.9905 | 46.3978 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 11.56 | 762 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 960.6823 | 7.2203 | 133.0534 | 960.6823 | 7.2203 | 133.0534 | 1123.0485 | 8.4406 | 133.0534 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2028 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.17383 | 0 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.7632 | 0.10857 | 7.0293 | 0.7632 | 0.10857 | 7.0293 | 0.89219 | 0.12692 | 7.0293 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.77126 | 53 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 33.674 | 0.48172 | 69.9038 | 33.674 | 0.48172 | 69.9038 | 39.3653 | 0.56314 | 69.9038 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 5.0473 | 259 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 61.6503 | 3.1525 | 19.556 | 61.6503 | 3.1525 | 19.556 | 72.0699 | 3.6853 | 19.556 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 13.8096 | 549 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 152.5001 | 8.6253 | 17.6805 | 152.5001 | 8.6253 | 17.6805 | 178.2744 | 10.0831 | 17.6805 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 11.815 | 901 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 741.2094 | 7.3795 | 100.4417 | 741.2094 | 7.3795 | 100.4417 | 866.4823 | 8.6267 | 100.4417 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 20.6063 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 143.2712 | 12.8705 | 11.1318 | 143.2712 | 12.8705 | 11.1318 | 167.4857 | 15.0457 | 11.1318 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2028 | 476 | CB 476 | Tier-2 | Tier-2---2 | 5--5 | 3.9551 | 0 | 100% | 7260.3217 | 73.64% | 26.17% | 0.1876% | 264.6639 | 0 | 0 | 264.6639 | 0 | 229.7455 | 2.4703 | 93.0026 | 229.7455 | 2.4703 | 93.0026 | 268.5751 | 2.8878 | 93.0026 | 3.645% | 0.20125 | 0.19129 | 36075.4158 | 6663.2216 | 8787.8653 | 20624.3289 | 36570.586 | 0 | 0 | 36570.586 | 0.008728%
2028 | 386 | 386-25R | Tier-2 | Tier-2---15 | 3--4 | 0.7066 | 0 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 2.5144 | 0 | 0 | 2.5144 | 0 | 2.1827 | 0.44133 | 4.9456 | 2.1827 | 0.44133 | 4.9456 | 2.5516 | 0.51593 | 4.9456 | 1.75% | 0.019083 | 0.018138 | 7528.0087 | 552.5881 | 4465.4268 | 2509.9939 | 7781.4266 | 0 | 0 | 7781.4266 | 8.292e-05%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 0.80794 | 5 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 30.9346 | 0 | 0 | 30.9346 | 0 | 26.8532 | 0.50463 | 53.2135 | 26.8532 | 0.50463 | 53.2135 | 31.3917 | 0.58992 | 53.2135 | 4.945% | 0.0036434 | 0.0034631 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171700.5551 | 0 | 0 | 171700.5551 | 0.00102%
2028 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 1.165 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 62.7303 | 0.72765 | 86.2089 | 62.7303 | 0.72765 | 86.2089 | 73.3324 | 0.85064 | 86.2089 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 9.7066 | 442 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 624.7291 | 6.0626 | 103.0456 | 624.7291 | 6.0626 | 103.0456 | 730.3154 | 7.0873 | 103.0456 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2028 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 8.2208 | 243 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 242.4537 | 5.1346 | 47.2193 | 242.4537 | 5.1346 | 47.2193 | 283.4311 | 6.0024 | 47.2193 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 11.3059 | 892 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 185.4129 | 7.0615 | 26.2568 | 185.4129 | 7.0615 | 26.2568 | 216.7498 | 8.255 | 26.2568 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 13.2995 | 353 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 393.0326 | 8.3067 | 47.3151 | 393.0326 | 8.3067 | 47.3151 | 459.4596 | 9.7106 | 47.3151 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 8.9197 | 519 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 55.6298 | 5.5711 | 9.9854 | 55.6298 | 5.5711 | 9.9854 | 65.0319 | 6.5127 | 9.9854 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 2.6869 | 284 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 18.2006 | 1.6782 | 10.8453 | 18.2006 | 1.6782 | 10.8453 | 21.2767 | 1.9618 | 10.8453 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2028 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 0.050947 | 0 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.75966 | 0.031821 | 23.873 | 0.75966 | 0.031821 | 23.873 | 0.88805 | 0.037199 | 23.873 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2028 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 1.2638 | 61 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 24.2686 | 0.78937 | 30.7442 | 24.2686 | 0.78937 | 30.7442 | 28.3703 | 0.92279 | 30.7442 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2028 | 308 | 308-486AE | Tier-2 | Tier-2---16 | 4--3 | 1.7369 | 0 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.19428 | 0 | 0 | 0.19428 | 0 | 0.16865 | 1.0848 | 0.15546 | 0.16865 | 1.0848 | 0.15546 | 0.19715 | 1.2682 | 0.15546 | 0.118% | 0.040279 | 0.038285 | 4088.4689 | 19.0997 | 3634.8848 | 434.4844 | 4296.3129 | 0 | 0 | 4296.3129 | 6.407e-06%
2028 | 295 | 295-1203F | Tier-2 | Tier-2---21 | 1--2 | 0.2153 | 0 | 100% | 0.80448 | 60.49% | 0% | 39.51% | 0.02409 | 0 | 0 | 0.02409 | 0 | 0.020911 | 0.13447 | 0.1555 | 0.020911 | 0.13447 | 0.1555 | 0.024446 | 0.1572 | 0.1555 | 2.994% | 0.0013362 | 0.0012701 | 602.062 | 79.8078 | 41.8021 | 480.452 | 614.4487 | 0 | 0 | 614.4487 | 7.944e-07%
2028 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 1.3216 | 258 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 103.7927 | 0.82547 | 125.7371 | 103.7927 | 0.82547 | 125.7371 | 121.3349 | 0.96499 | 125.7371 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2028 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 7.0884 | 586 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 352.7981 | 4.4274 | 79.6858 | 352.7981 | 4.4274 | 79.6858 | 412.425 | 5.1756 | 79.6858 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2028 | 450 | 450-50R | Tier-2 | Tier-2---11 | 4--4 | 0.3652 | 6 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 8.6479 | 0 | 0 | 8.6479 | 0 | 7.507 | 0.2281 | 32.9109 | 7.507 | 0.2281 | 32.9109 | 8.7757 | 0.26665 | 32.9109 | 1.61% | 0.071801 | 0.068247 | 7480.0024 | 403.5755 | 4618.5943 | 2457.8325 | 7742.8291 | 0 | 0 | 7742.8291 | 0.0002852%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 1.5712 | 63 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 19.5575 | 0.98136 | 19.929 | 19.5575 | 0.98136 | 19.929 | 22.8629 | 1.1472 | 19.929 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2028 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 11.7129 | 203 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 299.4236 | 7.3157 | 40.9286 | 299.4236 | 7.3157 | 40.9286 | 350.0296 | 8.5522 | 40.9286 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2028 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.78597 | 36 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 10.7401 | 0.49091 | 21.878 | 10.7401 | 0.49091 | 21.878 | 12.5553 | 0.57388 | 21.878 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2028 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 5.3936 | 448 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 31.124 | 3.3688 | 9.2389 | 31.124 | 3.3688 | 9.2389 | 36.3843 | 3.9382 | 9.2389 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 9.3687 | 504 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 533.188 | 5.8516 | 91.1183 | 533.188 | 5.8516 | 91.1183 | 623.3029 | 6.8406 | 91.1183 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2028 | 393 | CB 393 | Tier-2 | Tier-2---19 | 1--3 | 0.339 | 0 | 100% | 8.3766 | 93.83% | 0% | 6.171% | 0.38906 | 0 | 0 | 0.38906 | 0 | 0.33773 | 0.21174 | 1.595 | 0.33773 | 0.21174 | 1.595 | 0.3948 | 0.24752 | 1.595 | 4.645% | 0.0030912 | 0.0029382 | 2709.8263 | 11.6903 | 2486.8043 | 211.3317 | 2718.5348 | 0 | 0 | 2718.5348 | 1.283e-05%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 8.4553 | 115 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 223.2743 | 5.2811 | 42.278 | 223.2743 | 5.2811 | 42.278 | 261.0102 | 6.1737 | 42.278 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2028 | 443 | CB 443 | Tier-2 | Tier-2---17 | 2--4 | 1.4752 | 0 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 3.2669 | 0 | 0 | 3.2669 | 0 | 2.8359 | 0.92139 | 3.0779 | 2.8359 | 0.92139 | 3.0779 | 3.3152 | 1.0771 | 3.0779 | 4.865% | 0.007405 | 0.0070385 | 9067.8323 | 1863.6752 | 20.0371 | 7184.12 | 9075.9094 | 0 | 0 | 9075.9094 | 0.0001077%
2028 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 2.5689 | 85 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 174.9949 | 1.6045 | 109.0639 | 174.9949 | 1.6045 | 109.0639 | 204.571 | 1.8757 | 109.0639 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 10.4533 | 593 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 24.868 | 6.529 | 3.8089 | 24.868 | 6.529 | 3.8089 | 29.071 | 7.6325 | 3.8089 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2028 | 535 | CB 535 | Tier-2 | Tier-2---16 | 4--3 | 0.31174 | 0 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25308 | 0 | 0 | 0.25308 | 0 | 0.21969 | 0.19471 | 1.1283 | 0.21969 | 0.19471 | 1.1283 | 0.25682 | 0.22762 | 1.1283 | 0.227% | 0.059698 | 0.056743 | 1867.7052 | 14.9488 | 1426.0626 | 426.6938 | 1960.5113 | 0 | 0 | 1960.5113 | 8.346e-06%
2028 | 281 | CB 281 | Tier-2 | Tier-2---16 | 4--3 | 3.767 | 0 | 100% | 131.3229 | 1.145% | 96.36% | 2.498% | 0.07445 | 0 | 0 | 0.07445 | 0 | 0.064627 | 2.3528 | 0.027468 | 0.064627 | 2.3528 | 0.027468 | 0.07555 | 2.7505 | 0.027468 | 0.05669% | 0.046838 | 0.04452 | 2803.7555 | 3.8846 | 2517.4341 | 282.4368 | 2948.0968 | 0 | 0 | 2948.0968 | 2.455e-06%
2028 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.023485 | 0 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.7032 | 0.014668 | 184.2836 | 2.7032 | 0.014668 | 184.2836 | 3.16 | 0.017148 | 184.2836 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2028 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 15.3043 | 1286 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 136.0144 | 9.5589 | 14.229 | 136.0144 | 9.5589 | 14.229 | 159.0024 | 11.1745 | 14.229 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 3.3899 | 505 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 161.7017 | 2.1173 | 76.3715 | 161.7017 | 2.1173 | 76.3715 | 189.0311 | 2.4752 | 76.3715 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 14.7171 | 529 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 17.3558 | 9.1921 | 1.8881 | 17.3558 | 9.1921 | 1.8881 | 20.2891 | 10.7457 | 1.8881 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.87121 | 106 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.6843 | 0.54415 | 10.4462 | 5.6843 | 0.54415 | 10.4462 | 6.645 | 0.63612 | 10.4462 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 5.3095 | 781 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 389.9738 | 3.3163 | 117.5946 | 389.9738 | 3.3163 | 117.5946 | 455.8839 | 3.8767 | 117.5946 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2028 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 9.9971 | 673 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 522.7499 | 6.2441 | 83.7192 | 522.7499 | 6.2441 | 83.7192 | 611.1006 | 7.2994 | 83.7192 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2028 | 1139 | 1139-4F | Tier-2 | Tier-2---11 | 5--3 | 2.2023 | 0 | 100% | 472.1771 | 0.2595% | 99.27% | 0.4712% | 0.060646 | 0 | 0 | 0.060646 | 0 | 0.052645 | 1.3755 | 0.038272 | 0.052645 | 1.3755 | 0.038272 | 0.061542 | 1.608 | 0.038272 | 0.01284% | 0.11231 | 0.10675 | 4204.4022 | 7.5405 | 3803.8802 | 392.9815 | 4422.7903 | 0 | 0 | 4422.7903 | 2e-06%
2028 | 197 | 197-1157F | Tier-2 | Tier-2---18 | 3--3 | 0.1773 | 0 | 100% | 63.1655 | 1.305% | 98.13% | 0.5601% | 0.040803 | 0 | 0 | 0.040803 | 0 | 0.03542 | 0.11074 | 0.31985 | 0.03542 | 0.11074 | 0.31985 | 0.041406 | 0.12946 | 0.31985 | 0.0646% | 0.01787 | 0.016985 | 3534.7635 | 11.6765 | 2974.4275 | 548.6595 | 3716.4442 | 0 | 0 | 3716.4442 | 1.346e-06%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 5.1261 | 334 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 147.3159 | 3.2017 | 46.0112 | 147.3159 | 3.2017 | 46.0112 | 172.214 | 3.7429 | 46.0112 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2028 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 16.7214 | 1503 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1201.9032 | 10.444 | 115.0807 | 1201.9032 | 10.444 | 115.0807 | 1405.0386 | 12.2092 | 115.0807 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2028 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 11.1523 | 320 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 339.5288 | 6.9656 | 48.7438 | 339.5288 | 6.9656 | 48.7438 | 396.9131 | 8.1428 | 48.7438 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2028 | 311 | 311-1163F | Tier-2 | Tier-2---18 | 3--3 | 0.65624 | 4 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9366 | 0 | 0 | 1.9366 | 0 | 1.6811 | 0.40988 | 4.1015 | 1.6811 | 0.40988 | 4.1015 | 1.9653 | 0.47916 | 4.1015 | 4.192% | 0.018623 | 0.017701 | 2480.5668 | 274.9764 | 742.9932 | 1462.5972 | 2500.341 | 0 | 0 | 2500.341 | 6.386e-05%
2028 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 3.6983 | 195 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 34.4802 | 2.3099 | 14.927 | 34.4802 | 2.3099 | 14.927 | 40.3077 | 2.7003 | 14.927 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2028 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.39659 | 0 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.61831 | 0.24771 | 2.4961 | 0.61831 | 0.24771 | 2.4961 | 0.72281 | 0.28957 | 2.4961 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2028 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 1.0854 | 13 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 14.1083 | 0.67794 | 20.8105 | 14.1083 | 0.67794 | 20.8105 | 16.4928 | 0.79252 | 20.8105 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.31499 | 9 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 6.9875 | 0.19674 | 35.5163 | 6.9875 | 0.19674 | 35.5163 | 8.1685 | 0.22999 | 35.5163 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 17.9266 | 1150 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1753.1858 | 11.1967 | 156.5801 | 1753.1858 | 11.1967 | 156.5801 | 2049.4942 | 13.0891 | 156.5801 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 15.4477 | 756 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1582.9263 | 9.6485 | 164.0594 | 1582.9263 | 9.6485 | 164.0594 | 1850.4589 | 11.2792 | 164.0594 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2028 | 462 | CB 462 | Tier-2 | Tier-2---19 | 2--4 | 0.4439 | 0 | 100% | 42.4238 | 96.69% | 0% | 3.313% | 2.0304 | 0 | 0 | 2.0304 | 0 | 1.7625 | 0.27726 | 6.3571 | 1.7625 | 0.27726 | 6.3571 | 2.0604 | 0.32411 | 6.3571 | 4.786% | 0.0069768 | 0.0066314 | 6080.6996 | 1110.385 | 1800.7984 | 3169.5162 | 6091.1906 | 0 | 0 | 6091.1906 | 6.696e-05%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 17.4555 | 1930 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 770.8154 | 10.9025 | 70.7007 | 770.8154 | 10.9025 | 70.7007 | 901.092 | 12.7452 | 70.7007 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 5.0582 | 437 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 62.2533 | 3.1593 | 19.705 | 62.2533 | 3.1593 | 19.705 | 72.7748 | 3.6932 | 19.705 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 0.14415 | 0 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.1462 | 0.090033 | 23.8382 | 2.1462 | 0.090033 | 23.8382 | 2.509 | 0.10525 | 23.8382 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2028 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 5.8553 | 513 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 224.7004 | 3.6571 | 61.4417 | 224.7004 | 3.6571 | 61.4417 | 262.6774 | 4.2752 | 61.4417 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2028 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | 3--3 | 0.27065 | 0 | 100% | 40.9949 | 23.55% | 73.64% | 2.81% | 0.47782 | 0 | 0 | 0.47782 | 0 | 0.41478 | 0.16905 | 2.4536 | 0.41478 | 0.16905 | 2.4536 | 0.48488 | 0.19762 | 2.4536 | 1.166% | 0.021565 | 0.020497 | 1901.027 | 61.7007 | 1198.5032 | 640.8231 | 1976.7168 | 0 | 0 | 1976.7168 | 1.576e-05%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 7.3796 | 121 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 200.0322 | 4.6092 | 43.3983 | 200.0322 | 4.6092 | 43.3983 | 233.8399 | 5.3882 | 43.3983 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.50061 | 50 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 16.6154 | 0.31267 | 53.1399 | 16.6154 | 0.31267 | 53.1399 | 19.4236 | 0.36552 | 53.1399 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 13.2557 | 1015 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 115.3527 | 8.2794 | 13.9326 | 115.3527 | 8.2794 | 13.9326 | 134.8486 | 9.6787 | 13.9326 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2028 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 21.2556 | 676 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3377.4744 | 13.2761 | 254.4035 | 3377.4744 | 13.2761 | 254.4035 | 3948.3061 | 15.5199 | 254.4035 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 29.2157 | 713 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 358.6727 | 18.2478 | 19.6557 | 358.6727 | 18.2478 | 19.6557 | 419.2925 | 21.3319 | 19.6557 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 7.4915 | 112 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 155.2133 | 4.6791 | 33.1715 | 155.2133 | 4.6791 | 33.1715 | 181.4461 | 5.4699 | 33.1715 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2028 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 15.6835 | 943 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 959.7818 | 9.7958 | 97.9792 | 959.7818 | 9.7958 | 97.9792 | 1121.9958 | 11.4514 | 97.9792 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2028 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 2.0208 | 0 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 30.8639 | 1.2622 | 24.4526 | 30.8639 | 1.2622 | 24.4526 | 36.0802 | 1.4755 | 24.4526 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2028 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.1678 | 14 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 4.8583 | 0.10481 | 46.3547 | 4.8583 | 0.10481 | 46.3547 | 5.6795 | 0.12252 | 46.3547 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 6.2775 | 169 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 411.5912 | 3.9209 | 104.9749 | 411.5912 | 3.9209 | 104.9749 | 481.1548 | 4.5835 | 104.9749 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 8.9137 | 164 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 91.7748 | 5.5674 | 16.4844 | 91.7748 | 5.5674 | 16.4844 | 107.2858 | 6.5083 | 16.4844 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2028 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 3.55 | 286 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 216.8136 | 2.2173 | 97.7835 | 216.8136 | 2.2173 | 97.7835 | 253.4576 | 2.592 | 97.7835 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2028 | 500 | 500-1531 | Tier-2 | Tier-2---10 | 4--4 | 0.88746 | 14 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 8.56 | 0 | 0 | 8.56 | 0 | 7.4307 | 0.5543 | 13.4055 | 7.4307 | 0.5543 | 13.4055 | 8.6865 | 0.64798 | 13.4055 | 1.069% | 0.071178 | 0.067654 | 11247.1911 | 406.5986 | 8046.836 | 2793.7565 | 11706.3951 | 0 | 0 | 11706.3951 | 0.0002823%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 34.1718 | 1862 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1718.1256 | 21.3434 | 80.4993 | 1718.1256 | 21.3434 | 80.4993 | 2008.5084 | 24.9506 | 80.4993 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2028 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 1.4237 | 110 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 6.8723 | 0.88923 | 7.7284 | 6.8723 | 0.88923 | 7.7284 | 8.0338 | 1.0395 | 7.7284 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2028 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 3.4267 | 233 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.7807 | 2.1403 | 0.83203 | 1.7807 | 2.1403 | 0.83203 | 2.0817 | 2.502 | 0.83203 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2028 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 1.3115 | 241 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 9.6593 | 0.81917 | 11.7916 | 9.6593 | 0.81917 | 11.7916 | 11.2918 | 0.95761 | 11.7916 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 6.4924 | 205 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 19.2857 | 4.0551 | 4.7559 | 19.2857 | 4.0551 | 4.7559 | 22.5452 | 4.7404 | 4.7559 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2028 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 7.8576 | 482 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 68.9581 | 4.9078 | 14.0508 | 68.9581 | 4.9078 | 14.0508 | 80.6128 | 5.7372 | 14.0508 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 17.727 | 1369 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1495.8237 | 11.0721 | 135.0982 | 1495.8237 | 11.0721 | 135.0982 | 1748.6349 | 12.9434 | 135.0982 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 2.3271 | 116 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 65.5614 | 1.4535 | 45.1071 | 65.5614 | 1.4535 | 45.1071 | 76.642 | 1.6991 | 45.1071 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.49562 | 11 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 36.0619 | 0.30956 | 116.4953 | 36.0619 | 0.30956 | 116.4953 | 42.1568 | 0.36188 | 116.4953 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 2.1594 | 49 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 22.8477 | 1.3488 | 16.9397 | 22.8477 | 1.3488 | 16.9397 | 26.7092 | 1.5767 | 16.9397 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2028 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.010606 | 0 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0066244 | 0 | 0 | 0.0066244 | 0 | 0 | 0.007744 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2028 | 445 | 445-1315 | Tier-2 | Tier-2---19 | 1--5 | 0.080871 | 0 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 1.294 | 0 | 0 | 1.294 | 0 | 1.1233 | 0.050511 | 22.2389 | 1.1233 | 0.050511 | 22.2389 | 1.3132 | 0.059048 | 22.2389 | 4.93% | 0.000636 | 0.00060452 | 41272.5846 | 5558.0973 | 1215.1763 | 34499.311 | 41281.3528 | 0 | 0 | 41281.3528 | 4.267e-05%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.5007 | 0.021411 | 116.7955 | 2.5007 | 0.021411 | 116.7955 | 2.9233 | 0.02503 | 116.7955 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.57917 | 30 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 12.5585 | 0.36174 | 34.7169 | 12.5585 | 0.36174 | 34.7169 | 14.6811 | 0.42288 | 34.7169 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2028 | 175 | CB 175 | Tier-2 | Tier-2---10 | 5--4 | 0.0828 | 0 | 100% | 1236.5075 | 84.14% | 15.66% | 0.203% | 51.5004 | 0 | 0 | 51.5004 | 0 | 44.7057 | 0.051716 | 864.447 | 44.7057 | 0.051716 | 864.447 | 52.2615 | 0.060457 | 864.447 | 4.165% | 0.16723 | 0.15895 | 7393.9644 | 1133.6762 | 1185.8912 | 5074.397 | 7455.0304 | 0 | 0 | 7455.0304 | 0.001698%
2028 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 12.1911 | 327 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 360.5107 | 7.6144 | 47.3459 | 360.5107 | 7.6144 | 47.3459 | 421.4411 | 8.9013 | 47.3459 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 1.8653 | 423 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 16.6149 | 1.1651 | 14.2608 | 16.6149 | 1.1651 | 14.2608 | 19.423 | 1.362 | 14.2608 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2028 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.055682 | 34 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.066084 | 0.034778 | 1.9002 | 0.066084 | 0.034778 | 1.9002 | 0.077253 | 0.040656 | 1.9002 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 24.3072 | 878 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 714.7921 | 15.182 | 47.0816 | 714.7921 | 15.182 | 47.0816 | 835.6001 | 17.7479 | 47.0816 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2028 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 1.2636 | 41 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 17.7423 | 0.78925 | 22.4798 | 17.7423 | 0.78925 | 22.4798 | 20.7409 | 0.92265 | 22.4798 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 10.5112 | 997 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 81.6467 | 6.5652 | 12.4364 | 81.6467 | 6.5652 | 12.4364 | 95.4459 | 7.6747 | 12.4364 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2028 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 0.081438 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0022216 | 0.050865 | 0.043676 | 0.0022216 | 0.050865 | 0.043676 | 0.002597 | 0.059462 | 0.043676 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2028 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 7.3706 | 412 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 783.9792 | 4.6036 | 170.2962 | 783.9792 | 4.6036 | 170.2962 | 916.4806 | 5.3817 | 170.2962 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 22.4647 | 1409 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 362.6973 | 14.0312 | 25.8493 | 362.6973 | 14.0312 | 25.8493 | 423.9973 | 16.4027 | 25.8493 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2028 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 8.1866 | 140 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 37.1073 | 5.1132 | 7.2571 | 37.1073 | 5.1132 | 7.2571 | 43.3789 | 5.9774 | 7.2571 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2028 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.016856 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.28982 | 0.010528 | 27.5287 | 0.28982 | 0.010528 | 27.5287 | 0.33881 | 0.012307 | 27.5287 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2028 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 8.8214 | 139 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 103.165 | 5.5097 | 18.7241 | 103.165 | 5.5097 | 18.7241 | 120.601 | 6.4409 | 18.7241 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2028 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 0.22216 | 19 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.27411 | 0.13876 | 1.9755 | 0.27411 | 0.13876 | 1.9755 | 0.32044 | 0.16221 | 1.9755 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 1.2988 | 31 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 19.4933 | 0.81124 | 24.029 | 19.4933 | 0.81124 | 24.029 | 22.7878 | 0.94835 | 24.029 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2028 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 3.321 | 115 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 50.2897 | 2.0743 | 24.2445 | 50.2897 | 2.0743 | 24.2445 | 58.7892 | 2.4248 | 24.2445 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2028 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 14.5687 | 1091 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 576.8605 | 9.0995 | 63.395 | 576.8605 | 9.0995 | 63.395 | 674.3565 | 10.6374 | 63.395 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 2.3515 | 16 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 244.9741 | 1.4687 | 166.7922 | 244.9741 | 1.4687 | 166.7922 | 286.3776 | 1.717 | 166.7922 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.41229 | 18 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 12.9002 | 0.25751 | 50.0961 | 12.9002 | 0.25751 | 50.0961 | 15.0805 | 0.30103 | 50.0961 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 6.2353 | 440 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 150.6352 | 3.8945 | 38.6792 | 150.6352 | 3.8945 | 38.6792 | 176.0942 | 4.5527 | 38.6792 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2028 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 2.0774 | 340 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 107.356 | 1.2975 | 82.7384 | 107.356 | 1.2975 | 82.7384 | 125.5004 | 1.5168 | 82.7384 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2028 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.76383 | 6 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 7.3264 | 0.47708 | 15.3568 | 7.3264 | 0.47708 | 15.3568 | 8.5646 | 0.55771 | 15.3568 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 5.8533 | 585 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 57.8421 | 3.6559 | 15.8217 | 57.8421 | 3.6559 | 15.8217 | 67.6181 | 4.2738 | 15.8217 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 4.0824 | 392 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 18.2705 | 2.5498 | 7.1655 | 18.2705 | 2.5498 | 7.1655 | 21.3584 | 2.9807 | 7.1655 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 15.1559 | 793 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 102.9619 | 9.4662 | 10.8768 | 102.9619 | 9.4662 | 10.8768 | 120.3637 | 11.0661 | 10.8768 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 19.9074 | 1826 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1116.9255 | 12.4339 | 89.8289 | 1116.9255 | 12.4339 | 89.8289 | 1305.6986 | 14.5354 | 89.8289 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 8.7188 | 73 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 304.0085 | 5.4456 | 55.826 | 304.0085 | 5.4456 | 55.826 | 355.3895 | 6.366 | 55.826 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2028 | 239 | CB 239 | Tier-3 | Tier-3---20 | 1--5 | 0.039773 | 0 | 100% | 10.6776 | 99.64% | 0% | 0.3633% | 0.52662 | 0 | 0 | 0.52662 | 0 | 0.45714 | 0.024842 | 18.4022 | 0.45714 | 0.024842 | 18.4022 | 0.53441 | 0.02904 | 18.4022 | 4.932% | 0.0001826 | 0.00017356 | 58475.5699 | 8842.2618 | 1906.0953 | 47727.2128 | 58486.6341 | 0 | 0 | 58486.6341 | 1.737e-05%
2028 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.84619 | 35 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 90.3172 | 0.52852 | 170.887 | 90.3172 | 0.52852 | 170.887 | 105.5818 | 0.61785 | 170.887 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 3.4333 | 98 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 15.6819 | 2.1444 | 7.3129 | 15.6819 | 2.1444 | 7.3129 | 18.3323 | 2.5068 | 7.3129 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.34621 | 18 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 6.7644 | 0.21624 | 31.2817 | 6.7644 | 0.21624 | 31.2817 | 7.9076 | 0.25279 | 31.2817 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2028 | 948 | 948-5R | Tier-2 | Tier-2---21 | 1--2 | 0.1373 | 0 | 100% | 3.6494 | 90.16% | 0% | 9.838% | 0.16287 | 0 | 0 | 0.16287 | 0 | 0.14138 | 0.085756 | 1.6487 | 0.14138 | 0.085756 | 1.6487 | 0.16528 | 0.10025 | 1.6487 | 4.463% | 0.0023872 | 0.002269 | 1528.7338 | 203.4062 | 386.7322 | 938.5955 | 1536.5665 | 0 | 0 | 1536.5665 | 5.371e-06%
2028 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 0.81042 | 160 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.704 | 0.50618 | 5.342 | 2.704 | 0.50618 | 5.342 | 3.161 | 0.59173 | 5.342 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2028 | 533 | CB 533 | Tier-2 | Tier-2---20 | 4--1 | 0.027511 | 0 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.01766 | 0 | 0 | 0.01766 | 0 | 0.01533 | 0.017183 | 0.89216 | 0.01533 | 0.017183 | 0.89216 | 0.017921 | 0.020087 | 0.89216 | 0.1665% | 0.06013 | 0.057154 | 176.3723 | 1.2595 | 133.5547 | 41.5581 | 185.2484 | 0 | 0 | 185.2484 | 5.824e-07%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 13.4125 | 992 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 69.754 | 8.3773 | 8.3265 | 69.754 | 8.3773 | 8.3265 | 81.5432 | 9.7932 | 8.3265 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 1.0659 | 28 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 56.4831 | 0.66575 | 84.8411 | 56.4831 | 0.66575 | 84.8411 | 66.0294 | 0.77827 | 84.8411 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2028 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 14.5985 | 935 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 485.1895 | 9.1181 | 53.2118 | 485.1895 | 9.1181 | 53.2118 | 567.1921 | 10.6591 | 53.2118 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.64526 | 37 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.3266 | 0.40302 | 13.2168 | 5.3266 | 0.40302 | 13.2168 | 6.2269 | 0.47113 | 13.2168 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2028 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 2.803 | 3 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 3.9605 | 1.7507 | 2.2622 | 3.9605 | 1.7507 | 2.2622 | 4.6299 | 2.0466 | 2.2622 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 7.564 | 846 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 87.4066 | 4.7244 | 18.5011 | 87.4066 | 4.7244 | 18.5011 | 102.1793 | 5.5229 | 18.5011 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2028 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 24.6051 | 1562 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 269.5166 | 15.3681 | 17.5374 | 269.5166 | 15.3681 | 17.5374 | 315.068 | 17.9655 | 17.5374 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 5.7333 | 63 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 226.556 | 3.581 | 63.2667 | 226.556 | 3.581 | 63.2667 | 264.8465 | 4.1862 | 63.2667 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2028 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 10.6382 | 730 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 94.2766 | 6.6445 | 14.1886 | 94.2766 | 6.6445 | 14.1886 | 110.2104 | 7.7675 | 14.1886 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 10.5116 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 371.4043 | 6.5654 | 56.5698 | 371.4043 | 6.5654 | 56.5698 | 434.1758 | 7.6751 | 56.5698 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 1.4734 | 189 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.0984 | 0.9203 | 3.3667 | 3.0984 | 0.9203 | 3.3667 | 3.6221 | 1.0758 | 3.3667 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2028 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 20.5957 | 1555 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2356.8951 | 12.8638 | 183.2187 | 2356.8951 | 12.8638 | 183.2187 | 2755.2372 | 15.038 | 183.2187 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2028 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 4.4809 | 263 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 41.1366 | 2.7987 | 14.6985 | 41.1366 | 2.7987 | 14.6985 | 48.0892 | 3.2717 | 14.6985 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 22.8015 | 890 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 72.2185 | 14.2416 | 5.071 | 72.2185 | 14.2416 | 5.071 | 84.4243 | 16.6486 | 5.071 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2028 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.125 | 26 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 3.7465 | 0.078074 | 47.9869 | 3.7465 | 0.078074 | 47.9869 | 4.3797 | 0.091269 | 47.9869 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2028 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.092045 | 7 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 10.7819 | 0.05749 | 187.5432 | 10.7819 | 0.05749 | 187.5432 | 12.6042 | 0.067207 | 187.5432 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2028 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 9.5829 | 976 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 56.178 | 5.9854 | 9.3858 | 56.178 | 5.9854 | 9.3858 | 65.6727 | 6.997 | 9.3858 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2028 | 728 | 728-1570F | Tier-2 | Tier-2---19 | 1--5 | 0.0015 | 0 | 100% | 33.2807 | 99.79% | 0% | 0.2133% | 1.6439 | 0 | 0 | 1.6439 | 0 | 1.427 | 0.00093688 | 1523.1308 | 1.427 | 0.00093688 | 1523.1308 | 1.6682 | 0.0010952 | 1523.1308 | 4.939% | 0.0003472 | 0.00033001 | 95854.6419 | 22304.1965 | 20.1049 | 73530.3404 | 95865.2904 | 0 | 0 | 95865.2904 | 5.421e-05%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 12.1965 | 973 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 356.2423 | 7.6178 | 46.7646 | 356.2423 | 7.6178 | 46.7646 | 416.4513 | 8.9053 | 46.7646 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 20.8132 | 1273 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 381.0599 | 12.9997 | 29.3129 | 381.0599 | 12.9997 | 29.3129 | 445.4634 | 15.1968 | 29.3129 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2028 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 2.4181 | 206 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 73.0958 | 1.5103 | 48.3969 | 73.0958 | 1.5103 | 48.3969 | 85.4498 | 1.7656 | 48.3969 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 4.0926 | 174 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 284.0073 | 2.5562 | 111.105 | 284.0073 | 2.5562 | 111.105 | 332.0078 | 2.9882 | 111.105 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2028 | 972 | 972-1642 | Tier-2 | Tier-2---16 | 5--2 | 0.038636 | 0 | 100% | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.024132 | 0 | 0 | 0.024132 | 0 | 0 | 0.02821 | 0 | 0% | 0.11047 | 0.105 | 1677.3427 | 1.9611 | 1510.6909 | 164.6906 | 1764.6951 | 0 | 0 | 1764.6951 | 0%
2028 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.2301 | 17 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 13.8695 | 0.14372 | 96.506 | 13.8695 | 0.14372 | 96.506 | 16.2136 | 0.16801 | 96.506 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2028 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.38903 | 14 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 29.618 | 0.24299 | 121.892 | 29.618 | 0.24299 | 121.892 | 34.6238 | 0.28405 | 121.892 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 12.821 | 921 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 137.5976 | 8.0079 | 17.1828 | 137.5976 | 8.0079 | 17.1828 | 160.8532 | 9.3613 | 17.1828 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 10.8114 | 889 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 75.7606 | 6.7527 | 11.2193 | 75.7606 | 6.7527 | 11.2193 | 88.565 | 7.894 | 11.2193 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 2.6777 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 216.3509 | 1.6724 | 129.3619 | 216.3509 | 1.6724 | 129.3619 | 252.9167 | 1.9551 | 129.3619 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 11.5801 | 469 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 439.4785 | 7.2328 | 60.7618 | 439.4785 | 7.2328 | 60.7618 | 513.7554 | 8.4552 | 60.7618 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2028 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 2.4417 | 29 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 8.9573 | 1.525 | 5.8735 | 8.9573 | 1.525 | 5.8735 | 10.4711 | 1.7828 | 5.8735 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2028 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 9.2184 | 137 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 17.2479 | 5.7577 | 2.9956 | 17.2479 | 5.7577 | 2.9956 | 20.163 | 6.7308 | 2.9956 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2028 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.075568 | 0 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 8.2404 | 0.047199 | 174.5888 | 8.2404 | 0.047199 | 174.5888 | 9.6331 | 0.055176 | 174.5888 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 6.8952 | 725 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 36.2581 | 4.3067 | 8.419 | 36.2581 | 4.3067 | 8.419 | 42.3861 | 5.0346 | 8.419 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 3.5241 | 66 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 55.6541 | 2.2011 | 25.2848 | 55.6541 | 2.2011 | 25.2848 | 65.0603 | 2.5731 | 25.2848 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2028 | 386 | CB 386 | Tier-2 | Tier-2---14 | 4--4 | 2.7822 | 0 | 100% | 266.4482 | 58.89% | 39.19% | 1.927% | 7.7666 | 0 | 0 | 7.7666 | 0 | 6.7419 | 1.7377 | 3.8797 | 6.7419 | 1.7377 | 3.8797 | 7.8814 | 2.0314 | 3.8797 | 2.915% | 0.037437 | 0.035584 | 7117.2424 | 561.1032 | 3326.6838 | 3229.4554 | 7269.6317 | 0 | 0 | 7269.6317 | 0.0002561%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 11.3933 | 245 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 50.7321 | 7.1161 | 7.1292 | 50.7321 | 7.1161 | 7.1292 | 59.3064 | 8.3189 | 7.1292 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 1.2636 | 4 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 19.5034 | 0.78923 | 24.7119 | 19.5034 | 0.78923 | 24.7119 | 22.7997 | 0.92262 | 24.7119 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2028 | 858 | 858-14 | Tier-2 | Tier-2---12 | 2--5 | 1.3439 | 0 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 20.2792 | 0 | 0 | 20.2792 | 0 | 17.6037 | 0.83939 | 20.9721 | 17.6037 | 0.83939 | 20.9721 | 20.5789 | 0.98125 | 20.9721 | 4.926% | 0.010043 | 0.0095457 | 40994.194 | 8631.9946 | 63.0219 | 32299.1775 | 41004.6459 | 0 | 0 | 41004.6459 | 0.0006687%
2028 | 282 | CB 282 | Tier-2 | Tier-2---15 | 4--3 | 0.221 | 0 | 100% | 152.5069 | 4.749% | 94.48% | 0.7672% | 0.3585 | 0 | 0 | 0.3585 | 0 | 0.3112 | 0.13803 | 2.2545 | 0.3112 | 0.13803 | 2.2545 | 0.3638 | 0.16136 | 2.2545 | 0.2351% | 0.035573 | 0.033812 | 4287.153 | 11.5968 | 3743.6752 | 531.8809 | 4499.8161 | 0 | 0 | 4499.8161 | 1.182e-05%
2028 | 795 | 795-816R | Tier-2 | Tier-2---13 | 4--4 | 2.6195 | 0 | 100% | 228.7654 | 4.756% | 93.08% | 2.167% | 0.53859 | 0 | 0 | 0.53859 | 0 | 0.46753 | 1.6361 | 0.28576 | 0.46753 | 1.6361 | 0.28576 | 0.54655 | 1.9126 | 0.28576 | 0.2354% | 0.036491 | 0.034684 | 6269.16 | 14.3219 | 5608.3339 | 646.5042 | 6580.116 | 0 | 0 | 6580.116 | 1.776e-05%
2028 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 0.64526 | 21 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 14.0656 | 0.40303 | 34.9 | 14.0656 | 0.40303 | 34.9 | 16.4428 | 0.47114 | 34.9 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 3.4282 | 107 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 61.1318 | 2.1412 | 28.5503 | 61.1318 | 2.1412 | 28.5503 | 71.4638 | 2.5031 | 28.5503 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 11.6815 | 979 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 284.7731 | 7.2961 | 39.0308 | 284.7731 | 7.2961 | 39.0308 | 332.9031 | 8.5292 | 39.0308 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2028 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 20.7706 | 2353 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 282.962 | 12.9731 | 21.8114 | 282.962 | 12.9731 | 21.8114 | 330.7858 | 15.1657 | 21.8114 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2028 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 10.4561 | 129 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 29.9452 | 6.5308 | 4.5853 | 29.9452 | 6.5308 | 4.5853 | 35.0063 | 7.6345 | 4.5853 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 2.8193 | 65 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 15.9736 | 1.7609 | 9.0712 | 15.9736 | 1.7609 | 9.0712 | 18.6733 | 2.0585 | 9.0712 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 13.3513 | 1600 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 383.592 | 8.3391 | 45.9993 | 383.592 | 8.3391 | 45.9993 | 448.4235 | 9.7485 | 45.9993 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2028 | 928 | 928-20 | Tier-2 | Tier-2---20 | 4--2 | 0.0328 | 0 | 100% | 27.1749 | 93.08% | 6.522% | 0.4024% | 1.252 | 0 | 0 | 1.252 | 0 | 1.0868 | 0.020487 | 53.0508 | 1.0868 | 0.020487 | 53.0508 | 1.2705 | 0.023949 | 53.0508 | 4.607% | 0.044362 | 0.042166 | 612.5656 | 93.209 | 34.6926 | 484.664 | 614.7746 | 0 | 0 | 614.7746 | 4.129e-05%
2028 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 4.9693 | 637 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 31.1245 | 3.1038 | 10.0279 | 31.1245 | 3.1038 | 10.0279 | 36.3849 | 3.6284 | 10.0279 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2028 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 5.2678 | 343 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 41.7314 | 3.2902 | 12.6835 | 41.7314 | 3.2902 | 12.6835 | 48.7844 | 3.8463 | 12.6835 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2028 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 14.5858 | 738 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1000.831 | 9.1101 | 109.8593 | 1000.831 | 9.1101 | 109.8593 | 1169.9829 | 10.6498 | 109.8593 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2028 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 0.049053 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.094363 | 0.030638 | 3.0799 | 0.094363 | 0.030638 | 3.0799 | 0.11031 | 0.035816 | 3.0799 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2028 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 0.20947 | 11 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 5.8904 | 0.13083 | 45.022 | 5.8904 | 0.13083 | 45.022 | 6.8859 | 0.15294 | 45.022 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2028 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 9.6756 | 209 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 61.9628 | 6.0433 | 10.2532 | 61.9628 | 6.0433 | 10.2532 | 72.4352 | 7.0647 | 10.2532 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 2.7722 | 17 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.6887 | 1.7315 | 0.97532 | 1.6887 | 1.7315 | 0.97532 | 1.9742 | 2.0241 | 0.97532 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2028 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 3.6174 | 367 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 191.5196 | 2.2594 | 84.7651 | 191.5196 | 2.2594 | 84.7651 | 223.8887 | 2.6413 | 84.7651 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2028 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 9.2129 | 303 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 196.2268 | 5.7543 | 34.101 | 196.2268 | 5.7543 | 34.101 | 229.3913 | 6.7268 | 34.101 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2028 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 7.3522 | 285 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 142.8362 | 4.5921 | 31.1046 | 142.8362 | 4.5921 | 31.1046 | 166.9772 | 5.3682 | 31.1046 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.32386 | 57 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 16.9319 | 0.20228 | 83.7047 | 16.9319 | 0.20228 | 83.7047 | 19.7936 | 0.23647 | 83.7047 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2028 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 1.7152 | 34 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 307.9689 | 1.0713 | 287.4814 | 307.9689 | 1.0713 | 287.4814 | 360.0191 | 1.2523 | 287.4814 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 10.7038 | 848 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 281.0624 | 6.6855 | 42.0408 | 281.0624 | 6.6855 | 42.0408 | 328.5651 | 7.8154 | 42.0408 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2028 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 1.7237 | 253 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 58.3493 | 1.0766 | 54.1981 | 58.3493 | 1.0766 | 54.1981 | 68.211 | 1.2585 | 54.1981 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2028 | 243 | CB 243 | Tier-2 | Tier-2---14 | 4--4 | 0.7388 | 0 | 100% | 284.2808 | 92.1% | 7.127% | 0.7733% | 12.9602 | 0 | 0 | 12.9602 | 0 | 11.2503 | 0.46145 | 24.3804 | 11.2503 | 0.46145 | 24.3804 | 13.1517 | 0.53944 | 24.3804 | 4.559% | 0.039288 | 0.037343 | 7235.7813 | 1297.464 | 840.9216 | 5097.3957 | 7265.5523 | 0 | 0 | 7265.5523 | 0.0004274%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 10.906 | 246 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 274.7145 | 6.8118 | 40.3292 | 274.7145 | 6.8118 | 40.3292 | 321.1444 | 7.9631 | 40.3292 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2028 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | 4--1 | 0.012311 | 0 | 100% | 2.3826 | 9.042% | 83.57% | 7.391% | 0.010664 | 0 | 0 | 0.010664 | 0 | 0.0092569 | 0.0076893 | 1.2039 | 0.0092569 | 0.0076893 | 1.2039 | 0.010821 | 0.0089889 | 1.2039 | 0.4476% | 0.059368 | 0.05643 | 40.1318 | 0.36722 | 29.4839 | 10.2807 | 42.0328 | 0 | 0 | 42.0328 | 3.517e-07%
2028 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.11724 | 0 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 14.3554 | 0.073224 | 196.049 | 14.3554 | 0.073224 | 196.049 | 16.7817 | 0.085599 | 196.049 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 33.4712 | 1238 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2785.0787 | 20.9057 | 133.2208 | 2785.0787 | 20.9057 | 133.2208 | 3255.7888 | 24.439 | 133.2208 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2028 | 920 | 920-823 | Tier-2 | Tier-2---11 | 4--4 | 0.871 | 0 | 100% | 458.2189 | 68.35% | 31.14% | 0.5113% | 15.5021 | 0 | 0 | 15.5021 | 0 | 13.4569 | 0.54402 | 24.7361 | 13.4569 | 0.54402 | 24.7361 | 15.7312 | 0.63596 | 24.7361 | 3.383% | 0.054577 | 0.051875 | 8395.8542 | 937.9397 | 2311.5146 | 5146.3999 | 8534.2572 | 0 | 0 | 8534.2572 | 0.0005112%
2028 | 280 | CB 280 | Tier-2 | Tier-2---14 | 4--4 | 2.6745 | 17 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 2.4753 | 0 | 0 | 2.4753 | 0 | 2.1488 | 1.6704 | 1.2863 | 2.1488 | 1.6704 | 1.2863 | 2.5119 | 1.9528 | 1.2863 | 0.7965% | 0.042409 | 0.04031 | 7328.4886 | 170.2669 | 5820.5339 | 1337.6878 | 7648.7329 | 0 | 0 | 7648.7329 | 8.163e-05%
2028 | 355 | 355-65R | Tier-2 | Tier-2---21 | 1--2 | 0.007576 | 0 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.0015289 | 0 | 0 | 0.0015289 | 0 | 0.0013272 | 0.0047319 | 0.28047 | 0.0013272 | 0.0047319 | 0.28047 | 0.0015515 | 0.0055316 | 0.28047 | 2.282% | 7.02e-05 | 6.6725e-05 | 954.2713 | 72.5365 | 46.719 | 835.0158 | 981.0548 | 0 | 0 | 981.0548 | 5.042e-08%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 6.5815 | 222 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 53.0108 | 4.1107 | 12.8957 | 53.0108 | 4.1107 | 12.8957 | 61.9702 | 4.8055 | 12.8957 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2028 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 19.1678 | 1740 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 390.5476 | 11.972 | 32.6217 | 390.5476 | 11.972 | 32.6217 | 456.5546 | 13.9954 | 32.6217 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2028 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.033523 | 0 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.49012 | 0.020938 | 23.408 | 0.49012 | 0.020938 | 23.408 | 0.57295 | 0.024477 | 23.408 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2028 | 235 | CB 235 | Tier-2 | Tier-2---12 | 1--5 | 0.15928 | 0 | 100% | 443.5427 | 99.96% | 0% | 0.03939% | 21.9467 | 0 | 0 | 21.9467 | 0 | 19.0512 | 0.099485 | 191.4988 | 19.0512 | 0.099485 | 191.4988 | 22.271 | 0.1163 | 191.4988 | 4.948% | 0.0007134 | 0.00067809 | 621730.7449 | 100003.5038 | 3209.2492 | 518517.9918 | 621743.4984 | 0 | 0 | 621743.4984 | 0.0007237%
2028 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 5.3209 | 577 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 144.0231 | 3.3234 | 43.3365 | 144.0231 | 3.3234 | 43.3365 | 168.3647 | 3.8851 | 43.3365 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2028 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 8.1068 | 164 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 21.4448 | 5.0634 | 4.2352 | 21.4448 | 5.0634 | 4.2352 | 25.0692 | 5.9192 | 4.2352 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2028 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 7.7129 | 463 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 5.4996 | 4.8174 | 1.1416 | 5.4996 | 4.8174 | 1.1416 | 6.4291 | 5.6316 | 1.1416 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2028 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.58561 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 3.6818 | 0.36576 | 10.066 | 3.6818 | 0.36576 | 10.066 | 4.304 | 0.42758 | 10.066 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 7.0273 | 9 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 13.8599 | 4.3892 | 3.1577 | 13.8599 | 4.3892 | 3.1577 | 16.2024 | 5.131 | 3.1577 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 10.6015 | 361 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 38.2345 | 6.6216 | 5.7742 | 38.2345 | 6.6216 | 5.7742 | 44.6966 | 7.7407 | 5.7742 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 3.3435 | 149 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 368.6686 | 2.0883 | 176.5371 | 368.6686 | 2.0883 | 176.5371 | 430.9777 | 2.4413 | 176.5371 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2028 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 3.5375 | 52 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.081067 | 2.2095 | 0.03669 | 0.081067 | 2.2095 | 0.03669 | 0.094768 | 2.5829 | 0.03669 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 5.4324 | 4 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 19.6111 | 3.393 | 5.7799 | 19.6111 | 3.393 | 5.7799 | 22.9256 | 3.9665 | 5.7799 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 0.38934 | 15 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 7.7742 | 0.24318 | 31.969 | 7.7742 | 0.24318 | 31.969 | 9.0882 | 0.28428 | 31.969 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2028 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | 3--3 | 2.0388 | 0 | 100% | 117.3021 | 94.99% | 0% | 5.009% | 5.5156 | 0 | 0 | 5.5156 | 0 | 4.7879 | 1.2734 | 3.7599 | 4.7879 | 1.2734 | 3.7599 | 5.5971 | 1.4887 | 3.7599 | 4.702% | 0.027256 | 0.025907 | 4303.7498 | 1020.4795 | 248.6707 | 3034.5996 | 4314.9761 | 0 | 0 | 4314.9761 | 0.0001819%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 7.8127 | 414 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 829.0555 | 4.8797 | 169.8986 | 829.0555 | 4.8797 | 169.8986 | 969.1753 | 5.7044 | 169.8986 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2028 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 3.1864 | 107 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 129.9481 | 1.9902 | 65.2949 | 129.9481 | 1.9902 | 65.2949 | 151.9108 | 2.3265 | 65.2949 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 1.1027 | 132 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 31.5786 | 0.68872 | 45.8509 | 31.5786 | 0.68872 | 45.8509 | 36.9157 | 0.80513 | 45.8509 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 7.8693 | 814 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 412.3272 | 4.9151 | 83.8904 | 412.3272 | 4.9151 | 83.8904 | 482.0151 | 5.7458 | 83.8904 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2028 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.053788 | 0 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.080746 | 0.033595 | 2.4035 | 0.080746 | 0.033595 | 2.4035 | 0.094393 | 0.039273 | 2.4035 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2028 | 452 | 452-717 | Tier-2 | Tier-2---19 | 1--5 | 0.0871 | 0 | 100% | 24.802 | 99.04% | 0% | 0.9608% | 1.2159 | 0 | 0 | 1.2159 | 0 | 1.0555 | 0.054402 | 19.4017 | 1.0555 | 0.054402 | 19.4017 | 1.2339 | 0.063596 | 19.4017 | 4.902% | 0.000973 | 0.00092484 | 25490.2561 | 9086.828 | 25.5586 | 16377.8695 | 25503.0101 | 0 | 0 | 25503.0101 | 4.01e-05%
2028 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 13.2184 | 308 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 164.8649 | 8.2561 | 19.9689 | 164.8649 | 8.2561 | 19.9689 | 192.729 | 9.6515 | 19.9689 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2028 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.027841 | 0 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.25966 | 0.017389 | 14.9323 | 0.25966 | 0.017389 | 14.9323 | 0.30355 | 0.020328 | 14.9323 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 6.3703 | 486 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 615.1953 | 3.9788 | 154.6173 | 615.1953 | 3.9788 | 154.6173 | 719.1703 | 4.6513 | 154.6173 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2028 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 2.6683 | 515 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 21.7739 | 1.6666 | 13.0647 | 21.7739 | 1.6666 | 13.0647 | 25.454 | 1.9483 | 13.0647 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 11.3506 | 1487 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 269.7477 | 7.0895 | 38.0491 | 269.7477 | 7.0895 | 38.0491 | 315.3382 | 8.2877 | 38.0491 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2028 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 6.121 | 113 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 87.8869 | 3.8231 | 22.9884 | 87.8869 | 3.8231 | 22.9884 | 102.7408 | 4.4692 | 22.9884 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 6.7335 | 641 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 625.2178 | 4.2057 | 148.6608 | 625.2178 | 4.2057 | 148.6608 | 730.8867 | 4.9165 | 148.6608 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2028 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 1.5907 | 12 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.123 | 0.99353 | 3.1433 | 3.123 | 0.99353 | 3.1433 | 3.6508 | 1.1615 | 3.1433 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2028 | 266 | 266-485F | Tier-2 | Tier-2---21 | 1--4 | 0.047 | 0 | 100% | 3.9025 | 97.35% | 0% | 2.654% | 0.18805 | 0 | 0 | 0.18805 | 0 | 0.16324 | 0.029356 | 5.5607 | 0.16324 | 0.029356 | 5.5607 | 0.19083 | 0.034317 | 5.5607 | 4.819% | 0.000646 | 0.00061402 | 6041.0896 | 954.7948 | 18.9693 | 5067.3254 | 6049.4401 | 0 | 0 | 6049.4401 | 6.201e-06%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 6.8056 | 645 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 68.7279 | 4.2507 | 16.1685 | 68.7279 | 4.2507 | 16.1685 | 80.3437 | 4.9692 | 16.1685 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 11.3022 | 654 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 953.2756 | 7.0593 | 135.039 | 953.2756 | 7.0593 | 135.039 | 1114.3901 | 8.2524 | 135.039 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 7.9883 | 1090 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 129.5064 | 4.9894 | 25.9563 | 129.5064 | 4.9894 | 25.9563 | 151.3944 | 5.8327 | 25.9563 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 6.2962 | 587 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 317.4625 | 3.9326 | 80.7267 | 317.4625 | 3.9326 | 80.7267 | 371.1173 | 4.5972 | 80.7267 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2028 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 0.60433 | 297 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 18.6264 | 0.37746 | 49.3469 | 18.6264 | 0.37746 | 49.3469 | 21.7744 | 0.44125 | 49.3469 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2028 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 0.61936 | 43 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.6704 | 0.38685 | 1.733 | 0.6704 | 0.38685 | 1.733 | 0.78371 | 0.45223 | 1.733 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2028 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 34.4453 | 2656 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 232.1573 | 21.5142 | 10.7909 | 232.1573 | 21.5142 | 10.7909 | 271.3946 | 25.1503 | 10.7909 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 3.289 | 353 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 26.2058 | 2.0543 | 12.7567 | 26.2058 | 2.0543 | 12.7567 | 30.6349 | 2.4015 | 12.7567 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 3.4321 | 23 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.577 | 2.1436 | 4.0011 | 8.577 | 2.1436 | 4.0011 | 10.0266 | 2.5059 | 4.0011 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 2.081 | 79 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 7.4657 | 1.2998 | 5.7438 | 7.4657 | 1.2998 | 5.7438 | 8.7275 | 1.5195 | 5.7438 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2028 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 9.6284 | 454 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 444.2579 | 6.0138 | 73.8729 | 444.2579 | 6.0138 | 73.8729 | 519.3425 | 7.0302 | 73.8729 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2028 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 4.8606 | 121 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 15.7744 | 3.0359 | 5.196 | 15.7744 | 3.0359 | 5.196 | 18.4404 | 3.549 | 5.196 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2028 | 252 | 252-129 | Tier-2 | Tier-2---18 | 3--3 | 4.2973 | 9 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 2.1229 | 0 | 0 | 2.1229 | 0 | 1.8428 | 2.6841 | 0.68657 | 1.8428 | 2.6841 | 0.68657 | 2.1542 | 3.1377 | 0.68657 | 4.29% | 0.02391 | 0.022726 | 2069.6845 | 324.0484 | 134.0961 | 1611.54 | 2084.0584 | 0 | 0 | 2084.0584 | 7e-05%
2028 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 4.0623 | 220 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 22.0588 | 2.5373 | 8.6939 | 22.0588 | 2.5373 | 8.6939 | 25.787 | 2.9661 | 8.6939 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 20.3065 | 1265 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 168.4859 | 12.6832 | 13.2842 | 168.4859 | 12.6832 | 13.2842 | 196.962 | 14.8268 | 13.2842 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 5.9877 | 433 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 229.1356 | 3.7399 | 61.2682 | 229.1356 | 3.7399 | 61.2682 | 267.8621 | 4.372 | 61.2682 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2028 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 12.0589 | 918 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 264.6183 | 7.5319 | 35.1332 | 264.6183 | 7.5319 | 35.1332 | 309.3418 | 8.8048 | 35.1332 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2028 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 6.3104 | 318 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 4.8841 | 3.9414 | 1.2392 | 4.8841 | 3.9414 | 1.2392 | 5.7095 | 4.6075 | 1.2392 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2028 | 280 | 280-24AE | Tier-2 | Tier-2---12 | 4--4 | 0.5631 | 0 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.56941 | 0 | 0 | 0.56941 | 0 | 0.49428 | 0.35171 | 1.4054 | 0.49428 | 0.35171 | 1.4054 | 0.57782 | 0.41115 | 1.4054 | 0.1557% | 0.037093 | 0.035257 | 9861.3901 | 49.7133 | 8813.1546 | 998.5222 | 10358.7999 | 0 | 0 | 10358.7999 | 1.878e-05%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 27.9316 | 2562 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1099.4968 | 17.4458 | 63.0236 | 1099.4968 | 17.4458 | 63.0236 | 1285.3243 | 20.3943 | 63.0236 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2028 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 5.7761 | 269 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 500.606 | 3.6077 | 138.7599 | 500.606 | 3.6077 | 138.7599 | 585.2141 | 4.2175 | 138.7599 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2028 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.95666 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 53.258 | 0.59752 | 89.1317 | 53.258 | 0.59752 | 89.1317 | 62.2592 | 0.69851 | 89.1317 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 7.5917 | 224 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 433.3562 | 4.7417 | 91.3928 | 433.3562 | 4.7417 | 91.3928 | 506.5984 | 5.5431 | 91.3928 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 8.614 | 942 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 81.1115 | 5.3802 | 15.0758 | 81.1115 | 5.3802 | 15.0758 | 94.8202 | 6.2895 | 15.0758 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2.1411 | 3 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 18.5876 | 1.3373 | 13.8995 | 18.5876 | 1.3373 | 13.8995 | 21.7291 | 1.5633 | 13.8995 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 1.8381 | 85 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 54.8409 | 1.1481 | 47.7682 | 54.8409 | 1.1481 | 47.7682 | 64.1096 | 1.3421 | 47.7682 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2028 | 308 | CB 308 | Tier-2 | Tier-2---18 | 4--3 | 0.8729 | 0 | 100% | 77.7948 | 18.36% | 79.79% | 1.851% | 0.70708 | 0 | 0 | 0.70708 | 0 | 0.61379 | 0.5452 | 1.1258 | 0.61379 | 0.5452 | 1.1258 | 0.71753 | 0.63735 | 1.1258 | 0.9089% | 0.037941 | 0.036063 | 2050.437 | 12.1248 | 1817.8081 | 220.5041 | 2137.6123 | 0 | 0 | 2137.6123 | 2.332e-05%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 3.0796 | 188 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 8.2934 | 1.9235 | 4.3116 | 8.2934 | 1.9235 | 4.3116 | 9.695 | 2.2486 | 4.3116 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 10.0146 | 475 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 30.1439 | 6.255 | 4.8192 | 30.1439 | 6.255 | 4.8192 | 35.2385 | 7.3122 | 4.8192 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2028 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 1.532 | 0 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 244.7238 | 0.95688 | 255.7529 | 244.7238 | 0.95688 | 255.7529 | 286.0849 | 1.1186 | 255.7529 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2028 | 401 | 401-39R | Tier-2 | Tier-2---14 | 4--4 | 0.0585 | 0 | 100% | 323.2323 | 3.193% | 96.7% | 0.1048% | 0.51091 | 0 | 0 | 0.51091 | 0 | 0.4435 | 0.036538 | 12.1379 | 0.4435 | 0.036538 | 12.1379 | 0.51846 | 0.042714 | 12.1379 | 0.1581% | 0.031872 | 0.030295 | 10141.4477 | 77.0794 | 9013.6522 | 1050.7162 | 10652.728 | 0 | 0 | 10652.728 | 1.685e-05%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 0.63484 | 10 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.31798 | 0.39651 | 0.80194 | 0.31798 | 0.39651 | 0.80194 | 0.37173 | 0.46353 | 0.80194 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2028 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 8.7678 | 225 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 17.0436 | 5.4763 | 3.1123 | 17.0436 | 5.4763 | 3.1123 | 19.9241 | 6.4018 | 3.1123 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.87727 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 62.4639 | 0.54794 | 113.9987 | 62.4639 | 0.54794 | 113.9987 | 73.021 | 0.64054 | 113.9987 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2028 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011932 | 0 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074526 | 0 | 0 | 0.0074526 | 0 | 0 | 0.0087122 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2028 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 3.06 | 54 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 90.1294 | 1.9112 | 47.1574 | 90.1294 | 1.9112 | 47.1574 | 105.3623 | 2.2343 | 47.1574 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 1.6544 | 24 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 221.4077 | 1.0333 | 214.2739 | 221.4077 | 1.0333 | 214.2739 | 258.8282 | 1.2079 | 214.2739 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2028 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 0.11231 | 25 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.14837 | 0.070148 | 2.1151 | 0.14837 | 0.070148 | 2.1151 | 0.17345 | 0.082004 | 2.1151 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2028 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 3.4226 | 424 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 180.3315 | 2.1377 | 84.3577 | 180.3315 | 2.1377 | 84.3577 | 210.8095 | 2.499 | 84.3577 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2028 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 2.6673 | 417 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 64.3998 | 1.6659 | 38.6568 | 64.3998 | 1.6659 | 38.6568 | 75.2841 | 1.9475 | 38.6568 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2028 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 0 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.6644 | 0.021411 | 31.0308 | 0.6644 | 0.021411 | 31.0308 | 0.77669 | 0.02503 | 31.0308 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.87803 | 24 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 27.936 | 0.54841 | 50.9401 | 27.936 | 0.54841 | 50.9401 | 32.6575 | 0.6411 | 50.9401 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2028 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 17.882 | 25 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 53.265 | 11.1689 | 4.769 | 53.265 | 11.1689 | 4.769 | 62.2674 | 13.0566 | 4.769 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.030114 | 6 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 4.9855 | 0.018809 | 265.0633 | 4.9855 | 0.018809 | 265.0633 | 5.8282 | 0.021988 | 265.0633 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 9.9068 | 699 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 78.0879 | 6.1877 | 12.6199 | 78.0879 | 6.1877 | 12.6199 | 91.2856 | 7.2335 | 12.6199 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 2.1343 | 19 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 31.153 | 1.333 | 23.3701 | 31.153 | 1.333 | 23.3701 | 36.4183 | 1.5583 | 23.3701 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 1.1486 | 101 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.0065 | 0.71743 | 12.5539 | 9.0065 | 0.71743 | 12.5539 | 10.5287 | 0.83869 | 12.5539 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2028 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.46834 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 33.9963 | 0.29252 | 116.2189 | 33.9963 | 0.29252 | 116.2189 | 39.742 | 0.34196 | 116.2189 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2028 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.23902 | 0 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 0.97851 | 0.14929 | 6.5546 | 0.97851 | 0.14929 | 6.5546 | 1.1439 | 0.17452 | 6.5546 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 17.7839 | 336 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 226.6062 | 11.1076 | 20.4009 | 226.6062 | 11.1076 | 20.4009 | 264.9052 | 12.985 | 20.4009 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 27.7907 | 1376 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 781.526 | 17.3578 | 45.0246 | 781.526 | 17.3578 | 45.0246 | 913.6128 | 20.2914 | 45.0246 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2028 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 1.0255 | 5 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 13.6308 | 0.64053 | 21.2804 | 13.6308 | 0.64053 | 21.2804 | 15.9345 | 0.74879 | 21.2804 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 1.6259 | 6 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 17.6223 | 1.0155 | 17.3525 | 17.6223 | 1.0155 | 17.3525 | 20.6007 | 1.1872 | 17.3525 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2028 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 9.0746 | 475 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 207.1447 | 5.6679 | 36.5471 | 207.1447 | 5.6679 | 36.5471 | 242.1545 | 6.6258 | 36.5471 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 10.35 | 778 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 183.7705 | 6.4645 | 28.4276 | 183.7705 | 6.4645 | 28.4276 | 214.8298 | 7.5571 | 28.4276 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 5.1765 | 270 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 118.0052 | 3.2332 | 36.4979 | 118.0052 | 3.2332 | 36.4979 | 137.9494 | 3.7797 | 36.4979 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.94526 | 13 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 154.3856 | 0.5904 | 261.4946 | 154.3856 | 0.5904 | 261.4946 | 180.4785 | 0.69018 | 261.4946 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2028 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.47553 | 18 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 25.0438 | 0.29701 | 84.3201 | 25.0438 | 0.29701 | 84.3201 | 29.2765 | 0.34721 | 84.3201 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2028 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 2.6021 | 514 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 55.5815 | 1.6253 | 34.1985 | 55.5815 | 1.6253 | 34.1985 | 64.9754 | 1.8999 | 34.1985 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 19.0867 | 1839 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 182.6123 | 11.9213 | 15.3181 | 182.6123 | 11.9213 | 15.3181 | 213.4758 | 13.9362 | 15.3181 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2028 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.70208 | 157 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 4.5649 | 0.43851 | 10.41 | 4.5649 | 0.43851 | 10.41 | 5.3364 | 0.51263 | 10.41 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2028 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 4.4396 | 19 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 27.148 | 2.7729 | 9.7904 | 27.148 | 2.7729 | 9.7904 | 31.7363 | 3.2416 | 9.7904 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 7.7195 | 1158 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 164.0457 | 4.8215 | 34.0237 | 164.0457 | 4.8215 | 34.0237 | 191.7713 | 5.6364 | 34.0237 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2028 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.46496 | 50 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 55.7749 | 0.29041 | 192.0556 | 55.7749 | 0.29041 | 192.0556 | 65.2015 | 0.33949 | 192.0556 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 2.2173 | 249 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 94.2008 | 1.3849 | 68.0203 | 94.2008 | 1.3849 | 68.0203 | 110.1218 | 1.619 | 68.0203 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2028 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 5.5852 | 7 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 167.5586 | 3.4885 | 48.0321 | 167.5586 | 3.4885 | 48.0321 | 195.878 | 4.0781 | 48.0321 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 2.0289 | 237 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 28.6595 | 1.2673 | 22.6154 | 28.6595 | 1.2673 | 22.6154 | 33.5032 | 1.4814 | 22.6154 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 9.4684 | 640 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 85.7236 | 5.9139 | 14.4954 | 85.7236 | 5.9139 | 14.4954 | 100.2118 | 6.9134 | 14.4954 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2028 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 2.7573 | 110 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 33.5626 | 1.7222 | 19.4882 | 33.5626 | 1.7222 | 19.4882 | 39.2351 | 2.0133 | 19.4882 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 3.4339 | 102 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 181.5394 | 2.1448 | 84.6429 | 181.5394 | 2.1448 | 84.6429 | 212.2217 | 2.5073 | 84.6429 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2028 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.052273 | 0 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.1042 | 0.032649 | 3.1915 | 0.1042 | 0.032649 | 3.1915 | 0.12181 | 0.038167 | 3.1915 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2028 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 3.3255 | 21 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 9.1054 | 2.0771 | 4.3837 | 9.1054 | 2.0771 | 4.3837 | 10.6443 | 2.4281 | 4.3837 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 11.8649 | 1745 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 208.243 | 7.4107 | 28.1003 | 208.243 | 7.4107 | 28.1003 | 243.4385 | 8.6632 | 28.1003 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2028 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 17.4926 | 1898 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 233.7156 | 10.9257 | 21.3914 | 233.7156 | 10.9257 | 21.3914 | 273.2162 | 12.7723 | 21.3914 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2028 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 14.2375 | 375 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 1931.0119 | 8.8926 | 217.149 | 1931.0119 | 8.8926 | 217.149 | 2257.3749 | 10.3955 | 217.149 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2028 | 534 | CB 534 | Tier-2 | Tier-2---21 | 4--1 | 0.38371 | 0 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11233 | 0 | 0 | 0.11233 | 0 | 0.097511 | 0.23966 | 0.40687 | 0.097511 | 0.23966 | 0.40687 | 0.11399 | 0.28017 | 0.40687 | 1.782% | 0.060541 | 0.057544 | 104.1456 | 5.1049 | 50.6919 | 48.3488 | 107.6172 | 0 | 0 | 107.6172 | 3.704e-06%
2028 | 296 | 296-66F | Tier-2 | Tier-2---21 | 1--3 | 0.0214 | 0 | 100% | 2.284 | 90.58% | 0% | 9.421% | 0.10241 | 0 | 0 | 0.10241 | 0 | 0.088895 | 0.013366 | 6.6507 | 0.088895 | 0.013366 | 6.6507 | 0.10392 | 0.015625 | 6.6507 | 4.484% | 0.0006178 | 0.00058722 | 3696.9667 | 843.8145 | 35.5403 | 2817.6118 | 3715.1054 | 0 | 0 | 3715.1054 | 3.377e-06%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 17.4388 | 870 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 86.435 | 10.8921 | 7.9356 | 86.435 | 10.8921 | 7.9356 | 101.0435 | 12.733 | 7.9356 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 3.8686 | 155 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 158.4522 | 2.4163 | 65.5774 | 158.4522 | 2.4163 | 65.5774 | 185.2324 | 2.8246 | 65.5774 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2028 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 3.9246 | 150 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 142.9356 | 2.4513 | 58.3104 | 142.9356 | 2.4513 | 58.3104 | 167.0934 | 2.8656 | 58.3104 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 0.43788 | 86 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 17.4277 | 0.27349 | 63.7221 | 17.4277 | 0.27349 | 63.7221 | 20.3731 | 0.31972 | 63.7221 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 6.1356 | 318 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 94.0298 | 3.8322 | 24.5366 | 94.0298 | 3.8322 | 24.5366 | 109.922 | 4.4799 | 24.5366 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 13.604 | 933 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 783.9515 | 8.4969 | 92.263 | 783.9515 | 8.4969 | 92.263 | 916.4483 | 9.933 | 92.263 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 8.2782 | 212 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 23.3118 | 5.1705 | 4.5086 | 23.3118 | 5.1705 | 4.5086 | 27.2518 | 6.0444 | 4.5086 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2028 | 461 | CB 461 | Tier-2 | Tier-2---15 | 2--4 | 2.3375 | 0 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 4.9747 | 0 | 0 | 4.9747 | 0 | 4.3183 | 1.46 | 2.9578 | 4.3183 | 1.46 | 2.9578 | 5.0482 | 1.7068 | 2.9578 | 4.883% | 0.0097562 | 0.0092733 | 10441.6529 | 2274.299 | 1515.1673 | 6652.1866 | 10448.9777 | 0 | 0 | 10448.9777 | 0.000164%
2028 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 16.0805 | 603 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 140.6197 | 10.0437 | 14.0008 | 140.6197 | 10.0437 | 14.0008 | 164.386 | 11.7412 | 14.0008 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2028 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.11194 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 6.4939 | 0.069916 | 92.8817 | 6.4939 | 0.069916 | 92.8817 | 7.5915 | 0.081732 | 92.8817 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 5.7011 | 315 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 347.982 | 3.5609 | 97.7242 | 347.982 | 3.5609 | 97.7242 | 406.795 | 4.1627 | 97.7242 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 12.622 | 1027 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1002.9466 | 7.8836 | 127.22 | 1002.9466 | 7.8836 | 127.22 | 1172.456 | 9.216 | 127.22 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 13.7044 | 1345 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 306.5225 | 8.5596 | 35.8104 | 306.5225 | 8.5596 | 35.8104 | 358.3282 | 10.0063 | 35.8104 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2028 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 4.354 | 0 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 20.1346 | 2.7195 | 7.4039 | 20.1346 | 2.7195 | 7.4039 | 23.5376 | 3.1791 | 7.4039 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2028 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 6.0637 | 134 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 45.8033 | 3.7873 | 12.0939 | 45.8033 | 3.7873 | 12.0939 | 53.5446 | 4.4274 | 12.0939 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2028 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 12.4352 | 2343 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 307.5141 | 7.7669 | 39.5929 | 307.5141 | 7.7669 | 39.5929 | 359.4875 | 9.0796 | 39.5929 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2028 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 8.4532 | 216 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 138.3721 | 5.2798 | 26.2079 | 138.3721 | 5.2798 | 26.2079 | 161.7586 | 6.1721 | 26.2079 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2028 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.18447 | 1 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.3218 | 0.11522 | 20.1516 | 2.3218 | 0.11522 | 20.1516 | 2.7142 | 0.13469 | 20.1516 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 10.2425 | 319 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 64.9052 | 6.3973 | 10.1457 | 64.9052 | 6.3973 | 10.1457 | 75.8749 | 7.4786 | 10.1457 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 7.3926 | 433 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 152.0946 | 4.6173 | 32.9399 | 152.0946 | 4.6173 | 32.9399 | 177.8003 | 5.3977 | 32.9399 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2028 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 4.8975 | 133 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 66.0073 | 3.0589 | 21.5786 | 66.0073 | 3.0589 | 21.5786 | 77.1633 | 3.5759 | 21.5786 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 0.074242 | 9 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.28573 | 0.046371 | 6.1619 | 0.28573 | 0.046371 | 6.1619 | 0.33402 | 0.054208 | 6.1619 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2028 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.13314 | 0 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 5.7351 | 0.08316 | 68.964 | 5.7351 | 0.08316 | 68.964 | 6.7044 | 0.097215 | 68.964 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 0.85906 | 38 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.013145 | 0.53656 | 0.024499 | 0.013145 | 0.53656 | 0.024499 | 0.015367 | 0.62725 | 0.024499 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 3.4163 | 163 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 96.7369 | 2.1338 | 45.3358 | 96.7369 | 2.1338 | 45.3358 | 113.0865 | 2.4944 | 45.3358 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2028 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 12.5079 | 404 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1593.0007 | 7.8123 | 203.909 | 1593.0007 | 7.8123 | 203.909 | 1862.236 | 9.1327 | 203.909 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2028 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 10.6068 | 689 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 489.052 | 6.6249 | 73.8203 | 489.052 | 6.6249 | 73.8203 | 571.7074 | 7.7446 | 73.8203 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2028 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 31.2755 | 3380 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 696.8774 | 19.5344 | 35.6744 | 696.8774 | 19.5344 | 35.6744 | 814.6577 | 22.8359 | 35.6744 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 12.3091 | 638 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 583.1815 | 7.6881 | 75.8547 | 583.1815 | 7.6881 | 75.8547 | 681.7459 | 8.9875 | 75.8547 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2028 | 188 | 188-11F | Tier-2 | Tier-2---7 | 3--5 | 1.2193 | 0 | 100% | 2209.344 | 99.86% | 0% | 0.1429% | 109.2062 | 0 | 0 | 109.2062 | 0 | 94.7981 | 0.76156 | 124.4786 | 94.7981 | 0.76156 | 124.4786 | 110.8201 | 0.89027 | 124.4786 | 4.943% | 0.019333 | 0.018376 | 114277.2032 | 24326.824 | 78.3726 | 89872.0066 | 114285.7081 | 0 | 0 | 114285.7081 | 0.003601%
2028 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 0.29224 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.73388 | 0.18253 | 4.0207 | 0.73388 | 0.18253 | 4.0207 | 0.85792 | 0.21338 | 4.0207 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2028 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 0.3025 | 0 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 114.3559 | 0.18894 | 605.2556 | 114.3559 | 0.18894 | 605.2556 | 133.6834 | 0.22087 | 605.2556 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2028 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 6.4721 | 550 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 182.2987 | 4.0424 | 45.0965 | 182.2987 | 4.0424 | 45.0965 | 213.1093 | 4.7256 | 45.0965 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2028 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 2.8459 | 44 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.2511 | 1.7775 | 6.3298 | 11.2511 | 1.7775 | 6.3298 | 13.1527 | 2.0779 | 6.3298 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 6.8671 | 1644 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 69.9765 | 4.2891 | 16.315 | 69.9765 | 4.2891 | 16.315 | 81.8033 | 5.014 | 16.315 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2028 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.085985 | 0 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.0369 | 0.053705 | 56.5474 | 3.0369 | 0.053705 | 56.5474 | 3.5502 | 0.062782 | 56.5474 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2028 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 2.8273 | 20 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 4.7628 | 1.7659 | 2.6971 | 4.7628 | 1.7659 | 2.6971 | 5.5678 | 2.0643 | 2.6971 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2028 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 1.6392 | 113 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.4094 | 1.0238 | 4.3068 | 4.4094 | 1.0238 | 4.3068 | 5.1546 | 1.1969 | 4.3068 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 6.7626 | 34 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 126.6489 | 4.2238 | 29.9845 | 126.6489 | 4.2238 | 29.9845 | 148.054 | 4.9377 | 29.9845 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2028 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 29.745 | 3357 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 218.0371 | 18.5784 | 11.736 | 218.0371 | 18.5784 | 11.736 | 254.8879 | 21.7184 | 11.736 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 3.6661 | 221 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 216.1178 | 2.2898 | 94.3826 | 216.1178 | 2.2898 | 94.3826 | 252.6441 | 2.6768 | 94.3826 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 5.2246 | 108 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 43.3507 | 3.2632 | 13.2846 | 43.3507 | 3.2632 | 13.2846 | 50.6775 | 3.8148 | 13.2846 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 11.5796 | 1397 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 211.088 | 7.2325 | 29.1861 | 211.088 | 7.2325 | 29.1861 | 246.7643 | 8.4549 | 29.1861 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 1.3334 | 164 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 276.8533 | 0.8328 | 332.4376 | 276.8533 | 0.8328 | 332.4376 | 323.6447 | 0.97355 | 332.4376 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2028 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 2.7707 | 131 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 67.2079 | 1.7305 | 38.8368 | 67.2079 | 1.7305 | 38.8368 | 78.5668 | 2.023 | 38.8368 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2028 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.14849 | 7 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 5.7481 | 0.092742 | 61.9791 | 5.7481 | 0.092742 | 61.9791 | 6.7196 | 0.10842 | 61.9791 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2028 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 8.7312 | 1001 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 124.5986 | 5.4534 | 22.8478 | 124.5986 | 5.4534 | 22.8478 | 145.6572 | 6.3751 | 22.8478 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2028 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 3.232 | 330 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 159.3136 | 2.0187 | 78.9208 | 159.3136 | 2.0187 | 78.9208 | 186.2394 | 2.3598 | 78.9208 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2028 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.13579 | 2 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 2.7314 | 0.084816 | 32.2035 | 2.7314 | 0.084816 | 32.2035 | 3.193 | 0.099151 | 32.2035 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.038118 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.0652 | 0.023808 | 44.7399 | 1.0652 | 0.023808 | 44.7399 | 1.2452 | 0.027832 | 44.7399 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2028 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 17.8309 | 1143 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 109.6733 | 11.137 | 9.8476 | 109.6733 | 11.137 | 9.8476 | 128.2093 | 13.0193 | 9.8476 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 1.6328 | 9 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.4162 | 1.0198 | 10.2138 | 10.4162 | 1.0198 | 10.2138 | 12.1767 | 1.1922 | 10.2138 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2028 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.43141 | 5 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 4.9295 | 0.26946 | 18.2942 | 4.9295 | 0.26946 | 18.2942 | 5.7626 | 0.315 | 18.2942 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.052462 | 10 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.0599 | 0.032767 | 93.3816 | 3.0599 | 0.032767 | 93.3816 | 3.577 | 0.038305 | 93.3816 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2028 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 0.41062 | 16 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.088634 | 0.25647 | 0.34559 | 0.088634 | 0.25647 | 0.34559 | 0.10361 | 0.29982 | 0.34559 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 7.3674 | 675 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 171.5694 | 4.6016 | 37.2847 | 171.5694 | 4.6016 | 37.2847 | 200.5666 | 5.3793 | 37.2847 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.99152 | 143 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 75.8931 | 0.61929 | 122.5483 | 75.8931 | 0.61929 | 122.5483 | 88.7199 | 0.72396 | 122.5483 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2028 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 3.9579 | 66 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 109.5158 | 2.4721 | 44.3011 | 109.5158 | 2.4721 | 44.3011 | 128.0252 | 2.8899 | 44.3011 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 8.6068 | 696 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 106.6551 | 5.3757 | 19.8402 | 106.6551 | 5.3757 | 19.8402 | 124.681 | 6.2843 | 19.8402 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 4.5924 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 410.2539 | 2.8684 | 143.0277 | 410.2539 | 2.8684 | 143.0277 | 479.5915 | 3.3531 | 143.0277 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2028 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 0.49168 | 169 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 1.822 | 0.3071 | 5.933 | 1.822 | 0.3071 | 5.933 | 2.1299 | 0.359 | 5.933 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2028 | 214 | CB 214 | Tier-3 | Tier-3---20 | 1--5 | 0.040909 | 0 | 100% | 59.1996 | 99.88% | 0% | 0.1188% | 2.9269 | 0 | 0 | 2.9269 | 0 | 2.5407 | 0.025551 | 99.4367 | 2.5407 | 0.025551 | 99.4367 | 2.9702 | 0.02987 | 99.4367 | 4.944% | 0.0002016 | 0.00019162 | 293649.0501 | 47091.7983 | 966.5627 | 245590.6891 | 293667.224 | 0 | 0 | 293667.224 | 9.652e-05%
2028 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.91593 | 107 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 91.914 | 0.57208 | 160.6657 | 91.914 | 0.57208 | 160.6657 | 107.4485 | 0.66877 | 160.6657 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2028 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.036174 | 0 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.0815 | 0.022594 | 47.8669 | 1.0815 | 0.022594 | 47.8669 | 1.2643 | 0.026413 | 47.8669 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 11.2661 | 800 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 649.5434 | 7.0367 | 92.308 | 649.5434 | 7.0367 | 92.308 | 759.3236 | 8.226 | 92.308 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 4.9145 | 192 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 208.5089 | 3.0696 | 67.9278 | 208.5089 | 3.0696 | 67.9278 | 243.7493 | 3.5884 | 67.9278 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2028 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 1.0576 | 36 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 5.9914 | 0.66055 | 9.0703 | 5.9914 | 0.66055 | 9.0703 | 7.004 | 0.77219 | 9.0703 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2028 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.034091 | 0 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.1426 | 0.021293 | 53.6602 | 1.1426 | 0.021293 | 53.6602 | 1.3357 | 0.024892 | 53.6602 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2028 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 7.2415 | 169 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 91.0147 | 4.523 | 20.1229 | 91.0147 | 4.523 | 20.1229 | 106.3972 | 5.2874 | 20.1229 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2028 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 5.9928 | 403 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 229.2998 | 3.743 | 61.2603 | 229.2998 | 3.743 | 61.2603 | 268.0541 | 4.3757 | 61.2603 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 8.9743 | 875 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 479.4093 | 5.6052 | 85.5289 | 479.4093 | 5.6052 | 85.5289 | 560.435 | 6.5526 | 85.5289 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2028 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.026705 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.2769 | 0.01668 | 76.5562 | 1.2769 | 0.01668 | 76.5562 | 1.4927 | 0.019499 | 76.5562 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2028 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 1.221 | 60 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 95.1404 | 0.76264 | 124.7517 | 95.1404 | 0.76264 | 124.7517 | 111.2202 | 0.89153 | 124.7517 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2028 | 401 | 401-684R | Tier-2 | Tier-2---21 | 4--1 | 0.051326 | 0 | 100% | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049319 | 0 | 0 | 0.049319 | 0 | 0.042812 | 0.032058 | 1.3355 | 0.042812 | 0.032058 | 1.3355 | 0.050048 | 0.037476 | 1.3355 | 3.09% | 0.030395 | 0.028891 | 52.5129 | 8.9983 | 14.8334 | 28.6812 | 53.5406 | 0 | 0 | 53.5406 | 1.626e-06%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 2.1386 | 171 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 46.343 | 1.3357 | 34.6947 | 46.343 | 1.3357 | 34.6947 | 54.1755 | 1.5615 | 34.6947 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2028 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.057008 | 0 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.51583 | 0.035607 | 14.4868 | 0.51583 | 0.035607 | 14.4868 | 0.60301 | 0.041625 | 14.4868 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2028 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 5.5421 | 257 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 49.9494 | 3.4615 | 14.4299 | 49.9494 | 3.4615 | 14.4299 | 58.3914 | 4.0466 | 14.4299 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2028 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.043939 | 0 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.46405 | 0.027444 | 16.9092 | 0.46405 | 0.027444 | 16.9092 | 0.54248 | 0.032082 | 16.9092 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2028 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 3.2034 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 58.9313 | 2.0008 | 29.4541 | 58.9313 | 2.0008 | 29.4541 | 68.8914 | 2.3389 | 29.4541 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.64962 | 17 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 30.3569 | 0.40575 | 74.8174 | 30.3569 | 0.40575 | 74.8174 | 35.4876 | 0.47432 | 74.8174 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2028 | 221 | 221-1235F | Tier-3 | Tier-3---18 | 5--2 | 0.0489 | 0 | 100% | 236.1769 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.030542 | 0 | 0 | 0.030542 | 0 | 0 | 0.035704 | 0 | 0% | 0.16409 | 0.15597 | 1439.2989 | 2.105 | 1306.2711 | 130.9227 | 1514.2545 | 0 | 0 | 1514.2545 | 0%

## Veg_Detail_Inspection
Veg Detail Inspection - Risk & Cost Benefit | [30 empty] | Summary Table |  |  | Baseline 2024 | Baseline 2024 | Baseline 2024 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R
[31 empty] | Year | Total Units (Miles) | Total Units (Trees) | WF + PSPS + PEDS Risk Baseline (K$) | Baseline Risk Reduction (K$) | Baseline Risk Reduction (%) | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR WACC | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR HDR | PV Risk Reduced (K$) Year 40 | PV Total Cost Capital + O&M (K$) Year 40 | CBR SDR | Service Territory Risk Reduction (%) | Transmission Units (Miles)
back to index | [30 empty] | 2026 | 8736.8183 | 485500 | 3016574.4786 | 143144.891 | 4.745% | 136550.501 | 9025.9483 | 15.1287 | 136550.501 | 9025.9483 | 15.1287 | 143846.5817 | 9508.2171 | 15.1287 | 4.72% | 1763.1817
[10 empty] | Assumptions | Value | Units | Last Update | Comments |  |  |  | Notes | [12 empty] | 2027 | 8736.8183 | 485500 | 3016574.4786 | 143144.891 | 4.745% | 130259.9009 | 8610.1414 | 15.1287 | 130259.9009 | 8610.1414 | 15.1287 | 144551.712 | 9554.826 | 15.1287 | 4.72% | 1763.1817
[10 empty] | Capital Cost only in Year 0 | 1.083 | K$/mile | 2025-06-30 |  |  |  |  | [1] SDG&E does not calculate the risk reduction for the safety and reliability attributes for this program. All risk reduction is considered to fall within the financial attribute. | [12 empty] | 2028 | 8736.8183 | 485500 | 3016574.4786 | 143144.891 | 4.745% | 124259.0958 | 8213.49 | 15.1287 | 124259.0958 | 8213.49 | 15.1287 | 145260.2988 | 9601.6633 | 15.1287 | 4.72% | 1763.1817
[10 empty] | Service Drop factor | 0% | % | 2025-06-30 |  |  |  |  | [2] To avoid double counting of foundational cost SDG&E assumes no foundational cost for this program. | [12 empty] | Total 2026-2028 | 26210.4548 | 1456500 | 9049723.4358 | 429434.6731 | 4.745% | 391069.4977 | 25849.5796 | 15.1287 | 391069.4977 | 25849.5796 | 15.1287 | 433658.5925 | 28664.7064 | 15.1287 | 14.16% | 5289.5452
[10 empty] | OH to UG conversion factor | 0% | % | 2025-06-30
[10 empty] | Long-term Ongoing costs | 0 | $/unit | 2025-06-30
[10 empty] | Lifetime | 1 | Years | 2025-06-30
[10 empty] | Inflation Assumption to adjust Baseline | 2.5% |  | 2025-06-30
[10 empty] | Mitigation Effectiveness Estimate (%) | 4.95% | % | 2025-06-30
[10 empty] | Additional Installation Cost (O&M) only in Year 0 | 0 | M$/mile | 2025-06-30
[14 empty] | [1] | [1] | [1] | [2]
[9 empty] | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | Baseline 2025 | WACC | WACC | WACC | H.D.R | H.D.R | H.D.R | S.D.R | S.D.R | S.D.R |  |  |  | Pre - Mitigation CoRE |  |  |  | Post - Mitigation CoRE
Year | Feeder | Feeder Segment | HFTD Tier | Tranche ID HTM | Tranche ID Quintile | Total Circuit Miles | Total Units | %Trees in the Scope | WF + PSPS + PEDS Risk Baseline (K$/year) | Baseline Wildfire (%) | Baseline PSPS (%) | Baseline PEDS (%) | Risk Reduction (K$/year) | Safety Risk Reduction (K$/year) | Reliability Risk Reduction (K$/year) | Financial Risk Reduction (K$/year) | Mitigation Annual Cost (K$/year) | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR WACC | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR HDR | PV Risk Reduced (K$) Year N | PV Total Cost Capital + O&M (K$) Year N | CBR SDR | Risk Reduction % | Pre-Mitigation LoRE | Post-Mitigation LoRE | Pre-Mitigated CoRE [K$] | Pre-Mitigated CoRE Safety [K$] | Pre-Mitigated CoRE Reliability [K$] | Pre-Mitigated CoRE Financial [K$] | Post-Mitigated CoRE [K$] | Post-Mitigated CoRE Safety [K$] | Post-Mitigated CoRE Reliability [K$] | Post-Mitigated CoRE Financial [K$] | Service Territory Risk Reduction (%)
2026 | 1153 | CB 1153 | Tier-1 | Non-HFTD---19 | 1--2 | 0.09697 | 1 | 100% | 0.54442 | 68.22% | 0% | 31.78% | 0.018384 | 0 | 0 | 0.018384 | 0 | 0.017537 | 0.10018 | 0.17506 | 0.017537 | 0.10018 | 0.17506 | 0.018474 | 0.10553 | 0.17506 | 3.377% | 0.0005088 | 0.00048361 | 1070.015 | 113.1086 | 30.893 | 926.0134 | 1087.7256 | 0 | 0 | 1087.7256 | 6.062e-07%
2026 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 6.8811 | 261 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 473.1787 | 7.1088 | 66.5626 | 473.1787 | 7.1088 | 66.5626 | 498.4613 | 7.4886 | 66.5626 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2026 | 509 | 509-1227R | Tier-1 | Non-HFTD---13 | 2--2 | 2.0561 | 86 | 100% | 6.8178 | 77.37% | 0% | 22.63% | 0.26111 | 0 | 0 | 0.26111 | 0 | 0.24908 | 2.1241 | 0.11726 | 0.24908 | 2.1241 | 0.11726 | 0.26239 | 2.2376 | 0.11726 | 3.83% | 0.0063694 | 0.0060541 | 1070.3915 | 53.8343 | 522.4019 | 494.1553 | 1083.0058 | 0 | 0 | 1083.0058 | 8.61e-06%
2026 | 142 | 142-8R | Tier-1 | Non-HFTD---8 | 3--2 | 6.7481 | 216 | 100% | 40.8893 | 6.402% | 80.66% | 12.94% | 0.12957 | 0 | 0 | 0.12957 | 0 | 0.1236 | 6.9715 | 0.017729 | 0.1236 | 6.9715 | 0.017729 | 0.1302 | 7.3439 | 0.017729 | 0.3169% | 0.027724 | 0.026352 | 1474.8579 | 5.0539 | 1173.9231 | 295.8809 | 1546.7485 | 0 | 0 | 1546.7485 | 4.273e-06%
2026 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 0 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.73012 | 0.035415 | 20.6162 | 0.73012 | 0.035415 | 20.6162 | 0.76913 | 0.037307 | 20.6162 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2026 | 391 | CB 391 | Tier-1 | Non-HFTD---2 | 4--4 | 0.66137 | 36 | 100% | 550.2041 | 0.5245% | 99.39% | 0.08518% | 0.14286 | 0 | 0 | 0.14286 | 0 | 0.13628 | 0.68326 | 0.19945 | 0.13628 | 0.68326 | 0.19945 | 0.14356 | 0.71977 | 0.19945 | 0.02597% | 0.089115 | 0.084704 | 6174.0912 | 11.3908 | 5617.0317 | 545.6688 | 6493.938 | 0 | 0 | 6493.938 | 4.711e-06%
2026 | 84 | CB 84 | Tier-1 | Non-HFTD---12 | 3--2 | 6.597 | 272 | 100% | 11.1569 | 60.04% | 0% | 39.96% | 0.33156 | 0 | 0 | 0.33156 | 0 | 0.31628 | 6.8153 | 0.046408 | 0.31628 | 6.8153 | 0.046408 | 0.33318 | 7.1794 | 0.046408 | 2.972% | 0.018717 | 0.01779 | 596.0964 | 9.118 | 324.3476 | 262.6307 | 608.5026 | 0 | 0 | 608.5026 | 1.093e-05%
2026 | 325 | 325-25 | Tier-1 | Non-HFTD---13 | 1--3 | 1.2847 | 29 | 100% | 8.3612 | 88.04% | 0% | 11.96% | 0.36437 | 0 | 0 | 0.36437 | 0 | 0.34758 | 1.3272 | 0.2619 | 0.34758 | 1.3272 | 0.2619 | 0.36615 | 1.3981 | 0.2619 | 4.358% | 0.0037654 | 0.003579 | 2220.5219 | 1.0278 | 1973.9755 | 245.5186 | 2234.3551 | 0 | 0 | 2234.3551 | 1.202e-05%
2026 | 221 | 221-1466 | Tier-3 | Not Applicable | Not Applicable | 0.6294 | 0 | 100% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.65023 | 0 | 0 | 0.65023 | 0 | 0 | 0.68497 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2026 | 390 | CB 390 | Tier-1 | Non-HFTD---2 | 5--4 | 1.4761 | 48 | 100% | 555.1958 | 4.119% | 95.66% | 0.2245% | 1.1319 | 0 | 0 | 1.1319 | 0 | 1.0797 | 1.5249 | 0.70805 | 1.0797 | 1.5249 | 0.70805 | 1.1374 | 1.6064 | 0.70805 | 0.2039% | 0.093583 | 0.088951 | 5932.6308 | 27.2019 | 5249.9711 | 655.4577 | 6228.8647 | 0 | 0 | 6228.8647 | 3.733e-05%
2026 | 445 | 445-1315 | Tier-2 | Tier-2---19 | 1--5 | 0.080871 | 0 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 1.294 | 0 | 0 | 1.294 | 0 | 1.2344 | 0.083548 | 14.7752 | 1.2344 | 0.083548 | 14.7752 | 1.3004 | 0.088012 | 14.7752 | 4.93% | 0.000636 | 0.00060452 | 41272.5846 | 5558.0973 | 1215.1763 | 34499.311 | 41281.3528 | 0 | 0 | 41281.3528 | 4.267e-05%
2026 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 10.7038 | 1013 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 308.8644 | 11.058 | 27.9313 | 308.8644 | 11.058 | 27.9313 | 325.3674 | 11.6489 | 27.9313 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2026 | 93 | CB 93 | Tier-1 | Non-HFTD---3 | 3--4 | 6.2065 | 398 | 100% | 117.8522 | 49.76% | 46.78% | 3.462% | 2.9028 | 0 | 0 | 2.9028 | 0 | 2.7691 | 6.4119 | 0.43186 | 2.7691 | 6.4119 | 0.43186 | 2.917 | 6.7545 | 0.43186 | 2.463% | 0.023557 | 0.022391 | 5002.7692 | 337.5468 | 2573.6674 | 2091.555 | 5133.6638 | 0 | 0 | 5133.6638 | 9.572e-05%
2026 | 733 | 733-20AE | Tier-1 | Non-HFTD---8 | 3--2 | 9.4582 | 571 | 100% | 39.7294 | 85.07% | 0% | 14.93% | 1.6731 | 0 | 0 | 1.6731 | 0 | 1.596 | 9.7712 | 0.16334 | 1.596 | 9.7712 | 0.16334 | 1.6813 | 10.2933 | 0.16334 | 4.211% | 0.026087 | 0.024795 | 1522.9809 | 217.8105 | 467.7091 | 837.4613 | 1534.8195 | 0 | 0 | 1534.8195 | 5.517e-05%
2026 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 15.066 | 1487 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 141.6855 | 15.5645 | 9.1031 | 141.6855 | 15.5645 | 9.1031 | 149.2559 | 16.3962 | 9.1031 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2026 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 2.2173 | 257 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 103.5189 | 2.2907 | 45.1917 | 103.5189 | 2.2907 | 45.1917 | 109.0501 | 2.4131 | 45.1917 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2026 | 1085 | CB 1085 | Tier-1 | Non-HFTD---4 | 2--4 | 0.4608 | 15 | 100% | 121.8151 | 29.33% | 70.28% | 0.3892% | 1.7686 | 0 | 0 | 1.7686 | 0 | 1.6871 | 0.47604 | 3.5439 | 1.6871 | 0.47604 | 3.5439 | 1.7772 | 0.50148 | 3.5439 | 1.452% | 0.009242 | 0.0087845 | 13180.5987 | 392.6277 | 10019.0268 | 2768.9443 | 13665.6902 | 0 | 0 | 13665.6902 | 5.832e-05%
2026 | 299 | CB 299 | Tier-1 | Non-HFTD---11 | 1--3 | 0.95907 | 13 | 100% | 9.1156 | 92.89% | 0% | 7.105% | 0.41916 | 0 | 0 | 0.41916 | 0 | 0.39985 | 0.99081 | 0.40356 | 0.39985 | 0.99081 | 0.40356 | 0.42122 | 1.0438 | 0.40356 | 4.598% | 0.0028978 | 0.0027544 | 3145.7096 | 173.9595 | 1876.4075 | 1095.3426 | 3157.3492 | 0 | 0 | 3157.3492 | 1.382e-05%
2026 | 732 | 732-15R | Tier-1 | Non-HFTD---1 | 3--5 | 5.2317 | 420 | 100% | 342.6373 | 98.93% | 0% | 1.067% | 16.7796 | 0 | 0 | 16.7796 | 0 | 16.0066 | 5.4048 | 2.9615 | 16.0066 | 5.4048 | 2.9615 | 16.8618 | 5.6936 | 2.9615 | 4.897% | 0.02096 | 0.019923 | 16347.0441 | 3636.1945 | 124.2963 | 12586.5533 | 16356.1285 | 0 | 0 | 16356.1285 | 0.0005533%
2026 | 1119 | 1119-6F | Tier-1 | Non-HFTD---11 | 1--4 | 0.65508 | 30 | 100% | 14.1126 | 96.32% | 0% | 3.68% | 0.67286 | 0 | 0 | 0.67286 | 0 | 0.64187 | 0.67676 | 0.94845 | 0.64187 | 0.67676 | 0.94845 | 0.67616 | 0.71292 | 0.94845 | 4.768% | 0.002277 | 0.0021643 | 6197.8946 | 838.8203 | 861.0344 | 4498.0399 | 6209.7735 | 0 | 0 | 6209.7735 | 2.219e-05%
2026 | 256 | CB 256 | Tier-1 | Non-HFTD---11 | 2--2 | 3.543 | 127 | 100% | 11.4393 | 77.87% | 0% | 22.13% | 0.44094 | 0 | 0 | 0.44094 | 0 | 0.42063 | 3.6602 | 0.11492 | 0.42063 | 3.6602 | 0.11492 | 0.4431 | 3.8558 | 0.11492 | 3.855% | 0.011638 | 0.011062 | 982.9441 | 22.1853 | 662.0367 | 298.7221 | 994.2718 | 0 | 0 | 994.2718 | 1.454e-05%
2026 | 572 | CB 572 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1793 | 12 | 100% | 3.33 | 52.2% | 0% | 47.8% | 0.086046 | 0 | 0 | 0.086046 | 0 | 0.082082 | 1.2183 | 0.067373 | 0.082082 | 1.2183 | 0.067373 | 0.086468 | 1.2834 | 0.067373 | 2.584% | 0.0045428 | 0.0043179 | 733.0269 | 0.26885 | 414.4483 | 318.3098 | 751.2737 | 0 | 0 | 751.2737 | 2.837e-06%
2026 | 901 | 901-1124 | Tier-1 | Non-HFTD---1 | 2--5 | 2.1134 | 202 | 100% | 225.4814 | 99.29% | 0% | 0.709% | 11.0822 | 0 | 0 | 11.0822 | 0 | 10.5717 | 2.1833 | 4.842 | 10.5717 | 2.1833 | 4.842 | 11.1365 | 2.3 | 4.842 | 4.915% | 0.0087544 | 0.0083211 | 25756.3496 | 4178.6743 | 36.5656 | 21541.1098 | 25765.8596 | 0 | 0 | 25765.8596 | 0.0003654%
2026 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 3.165 | 217 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 16.5472 | 3.2698 | 5.0607 | 16.5472 | 3.2698 | 5.0607 | 17.4313 | 3.4445 | 5.0607 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2026 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 8.4832 | 262 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 237.9521 | 8.7639 | 27.1514 | 237.9521 | 8.7639 | 27.1514 | 250.6662 | 9.2322 | 27.1514 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2026 | 546 | 546-14R | Tier-1 | Non-HFTD---1 | 3--4 | 3.7622 | 61 | 100% | 227.2127 | 1.45% | 97.43% | 1.118% | 0.16304 | 0 | 0 | 0.16304 | 0 | 0.15553 | 3.8867 | 0.040017 | 0.15553 | 3.8867 | 0.040017 | 0.16384 | 4.0943 | 0.040017 | 0.07176% | 0.020679 | 0.019656 | 10987.501 | 12.3302 | 9969.5471 | 1005.6237 | 11551.4115 | 0 | 0 | 11551.4115 | 5.377e-06%
2026 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 12.0339 | 277 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 284.8981 | 12.4322 | 22.9162 | 284.8981 | 12.4322 | 22.9162 | 300.1206 | 13.0964 | 22.9162 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2026 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 6.8671 | 1649 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 76.8984 | 7.0943 | 10.8394 | 76.8984 | 7.0943 | 10.8394 | 81.0071 | 7.4734 | 10.8394 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2026 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 9.4852 | 776 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 550.6852 | 9.7991 | 56.1973 | 550.6852 | 9.7991 | 56.1973 | 580.1091 | 10.3227 | 56.1973 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2026 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 13.8235 | 537 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 18.954 | 14.2809 | 1.3272 | 18.954 | 14.2809 | 1.3272 | 19.9668 | 15.044 | 1.3272 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2026 | 280 | CB 280 | Tier-2 | Tier-2---14 | 4--4 | 4.0675 | 139 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 2.4753 | 0 | 0 | 2.4753 | 0 | 2.3613 | 4.2021 | 0.56194 | 2.3613 | 4.2021 | 0.56194 | 2.4875 | 4.4266 | 0.56194 | 0.7965% | 0.042409 | 0.04031 | 7328.4886 | 170.2669 | 5820.5339 | 1337.6878 | 7648.7329 | 0 | 0 | 7648.7329 | 8.163e-05%
2026 | 322 | CB 322 | Tier-1 | Non-HFTD---8 | 3--3 | 6.9822 | 212 | 100% | 42.0776 | 89.49% | 0% | 10.51% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.7781 | 7.2133 | 0.2465 | 1.7781 | 7.2133 | 0.2465 | 1.8731 | 7.5987 | 0.2465 | 4.43% | 0.018945 | 0.018007 | 2221.0419 | 151.6209 | 1083.6314 | 985.7895 | 2233.1993 | 0 | 0 | 2233.1993 | 6.147e-05%
2026 | 56 | CB 56 | Tier-1 | Non-HFTD---3 | 3--4 | 3.7124 | 66 | 100% | 122.2122 | 9.667% | 86.95% | 3.388% | 0.58481 | 0 | 0 | 0.58481 | 0 | 0.55787 | 3.8352 | 0.14546 | 0.55787 | 3.8352 | 0.14546 | 0.58768 | 4.0401 | 0.14546 | 0.4785% | 0.023301 | 0.022147 | 5245.0232 | 5.0181 | 4537.7925 | 702.2126 | 5491.767 | 0 | 0 | 5491.767 | 1.929e-05%
2026 | 80 | 80-564 | Tier-1 | Non-HFTD---8 | 3--2 | 9.7153 | 219 | 100% | 31.4137 | 77.77% | 0% | 22.23% | 1.2093 | 0 | 0 | 1.2093 | 0 | 1.1536 | 10.0368 | 0.11494 | 1.1536 | 10.0368 | 0.11494 | 1.2152 | 10.5731 | 0.11494 | 3.85% | 0.028026 | 0.026639 | 1120.8843 | 9.0416 | 839.8211 | 272.0216 | 1133.8606 | 0 | 0 | 1133.8606 | 3.988e-05%
2026 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 0.074242 | 8 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.31399 | 0.076699 | 4.0938 | 0.31399 | 0.076699 | 4.0938 | 0.33077 | 0.080798 | 4.0938 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2026 | 480 | 480-32 | Tier-1 | Non-HFTD---10 | 3--2 | 7.1091 | 262 | 100% | 17.2812 | 70.33% | 0% | 29.67% | 0.60164 | 0 | 0 | 0.60164 | 0 | 0.57392 | 7.3443 | 0.078145 | 0.57392 | 7.3443 | 0.078145 | 0.60459 | 7.7368 | 0.078145 | 3.481% | 0.019568 | 0.018599 | 883.1465 | 0.19748 | 644.9364 | 238.0126 | 896.7913 | 0 | 0 | 896.7913 | 1.984e-05%
2026 | 461 | 461-644R | Tier-1 | Non-HFTD---17 | 1--3 | 0.27861 | 0 | 100% | 1.9699 | 87.49% | 0% | 12.51% | 0.085309 | 0 | 0 | 0.085309 | 0 | 0.081379 | 0.28783 | 0.28273 | 0.081379 | 0.28783 | 0.28273 | 0.085727 | 0.30321 | 0.28273 | 4.331% | 0.0008654 | 0.00082256 | 2276.3126 | 196.7287 | 798.4144 | 1281.1695 | 2291.1467 | 0 | 0 | 2291.1467 | 2.813e-06%
2026 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 4.5645 | 666 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 14.3975 | 4.7156 | 3.0532 | 14.3975 | 4.7156 | 3.0532 | 15.1667 | 4.9676 | 3.0532 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2026 | 171 | 171-34 | Tier-1 | Non-HFTD---6 | 4--3 | 4.3813 | 60 | 100% | 81.2035 | 44.67% | 51.64% | 3.687% | 1.7955 | 0 | 0 | 1.7955 | 0 | 1.7128 | 4.5263 | 0.37842 | 1.7128 | 4.5263 | 0.37842 | 1.8043 | 4.7681 | 0.37842 | 2.211% | 0.043687 | 0.041525 | 1858.7395 | 129.5883 | 851.5868 | 877.5644 | 1912.2988 | 0 | 0 | 1912.2988 | 5.921e-05%
2026 | 70 | CB 70 | Tier-1 | Non-HFTD---12 | 3--2 | 6.5709 | 60 | 100% | 14.3505 | 72.4% | 0% | 27.6% | 0.51431 | 0 | 0 | 0.51431 | 0 | 0.49062 | 6.7883 | 0.072274 | 0.49062 | 6.7883 | 0.072274 | 0.51683 | 7.151 | 0.072274 | 3.584% | 0.016758 | 0.015928 | 856.3389 | 1.8915 | 630.9279 | 223.5195 | 868.6465 | 0 | 0 | 868.6465 | 1.696e-05%
2026 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 5.0178 | 378 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 277.0305 | 5.1838 | 53.4412 | 277.0305 | 5.1838 | 53.4412 | 291.8326 | 5.4608 | 53.4412 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2026 | 1434 | 1434-10AE | Tier-1 | Non-HFTD---10 | 3--2 | 6.6536 | 200 | 100% | 17.6762 | 78.96% | 0% | 21.04% | 0.69087 | 0 | 0 | 0.69087 | 0 | 0.65904 | 6.8737 | 0.095878 | 0.65904 | 6.8737 | 0.095878 | 0.69426 | 7.241 | 0.095878 | 3.908% | 0.017501 | 0.016634 | 1010.0366 | 133.2202 | 327.76 | 549.0563 | 1021.1043 | 0 | 0 | 1021.1043 | 2.278e-05%
2026 | 55 | 55-484F | Tier-1 | Non-HFTD---20 | 1--1 | 0.58822 | 21 | 100% | 0.44013 | 10.92% | 0% | 89.08% | 0.0023797 | 0 | 0 | 0.0023797 | 0 | 0.0022701 | 0.60768 | 0.0037356 | 0.0022701 | 0.60768 | 0.0037356 | 0.0023914 | 0.64015 | 0.0037356 | 0.5407% | 0.0015886 | 0.00151 | 277.0544 | 0.1857 | 52.6811 | 224.1876 | 289.9068 | 0 | 0 | 289.9068 | 7.847e-08%
2026 | 719 | CB 719 | Tier-1 | Non-HFTD---8 | 3--3 | 5.0596 | 131 | 100% | 28.3767 | 85.41% | 0% | 14.59% | 1.1998 | 0 | 0 | 1.1998 | 0 | 1.1445 | 5.2271 | 0.21896 | 1.1445 | 5.2271 | 0.21896 | 1.2056 | 5.5064 | 0.21896 | 4.228% | 0.015223 | 0.01447 | 1864.0191 | 0.59716 | 1614.3662 | 249.0557 | 1878.1781 | 0 | 0 | 1878.1781 | 3.956e-05%
2026 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 7.7339 | 601 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 58.7357 | 7.9898 | 7.3513 | 58.7357 | 7.9898 | 7.3513 | 61.8741 | 8.4168 | 7.3513 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2026 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | 3--3 | 8.0419 | 234 | 100% | 117.3021 | 94.99% | 0% | 5.009% | 5.5156 | 0 | 0 | 5.5156 | 0 | 5.2615 | 8.308 | 0.63331 | 5.2615 | 8.308 | 0.63331 | 5.5427 | 8.7519 | 0.63331 | 4.702% | 0.027256 | 0.025907 | 4303.7498 | 1020.4795 | 248.6707 | 3034.5996 | 4314.9761 | 0 | 0 | 4314.9761 | 0.0001819%
2026 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 15.1559 | 814 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 113.1467 | 15.6574 | 7.2264 | 113.1467 | 15.6574 | 7.2264 | 119.1922 | 16.494 | 7.2264 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2026 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 10.2425 | 356 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 71.3254 | 10.5814 | 6.7406 | 71.3254 | 10.5814 | 6.7406 | 75.1364 | 11.1468 | 6.7406 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2026 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 0.81042 | 169 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.9715 | 0.83724 | 3.5491 | 2.9715 | 0.83724 | 3.5491 | 3.1302 | 0.88197 | 3.5491 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2026 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 17.7839 | 395 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 249.0215 | 18.3724 | 13.5541 | 249.0215 | 18.3724 | 13.5541 | 262.327 | 19.3541 | 13.5541 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2026 | 262 | CB 262 | Tier-1 | Non-HFTD---13 | 1--2 | 1.333 | 30 | 100% | 8.1125 | 88.1% | 0% | 11.9% | 0.35378 | 0 | 0 | 0.35378 | 0 | 0.33748 | 1.3771 | 0.24508 | 0.33748 | 1.3771 | 0.24508 | 0.35552 | 1.4506 | 0.24508 | 4.361% | 0.004918 | 0.0046746 | 1649.5582 | 174.8972 | 367.1245 | 1107.5365 | 1659.7811 | 0 | 0 | 1659.7811 | 1.167e-05%
2026 | 372 | CB 372 | Tier-1 | Non-HFTD---18 | 2--1 | 2.0544 | 108 | 100% | 2.0256 | 27.04% | 0% | 72.96% | 0.027112 | 0 | 0 | 0.027112 | 0 | 0.025863 | 2.1224 | 0.012186 | 0.025863 | 2.1224 | 0.012186 | 0.027245 | 2.2358 | 0.012186 | 1.339% | 0.0057966 | 0.0055097 | 349.4394 | 0.28023 | 117.0886 | 232.0705 | 362.7165 | 0 | 0 | 362.7165 | 8.941e-07%
2026 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.64962 | 16 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 33.3597 | 0.67112 | 49.7076 | 33.3597 | 0.67112 | 49.7076 | 35.1422 | 0.70698 | 49.7076 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2026 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 7.3926 | 440 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 167.1394 | 7.6372 | 21.8848 | 167.1394 | 7.6372 | 21.8848 | 176.0699 | 8.0453 | 21.8848 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2026 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 6.2909 | 231 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 2.0506 | 6.4991 | 0.31552 | 2.0506 | 6.4991 | 0.31552 | 2.1601 | 6.8463 | 0.31552 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2026 | 81 | 81-193AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.28938 | 8 | 100% | 0.44576 | 14.6% | 0% | 85.4% | 0.0032221 | 0 | 0 | 0.0032221 | 0 | 0.0030737 | 0.29895 | 0.010282 | 0.0030737 | 0.29895 | 0.010282 | 0.0032379 | 0.31493 | 0.010282 | 0.7228% | 0.0011408 | 0.0010843 | 390.747 | 0.25109 | 87.3722 | 303.1238 | 408.1247 | 0 | 0 | 408.1247 | 1.063e-07%
2026 | 170 | 170-42 | Tier-1 | Non-HFTD---10 | 4--2 | 2.6307 | 74 | 100% | 23.9542 | 86.3% | 7.76% | 5.937% | 1.0233 | 0 | 0 | 1.0233 | 0 | 0.97618 | 2.7177 | 0.35919 | 0.97618 | 2.7177 | 0.35919 | 1.0283 | 2.863 | 0.35919 | 4.272% | 0.037594 | 0.035733 | 637.182 | 77.2313 | 106.2759 | 453.6748 | 641.7271 | 0 | 0 | 641.7271 | 3.375e-05%
2026 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 17.4522 | 914 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 94.985 | 18.0298 | 5.2682 | 94.985 | 18.0298 | 5.2682 | 100.0601 | 18.9931 | 5.2682 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2026 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 0.41062 | 17 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.097401 | 0.42421 | 0.22961 | 0.097401 | 0.42421 | 0.22961 | 0.10261 | 0.44687 | 0.22961 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2026 | 72 | 72-12F | Tier-1 | Non-HFTD---19 | 1--1 | 0.23446 | 7 | 100% | 0.35888 | 36.92% | 0% | 63.08% | 0.0065581 | 0 | 0 | 0.0065581 | 0 | 0.006256 | 0.24222 | 0.025828 | 0.006256 | 0.24222 | 0.025828 | 0.0065903 | 0.25516 | 0.025828 | 1.827% | 0.0007194 | 0.00068379 | 498.8599 | 8.4651 | 162.404 | 327.9909 | 515.2486 | 0 | 0 | 515.2486 | 2.163e-07%
2026 | 792 | 792-1172F | Tier-1 | Non-HFTD---14 | 3--1 | 5.2345 | 273 | 100% | 6.3558 | 40.89% | 0% | 59.11% | 0.12864 | 0 | 0 | 0.12864 | 0 | 0.12272 | 5.4077 | 0.022693 | 0.12272 | 5.4077 | 0.022693 | 0.12927 | 5.6966 | 0.022693 | 2.024% | 0.014697 | 0.013969 | 432.4678 | 0.27436 | 199.5532 | 232.6402 | 445.7806 | 0 | 0 | 445.7806 | 4.242e-06%
2026 | 452 | 452-37AE | Tier-1 | Non-HFTD---5 | 1--5 | 0.40967 | 44 | 100% | 90.6209 | 99.66% | 0% | 0.3391% | 4.4705 | 0 | 0 | 4.4705 | 0 | 4.2646 | 0.42323 | 10.0763 | 4.2646 | 0.42323 | 10.0763 | 4.4924 | 0.44584 | 10.0763 | 4.933% | 0.0017838 | 0.0016955 | 50802.159 | 10626.9011 | 18.8338 | 40156.424 | 50811.1291 | 0 | 0 | 50811.1291 | 0.0001474%
2026 | 90 | 90-24 | Tier-1 | Non-HFTD---7 | 2--3 | 0.60288 | 19 | 100% | 27.778 | 1.28% | 96.39% | 2.335% | 0.017597 | 0 | 0 | 0.017597 | 0 | 0.016786 | 0.62283 | 0.026951 | 0.016786 | 0.62283 | 0.026951 | 0.017683 | 0.65611 | 0.026951 | 0.06335% | 0.0071986 | 0.0068423 | 3858.8091 | 4.7029 | 3414.9982 | 439.108 | 4057.1958 | 0 | 0 | 4057.1958 | 5.803e-07%
2026 | 275 | CB 275 | Tier-1 | Non-HFTD---2 | 3--4 | 3.0089 | 148 | 100% | 206.6235 | 45.85% | 53.34% | 0.8107% | 4.6895 | 0 | 0 | 4.6895 | 0 | 4.4734 | 3.1084 | 1.4391 | 4.4734 | 3.1084 | 1.4391 | 4.7125 | 3.2745 | 1.4391 | 2.27% | 0.025053 | 0.023813 | 8247.3894 | 358.5021 | 5488.4618 | 2400.4254 | 8479.9674 | 0 | 0 | 8479.9674 | 0.0001546%
2026 | 42 | CB 42 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3775 | 32 | 100% | 5.9866 | 70.69% | 0% | 29.31% | 0.20948 | 0 | 0 | 0.20948 | 0 | 0.19983 | 2.4561 | 0.081358 | 0.19983 | 2.4561 | 0.081358 | 0.2105 | 2.5874 | 0.081358 | 3.499% | 0.00755 | 0.0071763 | 792.9237 | 22.0026 | 447.2899 | 323.6312 | 805.0273 | 0 | 0 | 805.0273 | 6.908e-06%
2026 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 15.5693 | 654 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 169.8732 | 16.0845 | 10.5613 | 169.8732 | 16.0845 | 10.5613 | 178.9497 | 16.9439 | 10.5613 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2026 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 12.821 | 928 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 151.2085 | 13.2453 | 11.416 | 151.2085 | 13.2453 | 11.416 | 159.2877 | 13.953 | 11.416 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2026 | 525 | CB 525 | Tier-1 | Non-HFTD---5 | 2--4 | 0.53731 | 44 | 100% | 72.1571 | 17.62% | 81.53% | 0.8516% | 0.62936 | 0 | 0 | 0.62936 | 0 | 0.60036 | 0.55509 | 1.0816 | 0.60036 | 0.55509 | 1.0816 | 0.63244 | 0.58475 | 1.0816 | 0.8722% | 0.0072554 | 0.0068963 | 9945.2959 | 206.1053 | 8187.2341 | 1551.9565 | 10371.9649 | 0 | 0 | 10371.9649 | 2.075e-05%
2026 | 306 | 306-961 | Tier-1 | Non-HFTD---8 | 4--2 | 0.25951 | 21 | 100% | 44.8989 | 37.41% | 62.22% | 0.3782% | 0.83134 | 0 | 0 | 0.83134 | 0 | 0.79304 | 0.2681 | 2.958 | 0.79304 | 0.2681 | 2.958 | 0.83541 | 0.28242 | 2.958 | 1.852% | 0.052982 | 0.050359 | 847.4364 | 49.5718 | 468.5847 | 329.2799 | 875.061 | 0 | 0 | 875.061 | 2.741e-05%
2026 | 287 | CB 287 | Tier-1 | Non-HFTD---4 | 3--4 | 2.9707 | 127 | 100% | 114.6676 | 71.93% | 25.48% | 2.591% | 4.0827 | 0 | 0 | 4.0827 | 0 | 3.8946 | 3.069 | 1.269 | 3.8946 | 3.069 | 1.269 | 4.1027 | 3.2329 | 1.269 | 3.56% | 0.015966 | 0.015175 | 7182.079 | 404.9612 | 4312.5318 | 2464.586 | 7287.0718 | 0 | 0 | 7287.0718 | 0.0001346%
2026 | 1094 | CB 1094 | Tier-1 | Non-HFTD---9 | 1--5 | 0.38073 | 5 | 100% | 25.2689 | 98.73% | 0% | 1.267% | 1.235 | 0 | 0 | 1.235 | 0 | 1.1781 | 0.39333 | 2.9951 | 1.1781 | 0.39333 | 2.9951 | 1.241 | 0.41434 | 2.9951 | 4.887% | 0.001448 | 0.0013763 | 17450.9081 | 2431.0189 | 2381.051 | 12638.8381 | 17462.4248 | 0 | 0 | 17462.4248 | 4.072e-05%
2026 | 1438 | 1438-333F | Tier-1 | Non-HFTD---20 | 1--1 | 0.44675 | 30 | 100% | 0.3138 | 20.87% | 0% | 79.13% | 0.0032416 | 0 | 0 | 0.0032416 | 0 | 0.0030923 | 0.46154 | 0.0067 | 0.0030923 | 0.46154 | 0.0067 | 0.0032575 | 0.4862 | 0.0067 | 1.033% | 0.0012552 | 0.0011931 | 249.9971 | 2.9701 | 52.7852 | 194.2418 | 260.2993 | 0 | 0 | 260.2993 | 1.069e-07%
2026 | 489 | 489-33 | Tier-1 | Non-HFTD---20 | 1--1 | 1.3928 | 37 | 100% | 0.5266 | 10.19% | 0% | 89.81% | 0.002657 | 0 | 0 | 0.002657 | 0 | 0.0025346 | 1.4389 | 0.0017615 | 0.0025346 | 1.4389 | 0.0017615 | 0.00267 | 1.5158 | 0.0017615 | 0.5046% | 0.0028464 | 0.0027055 | 185.0048 | 0.12502 | 33.9508 | 150.929 | 193.6574 | 0 | 0 | 193.6574 | 8.762e-08%
2026 | 80 | 80-575R | Tier-1 | Non-HFTD---15 | 1--2 | 1.7536 | 42 | 100% | 3.3604 | 69.22% | 0% | 30.78% | 0.11514 | 0 | 0 | 0.11514 | 0 | 0.10983 | 1.8117 | 0.060625 | 0.10983 | 1.8117 | 0.060625 | 0.1157 | 1.9085 | 0.060625 | 3.426% | 0.0044504 | 0.0042301 | 755.0854 | 6.5404 | 504.3875 | 244.1574 | 767.1901 | 0 | 0 | 767.1901 | 3.797e-06%
2026 | 178 | 178-983AE | Tier-1 | Non-HFTD---9 | 1--5 | 0.24788 | 9 | 100% | 24.3065 | 99.32% | 0% | 0.6782% | 1.195 | 0 | 0 | 1.195 | 0 | 1.14 | 0.25608 | 4.4515 | 1.14 | 0.25608 | 4.4515 | 1.2009 | 0.26977 | 4.4515 | 4.916% | 0.00085 | 0.00080793 | 28595.879 | 4615.9311 | 22.2023 | 23957.7456 | 28605.9786 | 0 | 0 | 28605.9786 | 3.941e-05%
2026 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.094697 | 7 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.4787 | 0.097831 | 56.0018 | 5.4787 | 0.097831 | 56.0018 | 5.7714 | 0.10306 | 56.0018 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2026 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | 1--3 | 0.55455 | 52 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.18461 | 0 | 0 | 0.18461 | 0 | 0.17611 | 0.5729 | 0.3074 | 0.17611 | 0.5729 | 0.3074 | 0.18552 | 0.60351 | 0.3074 | 4.394% | 0.002261 | 0.0021491 | 1858.0978 | 176.4132 | 558.9214 | 1122.7631 | 1868.9599 | 0 | 0 | 1868.9599 | 6.088e-06%
2026 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.03428 | 0 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.1865 | 0.035415 | 33.5039 | 1.1865 | 0.035415 | 33.5039 | 1.2499 | 0.037307 | 33.5039 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2026 | 740 | 740-856F | Tier-1 | Non-HFTD---16 | 2--1 | 2.888 | 214 | 100% | 2.9768 | 34.05% | 0% | 65.95% | 0.050176 | 0 | 0 | 0.050176 | 0 | 0.047864 | 2.9836 | 0.016042 | 0.047864 | 2.9836 | 0.016042 | 0.050422 | 3.143 | 0.016042 | 1.686% | 0.0078388 | 0.0074508 | 379.746 | 4.2927 | 127.0305 | 248.4227 | 392.788 | 0 | 0 | 392.788 | 1.655e-06%
2026 | 578 | 578-242F | Tier-1 | Non-HFTD---3 | 3--4 | 2.7303 | 60 | 100% | 101.2493 | 1.118% | 96.96% | 1.921% | 0.056018 | 0 | 0 | 0.056018 | 0 | 0.053438 | 2.8206 | 0.018945 | 0.053438 | 2.8206 | 0.018945 | 0.056293 | 2.9713 | 0.018945 | 0.05533% | 0.017989 | 0.017099 | 5628.2774 | 9.7279 | 4959.9632 | 658.5863 | 5918.1099 | 0 | 0 | 5918.1099 | 1.847e-06%
2026 | 506 | 506-160AE | Tier-1 | Non-HFTD---19 | 1--2 | 0.047538 | 2 | 100% | 0.28387 | 86.74% | 0% | 13.26% | 0.012188 | 0 | 0 | 0.012188 | 0 | 0.011627 | 0.049111 | 0.23675 | 0.011627 | 0.049111 | 0.23675 | 0.012248 | 0.051735 | 0.23675 | 4.294% | 0.0001712 | 0.00016273 | 1658.1166 | 166.0816 | 438.3656 | 1053.6695 | 1669.5667 | 0 | 0 | 1669.5667 | 4.019e-07%
2026 | 57 | CB 57 | Tier-1 | Non-HFTD---2 | 4--4 | 7.9972 | 102 | 100% | 246.5725 | 13.42% | 83.87% | 2.714% | 1.6375 | 0 | 0 | 1.6375 | 0 | 1.5621 | 8.2619 | 0.18907 | 1.5621 | 8.2619 | 0.18907 | 1.6456 | 8.7033 | 0.18907 | 0.6641% | 0.034392 | 0.03269 | 7169.3891 | 7.2057 | 6458.1009 | 704.0825 | 7492.6625 | 0 | 0 | 7492.6625 | 5.4e-05%
2026 | 781 | CB 781 | Tier-1 | Non-HFTD---4 | 3--4 | 3.2938 | 134 | 100% | 155.4252 | 25.13% | 72.94% | 1.931% | 1.9333 | 0 | 0 | 1.9333 | 0 | 1.8442 | 3.4028 | 0.54197 | 1.8442 | 3.4028 | 0.54197 | 1.9427 | 3.5846 | 0.54197 | 1.244% | 0.021159 | 0.020111 | 7345.7215 | 11.4899 | 6707.1006 | 627.1309 | 7632.1422 | 0 | 0 | 7632.1422 | 6.375e-05%
2026 | 57 | 57-1292F | Tier-1 | Non-HFTD---9 | 2--2 | 0.68467 | 37 | 100% | 21.0439 | 0.2676% | 97.17% | 2.561% | 0.0027876 | 0 | 0 | 0.0027876 | 0 | 0.0026591 | 0.70733 | 0.0037594 | 0.0026591 | 0.70733 | 0.0037594 | 0.0028012 | 0.74513 | 0.0037594 | 0.01325% | 0.012624 | 0.011999 | 1666.9469 | 1.8812 | 1483.5097 | 181.556 | 1753.5256 | 0 | 0 | 1753.5256 | 9.192e-08%
2026 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 2.4583 | 117 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 299.7005 | 2.5397 | 118.007 | 299.7005 | 2.5397 | 118.007 | 315.7139 | 2.6754 | 118.007 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2026 | 723 | 723-793F | Tier-1 | Non-HFTD---20 | 1--1 | 0.16136 | 30 | 100% | 0.15365 | 52.88% | 0% | 47.12% | 0.004022 | 0 | 0 | 0.004022 | 0 | 0.0038367 | 0.1667 | 0.023015 | 0.0038367 | 0.1667 | 0.023015 | 0.0040417 | 0.17561 | 0.023015 | 2.618% | 0.0004994 | 0.00047468 | 307.6774 | 26.5 | 14.647 | 266.5305 | 315.2275 | 0 | 0 | 315.2275 | 1.326e-07%
2026 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 16.5898 | 1848 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 734.3072 | 17.1388 | 42.8447 | 734.3072 | 17.1388 | 42.8447 | 773.5422 | 18.0546 | 42.8447 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2026 | 474 | 474-22AE | Tier-1 | Non-HFTD---1 | 4--5 | 9.6011 | 965 | 100% | 6435.9834 | 99.89% | 0% | 0.1146% | 318.2162 | 0 | 0 | 318.2162 | 0 | 303.5566 | 9.9189 | 30.604 | 303.5566 | 9.9189 | 30.604 | 319.7761 | 10.4488 | 30.604 | 4.944% | 0.046635 | 0.044327 | 138007.5774 | 24328.5202 | 121.2373 | 113557.8199 | 138015.8115 | 0 | 0 | 138015.8115 | 0.01049%
2026 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 8.9873 | 712 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 74.8329 | 9.2847 | 8.0598 | 74.8329 | 9.2847 | 8.0598 | 78.8314 | 9.7808 | 8.0598 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2026 | NO1 | CB NO1 | Tier-1 | Non-HFTD---20 | 1--1 | 0.16004 | 5 | 100% | 0.11186 | 6.282% | 0% | 93.72% | 0.00034784 | 0 | 0 | 0.00034784 | 0 | 0.00033181 | 0.16534 | 0.0020069 | 0.00033181 | 0.16534 | 0.0020069 | 0.00034954 | 0.17417 | 0.0020069 | 0.311% | 0.0004254 | 0.00040434 | 262.9516 | 0.18543 | 38.9048 | 223.8613 | 275.7853 | 0 | 0 | 275.7853 | 1.147e-08%
2026 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 6.7553 | 1558 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 135.4211 | 6.9789 | 19.4044 | 135.4211 | 6.9789 | 19.4044 | 142.6568 | 7.3518 | 19.4044 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2026 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | 4--1 | 0.16307 | 3 | 100% | 2.3826 | 9.042% | 83.57% | 7.391% | 0.010664 | 0 | 0 | 0.010664 | 0 | 0.010173 | 0.16846 | 0.060384 | 0.010173 | 0.16846 | 0.060384 | 0.010716 | 0.17747 | 0.060384 | 0.4476% | 0.059368 | 0.05643 | 40.1318 | 0.36722 | 29.4839 | 10.2807 | 42.0328 | 0 | 0 | 42.0328 | 3.517e-07%
2026 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.038636 | 0 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.78372 | 0.039915 | 19.6348 | 0.78372 | 0.039915 | 19.6348 | 0.8256 | 0.042048 | 19.6348 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2026 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 1.5002 | 51 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.9468 | 1.5498 | 1.2561 | 1.9468 | 1.5498 | 1.2561 | 2.0508 | 1.6326 | 1.2561 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2026 | 252 | 252-277F | Tier-1 | Non-HFTD---15 | 1--2 | 0.90889 | 30 | 100% | 3.3511 | 64.95% | 0% | 35.05% | 0.10774 | 0 | 0 | 0.10774 | 0 | 0.10277 | 0.93897 | 0.10945 | 0.10277 | 0.93897 | 0.10945 | 0.10826 | 0.98914 | 0.10945 | 3.215% | 0.0037008 | 0.0035176 | 905.5022 | 85.5311 | 154.0815 | 665.8897 | 922.0312 | 0 | 0 | 922.0312 | 3.553e-06%
2026 | 1286 | CB 1286 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1557 | 55 | 100% | 2.6947 | 57.45% | 0% | 42.55% | 0.076626 | 0 | 0 | 0.076626 | 0 | 0.073096 | 1.1939 | 0.061225 | 0.073096 | 1.1939 | 0.061225 | 0.077002 | 1.2577 | 0.061225 | 2.844% | 0.0043234 | 0.0041094 | 623.2816 | 31.002 | 192.2211 | 400.0585 | 637.0941 | 0 | 0 | 637.0941 | 2.527e-06%
2026 | 161 | 161-974F | Tier-1 | Non-HFTD---15 | 1--2 | 1.2625 | 35 | 100% | 2.9871 | 73.28% | 0% | 26.72% | 0.10836 | 0 | 0 | 0.10836 | 0 | 0.10337 | 1.3043 | 0.07925 | 0.10337 | 1.3043 | 0.07925 | 0.10889 | 1.374 | 0.07925 | 3.628% | 0.0046736 | 0.0044423 | 639.1485 | 67.3315 | 71.5481 | 500.2689 | 648.0412 | 0 | 0 | 648.0412 | 3.573e-06%
2026 | 770 | 770-250R | Tier-1 | Non-HFTD---13 | 1--3 | 0.94323 | 92 | 100% | 8.2742 | 91.72% | 0% | 8.276% | 0.37568 | 0 | 0 | 0.37568 | 0 | 0.35837 | 0.97444 | 0.36777 | 0.35837 | 0.97444 | 0.36777 | 0.37752 | 1.0265 | 0.36777 | 4.54% | 0.003255 | 0.0030939 | 2542.0097 | 485.388 | 24.5872 | 2032.0344 | 2552.9659 | 0 | 0 | 2552.9659 | 1.239e-05%
2026 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 13.8138 | 967 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 530.5991 | 14.271 | 37.1803 | 530.5991 | 14.271 | 37.1803 | 558.9498 | 15.0335 | 37.1803 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2026 | 188 | 188-11F | Tier-2 | Tier-2---7 | 3--5 | 5.0004 | 427 | 100% | 2209.344 | 99.86% | 0% | 0.1429% | 109.2062 | 0 | 0 | 109.2062 | 0 | 104.1753 | 5.1658 | 20.1662 | 104.1753 | 5.1658 | 20.1662 | 109.7416 | 5.4419 | 20.1662 | 4.943% | 0.019333 | 0.018376 | 114277.2032 | 24326.824 | 78.3726 | 89872.0066 | 114285.7081 | 0 | 0 | 114285.7081 | 0.003601%
2026 | 175 | CB 175 | Tier-2 | Tier-2---10 | 5--4 | 2.8512 | 275 | 100% | 1236.5075 | 84.14% | 15.66% | 0.203% | 51.5004 | 0 | 0 | 51.5004 | 0 | 49.1279 | 2.9455 | 16.6788 | 49.1279 | 2.9455 | 16.6788 | 51.7529 | 3.1029 | 16.6788 | 4.165% | 0.16723 | 0.15895 | 7393.9644 | 1133.6762 | 1185.8912 | 5074.397 | 7455.0304 | 0 | 0 | 7455.0304 | 0.001698%
2026 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 3.0667 | 69 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 23.6499 | 3.1682 | 7.4648 | 23.6499 | 3.1682 | 7.4648 | 24.9135 | 3.3375 | 7.4648 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2026 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 13.4184 | 1026 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1514.5818 | 13.8624 | 109.2582 | 1514.5818 | 13.8624 | 109.2582 | 1595.508 | 14.6031 | 109.2582 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2026 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 3.4998 | 176 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 21.4215 | 3.6156 | 5.9247 | 21.4215 | 3.6156 | 5.9247 | 22.5661 | 3.8088 | 5.9247 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2026 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 20.6608 | 1532 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1087.6046 | 21.3445 | 50.9548 | 1087.6046 | 21.3445 | 50.9548 | 1145.7168 | 22.485 | 50.9548 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2026 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 11.56 | 909 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1055.7106 | 11.9426 | 88.3987 | 1055.7106 | 11.9426 | 88.3987 | 1112.1187 | 12.5807 | 88.3987 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2026 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 5.1261 | 362 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 161.888 | 5.2958 | 30.5692 | 161.888 | 5.2958 | 30.5692 | 170.5379 | 5.5788 | 30.5692 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2026 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 2.1386 | 164 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 50.9272 | 2.2094 | 23.0506 | 50.9272 | 2.2094 | 23.0506 | 53.6483 | 2.3274 | 23.0506 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2026 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 5.9518 | 999 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 424.5109 | 6.1487 | 69.0406 | 424.5109 | 6.1487 | 69.0406 | 447.1931 | 6.4773 | 69.0406 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2026 | 1438 | 1438-331F | Tier-1 | Non-HFTD---19 | 1--1 | 0.11725 | 0 | 100% | 0.12483 | 14.96% | 0% | 85.04% | 0.00092462 | 0 | 0 | 0.00092462 | 0 | 0.00088202 | 0.12113 | 0.0072813 | 0.00088202 | 0.12113 | 0.0072813 | 0.00092915 | 0.12761 | 0.0072813 | 0.7407% | 0.000355 | 0.00033743 | 351.6369 | 0.225 | 79.7806 | 271.6313 | 367.2091 | 0 | 0 | 367.2091 | 3.049e-08%
2026 | 161 | 161-991F | Tier-1 | Non-HFTD---12 | 3--1 | 9.0516 | 207 | 100% | 10.7177 | 44.4% | 0% | 55.6% | 0.23557 | 0 | 0 | 0.23557 | 0 | 0.22472 | 9.3511 | 0.024031 | 0.22472 | 9.3511 | 0.024031 | 0.23673 | 9.8507 | 0.024031 | 2.198% | 0.025268 | 0.024017 | 424.1613 | 21.5449 | 118.7087 | 283.9078 | 436.4423 | 0 | 0 | 436.4423 | 7.768e-06%
2026 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 1.0659 | 30 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 62.0703 | 1.1012 | 56.3672 | 62.0703 | 1.1012 | 56.3672 | 65.3868 | 1.16 | 56.3672 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2026 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 3.7138 | 186 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 105.2609 | 3.8367 | 27.4349 | 105.2609 | 3.8367 | 27.4349 | 110.8851 | 4.0417 | 27.4349 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2026 | 713 | 713-169 | Tier-1 | Non-HFTD---19 | 1--1 | 0.36193 | 0 | 100% | 0.56535 | 24.4% | 0% | 75.6% | 0.0068286 | 0 | 0 | 0.0068286 | 0 | 0.0065141 | 0.37391 | 0.017421 | 0.0065141 | 0.37391 | 0.017421 | 0.0068621 | 0.39389 | 0.017421 | 1.208% | 0.0014716 | 0.0013988 | 384.1744 | 11.8523 | 47.4609 | 324.8612 | 399.2994 | 0 | 0 | 399.2994 | 2.252e-07%
2026 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 13.767 | 1106 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 602.1374 | 14.2226 | 42.3366 | 602.1374 | 14.2226 | 42.3366 | 634.3104 | 14.9826 | 42.3366 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2026 | 92 | 92-619F | Tier-2 | Tier-2---14 | 3--4 | 3.3373 | 77 | 100% | 202.8689 | 46.88% | 52.08% | 1.034% | 4.708 | 0 | 0 | 4.708 | 0 | 4.4911 | 3.4478 | 1.3026 | 4.4911 | 3.4478 | 1.3026 | 4.7311 | 3.632 | 1.3026 | 2.321% | 0.015617 | 0.014844 | 12990.5937 | 1279.3739 | 6200.2786 | 5510.9412 | 13349.9397 | 0 | 0 | 13349.9397 | 0.0001553%
2026 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 17.727 | 1516 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1643.7869 | 18.3137 | 89.7573 | 1643.7869 | 18.3137 | 89.7573 | 1731.6167 | 19.2922 | 89.7573 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2026 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 8.6068 | 720 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 117.2051 | 8.8916 | 13.1815 | 117.2051 | 8.8916 | 13.1815 | 123.4676 | 9.3667 | 13.1815 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2026 | 928 | 928-20 | Tier-2 | Tier-2---20 | 4--2 | 0.15818 | 49 | 100% | 27.1749 | 93.08% | 6.522% | 0.4024% | 1.252 | 0 | 0 | 1.252 | 0 | 1.1943 | 0.16341 | 7.3087 | 1.1943 | 0.16341 | 7.3087 | 1.2581 | 0.17214 | 7.3087 | 4.607% | 0.044362 | 0.042166 | 612.5656 | 93.209 | 34.6926 | 484.664 | 614.7746 | 0 | 0 | 614.7746 | 4.129e-05%
2026 | AD2 | CB AD2 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3572 | 43 | 100% | 40.3722 | 2.888% | 92.69% | 4.427% | 0.057707 | 0 | 0 | 0.057707 | 0 | 0.055048 | 2.4352 | 0.022605 | 0.055048 | 2.4352 | 0.022605 | 0.05799 | 2.5653 | 0.022605 | 0.1429% | 0.011539 | 0.010968 | 3498.6997 | 6.8788 | 3053.1148 | 438.7061 | 3675.6431 | 0 | 0 | 3675.6431 | 1.903e-06%
2026 | 90 | 90-44AE | Tier-1 | Non-HFTD---4 | 3--4 | 3.5829 | 134 | 100% | 101.3703 | 11.74% | 85.7% | 2.562% | 0.58913 | 0 | 0 | 0.58913 | 0 | 0.56199 | 3.7015 | 0.15183 | 0.56199 | 3.7015 | 0.15183 | 0.59202 | 3.8993 | 0.15183 | 0.5812% | 0.015099 | 0.014352 | 6713.5305 | 6.5653 | 6082.8987 | 624.0665 | 7022.1078 | 0 | 0 | 7022.1078 | 1.943e-05%
2026 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 2.8193 | 63 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 17.5537 | 2.9126 | 6.0268 | 17.5537 | 2.9126 | 6.0268 | 18.4916 | 3.0682 | 6.0268 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2026 | EOS3 | CB EOS3 | Tier-1 | Non-HFTD---11 | 2--3 | 2.4386 | 83 | 100% | 14.1826 | 87.38% | 0% | 12.62% | 0.61345 | 0 | 0 | 0.61345 | 0 | 0.58519 | 2.5193 | 0.23228 | 0.58519 | 2.5193 | 0.23228 | 0.61645 | 2.6539 | 0.23228 | 4.325% | 0.0075404 | 0.0071672 | 1880.8804 | 242.4617 | 179.6503 | 1458.7683 | 1893.2412 | 0 | 0 | 1893.2412 | 2.023e-05%
2026 | 392 | 392-23F | Tier-1 | Non-HFTD---2 | 5--3 | 2.6426 | 50 | 100% | 466.525 | 0.9229% | 98.62% | 0.4561% | 0.21313 | 0 | 0 | 0.21313 | 0 | 0.20331 | 2.73 | 0.074471 | 0.20331 | 2.73 | 0.074471 | 0.21417 | 2.8759 | 0.074471 | 0.04568% | 0.10259 | 0.097512 | 4547.4707 | 15.3107 | 3769.5708 | 762.5892 | 4782.1075 | 0 | 0 | 4782.1075 | 7.028e-06%
2026 | 949 | 949-22R | Tier-1 | Non-HFTD---12 | 3--2 | 5.1989 | 436 | 100% | 9.2316 | 56.06% | 0% | 43.94% | 0.25619 | 0 | 0 | 0.25619 | 0 | 0.24439 | 5.3709 | 0.045502 | 0.24439 | 5.3709 | 0.045502 | 0.25745 | 5.6579 | 0.045502 | 2.775% | 0.016401 | 0.015589 | 562.8643 | 27.9703 | 168.0106 | 366.8833 | 575.7433 | 0 | 0 | 575.7433 | 8.448e-06%
2026 | 245 | 245-486 | Tier-1 | Non-HFTD---2 | 4--4 | 4.3474 | 192 | 100% | 294.2309 | 35.69% | 63.39% | 0.9197% | 5.1981 | 0 | 0 | 5.1981 | 0 | 4.9586 | 4.4912 | 1.1041 | 4.9586 | 4.4912 | 1.1041 | 5.2236 | 4.7312 | 1.1041 | 1.767% | 0.039483 | 0.037529 | 7452.0521 | 531.8785 | 4332.7245 | 2587.4492 | 7701.6294 | 0 | 0 | 7701.6294 | 0.0001714%
2026 | 452 | 452-39AE | Tier-1 | Non-HFTD---1 | 2--5 | 1.292 | 196 | 100% | 261.2424 | 99.61% | 0% | 0.3884% | 12.8813 | 0 | 0 | 12.8813 | 0 | 12.2879 | 1.3348 | 9.2059 | 12.2879 | 1.3348 | 9.2059 | 12.9444 | 1.4061 | 9.2059 | 4.931% | 0.0055772 | 0.0053011 | 46841.1346 | 13719.2411 | 19.0906 | 33102.8029 | 46850.6095 | 0 | 0 | 46850.6095 | 0.0004248%
2026 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 4.0824 | 476 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 20.0778 | 4.2175 | 4.7606 | 20.0778 | 4.2175 | 4.7606 | 21.1505 | 4.4428 | 4.7606 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2026 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 13.2557 | 1044 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 126.7631 | 13.6944 | 9.2566 | 126.7631 | 13.6944 | 9.2566 | 133.5362 | 14.4261 | 9.2566 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2026 | 474 | CB 474 | Tier-1 | Non-HFTD---1 | 3--5 | 4.6676 | 497 | 100% | 794.8798 | 99.6% | 0% | 0.3957% | 39.1908 | 0 | 0 | 39.1908 | 0 | 37.3854 | 4.822 | 7.753 | 37.3854 | 4.822 | 7.753 | 39.383 | 5.0797 | 7.753 | 4.93% | 0.016088 | 0.015291 | 49409.4676 | 7937.2559 | 481.7871 | 40990.4246 | 49419.6498 | 0 | 0 | 49419.6498 | 0.001292%
2026 | 164 | CB 164 | Tier-1 | Non-HFTD---13 | 1--2 | 1.583 | 41 | 100% | 5.3562 | 79.49% | 0% | 20.51% | 0.21076 | 0 | 0 | 0.21076 | 0 | 0.20105 | 1.6354 | 0.12294 | 0.20105 | 1.6354 | 0.12294 | 0.21179 | 1.7228 | 0.12294 | 3.935% | 0.0047404 | 0.0045058 | 1129.913 | 8.1525 | 869.9018 | 251.8587 | 1141.9803 | 0 | 0 | 1141.9803 | 6.95e-06%
2026 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 1.2773 | 61 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 26.8592 | 1.3195 | 20.355 | 26.8592 | 1.3195 | 20.355 | 28.2944 | 1.39 | 20.355 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2026 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 7.3796 | 119 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 219.8189 | 7.6238 | 28.8332 | 219.8189 | 7.6238 | 28.8332 | 231.5641 | 8.0312 | 28.8332 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2026 | DS1 | CB DS1 | Tier-1 | Non-HFTD---12 | 3--2 | 1.7008 | 75 | 100% | 13.0351 | 8.296% | 84.41% | 7.29% | 0.053527 | 0 | 0 | 0.053527 | 0 | 0.051061 | 1.7571 | 0.02906 | 0.051061 | 1.7571 | 0.02906 | 0.053789 | 1.8509 | 0.02906 | 0.4106% | 0.014723 | 0.013994 | 885.347 | 9.9559 | 707.4464 | 167.9447 | 927.6291 | 0 | 0 | 927.6291 | 1.765e-06%
2026 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.87803 | 17 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 30.6993 | 0.90709 | 33.8438 | 30.6993 | 0.90709 | 33.8438 | 32.3396 | 0.95555 | 33.8438 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2026 | 554 | CB 554 | Tier-1 | Non-HFTD---15 | 1--2 | 0.48106 | 1 | 100% | 2.8878 | 78.27% | 0% | 21.73% | 0.11188 | 0 | 0 | 0.11188 | 0 | 0.10673 | 0.49698 | 0.21475 | 0.10673 | 0.49698 | 0.21475 | 0.11243 | 0.52353 | 0.21475 | 3.874% | 0.0020388 | 0.0019379 | 1416.4094 | 124.7784 | 373.0089 | 918.622 | 1432.4394 | 0 | 0 | 1432.4394 | 3.689e-06%
2026 | 452 | 452-717 | Tier-2 | Tier-2---19 | 1--5 | 0.29487 | 27 | 100% | 24.802 | 99.04% | 0% | 0.9608% | 1.2159 | 0 | 0 | 1.2159 | 0 | 1.1599 | 0.30462 | 3.8076 | 1.1599 | 0.30462 | 3.8076 | 1.2219 | 0.3209 | 3.8076 | 4.902% | 0.000973 | 0.00092484 | 25490.2561 | 9086.828 | 25.5586 | 16377.8695 | 25503.0101 | 0 | 0 | 25503.0101 | 4.01e-05%
2026 | 250 | 250-47 | Tier-1 | Non-HFTD---19 | 1--2 | 0.076894 | 8 | 100% | 0.26608 | 73.81% | 0% | 26.19% | 0.009721 | 0 | 0 | 0.009721 | 0 | 0.0092732 | 0.079439 | 0.11673 | 0.0092732 | 0.079439 | 0.11673 | 0.0097686 | 0.083683 | 0.11673 | 3.653% | 0.0002818 | 0.00026785 | 944.2218 | 112.5399 | 22.9232 | 808.7588 | 957.1024 | 0 | 0 | 957.1024 | 3.206e-07%
2026 | 195 | CB 195 | Tier-1 | Non-HFTD---1 | 4--4 | 2.8899 | 388 | 100% | 363.2496 | 59.46% | 39.93% | 0.6035% | 10.6919 | 0 | 0 | 10.6919 | 0 | 10.1993 | 2.9856 | 3.4162 | 10.1993 | 2.9856 | 3.4162 | 10.7443 | 3.1451 | 3.4162 | 2.943% | 0.029402 | 0.027947 | 12354.4195 | 1165.0324 | 4745.6591 | 6443.728 | 12615.2346 | 0 | 0 | 12615.2346 | 0.0003526%
2026 | 597 | CB 597 | Tier-2 | Tier-2---14 | 1--5 | 1.0557 | 113 | 100% | 218.0489 | 99.66% | 0% | 0.3378% | 10.757 | 0 | 0 | 10.757 | 0 | 10.2614 | 1.0906 | 9.4088 | 10.2614 | 1.0906 | 9.4088 | 10.8097 | 1.1489 | 9.4088 | 4.933% | 0.0040332 | 0.0038336 | 54063.4858 | 8115.5826 | 4098.4737 | 41849.4295 | 54072.9953 | 0 | 0 | 54072.9953 | 0.0003547%
2026 | OT2 | CB OT2 | Tier-1 | Non-HFTD---8 | 3--3 | 3.4801 | 92 | 100% | 45.4213 | 3.226% | 91.33% | 5.441% | 0.072536 | 0 | 0 | 0.072536 | 0 | 0.069194 | 3.5953 | 0.019246 | 0.069194 | 3.5953 | 0.019246 | 0.072892 | 3.7874 | 0.019246 | 0.1597% | 0.024647 | 0.023427 | 1842.8901 | 7.4819 | 1565.7674 | 269.6408 | 1935.7675 | 0 | 0 | 1935.7675 | 2.392e-06%
2026 | 968 | 968-476F | Tier-2 | Tier-2---17 | 3--3 | 2.5405 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 2.9977 | 0 | 0 | 2.9977 | 0 | 2.8596 | 2.6246 | 1.0895 | 2.8596 | 2.6246 | 1.0895 | 3.0124 | 2.7648 | 1.0895 | 4.797% | 0.015315 | 0.014557 | 4080.3921 | 1049.3579 | 36.5623 | 2994.4719 | 4086.964 | 0 | 0 | 4086.964 | 9.885e-05%
2026 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 3.8122 | 504 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 438.0272 | 3.9383 | 111.2217 | 438.0272 | 3.9383 | 111.2217 | 461.4316 | 4.1488 | 111.2217 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2026 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 10.9521 | 993 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 708.5447 | 11.3145 | 62.6226 | 708.5447 | 11.3145 | 62.6226 | 746.4032 | 11.9191 | 62.6226 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2026 | 723 | 723-792F | Tier-1 | Non-HFTD---19 | 1--1 | 0.2026 | 9 | 100% | 0.19474 | 41.11% | 0% | 58.89% | 0.0039627 | 0 | 0 | 0.0039627 | 0 | 0.0037802 | 0.20931 | 0.01806 | 0.0037802 | 0.20931 | 0.01806 | 0.0039821 | 0.22049 | 0.01806 | 2.035% | 0.0005522 | 0.00052487 | 352.6648 | 19.2157 | 47.4573 | 285.9917 | 363.4808 | 0 | 0 | 363.4808 | 1.307e-07%
2026 | 161 | CB 161 | Tier-1 | Non-HFTD---11 | 1--3 | 0.78239 | 11 | 100% | 13.2728 | 94.99% | 0% | 5.009% | 0.62409 | 0 | 0 | 0.62409 | 0 | 0.59534 | 0.80828 | 0.73656 | 0.59534 | 0.80828 | 0.73656 | 0.62715 | 0.85147 | 0.73656 | 4.702% | 0.002891 | 0.0027479 | 4591.0843 | 3.1452 | 4363.6333 | 224.3059 | 4603.061 | 0 | 0 | 4603.061 | 2.058e-05%
2026 | 342 | 342-514F | Tier-1 | Non-HFTD---16 | 2--1 | 4.5697 | 173 | 100% | 4.6383 | 28.46% | 0% | 71.54% | 0.065351 | 0 | 0 | 0.065351 | 0 | 0.06234 | 4.7209 | 0.013205 | 0.06234 | 4.7209 | 0.013205 | 0.065671 | 4.9732 | 0.013205 | 1.409% | 0.013236 | 0.012581 | 350.4217 | 5.7925 | 88.2778 | 256.3514 | 363.4765 | 0 | 0 | 363.4765 | 2.155e-06%
2026 | 334 | 334-21 | Tier-1 | Non-HFTD---2 | 5--3 | 7.2951 | 196 | 100% | 378.2145 | 89.09% | 9.517% | 1.396% | 16.6786 | 0 | 0 | 16.6786 | 0 | 15.9103 | 7.5365 | 2.1111 | 15.9103 | 7.5365 | 2.1111 | 16.7604 | 7.9392 | 2.1111 | 4.41% | 0.11474 | 0.10906 | 3296.3029 | 544.604 | 266.9039 | 2484.795 | 3315.0355 | 0 | 0 | 3315.0355 | 0.00055%
2026 | 314 | CB 314 | Tier-1 | Non-HFTD---1 | 3--4 | 1.0947 | 32 | 100% | 255.5795 | 52.94% | 46.78% | 0.2824% | 6.6973 | 0 | 0 | 6.6973 | 0 | 6.3887 | 1.1309 | 5.6493 | 6.3887 | 1.1309 | 5.6493 | 6.7301 | 1.1913 | 5.6493 | 2.62% | 0.021433 | 0.020372 | 11924.6916 | 952.6976 | 5630.0979 | 5341.896 | 12216.954 | 0 | 0 | 12216.954 | 0.0002209%
2026 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 7.6676 | 440 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 27.1082 | 7.9213 | 3.4222 | 27.1082 | 7.9213 | 3.4222 | 28.5567 | 8.3446 | 3.4222 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2026 | 771 | 771-274AE | Tier-1 | Non-HFTD---19 | 1--2 | 0.13125 | 10 | 100% | 0.57016 | 61.28% | 0% | 38.72% | 0.017295 | 0 | 0 | 0.017295 | 0 | 0.016498 | 0.13559 | 0.12167 | 0.016498 | 0.13559 | 0.12167 | 0.017379 | 0.14284 | 0.12167 | 3.033% | 0.0006212 | 0.00059045 | 917.8285 | 52.5226 | 272.2512 | 593.0547 | 936.3367 | 0 | 0 | 936.3367 | 5.703e-07%
2026 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 4.4809 | 284 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 45.2058 | 4.6292 | 9.7654 | 45.2058 | 4.6292 | 9.7654 | 47.6212 | 4.8765 | 9.7654 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2026 | 545 | 545-874R | Tier-1 | Non-HFTD---4 | 3--4 | 3.5507 | 93 | 100% | 149.8608 | 5.982% | 92.24% | 1.775% | 0.44376 | 0 | 0 | 0.44376 | 0 | 0.42332 | 3.6682 | 0.1154 | 0.42332 | 3.6682 | 0.1154 | 0.44594 | 3.8642 | 0.1154 | 0.2961% | 0.020584 | 0.019565 | 7280.5198 | 7.5721 | 6605.319 | 667.6287 | 7636.9922 | 0 | 0 | 7636.9922 | 1.463e-05%
2026 | 562 | CB 562 | Tier-1 | Non-HFTD---1 | 2--5 | 1.5066 | 1 | 100% | 385.0598 | 99.74% | 0% | 0.2579% | 19.0113 | 0 | 0 | 19.0113 | 0 | 18.1355 | 1.5565 | 11.6514 | 18.1355 | 1.5565 | 11.6514 | 19.1045 | 1.6397 | 11.6514 | 4.937% | 0.0064962 | 0.0061746 | 59274.622 | 37636.7204 | 2222.5751 | 19415.3265 | 59282.5839 | 0 | 0 | 59282.5839 | 0.0006269%
2026 | 256 | 256-39AE | Tier-1 | Non-HFTD---18 | 1--1 | 1.2698 | 44 | 100% | 1.0609 | 19.16% | 0% | 80.84% | 0.010061 | 0 | 0 | 0.010061 | 0 | 0.0095973 | 1.3119 | 0.0073157 | 0.0095973 | 1.3119 | 0.0073157 | 0.01011 | 1.382 | 0.0073157 | 0.9484% | 0.0034328 | 0.0032629 | 309.0347 | 0.18799 | 81.9019 | 226.9448 | 322.0452 | 0 | 0 | 322.0452 | 3.318e-07%
2026 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 13.0331 | 1634 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 873.3342 | 13.4644 | 64.8623 | 873.3342 | 13.4644 | 64.8623 | 919.9977 | 14.1839 | 64.8623 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2026 | 855 | 855-45 | Tier-1 | Non-HFTD---20 | 1--1 | 0.17043 | 1 | 100% | 0.068838 | 3.968% | 0% | 96.03% | 0.00013522 | 0 | 0 | 0.00013522 | 0 | 0.00012899 | 0.17607 | 0.00073263 | 0.00012899 | 0.17607 | 0.00073263 | 0.00013588 | 0.18547 | 0.00073263 | 0.1964% | 0.0003944 | 0.00037488 | 174.5396 | 0.12612 | 22.1525 | 152.261 | 183.2685 | 0 | 0 | 183.2685 | 4.459e-09%
2026 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 12.3091 | 646 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 640.8684 | 12.7165 | 50.3967 | 640.8684 | 12.7165 | 50.3967 | 675.1109 | 13.3959 | 50.3967 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2026 | 288 | 288-18 | Tier-1 | Non-HFTD---1 | 3--5 | 5.4562 | 1025 | 100% | 1717.8671 | 96.12% | 3.649% | 0.229% | 81.7367 | 0 | 0 | 81.7367 | 0 | 77.9713 | 5.6368 | 13.8326 | 77.9713 | 5.6368 | 13.8326 | 82.1374 | 5.938 | 13.8326 | 4.758% | 0.026137 | 0.024843 | 65724.9856 | 11143.2146 | 2230.6061 | 52351.1649 | 65857.7245 | 0 | 0 | 65857.7245 | 0.002695%
2026 | 452 | 452-47 | Tier-1 | Non-HFTD---11 | 2--3 | 1.7508 | 32 | 100% | 8.9597 | 85.97% | 0% | 14.03% | 0.3813 | 0 | 0 | 0.3813 | 0 | 0.36373 | 1.8087 | 0.2011 | 0.36373 | 1.8087 | 0.2011 | 0.38317 | 1.9053 | 0.2011 | 4.256% | 0.0051162 | 0.0048629 | 1751.2376 | 0.18482 | 1527.9269 | 223.1259 | 1764.0292 | 0 | 0 | 1764.0292 | 1.257e-05%
2026 | 69 | 69-45F | Tier-1 | Non-HFTD---4 | 2--4 | 0.32272 | 10 | 100% | 106.7813 | 2.696% | 97.13% | 0.1713% | 0.14248 | 0 | 0 | 0.14248 | 0 | 0.13592 | 0.33339 | 0.40767 | 0.13592 | 0.33339 | 0.40767 | 0.14318 | 0.35121 | 0.40767 | 0.1334% | 0.008264 | 0.0078549 | 12921.2611 | 83.6052 | 11175.4926 | 1662.1634 | 13576.0339 | 0 | 0 | 13576.0339 | 4.698e-06%
2026 | ALV1 | CB ALV1 | Tier-1 | Non-HFTD---9 | 2--3 | 1.8195 | 145 | 100% | 23.1135 | 96.16% | 0% | 3.841% | 1.1002 | 0 | 0 | 1.1002 | 0 | 1.0495 | 1.8797 | 0.55832 | 1.0495 | 1.8797 | 0.55832 | 1.1056 | 1.9802 | 0.55832 | 4.76% | 0.0050056 | 0.0047578 | 4617.5342 | 724.8553 | 33.5047 | 3859.1742 | 4626.7717 | 0 | 0 | 4626.7717 | 3.628e-05%
2026 | 60 | 60-574 | Tier-1 | Non-HFTD---13 | 2--2 | 3.014 | 84 | 100% | 8.5311 | 71.96% | 0% | 28.04% | 0.3039 | 0 | 0 | 0.3039 | 0 | 0.2899 | 3.1138 | 0.093101 | 0.2899 | 3.1138 | 0.093101 | 0.30539 | 3.2802 | 0.093101 | 3.562% | 0.0093494 | 0.0088866 | 912.477 | 24.9805 | 528.1696 | 359.327 | 925.7996 | 0 | 0 | 925.7996 | 1.002e-05%
2026 | 703 | CB 703 | Tier-1 | Non-HFTD---13 | 2--2 | 0.13314 | 1 | 100% | 6.8734 | 94.98% | 2.252% | 2.765% | 0.32316 | 0 | 0 | 0.32316 | 0 | 0.30827 | 0.13755 | 2.2412 | 0.30827 | 0.13755 | 2.2412 | 0.32475 | 0.1449 | 2.2412 | 4.702% | 0.0055408 | 0.0052665 | 1240.5052 | 28.6229 | 1027.2685 | 184.6138 | 1243.7466 | 0 | 0 | 1243.7466 | 1.066e-05%
2026 | 229 | CB 229 | Tier-1 | Non-HFTD---15 | 1--3 | 0.16098 | 0 | 100% | 2.744 | 94.71% | 0% | 5.287% | 0.12865 | 0 | 0 | 0.12865 | 0 | 0.12272 | 0.16631 | 0.73791 | 0.12272 | 0.16631 | 0.73791 | 0.12928 | 0.1752 | 0.73791 | 4.688% | 0.0005864 | 0.00055737 | 4679.4778 | 389.4263 | 2294.1086 | 1995.9429 | 4692.3613 | 0 | 0 | 4692.3613 | 4.242e-06%
2026 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 2.6869 | 346 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 20.0009 | 2.7758 | 7.2055 | 20.0009 | 2.7758 | 7.2055 | 21.0696 | 2.9241 | 7.2055 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2026 | 532 | CB 532 | Tier-1 | Non-HFTD---10 | 3--2 | 5.6968 | 88 | 100% | 16.397 | 75.87% | 0% | 24.13% | 0.61579 | 0 | 0 | 0.61579 | 0 | 0.58742 | 5.8853 | 0.099812 | 0.58742 | 5.8853 | 0.099812 | 0.61881 | 6.1997 | 0.099812 | 3.756% | 0.016027 | 0.015234 | 1023.0743 | 0.6764 | 795.5841 | 226.8138 | 1035.9312 | 0 | 0 | 1035.9312 | 2.031e-05%
2026 | 572 | 572-493F | Tier-1 | Non-HFTD---20 | 1--1 | 0.20172 | 3 | 100% | 0.12336 | 2.076% | 0% | 97.92% | 0.00012676 | 0 | 0 | 0.00012676 | 0 | 0.00012092 | 0.2084 | 0.00058022 | 0.00012092 | 0.2084 | 0.00058022 | 0.00012738 | 0.21953 | 0.00058022 | 0.1027% | 0.000542 | 0.00051517 | 227.6098 | 0.16771 | 24.9717 | 202.4705 | 239.2172 | 0 | 0 | 239.2172 | 4.18e-09%
2026 | 456 | CB 456 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0005 | 145 | 100% | 54.2335 | 91.66% | 0% | 8.342% | 2.4606 | 0 | 0 | 2.4606 | 0 | 2.3473 | 6.1991 | 0.37865 | 2.3473 | 6.1991 | 0.37865 | 2.4727 | 6.5303 | 0.37865 | 4.537% | 0.018506 | 0.01759 | 2930.6543 | 41.8221 | 2453.6064 | 435.2259 | 2943.3855 | 0 | 0 | 2943.3855 | 8.114e-05%
2026 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 16.7242 | 1062 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1445.8524 | 17.2777 | 83.6832 | 1445.8524 | 17.2777 | 83.6832 | 1523.1063 | 18.2009 | 83.6832 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2026 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 1.5242 | 73 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 12.9185 | 1.5747 | 8.204 | 12.9185 | 1.5747 | 8.204 | 13.6088 | 1.6588 | 8.204 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2026 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 3.4282 | 109 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 67.1788 | 3.5416 | 18.9684 | 67.1788 | 3.5416 | 18.9684 | 70.7683 | 3.7309 | 18.9684 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2026 | 314 | 314-13F | Tier-1 | Non-HFTD---6 | 3--3 | 0.47273 | 5 | 100% | 74.5408 | 76.13% | 23.46% | 0.4094% | 2.809 | 0 | 0 | 2.809 | 0 | 2.6796 | 0.48837 | 5.4868 | 2.6796 | 0.48837 | 5.4868 | 2.8228 | 0.51447 | 5.4868 | 3.768% | 0.019129 | 0.018182 | 3896.6601 | 485.4254 | 838.4338 | 2572.801 | 3945.1005 | 0 | 0 | 3945.1005 | 9.263e-05%
2026 | 80 | CB 80 | Tier-1 | Non-HFTD---7 | 3--3 | 5.2693 | 48 | 100% | 44.4535 | 89.11% | 0% | 10.89% | 1.9609 | 0 | 0 | 1.9609 | 0 | 1.8705 | 5.4437 | 0.34361 | 1.8705 | 5.4437 | 0.34361 | 1.9705 | 5.7345 | 0.34361 | 4.411% | 0.017052 | 0.016208 | 2606.9684 | 6.287 | 2311.46 | 289.2215 | 2621.7513 | 0 | 0 | 2621.7513 | 6.466e-05%
2026 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 1.6445 | 445 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 9.86 | 1.6989 | 5.8037 | 9.86 | 1.6989 | 5.8037 | 10.3868 | 1.7897 | 5.8037 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2026 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 5.2246 | 110 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 47.6389 | 5.3975 | 8.8261 | 47.6389 | 5.3975 | 8.8261 | 50.1843 | 5.6859 | 8.8261 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2026 | 57 | 57-1295F | Tier-1 | Non-HFTD---14 | 3--1 | 0.73143 | 22 | 100% | 5.7785 | 18.72% | 64.33% | 16.95% | 0.053541 | 0 | 0 | 0.053541 | 0 | 0.051075 | 0.75563 | 0.067592 | 0.051075 | 0.75563 | 0.067592 | 0.053804 | 0.79601 | 0.067592 | 0.9266% | 0.013816 | 0.013132 | 418.2342 | 0.34202 | 329.9664 | 87.9258 | 435.938 | 0 | 0 | 435.938 | 1.766e-06%
2026 | 1434 | CB 1434 | Tier-1 | Non-HFTD---13 | 2--2 | 2.2678 | 40 | 100% | 5.9882 | 73.95% | 0% | 26.05% | 0.21921 | 0 | 0 | 0.21921 | 0 | 0.20911 | 2.3428 | 0.089255 | 0.20911 | 2.3428 | 0.089255 | 0.22028 | 2.468 | 0.089255 | 3.661% | 0.0060046 | 0.0057074 | 997.2619 | 1.3501 | 754.0153 | 241.8966 | 1010.7891 | 0 | 0 | 1010.7891 | 7.229e-06%
2026 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 1.9464 | 59 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.86782 | 2.0108 | 0.43158 | 0.86782 | 2.0108 | 0.43158 | 0.91419 | 2.1183 | 0.43158 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2026 | 548 | 548-17F | Tier-1 | Non-HFTD---4 | 2--4 | 2.5892 | 226 | 100% | 104.2118 | 98.1% | 0% | 1.901% | 5.0604 | 0 | 0 | 5.0604 | 0 | 4.8273 | 2.6749 | 1.8047 | 4.8273 | 2.6749 | 1.8047 | 5.0852 | 2.8178 | 1.8047 | 4.856% | 0.010934 | 0.010393 | 9530.6409 | 2004.1168 | 69.3119 | 7457.2122 | 9540.0775 | 0 | 0 | 9540.0775 | 0.0001669%
2026 | 254 | CB 254 | Tier-1 | Non-HFTD---17 | 1--2 | 0.16193 | 0 | 100% | 0.87557 | 85.54% | 0% | 14.46% | 0.037073 | 0 | 0 | 0.037073 | 0 | 0.035365 | 0.16729 | 0.2114 | 0.035365 | 0.16729 | 0.2114 | 0.037254 | 0.17623 | 0.2114 | 4.234% | 0.0005892 | 0.00056003 | 1486.0267 | 199.9018 | 58.8156 | 1227.3092 | 1497.2186 | 0 | 0 | 1497.2186 | 1.223e-06%
2026 | 58 | 58-756F | Tier-1 | Non-HFTD---11 | 2--2 | 0.3534 | 9 | 100% | 14.7362 | 1.289% | 96.53% | 2.184% | 0.009405 | 0 | 0 | 0.009405 | 0 | 0.0089717 | 0.36509 | 0.024574 | 0.0089717 | 0.36509 | 0.024574 | 0.0094511 | 0.3846 | 0.024574 | 0.06382% | 0.012057 | 0.01146 | 1222.212 | 3.1244 | 1076.1922 | 142.8953 | 1285.0415 | 0 | 0 | 1285.0415 | 3.101e-07%
2026 | 186 | 186-940R | Tier-1 | Non-HFTD---1 | 4--4 | 2.8176 | 388 | 100% | 708.016 | 27.23% | 72.48% | 0.2936% | 9.5427 | 0 | 0 | 9.5427 | 0 | 9.1031 | 2.9108 | 3.1273 | 9.1031 | 2.9108 | 3.1273 | 9.5895 | 3.0664 | 3.1273 | 1.348% | 0.051585 | 0.049032 | 13725.1247 | 759.9823 | 9159.4783 | 3805.6641 | 14245.2769 | 0 | 0 | 14245.2769 | 0.0003147%
2026 | 168 | 168-703F | Tier-1 | Non-HFTD---15 | 2--1 | 1.968 | 106 | 100% | 2.7691 | 40.41% | 0% | 59.59% | 0.055392 | 0 | 0 | 0.055392 | 0 | 0.05284 | 2.0331 | 0.02599 | 0.05284 | 2.0331 | 0.02599 | 0.055664 | 2.1418 | 0.02599 | 2% | 0.0058996 | 0.0056076 | 469.3702 | 3.0577 | 197.5515 | 268.7611 | 483.9359 | 0 | 0 | 483.9359 | 1.827e-06%
2026 | 57 | 57-1296F | Tier-1 | Non-HFTD---6 | 3--3 | 4.3852 | 419 | 100% | 54.2561 | 82.4% | 11.86% | 5.738% | 2.2131 | 0 | 0 | 2.2131 | 0 | 2.1111 | 4.5303 | 0.466 | 2.1111 | 4.5303 | 0.466 | 2.2239 | 4.7724 | 0.466 | 4.079% | 0.026297 | 0.024995 | 2063.1894 | 274.7024 | 258.9091 | 1529.5779 | 2082.0976 | 0 | 0 | 2082.0976 | 7.298e-05%
2026 | 190 | 190-1868R | Tier-1 | Non-HFTD---11 | 1--4 | 0.48108 | 19 | 100% | 12.0699 | 97.67% | 0% | 2.333% | 0.58352 | 0 | 0 | 0.58352 | 0 | 0.55664 | 0.497 | 1.12 | 0.55664 | 0.497 | 1.12 | 0.58638 | 0.52355 | 1.12 | 4.835% | 0.0015928 | 0.001514 | 7577.7716 | 422.4158 | 4765.8195 | 2389.5362 | 7586.9772 | 0 | 0 | 7586.9772 | 1.924e-05%
2026 | 1139 | CB 1139 | Tier-1 | Non-HFTD---17 | 1--3 | 0.21402 | 0 | 100% | 1.9809 | 88.52% | 0% | 11.48% | 0.086804 | 0 | 0 | 0.086804 | 0 | 0.082805 | 0.2211 | 0.37452 | 0.082805 | 0.2211 | 0.37452 | 0.087229 | 0.23291 | 0.37452 | 4.382% | 0.0008862 | 0.00084233 | 2235.3083 | 105.1437 | 1355.0151 | 775.1495 | 2248.667 | 0 | 0 | 2248.667 | 2.862e-06%
2026 | LA1 | CB LA1 | Tier-1 | Non-HFTD---12 | 4--1 | 10.8148 | 231 | 100% | 14.2144 | 47.91% | 0% | 52.09% | 0.33709 | 0 | 0 | 0.33709 | 0 | 0.32156 | 11.1727 | 0.028781 | 0.32156 | 11.1727 | 0.028781 | 0.33874 | 11.7696 | 0.028781 | 2.371% | 0.029769 | 0.028295 | 477.4907 | 3.6261 | 230.2568 | 243.6078 | 490.4441 | 0 | 0 | 490.4441 | 1.112e-05%
2026 | 417 | 417-44AE | Tier-1 | Non-HFTD---5 | 2--4 | 0.70607 | 9 | 100% | 68.544 | 0.1089% | 99.12% | 0.7728% | 0.0036964 | 0 | 0 | 0.0036964 | 0 | 0.0035261 | 0.72943 | 0.004834 | 0.0035261 | 0.72943 | 0.004834 | 0.0037145 | 0.76841 | 0.004834 | 0.005393% | 0.0129 | 0.012261 | 5313.5687 | 6.798 | 4793.3964 | 513.3743 | 5589.9865 | 0 | 0 | 5589.9865 | 1.219e-07%
2026 | 1077 | CB 1077 | Tier-1 | Non-HFTD---8 | 3--2 | 8.2547 | 281 | 100% | 27.171 | 78.66% | 0% | 21.34% | 1.058 | 0 | 0 | 1.058 | 0 | 1.0092 | 8.5279 | 0.11834 | 1.0092 | 8.5279 | 0.11834 | 1.0631 | 8.9835 | 0.11834 | 3.894% | 0.023107 | 0.021963 | 1175.8656 | 180.5721 | 140.8614 | 854.4321 | 1188.933 | 0 | 0 | 1188.933 | 3.489e-05%
2026 | 738 | CB 738 | Tier-1 | Non-HFTD---17 | 1--2 | 0.53655 | 33 | 100% | 2.031 | 77.55% | 0% | 22.45% | 0.077964 | 0 | 0 | 0.077964 | 0 | 0.074373 | 0.55431 | 0.13417 | 0.074373 | 0.55431 | 0.13417 | 0.078346 | 0.58393 | 0.13417 | 3.839% | 0.0021108 | 0.0020063 | 962.2085 | 113.8791 | 22.5007 | 825.8287 | 973.4589 | 0 | 0 | 973.4589 | 2.571e-06%
2026 | 578 | CB 578 | Tier-1 | Non-HFTD---3 | 3--4 | 4.9491 | 87 | 100% | 140.4916 | 12.05% | 84.92% | 3.035% | 0.83787 | 0 | 0 | 0.83787 | 0 | 0.79927 | 5.1128 | 0.15633 | 0.79927 | 5.1128 | 0.15633 | 0.84197 | 5.386 | 0.15633 | 0.5964% | 0.025495 | 0.024233 | 5510.5967 | 5.2725 | 4912.3512 | 592.973 | 5763.0011 | 0 | 0 | 5763.0011 | 2.763e-05%
2026 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 22.2475 | 1918 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 483.4663 | 22.9837 | 21.0352 | 483.4663 | 22.9837 | 21.0352 | 509.2986 | 24.2118 | 21.0352 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2026 | BN2 | CB BN2 | Tier-1 | Non-HFTD---1 | 4--5 | 10.1083 | 520 | 100% | 1098.8312 | 99.36% | 0% | 0.6449% | 54.0413 | 0 | 0 | 54.0413 | 0 | 51.5518 | 10.4429 | 4.9366 | 51.5518 | 10.4429 | 4.9366 | 54.3063 | 11.0008 | 4.9366 | 4.918% | 0.034221 | 0.032527 | 32110.0379 | 7492.6936 | 90.1662 | 24527.178 | 32120.8227 | 0 | 0 | 32120.8227 | 0.001782%
2026 | 582 | CB 582 | Tier-1 | Non-HFTD---17 | 1--2 | 0.3354 | 8 | 100% | 1.2456 | 82.48% | 0% | 17.52% | 0.050855 | 0 | 0 | 0.050855 | 0 | 0.048512 | 0.3465 | 0.14001 | 0.048512 | 0.3465 | 0.14001 | 0.051104 | 0.36501 | 0.14001 | 4.083% | 0.0009004 | 0.00085583 | 1383.3541 | 0.23444 | 1162.7176 | 220.4021 | 1395.9743 | 0 | 0 | 1395.9743 | 1.677e-06%
2026 | 431 | 431-48AE | Tier-1 | Non-HFTD---18 | 1--1 | 1.1947 | 55 | 100% | 1.4033 | 31.02% | 0% | 68.98% | 0.021548 | 0 | 0 | 0.021548 | 0 | 0.020556 | 1.2342 | 0.016654 | 0.020556 | 1.2342 | 0.016654 | 0.021654 | 1.3002 | 0.016654 | 1.536% | 0.0035406 | 0.0033653 | 396.3532 | 0.23934 | 147.5741 | 248.5398 | 410.5915 | 0 | 0 | 410.5915 | 7.106e-07%
2026 | 595 | 595-1454F | Tier-2 | Tier-2---15 | 3--4 | 1.3606 | 113 | 100% | 124.9246 | 83.27% | 16% | 0.7306% | 5.1495 | 0 | 0 | 5.1495 | 0 | 4.9122 | 1.4056 | 3.4947 | 4.9122 | 1.4056 | 3.4947 | 5.1747 | 1.4807 | 3.4947 | 4.122% | 0.018776 | 0.017847 | 6653.3471 | 1471.8841 | 978.4778 | 4202.9852 | 6711.3017 | 0 | 0 | 6711.3017 | 0.0001698%
2026 | UP2 | CB UP2 | Tier-1 | Non-HFTD---12 | 3--2 | 6.268 | 169 | 100% | 9.6733 | 51.85% | 0% | 48.15% | 0.24825 | 0 | 0 | 0.24825 | 0 | 0.23682 | 6.4754 | 0.036572 | 0.23682 | 6.4754 | 0.036572 | 0.24947 | 6.8214 | 0.036572 | 2.566% | 0.018016 | 0.017125 | 536.9147 | 0.19455 | 301.8547 | 234.8654 | 550.3792 | 0 | 0 | 550.3792 | 8.186e-06%
2026 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 5.4881 | 1424 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 69.6651 | 5.6697 | 12.2873 | 69.6651 | 5.6697 | 12.2873 | 73.3874 | 5.9726 | 12.2873 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2026 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 7.564 | 793 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 96.0526 | 7.8143 | 12.2919 | 96.0526 | 7.8143 | 12.2919 | 101.1849 | 8.2319 | 12.2919 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2026 | 39 | CB 39 | Tier-1 | Non-HFTD---19 | 1--1 | 0.092003 | 0 | 100% | 0.12086 | 14.55% | 0% | 85.45% | 0.00087056 | 0 | 0 | 0.00087056 | 0 | 0.00083045 | 0.095048 | 0.0087372 | 0.00083045 | 0.095048 | 0.0087372 | 0.00087482 | 0.10013 | 0.0087372 | 0.7203% | 0.000339 | 0.00032222 | 356.5086 | 8.0102 | 30.562 | 317.9364 | 372.373 | 0 | 0 | 372.373 | 2.871e-08%
2026 | 313 | 313-548AE | Tier-1 | Non-HFTD---12 | 3--2 | 0.1225 | 4 | 100% | 14.2935 | 9.237% | 90.04% | 0.7189% | 0.065357 | 0 | 0 | 0.065357 | 0 | 0.062346 | 0.12655 | 0.49266 | 0.062346 | 0.12655 | 0.49266 | 0.065678 | 0.13331 | 0.49266 | 0.4573% | 0.017367 | 0.016507 | 823.0292 | 13.4104 | 588.2213 | 221.3976 | 861.9315 | 0 | 0 | 861.9315 | 2.155e-06%
2026 | 366 | 366-48 | Tier-1 | Non-HFTD---5 | 3--4 | 2.5229 | 51 | 100% | 85.178 | 1.803% | 95.42% | 2.781% | 0.076004 | 0 | 0 | 0.076004 | 0 | 0.072503 | 2.6064 | 0.027818 | 0.072503 | 2.6064 | 0.027818 | 0.076377 | 2.7456 | 0.027818 | 0.08923% | 0.013571 | 0.012899 | 6276.6562 | 7.3618 | 5560.2911 | 709.0033 | 6597.6387 | 0 | 0 | 6597.6387 | 2.506e-06%
2026 | 1140 | CB 1140 | Tier-1 | Non-HFTD---2 | 4--4 | 0.29399 | 56 | 100% | 668.0984 | 0.02919% | 99.94% | 0.02644% | 0.0096542 | 0 | 0 | 0.0096542 | 0 | 0.0092095 | 0.30372 | 0.030323 | 0.0092095 | 0.30372 | 0.030323 | 0.0097015 | 0.31994 | 0.030323 | 0.001445% | 0.087146 | 0.082832 | 7666.4439 | 10.8548 | 7025.307 | 630.2821 | 8065.5793 | 0 | 0 | 8065.5793 | 3.184e-07%
2026 | 35 | 35-297AE | Tier-1 | Non-HFTD---11 | 2--2 | 0.30568 | 35 | 100% | 10.2793 | 20.26% | 76.41% | 3.337% | 0.10307 | 0 | 0 | 0.10307 | 0 | 0.098321 | 0.3158 | 0.31134 | 0.098321 | 0.3158 | 0.31134 | 0.10357 | 0.33267 | 0.31134 | 1.003% | 0.0071058 | 0.0067541 | 1446.6053 | 46.2284 | 897.7038 | 502.6731 | 1506.6811 | 0 | 0 | 1506.6811 | 3.399e-06%
2026 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 2.4038 | 65 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 68.4792 | 2.4833 | 27.5755 | 68.4792 | 2.4833 | 27.5755 | 72.1381 | 2.616 | 27.5755 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2026 | 208 | CB 208 | Tier-1 | Non-HFTD---13 | 1--3 | 0.50053 | 7 | 100% | 7.9912 | 93.78% | 0% | 6.225% | 0.37094 | 0 | 0 | 0.37094 | 0 | 0.35385 | 0.5171 | 0.6843 | 0.35385 | 0.5171 | 0.6843 | 0.37276 | 0.54473 | 0.6843 | 4.642% | 0.0017112 | 0.0016265 | 4669.9217 | 68.1319 | 3989.8459 | 611.9439 | 4685.0604 | 0 | 0 | 4685.0604 | 1.223e-05%
2026 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 4.6394 | 937 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 214.8823 | 4.793 | 44.8328 | 214.8823 | 4.793 | 44.8328 | 226.3638 | 5.0491 | 44.8328 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2026 | 171 | 171-568 | Tier-1 | Non-HFTD---8 | 4--2 | 1.7236 | 45 | 100% | 31.0781 | 60.02% | 35.24% | 4.741% | 0.92333 | 0 | 0 | 0.92333 | 0 | 0.8808 | 1.7807 | 0.49464 | 0.8808 | 1.7807 | 0.49464 | 0.92786 | 1.8758 | 0.49464 | 2.971% | 0.032551 | 0.03094 | 954.7509 | 88.4522 | 317.464 | 548.8347 | 974.6293 | 0 | 0 | 974.6293 | 3.045e-05%
2026 | 581 | 581-49 | Tier-1 | Non-HFTD---9 | 2--3 | 2.7263 | 67 | 100% | 15.9576 | 84.86% | 0% | 15.14% | 0.67032 | 0 | 0 | 0.67032 | 0 | 0.63944 | 2.8165 | 0.22703 | 0.63944 | 2.8165 | 0.22703 | 0.67361 | 2.967 | 0.22703 | 4.201% | 0.0089802 | 0.0085357 | 1776.972 | 49.0609 | 1234.3778 | 493.5333 | 1790.9809 | 0 | 0 | 1790.9809 | 2.21e-05%
2026 | 156 | 156-529AE | Tier-1 | Non-HFTD---18 | 2--1 | 1.9048 | 13 | 100% | 2.0617 | 40.76% | 0% | 59.24% | 0.041597 | 0 | 0 | 0.041597 | 0 | 0.03968 | 1.9678 | 0.020165 | 0.03968 | 1.9678 | 0.020165 | 0.041801 | 2.073 | 0.020165 | 2.018% | 0.0054304 | 0.0051616 | 379.6623 | 1.8858 | 164.6049 | 213.1716 | 391.3754 | 0 | 0 | 391.3754 | 1.372e-06%
2026 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 6.3664 | 344 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 159.7982 | 6.5771 | 24.296 | 159.7982 | 6.5771 | 24.296 | 168.3364 | 6.9286 | 24.296 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2026 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 5.1765 | 273 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 129.6779 | 5.3478 | 24.2487 | 129.6779 | 5.3478 | 24.2487 | 136.6068 | 5.6336 | 24.2487 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2026 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.64526 | 41 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.8535 | 0.66661 | 8.781 | 5.8535 | 0.66661 | 8.781 | 6.1663 | 0.70223 | 8.781 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2026 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 0.68764 | 56 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.49467 | 0.7104 | 0.69633 | 0.49467 | 0.7104 | 0.69633 | 0.5211 | 0.74836 | 0.69633 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2026 | 900 | 900-1118F | Tier-1 | Non-HFTD---15 | 1--3 | 0.4102 | 22 | 100% | 3.8209 | 95.13% | 0% | 4.872% | 0.17992 | 0 | 0 | 0.17992 | 0 | 0.17163 | 0.42377 | 0.405 | 0.17163 | 0.42377 | 0.405 | 0.1808 | 0.44642 | 0.405 | 4.709% | 0.0011032 | 0.0010486 | 3463.4496 | 535.7058 | 23.7271 | 2904.0167 | 3472.2375 | 0 | 0 | 3472.2375 | 5.933e-06%
2026 | CG1 | CB CG1 | Tier-1 | Non-HFTD---1 | 4--4 | 8.3125 | 886 | 100% | 278.5213 | 94.12% | 3.851% | 2.028% | 12.9764 | 0 | 0 | 12.9764 | 0 | 12.3786 | 8.5876 | 1.4414 | 12.3786 | 8.5876 | 1.4414 | 13.04 | 9.0465 | 1.4414 | 4.659% | 0.029972 | 0.028488 | 9292.8406 | 1535.1687 | 384.8682 | 7372.8037 | 9321.2885 | 0 | 0 | 9321.2885 | 0.0004279%
2026 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 11.8649 | 1839 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 228.8419 | 12.2576 | 18.6694 | 228.8419 | 12.2576 | 18.6694 | 241.0693 | 12.9125 | 18.6694 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2026 | 143 | 143-147F | Tier-1 | Non-HFTD---9 | 2--3 | 0.3229 | 0 | 100% | 25.6591 | 1.387% | 97.22% | 1.391% | 0.017616 | 0 | 0 | 0.017616 | 0 | 0.016804 | 0.33359 | 0.050374 | 0.016804 | 0.33359 | 0.050374 | 0.017702 | 0.35141 | 0.050374 | 0.06865% | 0.0072518 | 0.0068928 | 3538.3122 | 10.6062 | 3051.6105 | 476.0955 | 3720.0242 | 0 | 0 | 3720.0242 | 5.809e-07%
2026 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 4.8509 | 338 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 88.4542 | 5.0115 | 17.6503 | 88.4542 | 5.0115 | 17.6503 | 93.1805 | 5.2792 | 17.6503 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2026 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 8.4771 | 468 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 657.6222 | 8.7577 | 75.0911 | 657.6222 | 8.7577 | 75.0911 | 692.7598 | 9.2256 | 75.0911 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2026 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 5.4265 | 797 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 548.8338 | 5.6061 | 97.8998 | 548.8338 | 5.6061 | 97.8998 | 578.1587 | 5.9056 | 97.8998 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2026 | 946 | CB 946 | Tier-1 | Non-HFTD---10 | 3--2 | 9.2432 | 373 | 100% | 21.7172 | 73.55% | 0% | 26.45% | 0.79062 | 0 | 0 | 0.79062 | 0 | 0.7542 | 9.5491 | 0.078981 | 0.7542 | 9.5491 | 0.078981 | 0.79449 | 10.0593 | 0.078981 | 3.641% | 0.025949 | 0.024665 | 836.9106 | 3.7986 | 613.2175 | 219.8946 | 848.4404 | 0 | 0 | 848.4404 | 2.607e-05%
2026 | 515 | CB 515 | Tier-1 | Non-HFTD---14 | 2--2 | 3.1625 | 51 | 100% | 7.211 | 59.11% | 0% | 40.89% | 0.21099 | 0 | 0 | 0.21099 | 0 | 0.20127 | 3.2672 | 0.061604 | 0.20127 | 3.2672 | 0.061604 | 0.21203 | 3.4418 | 0.061604 | 2.926% | 0.011304 | 0.010745 | 637.9041 | 25.5438 | 265.137 | 347.2233 | 651.4877 | 0 | 0 | 651.4877 | 6.958e-06%
2026 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 13.6103 | 643 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 115.3852 | 14.0607 | 8.2062 | 115.3852 | 14.0607 | 8.2062 | 121.5504 | 14.812 | 8.2062 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2026 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 12.5093 | 872 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 408.7995 | 12.9233 | 31.6328 | 408.7995 | 12.9233 | 31.6328 | 430.6423 | 13.6138 | 31.6328 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2026 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 6.6053 | 288 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 183.0917 | 6.8239 | 26.8309 | 183.0917 | 6.8239 | 26.8309 | 192.8746 | 7.1885 | 26.8309 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2026 | 481 | CB 481 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8417 | 224 | 100% | 2.6593 | 32.47% | 0% | 67.53% | 0.042738 | 0 | 0 | 0.042738 | 0 | 0.040769 | 2.9357 | 0.013887 | 0.040769 | 2.9357 | 0.013887 | 0.042947 | 3.0926 | 0.013887 | 1.607% | 0.0074788 | 0.0071086 | 355.573 | 8.8932 | 83.5025 | 263.1773 | 368.0784 | 0 | 0 | 368.0784 | 1.409e-06%
2026 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 6.3644 | 324 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 278.8709 | 6.575 | 42.414 | 278.8709 | 6.575 | 42.414 | 293.7714 | 6.9263 | 42.414 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2026 | 58 | 58-522 | Tier-1 | Non-HFTD---8 | 2--3 | 0.66855 | 23 | 100% | 27.7406 | 11.51% | 86.26% | 2.232% | 0.15806 | 0 | 0 | 0.15806 | 0 | 0.15078 | 0.69067 | 0.2183 | 0.15078 | 0.69067 | 0.2183 | 0.15883 | 0.72758 | 0.2183 | 0.5698% | 0.012983 | 0.01234 | 2136.6878 | 9.4433 | 1891.1628 | 236.0817 | 2235.1536 | 0 | 0 | 2235.1536 | 5.212e-06%
2026 | 85 | CB 85 | Tier-1 | Non-HFTD---6 | 3--3 | 6.3067 | 296 | 100% | 49.3225 | 92.1% | 0% | 7.898% | 2.2486 | 0 | 0 | 2.2486 | 0 | 2.145 | 6.5154 | 0.32923 | 2.145 | 6.5154 | 0.32923 | 2.2597 | 6.8635 | 0.32923 | 4.559% | 0.02128 | 0.020227 | 2317.7858 | 252.1431 | 971.833 | 1093.8096 | 2327.3193 | 0 | 0 | 2327.3193 | 7.415e-05%
2026 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 13.604 | 899 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 861.4981 | 14.0542 | 61.2982 | 861.4981 | 14.0542 | 61.2982 | 907.5291 | 14.8051 | 61.2982 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2026 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 20.4475 | 1782 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 130.6179 | 21.1242 | 6.1833 | 130.6179 | 21.1242 | 6.1833 | 137.597 | 22.2529 | 6.1833 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2026 | 130 | 130-14F | Tier-1 | Non-HFTD---17 | 1--1 | 0.84125 | 47 | 100% | 1.0142 | 40.98% | 0% | 59.02% | 0.020571 | 0 | 0 | 0.020571 | 0 | 0.019623 | 0.86909 | 0.022579 | 0.019623 | 0.86909 | 0.022579 | 0.020672 | 0.91553 | 0.022579 | 2.028% | 0.002514 | 0.0023896 | 403.4011 | 3.3646 | 167.0213 | 233.0153 | 415.8008 | 0 | 0 | 415.8008 | 6.783e-07%
2026 | 361 | CB 361 | Tier-1 | Non-HFTD---5 | 2--4 | 1.65 | 12 | 100% | 72.0528 | 3.654% | 93.91% | 2.433% | 0.13032 | 0 | 0 | 0.13032 | 0 | 0.12431 | 1.7046 | 0.072929 | 0.12431 | 1.7046 | 0.072929 | 0.13096 | 1.7957 | 0.072929 | 0.1809% | 0.010387 | 0.0098725 | 6937.0919 | 7.1268 | 6176.303 | 753.6622 | 7285.1607 | 0 | 0 | 7285.1607 | 4.297e-06%
2026 | 310 | 310-719F | Tier-1 | Non-HFTD---3 | 3--4 | 3.2121 | 143 | 100% | 124.5147 | 2.263% | 95.99% | 1.745% | 0.13948 | 0 | 0 | 0.13948 | 0 | 0.13306 | 3.3184 | 0.040097 | 0.13306 | 3.3184 | 0.040097 | 0.14017 | 3.4957 | 0.040097 | 0.112% | 0.025632 | 0.024363 | 4857.7828 | 6.9446 | 4370.4656 | 480.3726 | 5105.0406 | 0 | 0 | 5105.0406 | 4.6e-06%
2026 | 1283 | CB 1283 | Tier-1 | Non-HFTD---15 | 1--3 | 0.69583 | 17 | 100% | 4.6015 | 87.53% | 0% | 12.47% | 0.19938 | 0 | 0 | 0.19938 | 0 | 0.19019 | 0.71886 | 0.26457 | 0.19019 | 0.71886 | 0.26457 | 0.20035 | 0.75727 | 0.26457 | 4.333% | 0.002425 | 0.002305 | 1897.5339 | 258.5117 | 88.6838 | 1550.3385 | 1909.8545 | 0 | 0 | 1909.8545 | 6.575e-06%
2026 | 518 | CB 518 | Tier-1 | Non-HFTD---11 | 2--3 | 2.5012 | 35 | 100% | 15.0618 | 85.82% | 0% | 14.18% | 0.63981 | 0 | 0 | 0.63981 | 0 | 0.61033 | 2.5839 | 0.2362 | 0.61033 | 2.5839 | 0.2362 | 0.64294 | 2.722 | 0.2362 | 4.248% | 0.008289 | 0.0078787 | 1817.08 | 17.4829 | 1476.3748 | 323.2224 | 1830.5026 | 0 | 0 | 1830.5026 | 2.11e-05%
2026 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 15.4477 | 850 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1739.5055 | 15.959 | 108.9986 | 1739.5055 | 15.959 | 108.9986 | 1832.4497 | 16.8117 | 108.9986 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2026 | 76 | CB 76 | Tier-1 | Non-HFTD---17 | 1--2 | 0.68485 | 11 | 100% | 2.0654 | 56.67% | 0% | 43.33% | 0.057942 | 0 | 0 | 0.057942 | 0 | 0.055273 | 0.70752 | 0.078122 | 0.055273 | 0.70752 | 0.078122 | 0.058226 | 0.74532 | 0.078122 | 2.805% | 0.0027636 | 0.0026268 | 747.3661 | 2.0048 | 442.1787 | 303.1826 | 764.2293 | 0 | 0 | 764.2293 | 1.911e-06%
2026 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 31.9017 | 2321 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 398.5744 | 32.9574 | 12.0936 | 398.5744 | 32.9574 | 12.0936 | 419.8708 | 34.7184 | 12.0936 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2026 | 169 | CB 169 | Tier-1 | Non-HFTD---19 | 1--2 | 0.17503 | 9 | 100% | 0.4733 | 37.59% | 0% | 62.41% | 0.008807 | 0 | 0 | 0.008807 | 0 | 0.0084013 | 0.18082 | 0.046461 | 0.0084013 | 0.18082 | 0.046461 | 0.0088502 | 0.19049 | 0.046461 | 1.861% | 0.0007436 | 0.00070679 | 636.5041 | 14.2067 | 190.1326 | 432.1648 | 657.1913 | 0 | 0 | 657.1913 | 2.904e-07%
2026 | 415 | 415-33 | Tier-1 | Non-HFTD---3 | 4--3 | 9.518 | 398 | 100% | 139.7786 | 20.17% | 75.04% | 4.79% | 1.3955 | 0 | 0 | 1.3955 | 0 | 1.3312 | 9.833 | 0.13538 | 1.3312 | 9.833 | 0.13538 | 1.4023 | 10.3584 | 0.13538 | 0.9983% | 0.039288 | 0.037343 | 3557.7759 | 167.3493 | 2542.2057 | 848.2208 | 3705.6889 | 0 | 0 | 3705.6889 | 4.602e-05%
2026 | QN1 | CB QN1 | Tier-1 | Non-HFTD---12 | 2--2 | 2.5479 | 232 | 100% | 9.4771 | 20.58% | 60.74% | 18.68% | 0.096528 | 0 | 0 | 0.096528 | 0 | 0.092082 | 2.6322 | 0.034982 | 0.092082 | 2.6322 | 0.034982 | 0.097002 | 2.7729 | 0.034982 | 1.019% | 0.01229 | 0.011681 | 771.15 | 21.6223 | 474.8473 | 274.6805 | 803.0463 | 0 | 0 | 803.0463 | 3.183e-06%
2026 | 535 | CB 535 | Tier-2 | Tier-2---16 | 4--3 | 0.31174 | 0 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25308 | 0 | 0 | 0.25308 | 0 | 0.24142 | 0.32206 | 0.74961 | 0.24142 | 0.32206 | 0.74961 | 0.25432 | 0.33927 | 0.74961 | 0.227% | 0.059698 | 0.056743 | 1867.7052 | 14.9488 | 1426.0626 | 426.6938 | 1960.5113 | 0 | 0 | 1960.5113 | 8.346e-06%
2026 | 72 | 72-16 | Tier-1 | Non-HFTD---14 | 2--1 | 4.3345 | 108 | 100% | 6.3445 | 45.63% | 0% | 54.37% | 0.1433 | 0 | 0 | 0.1433 | 0 | 0.1367 | 4.4779 | 0.030527 | 0.1367 | 4.4779 | 0.030527 | 0.144 | 4.7172 | 0.030527 | 2.259% | 0.012945 | 0.012305 | 490.0991 | 5.3198 | 229.2157 | 255.5636 | 503.9765 | 0 | 0 | 503.9765 | 4.725e-06%
2026 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 11.0435 | 650 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 61.1326 | 11.409 | 5.3583 | 61.1326 | 11.409 | 5.3583 | 64.399 | 12.0186 | 5.3583 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2026 | 197 | 197-1157F | Tier-2 | Tier-2---18 | 3--3 | 0.44794 | 76 | 100% | 63.1655 | 1.305% | 98.13% | 0.5601% | 0.040803 | 0 | 0 | 0.040803 | 0 | 0.038923 | 0.46277 | 0.08411 | 0.038923 | 0.46277 | 0.08411 | 0.041003 | 0.48749 | 0.08411 | 0.0646% | 0.01787 | 0.016985 | 3534.7635 | 11.6765 | 2974.4275 | 548.6595 | 3716.4442 | 0 | 0 | 3716.4442 | 1.346e-06%
2026 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 11.3506 | 1480 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 296.4305 | 11.7262 | 25.2793 | 296.4305 | 11.7262 | 25.2793 | 312.2692 | 12.3528 | 25.2793 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2026 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 6.2962 | 610 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 348.8651 | 6.5046 | 53.6337 | 348.8651 | 6.5046 | 53.6337 | 367.5055 | 6.8521 | 53.6337 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2026 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.99152 | 180 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 83.4003 | 1.0243 | 81.4193 | 83.4003 | 1.0243 | 81.4193 | 87.8565 | 1.0791 | 81.4193 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2026 | 298 | 298-384 | Tier-1 | Non-HFTD---19 | 1--2 | 0.022348 | 0 | 100% | 0.1467 | 75.48% | 0% | 24.52% | 0.0054809 | 0 | 0 | 0.0054809 | 0 | 0.0052284 | 0.023088 | 0.22645 | 0.0052284 | 0.023088 | 0.22645 | 0.0055078 | 0.024322 | 0.22645 | 3.736% | 0.0001034 | 9.8282e-05 | 1418.7583 | 113.2285 | 410.6318 | 894.898 | 1436.8769 | 0 | 0 | 1436.8769 | 1.807e-07%
2026 | 728 | 728-1570F | Tier-2 | Tier-2---19 | 1--5 | 0.074417 | 14 | 100% | 33.2807 | 99.79% | 0% | 0.2133% | 1.6439 | 0 | 0 | 1.6439 | 0 | 1.5682 | 0.076879 | 20.3976 | 1.5682 | 0.076879 | 20.3976 | 1.6519 | 0.080987 | 20.3976 | 4.939% | 0.0003472 | 0.00033001 | 95854.6419 | 22304.1965 | 20.1049 | 73530.3404 | 95865.2904 | 0 | 0 | 95865.2904 | 5.421e-05%
2026 | 176 | CB 176 | Tier-1 | Non-HFTD---10 | 4--1 | 0.063306 | 6 | 100% | 15.5544 | 4.631% | 94.88% | 0.4893% | 0.035657 | 0 | 0 | 0.035657 | 0 | 0.034014 | 0.065401 | 0.52009 | 0.034014 | 0.065401 | 0.52009 | 0.035832 | 0.068896 | 0.52009 | 0.2292% | 0.032585 | 0.030972 | 477.3549 | 3.466 | 417.7975 | 56.0913 | 501.0632 | 0 | 0 | 501.0632 | 1.176e-06%
2026 | 44 | CB 44 | Tier-1 | Non-HFTD---9 | 3--2 | 5.4639 | 138 | 100% | 25.8658 | 84.4% | 0% | 15.6% | 1.0806 | 0 | 0 | 1.0806 | 0 | 1.0308 | 5.6447 | 0.18262 | 1.0308 | 5.6447 | 0.18262 | 1.0859 | 5.9463 | 0.18262 | 4.178% | 0.016291 | 0.015485 | 1587.7136 | 11.2067 | 1294.5636 | 281.9434 | 1600.6131 | 0 | 0 | 1600.6131 | 3.563e-05%
2026 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.31499 | 10 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.6787 | 0.32542 | 23.5965 | 7.6787 | 0.32542 | 23.5965 | 8.089 | 0.34281 | 23.5965 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2026 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 12.7815 | 1624 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1267.761 | 13.2045 | 96.01 | 1267.761 | 13.2045 | 96.01 | 1335.4992 | 13.91 | 96.01 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2026 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 5.0748 | 159 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 183.9861 | 5.2427 | 35.0936 | 183.9861 | 5.2427 | 35.0936 | 193.8167 | 5.5229 | 35.0936 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2026 | 759 | CB 759 | Tier-1 | Non-HFTD---11 | 2--2 | 3.6532 | 193 | 100% | 13.6768 | 80.97% | 0% | 19.03% | 0.5482 | 0 | 0 | 0.5482 | 0 | 0.52294 | 3.7741 | 0.13856 | 0.52294 | 3.7741 | 0.13856 | 0.55088 | 3.9757 | 0.13856 | 4.008% | 0.010883 | 0.010344 | 1256.7154 | 15.5947 | 944.7873 | 296.3334 | 1269.1674 | 0 | 0 | 1269.1674 | 1.808e-05%
2026 | 325 | 325-1227F | Tier-1 | Non-HFTD---13 | 1--4 | 0.24205 | 4 | 100% | 7.4492 | 97.14% | 0% | 2.857% | 0.3582 | 0 | 0 | 0.3582 | 0 | 0.3417 | 0.25006 | 1.3665 | 0.3417 | 0.25006 | 1.3665 | 0.35996 | 0.26342 | 1.3665 | 4.809% | 0.000908 | 0.00086305 | 8203.9485 | 1304.1799 | 23.899 | 6875.8695 | 8216.1539 | 0 | 0 | 8216.1539 | 1.181e-05%
2026 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 6.2051 | 618 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.88582 | 6.4105 | 0.13818 | 0.88582 | 6.4105 | 0.13818 | 0.93315 | 6.753 | 0.13818 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2026 | 794 | 794-1002 | Tier-1 | Non-HFTD---4 | 3--4 | 1.1659 | 43 | 100% | 176.6639 | 5.845% | 93.67% | 0.4796% | 0.51118 | 0 | 0 | 0.51118 | 0 | 0.48763 | 1.2044 | 0.40486 | 0.48763 | 1.2044 | 0.40486 | 0.51368 | 1.2688 | 0.40486 | 0.2894% | 0.021091 | 0.020047 | 8376.1891 | 42.6247 | 7445.0358 | 888.5286 | 8786.9043 | 0 | 0 | 8786.9043 | 1.686e-05%
2026 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 10.0271 | 878 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 29.8334 | 10.3589 | 2.88 | 29.8334 | 10.3589 | 2.88 | 31.4275 | 10.9124 | 2.88 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2026 | 795 | CB 795 | Tier-1 | Non-HFTD---12 | 3--2 | 0.64564 | 34 | 100% | 12.7544 | 93.94% | 1.477% | 4.587% | 0.59306 | 0 | 0 | 0.59306 | 0 | 0.56574 | 0.66701 | 0.84817 | 0.56574 | 0.66701 | 0.84817 | 0.59596 | 0.70265 | 0.84817 | 4.65% | 0.020541 | 0.019524 | 620.9301 | 28.9913 | 416.0915 | 175.8474 | 622.891 | 0 | 0 | 622.891 | 1.956e-05%
2026 | 74 | 74-35R | Tier-1 | Non-HFTD---5 | 2--4 | 1.7629 | 93 | 100% | 50.9295 | 97.64% | 0% | 2.355% | 2.4616 | 0 | 0 | 2.4616 | 0 | 2.3482 | 1.8212 | 1.2894 | 2.3482 | 1.8212 | 1.2894 | 2.4737 | 1.9185 | 1.2894 | 4.833% | 0.0071104 | 0.0067584 | 7162.6834 | 1136.9423 | 64.4037 | 5961.3374 | 7171.4683 | 0 | 0 | 7171.4683 | 8.118e-05%
2026 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.43141 | 4 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 5.4171 | 0.44569 | 12.1544 | 5.4171 | 0.44569 | 12.1544 | 5.7065 | 0.4695 | 12.1544 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2026 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.44811 | 21 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.8774 | 0.46294 | 10.5357 | 4.8774 | 0.46294 | 10.5357 | 5.138 | 0.48767 | 10.5357 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2026 | 322 | 322-821F | Tier-1 | Non-HFTD---10 | 4--2 | 12.5641 | 239 | 100% | 18.5107 | 56.59% | 0% | 43.41% | 0.51854 | 0 | 0 | 0.51854 | 0 | 0.49465 | 12.9798 | 0.038109 | 0.49465 | 12.9798 | 0.038109 | 0.52108 | 13.6734 | 0.038109 | 2.801% | 0.033072 | 0.031435 | 559.7082 | 23.5182 | 196.1441 | 340.0459 | 572.3609 | 0 | 0 | 572.3609 | 1.71e-05%
2026 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 4.2677 | 342 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 60.2656 | 4.4089 | 13.6691 | 60.2656 | 4.4089 | 13.6691 | 63.4857 | 4.6445 | 13.6691 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2026 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 14.6288 | 344 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 40.436 | 15.1129 | 2.6756 | 40.436 | 15.1129 | 2.6756 | 42.5966 | 15.9204 | 2.6756 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2026 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 0.11231 | 26 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.16305 | 0.11603 | 1.4053 | 0.16305 | 0.11603 | 1.4053 | 0.17176 | 0.12223 | 1.4053 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2026 | 546 | 546-12 | Tier-1 | Non-HFTD---11 | 2--2 | 0.83025 | 13 | 100% | 14.4143 | 0.3875% | 96.68% | 2.928% | 0.0027652 | 0 | 0 | 0.0027652 | 0 | 0.0026378 | 0.85773 | 0.0030753 | 0.0026378 | 0.85773 | 0.0030753 | 0.0027787 | 0.90356 | 0.0030753 | 0.01918% | 0.01256 | 0.011939 | 1147.5972 | 1.952 | 997.2808 | 148.3644 | 1207.13 | 0 | 0 | 1207.13 | 9.119e-08%
2026 | 266 | 266-485F | Tier-2 | Tier-2---21 | 1--4 | 0.18886 | 56 | 100% | 3.9025 | 97.35% | 0% | 2.654% | 0.18805 | 0 | 0 | 0.18805 | 0 | 0.17939 | 0.19511 | 0.91943 | 0.17939 | 0.19511 | 0.91943 | 0.18897 | 0.20553 | 0.91943 | 4.819% | 0.000646 | 0.00061402 | 6041.0896 | 954.7948 | 18.9693 | 5067.3254 | 6049.4401 | 0 | 0 | 6049.4401 | 6.201e-06%
2026 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 12.6949 | 1154 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 318.8395 | 13.115 | 24.311 | 318.8395 | 13.115 | 24.311 | 335.8755 | 13.8158 | 24.311 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2026 | 859 | CB 859 | Tier-1 | Non-HFTD---13 | 1--4 | 0.2674 | 5 | 100% | 6.3536 | 96.15% | 0% | 3.853% | 0.30239 | 0 | 0 | 0.30239 | 0 | 0.28846 | 0.27625 | 1.0442 | 0.28846 | 0.27625 | 1.0442 | 0.30387 | 0.29101 | 1.0442 | 4.759% | 0.0009722 | 0.00092408 | 6535.3261 | 323.1257 | 4329.0086 | 1883.1918 | 6548.4396 | 0 | 0 | 6548.4396 | 9.972e-06%
2026 | 376 | 376-491R | Tier-1 | Non-HFTD---10 | 2--2 | 4.3338 | 110 | 100% | 15.387 | 85.15% | 0% | 14.85% | 0.64853 | 0 | 0 | 0.64853 | 0 | 0.61865 | 4.4772 | 0.13818 | 0.61865 | 4.4772 | 0.13818 | 0.65171 | 4.7164 | 0.13818 | 4.215% | 0.011779 | 0.011196 | 1306.2651 | 20.6652 | 1016.2338 | 269.3662 | 1316.3691 | 0 | 0 | 1316.3691 | 2.139e-05%
2026 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.052462 | 7 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.3625 | 0.054198 | 62.0412 | 3.3625 | 0.054198 | 62.0412 | 3.5422 | 0.057094 | 62.0412 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2026 | 310 | 310-718F | Tier-1 | Non-HFTD---17 | 1--3 | 0.087462 | 0 | 100% | 0.81802 | 90.7% | 0% | 9.303% | 0.036725 | 0 | 0 | 0.036725 | 0 | 0.035033 | 0.090357 | 0.38772 | 0.035033 | 0.090357 | 0.38772 | 0.036905 | 0.095184 | 0.38772 | 4.49% | 0.000254 | 0.00024143 | 3220.5537 | 0.90818 | 2943.8401 | 275.8054 | 3236.1564 | 0 | 0 | 3236.1564 | 1.211e-06%
2026 | 548 | 548-15F | Tier-1 | Non-HFTD---11 | 2--3 | 1.8856 | 63 | 100% | 14.762 | 91.23% | 0% | 8.768% | 0.66665 | 0 | 0 | 0.66665 | 0 | 0.63594 | 1.948 | 0.32645 | 0.63594 | 1.948 | 0.32645 | 0.66992 | 2.0521 | 0.32645 | 4.516% | 0.005445 | 0.0051755 | 2711.1073 | 395.5509 | 80.5547 | 2235.0017 | 2723.487 | 0 | 0 | 2723.487 | 2.198e-05%
2026 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 3.6661 | 275 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 237.4956 | 3.7874 | 62.7064 | 237.4956 | 3.7874 | 62.7064 | 250.1853 | 3.9898 | 62.7064 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2026 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 11.4998 | 62 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 64.4441 | 11.8803 | 5.4244 | 64.4441 | 11.8803 | 5.4244 | 67.8874 | 12.5151 | 5.4244 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2026 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 0.92708 | 47 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.12044 | 0.95776 | 0.12576 | 0.12044 | 0.95776 | 0.12576 | 0.12688 | 1.0089 | 0.12576 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2026 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.87727 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 68.6427 | 0.9063 | 75.7391 | 68.6427 | 0.9063 | 75.7391 | 72.3104 | 0.95473 | 75.7391 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2026 | 1406 | 1406-19F | Tier-1 | Non-HFTD---11 | 3--2 | 5.6559 | 78 | 100% | 15.0674 | 83.86% | 0% | 16.14% | 0.62542 | 0 | 0 | 0.62542 | 0 | 0.59661 | 5.843 | 0.10211 | 0.59661 | 5.843 | 0.10211 | 0.62849 | 6.1553 | 0.10211 | 4.151% | 0.013569 | 0.012898 | 1110.3933 | 84.7049 | 427.6552 | 598.0332 | 1119.7291 | 0 | 0 | 1119.7291 | 2.062e-05%
2026 | BT1 | CB BT1 | Tier-1 | Non-HFTD---17 | 1--1 | 1.1276 | 81 | 100% | 1.503 | 53.13% | 0% | 46.87% | 0.03953 | 0 | 0 | 0.03953 | 0 | 0.037709 | 1.1649 | 0.032371 | 0.037709 | 1.1649 | 0.032371 | 0.039724 | 1.2272 | 0.032371 | 2.63% | 0.0030182 | 0.0028688 | 497.9935 | 40.6456 | 38.8309 | 418.5169 | 510.1485 | 0 | 0 | 510.1485 | 1.304e-06%
2026 | 509 | CB 509 | Tier-1 | Non-HFTD---10 | 3--2 | 10.0667 | 447 | 100% | 23.3118 | 74.78% | 0% | 25.22% | 0.86292 | 0 | 0 | 0.86292 | 0 | 0.82317 | 10.3998 | 0.079152 | 0.82317 | 10.3998 | 0.079152 | 0.86715 | 10.9555 | 0.079152 | 3.702% | 0.027199 | 0.025853 | 857.0759 | 12.4778 | 585.3688 | 259.2293 | 868.3324 | 0 | 0 | 868.3324 | 2.846e-05%
2026 | 567 | CB 567 | Tier-1 | Non-HFTD---7 | 1--4 | 0.56364 | 51 | 100% | 37.3049 | 99.02% | 0% | 0.9826% | 1.8284 | 0 | 0 | 1.8284 | 0 | 1.7442 | 0.58229 | 2.9954 | 1.7442 | 0.58229 | 2.9954 | 1.8374 | 0.6134 | 2.9954 | 4.901% | 0.0023798 | 0.002262 | 15675.6634 | 2324.2738 | 1292.524 | 12058.8657 | 15683.6852 | 0 | 0 | 15683.6852 | 6.03e-05%
2026 | 900 | 900-1163F | Tier-1 | Non-HFTD---19 | 1--1 | 0.24072 | 21 | 100% | 0.28819 | 42.17% | 0% | 57.83% | 0.0060154 | 0 | 0 | 0.0060154 | 0 | 0.0057383 | 0.24869 | 0.023075 | 0.0057383 | 0.24869 | 0.023075 | 0.0060449 | 0.26197 | 0.023075 | 2.087% | 0.0008402 | 0.00079861 | 343.0068 | 17.2218 | 58.4349 | 267.35 | 353.3375 | 0 | 0 | 353.3375 | 1.984e-07%
2026 | 1180 | 1180-9 | Tier-1 | Non-HFTD---15 | 2--2 | 2.6981 | 65 | 100% | 4.0697 | 57.31% | 0% | 42.69% | 0.11546 | 0 | 0 | 0.11546 | 0 | 0.11014 | 2.7874 | 0.039514 | 0.11014 | 2.7874 | 0.039514 | 0.11603 | 2.9364 | 0.039514 | 2.837% | 0.00751 | 0.0071383 | 541.9067 | 54.2911 | 113.8438 | 373.7718 | 553.9532 | 0 | 0 | 553.9532 | 3.807e-06%
2026 | NO2 | CB NO2 | Tier-1 | Non-HFTD---12 | 3--1 | 8.0842 | 188 | 100% | 8.9476 | 36.78% | 0% | 63.22% | 0.16292 | 0 | 0 | 0.16292 | 0 | 0.15541 | 8.3518 | 0.018609 | 0.15541 | 8.3518 | 0.018609 | 0.16372 | 8.798 | 0.018609 | 1.821% | 0.022313 | 0.021209 | 401.0024 | 0.19075 | 170.5339 | 230.2778 | 414.204 | 0 | 0 | 414.204 | 5.372e-06%
2026 | 35 | 35-2 | Tier-1 | Non-HFTD---5 | 2--4 | 0.48065 | 5 | 100% | 55.5571 | 6.064% | 93.16% | 0.7781% | 0.16677 | 0 | 0 | 0.16677 | 0 | 0.15909 | 0.49655 | 0.32038 | 0.15909 | 0.49655 | 0.32038 | 0.16759 | 0.52308 | 0.32038 | 0.3002% | 0.0075196 | 0.0071474 | 7388.3078 | 76.3747 | 6138.5143 | 1173.4188 | 7749.742 | 0 | 0 | 7749.742 | 5.499e-06%
2026 | 462 | 462-1523F | Tier-1 | Non-HFTD---13 | 1--3 | 0.86758 | 18 | 100% | 5.2887 | 89.35% | 0% | 10.65% | 0.2339 | 0 | 0 | 0.2339 | 0 | 0.22313 | 0.89629 | 0.24895 | 0.22313 | 0.89629 | 0.24895 | 0.23505 | 0.94418 | 0.24895 | 4.423% | 0.0023366 | 0.0022209 | 2263.4326 | 314.0218 | 110.4125 | 1838.9983 | 2275.9905 | 0 | 0 | 2275.9905 | 7.713e-06%
2026 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 10.906 | 208 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 301.8886 | 11.267 | 26.7942 | 301.8886 | 11.267 | 26.7942 | 318.019 | 11.869 | 26.7942 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2026 | 190 | 190-1125F | Tier-1 | Non-HFTD---17 | 1--4 | 0.044508 | 0 | 100% | 1.3314 | 97.57% | 0% | 2.433% | 0.064301 | 0 | 0 | 0.064301 | 0 | 0.061339 | 0.04598 | 1.334 | 0.061339 | 0.04598 | 1.334 | 0.064616 | 0.048437 | 1.334 | 4.83% | 0.0001574 | 0.00014961 | 8458.7881 | 1300.024 | 20.0108 | 7138.7533 | 8469.5078 | 0 | 0 | 8469.5078 | 2.12e-06%
2026 | 63 | CB 63 | Tier-1 | Non-HFTD---1 | 3--4 | 2.7163 | 250 | 100% | 198.805 | 36.18% | 62.9% | 0.9206% | 3.5599 | 0 | 0 | 3.5599 | 0 | 3.3959 | 2.8062 | 1.2102 | 3.3959 | 2.8062 | 1.2102 | 3.5774 | 2.9561 | 1.2102 | 1.791% | 0.019218 | 0.018267 | 10344.6205 | 564.0493 | 6645.6212 | 3134.95 | 10688.4616 | 0 | 0 | 10688.4616 | 0.0001174%
2026 | 325 | 325-22R | Tier-1 | Non-HFTD---12 | 3--2 | 8.3706 | 226 | 100% | 13.8312 | 56.1% | 0% | 43.9% | 0.38407 | 0 | 0 | 0.38407 | 0 | 0.36638 | 8.6477 | 0.042368 | 0.36638 | 8.6477 | 0.042368 | 0.38596 | 9.1097 | 0.042368 | 2.777% | 0.024153 | 0.022957 | 572.6603 | 37.8929 | 176.6374 | 358.13 | 585.7531 | 0 | 0 | 585.7531 | 1.267e-05%
2026 | 1219 | CB 1219 | Tier-1 | Non-HFTD---19 | 1--1 | 0.23918 | 9 | 100% | 0.3441 | 26.91% | 0% | 73.09% | 0.0045828 | 0 | 0 | 0.0045828 | 0 | 0.0043716 | 0.2471 | 0.017692 | 0.0043716 | 0.2471 | 0.017692 | 0.0046052 | 0.2603 | 0.017692 | 1.332% | 0.0008074 | 0.00076743 | 426.1824 | 17.8119 | 34.3349 | 374.0356 | 442.4055 | 0 | 0 | 442.4055 | 1.511e-07%
2026 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 4.9148 | 696 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 33.6771 | 5.0775 | 6.6327 | 33.6771 | 5.0775 | 6.6327 | 35.4765 | 5.3487 | 6.6327 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2026 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.085985 | 0 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.3373 | 0.08883 | 37.5694 | 3.3373 | 0.08883 | 37.5694 | 3.5156 | 0.093577 | 37.5694 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2026 | LJ3 | CB LJ3 | Tier-1 | Non-HFTD---14 | 3--1 | 5.2941 | 292 | 100% | 6.3096 | 39.49% | 0% | 60.51% | 0.12333 | 0 | 0 | 0.12333 | 0 | 0.11764 | 5.4693 | 0.02151 | 0.11764 | 5.4693 | 0.02151 | 0.12393 | 5.7615 | 0.02151 | 1.955% | 0.014718 | 0.013989 | 428.7031 | 0.52088 | 190.8463 | 237.3358 | 442.2133 | 0 | 0 | 442.2133 | 4.067e-06%
2026 | 286 | 286-990AE | Tier-1 | Non-HFTD---6 | 3--3 | 4.5934 | 275 | 100% | 50.0124 | 5.334% | 88.41% | 6.257% | 0.13205 | 0 | 0 | 0.13205 | 0 | 0.12597 | 4.7454 | 0.026546 | 0.12597 | 4.7454 | 0.026546 | 0.1327 | 4.9989 | 0.026546 | 0.264% | 0.018547 | 0.017629 | 2696.5813 | 3.2353 | 2292.3777 | 400.9683 | 2829.5225 | 0 | 0 | 2829.5225 | 4.355e-06%
2026 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 10.6016 | 377 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 42.0166 | 10.9524 | 3.8363 | 42.0166 | 10.9524 | 3.8363 | 44.2616 | 11.5376 | 3.8363 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2026 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 4.2055 | 350 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 170.7918 | 4.3447 | 39.3108 | 170.7918 | 4.3447 | 39.3108 | 179.9174 | 4.5768 | 39.3108 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2026 | 700 | 700-259F | Tier-1 | Non-HFTD---18 | 2--1 | 0.55551 | 19 | 100% | 1.7805 | 42.11% | 22.63% | 35.26% | 0.037115 | 0 | 0 | 0.037115 | 0 | 0.035405 | 0.5739 | 0.061693 | 0.035405 | 0.5739 | 0.061693 | 0.037297 | 0.60456 | 0.061693 | 2.085% | 0.0075412 | 0.0071679 | 236.1005 | 16.7944 | 50.0362 | 169.27 | 243.2182 | 0 | 0 | 243.2182 | 1.224e-06%
2026 | 311 | 311-14R | Tier-2 | Tier-2---14 | 3--4 | 0.75338 | 24 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 2.2455 | 0 | 0 | 2.2455 | 0 | 2.1421 | 0.77831 | 2.7522 | 2.1421 | 0.77831 | 2.7522 | 2.2565 | 0.8199 | 2.7522 | 0.8058% | 0.018935 | 0.017998 | 14715.9264 | 335.1634 | 11691.6167 | 2689.1463 | 15357.5365 | 0 | 0 | 15357.5365 | 7.405e-05%
2026 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 13.7044 | 1323 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 336.8429 | 14.1579 | 23.7919 | 336.8429 | 14.1579 | 23.7919 | 354.8409 | 14.9144 | 23.7919 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2026 | SC1 | CB SC1 | Tier-1 | Non-HFTD---2 | 4--4 | 7.9705 | 397 | 100% | 245.1307 | 1.784% | 95.78% | 2.439% | 0.21643 | 0 | 0 | 0.21643 | 0 | 0.20646 | 8.2343 | 0.025073 | 0.20646 | 8.2343 | 0.025073 | 0.21749 | 8.6742 | 0.025073 | 0.08829% | 0.040226 | 0.038235 | 6093.8082 | 6.9984 | 5431.9692 | 654.8405 | 6405.5002 | 0 | 0 | 6405.5002 | 7.137e-06%
2026 | 381 | 381-48 | Tier-1 | Non-HFTD---13 | 2--2 | 2.1998 | 102 | 100% | 7.9134 | 78.55% | 0% | 21.45% | 0.30769 | 0 | 0 | 0.30769 | 0 | 0.29351 | 2.2726 | 0.12915 | 0.29351 | 2.2726 | 0.12915 | 0.30919 | 2.394 | 0.12915 | 3.888% | 0.0068838 | 0.0065431 | 1149.5636 | 150.1274 | 123.1813 | 876.2549 | 1162.4055 | 0 | 0 | 1162.4055 | 1.015e-05%
2026 | CHA1 | CB CHA1 | Tier-1 | Non-HFTD---10 | 3--2 | 4.0496 | 334 | 100% | 19.2146 | 44.26% | 40.89% | 14.85% | 0.42097 | 0 | 0 | 0.42097 | 0 | 0.40158 | 4.1836 | 0.095988 | 0.40158 | 4.1836 | 0.095988 | 0.42304 | 4.4072 | 0.095988 | 2.191% | 0.016682 | 0.015856 | 1151.8035 | 79.964 | 473.8867 | 597.9528 | 1185.238 | 0 | 0 | 1185.238 | 1.388e-05%
2026 | 279 | 279-11AE | Tier-1 | Non-HFTD---2 | 4--3 | 13.9777 | 317 | 100% | 201.506 | 3.082% | 92.11% | 4.808% | 0.30745 | 0 | 0 | 0.30745 | 0 | 0.29329 | 14.4402 | 0.02031 | 0.29329 | 14.4402 | 0.02031 | 0.30896 | 15.2118 | 0.02031 | 0.1526% | 0.055223 | 0.052489 | 3648.9772 | 5.6056 | 3185.2795 | 458.092 | 3833.1507 | 0 | 0 | 3833.1507 | 1.014e-05%
2026 | 162 | 162-19F | Tier-1 | Non-HFTD---12 | 4--2 | 10.1582 | 296 | 100% | 15.1555 | 52.93% | 0% | 47.07% | 0.39707 | 0 | 0 | 0.39707 | 0 | 0.37877 | 10.4943 | 0.036093 | 0.37877 | 10.4943 | 0.036093 | 0.39901 | 11.0551 | 0.036093 | 2.62% | 0.029254 | 0.027806 | 518.0585 | 22.6254 | 158.6224 | 336.8107 | 530.7581 | 0 | 0 | 530.7581 | 1.309e-05%
2026 | PL6 | CB PL6 | Tier-1 | Non-HFTD---12 | 4--1 | 10.6356 | 602 | 100% | 11.6399 | 35.44% | 0% | 64.56% | 0.20418 | 0 | 0 | 0.20418 | 0 | 0.19477 | 10.9876 | 0.017726 | 0.19477 | 10.9876 | 0.017726 | 0.20518 | 11.5746 | 0.017726 | 1.754% | 0.029655 | 0.028187 | 392.5082 | 0.9255 | 157.6202 | 233.9625 | 405.7056 | 0 | 0 | 405.7056 | 6.733e-06%
2026 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 4.8645 | 919 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 21.4326 | 5.0255 | 4.2647 | 21.4326 | 5.0255 | 4.2647 | 22.5778 | 5.2941 | 4.2647 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2026 | LJ4 | CB LJ4 | Tier-1 | Non-HFTD---16 | 2--1 | 2.5968 | 116 | 100% | 3.329 | 11.7% | 0% | 88.3% | 0.019278 | 0 | 0 | 0.019278 | 0 | 0.01839 | 2.6828 | 0.0068548 | 0.01839 | 2.6828 | 0.0068548 | 0.019372 | 2.8261 | 0.0068548 | 0.5791% | 0.0094594 | 0.0089912 | 351.9241 | 0.35466 | 68.6606 | 282.9088 | 368.1074 | 0 | 0 | 368.1074 | 6.357e-07%
2026 | 44 | 44-41 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2296 | 47 | 100% | 1.0965 | 21.81% | 0% | 78.19% | 0.011837 | 0 | 0 | 0.011837 | 0 | 0.011292 | 1.2703 | 0.0088893 | 0.011292 | 1.2703 | 0.0088893 | 0.011895 | 1.3381 | 0.0088893 | 1.079% | 0.0032776 | 0.0031154 | 334.5534 | 0.42375 | 95.3401 | 238.7896 | 348.1766 | 0 | 0 | 348.1766 | 3.903e-07%
2026 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 1.1027 | 145 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 34.7023 | 1.1392 | 30.4627 | 34.7023 | 1.1392 | 30.4627 | 36.5565 | 1.2 | 30.4627 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2026 | 59 | CB 59 | Tier-1 | Non-HFTD---5 | 2--4 | 0.80076 | 2 | 100% | 54.4254 | 99.08% | 0.2847% | 0.6369% | 2.6692 | 0 | 0 | 2.6692 | 0 | 2.5463 | 0.82726 | 3.078 | 2.5463 | 0.82726 | 3.078 | 2.6823 | 0.87146 | 3.078 | 4.904% | 0.0099342 | 0.0094425 | 5478.5927 | 848.4383 | 1089.8599 | 3540.2945 | 5481.2223 | 0 | 0 | 5481.2223 | 8.802e-05%
2026 | 131 | CB 131 | Tier-1 | Non-HFTD---15 | 2--2 | 1.6525 | 6 | 100% | 3.9586 | 65.37% | 0% | 34.63% | 0.1281 | 0 | 0 | 0.1281 | 0 | 0.12219 | 1.7072 | 0.071576 | 0.12219 | 1.7072 | 0.071576 | 0.12872 | 1.7984 | 0.071576 | 3.236% | 0.0054554 | 0.0051854 | 725.6284 | 55.3628 | 156.9776 | 513.288 | 738.7144 | 0 | 0 | 738.7144 | 4.224e-06%
2026 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 10.8114 | 954 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 83.2547 | 11.1692 | 7.454 | 83.2547 | 11.1692 | 7.454 | 87.7031 | 11.766 | 7.454 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2026 | 321 | 321-740AE | Tier-1 | Non-HFTD---14 | 3--1 | 5.658 | 154 | 100% | 5.6044 | 24.77% | 0% | 75.23% | 0.068724 | 0 | 0 | 0.068724 | 0 | 0.065558 | 5.8452 | 0.011216 | 0.065558 | 5.8452 | 0.011216 | 0.069061 | 6.1576 | 0.011216 | 1.226% | 0.016283 | 0.015477 | 344.189 | 0.80306 | 105.0413 | 238.3446 | 357.6731 | 0 | 0 | 357.6731 | 2.266e-06%
2026 | 780 | 780-468R | Tier-1 | Non-HFTD---4 | 3--4 | 1.3398 | 27 | 100% | 132.1756 | 2.152% | 97.23% | 0.6129% | 0.14083 | 0 | 0 | 0.14083 | 0 | 0.13434 | 1.3841 | 0.097058 | 0.13434 | 1.3841 | 0.097058 | 0.14152 | 1.4581 | 0.097058 | 0.1065% | 0.014295 | 0.013588 | 9246.1513 | 26.0626 | 8234.6389 | 985.4497 | 9717.3064 | 0 | 0 | 9717.3064 | 4.644e-06%
2026 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 2.6099 | 102 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 91.3622 | 2.6962 | 33.885 | 91.3622 | 2.6962 | 33.885 | 96.2438 | 2.8403 | 33.885 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2026 | 775 | 775-185 | Tier-1 | Non-HFTD---16 | 2--1 | 2.1559 | 84 | 100% | 2.4124 | 31.06% | 0% | 68.94% | 0.037091 | 0 | 0 | 0.037091 | 0 | 0.035382 | 2.2272 | 0.015886 | 0.035382 | 2.2272 | 0.015886 | 0.037273 | 2.3462 | 0.015886 | 1.538% | 0.0065622 | 0.0062374 | 367.6213 | 10.1886 | 93.1395 | 264.2932 | 380.8197 | 0 | 0 | 380.8197 | 1.223e-06%
2026 | 1406 | CB 1406 | Tier-1 | Non-HFTD---17 | 1--3 | 0.036742 | 0 | 100% | 0.71787 | 90.65% | 0% | 9.349% | 0.032213 | 0 | 0 | 0.032213 | 0 | 0.030729 | 0.037958 | 0.80953 | 0.030729 | 0.037958 | 0.80953 | 0.03237 | 0.039987 | 0.80953 | 4.487% | 0.0001864 | 0.00017717 | 3851.2388 | 0.27092 | 3523.903 | 327.0649 | 3869.9891 | 0 | 0 | 3869.9891 | 1.062e-06%
2026 | 458 | CB 458 | Tier-1 | Non-HFTD---20 | 1--1 | 0.51493 | 1 | 100% | 0.4923 | 10.29% | 0% | 89.71% | 0.0025064 | 0 | 0 | 0.0025064 | 0 | 0.0023909 | 0.53197 | 0.0044944 | 0.0023909 | 0.53197 | 0.0044944 | 0.0025187 | 0.56039 | 0.0044944 | 0.5091% | 0.0016434 | 0.0015621 | 299.5635 | 3.6595 | 33.8007 | 262.1032 | 313.5596 | 0 | 0 | 313.5596 | 8.265e-08%
2026 | 252 | 252-129 | Tier-2 | Tier-2---18 | 3--3 | 4.6668 | 14 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 2.1229 | 0 | 0 | 2.1229 | 0 | 2.0251 | 4.8213 | 0.42003 | 2.0251 | 4.8213 | 0.42003 | 2.1333 | 5.0789 | 0.42003 | 4.29% | 0.02391 | 0.022726 | 2069.6845 | 324.0484 | 134.0961 | 1611.54 | 2084.0584 | 0 | 0 | 2084.0584 | 7e-05%
2026 | 172 | 172-615R | Tier-1 | Non-HFTD---6 | 4--2 | 6.2257 | 251 | 100% | 65.0211 | 31.38% | 63.15% | 5.469% | 1.0101 | 0 | 0 | 1.0101 | 0 | 0.96353 | 6.4317 | 0.14981 | 0.96353 | 6.4317 | 0.14981 | 1.015 | 6.7754 | 0.14981 | 1.553% | 0.053579 | 0.050927 | 1213.547 | 17.4537 | 970.9978 | 225.0954 | 1256.9124 | 0 | 0 | 1256.9124 | 3.331e-05%
2026 | 45 | 45-16 | Tier-1 | Non-HFTD---11 | 2--2 | 2.7608 | 126 | 100% | 10.6609 | 86.29% | 0% | 13.71% | 0.45536 | 0 | 0 | 0.45536 | 0 | 0.43438 | 2.8521 | 0.1523 | 0.43438 | 2.8521 | 0.1523 | 0.45759 | 3.0045 | 0.1523 | 4.271% | 0.0075584 | 0.0071843 | 1410.4753 | 328.5278 | 122.7581 | 959.1895 | 1420.5468 | 0 | 0 | 1420.5468 | 1.502e-05%
2026 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 10.1081 | 575 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 33.1256 | 10.4426 | 3.1722 | 33.1256 | 10.4426 | 3.1722 | 34.8956 | 11.0006 | 3.1722 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2026 | 83 | CB 83 | Tier-1 | Non-HFTD---11 | 2--2 | 5.2235 | 109 | 100% | 14.2823 | 84.51% | 0% | 15.49% | 0.59746 | 0 | 0 | 0.59746 | 0 | 0.56994 | 5.3963 | 0.10562 | 0.56994 | 5.3963 | 0.10562 | 0.60039 | 5.6847 | 0.10562 | 4.183% | 0.012231 | 0.011626 | 1167.6768 | 4.647 | 975.6795 | 187.3504 | 1177.0966 | 0 | 0 | 1177.0966 | 1.97e-05%
2026 | HL3 | CB HL3 | Tier-1 | Non-HFTD---12 | 3--1 | 8.2549 | 102 | 100% | 9.4251 | 40.92% | 0% | 59.08% | 0.19092 | 0 | 0 | 0.19092 | 0 | 0.18212 | 8.5281 | 0.021356 | 0.18212 | 8.5281 | 0.021356 | 0.19186 | 8.9838 | 0.021356 | 2.026% | 0.021995 | 0.020907 | 428.5039 | 2.1065 | 186.5448 | 239.8526 | 441.6875 | 0 | 0 | 441.6875 | 6.296e-06%
2026 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 12.1512 | 539 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 175.0719 | 12.5533 | 13.9463 | 175.0719 | 12.5533 | 13.9463 | 184.4262 | 13.224 | 13.9463 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2026 | 197 | 197-1150F | Tier-2 | Tier-2---15 | 3--4 | 1.3604 | 2 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 9.0248 | 0 | 0 | 9.0248 | 0 | 8.609 | 1.4054 | 6.1255 | 8.609 | 1.4054 | 6.1255 | 9.069 | 1.4805 | 6.1255 | 4.917% | 0.021777 | 0.020699 | 8428.1597 | 1361.8326 | 10.8364 | 7055.4907 | 8431.076 | 0 | 0 | 8431.076 | 0.0002976%
2026 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 34.1718 | 1855 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1888.0784 | 35.3027 | 53.4826 | 1888.0784 | 35.3027 | 53.4826 | 1988.961 | 37.1889 | 53.4826 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2026 | 1173 | CB 1173 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1624 | 51 | 100% | 2.9682 | 59.25% | 0% | 40.75% | 0.087048 | 0 | 0 | 0.087048 | 0 | 0.083038 | 1.2008 | 0.069151 | 0.083038 | 1.2008 | 0.069151 | 0.087474 | 1.265 | 0.069151 | 2.933% | 0.0040836 | 0.0038815 | 726.8498 | 0.22289 | 457.5433 | 269.0836 | 742.276 | 0 | 0 | 742.276 | 2.871e-06%
2026 | 493 | CB 493 | Tier-1 | Non-HFTD---17 | 1--2 | 0.20795 | 11 | 100% | 1.0505 | 81.53% | 0% | 18.47% | 0.042395 | 0 | 0 | 0.042395 | 0 | 0.040442 | 0.21484 | 0.18824 | 0.040442 | 0.21484 | 0.18824 | 0.042602 | 0.22632 | 0.18824 | 4.036% | 0.0008612 | 0.00081857 | 1219.8489 | 9.8539 | 955.0049 | 254.9902 | 1231.585 | 0 | 0 | 1231.585 | 1.398e-06%
2026 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 4.8975 | 156 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 66.5395 | 5.0596 | 13.1512 | 66.5395 | 5.0596 | 13.1512 | 70.0948 | 5.3299 | 13.1512 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2026 | 153 | 153-1119R | Tier-1 | Non-HFTD---13 | 2--2 | 2.4303 | 39 | 100% | 8.0116 | 75.45% | 0% | 24.55% | 0.2992 | 0 | 0 | 0.2992 | 0 | 0.28541 | 2.5108 | 0.11368 | 0.28541 | 2.5108 | 0.11368 | 0.30066 | 2.6449 | 0.11368 | 3.735% | 0.0073252 | 0.0069626 | 1093.6986 | 0.20207 | 849.5472 | 243.9493 | 1107.6839 | 0 | 0 | 1107.6839 | 9.866e-06%
2026 | 323 | CB 323 | Tier-1 | Non-HFTD---11 | 1--4 | 0.54113 | 18 | 100% | 12.9162 | 95.89% | 0% | 4.106% | 0.6131 | 0 | 0 | 0.6131 | 0 | 0.58486 | 0.55903 | 1.0462 | 0.58486 | 0.55903 | 1.0462 | 0.61611 | 0.5889 | 1.0462 | 4.747% | 0.0019678 | 0.0018704 | 6563.758 | 128.289 | 5536.1599 | 899.3092 | 6577.7919 | 0 | 0 | 6577.7919 | 2.022e-05%
2026 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 3.3899 | 476 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 177.6968 | 3.5021 | 50.7401 | 177.6968 | 3.5021 | 50.7401 | 187.1914 | 3.6892 | 50.7401 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2026 | 146 | CB 146 | Tier-1 | Non-HFTD---15 | 2--2 | 0.18561 | 0 | 100% | 2.7748 | 92.6% | 1.913% | 5.483% | 0.12719 | 0 | 0 | 0.12719 | 0 | 0.12134 | 0.19175 | 0.63278 | 0.12134 | 0.19175 | 0.63278 | 0.12782 | 0.20199 | 0.63278 | 4.584% | 0.0054076 | 0.0051399 | 513.1328 | 60.6904 | 208.0736 | 244.3689 | 515.1093 | 0 | 0 | 515.1093 | 4.194e-06%
2026 | DR1 | CB DR1 | Tier-1 | Non-HFTD---10 | 3--2 | 5.4435 | 420 | 100% | 21.3264 | 25.84% | 59.63% | 14.53% | 0.27278 | 0 | 0 | 0.27278 | 0 | 0.26021 | 5.6237 | 0.046271 | 0.26021 | 5.6237 | 0.046271 | 0.27412 | 5.9242 | 0.046271 | 1.279% | 0.019541 | 0.018574 | 1091.3677 | 40.6433 | 651.42 | 399.3043 | 1133.5175 | 0 | 0 | 1133.5175 | 8.995e-06%
2026 | 414 | CB 414 | Tier-1 | Non-HFTD---2 | 4--3 | 16.8574 | 578 | 100% | 223.669 | 40.12% | 54.98% | 4.902% | 4.4417 | 0 | 0 | 4.4417 | 0 | 4.237 | 17.4153 | 0.24329 | 4.237 | 17.4153 | 0.24329 | 4.4634 | 18.3458 | 0.24329 | 1.986% | 0.060264 | 0.057281 | 3711.4858 | 297.0369 | 2040.8852 | 1373.5637 | 3827.2303 | 0 | 0 | 3827.2303 | 0.0001465%
2026 | 443 | 443-218R | Tier-1 | Non-HFTD---3 | 5--2 | 2.5293 | 0 | 100% | 96.9814 | 95.91% | 2.964% | 1.126% | 4.6043 | 0 | 0 | 4.6043 | 0 | 4.3922 | 2.613 | 1.6809 | 4.3922 | 2.613 | 1.6809 | 4.6268 | 2.7527 | 1.6809 | 4.748% | 0.096176 | 0.091415 | 1008.3738 | 175.6292 | 24.7239 | 808.0207 | 1010.5213 | 0 | 0 | 1010.5213 | 0.0001518%
2026 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 1.4734 | 170 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.4049 | 1.5222 | 2.2368 | 3.4049 | 1.5222 | 2.2368 | 3.5868 | 1.6035 | 2.2368 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2026 | 702 | 702-25 | Tier-1 | Non-HFTD---4 | 2--4 | 0.91362 | 18 | 100% | 105.79 | 16.96% | 82.58% | 0.4592% | 0.88821 | 0 | 0 | 0.88821 | 0 | 0.8473 | 0.94386 | 0.89769 | 0.8473 | 0.94386 | 0.89769 | 0.89257 | 0.99429 | 0.89769 | 0.8396% | 0.0085112 | 0.0080899 | 12429.5062 | 105.0973 | 10920.6101 | 1403.7989 | 12967.0151 | 0 | 0 | 12967.0151 | 2.929e-05%
2026 | TY1 | CB TY1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.27729 | 7 | 100% | 0.35043 | 36.25% | 0% | 63.75% | 0.0062889 | 0 | 0 | 0.0062889 | 0 | 0.0059992 | 0.28647 | 0.020942 | 0.0059992 | 0.28647 | 0.020942 | 0.0063197 | 0.30178 | 0.020942 | 1.795% | 0.0008392 | 0.00079766 | 417.5792 | 9.9722 | 115.9508 | 291.6562 | 431.4417 | 0 | 0 | 431.4417 | 2.074e-07%
2026 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 4.2257 | 174 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 87.8513 | 4.3656 | 20.1236 | 87.8513 | 4.3656 | 20.1236 | 92.5454 | 4.5988 | 20.1236 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2026 | 64 | CB 64 | Tier-1 | Non-HFTD---4 | 3--4 | 3.6049 | 136 | 100% | 105.4157 | 32.05% | 65.74% | 2.205% | 1.6724 | 0 | 0 | 1.6724 | 0 | 1.5954 | 3.7242 | 0.42837 | 1.5954 | 3.7242 | 0.42837 | 1.6806 | 3.9232 | 0.42837 | 1.586% | 0.017938 | 0.01705 | 5876.6069 | 242.5487 | 3978.8464 | 1655.2117 | 6084.5618 | 0 | 0 | 6084.5618 | 5.515e-05%
2026 | 278 | 278-22R | Tier-1 | Non-HFTD---2 | 4--3 | 15.5778 | 433 | 100% | 285.1665 | 5.51% | 90.91% | 3.576% | 0.77782 | 0 | 0 | 0.77782 | 0 | 0.74199 | 16.0934 | 0.046105 | 0.74199 | 16.0934 | 0.046105 | 0.78163 | 16.9533 | 0.046105 | 0.2728% | 0.058535 | 0.055637 | 4871.7604 | 23.1046 | 4253.0091 | 595.6468 | 5111.491 | 0 | 0 | 5111.491 | 2.565e-05%
2026 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 20.8132 | 1063 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 418.7535 | 21.502 | 19.4751 | 418.7535 | 21.502 | 19.4751 | 441.128 | 22.6509 | 19.4751 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2026 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 0.8655 | 53 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.014446 | 0.89415 | 0.016156 | 0.014446 | 0.89415 | 0.016156 | 0.015217 | 0.94192 | 0.016156 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2026 | 41 | 41-44AE | Tier-1 | Non-HFTD---15 | 2--2 | 2.7028 | 103 | 100% | 4.0717 | 49.31% | 0% | 50.69% | 0.099392 | 0 | 0 | 0.099392 | 0 | 0.094813 | 2.7923 | 0.033955 | 0.094813 | 2.7923 | 0.033955 | 0.099879 | 2.9415 | 0.033955 | 2.441% | 0.0078416 | 0.0074534 | 519.2383 | 3.8166 | 257.6774 | 257.7443 | 532.9441 | 0 | 0 | 532.9441 | 3.278e-06%
2026 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 6.4578 | 311 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 59.4254 | 6.6715 | 8.9074 | 59.4254 | 6.6715 | 8.9074 | 62.6005 | 7.028 | 8.9074 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2026 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 5.507 | 474 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 146.4383 | 5.6892 | 25.7396 | 146.4383 | 5.6892 | 25.7396 | 154.2627 | 5.9932 | 25.7396 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2026 | 598 | CB 598 | Tier-1 | Non-HFTD---9 | 1--4 | 0.66591 | 21 | 100% | 17.2197 | 95.45% | 0% | 4.551% | 0.81358 | 0 | 0 | 0.81358 | 0 | 0.7761 | 0.68795 | 1.1281 | 0.7761 | 0.68795 | 1.1281 | 0.81757 | 0.7247 | 1.1281 | 4.725% | 0.0027812 | 0.0026435 | 6191.4698 | 926.9749 | 243.7416 | 5020.7533 | 6206.1445 | 0 | 0 | 6206.1445 | 2.683e-05%
2026 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 18.1587 | 322 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 71.9999 | 18.7596 | 3.838 | 71.9999 | 18.7596 | 3.838 | 75.847 | 19.762 | 3.838 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2026 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 11.815 | 984 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 814.528 | 12.206 | 66.732 | 814.528 | 12.206 | 66.732 | 858.0494 | 12.8581 | 66.732 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2026 | 516 | CB 516 | Tier-1 | Non-HFTD---13 | 2--2 | 1.9939 | 56 | 100% | 4.9777 | 55.1% | 0% | 44.9% | 0.13576 | 0 | 0 | 0.13576 | 0 | 0.12951 | 2.0599 | 0.062869 | 0.12951 | 2.0599 | 0.062869 | 0.13643 | 2.17 | 0.062869 | 2.727% | 0.0070882 | 0.0067373 | 702.2584 | 0.23727 | 415.5749 | 286.4462 | 718.68 | 0 | 0 | 718.68 | 4.477e-06%
2026 | 205 | 205-1550 | Tier-2 | Tier-2---15 | 2--4 | 2.7852 | 227 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 6.0476 | 0 | 0 | 6.0476 | 0 | 5.769 | 2.8774 | 2.0049 | 5.769 | 2.8774 | 2.0049 | 6.0772 | 3.0311 | 2.0049 | 4.877% | 0.008789 | 0.0083539 | 14109.2738 | 2221.4405 | 309.7116 | 11578.1217 | 14120.1329 | 0 | 0 | 14120.1329 | 0.0001994%
2026 | HV1 | CB HV1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2047 | 174 | 100% | 1.373 | 42.97% | 0% | 57.03% | 0.029203 | 0 | 0 | 0.029203 | 0 | 0.027857 | 1.2446 | 0.022383 | 0.027857 | 1.2446 | 0.022383 | 0.029346 | 1.3111 | 0.022383 | 2.127% | 0.0035008 | 0.0033275 | 392.1896 | 29.8125 | 41.3066 | 321.0705 | 403.8379 | 0 | 0 | 403.8379 | 9.63e-07%
2026 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 1.8014 | 103 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.2899 | 1.861 | 1.2305 | 2.2899 | 1.861 | 1.2305 | 2.4122 | 1.9604 | 1.2305 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2026 | 361 | 361-45R | Tier-1 | Non-HFTD---5 | 3--4 | 2.965 | 64 | 100% | 74.9226 | 4.739% | 91.81% | 3.451% | 0.17574 | 0 | 0 | 0.17574 | 0 | 0.16764 | 3.0631 | 0.05473 | 0.16764 | 3.0631 | 0.05473 | 0.1766 | 3.2268 | 0.05473 | 0.2346% | 0.01487 | 0.014134 | 5038.4415 | 12.6045 | 4395.9502 | 629.8868 | 5288.3992 | 0 | 0 | 5288.3992 | 5.795e-06%
2026 | 368 | 368-1054F | Tier-1 | Non-HFTD---5 | 2--4 | 0.47745 | 4 | 100% | 80.991 | 0.1968% | 99.37% | 0.4288% | 0.0078897 | 0 | 0 | 0.0078897 | 0 | 0.0075262 | 0.49325 | 0.015258 | 0.0075262 | 0.49325 | 0.015258 | 0.0079284 | 0.5196 | 0.015258 | 0.009741% | 0.0067372 | 0.0064037 | 12021.4569 | 14.7322 | 10791.9159 | 1214.8087 | 12646.2765 | 0 | 0 | 12646.2765 | 2.602e-07%
2026 | LM3 | CB LM3 | Tier-1 | Non-HFTD---16 | 2--1 | 3.229 | 148 | 100% | 2.8437 | 17.95% | 0% | 82.05% | 0.025272 | 0 | 0 | 0.025272 | 0 | 0.024108 | 3.3359 | 0.0072268 | 0.024108 | 3.3359 | 0.0072268 | 0.025396 | 3.5141 | 0.0072268 | 0.8887% | 0.0089108 | 0.0084697 | 319.1341 | 1.177 | 75.099 | 242.8581 | 332.7702 | 0 | 0 | 332.7702 | 8.334e-07%
2026 | 308 | 308-464 | Tier-1 | Non-HFTD---3 | 4--3 | 3.726 | 137 | 100% | 187.2147 | 5.297% | 93.54% | 1.164% | 0.49085 | 0 | 0 | 0.49085 | 0 | 0.46824 | 3.8493 | 0.12164 | 0.46824 | 3.8493 | 0.12164 | 0.49326 | 4.0549 | 0.12164 | 0.2622% | 0.040091 | 0.038106 | 4669.7896 | 26.7777 | 4109.7012 | 533.3108 | 4900.101 | 0 | 0 | 4900.101 | 1.619e-05%
2026 | 155 | CB 155 | Tier-1 | Non-HFTD---7 | 2--3 | 4.6852 | 45 | 100% | 44.4963 | 94.43% | 0% | 5.571% | 2.0799 | 0 | 0 | 2.0799 | 0 | 1.984 | 4.8403 | 0.4099 | 1.984 | 4.8403 | 0.4099 | 2.0901 | 5.0989 | 0.4099 | 4.674% | 0.013451 | 0.012786 | 3307.9312 | 28.3316 | 2967.8681 | 311.7315 | 3317.529 | 0 | 0 | 3317.529 | 6.859e-05%
2026 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 4.3966 | 74 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 609.9489 | 4.5421 | 134.2887 | 609.9489 | 4.5421 | 134.2887 | 642.5393 | 4.7848 | 134.2887 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2026 | 244 | 244-32F | Tier-1 | Non-HFTD---6 | 3--3 | 0.80758 | 17 | 100% | 51.191 | 8.266% | 90.61% | 1.12% | 0.20945 | 0 | 0 | 0.20945 | 0 | 0.19981 | 0.8343 | 0.23949 | 0.19981 | 0.8343 | 0.23949 | 0.21048 | 0.87888 | 0.23949 | 0.4092% | 0.026609 | 0.025291 | 1923.8516 | 6.2615 | 1678.6755 | 238.9145 | 2015.76 | 0 | 0 | 2015.76 | 6.907e-06%
2026 | 730 | 730-1079 | Tier-1 | Non-HFTD---10 | 4--2 | 13.1661 | 615 | 100% | 24.9152 | 67.14% | 0% | 32.86% | 0.8281 | 0 | 0 | 0.8281 | 0 | 0.78995 | 13.6018 | 0.058077 | 0.78995 | 13.6018 | 0.058077 | 0.83216 | 14.3285 | 0.058077 | 3.324% | 0.039453 | 0.0375 | 631.5134 | 48.4936 | 242.245 | 340.7748 | 642.3187 | 0 | 0 | 642.3187 | 2.731e-05%
2026 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 5.8533 | 590 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 63.5637 | 6.047 | 10.5117 | 63.5637 | 6.047 | 10.5117 | 66.96 | 6.3701 | 10.5117 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2026 | 397 | CB 397 | Tier-1 | Non-HFTD---10 | 3--2 | 5.8458 | 263 | 100% | 18.3403 | 77.93% | 0% | 22.07% | 0.70752 | 0 | 0 | 0.70752 | 0 | 0.67493 | 6.0393 | 0.11176 | 0.67493 | 6.0393 | 0.11176 | 0.71099 | 6.362 | 0.11176 | 3.858% | 0.016356 | 0.015546 | 1121.3207 | 1.3088 | 889.4625 | 230.5495 | 1134.2064 | 0 | 0 | 1134.2064 | 2.333e-05%
2026 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 3.8686 | 160 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 174.1258 | 3.9966 | 43.5687 | 174.1258 | 3.9966 | 43.5687 | 183.4296 | 4.2101 | 43.5687 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2026 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 2.001 | 355 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 304.239 | 2.0672 | 147.1755 | 304.239 | 2.0672 | 147.1755 | 320.4949 | 2.1776 | 147.1755 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2026 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 7.3438 | 745 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 323.2915 | 7.5868 | 42.6123 | 323.2915 | 7.5868 | 42.6123 | 340.5654 | 7.9922 | 42.6123 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2026 | EN1 | CB EN1 | Tier-1 | Non-HFTD---6 | 4--3 | 9.5242 | 860 | 100% | 70.8621 | 16.44% | 73.67% | 9.888% | 0.57673 | 0 | 0 | 0.57673 | 0 | 0.55016 | 9.8394 | 0.055914 | 0.55016 | 9.8394 | 0.055914 | 0.57956 | 10.3652 | 0.055914 | 0.8139% | 0.03227 | 0.030673 | 2195.9128 | 34.015 | 1636.754 | 525.1438 | 2291.4685 | 0 | 0 | 2291.4685 | 1.902e-05%
2026 | 551 | CB 551 | Tier-1 | Non-HFTD---17 | 1--3 | 0.22538 | 1 | 100% | 2.2115 | 88.35% | 0% | 11.65% | 0.096715 | 0 | 0 | 0.096715 | 0 | 0.09226 | 0.23284 | 0.39623 | 0.09226 | 0.23284 | 0.39623 | 0.097189 | 0.24528 | 0.39623 | 4.373% | 0.000778 | 0.00073949 | 2842.6003 | 2.9889 | 2524.6412 | 314.9702 | 2859.8501 | 0 | 0 | 2859.8501 | 3.189e-06%
2026 | 196 | CB 196 | Tier-2 | Tier-2---15 | 3--4 | 0.59317 | 34 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.19951 | 0.6128 | 0.32557 | 0.19951 | 0.6128 | 0.32557 | 0.21017 | 0.64554 | 0.32557 | 0.1555% | 0.019464 | 0.018501 | 6908.5051 | 30.9312 | 5935.5679 | 942.006 | 7256.9805 | 0 | 0 | 7256.9805 | 6.897e-06%
2026 | CA1 | CB CA1 | Tier-1 | Non-HFTD---8 | 3--2 | 4.8453 | 343 | 100% | 26.9004 | 5.027% | 82.43% | 12.54% | 0.066943 | 0 | 0 | 0.066943 | 0 | 0.063859 | 5.0056 | 0.012757 | 0.063859 | 5.0056 | 0.012757 | 0.067271 | 5.2731 | 0.012757 | 0.2489% | 0.01864 | 0.017718 | 1443.1369 | 5.8286 | 1152.8354 | 284.4728 | 1514.514 | 0 | 0 | 1514.514 | 2.208e-06%
2026 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 3.7273 | 332 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 369.6702 | 3.8506 | 96.0033 | 369.6702 | 3.8506 | 96.0033 | 389.4222 | 4.0563 | 96.0033 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2026 | 1436 | CB 1436 | Tier-1 | Non-HFTD---13 | 1--3 | 0.38731 | 13 | 100% | 5.4228 | 92.93% | 0% | 7.074% | 0.24944 | 0 | 0 | 0.24944 | 0 | 0.23795 | 0.40013 | 0.59468 | 0.23795 | 0.40013 | 0.59468 | 0.25066 | 0.42151 | 0.59468 | 4.6% | 0.0017518 | 0.0016651 | 3095.5311 | 14.7451 | 2805.6585 | 275.1275 | 3106.9346 | 0 | 0 | 3106.9346 | 8.226e-06%
2026 | 153 | 153-581F | Tier-1 | Non-HFTD---12 | 3--1 | 7.8703 | 195 | 100% | 9.378 | 55.57% | 0% | 44.43% | 0.25798 | 0 | 0 | 0.25798 | 0 | 0.24609 | 8.1308 | 0.030267 | 0.24609 | 8.1308 | 0.030267 | 0.25924 | 8.5652 | 0.030267 | 2.751% | 0.019874 | 0.01889 | 471.8682 | 14.7491 | 216.5363 | 240.5828 | 482.7857 | 0 | 0 | 482.7857 | 8.507e-06%
2026 | 1297 | 1297-35F | Tier-1 | Non-HFTD---5 | 2--3 | 1.8046 | 25 | 100% | 50.4009 | 3.614% | 93.45% | 2.939% | 0.090151 | 0 | 0 | 0.090151 | 0 | 0.085998 | 1.8643 | 0.046129 | 0.085998 | 1.8643 | 0.046129 | 0.090593 | 1.9639 | 0.046129 | 0.1789% | 0.011686 | 0.011107 | 4313.0011 | 4.498 | 3844.9239 | 463.5793 | 4529.4966 | 0 | 0 | 4529.4966 | 2.973e-06%
2026 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 12.6964 | 992 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 518.2225 | 13.1166 | 39.5089 | 518.2225 | 13.1166 | 39.5089 | 545.9119 | 13.8174 | 39.5089 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2026 | 364 | CB 364 | Tier-1 | Non-HFTD---3 | 3--4 | 4.5699 | 87 | 100% | 99.5129 | 18.42% | 77.53% | 4.054% | 0.90733 | 0 | 0 | 0.90733 | 0 | 0.86553 | 4.7211 | 0.18333 | 0.86553 | 4.7211 | 0.18333 | 0.91178 | 4.9734 | 0.18333 | 0.9118% | 0.019381 | 0.018422 | 5134.505 | 5.0746 | 4604.1532 | 525.2772 | 5352.6459 | 0 | 0 | 5352.6459 | 2.992e-05%
2026 | 591 | CB 591 | Tier-1 | Non-HFTD---1 | 4--4 | 9.3315 | 487 | 100% | 1060.5472 | 90.24% | 9.188% | 0.5739% | 47.3724 | 0 | 0 | 47.3724 | 0 | 45.1901 | 9.6403 | 4.6876 | 45.1901 | 9.6403 | 4.6876 | 47.6046 | 10.1554 | 4.6876 | 4.467% | 0.066615 | 0.063317 | 15920.6417 | 3763.87 | 1847.5145 | 10309.2572 | 16001.5783 | 0 | 0 | 16001.5783 | 0.001562%
2026 | 320 | CB 320 | Tier-1 | Non-HFTD---13 | 1--3 | 0.72523 | 16 | 100% | 4.9303 | 88.31% | 0% | 11.69% | 0.21551 | 0 | 0 | 0.21551 | 0 | 0.20558 | 0.74923 | 0.2744 | 0.20558 | 0.74923 | 0.2744 | 0.21657 | 0.78926 | 0.2744 | 4.371% | 0.002136 | 0.0020303 | 2308.1856 | 59.5018 | 1700.6421 | 548.0417 | 2322.2409 | 0 | 0 | 2322.2409 | 7.107e-06%
2026 | 770 | CB 770 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3017 | 137 | 100% | 5.4599 | 68.13% | 0% | 31.87% | 0.18414 | 0 | 0 | 0.18414 | 0 | 0.17566 | 2.3779 | 0.073871 | 0.17566 | 2.3779 | 0.073871 | 0.18504 | 2.505 | 0.073871 | 3.373% | 0.008087 | 0.0076867 | 675.1471 | 60.111 | 111.1789 | 503.8571 | 686.3515 | 0 | 0 | 686.3515 | 6.072e-06%
2026 | 777 | 777-268F | Tier-1 | Non-HFTD---19 | 1--3 | 0.02803 | 0 | 100% | 0.57885 | 94.54% | 0% | 5.457% | 0.027089 | 0 | 0 | 0.027089 | 0 | 0.025841 | 0.028958 | 0.89237 | 0.025841 | 0.028958 | 0.89237 | 0.027222 | 0.030505 | 0.89237 | 4.68% | 0.0001222 | 0.00011615 | 4736.8697 | 723.3986 | 27.1305 | 3986.3407 | 4750.3318 | 0 | 0 | 4750.3318 | 8.933e-07%
2026 | 58 | 58-754F | Tier-1 | Non-HFTD---4 | 3--4 | 2.4574 | 37 | 100% | 111.5609 | 10.85% | 87.5% | 1.644% | 0.5994 | 0 | 0 | 0.5994 | 0 | 0.57179 | 2.5387 | 0.22522 | 0.57179 | 2.5387 | 0.22522 | 0.60234 | 2.6744 | 0.22522 | 0.5373% | 0.017828 | 0.016946 | 6257.4815 | 6.3235 | 5703.0525 | 548.1055 | 6547.9864 | 0 | 0 | 6547.9864 | 1.977e-05%
2026 | 781 | 781-43AE | Tier-1 | Non-HFTD---18 | 2--1 | 0.15072 | 4 | 100% | 1.2651 | 4.138% | 85.16% | 10.71% | 0.002591 | 0 | 0 | 0.002591 | 0 | 0.0024716 | 0.15571 | 0.015873 | 0.0024716 | 0.15571 | 0.015873 | 0.0026037 | 0.16403 | 0.015873 | 0.2048% | 0.011135 | 0.010584 | 113.6153 | 0.81972 | 89.1208 | 23.6748 | 119.2873 | 0 | 0 | 119.2873 | 8.544e-08%
2026 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 7.7195 | 976 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 180.2727 | 7.975 | 22.6048 | 180.2727 | 7.975 | 22.6048 | 189.905 | 8.4011 | 22.6048 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2026 | 482 | 482-382F | Tier-1 | Non-HFTD---15 | 2--2 | 2.7703 | 50 | 100% | 4.259 | 56.74% | 0% | 43.26% | 0.11962 | 0 | 0 | 0.11962 | 0 | 0.11411 | 2.8619 | 0.039871 | 0.11411 | 2.8619 | 0.039871 | 0.1202 | 3.0149 | 0.039871 | 2.809% | 0.0074466 | 0.007078 | 571.9423 | 0.18618 | 346.992 | 224.7641 | 584.8278 | 0 | 0 | 584.8278 | 3.945e-06%
2026 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | 2--4 | 1.7013 | 9 | 100% | 70.6534 | 98.66% | 0% | 1.337% | 3.4506 | 0 | 0 | 3.4506 | 0 | 3.2916 | 1.7576 | 1.8728 | 3.2916 | 1.7576 | 1.8728 | 3.4675 | 1.8515 | 1.8728 | 4.884% | 0.0070442 | 0.0066955 | 10030.0143 | 2447.2684 | 423.376 | 7159.37 | 10036.9961 | 0 | 0 | 10036.9961 | 0.0001138%
2026 | SK1 | CB SK1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.026705 | 0 | 100% | 0.041248 | 11.22% | 0% | 88.78% | 0.00022901 | 0 | 0 | 0.00022901 | 0 | 0.00021846 | 0.027588 | 0.0079185 | 0.00021846 | 0.027588 | 0.0079185 | 0.00023013 | 0.029062 | 0.0079185 | 0.5552% | 0.0001128 | 0.00010722 | 365.6737 | 6.7467 | 30.4931 | 328.4339 | 382.5813 | 0 | 0 | 382.5813 | 7.552e-09%
2026 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 20.7013 | 1682 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1330.4034 | 21.3864 | 62.208 | 1330.4034 | 21.3864 | 62.208 | 1401.4886 | 22.5291 | 62.208 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2026 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 7.4915 | 117 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 170.5666 | 7.7394 | 22.0387 | 170.5666 | 7.7394 | 22.0387 | 179.6802 | 8.1529 | 22.0387 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2026 | 140 | 140-496 | Tier-1 | Non-HFTD---5 | 3--4 | 2.3094 | 156 | 100% | 76.0759 | 10.21% | 86.85% | 2.935% | 0.38454 | 0 | 0 | 0.38454 | 0 | 0.36683 | 2.3858 | 0.15375 | 0.36683 | 2.3858 | 0.15375 | 0.38643 | 2.5133 | 0.15375 | 0.5055% | 0.01454 | 0.01382 | 5232.251 | 43.4645 | 4467.4961 | 721.2904 | 5476.9106 | 0 | 0 | 5476.9106 | 1.268e-05%
2026 | 462 | 462-1035F | Tier-1 | Non-HFTD---19 | 1--2 | 0.022159 | 4 | 100% | 0.24779 | 73.53% | 0% | 26.47% | 0.0090189 | 0 | 0 | 0.0090189 | 0 | 0.0086035 | 0.022892 | 0.37582 | 0.0086035 | 0.022892 | 0.37582 | 0.0090632 | 0.024116 | 0.37582 | 3.64% | 0.0001494 | 0.000142 | 1658.5735 | 0.33035 | 1259.4318 | 398.8113 | 1681.4368 | 0 | 0 | 1681.4368 | 2.974e-07%
2026 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 3.9252 | 376 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 190.7281 | 4.0551 | 47.034 | 190.7281 | 4.0551 | 47.034 | 200.9189 | 4.2718 | 47.034 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2026 | 911 | CB 911 | Tier-2 | Tier-2---14 | 1--5 | 0.9375 | 47 | 100% | 193.6033 | 99.75% | 0% | 0.253% | 9.5591 | 0 | 0 | 9.5591 | 0 | 9.1187 | 0.96852 | 9.4151 | 9.1187 | 0.96852 | 9.4151 | 9.606 | 1.0203 | 9.4151 | 4.937% | 0.0040632 | 0.0038621 | 47647.9856 | 7461.2719 | 1706.7058 | 38480.0078 | 47654.2641 | 0 | 0 | 47654.2641 | 0.0003152%
2026 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 2.7653 | 360 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 133.2483 | 2.8569 | 46.6416 | 133.2483 | 2.8569 | 46.6416 | 140.368 | 3.0095 | 46.6416 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2026 | 516 | 516-7F | Tier-1 | Non-HFTD---19 | 1--1 | 0.27315 | 23 | 100% | 0.35341 | 11.58% | 0% | 88.42% | 0.0020258 | 0 | 0 | 0.0020258 | 0 | 0.0019324 | 0.28219 | 0.006848 | 0.0019324 | 0.28219 | 0.006848 | 0.0020357 | 0.29727 | 0.006848 | 0.5732% | 0.0009896 | 0.00094061 | 357.1201 | 0.2376 | 70.0389 | 286.8436 | 373.5645 | 0 | 0 | 373.5645 | 6.68e-08%
2026 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 7.6936 | 531 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 94.9689 | 7.9482 | 11.9485 | 94.9689 | 7.9482 | 11.9485 | 100.0432 | 8.3729 | 11.9485 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2026 | 330 | 330-8R | Tier-1 | Non-HFTD---2 | 4--4 | 9.8311 | 664 | 100% | 217.2506 | 11.57% | 85.07% | 3.362% | 1.2444 | 0 | 0 | 1.2444 | 0 | 1.1871 | 10.1564 | 0.11688 | 1.1871 | 10.1564 | 0.11688 | 1.2505 | 10.6991 | 0.11688 | 0.5728% | 0.044939 | 0.042715 | 4834.3005 | 5.4086 | 4300.9723 | 527.9196 | 5056.9268 | 0 | 0 | 5056.9268 | 4.104e-05%
2026 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 14.6036 | 803 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 61.1985 | 15.0869 | 4.0564 | 61.1985 | 15.0869 | 4.0564 | 64.4684 | 15.893 | 4.0564 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2026 | 329 | 329-793F | Tier-1 | Non-HFTD---14 | 3--1 | 0.54544 | 10 | 100% | 8.6222 | 27.32% | 66.37% | 6.318% | 0.11658 | 0 | 0 | 0.11658 | 0 | 0.11121 | 0.56349 | 0.19736 | 0.11121 | 0.56349 | 0.19736 | 0.11716 | 0.5936 | 0.19736 | 1.352% | 0.019245 | 0.018293 | 448.0142 | 14.326 | 282.864 | 150.8242 | 464.9726 | 0 | 0 | 464.9726 | 3.845e-06%
2026 | 90 | 90-49 | Tier-1 | Non-HFTD---11 | 2--3 | 0.38809 | 7 | 100% | 11.9536 | 0.3922% | 96.08% | 3.526% | 0.0023207 | 0 | 0 | 0.0023207 | 0 | 0.0022138 | 0.40093 | 0.0055216 | 0.0022138 | 0.40093 | 0.0055216 | 0.0023321 | 0.42236 | 0.0055216 | 0.01941% | 0.0065452 | 0.0062212 | 1826.3158 | 2.1347 | 1619.3491 | 204.832 | 1921.0534 | 0 | 0 | 1921.0534 | 7.653e-08%
2026 | 702 | 702-448F | Tier-1 | Non-HFTD---19 | 1--3 | 0.029545 | 0 | 100% | 0.36733 | 90.03% | 0% | 9.967% | 0.016371 | 0 | 0 | 0.016371 | 0 | 0.015617 | 0.030523 | 0.51163 | 0.015617 | 0.030523 | 0.51163 | 0.016451 | 0.032154 | 0.51163 | 4.457% | 0.0001214 | 0.00011539 | 3025.8156 | 1.795 | 2741.9742 | 282.0463 | 3041.5218 | 0 | 0 | 3041.5218 | 5.398e-07%
2026 | 151 | CB 151 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8715 | 54 | 100% | 3.6088 | 37.51% | 0% | 62.49% | 0.067008 | 0 | 0 | 0.067008 | 0 | 0.063921 | 2.9666 | 0.021547 | 0.063921 | 2.9666 | 0.021547 | 0.067336 | 3.1251 | 0.021547 | 1.857% | 0.0086214 | 0.0081946 | 418.5864 | 20.5993 | 55.0518 | 342.9354 | 432.2085 | 0 | 0 | 432.2085 | 2.21e-06%
2026 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 1.1019 | 43 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 25.691 | 1.1384 | 22.5684 | 25.691 | 1.1384 | 22.5684 | 27.0637 | 1.1992 | 22.5684 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2026 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.11723 | 0 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 15.7754 | 0.12111 | 130.2523 | 15.7754 | 0.12111 | 130.2523 | 16.6183 | 0.12759 | 130.2523 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2026 | 136 | CB 136 | Tier-1 | Non-HFTD---11 | 2--2 | 3.5625 | 63 | 100% | 14.7465 | 75.99% | 0% | 24.01% | 0.55467 | 0 | 0 | 0.55467 | 0 | 0.52912 | 3.6804 | 0.14377 | 0.52912 | 3.6804 | 0.14377 | 0.55739 | 3.8771 | 0.14377 | 3.761% | 0.012814 | 0.012179 | 1150.8466 | 68.1179 | 481.9548 | 600.7739 | 1165.2384 | 0 | 0 | 1165.2384 | 1.829e-05%
2026 | AG1 | CB AG1 | Tier-1 | Non-HFTD---6 | 3--3 | 2.6702 | 142 | 100% | 54.2692 | 2.264% | 94.2% | 3.533% | 0.060827 | 0 | 0 | 0.060827 | 0 | 0.058025 | 2.7586 | 0.021034 | 0.058025 | 2.7586 | 0.021034 | 0.061125 | 2.906 | 0.021034 | 0.1121% | 0.01771 | 0.016834 | 3064.2572 | 3.3404 | 2723.0059 | 337.911 | 3220.2238 | 0 | 0 | 3220.2238 | 2.006e-06%
2026 | 58 | 58-110F | Tier-1 | Non-HFTD---3 | 4--3 | 6.2108 | 237 | 100% | 93.5151 | 11.61% | 83.8% | 4.592% | 0.53721 | 0 | 0 | 0.53721 | 0 | 0.51247 | 6.4163 | 0.079869 | 0.51247 | 6.4163 | 0.079869 | 0.53985 | 6.7592 | 0.079869 | 0.5745% | 0.033104 | 0.031465 | 2824.9053 | 53.6585 | 2259.5047 | 511.7421 | 2954.947 | 0 | 0 | 2954.947 | 1.772e-05%
2026 | 53 | CB 53 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2979 | 50 | 100% | 0.88951 | 10.17% | 0% | 89.83% | 0.0044771 | 0 | 0 | 0.0044771 | 0 | 0.0042709 | 1.3409 | 0.0031852 | 0.0042709 | 1.3409 | 0.0031852 | 0.0044991 | 1.4125 | 0.0031852 | 0.5033% | 0.0032354 | 0.0030752 | 274.9306 | 0.18584 | 50.3908 | 224.354 | 287.7926 | 0 | 0 | 287.7926 | 1.476e-07%
2026 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | 2--3 | 2.0286 | 23 | 100% | 14.0801 | 87.11% | 0% | 12.89% | 0.60712 | 0 | 0 | 0.60712 | 0 | 0.57915 | 2.0957 | 0.27635 | 0.57915 | 2.0957 | 0.27635 | 0.6101 | 2.2077 | 0.27635 | 4.312% | 0.0077936 | 0.0074078 | 1806.6243 | 178.7989 | 575.1368 | 1052.6887 | 1818.7529 | 0 | 0 | 1818.7529 | 2.002e-05%
2026 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 12.622 | 987 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1102.1556 | 13.0397 | 84.5231 | 1102.1556 | 13.0397 | 84.5231 | 1161.0453 | 13.7364 | 84.5231 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2026 | 242 | 242-1413F | Tier-1 | Non-HFTD---2 | 5--3 | 1.8794 | 86 | 100% | 367.3537 | 8.271% | 91.36% | 0.3661% | 1.5041 | 0 | 0 | 1.5041 | 0 | 1.4348 | 1.9415 | 0.73899 | 1.4348 | 1.9415 | 0.73899 | 1.5114 | 2.0453 | 0.73899 | 0.4094% | 0.10056 | 0.095586 | 3652.9198 | 53.8188 | 2967.9065 | 631.1945 | 3827.4209 | 0 | 0 | 3827.4209 | 4.96e-05%
2026 | 186 | CB 186 | Tier-1 | Non-HFTD---5 | 3--4 | 4.111 | 213 | 100% | 92.3894 | 96.63% | 0% | 3.367% | 4.4193 | 0 | 0 | 4.4193 | 0 | 4.2157 | 4.2471 | 0.99262 | 4.2157 | 4.2471 | 0.99262 | 4.441 | 4.474 | 0.99262 | 4.783% | 0.015082 | 0.014336 | 6125.6456 | 905.7849 | 2088.3006 | 3131.5601 | 6136.3851 | 0 | 0 | 6136.3851 | 0.0001457%
2026 | 570 | 570-491F | Tier-1 | Non-HFTD---20 | 1--1 | 0.70831 | 56 | 100% | 0.50055 | 7.694% | 0% | 92.31% | 0.0019065 | 0 | 0 | 0.0019065 | 0 | 0.0018187 | 0.73175 | 0.0024854 | 0.0018187 | 0.73175 | 0.0024854 | 0.0019158 | 0.77085 | 0.0024854 | 0.3809% | 0.001908 | 0.0018136 | 262.3439 | 0.27517 | 41.617 | 220.4517 | 274.9549 | 0 | 0 | 274.9549 | 6.287e-08%
2026 | 546 | CB 546 | Tier-1 | Non-HFTD---1 | 4--4 | 7.344 | 174 | 100% | 334.1605 | 5.89% | 92.51% | 1.604% | 0.97427 | 0 | 0 | 0.97427 | 0 | 0.92939 | 7.587 | 0.1225 | 0.92939 | 7.587 | 0.1225 | 0.97905 | 7.9924 | 0.1225 | 0.2916% | 0.030456 | 0.028948 | 10971.9113 | 11.4011 | 9971.8641 | 988.6462 | 11509.6495 | 0 | 0 | 11509.6495 | 3.213e-05%
2026 | EOS1 | CB EOS1 | Tier-1 | Non-HFTD---6 | 4--2 | 17.8417 | 865 | 100% | 70.9236 | 82.85% | 0% | 17.15% | 2.9086 | 0 | 0 | 2.9086 | 0 | 2.7746 | 18.4321 | 0.15053 | 2.7746 | 18.4321 | 0.15053 | 2.9228 | 19.4169 | 0.15053 | 4.101% | 0.050825 | 0.048309 | 1395.4534 | 210.0698 | 229.3399 | 956.0438 | 1407.9183 | 0 | 0 | 1407.9183 | 9.591e-05%
2026 | 515 | 515-49R | Tier-1 | Non-HFTD---17 | 1--2 | 0.3564 | 2 | 100% | 0.93866 | 50.3% | 0% | 49.7% | 0.023373 | 0 | 0 | 0.023373 | 0 | 0.022296 | 0.3682 | 0.060555 | 0.022296 | 0.3682 | 0.060555 | 0.023488 | 0.38787 | 0.060555 | 2.49% | 0.0014364 | 0.0013653 | 653.4775 | 1.8578 | 348.3582 | 303.2615 | 670.3899 | 0 | 0 | 670.3899 | 7.708e-07%
2026 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 6.3703 | 516 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 676.0489 | 6.5811 | 102.7255 | 676.0489 | 6.5811 | 102.7255 | 712.1711 | 6.9328 | 102.7255 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2026 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | 5--4 | 1.3333 | 233 | 100% | 1005.6854 | 94.09% | 5.81% | 0.1042% | 46.8371 | 0 | 0 | 46.8371 | 0 | 44.6794 | 1.3775 | 32.4361 | 44.6794 | 1.3775 | 32.4361 | 47.0667 | 1.4511 | 32.4361 | 4.657% | 0.097832 | 0.09299 | 10279.6968 | 1573.4563 | 574.8933 | 8131.3471 | 10311.3601 | 0 | 0 | 10311.3601 | 0.001545%
2026 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 20.3065 | 1258 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 185.1522 | 20.9785 | 8.8258 | 185.1522 | 20.9785 | 8.8258 | 195.0451 | 22.0994 | 8.8258 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2026 | 76 | 76-272 | Tier-1 | Non-HFTD---15 | 1--2 | 1.5693 | 60 | 100% | 2.4692 | 55.93% | 0% | 44.07% | 0.068363 | 0 | 0 | 0.068363 | 0 | 0.065214 | 1.6212 | 0.040226 | 0.065214 | 1.6212 | 0.040226 | 0.068698 | 1.7078 | 0.040226 | 2.769% | 0.0043474 | 0.0041322 | 567.9648 | 0.63038 | 337.7103 | 229.6241 | 580.9991 | 0 | 0 | 580.9991 | 2.254e-06%
2026 | 65 | CB 65 | Tier-1 | Non-HFTD---2 | 3--4 | 6.2999 | 644 | 100% | 189.2656 | 62.06% | 35.57% | 2.376% | 5.814 | 0 | 0 | 5.814 | 0 | 5.5462 | 6.5083 | 0.85216 | 5.5462 | 6.5083 | 0.85216 | 5.8425 | 6.8561 | 0.85216 | 3.072% | 0.027671 | 0.026302 | 6839.7543 | 634.4467 | 2950.5287 | 3254.7788 | 6974.9036 | 0 | 0 | 6974.9036 | 0.0001917%
2026 | 374 | CB 374 | Tier-1 | Non-HFTD---8 | 4--2 | 13.2841 | 373 | 100% | 28.091 | 64.57% | 0% | 35.43% | 0.89782 | 0 | 0 | 0.89782 | 0 | 0.85646 | 13.7237 | 0.062407 | 0.85646 | 13.7237 | 0.062407 | 0.90222 | 14.457 | 0.062407 | 3.196% | 0.037158 | 0.035318 | 755.9952 | 0.21604 | 512.3714 | 243.4078 | 769.9451 | 0 | 0 | 769.9451 | 2.961e-05%
2026 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 2.6388 | 132 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 8.2042 | 2.7261 | 3.0095 | 8.2042 | 2.7261 | 3.0095 | 8.6426 | 2.8718 | 3.0095 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2026 | 703 | 703-279R | Tier-1 | Non-HFTD---2 | 4--4 | 8.8328 | 321 | 100% | 201.9742 | 33.23% | 63.5% | 3.273% | 3.3219 | 0 | 0 | 3.3219 | 0 | 3.1689 | 9.1251 | 0.34727 | 3.1689 | 9.1251 | 0.34727 | 3.3382 | 9.6126 | 0.34727 | 1.645% | 0.030988 | 0.029454 | 6517.9035 | 105.9052 | 5595.0681 | 816.9302 | 6744.5585 | 0 | 0 | 6744.5585 | 0.0001095%
2026 | 274 | CB 274 | Tier-1 | Non-HFTD---4 | 3--4 | 0.089394 | 2 | 100% | 104.8089 | 0.2793% | 99.62% | 0.1033% | 0.014491 | 0 | 0 | 0.014491 | 0 | 0.013823 | 0.092352 | 0.14968 | 0.013823 | 0.092352 | 0.14968 | 0.014562 | 0.097287 | 0.14968 | 0.01383% | 0.014981 | 0.014239 | 6996.2133 | 9.5886 | 6367.3875 | 619.2371 | 7359.5434 | 0 | 0 | 7359.5434 | 4.779e-07%
2026 | 51 | 51-861R | Tier-1 | Non-HFTD---16 | 2--1 | 3.5 | 123 | 100% | 2.9058 | 18.9% | 0% | 81.1% | 0.027191 | 0 | 0 | 0.027191 | 0 | 0.025939 | 3.6158 | 0.0071736 | 0.025939 | 3.6158 | 0.0071736 | 0.027325 | 3.809 | 0.0071736 | 0.9358% | 0.0093474 | 0.0088847 | 310.8674 | 0.1897 | 81.668 | 229.0098 | 323.9963 | 0 | 0 | 323.9963 | 8.967e-07%
2026 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 23.0074 | 900 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 79.3622 | 23.7688 | 3.3389 | 79.3622 | 23.7688 | 3.3389 | 83.6027 | 25.0388 | 3.3389 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2026 | 454 | CB 454 | Tier-1 | Non-HFTD---11 | 3--2 | 5.108 | 105 | 100% | 14.4703 | 77.76% | 0% | 22.24% | 0.557 | 0 | 0 | 0.557 | 0 | 0.53134 | 5.277 | 0.10069 | 0.53134 | 5.277 | 0.10069 | 0.55973 | 5.559 | 0.10069 | 3.849% | 0.014027 | 0.013332 | 1031.6351 | 0.20077 | 822.8982 | 208.5361 | 1043.582 | 0 | 0 | 1043.582 | 1.837e-05%
2026 | 761 | CB 761 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3415 | 77 | 100% | 36.3819 | 95.87% | 0% | 4.131% | 1.7265 | 0 | 0 | 1.7265 | 0 | 1.647 | 2.419 | 0.68086 | 1.647 | 2.419 | 0.68086 | 1.735 | 2.5482 | 0.68086 | 4.746% | 0.0090226 | 0.008576 | 4032.309 | 532.6165 | 590.1313 | 2909.5613 | 4040.9834 | 0 | 0 | 4040.9834 | 5.693e-05%
2026 | 209 | 209-660R | Tier-1 | Non-HFTD---13 | 1--3 | 0.73613 | 58 | 100% | 6.8017 | 90.67% | 0% | 9.327% | 0.30528 | 0 | 0 | 0.30528 | 0 | 0.29122 | 0.76049 | 0.38294 | 0.29122 | 0.76049 | 0.38294 | 0.30678 | 0.80112 | 0.38294 | 4.488% | 0.0025076 | 0.0023835 | 2712.4478 | 81.1565 | 1987.9733 | 643.318 | 2725.6234 | 0 | 0 | 2725.6234 | 1.007e-05%
2026 | 400 | 400-1019 | Tier-1 | Non-HFTD---12 | 4--1 | 14.5055 | 252 | 100% | 13.8376 | 46.13% | 0% | 53.87% | 0.31594 | 0 | 0 | 0.31594 | 0 | 0.30138 | 14.9855 | 0.020112 | 0.30138 | 14.9855 | 0.020112 | 0.31749 | 15.7862 | 0.020112 | 2.283% | 0.036477 | 0.034671 | 379.3524 | 0.8422 | 189.3108 | 189.1995 | 389.9959 | 0 | 0 | 389.9959 | 1.042e-05%
2026 | 545 | 545-50F | Tier-1 | Non-HFTD---4 | 3--4 | 3.0186 | 22 | 100% | 135.8264 | 1.065% | 96.96% | 1.972% | 0.071585 | 0 | 0 | 0.071585 | 0 | 0.068288 | 3.1185 | 0.021898 | 0.068288 | 3.1185 | 0.021898 | 0.071936 | 3.2851 | 0.021898 | 0.0527% | 0.019507 | 0.018541 | 6963.0284 | 7.5673 | 6209.716 | 745.7451 | 7321.7871 | 0 | 0 | 7321.7871 | 2.361e-06%
2026 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 17.8147 | 1731 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 405.8445 | 18.4043 | 22.0516 | 405.8445 | 18.4043 | 22.0516 | 427.5294 | 19.3876 | 22.0516 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2026 | GN1 | CB GN1 | Tier-1 | Non-HFTD---6 | 3--3 | 4.8692 | 151 | 100% | 90.3459 | 4.418% | 91.44% | 4.142% | 0.1976 | 0 | 0 | 0.1976 | 0 | 0.1885 | 5.0303 | 0.037472 | 0.1885 | 5.0303 | 0.037472 | 0.19857 | 5.2991 | 0.037472 | 0.2187% | 0.024571 | 0.023355 | 3676.9336 | 12.2101 | 3193.0279 | 471.6956 | 3859.9596 | 0 | 0 | 3859.9596 | 6.516e-06%
2026 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 1.6021 | 38 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 28.5516 | 1.6551 | 17.2507 | 28.5516 | 1.6551 | 17.2507 | 30.0772 | 1.7435 | 17.2507 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2026 | 511 | CB 511 | Tier-1 | Non-HFTD---4 | 3--4 | 2.4116 | 87 | 100% | 163.9412 | 95.95% | 3.193% | 0.8556% | 7.7866 | 0 | 0 | 7.7866 | 0 | 7.4279 | 2.4914 | 2.9814 | 7.4279 | 2.4914 | 2.9814 | 7.8247 | 2.6245 | 2.9814 | 4.75% | 0.019336 | 0.018379 | 8478.4598 | 1002.8854 | 2208.1517 | 5267.4227 | 8496.3346 | 0 | 0 | 8496.3346 | 0.0002568%
2026 | 403 | 403-15F | Tier-1 | Non-HFTD---17 | 1--2 | 0.21288 | 44 | 100% | 1.6081 | 91.84% | 0% | 8.156% | 0.073108 | 0 | 0 | 0.073108 | 0 | 0.06974 | 0.21992 | 0.31711 | 0.06974 | 0.21992 | 0.31711 | 0.073466 | 0.23167 | 0.31711 | 4.546% | 0.001071 | 0.001018 | 1501.4701 | 224.8932 | 11.1242 | 1265.4527 | 1507.8474 | 0 | 0 | 1507.8474 | 2.411e-06%
2026 | 155 | 155-1236R | Tier-1 | Non-HFTD---8 | 2--3 | 4.1822 | 117 | 100% | 27.9773 | 89.48% | 0% | 10.52% | 1.2392 | 0 | 0 | 1.2392 | 0 | 1.1821 | 4.3206 | 0.27359 | 1.1821 | 4.3206 | 0.27359 | 1.2452 | 4.5515 | 0.27359 | 4.429% | 0.01302 | 0.012376 | 2148.7604 | 291.0687 | 669.5809 | 1188.1108 | 2160.534 | 0 | 0 | 2160.534 | 4.086e-05%
2026 | 52 | 52-16F | Tier-1 | Non-HFTD---19 | 1--1 | 0.61587 | 22 | 100% | 0.6475 | 11.64% | 0% | 88.36% | 0.0037321 | 0 | 0 | 0.0037321 | 0 | 0.0035602 | 0.63625 | 0.0055955 | 0.0035602 | 0.63625 | 0.0055955 | 0.0037504 | 0.67025 | 0.0055955 | 0.5764% | 0.001922 | 0.0018269 | 336.889 | 0.24654 | 66.1207 | 270.5218 | 352.3906 | 0 | 0 | 352.3906 | 1.231e-07%
2026 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 5.4023 | 497 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 50.8518 | 5.581 | 9.1115 | 50.8518 | 5.581 | 9.1115 | 53.5689 | 5.8792 | 9.1115 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2026 | 857 | 857-60 | Tier-1 | Non-HFTD---11 | 1--4 | 0.99317 | 41 | 100% | 13.5992 | 95.18% | 0% | 4.819% | 0.64072 | 0 | 0 | 0.64072 | 0 | 0.6112 | 1.026 | 0.59569 | 0.6112 | 1.026 | 0.59569 | 0.64386 | 1.0809 | 0.59569 | 4.711% | 0.0028286 | 0.0026886 | 4807.7559 | 729.0888 | 145.8859 | 3932.7813 | 4819.8226 | 0 | 0 | 4819.8226 | 2.113e-05%
2026 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 17.4555 | 1680 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 847.0626 | 18.0332 | 46.9725 | 847.0626 | 18.0332 | 46.9725 | 892.3223 | 18.9967 | 46.9725 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2026 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 3.42 | 209 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 29.9106 | 3.5332 | 8.4656 | 29.9106 | 3.5332 | 8.4656 | 31.5088 | 3.722 | 8.4656 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2026 | 553 | CB 553 | Tier-1 | Non-HFTD---5 | 2--3 | 3.1561 | 136 | 100% | 49.0638 | 94.65% | 0% | 5.347% | 2.2988 | 0 | 0 | 2.2988 | 0 | 2.1929 | 3.2605 | 0.67256 | 2.1929 | 3.2605 | 0.67256 | 2.3101 | 3.4347 | 0.67256 | 4.685% | 0.011308 | 0.010749 | 4338.7071 | 494.3233 | 1109.1201 | 2735.2637 | 4350.7882 | 0 | 0 | 4350.7882 | 7.581e-05%
2026 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 11.9254 | 907 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 262.6012 | 12.32 | 21.315 | 262.6012 | 12.32 | 21.315 | 276.6324 | 12.9783 | 21.315 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2026 | 1047 | 1047-35F | Tier-1 | Non-HFTD---15 | 1--2 | 1.687 | 51 | 100% | 2.3448 | 49.08% | 0% | 50.92% | 0.056963 | 0 | 0 | 0.056963 | 0 | 0.054339 | 1.7428 | 0.031179 | 0.054339 | 1.7428 | 0.031179 | 0.057242 | 1.8359 | 0.031179 | 2.429% | 0.004654 | 0.0044236 | 503.8208 | 0.79361 | 266.8776 | 236.1496 | 517.1817 | 0 | 0 | 517.1817 | 1.878e-06%
2026 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 12.6807 | 909 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 163.4677 | 13.1004 | 12.4781 | 163.4677 | 13.1004 | 12.4781 | 172.202 | 13.8003 | 12.4781 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2026 | 450 | 450-50R | Tier-2 | Tier-2---11 | 4--4 | 0.51918 | 36 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 8.6479 | 0 | 0 | 8.6479 | 0 | 8.2495 | 0.53636 | 15.3806 | 8.2495 | 0.53636 | 15.3806 | 8.6903 | 0.56502 | 15.3806 | 1.61% | 0.071801 | 0.068247 | 7480.0024 | 403.5755 | 4618.5943 | 2457.8325 | 7742.8291 | 0 | 0 | 7742.8291 | 0.0002852%
2026 | 85 | 85-498F | Tier-1 | Non-HFTD---13 | 1--3 | 0.76871 | 66 | 100% | 5.1045 | 87.99% | 0% | 12.01% | 0.22234 | 0 | 0 | 0.22234 | 0 | 0.2121 | 0.79415 | 0.26707 | 0.2121 | 0.79415 | 0.26707 | 0.22343 | 0.83658 | 0.26707 | 4.356% | 0.002808 | 0.002669 | 1817.8549 | 381.7426 | 31.0024 | 1405.1099 | 1829.2212 | 0 | 0 | 1829.2212 | 7.332e-06%
2026 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.075568 | 0 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 9.0555 | 0.078069 | 115.9939 | 9.0555 | 0.078069 | 115.9939 | 9.5394 | 0.08224 | 115.9939 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2026 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 2.1594 | 50 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 25.1077 | 2.2309 | 11.2545 | 25.1077 | 2.2309 | 11.2545 | 26.4492 | 2.3501 | 11.2545 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2026 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 10.6674 | 427 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 936.1138 | 11.0204 | 84.9436 | 936.1138 | 11.0204 | 84.9436 | 986.1317 | 11.6093 | 84.9436 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2026 | RD1 | CB RD1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.1822 | 221 | 100% | 3.8065 | 31.86% | 0% | 68.14% | 0.060024 | 0 | 0 | 0.060024 | 0 | 0.057259 | 3.2876 | 0.017417 | 0.057259 | 3.2876 | 0.017417 | 0.060318 | 3.4632 | 0.017417 | 1.577% | 0.009563 | 0.0090896 | 398.0431 | 3.9878 | 128.2654 | 265.7899 | 412.1688 | 0 | 0 | 412.1688 | 1.979e-06%
2026 | 64 | 64-14F | Tier-1 | Non-HFTD---3 | 4--3 | 8.9328 | 168 | 100% | 111.7051 | 4.553% | 91.33% | 4.117% | 0.25173 | 0 | 0 | 0.25173 | 0 | 0.24013 | 9.2284 | 0.026021 | 0.24013 | 9.2284 | 0.026021 | 0.25297 | 9.7215 | 0.026021 | 0.2254% | 0.030765 | 0.029242 | 3630.8929 | 16.1011 | 3147.9882 | 466.8035 | 3811.3735 | 0 | 0 | 3811.3735 | 8.301e-06%
2026 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 3.4333 | 108 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 17.2331 | 3.5469 | 4.8586 | 17.2331 | 3.5469 | 4.8586 | 18.1539 | 3.7364 | 4.8586 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2026 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 24.3072 | 930 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 785.4976 | 25.1116 | 31.2803 | 785.4976 | 25.1116 | 31.2803 | 827.4678 | 26.4533 | 31.2803 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2026 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 11.8164 | 264 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 55.7504 | 12.2075 | 4.5669 | 55.7504 | 12.2075 | 4.5669 | 58.7292 | 12.8597 | 4.5669 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2026 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 9.7066 | 444 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 686.5258 | 10.0278 | 68.462 | 686.5258 | 10.0278 | 68.462 | 723.2078 | 10.5636 | 68.462 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2026 | 410 | 410-50R | Tier-1 | Non-HFTD---1 | 4--5 | 11.9653 | 1104 | 100% | 1314.3326 | 99.38% | 0% | 0.6151% | 64.6593 | 0 | 0 | 64.6593 | 0 | 61.6806 | 12.3613 | 4.9898 | 61.6806 | 12.3613 | 4.9898 | 64.9763 | 13.0217 | 4.9898 | 4.92% | 0.044038 | 0.041858 | 29845.69 | 7721.7282 | 133.8501 | 21990.1116 | 29855.2499 | 0 | 0 | 29855.2499 | 0.002132%
2026 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 6.4307 | 367 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 253.85 | 6.6435 | 38.21 | 253.85 | 6.6435 | 38.21 | 267.4135 | 6.9985 | 38.21 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2026 | 60 | 60-576F | Tier-1 | Non-HFTD---16 | 2--1 | 2.3228 | 78 | 100% | 2.6375 | 57.75% | 0% | 42.25% | 0.075392 | 0 | 0 | 0.075392 | 0 | 0.071919 | 2.3996 | 0.029971 | 0.071919 | 2.3996 | 0.029971 | 0.075762 | 2.5278 | 0.029971 | 2.858% | 0.0059106 | 0.005618 | 446.2382 | 1.1181 | 268.8191 | 176.301 | 456.0577 | 0 | 0 | 456.0577 | 2.486e-06%
2026 | 516 | 516-5F | Tier-1 | Non-HFTD---18 | 1--1 | 1.126 | 37 | 100% | 1.2452 | 18.96% | 0% | 81.04% | 0.011684 | 0 | 0 | 0.011684 | 0 | 0.011145 | 1.1632 | 0.0095814 | 0.011145 | 1.1632 | 0.0095814 | 0.011741 | 1.2254 | 0.0095814 | 0.9383% | 0.0037102 | 0.0035265 | 335.6145 | 0.20467 | 88.3256 | 247.0843 | 349.7795 | 0 | 0 | 349.7795 | 3.853e-07%
2026 | 276 | 276-228 | Tier-1 | Non-HFTD---2 | 4--3 | 17.7437 | 786 | 100% | 290.9914 | 11.65% | 84% | 4.346% | 1.6788 | 0 | 0 | 1.6788 | 0 | 1.6014 | 18.3309 | 0.087363 | 1.6014 | 18.3309 | 0.087363 | 1.687 | 19.3104 | 0.087363 | 0.5769% | 0.065634 | 0.062385 | 4433.5468 | 54.5858 | 3672.1531 | 706.8079 | 4637.5265 | 0 | 0 | 4637.5265 | 5.536e-05%
2026 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 2.7701 | 39 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 32.1455 | 2.8617 | 11.2329 | 32.1455 | 2.8617 | 11.2329 | 33.8631 | 3.0146 | 11.2329 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2026 | 141 | CB 141 | Tier-1 | Non-HFTD---13 | 2--2 | 0.62292 | 9 | 100% | 7.7413 | 92.75% | 0.6935% | 6.554% | 0.35542 | 0 | 0 | 0.35542 | 0 | 0.33905 | 0.64353 | 0.52686 | 0.33905 | 0.64353 | 0.52686 | 0.35717 | 0.67792 | 0.52686 | 4.591% | 0.0076852 | 0.0073048 | 1007.3001 | 119.4264 | 208.7958 | 679.0778 | 1011.1018 | 0 | 0 | 1011.1018 | 1.172e-05%
2026 | 160 | 160-20R | Tier-1 | Non-HFTD---10 | 3--2 | 5.9633 | 134 | 100% | 17.1087 | 69.24% | 0% | 30.76% | 0.58642 | 0 | 0 | 0.58642 | 0 | 0.5594 | 6.1606 | 0.090803 | 0.5594 | 6.1606 | 0.090803 | 0.58929 | 6.4898 | 0.090803 | 3.428% | 0.018715 | 0.017789 | 914.1502 | 3.7049 | 637.1365 | 273.3088 | 928.792 | 0 | 0 | 928.792 | 1.934e-05%
2026 | 730 | 730-835 | Tier-1 | Non-HFTD---6 | 3--3 | 4.7612 | 180 | 100% | 55.2599 | 94.32% | 0% | 5.676% | 2.5801 | 0 | 0 | 2.5801 | 0 | 2.4612 | 4.9188 | 0.50038 | 2.4612 | 4.9188 | 0.50038 | 2.5927 | 5.1816 | 0.50038 | 4.669% | 0.01382 | 0.013136 | 3998.6627 | 454.843 | 1618.098 | 1925.7217 | 4010.4832 | 0 | 0 | 4010.4832 | 8.508e-05%
2026 | 378 | CB 378 | Tier-1 | Non-HFTD---18 | 1--1 | 0.98752 | 1 | 100% | 1.1196 | 10.82% | 0% | 89.18% | 0.0059945 | 0 | 0 | 0.0059945 | 0 | 0.0057183 | 1.0202 | 0.0056051 | 0.0057183 | 1.0202 | 0.0056051 | 0.0060239 | 1.0747 | 0.0056051 | 0.5354% | 0.0033556 | 0.0031895 | 333.65 | 5.5607 | 29.9513 | 298.138 | 349.1463 | 0 | 0 | 349.1463 | 1.977e-07%
2026 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.7481 | 0.035415 | 77.5965 | 2.7481 | 0.035415 | 77.5965 | 2.8949 | 0.037307 | 77.5965 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2026 | 409 | CB 409 | Tier-1 | Non-HFTD---8 | 3--2 | 6.5118 | 143 | 100% | 29.0295 | 85.38% | 0% | 14.62% | 1.2269 | 0 | 0 | 1.2269 | 0 | 1.1704 | 6.7273 | 0.17398 | 1.1704 | 6.7273 | 0.17398 | 1.2329 | 7.0867 | 0.17398 | 4.226% | 0.017884 | 0.016999 | 1623.1908 | 7.6402 | 1361.7978 | 253.7528 | 1635.548 | 0 | 0 | 1635.548 | 4.046e-05%
2026 | 149 | 149-129R | Tier-1 | Non-HFTD---13 | 2--2 | 0.15038 | 7 | 100% | 5.3596 | 91.52% | 2.339% | 6.145% | 0.24279 | 0 | 0 | 0.24279 | 0 | 0.2316 | 0.15536 | 1.4908 | 0.2316 | 0.15536 | 1.4908 | 0.24398 | 0.16366 | 1.4908 | 4.53% | 0.007042 | 0.0066934 | 761.089 | 113.4886 | 18.657 | 628.9434 | 764.452 | 0 | 0 | 764.452 | 8.006e-06%
2026 | 140 | CB 140 | Tier-1 | Non-HFTD---5 | 3--4 | 3.3106 | 54 | 100% | 74.8313 | 17.08% | 79.52% | 3.4% | 0.63266 | 0 | 0 | 0.63266 | 0 | 0.60352 | 3.4202 | 0.17646 | 0.60352 | 3.4202 | 0.17646 | 0.63576 | 3.6029 | 0.17646 | 0.8455% | 0.014532 | 0.013812 | 5149.556 | 4.4743 | 4651.9396 | 493.1422 | 5371.9295 | 0 | 0 | 5371.9295 | 2.086e-05%
2026 | 296 | CB 296 | Tier-2 | Tier-2---19 | 1--5 | 0.44716 | 96 | 100% | 39.5699 | 99.22% | 0% | 0.7837% | 1.9434 | 0 | 0 | 1.9434 | 0 | 1.8538 | 0.46196 | 4.013 | 1.8538 | 0.46196 | 4.013 | 1.9529 | 0.48664 | 4.013 | 4.911% | 0.0016582 | 0.0015761 | 23863.1595 | 3322.2329 | 3363.4423 | 17177.4843 | 23872.899 | 0 | 0 | 23872.899 | 6.408e-05%
2026 | 172 | CB 172 | Tier-1 | Non-HFTD---8 | 4--2 | 4.7581 | 37 | 100% | 28.3098 | 70.45% | 18.79% | 10.75% | 0.98726 | 0 | 0 | 0.98726 | 0 | 0.94178 | 4.9156 | 0.19159 | 0.94178 | 4.9156 | 0.19159 | 0.9921 | 5.1782 | 0.19159 | 3.487% | 0.048261 | 0.045872 | 586.5969 | 29.8676 | 317.2028 | 239.5265 | 595.6234 | 0 | 0 | 595.6234 | 3.256e-05%
2026 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 20.6063 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 157.4433 | 21.2882 | 7.3958 | 157.4433 | 21.2882 | 7.3958 | 165.8557 | 22.4257 | 7.3958 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2026 | 514 | CB 514 | Tier-1 | Non-HFTD---3 | 4--3 | 20.4863 | 910 | 100% | 180.2752 | 92.03% | 0% | 7.975% | 8.212 | 0 | 0 | 8.212 | 0 | 7.8337 | 21.1643 | 0.37014 | 7.8337 | 21.1643 | 0.37014 | 8.2522 | 22.2951 | 0.37014 | 4.555% | 0.058723 | 0.055816 | 3069.9453 | 628.347 | 399.7755 | 2041.8228 | 3082.6949 | 0 | 0 | 3082.6949 | 0.0002708%
2026 | 48 | CB 48 | Tier-1 | Non-HFTD---18 | 2--1 | 1.5148 | 3 | 100% | 1.5208 | 11.23% | 0% | 88.77% | 0.0084538 | 0 | 0 | 0.0084538 | 0 | 0.0080643 | 1.5649 | 0.0051531 | 0.0080643 | 1.5649 | 0.0051531 | 0.0084952 | 1.6486 | 0.0051531 | 0.5559% | 0.0049642 | 0.0047185 | 306.3449 | 5.7261 | 24.7034 | 275.9155 | 320.507 | 0 | 0 | 320.507 | 2.788e-07%
2026 | 181 | CB 181 | Tier-1 | Non-HFTD---15 | 1--2 | 0.7286 | 20 | 100% | 2.8335 | 82.32% | 0% | 17.68% | 0.11546 | 0 | 0 | 0.11546 | 0 | 0.11015 | 0.75271 | 0.14633 | 0.11015 | 0.75271 | 0.14633 | 0.11603 | 0.79293 | 0.14633 | 4.075% | 0.0024946 | 0.0023711 | 1135.8594 | 18.9687 | 837.4512 | 279.4394 | 1146.3163 | 0 | 0 | 1146.3163 | 3.808e-06%
2026 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 2.6777 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 237.7519 | 2.7663 | 85.9462 | 237.7519 | 2.7663 | 85.9462 | 250.4553 | 2.9141 | 85.9462 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2026 | BW1 | CB BW1 | Tier-1 | Non-HFTD---11 | 1--3 | 1.0872 | 45 | 100% | 8.712 | 88.19% | 0% | 11.81% | 0.3803 | 0 | 0 | 0.3803 | 0 | 0.36278 | 1.1231 | 0.32301 | 0.36278 | 1.1231 | 0.32301 | 0.38217 | 1.1832 | 0.32301 | 4.365% | 0.0039232 | 0.003729 | 2220.6335 | 316.4948 | 49.7388 | 1854.3999 | 2234.2939 | 0 | 0 | 2234.2939 | 1.254e-05%
2026 | 406 | CB 406 | Tier-1 | Non-HFTD---12 | 3--2 | 5.5205 | 205 | 100% | 8.8138 | 58.69% | 0% | 41.31% | 0.25605 | 0 | 0 | 0.25605 | 0 | 0.24425 | 5.7032 | 0.042827 | 0.24425 | 5.7032 | 0.042827 | 0.2573 | 6.0079 | 0.042827 | 2.905% | 0.014645 | 0.01392 | 601.8164 | 0.6689 | 372.8417 | 228.3057 | 614.7641 | 0 | 0 | 614.7641 | 8.443e-06%
2026 | 241 | 241-820AE | Tier-1 | Non-HFTD---2 | 5--3 | 3.04 | 97 | 100% | 286.7702 | 14.9% | 84.42% | 0.6786% | 2.1155 | 0 | 0 | 2.1155 | 0 | 2.018 | 3.1406 | 0.64258 | 2.018 | 3.1406 | 0.64258 | 2.1259 | 3.3084 | 0.64258 | 0.7377% | 0.10624 | 0.10098 | 2699.1913 | 103.9208 | 2115.2903 | 479.9802 | 2818.8105 | 0 | 0 | 2818.8105 | 6.976e-05%
2026 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 3.4321 | 22 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 9.4254 | 3.5456 | 2.6583 | 9.4254 | 3.5456 | 2.6583 | 9.929 | 3.7351 | 2.6583 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2026 | 96 | CB 96 | Tier-1 | Non-HFTD---7 | 2--3 | 0.84791 | 78 | 100% | 37.3393 | 43.85% | 54.05% | 2.092% | 0.81053 | 0 | 0 | 0.81053 | 0 | 0.77319 | 0.87597 | 0.88267 | 0.77319 | 0.87597 | 0.88267 | 0.8145 | 0.92278 | 0.88267 | 2.171% | 0.0084764 | 0.0080568 | 4405.0953 | 227.7051 | 3027.1235 | 1150.2667 | 4533.9014 | 0 | 0 | 4533.9014 | 2.673e-05%
2026 | 145 | 145-633 | Tier-1 | Non-HFTD---11 | 2--2 | 0.17216 | 0 | 100% | 10.3552 | 34.57% | 64.03% | 1.397% | 0.1772 | 0 | 0 | 0.1772 | 0 | 0.16903 | 0.17786 | 0.9504 | 0.16903 | 0.17786 | 0.9504 | 0.17807 | 0.18736 | 0.9504 | 1.711% | 0.0067068 | 0.0063748 | 1543.9807 | 37.6917 | 1219.1738 | 287.1152 | 1596.5913 | 0 | 0 | 1596.5913 | 5.843e-06%
2026 | 178 | 178-982 | Tier-2 | Tier-2---21 | 1--1 | 1.1551 | 19 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0063254 | 0 | 0 | 0.0063254 | 0 | 0.006034 | 1.1933 | 0.0050564 | 0.006034 | 1.1933 | 0.0050564 | 0.0063564 | 1.2571 | 0.0050564 | 0.6625% | 0.0033454 | 0.0031798 | 285.4035 | 0.62363 | 58.6739 | 226.106 | 298.2775 | 0 | 0 | 298.2775 | 2.086e-07%
2026 | NO1 | NO1-288F | Tier-1 | Non-HFTD---18 | 1--1 | 1.0576 | 14 | 100% | 0.81031 | 11.55% | 0% | 88.45% | 0.0046337 | 0 | 0 | 0.0046337 | 0 | 0.0044202 | 1.0926 | 0.0040457 | 0.0044202 | 1.0926 | 0.0040457 | 0.0046564 | 1.151 | 0.0040457 | 0.5718% | 0.002839 | 0.0026985 | 285.4227 | 0.18996 | 55.9053 | 229.3274 | 298.5697 | 0 | 0 | 298.5697 | 1.528e-07%
2026 | 712 | 712-26 | Tier-1 | Non-HFTD---19 | 1--2 | 0.16006 | 32 | 100% | 0.49531 | 70.46% | 0% | 29.54% | 0.017274 | 0 | 0 | 0.017274 | 0 | 0.016478 | 0.16536 | 0.099654 | 0.016478 | 0.16536 | 0.099654 | 0.017359 | 0.17419 | 0.099654 | 3.488% | 0.0005438 | 0.00051688 | 910.8315 | 103.0746 | 31.4131 | 776.3438 | 924.8457 | 0 | 0 | 924.8457 | 5.696e-07%
2026 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.036174 | 0 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.1885 | 0.037371 | 31.8018 | 1.1885 | 0.037371 | 31.8018 | 1.252 | 0.039368 | 31.8018 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2026 | 532 | 532-763 | Tier-1 | Non-HFTD---2 | 5--4 | 6.6682 | 237 | 100% | 872.9353 | 22.07% | 77.46% | 0.4675% | 9.5372 | 0 | 0 | 9.5372 | 0 | 9.0978 | 6.8889 | 1.3207 | 9.0978 | 6.8889 | 1.3207 | 9.5839 | 7.2569 | 1.3207 | 1.093% | 0.10819 | 0.10283 | 8068.6143 | 305.6113 | 5713.7599 | 2049.2431 | 8396.0666 | 0 | 0 | 8396.0666 | 0.0003145%
2026 | 138 | 138-360F | Tier-1 | Non-HFTD---17 | 1--2 | 0.59812 | 11 | 100% | 1.3988 | 40.66% | 0% | 59.34% | 0.02815 | 0 | 0 | 0.02815 | 0 | 0.026853 | 0.61791 | 0.043457 | 0.026853 | 0.61791 | 0.043457 | 0.028288 | 0.65093 | 0.043457 | 2.012% | 0.0024168 | 0.0022972 | 578.7745 | 0.25845 | 266.504 | 312.012 | 596.6618 | 0 | 0 | 596.6618 | 9.283e-07%
2026 | 1435 | 1435-1075F | Tier-1 | Non-HFTD---15 | 2--2 | 2.7231 | 121 | 100% | 4.6893 | 70.05% | 0% | 29.95% | 0.1626 | 0 | 0 | 0.1626 | 0 | 0.15511 | 2.8132 | 0.055134 | 0.15511 | 2.8132 | 0.055134 | 0.16339 | 2.9636 | 0.055134 | 3.467% | 0.0067656 | 0.0064307 | 693.1065 | 136.0595 | 69.2928 | 487.7542 | 703.9175 | 0 | 0 | 703.9175 | 5.362e-06%
2026 | 1202 | 1202-9 | Tier-2 | Tier-2---17 | 2--4 | 3.468 | 67 | 100% | 73.4421 | 96.84% | 0% | 3.16% | 3.5205 | 0 | 0 | 3.5205 | 0 | 3.3583 | 3.5827 | 0.93737 | 3.3583 | 3.5827 | 0.93737 | 3.5378 | 3.7741 | 0.93737 | 4.794% | 0.01182 | 0.011235 | 6213.48 | 1453.8319 | 498.5132 | 4261.1349 | 6223.7055 | 0 | 0 | 6223.7055 | 0.0001161%
2026 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 11.5724 | 1453 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 124.1616 | 11.9553 | 10.3855 | 124.1616 | 11.9553 | 10.3855 | 130.7958 | 12.5941 | 10.3855 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2026 | 274 | 274-40 | Tier-1 | Non-HFTD---3 | 4--3 | 7.8386 | 296 | 100% | 130.2262 | 2.649% | 92.8% | 4.548% | 0.17075 | 0 | 0 | 0.17075 | 0 | 0.16289 | 8.098 | 0.020114 | 0.16289 | 8.098 | 0.020114 | 0.17159 | 8.5307 | 0.020114 | 0.1311% | 0.037195 | 0.035354 | 3501.1361 | 5.6164 | 3059.4974 | 436.0223 | 3678.638 | 0 | 0 | 3678.638 | 5.631e-06%
2026 | 270 | CB 270 | Tier-1 | Non-HFTD---5 | 3--4 | 2.0546 | 375 | 100% | 71.4588 | 15.92% | 82.32% | 1.76% | 0.56317 | 0 | 0 | 0.56317 | 0 | 0.53723 | 2.1225 | 0.25311 | 0.53723 | 2.1225 | 0.25311 | 0.56593 | 2.236 | 0.25311 | 0.7881% | 0.0142 | 0.013497 | 5032.3124 | 129.2561 | 3832.2088 | 1070.8475 | 5252.6589 | 0 | 0 | 5252.6589 | 1.857e-05%
2026 | 563 | CB 563 | Tier-1 | Non-HFTD---11 | 1--4 | 0.17481 | 35 | 100% | 10.231 | 98.75% | 0% | 1.252% | 0.50009 | 0 | 0 | 0.50009 | 0 | 0.47705 | 0.1806 | 2.6416 | 0.47705 | 0.1806 | 2.6416 | 0.50254 | 0.19025 | 2.6416 | 4.888% | 0.0006932 | 0.00065889 | 14759.0669 | 2171.1529 | 3891.2279 | 8696.6862 | 14768.6918 | 0 | 0 | 14768.6918 | 1.649e-05%
2026 | 700 | CB 700 | Tier-1 | Non-HFTD---13 | 1--3 | 0.40907 | 7 | 100% | 6.7901 | 95.69% | 0% | 4.313% | 0.32161 | 0 | 0 | 0.32161 | 0 | 0.3068 | 0.42261 | 0.72596 | 0.3068 | 0.42261 | 0.72596 | 0.32319 | 0.44519 | 0.72596 | 4.736% | 0.0015946 | 0.0015157 | 4258.1661 | 656.9619 | 50.5505 | 3550.6537 | 4267.7311 | 0 | 0 | 4267.7311 | 1.061e-05%
2026 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 27.7907 | 1435 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 858.8326 | 28.7104 | 29.9137 | 858.8326 | 28.7104 | 29.9137 | 904.7212 | 30.2444 | 29.9137 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2026 | 189 | 189-645 | Tier-1 | Non-HFTD---11 | 2--3 | 1.8176 | 78 | 100% | 13.5881 | 92.26% | 0% | 7.743% | 0.62053 | 0 | 0 | 0.62053 | 0 | 0.59194 | 1.8778 | 0.31524 | 0.59194 | 1.8778 | 0.31524 | 0.62357 | 1.9781 | 0.31524 | 4.567% | 0.0052774 | 0.0050162 | 2574.7796 | 257.5393 | 821.9251 | 1495.3153 | 2585.1626 | 0 | 0 | 2585.1626 | 2.046e-05%
2026 | 368 | 368-403F | Tier-1 | Non-HFTD---11 | 2--2 | 0.42387 | 9 | 100% | 10.4781 | 1.466% | 94.68% | 3.85% | 0.0076023 | 0 | 0 | 0.0076023 | 0 | 0.007252 | 0.4379 | 0.016561 | 0.007252 | 0.4379 | 0.016561 | 0.0076395 | 0.46129 | 0.016561 | 0.07255% | 0.0067636 | 0.0064288 | 1549.1827 | 1.6714 | 1373.0792 | 174.432 | 1628.6783 | 0 | 0 | 1628.6783 | 2.507e-07%
2026 | 719 | 719-28 | Tier-1 | Non-HFTD---19 | 1--3 | 0.011364 | 0 | 100% | 0.19101 | 81.43% | 0% | 18.57% | 0.0076988 | 0 | 0 | 0.0076988 | 0 | 0.0073442 | 0.01174 | 0.62558 | 0.0073442 | 0.01174 | 0.62558 | 0.0077366 | 0.012367 | 0.62558 | 4.031% | 7.58e-05 | 7.2048e-05 | 2519.9154 | 0.35219 | 2094.389 | 425.1743 | 2544.2902 | 0 | 0 | 2544.2902 | 2.539e-07%
2026 | 62 | CB 62 | Tier-1 | Non-HFTD---5 | 3--4 | 1.8229 | 124 | 100% | 88.5913 | 17.86% | 80.39% | 1.758% | 0.78309 | 0 | 0 | 0.78309 | 0 | 0.74701 | 1.8833 | 0.39666 | 0.74701 | 1.8833 | 0.39666 | 0.78692 | 1.9839 | 0.39666 | 0.8839% | 0.016405 | 0.015593 | 5400.2599 | 65.1821 | 4479.0088 | 856.069 | 5631.2734 | 0 | 0 | 5631.2734 | 2.582e-05%
2026 | 88 | 88-27F | Tier-1 | Non-HFTD---15 | 1--3 | 0.14678 | 11 | 100% | 2.2245 | 92.57% | 0% | 7.426% | 0.10194 | 0 | 0 | 0.10194 | 0 | 0.097241 | 0.15164 | 0.64127 | 0.097241 | 0.15164 | 0.64127 | 0.10244 | 0.15974 | 0.64127 | 4.582% | 0.0008056 | 0.00076572 | 2761.3126 | 412.5963 | 52.951 | 2295.7652 | 2771.9912 | 0 | 0 | 2771.9912 | 3.361e-06%
2026 | 309 | 309-15F | Tier-1 | Non-HFTD---12 | 3--1 | 8.7252 | 163 | 100% | 10.1949 | 53% | 0% | 47% | 0.26747 | 0 | 0 | 0.26747 | 0 | 0.25515 | 9.0139 | 0.028307 | 0.25515 | 9.0139 | 0.028307 | 0.26879 | 9.4955 | 0.028307 | 2.624% | 0.023995 | 0.022807 | 424.8851 | 7.9838 | 195.2064 | 221.6949 | 435.2844 | 0 | 0 | 435.2844 | 8.82e-06%
2026 | 161 | 161-975F | Tier-1 | Non-HFTD---13 | 2--2 | 3.2134 | 83 | 100% | 8.5862 | 76.7% | 0% | 23.3% | 0.32599 | 0 | 0 | 0.32599 | 0 | 0.31097 | 3.3198 | 0.093673 | 0.31097 | 3.3198 | 0.093673 | 0.32759 | 3.4972 | 0.093673 | 3.797% | 0.0085198 | 0.0080981 | 1007.7888 | 0.42746 | 792.7442 | 214.6171 | 1020.0168 | 0 | 0 | 1020.0168 | 1.075e-05%
2026 | 90 | CB 90 | Tier-1 | Non-HFTD---9 | 2--3 | 0.018939 | 0 | 100% | 16.6741 | 2.335% | 97.48% | 0.1839% | 0.019272 | 0 | 0 | 0.019272 | 0 | 0.018384 | 0.019566 | 0.93959 | 0.018384 | 0.019566 | 0.93959 | 0.019367 | 0.020612 | 0.93959 | 0.1156% | 0.0049876 | 0.0047407 | 3343.1051 | 4.348 | 3056.2234 | 282.5337 | 3513.1416 | 0 | 0 | 3513.1416 | 6.355e-07%
2026 | 183 | CB 183 | Tier-1 | Non-HFTD---4 | 3--4 | 2.7093 | 99 | 100% | 128.8021 | 22.66% | 75.77% | 1.57% | 1.4445 | 0 | 0 | 1.4445 | 0 | 1.3779 | 2.799 | 0.4923 | 1.3779 | 2.799 | 0.4923 | 1.4516 | 2.9485 | 0.4923 | 1.121% | 0.022326 | 0.021221 | 5769.2045 | 129.7649 | 4423.5742 | 1215.8654 | 6001.5822 | 0 | 0 | 6001.5822 | 4.763e-05%
2026 | 854 | 854-607F | Tier-1 | Non-HFTD---13 | 1--5 | 0.039394 | 11 | 100% | 5.4805 | 98.61% | 0% | 1.386% | 0.26752 | 0 | 0 | 0.26752 | 0 | 0.2552 | 0.040698 | 6.2706 | 0.2552 | 0.040698 | 6.2706 | 0.26883 | 0.042872 | 6.2706 | 4.881% | 0.000262 | 0.00024903 | 20917.8697 | 3367.0159 | 28.8837 | 17521.9701 | 20932.9704 | 0 | 0 | 20932.9704 | 8.822e-06%
2026 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 13.2995 | 388 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 431.9104 | 13.7396 | 31.4355 | 431.9104 | 13.7396 | 31.4355 | 454.988 | 14.4737 | 31.4355 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2026 | 54 | CB 54 | Tier-1 | Non-HFTD---11 | 2--2 | 2.685 | 55 | 100% | 9.0518 | 74.11% | 0% | 25.89% | 0.33207 | 0 | 0 | 0.33207 | 0 | 0.31677 | 2.7739 | 0.1142 | 0.31677 | 2.7739 | 0.1142 | 0.33369 | 2.9221 | 0.1142 | 3.669% | 0.0079966 | 0.0076008 | 1131.9509 | 0.54614 | 863.4862 | 267.9186 | 1147.2119 | 0 | 0 | 1147.2119 | 1.095e-05%
2026 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.57917 | 50 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.8008 | 0.59833 | 23.0654 | 13.8008 | 0.59833 | 23.0654 | 14.5382 | 0.6303 | 23.0654 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2026 | 51 | CB 51 | Tier-1 | Non-HFTD---14 | 3--1 | 5.1357 | 233 | 100% | 6.4086 | 44.95% | 0% | 55.05% | 0.14259 | 0 | 0 | 0.14259 | 0 | 0.13602 | 5.3056 | 0.025638 | 0.13602 | 5.3056 | 0.025638 | 0.14329 | 5.5891 | 0.025638 | 2.225% | 0.014079 | 0.013382 | 455.1864 | 0.18855 | 227.3695 | 227.6283 | 468.236 | 0 | 0 | 468.236 | 4.702e-06%
2026 | 946 | 946-25F | Tier-1 | Non-HFTD---20 | 1--1 | 0.62441 | 13 | 100% | 0.39407 | 18.79% | 0% | 81.21% | 0.0036656 | 0 | 0 | 0.0036656 | 0 | 0.0034967 | 0.64507 | 0.0054207 | 0.0034967 | 0.64507 | 0.0054207 | 0.0036836 | 0.67954 | 0.0054207 | 0.9302% | 0.0015836 | 0.0015052 | 248.8471 | 0.15206 | 65.1198 | 183.5753 | 259.3713 | 0 | 0 | 259.3713 | 1.209e-07%
2026 | NO1 | NO1-287F | Tier-1 | Non-HFTD---18 | 2--1 | 1.8949 | 50 | 100% | 1.6275 | 20.71% | 0% | 79.29% | 0.016687 | 0 | 0 | 0.016687 | 0 | 0.015918 | 1.9576 | 0.0081316 | 0.015918 | 1.9576 | 0.0081316 | 0.016769 | 2.0622 | 0.0081316 | 1.025% | 0.0051894 | 0.0049325 | 313.6146 | 0.1871 | 87.5499 | 225.8776 | 326.5639 | 0 | 0 | 326.5639 | 5.503e-07%
2026 | 205 | CB 205 | Tier-1 | Non-HFTD---7 | 3--3 | 5.2694 | 405 | 100% | 38.7792 | 89.82% | 0% | 10.18% | 1.7242 | 0 | 0 | 1.7242 | 0 | 1.6447 | 5.4437 | 0.30214 | 1.6447 | 5.4437 | 0.30214 | 1.7326 | 5.7346 | 0.30214 | 4.446% | 0.016219 | 0.015416 | 2391.0005 | 150.1089 | 1253.224 | 987.6676 | 2403.6753 | 0 | 0 | 2403.6753 | 5.686e-05%
2026 | 296 | 296-66F | Tier-2 | Tier-2---21 | 1--3 | 0.14451 | 7 | 100% | 2.284 | 90.58% | 0% | 9.421% | 0.10241 | 0 | 0 | 0.10241 | 0 | 0.097688 | 0.14929 | 0.65436 | 0.097688 | 0.14929 | 0.65436 | 0.10291 | 0.15726 | 0.65436 | 4.484% | 0.0006178 | 0.00058722 | 3696.9667 | 843.8145 | 35.5403 | 2817.6118 | 3715.1054 | 0 | 0 | 3715.1054 | 3.377e-06%
2026 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 2.3455 | 224 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 203.6169 | 2.4231 | 84.031 | 203.6169 | 2.4231 | 84.031 | 214.4964 | 2.5526 | 84.031 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2026 | EN2 | CB EN2 | Tier-1 | Non-HFTD---8 | 3--3 | 5.9322 | 649 | 100% | 45.2165 | 53.61% | 36.84% | 9.55% | 1.2 | 0 | 0 | 1.2 | 0 | 1.1447 | 6.1285 | 0.18679 | 1.1447 | 6.1285 | 0.18679 | 1.2059 | 6.4559 | 0.18679 | 2.654% | 0.022788 | 0.02166 | 1984.2222 | 155.0903 | 804.1172 | 1025.0147 | 2032.1547 | 0 | 0 | 2032.1547 | 3.957e-05%
2026 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | 3--5 | 9.2025 | 702 | 100% | 1424.1907 | 99.61% | 0% | 0.3928% | 70.2205 | 0 | 0 | 70.2205 | 0 | 66.9856 | 9.507 | 7.0459 | 66.9856 | 9.507 | 7.0459 | 70.5647 | 10.015 | 7.0459 | 4.931% | 0.028304 | 0.026903 | 50317.6471 | 8145.1206 | 368.3302 | 41804.1963 | 50327.94 | 0 | 0 | 50327.94 | 0.002316%
2026 | 380 | CB 380 | Tier-1 | Non-HFTD---6 | 3--3 | 6.7373 | 225 | 100% | 65.1412 | 93.43% | 0% | 6.569% | 3.0127 | 0 | 0 | 3.0127 | 0 | 2.8739 | 6.9603 | 0.4129 | 2.8739 | 6.9603 | 0.4129 | 3.0274 | 7.3322 | 0.4129 | 4.625% | 0.019847 | 0.018864 | 3282.237 | 399.2549 | 1245.0692 | 1637.9129 | 3293.4656 | 0 | 0 | 3293.4656 | 9.935e-05%
2026 | 792 | 792-47R | Tier-1 | Non-HFTD---1 | 4--4 | 7.7364 | 716 | 100% | 393.985 | 1.678% | 96.94% | 1.378% | 0.32719 | 0 | 0 | 0.32719 | 0 | 0.31212 | 7.9924 | 0.039052 | 0.31212 | 7.9924 | 0.039052 | 0.32879 | 8.4194 | 0.039052 | 0.08305% | 0.039069 | 0.037135 | 10084.4423 | 11.8059 | 9078.6124 | 994.0241 | 10600.8076 | 0 | 0 | 10600.8076 | 1.079e-05%
2026 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 27.9316 | 2565 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1208.2563 | 28.856 | 41.8719 | 1208.2563 | 28.856 | 41.8719 | 1272.8151 | 30.3978 | 41.8719 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2026 | 56 | 56-670F | Tier-1 | Non-HFTD---6 | 3--3 | 1.1852 | 40 | 100% | 49.2251 | 0.5924% | 97.4% | 2.005% | 0.014434 | 0 | 0 | 0.014434 | 0 | 0.013769 | 1.2244 | 0.011245 | 0.013769 | 1.2244 | 0.011245 | 0.014505 | 1.2898 | 0.011245 | 0.02932% | 0.014208 | 0.013505 | 3464.6013 | 3.8619 | 3012.3419 | 448.3975 | 3643.9615 | 0 | 0 | 3643.9615 | 4.76e-07%
2026 | 133 | CB 133 | Tier-1 | Non-HFTD---14 | 3--2 | 6.2032 | 134 | 100% | 8.7184 | 49.78% | 0% | 50.22% | 0.21483 | 0 | 0 | 0.21483 | 0 | 0.20493 | 6.4085 | 0.031978 | 0.20493 | 6.4085 | 0.031978 | 0.21588 | 6.7509 | 0.031978 | 2.464% | 0.017124 | 0.016276 | 509.131 | 1.8919 | 270.3959 | 236.8432 | 522.4469 | 0 | 0 | 522.4469 | 7.084e-06%
2026 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 0.75759 | 163 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.3205 | 0.78266 | 4.2426 | 3.3205 | 0.78266 | 4.2426 | 3.4979 | 0.82448 | 4.2426 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2026 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 13.5415 | 913 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 461.7857 | 13.9896 | 33.0092 | 461.7857 | 13.9896 | 33.0092 | 486.4596 | 14.7371 | 33.0092 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2026 | 163 | CB 163 | Tier-1 | Non-HFTD---6 | 4--2 | 19.7841 | 299 | 100% | 56.8724 | 88.67% | 0% | 11.33% | 2.4962 | 0 | 0 | 2.4962 | 0 | 2.3812 | 20.4388 | 0.11651 | 2.3812 | 20.4388 | 0.11651 | 2.5085 | 21.5309 | 0.11651 | 4.389% | 0.038275 | 0.03638 | 1485.8961 | 18.0474 | 1223.2724 | 244.5763 | 1494.6629 | 0 | 0 | 1494.6629 | 8.232e-05%
2026 | 482 | 482-381F | Tier-1 | Non-HFTD---18 | 1--1 | 1.6901 | 145 | 100% | 1.247 | 13.37% | 0% | 86.63% | 0.0082507 | 0 | 0 | 0.0082507 | 0 | 0.0078706 | 1.7461 | 0.0045077 | 0.0078706 | 1.7461 | 0.0045077 | 0.0082912 | 1.8394 | 0.0045077 | 0.6617% | 0.0044034 | 0.0041854 | 283.1864 | 0.18461 | 60.1392 | 222.8626 | 295.9628 | 0 | 0 | 295.9628 | 2.721e-07%
2026 | 463 | CB 463 | Tier-2 | Tier-2---17 | 2--5 | 1.5028 | 87 | 100% | 99.9729 | 99.18% | 0% | 0.8185% | 4.9082 | 0 | 0 | 4.9082 | 0 | 4.682 | 1.5526 | 3.0157 | 4.682 | 1.5526 | 3.0157 | 4.9322 | 1.6355 | 3.0157 | 4.909% | 0.0053474 | 0.0050827 | 18695.6146 | 4709.0355 | 4354.0593 | 9632.5197 | 18703.5841 | 0 | 0 | 18703.5841 | 0.0001619%
2026 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 10.5112 | 1091 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 89.723 | 10.859 | 8.2625 | 89.723 | 10.859 | 8.2625 | 94.517 | 11.4392 | 8.2625 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2026 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 0.095455 | 38 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.7918 | 0.098613 | 18.1696 | 1.7918 | 0.098613 | 18.1696 | 1.8875 | 0.10388 | 18.1696 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2026 | 124 | CB 124 | Tier-1 | Non-HFTD---15 | 1--2 | 0.95 | 6 | 100% | 3.2925 | 66.24% | 0% | 33.76% | 0.10796 | 0 | 0 | 0.10796 | 0 | 0.10298 | 0.98144 | 0.10493 | 0.10298 | 0.98144 | 0.10493 | 0.10849 | 1.0339 | 0.10493 | 3.279% | 0.0040986 | 0.0038957 | 803.3242 | 53.1781 | 266.286 | 483.8601 | 817.4481 | 0 | 0 | 817.4481 | 3.56e-06%
2026 | 701 | CB 701 | Tier-1 | Non-HFTD---2 | 4--3 | 17.7385 | 540 | 100% | 193.6018 | 45.82% | 47.23% | 6.946% | 4.3911 | 0 | 0 | 4.3911 | 0 | 4.1888 | 18.3255 | 0.22858 | 4.1888 | 18.3255 | 0.22858 | 4.4126 | 19.3047 | 0.22858 | 2.268% | 0.065404 | 0.062166 | 2960.1098 | 147.5713 | 1958.5218 | 854.0167 | 3043.6312 | 0 | 0 | 3043.6312 | 0.0001448%
2026 | 213 | 213-262F | Tier-1 | Non-HFTD---19 | 1--2 | 0.083756 | 5 | 100% | 0.16168 | 79.23% | 0% | 20.77% | 0.0063411 | 0 | 0 | 0.0063411 | 0 | 0.0060489 | 0.086528 | 0.069907 | 0.0060489 | 0.086528 | 0.069907 | 0.0063721 | 0.091151 | 0.069907 | 3.922% | 0.0001976 | 0.00018782 | 818.194 | 104.1852 | 22.3943 | 691.6145 | 827.0423 | 0 | 0 | 827.0423 | 2.091e-07%
2026 | 1139 | 1139-4F | Tier-2 | Tier-2---11 | 5--3 | 4.1474 | 89 | 100% | 472.1771 | 0.2595% | 99.27% | 0.4712% | 0.060646 | 0 | 0 | 0.060646 | 0 | 0.057852 | 4.2846 | 0.013502 | 0.057852 | 4.2846 | 0.013502 | 0.060943 | 4.5136 | 0.013502 | 0.01284% | 0.11231 | 0.10675 | 4204.4022 | 7.5405 | 3803.8802 | 392.9815 | 4422.7903 | 0 | 0 | 4422.7903 | 2e-06%
2026 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.84619 | 36 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 99.2512 | 0.87419 | 113.5349 | 99.2512 | 0.87419 | 113.5349 | 104.5543 | 0.9209 | 113.5349 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2026 | 451 | 451-38F | Tier-1 | Non-HFTD---17 | 1--1 | 1.3801 | 116 | 100% | 1.6743 | 45.15% | 0% | 54.85% | 0.037424 | 0 | 0 | 0.037424 | 0 | 0.0357 | 1.4258 | 0.025038 | 0.0357 | 1.4258 | 0.025038 | 0.037607 | 1.502 | 0.025038 | 2.235% | 0.004114 | 0.0039104 | 406.98 | 0.16796 | 204.0476 | 202.7644 | 418.6042 | 0 | 0 | 418.6042 | 1.234e-06%
2026 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.76383 | 10 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 8.0511 | 0.7891 | 10.2028 | 8.0511 | 0.7891 | 10.2028 | 8.4812 | 0.83127 | 10.2028 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2026 | 480 | 480-35 | Tier-1 | Non-HFTD---10 | 4--1 | 16.4336 | 1010 | 100% | 19.5827 | 39.21% | 0% | 60.79% | 0.38007 | 0 | 0 | 0.38007 | 0 | 0.36256 | 16.9774 | 0.021355 | 0.36256 | 16.9774 | 0.021355 | 0.38193 | 17.8845 | 0.021355 | 1.941% | 0.047129 | 0.044796 | 415.5112 | 23.8764 | 99.4507 | 292.1841 | 428.6657 | 0 | 0 | 428.6657 | 1.253e-05%
2026 | 719 | 719-33 | Tier-1 | Non-HFTD---16 | 2--1 | 4.6088 | 110 | 100% | 4.0499 | 25.39% | 0% | 74.61% | 0.050892 | 0 | 0 | 0.050892 | 0 | 0.048548 | 4.7613 | 0.010196 | 0.048548 | 4.7613 | 0.010196 | 0.051142 | 5.0157 | 0.010196 | 1.257% | 0.012955 | 0.012314 | 312.6002 | 0.17551 | 100.5469 | 211.8778 | 324.7469 | 0 | 0 | 324.7469 | 1.678e-06%
2026 | 83 | 83-622F | Tier-1 | Non-HFTD---18 | 2--1 | 3.0943 | 66 | 100% | 1.5636 | 25.94% | 0% | 74.06% | 0.020078 | 0 | 0 | 0.020078 | 0 | 0.019153 | 3.1967 | 0.0059914 | 0.019153 | 3.1967 | 0.0059914 | 0.020176 | 3.3675 | 0.0059914 | 1.284% | 0.00696 | 0.0066155 | 224.6568 | 1.1983 | 66.8397 | 156.6188 | 233.3214 | 0 | 0 | 233.3214 | 6.621e-07%
2026 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 19.7983 | 1084 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 205.1652 | 20.4534 | 10.0308 | 205.1652 | 20.4534 | 10.0308 | 216.1274 | 21.5463 | 10.0308 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2026 | 1079 | CB 1079 | Tier-1 | Non-HFTD---9 | 2--3 | 2.5269 | 152 | 100% | 15.9736 | 90.06% | 0% | 9.938% | 0.71212 | 0 | 0 | 0.71212 | 0 | 0.67931 | 2.6105 | 0.26023 | 0.67931 | 2.6105 | 0.26023 | 0.71561 | 2.75 | 0.26023 | 4.458% | 0.0072148 | 0.0068577 | 2214.0112 | 265.8554 | 1002.265 | 945.8908 | 2225.4696 | 0 | 0 | 2225.4696 | 2.348e-05%
2026 | 207 | CB 207 | Tier-1 | Non-HFTD---7 | 2--3 | 2.9445 | 104 | 100% | 36.13 | 94.58% | 0% | 5.421% | 1.6915 | 0 | 0 | 1.6915 | 0 | 1.6136 | 3.042 | 0.53043 | 1.6136 | 3.042 | 0.53043 | 1.6998 | 3.2045 | 0.53043 | 4.682% | 0.0090126 | 0.0085665 | 4008.8284 | 146.4393 | 2915.0578 | 947.3313 | 4020.1468 | 0 | 0 | 4020.1468 | 5.578e-05%
2026 | 1418 | 1418-31R | Tier-1 | Non-HFTD---15 | 1--2 | 0.66439 | 18 | 100% | 2.7275 | 78.81% | 0% | 21.19% | 0.1064 | 0 | 0 | 0.1064 | 0 | 0.1015 | 0.68638 | 0.14787 | 0.1015 | 0.68638 | 0.14787 | 0.10692 | 0.72306 | 0.14787 | 3.901% | 0.0024528 | 0.0023314 | 1112.0026 | 74.6408 | 441.9379 | 595.4239 | 1124.2767 | 0 | 0 | 1124.2767 | 3.509e-06%
2026 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 5.4324 | 19 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 21.551 | 5.6122 | 3.8401 | 21.551 | 5.6122 | 3.8401 | 22.7025 | 5.912 | 3.8401 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2026 | 431 | 431-46AE | Tier-1 | Non-HFTD---14 | 2--1 | 4.3178 | 34 | 100% | 5.4602 | 36.55% | 0% | 63.45% | 0.098795 | 0 | 0 | 0.098795 | 0 | 0.094244 | 4.4607 | 0.021128 | 0.094244 | 4.4607 | 0.021128 | 0.09928 | 4.699 | 0.021128 | 1.809% | 0.012491 | 0.011873 | 437.1166 | 0.2108 | 184.9596 | 251.9462 | 451.5597 | 0 | 0 | 451.5597 | 3.258e-06%
2026 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 16.422 | 1638 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 522.9766 | 16.9654 | 30.826 | 522.9766 | 16.9654 | 30.826 | 550.9199 | 17.8719 | 30.826 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2026 | BO1 | CB BO1 | Tier-1 | Non-HFTD---18 | 2--1 | 1.7728 | 43 | 100% | 1.9101 | 28.77% | 0% | 71.23% | 0.027199 | 0 | 0 | 0.027199 | 0 | 0.025946 | 1.8314 | 0.014167 | 0.025946 | 1.8314 | 0.014167 | 0.027332 | 1.9293 | 0.014167 | 1.424% | 0.0052326 | 0.0049736 | 365.037 | 0.49286 | 127.5995 | 236.9446 | 378.5787 | 0 | 0 | 378.5787 | 8.969e-07%
2026 | 545 | CB 545 | Tier-1 | Non-HFTD---5 | 3--3 | 1.9879 | 35 | 100% | 70.9796 | 19.97% | 77.85% | 2.177% | 0.7018 | 0 | 0 | 0.7018 | 0 | 0.66947 | 2.0537 | 0.32599 | 0.66947 | 2.0537 | 0.32599 | 0.70524 | 2.1634 | 0.32599 | 0.9887% | 0.015929 | 0.01514 | 4456.0552 | 3.8159 | 4082.19 | 370.0493 | 4641.7637 | 0 | 0 | 4641.7637 | 2.314e-05%
2026 | 150 | 150-434AE | Tier-1 | Non-HFTD---9 | 1--4 | 1.1161 | 6 | 100% | 24.5324 | 96.53% | 0% | 3.474% | 1.1722 | 0 | 0 | 1.1722 | 0 | 1.1182 | 1.153 | 0.96976 | 1.1182 | 1.153 | 0.96976 | 1.1779 | 1.2146 | 0.96976 | 4.778% | 0.0042426 | 0.0040326 | 5782.3912 | 1118.2339 | 22.284 | 4641.8732 | 5792.8535 | 0 | 0 | 5792.8535 | 3.865e-05%
2026 | 144 | 144-442F | Tier-1 | Non-HFTD---5 | 3--4 | 3.5848 | 126 | 100% | 88.4511 | 1.673% | 95.65% | 2.673% | 0.073245 | 0 | 0 | 0.073245 | 0 | 0.069871 | 3.7034 | 0.018866 | 0.069871 | 3.7034 | 0.018866 | 0.073604 | 3.9013 | 0.018866 | 0.08281% | 0.015509 | 0.014741 | 5703.2117 | 6.9384 | 5087.8182 | 608.4551 | 5995.254 | 0 | 0 | 5995.254 | 2.415e-06%
2026 | 990 | 990-713 | Tier-2 | Tier-2---17 | 3--3 | 0.065909 | 13 | 100% | 85.9224 | 0.4524% | 99.5% | 0.04623% | 0.01924 | 0 | 0 | 0.01924 | 0 | 0.018353 | 0.06809 | 0.26955 | 0.018353 | 0.06809 | 0.26955 | 0.019334 | 0.071728 | 0.26955 | 0.02239% | 0.017823 | 0.01694 | 4820.9793 | 10.6403 | 4200.4141 | 609.9249 | 5070.9099 | 0 | 0 | 5070.9099 | 6.345e-07%
2026 | 160 | CB 160 | Tier-1 | Non-HFTD---7 | 2--3 | 3.6716 | 129 | 100% | 31.5499 | 92.29% | 0% | 7.71% | 1.4413 | 0 | 0 | 1.4413 | 0 | 1.3749 | 3.7931 | 0.36248 | 1.3749 | 3.7931 | 0.36248 | 1.4484 | 3.9958 | 0.36248 | 4.568% | 0.01025 | 0.0097426 | 3078.0386 | 0.58515 | 2859.7845 | 217.6689 | 3090.397 | 0 | 0 | 3090.397 | 4.753e-05%
2026 | 390 | 390-18 | Tier-1 | Non-HFTD---2 | 5--3 | 3.9404 | 129 | 100% | 318.8449 | 16.58% | 82.54% | 0.8771% | 2.617 | 0 | 0 | 2.617 | 0 | 2.4964 | 4.0708 | 0.61325 | 2.4964 | 4.0708 | 0.61325 | 2.6298 | 4.2883 | 0.61325 | 0.8208% | 0.10878 | 0.1034 | 2931.0773 | 106.6158 | 2119.5636 | 704.8979 | 3058.4114 | 0 | 0 | 3058.4114 | 8.63e-05%
2026 | GA1 | CB GA1 | Tier-1 | Non-HFTD---14 | 3--1 | 7.5047 | 189 | 100% | 7.2576 | 27.71% | 0% | 72.29% | 0.099541 | 0 | 0 | 0.099541 | 0 | 0.094955 | 7.7531 | 0.012247 | 0.094955 | 7.7531 | 0.012247 | 0.10003 | 8.1673 | 0.012247 | 1.372% | 0.021919 | 0.020834 | 331.1033 | 2.6119 | 98.6514 | 229.84 | 343.5687 | 0 | 0 | 343.5687 | 3.282e-06%
2026 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 5.0473 | 319 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 67.7486 | 5.2144 | 12.9927 | 67.7486 | 5.2144 | 12.9927 | 71.3684 | 5.493 | 12.9927 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2026 | 473 | 473-36R | Tier-1 | Non-HFTD---1 | 5--4 | 14.9443 | 562 | 100% | 1339.2067 | 0.8137% | 98.49% | 0.6935% | 0.53941 | 0 | 0 | 0.53941 | 0 | 0.51456 | 15.4388 | 0.033329 | 0.51456 | 15.4388 | 0.033329 | 0.54206 | 16.2638 | 0.033329 | 0.04028% | 0.11477 | 0.10909 | 11668.3486 | 17.7885 | 10476.9993 | 1173.5608 | 12271.0665 | 0 | 0 | 12271.0665 | 1.779e-05%
2026 | HC4 | CB HC4 | Tier-1 | Non-HFTD---8 | 3--2 | 6.4726 | 321 | 100% | 33.1006 | 83.29% | 0% | 16.71% | 1.3646 | 0 | 0 | 1.3646 | 0 | 1.3018 | 6.6868 | 0.19468 | 1.3018 | 6.6868 | 0.19468 | 1.3713 | 7.044 | 0.19468 | 4.123% | 0.021599 | 0.02053 | 1532.5221 | 272.5227 | 181.5019 | 1078.4974 | 1545.8612 | 0 | 0 | 1545.8612 | 4.5e-05%
2026 | 555 | 555-2F | Tier-1 | Non-HFTD---17 | 1--2 | 0.42273 | 2 | 100% | 0.84765 | 38.63% | 0% | 61.37% | 0.016208 | 0 | 0 | 0.016208 | 0 | 0.015461 | 0.43672 | 0.035403 | 0.015461 | 0.43672 | 0.035403 | 0.016287 | 0.46005 | 0.035403 | 1.912% | 0.0015912 | 0.0015124 | 532.7136 | 32.3462 | 37.5358 | 462.8316 | 549.7399 | 0 | 0 | 549.7399 | 5.345e-07%
2026 | 281 | CB 281 | Tier-2 | Tier-2---16 | 4--3 | 6.8986 | 157 | 100% | 131.3229 | 1.145% | 96.36% | 2.498% | 0.07445 | 0 | 0 | 0.07445 | 0 | 0.07102 | 7.1269 | 0.009965 | 0.07102 | 7.1269 | 0.009965 | 0.074814 | 7.5077 | 0.009965 | 0.05669% | 0.046838 | 0.04452 | 2803.7555 | 3.8846 | 2517.4341 | 282.4368 | 2948.0968 | 0 | 0 | 2948.0968 | 2.455e-06%
2026 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | 4--5 | 7.0648 | 1685 | 100% | 4233.8665 | 96.93% | 2.943% | 0.1312% | 203.133 | 0 | 0 | 203.133 | 0 | 193.7751 | 7.2986 | 26.5497 | 193.7751 | 7.2986 | 26.5497 | 204.1288 | 7.6885 | 26.5497 | 4.798% | 0.080233 | 0.076262 | 52769.5087 | 8342.6927 | 1399.583 | 43027.233 | 52853.9991 | 0 | 0 | 52853.9991 | 0.006699%
2026 | MK1 | CB MK1 | Tier-1 | Non-HFTD---14 | 3--1 | 6.0093 | 122 | 100% | 7.4473 | 44.14% | 0% | 55.86% | 0.16271 | 0 | 0 | 0.16271 | 0 | 0.15522 | 6.2081 | 0.025002 | 0.15522 | 6.2081 | 0.025002 | 0.16351 | 6.5398 | 0.025002 | 2.185% | 0.016865 | 0.01603 | 441.5759 | 36.2896 | 78.2242 | 327.062 | 454.4219 | 0 | 0 | 454.4219 | 5.366e-06%
2026 | 532 | 532-1293F | Tier-1 | Non-HFTD---17 | 1--2 | 0.79053 | 19 | 100% | 1.3366 | 55.6% | 0% | 44.4% | 0.036789 | 0 | 0 | 0.036789 | 0 | 0.035094 | 0.8167 | 0.042971 | 0.035094 | 0.8167 | 0.042971 | 0.036969 | 0.86033 | 0.042971 | 2.752% | 0.0023122 | 0.0021977 | 578.0789 | 32.7375 | 145.1444 | 400.197 | 591.4446 | 0 | 0 | 591.4446 | 1.213e-06%
2026 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 7.806 | 514 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 786.9145 | 8.0644 | 97.5793 | 786.9145 | 8.0644 | 97.5793 | 828.9604 | 8.4953 | 97.5793 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2026 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 4.7979 | 602 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 109.4668 | 4.9567 | 22.0848 | 109.4668 | 4.9567 | 22.0848 | 115.3157 | 5.2215 | 22.0848 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2026 | VO1 | CB VO1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.214 | 26 | 100% | 1.1072 | 22.13% | 0% | 77.87% | 0.012131 | 0 | 0 | 0.012131 | 0 | 0.011572 | 1.2542 | 0.0092265 | 0.011572 | 1.2542 | 0.0092265 | 0.01219 | 1.3212 | 0.0092265 | 1.096% | 0.003819 | 0.00363 | 289.9083 | 0.16986 | 84.6753 | 205.0631 | 301.6643 | 0 | 0 | 301.6643 | 4e-07%
2026 | WA4 | CB WA4 | Tier-1 | Non-HFTD---10 | 3--2 | 7.4043 | 239 | 100% | 23.9832 | 78.04% | 0% | 21.96% | 0.92645 | 0 | 0 | 0.92645 | 0 | 0.88377 | 7.6494 | 0.11554 | 0.88377 | 7.6494 | 0.11554 | 0.931 | 8.0581 | 0.11554 | 3.863% | 0.022554 | 0.021438 | 1063.3699 | 52.777 | 527.6231 | 482.9698 | 1075.5315 | 0 | 0 | 1075.5315 | 3.055e-05%
2026 | 299 | 299-1011 | Tier-1 | Non-HFTD---5 | 2--3 | 4.203 | 102 | 100% | 54.9991 | 94.1% | 0% | 5.9% | 2.5618 | 0 | 0 | 2.5618 | 0 | 2.4438 | 4.3421 | 0.56282 | 2.4438 | 4.3421 | 0.56282 | 2.5744 | 4.5741 | 0.56282 | 4.658% | 0.013194 | 0.012541 | 4168.5545 | 546.6465 | 589.0831 | 3032.8249 | 4181.3634 | 0 | 0 | 4181.3634 | 8.448e-05%
2026 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.58561 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 4.0459 | 0.60499 | 6.6877 | 4.0459 | 0.60499 | 6.6877 | 4.2621 | 0.63731 | 6.6877 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2026 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 5.7333 | 62 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 248.9663 | 5.923 | 42.0335 | 248.9663 | 5.923 | 42.0335 | 262.269 | 6.2395 | 42.0335 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2026 | 700 | 700-255 | Tier-1 | Non-HFTD---9 | 2--2 | 1.2451 | 22 | 100% | 16.4031 | 90.17% | 3.905% | 5.929% | 0.7321 | 0 | 0 | 0.7321 | 0 | 0.69837 | 1.2863 | 0.54293 | 0.69837 | 1.2863 | 0.54293 | 0.73569 | 1.355 | 0.54293 | 4.463% | 0.010214 | 0.009708 | 1606.0068 | 234.45 | 79.4931 | 1292.0638 | 1614.2322 | 0 | 0 | 1614.2322 | 2.414e-05%
2026 | 321 | 321-646 | Tier-1 | Non-HFTD---18 | 2--1 | 1.9246 | 24 | 100% | 2.1274 | 32.02% | 0% | 67.98% | 0.033717 | 0 | 0 | 0.033717 | 0 | 0.032164 | 1.9883 | 0.016177 | 0.032164 | 1.9883 | 0.016177 | 0.033882 | 2.0945 | 0.016177 | 1.585% | 0.0057906 | 0.005504 | 367.3897 | 7.7909 | 93.4102 | 266.1885 | 380.3966 | 0 | 0 | 380.3966 | 1.112e-06%
2026 | 740 | CB 740 | Tier-1 | Non-HFTD---10 | 4--2 | 12.6747 | 722 | 100% | 25.6721 | 66.02% | 0% | 33.98% | 0.839 | 0 | 0 | 0.839 | 0 | 0.80035 | 13.0941 | 0.061123 | 0.80035 | 13.0941 | 0.061123 | 0.84311 | 13.7937 | 0.061123 | 3.268% | 0.034483 | 0.032776 | 744.476 | 0.22301 | 514.3039 | 229.9491 | 757.6491 | 0 | 0 | 757.6491 | 2.767e-05%
2026 | 308 | 308-486AE | Tier-2 | Tier-2---16 | 4--3 | 3.6318 | 154 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.19428 | 0 | 0 | 0.19428 | 0 | 0.18533 | 3.752 | 0.049396 | 0.18533 | 3.752 | 0.049396 | 0.19524 | 3.9524 | 0.049396 | 0.118% | 0.040279 | 0.038285 | 4088.4689 | 19.0997 | 3634.8848 | 434.4844 | 4296.3129 | 0 | 0 | 4296.3129 | 6.407e-06%
2026 | SW4 | CB SW4 | Tier-1 | Non-HFTD---16 | 2--1 | 3.3697 | 89 | 100% | 2.7806 | 34.41% | 0% | 65.59% | 0.047357 | 0 | 0 | 0.047357 | 0 | 0.045175 | 3.4812 | 0.012977 | 0.045175 | 3.4812 | 0.012977 | 0.047589 | 3.6672 | 0.012977 | 1.703% | 0.0083328 | 0.0079203 | 333.6959 | 7.2394 | 91.3226 | 235.1339 | 345.095 | 0 | 0 | 345.095 | 1.562e-06%
2026 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 2.1343 | 23 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 34.2346 | 2.2049 | 15.5267 | 34.2346 | 2.2049 | 15.5267 | 36.0638 | 2.3227 | 15.5267 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2026 | 166 | 166-463F | Tier-1 | Non-HFTD---19 | 1--1 | 0.081818 | 8 | 100% | 0.15952 | 10.72% | 0% | 89.28% | 0.0008462 | 0 | 0 | 0.0008462 | 0 | 0.00080722 | 0.084526 | 0.0095499 | 0.00080722 | 0.084526 | 0.0095499 | 0.00085035 | 0.089042 | 0.0095499 | 0.5305% | 0.0003874 | 0.00036822 | 411.7579 | 0.27663 | 77.5231 | 333.9581 | 430.9033 | 0 | 0 | 430.9033 | 2.79e-08%
2026 | BK1 | CB BK1 | Tier-1 | Non-HFTD---8 | 3--3 | 3.8556 | 133 | 100% | 44.2018 | 7.123% | 86.74% | 6.139% | 0.15584 | 0 | 0 | 0.15584 | 0 | 0.14866 | 3.9832 | 0.037322 | 0.14866 | 3.9832 | 0.037322 | 0.1566 | 4.1961 | 0.037322 | 0.3526% | 0.021968 | 0.02088 | 2012.1178 | 13.6327 | 1683.8934 | 314.5917 | 2109.4411 | 0 | 0 | 2109.4411 | 5.139e-06%
2026 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 1.5403 | 228 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 38.6279 | 1.5913 | 24.2745 | 38.6279 | 1.5913 | 24.2745 | 40.6918 | 1.6763 | 24.2745 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2026 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 1.0739 | 170 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 9.6013 | 1.1094 | 8.6543 | 9.6013 | 1.1094 | 8.6543 | 10.1143 | 1.1687 | 8.6543 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2026 | 381 | 381-451F | Tier-1 | Non-HFTD---10 | 3--2 | 6.7813 | 160 | 100% | 23.3181 | 88.11% | 0% | 11.89% | 1.017 | 0 | 0 | 1.017 | 0 | 0.97017 | 7.0057 | 0.13848 | 0.97017 | 7.0057 | 0.13848 | 1.022 | 7.38 | 0.13848 | 4.362% | 0.018659 | 0.017735 | 1249.6956 | 131.9022 | 309.5549 | 808.2386 | 1257.4325 | 0 | 0 | 1257.4325 | 3.354e-05%
2026 | WA3 | CB WA3 | Tier-1 | Non-HFTD---8 | 4--2 | 13.982 | 461 | 100% | 27.563 | 70.26% | 0% | 29.74% | 0.95857 | 0 | 0 | 0.95857 | 0 | 0.91441 | 14.4448 | 0.063304 | 0.91441 | 14.4448 | 0.063304 | 0.96327 | 15.2166 | 0.063304 | 3.478% | 0.039294 | 0.037349 | 701.463 | 20.3909 | 425.071 | 256.0011 | 712.3281 | 0 | 0 | 712.3281 | 3.161e-05%
2026 | 821 | CB 821 | Tier-1 | Non-HFTD---8 | 4--2 | 11.9876 | 611 | 100% | 39.8764 | 81.44% | 0% | 18.56% | 1.6076 | 0 | 0 | 1.6076 | 0 | 1.5336 | 12.3844 | 0.12383 | 1.5336 | 12.3844 | 0.12383 | 1.6155 | 13.0461 | 0.12383 | 4.032% | 0.03208 | 0.030492 | 1243.0135 | 29.5845 | 853.3576 | 360.0714 | 1255.025 | 0 | 0 | 1255.025 | 5.301e-05%
2026 | 454 | 454-49F | Tier-2 | Tier-2---13 | 4--3 | 1.5199 | 92 | 100% | 292.9743 | 76.06% | 23.59% | 0.3558% | 11.0299 | 0 | 0 | 11.0299 | 0 | 10.5217 | 1.5702 | 6.7011 | 10.5217 | 1.5702 | 6.7011 | 11.0839 | 1.6541 | 6.7011 | 3.765% | 0.077203 | 0.073382 | 3794.8464 | 847.9473 | 816.929 | 2129.9701 | 3842.1656 | 0 | 0 | 3842.1656 | 0.0003637%
2026 | 196 | 196-43F | Tier-2 | Tier-2---17 | 3--4 | 0.2589 | 52 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.23855 | 0 | 0 | 0.23855 | 0 | 0.22756 | 0.26747 | 0.8508 | 0.22756 | 0.26747 | 0.8508 | 0.23972 | 0.28176 | 0.8508 | 0.2544% | 0.017356 | 0.016497 | 5402.3367 | 48.5246 | 4687.8466 | 665.9656 | 5669.2187 | 0 | 0 | 5669.2187 | 7.867e-06%
2026 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 8.3178 | 81 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 284.1236 | 8.593 | 33.0644 | 284.1236 | 8.593 | 33.0644 | 299.3047 | 9.0522 | 33.0644 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2026 | 243 | CB 243 | Tier-2 | Tier-2---14 | 4--4 | 3.2755 | 98 | 100% | 284.2808 | 92.1% | 7.127% | 0.7733% | 12.9602 | 0 | 0 | 12.9602 | 0 | 12.3631 | 3.3839 | 3.6535 | 12.3631 | 3.3839 | 3.6535 | 13.0237 | 3.5647 | 3.6535 | 4.559% | 0.039288 | 0.037343 | 7235.7813 | 1297.464 | 840.9216 | 5097.3957 | 7265.5523 | 0 | 0 | 7265.5523 | 0.0004274%
2026 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 12.3028 | 1609 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 484.7261 | 12.71 | 38.1375 | 484.7261 | 12.71 | 38.1375 | 510.6256 | 13.3891 | 38.1375 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2026 | 558 | 558-301R | Tier-1 | Non-HFTD---1 | 2--5 | 2.4663 | 84 | 100% | 286.6551 | 99.35% | 0% | 0.6493% | 14.0973 | 0 | 0 | 14.0973 | 0 | 13.4479 | 2.548 | 5.2779 | 13.4479 | 2.548 | 5.2779 | 14.1664 | 2.6841 | 5.2779 | 4.918% | 0.010369 | 0.0098561 | 27644.3313 | 6740.2704 | 35.1226 | 20868.9383 | 27653.6787 | 0 | 0 | 27653.6787 | 0.0004649%
2026 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 19.9074 | 1772 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1227.409 | 20.5662 | 59.681 | 1227.409 | 20.5662 | 59.681 | 1292.9912 | 21.665 | 59.681 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2026 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 3.397 | 63 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 12.3641 | 3.5094 | 3.5231 | 12.3641 | 3.5094 | 3.5231 | 13.0247 | 3.6969 | 3.5231 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2026 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.47178 | 3 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 5.3951 | 0.48739 | 11.0693 | 5.3951 | 0.48739 | 11.0693 | 5.6834 | 0.51344 | 11.0693 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2026 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 1.6544 | 27 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 243.3088 | 1.7091 | 142.3605 | 243.3088 | 1.7091 | 142.3605 | 256.3092 | 1.8004 | 142.3605 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2026 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 22.0576 | 2114 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 162.4058 | 22.7875 | 7.127 | 162.4058 | 22.7875 | 7.127 | 171.0834 | 24.0051 | 7.127 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2026 | 94 | 94-16F | Tier-1 | Non-HFTD---15 | 2--2 | 2.6851 | 41 | 100% | 4.4816 | 61.07% | 0% | 38.93% | 0.13547 | 0 | 0 | 0.13547 | 0 | 0.12923 | 2.7739 | 0.046587 | 0.12923 | 2.7739 | 0.046587 | 0.13613 | 2.9221 | 0.046587 | 3.023% | 0.007584 | 0.0072086 | 590.9306 | 44.9122 | 129.254 | 416.7645 | 602.9122 | 0 | 0 | 602.9122 | 4.467e-06%
2026 | 511 | 511-831 | Tier-1 | Non-HFTD---5 | 2--3 | 0.15682 | 10 | 100% | 45.7736 | 11.2% | 88.5% | 0.2943% | 0.25387 | 0 | 0 | 0.25387 | 0 | 0.24217 | 0.16201 | 1.4948 | 0.24217 | 0.16201 | 1.4948 | 0.25511 | 0.17066 | 1.4948 | 0.5546% | 0.011273 | 0.010715 | 4060.4617 | 56.9583 | 3419.2148 | 584.2885 | 4248.229 | 0 | 0 | 4248.229 | 8.372e-06%
2026 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 10.1674 | 862 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 262.0699 | 10.5039 | 24.9499 | 262.0699 | 10.5039 | 24.9499 | 276.0727 | 11.0651 | 24.9499 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2026 | 571 | 571-49F | Tier-1 | Non-HFTD---11 | 2--2 | 4.1737 | 180 | 100% | 14.8937 | 75.79% | 0% | 24.21% | 0.55872 | 0 | 0 | 0.55872 | 0 | 0.53298 | 4.3118 | 0.12361 | 0.53298 | 4.3118 | 0.12361 | 0.56146 | 4.5422 | 0.12361 | 3.751% | 0.013087 | 0.01244 | 1138.0185 | 7.555 | 852.2014 | 278.2621 | 1152.3692 | 0 | 0 | 1152.3692 | 1.842e-05%
2026 | 161 | 161-610R | Tier-1 | Non-HFTD---8 | 4--2 | 15.3086 | 353 | 100% | 29.9374 | 67.56% | 0% | 32.44% | 1.0012 | 0 | 0 | 1.0012 | 0 | 0.95505 | 15.8152 | 0.060388 | 0.95505 | 15.8152 | 0.060388 | 1.0061 | 16.6602 | 0.060388 | 3.344% | 0.041579 | 0.039521 | 720.0082 | 5.3968 | 475.6596 | 238.9517 | 732.172 | 0 | 0 | 732.172 | 3.302e-05%
2026 | PB1 | CB PB1 | Tier-1 | Non-HFTD---3 | 4--3 | 6.9699 | 84 | 100% | 137.6037 | 3.283% | 92.37% | 4.346% | 0.2236 | 0 | 0 | 0.2236 | 0 | 0.21329 | 7.2006 | 0.029622 | 0.21329 | 7.2006 | 0.029622 | 0.22469 | 7.5853 | 0.029622 | 0.1625% | 0.031616 | 0.030051 | 4352.3713 | 4.764 | 3790.0764 | 557.531 | 4571.5929 | 0 | 0 | 4571.5929 | 7.373e-06%
2026 | 257 | 257-31AE | Tier-1 | Non-HFTD---14 | 2--1 | 4.2349 | 159 | 100% | 5.7719 | 39.09% | 0% | 60.91% | 0.11168 | 0 | 0 | 0.11168 | 0 | 0.10653 | 4.375 | 0.024351 | 0.10653 | 4.375 | 0.024351 | 0.11223 | 4.6088 | 0.024351 | 1.935% | 0.012621 | 0.011996 | 457.3241 | 0.20961 | 204.0654 | 253.0491 | 471.8311 | 0 | 0 | 471.8311 | 3.683e-06%
2026 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 6.7335 | 568 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 687.0628 | 6.9563 | 98.7681 | 687.0628 | 6.9563 | 98.7681 | 723.7735 | 7.328 | 98.7681 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2026 | 137 | CB 137 | Tier-1 | Non-HFTD---18 | 1--1 | 0.9422 | 16 | 100% | 0.70761 | 22.42% | 0% | 77.58% | 0.0078535 | 0 | 0 | 0.0078535 | 0 | 0.0074917 | 0.97339 | 0.0076966 | 0.0074917 | 0.97339 | 0.0076966 | 0.007892 | 1.0254 | 0.0076966 | 1.11% | 0.0024496 | 0.0023283 | 288.869 | 0.16863 | 85.1261 | 203.5742 | 300.5396 | 0 | 0 | 300.5396 | 2.59e-07%
2026 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 0.0058712 | 6 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.081643 | 0.0060655 | 13.4602 | 0.081643 | 0.0060655 | 13.4602 | 0.086005 | 0.0063896 | 13.4602 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2026 | 120 | 120-360F | Tier-1 | Non-HFTD---9 | 2--3 | 0.90587 | 65 | 100% | 24.5458 | 1.164% | 95.41% | 3.43% | 0.014138 | 0 | 0 | 0.014138 | 0 | 0.013487 | 0.93585 | 0.014412 | 0.013487 | 0.93585 | 0.014412 | 0.014208 | 0.98586 | 0.014412 | 0.0576% | 0.010414 | 0.0098981 | 2357.0882 | 2.378 | 2024.3177 | 330.3924 | 2478.4119 | 0 | 0 | 2478.4119 | 4.662e-07%
2026 | WA1 | CB WA1 | Tier-1 | Non-HFTD---8 | 3--2 | 7.9261 | 417 | 100% | 35.576 | 87.53% | 0% | 12.47% | 1.5414 | 0 | 0 | 1.5414 | 0 | 1.4704 | 8.1884 | 0.17957 | 1.4704 | 8.1884 | 0.17957 | 1.5489 | 8.6259 | 0.17957 | 4.333% | 0.024123 | 0.022929 | 1474.761 | 154.3788 | 361.2267 | 959.1555 | 1484.3394 | 0 | 0 | 1484.3394 | 5.083e-05%
2026 | 1152 | CB 1152 | Tier-1 | Non-HFTD---17 | 1--2 | 0.225 | 0 | 100% | 1.2601 | 88.07% | 0% | 11.93% | 0.054936 | 0 | 0 | 0.054936 | 0 | 0.052405 | 0.23245 | 0.22545 | 0.052405 | 0.23245 | 0.22545 | 0.055205 | 0.24487 | 0.22545 | 4.36% | 0.0009632 | 0.00091552 | 1308.2728 | 166.1488 | 97.0862 | 1045.0378 | 1316.4 | 0 | 0 | 1316.4 | 1.812e-06%
2026 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 24.1038 | 1376 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 739.2025 | 24.9015 | 29.685 | 739.2025 | 24.9015 | 29.685 | 778.6991 | 26.232 | 29.685 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2026 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 6.7626 | 86 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 139.1767 | 6.9863 | 19.9212 | 139.1767 | 6.9863 | 19.9212 | 146.6131 | 7.3596 | 19.9212 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2026 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.56254 | 0 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.8521 | 0.58116 | 10.0697 | 5.8521 | 0.58116 | 10.0697 | 6.1647 | 0.61221 | 10.0697 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2026 | 948 | 948-5R | Tier-2 | Tier-2---21 | 1--2 | 0.64563 | 19 | 100% | 3.6494 | 90.16% | 0% | 9.838% | 0.16287 | 0 | 0 | 0.16287 | 0 | 0.15537 | 0.667 | 0.23294 | 0.15537 | 0.667 | 0.23294 | 0.16367 | 0.70264 | 0.23294 | 4.463% | 0.0023872 | 0.002269 | 1528.7338 | 203.4062 | 386.7322 | 938.5955 | 1536.5665 | 0 | 0 | 1536.5665 | 5.371e-06%
2026 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 4.5924 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 450.8352 | 4.7444 | 95.0255 | 450.8352 | 4.7444 | 95.0255 | 474.924 | 4.9979 | 95.0255 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2026 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 4.4941 | 255 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 430.6267 | 4.6428 | 92.7506 | 430.6267 | 4.6428 | 92.7506 | 453.6357 | 4.8909 | 92.7506 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2026 | 486 | 486-61R | Tier-1 | Non-HFTD---1 | 4--4 | 8.0996 | 279 | 100% | 415.5682 | 98.69% | 0% | 1.309% | 20.3013 | 0 | 0 | 20.3013 | 0 | 19.366 | 8.3676 | 2.3144 | 19.366 | 8.3676 | 2.3144 | 20.4008 | 8.8147 | 2.3144 | 4.885% | 0.031655 | 0.030088 | 13128.0422 | 2294.0601 | 163.567 | 10670.4151 | 13136.9945 | 0 | 0 | 13136.9945 | 0.0006695%
2026 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 8.7188 | 72 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 334.0803 | 9.0073 | 37.09 | 334.0803 | 9.0073 | 37.09 | 351.9307 | 9.4886 | 37.09 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2026 | 116 | 116-12R | Tier-1 | Non-HFTD---6 | 3--3 | 3.2824 | 68 | 100% | 54.5549 | 5.544% | 89.94% | 4.52% | 0.14973 | 0 | 0 | 0.14973 | 0 | 0.14283 | 3.391 | 0.04212 | 0.14283 | 3.391 | 0.04212 | 0.15046 | 3.5722 | 0.04212 | 0.2745% | 0.024461 | 0.02325 | 2230.262 | 3.7698 | 1966.9777 | 259.5146 | 2339.9695 | 0 | 0 | 2339.9695 | 4.937e-06%
2026 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 21.0708 | 1905 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 384.6902 | 21.7681 | 17.6722 | 384.6902 | 21.7681 | 17.6722 | 405.2447 | 22.9312 | 17.6722 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2026 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.41228 | 17 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 14.1762 | 0.42593 | 33.2831 | 14.1762 | 0.42593 | 33.2831 | 14.9337 | 0.44869 | 33.2831 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2026 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 8.3421 | 383 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1325.1737 | 8.6181 | 153.766 | 1325.1737 | 8.6181 | 153.766 | 1395.9796 | 9.0786 | 153.766 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2026 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 13.3513 | 1654 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 421.536 | 13.7931 | 30.5613 | 421.536 | 13.7931 | 30.5613 | 444.0593 | 14.5301 | 30.5613 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2026 | 68 | CB 68 | Tier-1 | Non-HFTD---4 | 3--4 | 1.521 | 13 | 100% | 125.6028 | 97.63% | 1.574% | 0.7918% | 6.0702 | 0 | 0 | 6.0702 | 0 | 5.7906 | 1.5714 | 3.6851 | 5.7906 | 1.5714 | 3.6851 | 6.1 | 1.6553 | 3.6851 | 4.833% | 0.015716 | 0.014938 | 7992.034 | 1382.4541 | 1171.7344 | 5437.8454 | 8001.8815 | 0 | 0 | 8001.8815 | 0.0002002%
2026 | 306 | CB 306 | Tier-1 | Non-HFTD---1 | 4--4 | 1.2839 | 275 | 100% | 737.4997 | 97.09% | 2.802% | 0.1119% | 35.4424 | 0 | 0 | 35.4424 | 0 | 33.8097 | 1.3264 | 25.4907 | 33.8097 | 1.3264 | 25.4907 | 35.6162 | 1.3972 | 25.4907 | 4.806% | 0.057753 | 0.054894 | 12769.9388 | 2020.535 | 320.1958 | 10429.208 | 12789.3181 | 0 | 0 | 12789.3181 | 0.001169%
2026 | OS5 | CB OS5 | Tier-1 | Non-HFTD---18 | 1--1 | 1.275 | 40 | 100% | 1.4382 | 31.82% | 0% | 68.18% | 0.022652 | 0 | 0 | 0.022652 | 0 | 0.021608 | 1.3172 | 0.016404 | 0.021608 | 1.3172 | 0.016404 | 0.022763 | 1.3876 | 0.016404 | 1.575% | 0.0036598 | 0.0034786 | 392.9844 | 0.52405 | 147.391 | 245.0693 | 406.9386 | 0 | 0 | 406.9386 | 7.47e-07%
2026 | 394 | 394-422F | Tier-1 | Non-HFTD---2 | 5--3 | 1.6971 | 43 | 100% | 314.1506 | 0.33% | 99.33% | 0.3425% | 0.051318 | 0 | 0 | 0.051318 | 0 | 0.048954 | 1.7533 | 0.027921 | 0.048954 | 1.7533 | 0.027921 | 0.05157 | 1.847 | 0.027921 | 0.01634% | 0.095311 | 0.090593 | 3296.0513 | 5.5188 | 2895.8033 | 394.7292 | 3467.1361 | 0 | 0 | 3467.1361 | 1.692e-06%
2026 | 171 | 171-708R | Tier-1 | Non-HFTD---3 | 4--3 | 12.6172 | 98 | 100% | 144.3815 | 64.32% | 29.9% | 5.783% | 4.597 | 0 | 0 | 4.597 | 0 | 4.3852 | 13.0347 | 0.33642 | 4.3852 | 13.0347 | 0.33642 | 4.6195 | 13.7312 | 0.33642 | 3.184% | 0.084326 | 0.080152 | 1712.186 | 173.3767 | 499.0152 | 1039.7942 | 1743.9994 | 0 | 0 | 1743.9994 | 0.0001516%
2026 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2.1411 | 4 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 20.4262 | 2.2119 | 9.2346 | 20.4262 | 2.2119 | 9.2346 | 21.5176 | 2.3301 | 9.2346 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2026 | 431 | 431-474 | Tier-1 | Non-HFTD---15 | 2--1 | 1.7021 | 18 | 100% | 2.429 | 35.21% | 0% | 64.79% | 0.04233 | 0 | 0 | 0.04233 | 0 | 0.04038 | 1.7584 | 0.022964 | 0.04038 | 1.7584 | 0.022964 | 0.042538 | 1.8524 | 0.022964 | 1.743% | 0.0053256 | 0.005062 | 456.099 | 0.22237 | 187.4203 | 268.4563 | 471.4893 | 0 | 0 | 471.4893 | 1.396e-06%
2026 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 2.4735 | 122 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 204.4821 | 2.5554 | 80.0202 | 204.4821 | 2.5554 | 80.0202 | 215.4079 | 2.6919 | 80.0202 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2026 | 476 | 476-6F | Tier-1 | Non-HFTD---10 | 5--1 | 0.074053 | 11 | 100% | 18.587 | 5.339% | 94.33% | 0.3325% | 0.049124 | 0 | 0 | 0.049124 | 0 | 0.046861 | 0.076504 | 0.61253 | 0.046861 | 0.076504 | 0.61253 | 0.049365 | 0.080591 | 0.61253 | 0.2643% | 0.15628 | 0.14854 | 118.9364 | 1.3234 | 95.4058 | 22.2073 | 124.7997 | 0 | 0 | 124.7997 | 1.62e-06%
2026 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 1.7031 | 141 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.4459 | 1.7594 | 2.5269 | 4.4459 | 1.7594 | 2.5269 | 4.6834 | 1.8534 | 2.5269 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2026 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 1.8653 | 473 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 18.2584 | 1.9271 | 9.4747 | 18.2584 | 1.9271 | 9.4747 | 19.234 | 2.03 | 9.4747 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2026 | BF1 | CB BF1 | Tier-1 | Non-HFTD---9 | 2--3 | 1.6113 | 1 | 100% | 20.8946 | 91.56% | 0% | 8.439% | 0.947 | 0 | 0 | 0.947 | 0 | 0.90337 | 1.6646 | 0.54268 | 0.90337 | 1.6646 | 0.54268 | 0.95164 | 1.7536 | 0.54268 | 4.532% | 0.0060496 | 0.0057501 | 3453.8829 | 552.2417 | 48.3246 | 2853.3166 | 3469.0626 | 0 | 0 | 3469.0626 | 3.123e-05%
2026 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 3.6322 | 118 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.5364 | 3.7524 | 1.2089 | 4.5364 | 3.7524 | 1.2089 | 4.7787 | 3.9529 | 1.2089 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2026 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 16.0985 | 1221 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 406.782 | 16.6312 | 24.4589 | 406.782 | 16.6312 | 24.4589 | 428.5169 | 17.5199 | 24.4589 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2026 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 9.1409 | 907 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 160.2048 | 9.4434 | 16.9647 | 160.2048 | 9.4434 | 16.9647 | 168.7647 | 9.948 | 16.9647 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2026 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 17.9266 | 1368 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1926.6067 | 18.5198 | 104.0295 | 1926.6067 | 18.5198 | 104.0295 | 2029.5479 | 19.5093 | 104.0295 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2026 | 297 | 297-828AE | Tier-1 | Non-HFTD---5 | 2--4 | 1.7713 | 112 | 100% | 51.9776 | 97.72% | 0% | 2.278% | 2.5143 | 0 | 0 | 2.5143 | 0 | 2.3984 | 1.8299 | 1.3107 | 2.3984 | 1.8299 | 1.3107 | 2.5266 | 1.9277 | 1.3107 | 4.837% | 0.0062854 | 0.0059743 | 8269.5727 | 1759.1338 | 61.0431 | 6449.3958 | 8279.3842 | 0 | 0 | 8279.3842 | 8.291e-05%
2026 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 10.907 | 490 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 431.684 | 11.2679 | 38.3109 | 431.684 | 11.2679 | 38.3109 | 454.7494 | 11.87 | 38.3109 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2026 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 3.6616 | 65 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.981 | 3.7827 | 3.1673 | 11.981 | 3.7827 | 3.1673 | 12.6212 | 3.9849 | 3.1673 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2026 | 1076 | CB 1076 | Tier-1 | Non-HFTD---9 | 2--3 | 3.9479 | 154 | 100% | 20.7787 | 85.56% | 0% | 14.44% | 0.88007 | 0 | 0 | 0.88007 | 0 | 0.83952 | 4.0785 | 0.20584 | 0.83952 | 4.0785 | 0.20584 | 0.88438 | 4.2964 | 0.20584 | 4.235% | 0.011545 | 0.010974 | 1799.7403 | 1.5108 | 1555.3284 | 242.9011 | 1813.2706 | 0 | 0 | 1813.2706 | 2.902e-05%
2026 | CD4 | CB CD4 | Tier-1 | Non-HFTD---8 | 3--3 | 4.5362 | 259 | 100% | 39.5125 | 6.129% | 86.05% | 7.825% | 0.11988 | 0 | 0 | 0.11988 | 0 | 0.11436 | 4.6863 | 0.024402 | 0.11436 | 4.6863 | 0.024402 | 0.12047 | 4.9367 | 0.024402 | 0.3034% | 0.022929 | 0.021794 | 1723.2234 | 10.1387 | 1416.6051 | 296.4796 | 1807.4647 | 0 | 0 | 1807.4647 | 3.953e-06%
2026 | 412 | CB 412 | Tier-1 | Non-HFTD---1 | 4--5 | 17.7277 | 1039 | 100% | 1311.9921 | 88.37% | 10.81% | 0.8215% | 57.392 | 0 | 0 | 57.392 | 0 | 54.7481 | 18.3143 | 2.9894 | 54.7481 | 18.3143 | 2.9894 | 57.6734 | 19.2929 | 2.9894 | 4.374% | 0.071433 | 0.067897 | 18366.6483 | 2615.4927 | 2100.6109 | 13650.5447 | 18477.8687 | 0 | 0 | 18477.8687 | 0.001893%
2026 | 45 | 45-15AE | Tier-1 | Non-HFTD---11 | 1--3 | 0.56231 | 24 | 100% | 8.7551 | 92.94% | 0% | 7.056% | 0.4028 | 0 | 0 | 0.4028 | 0 | 0.38424 | 0.58092 | 0.66144 | 0.38424 | 0.58092 | 0.66144 | 0.40477 | 0.61196 | 0.66144 | 4.601% | 0.0022584 | 0.0021466 | 3876.685 | 65.548 | 3228.8334 | 582.3036 | 3890.931 | 0 | 0 | 3890.931 | 1.328e-05%
2026 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 0.80794 | 3 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 30.9346 | 0 | 0 | 30.9346 | 0 | 29.5095 | 0.83468 | 35.3543 | 29.5095 | 0.83468 | 35.3543 | 31.0862 | 0.87928 | 35.3543 | 4.945% | 0.0036434 | 0.0034631 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171700.5551 | 0 | 0 | 171700.5551 | 0.00102%
2026 | 795 | 795-816R | Tier-2 | Tier-2---13 | 4--4 | 6.4011 | 361 | 100% | 228.7654 | 4.756% | 93.08% | 2.167% | 0.53859 | 0 | 0 | 0.53859 | 0 | 0.51378 | 6.613 | 0.077693 | 0.51378 | 6.613 | 0.077693 | 0.54123 | 6.9663 | 0.077693 | 0.2354% | 0.036491 | 0.034684 | 6269.16 | 14.3219 | 5608.3339 | 646.5042 | 6580.116 | 0 | 0 | 6580.116 | 1.776e-05%
2026 | 859 | 859-1064 | Tier-1 | Non-HFTD---7 | 2--3 | 4.2178 | 255 | 100% | 40.2522 | 93.55% | 0% | 6.452% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.7781 | 4.3573 | 0.40806 | 1.7781 | 4.3573 | 0.40806 | 1.8731 | 4.5902 | 0.40806 | 4.631% | 0.011569 | 0.010996 | 3479.3123 | 521.49 | 92.9503 | 2864.872 | 3491.0022 | 0 | 0 | 3491.0022 | 6.147e-05%
2026 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 9.5078 | 505 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 577.5146 | 9.8224 | 58.7956 | 577.5146 | 9.8224 | 58.7956 | 608.372 | 10.3472 | 58.7956 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2026 | 1173 | 1173-70 | Tier-1 | Non-HFTD---9 | 2--3 | 0.44863 | 4 | 100% | 15.3764 | 0.6778% | 97.23% | 2.096% | 0.0051591 | 0 | 0 | 0.0051591 | 0 | 0.0049215 | 0.46347 | 0.010619 | 0.0049215 | 0.46347 | 0.010619 | 0.0051844 | 0.48824 | 0.010619 | 0.03355% | 0.008697 | 0.0082665 | 1768.0079 | 1.6115 | 1488.7681 | 277.6283 | 1859.4579 | 0 | 0 | 1859.4579 | 1.701e-07%
2026 | 386 | CB 386 | Tier-2 | Tier-2---14 | 4--4 | 7.9203 | 582 | 100% | 266.4482 | 58.89% | 39.19% | 1.927% | 7.7666 | 0 | 0 | 7.7666 | 0 | 7.4088 | 8.1824 | 0.90546 | 7.4088 | 8.1824 | 0.90546 | 7.8047 | 8.6196 | 0.90546 | 2.915% | 0.037437 | 0.035584 | 7117.2424 | 561.1032 | 3326.6838 | 3229.4554 | 7269.6317 | 0 | 0 | 7269.6317 | 0.0002561%
2026 | 122 | CB 122 | Tier-1 | Non-HFTD---13 | 2--2 | 2.0557 | 0 | 100% | 8.11 | 77.73% | 0% | 22.27% | 0.31204 | 0 | 0 | 0.31204 | 0 | 0.29766 | 2.1237 | 0.14016 | 0.29766 | 2.1237 | 0.14016 | 0.31357 | 2.2372 | 0.14016 | 3.848% | 0.0070694 | 0.0067195 | 1147.1966 | 45.0636 | 638.2561 | 463.8769 | 1160.5021 | 0 | 0 | 1160.5021 | 1.029e-05%
2026 | 172 | 172-630R | Tier-1 | Non-HFTD---6 | 4--2 | 4.8346 | 15 | 100% | 66.3107 | 6.519% | 90.48% | 2.997% | 0.21398 | 0 | 0 | 0.21398 | 0 | 0.20413 | 4.9946 | 0.040869 | 0.20413 | 4.9946 | 0.040869 | 0.21503 | 5.2615 | 0.040869 | 0.3227% | 0.053137 | 0.050507 | 1247.9203 | 10.8427 | 1030.4852 | 206.5924 | 1308.6726 | 0 | 0 | 1308.6726 | 7.056e-06%
2026 | CS1 | CB CS1 | Tier-1 | Non-HFTD---14 | 3--1 | 6.2901 | 165 | 100% | 6.8922 | 38.03% | 0% | 61.97% | 0.12974 | 0 | 0 | 0.12974 | 0 | 0.12377 | 6.4983 | 0.019046 | 0.12377 | 6.4983 | 0.019046 | 0.13038 | 6.8455 | 0.019046 | 1.882% | 0.017311 | 0.016454 | 398.15 | 1.1079 | 168.1623 | 228.8798 | 410.9994 | 0 | 0 | 410.9994 | 4.278e-06%
2026 | 114 | 114-48 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0661 | 157 | 100% | 88.8606 | 4.08% | 91.67% | 4.249% | 0.17946 | 0 | 0 | 0.17946 | 0 | 0.17119 | 6.2668 | 0.027317 | 0.17119 | 6.2668 | 0.027317 | 0.18034 | 6.6017 | 0.027317 | 0.202% | 0.02752 | 0.026158 | 3228.8995 | 11.4775 | 2773.9851 | 443.4369 | 3390.1931 | 0 | 0 | 3390.1931 | 5.918e-06%
2026 | 114 | CB 114 | Tier-1 | Non-HFTD---7 | 2--3 | 1.6892 | 172 | 100% | 43.2481 | 88.83% | 8.106% | 3.062% | 1.9017 | 0 | 0 | 1.9017 | 0 | 1.8141 | 1.7451 | 1.0395 | 1.8141 | 1.7451 | 1.0395 | 1.911 | 1.8383 | 1.0395 | 4.397% | 0.013188 | 0.012535 | 3279.4498 | 356.1869 | 963.7932 | 1959.4698 | 3298.5242 | 0 | 0 | 3298.5242 | 6.271e-05%
2026 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 0.26853 | 62 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.9389 | 0.27742 | 6.9893 | 1.9389 | 0.27742 | 6.9893 | 2.0425 | 0.29224 | 6.9893 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2026 | 390 | 390-15 | Tier-1 | Non-HFTD---2 | 5--3 | 1.561 | 36 | 100% | 260.9963 | 0.6321% | 98.96% | 0.4064% | 0.081661 | 0 | 0 | 0.081661 | 0 | 0.077899 | 1.6126 | 0.048306 | 0.077899 | 1.6126 | 0.048306 | 0.082061 | 1.6988 | 0.048306 | 0.03129% | 0.099654 | 0.094722 | 2619.0141 | 6.4394 | 2346.7211 | 265.8535 | 2754.5446 | 0 | 0 | 2754.5446 | 2.693e-06%
2026 | 257 | 257-29AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.4854 | 75 | 100% | 2.2983 | 19.76% | 0% | 80.24% | 0.022484 | 0 | 0 | 0.022484 | 0 | 0.021448 | 2.5677 | 0.0083532 | 0.021448 | 2.5677 | 0.0083532 | 0.022594 | 2.7048 | 0.0083532 | 0.9783% | 0.006989 | 0.006643 | 328.8485 | 0.19854 | 88.9601 | 239.6899 | 342.5897 | 0 | 0 | 342.5897 | 7.414e-07%
2026 | 189 | CB 189 | Tier-1 | Non-HFTD---7 | 2--4 | 1.6267 | 68 | 100% | 36.5503 | 96.65% | 0% | 3.352% | 1.7486 | 0 | 0 | 1.7486 | 0 | 1.668 | 1.6806 | 0.99255 | 1.668 | 1.6806 | 0.99255 | 1.7572 | 1.7704 | 0.99255 | 4.784% | 0.0052996 | 0.0050373 | 6896.7976 | 807.5104 | 1754.8536 | 4334.4335 | 6908.8371 | 0 | 0 | 6908.8371 | 5.766e-05%
2026 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 13.4125 | 974 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 76.6538 | 13.8564 | 5.532 | 76.6538 | 13.8564 | 5.532 | 80.7496 | 14.5967 | 5.532 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2026 | 310 | 310-9R | Tier-1 | Non-HFTD---13 | 1--3 | 1.5318 | 84 | 100% | 7.8805 | 85.45% | 0% | 14.55% | 0.33331 | 0 | 0 | 0.33331 | 0 | 0.31796 | 1.5825 | 0.20092 | 0.31796 | 1.5825 | 0.20092 | 0.33495 | 1.6671 | 0.20092 | 4.23% | 0.0044784 | 0.0042567 | 1759.6775 | 1.0284 | 1521.6386 | 237.0105 | 1773.015 | 0 | 0 | 1773.015 | 1.099e-05%
2026 | 69 | CB 69 | Tier-1 | Non-HFTD---5 | 2--3 | 1.1767 | 12 | 100% | 50.7962 | 92.2% | 5.783% | 2.017% | 2.3183 | 0 | 0 | 2.3183 | 0 | 2.2115 | 1.2157 | 1.8191 | 2.2115 | 1.2157 | 1.8191 | 2.3297 | 1.2806 | 1.8191 | 4.564% | 0.011719 | 0.011139 | 4334.4449 | 720.874 | 567.5626 | 3046.0083 | 4352.0516 | 0 | 0 | 4352.0516 | 7.645e-05%
2026 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 6.1356 | 334 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 103.331 | 6.3387 | 16.3017 | 103.331 | 6.3387 | 16.3017 | 108.8522 | 6.6773 | 16.3017 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2026 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 2.0289 | 257 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 31.4944 | 2.0961 | 15.0253 | 31.4944 | 2.0961 | 15.0253 | 33.1772 | 2.2081 | 15.0253 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2026 | 242 | 242-1411F | Tier-1 | Non-HFTD---1 | 5--4 | 0.27213 | 21 | 100% | 861.0308 | 0.3297% | 99.65% | 0.02489% | 0.14053 | 0 | 0 | 0.14053 | 0 | 0.13405 | 0.28114 | 0.47682 | 0.13405 | 0.28114 | 0.47682 | 0.14122 | 0.29616 | 0.47682 | 0.01632% | 0.09372 | 0.08908 | 9187.308 | 16.4683 | 8354.5754 | 816.2643 | 9664.1858 | 0 | 0 | 9664.1858 | 4.634e-06%
2026 | CA2 | CB CA2 | Tier-1 | Non-HFTD---9 | 2--2 | 0.94321 | 19 | 100% | 20.4637 | 1.406% | 94.71% | 3.883% | 0.014245 | 0 | 0 | 0.014245 | 0 | 0.013589 | 0.97442 | 0.013946 | 0.013589 | 0.97442 | 0.013946 | 0.014315 | 1.0265 | 0.013946 | 0.06961% | 0.013315 | 0.012656 | 1536.8705 | 2.0039 | 1342.2543 | 192.6124 | 1615.7819 | 0 | 0 | 1615.7819 | 4.698e-07%
2026 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 29.2157 | 767 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 394.1517 | 30.1825 | 13.0589 | 394.1517 | 30.1825 | 13.0589 | 415.2118 | 31.7952 | 13.0589 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2026 | 488 | CB 488 | Tier-1 | Non-HFTD---15 | 1--2 | 1.7068 | 32 | 100% | 3.9951 | 71.83% | 0% | 28.17% | 0.14206 | 0 | 0 | 0.14206 | 0 | 0.13551 | 1.7633 | 0.076852 | 0.13551 | 1.7633 | 0.076852 | 0.14275 | 1.8575 | 0.076852 | 3.556% | 0.0047686 | 0.0045326 | 837.8017 | 0.17757 | 623.2495 | 214.3746 | 850.0916 | 0 | 0 | 850.0916 | 4.684e-06%
2026 | 56 | 56-669F | Tier-1 | Non-HFTD---4 | 2--4 | 0.57918 | 1 | 100% | 107.608 | 0.09989% | 99.43% | 0.4717% | 0.0053209 | 0 | 0 | 0.0053209 | 0 | 0.0050758 | 0.59834 | 0.0084831 | 0.0050758 | 0.59834 | 0.0084831 | 0.005347 | 0.63031 | 0.0084831 | 0.004945% | 0.012314 | 0.011705 | 8738.387 | 10.1815 | 7924.2222 | 803.9833 | 9193.0088 | 0 | 0 | 9193.0088 | 1.755e-07%
2026 | 308 | 308-485AE | Tier-2 | Tier-2---15 | 4--3 | 1.6722 | 57 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.217 | 0 | 0 | 0.217 | 0 | 0.207 | 1.7275 | 0.11982 | 0.207 | 1.7275 | 0.11982 | 0.21806 | 1.8198 | 0.11982 | 0.1374% | 0.034738 | 0.033018 | 4547.6785 | 25.2626 | 4047.4864 | 474.9295 | 4777.9399 | 0 | 0 | 4777.9399 | 7.156e-06%
2026 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.77126 | 73 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 37.005 | 0.79678 | 46.4431 | 37.005 | 0.79678 | 46.4431 | 38.9822 | 0.83935 | 46.4431 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2026 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 1.5712 | 55 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 21.4921 | 1.6232 | 13.2405 | 21.4921 | 1.6232 | 13.2405 | 22.6404 | 1.7099 | 13.2405 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2026 | 40 | CB 40 | Tier-1 | Non-HFTD---6 | 3--3 | 7.115 | 166 | 100% | 69.5172 | 93.23% | 0% | 6.766% | 3.2083 | 0 | 0 | 3.2083 | 0 | 3.0605 | 7.3505 | 0.41637 | 3.0605 | 7.3505 | 0.41637 | 3.224 | 7.7432 | 0.41637 | 4.615% | 0.021321 | 0.020266 | 3260.5047 | 598.6862 | 390.1907 | 2271.6278 | 3271.993 | 0 | 0 | 3271.993 | 0.0001058%
2026 | 137 | 137-34AE | Tier-1 | Non-HFTD---16 | 2--1 | 3.2265 | 148 | 100% | 3.1884 | 24.97% | 0% | 75.03% | 0.039416 | 0 | 0 | 0.039416 | 0 | 0.0376 | 3.3332 | 0.01128 | 0.0376 | 3.3332 | 0.01128 | 0.039609 | 3.5113 | 0.01128 | 1.236% | 0.0099752 | 0.0094814 | 319.6366 | 0.18045 | 101.6106 | 217.8455 | 332.1254 | 0 | 0 | 332.1254 | 1.3e-06%
2026 | 275 | 275-48F | Tier-1 | Non-HFTD---3 | 3--4 | 3.4754 | 51 | 100% | 122.1483 | 5.775% | 92.83% | 1.397% | 0.34918 | 0 | 0 | 0.34918 | 0 | 0.3331 | 3.5904 | 0.092774 | 0.3331 | 3.5904 | 0.092774 | 0.35089 | 3.7822 | 0.092774 | 0.2859% | 0.024465 | 0.023254 | 4992.7367 | 48.2186 | 4344.9921 | 599.526 | 5237.7319 | 0 | 0 | 5237.7319 | 1.151e-05%
2026 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 2.9135 | 351 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 236.5455 | 3.0099 | 78.5897 | 236.5455 | 3.0099 | 78.5897 | 249.1845 | 3.1707 | 78.5897 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2026 | NC3 | CB NC3 | Tier-1 | Non-HFTD---18 | 1--1 | 1.3062 | 16 | 100% | 1.3141 | 19.33% | 0% | 80.67% | 0.012576 | 0 | 0 | 0.012576 | 0 | 0.011997 | 1.3494 | 0.0088904 | 0.011997 | 1.3494 | 0.0088904 | 0.012638 | 1.4215 | 0.0088904 | 0.9571% | 0.004054 | 0.0038533 | 324.1367 | 12.2073 | 35.4768 | 276.4527 | 337.7533 | 0 | 0 | 337.7533 | 4.147e-07%
2026 | 341 | 341-1155F | Tier-1 | Non-HFTD---1 | 3--5 | 4.5127 | 433 | 100% | 374.3613 | 99.24% | 0% | 0.7589% | 18.3903 | 0 | 0 | 18.3903 | 0 | 17.5431 | 4.662 | 3.763 | 17.5431 | 4.662 | 3.763 | 18.4804 | 4.9111 | 3.763 | 4.912% | 0.015477 | 0.014711 | 24187.611 | 4353.0066 | 31.6958 | 19802.9086 | 24197.1702 | 0 | 0 | 24197.1702 | 0.0006064%
2026 | BN1 | CB BN1 | Tier-1 | Non-HFTD---4 | 4--4 | 10.2073 | 521 | 100% | 173.8031 | 96.37% | 0% | 3.629% | 8.291 | 0 | 0 | 8.291 | 0 | 7.9091 | 10.5451 | 0.75002 | 7.9091 | 10.5451 | 0.75002 | 8.3317 | 11.1086 | 0.75002 | 4.77% | 0.028851 | 0.027423 | 6024.1621 | 939.3966 | 90.5041 | 4994.2615 | 6035.548 | 0 | 0 | 6035.548 | 0.0002734%
2026 | 255 | 255-1080R | Tier-1 | Non-HFTD---18 | 2--1 | 2.5939 | 84 | 100% | 2.1745 | 29.65% | 0% | 70.35% | 0.031915 | 0 | 0 | 0.031915 | 0 | 0.030445 | 2.6798 | 0.011361 | 0.030445 | 2.6798 | 0.011361 | 0.032072 | 2.823 | 0.011361 | 1.468% | 0.006657 | 0.0063275 | 326.6462 | 0.17291 | 117.7275 | 208.7459 | 338.6134 | 0 | 0 | 338.6134 | 1.052e-06%
2026 | 454 | 454-47R | Tier-1 | Non-HFTD---17 | 1--2 | 0.27501 | 6 | 100% | 0.77526 | 68.13% | 0% | 31.87% | 0.026144 | 0 | 0 | 0.026144 | 0 | 0.02494 | 0.28411 | 0.087782 | 0.02494 | 0.28411 | 0.087782 | 0.026272 | 0.29929 | 0.087782 | 3.372% | 0.0008848 | 0.000841 | 876.1933 | 0.21014 | 622.2981 | 253.6851 | 890.7368 | 0 | 0 | 890.7368 | 8.621e-07%
2026 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.94526 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 169.657 | 0.97654 | 173.7332 | 169.657 | 0.97654 | 173.7332 | 178.722 | 1.0287 | 173.7332 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2026 | ES4 | CB ES4 | Tier-1 | Non-HFTD---10 | 4--1 | 15.6208 | 619 | 100% | 17.8102 | 40.04% | 0% | 59.96% | 0.35302 | 0 | 0 | 0.35302 | 0 | 0.33676 | 16.1377 | 0.020868 | 0.33676 | 16.1377 | 0.020868 | 0.35475 | 17 | 0.020868 | 1.982% | 0.043584 | 0.041426 | 408.6447 | 3.4145 | 166.1409 | 239.0894 | 421.4043 | 0 | 0 | 421.4043 | 1.164e-05%
2026 | SR1 | CB SR1 | Tier-1 | Non-HFTD---12 | 4--1 | 11.5445 | 296 | 100% | 12.5988 | 40.76% | 0% | 59.24% | 0.25419 | 0 | 0 | 0.25419 | 0 | 0.24248 | 11.9266 | 0.020331 | 0.24248 | 11.9266 | 0.020331 | 0.25544 | 12.5638 | 0.020331 | 2.018% | 0.032342 | 0.030741 | 389.5505 | 31.2637 | 84.0563 | 274.2304 | 401.5686 | 0 | 0 | 401.5686 | 8.382e-06%
2026 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 17.63 | 253 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 22.317 | 18.2134 | 1.2253 | 22.317 | 18.2134 | 1.2253 | 23.5094 | 19.1865 | 1.2253 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2026 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 4.3521 | 411 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 147.7158 | 4.4961 | 32.8542 | 147.7158 | 4.4961 | 32.8542 | 155.6084 | 4.7363 | 32.8542 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2026 | 280 | 280-24AE | Tier-2 | Tier-2---12 | 4--4 | 2.1642 | 148 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.56941 | 0 | 0 | 0.56941 | 0 | 0.54317 | 2.2359 | 0.24294 | 0.54317 | 2.2359 | 0.24294 | 0.5722 | 2.3553 | 0.24294 | 0.1557% | 0.037093 | 0.035257 | 9861.3901 | 49.7133 | 8813.1546 | 998.5222 | 10358.7999 | 0 | 0 | 10358.7999 | 1.878e-05%
2026 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 9.9068 | 758 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 85.8122 | 10.2347 | 8.3845 | 85.8122 | 10.2347 | 8.3845 | 90.3972 | 10.7815 | 8.3845 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2026 | 1072 | 1072-6 | Tier-1 | Non-HFTD---1 | 3--4 | 0.23504 | 5 | 100% | 193.6121 | 0.3692% | 99.58% | 0.05199% | 0.035387 | 0 | 0 | 0.035387 | 0 | 0.033757 | 0.24282 | 0.13902 | 0.033757 | 0.24282 | 0.13902 | 0.03556 | 0.25579 | 0.13902 | 0.01828% | 0.01694 | 0.016102 | 11429.1521 | 20.5352 | 10413.4738 | 995.1431 | 12022.16 | 0 | 0 | 12022.16 | 1.167e-06%
2026 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 7.8127 | 466 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 911.0636 | 8.0712 | 112.8782 | 911.0636 | 8.0712 | 112.8782 | 959.743 | 8.5025 | 112.8782 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2026 | CD1 | CB CD1 | Tier-1 | Non-HFTD---7 | 3--3 | 1.308 | 51 | 100% | 43.6009 | 1.546% | 95.78% | 2.676% | 0.033356 | 0 | 0 | 0.033356 | 0 | 0.031819 | 1.3513 | 0.023548 | 0.031819 | 1.3513 | 0.023548 | 0.03352 | 1.4235 | 0.023548 | 0.0765% | 0.014488 | 0.01377 | 3009.5292 | 3.7078 | 2622.1215 | 383.7 | 3163.8368 | 0 | 0 | 3163.8368 | 1.1e-06%
2026 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 0.049053 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.1037 | 0.050676 | 2.0463 | 0.1037 | 0.050676 | 2.0463 | 0.10924 | 0.053384 | 2.0463 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2026 | 434 | CB 434 | Tier-1 | Non-HFTD---11 | 1--4 | 0.56686 | 54 | 100% | 12.9164 | 95.4% | 0% | 4.605% | 0.60992 | 0 | 0 | 0.60992 | 0 | 0.58182 | 0.58562 | 0.99353 | 0.58182 | 0.58562 | 0.99353 | 0.61291 | 0.61691 | 0.99353 | 4.722% | 0.0024398 | 0.002319 | 5294.056 | 339.8058 | 2981.8904 | 1972.3599 | 5306.7514 | 0 | 0 | 5306.7514 | 2.011e-05%
2026 | 60 | 60-603F | Tier-1 | Non-HFTD---3 | 4--4 | 6.0002 | 140 | 100% | 169.5135 | 9.049% | 88.6% | 2.35% | 0.75926 | 0 | 0 | 0.75926 | 0 | 0.72428 | 6.1988 | 0.11684 | 0.72428 | 6.1988 | 0.11684 | 0.76298 | 6.53 | 0.11684 | 0.4479% | 0.032694 | 0.031076 | 5184.8494 | 70.8257 | 4426.3803 | 687.6434 | 5430.4326 | 0 | 0 | 5430.4326 | 2.504e-05%
2026 | 282 | 282-565F | Tier-1 | Non-HFTD---6 | 4--3 | 0.85098 | 17 | 100% | 89.9778 | 0.4154% | 98.82% | 0.7661% | 0.018499 | 0 | 0 | 0.018499 | 0 | 0.017647 | 0.87914 | 0.020073 | 0.017647 | 0.87914 | 0.020073 | 0.01859 | 0.92611 | 0.020073 | 0.02056% | 0.032683 | 0.031065 | 2753.0459 | 5.5294 | 2228.0176 | 519.4989 | 2895.8231 | 0 | 0 | 2895.8231 | 6.1e-07%
2026 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 1.4693 | 17 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 95.5517 | 1.5179 | 62.9494 | 95.5517 | 1.5179 | 62.9494 | 100.6572 | 1.599 | 62.9494 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2026 | 38 | 38-11 | Tier-1 | Non-HFTD---10 | 4--2 | 9.7832 | 399 | 100% | 25.7057 | 75.43% | 0% | 24.57% | 0.95975 | 0 | 0 | 0.95975 | 0 | 0.91554 | 10.1069 | 0.090585 | 0.91554 | 10.1069 | 0.090585 | 0.96446 | 10.6469 | 0.090585 | 3.734% | 0.028609 | 0.027193 | 898.5174 | 56.9208 | 481.0436 | 360.553 | 910.0159 | 0 | 0 | 910.0159 | 3.165e-05%
2026 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 5.8841 | 510 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 72.0465 | 6.0788 | 11.8521 | 72.0465 | 6.0788 | 11.8521 | 75.8961 | 6.4036 | 11.8521 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2026 | 43 | 43-445 | Tier-1 | Non-HFTD---10 | 4--2 | 11.0882 | 259 | 100% | 17.7138 | 50.11% | 0% | 49.89% | 0.43939 | 0 | 0 | 0.43939 | 0 | 0.41915 | 11.4552 | 0.036591 | 0.41915 | 11.4552 | 0.036591 | 0.44155 | 12.0673 | 0.036591 | 2.481% | 0.033392 | 0.031739 | 530.477 | 16.8718 | 186.6503 | 326.9548 | 544.2593 | 0 | 0 | 544.2593 | 1.449e-05%
2026 | 297 | CB 297 | Tier-2 | Tier-2---19 | 1--3 | 0.42898 | 9 | 100% | 7.4286 | 94.8% | 0% | 5.203% | 0.34859 | 0 | 0 | 0.34859 | 0 | 0.33253 | 0.44317 | 0.75033 | 0.33253 | 0.44317 | 0.75033 | 0.35029 | 0.46685 | 0.75033 | 4.692% | 0.0019588 | 0.0018618 | 3792.4284 | 350.5573 | 1464.3094 | 1977.5617 | 3802.7036 | 0 | 0 | 3802.7036 | 1.15e-05%
2026 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 11.5801 | 478 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 482.9506 | 11.9633 | 40.3693 | 482.9506 | 11.9633 | 40.3693 | 508.7553 | 12.6025 | 40.3693 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2026 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 6.0637 | 149 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 50.3341 | 6.2643 | 8.035 | 50.3341 | 6.2643 | 8.035 | 53.0235 | 6.599 | 8.035 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2026 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 19.582 | 1188 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1249.9804 | 20.23 | 61.7884 | 1249.9804 | 20.23 | 61.7884 | 1316.7686 | 21.3109 | 61.7884 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2026 | 1071 | 1071-226F | Tier-1 | Non-HFTD---9 | 1--4 | 0.36818 | 42 | 100% | 15.0528 | 98.32% | 0% | 1.683% | 0.73257 | 0 | 0 | 0.73257 | 0 | 0.69883 | 0.38037 | 1.8372 | 0.69883 | 0.38037 | 1.8372 | 0.73616 | 0.40069 | 1.8372 | 4.867% | 0.0017068 | 0.0016223 | 8819.3233 | 1269.9582 | 917.792 | 6631.5731 | 8827.0536 | 0 | 0 | 8827.0536 | 2.416e-05%
2026 | 331 | CB 331 | Tier-2 | Tier-2---14 | 2--5 | 2.8949 | 3 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 12.8498 | 0 | 0 | 12.8498 | 0 | 12.2578 | 2.9907 | 4.0987 | 12.2578 | 2.9907 | 4.0987 | 12.9128 | 3.1505 | 4.0987 | 4.919% | 0.010352 | 0.0098396 | 25232.8512 | 3536.4388 | 3219.2744 | 18477.138 | 25240.9927 | 0 | 0 | 25240.9927 | 0.0004237%
2026 | 920 | CB 920 | Tier-1 | Non-HFTD---1 | 1--5 | 0.96496 | 63 | 100% | 251.9037 | 99.78% | 0% | 0.2231% | 12.4414 | 0 | 0 | 12.4414 | 0 | 11.8683 | 0.9969 | 11.9052 | 11.8683 | 0.9969 | 11.9052 | 12.5024 | 1.0502 | 11.9052 | 4.939% | 0.0036978 | 0.0035148 | 68122.5856 | 11982.8045 | 3000.2837 | 53139.4975 | 68130.5015 | 0 | 0 | 68130.5015 | 0.0004103%
2026 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 33.1318 | 3002 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 151.314 | 34.2283 | 4.4207 | 151.314 | 34.2283 | 4.4207 | 159.3989 | 36.0571 | 4.4207 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2026 | 243 | 243-14R | Tier-2 | Tier-2---11 | 4--4 | 13.05 | 653 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 5.9029 | 0 | 0 | 5.9029 | 0 | 5.631 | 13.4819 | 0.41767 | 5.631 | 13.4819 | 0.41767 | 5.9318 | 14.2022 | 0.41767 | 1.46% | 0.066445 | 0.063156 | 6084.1314 | 280.7794 | 3933.5085 | 1869.8435 | 6307.5143 | 0 | 0 | 6307.5143 | 0.0001947%
2026 | OH1 | CB OH1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2021 | 28 | 100% | 1.3845 | 20.15% | 0% | 79.85% | 0.013811 | 0 | 0 | 0.013811 | 0 | 0.013175 | 1.2418 | 0.010609 | 0.013175 | 1.2418 | 0.010609 | 0.013879 | 1.3082 | 0.010609 | 0.9975% | 0.003942 | 0.0037469 | 351.2235 | 0.21102 | 96.2554 | 254.7571 | 365.8284 | 0 | 0 | 365.8284 | 4.554e-07%
2026 | PH1 | CB PH1 | Tier-1 | Non-HFTD---18 | 1--1 | 0.61361 | 30 | 100% | 0.70429 | 28.38% | 0% | 71.62% | 0.0098948 | 0 | 0 | 0.0098948 | 0 | 0.009439 | 0.63391 | 0.01489 | 0.009439 | 0.63391 | 0.01489 | 0.0099433 | 0.66778 | 0.01489 | 1.405% | 0.0018738 | 0.001781 | 375.86 | 13.3825 | 50.7092 | 311.7684 | 389.8784 | 0 | 0 | 389.8784 | 3.263e-07%
2026 | 289 | 289-905AE | Tier-1 | Non-HFTD---8 | 3--3 | 4.6523 | 300 | 100% | 40.9452 | 16.44% | 75.92% | 7.645% | 0.33316 | 0 | 0 | 0.33316 | 0 | 0.31781 | 4.8063 | 0.066124 | 0.31781 | 4.8063 | 0.066124 | 0.33479 | 5.0631 | 0.066124 | 0.8137% | 0.0188 | 0.01787 | 2177.8917 | 8.1279 | 1808.1136 | 361.6502 | 2272.6681 | 0 | 0 | 2272.6681 | 1.099e-05%
2026 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 14.3572 | 1792 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 227.721 | 14.8324 | 15.353 | 227.721 | 14.8324 | 15.353 | 239.8884 | 15.6249 | 15.353 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2026 | 154 | 154-894R | Tier-1 | Non-HFTD---14 | 3--1 | 8.141 | 246 | 100% | 8.6688 | 30.94% | 0% | 69.06% | 0.13274 | 0 | 0 | 0.13274 | 0 | 0.12663 | 8.4104 | 0.015056 | 0.12663 | 8.4104 | 0.015056 | 0.1334 | 8.8597 | 0.015056 | 1.531% | 0.023715 | 0.022541 | 365.5396 | 2.5977 | 126.4957 | 236.4462 | 378.6872 | 0 | 0 | 378.6872 | 4.377e-06%
2026 | 443 | CB 443 | Tier-2 | Tier-2---17 | 2--4 | 1.7657 | 0 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 3.2669 | 0 | 0 | 3.2669 | 0 | 3.1164 | 1.8242 | 1.7084 | 3.1164 | 1.8242 | 1.7084 | 3.283 | 1.9216 | 1.7084 | 4.865% | 0.007405 | 0.0070385 | 9067.8323 | 1863.6752 | 20.0371 | 7184.12 | 9075.9094 | 0 | 0 | 9075.9094 | 0.0001077%
2026 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 4.1521 | 373 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.17656 | 4.2895 | 0.04116 | 0.17656 | 4.2895 | 0.04116 | 0.18599 | 4.5187 | 0.04116 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2026 | 707 | CB 707 | Tier-1 | Non-HFTD---9 | 2--3 | 0.76856 | 33 | 100% | 24.2722 | 35% | 62.06% | 2.94% | 0.42051 | 0 | 0 | 0.42051 | 0 | 0.40114 | 0.79399 | 0.50522 | 0.40114 | 0.79399 | 0.50522 | 0.42257 | 0.83642 | 0.50522 | 1.732% | 0.0080484 | 0.00765 | 3015.7851 | 147.2421 | 1865.593 | 1002.95 | 3117.8717 | 0 | 0 | 3117.8717 | 1.387e-05%
2026 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 3.7048 | 795 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 125.6678 | 3.8274 | 32.8339 | 125.6678 | 3.8274 | 32.8339 | 132.3824 | 4.0319 | 32.8339 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2026 | 547 | 547-22R | Tier-1 | Non-HFTD---13 | 2--2 | 3.5843 | 62 | 100% | 7.8544 | 68.58% | 0% | 31.42% | 0.26665 | 0 | 0 | 0.26665 | 0 | 0.25437 | 3.7029 | 0.068694 | 0.25437 | 3.7029 | 0.068694 | 0.26796 | 3.9008 | 0.068694 | 3.395% | 0.010488 | 0.009969 | 748.881 | 11.7437 | 463.65 | 273.4873 | 761.1333 | 0 | 0 | 761.1333 | 8.793e-06%
2026 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 1.532 | 0 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 268.9313 | 1.5827 | 169.9186 | 268.9313 | 1.5827 | 169.9186 | 283.3006 | 1.6673 | 169.9186 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2026 | 452 | CB 452 | Tier-1 | Non-HFTD---10 | 3--2 | 7.2271 | 173 | 100% | 25.8874 | 80.5% | 0% | 19.5% | 1.0316 | 0 | 0 | 1.0316 | 0 | 0.98405 | 7.4663 | 0.1318 | 0.98405 | 7.4663 | 0.1318 | 1.0366 | 7.8652 | 0.1318 | 3.985% | 0.020795 | 0.019766 | 1244.886 | 0.18265 | 1024.2061 | 220.4972 | 1257.5268 | 0 | 0 | 1257.5268 | 3.402e-05%
2026 | 731 | 731-1245F | Tier-1 | Non-HFTD---17 | 1--2 | 0.46347 | 27 | 100% | 1.7231 | 81.35% | 0% | 18.65% | 0.06939 | 0 | 0 | 0.06939 | 0 | 0.066193 | 0.4788 | 0.13825 | 0.066193 | 0.4788 | 0.13825 | 0.06973 | 0.50439 | 0.13825 | 4.027% | 0.0013412 | 0.0012748 | 1284.744 | 169.7674 | 30.9305 | 1084.0462 | 1297.2191 | 0 | 0 | 1297.2191 | 2.288e-06%
2026 | 556 | CB 556 | Tier-1 | Non-HFTD---1 | 2--5 | 1.5472 | 11 | 100% | 422.664 | 99.75% | 0% | 0.2546% | 20.8686 | 0 | 0 | 20.8686 | 0 | 19.9072 | 1.5984 | 12.4548 | 19.9072 | 1.5984 | 12.4548 | 20.9709 | 1.6838 | 12.4548 | 4.937% | 0.0069694 | 0.0066244 | 60645.6807 | 39316.7744 | 1050.0285 | 20278.8779 | 60653.7228 | 0 | 0 | 60653.7228 | 0.0006882%
2026 | 723 | CB 723 | Tier-1 | Non-HFTD---10 | 3--2 | 5.7311 | 124 | 100% | 19.8762 | 84.22% | 0% | 15.78% | 0.82858 | 0 | 0 | 0.82858 | 0 | 0.79041 | 5.9207 | 0.1335 | 0.79041 | 5.9207 | 0.1335 | 0.83264 | 6.2371 | 0.1335 | 4.169% | 0.01527 | 0.014514 | 1301.6828 | 11.1848 | 1047.4878 | 243.0102 | 1312.3823 | 0 | 0 | 1312.3823 | 2.732e-05%
2026 | 401 | 401-39R | Tier-2 | Tier-2---14 | 4--4 | 0.64865 | 64 | 100% | 323.2323 | 3.193% | 96.7% | 0.1048% | 0.51091 | 0 | 0 | 0.51091 | 0 | 0.48737 | 0.67012 | 0.72729 | 0.48737 | 0.67012 | 0.72729 | 0.51341 | 0.70592 | 0.72729 | 0.1581% | 0.031872 | 0.030295 | 10141.4477 | 77.0794 | 9013.6522 | 1050.7162 | 10652.728 | 0 | 0 | 10652.728 | 1.685e-05%
2026 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 5.3305 | 262 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 104.6722 | 5.5069 | 19.0075 | 104.6722 | 5.5069 | 19.0075 | 110.265 | 5.8011 | 19.0075 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2026 | EO1 | CB EO1 | Tier-1 | Non-HFTD---10 | 3--2 | 8.4572 | 310 | 100% | 23.8797 | 77.35% | 0% | 22.65% | 0.91436 | 0 | 0 | 0.91436 | 0 | 0.87224 | 8.7371 | 0.099831 | 0.87224 | 8.7371 | 0.099831 | 0.91884 | 9.2039 | 0.099831 | 3.829% | 0.022403 | 0.021294 | 1065.904 | 118.5711 | 123.3524 | 823.9805 | 1078.4747 | 0 | 0 | 1078.4747 | 3.015e-05%
2026 | 416 | 416-21 | Tier-1 | Non-HFTD---9 | 2--3 | 2.1076 | 56 | 100% | 17.0536 | 88.2% | 0% | 11.8% | 0.74451 | 0 | 0 | 0.74451 | 0 | 0.71021 | 2.1773 | 0.32619 | 0.71021 | 2.1773 | 0.32619 | 0.74816 | 2.2937 | 0.32619 | 4.366% | 0.0069518 | 0.0066077 | 2453.1267 | 2.6942 | 2174.6936 | 275.7389 | 2468.2065 | 0 | 0 | 2468.2065 | 2.455e-05%
2026 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 6.4924 | 212 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 21.1934 | 6.7072 | 3.1598 | 21.1934 | 6.7072 | 3.1598 | 22.3257 | 7.0656 | 3.1598 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2026 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 11.2661 | 731 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 713.7946 | 11.639 | 61.3281 | 713.7946 | 11.639 | 61.3281 | 751.9337 | 12.2608 | 61.3281 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2026 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | 4--5 | 5.5248 | 1388 | 100% | 2371.786 | 97.71% | 2.108% | 0.1806% | 114.7166 | 0 | 0 | 114.7166 | 0 | 109.4319 | 5.7077 | 19.1728 | 109.4319 | 5.7077 | 19.1728 | 115.279 | 6.0126 | 19.1728 | 4.837% | 0.074138 | 0.070468 | 31991.6747 | 5091.6051 | 638.7369 | 26261.3327 | 32029.8024 | 0 | 0 | 32029.8024 | 0.003783%
2026 | 458 | 458-43F | Tier-1 | Non-HFTD---16 | 2--1 | 1.8401 | 69 | 100% | 2.2689 | 42.12% | 0% | 57.88% | 0.047309 | 0 | 0 | 0.047309 | 0 | 0.04513 | 1.901 | 0.023739 | 0.04513 | 1.901 | 0.023739 | 0.047541 | 2.0026 | 0.023739 | 2.085% | 0.0053162 | 0.005053 | 426.7836 | 1.0552 | 196.9069 | 228.8215 | 439.647 | 0 | 0 | 439.647 | 1.56e-06%
2026 | 74 | CB 74 | Tier-1 | Non-HFTD---10 | 3--2 | 6.9906 | 197 | 100% | 19.9911 | 76.58% | 0% | 23.42% | 0.75785 | 0 | 0 | 0.75785 | 0 | 0.72294 | 7.2219 | 0.1001 | 0.72294 | 7.2219 | 0.1001 | 0.76156 | 7.6078 | 0.1001 | 3.791% | 0.019147 | 0.018199 | 1044.0736 | 1.8204 | 811.7883 | 230.4649 | 1056.8053 | 0 | 0 | 1056.8053 | 2.499e-05%
2026 | SC2 | CB SC2 | Tier-1 | Non-HFTD---2 | 4--4 | 7.0339 | 233 | 100% | 261.4516 | 2.208% | 95.93% | 1.858% | 0.28577 | 0 | 0 | 0.28577 | 0 | 0.27261 | 7.2667 | 0.037514 | 0.27261 | 7.2667 | 0.037514 | 0.28717 | 7.655 | 0.037514 | 0.1093% | 0.037006 | 0.035174 | 7065.0763 | 7.3313 | 6299.5139 | 758.2311 | 7424.8859 | 0 | 0 | 7424.8859 | 9.424e-06%
2026 | 529 | CB 529 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3037 | 55 | 100% | 27.2988 | 93.37% | 0% | 6.628% | 1.2617 | 0 | 0 | 1.2617 | 0 | 1.2036 | 2.38 | 0.50572 | 1.2036 | 2.38 | 0.50572 | 1.2679 | 2.5071 | 0.50572 | 4.622% | 0.0089244 | 0.0084826 | 3058.8995 | 429.8777 | 198.033 | 2430.9888 | 3069.4573 | 0 | 0 | 3069.4573 | 4.161e-05%
2026 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | 4--1 | 0.90625 | 0 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.15233 | 0 | 0 | 0.15233 | 0 | 0.14531 | 0.93624 | 0.1552 | 0.14531 | 0.93624 | 0.1552 | 0.15307 | 0.98627 | 0.1552 | 0.8348% | 0.061771 | 0.058714 | 295.3886 | 6.838 | 193.9385 | 94.612 | 308.1774 | 0 | 0 | 308.1774 | 5.023e-06%
2026 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 10.0072 | 279 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 70.4248 | 10.3384 | 6.812 | 70.4248 | 10.3384 | 6.812 | 74.1877 | 10.8908 | 6.812 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2026 | 34 | CB 34 | Tier-1 | Non-HFTD---19 | 1--1 | 0.1034 | 3 | 100% | 0.13232 | 2.437% | 0% | 97.56% | 0.00015964 | 0 | 0 | 0.00015964 | 0 | 0.00015228 | 0.10682 | 0.0014257 | 0.00015228 | 0.10682 | 0.0014257 | 0.00016042 | 0.11252 | 0.0014257 | 0.1206% | 0.0003968 | 0.00037716 | 333.478 | 0.37096 | 36.9115 | 296.1955 | 350.4215 | 0 | 0 | 350.4215 | 5.264e-09%
2026 | 190 | 190-1122F | Tier-1 | Non-HFTD---9 | 1--4 | 0.44692 | 22 | 100% | 22.2623 | 98.77% | 0% | 1.233% | 1.0884 | 0 | 0 | 1.0884 | 0 | 1.0383 | 0.46171 | 2.2487 | 1.0383 | 0.46171 | 2.2487 | 1.0937 | 0.48638 | 2.2487 | 4.889% | 0.001452 | 0.0013801 | 15332.18 | 2415.7745 | 19.2027 | 12897.2028 | 15342.0229 | 0 | 0 | 15342.0229 | 3.589e-05%
2026 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.023485 | 0 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.9706 | 0.024262 | 122.4361 | 2.9706 | 0.024262 | 122.4361 | 3.1293 | 0.025558 | 122.4361 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2026 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 6.8952 | 718 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 39.8446 | 7.1234 | 5.5935 | 39.8446 | 7.1234 | 5.5935 | 41.9736 | 7.504 | 5.5935 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2026 | 963 | 963-35 | Tier-1 | Non-HFTD---7 | 2--3 | 3.1555 | 180 | 100% | 30.7376 | 94.18% | 0% | 5.818% | 1.433 | 0 | 0 | 1.433 | 0 | 1.367 | 3.2599 | 0.41933 | 1.367 | 3.2599 | 0.41933 | 1.44 | 3.4341 | 0.41933 | 4.662% | 0.012897 | 0.012259 | 2383.2808 | 325.3782 | 213.264 | 1844.6386 | 2390.5024 | 0 | 0 | 2390.5024 | 4.725e-05%
2026 | 303 | 303-189AE | Tier-1 | Non-HFTD---3 | 4--4 | 8.0475 | 408 | 100% | 171.0034 | 3.397% | 93.81% | 2.795% | 0.28756 | 0 | 0 | 0.28756 | 0 | 0.27431 | 8.3139 | 0.032994 | 0.27431 | 8.3139 | 0.032994 | 0.28896 | 8.7581 | 0.032994 | 0.1682% | 0.032667 | 0.03105 | 5234.7139 | 12.8116 | 4649.2999 | 572.6024 | 5498.0656 | 0 | 0 | 5498.0656 | 9.483e-06%
2026 | 1082 | CB 1082 | Tier-1 | Non-HFTD---10 | 3--2 | 1.1544 | 45 | 100% | 15.7927 | 61.51% | 33.76% | 4.733% | 0.48084 | 0 | 0 | 0.48084 | 0 | 0.45869 | 1.1926 | 0.38462 | 0.45869 | 1.1926 | 0.38462 | 0.48319 | 1.2563 | 0.38462 | 3.045% | 0.014222 | 0.013518 | 1110.4405 | 109.3438 | 313.5434 | 687.5533 | 1132.6997 | 0 | 0 | 1132.6997 | 1.586e-05%
2026 | 740 | 740-857F | Tier-1 | Non-HFTD---19 | 1--1 | 0.23295 | 18 | 100% | 0.392 | 20.4% | 0% | 79.6% | 0.0039577 | 0 | 0 | 0.0039577 | 0 | 0.0037754 | 0.24066 | 0.015687 | 0.0037754 | 0.24066 | 0.015687 | 0.0039771 | 0.25352 | 0.015687 | 1.01% | 0.0010222 | 0.0009716 | 383.4881 | 10.7399 | 40.9688 | 331.7794 | 399.386 | 0 | 0 | 399.386 | 1.305e-07%
2026 | 61 | 61-13F | Tier-1 | Non-HFTD---5 | 3--3 | 1.5653 | 221 | 100% | 66.9136 | 1.1% | 96.65% | 2.249% | 0.036446 | 0 | 0 | 0.036446 | 0 | 0.034767 | 1.6171 | 0.021499 | 0.034767 | 1.6171 | 0.021499 | 0.036625 | 1.7035 | 0.021499 | 0.05447% | 0.016091 | 0.015295 | 4158.3434 | 4.7662 | 3732.5049 | 421.0723 | 4372.5181 | 0 | 0 | 4372.5181 | 1.202e-06%
2026 | 159 | 159-1010F | Tier-1 | Non-HFTD---20 | 1--1 | 0.18916 | 14 | 100% | 0.072864 | 14.16% | 0% | 85.84% | 0.00051071 | 0 | 0 | 0.00051071 | 0 | 0.00048718 | 0.19542 | 0.002493 | 0.00048718 | 0.19542 | 0.002493 | 0.00051321 | 0.20586 | 0.002493 | 0.7009% | 0.0003894 | 0.00037012 | 187.1198 | 0.12086 | 41.0868 | 145.9122 | 195.4848 | 0 | 0 | 195.4848 | 1.684e-08%
2026 | 855 | CB 855 | Tier-1 | Non-HFTD---1 | 2--5 | 3.5599 | 173 | 100% | 270.5618 | 99.37% | 0% | 0.6324% | 13.3081 | 0 | 0 | 13.3081 | 0 | 12.695 | 3.6777 | 3.4519 | 12.695 | 3.6777 | 3.4519 | 13.3733 | 3.8742 | 3.4519 | 4.919% | 0.01085 | 0.010313 | 24937.4896 | 3437.8657 | 3656.8715 | 17842.7524 | 24945.7025 | 0 | 0 | 24945.7025 | 0.0004389%
2026 | RV1 | CB RV1 | Tier-1 | Non-HFTD---14 | 3--1 | 7.5803 | 408 | 100% | 5.6011 | 21.45% | 0% | 78.55% | 0.059471 | 0 | 0 | 0.059471 | 0 | 0.056732 | 7.8311 | 0.0072444 | 0.056732 | 7.8311 | 0.0072444 | 0.059763 | 8.2496 | 0.0072444 | 1.062% | 0.019991 | 0.019001 | 280.18 | 0.1656 | 80.0914 | 199.9231 | 291.6414 | 0 | 0 | 291.6414 | 1.961e-06%
2026 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 7.6085 | 805 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 137.9346 | 7.8603 | 17.5482 | 137.9346 | 7.8603 | 17.5482 | 145.3046 | 8.2803 | 17.5482 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2026 | 777 | 777-10 | Tier-1 | Non-HFTD---19 | 1--2 | 0.1028 | 0 | 100% | 0.21948 | 49.99% | 0% | 50.01% | 0.0054313 | 0 | 0 | 0.0054313 | 0 | 0.0051811 | 0.1062 | 0.048787 | 0.0051811 | 0.1062 | 0.048787 | 0.0054579 | 0.11187 | 0.048787 | 2.475% | 0.0003706 | 0.00035226 | 592.216 | 47.9707 | 27.3549 | 516.8903 | 607.6387 | 0 | 0 | 607.6387 | 1.791e-07%
2026 | 87 | CB 87 | Tier-1 | Non-HFTD---14 | 3--1 | 6.3328 | 197 | 100% | 8.2544 | 42.74% | 0% | 57.26% | 0.17463 | 0 | 0 | 0.17463 | 0 | 0.16659 | 6.5424 | 0.025463 | 0.16659 | 6.5424 | 0.025463 | 0.17549 | 6.8919 | 0.025463 | 2.116% | 0.018391 | 0.017481 | 448.8306 | 2.7145 | 199.6816 | 246.4345 | 462.2148 | 0 | 0 | 462.2148 | 5.759e-06%
2026 | 363 | CB 363 | Tier-1 | Non-HFTD---5 | 3--4 | 3.2214 | 67 | 100% | 93.3136 | 5.828% | 91.17% | 3.003% | 0.26918 | 0 | 0 | 0.26918 | 0 | 0.25678 | 3.3281 | 0.077157 | 0.25678 | 3.3281 | 0.077157 | 0.2705 | 3.5059 | 0.077157 | 0.2885% | 0.014683 | 0.013956 | 6355.3857 | 6.7587 | 5611.6916 | 736.9354 | 6667.0722 | 0 | 0 | 6667.0722 | 8.877e-06%
2026 | 116 | CB 116 | Tier-1 | Non-HFTD---2 | 4--4 | 7.0256 | 286 | 100% | 265.4697 | 47.19% | 51.3% | 1.507% | 6.2014 | 0 | 0 | 6.2014 | 0 | 5.9157 | 7.2581 | 0.81506 | 5.9157 | 7.2581 | 0.81506 | 6.2318 | 7.6459 | 0.81506 | 2.336% | 0.037029 | 0.035196 | 7169.199 | 559.0648 | 4185.9405 | 2424.1937 | 7366.3596 | 0 | 0 | 7366.3596 | 0.0002045%
2026 | 221 | 221-1249R | Tier-1 | Non-HFTD---2 | 5--2 | 25.1976 | 192 | 100% | 329.3718 | 60.93% | 35.44% | 3.632% | 9.9343 | 0 | 0 | 9.9343 | 0 | 9.4767 | 26.0315 | 0.36405 | 9.4767 | 26.0315 | 0.36405 | 9.983 | 27.4224 | 0.36405 | 3.016% | 0.32343 | 0.30742 | 1018.3674 | 70.1582 | 373.9946 | 574.2146 | 1039.0867 | 0 | 0 | 1039.0867 | 0.0003276%
2026 | 418 | 418-25R | Tier-1 | Non-HFTD---14 | 2--2 | 3.847 | 112 | 100% | 6.5111 | 53.05% | 0% | 46.95% | 0.171 | 0 | 0 | 0.171 | 0 | 0.16312 | 3.9743 | 0.041044 | 0.16312 | 3.9743 | 0.041044 | 0.17183 | 4.1866 | 0.041044 | 2.626% | 0.011457 | 0.01089 | 568.3108 | 3.1871 | 307.4186 | 257.7051 | 582.2048 | 0 | 0 | 582.2048 | 5.639e-06%
2026 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 5.1074 | 166 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 538.3214 | 5.2764 | 102.0247 | 538.3214 | 5.2764 | 102.0247 | 567.0846 | 5.5583 | 102.0247 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2026 | MNR3 | CB MNR3 | Tier-1 | Non-HFTD---8 | 3--2 | 4.6053 | 258 | 100% | 32.2512 | 24.3% | 64.69% | 11.01% | 0.38795 | 0 | 0 | 0.38795 | 0 | 0.37008 | 4.7577 | 0.077786 | 0.37008 | 4.7577 | 0.077786 | 0.38985 | 5.0119 | 0.077786 | 1.203% | 0.019891 | 0.018906 | 1621.3979 | 77.741 | 1023.8427 | 519.8142 | 1685.3173 | 0 | 0 | 1685.3173 | 1.279e-05%
2026 | 313 | 313-920F | Tier-1 | Non-HFTD---10 | 3--2 | 0.7511 | 67 | 100% | 25.9898 | 2.478% | 94.94% | 2.583% | 0.03188 | 0 | 0 | 0.03188 | 0 | 0.030411 | 0.77595 | 0.039192 | 0.030411 | 0.77595 | 0.039192 | 0.032036 | 0.81741 | 0.039192 | 0.1227% | 0.019352 | 0.018394 | 1342.9879 | 6.3375 | 1055.0399 | 281.6105 | 1411.1947 | 0 | 0 | 1411.1947 | 1.051e-06%
2026 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 19.4272 | 2033 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 200.6758 | 20.0701 | 9.9987 | 200.6758 | 20.0701 | 9.9987 | 211.3982 | 21.1425 | 9.9987 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2026 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 18.9327 | 1474 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 960.4166 | 19.5593 | 49.1028 | 960.4166 | 19.5593 | 49.1028 | 1011.733 | 20.6044 | 49.1028 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2026 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 11.8401 | 434 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 124.7575 | 12.232 | 10.1993 | 124.7575 | 12.232 | 10.1993 | 131.4234 | 12.8855 | 10.1993 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2026 | 533 | 533-7AE | Tier-1 | Non-HFTD---6 | 4--2 | 2.0012 | 69 | 100% | 45.7464 | 11.34% | 84.92% | 3.741% | 0.25674 | 0 | 0 | 0.25674 | 0 | 0.24491 | 2.0674 | 0.11846 | 0.24491 | 2.0674 | 0.11846 | 0.258 | 2.1779 | 0.11846 | 0.5612% | 0.066097 | 0.062825 | 692.1106 | 12.2731 | 470.7532 | 209.0843 | 724.0677 | 0 | 0 | 724.0677 | 8.466e-06%
2026 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.49562 | 10 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 39.6291 | 0.51202 | 77.3978 | 39.6291 | 0.51202 | 77.3978 | 41.7465 | 0.53938 | 77.3978 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2026 | 397 | 397-550F | Tier-1 | Non-HFTD---16 | 3--1 | 4.9887 | 155 | 100% | 4.542 | 25.73% | 0% | 74.27% | 0.057853 | 0 | 0 | 0.057853 | 0 | 0.055187 | 5.1538 | 0.010708 | 0.055187 | 5.1538 | 0.010708 | 0.058136 | 5.4292 | 0.010708 | 1.274% | 0.013683 | 0.013005 | 331.9512 | 4.2581 | 82.8811 | 244.812 | 344.7902 | 0 | 0 | 344.7902 | 1.908e-06%
2026 | 156 | CB 156 | Tier-1 | Non-HFTD---7 | 2--3 | 3.9841 | 144 | 100% | 34.4406 | 92.43% | 0% | 7.569% | 1.5758 | 0 | 0 | 1.5758 | 0 | 1.5032 | 4.1159 | 0.36521 | 1.5032 | 4.1159 | 0.36521 | 1.5835 | 4.3359 | 0.36521 | 4.575% | 0.012401 | 0.011788 | 2777.1524 | 583.7733 | 709.3221 | 1484.0571 | 2788.0993 | 0 | 0 | 2788.0993 | 5.196e-05%
2026 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 16.0076 | 996 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 985.7421 | 16.5373 | 59.6071 | 985.7421 | 16.5373 | 59.6071 | 1038.4116 | 17.4209 | 59.6071 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2026 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 7.3674 | 622 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 188.5406 | 7.6112 | 24.7714 | 188.5406 | 7.6112 | 24.7714 | 198.6146 | 8.0179 | 24.7714 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2026 | 255 | 255-43AE | Tier-1 | Non-HFTD---6 | 4--2 | 17.4344 | 666 | 100% | 53.0999 | 77.76% | 0% | 22.24% | 2.0438 | 0 | 0 | 2.0438 | 0 | 1.9496 | 18.0114 | 0.10824 | 1.9496 | 18.0114 | 0.10824 | 2.0538 | 18.9738 | 0.10824 | 3.849% | 0.048441 | 0.046043 | 1096.1851 | 147.1891 | 267.7558 | 681.2403 | 1108.8831 | 0 | 0 | 1108.8831 | 6.74e-05%
2026 | 50 | CB 50 | Tier-1 | Non-HFTD---16 | 2--1 | 3.922 | 170 | 100% | 4.8179 | 39.4% | 0% | 60.6% | 0.093953 | 0 | 0 | 0.093953 | 0 | 0.089625 | 4.0518 | 0.02212 | 0.089625 | 4.0518 | 0.02212 | 0.094413 | 4.2683 | 0.02212 | 1.95% | 0.010946 | 0.010404 | 440.1426 | 0.20072 | 197.6284 | 242.3134 | 454.0341 | 0 | 0 | 454.0341 | 3.098e-06%
2026 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 7.5286 | 403 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 50.6581 | 7.7778 | 6.5132 | 50.6581 | 7.7778 | 6.5132 | 53.3649 | 8.1934 | 6.5132 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2026 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 14.1159 | 1193 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 81.2969 | 14.5831 | 5.5748 | 81.2969 | 14.5831 | 5.5748 | 85.6408 | 15.3623 | 5.5748 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2026 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 17.3068 | 1251 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 251.2008 | 17.8795 | 14.0496 | 251.2008 | 17.8795 | 14.0496 | 264.6228 | 18.8348 | 14.0496 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2026 | 139 | 139-245AE | Tier-1 | Non-HFTD---14 | 2--2 | 3.4127 | 72 | 100% | 5.6722 | 51.84% | 0% | 48.16% | 0.14554 | 0 | 0 | 0.14554 | 0 | 0.13884 | 3.5256 | 0.03938 | 0.13884 | 3.5256 | 0.03938 | 0.14626 | 3.714 | 0.03938 | 2.566% | 0.010451 | 0.0099339 | 542.7299 | 27.8649 | 162.7078 | 352.1572 | 556.343 | 0 | 0 | 556.343 | 4.799e-06%
2026 | 512 | CB 512 | Tier-1 | Non-HFTD---5 | 2--4 | 0.53466 | 12 | 100% | 72.9923 | 9.966% | 89.3% | 0.7365% | 0.36007 | 0 | 0 | 0.36007 | 0 | 0.34349 | 0.55235 | 0.62186 | 0.34349 | 0.55235 | 0.62186 | 0.36184 | 0.58187 | 0.62186 | 0.4933% | 0.012277 | 0.01167 | 5945.2569 | 37.3623 | 5220.9585 | 686.9361 | 6224.0176 | 0 | 0 | 6224.0176 | 1.187e-05%
2026 | 189 | 189-750 | Tier-2 | Tier-2---21 | 1--2 | 0.37597 | 5 | 100% | 1.7248 | 88.21% | 0% | 11.79% | 0.075309 | 0 | 0 | 0.075309 | 0 | 0.07184 | 0.38841 | 0.18496 | 0.07184 | 0.38841 | 0.18496 | 0.075679 | 0.40916 | 0.18496 | 4.366% | 0.001013 | 0.00096286 | 1702.705 | 2.2891 | 1507.0729 | 193.3431 | 1713.1637 | 0 | 0 | 1713.1637 | 2.483e-06%
2026 | 361 | 361-684F | Tier-1 | Non-HFTD---18 | 2--1 | 0.31534 | 15 | 100% | 0.70004 | 34.6% | 14.74% | 50.66% | 0.011991 | 0 | 0 | 0.011991 | 0 | 0.011438 | 0.32578 | 0.035111 | 0.011438 | 0.32578 | 0.035111 | 0.012049 | 0.34318 | 0.035111 | 1.713% | 0.0069836 | 0.0066379 | 100.2413 | 5.6671 | 18.5544 | 76.0198 | 103.6552 | 0 | 0 | 103.6552 | 3.954e-07%
2026 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 13.7784 | 1046 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 84.8362 | 14.2344 | 5.9599 | 84.8362 | 14.2344 | 5.9599 | 89.3691 | 14.995 | 5.9599 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2026 | 120 | 120-367F | Tier-1 | Non-HFTD---13 | 2--2 | 0.019508 | 2 | 100% | 8.1563 | 0% | 99.6% | 0.404% | 0 | 0 | 0 | 0 | 0 | 0 | 0.020153 | 0 | 0 | 0.020153 | 0 | 0 | 0.02123 | 0 | 0% | 0.0075852 | 0.0072097 | 1075.2925 | 1.6858 | 978.9966 | 94.6101 | 1131.2914 | 0 | 0 | 1131.2914 | 0%
2026 | 87 | 87-41AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.2464 | 37 | 100% | 0.28157 | 26.88% | 0% | 73.12% | 0.0037471 | 0 | 0 | 0.0037471 | 0 | 0.0035745 | 0.25456 | 0.014042 | 0.0035745 | 0.25456 | 0.014042 | 0.0037655 | 0.26816 | 0.014042 | 1.331% | 0.0008986 | 0.00085412 | 313.3426 | 10.7167 | 37.6883 | 264.9376 | 325.2737 | 0 | 0 | 325.2737 | 1.236e-07%
2026 | 321 | 321-1332R | Tier-1 | Non-HFTD---12 | 2--2 | 4.7077 | 80 | 100% | 9.6163 | 68.26% | 0% | 31.74% | 0.32491 | 0 | 0 | 0.32491 | 0 | 0.30994 | 4.8635 | 0.063728 | 0.30994 | 4.8635 | 0.063728 | 0.3265 | 5.1234 | 0.063728 | 3.379% | 0.013392 | 0.012729 | 718.0629 | 3.1766 | 492.4341 | 222.4522 | 729.9331 | 0 | 0 | 729.9331 | 1.071e-05%
2026 | 770 | 770-259R | Tier-2 | Tier-2---17 | 2--3 | 1.5089 | 0 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 2.0515 | 0 | 0 | 2.0515 | 0 | 1.957 | 1.5588 | 1.2554 | 1.957 | 1.5588 | 1.2554 | 2.0616 | 1.6421 | 1.2554 | 4.826% | 0.010605 | 0.01008 | 4008.538 | 787.4023 | 25.9222 | 3195.2135 | 4013.7737 | 0 | 0 | 4013.7737 | 6.765e-05%
2026 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 3.6864 | 237 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 152.7457 | 3.8084 | 40.1077 | 152.7457 | 3.8084 | 40.1077 | 160.9071 | 4.0119 | 40.1077 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2026 | 371 | CB 371 | Tier-1 | Non-HFTD---18 | 1--1 | 0.65097 | 0 | 100% | 0.79179 | 5.127% | 0% | 94.87% | 0.0020093 | 0 | 0 | 0.0020093 | 0 | 0.0019167 | 0.67251 | 0.0028501 | 0.0019167 | 0.67251 | 0.0028501 | 0.0020191 | 0.70844 | 0.0028501 | 0.2538% | 0.0026386 | 0.002508 | 300.0814 | 2.4613 | 27.3455 | 270.2746 | 314.9079 | 0 | 0 | 314.9079 | 6.626e-08%
2026 | 206 | 206-961F | Tier-1 | Non-HFTD---17 | 1--2 | 0.31686 | 31 | 100% | 0.73497 | 72.73% | 0% | 27.27% | 0.026461 | 0 | 0 | 0.026461 | 0 | 0.025242 | 0.32734 | 0.077113 | 0.025242 | 0.32734 | 0.077113 | 0.026591 | 0.34483 | 0.077113 | 3.6% | 0.0009058 | 0.00086096 | 811.4096 | 93.8104 | 38.4901 | 679.1091 | 822.9314 | 0 | 0 | 822.9314 | 8.726e-07%
2026 | 303 | 303-487AE | Tier-1 | Non-HFTD---4 | 3--4 | 1.8256 | 101 | 100% | 106.3501 | 4.982% | 93.81% | 1.206% | 0.26227 | 0 | 0 | 0.26227 | 0 | 0.25018 | 1.886 | 0.13265 | 0.25018 | 1.886 | 0.13265 | 0.26355 | 1.9868 | 0.13265 | 0.2466% | 0.016038 | 0.015244 | 6631.1342 | 30.8907 | 5898.0053 | 702.2382 | 6959.2651 | 0 | 0 | 6959.2651 | 8.649e-06%
2026 | 206 | CB 206 | Tier-1 | Non-HFTD---11 | 2--3 | 3.0087 | 131 | 100% | 15.0084 | 86.35% | 0% | 13.65% | 0.64153 | 0 | 0 | 0.64153 | 0 | 0.61198 | 3.1083 | 0.19689 | 0.61198 | 3.1083 | 0.19689 | 0.64468 | 3.2744 | 0.19689 | 4.274% | 0.0084374 | 0.0080197 | 1778.7928 | 21.532 | 1427.2919 | 329.9688 | 1791.4343 | 0 | 0 | 1791.4343 | 2.116e-05%
2026 | MU1 | CB MU1 | Tier-1 | Non-HFTD---8 | 3--2 | 2.842 | 486 | 100% | 27.925 | 4.407% | 87.94% | 7.651% | 0.060913 | 0 | 0 | 0.060913 | 0 | 0.058107 | 2.9361 | 0.019791 | 0.058107 | 2.9361 | 0.019791 | 0.061212 | 3.0929 | 0.019791 | 0.2181% | 0.018888 | 0.017953 | 1478.4806 | 11.8202 | 1223.4645 | 243.1959 | 1552.0837 | 0 | 0 | 1552.0837 | 2.009e-06%
2026 | 489 | 489-19AE | Tier-1 | Non-HFTD---11 | 2--2 | 2.8017 | 45 | 100% | 9.4748 | 79.25% | 0% | 20.75% | 0.37169 | 0 | 0 | 0.37169 | 0 | 0.35457 | 2.8944 | 0.1225 | 0.35457 | 2.8944 | 0.1225 | 0.37351 | 3.0491 | 0.1225 | 3.923% | 0.008219 | 0.0078122 | 1152.7879 | 219.8755 | 163.8034 | 769.109 | 1165.2439 | 0 | 0 | 1165.2439 | 1.226e-05%
2026 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 6.825 | 1872 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 22.2618 | 7.0509 | 3.1573 | 22.2618 | 7.0509 | 3.1573 | 23.4513 | 7.4276 | 3.1573 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2026 | 143 | 143-33 | Tier-1 | Non-HFTD---13 | 2--2 | 0.11532 | 2 | 100% | 7.5516 | 0.6961% | 97.86% | 1.439% | 0.0026022 | 0 | 0 | 0.0026022 | 0 | 0.0024823 | 0.11914 | 0.020836 | 0.0024823 | 0.11914 | 0.020836 | 0.002615 | 0.1255 | 0.020836 | 0.03446% | 0.0064842 | 0.0061632 | 1164.6172 | 2.5226 | 906.0378 | 256.0569 | 1224.8458 | 0 | 0 | 1224.8458 | 8.581e-08%
2026 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 1.2528 | 11 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 91.3318 | 1.2943 | 70.5645 | 91.3318 | 1.2943 | 70.5645 | 96.2118 | 1.3635 | 70.5645 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2026 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 3.3435 | 151 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 405.1363 | 3.4542 | 117.2887 | 405.1363 | 3.4542 | 117.2887 | 426.7833 | 3.6387 | 117.2887 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2026 | 128 | CB 128 | Tier-1 | Non-HFTD---16 | 2--1 | 3.2045 | 22 | 100% | 2.8222 | 5.175% | 0% | 94.82% | 0.0072295 | 0 | 0 | 0.0072295 | 0 | 0.0068964 | 3.3106 | 0.0020832 | 0.0068964 | 3.3106 | 0.0020832 | 0.0072649 | 3.4875 | 0.0020832 | 0.2562% | 0.010647 | 0.01012 | 265.0569 | 1.7417 | 26.7354 | 236.5798 | 278.1462 | 0 | 0 | 278.1462 | 2.384e-07%
2026 | 171 | 171-6R | Tier-1 | Non-HFTD---8 | 4--2 | 2.4529 | 22 | 100% | 40.3404 | 54.29% | 41.19% | 4.517% | 1.0841 | 0 | 0 | 1.0841 | 0 | 1.0342 | 2.5341 | 0.40811 | 1.0342 | 2.5341 | 0.40811 | 1.0894 | 2.6695 | 0.40811 | 2.687% | 0.036438 | 0.034634 | 1107.1099 | 96.9512 | 428.9197 | 581.2391 | 1133.4637 | 0 | 0 | 1133.4637 | 3.575e-05%
2026 | 171 | CB 171 | Tier-1 | Non-HFTD---3 | 4--3 | 2.7693 | 176 | 100% | 113.9192 | 33.8% | 64.29% | 1.906% | 1.9062 | 0 | 0 | 1.9062 | 0 | 1.8184 | 2.8609 | 0.63559 | 1.8184 | 2.8609 | 0.63559 | 1.9155 | 3.0138 | 0.63559 | 1.673% | 0.040057 | 0.038075 | 2843.8994 | 78.1486 | 2158.4913 | 607.2596 | 2941.9394 | 0 | 0 | 2941.9394 | 6.286e-05%
2026 | 159 | 159-38F | Tier-1 | Non-HFTD---16 | 2--1 | 2.7123 | 104 | 100% | 2.2472 | 22.94% | 0% | 77.06% | 0.025514 | 0 | 0 | 0.025514 | 0 | 0.024339 | 2.8021 | 0.0086859 | 0.024339 | 2.8021 | 0.0086859 | 0.025639 | 2.9518 | 0.0086859 | 1.135% | 0.00712 | 0.0067676 | 315.6205 | 0.4738 | 92.7094 | 222.4373 | 328.2873 | 0 | 0 | 328.2873 | 8.414e-07%
2026 | 392 | CB 392 | Tier-1 | Non-HFTD---2 | 5--4 | 4.5493 | 172 | 100% | 632.789 | 5.96% | 93.57% | 0.4686% | 1.8668 | 0 | 0 | 1.8668 | 0 | 1.7808 | 4.6998 | 0.37891 | 1.7808 | 4.6998 | 0.37891 | 1.876 | 4.951 | 0.37891 | 0.295% | 0.10236 | 0.097291 | 6182.1524 | 58.8165 | 5308.8037 | 814.5321 | 6484.9176 | 0 | 0 | 6484.9176 | 6.156e-05%
2026 | 172 | 172-567R | Tier-1 | Non-HFTD---3 | 4--3 | 10.6971 | 130 | 100% | 141.9219 | 62.19% | 32.78% | 5.033% | 4.369 | 0 | 0 | 4.369 | 0 | 4.1678 | 11.0511 | 0.37713 | 4.1678 | 11.0511 | 0.37713 | 4.3904 | 11.6416 | 0.37713 | 3.078% | 0.069555 | 0.066112 | 2040.4331 | 199.3667 | 664.6627 | 1176.4036 | 2080.609 | 0 | 0 | 2080.609 | 0.0001441%
2026 | 475 | CB 475 | Tier-1 | Non-HFTD---5 | 2--4 | 2.5995 | 183 | 100% | 67.5852 | 97.2% | 0% | 2.801% | 3.2518 | 0 | 0 | 3.2518 | 0 | 3.102 | 2.6855 | 1.1551 | 3.102 | 2.6855 | 1.1551 | 3.2677 | 2.829 | 1.1551 | 4.811% | 0.0082144 | 0.0078078 | 8227.6449 | 1225.4309 | 526.326 | 6475.888 | 8239.6468 | 0 | 0 | 8239.6468 | 0.0001072%
2026 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.038118 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1705 | 0.03938 | 29.7244 | 1.1705 | 0.03938 | 29.7244 | 1.2331 | 0.041484 | 29.7244 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2026 | 95 | 95-37F | Tier-1 | Non-HFTD---20 | 2--1 | 0.088838 | 3 | 100% | 0.46434 | 14.45% | 70.16% | 15.4% | 0.0033212 | 0 | 0 | 0.0033212 | 0 | 0.0031682 | 0.091778 | 0.03452 | 0.0031682 | 0.091778 | 0.03452 | 0.0033375 | 0.096682 | 0.03452 | 0.7152% | 0.0053792 | 0.0051129 | 86.3215 | 1.055 | 63.4057 | 21.8608 | 90.1673 | 0 | 0 | 90.1673 | 1.095e-07%
2026 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 14.7171 | 588 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 19.0725 | 15.2041 | 1.2544 | 19.0725 | 15.2041 | 1.2544 | 20.0916 | 16.0165 | 1.2544 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2026 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 8.9137 | 168 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 100.8529 | 9.2087 | 10.952 | 100.8529 | 9.2087 | 10.952 | 106.2416 | 9.7007 | 10.952 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2026 | AM1 | CB AM1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.6244 | 115 | 100% | 3.3578 | 29.51% | 0% | 70.49% | 0.049051 | 0 | 0 | 0.049051 | 0 | 0.046791 | 3.7444 | 0.012496 | 0.046791 | 3.7444 | 0.012496 | 0.049291 | 3.9444 | 0.012496 | 1.461% | 0.0096132 | 0.0091373 | 349.2893 | 0.61104 | 122.8396 | 225.8387 | 362.1114 | 0 | 0 | 362.1114 | 1.618e-06%
2026 | 580 | 580-690AE | Tier-1 | Non-HFTD---19 | 1--3 | 0.067992 | 0 | 100% | 0.50006 | 86.19% | 0% | 13.81% | 0.021335 | 0 | 0 | 0.021335 | 0 | 0.020352 | 0.070243 | 0.28974 | 0.020352 | 0.070243 | 0.28974 | 0.02144 | 0.073996 | 0.28974 | 4.266% | 0.0002812 | 0.00026728 | 1778.3079 | 201.1614 | 323.7794 | 1253.3671 | 1791.0959 | 0 | 0 | 1791.0959 | 7.035e-07%
2026 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 0.99238 | 48 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.87392 | 1.0252 | 0.85243 | 0.87392 | 1.0252 | 0.85243 | 0.92062 | 1.08 | 0.85243 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2026 | 416 | 416-35F | Tier-1 | Non-HFTD---17 | 1--1 | 0.98558 | 46 | 100% | 1.2958 | 41.8% | 0% | 58.2% | 0.026812 | 0 | 0 | 0.026812 | 0 | 0.025577 | 1.0182 | 0.02512 | 0.025577 | 1.0182 | 0.02512 | 0.026943 | 1.0726 | 0.02512 | 2.069% | 0.0029674 | 0.0028205 | 436.6793 | 1.3522 | 198.3951 | 236.932 | 449.9146 | 0 | 0 | 449.9146 | 8.842e-07%
2026 | 719 | 719-857F | Tier-1 | Non-HFTD---20 | 1--1 | 0.4199 | 8 | 100% | 0.29905 | 18.65% | 0% | 81.35% | 0.0027613 | 0 | 0 | 0.0027613 | 0 | 0.002634 | 0.43379 | 0.0060721 | 0.002634 | 0.43379 | 0.0060721 | 0.0027748 | 0.45697 | 0.0060721 | 0.9233% | 0.0010186 | 0.00096818 | 293.5913 | 0.17971 | 76.4595 | 216.9521 | 306.0289 | 0 | 0 | 306.0289 | 9.106e-08%
2026 | 972 | 972-1642 | Tier-2 | Tier-2---16 | 5--2 | 0.038636 | 0 | 100% | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.039915 | 0 | 0 | 0.039915 | 0 | 0 | 0.042048 | 0 | 0% | 0.11047 | 0.105 | 1677.3427 | 1.9611 | 1510.6909 | 164.6906 | 1764.6951 | 0 | 0 | 1764.6951 | 0%
2026 | 199 | 199-39AE | Tier-1 | Non-HFTD---13 | 2--2 | 2.4932 | 59 | 100% | 5.5063 | 65.09% | 0% | 34.91% | 0.17742 | 0 | 0 | 0.17742 | 0 | 0.16925 | 2.5757 | 0.065709 | 0.16925 | 2.5757 | 0.065709 | 0.17829 | 2.7133 | 0.065709 | 3.222% | 0.0073958 | 0.0070297 | 744.5212 | 70.5063 | 77.1367 | 596.8782 | 758.0554 | 0 | 0 | 758.0554 | 5.851e-06%
2026 | AM2 | CB AM2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.125 | 184 | 100% | 11.1682 | 52.54% | 0% | 47.46% | 0.29045 | 0 | 0 | 0.29045 | 0 | 0.27707 | 7.3607 | 0.037642 | 0.27707 | 7.3607 | 0.037642 | 0.29188 | 7.754 | 0.037642 | 2.601% | 0.02008 | 0.019086 | 556.1818 | 2.2661 | 303.5202 | 250.3954 | 569.9286 | 0 | 0 | 569.9286 | 9.578e-06%
2026 | RD4 | RD4-48F | Tier-1 | Non-HFTD---16 | 2--1 | 3.5216 | 269 | 100% | 3.4032 | 33.95% | 0% | 66.05% | 0.057196 | 0 | 0 | 0.057196 | 0 | 0.054561 | 3.6382 | 0.014997 | 0.054561 | 3.6382 | 0.014997 | 0.057476 | 3.8326 | 0.014997 | 1.681% | 0.0093526 | 0.0088896 | 363.8725 | 1.432 | 137.6932 | 224.7473 | 376.3882 | 0 | 0 | 376.3882 | 1.886e-06%
2026 | 852 | CB 852 | Tier-1 | Non-HFTD---7 | 1--5 | 0.13314 | 18 | 100% | 34.4559 | 99.59% | 0% | 0.4114% | 1.6986 | 0 | 0 | 1.6986 | 0 | 1.6203 | 0.13755 | 11.7797 | 1.6203 | 0.13755 | 11.7797 | 1.7069 | 0.1449 | 11.7797 | 4.93% | 0.0007638 | 0.00072599 | 45111.1902 | 8830.4114 | 18.3177 | 36262.461 | 45120.855 | 0 | 0 | 45120.855 | 5.601e-05%
2026 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.50061 | 49 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 18.259 | 0.51717 | 35.3054 | 18.259 | 0.51717 | 35.3054 | 19.2346 | 0.54481 | 35.3054 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2026 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 6.2775 | 182 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 452.3048 | 6.4852 | 69.7438 | 452.3048 | 6.4852 | 69.7438 | 476.4721 | 6.8317 | 69.7438 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2026 | 180 | CB 180 | Tier-1 | Non-HFTD---13 | 1--3 | 0.94796 | 5 | 100% | 7.7122 | 90.8% | 0% | 9.202% | 0.34662 | 0 | 0 | 0.34662 | 0 | 0.33065 | 0.97933 | 0.33763 | 0.33065 | 0.97933 | 0.33763 | 0.34832 | 1.0317 | 0.33763 | 4.494% | 0.0030172 | 0.0028678 | 2556.0648 | 24.9107 | 2190.1936 | 340.9605 | 2568.3144 | 0 | 0 | 2568.3144 | 1.143e-05%
2026 | 430 | 430-321AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.3352 | 34 | 100% | 0.30658 | 15.66% | 0% | 84.34% | 0.0023773 | 0 | 0 | 0.0023773 | 0 | 0.0022678 | 0.3463 | 0.0065486 | 0.0022678 | 0.3463 | 0.0065486 | 0.0023889 | 0.3648 | 0.0065486 | 0.7754% | 0.0009426 | 0.00089594 | 325.2518 | 3.1534 | 57.757 | 264.3414 | 339.5368 | 0 | 0 | 339.5368 | 7.839e-08%
2026 | HP1 | CB HP1 | Tier-1 | Non-HFTD---10 | 4--1 | 18.2582 | 619 | 100% | 16.6755 | 30.85% | 0% | 69.15% | 0.25463 | 0 | 0 | 0.25463 | 0 | 0.2429 | 18.8624 | 0.012878 | 0.2429 | 18.8624 | 0.012878 | 0.25588 | 19.8702 | 0.012878 | 1.527% | 0.048206 | 0.04582 | 345.9227 | 0.91802 | 123.9165 | 221.0881 | 358.3803 | 0 | 0 | 358.3803 | 8.397e-06%
2026 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 6.9867 | 127 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 67.9477 | 7.2179 | 9.4138 | 67.9477 | 7.2179 | 9.4138 | 71.5783 | 7.6036 | 9.4138 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2026 | 461 | 461-24F | Tier-1 | Non-HFTD---15 | 1--3 | 0.42368 | 9 | 100% | 4.3764 | 89.98% | 0% | 10.02% | 0.19492 | 0 | 0 | 0.19492 | 0 | 0.18594 | 0.4377 | 0.42481 | 0.18594 | 0.4377 | 0.42481 | 0.19587 | 0.46109 | 0.42481 | 4.454% | 0.0015528 | 0.0014759 | 2818.3832 | 300.604 | 715.3571 | 1802.422 | 2833.0954 | 0 | 0 | 2833.0954 | 6.428e-06%
2026 | 504 | 504-287R | Tier-2 | Tier-2---12 | 4--4 | 7.8402 | 264 | 100% | 501.8283 | 98.94% | 0% | 1.063% | 24.5765 | 0 | 0 | 24.5765 | 0 | 23.4443 | 8.0996 | 2.8945 | 23.4443 | 8.0996 | 2.8945 | 24.6969 | 8.5324 | 2.8945 | 4.897% | 0.033132 | 0.031492 | 15146.1514 | 2418.4341 | 53.5553 | 12674.162 | 15154.5352 | 0 | 0 | 15154.5352 | 0.0008104%
2026 | SW1 | CB SW1 | Tier-1 | Non-HFTD---17 | 1--1 | 1.5451 | 35 | 100% | 1.6455 | 48.03% | 0% | 51.97% | 0.039125 | 0 | 0 | 0.039125 | 0 | 0.037322 | 1.5962 | 0.023381 | 0.037322 | 1.5962 | 0.023381 | 0.039317 | 1.6815 | 0.023381 | 2.378% | 0.0038896 | 0.0036971 | 423.0612 | 20.0581 | 101.1853 | 301.8178 | 434.5106 | 0 | 0 | 434.5106 | 1.29e-06%
2026 | 245 | CB 245 | Tier-1 | Non-HFTD---2 | 4--4 | 7.1536 | 280 | 100% | 248.3247 | 30.26% | 68.14% | 1.595% | 3.7197 | 0 | 0 | 3.7197 | 0 | 3.5483 | 7.3904 | 0.48012 | 3.5483 | 7.3904 | 0.48012 | 3.7379 | 7.7853 | 0.48012 | 1.498% | 0.044637 | 0.042428 | 5563.1534 | 331.3651 | 3704.159 | 1527.6293 | 5765.2004 | 0 | 0 | 5765.2004 | 0.0001227%
2026 | 74 | 74-24R | Tier-1 | Non-HFTD---12 | 3--2 | 8.6284 | 269 | 100% | 13.7632 | 60.93% | 0% | 39.07% | 0.41507 | 0 | 0 | 0.41507 | 0 | 0.39595 | 8.914 | 0.044419 | 0.39595 | 8.914 | 0.044419 | 0.41711 | 9.3902 | 0.044419 | 3.016% | 0.022875 | 0.021743 | 601.6686 | 1.4002 | 380.4228 | 219.8456 | 613.912 | 0 | 0 | 613.912 | 1.369e-05%
2026 | 341 | 341-920 | Tier-1 | Non-HFTD---3 | 4--3 | 12.9709 | 837 | 100% | 161.886 | 95.19% | 0% | 4.806% | 7.6283 | 0 | 0 | 7.6283 | 0 | 7.2768 | 13.4001 | 0.54304 | 7.2768 | 13.4001 | 0.54304 | 7.6657 | 14.1161 | 0.54304 | 4.712% | 0.035928 | 0.034149 | 4505.8945 | 872.5831 | 176.1223 | 3457.1891 | 4517.1713 | 0 | 0 | 4517.1713 | 0.0002516%
2026 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 9.4684 | 622 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 94.2031 | 9.7817 | 9.6305 | 94.2031 | 9.7817 | 9.6305 | 99.2365 | 10.3044 | 9.6305 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2026 | GM2 | CB GM2 | Tier-1 | Non-HFTD---2 | 4--3 | 12.8498 | 1166 | 100% | 185.8665 | 95.73% | 0% | 4.266% | 8.8079 | 0 | 0 | 8.8079 | 0 | 8.4022 | 13.275 | 0.63293 | 8.4022 | 13.275 | 0.63293 | 8.8511 | 13.9843 | 0.63293 | 4.739% | 0.042423 | 0.040323 | 4381.2884 | 678.342 | 70.1655 | 3632.7808 | 4391.021 | 0 | 0 | 4391.021 | 0.0002905%
2026 | 52 | 52-20R | Tier-1 | Non-HFTD---14 | 2--2 | 3.9289 | 85 | 100% | 5.9584 | 48.34% | 0% | 51.66% | 0.14257 | 0 | 0 | 0.14257 | 0 | 0.136 | 4.059 | 0.033506 | 0.136 | 4.059 | 0.033506 | 0.14327 | 4.2758 | 0.033506 | 2.393% | 0.011327 | 0.010766 | 526.0509 | 0.21605 | 278.8999 | 246.935 | 540.204 | 0 | 0 | 540.204 | 4.701e-06%
2026 | 504 | CB 504 | Tier-1 | Non-HFTD---7 | 2--3 | 4.505 | 174 | 100% | 34.4975 | 90.08% | 0% | 9.923% | 1.5382 | 0 | 0 | 1.5382 | 0 | 1.4673 | 4.6541 | 0.31528 | 1.4673 | 4.6541 | 0.31528 | 1.5457 | 4.9027 | 0.31528 | 4.459% | 0.013226 | 0.012571 | 2608.352 | 206.1348 | 1114.8562 | 1287.361 | 2621.8318 | 0 | 0 | 2621.8318 | 5.072e-05%
2026 | 114 | 114-18AE | Tier-1 | Non-HFTD---6 | 3--3 | 4.008 | 263 | 100% | 66.6834 | 4.686% | 91.31% | 4.003% | 0.15468 | 0 | 0 | 0.15468 | 0 | 0.14756 | 4.1406 | 0.035637 | 0.14756 | 4.1406 | 0.035637 | 0.15544 | 4.3619 | 0.035637 | 0.232% | 0.019386 | 0.018426 | 3439.7723 | 23.4352 | 2933.6014 | 482.7357 | 3610.5136 | 0 | 0 | 3610.5136 | 5.101e-06%
2026 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 3.289 | 349 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 28.7981 | 3.3979 | 8.4754 | 28.7981 | 3.3979 | 8.4754 | 30.3368 | 3.5794 | 8.4754 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2026 | 171 | 171-704R | Tier-1 | Non-HFTD---6 | 4--2 | 4.9861 | 76 | 100% | 80.6143 | 61.35% | 34.31% | 4.34% | 2.4483 | 0 | 0 | 2.4483 | 0 | 2.3355 | 5.1511 | 0.4534 | 2.3355 | 5.1511 | 0.4534 | 2.4603 | 5.4264 | 0.4534 | 3.037% | 0.048088 | 0.045707 | 1676.4044 | 165.028 | 536.4334 | 974.9431 | 1710.1431 | 0 | 0 | 1710.1431 | 8.074e-05%
2026 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 8.351 | 10 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 15.2309 | 8.6273 | 1.7654 | 15.2309 | 8.6273 | 1.7654 | 16.0447 | 9.0883 | 1.7654 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2026 | 59 | 59-465 | Tier-1 | Non-HFTD---6 | 4--3 | 7.5326 | 198 | 100% | 77.379 | 64.48% | 28.11% | 7.401% | 2.4699 | 0 | 0 | 2.4699 | 0 | 2.3562 | 7.7819 | 0.30278 | 2.3562 | 7.7819 | 0.30278 | 2.4821 | 8.1977 | 0.30278 | 3.192% | 0.036127 | 0.034339 | 2141.862 | 301.1171 | 633.9997 | 1206.7452 | 2181.4767 | 0 | 0 | 2181.4767 | 8.145e-05%
2026 | 588 | CB 588 | Tier-1 | Non-HFTD---9 | 1--4 | 0.38598 | 4 | 100% | 21.538 | 98.85% | 0% | 1.146% | 1.0539 | 0 | 0 | 1.0539 | 0 | 1.0054 | 0.39876 | 2.5212 | 1.0054 | 0.39876 | 2.5212 | 1.0591 | 0.42006 | 2.5212 | 4.893% | 0.0014694 | 0.0013967 | 14657.7162 | 2735.8339 | 186.8229 | 11735.0595 | 14666.4638 | 0 | 0 | 14666.4638 | 3.475e-05%
2026 | 1081 | 1081-666F | Tier-1 | Non-HFTD---4 | 3--4 | 5.8293 | 751 | 100% | 169.8745 | 80.26% | 17.52% | 2.222% | 6.7489 | 0 | 0 | 6.7489 | 0 | 6.438 | 6.0222 | 1.069 | 6.438 | 6.0222 | 1.069 | 6.782 | 6.344 | 1.069 | 3.973% | 0.027363 | 0.026009 | 6208.1833 | 1026.9206 | 1026.1932 | 4155.0696 | 6272.0024 | 0 | 0 | 6272.0024 | 0.0002226%
2026 | 86 | 86-552F | Tier-1 | Non-HFTD---2 | 4--3 | 20.0174 | 1804 | 100% | 186.6357 | 92.7% | 0% | 7.302% | 8.5639 | 0 | 0 | 8.5639 | 0 | 8.1694 | 20.6799 | 0.39504 | 8.1694 | 20.6799 | 0.39504 | 8.6059 | 21.7848 | 0.39504 | 4.589% | 0.057976 | 0.055107 | 3219.1671 | 590.7148 | 100.2194 | 2528.2329 | 3231.4085 | 0 | 0 | 3231.4085 | 0.0002824%
2026 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 7.8693 | 840 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 453.1135 | 8.1297 | 55.7356 | 453.1135 | 8.1297 | 55.7356 | 477.324 | 8.5641 | 55.7356 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2026 | 151 | 151-1044F | Tier-1 | Non-HFTD---18 | 1--1 | 1.7676 | 67 | 100% | 0.90758 | 10.2% | 0% | 89.8% | 0.0045835 | 0 | 0 | 0.0045835 | 0 | 0.0043723 | 1.8261 | 0.0023944 | 0.0043723 | 1.8261 | 0.0023944 | 0.0046059 | 1.9236 | 0.0023944 | 0.505% | 0.0041016 | 0.0038986 | 221.2741 | 0.23379 | 40.1127 | 180.9276 | 231.6219 | 0 | 0 | 231.6219 | 1.511e-07%
2026 | 1119 | 1119-9F | Tier-1 | Non-HFTD---7 | 2--3 | 1.7245 | 235 | 100% | 44.0578 | 1.729% | 95.21% | 3.066% | 0.037698 | 0 | 0 | 0.037698 | 0 | 0.035961 | 1.7815 | 0.020186 | 0.035961 | 1.7815 | 0.020186 | 0.037882 | 1.8767 | 0.020186 | 0.08556% | 0.01155 | 0.010978 | 3814.4644 | 11.0382 | 3336.1347 | 467.2915 | 4009.6797 | 0 | 0 | 4009.6797 | 1.243e-06%
2026 | 321 | 321-741 | Tier-1 | Non-HFTD---18 | 1--1 | 1.6644 | 22 | 100% | 1.2108 | 17.09% | 0% | 82.91% | 0.010243 | 0 | 0 | 0.010243 | 0 | 0.0097709 | 1.7195 | 0.0056824 | 0.0097709 | 1.7195 | 0.0056824 | 0.010293 | 1.8114 | 0.0056824 | 0.8459% | 0.0042182 | 0.0040094 | 287.0469 | 0.17908 | 70.6743 | 216.1935 | 299.441 | 0 | 0 | 299.441 | 3.378e-07%
2026 | CMP1 | CB CMP1 | Tier-1 | Non-HFTD---7 | 3--3 | 5.6403 | 486 | 100% | 37.1183 | 89.86% | 0% | 10.14% | 1.6511 | 0 | 0 | 1.6511 | 0 | 1.5751 | 5.827 | 0.27031 | 1.5751 | 5.827 | 0.27031 | 1.6592 | 6.1383 | 0.27031 | 4.448% | 0.016556 | 0.015736 | 2241.9834 | 320.7107 | 77.0021 | 1844.2706 | 2253.8174 | 0 | 0 | 2253.8174 | 5.445e-05%
2026 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 8.4553 | 119 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 245.3601 | 8.7351 | 28.0889 | 245.3601 | 8.7351 | 28.0889 | 258.47 | 9.2019 | 28.0889 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2026 | 221 | 221-1251R | Tier-1 | Non-HFTD---2 | 5--4 | 16.3418 | 150 | 100% | 1814.8505 | 87.56% | 11.92% | 0.5209% | 78.6628 | 0 | 0 | 78.6628 | 0 | 75.039 | 16.8827 | 4.4447 | 75.039 | 16.8827 | 4.4447 | 79.0484 | 17.7847 | 4.4447 | 4.334% | 0.27478 | 0.26118 | 6604.7785 | 826.9947 | 747.1453 | 5030.6385 | 6647.5552 | 0 | 0 | 6647.5552 | 0.002594%
2026 | 1435 | 1435-50 | Tier-1 | Non-HFTD---10 | 3--2 | 8.8248 | 347 | 100% | 15.0882 | 59.27% | 0% | 40.73% | 0.44264 | 0 | 0 | 0.44264 | 0 | 0.42225 | 9.1168 | 0.046315 | 0.42225 | 9.1168 | 0.046315 | 0.44481 | 9.604 | 0.046315 | 2.934% | 0.026149 | 0.024855 | 577.0099 | 71.0904 | 94.7801 | 411.1393 | 589.2502 | 0 | 0 | 589.2502 | 1.46e-05%
2026 | BY2 | CB BY2 | Tier-1 | Non-HFTD---14 | 3--1 | 5.662 | 220 | 100% | 6.8497 | 39.29% | 0% | 60.71% | 0.13321 | 0 | 0 | 0.13321 | 0 | 0.12707 | 5.8493 | 0.021724 | 0.12707 | 5.8493 | 0.021724 | 0.13386 | 6.1619 | 0.021724 | 1.945% | 0.017488 | 0.016622 | 391.6915 | 5.1993 | 144.7113 | 241.7808 | 404.0761 | 0 | 0 | 404.0761 | 4.393e-06%
2026 | 1094 | 1094-8AE | Tier-1 | Non-HFTD---17 | 1--2 | 0.30739 | 2 | 100% | 1.7277 | 85.41% | 0% | 14.59% | 0.073046 | 0 | 0 | 0.073046 | 0 | 0.069681 | 0.31756 | 0.21943 | 0.069681 | 0.31756 | 0.21943 | 0.073404 | 0.33453 | 0.21943 | 4.228% | 0.0010582 | 0.0010058 | 1632.6499 | 227.3238 | 25.8915 | 1379.4346 | 1645.0517 | 0 | 0 | 1645.0517 | 2.409e-06%
2026 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 11.3022 | 644 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 1047.5713 | 11.6763 | 89.7179 | 1047.5713 | 11.6763 | 89.7179 | 1103.5445 | 12.3002 | 89.7179 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2026 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 5.7011 | 351 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 382.4036 | 5.8898 | 64.9265 | 382.4036 | 5.8898 | 64.9265 | 402.8359 | 6.2045 | 64.9265 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2026 | 184 | CB 184 | Tier-1 | Non-HFTD---6 | 3--3 | 0.49848 | 58 | 100% | 52.4866 | 0.7232% | 98.61% | 0.668% | 0.018789 | 0 | 0 | 0.018789 | 0 | 0.017923 | 0.51498 | 0.034803 | 0.017923 | 0.51498 | 0.034803 | 0.018881 | 0.5425 | 0.034803 | 0.0358% | 0.015821 | 0.015038 | 3317.5286 | 5.4671 | 2617.7865 | 694.2749 | 3489.0489 | 0 | 0 | 3489.0489 | 6.196e-07%
2026 | 1049 | CB 1049 | Tier-1 | Non-HFTD---14 | 3--1 | 5.6832 | 256 | 100% | 5.616 | 24.5% | 0% | 75.5% | 0.068108 | 0 | 0 | 0.068108 | 0 | 0.06497 | 5.8713 | 0.011066 | 0.06497 | 5.8713 | 0.011066 | 0.068442 | 6.185 | 0.011066 | 1.213% | 0.016475 | 0.015659 | 340.8813 | 1.1864 | 100.8318 | 238.863 | 354.2843 | 0 | 0 | 354.2843 | 2.246e-06%
2026 | 1418 | CB 1418 | Tier-1 | Non-HFTD---8 | 3--3 | 6.1513 | 238 | 100% | 37.4539 | 88.02% | 0% | 11.98% | 1.6319 | 0 | 0 | 1.6319 | 0 | 1.5567 | 6.3548 | 0.24496 | 1.5567 | 6.3548 | 0.24496 | 1.6399 | 6.6944 | 0.24496 | 4.357% | 0.021901 | 0.020817 | 1710.114 | 123.2993 | 769.7961 | 817.0186 | 1720.7826 | 0 | 0 | 1720.7826 | 5.381e-05%
2026 | 480 | CB 480 | Tier-1 | Non-HFTD---9 | 3--2 | 5.8805 | 429 | 100% | 25.8202 | 85.83% | 0% | 14.17% | 1.097 | 0 | 0 | 1.097 | 0 | 1.0465 | 6.0751 | 0.17226 | 1.0465 | 6.0751 | 0.17226 | 1.1024 | 6.3997 | 0.17226 | 4.249% | 0.015407 | 0.014644 | 1675.8946 | 13.068 | 1380.5081 | 282.3185 | 1688.259 | 0 | 0 | 1688.259 | 3.618e-05%
2026 | BH1 | CB BH1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.0502 | 26 | 100% | 1.0465 | 22.49% | 0% | 77.51% | 0.011651 | 0 | 0 | 0.011651 | 0 | 0.011114 | 1.085 | 0.010244 | 0.011114 | 1.085 | 0.010244 | 0.011708 | 1.1429 | 0.010244 | 1.113% | 0.0030896 | 0.0029367 | 338.7265 | 0.6221 | 97.3891 | 240.7153 | 352.3993 | 0 | 0 | 352.3993 | 3.842e-07%
2026 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 6.7754 | 306 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 61.1593 | 6.9996 | 8.7375 | 61.1593 | 6.9996 | 8.7375 | 64.4271 | 7.3736 | 8.7375 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2026 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 33.4712 | 1327 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 3060.5719 | 34.5789 | 88.5099 | 3060.5719 | 34.5789 | 88.5099 | 3224.1024 | 36.4264 | 88.5099 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2026 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 4.4727 | 32 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.8558 | 4.6207 | 0.40162 | 1.8558 | 4.6207 | 0.40162 | 1.9549 | 4.8676 | 0.40162 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2026 | 928 | CB 928 | Tier-2 | Tier-2---7 | 4--5 | 3.6036 | 30 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 65.3395 | 0 | 0 | 65.3395 | 0 | 62.3294 | 3.7229 | 16.7424 | 62.3294 | 3.7229 | 16.7424 | 65.6598 | 3.9218 | 16.7424 | 3.948% | 0.057199 | 0.054367 | 28934.4603 | 4597.4585 | 5524.6499 | 18812.3519 | 29239.4879 | 0 | 0 | 29239.4879 | 0.002155%
2026 | 223 | 223-47AE | Tier-2 | Tier-2---19 | 1--3 | 1.211 | 4 | 100% | 19.4153 | 96.46% | 0% | 3.541% | 0.92702 | 0 | 0 | 0.92702 | 0 | 0.88432 | 1.2511 | 0.70685 | 0.88432 | 1.2511 | 0.70685 | 0.93157 | 1.3179 | 0.70685 | 4.775% | 0.0044072 | 0.004189 | 4405.3509 | 653.8395 | 200.8811 | 3550.6304 | 4413.4748 | 0 | 0 | 4413.4748 | 3.057e-05%
2026 | 274 | 274-23R | Tier-1 | Non-HFTD---2 | 4--3 | 14.1254 | 479 | 100% | 237.9284 | 4.707% | 91.23% | 4.063% | 0.55433 | 0 | 0 | 0.55433 | 0 | 0.5288 | 14.5928 | 0.036237 | 0.5288 | 14.5928 | 0.036237 | 0.55705 | 15.3725 | 0.036237 | 0.233% | 0.05657 | 0.05377 | 4205.9111 | 11.172 | 3702.6633 | 492.0758 | 4414.6365 | 0 | 0 | 4414.6365 | 1.828e-05%
2026 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 7.8388 | 378 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 428.2273 | 8.0982 | 52.8792 | 428.2273 | 8.0982 | 52.8792 | 451.1081 | 8.5309 | 52.8792 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2026 | 957 | 957-493 | Tier-1 | Non-HFTD---17 | 1--2 | 0.48785 | 55 | 100% | 2.0962 | 82.3% | 0% | 17.7% | 0.085395 | 0 | 0 | 0.085395 | 0 | 0.081461 | 0.504 | 0.16163 | 0.081461 | 0.504 | 0.16163 | 0.085814 | 0.53093 | 0.16163 | 4.074% | 0.001752 | 0.0016653 | 1196.4405 | 130.6529 | 183.8941 | 881.8936 | 1207.4687 | 0 | 0 | 1207.4687 | 2.816e-06%
2026 | 298 | 298-42R | Tier-1 | Non-HFTD---15 | 2--2 | 2.2522 | 46 | 100% | 3.8263 | 63.59% | 0% | 36.41% | 0.12045 | 0 | 0 | 0.12045 | 0 | 0.1149 | 2.3268 | 0.04938 | 0.1149 | 2.3268 | 0.04938 | 0.12104 | 2.4511 | 0.04938 | 3.148% | 0.0063514 | 0.006037 | 602.4284 | 45.032 | 128.6085 | 428.7879 | 613.8503 | 0 | 0 | 613.8503 | 3.972e-06%
2026 | 280 | 280-382AE | Tier-1 | Non-HFTD---3 | 4--3 | 4.587 | 113 | 100% | 117.9502 | 9.67% | 87.78% | 2.549% | 0.56458 | 0 | 0 | 0.56458 | 0 | 0.53858 | 4.7388 | 0.11365 | 0.53858 | 4.7388 | 0.11365 | 0.56735 | 4.992 | 0.11365 | 0.4787% | 0.044174 | 0.041988 | 2670.1025 | 42.9877 | 2159.6326 | 467.4822 | 2795.7093 | 0 | 0 | 2795.7093 | 1.862e-05%
2026 | 504 | 504-40R | Tier-1 | Non-HFTD---1 | 3--5 | 7.4225 | 827 | 100% | 796.3763 | 99.35% | 0% | 0.6476% | 39.1654 | 0 | 0 | 39.1654 | 0 | 37.3611 | 7.6682 | 4.8722 | 37.3611 | 7.6682 | 4.8722 | 39.3573 | 8.0779 | 4.8722 | 4.918% | 0.025961 | 0.024676 | 30675.6364 | 4949.6837 | 226.8975 | 25499.0552 | 30685.9814 | 0 | 0 | 30685.9814 | 0.001292%
2026 | 313 | CB 313 | Tier-1 | Non-HFTD---1 | 3--5 | 1.4046 | 49 | 100% | 413.0978 | 31.58% | 68.15% | 0.2787% | 6.4568 | 0 | 0 | 6.4568 | 0 | 6.1594 | 1.451 | 4.2448 | 6.1594 | 1.451 | 4.2448 | 6.4885 | 1.5286 | 4.2448 | 1.563% | 0.023731 | 0.022556 | 17407.518 | 802.6638 | 11509.0826 | 5095.7715 | 18027.8111 | 0 | 0 | 18027.8111 | 0.0002129%
2026 | 412 | 412-23AE | Tier-1 | Non-HFTD---7 | 3--3 | 1.1481 | 46 | 100% | 36.9619 | 12.24% | 85.64% | 2.113% | 0.22399 | 0 | 0 | 0.22399 | 0 | 0.21367 | 1.1861 | 0.18015 | 0.21367 | 1.1861 | 0.18015 | 0.22508 | 1.2494 | 0.18015 | 0.606% | 0.014019 | 0.013325 | 2636.6319 | 50.1124 | 2071.6936 | 514.8259 | 2757.1322 | 0 | 0 | 2757.1322 | 7.386e-06%
2026 | FM2 | CB FM2 | Tier-1 | Non-HFTD---5 | 2--4 | 0.69792 | 11 | 100% | 52.7223 | 13.09% | 85.83% | 1.077% | 0.34171 | 0 | 0 | 0.34171 | 0 | 0.32597 | 0.72101 | 0.4521 | 0.32597 | 0.72101 | 0.4521 | 0.34339 | 0.75954 | 0.4521 | 0.6481% | 0.0078724 | 0.0074827 | 6697.1021 | 78.5971 | 5715.8481 | 902.657 | 7000.2057 | 0 | 0 | 7000.2057 | 1.127e-05%
2026 | 781 | 781-1356R | Tier-1 | Non-HFTD---6 | 3--3 | 1.2461 | 146 | 100% | 45.6239 | 7.996% | 89.78% | 2.228% | 0.18059 | 0 | 0 | 0.18059 | 0 | 0.17227 | 1.2873 | 0.13382 | 0.17227 | 1.2873 | 0.13382 | 0.18147 | 1.3561 | 0.13382 | 0.3958% | 0.014432 | 0.013718 | 3161.2121 | 4.0758 | 2704.8503 | 452.2859 | 3312.6768 | 0 | 0 | 3312.6768 | 5.955e-06%
2026 | 1435 | 1435-49F | Tier-1 | Non-HFTD---18 | 2--1 | 2.382 | 56 | 100% | 2.1334 | 19.42% | 0% | 80.58% | 0.020506 | 0 | 0 | 0.020506 | 0 | 0.019562 | 2.4609 | 0.0079492 | 0.019562 | 2.4609 | 0.0079492 | 0.020607 | 2.5923 | 0.0079492 | 0.9612% | 0.0065472 | 0.0062231 | 325.8446 | 0.86487 | 82.925 | 242.0548 | 339.5187 | 0 | 0 | 339.5187 | 6.762e-07%
2026 | 730 | CB 730 | Tier-1 | Non-HFTD---8 | 3--3 | 6.5873 | 247 | 100% | 39.2172 | 89.21% | 0% | 10.79% | 1.7319 | 0 | 0 | 1.7319 | 0 | 1.6521 | 6.8053 | 0.24277 | 1.6521 | 6.8053 | 0.24277 | 1.7404 | 7.1689 | 0.24277 | 4.416% | 0.017589 | 0.016718 | 2229.6927 | 2.4263 | 1997.325 | 229.9414 | 2242.2171 | 0 | 0 | 2242.2171 | 5.711e-05%
2026 | VS1 | CB VS1 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6964 | 484 | 100% | 11.7597 | 45.03% | 0% | 54.97% | 0.26214 | 0 | 0 | 0.26214 | 0 | 0.25006 | 10.0173 | 0.024963 | 0.25006 | 10.0173 | 0.024963 | 0.26342 | 10.5526 | 0.024963 | 2.229% | 0.026595 | 0.025278 | 442.1842 | 4.4933 | 194.8415 | 242.8495 | 454.8421 | 0 | 0 | 454.8421 | 8.644e-06%
2026 | 570 | CB 570 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3449 | 49 | 100% | 7.1017 | 67.21% | 0% | 32.79% | 0.23626 | 0 | 0 | 0.23626 | 0 | 0.22537 | 2.4225 | 0.093034 | 0.22537 | 2.4225 | 0.093034 | 0.23741 | 2.5519 | 0.093034 | 3.327% | 0.0078126 | 0.0074259 | 909.0044 | 0.23797 | 637.9097 | 270.8567 | 924.5283 | 0 | 0 | 924.5283 | 7.791e-06%
2026 | 718 | 718-483R | Tier-1 | Non-HFTD---14 | 2--2 | 4.2839 | 92 | 100% | 8.2181 | 68.73% | 0% | 31.27% | 0.2796 | 0 | 0 | 0.2796 | 0 | 0.26672 | 4.4257 | 0.060266 | 0.26672 | 4.4257 | 0.060266 | 0.28097 | 4.6621 | 0.060266 | 3.402% | 0.013173 | 0.012521 | 623.8598 | 87.3514 | 82.9145 | 453.5939 | 634.0188 | 0 | 0 | 634.0188 | 9.22e-06%
2026 | 305 | CB 305 | Tier-1 | Non-HFTD---1 | 4--5 | 5.6647 | 1678 | 100% | 2786.7739 | 97.11% | 2.732% | 0.1605% | 133.9547 | 0 | 0 | 133.9547 | 0 | 127.7837 | 5.8522 | 21.8351 | 127.7837 | 5.8522 | 21.8351 | 134.6113 | 6.1649 | 21.8351 | 4.807% | 0.073949 | 0.070288 | 37685.1802 | 5958.9331 | 946.9636 | 30779.2836 | 37741.9553 | 0 | 0 | 37741.9553 | 0.004417%
2026 | S1 | CB S1 | Tier-1 | Non-HFTD---12 | 3--1 | 9.143 | 170 | 100% | 10.789 | 35.54% | 0% | 64.46% | 0.18979 | 0 | 0 | 0.18979 | 0 | 0.18105 | 9.4455 | 0.019168 | 0.18105 | 9.4455 | 0.019168 | 0.19072 | 9.9502 | 0.019168 | 1.759% | 0.026358 | 0.025053 | 409.3304 | 3.5481 | 148.5276 | 257.2547 | 423.0718 | 0 | 0 | 423.0718 | 6.259e-06%
2026 | CS3 | CB CS3 | Tier-1 | Non-HFTD---12 | 3--1 | 10.2084 | 309 | 100% | 11.962 | 43.21% | 0% | 56.79% | 0.25586 | 0 | 0 | 0.25586 | 0 | 0.24407 | 10.5462 | 0.023143 | 0.24407 | 10.5462 | 0.023143 | 0.25711 | 11.1097 | 0.023143 | 2.139% | 0.027808 | 0.026432 | 430.1588 | 12.7842 | 130.688 | 286.6866 | 442.8806 | 0 | 0 | 442.8806 | 8.437e-06%
2026 | 334 | CB 334 | Tier-2 | Tier-2---17 | 3--4 | 5.1123 | 83 | 100% | 70.5162 | 95.08% | 0% | 4.917% | 3.3189 | 0 | 0 | 3.3189 | 0 | 3.166 | 5.2815 | 0.59946 | 3.166 | 5.2815 | 0.59946 | 3.3352 | 5.5637 | 0.59946 | 4.707% | 0.014478 | 0.013762 | 4870.4444 | 330.0733 | 2622.0959 | 1918.2753 | 4882.9165 | 0 | 0 | 4882.9165 | 0.0001094%
2026 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 2.7814 | 123 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.8993 | 2.8735 | 5.1851 | 14.8993 | 2.8735 | 5.1851 | 15.6954 | 3.027 | 5.1851 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2026 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 3.4339 | 113 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 199.4969 | 3.5475 | 56.2355 | 199.4969 | 3.5475 | 56.2355 | 210.1563 | 3.7371 | 56.2355 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2026 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 2.7396 | 163 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 65.4226 | 2.8303 | 23.1152 | 65.4226 | 2.8303 | 23.1152 | 68.9182 | 2.9815 | 23.1152 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2026 | GH3 | CB GH3 | Tier-1 | Non-HFTD---14 | 2--1 | 4.7819 | 78 | 100% | 4.974 | 31.67% | 0% | 68.33% | 0.077982 | 0 | 0 | 0.077982 | 0 | 0.074389 | 4.9401 | 0.015058 | 0.074389 | 4.9401 | 0.015058 | 0.078364 | 5.2041 | 0.015058 | 1.568% | 0.013217 | 0.012562 | 376.3479 | 4.2189 | 117.7982 | 254.3308 | 389.7398 | 0 | 0 | 389.7398 | 2.572e-06%
2026 | 105 | 105-239F | Tier-1 | Non-HFTD---15 | 1--3 | 0.26155 | 20 | 100% | 2.4566 | 91.53% | 0% | 8.467% | 0.11131 | 0 | 0 | 0.11131 | 0 | 0.10618 | 0.27021 | 0.39295 | 0.10618 | 0.27021 | 0.39295 | 0.11185 | 0.28465 | 0.39295 | 4.531% | 0.0010678 | 0.0010149 | 2300.6028 | 305.3862 | 246.2943 | 1748.9223 | 2310.7468 | 0 | 0 | 2310.7468 | 3.67e-06%
2026 | 955 | CB 955 | Tier-1 | Non-HFTD---9 | 1--3 | 1.1538 | 14 | 100% | 15.216 | 95.67% | 0% | 4.328% | 0.7206 | 0 | 0 | 0.7206 | 0 | 0.6874 | 1.192 | 0.57669 | 0.6874 | 1.192 | 0.57669 | 0.72413 | 1.2557 | 0.57669 | 4.736% | 0.0047456 | 0.0045107 | 3206.3351 | 265.3654 | 1425.9225 | 1515.0472 | 3213.5613 | 0 | 0 | 3213.5613 | 2.376e-05%
2026 | BS1 | CB BS1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.2324 | 4 | 100% | 0.21229 | 51.44% | 0% | 48.56% | 0.0054051 | 0 | 0 | 0.0054051 | 0 | 0.0051561 | 0.2401 | 0.021475 | 0.0051561 | 0.2401 | 0.021475 | 0.0054316 | 0.25292 | 0.021475 | 2.546% | 0.0005254 | 0.00049939 | 404.0635 | 34.0597 | 17.826 | 352.1779 | 414.2829 | 0 | 0 | 414.2829 | 1.782e-07%
2026 | 191 | 191-1050R | Tier-1 | Non-HFTD---7 | 3--3 | 4.7722 | 123 | 100% | 34.1164 | 89.07% | 0% | 10.93% | 1.5041 | 0 | 0 | 1.5041 | 0 | 1.4348 | 4.9301 | 0.29104 | 1.4348 | 4.9301 | 0.29104 | 1.5115 | 5.1935 | 0.29104 | 4.409% | 0.014785 | 0.014053 | 2307.4666 | 326.6145 | 80.7742 | 1900.0778 | 2320.6044 | 0 | 0 | 2320.6044 | 4.96e-05%
2026 | 60 | CB 60 | Tier-1 | Non-HFTD---11 | 2--2 | 2.9972 | 97 | 100% | 10.2312 | 82.34% | 0% | 17.66% | 0.41699 | 0 | 0 | 0.41699 | 0 | 0.39778 | 3.0963 | 0.12847 | 0.39778 | 3.0963 | 0.12847 | 0.41904 | 3.2618 | 0.12847 | 4.076% | 0.0090716 | 0.0086226 | 1127.8283 | 37.9694 | 715.1314 | 374.7275 | 1138.2024 | 0 | 0 | 1138.2024 | 1.375e-05%
2026 | 137 | 137-767F | Tier-1 | Non-HFTD---11 | 2--2 | 2.2822 | 137 | 100% | 10.6804 | 81.68% | 0% | 18.32% | 0.43185 | 0 | 0 | 0.43185 | 0 | 0.41195 | 2.3577 | 0.17473 | 0.41195 | 2.3577 | 0.17473 | 0.43396 | 2.4837 | 0.17473 | 4.043% | 0.0070892 | 0.0067383 | 1506.5775 | 163.4925 | 256.9577 | 1086.1273 | 1520.9482 | 0 | 0 | 1520.9482 | 1.424e-05%
2026 | 41 | 41-43 | Tier-1 | Non-HFTD---10 | 4--2 | 14.0575 | 306 | 100% | 19.885 | 49.34% | 0% | 50.66% | 0.48568 | 0 | 0 | 0.48568 | 0 | 0.46331 | 14.5228 | 0.031902 | 0.46331 | 14.5228 | 0.031902 | 0.48806 | 15.2987 | 0.031902 | 2.442% | 0.039263 | 0.037319 | 506.4606 | 0.58714 | 271.667 | 234.2065 | 519.8217 | 0 | 0 | 519.8217 | 1.602e-05%
2026 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 12.1965 | 1116 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 391.4809 | 12.6001 | 31.0697 | 391.4809 | 12.6001 | 31.0697 | 412.3983 | 13.2733 | 31.0697 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2026 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 0.41023 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.80647 | 0.4238 | 1.9029 | 0.80647 | 0.4238 | 1.9029 | 0.84957 | 0.44645 | 1.9029 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2026 | 380 | 380-27 | Tier-1 | Non-HFTD---10 | 4--2 | 14.4385 | 565 | 100% | 22.878 | 63.4% | 0% | 36.6% | 0.71795 | 0 | 0 | 0.71795 | 0 | 0.68488 | 14.9163 | 0.045915 | 0.68488 | 14.9163 | 0.045915 | 0.72147 | 15.7133 | 0.045915 | 3.138% | 0.038378 | 0.036478 | 596.1298 | 23.7982 | 253.3548 | 318.9768 | 607.4932 | 0 | 0 | 607.4932 | 2.368e-05%
2026 | 936 | 936-188 | Tier-1 | Non-HFTD---4 | 2--4 | 1.8436 | 201 | 100% | 105.8404 | 98.55% | 0% | 1.448% | 5.1632 | 0 | 0 | 5.1632 | 0 | 4.9254 | 1.9046 | 2.586 | 4.9254 | 1.9046 | 2.586 | 5.1885 | 2.0064 | 2.586 | 4.878% | 0.0071268 | 0.006774 | 14851.04 | 3722.7452 | 36.3442 | 11091.9506 | 14862.2428 | 0 | 0 | 14862.2428 | 0.0001703%
2026 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 5.3095 | 739 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 428.5491 | 5.4852 | 78.1281 | 428.5491 | 5.4852 | 78.1281 | 451.4471 | 5.7783 | 78.1281 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2026 | 169 | 169-35F | Tier-1 | Non-HFTD---20 | 1--1 | 0.08387 | 2 | 100% | 0.038151 | 8.843% | 0% | 91.16% | 0.00016699 | 0 | 0 | 0.00016699 | 0 | 0.0001593 | 0.086645 | 0.0018385 | 0.0001593 | 0.086645 | 0.0018385 | 0.00016781 | 0.091275 | 0.0018385 | 0.4377% | 0.0001782 | 0.00016938 | 214.089 | 0.14685 | 36.6598 | 177.2824 | 224.2524 | 0 | 0 | 224.2524 | 5.507e-09%
2026 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 0.43788 | 83 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 19.1516 | 0.45237 | 42.3361 | 19.1516 | 0.45237 | 42.3361 | 20.1748 | 0.47654 | 42.3361 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2026 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 2.267 | 54 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 42.7961 | 2.3421 | 18.2728 | 42.7961 | 2.3421 | 18.2728 | 45.0828 | 2.4672 | 18.2728 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2026 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.057008 | 0 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.56685 | 0.058894 | 9.6249 | 0.56685 | 0.058894 | 9.6249 | 0.59714 | 0.062041 | 9.6249 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2026 | 344 | CB 344 | Tier-1 | Non-HFTD---14 | 3--1 | 4.5935 | 221 | 100% | 6.1717 | 46.7% | 0% | 53.3% | 0.14267 | 0 | 0 | 0.14267 | 0 | 0.1361 | 4.7456 | 0.028679 | 0.1361 | 4.7456 | 0.028679 | 0.14337 | 4.9991 | 0.028679 | 2.312% | 0.013899 | 0.013211 | 444.0383 | 5.5246 | 196.2264 | 242.2874 | 456.3636 | 0 | 0 | 456.3636 | 4.705e-06%
2026 | 518 | 518-42AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.19057 | 7 | 100% | 0.34431 | 29.34% | 0% | 70.66% | 0.0050004 | 0 | 0 | 0.0050004 | 0 | 0.00477 | 0.19688 | 0.024228 | 0.00477 | 0.19688 | 0.024228 | 0.0050249 | 0.2074 | 0.024228 | 1.452% | 0.0008198 | 0.00077922 | 419.9978 | 0.47523 | 148.6345 | 270.8881 | 435.4533 | 0 | 0 | 435.4533 | 1.649e-07%
2026 | FM3 | CB FM3 | Tier-1 | Non-HFTD---3 | 4--3 | 9.8417 | 866 | 100% | 121.1123 | 67.77% | 26.62% | 5.609% | 4.0628 | 0 | 0 | 4.0628 | 0 | 3.8756 | 10.1674 | 0.38118 | 3.8756 | 10.1674 | 0.38118 | 4.0827 | 10.7106 | 0.38118 | 3.355% | 0.035117 | 0.033379 | 3448.8213 | 613.5911 | 1013.3761 | 1821.8541 | 3506.7114 | 0 | 0 | 3506.7114 | 0.000134%
2026 | 402 | 402-819F | Tier-1 | Non-HFTD---20 | 1--1 | 0.13463 | 13 | 100% | 0.087285 | 16.51% | 0% | 83.49% | 0.00071325 | 0 | 0 | 0.00071325 | 0 | 0.0006804 | 0.13908 | 0.004892 | 0.0006804 | 0.13908 | 0.004892 | 0.00071675 | 0.14651 | 0.004892 | 0.8172% | 0.0003302 | 0.00031386 | 264.3403 | 3.766 | 41.5642 | 219.0101 | 275.834 | 0 | 0 | 275.834 | 2.352e-08%
2026 | HL1 | CB HL1 | Tier-1 | Non-HFTD---12 | 3--1 | 10.6881 | 256 | 100% | 10.8253 | 37.08% | 0% | 62.92% | 0.19871 | 0 | 0 | 0.19871 | 0 | 0.18955 | 11.0418 | 0.017167 | 0.18955 | 11.0418 | 0.017167 | 0.19968 | 11.6318 | 0.017167 | 1.836% | 0.02785 | 0.026472 | 388.6942 | 5.612 | 146.5056 | 236.5767 | 401.4302 | 0 | 0 | 401.4302 | 6.553e-06%
2026 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 6.1881 | 436 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 244.4546 | 6.3929 | 38.2385 | 244.4546 | 6.3929 | 38.2385 | 257.5161 | 6.7345 | 38.2385 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2026 | 491 | CB 491 | Tier-1 | Non-HFTD---14 | 2--2 | 2.3305 | 61 | 100% | 5.1621 | 58.11% | 0% | 41.89% | 0.14849 | 0 | 0 | 0.14849 | 0 | 0.14165 | 2.4077 | 0.058834 | 0.14165 | 2.4077 | 0.058834 | 0.14922 | 2.5363 | 0.058834 | 2.877% | 0.0082426 | 0.0078346 | 626.2758 | 50.0543 | 81.0381 | 495.1834 | 639.9375 | 0 | 0 | 639.9375 | 4.897e-06%
2026 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.19716 | 0 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.6814 | 0.20368 | 18.0742 | 3.6814 | 0.20368 | 18.0742 | 3.8781 | 0.21457 | 18.0742 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2026 | 214 | CB 214 | Tier-3 | Tier-3---20 | 1--5 | 0.040909 | 0 | 100% | 59.1996 | 99.88% | 0% | 0.1188% | 2.9269 | 0 | 0 | 2.9269 | 0 | 2.7921 | 0.042263 | 66.0642 | 2.7921 | 0.042263 | 66.0642 | 2.9412 | 0.044521 | 66.0642 | 4.944% | 0.0002016 | 0.00019162 | 293649.0501 | 47091.7983 | 966.5627 | 245590.6891 | 293667.224 | 0 | 0 | 293667.224 | 9.652e-05%
2026 | 188 | CB 188 | Tier-1 | Non-HFTD---1 | 4--4 | 10.3012 | 692 | 100% | 378.367 | 98.23% | 0% | 1.765% | 18.3985 | 0 | 0 | 18.3985 | 0 | 17.5509 | 10.6421 | 1.6492 | 17.5509 | 10.6421 | 1.6492 | 18.4887 | 11.2107 | 1.6492 | 4.863% | 0.035993 | 0.034211 | 10512.2388 | 2006.1945 | 714.6271 | 7791.4172 | 10521.9037 | 0 | 0 | 10521.9037 | 0.0006067%
2026 | 178 | CB 178 | Tier-1 | Non-HFTD---1 | 2--5 | 3.4303 | 94 | 100% | 644.514 | 99.63% | 0% | 0.3655% | 31.7868 | 0 | 0 | 31.7868 | 0 | 30.3225 | 3.5438 | 8.5565 | 30.3225 | 3.5438 | 8.5565 | 31.9426 | 3.7332 | 8.5565 | 4.932% | 0.013511 | 0.012843 | 47701.4988 | 11137.324 | 1569.0906 | 34995.0842 | 47710.5792 | 0 | 0 | 47710.5792 | 0.001048%
2026 | 123 | CB 123 | Tier-1 | Non-HFTD---13 | 1--3 | 0.55284 | 1 | 100% | 5.3856 | 82.28% | 0% | 17.72% | 0.21934 | 0 | 0 | 0.21934 | 0 | 0.20924 | 0.57114 | 0.36635 | 0.20924 | 0.57114 | 0.36635 | 0.22042 | 0.60165 | 0.36635 | 4.073% | 0.002683 | 0.0025502 | 2007.2952 | 0.86408 | 1679.9489 | 326.4822 | 2025.8209 | 0 | 0 | 2025.8209 | 7.233e-06%
2026 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 0.14415 | 19 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.3585 | 0.14892 | 15.8378 | 2.3585 | 0.14892 | 15.8378 | 2.4845 | 0.15687 | 15.8378 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2026 | 77 | 77-28R | Tier-1 | Non-HFTD---15 | 1--2 | 1.3614 | 102 | 100% | 2.2554 | 61.57% | 0% | 38.43% | 0.068739 | 0 | 0 | 0.068739 | 0 | 0.065573 | 1.4064 | 0.046624 | 0.065573 | 1.4064 | 0.046624 | 0.069076 | 1.4816 | 0.046624 | 3.048% | 0.003703 | 0.0035197 | 609.0688 | 47.1548 | 109.5378 | 452.3762 | 621.2579 | 0 | 0 | 621.2579 | 2.267e-06%
2026 | 395 | 395-33R | Tier-2 | Tier-2---11 | 4--3 | 0.79815 | 51 | 100% | 396.9757 | 0.1391% | 99.74% | 0.1245% | 0.02734 | 0 | 0 | 0.02734 | 0 | 0.026081 | 0.82457 | 0.03163 | 0.026081 | 0.82457 | 0.03163 | 0.027474 | 0.86862 | 0.03163 | 0.006887% | 0.092102 | 0.087543 | 4310.174 | 6.5289 | 3952.6979 | 350.9472 | 4534.3264 | 0 | 0 | 4534.3264 | 9.016e-07%
2026 | 1039 | CB 1039 | Tier-1 | Non-HFTD---6 | 4--3 | 0.84625 | 23 | 100% | 89.254 | 66.42% | 32.73% | 0.8498% | 2.9347 | 0 | 0 | 2.9347 | 0 | 2.7995 | 0.87425 | 3.2021 | 2.7995 | 0.87425 | 3.2021 | 2.9491 | 0.92096 | 3.2021 | 3.288% | 0.047241 | 0.044903 | 1889.3167 | 183.5723 | 702.9111 | 1002.8332 | 1922.3524 | 0 | 0 | 1922.3524 | 9.677e-05%
2026 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 18.6854 | 1073 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 253.1828 | 19.3037 | 13.1157 | 253.1828 | 19.3037 | 13.1157 | 266.7107 | 20.3352 | 13.1157 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2026 | 416 | 416-29AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.34208 | 11 | 100% | 0.44314 | 13.31% | 0% | 86.69% | 0.0029191 | 0 | 0 | 0.0029191 | 0 | 0.0027847 | 0.3534 | 0.0078796 | 0.0027847 | 0.3534 | 0.0078796 | 0.0029334 | 0.37228 | 0.0078796 | 0.6587% | 0.0012336 | 0.0011725 | 359.222 | 0.32475 | 75.5335 | 283.3638 | 375.4399 | 0 | 0 | 375.4399 | 9.626e-08%
2026 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.0060606 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.28378 | 0.0062612 | 45.3234 | 0.28378 | 0.0062612 | 45.3234 | 0.29894 | 0.0065957 | 45.3234 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2026 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.32386 | 75 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 18.6068 | 0.33458 | 55.6122 | 18.6068 | 0.33458 | 55.6122 | 19.601 | 0.35246 | 55.6122 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2026 | 941 | 941-33F | Tier-1 | Non-HFTD---10 | 3--2 | 9.9011 | 248 | 100% | 24.7891 | 72.11% | 0% | 27.89% | 0.88483 | 0 | 0 | 0.88483 | 0 | 0.84407 | 10.2288 | 0.082519 | 0.84407 | 10.2288 | 0.082519 | 0.88917 | 10.7753 | 0.082519 | 3.569% | 0.028474 | 0.027064 | 870.5979 | 65.8276 | 379.4765 | 425.2938 | 883.243 | 0 | 0 | 883.243 | 2.918e-05%
2026 | 330 | 330-810R | Tier-1 | Non-HFTD---2 | 3--4 | 2.7411 | 85 | 100% | 235.3556 | 4.74% | 94.16% | 1.096% | 0.55218 | 0 | 0 | 0.55218 | 0 | 0.52674 | 2.8318 | 0.18601 | 0.52674 | 2.8318 | 0.18601 | 0.55488 | 2.9831 | 0.18601 | 0.2346% | 0.026057 | 0.024767 | 9032.2679 | 9.3042 | 8071.7191 | 951.2446 | 9480.3546 | 0 | 0 | 9480.3546 | 1.821e-05%
2026 | 795 | 795-821F | Tier-1 | Non-HFTD---6 | 3--3 | 2.1524 | 92 | 100% | 48.0743 | 18.57% | 77.45% | 3.984% | 0.44179 | 0 | 0 | 0.44179 | 0 | 0.42144 | 2.2237 | 0.18953 | 0.42144 | 2.2237 | 0.18953 | 0.44396 | 2.3425 | 0.18953 | 0.919% | 0.024764 | 0.023538 | 1941.2839 | 16.1722 | 1572.1152 | 352.9965 | 2023.6128 | 0 | 0 | 2023.6128 | 1.457e-05%
2026 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.011364 | 0 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.032694 | 0.01174 | 2.7849 | 0.032694 | 0.01174 | 2.7849 | 0.03444 | 0.012367 | 2.7849 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2026 | 340 | 340-378F | Tier-1 | Non-HFTD---1 | 3--4 | 8.3752 | 891 | 100% | 393.7851 | 98.57% | 0% | 1.434% | 19.2129 | 0 | 0 | 19.2129 | 0 | 18.3278 | 8.6523 | 2.1182 | 18.3278 | 8.6523 | 2.1182 | 19.3071 | 9.1146 | 2.1182 | 4.879% | 0.02753 | 0.026167 | 14303.9568 | 3018.559 | 106.2503 | 11179.1475 | 14314.6375 | 0 | 0 | 14314.6375 | 0.0006336%
2026 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 2.3892 | 145 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 202.8579 | 2.4683 | 82.1854 | 202.8579 | 2.4683 | 82.1854 | 213.6968 | 2.6002 | 82.1854 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2026 | 426 | CB 426 | Tier-1 | Non-HFTD---19 | 1--1 | 0.040909 | 5 | 100% | 0.070175 | 3.474% | 0% | 96.53% | 0.00012067 | 0 | 0 | 0.00012067 | 0 | 0.00011511 | 0.042263 | 0.0027237 | 0.00011511 | 0.042263 | 0.0027237 | 0.00012126 | 0.044521 | 0.0027237 | 0.172% | 0.0001956 | 0.00018592 | 358.7676 | 1.9592 | 33.3661 | 323.4423 | 376.8024 | 0 | 0 | 376.8024 | 3.979e-09%
2026 | 310 | 310-1192F | Tier-1 | Non-HFTD---2 | 4--4 | 9.1648 | 499 | 100% | 284.9417 | 1.867% | 95.71% | 2.424% | 0.26335 | 0 | 0 | 0.26335 | 0 | 0.25121 | 9.4681 | 0.026533 | 0.25121 | 9.4681 | 0.026533 | 0.26464 | 9.9739 | 0.026533 | 0.09242% | 0.04251 | 0.040406 | 6702.9643 | 7.4996 | 5968.2158 | 727.249 | 7045.5227 | 0 | 0 | 7045.5227 | 8.684e-06%
2026 | 362 | 362-40F | Tier-1 | Non-HFTD---11 | 2--2 | 1.0875 | 41 | 100% | 13.0284 | 1.16% | 93.92% | 4.92% | 0.0074835 | 0 | 0 | 0.0074835 | 0 | 0.0071387 | 1.1235 | 0.0063541 | 0.0071387 | 1.1235 | 0.0063541 | 0.0075202 | 1.1835 | 0.0063541 | 0.05744% | 0.008482 | 0.0080621 | 1536.0068 | 3.2594 | 1317.0481 | 215.6994 | 1615.0705 | 0 | 0 | 1615.0705 | 2.468e-07%
2026 | 191 | CB 191 | Tier-1 | Non-HFTD---11 | 2--2 | 3.2041 | 104 | 100% | 11.195 | 80.08% | 0% | 19.92% | 0.44379 | 0 | 0 | 0.44379 | 0 | 0.42334 | 3.3102 | 0.12789 | 0.42334 | 3.3102 | 0.12789 | 0.44596 | 3.4871 | 0.12789 | 3.964% | 0.009482 | 0.0090126 | 1180.6585 | 96.7187 | 494.004 | 589.9358 | 1192.904 | 0 | 0 | 1192.904 | 1.463e-05%
2026 | 298 | CB 298 | Tier-1 | Non-HFTD---9 | 1--4 | 1.1671 | 125 | 100% | 17.6868 | 96.46% | 0% | 3.539% | 0.84451 | 0 | 0 | 0.84451 | 0 | 0.80561 | 1.2057 | 0.66817 | 0.80561 | 1.2057 | 0.66817 | 0.84865 | 1.2701 | 0.66817 | 4.775% | 0.0035214 | 0.0033471 | 5022.6742 | 642.7129 | 927.2824 | 3452.679 | 5031.9322 | 0 | 0 | 5031.9322 | 2.785e-05%
2026 | 143 | CB 143 | Tier-1 | Non-HFTD---4 | 3--4 | 3.3491 | 132 | 100% | 145.6039 | 54.61% | 44.11% | 1.276% | 3.9361 | 0 | 0 | 3.9361 | 0 | 3.7548 | 3.4599 | 1.0852 | 3.7548 | 3.4599 | 1.0852 | 3.9554 | 3.6448 | 1.0852 | 2.703% | 0.016042 | 0.015248 | 9076.1902 | 871.9142 | 5424.8557 | 2779.4204 | 9290.7228 | 0 | 0 | 9290.7228 | 0.0001298%
2026 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 8.614 | 1088 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 89.1348 | 8.8991 | 10.0162 | 89.1348 | 8.8991 | 10.0162 | 93.8974 | 9.3746 | 10.0162 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2026 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 3.0796 | 180 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 9.1137 | 3.1815 | 2.8646 | 9.1137 | 3.1815 | 2.8646 | 9.6007 | 3.3515 | 2.8646 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2026 | 381 | 381-49 | Tier-1 | Non-HFTD---19 | 1--1 | 0.0083333 | 0 | 100% | 0.029666 | 0.1223% | 0% | 99.88% | 1.7956e-06 | 0 | 0 | 1.7956e-06 | 0 | 1.7129e-06 | 0.0086091 | 0.00019896 | 1.7129e-06 | 0.0086091 | 0.00019896 | 1.8044e-06 | 0.0090691 | 0.00019896 | 0.006053% | 6.36e-05 | 6.0452e-05 | 466.4424 | 0.35055 | 42.8905 | 423.2013 | 490.704 | 0 | 0 | 490.704 | 5.921e-11%
2026 | 376 | 376-527AE | Tier-1 | Non-HFTD---19 | 1--3 | 0.051894 | 0 | 100% | 0.49148 | 77.98% | 0% | 22.02% | 0.018971 | 0 | 0 | 0.018971 | 0 | 0.018097 | 0.053611 | 0.33756 | 0.018097 | 0.053611 | 0.33756 | 0.019064 | 0.056476 | 0.33756 | 3.86% | 0.0002636 | 0.00025055 | 1864.5025 | 6.946 | 1450.3613 | 407.1952 | 1885.8844 | 0 | 0 | 1885.8844 | 6.256e-07%
2026 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.34621 | 20 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.4335 | 0.35767 | 20.7831 | 7.4335 | 0.35767 | 20.7831 | 7.8307 | 0.37678 | 20.7831 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2026 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.87121 | 109 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 6.2466 | 0.90004 | 6.9403 | 6.2466 | 0.90004 | 6.9403 | 6.5803 | 0.94813 | 6.9403 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2026 | 834 | 834-887AE | Tier-2 | Tier-2---17 | 2--4 | 1.3721 | 178 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 3.435 | 0 | 0 | 3.435 | 0 | 3.2767 | 1.4176 | 2.3115 | 3.2767 | 1.4176 | 2.3115 | 3.4518 | 1.4933 | 2.3115 | 4.883% | 0.0050886 | 0.0048367 | 13824.3748 | 4928.7906 | 56.7151 | 8838.8691 | 13834.1342 | 0 | 0 | 13834.1342 | 0.0001133%
2026 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 2.2803 | 93 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.2445 | 2.3557 | 0.52827 | 1.2445 | 2.3557 | 0.52827 | 1.311 | 2.4816 | 0.52827 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2026 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | 3--5 | 8.4224 | 554 | 100% | 1585.8519 | 99.67% | 0% | 0.3254% | 78.2443 | 0 | 0 | 78.2443 | 0 | 74.6397 | 8.7011 | 8.5782 | 74.6397 | 8.7011 | 8.5782 | 78.6278 | 9.166 | 8.5782 | 4.934% | 0.026002 | 0.024715 | 60989.6136 | 9907.2213 | 216.3013 | 50866.0909 | 60999.9476 | 0 | 0 | 60999.9476 | 0.00258%
2026 | 418 | CB 418 | Tier-1 | Non-HFTD---8 | 3--2 | 7.4191 | 168 | 100% | 32.4786 | 83.15% | 0% | 16.85% | 1.3368 | 0 | 0 | 1.3368 | 0 | 1.2753 | 7.6646 | 0.16638 | 1.2753 | 7.6646 | 0.16638 | 1.3434 | 8.0742 | 0.16638 | 4.116% | 0.022349 | 0.021243 | 1453.2194 | 9.9672 | 1170.7456 | 272.5066 | 1465.9693 | 0 | 0 | 1465.9693 | 4.408e-05%
2026 | SW3 | CB SW3 | Tier-1 | Non-HFTD---10 | 3--2 | 7.1382 | 267 | 100% | 18.2834 | 70.37% | 0% | 29.63% | 0.63685 | 0 | 0 | 0.63685 | 0 | 0.60751 | 7.3745 | 0.08238 | 0.60751 | 7.3745 | 0.08238 | 0.63997 | 7.7685 | 0.08238 | 3.483% | 0.021128 | 0.020082 | 865.3622 | 65.6443 | 230.815 | 568.9028 | 878.7164 | 0 | 0 | 878.7164 | 2.1e-05%
2026 | RV2 | CB RV2 | Tier-1 | Non-HFTD---18 | 1--1 | 0.8741 | 49 | 100% | 0.72292 | 8.676% | 0% | 91.32% | 0.0031046 | 0 | 0 | 0.0031046 | 0 | 0.0029616 | 0.90302 | 0.0032796 | 0.0029616 | 0.90302 | 0.0032796 | 0.0031198 | 0.95127 | 0.0032796 | 0.4295% | 0.0024738 | 0.0023513 | 292.2303 | 0.20082 | 49.5965 | 242.4329 | 306.1286 | 0 | 0 | 306.1286 | 1.024e-07%
2026 | 299 | 299-1153F | Tier-1 | Non-HFTD---11 | 1--4 | 0.33445 | 5 | 100% | 12.6944 | 96.89% | 0% | 3.107% | 0.60885 | 0 | 0 | 0.60885 | 0 | 0.5808 | 0.34552 | 1.6809 | 0.5808 | 0.34552 | 1.6809 | 0.61183 | 0.36398 | 1.6809 | 4.796% | 0.0013374 | 0.0012712 | 9491.8205 | 1360.071 | 891.9808 | 7239.7687 | 9507.1772 | 0 | 0 | 9507.1772 | 2.008e-05%
2026 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 3.4163 | 181 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 106.3059 | 3.5294 | 30.1205 | 106.3059 | 3.5294 | 30.1205 | 111.9859 | 3.7179 | 30.1205 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2026 | 138 | 138-366 | Tier-1 | Non-HFTD---19 | 1--1 | 0.08428 | 0 | 100% | 0.163 | 7.427% | 0% | 92.57% | 0.00059926 | 0 | 0 | 0.00059926 | 0 | 0.00057166 | 0.087069 | 0.0065655 | 0.00057166 | 0.087069 | 0.0065655 | 0.0006022 | 0.091722 | 0.0065655 | 0.3676% | 0.000406 | 0.0003859 | 401.4766 | 0.27966 | 63.5802 | 337.6168 | 420.8318 | 0 | 0 | 420.8318 | 1.976e-08%
2026 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 11.5796 | 1432 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 231.9683 | 11.9628 | 19.3908 | 231.9683 | 11.9628 | 19.3908 | 244.3627 | 12.602 | 19.3908 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2026 | 417 | 417-21R | Tier-1 | Non-HFTD---3 | 4--3 | 10.3053 | 362 | 100% | 169.2976 | 37.28% | 58.96% | 3.759% | 3.1239 | 0 | 0 | 3.1239 | 0 | 2.98 | 10.6463 | 0.27991 | 2.98 | 10.6463 | 0.27991 | 3.1392 | 11.2152 | 0.27991 | 1.845% | 0.039679 | 0.037715 | 4266.681 | 378.3982 | 2573.6009 | 1314.6819 | 4406.0517 | 0 | 0 | 4406.0517 | 0.000103%
2026 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 8.9743 | 877 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 526.8313 | 9.2713 | 56.8242 | 526.8313 | 9.2713 | 56.8242 | 554.9807 | 9.7666 | 56.8242 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2026 | 144 | 144-445F | Tier-1 | Non-HFTD---7 | 3--3 | 3.6072 | 172 | 100% | 44.172 | 3.542% | 89.64% | 6.821% | 0.077447 | 0 | 0 | 0.077447 | 0 | 0.073879 | 3.7266 | 0.019825 | 0.073879 | 3.7266 | 0.019825 | 0.077827 | 3.9257 | 0.019825 | 0.1753% | 0.01688 | 0.016045 | 2616.7604 | 3.9028 | 2254.4176 | 358.4401 | 2748.2088 | 0 | 0 | 2748.2088 | 2.554e-06%
2026 | 286 | 286-1053R | Tier-1 | Non-HFTD---6 | 4--3 | 9.9807 | 1044 | 100% | 76.5163 | 19.5% | 72.04% | 8.463% | 0.73848 | 0 | 0 | 0.73848 | 0 | 0.70446 | 10.311 | 0.068321 | 0.70446 | 10.311 | 0.068321 | 0.7421 | 10.8619 | 0.068321 | 0.9651% | 0.033619 | 0.031955 | 2275.9575 | 19.2195 | 1851.9212 | 404.8167 | 2371.3746 | 0 | 0 | 2371.3746 | 2.435e-05%
2026 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 10.35 | 794 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 201.9487 | 10.6925 | 18.8869 | 201.9487 | 10.6925 | 18.8869 | 212.7391 | 11.2639 | 18.8869 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2026 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 6.2353 | 475 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 165.5356 | 6.4416 | 25.6979 | 165.5356 | 6.4416 | 25.6979 | 174.3804 | 6.7858 | 25.6979 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2026 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 2.3515 | 10 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 269.2064 | 2.4293 | 110.8143 | 269.2064 | 2.4293 | 110.8143 | 283.5905 | 2.5592 | 110.8143 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2026 | 178 | 178-48 | Tier-1 | Non-HFTD---15 | 1--3 | 0.243 | 28 | 100% | 2.3951 | 91.42% | 0% | 8.578% | 0.10839 | 0 | 0 | 0.10839 | 0 | 0.10339 | 0.25104 | 0.41185 | 0.10339 | 0.25104 | 0.41185 | 0.10892 | 0.26446 | 0.41185 | 4.525% | 0.0008186 | 0.00077808 | 2925.8017 | 435.8246 | 30.2443 | 2459.7328 | 2938.8721 | 0 | 0 | 2938.8721 | 3.574e-06%
2026 | 719 | 719-856F | Tier-1 | Non-HFTD---20 | 1--1 | 0.65096 | 19 | 100% | 0.5127 | 9.051% | 0% | 90.95% | 0.0022971 | 0 | 0 | 0.0022971 | 0 | 0.0021913 | 0.6725 | 0.0032584 | 0.0021913 | 0.6725 | 0.0032584 | 0.0023084 | 0.70844 | 0.0032584 | 0.448% | 0.0018984 | 0.0018044 | 270.0677 | 0.18482 | 46.7574 | 223.1254 | 282.8592 | 0 | 0 | 282.8592 | 7.575e-08%
2026 | 308 | 308-484AE | Tier-1 | Non-HFTD---3 | 4--3 | 4.8747 | 173 | 100% | 121.7186 | 8.654% | 88.76% | 2.589% | 0.52141 | 0 | 0 | 0.52141 | 0 | 0.49739 | 5.036 | 0.098768 | 0.49739 | 5.036 | 0.098768 | 0.52397 | 5.3051 | 0.098768 | 0.4284% | 0.043365 | 0.041218 | 2806.8523 | 43.4645 | 2320.9674 | 442.4205 | 2940.3772 | 0 | 0 | 2940.3772 | 1.719e-05%
2026 | 517 | CB 517 | Tier-1 | Non-HFTD---13 | 2--2 | 2.9201 | 69 | 100% | 8.4391 | 68.2% | 0% | 31.8% | 0.28488 | 0 | 0 | 0.28488 | 0 | 0.27176 | 3.0167 | 0.090085 | 0.27176 | 3.0167 | 0.090085 | 0.28628 | 3.1779 | 0.090085 | 3.376% | 0.010508 | 0.0099879 | 803.1131 | 55.9391 | 225.7298 | 521.4442 | 816.4147 | 0 | 0 | 816.4147 | 9.394e-06%
2026 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | 4--5 | 1.5992 | 53 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 37.535 | 0 | 0 | 37.535 | 0 | 35.8058 | 1.6522 | 21.672 | 35.8058 | 1.6522 | 21.672 | 37.719 | 1.7404 | 21.672 | 3.124% | 0.042337 | 0.040241 | 28377.3086 | 3599.9822 | 10019.8495 | 14757.4769 | 28922.3867 | 0 | 0 | 28922.3867 | 0.001238%
2026 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 1.375 | 64 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 129.2749 | 1.4205 | 91.0092 | 129.2749 | 1.4205 | 91.0092 | 136.1822 | 1.4964 | 91.0092 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2026 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 2.9682 | 204 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 327.0901 | 3.0664 | 106.6677 | 327.0901 | 3.0664 | 106.6677 | 344.567 | 3.2303 | 106.6677 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2026 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 13.8096 | 550 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 167.585 | 14.2666 | 11.7466 | 167.585 | 14.2666 | 11.7466 | 176.5393 | 15.0289 | 11.7466 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2026 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 8.2782 | 241 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 25.6177 | 8.5522 | 2.9955 | 25.6177 | 8.5522 | 2.9955 | 26.9865 | 9.0091 | 2.9955 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2026 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 10.4533 | 579 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 27.3279 | 10.7992 | 2.5306 | 27.3279 | 10.7992 | 2.5306 | 28.7881 | 11.3762 | 2.5306 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2026 | 139 | 139-48 | Tier-1 | Non-HFTD---10 | 3--2 | 5.7198 | 188 | 100% | 22.1253 | 79.12% | 0% | 20.88% | 0.86657 | 0 | 0 | 0.86657 | 0 | 0.82665 | 5.9091 | 0.13989 | 0.82665 | 5.9091 | 0.13989 | 0.87082 | 6.2249 | 0.13989 | 3.917% | 0.020647 | 0.019625 | 1071.5768 | 0.73997 | 864.6922 | 206.1446 | 1083.2264 | 0 | 0 | 1083.2264 | 2.858e-05%
2026 | 595 | 595-500 | Tier-1 | Non-HFTD---1 | 3--4 | 2.1604 | 125 | 100% | 238.2364 | 29.81% | 69.49% | 0.6998% | 3.5151 | 0 | 0 | 3.5151 | 0 | 3.3532 | 2.2319 | 1.5024 | 3.3532 | 2.2319 | 1.5024 | 3.5324 | 2.3512 | 1.5024 | 1.475% | 0.021896 | 0.020812 | 10880.3635 | 1188.0308 | 6831.5625 | 2860.7703 | 11278.0913 | 0 | 0 | 11278.0913 | 0.0001159%
2026 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 4.354 | 0 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 22.1263 | 4.4981 | 4.9191 | 22.1263 | 4.4981 | 4.9191 | 23.3085 | 4.7384 | 4.9191 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2026 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 11.4604 | 813 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 203.7535 | 11.8397 | 17.2094 | 203.7535 | 11.8397 | 17.2094 | 214.6403 | 12.4723 | 17.2094 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2026 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 1.1486 | 90 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.8974 | 1.1867 | 8.3406 | 9.8974 | 1.1867 | 8.3406 | 10.4263 | 1.2501 | 8.3406 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2026 | 493 | 493-478R | Tier-1 | Non-HFTD---8 | 3--3 | 4.1928 | 240 | 100% | 28.2075 | 88.18% | 0% | 11.82% | 1.2312 | 0 | 0 | 1.2312 | 0 | 1.1745 | 4.3316 | 0.27114 | 1.1745 | 4.3316 | 0.27114 | 1.2372 | 4.563 | 0.27114 | 4.365% | 0.014664 | 0.013938 | 1923.5642 | 293.7928 | 238.0854 | 1391.686 | 1935.4086 | 0 | 0 | 1935.4086 | 4.06e-05%
2026 | 416 | CB 416 | Tier-1 | Non-HFTD---13 | 1--4 | 0.49546 | 7 | 100% | 7.4419 | 94.25% | 0% | 5.754% | 0.34718 | 0 | 0 | 0.34718 | 0 | 0.33119 | 0.51186 | 0.64703 | 0.33119 | 0.51186 | 0.64703 | 0.34888 | 0.53921 | 0.64703 | 4.665% | 0.0015346 | 0.0014586 | 4849.4324 | 38.4789 | 4361.574 | 449.3795 | 4863.9644 | 0 | 0 | 4863.9644 | 1.145e-05%
2026 | 243 | 243-20R | Tier-1 | Non-HFTD---2 | 4--4 | 10.387 | 501 | 100% | 388.804 | 72.37% | 26.23% | 1.398% | 13.9291 | 0 | 0 | 13.9291 | 0 | 13.2874 | 10.7307 | 1.2383 | 13.2874 | 10.7307 | 1.2383 | 13.9973 | 11.3041 | 1.2383 | 3.583% | 0.058161 | 0.055282 | 6684.9371 | 1057.1463 | 1810.7065 | 3817.0843 | 6781.1116 | 0 | 0 | 6781.1116 | 0.0004593%
2026 | 724 | CB 724 | Tier-1 | Non-HFTD---20 | 1--1 | 0.25037 | 5 | 100% | 0.16085 | 8.868% | 0% | 91.13% | 0.00070607 | 0 | 0 | 0.00070607 | 0 | 0.00067354 | 0.25865 | 0.002604 | 0.00067354 | 0.25865 | 0.002604 | 0.00070953 | 0.27247 | 0.002604 | 0.439% | 0.000606 | 0.000576 | 265.4252 | 0.18201 | 45.5111 | 219.7321 | 278.0222 | 0 | 0 | 278.0222 | 2.328e-08%
2026 | 706 | CB 706 | Tier-1 | Non-HFTD---7 | 2--3 | 1.7864 | 19 | 100% | 32.9411 | 96.6% | 0.3164% | 3.084% | 1.5751 | 0 | 0 | 1.5751 | 0 | 1.5026 | 1.8455 | 0.81419 | 1.5026 | 1.8455 | 0.81419 | 1.5829 | 1.9441 | 0.81419 | 4.782% | 0.010907 | 0.010367 | 3020.124 | 527.3897 | 16.8429 | 2475.8914 | 3025.472 | 0 | 0 | 3025.472 | 5.194e-05%
2026 | 145 | CB 145 | Tier-1 | Non-HFTD---5 | 2--4 | 1.2373 | 52 | 100% | 50.1579 | 64.45% | 33.49% | 2.055% | 1.6003 | 0 | 0 | 1.6003 | 0 | 1.5265 | 1.2782 | 1.1943 | 1.5265 | 1.2782 | 1.1943 | 1.6081 | 1.3465 | 1.1943 | 3.19% | 0.0096286 | 0.009152 | 5209.2634 | 427.9347 | 3048.2211 | 1733.1076 | 5305.6973 | 0 | 0 | 5305.6973 | 5.277e-05%
2026 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 10.5116 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 408.1427 | 10.8594 | 37.5841 | 408.1427 | 10.8594 | 37.5841 | 429.9503 | 11.4397 | 37.5841 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2026 | 411 | CB 411 | Tier-1 | Non-HFTD---17 | 1--4 | 0.039773 | 7 | 100% | 0.73685 | 95.5% | 0% | 4.499% | 0.034833 | 0 | 0 | 0.034833 | 0 | 0.033229 | 0.041089 | 0.8087 | 0.033229 | 0.041089 | 0.8087 | 0.035004 | 0.043284 | 0.8087 | 4.727% | 0.000145 | 0.00013782 | 5081.7307 | 456.5916 | 2088.6806 | 2536.4584 | 5093.636 | 0 | 0 | 5093.636 | 1.149e-06%
2026 | 916 | 916-381 | Tier-2 | Tier-2---12 | 4--4 | 1.3913 | 284 | 100% | 590.9122 | 71.07% | 28.73% | 0.1918% | 20.7893 | 0 | 0 | 20.7893 | 0 | 19.8316 | 1.4374 | 13.797 | 19.8316 | 1.4374 | 13.797 | 20.8912 | 1.5142 | 13.797 | 3.518% | 0.049834 | 0.047367 | 11857.5641 | 1782.085 | 3001.9836 | 7073.4955 | 12036.1866 | 0 | 0 | 12036.1866 | 0.0006856%
2026 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 31.8811 | 2437 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 642.8121 | 32.9361 | 19.5169 | 642.8121 | 32.9361 | 19.5169 | 677.1585 | 34.6959 | 19.5169 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2026 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 7.3848 | 136 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 43.8971 | 7.6292 | 5.7538 | 43.8971 | 7.6292 | 5.7538 | 46.2426 | 8.0368 | 5.7538 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2026 | 258 | CB 258 | Tier-1 | Non-HFTD---19 | 1--1 | 0.065341 | 0 | 100% | 0.17536 | 0.484% | 0% | 99.52% | 4.2015e-05 | 0 | 0 | 4.2015e-05 | 0 | 4.008e-05 | 0.067503 | 0.00059374 | 4.008e-05 | 0.067503 | 0.00059374 | 4.2221e-05 | 0.07111 | 0.00059374 | 0.02396% | 0.0003514 | 0.00033401 | 499.0252 | 0.67763 | 45.6717 | 452.6758 | 524.8876 | 0 | 0 | 524.8876 | 1.386e-09%
2026 | 63 | 63-797R | Tier-1 | Non-HFTD---1 | 3--5 | 3.9205 | 872 | 100% | 1294.9207 | 95.84% | 3.945% | 0.2104% | 61.435 | 0 | 0 | 61.435 | 0 | 58.6048 | 4.0502 | 14.4695 | 58.6048 | 4.0502 | 14.4695 | 61.7362 | 4.2666 | 14.4695 | 4.744% | 0.02549 | 0.024229 | 50800.3291 | 10671.1023 | 1938.6345 | 38190.5924 | 50910.264 | 0 | 0 | 50910.264 | 0.002026%
2026 | 366 | CB 366 | Tier-1 | Non-HFTD---5 | 3--4 | 3.4801 | 66 | 100% | 92.421 | 14.77% | 81.62% | 3.609% | 0.67569 | 0 | 0 | 0.67569 | 0 | 0.64456 | 3.5952 | 0.17928 | 0.64456 | 3.5952 | 0.17928 | 0.679 | 3.7873 | 0.17928 | 0.7311% | 0.016207 | 0.015404 | 5702.6756 | 6.2073 | 5082.696 | 613.7722 | 5955.7953 | 0 | 0 | 5955.7953 | 2.228e-05%
2026 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | 2--4 | 2.8968 | 266 | 100% | 92.0555 | 97.82% | 0% | 2.183% | 4.4573 | 0 | 0 | 4.4573 | 0 | 4.2519 | 2.9927 | 1.4208 | 4.2519 | 2.9927 | 1.4208 | 4.4791 | 3.1526 | 1.4208 | 4.842% | 0.0089936 | 0.0085484 | 10235.6661 | 2125.5614 | 107.0953 | 8003.0094 | 10247.3023 | 0 | 0 | 10247.3023 | 0.000147%
2026 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 6.8056 | 633 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 75.5263 | 7.0309 | 10.7421 | 75.5263 | 7.0309 | 10.7421 | 79.5617 | 7.4065 | 10.7421 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2026 | 1139 | 1139-5 | Tier-1 | Non-HFTD---2 | 5--3 | 0.75514 | 11 | 100% | 335.8565 | 0.3706% | 99.5% | 0.1331% | 0.061619 | 0 | 0 | 0.061619 | 0 | 0.05878 | 0.78013 | 0.075346 | 0.05878 | 0.78013 | 0.075346 | 0.061921 | 0.82181 | 0.075346 | 0.01835% | 0.10416 | 0.099006 | 3224.3672 | 4.3588 | 2910.0555 | 309.953 | 3391.6629 | 0 | 0 | 3391.6629 | 2.032e-06%
2026 | MA2 | CB MA2 | Tier-1 | Non-HFTD---8 | 3--2 | 3.6417 | 126 | 100% | 40.2518 | 2.195% | 91.76% | 6.046% | 0.043733 | 0 | 0 | 0.043733 | 0 | 0.041719 | 3.7622 | 0.011089 | 0.041719 | 3.7622 | 0.011089 | 0.043948 | 3.9632 | 0.011089 | 0.1086% | 0.025041 | 0.023801 | 1607.4358 | 4.4717 | 1386.7821 | 216.182 | 1689.3102 | 0 | 0 | 1689.3102 | 1.442e-06%
2026 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 0.38935 | 10 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 8.5432 | 0.40223 | 21.2397 | 8.5432 | 0.40223 | 21.2397 | 8.9997 | 0.42372 | 21.2397 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2026 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 9.5874 | 639 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 45.5695 | 9.9046 | 4.6008 | 45.5695 | 9.9046 | 4.6008 | 48.0044 | 10.4339 | 4.6008 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2026 | 165 | 165-621F | Tier-1 | Non-HFTD---3 | 4--3 | 12.0826 | 329 | 100% | 101.1468 | 91.67% | 0% | 8.335% | 4.5895 | 0 | 0 | 4.5895 | 0 | 4.378 | 12.4825 | 0.35074 | 4.378 | 12.4825 | 0.35074 | 4.612 | 13.1494 | 0.35074 | 4.537% | 0.037528 | 0.03567 | 2695.236 | 312.5984 | 579.2909 | 1803.3467 | 2706.9347 | 0 | 0 | 2706.9347 | 0.0001513%
2026 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 6.5815 | 249 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 58.2545 | 6.7993 | 8.5677 | 58.2545 | 6.7993 | 8.5677 | 61.3671 | 7.1626 | 8.5677 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2026 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 5.9877 | 450 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 251.8011 | 6.1859 | 40.7057 | 251.8011 | 6.1859 | 40.7057 | 265.2552 | 6.5164 | 40.7057 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2026 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 5.0582 | 548 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 68.4112 | 5.2255 | 13.0917 | 68.4112 | 5.2255 | 13.0917 | 72.0666 | 5.5048 | 13.0917 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2026 | MK2 | CB MK2 | Tier-1 | Non-HFTD---14 | 3--1 | 6.9771 | 167 | 100% | 8.3451 | 44.18% | 0% | 55.82% | 0.18252 | 0 | 0 | 0.18252 | 0 | 0.17411 | 7.208 | 0.024155 | 0.17411 | 7.208 | 0.024155 | 0.18341 | 7.5931 | 0.024155 | 2.187% | 0.019822 | 0.01884 | 421.0108 | 29.7884 | 90.8373 | 300.3851 | 433.2487 | 0 | 0 | 433.2487 | 6.019e-06%
2026 | 209 | 209-661 | Tier-1 | Non-HFTD---4 | 1--5 | 1.3877 | 115 | 100% | 118.7112 | 99.11% | 0% | 0.8879% | 5.824 | 0 | 0 | 5.824 | 0 | 5.5557 | 1.4337 | 3.8752 | 5.5557 | 1.4337 | 3.8752 | 5.8526 | 1.5103 | 3.8752 | 4.906% | 0.0044254 | 0.0042063 | 26824.9714 | 4214.0457 | 851.0995 | 21759.8261 | 26837.3758 | 0 | 0 | 26837.3758 | 0.0001921%
2026 | 340 | 340-376F | Tier-1 | Non-HFTD---7 | 2--3 | 2.4146 | 200 | 100% | 34.9276 | 95.82% | 0% | 4.178% | 1.6567 | 0 | 0 | 1.6567 | 0 | 1.5804 | 2.4945 | 0.63355 | 1.5804 | 2.4945 | 0.63355 | 1.6648 | 2.6277 | 0.63355 | 4.743% | 0.0073482 | 0.0069845 | 4753.2178 | 524.3665 | 2205.6799 | 2023.1714 | 4763.5601 | 0 | 0 | 4763.5601 | 5.463e-05%
2026 | 579 | CB 579 | Tier-1 | Non-HFTD---6 | 3--3 | 1.4538 | 9 | 100% | 49.6621 | 21.66% | 75.14% | 3.198% | 0.53254 | 0 | 0 | 0.53254 | 0 | 0.50801 | 1.5019 | 0.33825 | 0.50801 | 1.5019 | 0.33825 | 0.53515 | 1.5821 | 0.33825 | 1.072% | 0.015297 | 0.01454 | 3246.5274 | 3.0703 | 2897.813 | 345.6441 | 3378.9733 | 0 | 0 | 3378.9733 | 1.756e-05%
2026 | 325 | CB 325 | Tier-1 | Non-HFTD---7 | 1--4 | 1.1091 | 146 | 100% | 43.928 | 97.88% | 0% | 2.116% | 2.1284 | 0 | 0 | 2.1284 | 0 | 2.0304 | 1.1458 | 1.772 | 2.0304 | 1.1458 | 1.772 | 2.1389 | 1.207 | 1.772 | 4.845% | 0.0043742 | 0.0041577 | 10042.5141 | 384.3371 | 7501.7135 | 2156.4635 | 10053.582 | 0 | 0 | 10053.582 | 7.019e-05%
2026 | 368 | CB 368 | Tier-1 | Non-HFTD---4 | 3--4 | 3.9384 | 124 | 100% | 110.2844 | 13.26% | 83.59% | 3.156% | 0.72366 | 0 | 0 | 0.72366 | 0 | 0.69032 | 4.0688 | 0.16966 | 0.69032 | 4.0688 | 0.16966 | 0.7272 | 4.2862 | 0.16966 | 0.6562% | 0.016985 | 0.016144 | 6492.9689 | 7.2051 | 5795.9328 | 689.831 | 6786.285 | 0 | 0 | 6786.285 | 2.386e-05%
2026 | 480 | 480-1163R | Tier-1 | Non-HFTD---16 | 2--1 | 3.6682 | 75 | 100% | 3.8801 | 32.98% | 0% | 67.02% | 0.06334 | 0 | 0 | 0.06334 | 0 | 0.060422 | 3.7896 | 0.015944 | 0.060422 | 3.7896 | 0.015944 | 0.06365 | 3.9921 | 0.015944 | 1.632% | 0.010077 | 0.0095782 | 385.0495 | 0.19419 | 150.4248 | 234.4305 | 398.4891 | 0 | 0 | 398.4891 | 2.089e-06%
2026 | 500 | 500-1531 | Tier-2 | Tier-2---10 | 4--4 | 0.97704 | 34 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 8.56 | 0 | 0 | 8.56 | 0 | 8.1657 | 1.0094 | 8.0898 | 8.1657 | 1.0094 | 8.0898 | 8.602 | 1.0633 | 8.0898 | 1.069% | 0.071178 | 0.067654 | 11247.1911 | 406.5986 | 8046.836 | 2793.7565 | 11706.3951 | 0 | 0 | 11706.3951 | 0.0002823%
2026 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 2.2354 | 19 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 100.9567 | 2.3094 | 43.7154 | 100.9567 | 2.3094 | 43.7154 | 106.351 | 2.4328 | 43.7154 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2026 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 1.5907 | 13 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.4319 | 1.6433 | 2.0884 | 3.4319 | 1.6433 | 2.0884 | 3.6153 | 1.7311 | 2.0884 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2026 | 395 | CB 395 | Tier-1 | Non-HFTD---2 | 4--4 | 0.85682 | 57 | 100% | 731.6954 | 0.7674% | 99.15% | 0.08318% | 0.27795 | 0 | 0 | 0.27795 | 0 | 0.26515 | 0.88517 | 0.29954 | 0.26515 | 0.88517 | 0.29954 | 0.27931 | 0.93247 | 0.29954 | 0.03799% | 0.090668 | 0.08618 | 8070.0864 | 11.9063 | 7403.1498 | 655.0303 | 8487.134 | 0 | 0 | 8487.134 | 9.166e-06%
2026 | 508 | 508-1027F | Tier-1 | Non-HFTD---19 | 1--2 | 0.083367 | 2 | 100% | 0.19317 | 84.46% | 0% | 15.54% | 0.0080765 | 0 | 0 | 0.0080765 | 0 | 0.0077044 | 0.086126 | 0.089456 | 0.0077044 | 0.086126 | 0.089456 | 0.0081161 | 0.090727 | 0.089456 | 4.181% | 0.0001954 | 0.00018573 | 988.6113 | 136.442 | 18.1035 | 834.0658 | 996.6104 | 0 | 0 | 996.6104 | 2.663e-07%
2026 | 96 | 96-1041F | Tier-1 | Non-HFTD---13 | 2--2 | 0.096362 | 0 | 100% | 5.6175 | 97.14% | 1.791% | 1.068% | 0.27012 | 0 | 0 | 0.27012 | 0 | 0.25767 | 0.099551 | 2.5883 | 0.25767 | 0.099551 | 2.5883 | 0.27144 | 0.10487 | 2.5883 | 4.808% | 0.005633 | 0.0053542 | 997.2446 | 127.463 | 205.2994 | 664.4822 | 998.7294 | 0 | 0 | 998.7294 | 8.907e-06%
2026 | 531 | 531-36AE | Tier-1 | Non-HFTD---12 | 3--2 | 5.9676 | 195 | 100% | 9.706 | 61.11% | 0% | 38.89% | 0.29361 | 0 | 0 | 0.29361 | 0 | 0.28009 | 6.1651 | 0.045431 | 0.28009 | 6.1651 | 0.045431 | 0.29505 | 6.4946 | 0.045431 | 3.025% | 0.016 | 0.015208 | 606.6092 | 2.6548 | 376.9073 | 227.0471 | 618.894 | 0 | 0 | 618.894 | 9.682e-06%
2026 | 438 | CB 438 | Tier-1 | Non-HFTD---9 | 1--4 | 0.50947 | 74 | 100% | 16.6829 | 97.05% | 0% | 2.95% | 0.80144 | 0 | 0 | 0.80144 | 0 | 0.76452 | 0.52633 | 1.4526 | 0.76452 | 0.52633 | 1.4526 | 0.80537 | 0.55445 | 1.4526 | 4.804% | 0.0021344 | 0.0020287 | 7816.2233 | 299.4615 | 5763.6381 | 1753.1236 | 7828.2327 | 0 | 0 | 7828.2327 | 2.643e-05%
2026 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 1.6328 | 7 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 11.4466 | 1.6868 | 6.7859 | 11.4466 | 1.6868 | 6.7859 | 12.0582 | 1.7769 | 6.7859 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2026 | 791 | CB 791 | Tier-1 | Non-HFTD---1 | 2--5 | 2.9851 | 216 | 100% | 969.8887 | 99.78% | 0% | 0.2167% | 47.9055 | 0 | 0 | 47.9055 | 0 | 45.6986 | 3.0838 | 14.8187 | 45.6986 | 3.0838 | 14.8187 | 48.1403 | 3.2486 | 14.8187 | 4.939% | 0.010706 | 0.010176 | 90594.693 | 15315.6434 | 490.2766 | 74788.773 | 90604.9145 | 0 | 0 | 90604.9145 | 0.00158%
2026 | 920 | 920-823 | Tier-2 | Tier-2---11 | 4--4 | 3.3104 | 254 | 100% | 458.2189 | 68.35% | 31.14% | 0.5113% | 15.5021 | 0 | 0 | 15.5021 | 0 | 14.788 | 3.4199 | 4.324 | 14.788 | 3.4199 | 4.324 | 15.5781 | 3.6027 | 4.324 | 3.383% | 0.054577 | 0.051875 | 8395.8542 | 937.9397 | 2311.5146 | 5146.3999 | 8534.2572 | 0 | 0 | 8534.2572 | 0.0005112%
2026 | 518 | 518-41 | Tier-1 | Non-HFTD---19 | 1--2 | 0.051326 | 0 | 100% | 0.18129 | 60.97% | 0% | 39.03% | 0.0054716 | 0 | 0 | 0.0054716 | 0 | 0.0052195 | 0.053024 | 0.098436 | 0.0052195 | 0.053024 | 0.098436 | 0.0054984 | 0.055857 | 0.098436 | 3.018% | 0.000233 | 0.00022147 | 778.072 | 0.2285 | 501.9934 | 275.8501 | 793.8862 | 0 | 0 | 793.8862 | 1.804e-07%
2026 | 323 | 323-472AE | Tier-1 | Non-HFTD---13 | 2--2 | 2.246 | 49 | 100% | 8.3309 | 80.43% | 0% | 19.57% | 0.33167 | 0 | 0 | 0.33167 | 0 | 0.31639 | 2.3204 | 0.13635 | 0.31639 | 2.3204 | 0.13635 | 0.33329 | 2.4443 | 0.13635 | 3.981% | 0.0064722 | 0.0061518 | 1287.1873 | 162.8063 | 63.3921 | 1060.9888 | 1300.3075 | 0 | 0 | 1300.3075 | 1.094e-05%
2026 | 513 | CB 513 | Tier-1 | Non-HFTD---15 | 2--2 | 1.6305 | 55 | 100% | 4.8584 | 75.25% | 0% | 24.75% | 0.18097 | 0 | 0 | 0.18097 | 0 | 0.17263 | 1.6845 | 0.10248 | 0.17263 | 1.6845 | 0.10248 | 0.18186 | 1.7745 | 0.10248 | 3.725% | 0.005369 | 0.0051032 | 904.9068 | 3.7303 | 679.4251 | 221.7514 | 916.5709 | 0 | 0 | 916.5709 | 5.968e-06%
2026 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 7.5917 | 223 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 476.2228 | 7.8429 | 60.7201 | 476.2228 | 7.8429 | 60.7201 | 501.668 | 8.262 | 60.7201 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2026 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 3.4244 | 409 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 162.0011 | 3.5377 | 45.7922 | 162.0011 | 3.5377 | 45.7922 | 170.6571 | 3.7268 | 45.7922 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2026 | 365 | 365-34R | Tier-1 | Non-HFTD---4 | 3--4 | 4.1672 | 256 | 100% | 103.0739 | 4.771% | 91.96% | 3.266% | 0.24342 | 0 | 0 | 0.24342 | 0 | 0.23221 | 4.3051 | 0.053938 | 0.23221 | 4.3051 | 0.053938 | 0.24462 | 4.5351 | 0.053938 | 0.2362% | 0.017802 | 0.016921 | 5789.9516 | 7.6245 | 5140.9605 | 641.3666 | 6077.094 | 0 | 0 | 6077.094 | 8.027e-06%
2026 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 1.6259 | 7 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 19.3654 | 1.6798 | 11.5287 | 19.3654 | 1.6798 | 11.5287 | 20.4002 | 1.7695 | 11.5287 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2026 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 3.5953 | 311 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 242.2939 | 3.7142 | 65.2337 | 242.2939 | 3.7142 | 65.2337 | 255.24 | 3.9127 | 65.2337 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2026 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 0.60374 | 82 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 13.6065 | 0.62372 | 21.815 | 13.6065 | 0.62372 | 21.815 | 14.3335 | 0.65705 | 21.815 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2026 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | 4--5 | 3.7428 | 1032 | 100% | 2117.8574 | 97.53% | 2.33% | 0.1416% | 102.2432 | 0 | 0 | 102.2432 | 0 | 97.5331 | 3.8666 | 25.2243 | 97.5331 | 3.8666 | 25.2243 | 102.7444 | 4.0732 | 25.2243 | 4.828% | 0.067442 | 0.064104 | 31402.4615 | 4988.1224 | 677.5642 | 25736.7748 | 31442.8757 | 0 | 0 | 31442.8757 | 0.003372%
2026 | SLD1 | CB SLD1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.41002 | 165 | 100% | 0.56022 | 34.73% | 0% | 65.27% | 0.0096313 | 0 | 0 | 0.0096313 | 0 | 0.0091876 | 0.42359 | 0.02169 | 0.0091876 | 0.42359 | 0.02169 | 0.0096785 | 0.44622 | 0.02169 | 1.719% | 0.001298 | 0.0012337 | 431.6022 | 16.2295 | 84.9521 | 330.4206 | 446.2726 | 0 | 0 | 446.2726 | 3.176e-07%
2026 | 741 | 741-17 | Tier-1 | Non-HFTD---17 | 1--2 | 0.36707 | 29 | 100% | 0.86307 | 47.7% | 0% | 52.3% | 0.020379 | 0 | 0 | 0.020379 | 0 | 0.019441 | 0.37921 | 0.051265 | 0.019441 | 0.37921 | 0.051265 | 0.020479 | 0.39948 | 0.051265 | 2.361% | 0.0013504 | 0.0012836 | 639.1235 | 0.34753 | 334.6341 | 304.1418 | 656.5303 | 0 | 0 | 656.5303 | 6.72e-07%
2026 | 165 | 165-35R | Tier-1 | Non-HFTD---14 | 3--1 | 5.1646 | 147 | 100% | 6.4032 | 43.37% | 0% | 56.63% | 0.13745 | 0 | 0 | 0.13745 | 0 | 0.13112 | 5.3355 | 0.024575 | 0.13112 | 5.3355 | 0.024575 | 0.13813 | 5.6206 | 0.024575 | 2.147% | 0.014379 | 0.013667 | 445.3099 | 19.5075 | 97.6943 | 328.1081 | 458.4437 | 0 | 0 | 458.4437 | 4.533e-06%
2026 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 0.63484 | 9 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.34944 | 0.65585 | 0.5328 | 0.34944 | 0.65585 | 0.5328 | 0.36811 | 0.69089 | 0.5328 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2026 | 385 | CB 385 | Tier-1 | Non-HFTD---7 | 2--3 | 3.3032 | 122 | 100% | 37.1529 | 92.67% | 0% | 7.33% | 1.7043 | 0 | 0 | 1.7043 | 0 | 1.6258 | 3.4125 | 0.47641 | 1.6258 | 3.4125 | 0.47641 | 1.7126 | 3.5949 | 0.47641 | 4.587% | 0.011539 | 0.010968 | 3219.7101 | 608.925 | 454.3214 | 2156.4637 | 3231.9998 | 0 | 0 | 3231.9998 | 5.62e-05%
2026 | 377 | CB 377 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6765 | 756 | 100% | 10.2043 | 38.55% | 0% | 61.45% | 0.19472 | 0 | 0 | 0.19472 | 0 | 0.18575 | 9.9967 | 0.018581 | 0.18575 | 9.9967 | 0.018581 | 0.19567 | 10.5309 | 0.018581 | 1.908% | 0.025969 | 0.024684 | 392.9351 | 0.64012 | 170.596 | 221.699 | 405.5098 | 0 | 0 | 405.5098 | 6.421e-06%
2026 | 1081 | 1081-11 | Tier-1 | Non-HFTD---3 | 4--4 | 7.6814 | 575 | 100% | 174.6854 | 18.55% | 79% | 2.449% | 1.6041 | 0 | 0 | 1.6041 | 0 | 1.5302 | 7.9356 | 0.19282 | 1.5302 | 7.9356 | 0.19282 | 1.6119 | 8.3597 | 0.19282 | 0.9183% | 0.031395 | 0.029841 | 5564.0802 | 104.2628 | 4552.4133 | 907.4041 | 5800.0917 | 0 | 0 | 5800.0917 | 5.29e-05%
2026 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 4.9145 | 243 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 229.1341 | 5.0772 | 45.1303 | 229.1341 | 5.0772 | 45.1303 | 241.3771 | 5.3485 | 45.1303 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2026 | 462 | 462-1034F | Tier-1 | Non-HFTD---13 | 1--3 | 1.0586 | 56 | 100% | 6.6731 | 87.2% | 0% | 12.8% | 0.28803 | 0 | 0 | 0.28803 | 0 | 0.27476 | 1.0936 | 0.25125 | 0.27476 | 1.0936 | 0.25125 | 0.28945 | 1.152 | 0.25125 | 4.316% | 0.0032472 | 0.0030865 | 2055.0169 | 223.8756 | 449.9011 | 1381.2401 | 2068.7163 | 0 | 0 | 2068.7163 | 9.498e-06%
2026 | SEA1 | SEA1-384F | Tier-1 | Non-HFTD---6 | 3--3 | 6.4007 | 656 | 100% | 54.3248 | 19.85% | 71.87% | 8.289% | 0.53366 | 0 | 0 | 0.53366 | 0 | 0.50907 | 6.6125 | 0.076986 | 0.50907 | 6.6125 | 0.076986 | 0.53627 | 6.9658 | 0.076986 | 0.9823% | 0.028231 | 0.026833 | 1924.322 | 66.4401 | 1300.7116 | 557.1703 | 2004.6487 | 0 | 0 | 2004.6487 | 1.76e-05%
2026 | BA3 | CB BA3 | Tier-1 | Non-HFTD---14 | 3--1 | 7.1958 | 255 | 100% | 7.3804 | 35.46% | 0% | 64.54% | 0.12955 | 0 | 0 | 0.12955 | 0 | 0.12358 | 7.434 | 0.016624 | 0.12358 | 7.434 | 0.016624 | 0.13019 | 7.8312 | 0.016624 | 1.755% | 0.019996 | 0.019007 | 369.0877 | 1.4139 | 144.9388 | 222.735 | 381.4929 | 0 | 0 | 381.4929 | 4.272e-06%
2026 | 856 | CB 856 | Tier-1 | Non-HFTD---7 | 1--4 | 1.0902 | 50 | 100% | 37.8514 | 97.97% | 0% | 2.035% | 1.8355 | 0 | 0 | 1.8355 | 0 | 1.751 | 1.1262 | 1.5547 | 1.751 | 1.1262 | 1.5547 | 1.8445 | 1.1864 | 1.5547 | 4.849% | 0.0032934 | 0.0031304 | 11493.0959 | 2089.5504 | 861.3967 | 8542.1488 | 11505.2746 | 0 | 0 | 11505.2746 | 6.053e-05%
2026 | 458 | 458-41F | Tier-1 | Non-HFTD---19 | 1--1 | 0.10816 | 6 | 100% | 0.15945 | 9.171% | 0% | 90.83% | 0.00072386 | 0 | 0 | 0.00072386 | 0 | 0.00069051 | 0.11174 | 0.0061797 | 0.00069051 | 0.11174 | 0.0061797 | 0.00072741 | 0.11771 | 0.0061797 | 0.454% | 0.0004004 | 0.00038058 | 398.2281 | 0.27217 | 69.3796 | 328.5763 | 417.065 | 0 | 0 | 417.065 | 2.387e-08%
2026 | 455 | CB 455 | Tier-1 | Non-HFTD---1 | 3--5 | 7.4072 | 584 | 100% | 628.6508 | 99.14% | 0% | 0.8628% | 30.8497 | 0 | 0 | 30.8497 | 0 | 29.4285 | 7.6524 | 3.8457 | 29.4285 | 7.6524 | 3.8457 | 31.001 | 8.0613 | 3.8457 | 4.907% | 0.025428 | 0.024169 | 24722.9716 | 4556.7235 | 179.5676 | 19986.6805 | 24734.0802 | 0 | 0 | 24734.0802 | 0.001017%
2026 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 12.4373 | 1312 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 312.1007 | 12.8489 | 24.2901 | 312.1007 | 12.8489 | 24.2901 | 328.7766 | 13.5354 | 24.2901 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2026 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 4.4118 | 225 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.6856 | 4.5578 | 0.36983 | 1.6856 | 4.5578 | 0.36983 | 1.7757 | 4.8013 | 0.36983 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2026 | 492 | 492-1091F | Tier-1 | Non-HFTD---3 | 4--3 | 5.9958 | 185 | 100% | 120.6396 | 2.917% | 93.65% | 3.431% | 0.17419 | 0 | 0 | 0.17419 | 0 | 0.16617 | 6.1942 | 0.026826 | 0.16617 | 6.1942 | 0.026826 | 0.17504 | 6.5252 | 0.026826 | 0.1444% | 0.031661 | 0.030093 | 3810.4024 | 14.7006 | 3329.9773 | 465.7245 | 4003.0516 | 0 | 0 | 4003.0516 | 5.744e-06%
2026 | 334 | 334-45F | Tier-1 | Non-HFTD---17 | 1--2 | 0.45601 | 12 | 100% | 1.6737 | 78.33% | 0% | 21.67% | 0.06489 | 0 | 0 | 0.06489 | 0 | 0.061901 | 0.4711 | 0.13139 | 0.061901 | 0.4711 | 0.13139 | 0.065208 | 0.49628 | 0.13139 | 3.877% | 0.001477 | 0.0014039 | 1133.158 | 100.5295 | 294.453 | 738.1754 | 1145.9489 | 0 | 0 | 1145.9489 | 2.14e-06%
2026 | 472 | CB 472 | Tier-1 | Non-HFTD---6 | 3--3 | 6.9083 | 465 | 100% | 66.0921 | 92.91% | 0% | 7.09% | 3.0396 | 0 | 0 | 3.0396 | 0 | 2.8996 | 7.1369 | 0.40628 | 2.8996 | 7.1369 | 0.40628 | 3.0545 | 7.5182 | 0.40628 | 4.599% | 0.020578 | 0.019559 | 3211.8146 | 441.0584 | 309.4932 | 2461.263 | 3223.674 | 0 | 0 | 3223.674 | 0.0001002%
2026 | 86 | 86-1055F | Tier-1 | Non-HFTD---18 | 1--1 | 1.5329 | 61 | 100% | 1.2551 | 16.29% | 0% | 83.71% | 0.010118 | 0 | 0 | 0.010118 | 0 | 0.0096519 | 1.5837 | 0.0060947 | 0.0096519 | 1.5837 | 0.0060947 | 0.010168 | 1.6683 | 0.0060947 | 0.8061% | 0.0041652 | 0.003959 | 301.3402 | 2.7068 | 56.6739 | 241.9595 | 314.4776 | 0 | 0 | 314.4776 | 3.337e-07%
2026 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 11.6815 | 1018 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 312.9422 | 12.068 | 25.9315 | 312.9422 | 12.068 | 25.9315 | 329.6631 | 12.7129 | 25.9315 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2026 | 741 | CB 741 | Tier-1 | Non-HFTD---15 | 1--2 | 0.84259 | 34 | 100% | 3.3752 | 76.64% | 0% | 23.36% | 0.12804 | 0 | 0 | 0.12804 | 0 | 0.12214 | 0.87047 | 0.14031 | 0.12214 | 0.87047 | 0.14031 | 0.12866 | 0.91698 | 0.14031 | 3.793% | 0.0030248 | 0.0028751 | 1115.8402 | 4.7202 | 850.5122 | 260.6077 | 1129.4176 | 0 | 0 | 1129.4176 | 4.222e-06%
2026 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 9.3687 | 606 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 585.9297 | 9.6788 | 60.5377 | 585.9297 | 9.6788 | 60.5377 | 617.2367 | 10.1959 | 60.5377 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2026 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 7.9883 | 1120 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 142.3168 | 8.2526 | 17.245 | 142.3168 | 8.2526 | 17.245 | 149.921 | 8.6936 | 17.245 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2026 | 1161 | 1161-74 | Tier-1 | Non-HFTD---17 | 1--4 | 0.043561 | 3 | 100% | 1.4617 | 95.2% | 0% | 4.803% | 0.06888 | 0 | 0 | 0.06888 | 0 | 0.065706 | 0.045002 | 1.4601 | 0.065706 | 0.045002 | 1.4601 | 0.069217 | 0.047407 | 1.4601 | 4.712% | 0.0002106 | 0.00020018 | 6940.7274 | 1060.6781 | 30.2849 | 5849.7645 | 6958.0894 | 0 | 0 | 6958.0894 | 2.271e-06%
2026 | NO1 | NO1-289F | Tier-1 | Non-HFTD---16 | 2--1 | 2.4969 | 67 | 100% | 2.4755 | 21.95% | 0% | 78.05% | 0.026901 | 0 | 0 | 0.026901 | 0 | 0.025661 | 2.5796 | 0.0099479 | 0.025661 | 2.5796 | 0.0099479 | 0.027032 | 2.7174 | 0.0099479 | 1.087% | 0.0073078 | 0.0069461 | 338.7505 | 0.19894 | 98.3823 | 240.1693 | 352.5191 | 0 | 0 | 352.5191 | 8.871e-07%
2026 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 14.6369 | 1091 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1264.5743 | 15.1213 | 83.6288 | 1264.5743 | 15.1213 | 83.6288 | 1332.1422 | 15.9292 | 83.6288 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2026 | 549 | 549-33F | Tier-1 | Non-HFTD---15 | 1--3 | 0.21133 | 8 | 100% | 3.6274 | 94.05% | 0% | 5.95% | 0.16887 | 0 | 0 | 0.16887 | 0 | 0.16109 | 0.21833 | 0.73785 | 0.16109 | 0.21833 | 0.73785 | 0.1697 | 0.22999 | 0.73785 | 4.655% | 0.0007928 | 0.00075356 | 4575.3815 | 900.2459 | 28.5738 | 3646.5618 | 4589.5578 | 0 | 0 | 4589.5578 | 5.569e-06%
2026 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 5.8553 | 557 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 246.9272 | 6.049 | 40.821 | 246.9272 | 6.049 | 40.821 | 260.1209 | 6.3722 | 40.821 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2026 | 430 | 430-639 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8368 | 57 | 100% | 3.1665 | 30.19% | 0% | 69.81% | 0.047328 | 0 | 0 | 0.047328 | 0 | 0.045147 | 2.9307 | 0.015405 | 0.045147 | 2.9307 | 0.015405 | 0.04756 | 3.0872 | 0.015405 | 1.495% | 0.00835 | 0.0079367 | 379.2265 | 7.9045 | 91.3742 | 279.9478 | 393.0127 | 0 | 0 | 393.0127 | 1.561e-06%
2026 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 5.3936 | 438 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 34.2027 | 5.5721 | 6.1382 | 34.2027 | 5.5721 | 6.1382 | 36.0302 | 5.8698 | 6.1382 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2026 | 1446 | CB 1446 | Tier-1 | Non-HFTD---17 | 1--2 | 0.3625 | 5 | 100% | 1.7782 | 79.62% | 0% | 20.38% | 0.070088 | 0 | 0 | 0.070088 | 0 | 0.066859 | 0.3745 | 0.17853 | 0.066859 | 0.3745 | 0.17853 | 0.070432 | 0.39451 | 0.17853 | 3.941% | 0.0015656 | 0.0014881 | 1135.819 | 136.3299 | 64.1894 | 935.2997 | 1147.8711 | 0 | 0 | 1147.8711 | 2.311e-06%
2026 | 492 | CB 492 | Tier-1 | Non-HFTD---4 | 3--4 | 2.6833 | 129 | 100% | 147.6974 | 50.2% | 48.6% | 1.193% | 3.6704 | 0 | 0 | 3.6704 | 0 | 3.5013 | 2.7721 | 1.2631 | 3.5013 | 2.7721 | 1.2631 | 3.6884 | 2.9202 | 1.2631 | 2.485% | 0.022696 | 0.021573 | 6507.5812 | 522.8448 | 3980.5377 | 2004.1987 | 6676.3406 | 0 | 0 | 6676.3406 | 0.000121%
2026 | 295 | CB 295 | Tier-1 | Non-HFTD---13 | 1--3 | 0.49829 | 18 | 100% | 6.2908 | 96.1% | 0% | 3.899% | 0.29925 | 0 | 0 | 0.29925 | 0 | 0.28546 | 0.51478 | 0.55454 | 0.28546 | 0.51478 | 0.55454 | 0.30072 | 0.54228 | 0.55454 | 4.757% | 0.0015178 | 0.0014427 | 4144.6515 | 315.6182 | 2064.3478 | 1764.6855 | 4153.0684 | 0 | 0 | 4153.0684 | 9.868e-06%
2026 | 189 | 189-782F | Tier-1 | Non-HFTD---2 | 4--4 | 2.3879 | 104 | 100% | 270.4001 | 65.38% | 34.07% | 0.5513% | 8.7513 | 0 | 0 | 8.7513 | 0 | 8.3481 | 2.4669 | 3.384 | 8.3481 | 2.4669 | 3.384 | 8.7942 | 2.5987 | 3.384 | 3.236% | 0.052115 | 0.049536 | 5188.4869 | 959.5403 | 1630.2236 | 2598.723 | 5282.0256 | 0 | 0 | 5282.0256 | 0.0002886%
2026 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.1678 | 13 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.3389 | 0.17336 | 30.7974 | 5.3389 | 0.17336 | 30.7974 | 5.6242 | 0.18262 | 30.7974 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2026 | 61 | 61-21F | Tier-1 | Non-HFTD---4 | 3--4 | 1.9962 | 97 | 100% | 113.4454 | 6.678% | 92.1% | 1.219% | 0.37502 | 0 | 0 | 0.37502 | 0 | 0.35775 | 2.0623 | 0.17347 | 0.35775 | 2.0623 | 0.17347 | 0.37686 | 2.1725 | 0.17347 | 0.3306% | 0.016874 | 0.016039 | 6723.0064 | 49.7643 | 5828.0334 | 845.2086 | 7049.7441 | 0 | 0 | 7049.7441 | 1.237e-05%
2026 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 5.2595 | 161 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 5.2339 | 5.4335 | 0.96327 | 5.2339 | 5.4335 | 0.96327 | 5.5136 | 5.7238 | 0.96327 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2026 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.053788 | 0 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.088733 | 0.055568 | 1.5968 | 0.088733 | 0.055568 | 1.5968 | 0.093474 | 0.058537 | 1.5968 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2026 | 704 | CB 704 | Tier-1 | Non-HFTD---1 | 2--4 | 1.7828 | 25 | 100% | 194.5689 | 34.09% | 65.2% | 0.715% | 3.2833 | 0 | 0 | 3.2833 | 0 | 3.132 | 1.8418 | 1.7005 | 3.132 | 1.8418 | 1.7005 | 3.2993 | 1.9402 | 1.7005 | 1.687% | 0.012532 | 0.011912 | 15525.5161 | 542.8023 | 11295.5697 | 3687.1441 | 16058.4225 | 0 | 0 | 16058.4225 | 0.0001083%
2026 | 390 | 390-346AE | Tier-1 | Non-HFTD---3 | 5--2 | 1.9503 | 17 | 100% | 137.7692 | 30.57% | 68.57% | 0.8554% | 2.085 | 0 | 0 | 2.085 | 0 | 1.9889 | 2.0149 | 0.98712 | 1.9889 | 2.0149 | 0.98712 | 2.0952 | 2.1225 | 0.98712 | 1.513% | 0.10161 | 0.096578 | 1355.8897 | 68.0236 | 798.9805 | 488.8856 | 1404.9131 | 0 | 0 | 1404.9131 | 6.875e-05%
2026 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 11.1523 | 379 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 373.1142 | 11.5213 | 32.3847 | 373.1142 | 11.5213 | 32.3847 | 393.0502 | 12.1369 | 32.3847 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2026 | 368 | 368-21AE | Tier-1 | Non-HFTD---6 | 3--3 | 3.2028 | 121 | 100% | 50.8163 | 7.913% | 86.7% | 5.382% | 0.19904 | 0 | 0 | 0.19904 | 0 | 0.18987 | 3.3088 | 0.057383 | 0.18987 | 3.3088 | 0.057383 | 0.20002 | 3.4856 | 0.057383 | 0.3917% | 0.015098 | 0.01435 | 3365.8095 | 4.0471 | 2936.2763 | 425.4862 | 3527.2237 | 0 | 0 | 3527.2237 | 6.564e-06%
2026 | 393 | CB 393 | Tier-2 | Tier-2---19 | 1--3 | 1.0951 | 18 | 100% | 8.3766 | 93.83% | 0% | 6.171% | 0.38906 | 0 | 0 | 0.38906 | 0 | 0.37113 | 1.1313 | 0.32806 | 0.37113 | 1.1313 | 0.32806 | 0.39096 | 1.1917 | 0.32806 | 4.645% | 0.0030912 | 0.0029382 | 2709.8263 | 11.6903 | 2486.8043 | 211.3317 | 2718.5348 | 0 | 0 | 2718.5348 | 1.283e-05%
2026 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 10.9006 | 366 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 142.1765 | 11.2613 | 12.6252 | 142.1765 | 11.2613 | 12.6252 | 149.7732 | 11.8631 | 12.6252 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2026 | 545 | 545-885R | Tier-1 | Non-HFTD---7 | 2--3 | 0.51992 | 17 | 100% | 32.7256 | 0.2758% | 98.33% | 1.395% | 0.004467 | 0 | 0 | 0.004467 | 0 | 0.0042612 | 0.53713 | 0.0079334 | 0.0042612 | 0.53713 | 0.0079334 | 0.0044889 | 0.56583 | 0.0079334 | 0.01365% | 0.012213 | 0.011608 | 2679.6164 | 2.9972 | 2417.3334 | 259.2857 | 2818.7803 | 0 | 0 | 2818.7803 | 1.473e-07%
2026 | 493 | 493-480R | Tier-1 | Non-HFTD---13 | 1--4 | 0.16818 | 0 | 100% | 7.2779 | 97.57% | 0% | 2.432% | 0.3515 | 0 | 0 | 0.3515 | 0 | 0.3353 | 0.17375 | 1.9298 | 0.3353 | 0.17375 | 1.9298 | 0.35322 | 0.18303 | 1.9298 | 4.83% | 0.0008656 | 0.00082275 | 8407.9508 | 1265.6364 | 478.0477 | 6664.2667 | 8418.599 | 0 | 0 | 8418.599 | 1.159e-05%
2026 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 16.0805 | 638 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 154.5294 | 16.6126 | 9.3019 | 154.5294 | 16.6126 | 9.3019 | 162.7862 | 17.5002 | 9.3019 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2026 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 8.5739 | 534 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 257.6241 | 8.8576 | 29.0851 | 257.6241 | 8.8576 | 29.0851 | 271.3893 | 9.3309 | 29.0851 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2026 | DM1 | DM1-9R | Tier-1 | Non-HFTD---8 | 3--3 | 4.0288 | 231 | 100% | 39.7128 | 14.13% | 78.81% | 7.065% | 0.27771 | 0 | 0 | 0.27771 | 0 | 0.26492 | 4.1621 | 0.06365 | 0.26492 | 4.1621 | 0.06365 | 0.27907 | 4.3845 | 0.06365 | 0.6993% | 0.022154 | 0.021057 | 1792.5792 | 37.2507 | 1380.9748 | 374.3537 | 1872.7445 | 0 | 0 | 1872.7445 | 9.158e-06%
2026 | 555 | 555-24F | Tier-1 | Non-HFTD---15 | 2--2 | 2.2983 | 36 | 100% | 4.4061 | 53.21% | 0% | 46.79% | 0.11604 | 0 | 0 | 0.11604 | 0 | 0.1107 | 2.3744 | 0.046623 | 0.1107 | 2.3744 | 0.046623 | 0.11661 | 2.5012 | 0.046623 | 2.634% | 0.008161 | 0.007757 | 539.893 | 26.4554 | 148.5341 | 364.9035 | 553.0495 | 0 | 0 | 553.0495 | 3.827e-06%
2026 | 194 | CB 194 | Tier-1 | Non-HFTD---7 | 3--3 | 5.9897 | 219 | 100% | 41.3648 | 90.26% | 0% | 9.742% | 1.8481 | 0 | 0 | 1.8481 | 0 | 1.763 | 6.188 | 0.2849 | 1.763 | 6.188 | 0.2849 | 1.8572 | 6.5186 | 0.2849 | 4.468% | 0.018044 | 0.017151 | 2292.4387 | 249.104 | 561.289 | 1482.0457 | 2304.0686 | 0 | 0 | 2304.0686 | 6.094e-05%
2026 | 323 | 323-1134F | Tier-1 | Non-HFTD---17 | 1--1 | 1.1165 | 113 | 100% | 1.8006 | 61.04% | 0% | 38.96% | 0.054404 | 0 | 0 | 0.054404 | 0 | 0.051898 | 1.1534 | 0.044994 | 0.051898 | 1.1534 | 0.044994 | 0.054671 | 1.2151 | 0.044994 | 3.021% | 0.0037208 | 0.0035366 | 483.9282 | 45.0171 | 36.2195 | 402.6916 | 493.747 | 0 | 0 | 493.747 | 1.794e-06%
2026 | 488 | 488-32R | Tier-1 | Non-HFTD---15 | 2--1 | 2.7502 | 123 | 100% | 3.7644 | 43.12% | 0% | 56.88% | 0.080348 | 0 | 0 | 0.080348 | 0 | 0.076646 | 2.8412 | 0.026976 | 0.076646 | 2.8412 | 0.026976 | 0.080741 | 2.993 | 0.026976 | 2.134% | 0.008362 | 0.0079481 | 450.1773 | 0.19268 | 217.3752 | 232.6094 | 463.5125 | 0 | 0 | 463.5125 | 2.65e-06%
2026 | 474 | 474-29 | Tier-1 | Non-HFTD---1 | 2--5 | 1.8853 | 277 | 100% | 1510.7302 | 99.89% | 0% | 0.1058% | 74.702 | 0 | 0 | 74.702 | 0 | 71.2607 | 1.9476 | 36.5882 | 71.2607 | 1.9476 | 36.5882 | 75.0682 | 2.0517 | 36.5882 | 4.945% | 0.010755 | 0.010222 | 140472.931 | 24566.9965 | 189.9323 | 115716.0023 | 140480.6687 | 0 | 0 | 140480.6687 | 0.002463%
2026 | 410 | CB 410 | Tier-1 | Non-HFTD---6 | 3--3 | 6.5019 | 120 | 100% | 46.5416 | 89.87% | 0% | 10.13% | 2.0704 | 0 | 0 | 2.0704 | 0 | 1.975 | 6.7171 | 0.29403 | 1.975 | 6.7171 | 0.29403 | 2.0805 | 7.076 | 0.29403 | 4.448% | 0.019659 | 0.018686 | 2367.4198 | 207.1663 | 885.4486 | 1274.805 | 2379.9113 | 0 | 0 | 2379.9113 | 6.827e-05%
2026 | 731 | 731-49F | Tier-1 | Non-HFTD---3 | 4--3 | 16.5002 | 1184 | 100% | 102.8304 | 89.72% | 0% | 10.28% | 4.5668 | 0 | 0 | 4.5668 | 0 | 4.3564 | 17.0462 | 0.25556 | 4.3564 | 17.0462 | 0.25556 | 4.5892 | 17.957 | 0.25556 | 4.441% | 0.046272 | 0.043982 | 2222.3019 | 294.0745 | 219.4482 | 1708.7791 | 2234.2007 | 0 | 0 | 2234.2007 | 0.0001506%
2026 | 116 | 116-31F | Tier-1 | Non-HFTD---4 | 3--4 | 2.0027 | 95 | 100% | 141.4772 | 0.3709% | 98.55% | 1.083% | 0.025973 | 0 | 0 | 0.025973 | 0 | 0.024776 | 2.0689 | 0.011975 | 0.024776 | 2.0689 | 0.011975 | 0.0261 | 2.1795 | 0.011975 | 0.01836% | 0.020781 | 0.019753 | 6807.8774 | 10.0575 | 6163.2276 | 634.5922 | 7161.1021 | 0 | 0 | 7161.1021 | 8.565e-07%
2026 | CD3 | CB CD3 | Tier-1 | Non-HFTD---18 | 1--1 | 1.6606 | 80 | 100% | 1.5668 | 26.18% | 0% | 73.82% | 0.020307 | 0 | 0 | 0.020307 | 0 | 0.019372 | 1.7155 | 0.011292 | 0.019372 | 1.7155 | 0.011292 | 0.020407 | 1.8072 | 0.011292 | 1.296% | 0.0045772 | 0.0043506 | 342.3111 | 1.0113 | 107.5472 | 233.7526 | 355.4703 | 0 | 0 | 355.4703 | 6.697e-07%
2026 | 124 | 124-258R | Tier-1 | Non-HFTD---17 | 1--2 | 0.39356 | 0 | 100% | 1.2499 | 77.42% | 0% | 22.58% | 0.047899 | 0 | 0 | 0.047899 | 0 | 0.045693 | 0.40658 | 0.11238 | 0.045693 | 0.40658 | 0.11238 | 0.048134 | 0.42831 | 0.11238 | 3.832% | 0.0013672 | 0.0012995 | 914.1789 | 6.3342 | 688.3424 | 219.5024 | 924.9284 | 0 | 0 | 924.9284 | 1.58e-06%
2026 | 519 | CB 519 | Tier-1 | Non-HFTD---11 | 2--2 | 3.4237 | 69 | 100% | 14.2981 | 79.95% | 0% | 20.05% | 0.56585 | 0 | 0 | 0.56585 | 0 | 0.53978 | 3.537 | 0.15261 | 0.53978 | 3.537 | 0.15261 | 0.56862 | 3.7259 | 0.15261 | 3.958% | 0.011118 | 0.010568 | 1286.0072 | 5.5356 | 1018.7507 | 261.721 | 1299.4354 | 0 | 0 | 1299.4354 | 1.866e-05%
2026 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | 3--5 | 1.3063 | 338 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 13.1668 | 0 | 0 | 13.1668 | 0 | 12.5602 | 1.3495 | 9.3073 | 12.5602 | 1.3495 | 9.3073 | 13.2313 | 1.4216 | 9.3073 | 4.021% | 0.015736 | 0.014957 | 20808.6476 | 4091.2697 | 3467.4094 | 13249.9684 | 21012.0249 | 0 | 0 | 21012.0249 | 0.0004342%
2026 | UP1 | UP1-10 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6159 | 428 | 100% | 10.8294 | 44.21% | 0% | 55.79% | 0.23697 | 0 | 0 | 0.23697 | 0 | 0.22606 | 9.9342 | 0.022755 | 0.22606 | 9.9342 | 0.022755 | 0.23813 | 10.465 | 0.022755 | 2.188% | 0.026285 | 0.024984 | 412.0009 | 20.5611 | 108.9901 | 282.4498 | 423.9721 | 0 | 0 | 423.9721 | 7.814e-06%
2026 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 14.2375 | 394 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2122.0228 | 14.7086 | 144.2706 | 2122.0228 | 14.7086 | 144.2706 | 2235.4054 | 15.4945 | 144.2706 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2026 | EV1 | CB EV1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.3028 | 221 | 100% | 2.6461 | 17.66% | 0% | 82.34% | 0.023125 | 0 | 0 | 0.023125 | 0 | 0.02206 | 3.4121 | 0.0064651 | 0.02206 | 3.4121 | 0.0064651 | 0.023239 | 3.5944 | 0.0064651 | 0.8739% | 0.0091594 | 0.008706 | 288.895 | 0.179 | 72.6151 | 216.101 | 301.2838 | 0 | 0 | 301.2838 | 7.626e-07%
2026 | 496 | 496-21 | Tier-1 | Non-HFTD---20 | 1--1 | 0.33125 | 15 | 100% | 0.3919 | 1.941% | 0% | 98.06% | 0.00037644 | 0 | 0 | 0.00037644 | 0 | 0.0003591 | 0.34221 | 0.0010493 | 0.0003591 | 0.34221 | 0.0010493 | 0.00037829 | 0.3605 | 0.0010493 | 0.09606% | 0.0013684 | 0.0013007 | 286.3902 | 0.21132 | 31.0685 | 255.1103 | 301.0153 | 0 | 0 | 301.0153 | 1.241e-08%
2026 | 130 | CB 130 | Tier-1 | Non-HFTD---11 | 2--3 | 1.9606 | 69 | 100% | 14.2562 | 86.9% | 0% | 13.1% | 0.61324 | 0 | 0 | 0.61324 | 0 | 0.58499 | 2.0255 | 0.28882 | 0.58499 | 2.0255 | 0.28882 | 0.61625 | 2.1337 | 0.28882 | 4.302% | 0.0066204 | 0.0062927 | 2153.3693 | 1.5526 | 1888.1859 | 263.6308 | 2168.0593 | 0 | 0 | 2168.0593 | 2.022e-05%
2026 | 506 | CB 506 | Tier-1 | Non-HFTD---9 | 2--3 | 1.454 | 84 | 100% | 16.1242 | 91.65% | 0% | 8.345% | 0.73154 | 0 | 0 | 0.73154 | 0 | 0.69784 | 1.5021 | 0.46458 | 0.69784 | 1.5021 | 0.46458 | 0.73513 | 1.5824 | 0.46458 | 4.537% | 0.005379 | 0.0051127 | 2997.6192 | 25.0112 | 2618.7739 | 353.8341 | 3010.6465 | 0 | 0 | 3010.6465 | 2.412e-05%
2026 | 180 | 180-1156 | Tier-1 | Non-HFTD---17 | 1--1 | 0.91007 | 24 | 100% | 1.3219 | 52.08% | 0% | 47.92% | 0.034078 | 0 | 0 | 0.034078 | 0 | 0.032508 | 0.94019 | 0.034576 | 0.032508 | 0.94019 | 0.034576 | 0.034245 | 0.99043 | 0.034576 | 2.578% | 0.00285 | 0.0027089 | 463.8363 | 32.8306 | 62.4543 | 368.5515 | 475.4119 | 0 | 0 | 475.4119 | 1.124e-06%
2026 | DM1 | CB DM1 | Tier-1 | Non-HFTD---17 | 1--3 | 0.093371 | 9 | 100% | 1.7967 | 94.23% | 0% | 5.774% | 0.083802 | 0 | 0 | 0.083802 | 0 | 0.079941 | 0.096461 | 0.82874 | 0.079941 | 0.096461 | 0.82874 | 0.084213 | 0.10162 | 0.82874 | 4.664% | 0.000494 | 0.00046955 | 3637.0553 | 614.328 | 456.8195 | 2565.9079 | 3647.9913 | 0 | 0 | 3647.9913 | 2.763e-06%
2026 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 2.4181 | 238 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 80.3262 | 2.4982 | 32.1542 | 80.3262 | 2.4982 | 32.1542 | 84.6182 | 2.6316 | 32.1542 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2026 | 497 | CB 497 | Tier-1 | Non-HFTD---4 | 2--4 | 3.432 | 133 | 100% | 116.2654 | 98.23% | 0% | 1.77% | 5.6533 | 0 | 0 | 5.6533 | 0 | 5.3929 | 3.5456 | 1.521 | 5.3929 | 3.5456 | 1.521 | 5.681 | 3.735 | 1.521 | 4.862% | 0.012543 | 0.011922 | 9269.494 | 1186.1414 | 3789.5424 | 4293.8102 | 9278.0371 | 0 | 0 | 9278.0371 | 0.0001864%
2026 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 6.6007 | 891 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 148.7546 | 6.8192 | 21.8142 | 148.7546 | 6.8192 | 21.8142 | 156.7028 | 7.1835 | 21.8142 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2026 | GH1 | CB GH1 | Tier-1 | Non-HFTD---16 | 2--1 | 2.2529 | 134 | 100% | 2.7406 | 41.83% | 0% | 58.17% | 0.056751 | 0 | 0 | 0.056751 | 0 | 0.054136 | 2.3274 | 0.02326 | 0.054136 | 2.3274 | 0.02326 | 0.057029 | 2.4518 | 0.02326 | 2.071% | 0.0067936 | 0.0064573 | 403.4022 | 5.1571 | 159.0665 | 239.1785 | 415.6219 | 0 | 0 | 415.6219 | 1.871e-06%
2026 | RI1 | CB RI1 | Tier-1 | Non-HFTD---15 | 2--1 | 3.5895 | 135 | 100% | 4.7586 | 45.3% | 0% | 54.7% | 0.10671 | 0 | 0 | 0.10671 | 0 | 0.1018 | 3.7083 | 0.027451 | 0.1018 | 3.7083 | 0.027451 | 0.10724 | 3.9065 | 0.027451 | 2.243% | 0.010279 | 0.0097704 | 462.9377 | 10.357 | 170.4671 | 282.1136 | 476.1243 | 0 | 0 | 476.1243 | 3.519e-06%
2026 | 284 | CB 284 | Tier-1 | Non-HFTD---4 | 2--4 | 2.2045 | 412 | 100% | 126.8807 | 47.92% | 50.35% | 1.736% | 3.0095 | 0 | 0 | 3.0095 | 0 | 2.8708 | 2.2775 | 1.2605 | 2.8708 | 2.2775 | 1.2605 | 3.0242 | 2.3992 | 1.2605 | 2.372% | 0.01321 | 0.012556 | 9604.8958 | 620.4944 | 5222.3316 | 3762.0699 | 9865.4152 | 0 | 0 | 9865.4152 | 9.924e-05%
2026 | 596 | CB 596 | Tier-2 | Tier-2---14 | 2--5 | 1.4705 | 72 | 100% | 273.3297 | 99.62% | 0% | 0.3838% | 13.4779 | 0 | 0 | 13.4779 | 0 | 12.857 | 1.5191 | 8.4635 | 12.857 | 1.5191 | 8.4635 | 13.544 | 1.6003 | 8.4635 | 4.931% | 0.0060594 | 0.0057595 | 45108.3697 | 6928.3062 | 2440.2235 | 35739.84 | 45117.3849 | 0 | 0 | 45117.3849 | 0.0004445%
2026 | 363 | 363-25 | Tier-1 | Non-HFTD---9 | 2--3 | 0.49474 | 5 | 100% | 16.2298 | 0.2424% | 98% | 1.754% | 0.0019477 | 0 | 0 | 0.0019477 | 0 | 0.001858 | 0.51112 | 0.0036351 | 0.001858 | 0.51112 | 0.0036351 | 0.0019572 | 0.53842 | 0.0036351 | 0.012% | 0.0067338 | 0.0064005 | 2410.1955 | 3.3685 | 2072.0386 | 334.7885 | 2535.409 | 0 | 0 | 2535.409 | 6.423e-08%
2026 | 279 | 279-10AE | Tier-1 | Non-HFTD---3 | 4--3 | 13.1186 | 397 | 100% | 166.5714 | 5.911% | 88.12% | 5.969% | 0.4874 | 0 | 0 | 0.4874 | 0 | 0.46495 | 13.5527 | 0.034307 | 0.46495 | 13.5527 | 0.034307 | 0.48979 | 14.2768 | 0.034307 | 0.2926% | 0.054414 | 0.051721 | 3061.1869 | 21.6691 | 2585.1276 | 454.3903 | 3211.1832 | 0 | 0 | 3211.1832 | 1.607e-05%
2026 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 5.0489 | 229 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.089086 | 5.216 | 0.017079 | 0.089086 | 5.216 | 0.017079 | 0.093845 | 5.4947 | 0.017079 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2026 | 1116 | CB 1116 | Tier-1 | Non-HFTD---11 | 1--4 | 0.18467 | 5 | 100% | 9.3364 | 98.6% | 0% | 1.405% | 0.45566 | 0 | 0 | 0.45566 | 0 | 0.43467 | 0.19078 | 2.2783 | 0.43467 | 0.19078 | 2.2783 | 0.45789 | 0.20098 | 2.2783 | 4.88% | 0.0007112 | 0.000676 | 13127.6637 | 2116.3329 | 17.0252 | 10994.3055 | 13137.2689 | 0 | 0 | 13137.2689 | 1.503e-05%
2026 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 1.3115 | 242 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.6148 | 1.3549 | 7.8342 | 10.6148 | 1.3549 | 7.8342 | 11.1819 | 1.4273 | 7.8342 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2026 | 62 | 62-22AE | Tier-1 | Non-HFTD---3 | 4--3 | 8.7206 | 747 | 100% | 149.8506 | 12.38% | 83.65% | 3.975% | 0.91818 | 0 | 0 | 0.91818 | 0 | 0.87588 | 9.0092 | 0.097221 | 0.87588 | 9.0092 | 0.097221 | 0.92268 | 9.4906 | 0.097221 | 0.6127% | 0.035713 | 0.033945 | 4195.99 | 92.2315 | 3243.5589 | 860.1996 | 4387.459 | 0 | 0 | 4387.459 | 3.028e-05%
2026 | 462 | 462-868 | Tier-1 | Non-HFTD---13 | 2--2 | 2.5009 | 25 | 100% | 8.2724 | 79.98% | 0% | 20.02% | 0.32751 | 0 | 0 | 0.32751 | 0 | 0.31242 | 2.5837 | 0.12092 | 0.31242 | 2.5837 | 0.12092 | 0.32912 | 2.7217 | 0.12092 | 3.959% | 0.0067062 | 0.0063742 | 1233.54 | 39.6864 | 767.131 | 426.7227 | 1246.3996 | 0 | 0 | 1246.3996 | 1.08e-05%
2026 | CS4 | CB CS4 | Tier-1 | Non-HFTD---14 | 3--1 | 7.3911 | 183 | 100% | 7.7232 | 38.74% | 0% | 61.26% | 0.14811 | 0 | 0 | 0.14811 | 0 | 0.14129 | 7.6357 | 0.018503 | 0.14129 | 7.6357 | 0.018503 | 0.14883 | 8.0437 | 0.018503 | 1.918% | 0.019993 | 0.019004 | 386.2931 | 3.2342 | 152.261 | 230.798 | 398.6167 | 0 | 0 | 398.6167 | 4.884e-06%
2026 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 3.7494 | 937 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 18.4924 | 3.8735 | 4.7741 | 18.4924 | 3.8735 | 4.7741 | 19.4805 | 4.0805 | 4.7741 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2026 | 586 | 586-3 | Tier-1 | Non-HFTD---1 | 3--5 | 4.2473 | 442 | 100% | 516.8084 | 87.93% | 11.54% | 0.527% | 22.4945 | 0 | 0 | 22.4945 | 0 | 21.4582 | 4.3879 | 4.8904 | 21.4582 | 4.3879 | 4.8904 | 22.6048 | 4.6223 | 4.8904 | 4.353% | 0.028089 | 0.026699 | 18398.9604 | 3049.2137 | 1855.4913 | 13494.2554 | 18514.6041 | 0 | 0 | 18514.6041 | 0.0007418%
2026 | 166 | 166-462F | Tier-1 | Non-HFTD---14 | 3--1 | 6.8144 | 161 | 100% | 8.466 | 45.81% | 0% | 54.19% | 0.19198 | 0 | 0 | 0.19198 | 0 | 0.18313 | 7.04 | 0.026013 | 0.18313 | 7.04 | 0.026013 | 0.19292 | 7.4161 | 0.026013 | 2.268% | 0.020176 | 0.019178 | 419.5983 | 1.4039 | 205.3363 | 212.8581 | 431.4397 | 0 | 0 | 431.4397 | 6.331e-06%
2026 | 235 | CB 235 | Tier-2 | Tier-2---12 | 1--5 | 0.15928 | 0 | 100% | 443.5427 | 99.96% | 0% | 0.03939% | 21.9467 | 0 | 0 | 21.9467 | 0 | 20.9357 | 0.16455 | 127.2288 | 20.9357 | 0.16455 | 127.2288 | 22.0543 | 0.17334 | 127.2288 | 4.948% | 0.0007134 | 0.00067809 | 621730.7449 | 100003.5038 | 3209.2492 | 518517.9918 | 621743.4984 | 0 | 0 | 621743.4984 | 0.0007237%
2026 | 431 | 431-478 | Tier-1 | Non-HFTD---18 | 1--1 | 1.7773 | 17 | 100% | 1.8417 | 28.24% | 0% | 71.76% | 0.025748 | 0 | 0 | 0.025748 | 0 | 0.024562 | 1.8361 | 0.013377 | 0.024562 | 1.8361 | 0.013377 | 0.025874 | 1.9342 | 0.013377 | 1.398% | 0.004891 | 0.0046489 | 376.5557 | 0.20332 | 130.8951 | 245.4573 | 390.6275 | 0 | 0 | 390.6275 | 8.491e-07%
2026 | 531 | CB 531 | Tier-1 | Non-HFTD---6 | 3--3 | 6.3466 | 124 | 100% | 47.6835 | 90.24% | 0% | 9.762% | 2.1299 | 0 | 0 | 2.1299 | 0 | 2.0318 | 6.5566 | 0.30989 | 2.0318 | 6.5566 | 0.30989 | 2.1404 | 6.9069 | 0.30989 | 4.467% | 0.021006 | 0.019967 | 2269.9514 | 122.328 | 1530.9229 | 616.7005 | 2281.4913 | 0 | 0 | 2281.4913 | 7.024e-05%
2026 | 458 | 458-33F | Tier-1 | Non-HFTD---13 | 2--2 | 1.3521 | 11 | 100% | 7.8002 | 76.69% | 0% | 23.31% | 0.29609 | 0 | 0 | 0.29609 | 0 | 0.28245 | 1.3968 | 0.20221 | 0.28245 | 1.3968 | 0.20221 | 0.29754 | 1.4714 | 0.20221 | 3.796% | 0.0058714 | 0.0055808 | 1328.509 | 0.80331 | 1043.3685 | 284.3372 | 1344.6396 | 0 | 0 | 1344.6396 | 9.764e-06%
2026 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 3.7841 | 448 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 135.4283 | 3.9093 | 34.6426 | 135.4283 | 3.9093 | 34.6426 | 142.6644 | 4.1182 | 34.6426 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2026 | 549 | 549-36F | Tier-1 | Non-HFTD---17 | 1--1 | 0.72155 | 55 | 100% | 1.2095 | 52.11% | 0% | 47.89% | 0.031196 | 0 | 0 | 0.031196 | 0 | 0.029759 | 0.74542 | 0.039922 | 0.029759 | 0.74542 | 0.039922 | 0.031349 | 0.78525 | 0.039922 | 2.579% | 0.002468 | 0.0023458 | 490.0708 | 38.9275 | 37.7198 | 413.4235 | 502.2942 | 0 | 0 | 502.2942 | 1.029e-06%
2026 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.11194 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 7.1363 | 0.11564 | 61.709 | 7.1363 | 0.11564 | 61.709 | 7.5176 | 0.12182 | 61.709 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2026 | 492 | 492-1090F | Tier-1 | Non-HFTD---8 | 3--2 | 2.9425 | 77 | 100% | 34.6286 | 4.526% | 88.49% | 6.986% | 0.077582 | 0 | 0 | 0.077582 | 0 | 0.074008 | 3.0398 | 0.024346 | 0.074008 | 3.0398 | 0.024346 | 0.077963 | 3.2023 | 0.024346 | 0.224% | 0.023375 | 0.022218 | 1481.4265 | 7.0789 | 1228.0468 | 246.3007 | 1555.0841 | 0 | 0 | 1555.0841 | 2.558e-06%
2026 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 26.8775 | 335 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 183.9604 | 27.7669 | 6.6252 | 183.9604 | 27.7669 | 6.6252 | 193.7897 | 29.2505 | 6.6252 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2026 | 578 | 578-227AE | Tier-1 | Non-HFTD---2 | 4--4 | 7.3342 | 376 | 100% | 226.1954 | 3.205% | 94.33% | 2.464% | 0.35882 | 0 | 0 | 0.35882 | 0 | 0.34229 | 7.577 | 0.045176 | 0.34229 | 7.577 | 0.045176 | 0.36058 | 7.9818 | 0.045176 | 0.1586% | 0.032265 | 0.030668 | 7010.4637 | 18.2304 | 6217.6891 | 774.5442 | 7363.8535 | 0 | 0 | 7363.8535 | 1.183e-05%
2026 | 792 | 792-46 | Tier-1 | Non-HFTD---3 | 4--3 | 5.8164 | 352 | 100% | 104.7877 | 27.86% | 68.25% | 3.891% | 1.4453 | 0 | 0 | 1.4453 | 0 | 1.3787 | 6.0089 | 0.22944 | 1.3787 | 6.0089 | 0.22944 | 1.4523 | 6.33 | 0.22944 | 1.379% | 0.033958 | 0.032277 | 3085.8225 | 12.0566 | 2731.0247 | 342.7413 | 3201.7488 | 0 | 0 | 3201.7488 | 4.766e-05%
2026 | 1406 | 1406-436 | Tier-1 | Non-HFTD---17 | 1--2 | 0.48596 | 64 | 100% | 0.81719 | 51.42% | 0% | 48.58% | 0.020799 | 0 | 0 | 0.020799 | 0 | 0.019841 | 0.50204 | 0.039521 | 0.019841 | 0.50204 | 0.039521 | 0.020901 | 0.52887 | 0.039521 | 2.545% | 0.0015042 | 0.0014297 | 543.2743 | 2.4202 | 289.5714 | 251.2826 | 557.0192 | 0 | 0 | 557.0192 | 6.859e-07%
2026 | SR4 | CB SR4 | Tier-1 | Non-HFTD---16 | 3--1 | 4.8715 | 126 | 100% | 4.8983 | 33.88% | 0% | 66.12% | 0.082138 | 0 | 0 | 0.082138 | 0 | 0.078354 | 5.0328 | 0.015569 | 0.078354 | 5.0328 | 0.015569 | 0.08254 | 5.3017 | 0.015569 | 1.677% | 0.013512 | 0.012844 | 362.5061 | 1.3132 | 137.6442 | 223.5487 | 374.9894 | 0 | 0 | 374.9894 | 2.709e-06%
2026 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 8.4165 | 681 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 543.0092 | 8.6951 | 62.4504 | 543.0092 | 8.6951 | 62.4504 | 572.0229 | 9.1596 | 62.4504 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2026 | 239 | CB 239 | Tier-3 | Tier-3---20 | 1--5 | 0.039773 | 0 | 100% | 10.6776 | 99.64% | 0% | 0.3633% | 0.52662 | 0 | 0 | 0.52662 | 0 | 0.50236 | 0.041089 | 12.2262 | 0.50236 | 0.041089 | 12.2262 | 0.5292 | 0.043284 | 12.2262 | 4.932% | 0.0001826 | 0.00017356 | 58475.5699 | 8842.2618 | 1906.0953 | 47727.2128 | 58486.6341 | 0 | 0 | 58486.6341 | 1.737e-05%
2026 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 9.8927 | 660 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 234.7817 | 10.22 | 22.9727 | 234.7817 | 10.22 | 22.9727 | 247.3264 | 10.7661 | 22.9727 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2026 | 374 | 374-708R | Tier-1 | Non-HFTD---18 | 2--1 | 1.5335 | 37 | 100% | 1.7306 | 14.21% | 0% | 85.79% | 0.012174 | 0 | 0 | 0.012174 | 0 | 0.011613 | 1.5842 | 0.0073306 | 0.011613 | 1.5842 | 0.0073306 | 0.012234 | 1.6689 | 0.0073306 | 0.7035% | 0.005207 | 0.0049493 | 332.3667 | 0.21592 | 73.1264 | 259.0243 | 347.2158 | 0 | 0 | 347.2158 | 4.015e-07%
2026 | KR1 | CB KR1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.1231 | 29 | 100% | 0.82769 | 14.7% | 0% | 85.3% | 0.0060217 | 0 | 0 | 0.0060217 | 0 | 0.0057443 | 1.1603 | 0.0049509 | 0.0057443 | 1.1603 | 0.0049509 | 0.0060513 | 1.2223 | 0.0049509 | 0.7275% | 0.0031394 | 0.002984 | 263.645 | 0.16923 | 59.1795 | 204.2962 | 275.357 | 0 | 0 | 275.357 | 1.986e-07%
2026 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 5.9928 | 318 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 251.9816 | 6.1911 | 40.7005 | 251.9816 | 6.1911 | 40.7005 | 265.4453 | 6.5219 | 40.7005 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2026 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 1.221 | 97 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 104.5514 | 1.2614 | 82.8832 | 104.5514 | 1.2614 | 82.8832 | 110.1378 | 1.3288 | 82.8832 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2026 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 16.7214 | 1433 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1320.7925 | 17.2748 | 76.458 | 1320.7925 | 17.2748 | 76.458 | 1391.3643 | 18.1978 | 76.458 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2026 | 159 | CB 159 | Tier-1 | Non-HFTD---11 | 1--4 | 0.92049 | 19 | 100% | 13.6027 | 95.86% | 0% | 4.138% | 0.64547 | 0 | 0 | 0.64547 | 0 | 0.61573 | 0.95095 | 0.64749 | 0.61573 | 0.95095 | 0.64749 | 0.64863 | 1.0018 | 0.64749 | 4.745% | 0.002652 | 0.0025207 | 5129.2282 | 0.39825 | 4934.7904 | 194.0395 | 5140.2826 | 0 | 0 | 5140.2826 | 2.129e-05%
2026 | 52 | 52-17F | Tier-1 | Non-HFTD---17 | 1--1 | 1.5992 | 58 | 100% | 2.0098 | 43.61% | 0% | 56.39% | 0.043387 | 0 | 0 | 0.043387 | 0 | 0.041388 | 1.6521 | 0.025051 | 0.041388 | 1.6521 | 0.025051 | 0.0436 | 1.7404 | 0.025051 | 2.159% | 0.004336 | 0.0041214 | 463.5235 | 0.19668 | 225.8901 | 237.4367 | 477.1354 | 0 | 0 | 477.1354 | 1.431e-06%
2026 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 14.1729 | 547 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 491.6709 | 14.6419 | 33.5797 | 491.6709 | 14.6419 | 33.5797 | 517.9415 | 15.4242 | 33.5797 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2026 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 8.4532 | 208 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 152.0596 | 8.733 | 17.4121 | 152.0596 | 8.733 | 17.4121 | 160.1843 | 9.1996 | 17.4121 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2026 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.70208 | 149 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 5.0165 | 0.72532 | 6.9162 | 5.0165 | 0.72532 | 6.9162 | 5.2845 | 0.76407 | 6.9162 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2026 | 44 | 44-42 | Tier-1 | Non-HFTD---15 | 1--2 | 1.3706 | 57 | 100% | 2.2519 | 52.49% | 0% | 47.51% | 0.058511 | 0 | 0 | 0.058511 | 0 | 0.055816 | 1.416 | 0.039419 | 0.055816 | 1.416 | 0.039419 | 0.058798 | 1.4916 | 0.039419 | 2.598% | 0.0039988 | 0.0038009 | 563.136 | 3.0245 | 302.5201 | 257.5915 | 577.0687 | 0 | 0 | 577.0687 | 1.929e-06%
2026 | WY2 | CB WY2 | Tier-1 | Non-HFTD---12 | 3--1 | 6.6059 | 241 | 100% | 9.4104 | 47.5% | 0% | 52.5% | 0.22128 | 0 | 0 | 0.22128 | 0 | 0.21109 | 6.8245 | 0.030931 | 0.21109 | 6.8245 | 0.030931 | 0.22237 | 7.1891 | 0.030931 | 2.351% | 0.019962 | 0.018974 | 471.4249 | 6.182 | 215.7177 | 249.5253 | 484.3131 | 0 | 0 | 484.3131 | 7.297e-06%
2026 | 949 | CB 949 | Tier-1 | Non-HFTD---6 | 4--2 | 14.4241 | 605 | 100% | 45.6408 | 78.87% | 0% | 21.13% | 1.7818 | 0 | 0 | 1.7818 | 0 | 1.6998 | 14.9014 | 0.11407 | 1.6998 | 14.9014 | 0.11407 | 1.7906 | 15.6976 | 0.11407 | 3.904% | 0.046257 | 0.043967 | 986.6878 | 48.1518 | 564.3079 | 374.2281 | 997.5455 | 0 | 0 | 997.5455 | 5.876e-05%
2026 | 256 | 256-539R | Tier-1 | Non-HFTD---12 | 3--2 | 6.8941 | 186 | 100% | 14.3069 | 63.6% | 0% | 36.4% | 0.45041 | 0 | 0 | 0.45041 | 0 | 0.42966 | 7.1222 | 0.060326 | 0.42966 | 7.1222 | 0.060326 | 0.45261 | 7.5028 | 0.060326 | 3.148% | 0.019872 | 0.018888 | 719.955 | 0.45811 | 479.9475 | 239.5495 | 733.603 | 0 | 0 | 733.603 | 1.485e-05%
2026 | 163 | 163-29R | Tier-1 | Non-HFTD---8 | 4--2 | 15.7299 | 388 | 100% | 28.4362 | 60.97% | 0% | 39.03% | 0.85819 | 0 | 0 | 0.85819 | 0 | 0.81866 | 16.2505 | 0.050378 | 0.81866 | 16.2505 | 0.050378 | 0.8624 | 17.1187 | 0.050378 | 3.018% | 0.04406 | 0.041879 | 645.4007 | 34.614 | 206.1861 | 404.6006 | 658.5195 | 0 | 0 | 658.5195 | 2.83e-05%
2026 | 552 | CB 552 | Tier-1 | Non-HFTD---13 | 2--2 | 2.4147 | 53 | 100% | 6.5456 | 63.72% | 0% | 36.28% | 0.20646 | 0 | 0 | 0.20646 | 0 | 0.19695 | 2.4947 | 0.078949 | 0.19695 | 2.4947 | 0.078949 | 0.20748 | 2.628 | 0.078949 | 3.154% | 0.0083556 | 0.007942 | 783.3785 | 51.1813 | 212.1801 | 520.0172 | 798.1788 | 0 | 0 | 798.1788 | 6.808e-06%
2026 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 3.06 | 56 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 99.0448 | 3.1613 | 31.3307 | 99.0448 | 3.1613 | 31.3307 | 104.3369 | 3.3302 | 31.3307 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2026 | 550 | CB 550 | Tier-1 | Non-HFTD---9 | 2--3 | 3.4197 | 103 | 100% | 21.1748 | 85.53% | 0% | 14.47% | 0.89644 | 0 | 0 | 0.89644 | 0 | 0.85514 | 3.5328 | 0.24205 | 0.85514 | 3.5328 | 0.24205 | 0.90083 | 3.7216 | 0.24205 | 4.234% | 0.011507 | 0.010938 | 1840.1317 | 37.2939 | 1370.6401 | 432.1977 | 1854.0024 | 0 | 0 | 1854.0024 | 2.956e-05%
2026 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 3.8089 | 316 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.9791 | 3.9349 | 3.8067 | 14.9791 | 3.9349 | 3.8067 | 15.7795 | 4.1452 | 3.8067 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2026 | 548 | 548-14F | Tier-1 | Non-HFTD---17 | 1--1 | 0.7748 | 32 | 100% | 0.90709 | 48.04% | 0% | 51.96% | 0.02157 | 0 | 0 | 0.02157 | 0 | 0.020576 | 0.80044 | 0.025706 | 0.020576 | 0.80044 | 0.025706 | 0.021676 | 0.8432 | 0.025706 | 2.378% | 0.0019874 | 0.001889 | 456.4228 | 1.7166 | 231.3609 | 223.3454 | 468.7738 | 0 | 0 | 468.7738 | 7.113e-07%
2026 | 793 | 793-27AE | Tier-1 | Non-HFTD---6 | 3--3 | 0.72117 | 87 | 100% | 59.5906 | 9.102% | 90.07% | 0.8316% | 0.26849 | 0 | 0 | 0.26849 | 0 | 0.25612 | 0.74504 | 0.34377 | 0.25612 | 0.74504 | 0.34377 | 0.26981 | 0.78485 | 0.34377 | 0.4506% | 0.019759 | 0.018781 | 3015.8385 | 43.8924 | 2491.6172 | 480.3289 | 3158.6011 | 0 | 0 | 3158.6011 | 8.854e-06%
2026 | 777 | 777-101 | Tier-1 | Non-HFTD---15 | 1--2 | 0.41343 | 18 | 100% | 2.4847 | 82.51% | 0% | 17.49% | 0.10148 | 0 | 0 | 0.10148 | 0 | 0.096809 | 0.42712 | 0.22666 | 0.096809 | 0.42712 | 0.22666 | 0.10198 | 0.44994 | 0.22666 | 4.084% | 0.0015556 | 0.0014786 | 1597.2368 | 209.2569 | 51.6598 | 1336.3201 | 1611.7821 | 0 | 0 | 1611.7821 | 3.347e-06%
2026 | 162 | 162-44R | Tier-1 | Non-HFTD---14 | 3--1 | 5.8971 | 114 | 100% | 6.3779 | 35.8% | 0% | 64.2% | 0.11304 | 0 | 0 | 0.11304 | 0 | 0.10783 | 6.0923 | 0.0177 | 0.10783 | 6.0923 | 0.0177 | 0.11359 | 6.4178 | 0.0177 | 1.772% | 0.016132 | 0.015333 | 395.36 | 1.0985 | 160.8009 | 233.4606 | 408.5776 | 0 | 0 | 408.5776 | 3.728e-06%
2026 | LA3 | CB LA3 | Tier-1 | Non-HFTD---10 | 4--1 | 13.6913 | 366 | 100% | 17.5547 | 51.76% | 0% | 48.24% | 0.44975 | 0 | 0 | 0.44975 | 0 | 0.42904 | 14.1444 | 0.030332 | 0.42904 | 14.1444 | 0.030332 | 0.45196 | 14.9002 | 0.030332 | 2.562% | 0.035693 | 0.033927 | 491.8203 | 13.0666 | 197.3637 | 281.39 | 504.1765 | 0 | 0 | 504.1765 | 1.483e-05%
2026 | BRM1 | CB BRM1 | Tier-1 | Non-HFTD---3 | 4--3 | 7.8361 | 151 | 100% | 119.5681 | 4.577% | 89.64% | 5.783% | 0.27092 | 0 | 0 | 0.27092 | 0 | 0.25844 | 8.0955 | 0.031924 | 0.25844 | 8.0955 | 0.031924 | 0.27225 | 8.528 | 0.031924 | 0.2266% | 0.029242 | 0.027795 | 4088.8876 | 4.6513 | 3568.1907 | 516.0455 | 4292.0808 | 0 | 0 | 4292.0808 | 8.934e-06%
2026 | 1221 | 1221-2095F | Tier-1 | Non-HFTD---9 | 1--4 | 0.44394 | 1 | 100% | 19.6421 | 98.74% | 0% | 1.261% | 0.96002 | 0 | 0 | 0.96002 | 0 | 0.91579 | 0.45863 | 1.9968 | 0.91579 | 0.45863 | 1.9968 | 0.96473 | 0.48313 | 1.9968 | 4.888% | 0.0016714 | 0.0015887 | 11751.8616 | 4301.6259 | 14.6524 | 7435.5833 | 11759.5801 | 0 | 0 | 11759.5801 | 3.166e-05%
2026 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 8.2208 | 258 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 266.4366 | 8.4929 | 31.3718 | 266.4366 | 8.4929 | 31.3718 | 280.6727 | 8.9467 | 31.3718 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2026 | 42 | 42-46 | Tier-1 | Non-HFTD---8 | 4--2 | 17.2654 | 413 | 100% | 44.005 | 69.91% | 0% | 30.09% | 1.5227 | 0 | 0 | 1.5227 | 0 | 1.4526 | 17.8367 | 0.081437 | 1.4526 | 17.8367 | 0.081437 | 1.5302 | 18.7898 | 0.081437 | 3.46% | 0.051941 | 0.04937 | 847.2081 | 19.5159 | 531.7286 | 295.9636 | 860.4861 | 0 | 0 | 860.4861 | 5.021e-05%
2026 | 1007 | CB 1007 | Tier-1 | Non-HFTD---4 | 1--5 | 0.54489 | 21 | 100% | 183.252 | 99.8% | 0% | 0.2013% | 9.0527 | 0 | 0 | 9.0527 | 0 | 8.6357 | 0.56292 | 15.3409 | 8.6357 | 0.56292 | 15.3409 | 9.0971 | 0.593 | 15.3409 | 4.94% | 0.0023706 | 0.0022533 | 77301.9362 | 12237.1432 | 2369.9057 | 62694.8873 | 77310.0415 | 0 | 0 | 77310.0415 | 0.0002985%
2026 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 5.5421 | 271 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 54.8903 | 5.7255 | 9.587 | 54.8903 | 5.7255 | 9.587 | 57.8231 | 6.0314 | 9.587 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2026 | 799 | CB 799 | Tier-2 | Tier-2---15 | 1--5 | 1.1328 | 62 | 100% | 176.6165 | 99.47% | 0% | 0.5321% | 8.696 | 0 | 0 | 8.696 | 0 | 8.2954 | 1.1703 | 7.0886 | 8.2954 | 1.1703 | 7.0886 | 8.7386 | 1.2328 | 7.0886 | 4.924% | 0.0045468 | 0.0043217 | 38844.142 | 6076.6634 | 1382.7609 | 31384.7178 | 38854.9056 | 0 | 0 | 38854.9056 | 0.0002868%
2026 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 3.321 | 126 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 55.2642 | 3.4309 | 16.1077 | 55.2642 | 3.4309 | 16.1077 | 58.217 | 3.6142 | 16.1077 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2026 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 1.4237 | 112 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.5521 | 1.4708 | 5.1346 | 7.5521 | 1.4708 | 5.1346 | 7.9556 | 1.5494 | 5.1346 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2026 | 143 | 143-178F | Tier-1 | Non-HFTD---13 | 2--2 | 0.099242 | 3 | 100% | 7.6566 | 35.29% | 63.85% | 0.8587% | 0.13374 | 0 | 0 | 0.13374 | 0 | 0.12758 | 0.10253 | 1.2444 | 0.12758 | 0.10253 | 1.2444 | 0.1344 | 0.108 | 1.2444 | 1.747% | 0.0064626 | 0.0061427 | 1184.7481 | 68.836 | 601.4916 | 514.4204 | 1224.6747 | 0 | 0 | 1224.6747 | 4.41e-06%
2026 | 167 | 167-32F | Tier-1 | Non-HFTD---17 | 1--2 | 0.70002 | 13 | 100% | 1.7157 | 69.63% | 0% | 30.37% | 0.059132 | 0 | 0 | 0.059132 | 0 | 0.056408 | 0.72319 | 0.078 | 0.056408 | 0.72319 | 0.078 | 0.059422 | 0.76183 | 0.078 | 3.447% | 0.002212 | 0.0021025 | 775.6143 | 118.1037 | 56.1784 | 601.3322 | 787.882 | 0 | 0 | 787.882 | 1.95e-06%
2026 | 558 | CB 558 | Tier-1 | Non-HFTD---5 | 1--4 | 1.6337 | 37 | 100% | 60.2724 | 98.84% | 0% | 1.159% | 2.9489 | 0 | 0 | 2.9489 | 0 | 2.8131 | 1.6878 | 1.6667 | 2.8131 | 1.6878 | 1.6667 | 2.9634 | 1.778 | 1.6667 | 4.893% | 0.0040546 | 0.0038539 | 14865.197 | 2133.2107 | 1638.7721 | 11093.2142 | 14874.1658 | 0 | 0 | 14874.1658 | 9.724e-05%
2026 | 796 | 796-45 | Tier-1 | Non-HFTD---7 | 2--4 | 1.3418 | 200 | 100% | 28.511 | 97.42% | 0% | 2.579% | 1.3749 | 0 | 0 | 1.3749 | 0 | 1.3116 | 1.3863 | 0.94612 | 1.3116 | 1.3863 | 0.94612 | 1.3816 | 1.4603 | 0.94612 | 4.822% | 0.0051166 | 0.0048633 | 5572.2547 | 765.3252 | 756.2439 | 4050.6857 | 5579.7376 | 0 | 0 | 5579.7376 | 4.534e-05%
2026 | 152 | 152-1716F | Tier-1 | Non-HFTD---15 | 1--2 | 1.3556 | 9 | 100% | 4.2989 | 81.88% | 0% | 18.12% | 0.17424 | 0 | 0 | 0.17424 | 0 | 0.16621 | 1.4005 | 0.11868 | 0.16621 | 1.4005 | 0.11868 | 0.17509 | 1.4753 | 0.11868 | 4.053% | 0.0035886 | 0.003411 | 1197.9379 | 232.1636 | 50.7211 | 915.0532 | 1209.2431 | 0 | 0 | 1209.2431 | 5.746e-06%
2026 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 1.6392 | 98 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.8455 | 1.6934 | 2.8614 | 4.8455 | 1.6934 | 2.8614 | 5.1044 | 1.7839 | 2.8614 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2026 | 57 | 57-463AE | Tier-1 | Non-HFTD---6 | 3--3 | 5.4167 | 145 | 100% | 80.983 | 3.172% | 91.7% | 5.126% | 0.12717 | 0 | 0 | 0.12717 | 0 | 0.12132 | 5.596 | 0.021679 | 0.12132 | 5.596 | 0.021679 | 0.1278 | 5.895 | 0.021679 | 0.157% | 0.026238 | 0.024939 | 3086.4535 | 4.1795 | 2701.0745 | 381.1994 | 3242.09 | 0 | 0 | 3242.09 | 4.194e-06%
2026 | 325 | 325-1229F | Tier-1 | Non-HFTD---11 | 1--3 | 1.4292 | 43 | 100% | 10.0499 | 91.61% | 0% | 8.391% | 0.45572 | 0 | 0 | 0.45572 | 0 | 0.43473 | 1.4765 | 0.29444 | 0.43473 | 1.4765 | 0.29444 | 0.45796 | 1.5554 | 0.29444 | 4.535% | 0.0038216 | 0.0036324 | 2629.7498 | 120.9525 | 1901.9845 | 606.8128 | 2641.2417 | 0 | 0 | 2641.2417 | 1.503e-05%
2026 | 71 | CB 71 | Tier-1 | Non-HFTD---14 | 2--2 | 4.0099 | 46 | 100% | 7.9324 | 61.9% | 0% | 38.1% | 0.24303 | 0 | 0 | 0.24303 | 0 | 0.23184 | 4.1426 | 0.055964 | 0.23184 | 4.1426 | 0.055964 | 0.24423 | 4.3639 | 0.055964 | 3.064% | 0.012179 | 0.011576 | 651.3036 | 39.9085 | 181.853 | 429.5421 | 664.2281 | 0 | 0 | 664.2281 | 8.014e-06%
2026 | 450 | 450-114F | Tier-1 | Non-HFTD---7 | 1--4 | 0.63728 | 9 | 100% | 28.615 | 98.32% | 0% | 1.684% | 1.3926 | 0 | 0 | 1.3926 | 0 | 1.3284 | 0.65837 | 2.0177 | 1.3284 | 0.65837 | 2.0177 | 1.3994 | 0.69355 | 2.0177 | 4.867% | 0.0023436 | 0.0022276 | 12209.8338 | 1908.2658 | 365.7567 | 9935.8114 | 12220.543 | 0 | 0 | 12220.543 | 4.592e-05%
2026 | 967 | CB 967 | Tier-1 | Non-HFTD---15 | 1--2 | 0.4197 | 13 | 100% | 2.3533 | 86.82% | 0% | 13.18% | 0.10114 | 0 | 0 | 0.10114 | 0 | 0.096476 | 0.43359 | 0.22251 | 0.096476 | 0.43359 | 0.22251 | 0.10163 | 0.45675 | 0.22251 | 4.298% | 0.0017284 | 0.0016428 | 1361.5561 | 162.4621 | 165.1256 | 1033.9684 | 1370.9019 | 0 | 0 | 1370.9019 | 3.335e-06%
2026 | 570 | 570-490F | Tier-1 | Non-HFTD---9 | 2--2 | 0.62502 | 97 | 100% | 15.9869 | 5.745% | 91.56% | 2.699% | 0.045463 | 0 | 0 | 0.045463 | 0 | 0.043369 | 0.6457 | 0.067165 | 0.043369 | 0.6457 | 0.067165 | 0.045686 | 0.6802 | 0.067165 | 0.2844% | 0.009473 | 0.0090041 | 1687.6286 | 16.8664 | 1423.6306 | 247.1317 | 1770.4675 | 0 | 0 | 1770.4675 | 1.499e-06%
2026 | 177 | 177-941AE | Tier-1 | Non-HFTD---1 | 3--5 | 7.2284 | 562 | 100% | 569.5091 | 99.21% | 0% | 0.7896% | 27.9681 | 0 | 0 | 27.9681 | 0 | 26.6797 | 7.4677 | 3.5727 | 26.6797 | 7.4677 | 3.5727 | 28.1052 | 7.8667 | 3.5727 | 4.911% | 0.025296 | 0.024043 | 22514.1579 | 5020.4853 | 161.6801 | 17331.9925 | 22523.4155 | 0 | 0 | 22523.4155 | 0.0009223%
2026 | 745 | CB 745 | Tier-1 | Non-HFTD---11 | 1--3 | 0.81894 | 98 | 100% | 9.4012 | 94.7% | 0% | 5.302% | 0.44069 | 0 | 0 | 0.44069 | 0 | 0.42038 | 0.84604 | 0.49688 | 0.42038 | 0.84604 | 0.49688 | 0.44285 | 0.89125 | 0.49688 | 4.688% | 0.003239 | 0.0030787 | 2902.4859 | 435.0401 | 59.2072 | 2408.2386 | 2910.4997 | 0 | 0 | 2910.4997 | 1.453e-05%
2026 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 7.8576 | 547 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 75.7792 | 8.1176 | 9.3352 | 75.7792 | 8.1176 | 9.3352 | 79.8282 | 8.5513 | 9.3352 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2026 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 15.6835 | 1007 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1054.721 | 16.2026 | 65.0959 | 1054.721 | 16.2026 | 65.0959 | 1111.0762 | 17.0683 | 65.0959 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2026 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.057008 | 0 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.8232 | 0.058894 | 64.916 | 3.8232 | 0.058894 | 64.916 | 4.0275 | 0.062041 | 64.916 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2026 | 927 | CB 927 | Tier-1 | Non-HFTD---4 | 1--5 | 0.68868 | 51 | 100% | 165.3992 | 99.66% | 0% | 0.3413% | 8.1593 | 0 | 0 | 8.1593 | 0 | 7.7834 | 0.71147 | 10.9399 | 7.7834 | 0.71147 | 10.9399 | 8.1993 | 0.74949 | 10.9399 | 4.933% | 0.0030976 | 0.0029443 | 53395.9292 | 14102.6228 | 23.0019 | 39270.3045 | 53405.4192 | 0 | 0 | 53405.4192 | 0.0002691%
2026 | 560 | CB 560 | Tier-1 | Non-HFTD---13 | 1--4 | 0.31572 | 0 | 100% | 8.2251 | 96.67% | 0% | 3.328% | 0.39359 | 0 | 0 | 0.39359 | 0 | 0.37546 | 0.32616 | 1.1511 | 0.37546 | 0.32616 | 1.1511 | 0.39552 | 0.34359 | 1.1511 | 4.785% | 0.0011202 | 0.0010648 | 7342.5228 | 1158.0205 | 22.9992 | 6161.5031 | 7355.2484 | 0 | 0 | 7355.2484 | 1.298e-05%
2026 | 282 | 282-563F | Tier-1 | Non-HFTD---8 | 4--2 | 0.30794 | 17 | 100% | 27.9436 | 22.74% | 76.55% | 0.7188% | 0.31447 | 0 | 0 | 0.31447 | 0 | 0.29999 | 0.31813 | 0.94295 | 0.29999 | 0.31813 | 0.94295 | 0.31602 | 0.33513 | 0.94295 | 1.125% | 0.031532 | 0.029971 | 886.1932 | 32.7578 | 542.1953 | 311.2401 | 921.8518 | 0 | 0 | 921.8518 | 1.037e-05%
2026 | 519 | 519-46R | Tier-1 | Non-HFTD---14 | 3--2 | 4.9682 | 201 | 100% | 7.5925 | 54.37% | 0% | 45.63% | 0.20433 | 0 | 0 | 0.20433 | 0 | 0.19491 | 5.1326 | 0.037975 | 0.19491 | 5.1326 | 0.037975 | 0.20533 | 5.4069 | 0.037975 | 2.691% | 0.013855 | 0.013169 | 548.0015 | 0.18817 | 320.6507 | 227.1626 | 561.0244 | 0 | 0 | 561.0244 | 6.738e-06%
2026 | 1479 | CB 1479 | Tier-1 | Non-HFTD---14 | 3--1 | 5.0797 | 177 | 100% | 5.3828 | 21.29% | 0% | 78.71% | 0.056714 | 0 | 0 | 0.056714 | 0 | 0.054101 | 5.2478 | 0.010309 | 0.054101 | 5.2478 | 0.010309 | 0.056992 | 5.5282 | 0.010309 | 1.054% | 0.016809 | 0.015977 | 320.2293 | 0.28102 | 90.4979 | 229.4503 | 333.3564 | 0 | 0 | 333.3564 | 1.87e-06%
2026 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.027841 | 0 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.28535 | 0.028762 | 9.9209 | 0.28535 | 0.028762 | 9.9209 | 0.30059 | 0.030299 | 9.9209 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2026 | 93 | 93-559R | Tier-1 | Non-HFTD---2 | 3--4 | 6.9136 | 643 | 100% | 194.9296 | 89.74% | 7.915% | 2.344% | 8.6591 | 0 | 0 | 8.6591 | 0 | 8.2602 | 7.1424 | 1.1565 | 8.2602 | 7.1424 | 1.1565 | 8.7015 | 7.5241 | 1.1565 | 4.442% | 0.02667 | 0.02535 | 7308.8898 | 1504.7135 | 606.7669 | 5197.4095 | 7347.9399 | 0 | 0 | 7347.9399 | 0.0002855%
2026 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 13.7926 | 900 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 93.8928 | 14.249 | 6.5894 | 93.8928 | 14.249 | 6.5894 | 98.9097 | 15.0104 | 6.5894 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2026 | 307 | CB 307 | Tier-1 | Non-HFTD---1 | 4--4 | 1.1522 | 360 | 100% | 601.8674 | 89.73% | 10.15% | 0.1197% | 26.7338 | 0 | 0 | 26.7338 | 0 | 25.5023 | 1.1904 | 21.4238 | 25.5023 | 1.1904 | 21.4238 | 26.8649 | 1.254 | 21.4238 | 4.442% | 0.056404 | 0.053612 | 10670.688 | 1554.5631 | 980.4133 | 8135.7116 | 10727.7391 | 0 | 0 | 10727.7391 | 0.0008816%
2026 | 185 | 185-40AE | Tier-1 | Non-HFTD---9 | 3--2 | 0.21023 | 6 | 100% | 24.1775 | 44.9% | 54.65% | 0.4525% | 0.53732 | 0 | 0 | 0.53732 | 0 | 0.51257 | 0.21718 | 2.3601 | 0.51257 | 0.21718 | 2.3601 | 0.53996 | 0.22879 | 2.3601 | 2.222% | 0.014972 | 0.014231 | 1614.8054 | 161.7474 | 706.6761 | 746.3819 | 1661.1444 | 0 | 0 | 1661.1444 | 1.772e-05%
2026 | 1297 | CB 1297 | Tier-1 | Non-HFTD---13 | 2--2 | 0.36516 | 2 | 100% | 8.4009 | 39.85% | 56.35% | 3.796% | 0.16572 | 0 | 0 | 0.16572 | 0 | 0.15809 | 0.37725 | 0.41906 | 0.15809 | 0.37725 | 0.41906 | 0.16654 | 0.3974 | 0.41906 | 1.973% | 0.0061708 | 0.0058653 | 1361.4021 | 0.82568 | 1230.5774 | 129.999 | 1404.0463 | 0 | 0 | 1404.0463 | 5.465e-06%
2026 | 719 | 719-20AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.2593 | 0 | 100% | 0.25643 | 2.302% | 0% | 97.7% | 0.00029221 | 0 | 0 | 0.00029221 | 0 | 0.00027875 | 0.26789 | 0.0010406 | 0.00027875 | 0.26789 | 0.0010406 | 0.00029364 | 0.2822 | 0.0010406 | 0.114% | 0.0008862 | 0.00084233 | 289.3554 | 0.21272 | 32.3414 | 256.8012 | 304.0775 | 0 | 0 | 304.0775 | 9.636e-09%
2026 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.010606 | 0 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.010957 | 0 | 0 | 0.010957 | 0 | 0 | 0.011543 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2026 | 313 | 313-921F | Tier-1 | Non-HFTD---10 | 3--2 | 0.32122 | 1 | 100% | 17.8162 | 19.43% | 79.61% | 0.9597% | 0.17138 | 0 | 0 | 0.17138 | 0 | 0.16349 | 0.33185 | 0.49266 | 0.16349 | 0.33185 | 0.49266 | 0.17222 | 0.34958 | 0.49266 | 0.962% | 0.018006 | 0.017115 | 989.4465 | 32.4943 | 625.1022 | 331.85 | 1030.9611 | 0 | 0 | 1030.9611 | 5.652e-06%
2026 | 299 | 299-1010AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.44586 | 28 | 100% | 0.3009 | 15.95% | 0% | 84.05% | 0.0023758 | 0 | 0 | 0.0023758 | 0 | 0.0022664 | 0.46062 | 0.0049203 | 0.0022664 | 0.46062 | 0.0049203 | 0.0023875 | 0.48523 | 0.0049203 | 0.7896% | 0.001182 | 0.0011235 | 254.5679 | 0.31338 | 59.1142 | 195.1403 | 265.7105 | 0 | 0 | 265.7105 | 7.835e-08%
2026 | 313 | 313-550AE | Tier-1 | Non-HFTD---6 | 3--3 | 1.3333 | 153 | 100% | 63.0293 | 35.2% | 63.19% | 1.611% | 1.0982 | 0 | 0 | 1.0982 | 0 | 1.0476 | 1.3774 | 0.76056 | 1.0476 | 1.3774 | 0.76056 | 1.1036 | 1.451 | 0.76056 | 1.742% | 0.021034 | 0.019993 | 2996.5143 | 172.626 | 1569.8934 | 1253.9949 | 3097.636 | 0 | 0 | 3097.636 | 3.622e-05%
2026 | 546 | 546-525R | Tier-1 | Non-HFTD---6 | 3--3 | 3.3962 | 95 | 100% | 53.674 | 7.451% | 89.14% | 3.414% | 0.19796 | 0 | 0 | 0.19796 | 0 | 0.18884 | 3.5086 | 0.053821 | 0.18884 | 3.5086 | 0.053821 | 0.19893 | 3.6961 | 0.053821 | 0.3688% | 0.018842 | 0.01791 | 2848.5751 | 3.4959 | 2541.3825 | 303.6966 | 2985.8697 | 0 | 0 | 2985.8697 | 6.528e-06%
2026 | 152 | 152-513AE | Tier-1 | Non-HFTD---12 | 3--2 | 7.8357 | 74 | 100% | 12.0345 | 69.29% | 0% | 30.71% | 0.41277 | 0 | 0 | 0.41277 | 0 | 0.39376 | 8.095 | 0.048642 | 0.39376 | 8.095 | 0.048642 | 0.41479 | 8.5275 | 0.048642 | 3.43% | 0.019541 | 0.018574 | 615.8514 | 13.6547 | 361.2301 | 240.9665 | 625.7005 | 0 | 0 | 625.7005 | 1.361e-05%
2026 | 66 | CB 66 | Tier-1 | Non-HFTD---1 | 4--5 | 7.6461 | 1197 | 100% | 917.8674 | 93.46% | 5.958% | 0.5799% | 42.4641 | 0 | 0 | 42.4641 | 0 | 40.5079 | 7.8991 | 5.1282 | 40.5079 | 7.8991 | 5.1282 | 42.6723 | 8.3212 | 5.1282 | 4.626% | 0.036366 | 0.034566 | 25239.7123 | 4508.1978 | 1664.2037 | 19067.3107 | 25325.6439 | 0 | 0 | 25325.6439 | 0.0014%
2026 | 748 | CB 748 | Tier-1 | Non-HFTD---9 | 2--3 | 2.139 | 70 | 100% | 22.3424 | 93.96% | 0% | 6.041% | 1.0391 | 0 | 0 | 1.0391 | 0 | 0.99127 | 2.2098 | 0.44857 | 0.99127 | 2.2098 | 0.44857 | 1.0442 | 2.3279 | 0.44857 | 4.651% | 0.0077366 | 0.0073536 | 2887.8899 | 430.152 | 52.4027 | 2405.3352 | 2896.9749 | 0 | 0 | 2896.9749 | 3.427e-05%
2026 | 591 | 591-39AE | Tier-1 | Non-HFTD---1 | 4--4 | 8.7941 | 609 | 100% | 863.6817 | 30.54% | 68.77% | 0.684% | 13.0582 | 0 | 0 | 13.0582 | 0 | 12.4567 | 9.0851 | 1.3711 | 12.4567 | 9.0851 | 1.3711 | 13.1223 | 9.5706 | 1.3711 | 1.512% | 0.061092 | 0.058068 | 14137.3023 | 873.1637 | 8965.9062 | 4298.2324 | 14648.6655 | 0 | 0 | 14648.6655 | 0.0004306%
2026 | 130 | 130-692R | Tier-1 | Non-HFTD---8 | 4--2 | 9.1392 | 120 | 100% | 38.8551 | 79.61% | 0% | 20.39% | 1.5312 | 0 | 0 | 1.5312 | 0 | 1.4607 | 9.4417 | 0.15471 | 1.4607 | 9.4417 | 0.15471 | 1.5387 | 9.9461 | 0.15471 | 3.941% | 0.029616 | 0.02815 | 1311.9621 | 5.802 | 1040.3906 | 265.7695 | 1325.8909 | 0 | 0 | 1325.8909 | 5.049e-05%
2026 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 18.3176 | 1062 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 497.9891 | 18.9238 | 26.3155 | 497.9891 | 18.9238 | 26.3155 | 524.5974 | 19.9349 | 26.3155 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2026 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 12.4913 | 405 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 78.3562 | 12.9047 | 6.0719 | 78.3562 | 12.9047 | 6.0719 | 82.5429 | 13.5942 | 6.0719 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2026 | 75 | CB 75 | Tier-3 | Tier-3---21 | 1--4 | 0.14545 | 0 | 100% | 4.1734 | 97.63% | 0% | 2.371% | 0.20169 | 0 | 0 | 0.20169 | 0 | 0.1924 | 0.15027 | 1.2803 | 0.1924 | 0.15027 | 1.2803 | 0.20268 | 0.1583 | 1.2803 | 4.833% | 0.0006394 | 0.00060775 | 6527.0943 | 953.8716 | 494.2061 | 5079.0166 | 6535.1527 | 0 | 0 | 6535.1527 | 6.651e-06%
2026 | 496 | CB 496 | Tier-1 | Non-HFTD---20 | 1--1 | 0.23769 | 14 | 100% | 0.1626 | 10.49% | 0% | 89.51% | 0.00084466 | 0 | 0 | 0.00084466 | 0 | 0.00080575 | 0.24555 | 0.0032814 | 0.00080575 | 0.24555 | 0.0032814 | 0.0008488 | 0.25867 | 0.0032814 | 0.5195% | 0.0006016 | 0.00057182 | 270.2755 | 0.18203 | 50.3395 | 219.754 | 282.8737 | 0 | 0 | 282.8737 | 2.785e-08%
2026 | 505 | 505-635R | Tier-1 | Non-HFTD---2 | 4--4 | 22.8048 | 2172 | 100% | 591.8183 | 97.36% | 0% | 2.639% | 28.5218 | 0 | 0 | 28.5218 | 0 | 27.2079 | 23.5594 | 1.1549 | 27.2079 | 23.5594 | 1.1549 | 28.6616 | 24.8183 | 1.1549 | 4.819% | 0.06847 | 0.06508 | 8643.5194 | 1351.8242 | 175.5172 | 7116.178 | 8655.4003 | 0 | 0 | 8655.4003 | 0.0009405%
2026 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 0.49168 | 174 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 2.0022 | 0.50795 | 3.9418 | 2.0022 | 0.50795 | 3.9418 | 2.1092 | 0.53509 | 3.9418 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2026 | RD4 | RD4-49F | Tier-1 | Non-HFTD---16 | 2--1 | 3.5175 | 271 | 100% | 3.6354 | 25.76% | 0% | 74.24% | 0.046356 | 0 | 0 | 0.046356 | 0 | 0.044221 | 3.6339 | 0.012169 | 0.044221 | 3.6339 | 0.012169 | 0.046584 | 3.828 | 0.012169 | 1.275% | 0.010063 | 0.0095647 | 361.2667 | 2.1724 | 105.3352 | 253.7591 | 375.2341 | 0 | 0 | 375.2341 | 1.529e-06%
2026 | 185 | 185-52F | Tier-1 | Non-HFTD---18 | 3--1 | 0.068182 | 8 | 100% | 1.9986 | 0.2921% | 96.1% | 3.61% | 0.00028895 | 0 | 0 | 0.00028895 | 0 | 0.00027564 | 0.070438 | 0.0039132 | 0.00027564 | 0.070438 | 0.0039132 | 0.00029036 | 0.074202 | 0.0039132 | 0.01446% | 0.014577 | 0.013855 | 137.1083 | 0.56754 | 106.8603 | 29.6805 | 144.2278 | 0 | 0 | 144.2278 | 9.528e-09%
2026 | 77 | CB 77 | Tier-1 | Non-HFTD---3 | 4--3 | 15.8875 | 767 | 100% | 119.7495 | 90.14% | 0% | 9.861% | 5.3431 | 0 | 0 | 5.3431 | 0 | 5.0969 | 16.4133 | 0.31054 | 5.0969 | 16.4133 | 0.31054 | 5.3693 | 17.2902 | 0.31054 | 4.462% | 0.052353 | 0.049762 | 2287.3297 | 348.85 | 338.2815 | 1600.1982 | 2299.0765 | 0 | 0 | 2299.0765 | 0.0001762%
2026 | 719 | 719-21AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.2376 | 46 | 100% | 2.7569 | 40.49% | 0% | 59.51% | 0.055252 | 0 | 0 | 0.055252 | 0 | 0.052706 | 2.3117 | 0.0228 | 0.052706 | 2.3117 | 0.0228 | 0.055522 | 2.4352 | 0.0228 | 2.004% | 0.006419 | 0.0061013 | 429.4974 | 0.19234 | 197.1085 | 232.1966 | 442.809 | 0 | 0 | 442.809 | 1.822e-06%
2026 | 512 | 512-50AE | Tier-1 | Non-HFTD---5 | 3--3 | 2.2912 | 159 | 100% | 71.8244 | 0.7571% | 97.4% | 1.847% | 0.026916 | 0 | 0 | 0.026916 | 0 | 0.025676 | 2.3671 | 0.010847 | 0.025676 | 2.3671 | 0.010847 | 0.027048 | 2.4935 | 0.010847 | 0.03748% | 0.016424 | 0.015611 | 4373.1911 | 5.2566 | 3808.805 | 559.1295 | 4599.2133 | 0 | 0 | 4599.2133 | 8.876e-07%
2026 | 144 | 144-29 | Tier-1 | Non-HFTD---11 | 2--3 | 0.17619 | 16 | 100% | 11.682 | 0.1742% | 98.33% | 1.496% | 0.0010071 | 0 | 0 | 0.0010071 | 0 | 0.00096072 | 0.18202 | 0.0052782 | 0.00096072 | 0.18202 | 0.0052782 | 0.001012 | 0.19174 | 0.0052782 | 0.008621% | 0.0067282 | 0.0063952 | 1736.2798 | 2.3848 | 1561.9921 | 171.903 | 1826.5441 | 0 | 0 | 1826.5441 | 3.321e-08%
2026 | 81 | CB 81 | Tier-1 | Non-HFTD---10 | 3--2 | 6.9752 | 310 | 100% | 21.9247 | 77.75% | 0% | 22.25% | 0.84377 | 0 | 0 | 0.84377 | 0 | 0.8049 | 7.206 | 0.1117 | 0.8049 | 7.206 | 0.1117 | 0.8479 | 7.591 | 0.1117 | 3.848% | 0.01895 | 0.018012 | 1156.9885 | 0.24003 | 922.628 | 234.1205 | 1170.3967 | 0 | 0 | 1170.3967 | 2.782e-05%
2026 | CCB1 | CB CCB1 | Tier-1 | Non-HFTD---17 | 1--3 | 0.10833 | 0 | 100% | 2.0968 | 95.25% | 0% | 4.748% | 0.098863 | 0 | 0 | 0.098863 | 0 | 0.094309 | 0.11192 | 0.84266 | 0.094309 | 0.11192 | 0.84266 | 0.099348 | 0.1179 | 0.84266 | 4.715% | 0.0004866 | 0.00046251 | 4309.0626 | 662.563 | 60.6472 | 3585.8524 | 4319.7167 | 0 | 0 | 4319.7167 | 3.26e-06%
2026 | 714 | 714-549F | Tier-1 | Non-HFTD---5 | 2--4 | 1.7489 | 77 | 100% | 53.2751 | 98.07% | 0% | 1.933% | 2.5861 | 0 | 0 | 2.5861 | 0 | 2.467 | 1.8068 | 1.3654 | 2.467 | 1.8068 | 1.3654 | 2.5988 | 1.9033 | 1.3654 | 4.854% | 0.0067848 | 0.006449 | 7852.121 | 1591.0401 | 27.5154 | 6233.5655 | 7860.0249 | 0 | 0 | 7860.0249 | 8.528e-05%
2026 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 4.1122 | 459 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 389.022 | 4.2482 | 91.5725 | 389.022 | 4.2482 | 91.5725 | 409.808 | 4.4752 | 91.5725 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2026 | 492 | 492-343R | Tier-1 | Non-HFTD---1 | 3--4 | 3.0856 | 96 | 100% | 272.4272 | 37.19% | 62.03% | 0.7764% | 5.0152 | 0 | 0 | 5.0152 | 0 | 4.7842 | 3.1877 | 1.5008 | 4.7842 | 3.1877 | 1.5008 | 5.0398 | 3.3581 | 1.5008 | 1.841% | 0.024839 | 0.02361 | 10967.6322 | 612.0765 | 6977.3835 | 3378.1722 | 11326.3811 | 0 | 0 | 11326.3811 | 0.0001654%
2026 | 1173 | 1173-69 | Tier-1 | Non-HFTD---20 | 1--1 | 0.44187 | 41 | 100% | 0.23868 | 12.02% | 0% | 87.98% | 0.0014207 | 0 | 0 | 0.0014207 | 0 | 0.0013552 | 0.45649 | 0.0029688 | 0.0013552 | 0.45649 | 0.0029688 | 0.0014277 | 0.48089 | 0.0029688 | 0.5952% | 0.000946 | 0.00089917 | 252.3094 | 0.16703 | 50.503 | 201.6393 | 263.8692 | 0 | 0 | 263.8692 | 4.685e-08%
2026 | LR1 | CB LR1 | Tier-1 | Non-HFTD---3 | 4--3 | 12.453 | 567 | 100% | 104.9912 | 92.12% | 0% | 7.878% | 4.7876 | 0 | 0 | 4.7876 | 0 | 4.5671 | 12.8652 | 0.35499 | 4.5671 | 12.8652 | 0.35499 | 4.8111 | 13.5526 | 0.35499 | 4.56% | 0.036685 | 0.034869 | 2861.9797 | 416.4048 | 112.8622 | 2332.7126 | 2873.7222 | 0 | 0 | 2873.7222 | 0.0001579%
2026 | 790 | CB 790 | Tier-2 | Tier-2---10 | 4--4 | 1.346 | 112 | 100% | 864.253 | 62.67% | 37.21% | 0.1185% | 26.812 | 0 | 0 | 26.812 | 0 | 25.5768 | 1.3906 | 18.3932 | 25.5768 | 1.3906 | 18.3932 | 26.9434 | 1.4649 | 18.3932 | 3.102% | 0.092624 | 0.088039 | 9330.8076 | 1033.7577 | 3102.9179 | 5194.132 | 9512.1882 | 0 | 0 | 9512.1882 | 0.0008842%
2026 | 1049 | 1049-3F | Tier-1 | Non-HFTD---12 | 3--1 | 7.1382 | 182 | 100% | 8.8963 | 41.1% | 0% | 58.9% | 0.18101 | 0 | 0 | 0.18101 | 0 | 0.17267 | 7.3745 | 0.023414 | 0.17267 | 7.3745 | 0.023414 | 0.18189 | 7.7685 | 0.023414 | 2.035% | 0.019998 | 0.019008 | 444.8634 | 18.6046 | 93.9565 | 332.3023 | 458.5083 | 0 | 0 | 458.5083 | 5.969e-06%
2026 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.2301 | 18 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 15.2415 | 0.23771 | 64.117 | 15.2415 | 0.23771 | 64.117 | 16.0558 | 0.25041 | 64.117 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2026 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 12.4352 | 2333 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 337.9327 | 12.8467 | 26.3049 | 337.9327 | 12.8467 | 26.3049 | 355.9889 | 13.5332 | 26.3049 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2026 | 966 | CB 966 | Tier-1 | Non-HFTD---17 | 1--2 | 0.25966 | 0 | 100% | 1.248 | 85.91% | 0% | 14.09% | 0.053072 | 0 | 0 | 0.053072 | 0 | 0.050627 | 0.26825 | 0.18873 | 0.050627 | 0.26825 | 0.18873 | 0.053332 | 0.28259 | 0.18873 | 4.253% | 0.001115 | 0.0010598 | 1119.2714 | 148.4379 | 21.0289 | 949.8046 | 1127.4836 | 0 | 0 | 1127.4836 | 1.75e-06%
2026 | MAG1 | CB MAG1 | Tier-1 | Non-HFTD---8 | 5--1 | 0.88881 | 25 | 100% | 27.4341 | 1.826% | 95.93% | 2.248% | 0.024802 | 0 | 0 | 0.024802 | 0 | 0.023659 | 0.91822 | 0.025766 | 0.023659 | 0.91822 | 0.025766 | 0.024923 | 0.96728 | 0.025766 | 0.09041% | 0.095165 | 0.090455 | 288.2778 | 1.1724 | 249.3442 | 37.7612 | 303.0165 | 0 | 0 | 303.0165 | 8.179e-07%
2026 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 10.1766 | 1359 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 732.0261 | 10.5133 | 69.6283 | 732.0261 | 10.5133 | 69.6283 | 771.1393 | 11.0751 | 69.6283 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2026 | 490 | 490-23 | Tier-1 | Non-HFTD---15 | 1--4 | 0.21625 | 28 | 100% | 4.2948 | 96.52% | 0% | 3.476% | 0.2052 | 0 | 0 | 0.2052 | 0 | 0.19575 | 0.2234 | 0.8762 | 0.19575 | 0.2234 | 0.8762 | 0.20621 | 0.23534 | 0.8762 | 4.778% | 0.0007132 | 0.0006779 | 6021.8257 | 949.5603 | 22.0761 | 5050.1893 | 6032.728 | 0 | 0 | 6032.728 | 6.767e-06%
2026 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.01875 | 0 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.7021 | 0.01937 | 36.2458 | 0.7021 | 0.01937 | 36.2458 | 0.73961 | 0.020405 | 36.2458 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2026 | HC3 | CB HC3 | Tier-1 | Non-HFTD---10 | 4--2 | 12.0409 | 546 | 100% | 24.3902 | 66.04% | 0% | 33.96% | 0.79725 | 0 | 0 | 0.79725 | 0 | 0.76053 | 12.4394 | 0.061139 | 0.76053 | 12.4394 | 0.061139 | 0.80116 | 13.104 | 0.061139 | 3.269% | 0.035828 | 0.034054 | 680.7657 | 68.4975 | 157.3177 | 454.9505 | 692.8072 | 0 | 0 | 692.8072 | 2.629e-05%
2026 | 362 | 362-47F | Tier-1 | Non-HFTD---3 | 4--3 | 14.5108 | 539 | 100% | 174.2726 | 36.5% | 57.41% | 6.096% | 3.1484 | 0 | 0 | 3.1484 | 0 | 3.0034 | 14.991 | 0.20034 | 3.0034 | 14.991 | 0.20034 | 3.1638 | 15.792 | 0.20034 | 1.807% | 0.049116 | 0.046685 | 3548.1987 | 294.627 | 1994.8222 | 1258.7495 | 3665.5412 | 0 | 0 | 3665.5412 | 0.0001038%
2026 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 0.3653 | 59 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.57934 | 0.37739 | 1.5351 | 0.57934 | 0.37739 | 1.5351 | 0.61029 | 0.39755 | 1.5351 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2026 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.026705 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.4032 | 0.027588 | 50.8637 | 1.4032 | 0.027588 | 50.8637 | 1.4782 | 0.029062 | 50.8637 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2026 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.10398 | 4 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.9848 | 0.10742 | 111.5711 | 11.9848 | 0.10742 | 111.5711 | 12.6251 | 0.11316 | 111.5711 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2026 | 282 | CB 282 | Tier-2 | Tier-2---15 | 4--3 | 1.0646 | 34 | 100% | 152.5069 | 4.749% | 94.48% | 0.7672% | 0.3585 | 0 | 0 | 0.3585 | 0 | 0.34198 | 1.0998 | 0.31095 | 0.34198 | 1.0998 | 0.31095 | 0.36025 | 1.1586 | 0.31095 | 0.2351% | 0.035573 | 0.033812 | 4287.153 | 11.5968 | 3743.6752 | 531.8809 | 4499.8161 | 0 | 0 | 4499.8161 | 1.182e-05%
2026 | 123 | 123-437 | Tier-1 | Non-HFTD---17 | 1--2 | 0.28887 | 10 | 100% | 1.1053 | 75.1% | 0% | 24.9% | 0.041085 | 0 | 0 | 0.041085 | 0 | 0.039193 | 0.29843 | 0.13133 | 0.039193 | 0.29843 | 0.13133 | 0.041287 | 0.31438 | 0.13133 | 3.717% | 0.0010262 | 0.0009754 | 1077.05 | 100.0793 | 217.6769 | 759.2939 | 1091.0192 | 0 | 0 | 1091.0192 | 1.355e-06%
2026 | LA2 | CB LA2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.183 | 176 | 100% | 12.2214 | 57.22% | 0% | 42.78% | 0.34614 | 0 | 0 | 0.34614 | 0 | 0.33019 | 7.4207 | 0.044496 | 0.33019 | 7.4207 | 0.044496 | 0.34783 | 7.8172 | 0.044496 | 2.832% | 0.020909 | 0.019874 | 584.5039 | 23.2258 | 216.3025 | 344.9757 | 597.5271 | 0 | 0 | 597.5271 | 1.141e-05%
2026 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 11.7296 | 836 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 140.2011 | 12.1177 | 11.5699 | 140.2011 | 12.1177 | 11.5699 | 147.6922 | 12.7652 | 11.5699 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2026 | 857 | CB 857 | Tier-1 | Non-HFTD---4 | 2--4 | 2.4864 | 160 | 100% | 134.8206 | 98.53% | 0% | 1.467% | 6.5757 | 0 | 0 | 6.5757 | 0 | 6.2728 | 2.5687 | 2.442 | 6.2728 | 2.5687 | 2.442 | 6.6079 | 2.7059 | 2.442 | 4.877% | 0.0091096 | 0.0086587 | 14799.8335 | 2316.1863 | 406.4843 | 12077.1629 | 14811.1433 | 0 | 0 | 14811.1433 | 0.0002168%
2026 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 6.4721 | 569 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 200.3313 | 6.6863 | 29.9615 | 200.3313 | 6.6863 | 29.9615 | 211.0352 | 7.0436 | 29.9615 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2026 | 418 | 418-1260 | Tier-1 | Non-HFTD---18 | 2--1 | 2.407 | 55 | 100% | 2.1529 | 26.16% | 0% | 73.84% | 0.027881 | 0 | 0 | 0.027881 | 0 | 0.026597 | 2.4867 | 0.010696 | 0.026597 | 2.4867 | 0.010696 | 0.028018 | 2.6195 | 0.010696 | 1.295% | 0.0068202 | 0.0064826 | 315.6683 | 2.8639 | 87.2806 | 225.5239 | 327.8067 | 0 | 0 | 327.8067 | 9.194e-07%
2026 | ELE1 | CB ELE1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.0237 | 226 | 100% | 2.9214 | 23.25% | 0% | 76.75% | 0.033616 | 0 | 0 | 0.033616 | 0 | 0.032068 | 3.1238 | 0.010266 | 0.032068 | 3.1238 | 0.010266 | 0.033781 | 3.2907 | 0.010266 | 1.151% | 0.0086982 | 0.0082676 | 335.8673 | 0.21618 | 101.3542 | 234.2969 | 349.2925 | 0 | 0 | 349.2925 | 1.109e-06%
2026 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 9.5829 | 969 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 61.735 | 9.9001 | 6.2358 | 61.735 | 9.9001 | 6.2358 | 65.0335 | 10.429 | 6.2358 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2026 | 120 | 120-368F | Tier-1 | Non-HFTD---7 | 2--3 | 1.3866 | 191 | 100% | 30.1162 | 0.9946% | 95.55% | 3.451% | 0.014827 | 0 | 0 | 0.014827 | 0 | 0.014144 | 1.4325 | 0.009874 | 0.014144 | 1.4325 | 0.009874 | 0.0149 | 1.509 | 0.009874 | 0.04923% | 0.011459 | 0.010892 | 2628.1708 | 4.7284 | 2320.4806 | 302.9617 | 2763.6789 | 0 | 0 | 2763.6789 | 4.89e-07%
2026 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 4.6189 | 484 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 281.9725 | 4.7718 | 59.0914 | 281.9725 | 4.7718 | 59.0914 | 297.0387 | 5.0268 | 59.0914 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2026 | 548 | 548-18F | Tier-1 | Non-HFTD---17 | 1--1 | 1.1802 | 43 | 100% | 1.1676 | 51.97% | 0% | 48.03% | 0.030039 | 0 | 0 | 0.030039 | 0 | 0.028655 | 1.2192 | 0.023503 | 0.028655 | 1.2192 | 0.023503 | 0.030187 | 1.2844 | 0.023503 | 2.573% | 0.0027166 | 0.0025821 | 429.8188 | 0.57984 | 239.5369 | 189.7021 | 440.5693 | 0 | 0 | 440.5693 | 9.906e-07%
2026 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.14848 | 8 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 6.3167 | 0.1534 | 41.1781 | 6.3167 | 0.1534 | 41.1781 | 6.6542 | 0.1616 | 41.1781 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2026 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 27.7167 | 1055 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 240.4359 | 28.6339 | 8.3969 | 240.4359 | 28.6339 | 8.3969 | 253.2827 | 30.1639 | 8.3969 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2026 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 7.2309 | 112 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 246.6292 | 7.4702 | 33.0153 | 246.6292 | 7.4702 | 33.0153 | 259.807 | 7.8693 | 33.0153 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2026 | 483 | CB 483 | Tier-1 | Non-HFTD---11 | 2--2 | 2.1438 | 53 | 100% | 10.3604 | 90.93% | 0% | 9.069% | 0.46633 | 0 | 0 | 0.46633 | 0 | 0.44485 | 2.2147 | 0.20086 | 0.44485 | 2.2147 | 0.20086 | 0.46862 | 2.3331 | 0.20086 | 4.501% | 0.006517 | 0.0061944 | 1589.7521 | 232.4385 | 19.5086 | 1337.8049 | 1597.2601 | 0 | 0 | 1597.2601 | 1.538e-05%
2026 | 730 | 730-971R | Tier-1 | Non-HFTD---8 | 3--2 | 8.1335 | 250 | 100% | 26.5137 | 79.89% | 0% | 20.11% | 1.0484 | 0 | 0 | 1.0484 | 0 | 1.0001 | 8.4027 | 0.11903 | 1.0001 | 8.4027 | 0.11903 | 1.0536 | 8.8517 | 0.11903 | 3.954% | 0.02251 | 0.021395 | 1177.8833 | 63.4791 | 575.4887 | 538.9155 | 1190.2215 | 0 | 0 | 1190.2215 | 3.457e-05%
2026 | 551 | 551-19 | Tier-1 | Non-HFTD---12 | 3--2 | 6.4676 | 228 | 100% | 15.235 | 68.38% | 0% | 31.62% | 0.51569 | 0 | 0 | 0.51569 | 0 | 0.49193 | 6.6816 | 0.073625 | 0.49193 | 6.6816 | 0.073625 | 0.51822 | 7.0386 | 0.073625 | 3.385% | 0.018991 | 0.018051 | 802.2291 | 3.4308 | 551.779 | 247.0193 | 815.4385 | 0 | 0 | 815.4385 | 1.701e-05%
2026 | 855 | 855-46AE | Tier-2 | Tier-2---15 | 1--5 | 0.25303 | 0 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 9.3224 | 0 | 0 | 9.3224 | 0 | 8.893 | 0.2614 | 34.02 | 8.893 | 0.2614 | 34.02 | 9.3681 | 0.27537 | 34.02 | 4.944% | 0.0010888 | 0.0010349 | 173174.957 | 50966.8705 | 22.9996 | 122185.0869 | 173185.5197 | 0 | 0 | 173185.5197 | 0.0003074%
2026 | 95 | 95-35F | Tier-1 | Non-HFTD---9 | 2--2 | 2.2868 | 190 | 100% | 19.0547 | 69.14% | 22.45% | 8.414% | 0.65213 | 0 | 0 | 0.65213 | 0 | 0.62209 | 2.3624 | 0.26333 | 0.62209 | 2.3624 | 0.26333 | 0.65533 | 2.4887 | 0.26333 | 3.422% | 0.011941 | 0.01135 | 1595.6856 | 179.3204 | 352.6449 | 1063.7203 | 1621.3303 | 0 | 0 | 1621.3303 | 2.15e-05%
2026 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 5.7761 | 253 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 550.1247 | 5.9673 | 92.1901 | 550.1247 | 5.9673 | 92.1901 | 579.5186 | 6.2861 | 92.1901 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2026 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.05303 | 0 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 1.0269 | 0.054785 | 18.744 | 1.0269 | 0.054785 | 18.744 | 1.0818 | 0.057713 | 18.744 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2026 | 166 | 166-984F | Tier-1 | Non-HFTD---16 | 2--1 | 5.0462 | 201 | 100% | 4.5392 | 30.05% | 0% | 69.95% | 0.067511 | 0 | 0 | 0.067511 | 0 | 0.064401 | 5.2132 | 0.012354 | 0.064401 | 5.2132 | 0.012354 | 0.067842 | 5.4917 | 0.012354 | 1.487% | 0.013305 | 0.012647 | 341.1538 | 0.41222 | 122.751 | 217.9905 | 353.5821 | 0 | 0 | 353.5821 | 2.226e-06%
2026 | 564 | CB 564 | Tier-1 | Non-HFTD---5 | 1--5 | 0.65684 | 30 | 100% | 57.5722 | 99.31% | 0% | 0.6931% | 2.8301 | 0 | 0 | 2.8301 | 0 | 2.6997 | 0.67857 | 3.9785 | 2.6997 | 0.67857 | 3.9785 | 2.8439 | 0.71483 | 3.9785 | 4.916% | 0.002902 | 0.0027584 | 19838.8117 | 2914.289 | 1862.4717 | 15062.051 | 19845.9726 | 0 | 0 | 19845.9726 | 9.333e-05%
2026 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 1.0576 | 39 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 6.5841 | 1.0926 | 6.0262 | 6.5841 | 1.0926 | 6.0262 | 6.9359 | 1.151 | 6.0262 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2026 | 120 | CB 120 | Tier-1 | Non-HFTD---5 | 2--4 | 0.83351 | 54 | 100% | 72.8901 | 46.84% | 52.05% | 1.107% | 1.6901 | 0 | 0 | 1.6901 | 0 | 1.6123 | 0.86109 | 1.8723 | 1.6123 | 0.86109 | 1.8723 | 1.6984 | 0.9071 | 1.8723 | 2.319% | 0.010618 | 0.010093 | 6864.6422 | 601.3181 | 3453.7454 | 2809.5787 | 7054.6775 | 0 | 0 | 7054.6775 | 5.573e-05%
2026 | 781 | 781-44 | Tier-1 | Non-HFTD---2 | 4--4 | 15.9541 | 1118 | 100% | 408.0386 | 9.644% | 87.69% | 2.666% | 1.9479 | 0 | 0 | 1.9479 | 0 | 1.8581 | 16.4821 | 0.11274 | 1.8581 | 16.4821 | 0.11274 | 1.9574 | 17.3628 | 0.11274 | 0.4774% | 0.057288 | 0.054452 | 7122.6331 | 90.5718 | 5991.9403 | 1040.121 | 7457.7922 | 0 | 0 | 7457.7922 | 6.423e-05%
2026 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 21.2556 | 733 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3711.5659 | 21.9591 | 169.022 | 3711.5659 | 21.9591 | 169.022 | 3909.88 | 23.1324 | 169.022 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2026 | 473 | CB 473 | Tier-1 | Non-HFTD---2 | 5--4 | 8.3298 | 539 | 100% | 543.89 | 19.16% | 79.89% | 0.9474% | 5.1597 | 0 | 0 | 5.1597 | 0 | 4.922 | 8.6054 | 0.57197 | 4.922 | 8.6054 | 0.57197 | 5.185 | 9.0652 | 0.57197 | 0.9487% | 0.10114 | 0.096132 | 5377.691 | 163.6638 | 4088.0705 | 1125.9566 | 5604.0765 | 0 | 0 | 5604.0765 | 0.0001701%
2026 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 3.5733 | 151 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.602 | 3.6915 | 3.4138 | 12.602 | 3.6915 | 3.4138 | 13.2754 | 3.8887 | 3.4138 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2026 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.4697 | 0 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 5.0917 | 0.48524 | 10.4931 | 5.0917 | 0.48524 | 10.4931 | 5.3637 | 0.51117 | 10.4931 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2026 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 20.5957 | 1501 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2590.0334 | 21.2772 | 121.7278 | 2590.0334 | 21.2772 | 121.7278 | 2728.4224 | 22.4141 | 121.7278 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2026 | GH2 | CB GH2 | Tier-1 | Non-HFTD---16 | 2--1 | 2.462 | 67 | 100% | 2.4391 | 22.32% | 0% | 77.68% | 0.026948 | 0 | 0 | 0.026948 | 0 | 0.025707 | 2.5434 | 0.010107 | 0.025707 | 2.5434 | 0.010107 | 0.02708 | 2.6793 | 0.010107 | 1.105% | 0.0074138 | 0.0070468 | 328.9948 | 6.3654 | 58.4562 | 264.1731 | 342.304 | 0 | 0 | 342.304 | 8.886e-07%
2026 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 1.7237 | 249 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 64.1211 | 1.7807 | 36.0084 | 64.1211 | 1.7807 | 36.0084 | 67.5471 | 1.8759 | 36.0084 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2026 | 702 | 702-30 | Tier-1 | Non-HFTD---3 | 4--3 | 8.6788 | 214 | 100% | 100.3702 | 67.48% | 26.99% | 5.53% | 3.3524 | 0 | 0 | 3.3524 | 0 | 3.198 | 8.966 | 0.35668 | 3.198 | 8.966 | 0.35668 | 3.3689 | 9.4451 | 0.35668 | 3.34% | 0.033242 | 0.031597 | 3019.3805 | 488.6759 | 847.0105 | 1683.6941 | 3070.5224 | 0 | 0 | 3070.5224 | 0.0001106%
2026 | 205 | 205-369R | Tier-1 | Non-HFTD---2 | 4--4 | 15.9271 | 1706 | 100% | 370.1825 | 97.17% | 0% | 2.827% | 17.8061 | 0 | 0 | 17.8061 | 0 | 16.9858 | 16.4542 | 1.0323 | 16.9858 | 16.4542 | 1.0323 | 17.8934 | 17.3334 | 1.0323 | 4.81% | 0.046634 | 0.044326 | 7938.0395 | 1227.249 | 240.0519 | 6470.7387 | 7949.7244 | 0 | 0 | 7949.7244 | 0.0005872%
2026 | 154 | 154-897F | Tier-1 | Non-HFTD---20 | 1--1 | 0.72155 | 28 | 100% | 0.3167 | 2.18% | 0% | 97.82% | 0.00034168 | 0 | 0 | 0.00034168 | 0 | 0.00032594 | 0.74543 | 0.00043725 | 0.00032594 | 0.74543 | 0.00043725 | 0.00034336 | 0.78526 | 0.00043725 | 0.1079% | 0.002013 | 0.0019134 | 157.3294 | 0.11581 | 17.4095 | 139.8041 | 165.3442 | 0 | 0 | 165.3442 | 1.127e-08%
2026 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 3.8006 | 201 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 376.4593 | 3.9263 | 95.8807 | 376.4593 | 3.9263 | 95.8807 | 396.5741 | 4.1361 | 95.8807 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2026 | 481 | 481-30 | Tier-1 | Non-HFTD---16 | 2--1 | 3.2669 | 149 | 100% | 2.7763 | 24.5% | 0% | 75.5% | 0.033676 | 0 | 0 | 0.033676 | 0 | 0.032124 | 3.375 | 0.0095184 | 0.032124 | 3.375 | 0.0095184 | 0.033841 | 3.5553 | 0.0095184 | 1.213% | 0.0083508 | 0.0079374 | 332.4593 | 0.20057 | 104.1964 | 228.0624 | 345.5304 | 0 | 0 | 345.5304 | 1.111e-06%
2026 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 7.0653 | 395 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 635.4631 | 7.2991 | 87.06 | 635.4631 | 7.2991 | 87.06 | 669.4168 | 7.6891 | 87.06 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2026 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 0.4381 | 36 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.3639 | 0.4526 | 0.80403 | 0.3639 | 0.4526 | 0.80403 | 0.38334 | 0.47678 | 0.80403 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2026 | 188 | 188-12F | Tier-1 | Non-HFTD---19 | 1--2 | 0.24244 | 18 | 100% | 0.37445 | 60.74% | 0% | 39.26% | 0.011258 | 0 | 0 | 0.011258 | 0 | 0.010739 | 0.25047 | 0.042877 | 0.010739 | 0.25047 | 0.042877 | 0.011313 | 0.26385 | 0.042877 | 3.006% | 0.0006558 | 0.00062334 | 570.9839 | 56.1501 | 25.9997 | 488.8341 | 582.659 | 0 | 0 | 582.659 | 3.712e-07%
2026 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 7.1517 | 256 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 320.0792 | 7.3884 | 43.3219 | 320.0792 | 7.3884 | 43.3219 | 337.1815 | 7.7832 | 43.3219 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2026 | 777 | 777-263F | Tier-1 | Non-HFTD---17 | 1--2 | 0.28785 | 0 | 100% | 1.1231 | 80.53% | 0% | 19.47% | 0.044774 | 0 | 0 | 0.044774 | 0 | 0.042711 | 0.29738 | 0.14363 | 0.042711 | 0.29738 | 0.14363 | 0.044993 | 0.31327 | 0.14363 | 3.986% | 0.0008638 | 0.00082104 | 1300.2394 | 169.3313 | 25.8272 | 1105.0809 | 1313.4199 | 0 | 0 | 1313.4199 | 1.476e-06%
2026 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.23902 | 0 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 1.0753 | 0.24692 | 4.3548 | 1.0753 | 0.24692 | 4.3548 | 1.1328 | 0.26012 | 4.3548 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2026 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 2.4417 | 31 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 9.8433 | 2.5225 | 3.9022 | 9.8433 | 2.5225 | 3.9022 | 10.3692 | 2.6572 | 3.9022 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2026 | 733 | 733-23R | Tier-1 | Non-HFTD---10 | 4--1 | 14.2499 | 708 | 100% | 18.173 | 43.59% | 0% | 56.41% | 0.39211 | 0 | 0 | 0.39211 | 0 | 0.37404 | 14.7214 | 0.025408 | 0.37404 | 14.7214 | 0.025408 | 0.39403 | 15.508 | 0.025408 | 2.158% | 0.039686 | 0.037722 | 457.9176 | 5.4845 | 190.7048 | 261.7282 | 471.3702 | 0 | 0 | 471.3702 | 1.293e-05%
2026 | 138 | 138-358R | Tier-1 | Non-HFTD---8 | 3--3 | 5.9884 | 352 | 100% | 38.8456 | 86.43% | 0% | 13.57% | 1.6618 | 0 | 0 | 1.6618 | 0 | 1.5853 | 6.1866 | 0.25624 | 1.5853 | 6.1866 | 0.25624 | 1.67 | 6.5172 | 0.25624 | 4.278% | 0.022652 | 0.021531 | 1714.8689 | 4.9224 | 1481.4917 | 228.4549 | 1726.9914 | 0 | 0 | 1726.9914 | 5.48e-05%
2026 | 163 | 163-33R | Tier-1 | Non-HFTD---10 | 4--2 | 10.3481 | 566 | 100% | 25.0426 | 46.21% | 0% | 53.79% | 0.57287 | 0 | 0 | 0.57287 | 0 | 0.54648 | 10.6906 | 0.051118 | 0.54648 | 10.6906 | 0.051118 | 0.57568 | 11.2618 | 0.051118 | 2.288% | 0.044418 | 0.042219 | 563.798 | 5.8936 | 264.9054 | 292.999 | 579.5904 | 0 | 0 | 579.5904 | 1.889e-05%
2026 | RD2 | CB RD2 | Tier-1 | Non-HFTD---12 | 3--1 | 8.8002 | 319 | 100% | 9.3441 | 27.56% | 0% | 72.44% | 0.12749 | 0 | 0 | 0.12749 | 0 | 0.12162 | 9.0915 | 0.013377 | 0.12162 | 9.0915 | 0.013377 | 0.12812 | 9.5772 | 0.013377 | 1.364% | 0.026759 | 0.025434 | 349.1931 | 3.0965 | 101.4578 | 244.6387 | 362.3657 | 0 | 0 | 362.3657 | 4.204e-06%
2026 | 505 | 505-1676F | Tier-1 | Non-HFTD---4 | 3--4 | 5.4025 | 268 | 100% | 126.3109 | 97.31% | 0% | 2.687% | 6.0844 | 0 | 0 | 6.0844 | 0 | 5.8041 | 5.5813 | 1.0399 | 5.8041 | 5.5813 | 1.0399 | 6.1142 | 5.8795 | 1.0399 | 4.817% | 0.016119 | 0.015321 | 7836.1516 | 1240.1952 | 66.9195 | 6529.037 | 7847.1186 | 0 | 0 | 7847.1186 | 0.0002006%
2026 | 103 | CB 103 | Tier-1 | Non-HFTD---2 | 4--4 | 10.3631 | 451 | 100% | 251.3079 | 4.044% | 92.91% | 3.046% | 0.50308 | 0 | 0 | 0.50308 | 0 | 0.47991 | 10.706 | 0.044826 | 0.47991 | 10.706 | 0.044826 | 0.50555 | 11.278 | 0.044826 | 0.2002% | 0.044854 | 0.042634 | 5602.7475 | 13.1962 | 4846.1699 | 743.3814 | 5882.7266 | 0 | 0 | 5882.7266 | 1.659e-05%
2026 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.78597 | 38 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.8025 | 0.81198 | 14.5354 | 11.8025 | 0.81198 | 14.5354 | 12.4331 | 0.85537 | 14.5354 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2026 | 150 | 150-506 | Tier-1 | Non-HFTD---9 | 1--4 | 0.56136 | 3 | 100% | 17.1377 | 96.67% | 0% | 3.329% | 0.82008 | 0 | 0 | 0.82008 | 0 | 0.7823 | 0.57994 | 1.3489 | 0.7823 | 0.57994 | 1.3489 | 0.8241 | 0.61093 | 1.3489 | 4.785% | 0.0026668 | 0.0025348 | 6426.2995 | 1009.1063 | 19.5009 | 5397.6923 | 6437.4397 | 0 | 0 | 6437.4397 | 2.704e-05%
2026 | 43 | 43-475F | Tier-1 | Non-HFTD---20 | 1--1 | 0.15131 | 3 | 100% | 0.037927 | 13.96% | 0% | 86.04% | 0.00026216 | 0 | 0 | 0.00026216 | 0 | 0.00025008 | 0.15632 | 0.0015998 | 0.00025008 | 0.15632 | 0.0015998 | 0.00026345 | 0.16467 | 0.0015998 | 0.6912% | 0.0002508 | 0.00023839 | 151.2257 | 1.3755 | 25.089 | 124.7612 | 158.0014 | 0 | 0 | 158.0014 | 8.645e-09%
2026 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 1.5879 | 37 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 118.0741 | 1.6405 | 71.9758 | 118.0741 | 1.6405 | 71.9758 | 124.383 | 1.7281 | 71.9758 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2026 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 1.7432 | 394 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 24.149 | 1.8009 | 13.4095 | 24.149 | 1.8009 | 13.4095 | 25.4394 | 1.8971 | 13.4095 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2026 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 19.1678 | 2034 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 429.1796 | 19.8022 | 21.6734 | 429.1796 | 19.8022 | 21.6734 | 452.1112 | 20.8602 | 21.6734 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2026 | 415 | CB 415 | Tier-1 | Non-HFTD---3 | 3--3 | 5.4938 | 215 | 100% | 126.4207 | 27.6% | 69.15% | 3.246% | 1.7273 | 0 | 0 | 1.7273 | 0 | 1.6478 | 5.6756 | 0.29032 | 1.6478 | 5.6756 | 0.29032 | 1.7358 | 5.9789 | 0.29032 | 1.366% | 0.027526 | 0.026163 | 4592.8064 | 78.3926 | 3704.5785 | 809.8353 | 4765.9683 | 0 | 0 | 4765.9683 | 5.696e-05%
2026 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.47553 | 26 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 27.5211 | 0.49126 | 56.021 | 27.5211 | 0.49126 | 56.021 | 28.9916 | 0.51751 | 56.021 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2026 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 0.22216 | 17 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.30123 | 0.22951 | 1.3125 | 0.30123 | 0.22951 | 1.3125 | 0.31732 | 0.24177 | 1.3125 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2026 | 789 | CB 789 | Tier-1 | Non-HFTD---4 | 2--4 | 2.8581 | 104 | 100% | 122.362 | 98.67% | 0% | 1.333% | 5.9762 | 0 | 0 | 5.9762 | 0 | 5.7009 | 2.9527 | 1.9307 | 5.7009 | 2.9527 | 1.9307 | 6.0055 | 3.1105 | 1.9307 | 4.884% | 0.0078294 | 0.0074418 | 15628.5298 | 2423.9954 | 597.0903 | 12607.4441 | 15639.3767 | 0 | 0 | 15639.3767 | 0.0001971%
2026 | MF1 | CB MF1 | Tier-1 | Non-HFTD---7 | 3--3 | 4.0621 | 96 | 100% | 37.1269 | 4.679% | 88.17% | 7.156% | 0.085991 | 0 | 0 | 0.085991 | 0 | 0.08203 | 4.1966 | 0.019547 | 0.08203 | 4.1966 | 0.019547 | 0.086413 | 4.4208 | 0.019547 | 0.2316% | 0.015706 | 0.014928 | 2363.9287 | 4.6517 | 2018.9493 | 340.3277 | 2481.2767 | 0 | 0 | 2481.2767 | 2.836e-06%
2026 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 17.4926 | 1811 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 256.8342 | 18.0715 | 14.2121 | 256.8342 | 18.0715 | 14.2121 | 270.5572 | 19.0371 | 14.2121 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2026 | 255 | CB 255 | Tier-1 | Non-HFTD---8 | 3--3 | 5.8911 | 156 | 100% | 32.2801 | 87.28% | 0% | 12.72% | 1.3946 | 0 | 0 | 1.3946 | 0 | 1.3303 | 6.0861 | 0.21858 | 1.3303 | 6.0861 | 0.21858 | 1.4014 | 6.4113 | 0.21858 | 4.32% | 0.016748 | 0.015919 | 1927.4491 | 4.4433 | 1678.6079 | 244.3979 | 1940.2212 | 0 | 0 | 1940.2212 | 4.599e-05%
2026 | 1439 | 1439-29 | Tier-1 | Non-HFTD---17 | 1--2 | 0.26119 | 1 | 100% | 0.74654 | 53.38% | 0% | 46.62% | 0.019724 | 0 | 0 | 0.019724 | 0 | 0.018816 | 0.26983 | 0.069731 | 0.018816 | 0.26983 | 0.069731 | 0.019821 | 0.28425 | 0.069731 | 2.642% | 0.0010952 | 0.001041 | 681.6446 | 46.3387 | 108.2949 | 527.0109 | 698.1955 | 0 | 0 | 698.1955 | 6.504e-07%
2026 | 401 | 401-684R | Tier-2 | Tier-2---21 | 4--1 | 0.051326 | 14 | 100% | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049319 | 0 | 0 | 0.049319 | 0 | 0.047047 | 0.053024 | 0.88728 | 0.047047 | 0.053024 | 0.88728 | 0.049561 | 0.055857 | 0.88728 | 3.09% | 0.030395 | 0.028891 | 52.5129 | 8.9983 | 14.8334 | 28.6812 | 53.5406 | 0 | 0 | 53.5406 | 1.626e-06%
2026 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 11.6007 | 313 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 6.0182 | 11.9847 | 0.50216 | 6.0182 | 11.9847 | 0.50216 | 6.3398 | 12.625 | 0.50216 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2026 | 490 | 490-36 | Tier-1 | Non-HFTD---19 | 1--3 | 0.037879 | 3 | 100% | 0.34203 | 90.49% | 0% | 9.512% | 0.01532 | 0 | 0 | 0.01532 | 0 | 0.014614 | 0.039132 | 0.37346 | 0.014614 | 0.039132 | 0.37346 | 0.015395 | 0.041223 | 0.37346 | 4.479% | 0.000149 | 0.00014162 | 2295.4788 | 192.4507 | 911.964 | 1191.0641 | 2306.8493 | 0 | 0 | 2306.8493 | 5.052e-07%
2026 | 343 | 343-20 | Tier-1 | Non-HFTD---14 | 2--1 | 4.3719 | 186 | 100% | 6.0217 | 48.31% | 0% | 51.69% | 0.144 | 0 | 0 | 0.144 | 0 | 0.13736 | 4.5166 | 0.030413 | 0.13736 | 4.5166 | 0.030413 | 0.1447 | 4.7579 | 0.030413 | 2.391% | 0.012386 | 0.011773 | 486.184 | 9.777 | 199.1497 | 277.2573 | 499.2718 | 0 | 0 | 499.2718 | 4.748e-06%
2026 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 34.4453 | 2730 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 255.1218 | 35.5852 | 7.1693 | 255.1218 | 35.5852 | 7.1693 | 268.7533 | 37.4866 | 7.1693 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2026 | 213 | 213-263F | Tier-1 | Non-HFTD---7 | 1--4 | 0.84712 | 152 | 100% | 32.2974 | 98.29% | 0% | 1.706% | 1.5715 | 0 | 0 | 1.5715 | 0 | 1.4991 | 0.87515 | 1.7129 | 1.4991 | 0.87515 | 1.7129 | 1.5792 | 0.92191 | 1.7129 | 4.866% | 0.0030164 | 0.0028671 | 10707.2735 | 2157.1184 | 1406.2766 | 7143.8786 | 10716.7845 | 0 | 0 | 10716.7845 | 5.182e-05%
2026 | 508 | CB 508 | Tier-1 | Non-HFTD---9 | 2--3 | 2.0923 | 61 | 100% | 20.2639 | 91.46% | 0% | 8.542% | 0.91739 | 0 | 0 | 0.91739 | 0 | 0.87512 | 2.1615 | 0.40487 | 0.87512 | 2.1615 | 0.40487 | 0.92188 | 2.277 | 0.40487 | 4.527% | 0.0068532 | 0.006514 | 2956.8488 | 100.9812 | 2109.3369 | 746.5307 | 2970.0016 | 0 | 0 | 2970.0016 | 3.025e-05%
2026 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 3.5275 | 195 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 308.4441 | 3.6442 | 84.6398 | 308.4441 | 3.6442 | 84.6398 | 324.9247 | 3.8389 | 84.6398 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2026 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.18447 | 0 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.5515 | 0.19057 | 13.3884 | 2.5515 | 0.19057 | 13.3884 | 2.6878 | 0.20076 | 13.3884 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2026 | 156 | 156-538 | Tier-1 | Non-HFTD---8 | 3--3 | 5.9075 | 140 | 100% | 34.3358 | 87.94% | 0% | 12.06% | 1.4947 | 0 | 0 | 1.4947 | 0 | 1.4258 | 6.103 | 0.23362 | 1.4258 | 6.103 | 0.23362 | 1.502 | 6.4291 | 0.23362 | 4.353% | 0.018674 | 0.01775 | 1838.6947 | 313.0243 | 338.2317 | 1187.4387 | 1850.2417 | 0 | 0 | 1850.2417 | 4.929e-05%
2026 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 10.4561 | 132 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 32.9073 | 10.8021 | 3.0464 | 32.9073 | 10.8021 | 3.0464 | 34.6656 | 11.3793 | 3.0464 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2026 | 1483 | 1483-39 | Tier-1 | Non-HFTD---18 | 1--1 | 1.3201 | 34 | 100% | 1.247 | 34.85% | 0% | 65.15% | 0.021511 | 0 | 0 | 0.021511 | 0 | 0.02052 | 1.3638 | 0.015047 | 0.02052 | 1.3638 | 0.015047 | 0.021617 | 1.4366 | 0.015047 | 1.725% | 0.0033188 | 0.0031545 | 375.7288 | 1.7167 | 143.7713 | 230.2408 | 388.4768 | 0 | 0 | 388.4768 | 7.094e-07%
2026 | 199 | CB 199 | Tier-1 | Non-HFTD---5 | 3--3 | 5.8392 | 182 | 100% | 86.2492 | 95.28% | 0% | 4.716% | 4.068 | 0 | 0 | 4.068 | 0 | 3.8806 | 6.0324 | 0.64329 | 3.8806 | 6.0324 | 0.64329 | 4.0879 | 6.3548 | 0.64329 | 4.717% | 0.019491 | 0.018526 | 4425.0322 | 993.0316 | 124.6693 | 3307.3312 | 4435.8997 | 0 | 0 | 4435.8997 | 0.0001341%
2026 | 549 | CB 549 | Tier-1 | Non-HFTD---11 | 2--2 | 3.6668 | 74 | 100% | 10.14 | 74.51% | 0% | 25.49% | 0.37399 | 0 | 0 | 0.37399 | 0 | 0.35676 | 3.7882 | 0.094178 | 0.35676 | 3.7882 | 0.094178 | 0.37582 | 3.9906 | 0.094178 | 3.688% | 0.010939 | 0.010398 | 926.9394 | 30.6503 | 525.5764 | 370.7127 | 939.2439 | 0 | 0 | 939.2439 | 1.233e-05%
2026 | 277 | CB 277 | Tier-1 | Non-HFTD---11 | 1--4 | 0.46136 | 28 | 100% | 9.2421 | 96.22% | 0% | 3.783% | 0.44017 | 0 | 0 | 0.44017 | 0 | 0.4199 | 0.47663 | 0.88097 | 0.4199 | 0.47663 | 0.88097 | 0.44233 | 0.5021 | 0.88097 | 4.763% | 0.0016702 | 0.0015875 | 5533.5154 | 30.682 | 5156.0762 | 346.7572 | 5544.418 | 0 | 0 | 5544.418 | 1.452e-05%
2026 | 1047 | 1047-36F | Tier-1 | Non-HFTD---14 | 3--1 | 7.665 | 358 | 100% | 7.6285 | 33.56% | 0% | 66.44% | 0.12671 | 0 | 0 | 0.12671 | 0 | 0.12087 | 7.9187 | 0.015264 | 0.12087 | 7.9187 | 0.015264 | 0.12733 | 8.3418 | 0.015264 | 1.661% | 0.020747 | 0.01972 | 367.6979 | 0.66227 | 142.6229 | 224.4127 | 380.4213 | 0 | 0 | 380.4213 | 4.178e-06%
2026 | 510 | CB 510 | Tier-1 | Non-HFTD---11 | 2--2 | 0.63409 | 21 | 100% | 12.2941 | 84.64% | 10.34% | 5.026% | 0.51508 | 0 | 0 | 0.51508 | 0 | 0.49135 | 0.65508 | 0.75006 | 0.49135 | 0.65508 | 0.75006 | 0.5176 | 0.69008 | 0.75006 | 4.19% | 0.012771 | 0.012139 | 962.6446 | 60.1151 | 530.8101 | 371.7194 | 970.3456 | 0 | 0 | 970.3456 | 1.699e-05%
2026 | 1434 | 1434-11 | Tier-1 | Non-HFTD---17 | 1--3 | 0.30362 | 1 | 100% | 1.328 | 86.5% | 0% | 13.5% | 0.056858 | 0 | 0 | 0.056858 | 0 | 0.054239 | 0.31367 | 0.17292 | 0.054239 | 0.31367 | 0.17292 | 0.057137 | 0.33043 | 0.17292 | 4.282% | 0.000755 | 0.00071763 | 1758.899 | 88.6139 | 996.9745 | 673.3106 | 1771.2681 | 0 | 0 | 1771.2681 | 1.875e-06%
2026 | 1180 | CB 1180 | Tier-1 | Non-HFTD---7 | 1--4 | 1.2019 | 76 | 100% | 35.2333 | 97.75% | 0% | 2.252% | 1.7048 | 0 | 0 | 1.7048 | 0 | 1.6262 | 1.2417 | 1.3097 | 1.6262 | 1.2417 | 1.3097 | 1.7131 | 1.308 | 1.3097 | 4.839% | 0.0039062 | 0.0037128 | 9019.8397 | 919.8579 | 4656.5948 | 3443.387 | 9030.4183 | 0 | 0 | 9030.4183 | 5.622e-05%
2026 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 2.4644 | 87 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 22.199 | 2.546 | 8.7192 | 22.199 | 2.546 | 8.7192 | 23.3851 | 2.682 | 8.7192 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2026 | 489 | CB 489 | Tier-1 | Non-HFTD---12 | 3--2 | 5.9438 | 160 | 100% | 14.1275 | 73.98% | 0% | 26.02% | 0.51732 | 0 | 0 | 0.51732 | 0 | 0.49349 | 6.1405 | 0.080366 | 0.49349 | 6.1405 | 0.080366 | 0.51986 | 6.4686 | 0.080366 | 3.662% | 0.016022 | 0.015229 | 881.768 | 0.17267 | 673.1395 | 208.4558 | 893.7185 | 0 | 0 | 893.7185 | 1.706e-05%
2026 | 368 | 368-1057F | Tier-1 | Non-HFTD---12 | 2--2 | 1.2491 | 112 | 100% | 9.345 | 62.09% | 27.57% | 10.34% | 0.28721 | 0 | 0 | 0.28721 | 0 | 0.27398 | 1.2904 | 0.21232 | 0.27398 | 1.2904 | 0.21232 | 0.28862 | 1.3593 | 0.21232 | 3.073% | 0.01023 | 0.0097236 | 913.4882 | 55.7905 | 466.091 | 391.6067 | 931.523 | 0 | 0 | 931.523 | 9.471e-06%
2026 | 139 | 139-243AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.24791 | 3 | 100% | 0.28248 | 13.18% | 0% | 86.82% | 0.0018428 | 0 | 0 | 0.0018428 | 0 | 0.0017579 | 0.25612 | 0.0068637 | 0.0017579 | 0.25612 | 0.0068637 | 0.0018518 | 0.2698 | 0.0068637 | 0.6524% | 0.000781 | 0.00074234 | 361.6876 | 0.23629 | 76.193 | 285.2582 | 378.0411 | 0 | 0 | 378.0411 | 6.077e-08%
2026 | 189 | 189-783F | Tier-1 | Non-HFTD---17 | 1--2 | 0.44904 | 7 | 100% | 1.922 | 84.88% | 0% | 15.12% | 0.080752 | 0 | 0 | 0.080752 | 0 | 0.077031 | 0.4639 | 0.16605 | 0.077031 | 0.4639 | 0.16605 | 0.081147 | 0.48869 | 0.16605 | 4.201% | 0.0013618 | 0.0012944 | 1411.3883 | 12.6725 | 1141.007 | 257.7088 | 1422.5046 | 0 | 0 | 1422.5046 | 2.663e-06%
2026 | 140 | 140-481R | Tier-1 | Non-HFTD---6 | 3--3 | 5.1055 | 212 | 100% | 76.5519 | 22.22% | 72.37% | 5.415% | 0.84198 | 0 | 0 | 0.84198 | 0 | 0.80319 | 5.2744 | 0.15228 | 0.80319 | 5.2744 | 0.15228 | 0.8461 | 5.5563 | 0.15228 | 1.1% | 0.022011 | 0.020921 | 3477.9247 | 83.6911 | 2703.5551 | 690.6785 | 3618.8026 | 0 | 0 | 3618.8026 | 2.777e-05%
2026 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.45755 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 63.2779 | 0.47269 | 133.8663 | 63.2779 | 0.47269 | 133.8663 | 66.6589 | 0.49795 | 133.8663 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2026 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 2.6683 | 454 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 23.9277 | 2.7566 | 8.68 | 23.9277 | 2.7566 | 8.68 | 25.2062 | 2.9039 | 8.68 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2026 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 3.6174 | 384 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 210.4643 | 3.7372 | 56.3167 | 210.4643 | 3.7372 | 56.3167 | 221.7097 | 3.9368 | 56.3167 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2026 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 1.3381 | 157 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.973 | 1.3824 | 4.3209 | 5.973 | 1.3824 | 4.3209 | 6.2921 | 1.4562 | 4.3209 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2026 | 548 | CB 548 | Tier-1 | Non-HFTD---10 | 2--2 | 3.9959 | 122 | 100% | 15.6121 | 79.23% | 0% | 20.77% | 0.61227 | 0 | 0 | 0.61227 | 0 | 0.58406 | 4.1281 | 0.14148 | 0.58406 | 4.1281 | 0.14148 | 0.61527 | 4.3487 | 0.14148 | 3.922% | 0.012194 | 0.011591 | 1280.2923 | 2.5369 | 1024.1977 | 253.5578 | 1294.1425 | 0 | 0 | 1294.1425 | 2.019e-05%
2026 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 4.2816 | 41 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 28.5249 | 4.4233 | 6.4488 | 28.5249 | 4.4233 | 6.4488 | 30.0491 | 4.6597 | 6.4488 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2026 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 14.5985 | 959 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 533.1833 | 15.0816 | 35.3532 | 533.1833 | 15.0816 | 35.3532 | 561.672 | 15.8875 | 35.3532 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2026 | 95 | 95-29R | Tier-1 | Non-HFTD---6 | 4--3 | 9.681 | 422 | 100% | 60.1265 | 25.03% | 65.18% | 9.791% | 0.74481 | 0 | 0 | 0.74481 | 0 | 0.7105 | 10.0014 | 0.07104 | 0.7105 | 10.0014 | 0.07104 | 0.74846 | 10.5358 | 0.07104 | 1.239% | 0.032867 | 0.03124 | 1829.3755 | 34.6804 | 1347.9039 | 446.7912 | 1900.8041 | 0 | 0 | 1900.8041 | 2.456e-05%
2026 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 2.7176 | 192 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.6262 | 2.8075 | 2.7163 | 7.6262 | 2.8075 | 2.7163 | 8.0337 | 2.9575 | 2.7163 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2026 | 548 | 548-12F | Tier-1 | Non-HFTD---20 | 1--1 | 0.3271 | 5 | 100% | 0.21703 | 18.87% | 0% | 81.13% | 0.0020269 | 0 | 0 | 0.0020269 | 0 | 0.0019335 | 0.33792 | 0.0057217 | 0.0019335 | 0.33792 | 0.0057217 | 0.0020368 | 0.35598 | 0.0057217 | 0.9339% | 0.0007594 | 0.00072181 | 285.7879 | 6.0125 | 39.2503 | 240.5251 | 297.8631 | 0 | 0 | 297.8631 | 6.684e-08%
2026 | 775 | CB 775 | Tier-1 | Non-HFTD---17 | 1--2 | 0.29205 | 9 | 100% | 1.2409 | 63.86% | 0% | 36.14% | 0.039223 | 0 | 0 | 0.039223 | 0 | 0.037416 | 0.30171 | 0.12401 | 0.037416 | 0.30171 | 0.12401 | 0.039416 | 0.31783 | 0.12401 | 3.161% | 0.0013874 | 0.0013187 | 894.417 | 24.4609 | 451.2287 | 418.7273 | 911.2529 | 0 | 0 | 911.2529 | 1.293e-06%
2026 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 18.8384 | 1884 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 192.4478 | 19.4619 | 9.8885 | 192.4478 | 19.4619 | 9.8885 | 202.7306 | 20.5018 | 9.8885 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2026 | 1173 | 1173-68 | Tier-1 | Non-HFTD---13 | 1--3 | 1.1887 | 126 | 100% | 6.4999 | 85.9% | 0% | 14.1% | 0.27639 | 0 | 0 | 0.27639 | 0 | 0.26366 | 1.228 | 0.2147 | 0.26366 | 1.228 | 0.2147 | 0.27775 | 1.2936 | 0.2147 | 4.252% | 0.0037692 | 0.0035826 | 1724.4769 | 400.6816 | 34.3759 | 1289.4193 | 1737.1359 | 0 | 0 | 1737.1359 | 9.114e-06%
2026 | 1174 | CB 1174 | Tier-1 | Non-HFTD---20 | 1--1 | 0.2536 | 0 | 100% | 0.3405 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.26199 | 0 | 0 | 0.26199 | 0 | 0 | 0.27599 | 0 | 0% | 0.0011044 | 0.0010497 | 308.3124 | 0.232 | 28.0073 | 280.0731 | 324.3686 | 0 | 0 | 324.3686 | 0%
2026 | NC4 | CB NC4 | Tier-1 | Non-HFTD---14 | 3--1 | 6.1544 | 189 | 100% | 6.4492 | 25.78% | 0% | 74.22% | 0.082286 | 0 | 0 | 0.082286 | 0 | 0.078495 | 6.358 | 0.012346 | 0.078495 | 6.358 | 0.012346 | 0.08269 | 6.6978 | 0.012346 | 1.276% | 0.017682 | 0.016806 | 364.7392 | 1.3706 | 111.4291 | 251.9395 | 378.8379 | 0 | 0 | 378.8379 | 2.713e-06%
2026 | 123 | 123-557 | Tier-1 | Non-HFTD---19 | 1--2 | 0.005303 | 3 | 100% | 0.044985 | 24.83% | 0% | 75.17% | 0.00055285 | 0 | 0 | 0.00055285 | 0 | 0.00052738 | 0.0054785 | 0.096264 | 0.00052738 | 0.0054785 | 0.096264 | 0.00055556 | 0.0057712 | 0.096264 | 1.229% | 6.14e-05 | 5.8361e-05 | 732.6611 | 11.0369 | 166.3248 | 555.2994 | 761.3435 | 0 | 0 | 761.3435 | 1.823e-08%
2026 | 570 | 570-489F | Tier-1 | Non-HFTD---20 | 1--1 | 0.060397 | 11 | 100% | 0.036046 | 6.552% | 0% | 93.45% | 0.0001169 | 0 | 0 | 0.0001169 | 0 | 0.00011151 | 0.062396 | 0.0017872 | 0.00011151 | 0.062396 | 0.0017872 | 0.00011747 | 0.06573 | 0.0017872 | 0.3243% | 0.0001616 | 0.0001536 | 223.0577 | 0.15685 | 33.549 | 189.3518 | 233.913 | 0 | 0 | 233.913 | 3.855e-09%
2026 | 86 | 86-1058F | Tier-1 | Non-HFTD---19 | 1--1 | 0.34811 | 19 | 100% | 0.46174 | 17.14% | 0% | 82.86% | 0.0039179 | 0 | 0 | 0.0039179 | 0 | 0.0037374 | 0.35963 | 0.010392 | 0.0037374 | 0.35963 | 0.010392 | 0.0039371 | 0.37885 | 0.010392 | 0.8485% | 0.0012994 | 0.0012351 | 355.352 | 8.5613 | 36.0451 | 310.7455 | 370.6858 | 0 | 0 | 370.6858 | 1.292e-07%
2026 | 792 | 792-1173F | Tier-1 | Non-HFTD---12 | 3--2 | 0.42482 | 8 | 100% | 9.7258 | 44.88% | 50.38% | 4.732% | 0.21608 | 0 | 0 | 0.21608 | 0 | 0.20613 | 0.43888 | 0.46967 | 0.20613 | 0.43888 | 0.46967 | 0.21714 | 0.46233 | 0.46967 | 2.222% | 0.018988 | 0.018048 | 512.2147 | 5.2953 | 409.626 | 97.2933 | 526.9171 | 0 | 0 | 526.9171 | 7.126e-06%
2026 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 3.1864 | 101 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 142.8022 | 3.2918 | 43.381 | 142.8022 | 3.2918 | 43.381 | 150.4323 | 3.4677 | 43.381 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2026 | 241 | 241-570 | Tier-1 | Non-HFTD---2 | 5--4 | 18.8601 | 1038 | 100% | 1283.0682 | 34.99% | 64.02% | 0.9973% | 22.221 | 0 | 0 | 22.221 | 0 | 21.1973 | 19.4842 | 1.0879 | 21.1973 | 19.4842 | 1.0879 | 22.3299 | 20.5253 | 1.0879 | 1.732% | 0.15951 | 0.15162 | 8043.669 | 557.5746 | 4862.2355 | 2623.8589 | 8316.0062 | 0 | 0 | 8316.0062 | 0.0007328%
2026 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.68239 | 74 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 65.2006 | 0.70497 | 92.4873 | 65.2006 | 0.70497 | 92.4873 | 68.6844 | 0.74264 | 92.4873 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2026 | 55 | 55-483F | Tier-1 | Non-HFTD---11 | 2--2 | 2.7087 | 114 | 100% | 9.2861 | 71.18% | 0% | 28.82% | 0.32719 | 0 | 0 | 0.32719 | 0 | 0.31212 | 2.7983 | 0.11154 | 0.31212 | 2.7983 | 0.11154 | 0.32879 | 2.9478 | 0.11154 | 3.523% | 0.009502 | 0.0090317 | 977.2747 | 1.1382 | 715.4551 | 260.6814 | 991.9422 | 0 | 0 | 991.9422 | 1.079e-05%
2026 | 456 | 456-5 | Tier-1 | Non-HFTD---1 | 3--5 | 7.8148 | 407 | 100% | 584.4392 | 99.09% | 0% | 0.9055% | 28.6678 | 0 | 0 | 28.6678 | 0 | 27.3471 | 8.0734 | 3.3873 | 27.3471 | 8.0734 | 3.3873 | 28.8083 | 8.5048 | 3.3873 | 4.905% | 0.025435 | 0.024176 | 22978.1161 | 5310.5669 | 175.0323 | 17492.5169 | 22988.9519 | 0 | 0 | 22988.9519 | 0.0009454%
2026 | DM2 | CB DM2 | Tier-1 | Non-HFTD---3 | 3--3 | 4.8831 | 426 | 100% | 93.2156 | 56.52% | 39.8% | 3.676% | 2.608 | 0 | 0 | 2.608 | 0 | 2.4878 | 5.0447 | 0.49315 | 2.4878 | 5.0447 | 0.49315 | 2.6208 | 5.3143 | 0.49315 | 2.798% | 0.024472 | 0.023261 | 3809.0413 | 343.1954 | 1456.0262 | 2009.8197 | 3895.2895 | 0 | 0 | 3895.2895 | 8.6e-05%
2026 | 261 | CB 261 | Tier-1 | Non-HFTD---11 | 2--2 | 1.4223 | 54 | 100% | 8.7767 | 85.72% | 0% | 14.28% | 0.37239 | 0 | 0 | 0.37239 | 0 | 0.35523 | 1.4694 | 0.24176 | 0.35523 | 1.4694 | 0.24176 | 0.37421 | 1.5479 | 0.24176 | 4.243% | 0.0054352 | 0.0051662 | 1614.782 | 193.7429 | 186.2869 | 1234.7522 | 1626.7947 | 0 | 0 | 1626.7947 | 1.228e-05%
2026 | 93 | 93-10R | Tier-1 | Non-HFTD---2 | 4--4 | 9.5466 | 770 | 100% | 302.3321 | 90.71% | 7.303% | 1.988% | 13.575 | 0 | 0 | 13.575 | 0 | 12.9496 | 9.8625 | 1.313 | 12.9496 | 9.8625 | 1.313 | 13.6415 | 10.3895 | 1.313 | 4.49% | 0.035815 | 0.034042 | 8441.494 | 1852.3748 | 638.1878 | 5950.9314 | 8482.34 | 0 | 0 | 8482.34 | 0.0004477%
2026 | 368 | 368-24 | Tier-1 | Non-HFTD---3 | 3--4 | 6.8786 | 219 | 100% | 131.8203 | 5.447% | 90.51% | 4.044% | 0.35545 | 0 | 0 | 0.35545 | 0 | 0.33908 | 7.1063 | 0.047715 | 0.33908 | 7.1063 | 0.047715 | 0.35719 | 7.486 | 0.047715 | 0.2696% | 0.025227 | 0.023978 | 5225.4485 | 5.586 | 4642.0429 | 577.8196 | 5482.7545 | 0 | 0 | 5482.7545 | 1.172e-05%
2026 | 715 | CB 715 | Tier-1 | Non-HFTD---5 | 2--4 | 2.2625 | 177 | 100% | 64.2152 | 97.59% | 0% | 2.408% | 3.1021 | 0 | 0 | 3.1021 | 0 | 2.9592 | 2.3373 | 1.2661 | 2.9592 | 2.3373 | 1.2661 | 3.1173 | 2.4622 | 1.2661 | 4.831% | 0.0088918 | 0.0084517 | 7221.8396 | 1455.0968 | 1510.162 | 4256.5807 | 7230.8958 | 0 | 0 | 7230.8958 | 0.0001023%
2026 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 15.7168 | 1396 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1185.2748 | 16.2369 | 72.9987 | 1185.2748 | 16.2369 | 72.9987 | 1248.6056 | 17.1045 | 72.9987 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2026 | EOS2 | CB EOS2 | Tier-1 | Non-HFTD---10 | 4--2 | 15.5156 | 504 | 100% | 23.2282 | 49.67% | 0% | 50.33% | 0.57106 | 0 | 0 | 0.57106 | 0 | 0.54475 | 16.029 | 0.033985 | 0.54475 | 16.029 | 0.033985 | 0.57385 | 16.8855 | 0.033985 | 2.458% | 0.044799 | 0.042581 | 518.4987 | 9.3302 | 225.2181 | 283.9504 | 532.0901 | 0 | 0 | 532.0901 | 1.883e-05%
2026 | 794 | 794-15 | Tier-1 | Non-HFTD---6 | 4--3 | 4.1462 | 121 | 100% | 86.3748 | 7.031% | 89.79% | 3.183% | 0.30062 | 0 | 0 | 0.30062 | 0 | 0.28677 | 4.2834 | 0.066949 | 0.28677 | 4.2834 | 0.066949 | 0.30209 | 4.5123 | 0.066949 | 0.348% | 0.02911 | 0.027669 | 2967.1473 | 28.0705 | 2440.5619 | 498.5149 | 3110.8053 | 0 | 0 | 3110.8053 | 9.913e-06%
2026 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | 2--5 | 2.2297 | 144 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 7.5583 | 0 | 0 | 7.5583 | 0 | 7.2102 | 2.3035 | 3.1301 | 7.2102 | 2.3035 | 3.1301 | 7.5954 | 2.4266 | 3.1301 | 4.922% | 0.0076984 | 0.0073173 | 19947.1031 | 4677.56 | 10.2291 | 15259.3139 | 19952.9673 | 0 | 0 | 19952.9673 | 0.0002492%
2026 | 124 | 124-206R | Tier-1 | Non-HFTD---14 | 2--2 | 2.8064 | 55 | 100% | 5.0289 | 52.24% | 0% | 47.76% | 0.13003 | 0 | 0 | 0.13003 | 0 | 0.12404 | 2.8993 | 0.042784 | 0.12404 | 2.8993 | 0.042784 | 0.13067 | 3.0542 | 0.042784 | 2.586% | 0.0096408 | 0.0091636 | 521.6316 | 2.9356 | 277.9653 | 240.7307 | 534.6068 | 0 | 0 | 534.6068 | 4.288e-06%
2026 | 922 | 922-1143F | Tier-1 | Non-HFTD---9 | 2--3 | 2.9475 | 109 | 100% | 20.705 | 88.62% | 0% | 11.38% | 0.9083 | 0 | 0 | 0.9083 | 0 | 0.86645 | 3.0451 | 0.28454 | 0.86645 | 3.0451 | 0.28454 | 0.91275 | 3.2078 | 0.28454 | 4.387% | 0.0096708 | 0.0091921 | 2140.9782 | 289.3821 | 148.841 | 1702.7551 | 2153.6629 | 0 | 0 | 2153.6629 | 2.995e-05%
2026 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 9.6756 | 274 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 68.092 | 9.9958 | 6.8121 | 68.092 | 9.9958 | 6.8121 | 71.7303 | 10.5299 | 6.8121 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2026 | 277 | 277-48 | Tier-1 | Non-HFTD---2 | 4--4 | 10.0475 | 283 | 100% | 230.0219 | 5.859% | 91.22% | 2.918% | 0.66709 | 0 | 0 | 0.66709 | 0 | 0.63636 | 10.3801 | 0.061306 | 0.63636 | 10.3801 | 0.061306 | 0.67036 | 10.9347 | 0.061306 | 0.29% | 0.043712 | 0.041548 | 5262.2134 | 55.7509 | 4495.9402 | 710.5223 | 5520.2023 | 0 | 0 | 5520.2023 | 2.2e-05%
2026 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | 3--3 | 1.5256 | 31 | 100% | 40.9949 | 23.55% | 73.64% | 2.81% | 0.47782 | 0 | 0 | 0.47782 | 0 | 0.45581 | 1.5761 | 0.28921 | 0.45581 | 1.5761 | 0.28921 | 0.48016 | 1.6603 | 0.28921 | 1.166% | 0.021565 | 0.020497 | 1901.027 | 61.7007 | 1198.5032 | 640.8231 | 1976.7168 | 0 | 0 | 1976.7168 | 1.576e-05%
2026 | 276 | 276-158R | Tier-1 | Non-HFTD---3 | 4--3 | 15.2584 | 300 | 100% | 188.0595 | 4.698% | 89.13% | 6.174% | 0.43729 | 0 | 0 | 0.43729 | 0 | 0.41715 | 15.7633 | 0.026463 | 0.41715 | 15.7633 | 0.026463 | 0.43944 | 16.6056 | 0.026463 | 0.2325% | 0.060308 | 0.057323 | 3118.2966 | 14.6042 | 2673.243 | 430.4493 | 3273.0622 | 0 | 0 | 3273.0622 | 1.442e-05%
2026 | 95 | 95-36F | Tier-1 | Non-HFTD---9 | 3--2 | 3.9422 | 302 | 100% | 25.869 | 56.36% | 33.85% | 9.785% | 0.72172 | 0 | 0 | 0.72172 | 0 | 0.68847 | 4.0727 | 0.16905 | 0.68847 | 4.0727 | 0.16905 | 0.72526 | 4.2903 | 0.16905 | 2.79% | 0.016067 | 0.015272 | 1610.0531 | 145.5142 | 538.7895 | 925.7494 | 1646.6431 | 0 | 0 | 1646.6431 | 2.38e-05%
2026 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 6.9741 | 649 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 886.2644 | 7.2048 | 123.0094 | 886.2644 | 7.2048 | 123.0094 | 933.6187 | 7.5898 | 123.0094 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2026 | 142 | CB 142 | Tier-1 | Non-HFTD---3 | 4--3 | 10.8841 | 244 | 100% | 108.6332 | 57.02% | 36.05% | 6.937% | 3.066 | 0 | 0 | 3.066 | 0 | 2.9248 | 11.2443 | 0.26011 | 2.9248 | 11.2443 | 0.26011 | 3.0811 | 11.8451 | 0.26011 | 2.822% | 0.039142 | 0.037205 | 2775.333 | 244.59 | 1527.2947 | 1003.4483 | 2837.4565 | 0 | 0 | 2837.4565 | 0.0001011%
2026 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 15.3043 | 1539 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 149.4686 | 15.8108 | 9.4536 | 149.4686 | 15.8108 | 9.4536 | 157.4549 | 16.6556 | 9.4536 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2026 | 723 | 723-377 | Tier-1 | Non-HFTD---19 | 1--1 | 0.093039 | 6 | 100% | 0.11767 | 36.99% | 0% | 63.01% | 0.0021545 | 0 | 0 | 0.0021545 | 0 | 0.0020552 | 0.096118 | 0.021382 | 0.0020552 | 0.096118 | 0.021382 | 0.002165 | 0.10125 | 0.021382 | 1.831% | 0.0002816 | 0.00026766 | 417.8452 | 1.6299 | 169.7356 | 246.4797 | 431.5565 | 0 | 0 | 431.5565 | 7.105e-08%
2026 | 394 | CB 394 | Tier-1 | Non-HFTD---2 | 4--3 | 0.54963 | 25 | 100% | 400.0096 | 2.606% | 97.29% | 0.1022% | 0.51601 | 0 | 0 | 0.51601 | 0 | 0.49224 | 0.56782 | 0.86689 | 0.49224 | 0.56782 | 0.86689 | 0.51854 | 0.59816 | 0.86689 | 0.129% | 0.091335 | 0.086814 | 4379.6067 | 27.9554 | 3843.5806 | 508.0707 | 4601.7434 | 0 | 0 | 4601.7434 | 1.702e-05%
2026 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 9.2129 | 306 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 215.6371 | 9.5178 | 22.6562 | 215.6371 | 9.5178 | 22.6562 | 227.1588 | 10.0263 | 22.6562 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2026 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 3.6236 | 252 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.6768 | 3.7436 | 1.5164 | 5.6768 | 3.7436 | 1.5164 | 5.9801 | 3.9436 | 1.5164 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2026 | 324 | CB 324 | Tier-1 | Non-HFTD---7 | 1--4 | 1.1407 | 37 | 100% | 29.9941 | 97.06% | 0% | 2.94% | 1.4411 | 0 | 0 | 1.4411 | 0 | 1.3747 | 1.1785 | 1.1665 | 1.3747 | 1.1785 | 1.1665 | 1.4481 | 1.2414 | 1.1665 | 4.804% | 0.0044058 | 0.0041877 | 6807.8599 | 1023.5636 | 2848.5992 | 2935.6971 | 6818.2819 | 0 | 0 | 6818.2819 | 4.752e-05%
2026 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 8.2068 | 162 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 23.5661 | 8.4784 | 2.7795 | 23.5661 | 8.4784 | 2.7795 | 24.8252 | 8.9314 | 2.7795 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2026 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 1.7152 | 35 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 338.4324 | 1.7719 | 190.9985 | 338.4324 | 1.7719 | 190.9985 | 356.5153 | 1.8666 | 190.9985 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2026 | 151 | 151-97 | Tier-1 | Non-HFTD---20 | 1--1 | 0.20303 | 3 | 100% | 0.093775 | 23.98% | 0% | 76.02% | 0.001113 | 0 | 0 | 0.001113 | 0 | 0.0010618 | 0.20975 | 0.005062 | 0.0010618 | 0.20975 | 0.005062 | 0.0011185 | 0.22096 | 0.005062 | 1.187% | 0.0004212 | 0.00040035 | 222.6384 | 0.12736 | 68.7596 | 153.7515 | 231.4528 | 0 | 0 | 231.4528 | 3.67e-08%
2026 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 14.5687 | 1159 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 633.9221 | 15.0509 | 42.1187 | 633.9221 | 15.0509 | 42.1187 | 667.7935 | 15.855 | 42.1187 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2026 | GS1 | CB GS1 | Tier-1 | Non-HFTD---10 | 3--2 | 1.6765 | 71 | 100% | 15.4311 | 0.9691% | 90.27% | 8.765% | 0.0074024 | 0 | 0 | 0.0074024 | 0 | 0.0070614 | 1.732 | 0.0040771 | 0.0070614 | 1.732 | 0.0040771 | 0.0074387 | 1.8245 | 0.0040771 | 0.04797% | 0.019954 | 0.018967 | 773.3185 | 0.96411 | 654.1164 | 118.238 | 813.201 | 0 | 0 | 813.201 | 2.441e-07%
2026 | BK4 | CB BK4 | Tier-1 | Non-HFTD---8 | 3--2 | 2.4461 | 111 | 100% | 27.9552 | 2.318% | 91.59% | 6.093% | 0.032081 | 0 | 0 | 0.032081 | 0 | 0.030603 | 2.527 | 0.01211 | 0.030603 | 2.527 | 0.01211 | 0.032238 | 2.662 | 0.01211 | 0.1148% | 0.017152 | 0.016303 | 1629.8314 | 2.4593 | 1406.2531 | 221.119 | 1712.7417 | 0 | 0 | 1712.7417 | 1.058e-06%
2026 | 95 | 95-1353F | Tier-1 | Non-HFTD---19 | 1--2 | 0.0064394 | 0 | 100% | 0.032887 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0066525 | 0 | 0 | 0.0066525 | 0 | 0 | 0.0070079 | 0 | 0% | 4.94e-05 | 4.6955e-05 | 665.7292 | 0.50094 | 60.4753 | 604.753 | 700.399 | 0 | 0 | 700.399 | 0%
2026 | 295 | 295-1203F | Tier-2 | Tier-2---21 | 1--2 | 0.48803 | 33 | 100% | 0.80448 | 60.49% | 0% | 39.51% | 0.02409 | 0 | 0 | 0.02409 | 0 | 0.02298 | 0.50418 | 0.045579 | 0.02298 | 0.50418 | 0.045579 | 0.024208 | 0.53112 | 0.045579 | 2.994% | 0.0013362 | 0.0012701 | 602.062 | 79.8078 | 41.8021 | 480.452 | 614.4487 | 0 | 0 | 614.4487 | 7.944e-07%
2026 | 287 | 287-1118 | Tier-2 | Tier-2---17 | 2--4 | 0.3572 | 93 | 100% | 43.5784 | 73.95% | 25.25% | 0.8076% | 1.5951 | 0 | 0 | 1.5951 | 0 | 1.5216 | 0.36902 | 4.1235 | 1.5216 | 0.36902 | 4.1235 | 1.603 | 0.38873 | 4.1235 | 3.66% | 0.0072086 | 0.0068518 | 6045.3323 | 731.9415 | 1415.1289 | 3898.2619 | 6127.3544 | 0 | 0 | 6127.3544 | 5.26e-05%
2026 | 858 | 858-14 | Tier-2 | Tier-2---12 | 2--5 | 3.2698 | 298 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 20.2792 | 0 | 0 | 20.2792 | 0 | 19.345 | 3.3781 | 5.7267 | 19.345 | 3.3781 | 5.7267 | 20.3786 | 3.5586 | 5.7267 | 4.926% | 0.010043 | 0.0095457 | 40994.194 | 8631.9946 | 63.0219 | 32299.1775 | 41004.6459 | 0 | 0 | 41004.6459 | 0.0006687%
2026 | 1438 | CB 1438 | Tier-1 | Non-HFTD---10 | 4--2 | 13.0695 | 540 | 100% | 23.5165 | 61.83% | 0% | 38.17% | 0.71979 | 0 | 0 | 0.71979 | 0 | 0.68663 | 13.502 | 0.050854 | 0.68663 | 13.502 | 0.050854 | 0.72332 | 14.2234 | 0.050854 | 3.061% | 0.042229 | 0.040138 | 556.8862 | 44.3045 | 160.7551 | 351.8266 | 567.9549 | 0 | 0 | 567.9549 | 2.374e-05%
2026 | 139 | 139-426F | Tier-1 | Non-HFTD---13 | 1--2 | 1.0122 | 8 | 100% | 7.5054 | 85.27% | 0% | 14.73% | 0.31681 | 0 | 0 | 0.31681 | 0 | 0.30221 | 1.0457 | 0.28902 | 0.30221 | 1.0457 | 0.28902 | 0.31836 | 1.1015 | 0.28902 | 4.221% | 0.0044324 | 0.004213 | 1693.3052 | 0.18763 | 1466.5978 | 226.5198 | 1706.2913 | 0 | 0 | 1706.2913 | 1.045e-05%
2026 | 775 | 775-187AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.53754 | 21 | 100% | 0.5948 | 11.69% | 0% | 88.31% | 0.0034422 | 0 | 0 | 0.0034422 | 0 | 0.0032836 | 0.55533 | 0.0059129 | 0.0032836 | 0.55533 | 0.0059129 | 0.003459 | 0.585 | 0.0059129 | 0.5787% | 0.0018144 | 0.0017246 | 327.8194 | 2.8623 | 48.4676 | 276.4895 | 342.8956 | 0 | 0 | 342.8956 | 1.135e-07%
2026 | 166 | 166-465F | Tier-1 | Non-HFTD---20 | 1--1 | 0.70302 | 35 | 100% | 0.54405 | 10.51% | 0% | 89.49% | 0.0028298 | 0 | 0 | 0.0028298 | 0 | 0.0026994 | 0.72628 | 0.0037168 | 0.0026994 | 0.72628 | 0.0037168 | 0.0028437 | 0.76509 | 0.0037168 | 0.5201% | 0.0018838 | 0.0017906 | 288.8062 | 0.19448 | 53.8256 | 234.7861 | 302.2662 | 0 | 0 | 302.2662 | 9.332e-08%
2026 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | 4--5 | 16.7053 | 4693 | 100% | 5312.2676 | 97.77% | 1.999% | 0.2313% | 257.0917 | 0 | 0 | 257.0917 | 0 | 245.248 | 17.2581 | 14.2106 | 245.248 | 17.2581 | 14.2106 | 258.352 | 18.1802 | 14.2106 | 4.84% | 0.075145 | 0.071425 | 70693.7485 | 12854.9773 | 1446.2382 | 56392.533 | 70775.8701 | 0 | 0 | 70775.8701 | 0.008478%
2026 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 10.9093 | 781 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 103.6022 | 11.2703 | 9.1925 | 103.6022 | 11.2703 | 9.1925 | 109.1378 | 11.8725 | 9.1925 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2026 | 534 | CB 534 | Tier-2 | Tier-2---21 | 4--1 | 0.59621 | 0 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11233 | 0 | 0 | 0.11233 | 0 | 0.10716 | 0.61594 | 0.17397 | 0.10716 | 0.61594 | 0.17397 | 0.11288 | 0.64885 | 0.17397 | 1.782% | 0.060541 | 0.057544 | 104.1456 | 5.1049 | 50.6919 | 48.3488 | 107.6172 | 0 | 0 | 107.6172 | 3.704e-06%
2026 | 365 | 365-28AE | Tier-1 | Non-HFTD---13 | 2--2 | 0.82505 | 65 | 100% | 5.7486 | 52.15% | 38.57% | 9.281% | 0.14839 | 0 | 0 | 0.14839 | 0 | 0.14155 | 0.85235 | 0.16608 | 0.14155 | 0.85235 | 0.16608 | 0.14912 | 0.89789 | 0.16608 | 2.581% | 0.0083168 | 0.0079051 | 691.2044 | 57.8 | 253.5042 | 379.9002 | 708.4293 | 0 | 0 | 708.4293 | 4.893e-06%
2026 | 731 | CB 731 | Tier-1 | Non-HFTD---9 | 2--3 | 3.6858 | 132 | 100% | 19.0771 | 87.49% | 0% | 12.51% | 0.82616 | 0 | 0 | 0.82616 | 0 | 0.7881 | 3.8078 | 0.20697 | 0.7881 | 3.8078 | 0.20697 | 0.83021 | 4.0112 | 0.20697 | 4.331% | 0.010127 | 0.0096253 | 1883.8631 | 99.1754 | 1064.8601 | 719.8275 | 1896.1392 | 0 | 0 | 1896.1392 | 2.724e-05%
2026 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 12.1911 | 333 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 396.1715 | 12.5945 | 31.4559 | 396.1715 | 12.5945 | 31.4559 | 417.3395 | 13.2674 | 31.4559 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2026 | 162 | CB 162 | Tier-1 | Non-HFTD---13 | 1--3 | 1.571 | 46 | 100% | 8.4433 | 83.96% | 0% | 16.04% | 0.35092 | 0 | 0 | 0.35092 | 0 | 0.33475 | 1.623 | 0.20625 | 0.33475 | 1.623 | 0.20625 | 0.35264 | 1.7098 | 0.20625 | 4.156% | 0.0047568 | 0.0045213 | 1774.9918 | 1.6508 | 1507.3568 | 265.9842 | 1789.8161 | 0 | 0 | 1789.8161 | 1.157e-05%
2026 | 288 | CB 288 | Tier-1 | Non-HFTD---3 | 4--3 | 9.475 | 686 | 100% | 139.689 | 50.69% | 44.99% | 4.325% | 3.5048 | 0 | 0 | 3.5048 | 0 | 3.3433 | 9.7886 | 0.34155 | 3.3433 | 9.7886 | 0.34155 | 3.522 | 10.3116 | 0.34155 | 2.509% | 0.031221 | 0.029676 | 4474.1439 | 310.4337 | 2474.817 | 1688.8931 | 4589.0459 | 0 | 0 | 4589.0459 | 0.0001156%
2026 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 4.3252 | 245 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 24.2408 | 4.4683 | 5.425 | 24.2408 | 4.4683 | 5.425 | 25.536 | 4.7071 | 5.425 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2026 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 17.8309 | 1248 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 120.5219 | 18.421 | 6.5426 | 120.5219 | 18.421 | 6.5426 | 126.9615 | 19.4053 | 6.5426 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2026 | OS1 | CB OS1 | Tier-1 | Non-HFTD---12 | 3--2 | 6.9136 | 228 | 100% | 10.0644 | 54.01% | 0% | 45.99% | 0.26907 | 0 | 0 | 0.26907 | 0 | 0.25667 | 7.1424 | 0.035936 | 0.25667 | 7.1424 | 0.035936 | 0.27039 | 7.524 | 0.035936 | 2.673% | 0.018753 | 0.017825 | 536.6874 | 6.9162 | 271.0663 | 258.705 | 549.5416 | 0 | 0 | 549.5416 | 8.873e-06%
2026 | RD4 | RD4-50F | Tier-1 | Non-HFTD---14 | 2--1 | 4.4805 | 302 | 100% | 5.2842 | 37.48% | 0% | 62.52% | 0.098033 | 0 | 0 | 0.098033 | 0 | 0.093517 | 4.6288 | 0.020203 | 0.093517 | 4.6288 | 0.020203 | 0.098514 | 4.8761 | 0.020203 | 1.855% | 0.012567 | 0.011945 | 420.4788 | 12.2717 | 107.7406 | 300.4665 | 434.1695 | 0 | 0 | 434.1695 | 3.233e-06%
2026 | 52 | CB 52 | Tier-1 | Non-HFTD---19 | 1--1 | 0.47123 | 35 | 100% | 0.48161 | 27.86% | 0% | 72.14% | 0.0066407 | 0 | 0 | 0.0066407 | 0 | 0.0063348 | 0.48682 | 0.013012 | 0.0063348 | 0.48682 | 0.013012 | 0.0066732 | 0.51283 | 0.013012 | 1.379% | 0.0013064 | 0.0012417 | 368.6562 | 0.20013 | 126.8513 | 241.6047 | 382.5071 | 0 | 0 | 382.5071 | 2.19e-07%
2026 | 533 | CB 533 | Tier-2 | Tier-2---20 | 4--1 | 0.38679 | 0 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.01766 | 0 | 0 | 0.01766 | 0 | 0.016847 | 0.39959 | 0.042159 | 0.016847 | 0.39959 | 0.042159 | 0.017747 | 0.42094 | 0.042159 | 0.1665% | 0.06013 | 0.057154 | 176.3723 | 1.2595 | 133.5547 | 41.5581 | 185.2484 | 0 | 0 | 185.2484 | 5.824e-07%
2026 | 1434 | 1434-2 | Tier-1 | Non-HFTD---14 | 3--1 | 5.9692 | 171 | 100% | 5.8957 | 43.99% | 0% | 56.01% | 0.12838 | 0 | 0 | 0.12838 | 0 | 0.12246 | 6.1667 | 0.019859 | 0.12246 | 6.1667 | 0.019859 | 0.12901 | 6.4962 | 0.019859 | 2.177% | 0.014526 | 0.013807 | 405.8792 | 0.79827 | 195.3366 | 209.7443 | 417.7184 | 0 | 0 | 417.7184 | 4.233e-06%
2026 | 431 | 431-550 | Tier-1 | Non-HFTD---11 | 2--2 | 4.3572 | 164 | 100% | 13.1339 | 75.53% | 0% | 24.47% | 0.49104 | 0 | 0 | 0.49104 | 0 | 0.46842 | 4.5014 | 0.10406 | 0.46842 | 4.5014 | 0.10406 | 0.49345 | 4.7419 | 0.10406 | 3.739% | 0.012344 | 0.011733 | 1063.9583 | 1.4337 | 819.6558 | 242.8688 | 1077.517 | 0 | 0 | 1077.517 | 1.619e-05%
2026 | 968 | CB 968 | Tier-1 | Non-HFTD---15 | 1--3 | 0.3553 | 3 | 100% | 2.4046 | 84.55% | 0% | 15.45% | 0.10063 | 0 | 0 | 0.10063 | 0 | 0.095996 | 0.36706 | 0.26153 | 0.095996 | 0.36706 | 0.26153 | 0.10113 | 0.38667 | 0.26153 | 4.185% | 0.0014058 | 0.0013362 | 1710.4748 | 127.3956 | 651.9293 | 931.1499 | 1724.2412 | 0 | 0 | 1724.2412 | 3.318e-06%
2026 | IB2 | CB IB2 | Tier-1 | Non-HFTD---16 | 2--1 | 5.2097 | 121 | 100% | 4.5685 | 28.86% | 0% | 71.14% | 0.065256 | 0 | 0 | 0.065256 | 0 | 0.06225 | 5.3821 | 0.011566 | 0.06225 | 5.3821 | 0.011566 | 0.065576 | 5.6697 | 0.011566 | 1.428% | 0.013384 | 0.012721 | 341.3434 | 0.43381 | 119.0194 | 221.8902 | 353.9902 | 0 | 0 | 353.9902 | 2.152e-06%
2026 | 486 | CB 486 | Tier-1 | Non-HFTD---15 | 1--4 | 0.12424 | 11 | 100% | 2.895 | 93.41% | 0% | 6.589% | 0.13386 | 0 | 0 | 0.13386 | 0 | 0.12769 | 0.12835 | 0.99484 | 0.12769 | 0.12835 | 0.99484 | 0.13451 | 0.13521 | 0.99484 | 4.624% | 0.0005584 | 0.00053076 | 5184.3933 | 136.4681 | 4036.8272 | 1011.0981 | 5202.1844 | 0 | 0 | 5202.1844 | 4.414e-06%
2026 | 969 | CB 969 | Tier-1 | Non-HFTD---15 | 1--3 | 0.40417 | 27 | 100% | 3.3526 | 88.46% | 0% | 11.54% | 0.14681 | 0 | 0 | 0.14681 | 0 | 0.14005 | 0.41754 | 0.33541 | 0.14005 | 0.41754 | 0.33541 | 0.14753 | 0.43985 | 0.33541 | 4.379% | 0.0018268 | 0.0017364 | 1835.2417 | 238.0159 | 133.8154 | 1463.4105 | 1846.2677 | 0 | 0 | 1846.2677 | 4.841e-06%
2026 | 366 | 366-559 | Tier-1 | Non-HFTD---7 | 2--3 | 1.0561 | 6 | 100% | 36.9737 | 0.4866% | 97.35% | 2.161% | 0.0089065 | 0 | 0 | 0.0089065 | 0 | 0.0084962 | 1.091 | 0.0077874 | 0.0084962 | 1.091 | 0.0077874 | 0.0089501 | 1.1493 | 0.0077874 | 0.02409% | 0.0083398 | 0.007927 | 4433.4019 | 5.8876 | 3951.842 | 475.6723 | 4663.1604 | 0 | 0 | 4663.1604 | 2.937e-07%
2026 | 168 | CB 168 | Tier-1 | Non-HFTD---8 | 3--2 | 7.6273 | 374 | 100% | 32.7486 | 82.97% | 0% | 17.03% | 1.345 | 0 | 0 | 1.345 | 0 | 1.2831 | 7.8797 | 0.16283 | 1.2831 | 7.8797 | 0.16283 | 1.3516 | 8.3007 | 0.16283 | 4.107% | 0.023992 | 0.022804 | 1364.9793 | 11.4899 | 1084.5121 | 268.9774 | 1377.084 | 0 | 0 | 1377.084 | 4.435e-05%
2026 | 497 | 497-888F | Tier-1 | Non-HFTD---11 | 1--3 | 0.99355 | 104 | 100% | 9.8083 | 94.15% | 0% | 5.846% | 0.45713 | 0 | 0 | 0.45713 | 0 | 0.43607 | 1.0264 | 0.42484 | 0.43607 | 1.0264 | 0.42484 | 0.45937 | 1.0813 | 0.42484 | 4.661% | 0.0031776 | 0.0030203 | 3086.6864 | 271.9431 | 1260.4115 | 1554.3319 | 3096.0835 | 0 | 0 | 3096.0835 | 1.507e-05%
2026 | 1081 | 1081-38AE | Tier-1 | Non-HFTD---1 | 3--4 | 1.1752 | 119 | 100% | 213.0679 | 78.03% | 21.53% | 0.4327% | 8.23 | 0 | 0 | 8.23 | 0 | 7.8509 | 1.214 | 6.4667 | 7.8509 | 1.214 | 6.4667 | 8.2703 | 1.2789 | 6.4667 | 3.863% | 0.01533 | 0.014572 | 13898.3942 | 2058.13 | 2800.8861 | 9039.378 | 14057.3933 | 0 | 0 | 14057.3933 | 0.0002714%
2026 | 242 | 242-776F | Tier-1 | Non-HFTD---6 | 5--2 | 0.6741 | 30 | 100% | 89.0868 | 11.41% | 88.12% | 0.4676% | 0.50321 | 0 | 0 | 0.50321 | 0 | 0.48003 | 0.69641 | 0.68929 | 0.48003 | 0.69641 | 0.68929 | 0.50567 | 0.73362 | 0.68929 | 0.5649% | 0.097933 | 0.093086 | 909.6674 | 12.7136 | 757.5676 | 139.3862 | 951.6351 | 0 | 0 | 951.6351 | 1.659e-05%
2026 | VDN1 | CB VDN1 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0672 | 440 | 100% | 85.5226 | 4.345% | 90.68% | 4.973% | 0.18395 | 0 | 0 | 0.18395 | 0 | 0.17548 | 6.268 | 0.027996 | 0.17548 | 6.268 | 0.027996 | 0.18486 | 6.6029 | 0.027996 | 0.2151% | 0.027823 | 0.026446 | 3073.7667 | 13.6612 | 2620.1542 | 439.9513 | 3226.8862 | 0 | 0 | 3226.8862 | 6.066e-06%
2026 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 5.1365 | 431 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 118.5279 | 5.3065 | 22.3362 | 118.5279 | 5.3065 | 22.3362 | 124.861 | 5.5901 | 22.3362 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2026 | 376 | CB 376 | Tier-1 | Non-HFTD---10 | 3--2 | 7.7214 | 137 | 100% | 26.2471 | 76.46% | 0% | 23.54% | 0.99336 | 0 | 0 | 0.99336 | 0 | 0.9476 | 7.9769 | 0.11879 | 0.9476 | 7.9769 | 0.11879 | 0.99823 | 8.4031 | 0.11879 | 3.785% | 0.022473 | 0.021361 | 1167.9296 | 0.21143 | 917.9161 | 249.8021 | 1182.2491 | 0 | 0 | 1182.2491 | 3.276e-05%
2026 | 59 | 59-464AE | Tier-1 | Non-HFTD---14 | 3--2 | 0.95286 | 102 | 100% | 7.4345 | 25.7% | 64.22% | 10.07% | 0.094587 | 0 | 0 | 0.094587 | 0 | 0.090229 | 0.98439 | 0.09166 | 0.090229 | 0.98439 | 0.09166 | 0.09505 | 1.037 | 0.09166 | 1.272% | 0.014091 | 0.013394 | 527.5962 | 24.004 | 335.1416 | 168.4506 | 548.0102 | 0 | 0 | 548.0102 | 3.119e-06%
2026 | 63 | 63-35AE | Tier-1 | Non-HFTD---1 | 3--4 | 1.9439 | 124 | 100% | 256.4675 | 76.22% | 23.46% | 0.3199% | 9.6762 | 0 | 0 | 9.6762 | 0 | 9.2304 | 2.0083 | 4.5962 | 9.2304 | 2.0083 | 4.5962 | 9.7236 | 2.1156 | 4.5962 | 3.773% | 0.016955 | 0.016116 | 15126.187 | 2259.8593 | 3445.3068 | 9421.0209 | 15313.5135 | 0 | 0 | 15313.5135 | 0.0003191%
2026 | 712 | 712-311F | Tier-1 | Non-HFTD---15 | 1--2 | 0.68958 | 52 | 100% | 2.2762 | 61.21% | 0% | 38.79% | 0.06897 | 0 | 0 | 0.06897 | 0 | 0.065793 | 0.7124 | 0.092353 | 0.065793 | 0.7124 | 0.092353 | 0.069308 | 0.75047 | 0.092353 | 3.03% | 0.002841 | 0.0027004 | 801.2038 | 64.6949 | 121.7914 | 614.7175 | 817.3878 | 0 | 0 | 817.3878 | 2.274e-06%
2026 | VS3 | CB VS3 | Tier-1 | Non-HFTD---10 | 3--2 | 5.5108 | 560 | 100% | 22.658 | 81.41% | 0% | 18.59% | 0.91305 | 0 | 0 | 0.91305 | 0 | 0.87099 | 5.6932 | 0.15299 | 0.87099 | 5.6932 | 0.15299 | 0.91752 | 5.9974 | 0.15299 | 4.03% | 0.016726 | 0.015898 | 1354.6403 | 175.5967 | 54.3376 | 1124.7059 | 1367.7563 | 0 | 0 | 1367.7563 | 3.011e-05%
2026 | 242 | 242-1420F | Tier-1 | Non-HFTD---6 | 5--2 | 1.2443 | 17 | 100% | 89.5601 | 12.52% | 86.49% | 0.9881% | 0.55499 | 0 | 0 | 0.55499 | 0 | 0.52942 | 1.2855 | 0.41184 | 0.52942 | 1.2855 | 0.41184 | 0.55771 | 1.3542 | 0.41184 | 0.6197% | 0.1 | 0.095054 | 895.5638 | 14.9487 | 662.244 | 218.3711 | 936.3641 | 0 | 0 | 936.3641 | 1.83e-05%
2026 | 181 | 181-49 | Tier-1 | Non-HFTD---6 | 4--2 | 0.13883 | 1 | 100% | 64.7664 | 8.121% | 91.5% | 0.3833% | 0.26035 | 0 | 0 | 0.26035 | 0 | 0.24836 | 0.14342 | 1.7317 | 0.24836 | 0.14342 | 1.7317 | 0.26163 | 0.15108 | 1.7317 | 0.402% | 0.078852 | 0.074949 | 821.3685 | 11.8665 | 685.9557 | 123.5464 | 860.6699 | 0 | 0 | 860.6699 | 8.586e-06%
2026 | 100 | 100-1122R | Tier-1 | Non-HFTD---17 | 1--2 | 0.61362 | 11 | 100% | 1.1188 | 52.39% | 0% | 47.61% | 0.029016 | 0 | 0 | 0.029016 | 0 | 0.027679 | 0.63393 | 0.043663 | 0.027679 | 0.63393 | 0.043663 | 0.029158 | 0.6678 | 0.043663 | 2.594% | 0.002205 | 0.0020959 | 507.381 | 49.2152 | 31.6075 | 426.5583 | 519.9599 | 0 | 0 | 519.9599 | 9.568e-07%
2026 | 90 | 90-32 | Tier-1 | Non-HFTD---5 | 3--3 | 3.1322 | 91 | 100% | 76.4194 | 6.097% | 89.87% | 4.029% | 0.23063 | 0 | 0 | 0.23063 | 0 | 0.22 | 3.2358 | 0.06799 | 0.22 | 3.2358 | 0.06799 | 0.23176 | 3.4087 | 0.06799 | 0.3018% | 0.016016 | 0.015223 | 4771.4395 | 9.6024 | 4175.1996 | 586.6374 | 5004.776 | 0 | 0 | 5004.776 | 7.605e-06%
2026 | 1483 | 1483-40 | Tier-1 | Non-HFTD---20 | 1--1 | 0.44642 | 20 | 100% | 0.31443 | 22.37% | 0% | 77.63% | 0.0034821 | 0 | 0 | 0.0034821 | 0 | 0.0033217 | 0.46119 | 0.0072023 | 0.0033217 | 0.46119 | 0.0072023 | 0.0034992 | 0.48584 | 0.0072023 | 1.107% | 0.001097 | 0.0010427 | 286.6296 | 0.16743 | 84.3376 | 202.1246 | 298.2171 | 0 | 0 | 298.2171 | 1.148e-07%
2026 | 154 | 154-878R | Tier-1 | Non-HFTD---12 | 3--1 | 10.4622 | 189 | 100% | 14.2275 | 52.45% | 0% | 47.55% | 0.36939 | 0 | 0 | 0.36939 | 0 | 0.35237 | 10.8084 | 0.032601 | 0.35237 | 10.8084 | 0.032601 | 0.3712 | 11.3859 | 0.032601 | 2.596% | 0.028539 | 0.027127 | 498.52 | 0.24282 | 282.6124 | 215.6648 | 510.8648 | 0 | 0 | 510.8648 | 1.218e-05%
2026 | 181 | 181-54F | Tier-1 | Non-HFTD---16 | 3--1 | 1.2006 | 19 | 100% | 2.7236 | 29.54% | 39.02% | 31.44% | 0.039823 | 0 | 0 | 0.039823 | 0 | 0.037988 | 1.2403 | 0.030628 | 0.037988 | 1.2403 | 0.030628 | 0.040018 | 1.3066 | 0.030628 | 1.462% | 0.01856 | 0.017641 | 146.7509 | 7.1793 | 49.6425 | 89.929 | 152.1359 | 0 | 0 | 152.1359 | 1.313e-06%
2026 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 16.5478 | 1012 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 287.5688 | 17.0954 | 16.8214 | 287.5688 | 17.0954 | 16.8214 | 302.934 | 18.0088 | 16.8214 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2026 | 948 | CB 948 | Tier-1 | Non-HFTD---10 | 4--1 | 14.9462 | 579 | 100% | 22.208 | 55.27% | 0% | 44.73% | 0.60752 | 0 | 0 | 0.60752 | 0 | 0.57954 | 15.4409 | 0.037533 | 0.57954 | 15.4409 | 0.037533 | 0.6105 | 16.2659 | 0.037533 | 2.736% | 0.044785 | 0.042569 | 495.8748 | 16.8793 | 215.136 | 263.8595 | 507.4272 | 0 | 0 | 507.4272 | 2.003e-05%
2026 | 506 | 506-844 | Tier-1 | Non-HFTD---10 | 3--2 | 8.7868 | 165 | 100% | 22.4025 | 80.21% | 0% | 19.79% | 0.8895 | 0 | 0 | 0.8895 | 0 | 0.84853 | 9.0775 | 0.093475 | 0.84853 | 9.0775 | 0.093475 | 0.89386 | 9.5626 | 0.093475 | 3.971% | 0.021885 | 0.020802 | 1023.6455 | 1.2121 | 833.0026 | 189.4308 | 1034.1936 | 0 | 0 | 1034.1936 | 2.933e-05%
2026 | 461 | CB 461 | Tier-2 | Tier-2---15 | 2--4 | 2.4203 | 0 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 4.9747 | 0 | 0 | 4.9747 | 0 | 4.7455 | 2.5004 | 1.8979 | 4.7455 | 2.5004 | 1.8979 | 4.9991 | 2.634 | 1.8979 | 4.883% | 0.0097562 | 0.0092733 | 10441.6529 | 2274.299 | 1515.1673 | 6652.1866 | 10448.9777 | 0 | 0 | 10448.9777 | 0.000164%
2026 | 80 | 80-568F | Tier-1 | Non-HFTD---14 | 3--1 | 9.8088 | 176 | 100% | 8.3283 | 29.18% | 0% | 70.82% | 0.1203 | 0 | 0 | 0.1203 | 0 | 0.11476 | 10.1334 | 0.011325 | 0.11476 | 10.1334 | 0.011325 | 0.12089 | 10.6748 | 0.011325 | 1.445% | 0.025016 | 0.023778 | 332.9159 | 2.3303 | 105.3492 | 225.2364 | 345.194 | 0 | 0 | 345.194 | 3.967e-06%
2026 | BA2 | CB BA2 | Tier-1 | Non-HFTD---14 | 2--1 | 4.4718 | 100 | 100% | 5.2769 | 32.36% | 0% | 67.64% | 0.084525 | 0 | 0 | 0.084525 | 0 | 0.080631 | 4.6198 | 0.017453 | 0.080631 | 4.6198 | 0.017453 | 0.084939 | 4.8666 | 0.017453 | 1.602% | 0.013379 | 0.012717 | 394.4186 | 8.4721 | 101.3103 | 284.6363 | 408.3123 | 0 | 0 | 408.3123 | 2.787e-06%
2026 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.51875 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.3203 | 0.53592 | 4.3295 | 2.3203 | 0.53592 | 4.3295 | 2.4442 | 0.56455 | 4.3295 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2026 | WY3 | CB WY3 | Tier-1 | Non-HFTD---20 | 1--1 | 0.49583 | 5 | 100% | 0.64342 | 2.218% | 0% | 97.78% | 0.00070635 | 0 | 0 | 0.00070635 | 0 | 0.00067381 | 0.51224 | 0.0013154 | 0.00067381 | 0.51224 | 0.0013154 | 0.00070981 | 0.53961 | 0.0013154 | 0.1098% | 0.002013 | 0.0019134 | 319.6305 | 0.84233 | 31.6894 | 287.0987 | 335.907 | 0 | 0 | 335.907 | 2.329e-08%
2026 | 460 | CB 460 | Tier-2 | Tier-2---17 | 1--4 | 0.95644 | 7 | 100% | 58.9173 | 99.11% | 0% | 0.8919% | 2.8904 | 0 | 0 | 2.8904 | 0 | 2.7572 | 0.98809 | 2.7905 | 2.7572 | 0.98809 | 2.7905 | 2.9046 | 1.0409 | 2.7905 | 4.906% | 0.0037362 | 0.0035513 | 15769.3081 | 2295.5963 | 5550.7252 | 7922.9866 | 15776.6323 | 0 | 0 | 15776.6323 | 9.531e-05%
2026 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 9.6284 | 485 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 488.2028 | 9.9471 | 49.0801 | 488.2028 | 9.9471 | 49.0801 | 514.2881 | 10.4786 | 49.0801 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2026 | LPS1 | CB LPS1 | Tier-1 | Non-HFTD---18 | 2--1 | 2.5019 | 76 | 100% | 1.8545 | 27.68% | 0% | 72.32% | 0.02541 | 0 | 0 | 0.02541 | 0 | 0.024239 | 2.5847 | 0.009378 | 0.024239 | 2.5847 | 0.009378 | 0.025534 | 2.7228 | 0.009378 | 1.37% | 0.006253 | 0.0059435 | 296.5769 | 4.136 | 77.2739 | 215.167 | 307.7467 | 0 | 0 | 307.7467 | 8.379e-07%
2026 | 417 | 417-791AE | Tier-1 | Non-HFTD---4 | 3--4 | 1.9314 | 67 | 100% | 96.2517 | 1.815% | 96.36% | 1.824% | 0.086463 | 0 | 0 | 0.086463 | 0 | 0.08248 | 1.9953 | 0.041337 | 0.08248 | 1.9953 | 0.041337 | 0.086887 | 2.1019 | 0.041337 | 0.08983% | 0.016976 | 0.016136 | 5669.8675 | 7.6795 | 5119.2772 | 542.9108 | 5959.7835 | 0 | 0 | 5959.7835 | 2.851e-06%
2026 | 454 | 454-53F | Tier-2 | Tier-2---13 | 4--3 | 0.73506 | 31 | 100% | 272.5399 | 0.7301% | 99.1% | 0.1654% | 0.098502 | 0 | 0 | 0.098502 | 0 | 0.093964 | 0.75939 | 0.12374 | 0.093964 | 0.75939 | 0.12374 | 0.098985 | 0.79996 | 0.12374 | 0.03614% | 0.073094 | 0.069476 | 3728.6015 | 9.5009 | 3385.0726 | 334.0281 | 3921.3613 | 0 | 0 | 3921.3613 | 3.248e-06%
2026 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 7.2415 | 176 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 100.0176 | 7.4811 | 13.3693 | 100.0176 | 7.4811 | 13.3693 | 105.3617 | 7.8809 | 13.3693 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2026 | 438 | 438-45 | Tier-1 | Non-HFTD---15 | 1--3 | 0.46629 | 47 | 100% | 4.5379 | 93.11% | 0% | 6.89% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.19951 | 0.48172 | 0.41417 | 0.19951 | 0.48172 | 0.41417 | 0.21017 | 0.50746 | 0.41417 | 4.609% | 0.0017438 | 0.0016575 | 2602.317 | 452.2709 | 20.4829 | 2129.5632 | 2611.6552 | 0 | 0 | 2611.6552 | 6.897e-06%
2026 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 11.7129 | 151 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 329.0418 | 12.1005 | 27.1924 | 329.0418 | 12.1005 | 27.1924 | 346.623 | 12.7471 | 27.1924 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2026 | 355 | 355-65R | Tier-2 | Tier-2---21 | 1--2 | 0.0075758 | 0 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.0015289 | 0 | 0 | 0.0015289 | 0 | 0.0014584 | 0.0078265 | 0.18635 | 0.0014584 | 0.0078265 | 0.18635 | 0.0015364 | 0.0082446 | 0.18635 | 2.282% | 7.02e-05 | 6.6725e-05 | 954.2713 | 72.5365 | 46.719 | 835.0158 | 981.0548 | 0 | 0 | 981.0548 | 5.042e-08%
2026 | HW1 | CB HW1 | Tier-1 | Non-HFTD---4 | 1--5 | 1.0525 | 61 | 100% | 122.4382 | 99.35% | 0% | 0.6452% | 6.0216 | 0 | 0 | 6.0216 | 0 | 5.7442 | 1.0873 | 5.2831 | 5.7442 | 1.0873 | 5.2831 | 6.0511 | 1.1454 | 5.2831 | 4.918% | 0.0031138 | 0.0029597 | 39321.1613 | 6393.1555 | 36.0556 | 32891.9501 | 39334.373 | 0 | 0 | 39334.373 | 0.0001986%
2026 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 8.8214 | 157 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 113.3698 | 9.1133 | 12.44 | 113.3698 | 9.1133 | 12.44 | 119.4273 | 9.6002 | 12.44 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2026 | 595 | CB 595 | Tier-1 | Non-HFTD---17 | 1--2 | 0.39361 | 33 | 100% | 1.0072 | 61.92% | 0% | 38.08% | 0.030872 | 0 | 0 | 0.030872 | 0 | 0.029449 | 0.40663 | 0.072423 | 0.029449 | 0.40663 | 0.072423 | 0.031023 | 0.42836 | 0.072423 | 3.065% | 0.0014016 | 0.0013322 | 718.595 | 0.6485 | 467.1224 | 250.8241 | 732.8449 | 0 | 0 | 732.8449 | 1.018e-06%
2026 | 308 | CB 308 | Tier-2 | Tier-2---18 | 4--3 | 2.3447 | 90 | 100% | 77.7948 | 18.36% | 79.79% | 1.851% | 0.70708 | 0 | 0 | 0.70708 | 0 | 0.6745 | 2.4223 | 0.27846 | 0.6745 | 2.4223 | 0.27846 | 0.71054 | 2.5517 | 0.27846 | 0.9089% | 0.037941 | 0.036063 | 2050.437 | 12.1248 | 1817.8081 | 220.5041 | 2137.6123 | 0 | 0 | 2137.6123 | 2.332e-05%
2026 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 24.8581 | 458 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 479.8394 | 25.6807 | 18.6848 | 479.8394 | 25.6807 | 18.6848 | 505.4779 | 27.0529 | 18.6848 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2026 | 310 | 310-1194F | Tier-1 | Non-HFTD---19 | 1--1 | 0.20307 | 2 | 100% | 0.28675 | 29.07% | 0% | 70.93% | 0.0041261 | 0 | 0 | 0.0041261 | 0 | 0.003936 | 0.20979 | 0.018761 | 0.003936 | 0.20979 | 0.018761 | 0.0041463 | 0.221 | 0.018761 | 1.439% | 0.000692 | 0.00065775 | 414.3715 | 2.4094 | 133.3051 | 278.6571 | 429.678 | 0 | 0 | 429.678 | 1.361e-07%
2026 | 187 | CB 187 | Tier-1 | Non-HFTD---7 | 3--3 | 5.4221 | 206 | 100% | 43.4605 | 90.51% | 0% | 9.49% | 1.9471 | 0 | 0 | 1.9471 | 0 | 1.8574 | 5.6016 | 0.33159 | 1.8574 | 5.6016 | 0.33159 | 1.9567 | 5.9009 | 0.33159 | 4.48% | 0.017469 | 0.016605 | 2487.8091 | 217.7975 | 1012.4115 | 1257.6001 | 2500.1043 | 0 | 0 | 2500.1043 | 6.421e-05%
2026 | 241 | 241-746 | Tier-1 | Non-HFTD---2 | 5--3 | 0.38732 | 13 | 100% | 290.9824 | 9.93% | 90% | 0.07278% | 1.4303 | 0 | 0 | 1.4303 | 0 | 1.3644 | 0.40013 | 3.4099 | 1.3644 | 0.40013 | 3.4099 | 1.4373 | 0.42151 | 3.4099 | 0.4915% | 0.098458 | 0.093584 | 2955.4024 | 47.8838 | 2441.1448 | 466.3738 | 3094.0296 | 0 | 0 | 3094.0296 | 4.717e-05%
2026 | 312 | 312-40F | Tier-2 | Tier-2---20 | 3--2 | 0.089352 | 2 | 100% | 9.4163 | 0.07625% | 99.1% | 0.8244% | 0.00035539 | 0 | 0 | 0.00035539 | 0 | 0.00033902 | 0.092308 | 0.0036727 | 0.00033902 | 0.092308 | 0.0036727 | 0.00035713 | 0.097241 | 0.0036727 | 0.003774% | 0.017172 | 0.016322 | 548.3384 | 0.98367 | 493.2185 | 54.1362 | 576.8729 | 0 | 0 | 576.8729 | 1.172e-08%
2026 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.95666 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 58.5262 | 0.98832 | 59.2179 | 58.5262 | 0.98832 | 59.2179 | 61.6533 | 1.0411 | 59.2179 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2026 | 172 | 172-569R | Tier-1 | Non-HFTD---3 | 5--2 | 17.4465 | 526 | 100% | 174.5806 | 70.22% | 23.82% | 5.957% | 6.0684 | 0 | 0 | 6.0684 | 0 | 5.7888 | 18.0239 | 0.32117 | 5.7888 | 18.0239 | 0.32117 | 6.0981 | 18.987 | 0.32117 | 3.476% | 0.12865 | 0.12229 | 1356.9713 | 139.4703 | 376.51 | 840.9911 | 1378.015 | 0 | 0 | 1378.015 | 0.0002001%
2026 | 241 | CB 241 | Tier-2 | Tier-2---11 | 5--4 | 3.3744 | 106 | 100% | 614.4843 | 5.233% | 94.45% | 0.3166% | 1.5918 | 0 | 0 | 1.5918 | 0 | 1.5184 | 3.4861 | 0.43557 | 1.5184 | 3.4861 | 0.43557 | 1.5996 | 3.6723 | 0.43557 | 0.259% | 0.096356 | 0.091586 | 6377.2296 | 31.8975 | 5684.1218 | 661.2103 | 6691.9621 | 0 | 0 | 6691.9621 | 5.249e-05%
2026 | 170 | 170-410R | Tier-1 | Non-HFTD---8 | 5--1 | 12.3119 | 668 | 100% | 29.1667 | 31.01% | 45.41% | 23.57% | 0.44774 | 0 | 0 | 0.44774 | 0 | 0.42711 | 12.7193 | 0.03358 | 0.42711 | 12.7193 | 0.03358 | 0.44993 | 13.399 | 0.03358 | 1.535% | 0.10336 | 0.098244 | 282.1845 | 8.474 | 122.6089 | 151.1016 | 292.3227 | 0 | 0 | 292.3227 | 1.476e-05%
2026 | 90 | 90-50F | Tier-1 | Non-HFTD---9 | 2--3 | 0.94068 | 4 | 100% | 23.5914 | 2.577% | 94.35% | 3.073% | 0.030095 | 0 | 0 | 0.030095 | 0 | 0.028708 | 0.97181 | 0.029541 | 0.028708 | 0.97181 | 0.029541 | 0.030242 | 1.0237 | 0.029541 | 0.1276% | 0.0077394 | 0.0073563 | 3048.2262 | 3.32 | 2713.4595 | 331.4467 | 3202.8802 | 0 | 0 | 3202.8802 | 9.924e-07%
2026 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 17.8821 | 16 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 58.5338 | 18.4738 | 3.1685 | 58.5338 | 18.4738 | 3.1685 | 61.6614 | 19.4609 | 3.1685 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2026 | 453 | CB 453 | Tier-1 | Non-HFTD---8 | 3--3 | 4.5977 | 103 | 100% | 31.0059 | 88.32% | 0% | 11.68% | 1.3556 | 0 | 0 | 1.3556 | 0 | 1.2932 | 4.7499 | 0.27225 | 1.2932 | 4.7499 | 0.27225 | 1.3622 | 5.0037 | 0.27225 | 4.372% | 0.01456 | 0.013839 | 2129.5572 | 0.18709 | 1903.5138 | 225.8563 | 2142.5053 | 0 | 0 | 2142.5053 | 4.47e-05%
2026 | 57 | 57-1291F | Tier-1 | Non-HFTD---8 | 3--3 | 1.8095 | 10 | 100% | 33.0087 | 0.7107% | 94.92% | 4.37% | 0.011612 | 0 | 0 | 0.011612 | 0 | 0.011077 | 1.8694 | 0.0059255 | 0.011077 | 1.8694 | 0.0059255 | 0.011669 | 1.9693 | 0.0059255 | 0.03518% | 0.016049 | 0.015255 | 2056.6925 | 2.488 | 1785.8176 | 268.3869 | 2163.0395 | 0 | 0 | 2163.0395 | 3.829e-07%
2026 | RS1 | CB RS1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.6957 | 45 | 100% | 1.4439 | 25.65% | 0% | 74.35% | 0.018335 | 0 | 0 | 0.018335 | 0 | 0.017491 | 1.7518 | 0.0099844 | 0.017491 | 1.7518 | 0.0099844 | 0.018425 | 1.8454 | 0.0099844 | 1.27% | 0.0049182 | 0.0046747 | 293.5883 | 8.0472 | 47.0121 | 238.5291 | 304.9556 | 0 | 0 | 304.9556 | 6.046e-07%
2026 | 1140 | 1140-8F | Tier-1 | Non-HFTD---3 | 5--2 | 1.0602 | 12 | 100% | 97.4471 | 0.5522% | 98.8% | 0.6432% | 0.026634 | 0 | 0 | 0.026634 | 0 | 0.025407 | 1.0953 | 0.023196 | 0.025407 | 1.0953 | 0.023196 | 0.026765 | 1.1539 | 0.023196 | 0.02733% | 0.10414 | 0.098982 | 935.7622 | 1.7163 | 839.5416 | 94.5043 | 984.2256 | 0 | 0 | 984.2256 | 8.783e-07%
2026 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 0.050947 | 7 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.83481 | 0.052633 | 15.8609 | 0.83481 | 0.052633 | 15.8609 | 0.87941 | 0.055445 | 15.8609 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2026 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 3.232 | 294 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 175.0725 | 3.3389 | 52.4338 | 175.0725 | 3.3389 | 52.4338 | 184.4269 | 3.5173 | 52.4338 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2026 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 3.7312 | 271 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 18.1434 | 3.8547 | 4.7068 | 18.1434 | 3.8547 | 4.7068 | 19.1128 | 4.0607 | 4.7068 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2026 | 192 | CB 192 | Tier-1 | Non-HFTD---4 | 3--4 | 4.2902 | 298 | 100% | 109.5816 | 97.38% | 0% | 2.615% | 5.2824 | 0 | 0 | 5.2824 | 0 | 5.0391 | 4.4322 | 1.1369 | 5.0391 | 4.4322 | 1.1369 | 5.3083 | 4.669 | 1.1369 | 4.821% | 0.015026 | 0.014282 | 7292.705 | 958.338 | 2325.7233 | 4008.6436 | 7302.6378 | 0 | 0 | 7302.6378 | 0.0001742%
2026 | 320 | 320-1414 | Tier-1 | Non-HFTD---16 | 2--1 | 3.7206 | 70 | 100% | 2.9348 | 21.11% | 0% | 78.89% | 0.030668 | 0 | 0 | 0.030668 | 0 | 0.029255 | 3.8438 | 0.0076111 | 0.029255 | 3.8438 | 0.0076111 | 0.030818 | 4.0491 | 0.0076111 | 1.045% | 0.009875 | 0.0093862 | 297.1976 | 1.2363 | 77.5699 | 218.3914 | 309.4077 | 0 | 0 | 309.4077 | 1.011e-06%
2026 | 181 | 181-53F | Tier-1 | Non-HFTD---2 | 4--3 | 1.2419 | 70 | 100% | 294.6229 | 16.95% | 82.71% | 0.3308% | 2.4727 | 0 | 0 | 2.4727 | 0 | 2.3588 | 1.283 | 1.8385 | 2.3588 | 1.283 | 1.8385 | 2.4848 | 1.3516 | 1.8385 | 0.8393% | 0.081527 | 0.077492 | 3613.7987 | 100.59 | 2747.4951 | 765.7137 | 3770.0887 | 0 | 0 | 3770.0887 | 8.154e-05%
2026 | 555 | 555-21F | Tier-1 | Non-HFTD---19 | 1--3 | 0.052273 | 1 | 100% | 0.45337 | 83.79% | 0% | 16.21% | 0.018804 | 0 | 0 | 0.018804 | 0 | 0.017937 | 0.054003 | 0.33216 | 0.017937 | 0.054003 | 0.33216 | 0.018896 | 0.056888 | 0.33216 | 4.147% | 0.0002394 | 0.00022755 | 1893.7858 | 169.5298 | 576.4627 | 1147.7933 | 1909.7752 | 0 | 0 | 1909.7752 | 6.201e-07%
2026 | 458 | 458-44F | Tier-1 | Non-HFTD---17 | 1--2 | 0.18371 | 11 | 100% | 0.70314 | 61.18% | 0% | 38.82% | 0.021295 | 0 | 0 | 0.021295 | 0 | 0.020314 | 0.18979 | 0.10703 | 0.020314 | 0.18979 | 0.10703 | 0.021399 | 0.19993 | 0.10703 | 3.028% | 0.0008354 | 0.00079405 | 841.684 | 0.51996 | 542.8689 | 298.2952 | 858.6993 | 0 | 0 | 858.6993 | 7.022e-07%
2026 | 311 | 311-1163F | Tier-2 | Tier-2---18 | 3--3 | 0.65624 | 7 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9366 | 0 | 0 | 1.9366 | 0 | 1.8474 | 0.67796 | 2.725 | 1.8474 | 0.67796 | 2.725 | 1.9461 | 0.71419 | 2.725 | 4.192% | 0.018623 | 0.017701 | 2480.5668 | 274.9764 | 742.9932 | 1462.5972 | 2500.341 | 0 | 0 | 2500.341 | 6.386e-05%
2026 | 223 | 223-526R | Tier-1 | Non-HFTD---5 | 2--4 | 2.4396 | 32 | 100% | 76.1007 | 97.65% | 0% | 2.35% | 3.6784 | 0 | 0 | 3.6784 | 0 | 3.509 | 2.5203 | 1.3923 | 3.509 | 2.5203 | 1.3923 | 3.6965 | 2.655 | 1.3923 | 4.834% | 0.0098876 | 0.0093982 | 7696.5754 | 1180.4544 | 230.1408 | 6285.9802 | 7705.9964 | 0 | 0 | 7705.9964 | 0.0001213%
2026 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 6.96 | 556 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 45.4 | 7.1903 | 6.314 | 45.4 | 7.1903 | 6.314 | 47.8258 | 7.5745 | 6.314 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2026 | 902 | 902-48 | Tier-1 | Non-HFTD---11 | 2--2 | 3.1718 | 231 | 100% | 11.2569 | 82.99% | 0% | 17.01% | 0.46241 | 0 | 0 | 0.46241 | 0 | 0.44111 | 3.2767 | 0.13462 | 0.44111 | 3.2767 | 0.13462 | 0.46468 | 3.4518 | 0.13462 | 4.108% | 0.0088092 | 0.0083731 | 1277.8565 | 141.3697 | 477.3616 | 659.1252 | 1289.1791 | 0 | 0 | 1289.1791 | 1.525e-05%
2026 | MT1 | CB MT1 | Tier-1 | Non-HFTD---12 | 3--2 | 6.3385 | 192 | 100% | 10.6593 | 55.29% | 0% | 44.71% | 0.29175 | 0 | 0 | 0.29175 | 0 | 0.27831 | 6.5482 | 0.042502 | 0.27831 | 6.5482 | 0.042502 | 0.29318 | 6.8981 | 0.042502 | 2.737% | 0.019313 | 0.018357 | 551.9219 | 0.89395 | 324.0932 | 226.9347 | 564.7715 | 0 | 0 | 564.7715 | 9.621e-06%
2026 | 733 | CB 733 | Tier-1 | Non-HFTD---8 | 3--3 | 5.8684 | 166 | 100% | 28.3507 | 85.6% | 0% | 14.4% | 1.2013 | 0 | 0 | 1.2013 | 0 | 1.1459 | 6.0626 | 0.18902 | 1.1459 | 6.0626 | 0.18902 | 1.2072 | 6.3865 | 0.18902 | 4.237% | 0.016335 | 0.015526 | 1735.6201 | 10.6405 | 1444.5417 | 280.4379 | 1748.6355 | 0 | 0 | 1748.6355 | 3.961e-05%
2026 | 1103 | 1103-13AE | Tier-2 | Tier-2---17 | 1--5 | 0.27027 | 9 | 100% | 94.4662 | 99.77% | 0% | 0.2344% | 4.6651 | 0 | 0 | 4.6651 | 0 | 4.4502 | 0.27921 | 15.9386 | 4.4502 | 0.27921 | 15.9386 | 4.688 | 0.29413 | 15.9386 | 4.938% | 0.001345 | 0.0012784 | 70235.1135 | 11425.6816 | 17.29 | 58792.1418 | 70243.6865 | 0 | 0 | 70243.6865 | 0.0001538%
2026 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.092045 | 6 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.8484 | 0.095092 | 124.6004 | 11.8484 | 0.095092 | 124.6004 | 12.4815 | 0.10017 | 124.6004 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2026 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 6.3104 | 290 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 5.3672 | 6.5192 | 0.82329 | 5.3672 | 6.5192 | 0.82329 | 5.654 | 6.8675 | 0.82329 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2026 | 417 | CB 417 | Tier-1 | Non-HFTD---3 | 3--3 | 4.8645 | 180 | 100% | 116.5397 | 41.56% | 55.34% | 3.097% | 2.3977 | 0 | 0 | 2.3977 | 0 | 2.2872 | 5.0255 | 0.45512 | 2.2872 | 5.0255 | 0.45512 | 2.4094 | 5.294 | 0.45512 | 2.057% | 0.025451 | 0.024191 | 4579.0552 | 115.5393 | 3554.7727 | 908.7432 | 4718.4081 | 0 | 0 | 4718.4081 | 7.907e-05%
2026 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 2.0774 | 267 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 117.9754 | 2.1462 | 54.9702 | 117.9754 | 2.1462 | 54.9702 | 124.279 | 2.2608 | 54.9702 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2026 | RE1 | CB RE1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.5885 | 32 | 100% | 1.1035 | 28.77% | 0% | 71.23% | 0.015712 | 0 | 0 | 0.015712 | 0 | 0.014989 | 1.641 | 0.0091336 | 0.014989 | 1.641 | 0.0091336 | 0.015789 | 1.7287 | 0.0091336 | 1.424% | 0.0036542 | 0.0034733 | 301.9742 | 0.23132 | 105.981 | 195.762 | 313.1767 | 0 | 0 | 313.1767 | 5.181e-07%
2026 | 900 | 900-1166F | Tier-1 | Non-HFTD---7 | 1--4 | 1.1814 | 97 | 100% | 30.0591 | 97.43% | 0% | 2.568% | 1.4497 | 0 | 0 | 1.4497 | 0 | 1.3829 | 1.2205 | 1.1331 | 1.3829 | 1.2205 | 1.1331 | 1.4568 | 1.2857 | 1.1331 | 4.823% | 0.003966 | 0.0037697 | 7579.2001 | 1157.8569 | 322.158 | 6099.1853 | 7589.3359 | 0 | 0 | 7589.3359 | 4.781e-05%
2026 | 44 | 44-1101F | Tier-1 | Non-HFTD---16 | 2--1 | 2.2459 | 60 | 100% | 2.701 | 28.07% | 0% | 71.93% | 0.037524 | 0 | 0 | 0.037524 | 0 | 0.035795 | 2.3202 | 0.015428 | 0.035795 | 2.3202 | 0.015428 | 0.037707 | 2.4442 | 0.015428 | 1.389% | 0.0069664 | 0.0066216 | 387.7182 | 2.2876 | 121.4718 | 263.9588 | 402.2428 | 0 | 0 | 402.2428 | 1.237e-06%
2026 | 149 | CB 149 | Tier-1 | Non-HFTD---9 | 1--4 | 0.88352 | 8 | 100% | 21.25 | 97.47% | 0% | 2.53% | 1.0253 | 0 | 0 | 1.0253 | 0 | 0.97803 | 0.91276 | 1.0715 | 0.97803 | 0.91276 | 1.0715 | 1.0303 | 0.96153 | 1.0715 | 4.825% | 0.0036132 | 0.0034343 | 5881.2185 | 1195.3712 | 13.6562 | 4672.1912 | 5888.968 | 0 | 0 | 5888.968 | 3.381e-05%
2026 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 7.3706 | 429 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 861.5285 | 7.6146 | 113.1423 | 861.5285 | 7.6146 | 113.1423 | 907.5611 | 8.0214 | 113.1423 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2026 | 153 | CB 153 | Tier-1 | Non-HFTD---6 | 4--2 | 14.7847 | 313 | 100% | 50.6159 | 80.4% | 0% | 19.6% | 2.0143 | 0 | 0 | 2.0143 | 0 | 1.9215 | 15.2739 | 0.1258 | 1.9215 | 15.2739 | 0.1258 | 2.0242 | 16.09 | 0.1258 | 3.98% | 0.04186 | 0.039788 | 1209.1779 | 2.388 | 984.9183 | 221.8717 | 1221.5227 | 0 | 0 | 1221.5227 | 6.642e-05%
2026 | 545 | 545-47F | Tier-1 | Non-HFTD---4 | 3--4 | 2.6369 | 24 | 100% | 110.9793 | 1.36% | 96.25% | 2.393% | 0.074705 | 0 | 0 | 0.074705 | 0 | 0.071264 | 2.7242 | 0.02616 | 0.071264 | 2.7242 | 0.02616 | 0.075072 | 2.8697 | 0.02616 | 0.06731% | 0.019055 | 0.018112 | 5824.1558 | 6.8519 | 5193.1991 | 624.1048 | 6123.3406 | 0 | 0 | 6123.3406 | 2.464e-06%
2026 | 416 | 416-37F | Tier-1 | Non-HFTD---17 | 1--1 | 1.2439 | 52 | 100% | 1.7227 | 46.57% | 0% | 53.43% | 0.039708 | 0 | 0 | 0.039708 | 0 | 0.037879 | 1.2851 | 0.029476 | 0.037879 | 1.2851 | 0.029476 | 0.039903 | 1.3538 | 0.029476 | 2.305% | 0.0035008 | 0.0033275 | 492.0848 | 1.381 | 245.7278 | 244.9761 | 505.7782 | 0 | 0 | 505.7782 | 1.309e-06%
2026 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 1.2638 | 89 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 26.6692 | 1.3056 | 20.426 | 26.6692 | 1.3056 | 20.426 | 28.0941 | 1.3754 | 20.426 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2026 | 276 | CB 276 | Tier-1 | Non-HFTD---10 | 3--2 | 1.2919 | 18 | 100% | 26.0793 | 53.94% | 42.4% | 3.659% | 0.69637 | 0 | 0 | 0.69637 | 0 | 0.66429 | 1.3346 | 0.49774 | 0.66429 | 1.3346 | 0.49774 | 0.69979 | 1.4059 | 0.49774 | 2.67% | 0.01954 | 0.018573 | 1334.6469 | 19.5495 | 1128.3922 | 186.7052 | 1366.6586 | 0 | 0 | 1366.6586 | 2.296e-05%
2026 | 107 | CB 107 | Tier-1 | Non-HFTD---13 | 2--2 | 1.8139 | 62 | 100% | 5.6413 | 73.95% | 0% | 26.05% | 0.2065 | 0 | 0 | 0.2065 | 0 | 0.19698 | 1.8739 | 0.10512 | 0.19698 | 1.8739 | 0.10512 | 0.20751 | 1.974 | 0.10512 | 3.66% | 0.005587 | 0.0053104 | 1009.7148 | 3.394 | 755.2275 | 251.0933 | 1023.4136 | 0 | 0 | 1023.4136 | 6.809e-06%
2026 | FM1 | CB FM1 | Tier-1 | Non-HFTD---8 | 3--3 | 4.6271 | 262 | 100% | 36.2346 | 19.67% | 69.95% | 10.38% | 0.35276 | 0 | 0 | 0.35276 | 0 | 0.33651 | 4.7803 | 0.070397 | 0.33651 | 4.7803 | 0.070397 | 0.35449 | 5.0357 | 0.070397 | 0.9736% | 0.019823 | 0.018842 | 1827.9252 | 40.3343 | 1310.0854 | 477.5055 | 1904.3969 | 0 | 0 | 1904.3969 | 1.163e-05%
2026 | 1418 | 1418-581R | Tier-1 | Non-HFTD---13 | 2--2 | 1.5783 | 24 | 100% | 5.0692 | 77.2% | 0% | 22.8% | 0.19371 | 0 | 0 | 0.19371 | 0 | 0.18478 | 1.6305 | 0.11333 | 0.18478 | 1.6305 | 0.11333 | 0.19466 | 1.7176 | 0.11333 | 3.821% | 0.0055174 | 0.0052443 | 918.7654 | 53.7653 | 399.6633 | 465.3367 | 929.6757 | 0 | 0 | 929.6757 | 6.388e-06%
2026 | BK2 | CB BK2 | Tier-1 | Non-HFTD---9 | 3--3 | 1.5103 | 31 | 100% | 25.856 | 1.714% | 93.1% | 5.186% | 0.021942 | 0 | 0 | 0.021942 | 0 | 0.020931 | 1.5603 | 0.013415 | 0.020931 | 1.5603 | 0.013415 | 0.022049 | 1.6436 | 0.013415 | 0.08486% | 0.015094 | 0.014347 | 1712.9776 | 1.9461 | 1498.4147 | 212.6168 | 1800.6564 | 0 | 0 | 1800.6564 | 7.236e-07%
2026 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 10.606 | 589 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 277.4933 | 10.957 | 25.3256 | 277.4933 | 10.957 | 25.3256 | 292.3202 | 11.5425 | 25.3256 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2026 | 718 | CB 718 | Tier-1 | Non-HFTD---18 | 2--1 | 1.4828 | 46 | 100% | 2.2312 | 31.13% | 0% | 68.87% | 0.034382 | 0 | 0 | 0.034382 | 0 | 0.032798 | 1.5319 | 0.021411 | 0.032798 | 1.5319 | 0.021411 | 0.034551 | 1.6137 | 0.021411 | 1.541% | 0.0057306 | 0.0054469 | 389.3448 | 10.2878 | 84.1668 | 294.8901 | 403.3088 | 0 | 0 | 403.3088 | 1.134e-06%
2026 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 12.5079 | 454 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1750.5765 | 12.9218 | 135.4742 | 1750.5765 | 12.9218 | 135.4742 | 1844.1122 | 13.6123 | 135.4742 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2026 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 9.0746 | 469 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 227.6349 | 9.3749 | 24.2813 | 227.6349 | 9.3749 | 24.2813 | 239.7978 | 9.8758 | 24.2813 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2026 | 364 | 364-49R | Tier-1 | Non-HFTD---3 | 4--3 | 10.7492 | 161 | 100% | 138.1668 | 14.34% | 80.38% | 5.28% | 0.98106 | 0 | 0 | 0.98106 | 0 | 0.93586 | 11.1049 | 0.084274 | 0.93586 | 11.1049 | 0.084274 | 0.98587 | 11.6983 | 0.084274 | 0.7101% | 0.035529 | 0.033771 | 3888.8227 | 11.2159 | 3396.2712 | 481.3356 | 4062.2935 | 0 | 0 | 4062.2935 | 3.235e-05%
2026 | 154 | 154-13 | Tier-1 | Non-HFTD---20 | 1--1 | 0.50816 | 9 | 100% | 0.28839 | 3.646% | 0% | 96.35% | 0.00052053 | 0 | 0 | 0.00052053 | 0 | 0.00049655 | 0.52497 | 0.00094586 | 0.00049655 | 0.52497 | 0.00094586 | 0.00052308 | 0.55302 | 0.00094586 | 0.1805% | 0.0014332 | 0.0013623 | 201.2217 | 0.14589 | 24.9499 | 176.1259 | 211.3187 | 0 | 0 | 211.3187 | 1.717e-08%
2026 | 902 | 902-364F | Tier-1 | Non-HFTD---15 | 1--4 | 0.10985 | 8 | 100% | 3.0036 | 96.46% | 0% | 3.536% | 0.14342 | 0 | 0 | 0.14342 | 0 | 0.13682 | 0.11348 | 1.2056 | 0.13682 | 0.11348 | 1.2056 | 0.14413 | 0.11955 | 1.2056 | 4.775% | 0.0004588 | 0.00043609 | 6546.743 | 1491.2109 | 21.0318 | 5034.5003 | 6558.8002 | 0 | 0 | 6558.8002 | 4.73e-06%
2026 | 144 | CB 144 | Tier-1 | Non-HFTD---3 | 3--4 | 4.3479 | 193 | 100% | 116.3493 | 70.7% | 26.46% | 2.846% | 4.0717 | 0 | 0 | 4.0717 | 0 | 3.8841 | 4.4918 | 0.86472 | 3.8841 | 4.4918 | 0.86472 | 4.0917 | 4.7318 | 0.86472 | 3.5% | 0.021258 | 0.020206 | 5473.2508 | 269.7276 | 3553.0613 | 1650.4619 | 5556.7709 | 0 | 0 | 5556.7709 | 0.0001343%
2026 | 146 | 146-275R | Tier-1 | Non-HFTD---5 | 2--4 | 0.74015 | 44 | 100% | 50.1764 | 31.43% | 67.56% | 1.005% | 0.78065 | 0 | 0 | 0.78065 | 0 | 0.74468 | 0.76465 | 0.97389 | 0.74468 | 0.76465 | 0.97389 | 0.78447 | 0.8055 | 0.97389 | 1.556% | 0.0089436 | 0.0085009 | 5610.3123 | 271.1706 | 3574.616 | 1764.5257 | 5810.6541 | 0 | 0 | 5810.6541 | 2.574e-05%
2026 | 289 | 289-1559 | Tier-1 | Non-HFTD---15 | 2--2 | 0.52288 | 72 | 100% | 4.417 | 3.139% | 88.74% | 8.122% | 0.0068636 | 0 | 0 | 0.0068636 | 0 | 0.0065474 | 0.54018 | 0.012121 | 0.0065474 | 0.54018 | 0.012121 | 0.0068973 | 0.56904 | 0.012121 | 0.1554% | 0.0072536 | 0.0068945 | 608.9324 | 2.7259 | 506.3554 | 99.851 | 639.6487 | 0 | 0 | 639.6487 | 2.263e-07%
2026 | 138 | CB 138 | Tier-1 | Non-HFTD---17 | 1--2 | 0.18636 | 2 | 100% | 0.7202 | 42.47% | 0% | 57.53% | 0.01514 | 0 | 0 | 0.01514 | 0 | 0.014443 | 0.19253 | 0.075016 | 0.014443 | 0.19253 | 0.075016 | 0.015215 | 0.20282 | 0.075016 | 2.102% | 0.0010424 | 0.0009908 | 690.9099 | 0.2991 | 329.5323 | 361.0785 | 711.6101 | 0 | 0 | 711.6101 | 4.993e-07%
2026 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 6.479 | 1292 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 182.2481 | 6.6934 | 27.2281 | 182.2481 | 6.6934 | 27.2281 | 191.9859 | 7.051 | 27.2281 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2026 | PL2 | CB PL2 | Tier-1 | Non-HFTD---12 | 3--2 | 9.8748 | 367 | 100% | 14.4457 | 51.29% | 0% | 48.71% | 0.36674 | 0 | 0 | 0.36674 | 0 | 0.34985 | 10.2016 | 0.034293 | 0.34985 | 10.2016 | 0.034293 | 0.36854 | 10.7466 | 0.034293 | 2.539% | 0.027084 | 0.025743 | 533.3741 | 0.1955 | 297.1585 | 236.0201 | 546.9048 | 0 | 0 | 546.9048 | 1.209e-05%
2026 | 209 | CB 209 | Tier-1 | Non-HFTD---15 | 1--3 | 0.2739 | 2 | 100% | 2.9977 | 95.12% | 0% | 4.884% | 0.14114 | 0 | 0 | 0.14114 | 0 | 0.13464 | 0.28297 | 0.4758 | 0.13464 | 0.28297 | 0.4758 | 0.14183 | 0.29809 | 0.4758 | 4.708% | 0.000675 | 0.00064159 | 4441.0443 | 20.5708 | 4119.0788 | 301.3948 | 4452.339 | 0 | 0 | 4452.339 | 4.654e-06%
2026 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 3.9579 | 58 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 120.3488 | 4.0889 | 29.433 | 120.3488 | 4.0889 | 29.433 | 126.7793 | 4.3074 | 29.433 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2026 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.62576 | 81 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 10.0309 | 0.64647 | 15.5165 | 10.0309 | 0.64647 | 15.5165 | 10.5669 | 0.68101 | 15.5165 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2026 | 415 | 415-1237R | Tier-1 | Non-HFTD---3 | 4--3 | 9.2329 | 453 | 100% | 133.0958 | 12.64% | 83.05% | 4.312% | 0.83274 | 0 | 0 | 0.83274 | 0 | 0.79438 | 9.5385 | 0.083282 | 0.79438 | 9.5385 | 0.083282 | 0.83683 | 10.0481 | 0.083282 | 0.6257% | 0.037795 | 0.035924 | 3521.4997 | 33.7505 | 3007.5656 | 480.1837 | 3681.7114 | 0 | 0 | 3681.7114 | 2.746e-05%
2026 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 1.165 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 68.9354 | 1.2036 | 57.2759 | 68.9354 | 1.2036 | 57.2759 | 72.6187 | 1.2679 | 57.2759 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2026 | WA6 | CB WA6 | Tier-1 | Non-HFTD---8 | 4--2 | 13.9047 | 410 | 100% | 38.8392 | 75.37% | 0% | 24.63% | 1.4489 | 0 | 0 | 1.4489 | 0 | 1.3822 | 14.3649 | 0.09622 | 1.3822 | 14.3649 | 0.09622 | 1.456 | 15.1324 | 0.09622 | 3.731% | 0.043551 | 0.041395 | 891.8131 | 93.2124 | 376.5501 | 422.0507 | 903.2543 | 0 | 0 | 903.2543 | 4.778e-05%
2026 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 20.7706 | 2370 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 310.9519 | 21.458 | 14.4912 | 310.9519 | 21.458 | 14.4912 | 327.5665 | 22.6045 | 14.4912 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2026 | 284 | 284-660R | Tier-1 | Non-HFTD---5 | 2--4 | 0.21894 | 31 | 100% | 67.7111 | 37.42% | 62.28% | 0.3086% | 1.2541 | 0 | 0 | 1.2541 | 0 | 1.1963 | 0.22618 | 5.2891 | 1.1963 | 0.22618 | 5.2891 | 1.2602 | 0.23827 | 5.2891 | 1.852% | 0.0068676 | 0.0065277 | 9859.4941 | 664.3708 | 5544.4409 | 3650.6824 | 10180.8369 | 0 | 0 | 10180.8369 | 4.136e-05%
2026 | 856 | 856-1141R | Tier-1 | Non-HFTD---7 | 2--3 | 3.289 | 191 | 100% | 34.972 | 93.55% | 0% | 6.449% | 1.6195 | 0 | 0 | 1.6195 | 0 | 1.5449 | 3.3979 | 0.45466 | 1.5449 | 3.3979 | 0.45466 | 1.6274 | 3.5794 | 0.45466 | 4.631% | 0.0095222 | 0.0090509 | 3672.677 | 493.2945 | 440.7828 | 2738.5997 | 3685.0115 | 0 | 0 | 3685.0115 | 5.34e-05%
2026 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 7.0073 | 245 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 96.5805 | 7.2392 | 13.3412 | 96.5805 | 7.2392 | 13.3412 | 101.7409 | 7.626 | 13.3412 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2026 | 1001 | 1001-1232F | Tier-1 | Non-HFTD---15 | 1--4 | 0.060606 | 13 | 100% | 3.7082 | 98.25% | 0% | 1.746% | 0.18035 | 0 | 0 | 0.18035 | 0 | 0.17204 | 0.062612 | 2.7477 | 0.17204 | 0.062612 | 2.7477 | 0.18123 | 0.065957 | 2.7477 | 4.864% | 0.0002536 | 0.00024105 | 14622.1214 | 2186.2186 | 960.6365 | 11475.2662 | 14635.4188 | 0 | 0 | 14635.4188 | 5.947e-06%
2026 | 789 | 789-15 | Tier-1 | Non-HFTD---1 | 1--5 | 1.1117 | 192 | 100% | 761.9806 | 99.91% | 0% | 0.08626% | 37.6855 | 0 | 0 | 37.6855 | 0 | 35.9494 | 1.1485 | 31.3008 | 35.9494 | 1.1485 | 31.3008 | 37.8702 | 1.2099 | 31.3008 | 4.946% | 0.0041662 | 0.00396 | 182895.8194 | 29633.7506 | 30.7403 | 153231.3285 | 182904.0354 | 0 | 0 | 182904.0354 | 0.001243%
2026 | 854 | CB 854 | Tier-1 | Non-HFTD---15 | 1--3 | 0.2767 | 0 | 100% | 4.0846 | 92.31% | 0% | 7.692% | 0.18664 | 0 | 0 | 0.18664 | 0 | 0.17804 | 0.28586 | 0.62281 | 0.17804 | 0.28586 | 0.62281 | 0.18755 | 0.30114 | 0.62281 | 4.569% | 0.0011248 | 0.0010691 | 3631.4237 | 108.5173 | 2707.56 | 815.3464 | 3645.9705 | 0 | 0 | 3645.9705 | 6.155e-06%
2026 | AM3 | CB AM3 | Tier-1 | Non-HFTD---12 | 4--1 | 11.0803 | 284 | 100% | 10.6772 | 32.41% | 0% | 67.59% | 0.17131 | 0 | 0 | 0.17131 | 0 | 0.16342 | 11.447 | 0.014276 | 0.16342 | 11.447 | 0.014276 | 0.17215 | 12.0586 | 0.014276 | 1.604% | 0.029862 | 0.028384 | 357.5503 | 0.35634 | 136.7746 | 220.4194 | 370.1352 | 0 | 0 | 370.1352 | 5.649e-06%
2026 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 0.61936 | 96 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.73672 | 0.63986 | 1.1514 | 0.73672 | 0.63986 | 1.1514 | 0.77608 | 0.67405 | 1.1514 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2026 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 10.8632 | 1095 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 478.0277 | 11.2227 | 42.5946 | 478.0277 | 11.2227 | 42.5946 | 503.5694 | 11.8224 | 42.5946 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2026 | 417 | 417-41 | Tier-1 | Non-HFTD---19 | 1--3 | 0.067056 | 2 | 100% | 0.62272 | 87.14% | 0% | 12.86% | 0.02686 | 0 | 0 | 0.02686 | 0 | 0.025623 | 0.069275 | 0.36987 | 0.025623 | 0.069275 | 0.36987 | 0.026992 | 0.072977 | 0.36987 | 4.313% | 0.0002544 | 0.00024181 | 2447.8133 | 0.23691 | 2161.5664 | 286.0099 | 2464.2099 | 0 | 0 | 2464.2099 | 8.857e-07%
2026 | 750 | CB 750 | Tier-1 | Non-HFTD---4 | 1--5 | 1.0979 | 9 | 100% | 147.1702 | 99.68% | 0% | 0.3223% | 7.2614 | 0 | 0 | 7.2614 | 0 | 6.9269 | 1.1343 | 6.1071 | 6.9269 | 1.1343 | 6.1071 | 7.297 | 1.1949 | 6.1071 | 4.934% | 0.0040188 | 0.0038199 | 36620.4268 | 8634.8324 | 1589.051 | 26396.5433 | 36626.5736 | 0 | 0 | 36626.5736 | 0.0002395%
2026 | 547 | CB 547 | Tier-1 | Non-HFTD---9 | 2--3 | 3.8859 | 81 | 100% | 19.4827 | 85.43% | 0% | 14.57% | 0.82389 | 0 | 0 | 0.82389 | 0 | 0.78594 | 4.0145 | 0.19577 | 0.78594 | 4.0145 | 0.19577 | 0.82793 | 4.229 | 0.19577 | 4.229% | 0.011393 | 0.010829 | 1710.1181 | 8.849 | 1430.5531 | 270.716 | 1723.0928 | 0 | 0 | 1723.0928 | 2.717e-05%
2026 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 7.7129 | 412 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 6.0436 | 7.9681 | 0.75848 | 6.0436 | 7.9681 | 0.75848 | 6.3665 | 8.3939 | 0.75848 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2026 | 278 | 278-630 | Tier-1 | Non-HFTD---2 | 4--4 | 10.8269 | 311 | 100% | 273.7142 | 5.715% | 91.87% | 2.413% | 0.77427 | 0 | 0 | 0.77427 | 0 | 0.7386 | 11.1852 | 0.066034 | 0.7386 | 11.1852 | 0.066034 | 0.77806 | 11.7828 | 0.066034 | 0.2829% | 0.044769 | 0.042553 | 6113.9234 | 15.3034 | 5481.2841 | 617.3359 | 6414.1279 | 0 | 0 | 6414.1279 | 2.553e-05%
2026 | 1077 | 1077-8R | Tier-1 | Non-HFTD---9 | 2--3 | 2.8041 | 50 | 100% | 24.3832 | 90.75% | 0% | 9.248% | 1.0954 | 0 | 0 | 1.0954 | 0 | 1.0449 | 2.8969 | 0.36069 | 1.0449 | 2.8969 | 0.36069 | 1.1007 | 3.0517 | 0.36069 | 4.492% | 0.0094446 | 0.0089771 | 2581.7093 | 369.621 | 97.6273 | 2114.461 | 2594.143 | 0 | 0 | 2594.143 | 3.612e-05%
2026 | 780 | CB 780 | Tier-1 | Non-HFTD---6 | 3--3 | 4.5818 | 470 | 100% | 78.9953 | 26.13% | 69.84% | 4.031% | 1.0216 | 0 | 0 | 1.0216 | 0 | 0.97451 | 4.7335 | 0.20588 | 0.97451 | 4.7335 | 0.20588 | 1.0266 | 4.9864 | 0.20588 | 1.293% | 0.024043 | 0.022852 | 3285.6386 | 58.4415 | 2545.5101 | 681.687 | 3412.0448 | 0 | 0 | 3412.0448 | 3.369e-05%
2026 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011932 | 0 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.012327 | 0 | 0 | 0.012327 | 0 | 0 | 0.012985 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2026 | 487 | CB 487 | Tier-1 | Non-HFTD---19 | 1--3 | 0.046212 | 7 | 100% | 0.46682 | 83.57% | 0% | 16.43% | 0.01931 | 0 | 0 | 0.01931 | 0 | 0.018421 | 0.047741 | 0.38584 | 0.018421 | 0.047741 | 0.38584 | 0.019405 | 0.050292 | 0.38584 | 4.136% | 0.0001976 | 0.00018782 | 2362.465 | 321.7419 | 35.2696 | 2005.4535 | 2382.6846 | 0 | 0 | 2382.6846 | 6.368e-07%
2026 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 5.2678 | 335 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 45.8593 | 5.4421 | 8.4267 | 45.8593 | 5.4421 | 8.4267 | 48.3097 | 5.7329 | 8.4267 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2026 | 1073 | 1073-480 | Tier-1 | Non-HFTD---4 | 3--4 | 0.27083 | 8 | 100% | 99.1186 | 2.789% | 97.03% | 0.1826% | 0.13682 | 0 | 0 | 0.13682 | 0 | 0.13051 | 0.2798 | 0.46646 | 0.13051 | 0.2798 | 0.46646 | 0.13749 | 0.29475 | 0.46646 | 0.138% | 0.017172 | 0.016322 | 5772.1746 | 21.6593 | 5192.9171 | 557.5981 | 6064.3945 | 0 | 0 | 6064.3945 | 4.512e-06%
2026 | 400 | CB 400 | Tier-1 | Non-HFTD---10 | 4--2 | 12.2015 | 190 | 100% | 19.3977 | 65.59% | 0% | 34.41% | 0.62975 | 0 | 0 | 0.62975 | 0 | 0.60074 | 12.6053 | 0.047657 | 0.60074 | 12.6053 | 0.047657 | 0.63283 | 13.2788 | 0.047657 | 3.247% | 0.031276 | 0.029728 | 620.2148 | 1.8495 | 419.0813 | 199.284 | 631.3303 | 0 | 0 | 631.3303 | 2.077e-05%
2026 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 9.9971 | 609 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 574.459 | 10.3279 | 55.6218 | 574.459 | 10.3279 | 55.6218 | 605.1531 | 10.8798 | 55.6218 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2026 | 286 | CB 286 | Tier-1 | Non-HFTD---2 | 4--3 | 12.3718 | 1211 | 100% | 207.2412 | 65.65% | 29.54% | 4.807% | 6.7349 | 0 | 0 | 6.7349 | 0 | 6.4246 | 12.7812 | 0.50266 | 6.4246 | 12.7812 | 0.50266 | 6.7679 | 13.4642 | 0.50266 | 3.25% | 0.045864 | 0.043593 | 4518.6432 | 500.9662 | 1809.8664 | 2207.8107 | 4599.4713 | 0 | 0 | 4599.4713 | 0.0002221%
2026 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.93788 | 198 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.1512 | 0.96892 | 3.2523 | 3.1512 | 0.96892 | 3.2523 | 3.3196 | 1.0207 | 3.2523 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2026 | 81 | 81-177AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.11456 | 4 | 100% | 0.23558 | 5.771% | 0% | 94.23% | 0.00067299 | 0 | 0 | 0.00067299 | 0 | 0.00064199 | 0.11835 | 0.0054244 | 0.00064199 | 0.11835 | 0.0054244 | 0.00067629 | 0.12468 | 0.0054244 | 0.2857% | 0.0005608 | 0.00053304 | 420.0857 | 0.29786 | 60.2022 | 359.5856 | 440.7003 | 0 | 0 | 440.7003 | 2.219e-08%
2026 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 14.5858 | 915 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1099.8308 | 15.0685 | 72.9889 | 1099.8308 | 15.0685 | 72.9889 | 1158.5963 | 15.8736 | 72.9889 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2026 | 453 | 453-41 | Tier-1 | Non-HFTD---15 | 1--3 | 0.43601 | 31 | 100% | 2.6009 | 88.95% | 0% | 11.05% | 0.11451 | 0 | 0 | 0.11451 | 0 | 0.10924 | 0.45043 | 0.24252 | 0.10924 | 0.45043 | 0.24252 | 0.11508 | 0.4745 | 0.24252 | 4.403% | 0.0012658 | 0.0012031 | 2054.725 | 0.17088 | 1848.26 | 206.2942 | 2066.5516 | 0 | 0 | 2066.5516 | 3.776e-06%
2026 | 493 | 493-485F | Tier-1 | Non-HFTD---11 | 1--4 | 0.31738 | 26 | 100% | 12.8826 | 97.53% | 0% | 2.467% | 0.62196 | 0 | 0 | 0.62196 | 0 | 0.5933 | 0.32788 | 1.8095 | 0.5933 | 0.32788 | 1.8095 | 0.625 | 0.3454 | 1.8095 | 4.828% | 0.0014534 | 0.0013815 | 8863.7485 | 1806.2326 | 712.2066 | 6345.3093 | 8875.1362 | 0 | 0 | 8875.1362 | 2.051e-05%
2026 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 11.1993 | 195 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 70.6818 | 11.5699 | 6.1091 | 70.6818 | 11.5699 | 6.1091 | 74.4584 | 12.1881 | 6.1091 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2026 | 702 | CB 702 | Tier-1 | Non-HFTD---5 | 2--4 | 1.5752 | 2 | 100% | 63.7539 | 98.86% | 0% | 1.141% | 3.1198 | 0 | 0 | 3.1198 | 0 | 2.9761 | 1.6273 | 1.8288 | 2.9761 | 1.6273 | 1.8288 | 3.1351 | 1.7143 | 1.8288 | 4.894% | 0.005363 | 0.0050975 | 11887.738 | 811.1818 | 6774.97 | 4301.5862 | 11894.8026 | 0 | 0 | 11894.8026 | 0.0001029%
2026 | 94 | CB 94 | Tier-1 | Non-HFTD---5 | 2--4 | 3.3957 | 155 | 100% | 70.2599 | 96.42% | 0% | 3.58% | 3.3534 | 0 | 0 | 3.3534 | 0 | 3.1989 | 3.508 | 0.91187 | 3.1989 | 3.508 | 0.91187 | 3.3698 | 3.6955 | 0.91187 | 4.773% | 0.011842 | 0.011256 | 5932.9129 | 699.7774 | 1458.5408 | 3774.5947 | 5943.974 | 0 | 0 | 5943.974 | 0.0001106%
2026 | 130 | 130-13F | Tier-1 | Non-HFTD---14 | 3--1 | 5.4246 | 122 | 100% | 6.0639 | 48.34% | 0% | 51.66% | 0.14511 | 0 | 0 | 0.14511 | 0 | 0.13842 | 5.6042 | 0.0247 | 0.13842 | 5.6042 | 0.0247 | 0.14582 | 5.9036 | 0.0247 | 2.393% | 0.013826 | 0.013142 | 438.5851 | 0.71643 | 229.2325 | 208.6361 | 450.3837 | 0 | 0 | 450.3837 | 4.785e-06%
2026 | 402 | 402-30AE | Tier-1 | Non-HFTD---14 | 2--2 | 4.5258 | 344 | 100% | 8.257 | 62.04% | 0% | 37.96% | 0.25356 | 0 | 0 | 0.25356 | 0 | 0.24188 | 4.6756 | 0.051732 | 0.24188 | 4.6756 | 0.051732 | 0.2548 | 4.9254 | 0.051732 | 3.071% | 0.013009 | 0.012365 | 634.7125 | 33.2198 | 213.4395 | 388.0532 | 647.261 | 0 | 0 | 647.261 | 8.361e-06%
2026 | 289 | 289-906AE | Tier-1 | Non-HFTD---6 | 3--3 | 3.7338 | 241 | 100% | 60.6322 | 6.027% | 88.86% | 5.111% | 0.1809 | 0 | 0 | 0.1809 | 0 | 0.17256 | 3.8573 | 0.044737 | 0.17256 | 3.8573 | 0.044737 | 0.18178 | 4.0634 | 0.044737 | 0.2984% | 0.017149 | 0.0163 | 3535.6115 | 14.9936 | 2922.6536 | 597.9644 | 3708.6407 | 0 | 0 | 3708.6407 | 5.965e-06%
2026 | S2 | CB S2 | Tier-1 | Non-HFTD---14 | 3--1 | 5.3494 | 53 | 100% | 5.7564 | 31.81% | 0% | 68.19% | 0.090637 | 0 | 0 | 0.090637 | 0 | 0.086462 | 5.5264 | 0.015645 | 0.086462 | 5.5264 | 0.015645 | 0.091081 | 5.8217 | 0.015645 | 1.575% | 0.015094 | 0.014346 | 381.3818 | 0.43885 | 143.4346 | 237.5084 | 394.9256 | 0 | 0 | 394.9256 | 2.989e-06%
2026 | 206 | 206-963F | Tier-1 | Non-HFTD---1 | 3--5 | 4.5674 | 335 | 100% | 308.0085 | 98.9% | 0% | 1.099% | 15.0788 | 0 | 0 | 15.0788 | 0 | 14.3842 | 4.7186 | 3.0484 | 14.3842 | 4.7186 | 3.0484 | 15.1527 | 4.9707 | 3.0484 | 4.896% | 0.014856 | 0.014121 | 20732.6556 | 3229.8813 | 785.6991 | 16717.0751 | 20744.5251 | 0 | 0 | 20744.5251 | 0.0004972%
2026 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 2.5689 | 77 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 192.305 | 2.6539 | 72.4605 | 192.305 | 2.6539 | 72.4605 | 202.5801 | 2.7957 | 72.4605 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2026 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 3.7435 | 267 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.9569 | 3.8674 | 0.506 | 1.9569 | 3.8674 | 0.506 | 2.0615 | 4.074 | 0.506 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2026 | 513 | 513-42F | Tier-1 | Non-HFTD---6 | 4--2 | 0.8341 | 183 | 100% | 92.9137 | 5.505% | 93.9% | 0.5996% | 0.25318 | 0 | 0 | 0.25318 | 0 | 0.24152 | 0.8617 | 0.28028 | 0.24152 | 0.8617 | 0.28028 | 0.25442 | 0.90774 | 0.28028 | 0.2725% | 0.081117 | 0.077102 | 1145.4316 | 12.1451 | 972.7364 | 160.5501 | 1201.7995 | 0 | 0 | 1201.7995 | 8.349e-06%
2026 | 773 | 773-271F | Tier-1 | Non-HFTD---15 | 1--2 | 0.78394 | 74 | 100% | 3.1656 | 79.61% | 0% | 20.39% | 0.12475 | 0 | 0 | 0.12475 | 0 | 0.119 | 0.80988 | 0.14694 | 0.119 | 0.80988 | 0.14694 | 0.12536 | 0.85316 | 0.14694 | 3.941% | 0.0028064 | 0.0026675 | 1127.9942 | 136.9584 | 63.692 | 927.3438 | 1139.9718 | 0 | 0 | 1139.9718 | 4.114e-06%
2026 | WT1 | CB WT1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2778 | 28 | 100% | 0.98508 | 16.22% | 0% | 83.78% | 0.0079093 | 0 | 0 | 0.0079093 | 0 | 0.007545 | 1.3201 | 0.0057154 | 0.007545 | 1.3201 | 0.0057154 | 0.0079481 | 1.3906 | 0.0057154 | 0.8029% | 0.0033416 | 0.0031762 | 294.7938 | 0.18584 | 70.2523 | 224.3557 | 307.6558 | 0 | 0 | 307.6558 | 2.608e-07%
2026 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.17383 | 0 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.8387 | 0.17958 | 4.6702 | 0.8387 | 0.17958 | 4.6702 | 0.88351 | 0.18918 | 4.6702 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2026 | 397 | 397-39R | Tier-1 | Non-HFTD---15 | 1--2 | 1.061 | 27 | 100% | 3.5401 | 72.89% | 0% | 27.11% | 0.12772 | 0 | 0 | 0.12772 | 0 | 0.12184 | 1.0961 | 0.11115 | 0.12184 | 1.0961 | 0.11115 | 0.12835 | 1.1547 | 0.11115 | 3.608% | 0.003566 | 0.0033895 | 992.7325 | 10.2311 | 685.8367 | 296.6647 | 1006.7508 | 0 | 0 | 1006.7508 | 4.212e-06%
2026 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 6.1667 | 157 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 748.0666 | 6.3708 | 117.422 | 748.0666 | 6.3708 | 117.422 | 788.0369 | 6.7112 | 117.422 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2026 | 244 | 244-33F | Tier-1 | Non-HFTD---6 | 3--3 | 0.17124 | 0 | 100% | 53.967 | 0.1588% | 99.57% | 0.273% | 0.0042415 | 0 | 0 | 0.0042415 | 0 | 0.0040461 | 0.17691 | 0.022871 | 0.0040461 | 0.17691 | 0.022871 | 0.0042623 | 0.18636 | 0.022871 | 0.007859% | 0.025024 | 0.023786 | 2156.591 | 3.3966 | 1906.5038 | 246.6906 | 2268.7233 | 0 | 0 | 2268.7233 | 1.399e-07%
2026 | 498 | CB 498 | Tier-1 | Non-HFTD---11 | 1--4 | 0.40535 | 1 | 100% | 11.9856 | 98.23% | 0% | 1.767% | 0.5828 | 0 | 0 | 0.5828 | 0 | 0.55595 | 0.41876 | 1.3276 | 0.55595 | 0.41876 | 1.3276 | 0.58566 | 0.44114 | 1.3276 | 4.863% | 0.001257 | 0.0011948 | 9535.0565 | 1272.1609 | 1584.4485 | 6678.4471 | 9543.8307 | 0 | 0 | 9543.8307 | 1.922e-05%
2026 | 94 | 94-24F | Tier-2 | Tier-2---18 | 3--3 | 7.7121 | 186 | 100% | 46.367 | 91.68% | 0% | 8.321% | 2.1042 | 0 | 0 | 2.1042 | 0 | 2.0073 | 7.9673 | 0.25194 | 2.0073 | 7.9673 | 0.25194 | 2.1145 | 8.393 | 0.25194 | 4.538% | 0.020922 | 0.019886 | 2216.1834 | 511.0324 | 89.3586 | 1615.7924 | 2225.7865 | 0 | 0 | 2225.7865 | 6.939e-05%
2026 | 513 | 513-45F | Tier-1 | Non-HFTD---15 | 1--4 | 0.1356 | 13 | 100% | 3.6672 | 98% | 0% | 1.998% | 0.1779 | 0 | 0 | 0.1779 | 0 | 0.1697 | 0.14009 | 1.2114 | 0.1697 | 0.14009 | 1.2114 | 0.17877 | 0.14758 | 1.2114 | 4.851% | 0.0003442 | 0.00032716 | 10654.1784 | 1674.8537 | 49.3768 | 8929.9479 | 10665.2646 | 0 | 0 | 10665.2646 | 5.866e-06%
2026 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.12822 | 0 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 14.647 | 0.13246 | 110.5743 | 14.647 | 0.13246 | 110.5743 | 15.4296 | 0.13954 | 110.5743 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2026 | 401 | CB 401 | Tier-1 | Non-HFTD---10 | 3--2 | 7.5127 | 142 | 100% | 15.7522 | 74.38% | 0% | 25.62% | 0.58 | 0 | 0 | 0.58 | 0 | 0.55328 | 7.7613 | 0.071287 | 0.55328 | 7.7613 | 0.071287 | 0.58284 | 8.176 | 0.071287 | 3.682% | 0.020185 | 0.019185 | 780.4068 | 3.5494 | 583.2472 | 193.6101 | 790.8176 | 0 | 0 | 790.8176 | 1.913e-05%
2026 | 190 | CB 190 | Tier-1 | Non-HFTD---5 | 1--4 | 1.1379 | 17 | 100% | 50.7497 | 97.95% | 0% | 2.052% | 2.4606 | 0 | 0 | 2.4606 | 0 | 2.3472 | 1.1755 | 1.9967 | 2.3472 | 1.1755 | 1.9967 | 2.4726 | 1.2383 | 1.9967 | 4.848% | 0.0045876 | 0.0043605 | 11062.3637 | 1434.6717 | 5166.1533 | 4461.5387 | 11074.1836 | 0 | 0 | 11074.1836 | 8.114e-05%
2026 | 43 | CB 43 | Tier-1 | Non-HFTD---13 | 2--2 | 3.2973 | 61 | 100% | 8.3441 | 73.19% | 0% | 26.81% | 0.3023 | 0 | 0 | 0.3023 | 0 | 0.28837 | 3.4065 | 0.084654 | 0.28837 | 3.4065 | 0.084654 | 0.30378 | 3.5885 | 0.084654 | 3.623% | 0.0092432 | 0.0087857 | 902.7245 | 2.8525 | 666.2859 | 233.5861 | 915.3285 | 0 | 0 | 915.3285 | 9.969e-06%
2026 | 147 | CB 147 | Tier-1 | Non-HFTD---5 | 2--4 | 0.60265 | 82 | 100% | 56.2258 | 13.29% | 85.71% | 1% | 0.36979 | 0 | 0 | 0.36979 | 0 | 0.35275 | 0.6226 | 0.56658 | 0.35275 | 0.6226 | 0.56658 | 0.3716 | 0.65586 | 0.56658 | 0.6577% | 0.0071956 | 0.0068394 | 7813.9098 | 108.3524 | 6561.501 | 1144.0564 | 8166.7746 | 0 | 0 | 8166.7746 | 1.219e-05%
2026 | CS2 | CB CS2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.0863 | 160 | 100% | 10.8217 | 49.87% | 0% | 50.13% | 0.26714 | 0 | 0 | 0.26714 | 0 | 0.25483 | 7.3208 | 0.034809 | 0.25483 | 7.3208 | 0.034809 | 0.26845 | 7.712 | 0.034809 | 2.469% | 0.02081 | 0.01978 | 520.0357 | 1.0415 | 277.8082 | 241.1859 | 533.6123 | 0 | 0 | 533.6123 | 8.809e-06%
2026 | 170 | 170-3R | Tier-1 | Non-HFTD---3 | 4--3 | 7.9656 | 298 | 100% | 134.6076 | 71.34% | 24.69% | 3.975% | 4.7533 | 0 | 0 | 4.7533 | 0 | 4.5343 | 8.2292 | 0.55101 | 4.5343 | 8.2292 | 0.55101 | 4.7766 | 8.6689 | 0.55101 | 3.531% | 0.059016 | 0.056095 | 2280.8503 | 250.0057 | 616.1021 | 1414.7425 | 2314.8955 | 0 | 0 | 2314.8955 | 0.0001567%
2026 | 772 | CB 772 | Tier-1 | Non-HFTD---17 | 1--2 | 0.25341 | 97 | 100% | 0.92752 | 78.02% | 0% | 21.98% | 0.035822 | 0 | 0 | 0.035822 | 0 | 0.034172 | 0.2618 | 0.13053 | 0.034172 | 0.2618 | 0.13053 | 0.035997 | 0.27578 | 0.13053 | 3.862% | 0.0009252 | 0.0008794 | 1002.5093 | 43.9741 | 533.3948 | 425.1403 | 1013.9835 | 0 | 0 | 1013.9835 | 1.181e-06%
2026 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 2.5085 | 304 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 20.4688 | 2.5915 | 7.8984 | 20.4688 | 2.5915 | 7.8984 | 21.5625 | 2.73 | 7.8984 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2026 | 386 | 386-25R | Tier-2 | Tier-2---15 | 3--4 | 2.3127 | 96 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 2.5144 | 0 | 0 | 2.5144 | 0 | 2.3986 | 2.3892 | 1.0039 | 2.3986 | 2.3892 | 1.0039 | 2.5268 | 2.5169 | 1.0039 | 1.75% | 0.019083 | 0.018138 | 7528.0087 | 552.5881 | 4465.4268 | 2509.9939 | 7781.4266 | 0 | 0 | 7781.4266 | 8.292e-05%
2026 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 7.0884 | 662 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 387.696 | 7.323 | 52.9421 | 387.696 | 7.323 | 52.9421 | 408.4111 | 7.7143 | 52.9421 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2026 | 95 | 95-1352F | Tier-1 | Non-HFTD---19 | 1--2 | 0.00625 | 0 | 100% | 0.035566 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064568 | 0 | 0 | 0.0064568 | 0 | 0 | 0.0068018 | 0 | 0% | 5.34e-05 | 5.0757e-05 | 666.0341 | 0.50117 | 60.503 | 605.0299 | 700.7197 | 0 | 0 | 700.7197 | 0%
2026 | FL1 | CB FL1 | Tier-1 | Non-HFTD---18 | 1--1 | 0.99262 | 29 | 100% | 0.95174 | 21.32% | 0% | 78.68% | 0.010043 | 0 | 0 | 0.010043 | 0 | 0.0095804 | 1.0255 | 0.0093424 | 0.0095804 | 1.0255 | 0.0093424 | 0.010092 | 1.0803 | 0.0093424 | 1.055% | 0.0027542 | 0.0026179 | 345.5613 | 0.20459 | 98.3649 | 246.9919 | 359.7211 | 0 | 0 | 359.7211 | 3.312e-07%
2026 | SO1 | CB SO1 | Tier-1 | Non-HFTD---13 | 2--2 | 1.8291 | 60 | 100% | 6.6385 | 81.22% | 0% | 18.78% | 0.26688 | 0 | 0 | 0.26688 | 0 | 0.25459 | 1.8897 | 0.13473 | 0.25459 | 1.8897 | 0.13473 | 0.26819 | 1.9906 | 0.13473 | 4.02% | 0.0053988 | 0.0051316 | 1229.6237 | 149.2052 | 107.0402 | 973.3783 | 1241.6514 | 0 | 0 | 1241.6514 | 8.801e-06%
2026 | 1076 | 1076-37F | Tier-1 | Non-HFTD---10 | 4--2 | 11.6676 | 512 | 100% | 25.756 | 71.52% | 0% | 28.48% | 0.91186 | 0 | 0 | 0.91186 | 0 | 0.86985 | 12.0537 | 0.072164 | 0.86985 | 12.0537 | 0.072164 | 0.91633 | 12.6978 | 0.072164 | 3.54% | 0.031216 | 0.029671 | 825.094 | 10.3507 | 561.5168 | 253.2265 | 837.3304 | 0 | 0 | 837.3304 | 3.007e-05%
2026 | 462 | 462-1521F | Tier-1 | Non-HFTD---13 | 1--3 | 0.48601 | 15 | 100% | 6.0831 | 92.48% | 0% | 7.516% | 0.27849 | 0 | 0 | 0.27849 | 0 | 0.26566 | 0.50209 | 0.5291 | 0.26566 | 0.50209 | 0.5291 | 0.27985 | 0.52892 | 0.5291 | 4.578% | 0.0016764 | 0.0015934 | 3628.6943 | 497.4695 | 319.6242 | 2811.6007 | 3642.8968 | 0 | 0 | 3642.8968 | 9.183e-06%
2026 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 2.7707 | 116 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 73.856 | 2.8623 | 25.8026 | 73.856 | 2.8623 | 25.8026 | 77.8022 | 3.0153 | 25.8026 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2026 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 2.4656 | 168 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 36.5689 | 2.5472 | 14.3567 | 36.5689 | 2.5472 | 14.3567 | 38.5229 | 2.6833 | 14.3567 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2026 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 8.7678 | 229 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 18.7295 | 9.0579 | 2.0677 | 18.7295 | 9.0579 | 2.0677 | 19.7302 | 9.5419 | 2.0677 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2026 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 2.6673 | 399 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 70.7701 | 2.7555 | 25.683 | 70.7701 | 2.7555 | 25.683 | 74.5514 | 2.9028 | 25.683 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2026 | 490 | CB 490 | Tier-1 | Non-HFTD---17 | 1--3 | 0.11705 | 101 | 100% | 1.7253 | 96.38% | 0% | 3.622% | 0.082308 | 0 | 0 | 0.082308 | 0 | 0.078516 | 0.12092 | 0.64933 | 0.078516 | 0.12092 | 0.64933 | 0.082711 | 0.12738 | 0.64933 | 4.771% | 0.0004622 | 0.00043932 | 3732.7377 | 409.8645 | 1089.0962 | 2233.777 | 3739.7782 | 0 | 0 | 3739.7782 | 2.714e-06%
2026 | 439 | 439-42F | Tier-1 | Non-HFTD---13 | 1--5 | 0.094286 | 67 | 100% | 6.5642 | 99.01% | 0% | 0.991% | 0.32171 | 0 | 0 | 0.32171 | 0 | 0.30689 | 0.097407 | 3.1506 | 0.30689 | 0.097407 | 3.1506 | 0.32329 | 0.10261 | 3.1506 | 4.901% | 0.0003618 | 0.00034389 | 18143.2707 | 3639.6892 | 20.3353 | 14483.2462 | 18152.6341 | 0 | 0 | 18152.6341 | 1.061e-05%
2026 | 451 | CB 451 | Tier-1 | Non-HFTD---12 | 3--2 | 5.2964 | 121 | 100% | 9.9548 | 62.07% | 0% | 37.93% | 0.30587 | 0 | 0 | 0.30587 | 0 | 0.29178 | 5.4716 | 0.053325 | 0.29178 | 5.4716 | 0.053325 | 0.30737 | 5.764 | 0.053325 | 3.073% | 0.01523 | 0.014476 | 653.6494 | 0.18655 | 428.2521 | 225.2107 | 666.5605 | 0 | 0 | 666.5605 | 1.009e-05%
2026 | 381 | 381-450F | Tier-1 | Non-HFTD---19 | 1--2 | 0.24375 | 7 | 100% | 0.50113 | 65.42% | 0% | 34.58% | 0.016228 | 0 | 0 | 0.016228 | 0 | 0.015481 | 0.25182 | 0.061475 | 0.015481 | 0.25182 | 0.061475 | 0.016308 | 0.26527 | 0.061475 | 3.238% | 0.0009906 | 0.00094157 | 505.8881 | 53.5748 | 17.2796 | 435.0337 | 514.9984 | 0 | 0 | 514.9984 | 5.351e-07%
2026 | 1049 | 1049-7F | Tier-1 | Non-HFTD---16 | 2--1 | 3.8161 | 101 | 100% | 4.3969 | 41.77% | 0% | 58.23% | 0.090919 | 0 | 0 | 0.090919 | 0 | 0.086731 | 3.9424 | 0.021999 | 0.086731 | 3.9424 | 0.021999 | 0.091365 | 4.1531 | 0.021999 | 2.068% | 0.010687 | 0.010158 | 411.4223 | 11.17 | 126.457 | 273.7954 | 423.8979 | 0 | 0 | 423.8979 | 2.998e-06%
2026 | 579 | 579-350F | Tier-1 | Non-HFTD---4 | 3--4 | 0.61875 | 18 | 100% | 142.7673 | 2.23% | 97.26% | 0.5133% | 0.15763 | 0 | 0 | 0.15763 | 0 | 0.15037 | 0.63923 | 0.23523 | 0.15037 | 0.63923 | 0.23523 | 0.1584 | 0.67339 | 0.23523 | 0.1104% | 0.016794 | 0.015962 | 8501.2943 | 15.4192 | 7694.6748 | 791.2003 | 8934.1485 | 0 | 0 | 8934.1485 | 5.198e-06%
2026 | 143 | 143-179F | Tier-1 | Non-HFTD---18 | 2--1 | 0.022348 | 1 | 100% | 1.3702 | 64.14% | 33.11% | 2.747% | 0.043505 | 0 | 0 | 0.043505 | 0 | 0.041501 | 0.023088 | 1.7975 | 0.041501 | 0.023088 | 1.7975 | 0.043718 | 0.024322 | 1.7975 | 3.175% | 0.0062356 | 0.0059269 | 219.7357 | 23.4884 | 57.8583 | 138.3889 | 223.8388 | 0 | 0 | 223.8388 | 1.435e-06%
2026 | 55 | 55-479F | Tier-1 | Non-HFTD---17 | 1--1 | 0.60512 | 90 | 100% | 1.2239 | 36.64% | 0% | 63.36% | 0.022196 | 0 | 0 | 0.022196 | 0 | 0.021173 | 0.62514 | 0.033869 | 0.021173 | 0.62514 | 0.033869 | 0.022304 | 0.65854 | 0.033869 | 1.813% | 0.002537 | 0.0024114 | 482.4279 | 2.4251 | 191.0428 | 288.9599 | 498.3473 | 0 | 0 | 498.3473 | 7.319e-07%
2026 | 44 | 44-40AE | Tier-1 | Non-HFTD---17 | 1--2 | 0.95338 | 22 | 100% | 1.9267 | 51.29% | 0% | 48.71% | 0.048912 | 0 | 0 | 0.048912 | 0 | 0.046659 | 0.98493 | 0.047373 | 0.046659 | 0.98493 | 0.047373 | 0.049152 | 1.0376 | 0.047373 | 2.539% | 0.003574 | 0.0033971 | 539.0796 | 43.7572 | 32.3287 | 462.9937 | 552.7554 | 0 | 0 | 552.7554 | 1.613e-06%
2026 | 364 | 364-36 | Tier-1 | Non-HFTD---4 | 3--4 | 7.918 | 167 | 100% | 171.1869 | 2.025% | 94.55% | 3.426% | 0.17156 | 0 | 0 | 0.17156 | 0 | 0.16365 | 8.18 | 0.020007 | 0.16365 | 8.18 | 0.020007 | 0.1724 | 8.6171 | 0.020007 | 0.1002% | 0.027309 | 0.025958 | 6268.4256 | 8.2117 | 5535.3679 | 724.846 | 6588.2626 | 0 | 0 | 6588.2626 | 5.657e-06%
2026 | 244 | 244-29 | Tier-1 | Non-HFTD---2 | 4--4 | 20.8303 | 864 | 100% | 494.9076 | 37.84% | 59.66% | 2.496% | 9.2706 | 0 | 0 | 9.2706 | 0 | 8.8435 | 21.5196 | 0.41095 | 8.8435 | 21.5196 | 0.41095 | 9.316 | 22.6695 | 0.41095 | 1.873% | 0.082271 | 0.078198 | 6015.6074 | 554.6539 | 3442.3851 | 2018.5684 | 6210.3353 | 0 | 0 | 6210.3353 | 0.0003057%
2026 | 793 | 793-46F | Tier-1 | Non-HFTD---10 | 3--2 | 1.1603 | 43 | 100% | 23.4141 | 2.819% | 95.02% | 2.166% | 0.032668 | 0 | 0 | 0.032668 | 0 | 0.031163 | 1.1987 | 0.025998 | 0.031163 | 1.1987 | 0.025998 | 0.032828 | 1.2627 | 0.025998 | 0.1395% | 0.020148 | 0.01915 | 1162.1175 | 4.9845 | 1026.7024 | 130.4306 | 1220.9323 | 0 | 0 | 1220.9323 | 1.077e-06%
2026 | AD1 | CB AD1 | Tier-1 | Non-HFTD---3 | 4--3 | 9.4 | 277 | 100% | 147.8944 | 9.794% | 85.29% | 4.92% | 0.71697 | 0 | 0 | 0.71697 | 0 | 0.68394 | 9.7111 | 0.070429 | 0.68394 | 9.7111 | 0.070429 | 0.72049 | 10.23 | 0.070429 | 0.4848% | 0.031636 | 0.03007 | 4674.8186 | 81.3578 | 3791.6481 | 801.8126 | 4894.4299 | 0 | 0 | 4894.4299 | 2.364e-05%
2026 | 85 | 85-500F | Tier-1 | Non-HFTD---14 | 2--2 | 3.3993 | 63 | 100% | 4.936 | 60.97% | 0% | 39.03% | 0.14897 | 0 | 0 | 0.14897 | 0 | 0.14211 | 3.5118 | 0.040465 | 0.14211 | 3.5118 | 0.040465 | 0.1497 | 3.6994 | 0.040465 | 3.018% | 0.0098106 | 0.009325 | 503.1269 | 39.9485 | 81.0918 | 382.0867 | 513.3535 | 0 | 0 | 513.3535 | 4.912e-06%
2026 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.91593 | 133 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 101.0059 | 0.94624 | 106.7439 | 101.0059 | 0.94624 | 106.7439 | 106.4028 | 0.9968 | 106.7439 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2026 | 166 | 166-982F | Tier-1 | Non-HFTD---15 | 2--1 | 2.2852 | 49 | 100% | 2.9192 | 42.53% | 0% | 57.47% | 0.061449 | 0 | 0 | 0.061449 | 0 | 0.058618 | 2.3609 | 0.024829 | 0.058618 | 2.3609 | 0.024829 | 0.06175 | 2.487 | 0.024829 | 2.105% | 0.0065086 | 0.0061864 | 448.512 | 2.7669 | 198.387 | 247.3581 | 461.9366 | 0 | 0 | 461.9366 | 2.026e-06%
2026 | 45 | CB 45 | Tier-1 | Non-HFTD---9 | 2--3 | 1.9805 | 27 | 100% | 25.7276 | 93.88% | 0% | 6.12% | 1.1956 | 0 | 0 | 1.1956 | 0 | 1.1405 | 2.046 | 0.55743 | 1.1405 | 2.046 | 0.55743 | 1.2014 | 2.1553 | 0.55743 | 4.647% | 0.0069006 | 0.006559 | 3728.3111 | 135.5762 | 2690.8224 | 901.9126 | 3740.1941 | 0 | 0 | 3740.1941 | 3.943e-05%
2026 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 7.8716 | 546 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 23.0859 | 8.1321 | 2.8389 | 23.0859 | 8.1321 | 2.8389 | 24.3194 | 8.5666 | 2.8389 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2026 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 24.6051 | 1577 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 296.1766 | 25.4194 | 11.6516 | 296.1766 | 25.4194 | 11.6516 | 312.0017 | 26.7776 | 11.6516 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2026 | MA1 | CB MA1 | Tier-1 | Non-HFTD---3 | 4--3 | 11.2421 | 595 | 100% | 187.6887 | 3.137% | 92.99% | 3.876% | 0.29148 | 0 | 0 | 0.29148 | 0 | 0.27805 | 11.6141 | 0.023941 | 0.27805 | 11.6141 | 0.023941 | 0.29291 | 12.2347 | 0.023941 | 0.1553% | 0.044813 | 0.042595 | 4188.2268 | 5.9858 | 3692.2486 | 489.9924 | 4399.4977 | 0 | 0 | 4399.4977 | 9.612e-06%
2026 | 463 | 463-1137F | Tier-2 | Tier-2---19 | 1--5 | 0.125 | 0 | 100% | 11.7975 | 99.11% | 0% | 0.8934% | 0.57876 | 0 | 0 | 0.57876 | 0 | 0.5521 | 0.12914 | 4.2753 | 0.5521 | 0.12914 | 4.2753 | 0.5816 | 0.13604 | 4.2753 | 4.906% | 0.0005036 | 0.00047867 | 23426.3875 | 4696.5104 | 948.1966 | 17781.6805 | 23437.287 | 0 | 0 | 23437.287 | 1.909e-05%
2026 | 277 | 277-459F | Tier-1 | Non-HFTD---2 | 4--3 | 9.8924 | 276 | 100% | 196.3447 | 7.922% | 88.67% | 3.412% | 0.76992 | 0 | 0 | 0.76992 | 0 | 0.73445 | 10.2198 | 0.071866 | 0.73445 | 10.2198 | 0.071866 | 0.77369 | 10.7658 | 0.071866 | 0.3921% | 0.04286 | 0.040738 | 4581.0932 | 25.5864 | 3978.2585 | 577.2483 | 4800.7676 | 0 | 0 | 4800.7676 | 2.539e-05%
2026 | WA2 | CB WA2 | Tier-1 | Non-HFTD---12 | 3--2 | 5.65 | 280 | 100% | 10.82 | 65.84% | 0% | 34.16% | 0.35266 | 0 | 0 | 0.35266 | 0 | 0.33641 | 5.837 | 0.057634 | 0.33641 | 5.837 | 0.057634 | 0.35438 | 6.1489 | 0.057634 | 3.259% | 0.016911 | 0.016074 | 639.8077 | 57.0792 | 90.6841 | 492.0444 | 651.1883 | 0 | 0 | 651.1883 | 1.163e-05%
2026 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 3.3255 | 24 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 10.0061 | 3.4356 | 2.9125 | 10.0061 | 3.4356 | 2.9125 | 10.5407 | 3.6192 | 2.9125 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2026 | OCA1 | CB OCA1 | Tier-1 | Non-HFTD---14 | 2--2 | 0.66117 | 89 | 100% | 5.9345 | 0.6639% | 92.19% | 7.151% | 0.0019501 | 0 | 0 | 0.0019501 | 0 | 0.0018603 | 0.68305 | 0.0027235 | 0.0018603 | 0.68305 | 0.0027235 | 0.0019597 | 0.71954 | 0.0027235 | 0.03286% | 0.0090824 | 0.0086328 | 653.4036 | 0.7621 | 562.1423 | 90.4992 | 687.2056 | 0 | 0 | 687.2056 | 6.431e-08%
2026 | 289 | 289-907 | Tier-1 | Non-HFTD---7 | 3--3 | 4.268 | 277 | 100% | 40.1087 | 2.57% | 90.18% | 7.252% | 0.051033 | 0 | 0 | 0.051033 | 0 | 0.048682 | 4.4092 | 0.011041 | 0.048682 | 4.4092 | 0.011041 | 0.051283 | 4.6448 | 0.011041 | 0.1272% | 0.017391 | 0.01653 | 2306.2924 | 6.5848 | 1930.5725 | 369.135 | 2423.3119 | 0 | 0 | 2423.3119 | 1.683e-06%
2026 | 399 | CB 399 | Tier-1 | Non-HFTD---10 | 3--2 | 6.1078 | 357 | 100% | 19.1964 | 76.81% | 0% | 23.19% | 0.72985 | 0 | 0 | 0.72985 | 0 | 0.69623 | 6.3099 | 0.11034 | 0.69623 | 6.3099 | 0.11034 | 0.73343 | 6.6471 | 0.11034 | 3.802% | 0.017948 | 0.017059 | 1069.5788 | 24.012 | 698.2984 | 347.2685 | 1082.4967 | 0 | 0 | 1082.4967 | 2.407e-05%
2026 | 154 | 154-876R | Tier-1 | Non-HFTD---12 | 3--2 | 7.2587 | 212 | 100% | 9.9957 | 58.61% | 0% | 41.39% | 0.29001 | 0 | 0 | 0.29001 | 0 | 0.27665 | 7.499 | 0.036892 | 0.27665 | 7.499 | 0.036892 | 0.29143 | 7.8996 | 0.036892 | 2.901% | 0.018706 | 0.01778 | 534.3539 | 0.16641 | 333.2928 | 200.8947 | 545.871 | 0 | 0 | 545.871 | 9.564e-06%
2026 | 1482 | CB 1482 | Tier-1 | Non-HFTD---19 | 1--3 | 0.033523 | 3 | 100% | 0.35238 | 81.69% | 0% | 18.31% | 0.014248 | 0 | 0 | 0.014248 | 0 | 0.013592 | 0.034632 | 0.39247 | 0.013592 | 0.034632 | 0.39247 | 0.014318 | 0.036483 | 0.39247 | 4.043% | 0.0001796 | 0.00017071 | 1962.0387 | 0.27038 | 1635.3539 | 326.4145 | 1980.7517 | 0 | 0 | 1980.7517 | 4.699e-07%
2026 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 3.9246 | 193 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 157.0745 | 4.0545 | 38.7406 | 157.0745 | 4.0545 | 38.7406 | 165.4672 | 4.2712 | 38.7406 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2026 | JE1 | CB JE1 | Tier-1 | Non-HFTD---18 | 1--1 | 0.96179 | 61 | 100% | 0.75454 | 7.509% | 0% | 92.49% | 0.0028046 | 0 | 0 | 0.0028046 | 0 | 0.0026754 | 0.99362 | 0.0026926 | 0.0026754 | 0.99362 | 0.0026926 | 0.0028184 | 1.0467 | 0.0026926 | 0.3717% | 0.0027018 | 0.0025681 | 279.2739 | 0.19436 | 44.4353 | 234.6442 | 292.7257 | 0 | 0 | 292.7257 | 9.249e-08%
2026 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 1.0854 | 15 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 15.5039 | 1.1213 | 13.8262 | 15.5039 | 1.1213 | 13.8262 | 16.3322 | 1.1813 | 13.8262 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2026 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 8.4758 | 338 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 83.7784 | 8.7563 | 9.5678 | 83.7784 | 8.7563 | 9.5678 | 88.2548 | 9.2241 | 9.5678 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2026 | 506 | 506-161 | Tier-1 | Non-HFTD---15 | 2--2 | 1.9422 | 104 | 100% | 4.7204 | 74.33% | 0% | 25.67% | 0.17369 | 0 | 0 | 0.17369 | 0 | 0.16569 | 2.0065 | 0.082576 | 0.16569 | 2.0065 | 0.082576 | 0.17454 | 2.1137 | 0.082576 | 3.68% | 0.0058182 | 0.0055302 | 811.3208 | 47.4149 | 332.8733 | 431.0326 | 822.1649 | 0 | 0 | 822.1649 | 5.728e-06%
2026 | 409 | 409-1155R | Tier-1 | Non-HFTD---10 | 2--2 | 4.4515 | 143 | 100% | 15.855 | 79.34% | 0% | 20.66% | 0.62272 | 0 | 0 | 0.62272 | 0 | 0.59403 | 4.5989 | 0.12917 | 0.59403 | 4.5989 | 0.12917 | 0.62577 | 4.8446 | 0.12917 | 3.928% | 0.012886 | 0.012248 | 1230.387 | 1.5966 | 990.7436 | 238.0468 | 1243.622 | 0 | 0 | 1243.622 | 2.053e-05%
2026 | 86 | CB 86 | Tier-1 | Non-HFTD---17 | 1--3 | 0.28124 | 5 | 100% | 2.0292 | 91.13% | 0% | 8.873% | 0.091533 | 0 | 0 | 0.091533 | 0 | 0.087317 | 0.29054 | 0.30053 | 0.087317 | 0.29054 | 0.30053 | 0.091982 | 0.30607 | 0.30053 | 4.511% | 0.0007966 | 0.00075717 | 2547.343 | 6.272 | 2304.2733 | 236.7977 | 2559.1141 | 0 | 0 | 2559.1141 | 3.018e-06%
2026 | 1434 | 1434-37R | Tier-1 | Non-HFTD---8 | 3--2 | 9.4542 | 300 | 100% | 34.3658 | 81.72% | 0% | 18.28% | 1.3902 | 0 | 0 | 1.3902 | 0 | 1.3261 | 9.7671 | 0.13578 | 1.3261 | 9.7671 | 0.13578 | 1.397 | 10.2889 | 0.13578 | 4.045% | 0.027694 | 0.026323 | 1240.9281 | 98.0626 | 641.6225 | 501.2431 | 1252.7397 | 0 | 0 | 1252.7397 | 4.584e-05%
2026 | 197 | CB 197 | Tier-2 | Tier-2---21 | 1--4 | 0.097159 | 0 | 100% | 1.9198 | 98.18% | 0% | 1.817% | 0.093305 | 0 | 0 | 0.093305 | 0 | 0.089007 | 0.10037 | 0.88675 | 0.089007 | 0.10037 | 0.88675 | 0.093762 | 0.10574 | 0.88675 | 4.86% | 0.000314 | 0.00029846 | 6114.1 | 461.2612 | 3185.8611 | 2466.9777 | 6119.8844 | 0 | 0 | 6119.8844 | 3.077e-06%
2026 | 326 | 326-26 | Tier-1 | Non-HFTD---17 | 1--3 | 0.27121 | 19 | 100% | 1.9501 | 90.68% | 0% | 9.316% | 0.087536 | 0 | 0 | 0.087536 | 0 | 0.083503 | 0.28019 | 0.29803 | 0.083503 | 0.28019 | 0.29803 | 0.087965 | 0.29516 | 0.29803 | 4.489% | 0.0009188 | 0.00087332 | 2122.4058 | 3.4556 | 1922.3956 | 196.5546 | 2132.7026 | 0 | 0 | 2132.7026 | 2.887e-06%
2026 | 933 | 933-472F | Tier-1 | Non-HFTD---4 | 2--5 | 2.0138 | 194 | 100% | 165.8681 | 99.03% | 0% | 0.973% | 8.1306 | 0 | 0 | 8.1306 | 0 | 7.756 | 2.0804 | 3.7281 | 7.756 | 2.0804 | 3.7281 | 8.1704 | 2.1916 | 3.7281 | 4.902% | 0.0078904 | 0.0074998 | 21021.5038 | 4274.6156 | 66.263 | 16680.6253 | 21032.1561 | 0 | 0 | 21032.1561 | 0.0002681%
2026 | 779 | 779-25AE | Tier-1 | Non-HFTD---15 | 1--3 | 0.33084 | 22 | 100% | 3.5318 | 96.75% | 0% | 3.249% | 0.16914 | 0 | 0 | 0.16914 | 0 | 0.16135 | 0.34179 | 0.47208 | 0.16135 | 0.34179 | 0.47208 | 0.16997 | 0.36005 | 0.47208 | 4.789% | 0.0008446 | 0.00080279 | 4181.6044 | 654.541 | 38.406 | 3488.6574 | 4188.6793 | 0 | 0 | 4188.6793 | 5.578e-06%
2026 | BY3 | CB BY3 | Tier-1 | Non-HFTD---12 | 3--1 | 8.1915 | 286 | 100% | 10.3011 | 47.64% | 0% | 52.36% | 0.24292 | 0 | 0 | 0.24292 | 0 | 0.23173 | 8.4625 | 0.027383 | 0.23173 | 8.4625 | 0.027383 | 0.24411 | 8.9147 | 0.027383 | 2.358% | 0.023075 | 0.021933 | 446.413 | 16.8472 | 131.6677 | 297.8981 | 458.5857 | 0 | 0 | 458.5857 | 8.011e-06%
2026 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 8.4597 | 765 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 589.092 | 8.7396 | 67.4045 | 589.092 | 8.7396 | 67.4045 | 620.568 | 9.2066 | 67.4045 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2026 | 475 | 475-763F | Tier-1 | Non-HFTD---9 | 2--3 | 2.6615 | 141 | 100% | 16.724 | 89.58% | 0% | 10.42% | 0.74158 | 0 | 0 | 0.74158 | 0 | 0.70742 | 2.7496 | 0.25728 | 0.70742 | 2.7496 | 0.25728 | 0.74522 | 2.8965 | 0.25728 | 4.434% | 0.0076068 | 0.0072303 | 2198.5586 | 311.6157 | 88.9446 | 1797.9982 | 2210.4884 | 0 | 0 | 2210.4884 | 2.445e-05%
2026 | 900 | 900-1119F | Tier-1 | Non-HFTD---15 | 1--4 | 0.064205 | 4 | 100% | 3.0645 | 96.62% | 0% | 3.379% | 0.14657 | 0 | 0 | 0.14657 | 0 | 0.13982 | 0.066329 | 2.1079 | 0.13982 | 0.066329 | 2.1079 | 0.14729 | 0.069873 | 2.1079 | 4.783% | 0.000334 | 0.00031747 | 9175.1794 | 752.0584 | 4282.7612 | 4140.3597 | 9191.3258 | 0 | 0 | 9191.3258 | 4.833e-06%
2026 | TR1 | CB TR1 | Tier-1 | Non-HFTD---5 | 1--5 | 0.82749 | 70 | 100% | 65.5808 | 99.13% | 0% | 0.8721% | 3.2179 | 0 | 0 | 3.2179 | 0 | 3.0697 | 0.85488 | 3.5908 | 3.0697 | 0.85488 | 3.5908 | 3.2337 | 0.90055 | 3.5908 | 4.907% | 0.0027118 | 0.0025776 | 24183.476 | 3920.7975 | 31.6199 | 20231.0587 | 24194.4592 | 0 | 0 | 24194.4592 | 0.0001061%
2026 | 453 | 453-32R | Tier-1 | Non-HFTD---16 | 2--1 | 2.4413 | 131 | 100% | 2.5305 | 33.48% | 0% | 66.52% | 0.04194 | 0 | 0 | 0.04194 | 0 | 0.040008 | 2.5221 | 0.015863 | 0.040008 | 2.5221 | 0.015863 | 0.042146 | 2.6569 | 0.015863 | 1.657% | 0.0069622 | 0.0066176 | 363.4686 | 7.0606 | 101.7102 | 254.6977 | 376.0595 | 0 | 0 | 376.0595 | 1.383e-06%
2026 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 8.1866 | 142 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 40.7779 | 8.4575 | 4.8215 | 40.7779 | 8.4575 | 4.8215 | 42.9567 | 8.9094 | 4.8215 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2026 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 5.3209 | 576 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 158.2696 | 5.497 | 28.7922 | 158.2696 | 5.497 | 28.7922 | 166.7261 | 5.7907 | 28.7922 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2026 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.46496 | 52 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 61.292 | 0.48035 | 127.5989 | 61.292 | 0.48035 | 127.5989 | 64.5669 | 0.50601 | 127.5989 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2026 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3.0366 | 17 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 53.3631 | 3.137 | 17.0106 | 53.3631 | 3.137 | 17.0106 | 56.2144 | 3.3047 | 17.0106 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2026 | 492 | 492-14R | Tier-1 | Non-HFTD---2 | 4--3 | 10.8722 | 597 | 100% | 216.5783 | 3.253% | 93.45% | 3.298% | 0.34878 | 0 | 0 | 0.34878 | 0 | 0.33271 | 11.232 | 0.029622 | 0.33271 | 11.232 | 0.029622 | 0.35049 | 11.8321 | 0.029622 | 0.161% | 0.045206 | 0.042969 | 4790.8774 | 21.0243 | 4182.3297 | 587.5234 | 5032.259 | 0 | 0 | 5032.259 | 1.15e-05%
2026 | 76 | 76-49F | Tier-1 | Non-HFTD---15 | 1--2 | 0.71628 | 24 | 100% | 2.5849 | 70.44% | 0% | 29.56% | 0.09013 | 0 | 0 | 0.09013 | 0 | 0.085978 | 0.73999 | 0.11619 | 0.085978 | 0.73999 | 0.11619 | 0.090572 | 0.77953 | 0.11619 | 3.487% | 0.002558 | 0.0024314 | 1010.5197 | 2.3761 | 725.7796 | 282.364 | 1026.0758 | 0 | 0 | 1026.0758 | 2.972e-06%
2026 | 257 | CB 257 | Tier-1 | Non-HFTD---10 | 3--2 | 6.9074 | 160 | 100% | 24.5079 | 76.93% | 0% | 23.07% | 0.93326 | 0 | 0 | 0.93326 | 0 | 0.89027 | 7.136 | 0.12476 | 0.89027 | 7.136 | 0.12476 | 0.93784 | 7.5173 | 0.12476 | 3.808% | 0.021535 | 0.020469 | 1138.0399 | 1.5436 | 890.8784 | 245.6179 | 1151.7131 | 0 | 0 | 1151.7131 | 3.078e-05%
2026 | 476 | CB 476 | Tier-2 | Tier-2---2 | 5--5 | 18.0017 | 2125 | 100% | 7260.3217 | 73.64% | 26.17% | 0.1876% | 264.6639 | 0 | 0 | 264.6639 | 0 | 252.4713 | 18.5974 | 13.5756 | 252.4713 | 18.5974 | 13.5756 | 265.9612 | 19.5911 | 13.5756 | 3.645% | 0.20125 | 0.19129 | 36075.4158 | 6663.2216 | 8787.8653 | 20624.3289 | 36570.586 | 0 | 0 | 36570.586 | 0.008728%
2026 | 768 | 768-20AE | Tier-1 | Non-HFTD---5 | 1--5 | 0.6589 | 98 | 100% | 67.3049 | 99.42% | 0% | 0.5848% | 3.3121 | 0 | 0 | 3.3121 | 0 | 3.1595 | 0.68071 | 4.6415 | 3.1595 | 0.68071 | 4.6415 | 3.3283 | 0.71708 | 4.6415 | 4.921% | 0.002811 | 0.0026719 | 23943.3951 | 9554.3263 | 1502.6811 | 12886.3878 | 23950.6874 | 0 | 0 | 23950.6874 | 0.0001092%
2026 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.033523 | 0 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.5386 | 0.034632 | 15.552 | 0.5386 | 0.034632 | 15.552 | 0.56738 | 0.036483 | 15.552 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2026 | PB5 | CB PB5 | Tier-1 | Non-HFTD---6 | 3--3 | 5.8622 | 228 | 100% | 65.9306 | 5.839% | 87.56% | 6.598% | 0.19055 | 0 | 0 | 0.19055 | 0 | 0.18177 | 6.0562 | 0.030014 | 0.18177 | 6.0562 | 0.030014 | 0.19148 | 6.3798 | 0.030014 | 0.289% | 0.027149 | 0.025805 | 2428.4558 | 3.0271 | 2101.4761 | 323.9526 | 2547.5406 | 0 | 0 | 2547.5406 | 6.283e-06%
2026 | 135 | CB 135 | Tier-1 | Non-HFTD---20 | 1--1 | 0.62631 | 9 | 100% | 0.56317 | 1.996% | 0% | 98% | 0.00055646 | 0 | 0 | 0.00055646 | 0 | 0.00053083 | 0.64704 | 0.00082039 | 0.00053083 | 0.64704 | 0.00082039 | 0.00055919 | 0.68161 | 0.00082039 | 0.09881% | 0.0020306 | 0.0019301 | 277.341 | 0.20452 | 30.2271 | 246.9094 | 291.496 | 0 | 0 | 291.496 | 1.835e-08%
2026 | 299 | 299-815 | Tier-1 | Non-HFTD---7 | 2--3 | 3.2593 | 209 | 100% | 28.2256 | 91.52% | 0% | 8.482% | 1.2787 | 0 | 0 | 1.2787 | 0 | 1.2198 | 3.3671 | 0.36226 | 1.2198 | 3.3671 | 0.36226 | 1.2849 | 3.547 | 0.36226 | 4.53% | 0.010153 | 0.0096506 | 2779.9666 | 384.8777 | 211.0962 | 2183.9927 | 2792.246 | 0 | 0 | 2792.246 | 4.217e-05%
2026 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 1.5443 | 285 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 32.5317 | 1.5954 | 20.3906 | 32.5317 | 1.5954 | 20.3906 | 34.2699 | 1.6807 | 20.3906 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2026 | 159 | 159-37F | Tier-1 | Non-HFTD---14 | 3--1 | 7.37 | 197 | 100% | 7.089 | 33.87% | 0% | 66.13% | 0.11886 | 0 | 0 | 0.11886 | 0 | 0.11339 | 7.6139 | 0.014892 | 0.11339 | 7.6139 | 0.014892 | 0.11945 | 8.0208 | 0.014892 | 1.677% | 0.019669 | 0.018695 | 360.4176 | 0.40479 | 142.323 | 217.6898 | 372.8294 | 0 | 0 | 372.8294 | 3.92e-06%
2026 | MT3 | CB MT3 | Tier-1 | Non-HFTD---16 | 2--1 | 3.6305 | 161 | 100% | 4.5475 | 41.58% | 0% | 58.42% | 0.093595 | 0 | 0 | 0.093595 | 0 | 0.089283 | 3.7507 | 0.023805 | 0.089283 | 3.7507 | 0.023805 | 0.094053 | 3.9511 | 0.023805 | 2.058% | 0.011697 | 0.011118 | 388.7903 | 0.29705 | 181.7474 | 206.7459 | 400.6191 | 0 | 0 | 400.6191 | 3.086e-06%
2026 | 158 | 158-29 | Tier-1 | Non-HFTD---12 | 4--1 | 16.0678 | 488 | 100% | 14.9816 | 28.99% | 0% | 71.01% | 0.215 | 0 | 0 | 0.215 | 0 | 0.2051 | 16.5995 | 0.012356 | 0.2051 | 16.5995 | 0.012356 | 0.21606 | 17.4865 | 0.012356 | 1.435% | 0.043297 | 0.041154 | 346.0178 | 1.8646 | 116.0528 | 228.1004 | 358.8133 | 0 | 0 | 358.8133 | 7.09e-06%
2026 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.055682 | 33 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.072621 | 0.057525 | 1.2624 | 0.072621 | 0.057525 | 1.2624 | 0.076501 | 0.060598 | 1.2624 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2026 | 859 | 859-13F | Tier-1 | Non-HFTD---1 | 4--5 | 10.7166 | 869 | 100% | 1153.8557 | 99.35% | 0% | 0.6497% | 56.7448 | 0 | 0 | 56.7448 | 0 | 54.1307 | 11.0713 | 4.8893 | 54.1307 | 11.0713 | 4.8893 | 57.023 | 11.6628 | 4.8893 | 4.918% | 0.035677 | 0.033911 | 32341.7236 | 5122.1729 | 819.8446 | 26399.7061 | 32352.6656 | 0 | 0 | 32352.6656 | 0.001871%
2026 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 15.3767 | 416 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 50.6908 | 15.8856 | 3.191 | 50.6908 | 15.8856 | 3.191 | 53.3993 | 16.7344 | 3.191 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2026 | SE4 | CB SE4 | Tier-1 | Non-HFTD---12 | 3--2 | 1.139 | 45 | 100% | 13.0711 | 1.917% | 92.58% | 5.504% | 0.012405 | 0 | 0 | 0.012405 | 0 | 0.011833 | 1.1767 | 0.010056 | 0.011833 | 1.1767 | 0.010056 | 0.012465 | 1.2396 | 0.010056 | 0.0949% | 0.021339 | 0.020283 | 612.5496 | 1.2137 | 530.3816 | 80.9543 | 643.8382 | 0 | 0 | 643.8382 | 4.091e-07%
2026 | 340 | CB 340 | Tier-1 | Non-HFTD---7 | 1--5 | 0.42082 | 33 | 100% | 29.3144 | 98.84% | 0% | 1.164% | 1.4342 | 0 | 0 | 1.4342 | 0 | 1.3681 | 0.43474 | 3.1469 | 1.3681 | 0.43474 | 3.1469 | 1.4412 | 0.45797 | 3.1469 | 4.892% | 0.0015836 | 0.0015052 | 18511.2088 | 2537.4844 | 2809.9216 | 13163.8027 | 18522.4306 | 0 | 0 | 18522.4306 | 4.729e-05%
2026 | 507 | 507-1733 | Tier-1 | Non-HFTD---13 | 1--3 | 1.175 | 58 | 100% | 7.2494 | 86.12% | 0% | 13.88% | 0.30903 | 0 | 0 | 0.30903 | 0 | 0.29479 | 1.2139 | 0.24284 | 0.29479 | 1.2139 | 0.24284 | 0.31054 | 1.2788 | 0.24284 | 4.263% | 0.003877 | 0.0036851 | 1869.8551 | 69.1763 | 1211.0556 | 589.6232 | 1883.3737 | 0 | 0 | 1883.3737 | 1.019e-05%
2026 | 61 | 61-23F | Tier-1 | Non-HFTD---7 | 2--3 | 0.13197 | 28 | 100% | 42.4736 | 0.005397% | 99.75% | 0.2412% | 0.00011347 | 0 | 0 | 0.00011347 | 0 | 0.00010825 | 0.13633 | 0.00079397 | 0.00010825 | 0.13633 | 0.00079397 | 0.00011403 | 0.14362 | 0.00079397 | 0.0002672% | 0.011235 | 0.010679 | 3780.542 | 4.6215 | 3457.7842 | 318.1363 | 3977.4139 | 0 | 0 | 3977.4139 | 3.742e-09%
2026 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 31.2755 | 3127 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 765.8108 | 32.3106 | 23.7016 | 765.8108 | 32.3106 | 23.7016 | 806.7292 | 34.0369 | 23.7016 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2026 | 53 | 53-49 | Tier-1 | Non-HFTD---18 | 2--1 | 2.3103 | 59 | 100% | 1.7953 | 15.92% | 0% | 84.08% | 0.014151 | 0 | 0 | 0.014151 | 0 | 0.013499 | 2.3867 | 0.0056561 | 0.013499 | 2.3867 | 0.0056561 | 0.014221 | 2.5142 | 0.0056561 | 0.7883% | 0.0061878 | 0.0058815 | 290.1286 | 0.18355 | 68.3602 | 221.5848 | 302.8317 | 0 | 0 | 302.8317 | 4.667e-07%
2026 | 589 | CB 589 | Tier-1 | Non-HFTD---4 | 2--5 | 1.6411 | 159 | 100% | 115.513 | 99.19% | 0% | 0.8071% | 5.6717 | 0 | 0 | 5.6717 | 0 | 5.4105 | 1.6954 | 3.1912 | 5.4105 | 1.6954 | 3.1912 | 5.6995 | 1.786 | 3.1912 | 4.91% | 0.0061356 | 0.0058319 | 18826.6917 | 3852.5482 | 1417.3063 | 13556.8372 | 18834.6054 | 0 | 0 | 18834.6054 | 0.000187%
2026 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 5.5121 | 308 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 34.4739 | 5.6945 | 6.0539 | 34.4739 | 5.6945 | 6.0539 | 36.3159 | 5.9988 | 6.0539 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2026 | 342 | 342-521AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.2639 | 79 | 100% | 2.959 | 30.71% | 0% | 69.29% | 0.044974 | 0 | 0 | 0.044974 | 0 | 0.042903 | 2.3388 | 0.018344 | 0.042903 | 2.3388 | 0.018344 | 0.045195 | 2.4637 | 0.018344 | 1.52% | 0.0073744 | 0.0070094 | 401.2552 | 3.7445 | 126.7331 | 270.7777 | 415.7354 | 0 | 0 | 415.7354 | 1.483e-06%
2026 | 851 | CB 851 | Tier-1 | Non-HFTD---4 | 1--5 | 0.77311 | 72 | 100% | 102.5522 | 99.44% | 0% | 0.5561% | 5.0481 | 0 | 0 | 5.0481 | 0 | 4.8156 | 0.79869 | 6.0293 | 4.8156 | 0.79869 | 6.0293 | 5.0729 | 0.84137 | 6.0293 | 4.922% | 0.0031694 | 0.0030125 | 32356.9802 | 6963.0193 | 3626.5901 | 21767.3707 | 32366.3506 | 0 | 0 | 32366.3506 | 0.0001665%
2026 | 1073 | CB 1073 | Tier-1 | Non-HFTD---3 | 4--4 | 6.1307 | 211 | 100% | 166.0602 | 6.113% | 91.74% | 2.147% | 0.50246 | 0 | 0 | 0.50246 | 0 | 0.47931 | 6.3336 | 0.075678 | 0.47931 | 6.3336 | 0.075678 | 0.50492 | 6.672 | 0.075678 | 0.3026% | 0.033742 | 0.032072 | 4921.469 | 22.1347 | 4284.5904 | 614.7439 | 5162.102 | 0 | 0 | 5162.102 | 1.657e-05%
2026 | 289 | CB 289 | Tier-1 | Non-HFTD---6 | 3--3 | 4.3732 | 707 | 100% | 64.7389 | 39.27% | 55.62% | 5.104% | 1.2585 | 0 | 0 | 1.2585 | 0 | 1.2005 | 4.5179 | 0.26573 | 1.2005 | 4.5179 | 0.26573 | 1.2647 | 4.7593 | 0.26573 | 1.944% | 0.018234 | 0.017332 | 3550.4112 | 114.2687 | 2547.3845 | 888.758 | 3662.6956 | 0 | 0 | 3662.6956 | 4.15e-05%
2026 | 207 | 207-101R | Tier-1 | Non-HFTD---8 | 4--2 | 11.3577 | 523 | 100% | 42.8651 | 83.69% | 0% | 16.31% | 1.7758 | 0 | 0 | 1.7758 | 0 | 1.6939 | 11.7336 | 0.14437 | 1.6939 | 11.7336 | 0.14437 | 1.7845 | 12.3605 | 0.14437 | 4.143% | 0.032633 | 0.031017 | 1313.5599 | 147.1403 | 219.5178 | 946.9018 | 1324.7172 | 0 | 0 | 1324.7172 | 5.856e-05%
2026 | 129 | CB 129 | Tier-1 | Non-HFTD---16 | 2--1 | 2.6926 | 56 | 100% | 3.1821 | 23.64% | 0% | 76.36% | 0.037241 | 0 | 0 | 0.037241 | 0 | 0.035525 | 2.7817 | 0.012771 | 0.035525 | 2.7817 | 0.012771 | 0.037423 | 2.9304 | 0.012771 | 1.17% | 0.009111 | 0.00866 | 349.2616 | 7.9358 | 58.2971 | 283.0287 | 363.1501 | 0 | 0 | 363.1501 | 1.228e-06%
2026 | 1117 | 1117-1121F | Tier-1 | Non-HFTD---4 | 2--4 | 0.2763 | 27 | 100% | 101.5663 | 18.17% | 81.65% | 0.1832% | 0.91333 | 0 | 0 | 0.91333 | 0 | 0.87126 | 0.28544 | 3.0523 | 0.87126 | 0.28544 | 3.0523 | 0.91781 | 0.30069 | 3.0523 | 0.8992% | 0.007029 | 0.0066811 | 14449.6047 | 439.553 | 10775.9849 | 3234.0669 | 15065.4048 | 0 | 0 | 15065.4048 | 3.012e-05%
2026 | 462 | CB 462 | Tier-2 | Tier-2---19 | 2--4 | 2.1019 | 19 | 100% | 42.4238 | 96.69% | 0% | 3.313% | 2.0304 | 0 | 0 | 2.0304 | 0 | 1.9369 | 2.1714 | 0.89199 | 1.9369 | 2.1714 | 0.89199 | 2.0404 | 2.2874 | 0.89199 | 4.786% | 0.0069768 | 0.0066314 | 6080.6996 | 1110.385 | 1800.7984 | 3169.5162 | 6091.1906 | 0 | 0 | 6091.1906 | 6.696e-05%
2026 | 323 | 323-471 | Tier-1 | Non-HFTD---8 | 4--2 | 9.5176 | 267 | 100% | 28.3599 | 75.43% | 0% | 24.57% | 1.059 | 0 | 0 | 1.059 | 0 | 1.0102 | 9.8326 | 0.10274 | 1.0102 | 9.8326 | 0.10274 | 1.0641 | 10.358 | 0.10274 | 3.734% | 0.03033 | 0.028828 | 935.0577 | 152.0048 | 120.2204 | 662.8324 | 947.0204 | 0 | 0 | 947.0204 | 3.492e-05%
2026 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 0.20947 | 25 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 6.473 | 0.2164 | 29.912 | 6.473 | 0.2164 | 29.912 | 6.8189 | 0.22796 | 29.912 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2026 | 732 | CB 732 | Tier-1 | Non-HFTD---2 | 4--3 | 16.7686 | 825 | 100% | 213.1572 | 94.97% | 0% | 5.028% | 10.0208 | 0 | 0 | 10.0208 | 0 | 9.5591 | 17.3235 | 0.5518 | 9.5591 | 17.3235 | 0.5518 | 10.0699 | 18.2491 | 0.5518 | 4.701% | 0.049818 | 0.047352 | 4278.701 | 526.9055 | 864.1827 | 2887.6129 | 4289.9048 | 0 | 0 | 4289.9048 | 0.0003304%
2026 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 4.8975 | 146 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 72.5366 | 5.0596 | 14.3365 | 72.5366 | 5.0596 | 14.3365 | 76.4123 | 5.3299 | 14.3365 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2026 | 783 | CB 783 | Tier-1 | Non-HFTD---4 | 3--4 | 1.3273 | 6 | 100% | 129.217 | 41.62% | 57.78% | 0.5927% | 2.6624 | 0 | 0 | 2.6624 | 0 | 2.5397 | 1.3712 | 1.8522 | 2.5397 | 1.3712 | 1.8522 | 2.6754 | 1.4445 | 1.8522 | 2.06% | 0.014816 | 0.014083 | 8721.335 | 243.3525 | 6978.51 | 1499.4724 | 8986.4721 | 0 | 0 | 8986.4721 | 8.78e-05%
2026 | 341 | 341-1157F | Tier-1 | Non-HFTD---7 | 2--4 | 2.6621 | 96 | 100% | 34.4267 | 96.63% | 0% | 3.372% | 1.6467 | 0 | 0 | 1.6467 | 0 | 1.5708 | 2.7502 | 0.57115 | 1.5708 | 2.7502 | 0.57115 | 1.6547 | 2.8972 | 0.57115 | 4.783% | 0.0066766 | 0.0063461 | 5156.3263 | 996.266 | 92.4403 | 4067.62 | 5165.3804 | 0 | 0 | 5165.3804 | 5.43e-05%
2026 | 430 | CB 430 | Tier-1 | Non-HFTD---19 | 1--2 | 0.045833 | 1 | 100% | 0.27806 | 60.51% | 0% | 39.49% | 0.0083278 | 0 | 0 | 0.0083278 | 0 | 0.0079442 | 0.04735 | 0.16778 | 0.0079442 | 0.04735 | 0.16778 | 0.0083687 | 0.04988 | 0.16778 | 2.995% | 0.0002042 | 0.00019409 | 1361.6908 | 10.8448 | 808.9488 | 541.8972 | 1389.698 | 0 | 0 | 1389.698 | 2.746e-07%
2026 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 16.5267 | 1228 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 173.5489 | 17.0736 | 10.1648 | 173.5489 | 17.0736 | 10.1648 | 182.8218 | 17.9859 | 10.1648 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2026 | 322 | 322-32R | Tier-1 | Non-HFTD---19 | 1--2 | 0.064394 | 4 | 100% | 0.50266 | 78.22% | 0% | 21.78% | 0.019462 | 0 | 0 | 0.019462 | 0 | 0.018565 | 0.066525 | 0.27907 | 0.018565 | 0.066525 | 0.27907 | 0.019557 | 0.070079 | 0.27907 | 3.872% | 0.0003072 | 0.00029199 | 1636.2621 | 0.9533 | 1308.036 | 327.2728 | 1654.824 | 0 | 0 | 1654.824 | 6.418e-07%
2026 | 518 | 518-39 | Tier-1 | Non-HFTD---17 | 1--2 | 0.84644 | 38 | 100% | 1.403 | 67.89% | 0% | 32.11% | 0.047151 | 0 | 0 | 0.047151 | 0 | 0.044979 | 0.87445 | 0.051437 | 0.044979 | 0.87445 | 0.051437 | 0.047382 | 0.92117 | 0.051437 | 3.361% | 0.002089 | 0.0019856 | 671.6292 | 2.198 | 463.1642 | 206.267 | 682.8598 | 0 | 0 | 682.8598 | 1.555e-06%
2026 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 1.2636 | 42 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 19.4973 | 1.3055 | 14.9352 | 19.4973 | 1.3055 | 14.9352 | 20.539 | 1.3752 | 14.9352 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2026 | 152 | 152-1713F | Tier-1 | Non-HFTD---12 | 3--2 | 5.262 | 136 | 100% | 9.6728 | 69.07% | 0% | 30.93% | 0.33072 | 0 | 0 | 0.33072 | 0 | 0.31549 | 5.4361 | 0.058036 | 0.31549 | 5.4361 | 0.058036 | 0.33235 | 5.7265 | 0.058036 | 3.419% | 0.013625 | 0.01295 | 709.9482 | 124.6406 | 78.4846 | 506.823 | 721.3825 | 0 | 0 | 721.3825 | 1.091e-05%
2026 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 0.64527 | 28 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 15.4569 | 0.66662 | 23.187 | 15.4569 | 0.66662 | 23.187 | 16.2828 | 0.70224 | 23.187 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2026 | IB1 | CB IB1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.2845 | 58 | 100% | 2.8974 | 41.24% | 0% | 58.76% | 0.059153 | 0 | 0 | 0.059153 | 0 | 0.056428 | 3.3932 | 0.01663 | 0.056428 | 3.3932 | 0.01663 | 0.059443 | 3.5745 | 0.01663 | 2.042% | 0.0077878 | 0.0074023 | 372.0428 | 0.3241 | 172.327 | 199.3917 | 383.4268 | 0 | 0 | 383.4268 | 1.951e-06%
2026 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.46834 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 37.3591 | 0.48384 | 77.2141 | 37.3591 | 0.48384 | 77.2141 | 39.3553 | 0.50969 | 77.2141 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2026 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 2.6153 | 52 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.4094 | 2.7019 | 0.89175 | 2.4094 | 2.7019 | 0.89175 | 2.5382 | 2.8463 | 0.89175 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2026 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 13.2184 | 329 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 181.173 | 13.6559 | 13.2671 | 181.173 | 13.6559 | 13.2671 | 190.8533 | 14.3855 | 13.2671 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2026 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.054356 | 0 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.36233 | 0.056155 | 6.4524 | 0.36233 | 0.056155 | 6.4524 | 0.38169 | 0.059155 | 6.4524 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2026 | 702 | 702-27R | Tier-1 | Non-HFTD---3 | 4--3 | 12.2498 | 298 | 100% | 127.2983 | 14.57% | 79% | 6.429% | 0.91821 | 0 | 0 | 0.91821 | 0 | 0.87591 | 12.6552 | 0.069213 | 0.87591 | 12.6552 | 0.069213 | 0.92271 | 13.3314 | 0.069213 | 0.7213% | 0.039338 | 0.03739 | 3236.0467 | 32.4645 | 2654.2302 | 549.352 | 3380.0157 | 0 | 0 | 3380.0157 | 3.028e-05%
2026 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 4.9693 | 856 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 34.2033 | 5.1338 | 6.6624 | 34.2033 | 5.1338 | 6.6624 | 36.0308 | 5.4081 | 6.6624 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2026 | 192 | 192-657AE | Tier-1 | Non-HFTD---4 | 2--4 | 1.8044 | 96 | 100% | 94.561 | 98.93% | 0% | 1.074% | 4.6305 | 0 | 0 | 4.6305 | 0 | 4.4172 | 1.8641 | 2.3696 | 4.4172 | 1.8641 | 2.3696 | 4.6532 | 1.9637 | 2.3696 | 4.897% | 0.006219 | 0.0059112 | 15205.1851 | 2854.2403 | 2013.1644 | 10337.7804 | 15213.6876 | 0 | 0 | 15213.6876 | 0.0001527%
2026 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 2.7532 | 52 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 239.9918 | 2.8443 | 84.3759 | 239.9918 | 2.8443 | 84.3759 | 252.8149 | 2.9963 | 84.3759 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2026 | 52 | 52-18F | Tier-1 | Non-HFTD---12 | 2--2 | 3.9165 | 42 | 100% | 11.6184 | 68.06% | 0% | 31.94% | 0.39141 | 0 | 0 | 0.39141 | 0 | 0.37337 | 4.0461 | 0.09228 | 0.37337 | 4.0461 | 0.09228 | 0.39332 | 4.2623 | 0.09228 | 3.369% | 0.012594 | 0.011971 | 922.5162 | 0.22173 | 654.6115 | 267.6829 | 937.8622 | 0 | 0 | 937.8622 | 1.291e-05%
2026 | 940 | 940-391 | Tier-1 | Non-HFTD---18 | 1--1 | 1.8076 | 25 | 100% | 1.1106 | 27.65% | 0% | 72.35% | 0.015203 | 0 | 0 | 0.015203 | 0 | 0.014502 | 1.8674 | 0.0077658 | 0.014502 | 1.8674 | 0.0077658 | 0.015277 | 1.9672 | 0.0077658 | 1.369% | 0.004339 | 0.0041242 | 255.964 | 0.14879 | 87.5462 | 168.2691 | 265.6079 | 0 | 0 | 265.6079 | 5.013e-07%
2026 | 1081 | CB 1081 | Tier-1 | Non-HFTD---2 | 4--4 | 9.8183 | 503 | 100% | 237.9505 | 29.91% | 67.53% | 2.553% | 3.5234 | 0 | 0 | 3.5234 | 0 | 3.3611 | 10.1433 | 0.33136 | 3.3611 | 10.1433 | 0.33136 | 3.5406 | 10.6852 | 0.33136 | 1.481% | 0.036958 | 0.035128 | 6438.4369 | 198.6995 | 5359.42 | 880.3174 | 6673.437 | 0 | 0 | 6673.437 | 0.0001162%
2026 | 203 | 203-21R | Tier-1 | Non-HFTD---4 | 3--4 | 2.1493 | 204 | 100% | 165.9937 | 4.67% | 94.37% | 0.9641% | 0.38369 | 0 | 0 | 0.38369 | 0 | 0.36601 | 2.2204 | 0.16484 | 0.36601 | 2.2204 | 0.16484 | 0.38557 | 2.339 | 0.16484 | 0.2311% | 0.023296 | 0.022143 | 7125.2936 | 41.2792 | 6274.0075 | 810.0069 | 7479.0361 | 0 | 0 | 7479.0361 | 1.265e-05%
2026 | 510 | 510-49R | Tier-1 | Non-HFTD---1 | 3--4 | 2.222 | 211 | 100% | 240.5874 | 27.72% | 71.76% | 0.5245% | 3.301 | 0 | 0 | 3.301 | 0 | 3.149 | 2.2955 | 1.3718 | 3.149 | 2.2955 | 1.3718 | 3.3172 | 2.4182 | 1.3718 | 1.372% | 0.018276 | 0.017371 | 13164.1155 | 585.4029 | 9744.1726 | 2834.54 | 13659.6467 | 0 | 0 | 13659.6467 | 0.0001089%
2026 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 3.55 | 303 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 238.2603 | 3.6675 | 64.9659 | 238.2603 | 3.6675 | 64.9659 | 250.9909 | 3.8634 | 64.9659 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2026 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 2.7573 | 100 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 36.8826 | 2.8486 | 12.9477 | 36.8826 | 2.8486 | 12.9477 | 38.8532 | 3.0008 | 12.9477 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2026 | 362 | CB 362 | Tier-1 | Non-HFTD---5 | 3--3 | 4.5676 | 102 | 100% | 90.5945 | 20.96% | 74.63% | 4.416% | 0.93975 | 0 | 0 | 0.93975 | 0 | 0.89646 | 4.7188 | 0.18998 | 0.89646 | 4.7188 | 0.18998 | 0.94436 | 4.9709 | 0.18998 | 1.037% | 0.019673 | 0.018699 | 4605.0162 | 4.0643 | 4102.7241 | 498.2277 | 4794.5791 | 0 | 0 | 4794.5791 | 3.099e-05%
2026 | OS4 | CB OS4 | Tier-1 | Non-HFTD---16 | 2--1 | 2.4284 | 86 | 100% | 3.0117 | 33.83% | 0% | 66.17% | 0.050427 | 0 | 0 | 0.050427 | 0 | 0.048104 | 2.5088 | 0.019174 | 0.048104 | 2.5088 | 0.019174 | 0.050675 | 2.6428 | 0.019174 | 1.674% | 0.0070618 | 0.0067122 | 426.4805 | 1.5389 | 161.7401 | 263.2015 | 441.1779 | 0 | 0 | 441.1779 | 1.663e-06%
2026 | NTL1 | CB NTL1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.6614 | 519 | 100% | 2.8418 | 23.91% | 0% | 76.09% | 0.033635 | 0 | 0 | 0.033635 | 0 | 0.032085 | 3.7826 | 0.0084824 | 0.032085 | 3.7826 | 0.0084824 | 0.033799 | 3.9847 | 0.0084824 | 1.184% | 0.0099992 | 0.0095042 | 284.2073 | 4.5526 | 60.82 | 218.8347 | 295.4693 | 0 | 0 | 295.4693 | 1.109e-06%
2026 | 1297 | 1297-34F | Tier-1 | Non-HFTD---4 | 2--4 | 2.0714 | 47 | 100% | 97.1169 | 3.668% | 94.54% | 1.791% | 0.17635 | 0 | 0 | 0.17635 | 0 | 0.16822 | 2.1399 | 0.078613 | 0.16822 | 2.1399 | 0.078613 | 0.17721 | 2.2542 | 0.078613 | 0.1816% | 0.012533 | 0.011912 | 7749.0176 | 8.2538 | 6940.7523 | 800.0115 | 8137.7662 | 0 | 0 | 8137.7662 | 5.815e-06%
2026 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 0.081438 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0024413 | 0.084133 | 0.029017 | 0.0024413 | 0.084133 | 0.029017 | 0.0025718 | 0.088628 | 0.029017 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2026 | 1482 | 1482-28 | Tier-1 | Non-HFTD---14 | 2--2 | 3.2782 | 104 | 100% | 5.0457 | 55.06% | 0% | 44.94% | 0.13753 | 0 | 0 | 0.13753 | 0 | 0.13119 | 3.3867 | 0.038737 | 0.13119 | 3.3867 | 0.038737 | 0.1382 | 3.5677 | 0.038737 | 2.726% | 0.0090634 | 0.0086148 | 556.7146 | 0.18825 | 329.2696 | 227.2568 | 569.7429 | 0 | 0 | 569.7429 | 4.535e-06%
2026 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 17.9011 | 1159 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 526.6286 | 18.4935 | 28.4764 | 526.6286 | 18.4935 | 28.4764 | 554.7671 | 19.4817 | 28.4764 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2026 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 6.2326 | 240 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 4.3523 | 6.4388 | 0.67594 | 4.3523 | 6.4388 | 0.67594 | 4.5848 | 6.7828 | 0.67594 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2026 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 7.3522 | 280 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 156.9652 | 7.5955 | 20.6654 | 156.9652 | 7.5955 | 20.6654 | 165.3521 | 8.0014 | 20.6654 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2026 | 505 | CB 505 | Tier-1 | Non-HFTD---9 | 2--3 | 2.4237 | 236 | 100% | 21.0176 | 91.98% | 0% | 8.019% | 0.95694 | 0 | 0 | 0.95694 | 0 | 0.91285 | 2.5039 | 0.36458 | 0.91285 | 2.5039 | 0.36458 | 0.96163 | 2.6377 | 0.36458 | 4.553% | 0.0074238 | 0.0070563 | 2831.1077 | 271.0214 | 968.8336 | 1591.2527 | 2842.9314 | 0 | 0 | 2842.9314 | 3.156e-05%
2026 | 550 | 550-665R | Tier-1 | Non-HFTD---14 | 2--2 | 4.5705 | 162 | 100% | 7.2973 | 61.93% | 0% | 38.07% | 0.22372 | 0 | 0 | 0.22372 | 0 | 0.21341 | 4.7217 | 0.045198 | 0.21341 | 4.7217 | 0.045198 | 0.22481 | 4.974 | 0.045198 | 3.066% | 0.01349 | 0.012822 | 540.9468 | 37.0768 | 158.5779 | 345.2921 | 551.6702 | 0 | 0 | 551.6702 | 7.377e-06%
2026 | 92 | CB 92 | Tier-1 | Non-HFTD---6 | 3--3 | 2.9091 | 147 | 100% | 46.3322 | 87.55% | 8.668% | 3.778% | 2.008 | 0 | 0 | 2.008 | 0 | 1.9155 | 3.0054 | 0.63735 | 1.9155 | 3.0054 | 0.63735 | 2.0178 | 3.166 | 0.63735 | 4.334% | 0.013793 | 0.013111 | 3359.0098 | 253.9545 | 2011.5361 | 1093.5193 | 3380.7821 | 0 | 0 | 3380.7821 | 6.622e-05%
2026 | 403 | 403-9F | Tier-1 | Non-HFTD---20 | 1--1 | 0.82969 | 47 | 100% | 0.45165 | 12.22% | 0% | 87.78% | 0.0027327 | 0 | 0 | 0.0027327 | 0 | 0.0026068 | 0.85715 | 0.0030412 | 0.0026068 | 0.85715 | 0.0030412 | 0.0027461 | 0.90295 | 0.0030412 | 0.605% | 0.0021892 | 0.0020808 | 206.3063 | 0.33556 | 40.449 | 165.5217 | 215.737 | 0 | 0 | 215.737 | 9.011e-08%
2026 | 330 | 330-44R | Tier-1 | Non-HFTD---19 | 1--2 | 0.010227 | 0 | 100% | 0.13525 | 15.38% | 0% | 84.62% | 0.0010298 | 0 | 0 | 0.0010298 | 0 | 0.00098233 | 0.010566 | 0.092974 | 0.00098233 | 0.010566 | 0.092974 | 0.0010348 | 0.01113 | 0.092974 | 0.7614% | 0.0001638 | 0.00015569 | 825.6908 | 0.52574 | 190.4747 | 634.6904 | 862.0768 | 0 | 0 | 862.0768 | 3.396e-08%
2026 | 465 | CB 465 | Tier-1 | Non-HFTD---11 | 1--3 | 0.51648 | 20 | 100% | 9.9117 | 96.03% | 0% | 3.967% | 0.47116 | 0 | 0 | 0.47116 | 0 | 0.44946 | 0.53357 | 0.84236 | 0.44946 | 0.53357 | 0.84236 | 0.47347 | 0.56208 | 0.84236 | 4.754% | 0.0023928 | 0.0022744 | 4142.2995 | 915.7141 | 14.9285 | 3211.6569 | 4150.8578 | 0 | 0 | 4150.8578 | 1.554e-05%
2026 | VS2 | CB VS2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.0479 | 620 | 100% | 11.3625 | 51.95% | 0% | 48.05% | 0.29219 | 0 | 0 | 0.29219 | 0 | 0.27873 | 7.2812 | 0.038281 | 0.27873 | 7.2812 | 0.038281 | 0.29362 | 7.6702 | 0.038281 | 2.572% | 0.020771 | 0.019743 | 547.0307 | 29.9029 | 126.8526 | 390.2752 | 560.7192 | 0 | 0 | 560.7192 | 9.635e-06%
2026 | 765 | 765-53 | Tier-1 | Non-HFTD---11 | 1--4 | 0.22367 | 0 | 100% | 10.2799 | 97.92% | 0% | 2.076% | 0.49829 | 0 | 0 | 0.49829 | 0 | 0.47533 | 0.23108 | 2.057 | 0.47533 | 0.23108 | 2.057 | 0.50073 | 0.24342 | 2.057 | 4.847% | 0.0009128 | 0.00086762 | 11261.9019 | 1681.3147 | 2761.922 | 6818.6652 | 11274.0796 | 0 | 0 | 11274.0796 | 1.643e-05%
2026 | 256 | 256-46AE | Tier-1 | Non-HFTD---14 | 3--1 | 4.8671 | 108 | 100% | 5.4684 | 29.52% | 0% | 70.48% | 0.079899 | 0 | 0 | 0.079899 | 0 | 0.076218 | 5.0282 | 0.015158 | 0.076218 | 5.0282 | 0.015158 | 0.080291 | 5.2968 | 0.015158 | 1.461% | 0.01432 | 0.013611 | 381.8681 | 0.20253 | 137.1678 | 244.4977 | 395.8848 | 0 | 0 | 395.8848 | 2.635e-06%
2026 | 76 | 76-266F | Tier-1 | Non-HFTD---19 | 1--1 | 0.21686 | 20 | 100% | 0.3287 | 26.14% | 0% | 73.86% | 0.0042534 | 0 | 0 | 0.0042534 | 0 | 0.0040575 | 0.22403 | 0.018111 | 0.0040575 | 0.22403 | 0.018111 | 0.0042743 | 0.236 | 0.018111 | 1.294% | 0.0008422 | 0.00080051 | 390.2914 | 7.9469 | 80.8159 | 301.5286 | 405.3035 | 0 | 0 | 405.3035 | 1.403e-07%
2026 | 1480 | 1480-26F | Tier-1 | Non-HFTD---18 | 1--1 | 1.1896 | 35 | 100% | 1.5754 | 25.22% | 0% | 74.78% | 0.019667 | 0 | 0 | 0.019667 | 0 | 0.018761 | 1.229 | 0.015265 | 0.018761 | 1.229 | 0.015265 | 0.019764 | 1.2947 | 0.015265 | 1.248% | 0.0040818 | 0.0038798 | 385.9459 | 1.0392 | 118.4615 | 266.4452 | 400.9759 | 0 | 0 | 400.9759 | 6.486e-07%
2026 | WY1 | CB WY1 | Tier-1 | Non-HFTD---20 | 1--1 | 0.1875 | 0 | 100% | 0.14453 | 1.564% | 0% | 98.44% | 0.00011192 | 0 | 0 | 0.00011192 | 0 | 0.00010677 | 0.19371 | 0.00055117 | 0.00010677 | 0.19371 | 0.00055117 | 0.00011247 | 0.20406 | 0.00055117 | 0.07744% | 0.0005 | 0.00047525 | 289.0698 | 0.75643 | 26.8687 | 261.4447 | 303.8884 | 0 | 0 | 303.8884 | 3.691e-09%
2026 | 797 | CB 797 | Tier-1 | Non-HFTD---5 | 1--5 | 0.92273 | 13 | 100% | 65.0189 | 98.85% | 0% | 1.151% | 3.1814 | 0 | 0 | 3.1814 | 0 | 3.0348 | 0.95326 | 3.1836 | 3.0348 | 0.95326 | 3.1836 | 3.197 | 1.0042 | 3.1836 | 4.893% | 0.0039484 | 0.003753 | 16467.148 | 2087.333 | 3503.3467 | 10876.4683 | 16477.0185 | 0 | 0 | 16477.0185 | 0.0001049%
2026 | WA5 | CB WA5 | Tier-1 | Non-HFTD---8 | 4--2 | 14.9795 | 462 | 100% | 31.7966 | 66.36% | 0% | 33.64% | 1.0444 | 0 | 0 | 1.0444 | 0 | 0.99628 | 15.4752 | 0.064379 | 0.99628 | 15.4752 | 0.064379 | 1.0495 | 16.3021 | 0.064379 | 3.285% | 0.046317 | 0.044024 | 686.5028 | 95.2087 | 167.8003 | 423.4938 | 698.531 | 0 | 0 | 698.531 | 3.444e-05%
2026 | 322 | 322-822F | Tier-1 | Non-HFTD---18 | 1--1 | 1.136 | 22 | 100% | 0.86968 | 23.9% | 0% | 76.1% | 0.010288 | 0 | 0 | 0.010288 | 0 | 0.0098142 | 1.1735 | 0.0083628 | 0.0098142 | 1.1735 | 0.0083628 | 0.010339 | 1.2363 | 0.0083628 | 1.183% | 0.0028306 | 0.0026905 | 307.242 | 6.8624 | 53.816 | 246.5637 | 319.4186 | 0 | 0 | 319.4186 | 3.393e-07%
2026 | 365 | 365-648R | Tier-1 | Non-HFTD---7 | 3--3 | 3.785 | 254 | 100% | 37.1137 | 20.26% | 73.09% | 6.654% | 0.37221 | 0 | 0 | 0.37221 | 0 | 0.35506 | 3.9103 | 0.090803 | 0.35506 | 3.9103 | 0.090803 | 0.37403 | 4.1192 | 0.090803 | 1.003% | 0.015525 | 0.014757 | 2390.5758 | 8.2255 | 2060.9087 | 321.4416 | 2489.8485 | 0 | 0 | 2489.8485 | 1.227e-05%
2026 | 402 | 402-820F | Tier-1 | Non-HFTD---11 | 2--3 | 2.1513 | 197 | 100% | 12.3895 | 88.33% | 0% | 11.67% | 0.54174 | 0 | 0 | 0.54174 | 0 | 0.51678 | 2.2225 | 0.23252 | 0.51678 | 2.2225 | 0.23252 | 0.54439 | 2.3413 | 0.23252 | 4.373% | 0.0060732 | 0.0057726 | 2040.0308 | 5.8898 | 1788.8383 | 245.3027 | 2052.4249 | 0 | 0 | 2052.4249 | 1.786e-05%
2026 | MV1 | CB MV1 | Tier-1 | Non-HFTD---4 | 3--4 | 5.3483 | 429 | 100% | 150.3384 | 97.79% | 0% | 2.21% | 7.2773 | 0 | 0 | 7.2773 | 0 | 6.942 | 5.5253 | 1.2564 | 6.942 | 5.5253 | 1.2564 | 7.3129 | 5.8205 | 1.2564 | 4.841% | 0.014765 | 0.014034 | 10182.3567 | 1618.5344 | 97.4794 | 8466.3429 | 10194.0779 | 0 | 0 | 10194.0779 | 0.00024%
2026 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.39659 | 8 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.67947 | 0.40972 | 1.6584 | 0.67947 | 0.40972 | 1.6584 | 0.71577 | 0.43161 | 1.6584 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2026 | NO3 | CB NO3 | Tier-1 | Non-HFTD---16 | 2--1 | 3.3623 | 80 | 100% | 3.2681 | 33.34% | 0% | 66.66% | 0.053939 | 0 | 0 | 0.053939 | 0 | 0.051454 | 3.4735 | 0.014813 | 0.051454 | 3.4735 | 0.014813 | 0.054203 | 3.6591 | 0.014813 | 1.65% | 0.008886 | 0.0084461 | 367.7794 | 0.18447 | 144.8976 | 222.6973 | 380.5463 | 0 | 0 | 380.5463 | 1.779e-06%
2026 | 325 | 325-1220R | Tier-1 | Non-HFTD---8 | 4--2 | 21.6898 | 393 | 100% | 37.7086 | 59.54% | 0% | 40.46% | 1.1113 | 0 | 0 | 1.1113 | 0 | 1.0601 | 22.4076 | 0.047312 | 1.0601 | 22.4076 | 0.047312 | 1.1168 | 23.6049 | 0.047312 | 2.947% | 0.060023 | 0.057052 | 628.2334 | 4.0248 | 373.6526 | 250.5559 | 641.471 | 0 | 0 | 641.471 | 3.665e-05%
2026 | 166 | CB 166 | Tier-1 | Non-HFTD---10 | 3--2 | 5.1707 | 175 | 100% | 21.6566 | 82.43% | 0% | 17.57% | 0.88364 | 0 | 0 | 0.88364 | 0 | 0.84294 | 5.3418 | 0.1578 | 0.84294 | 5.3418 | 0.1578 | 0.88797 | 5.6272 | 0.1578 | 4.08% | 0.015112 | 0.014364 | 1433.0361 | 0.84572 | 1200.0855 | 232.1049 | 1446.1491 | 0 | 0 | 1446.1491 | 2.914e-05%
2026 | 94 | 94-41 | Tier-1 | Non-HFTD---2 | 4--4 | 13.5683 | 315 | 100% | 189.6711 | 96.69% | 0% | 3.312% | 9.0777 | 0 | 0 | 9.0777 | 0 | 8.6595 | 14.0174 | 0.61777 | 8.6595 | 14.0174 | 0.61777 | 9.1222 | 14.7663 | 0.61777 | 4.786% | 0.03601 | 0.034228 | 5267.1204 | 1003.7798 | 888.4702 | 3374.8704 | 5276.2062 | 0 | 0 | 5276.2062 | 0.0002994%
2026 | 88 | CB 88 | Tier-1 | Non-HFTD---6 | 4--3 | 10.0387 | 412 | 100% | 58.8668 | 89.39% | 0% | 10.61% | 2.6047 | 0 | 0 | 2.6047 | 0 | 2.4847 | 10.3709 | 0.23958 | 2.4847 | 10.3709 | 0.23958 | 2.6174 | 10.925 | 0.23958 | 4.425% | 0.033053 | 0.031417 | 1780.9916 | 215.4092 | 736.244 | 829.3384 | 1790.8352 | 0 | 0 | 1790.8352 | 8.589e-05%
2026 | 387 | CB 387 | Tier-1 | Non-HFTD---2 | 4--4 | 6.7638 | 316 | 100% | 522.65 | 70.14% | 28.94% | 0.9137% | 18.1467 | 0 | 0 | 18.1467 | 0 | 17.3107 | 6.9877 | 2.4773 | 17.3107 | 6.9877 | 2.4773 | 18.2357 | 7.361 | 2.4773 | 3.472% | 0.067633 | 0.064286 | 7727.6908 | 947.907 | 2193.816 | 4585.9679 | 7847.8494 | 0 | 0 | 7847.8494 | 0.0005984%
2026 | 365 | CB 365 | Tier-1 | Non-HFTD---3 | 4--3 | 10.8739 | 264 | 100% | 153.8294 | 16.84% | 79.11% | 4.05% | 1.282 | 0 | 0 | 1.282 | 0 | 1.2229 | 11.2338 | 0.10886 | 1.2229 | 11.2338 | 0.10886 | 1.2883 | 11.834 | 0.10886 | 0.8334% | 0.031529 | 0.029968 | 4879.0131 | 4.4935 | 4354.8547 | 519.6649 | 5090.3229 | 0 | 0 | 5090.3229 | 4.228e-05%
2026 | 161 | 161-989F | Tier-1 | Non-HFTD---17 | 1--2 | 0.19681 | 27 | 100% | 0.82181 | 77.98% | 0% | 22.02% | 0.031721 | 0 | 0 | 0.031721 | 0 | 0.03026 | 0.20332 | 0.14883 | 0.03026 | 0.20332 | 0.14883 | 0.031877 | 0.21419 | 0.14883 | 3.86% | 0.0006838 | 0.00064995 | 1201.8318 | 151.5 | 35.0825 | 1015.2493 | 1215.615 | 0 | 0 | 1215.615 | 1.046e-06%
2026 | 404 | CB 404 | Tier-1 | Non-HFTD---15 | 1--3 | 0.3267 | 6 | 100% | 3.4322 | 87.98% | 0% | 12.02% | 0.14946 | 0 | 0 | 0.14946 | 0 | 0.14258 | 0.33752 | 0.42243 | 0.14258 | 0.33752 | 0.42243 | 0.1502 | 0.35555 | 0.42243 | 4.355% | 0.0014236 | 0.0013531 | 2410.8954 | 1.0401 | 2142.2971 | 267.5582 | 2425.9921 | 0 | 0 | 2425.9921 | 4.929e-06%
2026 | 471 | CB 471 | Tier-1 | Non-HFTD---1 | 4--5 | 9.5888 | 824 | 100% | 3808.7328 | 99.83% | 0% | 0.1692% | 188.2133 | 0 | 0 | 188.2133 | 0 | 179.5427 | 9.9061 | 18.1244 | 179.5427 | 9.9061 | 18.1244 | 189.1359 | 10.4354 | 18.1244 | 4.942% | 0.030567 | 0.029054 | 124601.1385 | 20145.8945 | 297.3105 | 104157.9336 | 124612.117 | 0 | 0 | 124612.117 | 0.006207%
2026 | 900 | CB 900 | Tier-1 | Non-HFTD---19 | 1--3 | 0.042803 | 42 | 100% | 0.53356 | 93.68% | 0% | 6.317% | 0.024743 | 0 | 0 | 0.024743 | 0 | 0.023603 | 0.04422 | 0.53377 | 0.023603 | 0.04422 | 0.53377 | 0.024864 | 0.046582 | 0.53377 | 4.637% | 0.0001684 | 0.00016006 | 3168.3903 | 480.3966 | 18.1813 | 2669.8125 | 3178.8134 | 0 | 0 | 3178.8134 | 8.159e-07%
2026 | 263 | CB 263 | Tier-1 | Non-HFTD---13 | 1--2 | 1.1358 | 53 | 100% | 5.0642 | 81.76% | 0% | 18.24% | 0.20495 | 0 | 0 | 0.20495 | 0 | 0.1955 | 1.1734 | 0.16662 | 0.1955 | 1.1734 | 0.16662 | 0.20595 | 1.2361 | 0.16662 | 4.047% | 0.0045504 | 0.0043252 | 1112.9117 | 144.2639 | 21.0571 | 947.5907 | 1123.4851 | 0 | 0 | 1123.4851 | 6.758e-06%
2026 | 716 | CB 716 | Tier-1 | Non-HFTD---17 | 1--2 | 0.23504 | 15 | 100% | 1.616 | 79.4% | 0% | 20.6% | 0.063516 | 0 | 0 | 0.063516 | 0 | 0.06059 | 0.24282 | 0.24953 | 0.06059 | 0.24282 | 0.24953 | 0.063827 | 0.25579 | 0.24953 | 3.93% | 0.0010432 | 0.00099156 | 1549.1257 | 170.2187 | 205.5076 | 1173.3993 | 1565.7446 | 0 | 0 | 1565.7446 | 2.095e-06%
2026 | LV2 | CB LV2 | Tier-1 | Non-HFTD---10 | 3--2 | 9.3228 | 280 | 100% | 15.9867 | 57.43% | 0% | 42.57% | 0.4545 | 0 | 0 | 0.4545 | 0 | 0.43356 | 9.6313 | 0.045016 | 0.43356 | 9.6313 | 0.045016 | 0.45673 | 10.1459 | 0.045016 | 2.843% | 0.026716 | 0.025394 | 598.3883 | 38.8763 | 209.6571 | 349.8549 | 611.653 | 0 | 0 | 611.653 | 1.499e-05%
2026 | FRD1 | CB FRD1 | Tier-1 | Non-HFTD---20 | 1--1 | 0.72899 | 27 | 100% | 0.37361 | 16.66% | 0% | 83.34% | 0.0030815 | 0 | 0 | 0.0030815 | 0 | 0.0029395 | 0.75311 | 0.0039032 | 0.0029395 | 0.75311 | 0.0039032 | 0.0030966 | 0.79335 | 0.0039032 | 0.8248% | 0.001599 | 0.0015198 | 233.6497 | 0.89583 | 52.0165 | 180.7373 | 243.7901 | 0 | 0 | 243.7901 | 1.016e-07%
2026 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.034091 | 0 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.2556 | 0.035219 | 35.6511 | 1.2556 | 0.035219 | 35.6511 | 1.3227 | 0.037101 | 35.6511 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2026 | PL4 | CB PL4 | Tier-1 | Non-HFTD---12 | 3--1 | 10.2286 | 356 | 100% | 13.8266 | 47.94% | 0% | 52.06% | 0.3281 | 0 | 0 | 0.3281 | 0 | 0.31299 | 10.5671 | 0.029619 | 0.31299 | 10.5671 | 0.029619 | 0.32971 | 11.1317 | 0.029619 | 2.373% | 0.027903 | 0.026522 | 495.5242 | 0.19412 | 260.9853 | 234.3448 | 508.9589 | 0 | 0 | 508.9589 | 1.082e-05%
2026 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 2.6021 | 595 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 61.0795 | 2.6882 | 22.721 | 61.0795 | 2.6882 | 22.721 | 64.343 | 2.8319 | 22.721 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2026 | 454 | 454-45AE | Tier-1 | Non-HFTD---2 | 4--4 | 4.39 | 160 | 100% | 491.7858 | 41.61% | 57.78% | 0.6067% | 10.13 | 0 | 0 | 10.13 | 0 | 9.6633 | 4.5353 | 2.1307 | 9.6633 | 4.5353 | 2.1307 | 10.1796 | 4.7776 | 2.1307 | 2.06% | 0.084004 | 0.079846 | 5854.3004 | 713.107 | 3089.276 | 2051.9175 | 6032.3112 | 0 | 0 | 6032.3112 | 0.000334%
2026 | 329 | 329-215F | Tier-1 | Non-HFTD---6 | 3--3 | 1.3032 | 53 | 100% | 64.9248 | 1.785% | 96.02% | 2.2% | 0.05735 | 0 | 0 | 0.05735 | 0 | 0.054708 | 1.3463 | 0.040635 | 0.054708 | 1.3463 | 0.040635 | 0.057631 | 1.4183 | 0.040635 | 0.08833% | 0.021703 | 0.020628 | 2991.5676 | 12.9271 | 2341.0516 | 637.589 | 3144.5818 | 0 | 0 | 3144.5818 | 1.891e-06%
2026 | 155 | 155-40 | Tier-1 | Non-HFTD---16 | 2--1 | 4.411 | 109 | 100% | 3.7492 | 25.26% | 0% | 74.74% | 0.046886 | 0 | 0 | 0.046886 | 0 | 0.044726 | 4.5569 | 0.0098149 | 0.044726 | 4.5569 | 0.0098149 | 0.047116 | 4.8004 | 0.0098149 | 1.251% | 0.012188 | 0.011585 | 307.6104 | 0.55017 | 96.2898 | 210.7705 | 319.5829 | 0 | 0 | 319.5829 | 1.546e-06%
2026 | 326 | 326-35R | Tier-1 | Non-HFTD---2 | 4--4 | 13.9548 | 334 | 100% | 586.1826 | 18.71% | 79.88% | 1.411% | 5.4284 | 0 | 0 | 5.4284 | 0 | 5.1784 | 14.4166 | 0.35919 | 5.1784 | 14.4166 | 0.35919 | 5.455 | 15.1869 | 0.35919 | 0.9261% | 0.07497 | 0.071259 | 7818.9373 | 361.909 | 5822.8865 | 1634.1418 | 8149.9516 | 0 | 0 | 8149.9516 | 0.000179%
2026 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 3.2034 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 64.7607 | 3.3094 | 19.5689 | 64.7607 | 3.3094 | 19.5689 | 68.2209 | 3.4862 | 19.5689 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2026 | 701 | 701-48AE | Tier-1 | Non-HFTD---4 | 3--4 | 3.0439 | 162 | 100% | 111.3526 | 1.512% | 96.4% | 2.091% | 0.083358 | 0 | 0 | 0.083358 | 0 | 0.079518 | 3.1447 | 0.025287 | 0.079518 | 3.1447 | 0.025287 | 0.083767 | 3.3127 | 0.025287 | 0.07486% | 0.014184 | 0.013482 | 7850.7987 | 18.6835 | 7007.5279 | 824.5872 | 8253.4683 | 0 | 0 | 8253.4683 | 2.749e-06%
2026 | 170 | 170-46 | Tier-1 | Non-HFTD---6 | 5--2 | 14.4293 | 566 | 100% | 63.3107 | 39.69% | 47.72% | 12.59% | 1.2437 | 0 | 0 | 1.2437 | 0 | 1.1864 | 14.9068 | 0.07959 | 1.1864 | 14.9068 | 0.07959 | 1.2498 | 15.7033 | 0.07959 | 1.964% | 0.099838 | 0.094896 | 634.1343 | 13.2723 | 434.6906 | 186.1714 | 654.0524 | 0 | 0 | 654.0524 | 4.101e-05%
2026 | 61 | CB 61 | Tier-1 | Non-HFTD---3 | 4--4 | 8.4142 | 700 | 100% | 184.2595 | 17.6% | 78.77% | 3.63% | 1.6051 | 0 | 0 | 1.6051 | 0 | 1.5312 | 8.6926 | 0.17615 | 1.5312 | 8.6926 | 0.17615 | 1.613 | 9.1571 | 0.17615 | 0.8711% | 0.035306 | 0.033559 | 5218.8994 | 61.45 | 4296.865 | 860.5843 | 5442.858 | 0 | 0 | 5442.858 | 5.293e-05%
2026 | 708 | CB 708 | Tier-1 | Non-HFTD---11 | 2--2 | 0.79432 | 18 | 100% | 12.3602 | 94.92% | 0.8388% | 4.245% | 0.58072 | 0 | 0 | 0.58072 | 0 | 0.55397 | 0.8206 | 0.67508 | 0.55397 | 0.8206 | 0.67508 | 0.58357 | 0.86445 | 0.67508 | 4.698% | 0.0077752 | 0.0073903 | 1589.6964 | 132.6057 | 705.9862 | 751.1045 | 1593.9055 | 0 | 0 | 1593.9055 | 1.915e-05%
2026 | SW2 | CB SW2 | Tier-1 | Non-HFTD---14 | 3--1 | 6.287 | 115 | 100% | 6.1621 | 30.27% | 0% | 69.73% | 0.092335 | 0 | 0 | 0.092335 | 0 | 0.088081 | 6.495 | 0.013561 | 0.088081 | 6.495 | 0.013561 | 0.092787 | 6.8421 | 0.013561 | 1.498% | 0.016864 | 0.016029 | 365.4058 | 0.34604 | 132.8123 | 232.2474 | 378.6748 | 0 | 0 | 378.6748 | 3.045e-06%
2026 | EO2 | CB EO2 | Tier-1 | Non-HFTD---14 | 3--1 | 8.4316 | 236 | 100% | 6.9651 | 27.51% | 0% | 72.49% | 0.094861 | 0 | 0 | 0.094861 | 0 | 0.090491 | 8.7106 | 0.010389 | 0.090491 | 8.7106 | 0.010389 | 0.095326 | 9.176 | 0.010389 | 1.362% | 0.021169 | 0.020122 | 329.0193 | 1.1923 | 105.9838 | 221.8432 | 341.4396 | 0 | 0 | 341.4396 | 3.128e-06%
2026 | 95 | 95-34 | Tier-1 | Non-HFTD---9 | 2--3 | 1.5831 | 108 | 100% | 20.4353 | 56.35% | 39.11% | 4.547% | 0.56998 | 0 | 0 | 0.56998 | 0 | 0.54372 | 1.6355 | 0.33245 | 0.54372 | 1.6355 | 0.33245 | 0.57277 | 1.7229 | 0.33245 | 2.789% | 0.0092856 | 0.008826 | 2200.7529 | 196.7754 | 835.923 | 1168.0545 | 2250.7837 | 0 | 0 | 2250.7837 | 1.88e-05%
2026 | 341 | 341-1179 | Tier-1 | Non-HFTD---9 | 1--4 | 1.0375 | 44 | 100% | 16.5229 | 96.72% | 0% | 3.284% | 0.79103 | 0 | 0 | 0.79103 | 0 | 0.75459 | 1.0718 | 0.70401 | 0.75459 | 1.0718 | 0.70401 | 0.7949 | 1.1291 | 0.70401 | 4.787% | 0.002784 | 0.0026462 | 5934.9652 | 1118.6399 | 28.4603 | 4787.865 | 5945.1152 | 0 | 0 | 5945.1152 | 2.609e-05%
2026 | EO3 | CB EO3 | Tier-1 | Non-HFTD---3 | 4--3 | 14.1508 | 390 | 100% | 120.8831 | 92.52% | 0% | 7.481% | 5.5361 | 0 | 0 | 5.5361 | 0 | 5.281 | 14.6191 | 0.36124 | 5.281 | 14.6191 | 0.36124 | 5.5632 | 15.4002 | 0.36124 | 4.58% | 0.038956 | 0.037028 | 3103.0517 | 661.6926 | 179.4344 | 2261.9247 | 3115.1408 | 0 | 0 | 3115.1408 | 0.0001826%
2026 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 11.0316 | 1008 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 153.8343 | 11.3967 | 13.4981 | 153.8343 | 11.3967 | 13.4981 | 162.0539 | 12.0057 | 13.4981 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2026 | 759 | 759-13AE | Tier-1 | Non-HFTD---10 | 4--2 | 14.8888 | 631 | 100% | 22.2365 | 59.69% | 0% | 40.31% | 0.65701 | 0 | 0 | 0.65701 | 0 | 0.62675 | 15.3815 | 0.040747 | 0.62675 | 15.3815 | 0.040747 | 0.66023 | 16.2034 | 0.040747 | 2.955% | 0.039311 | 0.037365 | 565.6533 | 37.0216 | 132.6301 | 396.0016 | 577.5278 | 0 | 0 | 577.5278 | 2.167e-05%
2026 | 266 | CB 266 | Tier-1 | Non-HFTD---7 | 2--4 | 1.4792 | 31 | 100% | 30.6273 | 96.93% | 0% | 3.069% | 1.4695 | 0 | 0 | 1.4695 | 0 | 1.4018 | 1.5281 | 0.91736 | 1.4018 | 1.5281 | 0.91736 | 1.4767 | 1.6098 | 0.91736 | 4.798% | 0.005299 | 0.0050367 | 5779.8249 | 166.0393 | 4572.2436 | 1041.5419 | 5789.0623 | 0 | 0 | 5789.0623 | 4.846e-05%
2026 | 1481 | 1481-5AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.032977 | 0 | 100% | 0.036092 | 1.509% | 0% | 98.49% | 2.6963e-05 | 0 | 0 | 2.6963e-05 | 0 | 2.5721e-05 | 0.034069 | 0.00075497 | 2.5721e-05 | 0.034069 | 0.00075497 | 2.7095e-05 | 0.035889 | 0.00075497 | 0.07471% | 0.0001132 | 0.0001076 | 318.8351 | 0.53572 | 31.4788 | 286.8206 | 335.1888 | 0 | 0 | 335.1888 | 8.891e-10%
2026 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 12.0589 | 952 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 290.7937 | 12.458 | 23.342 | 290.7937 | 12.458 | 23.342 | 306.3312 | 13.1236 | 23.342 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2026 | 321 | CB 321 | Tier-1 | Non-HFTD---9 | 3--2 | 5.2511 | 131 | 100% | 22.0824 | 85.16% | 0% | 14.84% | 0.9309 | 0 | 0 | 0.9309 | 0 | 0.88801 | 5.4249 | 0.16369 | 0.88801 | 5.4249 | 0.16369 | 0.93546 | 5.7147 | 0.16369 | 4.216% | 0.014142 | 0.013442 | 1561.434 | 63.0678 | 966.4548 | 531.9115 | 1573.4991 | 0 | 0 | 1573.4991 | 3.07e-05%
2026 | 286 | 286-989AE | Tier-1 | Non-HFTD---3 | 4--3 | 10.8825 | 1225 | 100% | 139.8716 | 4.025% | 90.57% | 5.409% | 0.2787 | 0 | 0 | 0.2787 | 0 | 0.26586 | 11.2427 | 0.023647 | 0.26586 | 11.2427 | 0.023647 | 0.28006 | 11.8434 | 0.023647 | 0.1993% | 0.03669 | 0.034874 | 3812.2742 | 15.0936 | 3277.8049 | 519.3757 | 4002.8176 | 0 | 0 | 4002.8176 | 9.19e-06%
2026 | 303 | CB 303 | Tier-1 | Non-HFTD---2 | 4--4 | 12.3992 | 651 | 100% | 349.915 | 18.7% | 78.58% | 2.715% | 3.2397 | 0 | 0 | 3.2397 | 0 | 3.0905 | 12.8095 | 0.24126 | 3.0905 | 12.8095 | 0.24126 | 3.2556 | 13.494 | 0.24126 | 0.9259% | 0.047695 | 0.045334 | 7336.5129 | 14.6418 | 6603.3249 | 718.5462 | 7647.1195 | 0 | 0 | 7647.1195 | 0.0001068%
2026 | 409 | 409-38R | Tier-1 | Non-HFTD---14 | 2--2 | 3.0827 | 145 | 100% | 5.3106 | 56.43% | 0% | 43.57% | 0.14833 | 0 | 0 | 0.14833 | 0 | 0.14149 | 3.1847 | 0.044429 | 0.14149 | 3.1847 | 0.044429 | 0.14905 | 3.3549 | 0.044429 | 2.793% | 0.008986 | 0.0085412 | 590.983 | 1.708 | 347.574 | 241.701 | 604.394 | 0 | 0 | 604.394 | 4.891e-06%
2026 | 43 | 43-443 | Tier-1 | Non-HFTD---19 | 1--1 | 0.15364 | 0 | 100% | 0.25601 | 33.72% | 0% | 66.28% | 0.0042726 | 0 | 0 | 0.0042726 | 0 | 0.0040757 | 0.15873 | 0.025677 | 0.0040757 | 0.15873 | 0.025677 | 0.0042935 | 0.16721 | 0.025677 | 1.669% | 0.0005224 | 0.00049654 | 490.0579 | 1.5926 | 186.4105 | 302.0548 | 506.9745 | 0 | 0 | 506.9745 | 1.409e-07%
2026 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 6.0572 | 6 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 184.1331 | 6.2576 | 29.4253 | 184.1331 | 6.2576 | 29.4253 | 193.9716 | 6.592 | 29.4253 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2026 | 287 | 287-20 | Tier-1 | Non-HFTD---7 | 2--4 | 0.66515 | 101 | 100% | 45.5594 | 6.137% | 92.85% | 1.013% | 0.13841 | 0 | 0 | 0.13841 | 0 | 0.13204 | 0.68716 | 0.19215 | 0.13204 | 0.68716 | 0.19215 | 0.13909 | 0.72388 | 0.19215 | 0.3038% | 0.0081382 | 0.0077354 | 5598.2146 | 73.7618 | 4770.4937 | 753.9592 | 5871.8642 | 0 | 0 | 5871.8642 | 4.564e-06%
2026 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 1.3216 | 209 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 114.0597 | 1.3654 | 83.5379 | 114.0597 | 1.3654 | 83.5379 | 120.154 | 1.4383 | 83.5379 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2026 | 295 | 295-1201F | Tier-1 | Non-HFTD---19 | 1--2 | 0.16193 | 31 | 100% | 0.61619 | 77.51% | 0% | 22.49% | 0.023641 | 0 | 0 | 0.023641 | 0 | 0.022552 | 0.16729 | 0.13481 | 0.022552 | 0.16729 | 0.13481 | 0.023757 | 0.17623 | 0.13481 | 3.837% | 0.0006544 | 0.00062201 | 941.6139 | 118.3874 | 26.4172 | 796.8092 | 952.6431 | 0 | 0 | 952.6431 | 7.796e-07%
2026 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 3.6983 | 174 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 37.8909 | 3.8207 | 9.9173 | 37.8909 | 3.8207 | 9.9173 | 39.9154 | 4.0248 | 9.9173 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2026 | 122 | 122-196 | Tier-1 | Non-HFTD---17 | 1--3 | 0.094697 | 0 | 100% | 0.86843 | 83.21% | 0% | 16.79% | 0.035772 | 0 | 0 | 0.035772 | 0 | 0.034124 | 0.097831 | 0.3488 | 0.034124 | 0.097831 | 0.3488 | 0.035947 | 0.10306 | 0.3488 | 4.119% | 0.0004458 | 0.00042373 | 1948.0311 | 75.668 | 1186.0682 | 686.2949 | 1965.0602 | 0 | 0 | 1965.0602 | 1.18e-06%
2026 | AD3 | CB AD3 | Tier-1 | Non-HFTD---6 | 3--3 | 5.5978 | 142 | 100% | 83.3741 | 10.35% | 84.58% | 5.071% | 0.4273 | 0 | 0 | 0.4273 | 0 | 0.40762 | 5.783 | 0.070485 | 0.40762 | 5.783 | 0.070485 | 0.4294 | 6.092 | 0.070485 | 0.5125% | 0.020729 | 0.019703 | 4022.177 | 22.235 | 3421.9761 | 577.9659 | 4209.9556 | 0 | 0 | 4209.9556 | 1.409e-05%
2026 | 580 | CB 580 | Tier-1 | Non-HFTD---10 | 3--2 | 6.6564 | 112 | 100% | 16.6854 | 65.67% | 0% | 34.33% | 0.54239 | 0 | 0 | 0.54239 | 0 | 0.5174 | 6.8767 | 0.075239 | 0.5174 | 6.8767 | 0.075239 | 0.54505 | 7.2442 | 0.075239 | 3.251% | 0.021036 | 0.019994 | 793.1967 | 20.8991 | 418.7736 | 353.524 | 807.3777 | 0 | 0 | 807.3777 | 1.789e-05%
2026 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 5.1553 | 296 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 83.482 | 5.3259 | 15.6746 | 83.482 | 5.3259 | 15.6746 | 87.9426 | 5.6105 | 15.6746 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2026 | 381 | CB 381 | Tier-1 | Non-HFTD---5 | 1--4 | 0.78239 | 13 | 100% | 47.7165 | 98.4% | 0% | 1.604% | 2.3241 | 0 | 0 | 2.3241 | 0 | 2.217 | 0.80828 | 2.7429 | 2.217 | 0.80828 | 2.7429 | 2.3355 | 0.85147 | 2.7429 | 4.871% | 0.0039148 | 0.003721 | 12188.7447 | 1325.9661 | 5588.321 | 5274.4577 | 12198.9235 | 0 | 0 | 12198.9235 | 7.664e-05%
2026 | 781 | 781-1359 | Tier-1 | Non-HFTD---6 | 3--3 | 1.9735 | 131 | 100% | 56.4656 | 0.6389% | 97.32% | 2.039% | 0.017858 | 0 | 0 | 0.017858 | 0 | 0.017036 | 2.0388 | 0.0083558 | 0.017036 | 2.0388 | 0.0083558 | 0.017946 | 2.1477 | 0.0083558 | 0.03163% | 0.015735 | 0.014956 | 3588.4458 | 5.6419 | 3219.1315 | 363.6723 | 3774.1303 | 0 | 0 | 3774.1303 | 5.889e-07%
2026 | 198 | CB 198 | Tier-1 | Non-HFTD---7 | 2--3 | 2.6296 | 53 | 100% | 42.3989 | 95.29% | 0% | 4.712% | 1.9999 | 0 | 0 | 1.9999 | 0 | 1.9077 | 2.7166 | 0.70225 | 1.9077 | 2.7166 | 0.70225 | 2.0097 | 2.8617 | 0.70225 | 4.717% | 0.0090942 | 0.008644 | 4662.1866 | 881.6219 | 964.9735 | 2815.5912 | 4673.6267 | 0 | 0 | 4673.6267 | 6.595e-05%
2026 | 486 | 486-91 | Tier-1 | Non-HFTD---11 | 2--3 | 1.6947 | 55 | 100% | 14.7921 | 90.67% | 0% | 9.328% | 0.66391 | 0 | 0 | 0.66391 | 0 | 0.63332 | 1.7508 | 0.36174 | 0.63332 | 1.7508 | 0.36174 | 0.66716 | 1.8443 | 0.36174 | 4.488% | 0.0056232 | 0.0053449 | 2630.5487 | 105.0428 | 1762.2852 | 763.2207 | 2643.3281 | 0 | 0 | 2643.3281 | 2.189e-05%
2026 | 159 | 159-31R | Tier-1 | Non-HFTD---10 | 4--1 | 15.0642 | 475 | 100% | 17.9248 | 42.9% | 0% | 57.1% | 0.38062 | 0 | 0 | 0.38062 | 0 | 0.36309 | 15.5627 | 0.023331 | 0.36309 | 15.5627 | 0.023331 | 0.38249 | 16.3943 | 0.023331 | 2.123% | 0.041101 | 0.039067 | 436.1117 | 0.91666 | 205.6006 | 229.5944 | 449.0806 | 0 | 0 | 449.0806 | 1.255e-05%
2026 | 403 | 403-11F | Tier-1 | Non-HFTD---19 | 1--1 | 0.092612 | 1 | 100% | 0.13674 | 49.73% | 0% | 50.27% | 0.003366 | 0 | 0 | 0.003366 | 0 | 0.003211 | 0.095677 | 0.033561 | 0.003211 | 0.095677 | 0.033561 | 0.0033825 | 0.10079 | 0.033561 | 2.462% | 0.0002772 | 0.00026348 | 493.2752 | 2.7743 | 252.0099 | 238.491 | 506.1886 | 0 | 0 | 506.1886 | 1.11e-07%
2026 | 142 | 142-33 | Tier-1 | Non-HFTD---3 | 4--3 | 9.6922 | 296 | 100% | 118.7124 | 20.51% | 73.88% | 5.606% | 1.2055 | 0 | 0 | 1.2055 | 0 | 1.1499 | 10.013 | 0.11484 | 1.1499 | 10.013 | 0.11484 | 1.2114 | 10.548 | 0.11484 | 1.015% | 0.037439 | 0.035585 | 3170.8556 | 82.1006 | 2482.6954 | 606.0595 | 3302.112 | 0 | 0 | 3302.112 | 3.975e-05%
2026 | 1049 | 1049-4F | Tier-1 | Non-HFTD---15 | 2--2 | 1.9534 | 56 | 100% | 3.7141 | 55.35% | 0% | 44.65% | 0.10175 | 0 | 0 | 0.10175 | 0 | 0.097064 | 2.018 | 0.048099 | 0.097064 | 2.018 | 0.048099 | 0.10225 | 2.1258 | 0.048099 | 2.74% | 0.0062142 | 0.0059066 | 597.6775 | 50.3489 | 47.6467 | 499.6819 | 611.5765 | 0 | 0 | 611.5765 | 3.355e-06%
2026 | 313 | 313-923F | Tier-1 | Non-HFTD---8 | 3--2 | 2.539 | 201 | 100% | 37.7797 | 19.84% | 75.48% | 4.681% | 0.37105 | 0 | 0 | 0.37105 | 0 | 0.35396 | 2.623 | 0.13494 | 0.35396 | 2.623 | 0.13494 | 0.37287 | 2.7632 | 0.13494 | 0.9821% | 0.024714 | 0.023491 | 1528.6511 | 49.341 | 1018.188 | 461.1221 | 1592.4645 | 0 | 0 | 1592.4645 | 1.224e-05%
2026 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 0.043939 | 2 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.35337 | 0.045393 | 7.7846 | 0.35337 | 0.045393 | 7.7846 | 0.37225 | 0.047819 | 7.7846 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2026 | 413 | CB 413 | Tier-1 | Non-HFTD---14 | 2--2 | 2.979 | 41 | 100% | 5.219 | 51.24% | 0% | 48.76% | 0.13238 | 0 | 0 | 0.13238 | 0 | 0.12628 | 3.0776 | 0.041032 | 0.12628 | 3.0776 | 0.041032 | 0.13303 | 3.242 | 0.041032 | 2.537% | 0.0095502 | 0.0090775 | 546.4762 | 31.366 | 184.439 | 330.6712 | 560.3522 | 0 | 0 | 560.3522 | 4.365e-06%
2026 | 731 | 731-1247F | Tier-1 | Non-HFTD---8 | 3--2 | 8.847 | 410 | 100% | 26.8816 | 80.57% | 0% | 19.43% | 1.0721 | 0 | 0 | 1.0721 | 0 | 1.0227 | 9.1398 | 0.11189 | 1.0227 | 9.1398 | 0.11189 | 1.0773 | 9.6281 | 0.11189 | 3.988% | 0.023379 | 0.022222 | 1149.7989 | 119.8828 | 215.3653 | 814.5508 | 1161.4348 | 0 | 0 | 1161.4348 | 3.535e-05%
2026 | 581 | CB 581 | Tier-1 | Non-HFTD---14 | 2--2 | 4.2623 | 254 | 100% | 6.6929 | 56.27% | 0% | 43.73% | 0.18643 | 0 | 0 | 0.18643 | 0 | 0.17784 | 4.4034 | 0.040388 | 0.17784 | 4.4034 | 0.040388 | 0.18735 | 4.6387 | 0.040388 | 2.786% | 0.012283 | 0.011675 | 544.875 | 36.9163 | 103.2062 | 404.7526 | 557.283 | 0 | 0 | 557.283 | 6.148e-06%
2026 | 560 | 560-46F | Tier-1 | Non-HFTD---9 | 1--4 | 0.47552 | 5 | 100% | 21.1791 | 98.55% | 0% | 1.446% | 1.0332 | 0 | 0 | 1.0332 | 0 | 0.98561 | 0.49126 | 2.0063 | 0.98561 | 0.49126 | 2.0063 | 1.0383 | 0.51751 | 2.0063 | 4.878% | 0.0016054 | 0.0015259 | 13192.414 | 3248.8863 | 1203.2389 | 8740.2887 | 13202.348 | 0 | 0 | 13202.348 | 3.407e-05%
2026 | 206 | 206-974 | Tier-1 | Non-HFTD---1 | 4--5 | 8.7475 | 717 | 100% | 1943.6719 | 99.69% | 0% | 0.3117% | 95.9119 | 0 | 0 | 95.9119 | 0 | 91.4934 | 9.037 | 10.1243 | 91.4934 | 9.037 | 10.1243 | 96.382 | 9.5199 | 10.1243 | 4.935% | 0.028958 | 0.027525 | 67119.4507 | 10907.8418 | 251.1395 | 55960.4695 | 67130.3452 | 0 | 0 | 67130.3452 | 0.003163%
2026 | 430 | 430-42F | Tier-1 | Non-HFTD---16 | 2--1 | 4.3551 | 171 | 100% | 4.6808 | 37.11% | 0% | 62.89% | 0.085984 | 0 | 0 | 0.085984 | 0 | 0.082023 | 4.4993 | 0.01823 | 0.082023 | 4.4993 | 0.01823 | 0.086406 | 4.7397 | 0.01823 | 1.837% | 0.013 | 0.012357 | 360.0482 | 4.7005 | 126.5075 | 228.8402 | 371.8404 | 0 | 0 | 371.8404 | 2.835e-06%
2026 | CG2 | CB CG2 | Tier-1 | Non-HFTD---2 | 4--4 | 8.5261 | 945 | 100% | 237.5736 | 92.58% | 4.849% | 2.57% | 10.8874 | 0 | 0 | 10.8874 | 0 | 10.3858 | 8.8083 | 1.1791 | 10.3858 | 8.8083 | 1.1791 | 10.9408 | 9.2789 | 1.1791 | 4.583% | 0.033669 | 0.032002 | 7056.2378 | 1251.7365 | 402.879 | 5401.6224 | 7083.5019 | 0 | 0 | 7083.5019 | 0.000359%
2026 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 5.0727 | 240 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 30.0665 | 5.2406 | 5.7373 | 30.0665 | 5.2406 | 5.7373 | 31.673 | 5.5206 | 5.7373 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2026 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.043939 | 0 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.50996 | 0.045393 | 11.2341 | 0.50996 | 0.045393 | 11.2341 | 0.5372 | 0.047819 | 11.2341 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2026 | VS4 | CB VS4 | Tier-1 | Non-HFTD---12 | 3--1 | 6.475 | 300 | 100% | 8.974 | 52.07% | 0% | 47.93% | 0.23131 | 0 | 0 | 0.23131 | 0 | 0.22065 | 6.6893 | 0.032985 | 0.22065 | 6.6893 | 0.032985 | 0.23244 | 7.0467 | 0.032985 | 2.578% | 0.018085 | 0.017189 | 496.2256 | 31.5583 | 87.8288 | 376.8384 | 508.6116 | 0 | 0 | 508.6116 | 7.628e-06%
2026 | 403 | CB 403 | Tier-1 | Non-HFTD---11 | 1--3 | 1.3608 | 12 | 100% | 10.6218 | 92.93% | 0% | 7.069% | 0.48861 | 0 | 0 | 0.48861 | 0 | 0.4661 | 1.4058 | 0.33156 | 0.4661 | 1.4058 | 0.33156 | 0.49101 | 1.4809 | 0.33156 | 4.6% | 0.0034798 | 0.0033075 | 3052.4178 | 0.16237 | 2856.2333 | 196.0221 | 3063.6555 | 0 | 0 | 3063.6555 | 1.611e-05%
2026 | 168 | 168-702F | Tier-1 | Non-HFTD---5 | 3--3 | 4.9932 | 515 | 100% | 86.0496 | 96.13% | 0% | 3.875% | 4.0944 | 0 | 0 | 4.0944 | 0 | 3.9058 | 5.1584 | 0.75716 | 3.9058 | 5.1584 | 0.75716 | 4.1145 | 5.4341 | 0.75716 | 4.758% | 0.018904 | 0.017968 | 4551.8785 | 998.3577 | 182.1089 | 3371.4119 | 4561.0641 | 0 | 0 | 4561.0641 | 0.000135%
2026 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.1358 | 0 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 3.0016 | 0.14029 | 21.3955 | 3.0016 | 0.14029 | 21.3955 | 3.1619 | 0.14779 | 21.3955 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2026 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 4.5633 | 493 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 461.0302 | 4.7143 | 97.7945 | 461.0302 | 4.7143 | 97.7945 | 485.6637 | 4.9662 | 97.7945 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2026 | 58 | 58-753F | Tier-1 | Non-HFTD---9 | 2--2 | 0.24597 | 0 | 100% | 17.6789 | 0.1407% | 99.04% | 0.8181% | 0.001231 | 0 | 0 | 0.001231 | 0 | 0.0011743 | 0.25411 | 0.004621 | 0.0011743 | 0.25411 | 0.004621 | 0.001237 | 0.26769 | 0.004621 | 0.006963% | 0.011461 | 0.010893 | 1542.5838 | 1.9521 | 1400.9815 | 139.6502 | 1622.8053 | 0 | 0 | 1622.8053 | 4.059e-08%
2026 | 68 | 68-27 | Tier-1 | Non-HFTD---5 | 3--3 | 1.0051 | 139 | 100% | 64.4638 | 96.08% | 2.916% | 1.004% | 3.0659 | 0 | 0 | 3.0659 | 0 | 2.9246 | 1.0384 | 2.8165 | 2.9246 | 1.0384 | 2.8165 | 3.0809 | 1.0939 | 2.8165 | 4.756% | 0.014207 | 0.013503 | 4537.5974 | 1115.6501 | 119.135 | 3302.8124 | 4546.8608 | 0 | 0 | 4546.8608 | 0.0001011%
2026 | 64 | 64-13F | Tier-1 | Non-HFTD---13 | 2--2 | 0.11307 | 9 | 100% | 5.341 | 32.14% | 65.84% | 2.014% | 0.084982 | 0 | 0 | 0.084982 | 0 | 0.081067 | 0.11681 | 0.69401 | 0.081067 | 0.11681 | 0.69401 | 0.085399 | 0.12305 | 0.69401 | 1.591% | 0.0078982 | 0.0075072 | 676.2339 | 52.8868 | 355.4216 | 267.9254 | 700.1306 | 0 | 0 | 700.1306 | 2.802e-06%
2026 | 571 | 571-33 | Tier-1 | Non-HFTD---8 | 3--2 | 4.3138 | 257 | 100% | 41.773 | 16.82% | 74.21% | 8.975% | 0.34775 | 0 | 0 | 0.34775 | 0 | 0.33173 | 4.4566 | 0.074437 | 0.33173 | 4.4566 | 0.074437 | 0.34946 | 4.6947 | 0.074437 | 0.8325% | 0.024717 | 0.023494 | 1690.0234 | 1.9728 | 1442.354 | 245.6966 | 1763.2343 | 0 | 0 | 1763.2343 | 1.147e-05%
2026 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 8.7312 | 1277 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 136.9236 | 9.0202 | 15.1797 | 136.9236 | 9.0202 | 15.1797 | 144.2396 | 9.5021 | 15.1797 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2026 | 171 | 171-567 | Tier-1 | Non-HFTD---6 | 4--3 | 4.0096 | 49 | 100% | 70.6554 | 57.12% | 38.82% | 4.06% | 1.9978 | 0 | 0 | 1.9978 | 0 | 1.9057 | 4.1423 | 0.46006 | 1.9057 | 4.1423 | 0.46006 | 2.0075 | 4.3636 | 0.46006 | 2.827% | 0.041203 | 0.039164 | 1714.7945 | 149.6855 | 670.7195 | 894.3894 | 1753.0872 | 0 | 0 | 1753.0872 | 6.588e-05%
2026 | 712 | CB 712 | Tier-1 | Non-HFTD---17 | 1--2 | 0.30758 | 18 | 100% | 1.8273 | 79.32% | 0% | 20.68% | 0.071744 | 0 | 0 | 0.071744 | 0 | 0.068439 | 0.31775 | 0.21538 | 0.068439 | 0.31775 | 0.21538 | 0.072096 | 0.33473 | 0.21538 | 3.926% | 0.0012852 | 0.0012216 | 1421.816 | 151.1232 | 223.9631 | 1046.7297 | 1437.1307 | 0 | 0 | 1437.1307 | 2.366e-06%
2026 | 154 | CB 154 | Tier-1 | Non-HFTD---8 | 3--2 | 8.8996 | 202 | 100% | 34.1288 | 84.46% | 0% | 15.54% | 1.4268 | 0 | 0 | 1.4268 | 0 | 1.3611 | 9.1942 | 0.14804 | 1.3611 | 9.1942 | 0.14804 | 1.4338 | 9.6854 | 0.14804 | 4.181% | 0.024087 | 0.022895 | 1416.8753 | 0.16572 | 1216.6491 | 200.0605 | 1428.3445 | 0 | 0 | 1428.3445 | 4.705e-05%
2026 | 100 | CB 100 | Tier-1 | Non-HFTD---14 | 2--1 | 3.145 | 12 | 100% | 5.5173 | 52.94% | 0% | 47.06% | 0.14457 | 0 | 0 | 0.14457 | 0 | 0.13791 | 3.2491 | 0.042445 | 0.13791 | 3.2491 | 0.042445 | 0.14528 | 3.4227 | 0.042445 | 2.62% | 0.011123 | 0.010572 | 496.0224 | 30.1785 | 97.473 | 368.3709 | 508.18 | 0 | 0 | 508.18 | 4.767e-06%
2026 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 6.2526 | 373 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 193.8402 | 6.4596 | 30.0083 | 193.8402 | 6.4596 | 30.0083 | 204.1973 | 6.8047 | 30.0083 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2026 | 902 | CB 902 | Tier-1 | Non-HFTD---6 | 3--3 | 7.7576 | 271 | 100% | 88.9578 | 94.13% | 0% | 5.869% | 4.145 | 0 | 0 | 4.145 | 0 | 3.954 | 8.0143 | 0.49337 | 3.954 | 8.0143 | 0.49337 | 4.1653 | 8.4425 | 0.49337 | 4.659% | 0.02472 | 0.023497 | 3598.5877 | 613.2964 | 680.9324 | 2304.3589 | 3609.5869 | 0 | 0 | 3609.5869 | 0.0001367%
2026 | 57 | 57-736 | Tier-1 | Non-HFTD---4 | 3--4 | 1.4816 | 0 | 100% | 116.8924 | 0.4896% | 98.37% | 1.142% | 0.028331 | 0 | 0 | 0.028331 | 0 | 0.027026 | 1.5307 | 0.017656 | 0.027026 | 1.5307 | 0.017656 | 0.02847 | 1.6124 | 0.017656 | 0.02424% | 0.015165 | 0.014415 | 7707.8351 | 8.3652 | 6936.4124 | 763.0575 | 8107.2772 | 0 | 0 | 8107.2772 | 9.342e-07%
2026 | 1081 | 1081-668F | Tier-1 | Non-HFTD---7 | 2--3 | 0.89998 | 110 | 100% | 32.9591 | 15.19% | 83.12% | 1.695% | 0.24782 | 0 | 0 | 0.24782 | 0 | 0.2364 | 0.92977 | 0.25426 | 0.2364 | 0.92977 | 0.25426 | 0.24904 | 0.97945 | 0.25426 | 0.7519% | 0.013304 | 0.012645 | 2477.4214 | 66.1914 | 1948.4509 | 462.7791 | 2586.8423 | 0 | 0 | 2586.8423 | 8.172e-06%
2026 | 553 | 553-27R | Tier-1 | Non-HFTD---1 | 4--4 | 16.2339 | 1091 | 100% | 504.2652 | 97.83% | 0% | 2.166% | 24.4204 | 0 | 0 | 24.4204 | 0 | 23.2954 | 16.7711 | 1.389 | 23.2954 | 16.7711 | 1.389 | 24.5401 | 17.6672 | 1.389 | 4.843% | 0.054721 | 0.052013 | 9215.1363 | 1913.347 | 158.4888 | 7143.3005 | 9225.5318 | 0 | 0 | 9225.5318 | 0.0008053%
2026 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 2.0208 | 0 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 33.9169 | 2.0877 | 16.246 | 33.9169 | 2.0877 | 16.246 | 35.7291 | 2.1993 | 16.246 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2026 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.052273 | 0 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.11451 | 0.054003 | 2.1204 | 0.11451 | 0.054003 | 2.1204 | 0.12063 | 0.056888 | 2.1204 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2026 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.125 | 29 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 4.1171 | 0.12914 | 31.8818 | 4.1171 | 0.12914 | 31.8818 | 4.3371 | 0.13604 | 31.8818 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2026 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 4.8606 | 118 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 17.3347 | 5.0215 | 3.4521 | 17.3347 | 5.0215 | 3.4521 | 18.261 | 5.2898 | 3.4521 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2026 | 771 | CB 771 | Tier-1 | Non-HFTD---9 | 2--3 | 3.289 | 51 | 100% | 24.0595 | 89.94% | 0% | 10.06% | 1.0712 | 0 | 0 | 1.0712 | 0 | 1.0218 | 3.3978 | 0.30073 | 1.0218 | 3.3978 | 0.30073 | 1.0764 | 3.5794 | 0.30073 | 4.452% | 0.012612 | 0.011987 | 1907.7243 | 292.4297 | 438.977 | 1176.3177 | 1917.7151 | 0 | 0 | 1917.7151 | 3.532e-05%
2026 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.13314 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 6.3024 | 0.13755 | 45.8187 | 6.3024 | 0.13755 | 45.8187 | 6.6391 | 0.1449 | 45.8187 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2026 | GA3 | CB GA3 | Tier-1 | Non-HFTD---12 | 3--2 | 8.5176 | 228 | 100% | 14.7076 | 61.7% | 0% | 38.3% | 0.44919 | 0 | 0 | 0.44919 | 0 | 0.4285 | 8.7995 | 0.048696 | 0.4285 | 8.7995 | 0.048696 | 0.45139 | 9.2697 | 0.048696 | 3.054% | 0.024925 | 0.023691 | 590.0826 | 58.8012 | 95.7567 | 435.5246 | 601.8522 | 0 | 0 | 601.8522 | 1.481e-05%
2026 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 10.6068 | 603 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 537.4279 | 10.9578 | 49.0451 | 537.4279 | 10.9578 | 49.0451 | 566.1434 | 11.5433 | 49.0451 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2026 | 532 | 532-762 | Tier-1 | Non-HFTD---17 | 1--3 | 0.099583 | 5 | 100% | 0.90806 | 87.96% | 0% | 12.04% | 0.039537 | 0 | 0 | 0.039537 | 0 | 0.037716 | 0.10288 | 0.3666 | 0.037716 | 0.10288 | 0.3666 | 0.039731 | 0.10838 | 0.3666 | 4.354% | 0.0003776 | 0.00035891 | 2404.8082 | 35.439 | 1925.6662 | 443.703 | 2419.8862 | 0 | 0 | 2419.8862 | 1.304e-06%
2026 | 375 | CB 375 | Tier-1 | Non-HFTD---20 | 1--1 | 0.5411 | 62 | 100% | 0.68134 | 5.392% | 0% | 94.61% | 0.0018184 | 0 | 0 | 0.0018184 | 0 | 0.0017346 | 0.55901 | 0.003103 | 0.0017346 | 0.55901 | 0.003103 | 0.0018273 | 0.58888 | 0.003103 | 0.2669% | 0.0021338 | 0.0020282 | 319.3093 | 0.25077 | 44.5114 | 274.5471 | 335.0417 | 0 | 0 | 335.0417 | 5.996e-08%
2026 | 404 | 404-6AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.6847 | 111 | 100% | 2.5254 | 19.87% | 0% | 80.13% | 0.024835 | 0 | 0 | 0.024835 | 0 | 0.023691 | 2.7736 | 0.0085416 | 0.023691 | 2.7736 | 0.0085416 | 0.024956 | 2.9217 | 0.0085416 | 0.9834% | 0.0075878 | 0.0072122 | 332.8242 | 1.9467 | 79.6777 | 251.1998 | 346.7135 | 0 | 0 | 346.7135 | 8.19e-07%
2026 | 180 | 180-13 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1185 | 117 | 100% | 4.6843 | 83.08% | 0% | 16.92% | 0.19265 | 0 | 0 | 0.19265 | 0 | 0.18377 | 1.1555 | 0.15904 | 0.18377 | 1.1555 | 0.15904 | 0.19359 | 1.2173 | 0.15904 | 4.113% | 0.0036268 | 0.0034473 | 1291.5815 | 151.5131 | 169.6594 | 970.409 | 1302.96 | 0 | 0 | 1302.96 | 6.353e-06%
2026 | TM1 | CB TM1 | Tier-1 | Non-HFTD---7 | 1--5 | 0.014962 | 3 | 100% | 38.7396 | 99.8% | 0% | 0.1958% | 1.9139 | 0 | 0 | 1.9139 | 0 | 1.8257 | 0.015457 | 118.112 | 1.8257 | 0.015457 | 118.112 | 1.9232 | 0.016283 | 118.112 | 4.94% | 0.0001408 | 0.00013383 | 275139.3146 | 43811.8165 | 68.1712 | 231259.327 | 275167.3683 | 0 | 0 | 275167.3683 | 6.311e-05%
2026 | 279 | CB 279 | Tier-1 | Non-HFTD---6 | 3--3 | 4.4104 | 176 | 100% | 90.028 | 19.61% | 77.19% | 3.194% | 0.87403 | 0 | 0 | 0.87403 | 0 | 0.83377 | 4.5564 | 0.18299 | 0.83377 | 4.5564 | 0.18299 | 0.87832 | 4.7998 | 0.18299 | 0.9708% | 0.028282 | 0.026882 | 3183.1813 | 17.4479 | 2800.4627 | 365.2707 | 3316.4414 | 0 | 0 | 3316.4414 | 2.882e-05%
2026 | 450 | CB 450 | Tier-1 | Non-HFTD---13 | 1--3 | 0.74978 | 8 | 100% | 5.2749 | 90.32% | 0% | 9.679% | 0.23583 | 0 | 0 | 0.23583 | 0 | 0.22497 | 0.77459 | 0.29044 | 0.22497 | 0.77459 | 0.29044 | 0.23699 | 0.81598 | 0.29044 | 4.471% | 0.0022246 | 0.0021145 | 2371.1556 | 0.17269 | 2162.5037 | 208.4792 | 2383.1075 | 0 | 0 | 2383.1075 | 7.777e-06%
2026 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 9.2899 | 568 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 53.817 | 9.5974 | 5.6075 | 53.817 | 9.5974 | 5.6075 | 56.6925 | 10.1102 | 5.6075 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2026 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.38903 | 18 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 32.5478 | 0.40191 | 80.9832 | 32.5478 | 0.40191 | 80.9832 | 34.2868 | 0.42338 | 80.9832 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2026 | 450 | 450-113F | Tier-1 | Non-HFTD---17 | 1--4 | 0.057576 | 2 | 100% | 1.4984 | 95.09% | 0% | 4.911% | 0.070528 | 0 | 0 | 0.070528 | 0 | 0.067279 | 0.059481 | 1.1311 | 0.067279 | 0.059481 | 1.1311 | 0.070874 | 0.062659 | 1.1311 | 4.707% | 0.0002576 | 0.00024485 | 5816.7432 | 904.3973 | 28.2827 | 4884.0631 | 5831.6186 | 0 | 0 | 5831.6186 | 2.326e-06%
2026 | 95 | CB 95 | Tier-1 | Non-HFTD---9 | 2--3 | 1.4153 | 129 | 100% | 22.4303 | 86.17% | 9.176% | 4.655% | 0.95673 | 0 | 0 | 0.95673 | 0 | 0.91266 | 1.4622 | 0.62418 | 0.91266 | 1.4622 | 0.62418 | 0.96142 | 1.5403 | 0.62418 | 4.265% | 0.0095064 | 0.0090358 | 2359.4915 | 219.0536 | 893.0827 | 1247.3552 | 2376.4865 | 0 | 0 | 2376.4865 | 3.155e-05%
2026 | 361 | 361-686F | Tier-1 | Non-HFTD---5 | 3--4 | 4.0396 | 99 | 100% | 90.6744 | 3.585% | 93.42% | 2.993% | 0.16092 | 0 | 0 | 0.16092 | 0 | 0.15351 | 4.1733 | 0.036784 | 0.15351 | 4.1733 | 0.036784 | 0.16171 | 4.3962 | 0.036784 | 0.1775% | 0.016667 | 0.015842 | 5440.2244 | 15.7061 | 4798.4721 | 626.0462 | 5713.382 | 0 | 0 | 5713.382 | 5.307e-06%
2026 | 250 | 250-288F | Tier-1 | Non-HFTD---19 | 1--2 | 0.046023 | 0 | 100% | 0.22194 | 49.89% | 0% | 50.11% | 0.0054814 | 0 | 0 | 0.0054814 | 0 | 0.0052289 | 0.047546 | 0.10998 | 0.0052289 | 0.047546 | 0.10998 | 0.0055083 | 0.050086 | 0.10998 | 2.47% | 0.0002572 | 0.00024447 | 862.9068 | 69.1562 | 40.6738 | 753.0767 | 885.4234 | 0 | 0 | 885.4234 | 1.808e-07%
2026 | 275 | 275-45 | Tier-1 | Non-HFTD---4 | 3--4 | 1.1627 | 21 | 100% | 157.581 | 0.4262% | 99.03% | 0.5451% | 0.033242 | 0 | 0 | 0.033242 | 0 | 0.031711 | 1.2012 | 0.026401 | 0.031711 | 1.2012 | 0.026401 | 0.033405 | 1.2653 | 0.026401 | 0.0211% | 0.018421 | 0.017509 | 8554.512 | 15.6556 | 7786.8024 | 752.0539 | 8998.114 | 0 | 0 | 8998.114 | 1.096e-06%
2026 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 29.745 | 3637 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 239.6048 | 30.7294 | 7.7973 | 239.6048 | 30.7294 | 7.7973 | 252.4072 | 32.3713 | 7.7973 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2026 | 72 | CB 72 | Tier-1 | Non-HFTD---11 | 2--2 | 3.7652 | 140 | 100% | 12.136 | 75.45% | 0% | 24.55% | 0.45323 | 0 | 0 | 0.45323 | 0 | 0.43235 | 3.8898 | 0.11115 | 0.43235 | 3.8898 | 0.11115 | 0.45545 | 4.0976 | 0.11115 | 3.735% | 0.012052 | 0.011455 | 1006.99 | 15.7502 | 686.9496 | 304.2902 | 1019.8666 | 0 | 0 | 1019.8666 | 1.495e-05%
2026 | 41 | CB 41 | Tier-1 | Non-HFTD---9 | 3--2 | 4.8292 | 112 | 100% | 23.8741 | 85.94% | 0% | 14.06% | 1.0156 | 0 | 0 | 1.0156 | 0 | 0.9688 | 4.989 | 0.19419 | 0.9688 | 4.989 | 0.19419 | 1.0206 | 5.2555 | 0.19419 | 4.254% | 0.013957 | 0.013266 | 1710.5248 | 0.97502 | 1486.9644 | 222.5854 | 1723.0513 | 0 | 0 | 1723.0513 | 3.349e-05%
2026 | 407 | CB 407 | Tier-1 | Non-HFTD---14 | 3--1 | 5.0112 | 98 | 100% | 5.6418 | 32.16% | 0% | 67.84% | 0.089806 | 0 | 0 | 0.089806 | 0 | 0.085669 | 5.177 | 0.016548 | 0.085669 | 5.177 | 0.016548 | 0.090246 | 5.4537 | 0.016548 | 1.592% | 0.014713 | 0.013984 | 383.4683 | 0.85569 | 142.8953 | 239.7173 | 397.0166 | 0 | 0 | 397.0166 | 2.961e-06%
2026 | 373 | CB 373 | Tier-1 | Non-HFTD---19 | 1--1 | 0.33921 | 6 | 100% | 0.39748 | 23.53% | 0% | 76.47% | 0.0046292 | 0 | 0 | 0.0046292 | 0 | 0.0044159 | 0.35043 | 0.012601 | 0.0044159 | 0.35043 | 0.012601 | 0.0046519 | 0.36916 | 0.012601 | 1.165% | 0.0010574 | 0.0010051 | 375.899 | 0.2163 | 114.5547 | 261.128 | 390.8691 | 0 | 0 | 390.8691 | 1.527e-07%
2026 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 3.4226 | 354 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 198.1694 | 3.5358 | 56.0461 | 198.1694 | 3.5358 | 56.0461 | 208.7579 | 3.7248 | 56.0461 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2026 | 158 | CB 158 | Tier-1 | Non-HFTD---16 | 2--1 | 4.6192 | 158 | 100% | 4.5058 | 34.28% | 0% | 65.72% | 0.076457 | 0 | 0 | 0.076457 | 0 | 0.072935 | 4.772 | 0.015284 | 0.072935 | 4.772 | 0.015284 | 0.076832 | 5.027 | 0.015284 | 1.697% | 0.012279 | 0.011672 | 366.9398 | 1.1795 | 141.5538 | 224.2064 | 379.4985 | 0 | 0 | 379.4985 | 2.521e-06%
2026 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.016856 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.31849 | 0.017414 | 18.2896 | 0.31849 | 0.017414 | 18.2896 | 0.33551 | 0.018344 | 18.2896 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2026 | 326 | CB 326 | Tier-1 | Non-HFTD---8 | 3--3 | 5.6661 | 124 | 100% | 30.5714 | 87.97% | 0% | 12.03% | 1.3312 | 0 | 0 | 1.3312 | 0 | 1.2699 | 5.8536 | 0.21694 | 1.2699 | 5.8536 | 0.21694 | 1.3377 | 6.1664 | 0.21694 | 4.354% | 0.015429 | 0.014666 | 1981.3749 | 14.2383 | 1678.7619 | 288.3747 | 1993.7895 | 0 | 0 | 1993.7895 | 4.39e-05%
2026 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 3.0297 | 15 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 55.7189 | 3.13 | 17.8017 | 55.7189 | 3.13 | 17.8017 | 58.6961 | 3.2972 | 17.8017 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2026 | 86 | 86-553F | Tier-1 | Not Applicable | Not Applicable | 0.0223 | 0 | 100% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.023038 | 0 | 0 | 0.023038 | 0 | 0 | 0.024269 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2026 | 221 | 221-1235F | Tier-3 | Tier-3---18 | 5--2 | 0.0489 | 0 | 100% | 236.1769 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.050518 | 0 | 0 | 0.050518 | 0 | 0 | 0.053218 | 0 | 0% | 0.16409 | 0.15597 | 1439.2989 | 2.105 | 1306.2711 | 130.9227 | 1514.2545 | 0 | 0 | 1514.2545 | 0%
2026 | 1234 | 1234-732R | Tier-2 | Not Applicable | Not Applicable | 0.5958 | 0 | 100% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.61552 | 0 | 0 | 0.61552 | 0 | 0 | 0.6484 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2027 | 1153 | CB 1153 | Tier-1 | Non-HFTD---19 | 1--2 | 0.09697 | 1 | 100% | 0.54442 | 68.22% | 0% | 31.78% | 0.018384 | 0 | 0 | 0.018384 | 0 | 0.016729 | 0.095564 | 0.17506 | 0.016729 | 0.095564 | 0.17506 | 0.018565 | 0.10605 | 0.17506 | 3.377% | 0.0005088 | 0.00048361 | 1070.015 | 113.1086 | 30.893 | 926.0134 | 1087.7256 | 0 | 0 | 1087.7256 | 6.062e-07%
2027 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 6.8811 | 261 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 451.3803 | 6.7813 | 66.5626 | 451.3803 | 6.7813 | 66.5626 | 500.9047 | 7.5253 | 66.5626 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2027 | 509 | 509-1227R | Tier-1 | Non-HFTD---13 | 2--2 | 2.0561 | 86 | 100% | 6.8178 | 77.37% | 0% | 22.63% | 0.26111 | 0 | 0 | 0.26111 | 0 | 0.23761 | 2.0262 | 0.11726 | 0.23761 | 2.0262 | 0.11726 | 0.26368 | 2.2486 | 0.11726 | 3.83% | 0.0063694 | 0.0060541 | 1070.3915 | 53.8343 | 522.4019 | 494.1553 | 1083.0058 | 0 | 0 | 1083.0058 | 8.61e-06%
2027 | 142 | 142-8R | Tier-1 | Non-HFTD---8 | 3--2 | 6.7481 | 216 | 100% | 40.8893 | 6.402% | 80.66% | 12.94% | 0.12957 | 0 | 0 | 0.12957 | 0 | 0.1179 | 6.6503 | 0.017729 | 0.1179 | 6.6503 | 0.017729 | 0.13084 | 7.3799 | 0.017729 | 0.3169% | 0.027724 | 0.026352 | 1474.8579 | 5.0539 | 1173.9231 | 295.8809 | 1546.7485 | 0 | 0 | 1546.7485 | 4.273e-06%
2027 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 0 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.69648 | 0.033783 | 20.6162 | 0.69648 | 0.033783 | 20.6162 | 0.7729 | 0.03749 | 20.6162 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2027 | 391 | CB 391 | Tier-1 | Non-HFTD---2 | 4--4 | 0.66137 | 36 | 100% | 550.2041 | 0.5245% | 99.39% | 0.08518% | 0.14286 | 0 | 0 | 0.14286 | 0 | 0.13 | 0.65178 | 0.19945 | 0.13 | 0.65178 | 0.19945 | 0.14427 | 0.7233 | 0.19945 | 0.02597% | 0.089115 | 0.084704 | 6174.0912 | 11.3908 | 5617.0317 | 545.6688 | 6493.938 | 0 | 0 | 6493.938 | 4.711e-06%
2027 | 84 | CB 84 | Tier-1 | Non-HFTD---12 | 3--2 | 6.597 | 272 | 100% | 11.1569 | 60.04% | 0% | 39.96% | 0.33156 | 0 | 0 | 0.33156 | 0 | 0.30171 | 6.5013 | 0.046408 | 0.30171 | 6.5013 | 0.046408 | 0.33482 | 7.2146 | 0.046408 | 2.972% | 0.018717 | 0.01779 | 596.0964 | 9.118 | 324.3476 | 262.6307 | 608.5026 | 0 | 0 | 608.5026 | 1.093e-05%
2027 | 325 | 325-25 | Tier-1 | Non-HFTD---13 | 1--3 | 1.2847 | 29 | 100% | 8.3612 | 88.04% | 0% | 11.96% | 0.36437 | 0 | 0 | 0.36437 | 0 | 0.33157 | 1.266 | 0.2619 | 0.33157 | 1.266 | 0.2619 | 0.36795 | 1.4049 | 0.2619 | 4.358% | 0.0037654 | 0.003579 | 2220.5219 | 1.0278 | 1973.9755 | 245.5186 | 2234.3551 | 0 | 0 | 2234.3551 | 1.202e-05%
2027 | 221 | 221-1466 | Tier-3 | Not Applicable | Not Applicable | 0.6294 | 0 | 100% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.62027 | 0 | 0 | 0.62027 | 0 | 0 | 0.68833 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2027 | 390 | CB 390 | Tier-1 | Non-HFTD---2 | 5--4 | 1.4761 | 48 | 100% | 555.1958 | 4.119% | 95.66% | 0.2245% | 1.1319 | 0 | 0 | 1.1319 | 0 | 1.03 | 1.4547 | 0.70805 | 1.03 | 1.4547 | 0.70805 | 1.143 | 1.6143 | 0.70805 | 0.2039% | 0.093583 | 0.088951 | 5932.6308 | 27.2019 | 5249.9711 | 655.4577 | 6228.8647 | 0 | 0 | 6228.8647 | 3.733e-05%
2027 | 445 | 445-1315 | Tier-2 | Tier-2---19 | 1--5 | 0.080871 | 0 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 1.294 | 0 | 0 | 1.294 | 0 | 1.1776 | 0.079699 | 14.7752 | 1.1776 | 0.079699 | 14.7752 | 1.3068 | 0.088443 | 14.7752 | 4.93% | 0.000636 | 0.00060452 | 41272.5846 | 5558.0973 | 1215.1763 | 34499.311 | 41281.3528 | 0 | 0 | 41281.3528 | 4.267e-05%
2027 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 10.7038 | 1013 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 294.6356 | 10.5486 | 27.9313 | 294.6356 | 10.5486 | 27.9313 | 326.9624 | 11.706 | 27.9313 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2027 | 93 | CB 93 | Tier-1 | Non-HFTD---3 | 3--4 | 6.2065 | 398 | 100% | 117.8522 | 49.76% | 46.78% | 3.462% | 2.9028 | 0 | 0 | 2.9028 | 0 | 2.6415 | 6.1165 | 0.43186 | 2.6415 | 6.1165 | 0.43186 | 2.9313 | 6.7876 | 0.43186 | 2.463% | 0.023557 | 0.022391 | 5002.7692 | 337.5468 | 2573.6674 | 2091.555 | 5133.6638 | 0 | 0 | 5133.6638 | 9.572e-05%
2027 | 733 | 733-20AE | Tier-1 | Non-HFTD---8 | 3--2 | 9.4582 | 571 | 100% | 39.7294 | 85.07% | 0% | 14.93% | 1.6731 | 0 | 0 | 1.6731 | 0 | 1.5225 | 9.321 | 0.16334 | 1.5225 | 9.321 | 0.16334 | 1.6895 | 10.3437 | 0.16334 | 4.211% | 0.026087 | 0.024795 | 1522.9809 | 217.8105 | 467.7091 | 837.4613 | 1534.8195 | 0 | 0 | 1534.8195 | 5.517e-05%
2027 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 15.066 | 1487 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 135.1583 | 14.8475 | 9.1031 | 135.1583 | 14.8475 | 9.1031 | 149.9876 | 16.4765 | 9.1031 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2027 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 2.2173 | 257 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 98.75 | 2.1851 | 45.1917 | 98.75 | 2.1851 | 45.1917 | 109.5846 | 2.4249 | 45.1917 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2027 | 1085 | CB 1085 | Tier-1 | Non-HFTD---4 | 2--4 | 0.4608 | 15 | 100% | 121.8151 | 29.33% | 70.28% | 0.3892% | 1.7686 | 0 | 0 | 1.7686 | 0 | 1.6094 | 0.45411 | 3.5439 | 1.6094 | 0.45411 | 3.5439 | 1.7859 | 0.50394 | 3.5439 | 1.452% | 0.009242 | 0.0087845 | 13180.5987 | 392.6277 | 10019.0268 | 2768.9443 | 13665.6902 | 0 | 0 | 13665.6902 | 5.832e-05%
2027 | 299 | CB 299 | Tier-1 | Non-HFTD---11 | 1--3 | 0.95907 | 13 | 100% | 9.1156 | 92.89% | 0% | 7.105% | 0.41916 | 0 | 0 | 0.41916 | 0 | 0.38143 | 0.94517 | 0.40356 | 0.38143 | 0.94517 | 0.40356 | 0.42328 | 1.0489 | 0.40356 | 4.598% | 0.0028978 | 0.0027544 | 3145.7096 | 173.9595 | 1876.4075 | 1095.3426 | 3157.3492 | 0 | 0 | 3157.3492 | 1.382e-05%
2027 | 732 | 732-15R | Tier-1 | Non-HFTD---1 | 3--5 | 5.2317 | 420 | 100% | 342.6373 | 98.93% | 0% | 1.067% | 16.7796 | 0 | 0 | 16.7796 | 0 | 15.2692 | 5.1558 | 2.9615 | 15.2692 | 5.1558 | 2.9615 | 16.9445 | 5.7215 | 2.9615 | 4.897% | 0.02096 | 0.019923 | 16347.0441 | 3636.1945 | 124.2963 | 12586.5533 | 16356.1285 | 0 | 0 | 16356.1285 | 0.0005533%
2027 | 1119 | 1119-6F | Tier-1 | Non-HFTD---11 | 1--4 | 0.65508 | 30 | 100% | 14.1126 | 96.32% | 0% | 3.68% | 0.67286 | 0 | 0 | 0.67286 | 0 | 0.6123 | 0.64558 | 0.94845 | 0.6123 | 0.64558 | 0.94845 | 0.67948 | 0.71641 | 0.94845 | 4.768% | 0.002277 | 0.0021643 | 6197.8946 | 838.8203 | 861.0344 | 4498.0399 | 6209.7735 | 0 | 0 | 6209.7735 | 2.219e-05%
2027 | 256 | CB 256 | Tier-1 | Non-HFTD---11 | 2--2 | 3.543 | 127 | 100% | 11.4393 | 77.87% | 0% | 22.13% | 0.44094 | 0 | 0 | 0.44094 | 0 | 0.40125 | 3.4916 | 0.11492 | 0.40125 | 3.4916 | 0.11492 | 0.44528 | 3.8747 | 0.11492 | 3.855% | 0.011638 | 0.011062 | 982.9441 | 22.1853 | 662.0367 | 298.7221 | 994.2718 | 0 | 0 | 994.2718 | 1.454e-05%
2027 | 572 | CB 572 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1793 | 12 | 100% | 3.33 | 52.2% | 0% | 47.8% | 0.086046 | 0 | 0 | 0.086046 | 0 | 0.078301 | 1.1622 | 0.067373 | 0.078301 | 1.1622 | 0.067373 | 0.086892 | 1.2897 | 0.067373 | 2.584% | 0.0045428 | 0.0043179 | 733.0269 | 0.26885 | 414.4483 | 318.3098 | 751.2737 | 0 | 0 | 751.2737 | 2.837e-06%
2027 | 901 | 901-1124 | Tier-1 | Non-HFTD---1 | 2--5 | 2.1134 | 202 | 100% | 225.4814 | 99.29% | 0% | 0.709% | 11.0822 | 0 | 0 | 11.0822 | 0 | 10.0846 | 2.0828 | 4.842 | 10.0846 | 2.0828 | 4.842 | 11.1911 | 2.3113 | 4.842 | 4.915% | 0.0087544 | 0.0083211 | 25756.3496 | 4178.6743 | 36.5656 | 21541.1098 | 25765.8596 | 0 | 0 | 25765.8596 | 0.0003654%
2027 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 3.165 | 217 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 15.7849 | 3.1191 | 5.0607 | 15.7849 | 3.1191 | 5.0607 | 17.5167 | 3.4613 | 5.0607 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2027 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 8.4832 | 262 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 226.9901 | 8.3602 | 27.1514 | 226.9901 | 8.3602 | 27.1514 | 251.895 | 9.2774 | 27.1514 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2027 | 546 | 546-14R | Tier-1 | Non-HFTD---1 | 3--4 | 3.7622 | 61 | 100% | 227.2127 | 1.45% | 97.43% | 1.118% | 0.16304 | 0 | 0 | 0.16304 | 0 | 0.14837 | 3.7076 | 0.040017 | 0.14837 | 3.7076 | 0.040017 | 0.16464 | 4.1144 | 0.040017 | 0.07176% | 0.020679 | 0.019656 | 10987.501 | 12.3302 | 9969.5471 | 1005.6237 | 11551.4115 | 0 | 0 | 11551.4115 | 5.377e-06%
2027 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 12.0339 | 277 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 271.7734 | 11.8594 | 22.9162 | 271.7734 | 11.8594 | 22.9162 | 301.5917 | 13.1606 | 22.9162 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2027 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 6.8671 | 1649 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 73.3558 | 6.7675 | 10.8394 | 73.3558 | 6.7675 | 10.8394 | 81.4042 | 7.51 | 10.8394 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2027 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 9.4852 | 776 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 525.3163 | 9.3477 | 56.1973 | 525.3163 | 9.3477 | 56.1973 | 582.9527 | 10.3733 | 56.1973 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2027 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 13.8235 | 537 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 18.0809 | 13.623 | 1.3272 | 18.0809 | 13.623 | 1.3272 | 20.0646 | 15.1177 | 1.3272 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2027 | 280 | CB 280 | Tier-2 | Tier-2---14 | 4--4 | 4.0675 | 139 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 2.4753 | 0 | 0 | 2.4753 | 0 | 2.2525 | 4.0085 | 0.56194 | 2.2525 | 4.0085 | 0.56194 | 2.4997 | 4.4483 | 0.56194 | 0.7965% | 0.042409 | 0.04031 | 7328.4886 | 170.2669 | 5820.5339 | 1337.6878 | 7648.7329 | 0 | 0 | 7648.7329 | 8.163e-05%
2027 | 322 | CB 322 | Tier-1 | Non-HFTD---8 | 3--3 | 6.9822 | 212 | 100% | 42.0776 | 89.49% | 0% | 10.51% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.6961 | 6.881 | 0.2465 | 1.6961 | 6.881 | 0.2465 | 1.8822 | 7.6359 | 0.2465 | 4.43% | 0.018945 | 0.018007 | 2221.0419 | 151.6209 | 1083.6314 | 985.7895 | 2233.1993 | 0 | 0 | 2233.1993 | 6.147e-05%
2027 | 56 | CB 56 | Tier-1 | Non-HFTD---3 | 3--4 | 3.7124 | 66 | 100% | 122.2122 | 9.667% | 86.95% | 3.388% | 0.58481 | 0 | 0 | 0.58481 | 0 | 0.53217 | 3.6585 | 0.14546 | 0.53217 | 3.6585 | 0.14546 | 0.59056 | 4.0599 | 0.14546 | 0.4785% | 0.023301 | 0.022147 | 5245.0232 | 5.0181 | 4537.7925 | 702.2126 | 5491.767 | 0 | 0 | 5491.767 | 1.929e-05%
2027 | 80 | 80-564 | Tier-1 | Non-HFTD---8 | 3--2 | 9.7153 | 219 | 100% | 31.4137 | 77.77% | 0% | 22.23% | 1.2093 | 0 | 0 | 1.2093 | 0 | 1.1005 | 9.5745 | 0.11494 | 1.1005 | 9.5745 | 0.11494 | 1.2212 | 10.6249 | 0.11494 | 3.85% | 0.028026 | 0.026639 | 1120.8843 | 9.0416 | 839.8211 | 272.0216 | 1133.8606 | 0 | 0 | 1133.8606 | 3.988e-05%
2027 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 0.074242 | 8 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.29953 | 0.073166 | 4.0938 | 0.29953 | 0.073166 | 4.0938 | 0.33239 | 0.081194 | 4.0938 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2027 | 480 | 480-32 | Tier-1 | Non-HFTD---10 | 3--2 | 7.1091 | 262 | 100% | 17.2812 | 70.33% | 0% | 29.67% | 0.60164 | 0 | 0 | 0.60164 | 0 | 0.54748 | 7.006 | 0.078145 | 0.54748 | 7.006 | 0.078145 | 0.60755 | 7.7747 | 0.078145 | 3.481% | 0.019568 | 0.018599 | 883.1465 | 0.19748 | 644.9364 | 238.0126 | 896.7913 | 0 | 0 | 896.7913 | 1.984e-05%
2027 | 461 | 461-644R | Tier-1 | Non-HFTD---17 | 1--3 | 0.27861 | 0 | 100% | 1.9699 | 87.49% | 0% | 12.51% | 0.085309 | 0 | 0 | 0.085309 | 0 | 0.07763 | 0.27457 | 0.28273 | 0.07763 | 0.27457 | 0.28273 | 0.086148 | 0.30469 | 0.28273 | 4.331% | 0.0008654 | 0.00082256 | 2276.3126 | 196.7287 | 798.4144 | 1281.1695 | 2291.1467 | 0 | 0 | 2291.1467 | 2.813e-06%
2027 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 4.5645 | 666 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.7342 | 4.4984 | 3.0532 | 13.7342 | 4.4984 | 3.0532 | 15.2411 | 4.9919 | 3.0532 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2027 | 171 | 171-34 | Tier-1 | Non-HFTD---6 | 4--3 | 4.3813 | 60 | 100% | 81.2035 | 44.67% | 51.64% | 3.687% | 1.7955 | 0 | 0 | 1.7955 | 0 | 1.6339 | 4.3177 | 0.37842 | 1.6339 | 4.3177 | 0.37842 | 1.8132 | 4.7915 | 0.37842 | 2.211% | 0.043687 | 0.041525 | 1858.7395 | 129.5883 | 851.5868 | 877.5644 | 1912.2988 | 0 | 0 | 1912.2988 | 5.921e-05%
2027 | 70 | CB 70 | Tier-1 | Non-HFTD---12 | 3--2 | 6.5709 | 60 | 100% | 14.3505 | 72.4% | 0% | 27.6% | 0.51431 | 0 | 0 | 0.51431 | 0 | 0.46802 | 6.4756 | 0.072274 | 0.46802 | 6.4756 | 0.072274 | 0.51936 | 7.1861 | 0.072274 | 3.584% | 0.016758 | 0.015928 | 856.3389 | 1.8915 | 630.9279 | 223.5195 | 868.6465 | 0 | 0 | 868.6465 | 1.696e-05%
2027 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 5.0178 | 378 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 264.2682 | 4.945 | 53.4412 | 264.2682 | 4.945 | 53.4412 | 293.2631 | 5.4876 | 53.4412 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2027 | 1434 | 1434-10AE | Tier-1 | Non-HFTD---10 | 3--2 | 6.6536 | 200 | 100% | 17.6762 | 78.96% | 0% | 21.04% | 0.69087 | 0 | 0 | 0.69087 | 0 | 0.62868 | 6.5571 | 0.095878 | 0.62868 | 6.5571 | 0.095878 | 0.69766 | 7.2765 | 0.095878 | 3.908% | 0.017501 | 0.016634 | 1010.0366 | 133.2202 | 327.76 | 549.0563 | 1021.1043 | 0 | 0 | 1021.1043 | 2.278e-05%
2027 | 55 | 55-484F | Tier-1 | Non-HFTD---20 | 1--1 | 0.58822 | 21 | 100% | 0.44013 | 10.92% | 0% | 89.08% | 0.0023797 | 0 | 0 | 0.0023797 | 0 | 0.0021655 | 0.57969 | 0.0037356 | 0.0021655 | 0.57969 | 0.0037356 | 0.0024031 | 0.64329 | 0.0037356 | 0.5407% | 0.0015886 | 0.00151 | 277.0544 | 0.1857 | 52.6811 | 224.1876 | 289.9068 | 0 | 0 | 289.9068 | 7.847e-08%
2027 | 719 | CB 719 | Tier-1 | Non-HFTD---8 | 3--3 | 5.0596 | 131 | 100% | 28.3767 | 85.41% | 0% | 14.59% | 1.1998 | 0 | 0 | 1.1998 | 0 | 1.0918 | 4.9863 | 0.21896 | 1.0918 | 4.9863 | 0.21896 | 1.2116 | 5.5333 | 0.21896 | 4.228% | 0.015223 | 0.01447 | 1864.0191 | 0.59716 | 1614.3662 | 249.0557 | 1878.1781 | 0 | 0 | 1878.1781 | 3.956e-05%
2027 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 7.7339 | 601 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 56.0299 | 7.6218 | 7.3513 | 56.0299 | 7.6218 | 7.3513 | 62.1774 | 8.458 | 7.3513 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2027 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | 3--3 | 8.0419 | 234 | 100% | 117.3021 | 94.99% | 0% | 5.009% | 5.5156 | 0 | 0 | 5.5156 | 0 | 5.0191 | 7.9253 | 0.63331 | 5.0191 | 7.9253 | 0.63331 | 5.5698 | 8.7948 | 0.63331 | 4.702% | 0.027256 | 0.025907 | 4303.7498 | 1020.4795 | 248.6707 | 3034.5996 | 4314.9761 | 0 | 0 | 4314.9761 | 0.0001819%
2027 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 15.1559 | 814 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 107.9342 | 14.9361 | 7.2264 | 107.9342 | 14.9361 | 7.2264 | 119.7765 | 16.5749 | 7.2264 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2027 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 10.2425 | 356 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 68.0396 | 10.094 | 6.7406 | 68.0396 | 10.094 | 6.7406 | 75.5048 | 11.2014 | 6.7406 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2027 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 0.81042 | 169 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.8346 | 0.79867 | 3.5491 | 2.8346 | 0.79867 | 3.5491 | 3.1456 | 0.88629 | 3.5491 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2027 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 17.7839 | 395 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 237.5496 | 17.5261 | 13.5541 | 237.5496 | 17.5261 | 13.5541 | 263.613 | 19.449 | 13.5541 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2027 | 262 | CB 262 | Tier-1 | Non-HFTD---13 | 1--2 | 1.333 | 30 | 100% | 8.1125 | 88.1% | 0% | 11.9% | 0.35378 | 0 | 0 | 0.35378 | 0 | 0.32194 | 1.3136 | 0.24508 | 0.32194 | 1.3136 | 0.24508 | 0.35726 | 1.4578 | 0.24508 | 4.361% | 0.004918 | 0.0046746 | 1649.5582 | 174.8972 | 367.1245 | 1107.5365 | 1659.7811 | 0 | 0 | 1659.7811 | 1.167e-05%
2027 | 372 | CB 372 | Tier-1 | Non-HFTD---18 | 2--1 | 2.0544 | 108 | 100% | 2.0256 | 27.04% | 0% | 72.96% | 0.027112 | 0 | 0 | 0.027112 | 0 | 0.024672 | 2.0246 | 0.012186 | 0.024672 | 2.0246 | 0.012186 | 0.027379 | 2.2467 | 0.012186 | 1.339% | 0.0057966 | 0.0055097 | 349.4394 | 0.28023 | 117.0886 | 232.0705 | 362.7165 | 0 | 0 | 362.7165 | 8.941e-07%
2027 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.64962 | 16 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 31.8229 | 0.6402 | 49.7076 | 31.8229 | 0.6402 | 49.7076 | 35.3145 | 0.71044 | 49.7076 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2027 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 7.3926 | 440 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 159.4396 | 7.2854 | 21.8848 | 159.4396 | 7.2854 | 21.8848 | 176.933 | 8.0847 | 21.8848 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2027 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 6.2909 | 231 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 1.9561 | 6.1997 | 0.31552 | 1.9561 | 6.1997 | 0.31552 | 2.1707 | 6.8799 | 0.31552 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2027 | 81 | 81-193AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.28938 | 8 | 100% | 0.44576 | 14.6% | 0% | 85.4% | 0.0032221 | 0 | 0 | 0.0032221 | 0 | 0.0029321 | 0.28518 | 0.010282 | 0.0029321 | 0.28518 | 0.010282 | 0.0032538 | 0.31647 | 0.010282 | 0.7228% | 0.0011408 | 0.0010843 | 390.747 | 0.25109 | 87.3722 | 303.1238 | 408.1247 | 0 | 0 | 408.1247 | 1.063e-07%
2027 | 170 | 170-42 | Tier-1 | Non-HFTD---10 | 4--2 | 2.6307 | 74 | 100% | 23.9542 | 86.3% | 7.76% | 5.937% | 1.0233 | 0 | 0 | 1.0233 | 0 | 0.93121 | 2.5925 | 0.35919 | 0.93121 | 2.5925 | 0.35919 | 1.0334 | 2.877 | 0.35919 | 4.272% | 0.037594 | 0.035733 | 637.182 | 77.2313 | 106.2759 | 453.6748 | 641.7271 | 0 | 0 | 641.7271 | 3.375e-05%
2027 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 17.4522 | 914 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 90.6092 | 17.1992 | 5.2682 | 90.6092 | 17.1992 | 5.2682 | 100.5506 | 19.0862 | 5.2682 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2027 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 0.41062 | 17 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.092914 | 0.40467 | 0.22961 | 0.092914 | 0.40467 | 0.22961 | 0.10311 | 0.44907 | 0.22961 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2027 | 72 | 72-12F | Tier-1 | Non-HFTD---19 | 1--1 | 0.23446 | 7 | 100% | 0.35888 | 36.92% | 0% | 63.08% | 0.0065581 | 0 | 0 | 0.0065581 | 0 | 0.0059678 | 0.23106 | 0.025828 | 0.0059678 | 0.23106 | 0.025828 | 0.0066226 | 0.25641 | 0.025828 | 1.827% | 0.0007194 | 0.00068379 | 498.8599 | 8.4651 | 162.404 | 327.9909 | 515.2486 | 0 | 0 | 515.2486 | 2.163e-07%
2027 | 792 | 792-1172F | Tier-1 | Non-HFTD---14 | 3--1 | 5.2345 | 273 | 100% | 6.3558 | 40.89% | 0% | 59.11% | 0.12864 | 0 | 0 | 0.12864 | 0 | 0.11706 | 5.1586 | 0.022693 | 0.11706 | 5.1586 | 0.022693 | 0.12991 | 5.7246 | 0.022693 | 2.024% | 0.014697 | 0.013969 | 432.4678 | 0.27436 | 199.5532 | 232.6402 | 445.7806 | 0 | 0 | 445.7806 | 4.242e-06%
2027 | 452 | 452-37AE | Tier-1 | Non-HFTD---5 | 1--5 | 0.40967 | 44 | 100% | 90.6209 | 99.66% | 0% | 0.3391% | 4.4705 | 0 | 0 | 4.4705 | 0 | 4.0681 | 0.40373 | 10.0763 | 4.0681 | 0.40373 | 10.0763 | 4.5145 | 0.44803 | 10.0763 | 4.933% | 0.0017838 | 0.0016955 | 50802.159 | 10626.9011 | 18.8338 | 40156.424 | 50811.1291 | 0 | 0 | 50811.1291 | 0.0001474%
2027 | 90 | 90-24 | Tier-1 | Non-HFTD---7 | 2--3 | 0.60288 | 19 | 100% | 27.778 | 1.28% | 96.39% | 2.335% | 0.017597 | 0 | 0 | 0.017597 | 0 | 0.016013 | 0.59414 | 0.026951 | 0.016013 | 0.59414 | 0.026951 | 0.01777 | 0.65933 | 0.026951 | 0.06335% | 0.0071986 | 0.0068423 | 3858.8091 | 4.7029 | 3414.9982 | 439.108 | 4057.1958 | 0 | 0 | 4057.1958 | 5.803e-07%
2027 | 275 | CB 275 | Tier-1 | Non-HFTD---2 | 3--4 | 3.0089 | 148 | 100% | 206.6235 | 45.85% | 53.34% | 0.8107% | 4.6895 | 0 | 0 | 4.6895 | 0 | 4.2674 | 2.9652 | 1.4391 | 4.2674 | 2.9652 | 1.4391 | 4.7356 | 3.2906 | 1.4391 | 2.27% | 0.025053 | 0.023813 | 8247.3894 | 358.5021 | 5488.4618 | 2400.4254 | 8479.9674 | 0 | 0 | 8479.9674 | 0.0001546%
2027 | 42 | CB 42 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3775 | 32 | 100% | 5.9866 | 70.69% | 0% | 29.31% | 0.20948 | 0 | 0 | 0.20948 | 0 | 0.19062 | 2.343 | 0.081358 | 0.19062 | 2.343 | 0.081358 | 0.21154 | 2.6001 | 0.081358 | 3.499% | 0.00755 | 0.0071763 | 792.9237 | 22.0026 | 447.2899 | 323.6312 | 805.0273 | 0 | 0 | 805.0273 | 6.908e-06%
2027 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 15.5693 | 654 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 162.0475 | 15.3435 | 10.5613 | 162.0475 | 15.3435 | 10.5613 | 179.8269 | 17.027 | 10.5613 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2027 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 12.821 | 928 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 144.2426 | 12.6351 | 11.416 | 144.2426 | 12.6351 | 11.416 | 160.0686 | 14.0214 | 11.416 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2027 | 525 | CB 525 | Tier-1 | Non-HFTD---5 | 2--4 | 0.53731 | 44 | 100% | 72.1571 | 17.62% | 81.53% | 0.8516% | 0.62936 | 0 | 0 | 0.62936 | 0 | 0.57271 | 0.52952 | 1.0816 | 0.57271 | 0.52952 | 1.0816 | 0.63554 | 0.58762 | 1.0816 | 0.8722% | 0.0072554 | 0.0068963 | 9945.2959 | 206.1053 | 8187.2341 | 1551.9565 | 10371.9649 | 0 | 0 | 10371.9649 | 2.075e-05%
2027 | 306 | 306-961 | Tier-1 | Non-HFTD---8 | 4--2 | 0.25951 | 21 | 100% | 44.8989 | 37.41% | 62.22% | 0.3782% | 0.83134 | 0 | 0 | 0.83134 | 0 | 0.7565 | 0.25575 | 2.958 | 0.7565 | 0.25575 | 2.958 | 0.83951 | 0.28381 | 2.958 | 1.852% | 0.052982 | 0.050359 | 847.4364 | 49.5718 | 468.5847 | 329.2799 | 875.061 | 0 | 0 | 875.061 | 2.741e-05%
2027 | 287 | CB 287 | Tier-1 | Non-HFTD---4 | 3--4 | 2.9707 | 127 | 100% | 114.6676 | 71.93% | 25.48% | 2.591% | 4.0827 | 0 | 0 | 4.0827 | 0 | 3.7152 | 2.9276 | 1.269 | 3.7152 | 2.9276 | 1.269 | 4.1229 | 3.2488 | 1.269 | 3.56% | 0.015966 | 0.015175 | 7182.079 | 404.9612 | 4312.5318 | 2464.586 | 7287.0718 | 0 | 0 | 7287.0718 | 0.0001346%
2027 | 1094 | CB 1094 | Tier-1 | Non-HFTD---9 | 1--5 | 0.38073 | 5 | 100% | 25.2689 | 98.73% | 0% | 1.267% | 1.235 | 0 | 0 | 1.235 | 0 | 1.1238 | 0.37521 | 2.9951 | 1.1238 | 0.37521 | 2.9951 | 1.2471 | 0.41637 | 2.9951 | 4.887% | 0.001448 | 0.0013763 | 17450.9081 | 2431.0189 | 2381.051 | 12638.8381 | 17462.4248 | 0 | 0 | 17462.4248 | 4.072e-05%
2027 | 1438 | 1438-333F | Tier-1 | Non-HFTD---20 | 1--1 | 0.44675 | 30 | 100% | 0.3138 | 20.87% | 0% | 79.13% | 0.0032416 | 0 | 0 | 0.0032416 | 0 | 0.0029498 | 0.44027 | 0.0067 | 0.0029498 | 0.44027 | 0.0067 | 0.0032735 | 0.48858 | 0.0067 | 1.033% | 0.0012552 | 0.0011931 | 249.9971 | 2.9701 | 52.7852 | 194.2418 | 260.2993 | 0 | 0 | 260.2993 | 1.069e-07%
2027 | 489 | 489-33 | Tier-1 | Non-HFTD---20 | 1--1 | 1.3928 | 37 | 100% | 0.5266 | 10.19% | 0% | 89.81% | 0.002657 | 0 | 0 | 0.002657 | 0 | 0.0024178 | 1.3726 | 0.0017615 | 0.0024178 | 1.3726 | 0.0017615 | 0.0026831 | 1.5232 | 0.0017615 | 0.5046% | 0.0028464 | 0.0027055 | 185.0048 | 0.12502 | 33.9508 | 150.929 | 193.6574 | 0 | 0 | 193.6574 | 8.762e-08%
2027 | 80 | 80-575R | Tier-1 | Non-HFTD---15 | 1--2 | 1.7536 | 42 | 100% | 3.3604 | 69.22% | 0% | 30.78% | 0.11514 | 0 | 0 | 0.11514 | 0 | 0.10477 | 1.7282 | 0.060625 | 0.10477 | 1.7282 | 0.060625 | 0.11627 | 1.9178 | 0.060625 | 3.426% | 0.0044504 | 0.0042301 | 755.0854 | 6.5404 | 504.3875 | 244.1574 | 767.1901 | 0 | 0 | 767.1901 | 3.797e-06%
2027 | 178 | 178-983AE | Tier-1 | Non-HFTD---9 | 1--5 | 0.24788 | 9 | 100% | 24.3065 | 99.32% | 0% | 0.6782% | 1.195 | 0 | 0 | 1.195 | 0 | 1.0874 | 0.24429 | 4.4515 | 1.0874 | 0.24429 | 4.4515 | 1.2068 | 0.27109 | 4.4515 | 4.916% | 0.00085 | 0.00080793 | 28595.879 | 4615.9311 | 22.2023 | 23957.7456 | 28605.9786 | 0 | 0 | 28605.9786 | 3.941e-05%
2027 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.094697 | 7 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 5.2263 | 0.093324 | 56.0018 | 5.2263 | 0.093324 | 56.0018 | 5.7997 | 0.10356 | 56.0018 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2027 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | 1--3 | 0.55455 | 52 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.18461 | 0 | 0 | 0.18461 | 0 | 0.168 | 0.5465 | 0.3074 | 0.168 | 0.5465 | 0.3074 | 0.18643 | 0.60647 | 0.3074 | 4.394% | 0.002261 | 0.0021491 | 1858.0978 | 176.4132 | 558.9214 | 1122.7631 | 1868.9599 | 0 | 0 | 1868.9599 | 6.088e-06%
2027 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.03428 | 0 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.1319 | 0.033783 | 33.5039 | 1.1319 | 0.033783 | 33.5039 | 1.2561 | 0.03749 | 33.5039 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2027 | 740 | 740-856F | Tier-1 | Non-HFTD---16 | 2--1 | 2.888 | 214 | 100% | 2.9768 | 34.05% | 0% | 65.95% | 0.050176 | 0 | 0 | 0.050176 | 0 | 0.045659 | 2.8462 | 0.016042 | 0.045659 | 2.8462 | 0.016042 | 0.050669 | 3.1584 | 0.016042 | 1.686% | 0.0078388 | 0.0074508 | 379.746 | 4.2927 | 127.0305 | 248.4227 | 392.788 | 0 | 0 | 392.788 | 1.655e-06%
2027 | 578 | 578-242F | Tier-1 | Non-HFTD---3 | 3--4 | 2.7303 | 60 | 100% | 101.2493 | 1.118% | 96.96% | 1.921% | 0.056018 | 0 | 0 | 0.056018 | 0 | 0.050976 | 2.6907 | 0.018945 | 0.050976 | 2.6907 | 0.018945 | 0.056569 | 2.9859 | 0.018945 | 0.05533% | 0.017989 | 0.017099 | 5628.2774 | 9.7279 | 4959.9632 | 658.5863 | 5918.1099 | 0 | 0 | 5918.1099 | 1.847e-06%
2027 | 506 | 506-160AE | Tier-1 | Non-HFTD---19 | 1--2 | 0.047538 | 2 | 100% | 0.28387 | 86.74% | 0% | 13.26% | 0.012188 | 0 | 0 | 0.012188 | 0 | 0.011091 | 0.046849 | 0.23675 | 0.011091 | 0.046849 | 0.23675 | 0.012308 | 0.051989 | 0.23675 | 4.294% | 0.0001712 | 0.00016273 | 1658.1166 | 166.0816 | 438.3656 | 1053.6695 | 1669.5667 | 0 | 0 | 1669.5667 | 4.019e-07%
2027 | 57 | CB 57 | Tier-1 | Non-HFTD---2 | 4--4 | 7.9972 | 102 | 100% | 246.5725 | 13.42% | 83.87% | 2.714% | 1.6375 | 0 | 0 | 1.6375 | 0 | 1.4901 | 7.8812 | 0.18907 | 1.4901 | 7.8812 | 0.18907 | 1.6536 | 8.746 | 0.18907 | 0.6641% | 0.034392 | 0.03269 | 7169.3891 | 7.2057 | 6458.1009 | 704.0825 | 7492.6625 | 0 | 0 | 7492.6625 | 5.4e-05%
2027 | 781 | CB 781 | Tier-1 | Non-HFTD---4 | 3--4 | 3.2938 | 134 | 100% | 155.4252 | 25.13% | 72.94% | 1.931% | 1.9333 | 0 | 0 | 1.9333 | 0 | 1.7592 | 3.246 | 0.54197 | 1.7592 | 3.246 | 0.54197 | 1.9523 | 3.6022 | 0.54197 | 1.244% | 0.021159 | 0.020111 | 7345.7215 | 11.4899 | 6707.1006 | 627.1309 | 7632.1422 | 0 | 0 | 7632.1422 | 6.375e-05%
2027 | 57 | 57-1292F | Tier-1 | Non-HFTD---9 | 2--2 | 0.68467 | 37 | 100% | 21.0439 | 0.2676% | 97.17% | 2.561% | 0.0027876 | 0 | 0 | 0.0027876 | 0 | 0.0025366 | 0.67475 | 0.0037594 | 0.0025366 | 0.67475 | 0.0037594 | 0.002815 | 0.74878 | 0.0037594 | 0.01325% | 0.012624 | 0.011999 | 1666.9469 | 1.8812 | 1483.5097 | 181.556 | 1753.5256 | 0 | 0 | 1753.5256 | 9.192e-08%
2027 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 2.4583 | 117 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 285.8939 | 2.4227 | 118.007 | 285.8939 | 2.4227 | 118.007 | 317.2615 | 2.6885 | 118.007 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2027 | 723 | 723-793F | Tier-1 | Non-HFTD---20 | 1--1 | 0.16136 | 30 | 100% | 0.15365 | 52.88% | 0% | 47.12% | 0.004022 | 0 | 0 | 0.004022 | 0 | 0.00366 | 0.15902 | 0.023015 | 0.00366 | 0.15902 | 0.023015 | 0.0040615 | 0.17647 | 0.023015 | 2.618% | 0.0004994 | 0.00047468 | 307.6774 | 26.5 | 14.647 | 266.5305 | 315.2275 | 0 | 0 | 315.2275 | 1.326e-07%
2027 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 16.5898 | 1848 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 700.4791 | 16.3493 | 42.8447 | 700.4791 | 16.3493 | 42.8447 | 777.3341 | 18.1431 | 42.8447 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2027 | 474 | 474-22AE | Tier-1 | Non-HFTD---1 | 4--5 | 9.6011 | 965 | 100% | 6435.9834 | 99.89% | 0% | 0.1146% | 318.2162 | 0 | 0 | 318.2162 | 0 | 289.5724 | 9.4619 | 30.604 | 289.5724 | 9.4619 | 30.604 | 321.3436 | 10.5001 | 30.604 | 4.944% | 0.046635 | 0.044327 | 138007.5774 | 24328.5202 | 121.2373 | 113557.8199 | 138015.8115 | 0 | 0 | 138015.8115 | 0.01049%
2027 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 8.9873 | 712 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 71.3855 | 8.857 | 8.0598 | 71.3855 | 8.857 | 8.0598 | 79.2178 | 9.8288 | 8.0598 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2027 | NO1 | CB NO1 | Tier-1 | Non-HFTD---20 | 1--1 | 0.16004 | 5 | 100% | 0.11186 | 6.282% | 0% | 93.72% | 0.00034784 | 0 | 0 | 0.00034784 | 0 | 0.00031653 | 0.15772 | 0.0020069 | 0.00031653 | 0.15772 | 0.0020069 | 0.00035126 | 0.17503 | 0.0020069 | 0.311% | 0.0004254 | 0.00040434 | 262.9516 | 0.18543 | 38.9048 | 223.8613 | 275.7853 | 0 | 0 | 275.7853 | 1.147e-08%
2027 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 6.7553 | 1558 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 129.1825 | 6.6574 | 19.4044 | 129.1825 | 6.6574 | 19.4044 | 143.3561 | 7.3878 | 19.4044 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2027 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | 4--1 | 0.16307 | 3 | 100% | 2.3826 | 9.042% | 83.57% | 7.391% | 0.010664 | 0 | 0 | 0.010664 | 0 | 0.0097039 | 0.1607 | 0.060384 | 0.0097039 | 0.1607 | 0.060384 | 0.010769 | 0.17834 | 0.060384 | 0.4476% | 0.059368 | 0.05643 | 40.1318 | 0.36722 | 29.4839 | 10.2807 | 42.0328 | 0 | 0 | 42.0328 | 3.517e-07%
2027 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.038636 | 0 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.74762 | 0.038076 | 19.6348 | 0.74762 | 0.038076 | 19.6348 | 0.82964 | 0.042254 | 19.6348 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2027 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 1.5002 | 51 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.8571 | 1.4784 | 1.2561 | 1.8571 | 1.4784 | 1.2561 | 2.0608 | 1.6406 | 1.2561 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2027 | 252 | 252-277F | Tier-1 | Non-HFTD---15 | 1--2 | 0.90889 | 30 | 100% | 3.3511 | 64.95% | 0% | 35.05% | 0.10774 | 0 | 0 | 0.10774 | 0 | 0.098038 | 0.89571 | 0.10945 | 0.098038 | 0.89571 | 0.10945 | 0.10879 | 0.99399 | 0.10945 | 3.215% | 0.0037008 | 0.0035176 | 905.5022 | 85.5311 | 154.0815 | 665.8897 | 922.0312 | 0 | 0 | 922.0312 | 3.553e-06%
2027 | 1286 | CB 1286 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1557 | 55 | 100% | 2.6947 | 57.45% | 0% | 42.55% | 0.076626 | 0 | 0 | 0.076626 | 0 | 0.069729 | 1.1389 | 0.061225 | 0.069729 | 1.1389 | 0.061225 | 0.077379 | 1.2639 | 0.061225 | 2.844% | 0.0043234 | 0.0041094 | 623.2816 | 31.002 | 192.2211 | 400.0585 | 637.0941 | 0 | 0 | 637.0941 | 2.527e-06%
2027 | 161 | 161-974F | Tier-1 | Non-HFTD---15 | 1--2 | 1.2625 | 35 | 100% | 2.9871 | 73.28% | 0% | 26.72% | 0.10836 | 0 | 0 | 0.10836 | 0 | 0.098605 | 1.2442 | 0.07925 | 0.098605 | 1.2442 | 0.07925 | 0.10942 | 1.3807 | 0.07925 | 3.628% | 0.0046736 | 0.0044423 | 639.1485 | 67.3315 | 71.5481 | 500.2689 | 648.0412 | 0 | 0 | 648.0412 | 3.573e-06%
2027 | 770 | 770-250R | Tier-1 | Non-HFTD---13 | 1--3 | 0.94323 | 92 | 100% | 8.2742 | 91.72% | 0% | 8.276% | 0.37568 | 0 | 0 | 0.37568 | 0 | 0.34186 | 0.92955 | 0.36777 | 0.34186 | 0.92955 | 0.36777 | 0.37937 | 1.0315 | 0.36777 | 4.54% | 0.003255 | 0.0030939 | 2542.0097 | 485.388 | 24.5872 | 2032.0344 | 2552.9659 | 0 | 0 | 2552.9659 | 1.239e-05%
2027 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 13.8138 | 967 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 506.1555 | 13.6135 | 37.1803 | 506.1555 | 13.6135 | 37.1803 | 561.6897 | 15.1072 | 37.1803 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2027 | 188 | 188-11F | Tier-2 | Tier-2---7 | 3--5 | 5.0004 | 427 | 100% | 2209.344 | 99.86% | 0% | 0.1429% | 109.2062 | 0 | 0 | 109.2062 | 0 | 99.3762 | 4.9279 | 20.1662 | 99.3762 | 4.9279 | 20.1662 | 110.2795 | 5.4685 | 20.1662 | 4.943% | 0.019333 | 0.018376 | 114277.2032 | 24326.824 | 78.3726 | 89872.0066 | 114285.7081 | 0 | 0 | 114285.7081 | 0.003601%
2027 | 175 | CB 175 | Tier-2 | Tier-2---10 | 5--4 | 2.8512 | 275 | 100% | 1236.5075 | 84.14% | 15.66% | 0.203% | 51.5004 | 0 | 0 | 51.5004 | 0 | 46.8647 | 2.8098 | 16.6788 | 46.8647 | 2.8098 | 16.6788 | 52.0066 | 3.1181 | 16.6788 | 4.165% | 0.16723 | 0.15895 | 7393.9644 | 1133.6762 | 1185.8912 | 5074.397 | 7455.0304 | 0 | 0 | 7455.0304 | 0.001698%
2027 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 3.0667 | 69 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 22.5604 | 3.0222 | 7.4648 | 22.5604 | 3.0222 | 7.4648 | 25.0356 | 3.3538 | 7.4648 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2027 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 13.4184 | 1026 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1444.8081 | 13.2238 | 109.2582 | 1444.8081 | 13.2238 | 109.2582 | 1603.3291 | 14.6747 | 109.2582 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2027 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 3.4998 | 176 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 20.4346 | 3.449 | 5.9247 | 20.4346 | 3.449 | 5.9247 | 22.6767 | 3.8275 | 5.9247 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2027 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 20.6608 | 1532 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 1037.5009 | 20.3612 | 50.9548 | 1037.5009 | 20.3612 | 50.9548 | 1151.3331 | 22.5952 | 50.9548 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2027 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 11.56 | 909 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 1007.0762 | 11.3924 | 88.3987 | 1007.0762 | 11.3924 | 88.3987 | 1117.5702 | 12.6424 | 88.3987 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2027 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 5.1261 | 362 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 154.4302 | 5.0518 | 30.5692 | 154.4302 | 5.0518 | 30.5692 | 171.3739 | 5.6061 | 30.5692 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2027 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 2.1386 | 164 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 48.5811 | 2.1076 | 23.0506 | 48.5811 | 2.1076 | 23.0506 | 53.9113 | 2.3388 | 23.0506 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2027 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 5.9518 | 999 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 404.9546 | 5.8655 | 69.0406 | 404.9546 | 5.8655 | 69.0406 | 449.3853 | 6.509 | 69.0406 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2027 | 1438 | 1438-331F | Tier-1 | Non-HFTD---19 | 1--1 | 0.11725 | 0 | 100% | 0.12483 | 14.96% | 0% | 85.04% | 0.00092462 | 0 | 0 | 0.00092462 | 0 | 0.00084139 | 0.11555 | 0.0072813 | 0.00084139 | 0.11555 | 0.0072813 | 0.00093371 | 0.12823 | 0.0072813 | 0.7407% | 0.000355 | 0.00033743 | 351.6369 | 0.225 | 79.7806 | 271.6313 | 367.2091 | 0 | 0 | 367.2091 | 3.049e-08%
2027 | 161 | 161-991F | Tier-1 | Non-HFTD---12 | 3--1 | 9.0516 | 207 | 100% | 10.7177 | 44.4% | 0% | 55.6% | 0.23557 | 0 | 0 | 0.23557 | 0 | 0.21437 | 8.9203 | 0.024031 | 0.21437 | 8.9203 | 0.024031 | 0.23789 | 9.899 | 0.024031 | 2.198% | 0.025268 | 0.024017 | 424.1613 | 21.5449 | 118.7087 | 283.9078 | 436.4423 | 0 | 0 | 436.4423 | 7.768e-06%
2027 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 1.0659 | 30 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 59.2108 | 1.0504 | 56.3672 | 59.2108 | 1.0504 | 56.3672 | 65.7073 | 1.1657 | 56.3672 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2027 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 3.7138 | 186 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 100.4117 | 3.66 | 27.4349 | 100.4117 | 3.66 | 27.4349 | 111.4286 | 4.0616 | 27.4349 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2027 | 713 | 713-169 | Tier-1 | Non-HFTD---19 | 1--1 | 0.36193 | 0 | 100% | 0.56535 | 24.4% | 0% | 75.6% | 0.0068286 | 0 | 0 | 0.0068286 | 0 | 0.006214 | 0.35668 | 0.017421 | 0.006214 | 0.35668 | 0.017421 | 0.0068957 | 0.39582 | 0.017421 | 1.208% | 0.0014716 | 0.0013988 | 384.1744 | 11.8523 | 47.4609 | 324.8612 | 399.2994 | 0 | 0 | 399.2994 | 2.252e-07%
2027 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 13.767 | 1106 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 574.3981 | 13.5674 | 42.3366 | 574.3981 | 13.5674 | 42.3366 | 637.4198 | 15.056 | 42.3366 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2027 | 92 | 92-619F | Tier-2 | Tier-2---14 | 3--4 | 3.3373 | 77 | 100% | 202.8689 | 46.88% | 52.08% | 1.034% | 4.708 | 0 | 0 | 4.708 | 0 | 4.2842 | 3.2889 | 1.3026 | 4.2842 | 3.2889 | 1.3026 | 4.7543 | 3.6498 | 1.3026 | 2.321% | 0.015617 | 0.014844 | 12990.5937 | 1279.3739 | 6200.2786 | 5510.9412 | 13349.9397 | 0 | 0 | 13349.9397 | 0.0001553%
2027 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 17.727 | 1516 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1568.061 | 17.47 | 89.7573 | 1568.061 | 17.47 | 89.7573 | 1740.105 | 19.3868 | 89.7573 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2027 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 8.6068 | 720 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 111.8057 | 8.482 | 13.1815 | 111.8057 | 8.482 | 13.1815 | 124.0728 | 9.4126 | 13.1815 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2027 | 928 | 928-20 | Tier-2 | Tier-2---20 | 4--2 | 0.15818 | 49 | 100% | 27.1749 | 93.08% | 6.522% | 0.4024% | 1.252 | 0 | 0 | 1.252 | 0 | 1.1393 | 0.15589 | 7.3087 | 1.1393 | 0.15589 | 7.3087 | 1.2643 | 0.17299 | 7.3087 | 4.607% | 0.044362 | 0.042166 | 612.5656 | 93.209 | 34.6926 | 484.664 | 614.7746 | 0 | 0 | 614.7746 | 4.129e-05%
2027 | AD2 | CB AD2 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3572 | 43 | 100% | 40.3722 | 2.888% | 92.69% | 4.427% | 0.057707 | 0 | 0 | 0.057707 | 0 | 0.052512 | 2.323 | 0.022605 | 0.052512 | 2.323 | 0.022605 | 0.058274 | 2.5779 | 0.022605 | 0.1429% | 0.011539 | 0.010968 | 3498.6997 | 6.8788 | 3053.1148 | 438.7061 | 3675.6431 | 0 | 0 | 3675.6431 | 1.903e-06%
2027 | 90 | 90-44AE | Tier-1 | Non-HFTD---4 | 3--4 | 3.5829 | 134 | 100% | 101.3703 | 11.74% | 85.7% | 2.562% | 0.58913 | 0 | 0 | 0.58913 | 0 | 0.5361 | 3.531 | 0.15183 | 0.5361 | 3.531 | 0.15183 | 0.59492 | 3.9184 | 0.15183 | 0.5812% | 0.015099 | 0.014352 | 6713.5305 | 6.5653 | 6082.8987 | 624.0665 | 7022.1078 | 0 | 0 | 7022.1078 | 1.943e-05%
2027 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 2.8193 | 63 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 16.745 | 2.7784 | 6.0268 | 16.745 | 2.7784 | 6.0268 | 18.5822 | 3.0833 | 6.0268 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2027 | EOS3 | CB EOS3 | Tier-1 | Non-HFTD---11 | 2--3 | 2.4386 | 83 | 100% | 14.1826 | 87.38% | 0% | 12.62% | 0.61345 | 0 | 0 | 0.61345 | 0 | 0.55823 | 2.4032 | 0.23228 | 0.55823 | 2.4032 | 0.23228 | 0.61948 | 2.6669 | 0.23228 | 4.325% | 0.0075404 | 0.0071672 | 1880.8804 | 242.4617 | 179.6503 | 1458.7683 | 1893.2412 | 0 | 0 | 1893.2412 | 2.023e-05%
2027 | 392 | 392-23F | Tier-1 | Non-HFTD---2 | 5--3 | 2.6426 | 50 | 100% | 466.525 | 0.9229% | 98.62% | 0.4561% | 0.21313 | 0 | 0 | 0.21313 | 0 | 0.19394 | 2.6043 | 0.074471 | 0.19394 | 2.6043 | 0.074471 | 0.21522 | 2.89 | 0.074471 | 0.04568% | 0.10259 | 0.097512 | 4547.4707 | 15.3107 | 3769.5708 | 762.5892 | 4782.1075 | 0 | 0 | 4782.1075 | 7.028e-06%
2027 | 949 | 949-22R | Tier-1 | Non-HFTD---12 | 3--2 | 5.1989 | 436 | 100% | 9.2316 | 56.06% | 0% | 43.94% | 0.25619 | 0 | 0 | 0.25619 | 0 | 0.23313 | 5.1235 | 0.045502 | 0.23313 | 5.1235 | 0.045502 | 0.25871 | 5.6856 | 0.045502 | 2.775% | 0.016401 | 0.015589 | 562.8643 | 27.9703 | 168.0106 | 366.8833 | 575.7433 | 0 | 0 | 575.7433 | 8.448e-06%
2027 | 245 | 245-486 | Tier-1 | Non-HFTD---2 | 4--4 | 4.3474 | 192 | 100% | 294.2309 | 35.69% | 63.39% | 0.9197% | 5.1981 | 0 | 0 | 5.1981 | 0 | 4.7302 | 4.2843 | 1.1041 | 4.7302 | 4.2843 | 1.1041 | 5.2492 | 4.7544 | 1.1041 | 1.767% | 0.039483 | 0.037529 | 7452.0521 | 531.8785 | 4332.7245 | 2587.4492 | 7701.6294 | 0 | 0 | 7701.6294 | 0.0001714%
2027 | 452 | 452-39AE | Tier-1 | Non-HFTD---1 | 2--5 | 1.292 | 196 | 100% | 261.2424 | 99.61% | 0% | 0.3884% | 12.8813 | 0 | 0 | 12.8813 | 0 | 11.7218 | 1.2733 | 9.2059 | 11.7218 | 1.2733 | 9.2059 | 13.0079 | 1.413 | 9.2059 | 4.931% | 0.0055772 | 0.0053011 | 46841.1346 | 13719.2411 | 19.0906 | 33102.8029 | 46850.6095 | 0 | 0 | 46850.6095 | 0.0004248%
2027 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 4.0824 | 476 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 19.1528 | 4.0232 | 4.7606 | 19.1528 | 4.0232 | 4.7606 | 21.2542 | 4.4646 | 4.7606 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2027 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 13.2557 | 1044 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 120.9234 | 13.0635 | 9.2566 | 120.9234 | 13.0635 | 9.2566 | 134.1908 | 14.4968 | 9.2566 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2027 | 474 | CB 474 | Tier-1 | Non-HFTD---1 | 3--5 | 4.6676 | 497 | 100% | 794.8798 | 99.6% | 0% | 0.3957% | 39.1908 | 0 | 0 | 39.1908 | 0 | 35.6631 | 4.5999 | 7.753 | 35.6631 | 4.5999 | 7.753 | 39.576 | 5.1046 | 7.753 | 4.93% | 0.016088 | 0.015291 | 49409.4676 | 7937.2559 | 481.7871 | 40990.4246 | 49419.6498 | 0 | 0 | 49419.6498 | 0.001292%
2027 | 164 | CB 164 | Tier-1 | Non-HFTD---13 | 1--2 | 1.583 | 41 | 100% | 5.3562 | 79.49% | 0% | 20.51% | 0.21076 | 0 | 0 | 0.21076 | 0 | 0.19179 | 1.56 | 0.12294 | 0.19179 | 1.56 | 0.12294 | 0.21283 | 1.7312 | 0.12294 | 3.935% | 0.0047404 | 0.0045058 | 1129.913 | 8.1525 | 869.9018 | 251.8587 | 1141.9803 | 0 | 0 | 1141.9803 | 6.95e-06%
2027 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 1.2773 | 61 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 25.6219 | 1.2588 | 20.355 | 25.6219 | 1.2588 | 20.355 | 28.4331 | 1.3969 | 20.355 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2027 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 7.3796 | 119 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 209.6923 | 7.2726 | 28.8332 | 209.6923 | 7.2726 | 28.8332 | 232.6993 | 8.0705 | 28.8332 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2027 | DS1 | CB DS1 | Tier-1 | Non-HFTD---12 | 3--2 | 1.7008 | 75 | 100% | 13.0351 | 8.296% | 84.41% | 7.29% | 0.053527 | 0 | 0 | 0.053527 | 0 | 0.048709 | 1.6761 | 0.02906 | 0.048709 | 1.6761 | 0.02906 | 0.054053 | 1.86 | 0.02906 | 0.4106% | 0.014723 | 0.013994 | 885.347 | 9.9559 | 707.4464 | 167.9447 | 927.6291 | 0 | 0 | 927.6291 | 1.765e-06%
2027 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.87803 | 17 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 29.2851 | 0.8653 | 33.8438 | 29.2851 | 0.8653 | 33.8438 | 32.4982 | 0.96024 | 33.8438 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2027 | 554 | CB 554 | Tier-1 | Non-HFTD---15 | 1--2 | 0.48106 | 1 | 100% | 2.8878 | 78.27% | 0% | 21.73% | 0.11188 | 0 | 0 | 0.11188 | 0 | 0.10181 | 0.47409 | 0.21475 | 0.10181 | 0.47409 | 0.21475 | 0.11298 | 0.5261 | 0.21475 | 3.874% | 0.0020388 | 0.0019379 | 1416.4094 | 124.7784 | 373.0089 | 918.622 | 1432.4394 | 0 | 0 | 1432.4394 | 3.689e-06%
2027 | 452 | 452-717 | Tier-2 | Tier-2---19 | 1--5 | 0.29487 | 27 | 100% | 24.802 | 99.04% | 0% | 0.9608% | 1.2159 | 0 | 0 | 1.2159 | 0 | 1.1065 | 0.29059 | 3.8076 | 1.1065 | 0.29059 | 3.8076 | 1.2279 | 0.32247 | 3.8076 | 4.902% | 0.000973 | 0.00092484 | 25490.2561 | 9086.828 | 25.5586 | 16377.8695 | 25503.0101 | 0 | 0 | 25503.0101 | 4.01e-05%
2027 | 250 | 250-47 | Tier-1 | Non-HFTD---19 | 1--2 | 0.076894 | 8 | 100% | 0.26608 | 73.81% | 0% | 26.19% | 0.009721 | 0 | 0 | 0.009721 | 0 | 0.008846 | 0.075779 | 0.11673 | 0.008846 | 0.075779 | 0.11673 | 0.0098165 | 0.084093 | 0.11673 | 3.653% | 0.0002818 | 0.00026785 | 944.2218 | 112.5399 | 22.9232 | 808.7588 | 957.1024 | 0 | 0 | 957.1024 | 3.206e-07%
2027 | 195 | CB 195 | Tier-1 | Non-HFTD---1 | 4--4 | 2.8899 | 388 | 100% | 363.2496 | 59.46% | 39.93% | 0.6035% | 10.6919 | 0 | 0 | 10.6919 | 0 | 9.7294 | 2.848 | 3.4162 | 9.7294 | 2.848 | 3.4162 | 10.7969 | 3.1605 | 3.4162 | 2.943% | 0.029402 | 0.027947 | 12354.4195 | 1165.0324 | 4745.6591 | 6443.728 | 12615.2346 | 0 | 0 | 12615.2346 | 0.0003526%
2027 | 597 | CB 597 | Tier-2 | Tier-2---14 | 1--5 | 1.0557 | 113 | 100% | 218.0489 | 99.66% | 0% | 0.3378% | 10.757 | 0 | 0 | 10.757 | 0 | 9.7887 | 1.0404 | 9.4088 | 9.7887 | 1.0404 | 9.4088 | 10.8627 | 1.1545 | 9.4088 | 4.933% | 0.0040332 | 0.0038336 | 54063.4858 | 8115.5826 | 4098.4737 | 41849.4295 | 54072.9953 | 0 | 0 | 54072.9953 | 0.0003547%
2027 | OT2 | CB OT2 | Tier-1 | Non-HFTD---8 | 3--3 | 3.4801 | 92 | 100% | 45.4213 | 3.226% | 91.33% | 5.441% | 0.072536 | 0 | 0 | 0.072536 | 0 | 0.066007 | 3.4297 | 0.019246 | 0.066007 | 3.4297 | 0.019246 | 0.073249 | 3.8059 | 0.019246 | 0.1597% | 0.024647 | 0.023427 | 1842.8901 | 7.4819 | 1565.7674 | 269.6408 | 1935.7675 | 0 | 0 | 1935.7675 | 2.392e-06%
2027 | 968 | 968-476F | Tier-2 | Tier-2---17 | 3--3 | 2.5405 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 2.9977 | 0 | 0 | 2.9977 | 0 | 2.7279 | 2.5037 | 1.0895 | 2.7279 | 2.5037 | 1.0895 | 3.0271 | 2.7784 | 1.0895 | 4.797% | 0.015315 | 0.014557 | 4080.3921 | 1049.3579 | 36.5623 | 2994.4719 | 4086.964 | 0 | 0 | 4086.964 | 9.885e-05%
2027 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 3.8122 | 504 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 417.8482 | 3.7569 | 111.2217 | 417.8482 | 3.7569 | 111.2217 | 463.6936 | 4.1691 | 111.2217 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2027 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 10.9521 | 993 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 675.9035 | 10.7933 | 62.6226 | 675.9035 | 10.7933 | 62.6226 | 750.0621 | 11.9775 | 62.6226 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2027 | 723 | 723-792F | Tier-1 | Non-HFTD---19 | 1--1 | 0.2026 | 9 | 100% | 0.19474 | 41.11% | 0% | 58.89% | 0.0039627 | 0 | 0 | 0.0039627 | 0 | 0.003606 | 0.19967 | 0.01806 | 0.003606 | 0.19967 | 0.01806 | 0.0040017 | 0.22157 | 0.01806 | 2.035% | 0.0005522 | 0.00052487 | 352.6648 | 19.2157 | 47.4573 | 285.9917 | 363.4808 | 0 | 0 | 363.4808 | 1.307e-07%
2027 | 161 | CB 161 | Tier-1 | Non-HFTD---11 | 1--3 | 0.78239 | 11 | 100% | 13.2728 | 94.99% | 0% | 5.009% | 0.62409 | 0 | 0 | 0.62409 | 0 | 0.56792 | 0.77104 | 0.73656 | 0.56792 | 0.77104 | 0.73656 | 0.63023 | 0.85564 | 0.73656 | 4.702% | 0.002891 | 0.0027479 | 4591.0843 | 3.1452 | 4363.6333 | 224.3059 | 4603.061 | 0 | 0 | 4603.061 | 2.058e-05%
2027 | 342 | 342-514F | Tier-1 | Non-HFTD---16 | 2--1 | 4.5697 | 173 | 100% | 4.6383 | 28.46% | 0% | 71.54% | 0.065351 | 0 | 0 | 0.065351 | 0 | 0.059468 | 4.5035 | 0.013205 | 0.059468 | 4.5035 | 0.013205 | 0.065993 | 4.9976 | 0.013205 | 1.409% | 0.013236 | 0.012581 | 350.4217 | 5.7925 | 88.2778 | 256.3514 | 363.4765 | 0 | 0 | 363.4765 | 2.155e-06%
2027 | 334 | 334-21 | Tier-1 | Non-HFTD---2 | 5--3 | 7.2951 | 196 | 100% | 378.2145 | 89.09% | 9.517% | 1.396% | 16.6786 | 0 | 0 | 16.6786 | 0 | 15.1773 | 7.1893 | 2.1111 | 15.1773 | 7.1893 | 2.1111 | 16.8426 | 7.9781 | 2.1111 | 4.41% | 0.11474 | 0.10906 | 3296.3029 | 544.604 | 266.9039 | 2484.795 | 3315.0355 | 0 | 0 | 3315.0355 | 0.00055%
2027 | 314 | CB 314 | Tier-1 | Non-HFTD---1 | 3--4 | 1.0947 | 32 | 100% | 255.5795 | 52.94% | 46.78% | 0.2824% | 6.6973 | 0 | 0 | 6.6973 | 0 | 6.0944 | 1.0788 | 5.6493 | 6.0944 | 1.0788 | 5.6493 | 6.7631 | 1.1971 | 5.6493 | 2.62% | 0.021433 | 0.020372 | 11924.6916 | 952.6976 | 5630.0979 | 5341.896 | 12216.954 | 0 | 0 | 12216.954 | 0.0002209%
2027 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 7.6676 | 440 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 25.8594 | 7.5564 | 3.4222 | 25.8594 | 7.5564 | 3.4222 | 28.6967 | 8.3855 | 3.4222 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2027 | 771 | 771-274AE | Tier-1 | Non-HFTD---19 | 1--2 | 0.13125 | 10 | 100% | 0.57016 | 61.28% | 0% | 38.72% | 0.017295 | 0 | 0 | 0.017295 | 0 | 0.015738 | 0.12935 | 0.12167 | 0.015738 | 0.12935 | 0.12167 | 0.017464 | 0.14354 | 0.12167 | 3.033% | 0.0006212 | 0.00059045 | 917.8285 | 52.5226 | 272.2512 | 593.0547 | 936.3367 | 0 | 0 | 936.3367 | 5.703e-07%
2027 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 4.4809 | 284 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 43.1232 | 4.4159 | 9.7654 | 43.1232 | 4.4159 | 9.7654 | 47.8546 | 4.9004 | 9.7654 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2027 | 545 | 545-874R | Tier-1 | Non-HFTD---4 | 3--4 | 3.5507 | 93 | 100% | 149.8608 | 5.982% | 92.24% | 1.775% | 0.44376 | 0 | 0 | 0.44376 | 0 | 0.40382 | 3.4993 | 0.1154 | 0.40382 | 3.4993 | 0.1154 | 0.44812 | 3.8832 | 0.1154 | 0.2961% | 0.020584 | 0.019565 | 7280.5198 | 7.5721 | 6605.319 | 667.6287 | 7636.9922 | 0 | 0 | 7636.9922 | 1.463e-05%
2027 | 562 | CB 562 | Tier-1 | Non-HFTD---1 | 2--5 | 1.5066 | 1 | 100% | 385.0598 | 99.74% | 0% | 0.2579% | 19.0113 | 0 | 0 | 19.0113 | 0 | 17.3 | 1.4848 | 11.6514 | 17.3 | 1.4848 | 11.6514 | 19.1981 | 1.6477 | 11.6514 | 4.937% | 0.0064962 | 0.0061746 | 59274.622 | 37636.7204 | 2222.5751 | 19415.3265 | 59282.5839 | 0 | 0 | 59282.5839 | 0.0006269%
2027 | 256 | 256-39AE | Tier-1 | Non-HFTD---18 | 1--1 | 1.2698 | 44 | 100% | 1.0609 | 19.16% | 0% | 80.84% | 0.010061 | 0 | 0 | 0.010061 | 0 | 0.0091551 | 1.2514 | 0.0073157 | 0.0091551 | 1.2514 | 0.0073157 | 0.01016 | 1.3887 | 0.0073157 | 0.9484% | 0.0034328 | 0.0032629 | 309.0347 | 0.18799 | 81.9019 | 226.9448 | 322.0452 | 0 | 0 | 322.0452 | 3.318e-07%
2027 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 13.0331 | 1634 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 833.1015 | 12.8442 | 64.8623 | 833.1015 | 12.8442 | 64.8623 | 924.5075 | 14.2534 | 64.8623 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2027 | 855 | 855-45 | Tier-1 | Non-HFTD---20 | 1--1 | 0.17043 | 1 | 100% | 0.068838 | 3.968% | 0% | 96.03% | 0.00013522 | 0 | 0 | 0.00013522 | 0 | 0.00012305 | 0.16796 | 0.00073263 | 0.00012305 | 0.16796 | 0.00073263 | 0.00013655 | 0.18638 | 0.00073263 | 0.1964% | 0.0003944 | 0.00037488 | 174.5396 | 0.12612 | 22.1525 | 152.261 | 183.2685 | 0 | 0 | 183.2685 | 4.459e-09%
2027 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 12.3091 | 646 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 611.3449 | 12.1306 | 50.3967 | 611.3449 | 12.1306 | 50.3967 | 678.4203 | 13.4616 | 50.3967 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2027 | 288 | 288-18 | Tier-1 | Non-HFTD---1 | 3--5 | 5.4562 | 1025 | 100% | 1717.8671 | 96.12% | 3.649% | 0.229% | 81.7367 | 0 | 0 | 81.7367 | 0 | 74.3793 | 5.3771 | 13.8326 | 74.3793 | 5.3771 | 13.8326 | 82.54 | 5.9671 | 13.8326 | 4.758% | 0.026137 | 0.024843 | 65724.9856 | 11143.2146 | 2230.6061 | 52351.1649 | 65857.7245 | 0 | 0 | 65857.7245 | 0.002695%
2027 | 452 | 452-47 | Tier-1 | Non-HFTD---11 | 2--3 | 1.7508 | 32 | 100% | 8.9597 | 85.97% | 0% | 14.03% | 0.3813 | 0 | 0 | 0.3813 | 0 | 0.34698 | 1.7254 | 0.2011 | 0.34698 | 1.7254 | 0.2011 | 0.38505 | 1.9147 | 0.2011 | 4.256% | 0.0051162 | 0.0048629 | 1751.2376 | 0.18482 | 1527.9269 | 223.1259 | 1764.0292 | 0 | 0 | 1764.0292 | 1.257e-05%
2027 | 69 | 69-45F | Tier-1 | Non-HFTD---4 | 2--4 | 0.32272 | 10 | 100% | 106.7813 | 2.696% | 97.13% | 0.1713% | 0.14248 | 0 | 0 | 0.14248 | 0 | 0.12965 | 0.31804 | 0.40767 | 0.12965 | 0.31804 | 0.40767 | 0.14388 | 0.35293 | 0.40767 | 0.1334% | 0.008264 | 0.0078549 | 12921.2611 | 83.6052 | 11175.4926 | 1662.1634 | 13576.0339 | 0 | 0 | 13576.0339 | 4.698e-06%
2027 | ALV1 | CB ALV1 | Tier-1 | Non-HFTD---9 | 2--3 | 1.8195 | 145 | 100% | 23.1135 | 96.16% | 0% | 3.841% | 1.1002 | 0 | 0 | 1.1002 | 0 | 1.0011 | 1.7931 | 0.55832 | 1.0011 | 1.7931 | 0.55832 | 1.111 | 1.9899 | 0.55832 | 4.76% | 0.0050056 | 0.0047578 | 4617.5342 | 724.8553 | 33.5047 | 3859.1742 | 4626.7717 | 0 | 0 | 4626.7717 | 3.628e-05%
2027 | 60 | 60-574 | Tier-1 | Non-HFTD---13 | 2--2 | 3.014 | 84 | 100% | 8.5311 | 71.96% | 0% | 28.04% | 0.3039 | 0 | 0 | 0.3039 | 0 | 0.27654 | 2.9703 | 0.093101 | 0.27654 | 2.9703 | 0.093101 | 0.30688 | 3.2962 | 0.093101 | 3.562% | 0.0093494 | 0.0088866 | 912.477 | 24.9805 | 528.1696 | 359.327 | 925.7996 | 0 | 0 | 925.7996 | 1.002e-05%
2027 | 703 | CB 703 | Tier-1 | Non-HFTD---13 | 2--2 | 0.13314 | 1 | 100% | 6.8734 | 94.98% | 2.252% | 2.765% | 0.32316 | 0 | 0 | 0.32316 | 0 | 0.29407 | 0.13121 | 2.2412 | 0.29407 | 0.13121 | 2.2412 | 0.32634 | 0.14561 | 2.2412 | 4.702% | 0.0055408 | 0.0052665 | 1240.5052 | 28.6229 | 1027.2685 | 184.6138 | 1243.7466 | 0 | 0 | 1243.7466 | 1.066e-05%
2027 | 229 | CB 229 | Tier-1 | Non-HFTD---15 | 1--3 | 0.16098 | 0 | 100% | 2.744 | 94.71% | 0% | 5.287% | 0.12865 | 0 | 0 | 0.12865 | 0 | 0.11707 | 0.15865 | 0.73791 | 0.11707 | 0.15865 | 0.73791 | 0.12991 | 0.17606 | 0.73791 | 4.688% | 0.0005864 | 0.00055737 | 4679.4778 | 389.4263 | 2294.1086 | 1995.9429 | 4692.3613 | 0 | 0 | 4692.3613 | 4.242e-06%
2027 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 2.6869 | 346 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 19.0795 | 2.6479 | 7.2055 | 19.0795 | 2.6479 | 7.2055 | 21.1729 | 2.9385 | 7.2055 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2027 | 532 | CB 532 | Tier-1 | Non-HFTD---10 | 3--2 | 5.6968 | 88 | 100% | 16.397 | 75.87% | 0% | 24.13% | 0.61579 | 0 | 0 | 0.61579 | 0 | 0.56036 | 5.6142 | 0.099812 | 0.56036 | 5.6142 | 0.099812 | 0.62184 | 6.2301 | 0.099812 | 3.756% | 0.016027 | 0.015234 | 1023.0743 | 0.6764 | 795.5841 | 226.8138 | 1035.9312 | 0 | 0 | 1035.9312 | 2.031e-05%
2027 | 572 | 572-493F | Tier-1 | Non-HFTD---20 | 1--1 | 0.20172 | 3 | 100% | 0.12336 | 2.076% | 0% | 97.92% | 0.00012676 | 0 | 0 | 0.00012676 | 0 | 0.00011535 | 0.1988 | 0.00058022 | 0.00011535 | 0.1988 | 0.00058022 | 0.000128 | 0.22061 | 0.00058022 | 0.1027% | 0.000542 | 0.00051517 | 227.6098 | 0.16771 | 24.9717 | 202.4705 | 239.2172 | 0 | 0 | 239.2172 | 4.18e-09%
2027 | 456 | CB 456 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0005 | 145 | 100% | 54.2335 | 91.66% | 0% | 8.342% | 2.4606 | 0 | 0 | 2.4606 | 0 | 2.2391 | 5.9135 | 0.37865 | 2.2391 | 5.9135 | 0.37865 | 2.4848 | 6.5623 | 0.37865 | 4.537% | 0.018506 | 0.01759 | 2930.6543 | 41.8221 | 2453.6064 | 435.2259 | 2943.3855 | 0 | 0 | 2943.3855 | 8.114e-05%
2027 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 16.7242 | 1062 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1379.245 | 16.4817 | 83.6832 | 1379.245 | 16.4817 | 83.6832 | 1530.5725 | 18.2901 | 83.6832 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2027 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 1.5242 | 73 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 12.3234 | 1.5021 | 8.204 | 12.3234 | 1.5021 | 8.204 | 13.6755 | 1.6669 | 8.204 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2027 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 3.4282 | 109 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 64.084 | 3.3785 | 18.9684 | 64.084 | 3.3785 | 18.9684 | 71.1152 | 3.7491 | 18.9684 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2027 | 314 | 314-13F | Tier-1 | Non-HFTD---6 | 3--3 | 0.47273 | 5 | 100% | 74.5408 | 76.13% | 23.46% | 0.4094% | 2.809 | 0 | 0 | 2.809 | 0 | 2.5562 | 0.46587 | 5.4868 | 2.5562 | 0.46587 | 5.4868 | 2.8366 | 0.51699 | 5.4868 | 3.768% | 0.019129 | 0.018182 | 3896.6601 | 485.4254 | 838.4338 | 2572.801 | 3945.1005 | 0 | 0 | 3945.1005 | 9.263e-05%
2027 | 80 | CB 80 | Tier-1 | Non-HFTD---7 | 3--3 | 5.2693 | 48 | 100% | 44.4535 | 89.11% | 0% | 10.89% | 1.9609 | 0 | 0 | 1.9609 | 0 | 1.7843 | 5.1929 | 0.34361 | 1.7843 | 5.1929 | 0.34361 | 1.9801 | 5.7627 | 0.34361 | 4.411% | 0.017052 | 0.016208 | 2606.9684 | 6.287 | 2311.46 | 289.2215 | 2621.7513 | 0 | 0 | 2621.7513 | 6.466e-05%
2027 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 1.6445 | 445 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 9.4057 | 1.6206 | 5.8037 | 9.4057 | 1.6206 | 5.8037 | 10.4377 | 1.7984 | 5.8037 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2027 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 5.2246 | 110 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 45.4442 | 5.1488 | 8.8261 | 45.4442 | 5.1488 | 8.8261 | 50.4303 | 5.7138 | 8.8261 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2027 | 57 | 57-1295F | Tier-1 | Non-HFTD---14 | 3--1 | 0.73143 | 22 | 100% | 5.7785 | 18.72% | 64.33% | 16.95% | 0.053541 | 0 | 0 | 0.053541 | 0 | 0.048722 | 0.72082 | 0.067592 | 0.048722 | 0.72082 | 0.067592 | 0.054067 | 0.79991 | 0.067592 | 0.9266% | 0.013816 | 0.013132 | 418.2342 | 0.34202 | 329.9664 | 87.9258 | 435.938 | 0 | 0 | 435.938 | 1.766e-06%
2027 | 1434 | CB 1434 | Tier-1 | Non-HFTD---13 | 2--2 | 2.2678 | 40 | 100% | 5.9882 | 73.95% | 0% | 26.05% | 0.21921 | 0 | 0 | 0.21921 | 0 | 0.19948 | 2.2349 | 0.089255 | 0.19948 | 2.2349 | 0.089255 | 0.22136 | 2.4801 | 0.089255 | 3.661% | 0.0060046 | 0.0057074 | 997.2619 | 1.3501 | 754.0153 | 241.8966 | 1010.7891 | 0 | 0 | 1010.7891 | 7.229e-06%
2027 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 1.9464 | 59 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.82784 | 1.9182 | 0.43158 | 0.82784 | 1.9182 | 0.43158 | 0.91867 | 2.1286 | 0.43158 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2027 | 548 | 548-17F | Tier-1 | Non-HFTD---4 | 2--4 | 2.5892 | 226 | 100% | 104.2118 | 98.1% | 0% | 1.901% | 5.0604 | 0 | 0 | 5.0604 | 0 | 4.6049 | 2.5517 | 1.8047 | 4.6049 | 2.5517 | 1.8047 | 5.1101 | 2.8316 | 1.8047 | 4.856% | 0.010934 | 0.010393 | 9530.6409 | 2004.1168 | 69.3119 | 7457.2122 | 9540.0775 | 0 | 0 | 9540.0775 | 0.0001669%
2027 | 254 | CB 254 | Tier-1 | Non-HFTD---17 | 1--2 | 0.16193 | 0 | 100% | 0.87557 | 85.54% | 0% | 14.46% | 0.037073 | 0 | 0 | 0.037073 | 0 | 0.033736 | 0.15958 | 0.2114 | 0.033736 | 0.15958 | 0.2114 | 0.037437 | 0.17709 | 0.2114 | 4.234% | 0.0005892 | 0.00056003 | 1486.0267 | 199.9018 | 58.8156 | 1227.3092 | 1497.2186 | 0 | 0 | 1497.2186 | 1.223e-06%
2027 | 58 | 58-756F | Tier-1 | Non-HFTD---11 | 2--2 | 0.3534 | 9 | 100% | 14.7362 | 1.289% | 96.53% | 2.184% | 0.009405 | 0 | 0 | 0.009405 | 0 | 0.0085584 | 0.34827 | 0.024574 | 0.0085584 | 0.34827 | 0.024574 | 0.0094974 | 0.38649 | 0.024574 | 0.06382% | 0.012057 | 0.01146 | 1222.212 | 3.1244 | 1076.1922 | 142.8953 | 1285.0415 | 0 | 0 | 1285.0415 | 3.101e-07%
2027 | 186 | 186-940R | Tier-1 | Non-HFTD---1 | 4--4 | 2.8176 | 388 | 100% | 708.016 | 27.23% | 72.48% | 0.2936% | 9.5427 | 0 | 0 | 9.5427 | 0 | 8.6838 | 2.7768 | 3.1273 | 8.6838 | 2.7768 | 3.1273 | 9.6365 | 3.0814 | 3.1273 | 1.348% | 0.051585 | 0.049032 | 13725.1247 | 759.9823 | 9159.4783 | 3805.6641 | 14245.2769 | 0 | 0 | 14245.2769 | 0.0003147%
2027 | 168 | 168-703F | Tier-1 | Non-HFTD---15 | 2--1 | 1.968 | 106 | 100% | 2.7691 | 40.41% | 0% | 59.59% | 0.055392 | 0 | 0 | 0.055392 | 0 | 0.050406 | 1.9395 | 0.02599 | 0.050406 | 1.9395 | 0.02599 | 0.055937 | 2.1523 | 0.02599 | 2% | 0.0058996 | 0.0056076 | 469.3702 | 3.0577 | 197.5515 | 268.7611 | 483.9359 | 0 | 0 | 483.9359 | 1.827e-06%
2027 | 57 | 57-1296F | Tier-1 | Non-HFTD---6 | 3--3 | 4.3852 | 419 | 100% | 54.2561 | 82.4% | 11.86% | 5.738% | 2.2131 | 0 | 0 | 2.2131 | 0 | 2.0139 | 4.3216 | 0.466 | 2.0139 | 4.3216 | 0.466 | 2.2348 | 4.7958 | 0.466 | 4.079% | 0.026297 | 0.024995 | 2063.1894 | 274.7024 | 258.9091 | 1529.5779 | 2082.0976 | 0 | 0 | 2082.0976 | 7.298e-05%
2027 | 190 | 190-1868R | Tier-1 | Non-HFTD---11 | 1--4 | 0.48108 | 19 | 100% | 12.0699 | 97.67% | 0% | 2.333% | 0.58352 | 0 | 0 | 0.58352 | 0 | 0.531 | 0.4741 | 1.12 | 0.531 | 0.4741 | 1.12 | 0.58926 | 0.52612 | 1.12 | 4.835% | 0.0015928 | 0.001514 | 7577.7716 | 422.4158 | 4765.8195 | 2389.5362 | 7586.9772 | 0 | 0 | 7586.9772 | 1.924e-05%
2027 | 1139 | CB 1139 | Tier-1 | Non-HFTD---17 | 1--3 | 0.21402 | 0 | 100% | 1.9809 | 88.52% | 0% | 11.48% | 0.086804 | 0 | 0 | 0.086804 | 0 | 0.07899 | 0.21091 | 0.37452 | 0.07899 | 0.21091 | 0.37452 | 0.087657 | 0.23405 | 0.37452 | 4.382% | 0.0008862 | 0.00084233 | 2235.3083 | 105.1437 | 1355.0151 | 775.1495 | 2248.667 | 0 | 0 | 2248.667 | 2.862e-06%
2027 | LA1 | CB LA1 | Tier-1 | Non-HFTD---12 | 4--1 | 10.8148 | 231 | 100% | 14.2144 | 47.91% | 0% | 52.09% | 0.33709 | 0 | 0 | 0.33709 | 0 | 0.30675 | 10.658 | 0.028781 | 0.30675 | 10.658 | 0.028781 | 0.34041 | 11.8273 | 0.028781 | 2.371% | 0.029769 | 0.028295 | 477.4907 | 3.6261 | 230.2568 | 243.6078 | 490.4441 | 0 | 0 | 490.4441 | 1.112e-05%
2027 | 417 | 417-44AE | Tier-1 | Non-HFTD---5 | 2--4 | 0.70607 | 9 | 100% | 68.544 | 0.1089% | 99.12% | 0.7728% | 0.0036964 | 0 | 0 | 0.0036964 | 0 | 0.0033637 | 0.69583 | 0.004834 | 0.0033637 | 0.69583 | 0.004834 | 0.0037327 | 0.77218 | 0.004834 | 0.005393% | 0.0129 | 0.012261 | 5313.5687 | 6.798 | 4793.3964 | 513.3743 | 5589.9865 | 0 | 0 | 5589.9865 | 1.219e-07%
2027 | 1077 | CB 1077 | Tier-1 | Non-HFTD---8 | 3--2 | 8.2547 | 281 | 100% | 27.171 | 78.66% | 0% | 21.34% | 1.058 | 0 | 0 | 1.058 | 0 | 0.96273 | 8.135 | 0.11834 | 0.96273 | 8.135 | 0.11834 | 1.0684 | 9.0276 | 0.11834 | 3.894% | 0.023107 | 0.021963 | 1175.8656 | 180.5721 | 140.8614 | 854.4321 | 1188.933 | 0 | 0 | 1188.933 | 3.489e-05%
2027 | 738 | CB 738 | Tier-1 | Non-HFTD---17 | 1--2 | 0.53655 | 33 | 100% | 2.031 | 77.55% | 0% | 22.45% | 0.077964 | 0 | 0 | 0.077964 | 0 | 0.070946 | 0.52877 | 0.13417 | 0.070946 | 0.52877 | 0.13417 | 0.07873 | 0.58679 | 0.13417 | 3.839% | 0.0021108 | 0.0020063 | 962.2085 | 113.8791 | 22.5007 | 825.8287 | 973.4589 | 0 | 0 | 973.4589 | 2.571e-06%
2027 | 578 | CB 578 | Tier-1 | Non-HFTD---3 | 3--4 | 4.9491 | 87 | 100% | 140.4916 | 12.05% | 84.92% | 3.035% | 0.83787 | 0 | 0 | 0.83787 | 0 | 0.76245 | 4.8773 | 0.15633 | 0.76245 | 4.8773 | 0.15633 | 0.8461 | 5.4124 | 0.15633 | 0.5964% | 0.025495 | 0.024233 | 5510.5967 | 5.2725 | 4912.3512 | 592.973 | 5763.0011 | 0 | 0 | 5763.0011 | 2.763e-05%
2027 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 22.2475 | 1918 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 461.194 | 21.9249 | 21.0352 | 461.194 | 21.9249 | 21.0352 | 511.7951 | 24.3305 | 21.0352 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2027 | BN2 | CB BN2 | Tier-1 | Non-HFTD---1 | 4--5 | 10.1083 | 520 | 100% | 1098.8312 | 99.36% | 0% | 0.6449% | 54.0413 | 0 | 0 | 54.0413 | 0 | 49.1769 | 9.9618 | 4.9366 | 49.1769 | 9.9618 | 4.9366 | 54.5725 | 11.0548 | 4.9366 | 4.918% | 0.034221 | 0.032527 | 32110.0379 | 7492.6936 | 90.1662 | 24527.178 | 32120.8227 | 0 | 0 | 32120.8227 | 0.001782%
2027 | 582 | CB 582 | Tier-1 | Non-HFTD---17 | 1--2 | 0.3354 | 8 | 100% | 1.2456 | 82.48% | 0% | 17.52% | 0.050855 | 0 | 0 | 0.050855 | 0 | 0.046277 | 0.33054 | 0.14001 | 0.046277 | 0.33054 | 0.14001 | 0.051355 | 0.3668 | 0.14001 | 4.083% | 0.0009004 | 0.00085583 | 1383.3541 | 0.23444 | 1162.7176 | 220.4021 | 1395.9743 | 0 | 0 | 1395.9743 | 1.677e-06%
2027 | 431 | 431-48AE | Tier-1 | Non-HFTD---18 | 1--1 | 1.1947 | 55 | 100% | 1.4033 | 31.02% | 0% | 68.98% | 0.021548 | 0 | 0 | 0.021548 | 0 | 0.019609 | 1.1774 | 0.016654 | 0.019609 | 1.1774 | 0.016654 | 0.02176 | 1.3066 | 0.016654 | 1.536% | 0.0035406 | 0.0033653 | 396.3532 | 0.23934 | 147.5741 | 248.5398 | 410.5915 | 0 | 0 | 410.5915 | 7.106e-07%
2027 | 595 | 595-1454F | Tier-2 | Tier-2---15 | 3--4 | 1.3606 | 113 | 100% | 124.9246 | 83.27% | 16% | 0.7306% | 5.1495 | 0 | 0 | 5.1495 | 0 | 4.6859 | 1.3409 | 3.4947 | 4.6859 | 1.3409 | 3.4947 | 5.2001 | 1.488 | 3.4947 | 4.122% | 0.018776 | 0.017847 | 6653.3471 | 1471.8841 | 978.4778 | 4202.9852 | 6711.3017 | 0 | 0 | 6711.3017 | 0.0001698%
2027 | UP2 | CB UP2 | Tier-1 | Non-HFTD---12 | 3--2 | 6.268 | 169 | 100% | 9.6733 | 51.85% | 0% | 48.15% | 0.24825 | 0 | 0 | 0.24825 | 0 | 0.22591 | 6.1771 | 0.036572 | 0.22591 | 6.1771 | 0.036572 | 0.25069 | 6.8548 | 0.036572 | 2.566% | 0.018016 | 0.017125 | 536.9147 | 0.19455 | 301.8547 | 234.8654 | 550.3792 | 0 | 0 | 550.3792 | 8.186e-06%
2027 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 5.4881 | 1424 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 66.4558 | 5.4085 | 12.2873 | 66.4558 | 5.4085 | 12.2873 | 73.7472 | 6.0019 | 12.2873 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2027 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 7.564 | 793 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 91.6277 | 7.4543 | 12.2919 | 91.6277 | 7.4543 | 12.2919 | 101.6809 | 8.2722 | 12.2919 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2027 | 39 | CB 39 | Tier-1 | Non-HFTD---19 | 1--1 | 0.092003 | 0 | 100% | 0.12086 | 14.55% | 0% | 85.45% | 0.00087056 | 0 | 0 | 0.00087056 | 0 | 0.00079219 | 0.090669 | 0.0087372 | 0.00079219 | 0.090669 | 0.0087372 | 0.00087911 | 0.10062 | 0.0087372 | 0.7203% | 0.000339 | 0.00032222 | 356.5086 | 8.0102 | 30.562 | 317.9364 | 372.373 | 0 | 0 | 372.373 | 2.871e-08%
2027 | 313 | 313-548AE | Tier-1 | Non-HFTD---12 | 3--2 | 0.1225 | 4 | 100% | 14.2935 | 9.237% | 90.04% | 0.7189% | 0.065357 | 0 | 0 | 0.065357 | 0 | 0.059474 | 0.12072 | 0.49266 | 0.059474 | 0.12072 | 0.49266 | 0.066 | 0.13397 | 0.49266 | 0.4573% | 0.017367 | 0.016507 | 823.0292 | 13.4104 | 588.2213 | 221.3976 | 861.9315 | 0 | 0 | 861.9315 | 2.155e-06%
2027 | 366 | 366-48 | Tier-1 | Non-HFTD---5 | 3--4 | 2.5229 | 51 | 100% | 85.178 | 1.803% | 95.42% | 2.781% | 0.076004 | 0 | 0 | 0.076004 | 0 | 0.069163 | 2.4863 | 0.027818 | 0.069163 | 2.4863 | 0.027818 | 0.076751 | 2.7591 | 0.027818 | 0.08923% | 0.013571 | 0.012899 | 6276.6562 | 7.3618 | 5560.2911 | 709.0033 | 6597.6387 | 0 | 0 | 6597.6387 | 2.506e-06%
2027 | 1140 | CB 1140 | Tier-1 | Non-HFTD---2 | 4--4 | 0.29399 | 56 | 100% | 668.0984 | 0.02919% | 99.94% | 0.02644% | 0.0096542 | 0 | 0 | 0.0096542 | 0 | 0.0087852 | 0.28973 | 0.030323 | 0.0087852 | 0.28973 | 0.030323 | 0.0097491 | 0.32151 | 0.030323 | 0.001445% | 0.087146 | 0.082832 | 7666.4439 | 10.8548 | 7025.307 | 630.2821 | 8065.5793 | 0 | 0 | 8065.5793 | 3.184e-07%
2027 | 35 | 35-297AE | Tier-1 | Non-HFTD---11 | 2--2 | 0.30568 | 35 | 100% | 10.2793 | 20.26% | 76.41% | 3.337% | 0.10307 | 0 | 0 | 0.10307 | 0 | 0.093791 | 0.30125 | 0.31134 | 0.093791 | 0.30125 | 0.31134 | 0.10408 | 0.3343 | 0.31134 | 1.003% | 0.0071058 | 0.0067541 | 1446.6053 | 46.2284 | 897.7038 | 502.6731 | 1506.6811 | 0 | 0 | 1506.6811 | 3.399e-06%
2027 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 2.4038 | 65 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 65.3245 | 2.3689 | 27.5755 | 65.3245 | 2.3689 | 27.5755 | 72.4917 | 2.6288 | 27.5755 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2027 | 208 | CB 208 | Tier-1 | Non-HFTD---13 | 1--3 | 0.50053 | 7 | 100% | 7.9912 | 93.78% | 0% | 6.225% | 0.37094 | 0 | 0 | 0.37094 | 0 | 0.33755 | 0.49328 | 0.6843 | 0.33755 | 0.49328 | 0.6843 | 0.37459 | 0.5474 | 0.6843 | 4.642% | 0.0017112 | 0.0016265 | 4669.9217 | 68.1319 | 3989.8459 | 611.9439 | 4685.0604 | 0 | 0 | 4685.0604 | 1.223e-05%
2027 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 4.6394 | 937 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 204.9832 | 4.5722 | 44.8328 | 204.9832 | 4.5722 | 44.8328 | 227.4734 | 5.0738 | 44.8328 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2027 | 171 | 171-568 | Tier-1 | Non-HFTD---8 | 4--2 | 1.7236 | 45 | 100% | 31.0781 | 60.02% | 35.24% | 4.741% | 0.92333 | 0 | 0 | 0.92333 | 0 | 0.84022 | 1.6986 | 0.49464 | 0.84022 | 1.6986 | 0.49464 | 0.93241 | 1.885 | 0.49464 | 2.971% | 0.032551 | 0.03094 | 954.7509 | 88.4522 | 317.464 | 548.8347 | 974.6293 | 0 | 0 | 974.6293 | 3.045e-05%
2027 | 581 | 581-49 | Tier-1 | Non-HFTD---9 | 2--3 | 2.7263 | 67 | 100% | 15.9576 | 84.86% | 0% | 15.14% | 0.67032 | 0 | 0 | 0.67032 | 0 | 0.60999 | 2.6868 | 0.22703 | 0.60999 | 2.6868 | 0.22703 | 0.67691 | 2.9816 | 0.22703 | 4.201% | 0.0089802 | 0.0085357 | 1776.972 | 49.0609 | 1234.3778 | 493.5333 | 1790.9809 | 0 | 0 | 1790.9809 | 2.21e-05%
2027 | 156 | 156-529AE | Tier-1 | Non-HFTD---18 | 2--1 | 1.9048 | 13 | 100% | 2.0617 | 40.76% | 0% | 59.24% | 0.041597 | 0 | 0 | 0.041597 | 0 | 0.037852 | 1.8772 | 0.020165 | 0.037852 | 1.8772 | 0.020165 | 0.042006 | 2.0831 | 0.020165 | 2.018% | 0.0054304 | 0.0051616 | 379.6623 | 1.8858 | 164.6049 | 213.1716 | 391.3754 | 0 | 0 | 391.3754 | 1.372e-06%
2027 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 6.3664 | 344 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 152.4366 | 6.2741 | 24.296 | 152.4366 | 6.2741 | 24.296 | 169.1616 | 6.9625 | 24.296 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2027 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 5.1765 | 273 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 123.7039 | 5.1015 | 24.2487 | 123.7039 | 5.1015 | 24.2487 | 137.2764 | 5.6612 | 24.2487 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2027 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.64526 | 41 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.5839 | 0.6359 | 8.781 | 5.5839 | 0.6359 | 8.781 | 6.1965 | 0.70567 | 8.781 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2027 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 0.68764 | 56 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.47188 | 0.67767 | 0.69633 | 0.47188 | 0.67767 | 0.69633 | 0.52366 | 0.75202 | 0.69633 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2027 | 900 | 900-1118F | Tier-1 | Non-HFTD---15 | 1--3 | 0.4102 | 22 | 100% | 3.8209 | 95.13% | 0% | 4.872% | 0.17992 | 0 | 0 | 0.17992 | 0 | 0.16372 | 0.40425 | 0.405 | 0.16372 | 0.40425 | 0.405 | 0.18169 | 0.4486 | 0.405 | 4.709% | 0.0011032 | 0.0010486 | 3463.4496 | 535.7058 | 23.7271 | 2904.0167 | 3472.2375 | 0 | 0 | 3472.2375 | 5.933e-06%
2027 | CG1 | CB CG1 | Tier-1 | Non-HFTD---1 | 4--4 | 8.3125 | 886 | 100% | 278.5213 | 94.12% | 3.851% | 2.028% | 12.9764 | 0 | 0 | 12.9764 | 0 | 11.8083 | 8.192 | 1.4414 | 11.8083 | 8.192 | 1.4414 | 13.1039 | 9.0908 | 1.4414 | 4.659% | 0.029972 | 0.028488 | 9292.8406 | 1535.1687 | 384.8682 | 7372.8037 | 9321.2885 | 0 | 0 | 9321.2885 | 0.0004279%
2027 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 11.8649 | 1839 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 218.2996 | 11.6929 | 18.6694 | 218.2996 | 11.6929 | 18.6694 | 242.251 | 12.9758 | 18.6694 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2027 | 143 | 143-147F | Tier-1 | Non-HFTD---9 | 2--3 | 0.3229 | 0 | 100% | 25.6591 | 1.387% | 97.22% | 1.391% | 0.017616 | 0 | 0 | 0.017616 | 0 | 0.01603 | 0.31822 | 0.050374 | 0.01603 | 0.31822 | 0.050374 | 0.017789 | 0.35314 | 0.050374 | 0.06865% | 0.0072518 | 0.0068928 | 3538.3122 | 10.6062 | 3051.6105 | 476.0955 | 3720.0242 | 0 | 0 | 3720.0242 | 5.809e-07%
2027 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 4.8509 | 338 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 84.3793 | 4.7806 | 17.6503 | 84.3793 | 4.7806 | 17.6503 | 93.6372 | 5.3051 | 17.6503 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2027 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 8.4771 | 468 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 627.3269 | 8.3542 | 75.0911 | 627.3269 | 8.3542 | 75.0911 | 696.1557 | 9.2708 | 75.0911 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2027 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 5.4265 | 797 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 523.5501 | 5.3478 | 97.8998 | 523.5501 | 5.3478 | 97.8998 | 580.9928 | 5.9346 | 97.8998 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2027 | 946 | CB 946 | Tier-1 | Non-HFTD---10 | 3--2 | 9.2432 | 373 | 100% | 21.7172 | 73.55% | 0% | 26.45% | 0.79062 | 0 | 0 | 0.79062 | 0 | 0.71945 | 9.1092 | 0.078981 | 0.71945 | 9.1092 | 0.078981 | 0.79839 | 10.1086 | 0.078981 | 3.641% | 0.025949 | 0.024665 | 836.9106 | 3.7986 | 613.2175 | 219.8946 | 848.4404 | 0 | 0 | 848.4404 | 2.607e-05%
2027 | 515 | CB 515 | Tier-1 | Non-HFTD---14 | 2--2 | 3.1625 | 51 | 100% | 7.211 | 59.11% | 0% | 40.89% | 0.21099 | 0 | 0 | 0.21099 | 0 | 0.192 | 3.1167 | 0.061604 | 0.192 | 3.1167 | 0.061604 | 0.21307 | 3.4586 | 0.061604 | 2.926% | 0.011304 | 0.010745 | 637.9041 | 25.5438 | 265.137 | 347.2233 | 651.4877 | 0 | 0 | 651.4877 | 6.958e-06%
2027 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 13.6103 | 643 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 110.0696 | 13.4129 | 8.2062 | 110.0696 | 13.4129 | 8.2062 | 122.1462 | 14.8846 | 8.2062 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2027 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 12.5093 | 872 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 389.967 | 12.3279 | 31.6328 | 389.967 | 12.3279 | 31.6328 | 432.7533 | 13.6805 | 31.6328 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2027 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 6.6053 | 288 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 174.6571 | 6.5096 | 26.8309 | 174.6571 | 6.5096 | 26.8309 | 193.82 | 7.2238 | 26.8309 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2027 | 481 | CB 481 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8417 | 224 | 100% | 2.6593 | 32.47% | 0% | 67.53% | 0.042738 | 0 | 0 | 0.042738 | 0 | 0.038891 | 2.8005 | 0.013887 | 0.038891 | 2.8005 | 0.013887 | 0.043158 | 3.1077 | 0.013887 | 1.607% | 0.0074788 | 0.0071086 | 355.573 | 8.8932 | 83.5025 | 263.1773 | 368.0784 | 0 | 0 | 368.0784 | 1.409e-06%
2027 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 6.3644 | 324 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 266.0239 | 6.2721 | 42.414 | 266.0239 | 6.2721 | 42.414 | 295.2114 | 6.9602 | 42.414 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2027 | 58 | 58-522 | Tier-1 | Non-HFTD---8 | 2--3 | 0.66855 | 23 | 100% | 27.7406 | 11.51% | 86.26% | 2.232% | 0.15806 | 0 | 0 | 0.15806 | 0 | 0.14383 | 0.65886 | 0.2183 | 0.14383 | 0.65886 | 0.2183 | 0.15961 | 0.73114 | 0.2183 | 0.5698% | 0.012983 | 0.01234 | 2136.6878 | 9.4433 | 1891.1628 | 236.0817 | 2235.1536 | 0 | 0 | 2235.1536 | 5.212e-06%
2027 | 85 | CB 85 | Tier-1 | Non-HFTD---6 | 3--3 | 6.3067 | 296 | 100% | 49.3225 | 92.1% | 0% | 7.898% | 2.2486 | 0 | 0 | 2.2486 | 0 | 2.0462 | 6.2152 | 0.32923 | 2.0462 | 6.2152 | 0.32923 | 2.2707 | 6.8971 | 0.32923 | 4.559% | 0.02128 | 0.020227 | 2317.7858 | 252.1431 | 971.833 | 1093.8096 | 2327.3193 | 0 | 0 | 2327.3193 | 7.415e-05%
2027 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 13.604 | 899 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 821.8107 | 13.4068 | 61.2982 | 821.8107 | 13.4068 | 61.2982 | 911.9778 | 14.8777 | 61.2982 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2027 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 20.4475 | 1782 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 124.6006 | 20.1511 | 6.1833 | 124.6006 | 20.1511 | 6.1833 | 138.2715 | 22.362 | 6.1833 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2027 | 130 | 130-14F | Tier-1 | Non-HFTD---17 | 1--1 | 0.84125 | 47 | 100% | 1.0142 | 40.98% | 0% | 59.02% | 0.020571 | 0 | 0 | 0.020571 | 0 | 0.018719 | 0.82905 | 0.022579 | 0.018719 | 0.82905 | 0.022579 | 0.020773 | 0.92001 | 0.022579 | 2.028% | 0.002514 | 0.0023896 | 403.4011 | 3.3646 | 167.0213 | 233.0153 | 415.8008 | 0 | 0 | 415.8008 | 6.783e-07%
2027 | 361 | CB 361 | Tier-1 | Non-HFTD---5 | 2--4 | 1.65 | 12 | 100% | 72.0528 | 3.654% | 93.91% | 2.433% | 0.13032 | 0 | 0 | 0.13032 | 0 | 0.11859 | 1.6261 | 0.072929 | 0.11859 | 1.6261 | 0.072929 | 0.1316 | 1.8045 | 0.072929 | 0.1809% | 0.010387 | 0.0098725 | 6937.0919 | 7.1268 | 6176.303 | 753.6622 | 7285.1607 | 0 | 0 | 7285.1607 | 4.297e-06%
2027 | 310 | 310-719F | Tier-1 | Non-HFTD---3 | 3--4 | 3.2121 | 143 | 100% | 124.5147 | 2.263% | 95.99% | 1.745% | 0.13948 | 0 | 0 | 0.13948 | 0 | 0.12693 | 3.1656 | 0.040097 | 0.12693 | 3.1656 | 0.040097 | 0.14085 | 3.5129 | 0.040097 | 0.112% | 0.025632 | 0.024363 | 4857.7828 | 6.9446 | 4370.4656 | 480.3726 | 5105.0406 | 0 | 0 | 5105.0406 | 4.6e-06%
2027 | 1283 | CB 1283 | Tier-1 | Non-HFTD---15 | 1--3 | 0.69583 | 17 | 100% | 4.6015 | 87.53% | 0% | 12.47% | 0.19938 | 0 | 0 | 0.19938 | 0 | 0.18143 | 0.68574 | 0.26457 | 0.18143 | 0.68574 | 0.26457 | 0.20134 | 0.76098 | 0.26457 | 4.333% | 0.002425 | 0.002305 | 1897.5339 | 258.5117 | 88.6838 | 1550.3385 | 1909.8545 | 0 | 0 | 1909.8545 | 6.575e-06%
2027 | 518 | CB 518 | Tier-1 | Non-HFTD---11 | 2--3 | 2.5012 | 35 | 100% | 15.0618 | 85.82% | 0% | 14.18% | 0.63981 | 0 | 0 | 0.63981 | 0 | 0.58221 | 2.4649 | 0.2362 | 0.58221 | 2.4649 | 0.2362 | 0.64609 | 2.7353 | 0.2362 | 4.248% | 0.008289 | 0.0078787 | 1817.08 | 17.4829 | 1476.3748 | 323.2224 | 1830.5026 | 0 | 0 | 1830.5026 | 2.11e-05%
2027 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 15.4477 | 850 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1659.3701 | 15.2238 | 108.9986 | 1659.3701 | 15.2238 | 108.9986 | 1841.4323 | 16.8941 | 108.9986 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2027 | 76 | CB 76 | Tier-1 | Non-HFTD---17 | 1--2 | 0.68485 | 11 | 100% | 2.0654 | 56.67% | 0% | 43.33% | 0.057942 | 0 | 0 | 0.057942 | 0 | 0.052727 | 0.67492 | 0.078122 | 0.052727 | 0.67492 | 0.078122 | 0.058512 | 0.74897 | 0.078122 | 2.805% | 0.0027636 | 0.0026268 | 747.3661 | 2.0048 | 442.1787 | 303.1826 | 764.2293 | 0 | 0 | 764.2293 | 1.911e-06%
2027 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 31.9017 | 2321 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 380.2129 | 31.4391 | 12.0936 | 380.2129 | 31.4391 | 12.0936 | 421.929 | 34.8885 | 12.0936 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2027 | 169 | CB 169 | Tier-1 | Non-HFTD---19 | 1--2 | 0.17503 | 9 | 100% | 0.4733 | 37.59% | 0% | 62.41% | 0.008807 | 0 | 0 | 0.008807 | 0 | 0.0080143 | 0.17249 | 0.046461 | 0.0080143 | 0.17249 | 0.046461 | 0.0088936 | 0.19142 | 0.046461 | 1.861% | 0.0007436 | 0.00070679 | 636.5041 | 14.2067 | 190.1326 | 432.1648 | 657.1913 | 0 | 0 | 657.1913 | 2.904e-07%
2027 | 415 | 415-33 | Tier-1 | Non-HFTD---3 | 4--3 | 9.518 | 398 | 100% | 139.7786 | 20.17% | 75.04% | 4.79% | 1.3955 | 0 | 0 | 1.3955 | 0 | 1.2699 | 9.38 | 0.13538 | 1.2699 | 9.38 | 0.13538 | 1.4092 | 10.4092 | 0.13538 | 0.9983% | 0.039288 | 0.037343 | 3557.7759 | 167.3493 | 2542.2057 | 848.2208 | 3705.6889 | 0 | 0 | 3705.6889 | 4.602e-05%
2027 | QN1 | CB QN1 | Tier-1 | Non-HFTD---12 | 2--2 | 2.5479 | 232 | 100% | 9.4771 | 20.58% | 60.74% | 18.68% | 0.096528 | 0 | 0 | 0.096528 | 0 | 0.08784 | 2.511 | 0.034982 | 0.08784 | 2.511 | 0.034982 | 0.097477 | 2.7865 | 0.034982 | 1.019% | 0.01229 | 0.011681 | 771.15 | 21.6223 | 474.8473 | 274.6805 | 803.0463 | 0 | 0 | 803.0463 | 3.183e-06%
2027 | 535 | CB 535 | Tier-2 | Tier-2---16 | 4--3 | 0.31174 | 0 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25308 | 0 | 0 | 0.25308 | 0 | 0.2303 | 0.30722 | 0.74961 | 0.2303 | 0.30722 | 0.74961 | 0.25556 | 0.34093 | 0.74961 | 0.227% | 0.059698 | 0.056743 | 1867.7052 | 14.9488 | 1426.0626 | 426.6938 | 1960.5113 | 0 | 0 | 1960.5113 | 8.346e-06%
2027 | 72 | 72-16 | Tier-1 | Non-HFTD---14 | 2--1 | 4.3345 | 108 | 100% | 6.3445 | 45.63% | 0% | 54.37% | 0.1433 | 0 | 0 | 0.1433 | 0 | 0.1304 | 4.2716 | 0.030527 | 0.1304 | 4.2716 | 0.030527 | 0.14471 | 4.7403 | 0.030527 | 2.259% | 0.012945 | 0.012305 | 490.0991 | 5.3198 | 229.2157 | 255.5636 | 503.9765 | 0 | 0 | 503.9765 | 4.725e-06%
2027 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 11.0435 | 650 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 58.3163 | 10.8834 | 5.3583 | 58.3163 | 10.8834 | 5.3583 | 64.7147 | 12.0775 | 5.3583 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2027 | 197 | 197-1157F | Tier-2 | Tier-2---18 | 3--3 | 0.44794 | 76 | 100% | 63.1655 | 1.305% | 98.13% | 0.5601% | 0.040803 | 0 | 0 | 0.040803 | 0 | 0.03713 | 0.44145 | 0.08411 | 0.03713 | 0.44145 | 0.08411 | 0.041204 | 0.48988 | 0.08411 | 0.0646% | 0.01787 | 0.016985 | 3534.7635 | 11.6765 | 2974.4275 | 548.6595 | 3716.4442 | 0 | 0 | 3716.4442 | 1.346e-06%
2027 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 11.3506 | 1480 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 282.7746 | 11.186 | 25.2793 | 282.7746 | 11.186 | 25.2793 | 313.7999 | 12.4133 | 25.2793 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2027 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 6.2962 | 610 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 332.7936 | 6.2049 | 53.6337 | 332.7936 | 6.2049 | 53.6337 | 369.307 | 6.8857 | 53.6337 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2027 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.99152 | 180 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 79.5582 | 0.97714 | 81.4193 | 79.5582 | 0.97714 | 81.4193 | 88.2871 | 1.0844 | 81.4193 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2027 | 298 | 298-384 | Tier-1 | Non-HFTD---19 | 1--2 | 0.022348 | 0 | 100% | 0.1467 | 75.48% | 0% | 24.52% | 0.0054809 | 0 | 0 | 0.0054809 | 0 | 0.0049875 | 0.022024 | 0.22645 | 0.0049875 | 0.022024 | 0.22645 | 0.0055348 | 0.024441 | 0.22645 | 3.736% | 0.0001034 | 9.8282e-05 | 1418.7583 | 113.2285 | 410.6318 | 894.898 | 1436.8769 | 0 | 0 | 1436.8769 | 1.807e-07%
2027 | 728 | 728-1570F | Tier-2 | Tier-2---19 | 1--5 | 0.074417 | 14 | 100% | 33.2807 | 99.79% | 0% | 0.2133% | 1.6439 | 0 | 0 | 1.6439 | 0 | 1.4959 | 0.073338 | 20.3976 | 1.4959 | 0.073338 | 20.3976 | 1.66 | 0.081384 | 20.3976 | 4.939% | 0.0003472 | 0.00033001 | 95854.6419 | 22304.1965 | 20.1049 | 73530.3404 | 95865.2904 | 0 | 0 | 95865.2904 | 5.421e-05%
2027 | 176 | CB 176 | Tier-1 | Non-HFTD---10 | 4--1 | 0.063306 | 6 | 100% | 15.5544 | 4.631% | 94.88% | 0.4893% | 0.035657 | 0 | 0 | 0.035657 | 0 | 0.032448 | 0.062388 | 0.52009 | 0.032448 | 0.062388 | 0.52009 | 0.036008 | 0.069233 | 0.52009 | 0.2292% | 0.032585 | 0.030972 | 477.3549 | 3.466 | 417.7975 | 56.0913 | 501.0632 | 0 | 0 | 501.0632 | 1.176e-06%
2027 | 44 | CB 44 | Tier-1 | Non-HFTD---9 | 3--2 | 5.4639 | 138 | 100% | 25.8658 | 84.4% | 0% | 15.6% | 1.0806 | 0 | 0 | 1.0806 | 0 | 0.98334 | 5.3847 | 0.18262 | 0.98334 | 5.3847 | 0.18262 | 1.0912 | 5.9754 | 0.18262 | 4.178% | 0.016291 | 0.015485 | 1587.7136 | 11.2067 | 1294.5636 | 281.9434 | 1600.6131 | 0 | 0 | 1600.6131 | 3.563e-05%
2027 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.31499 | 10 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 7.325 | 0.31043 | 23.5965 | 7.325 | 0.31043 | 23.5965 | 8.1287 | 0.34449 | 23.5965 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2027 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 12.7815 | 1624 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1209.3579 | 12.5962 | 96.01 | 1209.3579 | 12.5962 | 96.01 | 1342.0458 | 13.9782 | 96.01 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2027 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 5.0748 | 159 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 175.5102 | 5.0012 | 35.0936 | 175.5102 | 5.0012 | 35.0936 | 194.7668 | 5.5499 | 35.0936 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2027 | 759 | CB 759 | Tier-1 | Non-HFTD---11 | 2--2 | 3.6532 | 193 | 100% | 13.6768 | 80.97% | 0% | 19.03% | 0.5482 | 0 | 0 | 0.5482 | 0 | 0.49885 | 3.6002 | 0.13856 | 0.49885 | 3.6002 | 0.13856 | 0.55358 | 3.9952 | 0.13856 | 4.008% | 0.010883 | 0.010344 | 1256.7154 | 15.5947 | 944.7873 | 296.3334 | 1269.1674 | 0 | 0 | 1269.1674 | 1.808e-05%
2027 | 325 | 325-1227F | Tier-1 | Non-HFTD---13 | 1--4 | 0.24205 | 4 | 100% | 7.4492 | 97.14% | 0% | 2.857% | 0.3582 | 0 | 0 | 0.3582 | 0 | 0.32596 | 0.23854 | 1.3665 | 0.32596 | 0.23854 | 1.3665 | 0.36172 | 0.26471 | 1.3665 | 4.809% | 0.000908 | 0.00086305 | 8203.9485 | 1304.1799 | 23.899 | 6875.8695 | 8216.1539 | 0 | 0 | 8216.1539 | 1.181e-05%
2027 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 6.2051 | 618 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.84502 | 6.1151 | 0.13818 | 0.84502 | 6.1151 | 0.13818 | 0.93773 | 6.7861 | 0.13818 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2027 | 794 | 794-1002 | Tier-1 | Non-HFTD---4 | 3--4 | 1.1659 | 43 | 100% | 176.6639 | 5.845% | 93.67% | 0.4796% | 0.51118 | 0 | 0 | 0.51118 | 0 | 0.46517 | 1.149 | 0.40486 | 0.46517 | 1.149 | 0.40486 | 0.5162 | 1.275 | 0.40486 | 0.2894% | 0.021091 | 0.020047 | 8376.1891 | 42.6247 | 7445.0358 | 888.5286 | 8786.9043 | 0 | 0 | 8786.9043 | 1.686e-05%
2027 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 10.0271 | 878 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 28.4591 | 9.8817 | 2.88 | 28.4591 | 9.8817 | 2.88 | 31.5815 | 10.9659 | 2.88 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2027 | 795 | CB 795 | Tier-1 | Non-HFTD---12 | 3--2 | 0.64564 | 34 | 100% | 12.7544 | 93.94% | 1.477% | 4.587% | 0.59306 | 0 | 0 | 0.59306 | 0 | 0.53967 | 0.63628 | 0.84817 | 0.53967 | 0.63628 | 0.84817 | 0.59889 | 0.70609 | 0.84817 | 4.65% | 0.020541 | 0.019524 | 620.9301 | 28.9913 | 416.0915 | 175.8474 | 622.891 | 0 | 0 | 622.891 | 1.956e-05%
2027 | 74 | 74-35R | Tier-1 | Non-HFTD---5 | 2--4 | 1.7629 | 93 | 100% | 50.9295 | 97.64% | 0% | 2.355% | 2.4616 | 0 | 0 | 2.4616 | 0 | 2.2401 | 1.7373 | 1.2894 | 2.2401 | 1.7373 | 1.2894 | 2.4858 | 1.9279 | 1.2894 | 4.833% | 0.0071104 | 0.0067584 | 7162.6834 | 1136.9423 | 64.4037 | 5961.3374 | 7171.4683 | 0 | 0 | 7171.4683 | 8.118e-05%
2027 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.43141 | 4 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 5.1675 | 0.42516 | 12.1544 | 5.1675 | 0.42516 | 12.1544 | 5.7345 | 0.47181 | 12.1544 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2027 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.44811 | 21 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.6527 | 0.44161 | 10.5357 | 4.6527 | 0.44161 | 10.5357 | 5.1631 | 0.49006 | 10.5357 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2027 | 322 | 322-821F | Tier-1 | Non-HFTD---10 | 4--2 | 12.5641 | 239 | 100% | 18.5107 | 56.59% | 0% | 43.41% | 0.51854 | 0 | 0 | 0.51854 | 0 | 0.47187 | 12.3819 | 0.038109 | 0.47187 | 12.3819 | 0.038109 | 0.52364 | 13.7404 | 0.038109 | 2.801% | 0.033072 | 0.031435 | 559.7082 | 23.5182 | 196.1441 | 340.0459 | 572.3609 | 0 | 0 | 572.3609 | 1.71e-05%
2027 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 4.2677 | 342 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 57.4893 | 4.2058 | 13.6691 | 57.4893 | 4.2058 | 13.6691 | 63.7969 | 4.6672 | 13.6691 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2027 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 14.6288 | 344 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 38.5732 | 14.4167 | 2.6756 | 38.5732 | 14.4167 | 2.6756 | 42.8054 | 15.9984 | 2.6756 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2027 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 0.11231 | 26 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.15554 | 0.11068 | 1.4053 | 0.15554 | 0.11068 | 1.4053 | 0.1726 | 0.12283 | 1.4053 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2027 | 546 | 546-12 | Tier-1 | Non-HFTD---11 | 2--2 | 0.83025 | 13 | 100% | 14.4143 | 0.3875% | 96.68% | 2.928% | 0.0027652 | 0 | 0 | 0.0027652 | 0 | 0.0025163 | 0.81822 | 0.0030753 | 0.0025163 | 0.81822 | 0.0030753 | 0.0027924 | 0.90799 | 0.0030753 | 0.01918% | 0.01256 | 0.011939 | 1147.5972 | 1.952 | 997.2808 | 148.3644 | 1207.13 | 0 | 0 | 1207.13 | 9.119e-08%
2027 | 266 | 266-485F | Tier-2 | Tier-2---21 | 1--4 | 0.18886 | 56 | 100% | 3.9025 | 97.35% | 0% | 2.654% | 0.18805 | 0 | 0 | 0.18805 | 0 | 0.17112 | 0.18612 | 0.91943 | 0.17112 | 0.18612 | 0.91943 | 0.1899 | 0.20654 | 0.91943 | 4.819% | 0.000646 | 0.00061402 | 6041.0896 | 954.7948 | 18.9693 | 5067.3254 | 6049.4401 | 0 | 0 | 6049.4401 | 6.201e-06%
2027 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 12.6949 | 1154 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 304.1512 | 12.5109 | 24.311 | 304.1512 | 12.5109 | 24.311 | 337.522 | 13.8835 | 24.311 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2027 | 859 | CB 859 | Tier-1 | Non-HFTD---13 | 1--4 | 0.2674 | 5 | 100% | 6.3536 | 96.15% | 0% | 3.853% | 0.30239 | 0 | 0 | 0.30239 | 0 | 0.27517 | 0.26352 | 1.0442 | 0.27517 | 0.26352 | 1.0442 | 0.30536 | 0.29244 | 1.0442 | 4.759% | 0.0009722 | 0.00092408 | 6535.3261 | 323.1257 | 4329.0086 | 1883.1918 | 6548.4396 | 0 | 0 | 6548.4396 | 9.972e-06%
2027 | 376 | 376-491R | Tier-1 | Non-HFTD---10 | 2--2 | 4.3338 | 110 | 100% | 15.387 | 85.15% | 0% | 14.85% | 0.64853 | 0 | 0 | 0.64853 | 0 | 0.59015 | 4.2709 | 0.13818 | 0.59015 | 4.2709 | 0.13818 | 0.6549 | 4.7395 | 0.13818 | 4.215% | 0.011779 | 0.011196 | 1306.2651 | 20.6652 | 1016.2338 | 269.3662 | 1316.3691 | 0 | 0 | 1316.3691 | 2.139e-05%
2027 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.052462 | 7 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.2076 | 0.051701 | 62.0412 | 3.2076 | 0.051701 | 62.0412 | 3.5596 | 0.057374 | 62.0412 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2027 | 310 | 310-718F | Tier-1 | Non-HFTD---17 | 1--3 | 0.087462 | 0 | 100% | 0.81802 | 90.7% | 0% | 9.303% | 0.036725 | 0 | 0 | 0.036725 | 0 | 0.033419 | 0.086194 | 0.38772 | 0.033419 | 0.086194 | 0.38772 | 0.037086 | 0.095651 | 0.38772 | 4.49% | 0.000254 | 0.00024143 | 3220.5537 | 0.90818 | 2943.8401 | 275.8054 | 3236.1564 | 0 | 0 | 3236.1564 | 1.211e-06%
2027 | 548 | 548-15F | Tier-1 | Non-HFTD---11 | 2--3 | 1.8856 | 63 | 100% | 14.762 | 91.23% | 0% | 8.768% | 0.66665 | 0 | 0 | 0.66665 | 0 | 0.60664 | 1.8583 | 0.32645 | 0.60664 | 1.8583 | 0.32645 | 0.6732 | 2.0622 | 0.32645 | 4.516% | 0.005445 | 0.0051755 | 2711.1073 | 395.5509 | 80.5547 | 2235.0017 | 2723.487 | 0 | 0 | 2723.487 | 2.198e-05%
2027 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 3.6661 | 275 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 226.5547 | 3.6129 | 62.7064 | 226.5547 | 3.6129 | 62.7064 | 251.4117 | 4.0093 | 62.7064 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2027 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 11.4998 | 62 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 61.4752 | 11.333 | 5.4244 | 61.4752 | 11.333 | 5.4244 | 68.2202 | 12.5765 | 5.4244 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2027 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 0.92708 | 47 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.1149 | 0.91364 | 0.12576 | 0.1149 | 0.91364 | 0.12576 | 0.1275 | 1.0139 | 0.12576 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2027 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.87727 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 65.4805 | 0.86455 | 75.7391 | 65.4805 | 0.86455 | 75.7391 | 72.6648 | 0.95941 | 75.7391 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2027 | 1406 | 1406-19F | Tier-1 | Non-HFTD---11 | 3--2 | 5.6559 | 78 | 100% | 15.0674 | 83.86% | 0% | 16.14% | 0.62542 | 0 | 0 | 0.62542 | 0 | 0.56913 | 5.5739 | 0.10211 | 0.56913 | 5.5739 | 0.10211 | 0.63157 | 6.1854 | 0.10211 | 4.151% | 0.013569 | 0.012898 | 1110.3933 | 84.7049 | 427.6552 | 598.0332 | 1119.7291 | 0 | 0 | 1119.7291 | 2.062e-05%
2027 | BT1 | CB BT1 | Tier-1 | Non-HFTD---17 | 1--1 | 1.1276 | 81 | 100% | 1.503 | 53.13% | 0% | 46.87% | 0.03953 | 0 | 0 | 0.03953 | 0 | 0.035972 | 1.1113 | 0.032371 | 0.035972 | 1.1113 | 0.032371 | 0.039919 | 1.2332 | 0.032371 | 2.63% | 0.0030182 | 0.0028688 | 497.9935 | 40.6456 | 38.8309 | 418.5169 | 510.1485 | 0 | 0 | 510.1485 | 1.304e-06%
2027 | 509 | CB 509 | Tier-1 | Non-HFTD---10 | 3--2 | 10.0667 | 447 | 100% | 23.3118 | 74.78% | 0% | 25.22% | 0.86292 | 0 | 0 | 0.86292 | 0 | 0.78524 | 9.9207 | 0.079152 | 0.78524 | 9.9207 | 0.079152 | 0.8714 | 11.0092 | 0.079152 | 3.702% | 0.027199 | 0.025853 | 857.0759 | 12.4778 | 585.3688 | 259.2293 | 868.3324 | 0 | 0 | 868.3324 | 2.846e-05%
2027 | 567 | CB 567 | Tier-1 | Non-HFTD---7 | 1--4 | 0.56364 | 51 | 100% | 37.3049 | 99.02% | 0% | 0.9826% | 1.8284 | 0 | 0 | 1.8284 | 0 | 1.6639 | 0.55546 | 2.9954 | 1.6639 | 0.55546 | 2.9954 | 1.8464 | 0.61641 | 2.9954 | 4.901% | 0.0023798 | 0.002262 | 15675.6634 | 2324.2738 | 1292.524 | 12058.8657 | 15683.6852 | 0 | 0 | 15683.6852 | 6.03e-05%
2027 | 900 | 900-1163F | Tier-1 | Non-HFTD---19 | 1--1 | 0.24072 | 21 | 100% | 0.28819 | 42.17% | 0% | 57.83% | 0.0060154 | 0 | 0 | 0.0060154 | 0 | 0.005474 | 0.23723 | 0.023075 | 0.005474 | 0.23723 | 0.023075 | 0.0060745 | 0.26326 | 0.023075 | 2.087% | 0.0008402 | 0.00079861 | 343.0068 | 17.2218 | 58.4349 | 267.35 | 353.3375 | 0 | 0 | 353.3375 | 1.984e-07%
2027 | 1180 | 1180-9 | Tier-1 | Non-HFTD---15 | 2--2 | 2.6981 | 65 | 100% | 4.0697 | 57.31% | 0% | 42.69% | 0.11546 | 0 | 0 | 0.11546 | 0 | 0.10507 | 2.659 | 0.039514 | 0.10507 | 2.659 | 0.039514 | 0.11659 | 2.9508 | 0.039514 | 2.837% | 0.00751 | 0.0071383 | 541.9067 | 54.2911 | 113.8438 | 373.7718 | 553.9532 | 0 | 0 | 553.9532 | 3.807e-06%
2027 | NO2 | CB NO2 | Tier-1 | Non-HFTD---12 | 3--1 | 8.0842 | 188 | 100% | 8.9476 | 36.78% | 0% | 63.22% | 0.16292 | 0 | 0 | 0.16292 | 0 | 0.14825 | 7.967 | 0.018609 | 0.14825 | 7.967 | 0.018609 | 0.16452 | 8.8411 | 0.018609 | 1.821% | 0.022313 | 0.021209 | 401.0024 | 0.19075 | 170.5339 | 230.2778 | 414.204 | 0 | 0 | 414.204 | 5.372e-06%
2027 | 35 | 35-2 | Tier-1 | Non-HFTD---5 | 2--4 | 0.48065 | 5 | 100% | 55.5571 | 6.064% | 93.16% | 0.7781% | 0.16677 | 0 | 0 | 0.16677 | 0 | 0.15176 | 0.47368 | 0.32038 | 0.15176 | 0.47368 | 0.32038 | 0.16841 | 0.52565 | 0.32038 | 0.3002% | 0.0075196 | 0.0071474 | 7388.3078 | 76.3747 | 6138.5143 | 1173.4188 | 7749.742 | 0 | 0 | 7749.742 | 5.499e-06%
2027 | 462 | 462-1523F | Tier-1 | Non-HFTD---13 | 1--3 | 0.86758 | 18 | 100% | 5.2887 | 89.35% | 0% | 10.65% | 0.2339 | 0 | 0 | 0.2339 | 0 | 0.21285 | 0.855 | 0.24895 | 0.21285 | 0.855 | 0.24895 | 0.2362 | 0.9488 | 0.24895 | 4.423% | 0.0023366 | 0.0022209 | 2263.4326 | 314.0218 | 110.4125 | 1838.9983 | 2275.9905 | 0 | 0 | 2275.9905 | 7.713e-06%
2027 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 10.906 | 208 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 287.9812 | 10.7479 | 26.7942 | 287.9812 | 10.7479 | 26.7942 | 319.5779 | 11.9271 | 26.7942 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2027 | 190 | 190-1125F | Tier-1 | Non-HFTD---17 | 1--4 | 0.044508 | 0 | 100% | 1.3314 | 97.57% | 0% | 2.433% | 0.064301 | 0 | 0 | 0.064301 | 0 | 0.058513 | 0.043862 | 1.334 | 0.058513 | 0.043862 | 1.334 | 0.064933 | 0.048675 | 1.334 | 4.83% | 0.0001574 | 0.00014961 | 8458.7881 | 1300.024 | 20.0108 | 7138.7533 | 8469.5078 | 0 | 0 | 8469.5078 | 2.12e-06%
2027 | 63 | CB 63 | Tier-1 | Non-HFTD---1 | 3--4 | 2.7163 | 250 | 100% | 198.805 | 36.18% | 62.9% | 0.9206% | 3.5599 | 0 | 0 | 3.5599 | 0 | 3.2395 | 2.6769 | 1.2102 | 3.2395 | 2.6769 | 1.2102 | 3.5949 | 2.9706 | 1.2102 | 1.791% | 0.019218 | 0.018267 | 10344.6205 | 564.0493 | 6645.6212 | 3134.95 | 10688.4616 | 0 | 0 | 10688.4616 | 0.0001174%
2027 | 325 | 325-22R | Tier-1 | Non-HFTD---12 | 3--2 | 8.3706 | 226 | 100% | 13.8312 | 56.1% | 0% | 43.9% | 0.38407 | 0 | 0 | 0.38407 | 0 | 0.3495 | 8.2493 | 0.042368 | 0.3495 | 8.2493 | 0.042368 | 0.38785 | 9.1544 | 0.042368 | 2.777% | 0.024153 | 0.022957 | 572.6603 | 37.8929 | 176.6374 | 358.13 | 585.7531 | 0 | 0 | 585.7531 | 1.267e-05%
2027 | 1219 | CB 1219 | Tier-1 | Non-HFTD---19 | 1--1 | 0.23918 | 9 | 100% | 0.3441 | 26.91% | 0% | 73.09% | 0.0045828 | 0 | 0 | 0.0045828 | 0 | 0.0041702 | 0.23572 | 0.017692 | 0.0041702 | 0.23572 | 0.017692 | 0.0046278 | 0.26158 | 0.017692 | 1.332% | 0.0008074 | 0.00076743 | 426.1824 | 17.8119 | 34.3349 | 374.0356 | 442.4055 | 0 | 0 | 442.4055 | 1.511e-07%
2027 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 4.9148 | 696 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 32.1257 | 4.8435 | 6.6327 | 32.1257 | 4.8435 | 6.6327 | 35.6504 | 5.375 | 6.6327 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2027 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.085985 | 0 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.1836 | 0.084738 | 37.5694 | 3.1836 | 0.084738 | 37.5694 | 3.5329 | 0.094035 | 37.5694 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2027 | LJ3 | CB LJ3 | Tier-1 | Non-HFTD---14 | 3--1 | 5.2941 | 292 | 100% | 6.3096 | 39.49% | 0% | 60.51% | 0.12333 | 0 | 0 | 0.12333 | 0 | 0.11222 | 5.2173 | 0.02151 | 0.11222 | 5.2173 | 0.02151 | 0.12454 | 5.7898 | 0.02151 | 1.955% | 0.014718 | 0.013989 | 428.7031 | 0.52088 | 190.8463 | 237.3358 | 442.2133 | 0 | 0 | 442.2133 | 4.067e-06%
2027 | 286 | 286-990AE | Tier-1 | Non-HFTD---6 | 3--3 | 4.5934 | 275 | 100% | 50.0124 | 5.334% | 88.41% | 6.257% | 0.13205 | 0 | 0 | 0.13205 | 0 | 0.12017 | 4.5268 | 0.026546 | 0.12017 | 4.5268 | 0.026546 | 0.13335 | 5.0234 | 0.026546 | 0.264% | 0.018547 | 0.017629 | 2696.5813 | 3.2353 | 2292.3777 | 400.9683 | 2829.5225 | 0 | 0 | 2829.5225 | 4.355e-06%
2027 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 10.6016 | 377 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 40.081 | 10.4478 | 3.8363 | 40.081 | 10.4478 | 3.8363 | 44.4786 | 11.5941 | 3.8363 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2027 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 4.2055 | 350 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 162.9237 | 4.1445 | 39.3108 | 162.9237 | 4.1445 | 39.3108 | 180.7993 | 4.5992 | 39.3108 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2027 | 700 | 700-259F | Tier-1 | Non-HFTD---18 | 2--1 | 0.55551 | 19 | 100% | 1.7805 | 42.11% | 22.63% | 35.26% | 0.037115 | 0 | 0 | 0.037115 | 0 | 0.033774 | 0.54746 | 0.061693 | 0.033774 | 0.54746 | 0.061693 | 0.03748 | 0.60752 | 0.061693 | 2.085% | 0.0075412 | 0.0071679 | 236.1005 | 16.7944 | 50.0362 | 169.27 | 243.2182 | 0 | 0 | 243.2182 | 1.224e-06%
2027 | 311 | 311-14R | Tier-2 | Tier-2---14 | 3--4 | 0.75338 | 24 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 2.2455 | 0 | 0 | 2.2455 | 0 | 2.0434 | 0.74245 | 2.7522 | 2.0434 | 0.74245 | 2.7522 | 2.2676 | 0.82391 | 2.7522 | 0.8058% | 0.018935 | 0.017998 | 14715.9264 | 335.1634 | 11691.6167 | 2689.1463 | 15357.5365 | 0 | 0 | 15357.5365 | 7.405e-05%
2027 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 13.7044 | 1323 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 321.3252 | 13.5057 | 23.7919 | 321.3252 | 13.5057 | 23.7919 | 356.5803 | 14.9875 | 23.7919 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2027 | SC1 | CB SC1 | Tier-1 | Non-HFTD---2 | 4--4 | 7.9705 | 397 | 100% | 245.1307 | 1.784% | 95.78% | 2.439% | 0.21643 | 0 | 0 | 0.21643 | 0 | 0.19695 | 7.8549 | 0.025073 | 0.19695 | 7.8549 | 0.025073 | 0.21856 | 8.7167 | 0.025073 | 0.08829% | 0.040226 | 0.038235 | 6093.8082 | 6.9984 | 5431.9692 | 654.8405 | 6405.5002 | 0 | 0 | 6405.5002 | 7.137e-06%
2027 | 381 | 381-48 | Tier-1 | Non-HFTD---13 | 2--2 | 2.1998 | 102 | 100% | 7.9134 | 78.55% | 0% | 21.45% | 0.30769 | 0 | 0 | 0.30769 | 0 | 0.27999 | 2.1679 | 0.12915 | 0.27999 | 2.1679 | 0.12915 | 0.31071 | 2.4058 | 0.12915 | 3.888% | 0.0068838 | 0.0065431 | 1149.5636 | 150.1274 | 123.1813 | 876.2549 | 1162.4055 | 0 | 0 | 1162.4055 | 1.015e-05%
2027 | CHA1 | CB CHA1 | Tier-1 | Non-HFTD---10 | 3--2 | 4.0496 | 334 | 100% | 19.2146 | 44.26% | 40.89% | 14.85% | 0.42097 | 0 | 0 | 0.42097 | 0 | 0.38308 | 3.9909 | 0.095988 | 0.38308 | 3.9909 | 0.095988 | 0.42511 | 4.4288 | 0.095988 | 2.191% | 0.016682 | 0.015856 | 1151.8035 | 79.964 | 473.8867 | 597.9528 | 1185.238 | 0 | 0 | 1185.238 | 1.388e-05%
2027 | 279 | 279-11AE | Tier-1 | Non-HFTD---2 | 4--3 | 13.9777 | 317 | 100% | 201.506 | 3.082% | 92.11% | 4.808% | 0.30745 | 0 | 0 | 0.30745 | 0 | 0.27978 | 13.775 | 0.02031 | 0.27978 | 13.775 | 0.02031 | 0.31047 | 15.2864 | 0.02031 | 0.1526% | 0.055223 | 0.052489 | 3648.9772 | 5.6056 | 3185.2795 | 458.092 | 3833.1507 | 0 | 0 | 3833.1507 | 1.014e-05%
2027 | 162 | 162-19F | Tier-1 | Non-HFTD---12 | 4--2 | 10.1582 | 296 | 100% | 15.1555 | 52.93% | 0% | 47.07% | 0.39707 | 0 | 0 | 0.39707 | 0 | 0.36133 | 10.0109 | 0.036093 | 0.36133 | 10.0109 | 0.036093 | 0.40097 | 11.1093 | 0.036093 | 2.62% | 0.029254 | 0.027806 | 518.0585 | 22.6254 | 158.6224 | 336.8107 | 530.7581 | 0 | 0 | 530.7581 | 1.309e-05%
2027 | PL6 | CB PL6 | Tier-1 | Non-HFTD---12 | 4--1 | 10.6356 | 602 | 100% | 11.6399 | 35.44% | 0% | 64.56% | 0.20418 | 0 | 0 | 0.20418 | 0 | 0.1858 | 10.4814 | 0.017726 | 0.1858 | 10.4814 | 0.017726 | 0.20618 | 11.6314 | 0.017726 | 1.754% | 0.029655 | 0.028187 | 392.5082 | 0.9255 | 157.6202 | 233.9625 | 405.7056 | 0 | 0 | 405.7056 | 6.733e-06%
2027 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 4.8645 | 919 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 20.4453 | 4.794 | 4.2647 | 20.4453 | 4.794 | 4.2647 | 22.6885 | 5.32 | 4.2647 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2027 | LJ4 | CB LJ4 | Tier-1 | Non-HFTD---16 | 2--1 | 2.5968 | 116 | 100% | 3.329 | 11.7% | 0% | 88.3% | 0.019278 | 0 | 0 | 0.019278 | 0 | 0.017543 | 2.5592 | 0.0068548 | 0.017543 | 2.5592 | 0.0068548 | 0.019467 | 2.84 | 0.0068548 | 0.5791% | 0.0094594 | 0.0089912 | 351.9241 | 0.35466 | 68.6606 | 282.9088 | 368.1074 | 0 | 0 | 368.1074 | 6.357e-07%
2027 | 44 | 44-41 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2296 | 47 | 100% | 1.0965 | 21.81% | 0% | 78.19% | 0.011837 | 0 | 0 | 0.011837 | 0 | 0.010772 | 1.2117 | 0.0088893 | 0.010772 | 1.2117 | 0.0088893 | 0.011953 | 1.3447 | 0.0088893 | 1.079% | 0.0032776 | 0.0031154 | 334.5534 | 0.42375 | 95.3401 | 238.7896 | 348.1766 | 0 | 0 | 348.1766 | 3.903e-07%
2027 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 1.1027 | 145 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 33.1036 | 1.0867 | 30.4627 | 33.1036 | 1.0867 | 30.4627 | 36.7357 | 1.2059 | 30.4627 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2027 | 59 | CB 59 | Tier-1 | Non-HFTD---5 | 2--4 | 0.80076 | 2 | 100% | 54.4254 | 99.08% | 0.2847% | 0.6369% | 2.6692 | 0 | 0 | 2.6692 | 0 | 2.429 | 0.78915 | 3.078 | 2.429 | 0.78915 | 3.078 | 2.6955 | 0.87573 | 3.078 | 4.904% | 0.0099342 | 0.0094425 | 5478.5927 | 848.4383 | 1089.8599 | 3540.2945 | 5481.2223 | 0 | 0 | 5481.2223 | 8.802e-05%
2027 | 131 | CB 131 | Tier-1 | Non-HFTD---15 | 2--2 | 1.6525 | 6 | 100% | 3.9586 | 65.37% | 0% | 34.63% | 0.1281 | 0 | 0 | 0.1281 | 0 | 0.11656 | 1.6285 | 0.071576 | 0.11656 | 1.6285 | 0.071576 | 0.12935 | 1.8072 | 0.071576 | 3.236% | 0.0054554 | 0.0051854 | 725.6284 | 55.3628 | 156.9776 | 513.288 | 738.7144 | 0 | 0 | 738.7144 | 4.224e-06%
2027 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 10.8114 | 954 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 79.4193 | 10.6546 | 7.454 | 79.4193 | 10.6546 | 7.454 | 88.133 | 11.8236 | 7.454 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2027 | 321 | 321-740AE | Tier-1 | Non-HFTD---14 | 3--1 | 5.658 | 154 | 100% | 5.6044 | 24.77% | 0% | 75.23% | 0.068724 | 0 | 0 | 0.068724 | 0 | 0.062538 | 5.576 | 0.011216 | 0.062538 | 5.576 | 0.011216 | 0.0694 | 6.1877 | 0.011216 | 1.226% | 0.016283 | 0.015477 | 344.189 | 0.80306 | 105.0413 | 238.3446 | 357.6731 | 0 | 0 | 357.6731 | 2.266e-06%
2027 | 780 | 780-468R | Tier-1 | Non-HFTD---4 | 3--4 | 1.3398 | 27 | 100% | 132.1756 | 2.152% | 97.23% | 0.6129% | 0.14083 | 0 | 0 | 0.14083 | 0 | 0.12815 | 1.3204 | 0.097058 | 0.12815 | 1.3204 | 0.097058 | 0.14221 | 1.4652 | 0.097058 | 0.1065% | 0.014295 | 0.013588 | 9246.1513 | 26.0626 | 8234.6389 | 985.4497 | 9717.3064 | 0 | 0 | 9717.3064 | 4.644e-06%
2027 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 2.6099 | 102 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 87.1533 | 2.572 | 33.885 | 87.1533 | 2.572 | 33.885 | 96.7155 | 2.8542 | 33.885 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2027 | 775 | 775-185 | Tier-1 | Non-HFTD---16 | 2--1 | 2.1559 | 84 | 100% | 2.4124 | 31.06% | 0% | 68.94% | 0.037091 | 0 | 0 | 0.037091 | 0 | 0.033752 | 2.1246 | 0.015886 | 0.033752 | 2.1246 | 0.015886 | 0.037456 | 2.3577 | 0.015886 | 1.538% | 0.0065622 | 0.0062374 | 367.6213 | 10.1886 | 93.1395 | 264.2932 | 380.8197 | 0 | 0 | 380.8197 | 1.223e-06%
2027 | 1406 | CB 1406 | Tier-1 | Non-HFTD---17 | 1--3 | 0.036742 | 0 | 100% | 0.71787 | 90.65% | 0% | 9.349% | 0.032213 | 0 | 0 | 0.032213 | 0 | 0.029313 | 0.03621 | 0.80953 | 0.029313 | 0.03621 | 0.80953 | 0.032529 | 0.040183 | 0.80953 | 4.487% | 0.0001864 | 0.00017717 | 3851.2388 | 0.27092 | 3523.903 | 327.0649 | 3869.9891 | 0 | 0 | 3869.9891 | 1.062e-06%
2027 | 458 | CB 458 | Tier-1 | Non-HFTD---20 | 1--1 | 0.51493 | 1 | 100% | 0.4923 | 10.29% | 0% | 89.71% | 0.0025064 | 0 | 0 | 0.0025064 | 0 | 0.0022808 | 0.50746 | 0.0044944 | 0.0022808 | 0.50746 | 0.0044944 | 0.002531 | 0.56314 | 0.0044944 | 0.5091% | 0.0016434 | 0.0015621 | 299.5635 | 3.6595 | 33.8007 | 262.1032 | 313.5596 | 0 | 0 | 313.5596 | 8.265e-08%
2027 | 252 | 252-129 | Tier-2 | Tier-2---18 | 3--3 | 4.6668 | 14 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 2.1229 | 0 | 0 | 2.1229 | 0 | 1.9318 | 4.5991 | 0.42003 | 1.9318 | 4.5991 | 0.42003 | 2.1437 | 5.1038 | 0.42003 | 4.29% | 0.02391 | 0.022726 | 2069.6845 | 324.0484 | 134.0961 | 1611.54 | 2084.0584 | 0 | 0 | 2084.0584 | 7e-05%
2027 | 172 | 172-615R | Tier-1 | Non-HFTD---6 | 4--2 | 6.2257 | 251 | 100% | 65.0211 | 31.38% | 63.15% | 5.469% | 1.0101 | 0 | 0 | 1.0101 | 0 | 0.91915 | 6.1354 | 0.14981 | 0.91915 | 6.1354 | 0.14981 | 1.02 | 6.8086 | 0.14981 | 1.553% | 0.053579 | 0.050927 | 1213.547 | 17.4537 | 970.9978 | 225.0954 | 1256.9124 | 0 | 0 | 1256.9124 | 3.331e-05%
2027 | 45 | 45-16 | Tier-1 | Non-HFTD---11 | 2--2 | 2.7608 | 126 | 100% | 10.6609 | 86.29% | 0% | 13.71% | 0.45536 | 0 | 0 | 0.45536 | 0 | 0.41437 | 2.7207 | 0.1523 | 0.41437 | 2.7207 | 0.1523 | 0.45984 | 3.0193 | 0.1523 | 4.271% | 0.0075584 | 0.0071843 | 1410.4753 | 328.5278 | 122.7581 | 959.1895 | 1420.5468 | 0 | 0 | 1420.5468 | 1.502e-05%
2027 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 10.1081 | 575 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 31.5996 | 9.9616 | 3.1722 | 31.5996 | 9.9616 | 3.1722 | 35.0666 | 11.0545 | 3.1722 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2027 | 83 | CB 83 | Tier-1 | Non-HFTD---11 | 2--2 | 5.2235 | 109 | 100% | 14.2823 | 84.51% | 0% | 15.49% | 0.59746 | 0 | 0 | 0.59746 | 0 | 0.54368 | 5.1477 | 0.10562 | 0.54368 | 5.1477 | 0.10562 | 0.60333 | 5.7125 | 0.10562 | 4.183% | 0.012231 | 0.011626 | 1167.6768 | 4.647 | 975.6795 | 187.3504 | 1177.0966 | 0 | 0 | 1177.0966 | 1.97e-05%
2027 | HL3 | CB HL3 | Tier-1 | Non-HFTD---12 | 3--1 | 8.2549 | 102 | 100% | 9.4251 | 40.92% | 0% | 59.08% | 0.19092 | 0 | 0 | 0.19092 | 0 | 0.17373 | 8.1353 | 0.021356 | 0.17373 | 8.1353 | 0.021356 | 0.1928 | 9.0278 | 0.021356 | 2.026% | 0.021995 | 0.020907 | 428.5039 | 2.1065 | 186.5448 | 239.8526 | 441.6875 | 0 | 0 | 441.6875 | 6.296e-06%
2027 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 12.1512 | 539 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 167.0067 | 11.975 | 13.9463 | 167.0067 | 11.975 | 13.9463 | 185.3303 | 13.2888 | 13.9463 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2027 | 197 | 197-1150F | Tier-2 | Tier-2---15 | 3--4 | 1.3604 | 2 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 9.0248 | 0 | 0 | 9.0248 | 0 | 8.2124 | 1.3407 | 6.1255 | 8.2124 | 1.3407 | 6.1255 | 9.1135 | 1.4878 | 6.1255 | 4.917% | 0.021777 | 0.020699 | 8428.1597 | 1361.8326 | 10.8364 | 7055.4907 | 8431.076 | 0 | 0 | 8431.076 | 0.0002976%
2027 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 34.1718 | 1855 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1801.0985 | 33.6764 | 53.4826 | 1801.0985 | 33.6764 | 53.4826 | 1998.7108 | 37.3712 | 53.4826 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2027 | 1173 | CB 1173 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1624 | 51 | 100% | 2.9682 | 59.25% | 0% | 40.75% | 0.087048 | 0 | 0 | 0.087048 | 0 | 0.079212 | 1.1455 | 0.069151 | 0.079212 | 1.1455 | 0.069151 | 0.087903 | 1.2712 | 0.069151 | 2.933% | 0.0040836 | 0.0038815 | 726.8498 | 0.22289 | 457.5433 | 269.0836 | 742.276 | 0 | 0 | 742.276 | 2.871e-06%
2027 | 493 | CB 493 | Tier-1 | Non-HFTD---17 | 1--2 | 0.20795 | 11 | 100% | 1.0505 | 81.53% | 0% | 18.47% | 0.042395 | 0 | 0 | 0.042395 | 0 | 0.038579 | 0.20494 | 0.18824 | 0.038579 | 0.20494 | 0.18824 | 0.042811 | 0.22742 | 0.18824 | 4.036% | 0.0008612 | 0.00081857 | 1219.8489 | 9.8539 | 955.0049 | 254.9902 | 1231.585 | 0 | 0 | 1231.585 | 1.398e-06%
2027 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 4.8975 | 156 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 63.4742 | 4.8265 | 13.1512 | 63.4742 | 4.8265 | 13.1512 | 70.4384 | 5.3561 | 13.1512 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2027 | 153 | 153-1119R | Tier-1 | Non-HFTD---13 | 2--2 | 2.4303 | 39 | 100% | 8.0116 | 75.45% | 0% | 24.55% | 0.2992 | 0 | 0 | 0.2992 | 0 | 0.27227 | 2.3951 | 0.11368 | 0.27227 | 2.3951 | 0.11368 | 0.30214 | 2.6579 | 0.11368 | 3.735% | 0.0073252 | 0.0069626 | 1093.6986 | 0.20207 | 849.5472 | 243.9493 | 1107.6839 | 0 | 0 | 1107.6839 | 9.866e-06%
2027 | 323 | CB 323 | Tier-1 | Non-HFTD---11 | 1--4 | 0.54113 | 18 | 100% | 12.9162 | 95.89% | 0% | 4.106% | 0.6131 | 0 | 0 | 0.6131 | 0 | 0.55791 | 0.53328 | 1.0462 | 0.55791 | 0.53328 | 1.0462 | 0.61913 | 0.59179 | 1.0462 | 4.747% | 0.0019678 | 0.0018704 | 6563.758 | 128.289 | 5536.1599 | 899.3092 | 6577.7919 | 0 | 0 | 6577.7919 | 2.022e-05%
2027 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 3.3899 | 476 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 169.5107 | 3.3408 | 50.7401 | 169.5107 | 3.3408 | 50.7401 | 188.109 | 3.7073 | 50.7401 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2027 | 146 | CB 146 | Tier-1 | Non-HFTD---15 | 2--2 | 0.18561 | 0 | 100% | 2.7748 | 92.6% | 1.913% | 5.483% | 0.12719 | 0 | 0 | 0.12719 | 0 | 0.11575 | 0.18291 | 0.63278 | 0.11575 | 0.18291 | 0.63278 | 0.12844 | 0.20298 | 0.63278 | 4.584% | 0.0054076 | 0.0051399 | 513.1328 | 60.6904 | 208.0736 | 244.3689 | 515.1093 | 0 | 0 | 515.1093 | 4.194e-06%
2027 | DR1 | CB DR1 | Tier-1 | Non-HFTD---10 | 3--2 | 5.4435 | 420 | 100% | 21.3264 | 25.84% | 59.63% | 14.53% | 0.27278 | 0 | 0 | 0.27278 | 0 | 0.24822 | 5.3646 | 0.046271 | 0.24822 | 5.3646 | 0.046271 | 0.27546 | 5.9532 | 0.046271 | 1.279% | 0.019541 | 0.018574 | 1091.3677 | 40.6433 | 651.42 | 399.3043 | 1133.5175 | 0 | 0 | 1133.5175 | 8.995e-06%
2027 | 414 | CB 414 | Tier-1 | Non-HFTD---2 | 4--3 | 16.8574 | 578 | 100% | 223.669 | 40.12% | 54.98% | 4.902% | 4.4417 | 0 | 0 | 4.4417 | 0 | 4.0418 | 16.613 | 0.24329 | 4.0418 | 16.613 | 0.24329 | 4.4853 | 18.4357 | 0.24329 | 1.986% | 0.060264 | 0.057281 | 3711.4858 | 297.0369 | 2040.8852 | 1373.5637 | 3827.2303 | 0 | 0 | 3827.2303 | 0.0001465%
2027 | 443 | 443-218R | Tier-1 | Non-HFTD---3 | 5--2 | 2.5293 | 0 | 100% | 96.9814 | 95.91% | 2.964% | 1.126% | 4.6043 | 0 | 0 | 4.6043 | 0 | 4.1898 | 2.4927 | 1.6809 | 4.1898 | 2.4927 | 1.6809 | 4.6495 | 2.7662 | 1.6809 | 4.748% | 0.096176 | 0.091415 | 1008.3738 | 175.6292 | 24.7239 | 808.0207 | 1010.5213 | 0 | 0 | 1010.5213 | 0.0001518%
2027 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 1.4734 | 170 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.248 | 1.4521 | 2.2368 | 3.248 | 1.4521 | 2.2368 | 3.6044 | 1.6114 | 2.2368 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2027 | 702 | 702-25 | Tier-1 | Non-HFTD---4 | 2--4 | 0.91362 | 18 | 100% | 105.79 | 16.96% | 82.58% | 0.4592% | 0.88821 | 0 | 0 | 0.88821 | 0 | 0.80826 | 0.90038 | 0.89769 | 0.80826 | 0.90038 | 0.89769 | 0.89694 | 0.99916 | 0.89769 | 0.8396% | 0.0085112 | 0.0080899 | 12429.5062 | 105.0973 | 10920.6101 | 1403.7989 | 12967.0151 | 0 | 0 | 12967.0151 | 2.929e-05%
2027 | TY1 | CB TY1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.27729 | 7 | 100% | 0.35043 | 36.25% | 0% | 63.75% | 0.0062889 | 0 | 0 | 0.0062889 | 0 | 0.0057228 | 0.27327 | 0.020942 | 0.0057228 | 0.27327 | 0.020942 | 0.0063507 | 0.30325 | 0.020942 | 1.795% | 0.0008392 | 0.00079766 | 417.5792 | 9.9722 | 115.9508 | 291.6562 | 431.4417 | 0 | 0 | 431.4417 | 2.074e-07%
2027 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 4.2257 | 174 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 83.8042 | 4.1645 | 20.1236 | 83.8042 | 4.1645 | 20.1236 | 92.999 | 4.6214 | 20.1236 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2027 | 64 | CB 64 | Tier-1 | Non-HFTD---4 | 3--4 | 3.6049 | 136 | 100% | 105.4157 | 32.05% | 65.74% | 2.205% | 1.6724 | 0 | 0 | 1.6724 | 0 | 1.5219 | 3.5526 | 0.42837 | 1.5219 | 3.5526 | 0.42837 | 1.6888 | 3.9424 | 0.42837 | 1.586% | 0.017938 | 0.01705 | 5876.6069 | 242.5487 | 3978.8464 | 1655.2117 | 6084.5618 | 0 | 0 | 6084.5618 | 5.515e-05%
2027 | 278 | 278-22R | Tier-1 | Non-HFTD---2 | 4--3 | 15.5778 | 433 | 100% | 285.1665 | 5.51% | 90.91% | 3.576% | 0.77782 | 0 | 0 | 0.77782 | 0 | 0.7078 | 15.352 | 0.046105 | 0.7078 | 15.352 | 0.046105 | 0.78546 | 17.0364 | 0.046105 | 0.2728% | 0.058535 | 0.055637 | 4871.7604 | 23.1046 | 4253.0091 | 595.6468 | 5111.491 | 0 | 0 | 5111.491 | 2.565e-05%
2027 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 20.8132 | 1063 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 399.4624 | 20.5115 | 19.4751 | 399.4624 | 20.5115 | 19.4751 | 443.2904 | 22.7619 | 19.4751 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2027 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 0.8655 | 53 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.01378 | 0.85295 | 0.016156 | 0.01378 | 0.85295 | 0.016156 | 0.015292 | 0.94654 | 0.016156 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2027 | 41 | 41-44AE | Tier-1 | Non-HFTD---15 | 2--2 | 2.7028 | 103 | 100% | 4.0717 | 49.31% | 0% | 50.69% | 0.099392 | 0 | 0 | 0.099392 | 0 | 0.090446 | 2.6637 | 0.033955 | 0.090446 | 2.6637 | 0.033955 | 0.10037 | 2.9559 | 0.033955 | 2.441% | 0.0078416 | 0.0074534 | 519.2383 | 3.8166 | 257.6774 | 257.7443 | 532.9441 | 0 | 0 | 532.9441 | 3.278e-06%
2027 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 6.4578 | 311 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 56.6878 | 6.3641 | 8.9074 | 56.6878 | 6.3641 | 8.9074 | 62.9074 | 7.0624 | 8.9074 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2027 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 5.507 | 474 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 139.6922 | 5.4271 | 25.7396 | 139.6922 | 5.4271 | 25.7396 | 155.0189 | 6.0226 | 25.7396 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2027 | 598 | CB 598 | Tier-1 | Non-HFTD---9 | 1--4 | 0.66591 | 21 | 100% | 17.2197 | 95.45% | 0% | 4.551% | 0.81358 | 0 | 0 | 0.81358 | 0 | 0.74035 | 0.65625 | 1.1281 | 0.74035 | 0.65625 | 1.1281 | 0.82158 | 0.72826 | 1.1281 | 4.725% | 0.0027812 | 0.0026435 | 6191.4698 | 926.9749 | 243.7416 | 5020.7533 | 6206.1445 | 0 | 0 | 6206.1445 | 2.683e-05%
2027 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 18.1587 | 322 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 68.683 | 17.8954 | 3.838 | 68.683 | 17.8954 | 3.838 | 76.2188 | 19.8588 | 3.838 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2027 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 11.815 | 984 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 777.0044 | 11.6437 | 66.732 | 777.0044 | 11.6437 | 66.732 | 862.2555 | 12.9212 | 66.732 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2027 | 516 | CB 516 | Tier-1 | Non-HFTD---13 | 2--2 | 1.9939 | 56 | 100% | 4.9777 | 55.1% | 0% | 44.9% | 0.13576 | 0 | 0 | 0.13576 | 0 | 0.12354 | 1.965 | 0.062869 | 0.12354 | 1.965 | 0.062869 | 0.13709 | 2.1806 | 0.062869 | 2.727% | 0.0070882 | 0.0067373 | 702.2584 | 0.23727 | 415.5749 | 286.4462 | 718.68 | 0 | 0 | 718.68 | 4.477e-06%
2027 | 205 | 205-1550 | Tier-2 | Tier-2---15 | 2--4 | 2.7852 | 227 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 6.0476 | 0 | 0 | 6.0476 | 0 | 5.5032 | 2.7448 | 2.0049 | 5.5032 | 2.7448 | 2.0049 | 6.107 | 3.046 | 2.0049 | 4.877% | 0.008789 | 0.0083539 | 14109.2738 | 2221.4405 | 309.7116 | 11578.1217 | 14120.1329 | 0 | 0 | 14120.1329 | 0.0001994%
2027 | HV1 | CB HV1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2047 | 174 | 100% | 1.373 | 42.97% | 0% | 57.03% | 0.029203 | 0 | 0 | 0.029203 | 0 | 0.026574 | 1.1873 | 0.022383 | 0.026574 | 1.1873 | 0.022383 | 0.02949 | 1.3175 | 0.022383 | 2.127% | 0.0035008 | 0.0033275 | 392.1896 | 29.8125 | 41.3066 | 321.0705 | 403.8379 | 0 | 0 | 403.8379 | 9.63e-07%
2027 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 1.8014 | 103 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.1844 | 1.7752 | 1.2305 | 2.1844 | 1.7752 | 1.2305 | 2.424 | 1.97 | 1.2305 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2027 | 361 | 361-45R | Tier-1 | Non-HFTD---5 | 3--4 | 2.965 | 64 | 100% | 74.9226 | 4.739% | 91.81% | 3.451% | 0.17574 | 0 | 0 | 0.17574 | 0 | 0.15992 | 2.922 | 0.05473 | 0.15992 | 2.922 | 0.05473 | 0.17747 | 3.2426 | 0.05473 | 0.2346% | 0.01487 | 0.014134 | 5038.4415 | 12.6045 | 4395.9502 | 629.8868 | 5288.3992 | 0 | 0 | 5288.3992 | 5.795e-06%
2027 | 368 | 368-1054F | Tier-1 | Non-HFTD---5 | 2--4 | 0.47745 | 4 | 100% | 80.991 | 0.1968% | 99.37% | 0.4288% | 0.0078897 | 0 | 0 | 0.0078897 | 0 | 0.0071795 | 0.47053 | 0.015258 | 0.0071795 | 0.47053 | 0.015258 | 0.0079672 | 0.52215 | 0.015258 | 0.009741% | 0.0067372 | 0.0064037 | 12021.4569 | 14.7322 | 10791.9159 | 1214.8087 | 12646.2765 | 0 | 0 | 12646.2765 | 2.602e-07%
2027 | LM3 | CB LM3 | Tier-1 | Non-HFTD---16 | 2--1 | 3.229 | 148 | 100% | 2.8437 | 17.95% | 0% | 82.05% | 0.025272 | 0 | 0 | 0.025272 | 0 | 0.022997 | 3.1822 | 0.0072268 | 0.022997 | 3.1822 | 0.0072268 | 0.02552 | 3.5313 | 0.0072268 | 0.8887% | 0.0089108 | 0.0084697 | 319.1341 | 1.177 | 75.099 | 242.8581 | 332.7702 | 0 | 0 | 332.7702 | 8.334e-07%
2027 | 308 | 308-464 | Tier-1 | Non-HFTD---3 | 4--3 | 3.726 | 137 | 100% | 187.2147 | 5.297% | 93.54% | 1.164% | 0.49085 | 0 | 0 | 0.49085 | 0 | 0.44667 | 3.6719 | 0.12164 | 0.44667 | 3.6719 | 0.12164 | 0.49568 | 4.0748 | 0.12164 | 0.2622% | 0.040091 | 0.038106 | 4669.7896 | 26.7777 | 4109.7012 | 533.3108 | 4900.101 | 0 | 0 | 4900.101 | 1.619e-05%
2027 | 155 | CB 155 | Tier-1 | Non-HFTD---7 | 2--3 | 4.6852 | 45 | 100% | 44.4963 | 94.43% | 0% | 5.571% | 2.0799 | 0 | 0 | 2.0799 | 0 | 1.8926 | 4.6173 | 0.4099 | 1.8926 | 4.6173 | 0.4099 | 2.1003 | 5.1239 | 0.4099 | 4.674% | 0.013451 | 0.012786 | 3307.9312 | 28.3316 | 2967.8681 | 311.7315 | 3317.529 | 0 | 0 | 3317.529 | 6.859e-05%
2027 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 4.3966 | 74 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 581.8498 | 4.3328 | 134.2887 | 581.8498 | 4.3328 | 134.2887 | 645.689 | 4.8082 | 134.2887 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2027 | 244 | 244-32F | Tier-1 | Non-HFTD---6 | 3--3 | 0.80758 | 17 | 100% | 51.191 | 8.266% | 90.61% | 1.12% | 0.20945 | 0 | 0 | 0.20945 | 0 | 0.1906 | 0.79587 | 0.23949 | 0.1906 | 0.79587 | 0.23949 | 0.21151 | 0.88319 | 0.23949 | 0.4092% | 0.026609 | 0.025291 | 1923.8516 | 6.2615 | 1678.6755 | 238.9145 | 2015.76 | 0 | 0 | 2015.76 | 6.907e-06%
2027 | 730 | 730-1079 | Tier-1 | Non-HFTD---10 | 4--2 | 13.1661 | 615 | 100% | 24.9152 | 67.14% | 0% | 32.86% | 0.8281 | 0 | 0 | 0.8281 | 0 | 0.75356 | 12.9752 | 0.058077 | 0.75356 | 12.9752 | 0.058077 | 0.83624 | 14.3988 | 0.058077 | 3.324% | 0.039453 | 0.0375 | 631.5134 | 48.4936 | 242.245 | 340.7748 | 642.3187 | 0 | 0 | 642.3187 | 2.731e-05%
2027 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 5.8533 | 590 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 60.6355 | 5.7684 | 10.5117 | 60.6355 | 5.7684 | 10.5117 | 67.2883 | 6.4013 | 10.5117 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2027 | 397 | CB 397 | Tier-1 | Non-HFTD---10 | 3--2 | 5.8458 | 263 | 100% | 18.3403 | 77.93% | 0% | 22.07% | 0.70752 | 0 | 0 | 0.70752 | 0 | 0.64383 | 5.7611 | 0.11176 | 0.64383 | 5.7611 | 0.11176 | 0.71447 | 6.3932 | 0.11176 | 3.858% | 0.016356 | 0.015546 | 1121.3207 | 1.3088 | 889.4625 | 230.5495 | 1134.2064 | 0 | 0 | 1134.2064 | 2.333e-05%
2027 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 3.8686 | 160 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 166.1042 | 3.8125 | 43.5687 | 166.1042 | 3.8125 | 43.5687 | 184.3288 | 4.2308 | 43.5687 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2027 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 2.001 | 355 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 290.2233 | 1.972 | 147.1755 | 290.2233 | 1.972 | 147.1755 | 322.0659 | 2.1883 | 147.1755 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2027 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 7.3438 | 745 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 308.3982 | 7.2373 | 42.6123 | 308.3982 | 7.2373 | 42.6123 | 342.2349 | 8.0314 | 42.6123 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2027 | EN1 | CB EN1 | Tier-1 | Non-HFTD---6 | 4--3 | 9.5242 | 860 | 100% | 70.8621 | 16.44% | 73.67% | 9.888% | 0.57673 | 0 | 0 | 0.57673 | 0 | 0.52482 | 9.3861 | 0.055914 | 0.52482 | 9.3861 | 0.055914 | 0.5824 | 10.416 | 0.055914 | 0.8139% | 0.03227 | 0.030673 | 2195.9128 | 34.015 | 1636.754 | 525.1438 | 2291.4685 | 0 | 0 | 2291.4685 | 1.902e-05%
2027 | 551 | CB 551 | Tier-1 | Non-HFTD---17 | 1--3 | 0.22538 | 1 | 100% | 2.2115 | 88.35% | 0% | 11.65% | 0.096715 | 0 | 0 | 0.096715 | 0 | 0.08801 | 0.22212 | 0.39623 | 0.08801 | 0.22212 | 0.39623 | 0.097666 | 0.24649 | 0.39623 | 4.373% | 0.000778 | 0.00073949 | 2842.6003 | 2.9889 | 2524.6412 | 314.9702 | 2859.8501 | 0 | 0 | 2859.8501 | 3.189e-06%
2027 | 196 | CB 196 | Tier-2 | Tier-2---15 | 3--4 | 0.59317 | 34 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.19032 | 0.58457 | 0.32557 | 0.19032 | 0.58457 | 0.32557 | 0.2112 | 0.64871 | 0.32557 | 0.1555% | 0.019464 | 0.018501 | 6908.5051 | 30.9312 | 5935.5679 | 942.006 | 7256.9805 | 0 | 0 | 7256.9805 | 6.897e-06%
2027 | CA1 | CB CA1 | Tier-1 | Non-HFTD---8 | 3--2 | 4.8453 | 343 | 100% | 26.9004 | 5.027% | 82.43% | 12.54% | 0.066943 | 0 | 0 | 0.066943 | 0 | 0.060917 | 4.775 | 0.012757 | 0.060917 | 4.775 | 0.012757 | 0.067601 | 5.2989 | 0.012757 | 0.2489% | 0.01864 | 0.017718 | 1443.1369 | 5.8286 | 1152.8354 | 284.4728 | 1514.514 | 0 | 0 | 1514.514 | 2.208e-06%
2027 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 3.7273 | 332 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 352.6402 | 3.6732 | 96.0033 | 352.6402 | 3.6732 | 96.0033 | 391.3311 | 4.0762 | 96.0033 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2027 | 1436 | CB 1436 | Tier-1 | Non-HFTD---13 | 1--3 | 0.38731 | 13 | 100% | 5.4228 | 92.93% | 0% | 7.074% | 0.24944 | 0 | 0 | 0.24944 | 0 | 0.22699 | 0.38169 | 0.59468 | 0.22699 | 0.38169 | 0.59468 | 0.25189 | 0.42357 | 0.59468 | 4.6% | 0.0017518 | 0.0016651 | 3095.5311 | 14.7451 | 2805.6585 | 275.1275 | 3106.9346 | 0 | 0 | 3106.9346 | 8.226e-06%
2027 | 153 | 153-581F | Tier-1 | Non-HFTD---12 | 3--1 | 7.8703 | 195 | 100% | 9.378 | 55.57% | 0% | 44.43% | 0.25798 | 0 | 0 | 0.25798 | 0 | 0.23475 | 7.7562 | 0.030267 | 0.23475 | 7.7562 | 0.030267 | 0.26051 | 8.6072 | 0.030267 | 2.751% | 0.019874 | 0.01889 | 471.8682 | 14.7491 | 216.5363 | 240.5828 | 482.7857 | 0 | 0 | 482.7857 | 8.507e-06%
2027 | 1297 | 1297-35F | Tier-1 | Non-HFTD---5 | 2--3 | 1.8046 | 25 | 100% | 50.4009 | 3.614% | 93.45% | 2.939% | 0.090151 | 0 | 0 | 0.090151 | 0 | 0.082037 | 1.7784 | 0.046129 | 0.082037 | 1.7784 | 0.046129 | 0.091037 | 1.9735 | 0.046129 | 0.1789% | 0.011686 | 0.011107 | 4313.0011 | 4.498 | 3844.9239 | 463.5793 | 4529.4966 | 0 | 0 | 4529.4966 | 2.973e-06%
2027 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 12.6964 | 992 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 494.3491 | 12.5123 | 39.5089 | 494.3491 | 12.5123 | 39.5089 | 548.5879 | 13.8852 | 39.5089 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2027 | 364 | CB 364 | Tier-1 | Non-HFTD---3 | 3--4 | 4.5699 | 87 | 100% | 99.5129 | 18.42% | 77.53% | 4.054% | 0.90733 | 0 | 0 | 0.90733 | 0 | 0.82566 | 4.5036 | 0.18333 | 0.82566 | 4.5036 | 0.18333 | 0.91625 | 4.9977 | 0.18333 | 0.9118% | 0.019381 | 0.018422 | 5134.505 | 5.0746 | 4604.1532 | 525.2772 | 5352.6459 | 0 | 0 | 5352.6459 | 2.992e-05%
2027 | 591 | CB 591 | Tier-1 | Non-HFTD---1 | 4--4 | 9.3315 | 487 | 100% | 1060.5472 | 90.24% | 9.188% | 0.5739% | 47.3724 | 0 | 0 | 47.3724 | 0 | 43.1082 | 9.1962 | 4.6876 | 43.1082 | 9.1962 | 4.6876 | 47.838 | 10.2051 | 4.6876 | 4.467% | 0.066615 | 0.063317 | 15920.6417 | 3763.87 | 1847.5145 | 10309.2572 | 16001.5783 | 0 | 0 | 16001.5783 | 0.001562%
2027 | 320 | CB 320 | Tier-1 | Non-HFTD---13 | 1--3 | 0.72523 | 16 | 100% | 4.9303 | 88.31% | 0% | 11.69% | 0.21551 | 0 | 0 | 0.21551 | 0 | 0.19611 | 0.71471 | 0.2744 | 0.19611 | 0.71471 | 0.2744 | 0.21763 | 0.79313 | 0.2744 | 4.371% | 0.002136 | 0.0020303 | 2308.1856 | 59.5018 | 1700.6421 | 548.0417 | 2322.2409 | 0 | 0 | 2322.2409 | 7.107e-06%
2027 | 770 | CB 770 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3017 | 137 | 100% | 5.4599 | 68.13% | 0% | 31.87% | 0.18414 | 0 | 0 | 0.18414 | 0 | 0.16757 | 2.2684 | 0.073871 | 0.16757 | 2.2684 | 0.073871 | 0.18595 | 2.5172 | 0.073871 | 3.373% | 0.008087 | 0.0076867 | 675.1471 | 60.111 | 111.1789 | 503.8571 | 686.3515 | 0 | 0 | 686.3515 | 6.072e-06%
2027 | 777 | 777-268F | Tier-1 | Non-HFTD---19 | 1--3 | 0.02803 | 0 | 100% | 0.57885 | 94.54% | 0% | 5.457% | 0.027089 | 0 | 0 | 0.027089 | 0 | 0.024651 | 0.027624 | 0.89237 | 0.024651 | 0.027624 | 0.89237 | 0.027355 | 0.030655 | 0.89237 | 4.68% | 0.0001222 | 0.00011615 | 4736.8697 | 723.3986 | 27.1305 | 3986.3407 | 4750.3318 | 0 | 0 | 4750.3318 | 8.933e-07%
2027 | 58 | 58-754F | Tier-1 | Non-HFTD---4 | 3--4 | 2.4574 | 37 | 100% | 111.5609 | 10.85% | 87.5% | 1.644% | 0.5994 | 0 | 0 | 0.5994 | 0 | 0.54544 | 2.4218 | 0.22522 | 0.54544 | 2.4218 | 0.22522 | 0.60529 | 2.6875 | 0.22522 | 0.5373% | 0.017828 | 0.016946 | 6257.4815 | 6.3235 | 5703.0525 | 548.1055 | 6547.9864 | 0 | 0 | 6547.9864 | 1.977e-05%
2027 | 781 | 781-43AE | Tier-1 | Non-HFTD---18 | 2--1 | 0.15072 | 4 | 100% | 1.2651 | 4.138% | 85.16% | 10.71% | 0.002591 | 0 | 0 | 0.002591 | 0 | 0.0023578 | 0.14854 | 0.015873 | 0.0023578 | 0.14854 | 0.015873 | 0.0026165 | 0.16483 | 0.015873 | 0.2048% | 0.011135 | 0.010584 | 113.6153 | 0.81972 | 89.1208 | 23.6748 | 119.2873 | 0 | 0 | 119.2873 | 8.544e-08%
2027 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 7.7195 | 976 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 171.9679 | 7.6076 | 22.6048 | 171.9679 | 7.6076 | 22.6048 | 190.8359 | 8.4423 | 22.6048 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2027 | 482 | 482-382F | Tier-1 | Non-HFTD---15 | 2--2 | 2.7703 | 50 | 100% | 4.259 | 56.74% | 0% | 43.26% | 0.11962 | 0 | 0 | 0.11962 | 0 | 0.10885 | 2.7301 | 0.039871 | 0.10885 | 2.7301 | 0.039871 | 0.12079 | 3.0296 | 0.039871 | 2.809% | 0.0074466 | 0.007078 | 571.9423 | 0.18618 | 346.992 | 224.7641 | 584.8278 | 0 | 0 | 584.8278 | 3.945e-06%
2027 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | 2--4 | 1.7013 | 9 | 100% | 70.6534 | 98.66% | 0% | 1.337% | 3.4506 | 0 | 0 | 3.4506 | 0 | 3.14 | 1.6767 | 1.8728 | 3.14 | 1.6767 | 1.8728 | 3.4845 | 1.8606 | 1.8728 | 4.884% | 0.0070442 | 0.0066955 | 10030.0143 | 2447.2684 | 423.376 | 7159.37 | 10036.9961 | 0 | 0 | 10036.9961 | 0.0001138%
2027 | SK1 | CB SK1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.026705 | 0 | 100% | 0.041248 | 11.22% | 0% | 88.78% | 0.00022901 | 0 | 0 | 0.00022901 | 0 | 0.00020839 | 0.026317 | 0.0079185 | 0.00020839 | 0.026317 | 0.0079185 | 0.00023126 | 0.029205 | 0.0079185 | 0.5552% | 0.0001128 | 0.00010722 | 365.6737 | 6.7467 | 30.4931 | 328.4339 | 382.5813 | 0 | 0 | 382.5813 | 7.552e-09%
2027 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 20.7013 | 1682 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1269.1144 | 20.4012 | 62.208 | 1269.1144 | 20.4012 | 62.208 | 1408.3587 | 22.6395 | 62.208 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2027 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 7.4915 | 117 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 162.7089 | 7.3829 | 22.0387 | 162.7089 | 7.3829 | 22.0387 | 180.561 | 8.1929 | 22.0387 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2027 | 140 | 140-496 | Tier-1 | Non-HFTD---5 | 3--4 | 2.3094 | 156 | 100% | 76.0759 | 10.21% | 86.85% | 2.935% | 0.38454 | 0 | 0 | 0.38454 | 0 | 0.34993 | 2.2759 | 0.15375 | 0.34993 | 2.2759 | 0.15375 | 0.38832 | 2.5256 | 0.15375 | 0.5055% | 0.01454 | 0.01382 | 5232.251 | 43.4645 | 4467.4961 | 721.2904 | 5476.9106 | 0 | 0 | 5476.9106 | 1.268e-05%
2027 | 462 | 462-1035F | Tier-1 | Non-HFTD---19 | 1--2 | 0.022159 | 4 | 100% | 0.24779 | 73.53% | 0% | 26.47% | 0.0090189 | 0 | 0 | 0.0090189 | 0 | 0.0082071 | 0.021838 | 0.37582 | 0.0082071 | 0.021838 | 0.37582 | 0.0091076 | 0.024234 | 0.37582 | 3.64% | 0.0001494 | 0.000142 | 1658.5735 | 0.33035 | 1259.4318 | 398.8113 | 1681.4368 | 0 | 0 | 1681.4368 | 2.974e-07%
2027 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 3.9252 | 376 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 181.9416 | 3.8683 | 47.034 | 181.9416 | 3.8683 | 47.034 | 201.9038 | 4.2927 | 47.034 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2027 | 911 | CB 911 | Tier-2 | Tier-2---14 | 1--5 | 0.9375 | 47 | 100% | 193.6033 | 99.75% | 0% | 0.253% | 9.5591 | 0 | 0 | 9.5591 | 0 | 8.6987 | 0.92391 | 9.4151 | 8.6987 | 0.92391 | 9.4151 | 9.6531 | 1.0253 | 9.4151 | 4.937% | 0.0040632 | 0.0038621 | 47647.9856 | 7461.2719 | 1706.7058 | 38480.0078 | 47654.2641 | 0 | 0 | 47654.2641 | 0.0003152%
2027 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 2.7653 | 360 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 127.1099 | 2.7252 | 46.6416 | 127.1099 | 2.7252 | 46.6416 | 141.0561 | 3.0243 | 46.6416 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2027 | 516 | 516-7F | Tier-1 | Non-HFTD---19 | 1--1 | 0.27315 | 23 | 100% | 0.35341 | 11.58% | 0% | 88.42% | 0.0020258 | 0 | 0 | 0.0020258 | 0 | 0.0018434 | 0.26919 | 0.006848 | 0.0018434 | 0.26919 | 0.006848 | 0.0020457 | 0.29872 | 0.006848 | 0.5732% | 0.0009896 | 0.00094061 | 357.1201 | 0.2376 | 70.0389 | 286.8436 | 373.5645 | 0 | 0 | 373.5645 | 6.68e-08%
2027 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 7.6936 | 531 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 90.5939 | 7.582 | 11.9485 | 90.5939 | 7.582 | 11.9485 | 100.5337 | 8.4139 | 11.9485 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2027 | 330 | 330-8R | Tier-1 | Non-HFTD---2 | 4--4 | 9.8311 | 664 | 100% | 217.2506 | 11.57% | 85.07% | 3.362% | 1.2444 | 0 | 0 | 1.2444 | 0 | 1.1324 | 9.6885 | 0.11688 | 1.1324 | 9.6885 | 0.11688 | 1.2567 | 10.7515 | 0.11688 | 0.5728% | 0.044939 | 0.042715 | 4834.3005 | 5.4086 | 4300.9723 | 527.9196 | 5056.9268 | 0 | 0 | 5056.9268 | 4.104e-05%
2027 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 14.6036 | 803 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 58.3792 | 14.3919 | 4.0564 | 58.3792 | 14.3919 | 4.0564 | 64.7844 | 15.971 | 4.0564 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2027 | 329 | 329-793F | Tier-1 | Non-HFTD---14 | 3--1 | 0.54544 | 10 | 100% | 8.6222 | 27.32% | 66.37% | 6.318% | 0.11658 | 0 | 0 | 0.11658 | 0 | 0.10609 | 0.53753 | 0.19736 | 0.10609 | 0.53753 | 0.19736 | 0.11773 | 0.59651 | 0.19736 | 1.352% | 0.019245 | 0.018293 | 448.0142 | 14.326 | 282.864 | 150.8242 | 464.9726 | 0 | 0 | 464.9726 | 3.845e-06%
2027 | 90 | 90-49 | Tier-1 | Non-HFTD---11 | 2--3 | 0.38809 | 7 | 100% | 11.9536 | 0.3922% | 96.08% | 3.526% | 0.0023207 | 0 | 0 | 0.0023207 | 0 | 0.0021118 | 0.38246 | 0.0055216 | 0.0021118 | 0.38246 | 0.0055216 | 0.0023435 | 0.42443 | 0.0055216 | 0.01941% | 0.0065452 | 0.0062212 | 1826.3158 | 2.1347 | 1619.3491 | 204.832 | 1921.0534 | 0 | 0 | 1921.0534 | 7.653e-08%
2027 | 702 | 702-448F | Tier-1 | Non-HFTD---19 | 1--3 | 0.029545 | 0 | 100% | 0.36733 | 90.03% | 0% | 9.967% | 0.016371 | 0 | 0 | 0.016371 | 0 | 0.014897 | 0.029117 | 0.51163 | 0.014897 | 0.029117 | 0.51163 | 0.016532 | 0.032312 | 0.51163 | 4.457% | 0.0001214 | 0.00011539 | 3025.8156 | 1.795 | 2741.9742 | 282.0463 | 3041.5218 | 0 | 0 | 3041.5218 | 5.398e-07%
2027 | 151 | CB 151 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8715 | 54 | 100% | 3.6088 | 37.51% | 0% | 62.49% | 0.067008 | 0 | 0 | 0.067008 | 0 | 0.060976 | 2.8299 | 0.021547 | 0.060976 | 2.8299 | 0.021547 | 0.067666 | 3.1404 | 0.021547 | 1.857% | 0.0086214 | 0.0081946 | 418.5864 | 20.5993 | 55.0518 | 342.9354 | 432.2085 | 0 | 0 | 432.2085 | 2.21e-06%
2027 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 1.1019 | 43 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 24.5074 | 1.0859 | 22.5684 | 24.5074 | 1.0859 | 22.5684 | 27.1963 | 1.2051 | 22.5684 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2027 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.11723 | 0 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 15.0487 | 0.11554 | 130.2523 | 15.0487 | 0.11554 | 130.2523 | 16.6998 | 0.12821 | 130.2523 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2027 | 136 | CB 136 | Tier-1 | Non-HFTD---11 | 2--2 | 3.5625 | 63 | 100% | 14.7465 | 75.99% | 0% | 24.01% | 0.55467 | 0 | 0 | 0.55467 | 0 | 0.50474 | 3.5109 | 0.14377 | 0.50474 | 3.5109 | 0.14377 | 0.56012 | 3.8961 | 0.14377 | 3.761% | 0.012814 | 0.012179 | 1150.8466 | 68.1179 | 481.9548 | 600.7739 | 1165.2384 | 0 | 0 | 1165.2384 | 1.829e-05%
2027 | AG1 | CB AG1 | Tier-1 | Non-HFTD---6 | 3--3 | 2.6702 | 142 | 100% | 54.2692 | 2.264% | 94.2% | 3.533% | 0.060827 | 0 | 0 | 0.060827 | 0 | 0.055352 | 2.6315 | 0.021034 | 0.055352 | 2.6315 | 0.021034 | 0.061425 | 2.9202 | 0.021034 | 0.1121% | 0.01771 | 0.016834 | 3064.2572 | 3.3404 | 2723.0059 | 337.911 | 3220.2238 | 0 | 0 | 3220.2238 | 2.006e-06%
2027 | 58 | 58-110F | Tier-1 | Non-HFTD---3 | 4--3 | 6.2108 | 237 | 100% | 93.5151 | 11.61% | 83.8% | 4.592% | 0.53721 | 0 | 0 | 0.53721 | 0 | 0.48886 | 6.1208 | 0.079869 | 0.48886 | 6.1208 | 0.079869 | 0.54249 | 6.7923 | 0.079869 | 0.5745% | 0.033104 | 0.031465 | 2824.9053 | 53.6585 | 2259.5047 | 511.7421 | 2954.947 | 0 | 0 | 2954.947 | 1.772e-05%
2027 | 53 | CB 53 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2979 | 50 | 100% | 0.88951 | 10.17% | 0% | 89.83% | 0.0044771 | 0 | 0 | 0.0044771 | 0 | 0.0040741 | 1.2791 | 0.0031852 | 0.0040741 | 1.2791 | 0.0031852 | 0.0045211 | 1.4194 | 0.0031852 | 0.5033% | 0.0032354 | 0.0030752 | 274.9306 | 0.18584 | 50.3908 | 224.354 | 287.7926 | 0 | 0 | 287.7926 | 1.476e-07%
2027 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | 2--3 | 2.0286 | 23 | 100% | 14.0801 | 87.11% | 0% | 12.89% | 0.60712 | 0 | 0 | 0.60712 | 0 | 0.55247 | 1.9992 | 0.27635 | 0.55247 | 1.9992 | 0.27635 | 0.61309 | 2.2185 | 0.27635 | 4.312% | 0.0077936 | 0.0074078 | 1806.6243 | 178.7989 | 575.1368 | 1052.6887 | 1818.7529 | 0 | 0 | 1818.7529 | 2.002e-05%
2027 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 12.622 | 987 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1051.3816 | 12.439 | 84.5231 | 1051.3816 | 12.439 | 84.5231 | 1166.7367 | 13.8038 | 84.5231 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2027 | 242 | 242-1413F | Tier-1 | Non-HFTD---2 | 5--3 | 1.8794 | 86 | 100% | 367.3537 | 8.271% | 91.36% | 0.3661% | 1.5041 | 0 | 0 | 1.5041 | 0 | 1.3687 | 1.8521 | 0.73899 | 1.3687 | 1.8521 | 0.73899 | 1.5188 | 2.0553 | 0.73899 | 0.4094% | 0.10056 | 0.095586 | 3652.9198 | 53.8188 | 2967.9065 | 631.1945 | 3827.4209 | 0 | 0 | 3827.4209 | 4.96e-05%
2027 | 186 | CB 186 | Tier-1 | Non-HFTD---5 | 3--4 | 4.111 | 213 | 100% | 92.3894 | 96.63% | 0% | 3.367% | 4.4193 | 0 | 0 | 4.4193 | 0 | 4.0215 | 4.0514 | 0.99262 | 4.0215 | 4.0514 | 0.99262 | 4.4627 | 4.4959 | 0.99262 | 4.783% | 0.015082 | 0.014336 | 6125.6456 | 905.7849 | 2088.3006 | 3131.5601 | 6136.3851 | 0 | 0 | 6136.3851 | 0.0001457%
2027 | 570 | 570-491F | Tier-1 | Non-HFTD---20 | 1--1 | 0.70831 | 56 | 100% | 0.50055 | 7.694% | 0% | 92.31% | 0.0019065 | 0 | 0 | 0.0019065 | 0 | 0.0017349 | 0.69804 | 0.0024854 | 0.0017349 | 0.69804 | 0.0024854 | 0.0019252 | 0.77463 | 0.0024854 | 0.3809% | 0.001908 | 0.0018136 | 262.3439 | 0.27517 | 41.617 | 220.4517 | 274.9549 | 0 | 0 | 274.9549 | 6.287e-08%
2027 | 546 | CB 546 | Tier-1 | Non-HFTD---1 | 4--4 | 7.344 | 174 | 100% | 334.1605 | 5.89% | 92.51% | 1.604% | 0.97427 | 0 | 0 | 0.97427 | 0 | 0.88657 | 7.2375 | 0.1225 | 0.88657 | 7.2375 | 0.1225 | 0.98385 | 8.0316 | 0.1225 | 0.2916% | 0.030456 | 0.028948 | 10971.9113 | 11.4011 | 9971.8641 | 988.6462 | 11509.6495 | 0 | 0 | 11509.6495 | 3.213e-05%
2027 | EOS1 | CB EOS1 | Tier-1 | Non-HFTD---6 | 4--2 | 17.8417 | 865 | 100% | 70.9236 | 82.85% | 0% | 17.15% | 2.9086 | 0 | 0 | 2.9086 | 0 | 2.6467 | 17.583 | 0.15053 | 2.6467 | 17.583 | 0.15053 | 2.9371 | 19.5121 | 0.15053 | 4.101% | 0.050825 | 0.048309 | 1395.4534 | 210.0698 | 229.3399 | 956.0438 | 1407.9183 | 0 | 0 | 1407.9183 | 9.591e-05%
2027 | 515 | 515-49R | Tier-1 | Non-HFTD---17 | 1--2 | 0.3564 | 2 | 100% | 0.93866 | 50.3% | 0% | 49.7% | 0.023373 | 0 | 0 | 0.023373 | 0 | 0.021269 | 0.35124 | 0.060555 | 0.021269 | 0.35124 | 0.060555 | 0.023603 | 0.38977 | 0.060555 | 2.49% | 0.0014364 | 0.0013653 | 653.4775 | 1.8578 | 348.3582 | 303.2615 | 670.3899 | 0 | 0 | 670.3899 | 7.708e-07%
2027 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 6.3703 | 516 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 644.9047 | 6.2779 | 102.7255 | 644.9047 | 6.2779 | 102.7255 | 715.6622 | 6.9667 | 102.7255 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2027 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | 5--4 | 1.3333 | 233 | 100% | 1005.6854 | 94.09% | 5.81% | 0.1042% | 46.8371 | 0 | 0 | 46.8371 | 0 | 42.6211 | 1.314 | 32.4361 | 42.6211 | 1.314 | 32.4361 | 47.2974 | 1.4582 | 32.4361 | 4.657% | 0.097832 | 0.09299 | 10279.6968 | 1573.4563 | 574.8933 | 8131.3471 | 10311.3601 | 0 | 0 | 10311.3601 | 0.001545%
2027 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 20.3065 | 1258 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 176.6226 | 20.012 | 8.8258 | 176.6226 | 20.012 | 8.8258 | 196.0012 | 22.2077 | 8.8258 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2027 | 76 | 76-272 | Tier-1 | Non-HFTD---15 | 1--2 | 1.5693 | 60 | 100% | 2.4692 | 55.93% | 0% | 44.07% | 0.068363 | 0 | 0 | 0.068363 | 0 | 0.06221 | 1.5465 | 0.040226 | 0.06221 | 1.5465 | 0.040226 | 0.069035 | 1.7162 | 0.040226 | 2.769% | 0.0043474 | 0.0041322 | 567.9648 | 0.63038 | 337.7103 | 229.6241 | 580.9991 | 0 | 0 | 580.9991 | 2.254e-06%
2027 | 65 | CB 65 | Tier-1 | Non-HFTD---2 | 3--4 | 6.2999 | 644 | 100% | 189.2656 | 62.06% | 35.57% | 2.376% | 5.814 | 0 | 0 | 5.814 | 0 | 5.2907 | 6.2085 | 0.85216 | 5.2907 | 6.2085 | 0.85216 | 5.8711 | 6.8897 | 0.85216 | 3.072% | 0.027671 | 0.026302 | 6839.7543 | 634.4467 | 2950.5287 | 3254.7788 | 6974.9036 | 0 | 0 | 6974.9036 | 0.0001917%
2027 | 374 | CB 374 | Tier-1 | Non-HFTD---8 | 4--2 | 13.2841 | 373 | 100% | 28.091 | 64.57% | 0% | 35.43% | 0.89782 | 0 | 0 | 0.89782 | 0 | 0.817 | 13.0915 | 0.062407 | 0.817 | 13.0915 | 0.062407 | 0.90664 | 14.5278 | 0.062407 | 3.196% | 0.037158 | 0.035318 | 755.9952 | 0.21604 | 512.3714 | 243.4078 | 769.9451 | 0 | 0 | 769.9451 | 2.961e-05%
2027 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 2.6388 | 132 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 7.8263 | 2.6005 | 3.0095 | 7.8263 | 2.6005 | 3.0095 | 8.685 | 2.8859 | 3.0095 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2027 | 703 | 703-279R | Tier-1 | Non-HFTD---2 | 4--4 | 8.8328 | 321 | 100% | 201.9742 | 33.23% | 63.5% | 3.273% | 3.3219 | 0 | 0 | 3.3219 | 0 | 3.0229 | 8.7047 | 0.34727 | 3.0229 | 8.7047 | 0.34727 | 3.3545 | 9.6598 | 0.34727 | 1.645% | 0.030988 | 0.029454 | 6517.9035 | 105.9052 | 5595.0681 | 816.9302 | 6744.5585 | 0 | 0 | 6744.5585 | 0.0001095%
2027 | 274 | CB 274 | Tier-1 | Non-HFTD---4 | 3--4 | 0.089394 | 2 | 100% | 104.8089 | 0.2793% | 99.62% | 0.1033% | 0.014491 | 0 | 0 | 0.014491 | 0 | 0.013187 | 0.088098 | 0.14968 | 0.013187 | 0.088098 | 0.14968 | 0.014633 | 0.097764 | 0.14968 | 0.01383% | 0.014981 | 0.014239 | 6996.2133 | 9.5886 | 6367.3875 | 619.2371 | 7359.5434 | 0 | 0 | 7359.5434 | 4.779e-07%
2027 | 51 | 51-861R | Tier-1 | Non-HFTD---16 | 2--1 | 3.5 | 123 | 100% | 2.9058 | 18.9% | 0% | 81.1% | 0.027191 | 0 | 0 | 0.027191 | 0 | 0.024744 | 3.4493 | 0.0071736 | 0.024744 | 3.4493 | 0.0071736 | 0.027458 | 3.8277 | 0.0071736 | 0.9358% | 0.0093474 | 0.0088847 | 310.8674 | 0.1897 | 81.668 | 229.0098 | 323.9963 | 0 | 0 | 323.9963 | 8.967e-07%
2027 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 23.0074 | 900 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 75.7062 | 22.6738 | 3.3389 | 75.7062 | 22.6738 | 3.3389 | 84.0125 | 25.1615 | 3.3389 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2027 | 454 | CB 454 | Tier-1 | Non-HFTD---11 | 3--2 | 5.108 | 105 | 100% | 14.4703 | 77.76% | 0% | 22.24% | 0.557 | 0 | 0 | 0.557 | 0 | 0.50686 | 5.0339 | 0.10069 | 0.50686 | 5.0339 | 0.10069 | 0.56248 | 5.5862 | 0.10069 | 3.849% | 0.014027 | 0.013332 | 1031.6351 | 0.20077 | 822.8982 | 208.5361 | 1043.582 | 0 | 0 | 1043.582 | 1.837e-05%
2027 | 761 | CB 761 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3415 | 77 | 100% | 36.3819 | 95.87% | 0% | 4.131% | 1.7265 | 0 | 0 | 1.7265 | 0 | 1.5711 | 2.3075 | 0.68086 | 1.5711 | 2.3075 | 0.68086 | 1.7435 | 2.5607 | 0.68086 | 4.746% | 0.0090226 | 0.008576 | 4032.309 | 532.6165 | 590.1313 | 2909.5613 | 4040.9834 | 0 | 0 | 4040.9834 | 5.693e-05%
2027 | 209 | 209-660R | Tier-1 | Non-HFTD---13 | 1--3 | 0.73613 | 58 | 100% | 6.8017 | 90.67% | 0% | 9.327% | 0.30528 | 0 | 0 | 0.30528 | 0 | 0.2778 | 0.72545 | 0.38294 | 0.2778 | 0.72545 | 0.38294 | 0.30828 | 0.80505 | 0.38294 | 4.488% | 0.0025076 | 0.0023835 | 2712.4478 | 81.1565 | 1987.9733 | 643.318 | 2725.6234 | 0 | 0 | 2725.6234 | 1.007e-05%
2027 | 400 | 400-1019 | Tier-1 | Non-HFTD---12 | 4--1 | 14.5055 | 252 | 100% | 13.8376 | 46.13% | 0% | 53.87% | 0.31594 | 0 | 0 | 0.31594 | 0 | 0.2875 | 14.2952 | 0.020112 | 0.2875 | 14.2952 | 0.020112 | 0.31904 | 15.8636 | 0.020112 | 2.283% | 0.036477 | 0.034671 | 379.3524 | 0.8422 | 189.3108 | 189.1995 | 389.9959 | 0 | 0 | 389.9959 | 1.042e-05%
2027 | 545 | 545-50F | Tier-1 | Non-HFTD---4 | 3--4 | 3.0186 | 22 | 100% | 135.8264 | 1.065% | 96.96% | 1.972% | 0.071585 | 0 | 0 | 0.071585 | 0 | 0.065142 | 2.9748 | 0.021898 | 0.065142 | 2.9748 | 0.021898 | 0.072289 | 3.3012 | 0.021898 | 0.0527% | 0.019507 | 0.018541 | 6963.0284 | 7.5673 | 6209.716 | 745.7451 | 7321.7871 | 0 | 0 | 7321.7871 | 2.361e-06%
2027 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 17.8147 | 1731 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 387.1481 | 17.5564 | 22.0516 | 387.1481 | 17.5564 | 22.0516 | 429.6251 | 19.4827 | 22.0516 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2027 | GN1 | CB GN1 | Tier-1 | Non-HFTD---6 | 3--3 | 4.8692 | 151 | 100% | 90.3459 | 4.418% | 91.44% | 4.142% | 0.1976 | 0 | 0 | 0.1976 | 0 | 0.17981 | 4.7986 | 0.037472 | 0.17981 | 4.7986 | 0.037472 | 0.19954 | 5.325 | 0.037472 | 0.2187% | 0.024571 | 0.023355 | 3676.9336 | 12.2101 | 3193.0279 | 471.6956 | 3859.9596 | 0 | 0 | 3859.9596 | 6.516e-06%
2027 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 1.6021 | 38 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 27.2363 | 1.5789 | 17.2507 | 27.2363 | 1.5789 | 17.2507 | 30.2246 | 1.7521 | 17.2507 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2027 | 511 | CB 511 | Tier-1 | Non-HFTD---4 | 3--4 | 2.4116 | 87 | 100% | 163.9412 | 95.95% | 3.193% | 0.8556% | 7.7866 | 0 | 0 | 7.7866 | 0 | 7.0857 | 2.3766 | 2.9814 | 7.0857 | 2.3766 | 2.9814 | 7.8631 | 2.6373 | 2.9814 | 4.75% | 0.019336 | 0.018379 | 8478.4598 | 1002.8854 | 2208.1517 | 5267.4227 | 8496.3346 | 0 | 0 | 8496.3346 | 0.0002568%
2027 | 403 | 403-15F | Tier-1 | Non-HFTD---17 | 1--2 | 0.21288 | 44 | 100% | 1.6081 | 91.84% | 0% | 8.156% | 0.073108 | 0 | 0 | 0.073108 | 0 | 0.066527 | 0.20979 | 0.31711 | 0.066527 | 0.20979 | 0.31711 | 0.073826 | 0.23281 | 0.31711 | 4.546% | 0.001071 | 0.001018 | 1501.4701 | 224.8932 | 11.1242 | 1265.4527 | 1507.8474 | 0 | 0 | 1507.8474 | 2.411e-06%
2027 | 155 | 155-1236R | Tier-1 | Non-HFTD---8 | 2--3 | 4.1822 | 117 | 100% | 27.9773 | 89.48% | 0% | 10.52% | 1.2392 | 0 | 0 | 1.2392 | 0 | 1.1276 | 4.1216 | 0.27359 | 1.1276 | 4.1216 | 0.27359 | 1.2513 | 4.5738 | 0.27359 | 4.429% | 0.01302 | 0.012376 | 2148.7604 | 291.0687 | 669.5809 | 1188.1108 | 2160.534 | 0 | 0 | 2160.534 | 4.086e-05%
2027 | 52 | 52-16F | Tier-1 | Non-HFTD---19 | 1--1 | 0.61587 | 22 | 100% | 0.6475 | 11.64% | 0% | 88.36% | 0.0037321 | 0 | 0 | 0.0037321 | 0 | 0.0033961 | 0.60694 | 0.0055955 | 0.0033961 | 0.60694 | 0.0055955 | 0.0037688 | 0.67353 | 0.0055955 | 0.5764% | 0.001922 | 0.0018269 | 336.889 | 0.24654 | 66.1207 | 270.5218 | 352.3906 | 0 | 0 | 352.3906 | 1.231e-07%
2027 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 5.4023 | 497 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 48.5092 | 5.3239 | 9.1115 | 48.5092 | 5.3239 | 9.1115 | 53.8315 | 5.9081 | 9.1115 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2027 | 857 | 857-60 | Tier-1 | Non-HFTD---11 | 1--4 | 0.99317 | 41 | 100% | 13.5992 | 95.18% | 0% | 4.819% | 0.64072 | 0 | 0 | 0.64072 | 0 | 0.58305 | 0.97877 | 0.59569 | 0.58305 | 0.97877 | 0.59569 | 0.64702 | 1.0862 | 0.59569 | 4.711% | 0.0028286 | 0.0026886 | 4807.7559 | 729.0888 | 145.8859 | 3932.7813 | 4819.8226 | 0 | 0 | 4819.8226 | 2.113e-05%
2027 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 17.4555 | 1680 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 808.0402 | 17.2024 | 46.9725 | 808.0402 | 17.2024 | 46.9725 | 896.6965 | 19.0898 | 46.9725 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2027 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 3.42 | 209 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 28.5327 | 3.3704 | 8.4656 | 28.5327 | 3.3704 | 8.4656 | 31.6632 | 3.7402 | 8.4656 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2027 | 553 | CB 553 | Tier-1 | Non-HFTD---5 | 2--3 | 3.1561 | 136 | 100% | 49.0638 | 94.65% | 0% | 5.347% | 2.2988 | 0 | 0 | 2.2988 | 0 | 2.0919 | 3.1103 | 0.67256 | 2.0919 | 3.1103 | 0.67256 | 2.3214 | 3.4516 | 0.67256 | 4.685% | 0.011308 | 0.010749 | 4338.7071 | 494.3233 | 1109.1201 | 2735.2637 | 4350.7882 | 0 | 0 | 4350.7882 | 7.581e-05%
2027 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 11.9254 | 907 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 250.5037 | 11.7524 | 21.315 | 250.5037 | 11.7524 | 21.315 | 277.9884 | 13.0419 | 21.315 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2027 | 1047 | 1047-35F | Tier-1 | Non-HFTD---15 | 1--2 | 1.687 | 51 | 100% | 2.3448 | 49.08% | 0% | 50.92% | 0.056963 | 0 | 0 | 0.056963 | 0 | 0.051835 | 1.6625 | 0.031179 | 0.051835 | 1.6625 | 0.031179 | 0.057523 | 1.8449 | 0.031179 | 2.429% | 0.004654 | 0.0044236 | 503.8208 | 0.79361 | 266.8776 | 236.1496 | 517.1817 | 0 | 0 | 517.1817 | 1.878e-06%
2027 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 12.6807 | 909 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 155.9371 | 12.4969 | 12.4781 | 155.9371 | 12.4969 | 12.4781 | 173.0461 | 13.868 | 12.4781 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2027 | 450 | 450-50R | Tier-2 | Tier-2---11 | 4--4 | 0.51918 | 36 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 8.6479 | 0 | 0 | 8.6479 | 0 | 7.8695 | 0.51165 | 15.3806 | 7.8695 | 0.51165 | 15.3806 | 8.7329 | 0.56779 | 15.3806 | 1.61% | 0.071801 | 0.068247 | 7480.0024 | 403.5755 | 4618.5943 | 2457.8325 | 7742.8291 | 0 | 0 | 7742.8291 | 0.0002852%
2027 | 85 | 85-498F | Tier-1 | Non-HFTD---13 | 1--3 | 0.76871 | 66 | 100% | 5.1045 | 87.99% | 0% | 12.01% | 0.22234 | 0 | 0 | 0.22234 | 0 | 0.20232 | 0.75756 | 0.26707 | 0.20232 | 0.75756 | 0.26707 | 0.22452 | 0.84068 | 0.26707 | 4.356% | 0.002808 | 0.002669 | 1817.8549 | 381.7426 | 31.0024 | 1405.1099 | 1829.2212 | 0 | 0 | 1829.2212 | 7.332e-06%
2027 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.075568 | 0 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 8.6384 | 0.074473 | 115.9939 | 8.6384 | 0.074473 | 115.9939 | 9.5861 | 0.082643 | 115.9939 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2027 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 2.1594 | 50 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 23.951 | 2.1281 | 11.2545 | 23.951 | 2.1281 | 11.2545 | 26.5789 | 2.3616 | 11.2545 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2027 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 10.6674 | 427 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 892.989 | 10.5127 | 84.9436 | 892.989 | 10.5127 | 84.9436 | 990.9657 | 11.6662 | 84.9436 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2027 | RD1 | CB RD1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.1822 | 221 | 100% | 3.8065 | 31.86% | 0% | 68.14% | 0.060024 | 0 | 0 | 0.060024 | 0 | 0.054621 | 3.1361 | 0.017417 | 0.054621 | 3.1361 | 0.017417 | 0.060614 | 3.4802 | 0.017417 | 1.577% | 0.009563 | 0.0090896 | 398.0431 | 3.9878 | 128.2654 | 265.7899 | 412.1688 | 0 | 0 | 412.1688 | 1.979e-06%
2027 | 64 | 64-14F | Tier-1 | Non-HFTD---3 | 4--3 | 8.9328 | 168 | 100% | 111.7051 | 4.553% | 91.33% | 4.117% | 0.25173 | 0 | 0 | 0.25173 | 0 | 0.22907 | 8.8033 | 0.026021 | 0.22907 | 8.8033 | 0.026021 | 0.25421 | 9.7692 | 0.026021 | 0.2254% | 0.030765 | 0.029242 | 3630.8929 | 16.1011 | 3147.9882 | 466.8035 | 3811.3735 | 0 | 0 | 3811.3735 | 8.301e-06%
2027 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 3.4333 | 108 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 16.4392 | 3.3835 | 4.8586 | 16.4392 | 3.3835 | 4.8586 | 18.2429 | 3.7548 | 4.8586 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2027 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 24.3072 | 930 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 749.3113 | 23.9547 | 31.2803 | 749.3113 | 23.9547 | 31.2803 | 831.524 | 26.583 | 31.2803 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2027 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 11.8164 | 264 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 53.1821 | 11.6451 | 4.5669 | 53.1821 | 11.6451 | 4.5669 | 59.0171 | 12.9228 | 4.5669 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2027 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 9.7066 | 444 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 654.899 | 9.5659 | 68.462 | 654.899 | 9.5659 | 68.462 | 726.7529 | 10.6154 | 68.462 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2027 | 410 | 410-50R | Tier-1 | Non-HFTD---1 | 4--5 | 11.9653 | 1104 | 100% | 1314.3326 | 99.38% | 0% | 0.6151% | 64.6593 | 0 | 0 | 64.6593 | 0 | 58.8391 | 11.7918 | 4.9898 | 58.8391 | 11.7918 | 4.9898 | 65.2948 | 13.0856 | 4.9898 | 4.92% | 0.044038 | 0.041858 | 29845.69 | 7721.7282 | 133.8501 | 21990.1116 | 29855.2499 | 0 | 0 | 29855.2499 | 0.002132%
2027 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 6.4307 | 367 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 242.1556 | 6.3375 | 38.21 | 242.1556 | 6.3375 | 38.21 | 268.7244 | 7.0328 | 38.21 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2027 | 60 | 60-576F | Tier-1 | Non-HFTD---16 | 2--1 | 2.3228 | 78 | 100% | 2.6375 | 57.75% | 0% | 42.25% | 0.075392 | 0 | 0 | 0.075392 | 0 | 0.068606 | 2.2891 | 0.029971 | 0.068606 | 2.2891 | 0.029971 | 0.076133 | 2.5402 | 0.029971 | 2.858% | 0.0059106 | 0.005618 | 446.2382 | 1.1181 | 268.8191 | 176.301 | 456.0577 | 0 | 0 | 456.0577 | 2.486e-06%
2027 | 516 | 516-5F | Tier-1 | Non-HFTD---18 | 1--1 | 1.126 | 37 | 100% | 1.2452 | 18.96% | 0% | 81.04% | 0.011684 | 0 | 0 | 0.011684 | 0 | 0.010632 | 1.1096 | 0.0095814 | 0.010632 | 1.1096 | 0.0095814 | 0.011798 | 1.2314 | 0.0095814 | 0.9383% | 0.0037102 | 0.0035265 | 335.6145 | 0.20467 | 88.3256 | 247.0843 | 349.7795 | 0 | 0 | 349.7795 | 3.853e-07%
2027 | 276 | 276-228 | Tier-1 | Non-HFTD---2 | 4--3 | 17.7437 | 786 | 100% | 290.9914 | 11.65% | 84% | 4.346% | 1.6788 | 0 | 0 | 1.6788 | 0 | 1.5277 | 17.4865 | 0.087363 | 1.5277 | 17.4865 | 0.087363 | 1.6953 | 19.405 | 0.087363 | 0.5769% | 0.065634 | 0.062385 | 4433.5468 | 54.5858 | 3672.1531 | 706.8079 | 4637.5265 | 0 | 0 | 4637.5265 | 5.536e-05%
2027 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 2.7701 | 39 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 30.6647 | 2.7299 | 11.2329 | 30.6647 | 2.7299 | 11.2329 | 34.0291 | 3.0294 | 11.2329 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2027 | 141 | CB 141 | Tier-1 | Non-HFTD---13 | 2--2 | 0.62292 | 9 | 100% | 7.7413 | 92.75% | 0.6935% | 6.554% | 0.35542 | 0 | 0 | 0.35542 | 0 | 0.32343 | 0.61388 | 0.52686 | 0.32343 | 0.61388 | 0.52686 | 0.35892 | 0.68124 | 0.52686 | 4.591% | 0.0076852 | 0.0073048 | 1007.3001 | 119.4264 | 208.7958 | 679.0778 | 1011.1018 | 0 | 0 | 1011.1018 | 1.172e-05%
2027 | 160 | 160-20R | Tier-1 | Non-HFTD---10 | 3--2 | 5.9633 | 134 | 100% | 17.1087 | 69.24% | 0% | 30.76% | 0.58642 | 0 | 0 | 0.58642 | 0 | 0.53363 | 5.8768 | 0.090803 | 0.53363 | 5.8768 | 0.090803 | 0.59218 | 6.5216 | 0.090803 | 3.428% | 0.018715 | 0.017789 | 914.1502 | 3.7049 | 637.1365 | 273.3088 | 928.792 | 0 | 0 | 928.792 | 1.934e-05%
2027 | 730 | 730-835 | Tier-1 | Non-HFTD---6 | 3--3 | 4.7612 | 180 | 100% | 55.2599 | 94.32% | 0% | 5.676% | 2.5801 | 0 | 0 | 2.5801 | 0 | 2.3479 | 4.6922 | 0.50038 | 2.3479 | 4.6922 | 0.50038 | 2.6055 | 5.207 | 0.50038 | 4.669% | 0.01382 | 0.013136 | 3998.6627 | 454.843 | 1618.098 | 1925.7217 | 4010.4832 | 0 | 0 | 4010.4832 | 8.508e-05%
2027 | 378 | CB 378 | Tier-1 | Non-HFTD---18 | 1--1 | 0.98752 | 1 | 100% | 1.1196 | 10.82% | 0% | 89.18% | 0.0059945 | 0 | 0 | 0.0059945 | 0 | 0.0054549 | 0.97321 | 0.0056051 | 0.0054549 | 0.97321 | 0.0056051 | 0.0060534 | 1.08 | 0.0056051 | 0.5354% | 0.0033556 | 0.0031895 | 333.65 | 5.5607 | 29.9513 | 298.138 | 349.1463 | 0 | 0 | 349.1463 | 1.977e-07%
2027 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.6215 | 0.033783 | 77.5965 | 2.6215 | 0.033783 | 77.5965 | 2.9091 | 0.03749 | 77.5965 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2027 | 409 | CB 409 | Tier-1 | Non-HFTD---8 | 3--2 | 6.5118 | 143 | 100% | 29.0295 | 85.38% | 0% | 14.62% | 1.2269 | 0 | 0 | 1.2269 | 0 | 1.1165 | 6.4174 | 0.17398 | 1.1165 | 6.4174 | 0.17398 | 1.239 | 7.1215 | 0.17398 | 4.226% | 0.017884 | 0.016999 | 1623.1908 | 7.6402 | 1361.7978 | 253.7528 | 1635.548 | 0 | 0 | 1635.548 | 4.046e-05%
2027 | 149 | 149-129R | Tier-1 | Non-HFTD---13 | 2--2 | 0.15038 | 7 | 100% | 5.3596 | 91.52% | 2.339% | 6.145% | 0.24279 | 0 | 0 | 0.24279 | 0 | 0.22094 | 0.1482 | 1.4908 | 0.22094 | 0.1482 | 1.4908 | 0.24518 | 0.16446 | 1.4908 | 4.53% | 0.007042 | 0.0066934 | 761.089 | 113.4886 | 18.657 | 628.9434 | 764.452 | 0 | 0 | 764.452 | 8.006e-06%
2027 | 140 | CB 140 | Tier-1 | Non-HFTD---5 | 3--4 | 3.3106 | 54 | 100% | 74.8313 | 17.08% | 79.52% | 3.4% | 0.63266 | 0 | 0 | 0.63266 | 0 | 0.57571 | 3.2626 | 0.17646 | 0.57571 | 3.2626 | 0.17646 | 0.63888 | 3.6206 | 0.17646 | 0.8455% | 0.014532 | 0.013812 | 5149.556 | 4.4743 | 4651.9396 | 493.1422 | 5371.9295 | 0 | 0 | 5371.9295 | 2.086e-05%
2027 | 296 | CB 296 | Tier-2 | Tier-2---19 | 1--5 | 0.44716 | 96 | 100% | 39.5699 | 99.22% | 0% | 0.7837% | 1.9434 | 0 | 0 | 1.9434 | 0 | 1.7684 | 0.44068 | 4.013 | 1.7684 | 0.44068 | 4.013 | 1.9625 | 0.48903 | 4.013 | 4.911% | 0.0016582 | 0.0015761 | 23863.1595 | 3322.2329 | 3363.4423 | 17177.4843 | 23872.899 | 0 | 0 | 23872.899 | 6.408e-05%
2027 | 172 | CB 172 | Tier-1 | Non-HFTD---8 | 4--2 | 4.7581 | 37 | 100% | 28.3098 | 70.45% | 18.79% | 10.75% | 0.98726 | 0 | 0 | 0.98726 | 0 | 0.8984 | 4.6891 | 0.19159 | 0.8984 | 4.6891 | 0.19159 | 0.99697 | 5.2036 | 0.19159 | 3.487% | 0.048261 | 0.045872 | 586.5969 | 29.8676 | 317.2028 | 239.5265 | 595.6234 | 0 | 0 | 595.6234 | 3.256e-05%
2027 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 20.6063 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 150.1902 | 20.3075 | 7.3958 | 150.1902 | 20.3075 | 7.3958 | 166.6687 | 22.5356 | 7.3958 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2027 | 514 | CB 514 | Tier-1 | Non-HFTD---3 | 4--3 | 20.4863 | 910 | 100% | 180.2752 | 92.03% | 0% | 7.975% | 8.212 | 0 | 0 | 8.212 | 0 | 7.4728 | 20.1893 | 0.37014 | 7.4728 | 20.1893 | 0.37014 | 8.2927 | 22.4044 | 0.37014 | 4.555% | 0.058723 | 0.055816 | 3069.9453 | 628.347 | 399.7755 | 2041.8228 | 3082.6949 | 0 | 0 | 3082.6949 | 0.0002708%
2027 | 48 | CB 48 | Tier-1 | Non-HFTD---18 | 2--1 | 1.5148 | 3 | 100% | 1.5208 | 11.23% | 0% | 88.77% | 0.0084538 | 0 | 0 | 0.0084538 | 0 | 0.0076928 | 1.4929 | 0.0051531 | 0.0076928 | 1.4929 | 0.0051531 | 0.0085369 | 1.6566 | 0.0051531 | 0.5559% | 0.0049642 | 0.0047185 | 306.3449 | 5.7261 | 24.7034 | 275.9155 | 320.507 | 0 | 0 | 320.507 | 2.788e-07%
2027 | 181 | CB 181 | Tier-1 | Non-HFTD---15 | 1--2 | 0.7286 | 20 | 100% | 2.8335 | 82.32% | 0% | 17.68% | 0.11546 | 0 | 0 | 0.11546 | 0 | 0.10507 | 0.71803 | 0.14633 | 0.10507 | 0.71803 | 0.14633 | 0.1166 | 0.79682 | 0.14633 | 4.075% | 0.0024946 | 0.0023711 | 1135.8594 | 18.9687 | 837.4512 | 279.4394 | 1146.3163 | 0 | 0 | 1146.3163 | 3.808e-06%
2027 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 2.6777 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 226.7991 | 2.6389 | 85.9462 | 226.7991 | 2.6389 | 85.9462 | 251.683 | 2.9284 | 85.9462 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2027 | BW1 | CB BW1 | Tier-1 | Non-HFTD---11 | 1--3 | 1.0872 | 45 | 100% | 8.712 | 88.19% | 0% | 11.81% | 0.3803 | 0 | 0 | 0.3803 | 0 | 0.34607 | 1.0714 | 0.32301 | 0.34607 | 1.0714 | 0.32301 | 0.38404 | 1.189 | 0.32301 | 4.365% | 0.0039232 | 0.003729 | 2220.6335 | 316.4948 | 49.7388 | 1854.3999 | 2234.2939 | 0 | 0 | 2234.2939 | 1.254e-05%
2027 | 406 | CB 406 | Tier-1 | Non-HFTD---12 | 3--2 | 5.5205 | 205 | 100% | 8.8138 | 58.69% | 0% | 41.31% | 0.25605 | 0 | 0 | 0.25605 | 0 | 0.233 | 5.4404 | 0.042827 | 0.233 | 5.4404 | 0.042827 | 0.25856 | 6.0373 | 0.042827 | 2.905% | 0.014645 | 0.01392 | 601.8164 | 0.6689 | 372.8417 | 228.3057 | 614.7641 | 0 | 0 | 614.7641 | 8.443e-06%
2027 | 241 | 241-820AE | Tier-1 | Non-HFTD---2 | 5--3 | 3.04 | 97 | 100% | 286.7702 | 14.9% | 84.42% | 0.6786% | 2.1155 | 0 | 0 | 2.1155 | 0 | 1.9251 | 2.9959 | 0.64258 | 1.9251 | 2.9959 | 0.64258 | 2.1363 | 3.3246 | 0.64258 | 0.7377% | 0.10624 | 0.10098 | 2699.1913 | 103.9208 | 2115.2903 | 479.9802 | 2818.8105 | 0 | 0 | 2818.8105 | 6.976e-05%
2027 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 3.4321 | 22 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.9912 | 3.3823 | 2.6583 | 8.9912 | 3.3823 | 2.6583 | 9.9777 | 3.7534 | 2.6583 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2027 | 96 | CB 96 | Tier-1 | Non-HFTD---7 | 2--3 | 0.84791 | 78 | 100% | 37.3393 | 43.85% | 54.05% | 2.092% | 0.81053 | 0 | 0 | 0.81053 | 0 | 0.73757 | 0.83562 | 0.88267 | 0.73757 | 0.83562 | 0.88267 | 0.8185 | 0.9273 | 0.88267 | 2.171% | 0.0084764 | 0.0080568 | 4405.0953 | 227.7051 | 3027.1235 | 1150.2667 | 4533.9014 | 0 | 0 | 4533.9014 | 2.673e-05%
2027 | 145 | 145-633 | Tier-1 | Non-HFTD---11 | 2--2 | 0.17216 | 0 | 100% | 10.3552 | 34.57% | 64.03% | 1.397% | 0.1772 | 0 | 0 | 0.1772 | 0 | 0.16125 | 0.16966 | 0.9504 | 0.16125 | 0.16966 | 0.9504 | 0.17894 | 0.18828 | 0.9504 | 1.711% | 0.0067068 | 0.0063748 | 1543.9807 | 37.6917 | 1219.1738 | 287.1152 | 1596.5913 | 0 | 0 | 1596.5913 | 5.843e-06%
2027 | 178 | 178-982 | Tier-2 | Tier-2---21 | 1--1 | 1.1551 | 19 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0063254 | 0 | 0 | 0.0063254 | 0 | 0.005756 | 1.1383 | 0.0050564 | 0.005756 | 1.1383 | 0.0050564 | 0.0063875 | 1.2632 | 0.0050564 | 0.6625% | 0.0033454 | 0.0031798 | 285.4035 | 0.62363 | 58.6739 | 226.106 | 298.2775 | 0 | 0 | 298.2775 | 2.086e-07%
2027 | NO1 | NO1-288F | Tier-1 | Non-HFTD---18 | 1--1 | 1.0576 | 14 | 100% | 0.81031 | 11.55% | 0% | 88.45% | 0.0046337 | 0 | 0 | 0.0046337 | 0 | 0.0042166 | 1.0422 | 0.0040457 | 0.0042166 | 1.0422 | 0.0040457 | 0.0046792 | 1.1566 | 0.0040457 | 0.5718% | 0.002839 | 0.0026985 | 285.4227 | 0.18996 | 55.9053 | 229.3274 | 298.5697 | 0 | 0 | 298.5697 | 1.528e-07%
2027 | 712 | 712-26 | Tier-1 | Non-HFTD---19 | 1--2 | 0.16006 | 32 | 100% | 0.49531 | 70.46% | 0% | 29.54% | 0.017274 | 0 | 0 | 0.017274 | 0 | 0.015719 | 0.15774 | 0.099654 | 0.015719 | 0.15774 | 0.099654 | 0.017444 | 0.17505 | 0.099654 | 3.488% | 0.0005438 | 0.00051688 | 910.8315 | 103.0746 | 31.4131 | 776.3438 | 924.8457 | 0 | 0 | 924.8457 | 5.696e-07%
2027 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.036174 | 0 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.1337 | 0.03565 | 31.8018 | 1.1337 | 0.03565 | 31.8018 | 1.2581 | 0.039561 | 31.8018 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2027 | 532 | 532-763 | Tier-1 | Non-HFTD---2 | 5--4 | 6.6682 | 237 | 100% | 872.9353 | 22.07% | 77.46% | 0.4675% | 9.5372 | 0 | 0 | 9.5372 | 0 | 8.6787 | 6.5715 | 1.3207 | 8.6787 | 6.5715 | 1.3207 | 9.6309 | 7.2925 | 1.3207 | 1.093% | 0.10819 | 0.10283 | 8068.6143 | 305.6113 | 5713.7599 | 2049.2431 | 8396.0666 | 0 | 0 | 8396.0666 | 0.0003145%
2027 | 138 | 138-360F | Tier-1 | Non-HFTD---17 | 1--2 | 0.59812 | 11 | 100% | 1.3988 | 40.66% | 0% | 59.34% | 0.02815 | 0 | 0 | 0.02815 | 0 | 0.025616 | 0.58945 | 0.043457 | 0.025616 | 0.58945 | 0.043457 | 0.028426 | 0.65412 | 0.043457 | 2.012% | 0.0024168 | 0.0022972 | 578.7745 | 0.25845 | 266.504 | 312.012 | 596.6618 | 0 | 0 | 596.6618 | 9.283e-07%
2027 | 1435 | 1435-1075F | Tier-1 | Non-HFTD---15 | 2--2 | 2.7231 | 121 | 100% | 4.6893 | 70.05% | 0% | 29.95% | 0.1626 | 0 | 0 | 0.1626 | 0 | 0.14796 | 2.6836 | 0.055134 | 0.14796 | 2.6836 | 0.055134 | 0.16419 | 2.9781 | 0.055134 | 3.467% | 0.0067656 | 0.0064307 | 693.1065 | 136.0595 | 69.2928 | 487.7542 | 703.9175 | 0 | 0 | 703.9175 | 5.362e-06%
2027 | 1202 | 1202-9 | Tier-2 | Tier-2---17 | 2--4 | 3.468 | 67 | 100% | 73.4421 | 96.84% | 0% | 3.16% | 3.5205 | 0 | 0 | 3.5205 | 0 | 3.2036 | 3.4177 | 0.93737 | 3.2036 | 3.4177 | 0.93737 | 3.5551 | 3.7926 | 0.93737 | 4.794% | 0.01182 | 0.011235 | 6213.48 | 1453.8319 | 498.5132 | 4261.1349 | 6223.7055 | 0 | 0 | 6223.7055 | 0.0001161%
2027 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 11.5724 | 1453 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 118.4418 | 11.4046 | 10.3855 | 118.4418 | 11.4046 | 10.3855 | 131.4369 | 12.6559 | 10.3855 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2027 | 274 | 274-40 | Tier-1 | Non-HFTD---3 | 4--3 | 7.8386 | 296 | 100% | 130.2262 | 2.649% | 92.8% | 4.548% | 0.17075 | 0 | 0 | 0.17075 | 0 | 0.15538 | 7.725 | 0.020114 | 0.15538 | 7.725 | 0.020114 | 0.17243 | 8.5726 | 0.020114 | 0.1311% | 0.037195 | 0.035354 | 3501.1361 | 5.6164 | 3059.4974 | 436.0223 | 3678.638 | 0 | 0 | 3678.638 | 5.631e-06%
2027 | 270 | CB 270 | Tier-1 | Non-HFTD---5 | 3--4 | 2.0546 | 375 | 100% | 71.4588 | 15.92% | 82.32% | 1.76% | 0.56317 | 0 | 0 | 0.56317 | 0 | 0.51248 | 2.0248 | 0.25311 | 0.51248 | 2.0248 | 0.25311 | 0.56871 | 2.2469 | 0.25311 | 0.7881% | 0.0142 | 0.013497 | 5032.3124 | 129.2561 | 3832.2088 | 1070.8475 | 5252.6589 | 0 | 0 | 5252.6589 | 1.857e-05%
2027 | 563 | CB 563 | Tier-1 | Non-HFTD---11 | 1--4 | 0.17481 | 35 | 100% | 10.231 | 98.75% | 0% | 1.252% | 0.50009 | 0 | 0 | 0.50009 | 0 | 0.45508 | 0.17228 | 2.6416 | 0.45508 | 0.17228 | 2.6416 | 0.50501 | 0.19118 | 2.6416 | 4.888% | 0.0006932 | 0.00065889 | 14759.0669 | 2171.1529 | 3891.2279 | 8696.6862 | 14768.6918 | 0 | 0 | 14768.6918 | 1.649e-05%
2027 | 700 | CB 700 | Tier-1 | Non-HFTD---13 | 1--3 | 0.40907 | 7 | 100% | 6.7901 | 95.69% | 0% | 4.313% | 0.32161 | 0 | 0 | 0.32161 | 0 | 0.29266 | 0.40314 | 0.72596 | 0.29266 | 0.40314 | 0.72596 | 0.32477 | 0.44737 | 0.72596 | 4.736% | 0.0015946 | 0.0015157 | 4258.1661 | 656.9619 | 50.5505 | 3550.6537 | 4267.7311 | 0 | 0 | 4267.7311 | 1.061e-05%
2027 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 27.7907 | 1435 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 819.268 | 27.3877 | 29.9137 | 819.268 | 27.3877 | 29.9137 | 909.1561 | 30.3927 | 29.9137 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2027 | 189 | 189-645 | Tier-1 | Non-HFTD---11 | 2--3 | 1.8176 | 78 | 100% | 13.5881 | 92.26% | 0% | 7.743% | 0.62053 | 0 | 0 | 0.62053 | 0 | 0.56467 | 1.7913 | 0.31524 | 0.56467 | 1.7913 | 0.31524 | 0.62663 | 1.9878 | 0.31524 | 4.567% | 0.0052774 | 0.0050162 | 2574.7796 | 257.5393 | 821.9251 | 1495.3153 | 2585.1626 | 0 | 0 | 2585.1626 | 2.046e-05%
2027 | 368 | 368-403F | Tier-1 | Non-HFTD---11 | 2--2 | 0.42387 | 9 | 100% | 10.4781 | 1.466% | 94.68% | 3.85% | 0.0076023 | 0 | 0 | 0.0076023 | 0 | 0.006918 | 0.41772 | 0.016561 | 0.006918 | 0.41772 | 0.016561 | 0.007677 | 0.46355 | 0.016561 | 0.07255% | 0.0067636 | 0.0064288 | 1549.1827 | 1.6714 | 1373.0792 | 174.432 | 1628.6783 | 0 | 0 | 1628.6783 | 2.507e-07%
2027 | 719 | 719-28 | Tier-1 | Non-HFTD---19 | 1--3 | 0.011364 | 0 | 100% | 0.19101 | 81.43% | 0% | 18.57% | 0.0076988 | 0 | 0 | 0.0076988 | 0 | 0.0070058 | 0.011199 | 0.62558 | 0.0070058 | 0.011199 | 0.62558 | 0.0077745 | 0.012428 | 0.62558 | 4.031% | 7.58e-05 | 7.2048e-05 | 2519.9154 | 0.35219 | 2094.389 | 425.1743 | 2544.2902 | 0 | 0 | 2544.2902 | 2.539e-07%
2027 | 62 | CB 62 | Tier-1 | Non-HFTD---5 | 3--4 | 1.8229 | 124 | 100% | 88.5913 | 17.86% | 80.39% | 1.758% | 0.78309 | 0 | 0 | 0.78309 | 0 | 0.7126 | 1.7965 | 0.39666 | 0.7126 | 1.7965 | 0.39666 | 0.79078 | 1.9936 | 0.39666 | 0.8839% | 0.016405 | 0.015593 | 5400.2599 | 65.1821 | 4479.0088 | 856.069 | 5631.2734 | 0 | 0 | 5631.2734 | 2.582e-05%
2027 | 88 | 88-27F | Tier-1 | Non-HFTD---15 | 1--3 | 0.14678 | 11 | 100% | 2.2245 | 92.57% | 0% | 7.426% | 0.10194 | 0 | 0 | 0.10194 | 0 | 0.092761 | 0.14465 | 0.64127 | 0.092761 | 0.14465 | 0.64127 | 0.10294 | 0.16052 | 0.64127 | 4.582% | 0.0008056 | 0.00076572 | 2761.3126 | 412.5963 | 52.951 | 2295.7652 | 2771.9912 | 0 | 0 | 2771.9912 | 3.361e-06%
2027 | 309 | 309-15F | Tier-1 | Non-HFTD---12 | 3--1 | 8.7252 | 163 | 100% | 10.1949 | 53% | 0% | 47% | 0.26747 | 0 | 0 | 0.26747 | 0 | 0.2434 | 8.5986 | 0.028307 | 0.2434 | 8.5986 | 0.028307 | 0.2701 | 9.5421 | 0.028307 | 2.624% | 0.023995 | 0.022807 | 424.8851 | 7.9838 | 195.2064 | 221.6949 | 435.2844 | 0 | 0 | 435.2844 | 8.82e-06%
2027 | 161 | 161-975F | Tier-1 | Non-HFTD---13 | 2--2 | 3.2134 | 83 | 100% | 8.5862 | 76.7% | 0% | 23.3% | 0.32599 | 0 | 0 | 0.32599 | 0 | 0.29665 | 3.1669 | 0.093673 | 0.29665 | 3.1669 | 0.093673 | 0.32919 | 3.5143 | 0.093673 | 3.797% | 0.0085198 | 0.0080981 | 1007.7888 | 0.42746 | 792.7442 | 214.6171 | 1020.0168 | 0 | 0 | 1020.0168 | 1.075e-05%
2027 | 90 | CB 90 | Tier-1 | Non-HFTD---9 | 2--3 | 0.018939 | 0 | 100% | 16.6741 | 2.335% | 97.48% | 0.1839% | 0.019272 | 0 | 0 | 0.019272 | 0 | 0.017537 | 0.018665 | 0.93959 | 0.017537 | 0.018665 | 0.93959 | 0.019461 | 0.020713 | 0.93959 | 0.1156% | 0.0049876 | 0.0047407 | 3343.1051 | 4.348 | 3056.2234 | 282.5337 | 3513.1416 | 0 | 0 | 3513.1416 | 6.355e-07%
2027 | 183 | CB 183 | Tier-1 | Non-HFTD---4 | 3--4 | 2.7093 | 99 | 100% | 128.8021 | 22.66% | 75.77% | 1.57% | 1.4445 | 0 | 0 | 1.4445 | 0 | 1.3145 | 2.67 | 0.4923 | 1.3145 | 2.67 | 0.4923 | 1.4587 | 2.963 | 0.4923 | 1.121% | 0.022326 | 0.021221 | 5769.2045 | 129.7649 | 4423.5742 | 1215.8654 | 6001.5822 | 0 | 0 | 6001.5822 | 4.763e-05%
2027 | 854 | 854-607F | Tier-1 | Non-HFTD---13 | 1--5 | 0.039394 | 11 | 100% | 5.4805 | 98.61% | 0% | 1.386% | 0.26752 | 0 | 0 | 0.26752 | 0 | 0.24344 | 0.038823 | 6.2706 | 0.24344 | 0.038823 | 6.2706 | 0.27015 | 0.043082 | 6.2706 | 4.881% | 0.000262 | 0.00024903 | 20917.8697 | 3367.0159 | 28.8837 | 17521.9701 | 20932.9704 | 0 | 0 | 20932.9704 | 8.822e-06%
2027 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 13.2995 | 388 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 412.0132 | 13.1066 | 31.4355 | 412.0132 | 13.1066 | 31.4355 | 457.2183 | 14.5447 | 31.4355 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2027 | 54 | CB 54 | Tier-1 | Non-HFTD---11 | 2--2 | 2.685 | 55 | 100% | 9.0518 | 74.11% | 0% | 25.89% | 0.33207 | 0 | 0 | 0.33207 | 0 | 0.30218 | 2.6461 | 0.1142 | 0.30218 | 2.6461 | 0.1142 | 0.33533 | 2.9364 | 0.1142 | 3.669% | 0.0079966 | 0.0076008 | 1131.9509 | 0.54614 | 863.4862 | 267.9186 | 1147.2119 | 0 | 0 | 1147.2119 | 1.095e-05%
2027 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.57917 | 50 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 13.165 | 0.57077 | 23.0654 | 13.165 | 0.57077 | 23.0654 | 14.6095 | 0.63339 | 23.0654 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2027 | 51 | CB 51 | Tier-1 | Non-HFTD---14 | 3--1 | 5.1357 | 233 | 100% | 6.4086 | 44.95% | 0% | 55.05% | 0.14259 | 0 | 0 | 0.14259 | 0 | 0.12976 | 5.0612 | 0.025638 | 0.12976 | 5.0612 | 0.025638 | 0.14399 | 5.6165 | 0.025638 | 2.225% | 0.014079 | 0.013382 | 455.1864 | 0.18855 | 227.3695 | 227.6283 | 468.236 | 0 | 0 | 468.236 | 4.702e-06%
2027 | 946 | 946-25F | Tier-1 | Non-HFTD---20 | 1--1 | 0.62441 | 13 | 100% | 0.39407 | 18.79% | 0% | 81.21% | 0.0036656 | 0 | 0 | 0.0036656 | 0 | 0.0033357 | 0.61535 | 0.0054207 | 0.0033357 | 0.61535 | 0.0054207 | 0.0037016 | 0.68287 | 0.0054207 | 0.9302% | 0.0015836 | 0.0015052 | 248.8471 | 0.15206 | 65.1198 | 183.5753 | 259.3713 | 0 | 0 | 259.3713 | 1.209e-07%
2027 | NO1 | NO1-287F | Tier-1 | Non-HFTD---18 | 2--1 | 1.8949 | 50 | 100% | 1.6275 | 20.71% | 0% | 79.29% | 0.016687 | 0 | 0 | 0.016687 | 0 | 0.015185 | 1.8674 | 0.0081316 | 0.015185 | 1.8674 | 0.0081316 | 0.016851 | 2.0723 | 0.0081316 | 1.025% | 0.0051894 | 0.0049325 | 313.6146 | 0.1871 | 87.5499 | 225.8776 | 326.5639 | 0 | 0 | 326.5639 | 5.503e-07%
2027 | 205 | CB 205 | Tier-1 | Non-HFTD---7 | 3--3 | 5.2694 | 405 | 100% | 38.7792 | 89.82% | 0% | 10.18% | 1.7242 | 0 | 0 | 1.7242 | 0 | 1.569 | 5.193 | 0.30214 | 1.569 | 5.193 | 0.30214 | 1.7411 | 5.7627 | 0.30214 | 4.446% | 0.016219 | 0.015416 | 2391.0005 | 150.1089 | 1253.224 | 987.6676 | 2403.6753 | 0 | 0 | 2403.6753 | 5.686e-05%
2027 | 296 | 296-66F | Tier-2 | Tier-2---21 | 1--3 | 0.14451 | 7 | 100% | 2.284 | 90.58% | 0% | 9.421% | 0.10241 | 0 | 0 | 0.10241 | 0 | 0.093188 | 0.14241 | 0.65436 | 0.093188 | 0.14241 | 0.65436 | 0.10341 | 0.15804 | 0.65436 | 4.484% | 0.0006178 | 0.00058722 | 3696.9667 | 843.8145 | 35.5403 | 2817.6118 | 3715.1054 | 0 | 0 | 3715.1054 | 3.377e-06%
2027 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 2.3455 | 224 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 194.2367 | 2.3115 | 84.031 | 194.2367 | 2.3115 | 84.031 | 215.5479 | 2.5651 | 84.031 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2027 | EN2 | CB EN2 | Tier-1 | Non-HFTD---8 | 3--3 | 5.9322 | 649 | 100% | 45.2165 | 53.61% | 36.84% | 9.55% | 1.2 | 0 | 0 | 1.2 | 0 | 1.092 | 5.8462 | 0.18679 | 1.092 | 5.8462 | 0.18679 | 1.2118 | 6.4876 | 0.18679 | 2.654% | 0.022788 | 0.02166 | 1984.2222 | 155.0903 | 804.1172 | 1025.0147 | 2032.1547 | 0 | 0 | 2032.1547 | 3.957e-05%
2027 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | 3--5 | 9.2025 | 702 | 100% | 1424.1907 | 99.61% | 0% | 0.3928% | 70.2205 | 0 | 0 | 70.2205 | 0 | 63.8997 | 9.069 | 7.0459 | 63.8997 | 9.069 | 7.0459 | 70.9107 | 10.0641 | 7.0459 | 4.931% | 0.028304 | 0.026903 | 50317.6471 | 8145.1206 | 368.3302 | 41804.1963 | 50327.94 | 0 | 0 | 50327.94 | 0.002316%
2027 | 380 | CB 380 | Tier-1 | Non-HFTD---6 | 3--3 | 6.7373 | 225 | 100% | 65.1412 | 93.43% | 0% | 6.569% | 3.0127 | 0 | 0 | 3.0127 | 0 | 2.7415 | 6.6397 | 0.4129 | 2.7415 | 6.6397 | 0.4129 | 3.0423 | 7.3681 | 0.4129 | 4.625% | 0.019847 | 0.018864 | 3282.237 | 399.2549 | 1245.0692 | 1637.9129 | 3293.4656 | 0 | 0 | 3293.4656 | 9.935e-05%
2027 | 792 | 792-47R | Tier-1 | Non-HFTD---1 | 4--4 | 7.7364 | 716 | 100% | 393.985 | 1.678% | 96.94% | 1.378% | 0.32719 | 0 | 0 | 0.32719 | 0 | 0.29774 | 7.6242 | 0.039052 | 0.29774 | 7.6242 | 0.039052 | 0.33041 | 8.4607 | 0.039052 | 0.08305% | 0.039069 | 0.037135 | 10084.4423 | 11.8059 | 9078.6124 | 994.0241 | 10600.8076 | 0 | 0 | 10600.8076 | 1.079e-05%
2027 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 27.9316 | 2565 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1152.5944 | 27.5267 | 41.8719 | 1152.5944 | 27.5267 | 41.8719 | 1279.0544 | 30.5468 | 41.8719 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2027 | 56 | 56-670F | Tier-1 | Non-HFTD---6 | 3--3 | 1.1852 | 40 | 100% | 49.2251 | 0.5924% | 97.4% | 2.005% | 0.014434 | 0 | 0 | 0.014434 | 0 | 0.013135 | 1.168 | 0.011245 | 0.013135 | 1.168 | 0.011245 | 0.014576 | 1.2962 | 0.011245 | 0.02932% | 0.014208 | 0.013505 | 3464.6013 | 3.8619 | 3012.3419 | 448.3975 | 3643.9615 | 0 | 0 | 3643.9615 | 4.76e-07%
2027 | 133 | CB 133 | Tier-1 | Non-HFTD---14 | 3--2 | 6.2032 | 134 | 100% | 8.7184 | 49.78% | 0% | 50.22% | 0.21483 | 0 | 0 | 0.21483 | 0 | 0.19549 | 6.1133 | 0.031978 | 0.19549 | 6.1133 | 0.031978 | 0.21694 | 6.784 | 0.031978 | 2.464% | 0.017124 | 0.016276 | 509.131 | 1.8919 | 270.3959 | 236.8432 | 522.4469 | 0 | 0 | 522.4469 | 7.084e-06%
2027 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 0.75759 | 163 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.1675 | 0.7466 | 4.2426 | 3.1675 | 0.7466 | 4.2426 | 3.5151 | 0.82852 | 4.2426 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2027 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 13.5415 | 913 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 440.5122 | 13.3451 | 33.0092 | 440.5122 | 13.3451 | 33.0092 | 488.8442 | 14.8093 | 33.0092 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2027 | 163 | CB 163 | Tier-1 | Non-HFTD---6 | 4--2 | 19.7841 | 299 | 100% | 56.8724 | 88.67% | 0% | 11.33% | 2.4962 | 0 | 0 | 2.4962 | 0 | 2.2715 | 19.4973 | 0.11651 | 2.2715 | 19.4973 | 0.11651 | 2.5208 | 21.6365 | 0.11651 | 4.389% | 0.038275 | 0.03638 | 1485.8961 | 18.0474 | 1223.2724 | 244.5763 | 1494.6629 | 0 | 0 | 1494.6629 | 8.232e-05%
2027 | 482 | 482-381F | Tier-1 | Non-HFTD---18 | 1--1 | 1.6901 | 145 | 100% | 1.247 | 13.37% | 0% | 86.63% | 0.0082507 | 0 | 0 | 0.0082507 | 0 | 0.0075081 | 1.6656 | 0.0045077 | 0.0075081 | 1.6656 | 0.0045077 | 0.0083318 | 1.8484 | 0.0045077 | 0.6617% | 0.0044034 | 0.0041854 | 283.1864 | 0.18461 | 60.1392 | 222.8626 | 295.9628 | 0 | 0 | 295.9628 | 2.721e-07%
2027 | 463 | CB 463 | Tier-2 | Tier-2---17 | 2--5 | 1.5028 | 87 | 100% | 99.9729 | 99.18% | 0% | 0.8185% | 4.9082 | 0 | 0 | 4.9082 | 0 | 4.4664 | 1.4811 | 3.0157 | 4.4664 | 1.4811 | 3.0157 | 4.9564 | 1.6435 | 3.0157 | 4.909% | 0.0053474 | 0.0050827 | 18695.6146 | 4709.0355 | 4354.0593 | 9632.5197 | 18703.5841 | 0 | 0 | 18703.5841 | 0.0001619%
2027 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 10.5112 | 1091 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 85.5897 | 10.3588 | 8.2625 | 85.5897 | 10.3588 | 8.2625 | 94.9804 | 11.4953 | 8.2625 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2027 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 0.095455 | 38 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.7092 | 0.094071 | 18.1696 | 1.7092 | 0.094071 | 18.1696 | 1.8968 | 0.10439 | 18.1696 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2027 | 124 | CB 124 | Tier-1 | Non-HFTD---15 | 1--2 | 0.95 | 6 | 100% | 3.2925 | 66.24% | 0% | 33.76% | 0.10796 | 0 | 0 | 0.10796 | 0 | 0.098239 | 0.93623 | 0.10493 | 0.098239 | 0.93623 | 0.10493 | 0.10902 | 1.0389 | 0.10493 | 3.279% | 0.0040986 | 0.0038957 | 803.3242 | 53.1781 | 266.286 | 483.8601 | 817.4481 | 0 | 0 | 817.4481 | 3.56e-06%
2027 | 701 | CB 701 | Tier-1 | Non-HFTD---2 | 4--3 | 17.7385 | 540 | 100% | 193.6018 | 45.82% | 47.23% | 6.946% | 4.3911 | 0 | 0 | 4.3911 | 0 | 3.9958 | 17.4813 | 0.22858 | 3.9958 | 17.4813 | 0.22858 | 4.4342 | 19.3993 | 0.22858 | 2.268% | 0.065404 | 0.062166 | 2960.1098 | 147.5713 | 1958.5218 | 854.0167 | 3043.6312 | 0 | 0 | 3043.6312 | 0.0001448%
2027 | 213 | 213-262F | Tier-1 | Non-HFTD---19 | 1--2 | 0.083756 | 5 | 100% | 0.16168 | 79.23% | 0% | 20.77% | 0.0063411 | 0 | 0 | 0.0063411 | 0 | 0.0057703 | 0.082542 | 0.069907 | 0.0057703 | 0.082542 | 0.069907 | 0.0064034 | 0.091598 | 0.069907 | 3.922% | 0.0001976 | 0.00018782 | 818.194 | 104.1852 | 22.3943 | 691.6145 | 827.0423 | 0 | 0 | 827.0423 | 2.091e-07%
2027 | 1139 | 1139-4F | Tier-2 | Tier-2---11 | 5--3 | 4.1474 | 89 | 100% | 472.1771 | 0.2595% | 99.27% | 0.4712% | 0.060646 | 0 | 0 | 0.060646 | 0 | 0.055187 | 4.0872 | 0.013502 | 0.055187 | 4.0872 | 0.013502 | 0.061242 | 4.5357 | 0.013502 | 0.01284% | 0.11231 | 0.10675 | 4204.4022 | 7.5405 | 3803.8802 | 392.9815 | 4422.7903 | 0 | 0 | 4422.7903 | 2e-06%
2027 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.84619 | 36 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 94.6789 | 0.83392 | 113.5349 | 94.6789 | 0.83392 | 113.5349 | 105.0668 | 0.92541 | 113.5349 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2027 | 451 | 451-38F | Tier-1 | Non-HFTD---17 | 1--1 | 1.3801 | 116 | 100% | 1.6743 | 45.15% | 0% | 54.85% | 0.037424 | 0 | 0 | 0.037424 | 0 | 0.034055 | 1.3601 | 0.025038 | 0.034055 | 1.3601 | 0.025038 | 0.037792 | 1.5094 | 0.025038 | 2.235% | 0.004114 | 0.0039104 | 406.98 | 0.16796 | 204.0476 | 202.7644 | 418.6042 | 0 | 0 | 418.6042 | 1.234e-06%
2027 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.76383 | 10 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 7.6802 | 0.75275 | 10.2028 | 7.6802 | 0.75275 | 10.2028 | 8.5228 | 0.83534 | 10.2028 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2027 | 480 | 480-35 | Tier-1 | Non-HFTD---10 | 4--1 | 16.4336 | 1010 | 100% | 19.5827 | 39.21% | 0% | 60.79% | 0.38007 | 0 | 0 | 0.38007 | 0 | 0.34586 | 16.1953 | 0.021355 | 0.34586 | 16.1953 | 0.021355 | 0.3838 | 17.9722 | 0.021355 | 1.941% | 0.047129 | 0.044796 | 415.5112 | 23.8764 | 99.4507 | 292.1841 | 428.6657 | 0 | 0 | 428.6657 | 1.253e-05%
2027 | 719 | 719-33 | Tier-1 | Non-HFTD---16 | 2--1 | 4.6088 | 110 | 100% | 4.0499 | 25.39% | 0% | 74.61% | 0.050892 | 0 | 0 | 0.050892 | 0 | 0.046311 | 4.5419 | 0.010196 | 0.046311 | 4.5419 | 0.010196 | 0.051393 | 5.0403 | 0.010196 | 1.257% | 0.012955 | 0.012314 | 312.6002 | 0.17551 | 100.5469 | 211.8778 | 324.7469 | 0 | 0 | 324.7469 | 1.678e-06%
2027 | 83 | 83-622F | Tier-1 | Non-HFTD---18 | 2--1 | 3.0943 | 66 | 100% | 1.5636 | 25.94% | 0% | 74.06% | 0.020078 | 0 | 0 | 0.020078 | 0 | 0.018271 | 3.0495 | 0.0059914 | 0.018271 | 3.0495 | 0.0059914 | 0.020275 | 3.384 | 0.0059914 | 1.284% | 0.00696 | 0.0066155 | 224.6568 | 1.1983 | 66.8397 | 156.6188 | 233.3214 | 0 | 0 | 233.3214 | 6.621e-07%
2027 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 19.7983 | 1084 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 195.7136 | 19.5112 | 10.0308 | 195.7136 | 19.5112 | 10.0308 | 217.1869 | 21.6519 | 10.0308 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2027 | 1079 | CB 1079 | Tier-1 | Non-HFTD---9 | 2--3 | 2.5269 | 152 | 100% | 15.9736 | 90.06% | 0% | 9.938% | 0.71212 | 0 | 0 | 0.71212 | 0 | 0.64802 | 2.4902 | 0.26023 | 0.64802 | 2.4902 | 0.26023 | 0.71912 | 2.7634 | 0.26023 | 4.458% | 0.0072148 | 0.0068577 | 2214.0112 | 265.8554 | 1002.265 | 945.8908 | 2225.4696 | 0 | 0 | 2225.4696 | 2.348e-05%
2027 | 207 | CB 207 | Tier-1 | Non-HFTD---7 | 2--3 | 2.9445 | 104 | 100% | 36.13 | 94.58% | 0% | 5.421% | 1.6915 | 0 | 0 | 1.6915 | 0 | 1.5392 | 2.9018 | 0.53043 | 1.5392 | 2.9018 | 0.53043 | 1.7081 | 3.2202 | 0.53043 | 4.682% | 0.0090126 | 0.0085665 | 4008.8284 | 146.4393 | 2915.0578 | 947.3313 | 4020.1468 | 0 | 0 | 4020.1468 | 5.578e-05%
2027 | 1418 | 1418-31R | Tier-1 | Non-HFTD---15 | 1--2 | 0.66439 | 18 | 100% | 2.7275 | 78.81% | 0% | 21.19% | 0.1064 | 0 | 0 | 0.1064 | 0 | 0.096819 | 0.65476 | 0.14787 | 0.096819 | 0.65476 | 0.14787 | 0.10744 | 0.7266 | 0.14787 | 3.901% | 0.0024528 | 0.0023314 | 1112.0026 | 74.6408 | 441.9379 | 595.4239 | 1124.2767 | 0 | 0 | 1124.2767 | 3.509e-06%
2027 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 5.4324 | 19 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 20.5582 | 5.3536 | 3.8401 | 20.5582 | 5.3536 | 3.8401 | 22.8138 | 5.941 | 3.8401 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2027 | 431 | 431-46AE | Tier-1 | Non-HFTD---14 | 2--1 | 4.3178 | 34 | 100% | 5.4602 | 36.55% | 0% | 63.45% | 0.098795 | 0 | 0 | 0.098795 | 0 | 0.089902 | 4.2552 | 0.021128 | 0.089902 | 4.2552 | 0.021128 | 0.099766 | 4.7221 | 0.021128 | 1.809% | 0.012491 | 0.011873 | 437.1166 | 0.2108 | 184.9596 | 251.9462 | 451.5597 | 0 | 0 | 451.5597 | 3.258e-06%
2027 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 16.422 | 1638 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 498.8841 | 16.1839 | 30.826 | 498.8841 | 16.1839 | 30.826 | 553.6205 | 17.9595 | 30.826 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2027 | BO1 | CB BO1 | Tier-1 | Non-HFTD---18 | 2--1 | 1.7728 | 43 | 100% | 1.9101 | 28.77% | 0% | 71.23% | 0.027199 | 0 | 0 | 0.027199 | 0 | 0.02475 | 1.7471 | 0.014167 | 0.02475 | 1.7471 | 0.014167 | 0.027466 | 1.9387 | 0.014167 | 1.424% | 0.0052326 | 0.0049736 | 365.037 | 0.49286 | 127.5995 | 236.9446 | 378.5787 | 0 | 0 | 378.5787 | 8.969e-07%
2027 | 545 | CB 545 | Tier-1 | Non-HFTD---5 | 3--3 | 1.9879 | 35 | 100% | 70.9796 | 19.97% | 77.85% | 2.177% | 0.7018 | 0 | 0 | 0.7018 | 0 | 0.63863 | 1.959 | 0.32599 | 0.63863 | 1.959 | 0.32599 | 0.7087 | 2.174 | 0.32599 | 0.9887% | 0.015929 | 0.01514 | 4456.0552 | 3.8159 | 4082.19 | 370.0493 | 4641.7637 | 0 | 0 | 4641.7637 | 2.314e-05%
2027 | 150 | 150-434AE | Tier-1 | Non-HFTD---9 | 1--4 | 1.1161 | 6 | 100% | 24.5324 | 96.53% | 0% | 3.474% | 1.1722 | 0 | 0 | 1.1722 | 0 | 1.0667 | 1.0999 | 0.96976 | 1.0667 | 1.0999 | 0.96976 | 1.1837 | 1.2206 | 0.96976 | 4.778% | 0.0042426 | 0.0040326 | 5782.3912 | 1118.2339 | 22.284 | 4641.8732 | 5792.8535 | 0 | 0 | 5792.8535 | 3.865e-05%
2027 | 144 | 144-442F | Tier-1 | Non-HFTD---5 | 3--4 | 3.5848 | 126 | 100% | 88.4511 | 1.673% | 95.65% | 2.673% | 0.073245 | 0 | 0 | 0.073245 | 0 | 0.066652 | 3.5328 | 0.018866 | 0.066652 | 3.5328 | 0.018866 | 0.073965 | 3.9205 | 0.018866 | 0.08281% | 0.015509 | 0.014741 | 5703.2117 | 6.9384 | 5087.8182 | 608.4551 | 5995.254 | 0 | 0 | 5995.254 | 2.415e-06%
2027 | 990 | 990-713 | Tier-2 | Tier-2---17 | 3--3 | 0.065909 | 13 | 100% | 85.9224 | 0.4524% | 99.5% | 0.04623% | 0.01924 | 0 | 0 | 0.01924 | 0 | 0.017508 | 0.064953 | 0.26955 | 0.017508 | 0.064953 | 0.26955 | 0.019429 | 0.07208 | 0.26955 | 0.02239% | 0.017823 | 0.01694 | 4820.9793 | 10.6403 | 4200.4141 | 609.9249 | 5070.9099 | 0 | 0 | 5070.9099 | 6.345e-07%
2027 | 160 | CB 160 | Tier-1 | Non-HFTD---7 | 2--3 | 3.6716 | 129 | 100% | 31.5499 | 92.29% | 0% | 7.71% | 1.4413 | 0 | 0 | 1.4413 | 0 | 1.3116 | 3.6183 | 0.36248 | 1.3116 | 3.6183 | 0.36248 | 1.4555 | 4.0153 | 0.36248 | 4.568% | 0.01025 | 0.0097426 | 3078.0386 | 0.58515 | 2859.7845 | 217.6689 | 3090.397 | 0 | 0 | 3090.397 | 4.753e-05%
2027 | 390 | 390-18 | Tier-1 | Non-HFTD---2 | 5--3 | 3.9404 | 129 | 100% | 318.8449 | 16.58% | 82.54% | 0.8771% | 2.617 | 0 | 0 | 2.617 | 0 | 2.3814 | 3.8832 | 0.61325 | 2.3814 | 3.8832 | 0.61325 | 2.6427 | 4.3093 | 0.61325 | 0.8208% | 0.10878 | 0.1034 | 2931.0773 | 106.6158 | 2119.5636 | 704.8979 | 3058.4114 | 0 | 0 | 3058.4114 | 8.63e-05%
2027 | GA1 | CB GA1 | Tier-1 | Non-HFTD---14 | 3--1 | 7.5047 | 189 | 100% | 7.2576 | 27.71% | 0% | 72.29% | 0.099541 | 0 | 0 | 0.099541 | 0 | 0.090581 | 7.3959 | 0.012247 | 0.090581 | 7.3959 | 0.012247 | 0.10052 | 8.2074 | 0.012247 | 1.372% | 0.021919 | 0.020834 | 331.1033 | 2.6119 | 98.6514 | 229.84 | 343.5687 | 0 | 0 | 343.5687 | 3.282e-06%
2027 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 5.0473 | 319 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 64.6275 | 4.9741 | 12.9927 | 64.6275 | 4.9741 | 12.9927 | 71.7183 | 5.5199 | 12.9927 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2027 | 473 | 473-36R | Tier-1 | Non-HFTD---1 | 5--4 | 14.9443 | 562 | 100% | 1339.2067 | 0.8137% | 98.49% | 0.6935% | 0.53941 | 0 | 0 | 0.53941 | 0 | 0.49086 | 14.7276 | 0.033329 | 0.49086 | 14.7276 | 0.033329 | 0.54472 | 16.3435 | 0.033329 | 0.04028% | 0.11477 | 0.10909 | 11668.3486 | 17.7885 | 10476.9993 | 1173.5608 | 12271.0665 | 0 | 0 | 12271.0665 | 1.779e-05%
2027 | HC4 | CB HC4 | Tier-1 | Non-HFTD---8 | 3--2 | 6.4726 | 321 | 100% | 33.1006 | 83.29% | 0% | 16.71% | 1.3646 | 0 | 0 | 1.3646 | 0 | 1.2418 | 6.3787 | 0.19468 | 1.2418 | 6.3787 | 0.19468 | 1.378 | 7.0786 | 0.19468 | 4.123% | 0.021599 | 0.02053 | 1532.5221 | 272.5227 | 181.5019 | 1078.4974 | 1545.8612 | 0 | 0 | 1545.8612 | 4.5e-05%
2027 | 555 | 555-2F | Tier-1 | Non-HFTD---17 | 1--2 | 0.42273 | 2 | 100% | 0.84765 | 38.63% | 0% | 61.37% | 0.016208 | 0 | 0 | 0.016208 | 0 | 0.014749 | 0.4166 | 0.035403 | 0.014749 | 0.4166 | 0.035403 | 0.016367 | 0.46231 | 0.035403 | 1.912% | 0.0015912 | 0.0015124 | 532.7136 | 32.3462 | 37.5358 | 462.8316 | 549.7399 | 0 | 0 | 549.7399 | 5.345e-07%
2027 | 281 | CB 281 | Tier-2 | Tier-2---16 | 4--3 | 6.8986 | 157 | 100% | 131.3229 | 1.145% | 96.36% | 2.498% | 0.07445 | 0 | 0 | 0.07445 | 0 | 0.067748 | 6.7986 | 0.009965 | 0.067748 | 6.7986 | 0.009965 | 0.075181 | 7.5445 | 0.009965 | 0.05669% | 0.046838 | 0.04452 | 2803.7555 | 3.8846 | 2517.4341 | 282.4368 | 2948.0968 | 0 | 0 | 2948.0968 | 2.455e-06%
2027 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | 4--5 | 7.0648 | 1685 | 100% | 4233.8665 | 96.93% | 2.943% | 0.1312% | 203.133 | 0 | 0 | 203.133 | 0 | 184.8483 | 6.9623 | 26.5497 | 184.8483 | 6.9623 | 26.5497 | 205.1294 | 7.7262 | 26.5497 | 4.798% | 0.080233 | 0.076262 | 52769.5087 | 8342.6927 | 1399.583 | 43027.233 | 52853.9991 | 0 | 0 | 52853.9991 | 0.006699%
2027 | MK1 | CB MK1 | Tier-1 | Non-HFTD---14 | 3--1 | 6.0093 | 122 | 100% | 7.4473 | 44.14% | 0% | 55.86% | 0.16271 | 0 | 0 | 0.16271 | 0 | 0.14807 | 5.9221 | 0.025002 | 0.14807 | 5.9221 | 0.025002 | 0.16431 | 6.5719 | 0.025002 | 2.185% | 0.016865 | 0.01603 | 441.5759 | 36.2896 | 78.2242 | 327.062 | 454.4219 | 0 | 0 | 454.4219 | 5.366e-06%
2027 | 532 | 532-1293F | Tier-1 | Non-HFTD---17 | 1--2 | 0.79053 | 19 | 100% | 1.3366 | 55.6% | 0% | 44.4% | 0.036789 | 0 | 0 | 0.036789 | 0 | 0.033477 | 0.77907 | 0.042971 | 0.033477 | 0.77907 | 0.042971 | 0.037151 | 0.86455 | 0.042971 | 2.752% | 0.0023122 | 0.0021977 | 578.0789 | 32.7375 | 145.1444 | 400.197 | 591.4446 | 0 | 0 | 591.4446 | 1.213e-06%
2027 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 7.806 | 514 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 750.663 | 7.6929 | 97.5793 | 750.663 | 7.6929 | 97.5793 | 833.024 | 8.5369 | 97.5793 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2027 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 4.7979 | 602 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 104.4239 | 4.7283 | 22.0848 | 104.4239 | 4.7283 | 22.0848 | 115.881 | 5.2471 | 22.0848 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2027 | VO1 | CB VO1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.214 | 26 | 100% | 1.1072 | 22.13% | 0% | 77.87% | 0.012131 | 0 | 0 | 0.012131 | 0 | 0.011039 | 1.1964 | 0.0092265 | 0.011039 | 1.1964 | 0.0092265 | 0.01225 | 1.3277 | 0.0092265 | 1.096% | 0.003819 | 0.00363 | 289.9083 | 0.16986 | 84.6753 | 205.0631 | 301.6643 | 0 | 0 | 301.6643 | 4e-07%
2027 | WA4 | CB WA4 | Tier-1 | Non-HFTD---10 | 3--2 | 7.4043 | 239 | 100% | 23.9832 | 78.04% | 0% | 21.96% | 0.92645 | 0 | 0 | 0.92645 | 0 | 0.84306 | 7.297 | 0.11554 | 0.84306 | 7.297 | 0.11554 | 0.93556 | 8.0976 | 0.11554 | 3.863% | 0.022554 | 0.021438 | 1063.3699 | 52.777 | 527.6231 | 482.9698 | 1075.5315 | 0 | 0 | 1075.5315 | 3.055e-05%
2027 | 299 | 299-1011 | Tier-1 | Non-HFTD---5 | 2--3 | 4.203 | 102 | 100% | 54.9991 | 94.1% | 0% | 5.9% | 2.5618 | 0 | 0 | 2.5618 | 0 | 2.3312 | 4.1421 | 0.56282 | 2.3312 | 4.1421 | 0.56282 | 2.587 | 4.5965 | 0.56282 | 4.658% | 0.013194 | 0.012541 | 4168.5545 | 546.6465 | 589.0831 | 3032.8249 | 4181.3634 | 0 | 0 | 4181.3634 | 8.448e-05%
2027 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.58561 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 3.8596 | 0.57712 | 6.6877 | 3.8596 | 0.57712 | 6.6877 | 4.283 | 0.64043 | 6.6877 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2027 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 5.7333 | 62 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 237.497 | 5.6502 | 42.0335 | 237.497 | 5.6502 | 42.0335 | 263.5546 | 6.2701 | 42.0335 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2027 | 700 | 700-255 | Tier-1 | Non-HFTD---9 | 2--2 | 1.2451 | 22 | 100% | 16.4031 | 90.17% | 3.905% | 5.929% | 0.7321 | 0 | 0 | 0.7321 | 0 | 0.6662 | 1.227 | 0.54293 | 0.6662 | 1.227 | 0.54293 | 0.7393 | 1.3617 | 0.54293 | 4.463% | 0.010214 | 0.009708 | 1606.0068 | 234.45 | 79.4931 | 1292.0638 | 1614.2322 | 0 | 0 | 1614.2322 | 2.414e-05%
2027 | 321 | 321-646 | Tier-1 | Non-HFTD---18 | 2--1 | 1.9246 | 24 | 100% | 2.1274 | 32.02% | 0% | 67.98% | 0.033717 | 0 | 0 | 0.033717 | 0 | 0.030682 | 1.8967 | 0.016177 | 0.030682 | 1.8967 | 0.016177 | 0.034048 | 2.1048 | 0.016177 | 1.585% | 0.0057906 | 0.005504 | 367.3897 | 7.7909 | 93.4102 | 266.1885 | 380.3966 | 0 | 0 | 380.3966 | 1.112e-06%
2027 | 740 | CB 740 | Tier-1 | Non-HFTD---10 | 4--2 | 12.6747 | 722 | 100% | 25.6721 | 66.02% | 0% | 33.98% | 0.839 | 0 | 0 | 0.839 | 0 | 0.76348 | 12.4909 | 0.061123 | 0.76348 | 12.4909 | 0.061123 | 0.84724 | 13.8614 | 0.061123 | 3.268% | 0.034483 | 0.032776 | 744.476 | 0.22301 | 514.3039 | 229.9491 | 757.6491 | 0 | 0 | 757.6491 | 2.767e-05%
2027 | 308 | 308-486AE | Tier-2 | Tier-2---16 | 4--3 | 3.6318 | 154 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.19428 | 0 | 0 | 0.19428 | 0 | 0.1768 | 3.5791 | 0.049396 | 0.1768 | 3.5791 | 0.049396 | 0.19619 | 3.9718 | 0.049396 | 0.118% | 0.040279 | 0.038285 | 4088.4689 | 19.0997 | 3634.8848 | 434.4844 | 4296.3129 | 0 | 0 | 4296.3129 | 6.407e-06%
2027 | SW4 | CB SW4 | Tier-1 | Non-HFTD---16 | 2--1 | 3.3697 | 89 | 100% | 2.7806 | 34.41% | 0% | 65.59% | 0.047357 | 0 | 0 | 0.047357 | 0 | 0.043094 | 3.3209 | 0.012977 | 0.043094 | 3.3209 | 0.012977 | 0.047822 | 3.6852 | 0.012977 | 1.703% | 0.0083328 | 0.0079203 | 333.6959 | 7.2394 | 91.3226 | 235.1339 | 345.095 | 0 | 0 | 345.095 | 1.562e-06%
2027 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 2.1343 | 23 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 32.6575 | 2.1033 | 15.5267 | 32.6575 | 2.1033 | 15.5267 | 36.2406 | 2.3341 | 15.5267 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2027 | 166 | 166-463F | Tier-1 | Non-HFTD---19 | 1--1 | 0.081818 | 8 | 100% | 0.15952 | 10.72% | 0% | 89.28% | 0.0008462 | 0 | 0 | 0.0008462 | 0 | 0.00077003 | 0.080632 | 0.0095499 | 0.00077003 | 0.080632 | 0.0095499 | 0.00085452 | 0.089479 | 0.0095499 | 0.5305% | 0.0003874 | 0.00036822 | 411.7579 | 0.27663 | 77.5231 | 333.9581 | 430.9033 | 0 | 0 | 430.9033 | 2.79e-08%
2027 | BK1 | CB BK1 | Tier-1 | Non-HFTD---8 | 3--3 | 3.8556 | 133 | 100% | 44.2018 | 7.123% | 86.74% | 6.139% | 0.15584 | 0 | 0 | 0.15584 | 0 | 0.14181 | 3.7997 | 0.037322 | 0.14181 | 3.7997 | 0.037322 | 0.15737 | 4.2166 | 0.037322 | 0.3526% | 0.021968 | 0.02088 | 2012.1178 | 13.6327 | 1683.8934 | 314.5917 | 2109.4411 | 0 | 0 | 2109.4411 | 5.139e-06%
2027 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 1.5403 | 228 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 36.8484 | 1.518 | 24.2745 | 36.8484 | 1.518 | 24.2745 | 40.8913 | 1.6845 | 24.2745 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2027 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 1.0739 | 170 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 9.159 | 1.0583 | 8.6543 | 9.159 | 1.0583 | 8.6543 | 10.1639 | 1.1744 | 8.6543 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2027 | 381 | 381-451F | Tier-1 | Non-HFTD---10 | 3--2 | 6.7813 | 160 | 100% | 23.3181 | 88.11% | 0% | 11.89% | 1.017 | 0 | 0 | 1.017 | 0 | 0.92548 | 6.683 | 0.13848 | 0.92548 | 6.683 | 0.13848 | 1.027 | 7.4162 | 0.13848 | 4.362% | 0.018659 | 0.017735 | 1249.6956 | 131.9022 | 309.5549 | 808.2386 | 1257.4325 | 0 | 0 | 1257.4325 | 3.354e-05%
2027 | WA3 | CB WA3 | Tier-1 | Non-HFTD---8 | 4--2 | 13.982 | 461 | 100% | 27.563 | 70.26% | 0% | 29.74% | 0.95857 | 0 | 0 | 0.95857 | 0 | 0.87229 | 13.7793 | 0.063304 | 0.87229 | 13.7793 | 0.063304 | 0.96799 | 15.2911 | 0.063304 | 3.478% | 0.039294 | 0.037349 | 701.463 | 20.3909 | 425.071 | 256.0011 | 712.3281 | 0 | 0 | 712.3281 | 3.161e-05%
2027 | 821 | CB 821 | Tier-1 | Non-HFTD---8 | 4--2 | 11.9876 | 611 | 100% | 39.8764 | 81.44% | 0% | 18.56% | 1.6076 | 0 | 0 | 1.6076 | 0 | 1.4629 | 11.8138 | 0.12383 | 1.4629 | 11.8138 | 0.12383 | 1.6234 | 13.11 | 0.12383 | 4.032% | 0.03208 | 0.030492 | 1243.0135 | 29.5845 | 853.3576 | 360.0714 | 1255.025 | 0 | 0 | 1255.025 | 5.301e-05%
2027 | 454 | 454-49F | Tier-2 | Tier-2---13 | 4--3 | 1.5199 | 92 | 100% | 292.9743 | 76.06% | 23.59% | 0.3558% | 11.0299 | 0 | 0 | 11.0299 | 0 | 10.037 | 1.4978 | 6.7011 | 10.037 | 1.4978 | 6.7011 | 11.1383 | 1.6622 | 6.7011 | 3.765% | 0.077203 | 0.073382 | 3794.8464 | 847.9473 | 816.929 | 2129.9701 | 3842.1656 | 0 | 0 | 3842.1656 | 0.0003637%
2027 | 196 | 196-43F | Tier-2 | Tier-2---17 | 3--4 | 0.2589 | 52 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.23855 | 0 | 0 | 0.23855 | 0 | 0.21708 | 0.25515 | 0.8508 | 0.21708 | 0.25515 | 0.8508 | 0.2409 | 0.28314 | 0.8508 | 0.2544% | 0.017356 | 0.016497 | 5402.3367 | 48.5246 | 4687.8466 | 665.9656 | 5669.2187 | 0 | 0 | 5669.2187 | 7.867e-06%
2027 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 8.3178 | 81 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 271.0346 | 8.1972 | 33.0644 | 271.0346 | 8.1972 | 33.0644 | 300.7719 | 9.0965 | 33.0644 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2027 | 243 | CB 243 | Tier-2 | Tier-2---14 | 4--4 | 3.2755 | 98 | 100% | 284.2808 | 92.1% | 7.127% | 0.7733% | 12.9602 | 0 | 0 | 12.9602 | 0 | 11.7936 | 3.228 | 3.6535 | 11.7936 | 3.228 | 3.6535 | 13.0875 | 3.5822 | 3.6535 | 4.559% | 0.039288 | 0.037343 | 7235.7813 | 1297.464 | 840.9216 | 5097.3957 | 7265.5523 | 0 | 0 | 7265.5523 | 0.0004274%
2027 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 12.3028 | 1609 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 462.3957 | 12.1244 | 38.1375 | 462.3957 | 12.1244 | 38.1375 | 513.1287 | 13.4547 | 38.1375 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2027 | 558 | 558-301R | Tier-1 | Non-HFTD---1 | 2--5 | 2.4663 | 84 | 100% | 286.6551 | 99.35% | 0% | 0.6493% | 14.0973 | 0 | 0 | 14.0973 | 0 | 12.8284 | 2.4306 | 5.2779 | 12.8284 | 2.4306 | 5.2779 | 14.2358 | 2.6973 | 5.2779 | 4.918% | 0.010369 | 0.0098561 | 27644.3313 | 6740.2704 | 35.1226 | 20868.9383 | 27653.6787 | 0 | 0 | 27653.6787 | 0.0004649%
2027 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 19.9074 | 1772 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1170.8648 | 19.6187 | 59.681 | 1170.8648 | 19.6187 | 59.681 | 1299.3294 | 21.7712 | 59.681 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2027 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 3.397 | 63 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.7945 | 3.3477 | 3.5231 | 11.7945 | 3.3477 | 3.5231 | 13.0885 | 3.715 | 3.5231 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2027 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.47178 | 3 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 5.1466 | 0.46494 | 11.0693 | 5.1466 | 0.46494 | 11.0693 | 5.7112 | 0.51595 | 11.0693 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2027 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 1.6544 | 27 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 232.1001 | 1.6304 | 142.3605 | 232.1001 | 1.6304 | 142.3605 | 257.5656 | 1.8092 | 142.3605 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2027 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 22.0576 | 2114 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 154.9241 | 21.7378 | 7.127 | 154.9241 | 21.7378 | 7.127 | 171.922 | 24.1228 | 7.127 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2027 | 94 | 94-16F | Tier-1 | Non-HFTD---15 | 2--2 | 2.6851 | 41 | 100% | 4.4816 | 61.07% | 0% | 38.93% | 0.13547 | 0 | 0 | 0.13547 | 0 | 0.12328 | 2.6461 | 0.046587 | 0.12328 | 2.6461 | 0.046587 | 0.1368 | 2.9365 | 0.046587 | 3.023% | 0.007584 | 0.0072086 | 590.9306 | 44.9122 | 129.254 | 416.7645 | 602.9122 | 0 | 0 | 602.9122 | 4.467e-06%
2027 | 511 | 511-831 | Tier-1 | Non-HFTD---5 | 2--3 | 0.15682 | 10 | 100% | 45.7736 | 11.2% | 88.5% | 0.2943% | 0.25387 | 0 | 0 | 0.25387 | 0 | 0.23102 | 0.15454 | 1.4948 | 0.23102 | 0.15454 | 1.4948 | 0.25636 | 0.1715 | 1.4948 | 0.5546% | 0.011273 | 0.010715 | 4060.4617 | 56.9583 | 3419.2148 | 584.2885 | 4248.229 | 0 | 0 | 4248.229 | 8.372e-06%
2027 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 10.1674 | 862 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 249.9969 | 10.02 | 24.9499 | 249.9969 | 10.02 | 24.9499 | 277.426 | 11.1193 | 24.9499 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2027 | 571 | 571-49F | Tier-1 | Non-HFTD---11 | 2--2 | 4.1737 | 180 | 100% | 14.8937 | 75.79% | 0% | 24.21% | 0.55872 | 0 | 0 | 0.55872 | 0 | 0.50843 | 4.1131 | 0.12361 | 0.50843 | 4.1131 | 0.12361 | 0.56421 | 4.5644 | 0.12361 | 3.751% | 0.013087 | 0.01244 | 1138.0185 | 7.555 | 852.2014 | 278.2621 | 1152.3692 | 0 | 0 | 1152.3692 | 1.842e-05%
2027 | 161 | 161-610R | Tier-1 | Non-HFTD---8 | 4--2 | 15.3086 | 353 | 100% | 29.9374 | 67.56% | 0% | 32.44% | 1.0012 | 0 | 0 | 1.0012 | 0 | 0.91106 | 15.0866 | 0.060388 | 0.91106 | 15.0866 | 0.060388 | 1.011 | 16.7419 | 0.060388 | 3.344% | 0.041579 | 0.039521 | 720.0082 | 5.3968 | 475.6596 | 238.9517 | 732.172 | 0 | 0 | 732.172 | 3.302e-05%
2027 | PB1 | CB PB1 | Tier-1 | Non-HFTD---3 | 4--3 | 6.9699 | 84 | 100% | 137.6037 | 3.283% | 92.37% | 4.346% | 0.2236 | 0 | 0 | 0.2236 | 0 | 0.20347 | 6.8688 | 0.029622 | 0.20347 | 6.8688 | 0.029622 | 0.22579 | 7.6225 | 0.029622 | 0.1625% | 0.031616 | 0.030051 | 4352.3713 | 4.764 | 3790.0764 | 557.531 | 4571.5929 | 0 | 0 | 4571.5929 | 7.373e-06%
2027 | 257 | 257-31AE | Tier-1 | Non-HFTD---14 | 2--1 | 4.2349 | 159 | 100% | 5.7719 | 39.09% | 0% | 60.91% | 0.11168 | 0 | 0 | 0.11168 | 0 | 0.10163 | 4.1735 | 0.024351 | 0.10163 | 4.1735 | 0.024351 | 0.11278 | 4.6314 | 0.024351 | 1.935% | 0.012621 | 0.011996 | 457.3241 | 0.20961 | 204.0654 | 253.0491 | 471.8311 | 0 | 0 | 471.8311 | 3.683e-06%
2027 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 6.7335 | 568 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 655.4112 | 6.6359 | 98.7681 | 655.4112 | 6.6359 | 98.7681 | 727.3214 | 7.3639 | 98.7681 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2027 | 137 | CB 137 | Tier-1 | Non-HFTD---18 | 1--1 | 0.9422 | 16 | 100% | 0.70761 | 22.42% | 0% | 77.58% | 0.0078535 | 0 | 0 | 0.0078535 | 0 | 0.0071466 | 0.92854 | 0.0076966 | 0.0071466 | 0.92854 | 0.0076966 | 0.0079307 | 1.0304 | 0.0076966 | 1.11% | 0.0024496 | 0.0023283 | 288.869 | 0.16863 | 85.1261 | 203.5742 | 300.5396 | 0 | 0 | 300.5396 | 2.59e-07%
2027 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 0.0058712 | 6 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.077882 | 0.0057861 | 13.4602 | 0.077882 | 0.0057861 | 13.4602 | 0.086427 | 0.0064209 | 13.4602 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2027 | 120 | 120-360F | Tier-1 | Non-HFTD---9 | 2--3 | 0.90587 | 65 | 100% | 24.5458 | 1.164% | 95.41% | 3.43% | 0.014138 | 0 | 0 | 0.014138 | 0 | 0.012866 | 0.89274 | 0.014412 | 0.012866 | 0.89274 | 0.014412 | 0.014277 | 0.99069 | 0.014412 | 0.0576% | 0.010414 | 0.0098981 | 2357.0882 | 2.378 | 2024.3177 | 330.3924 | 2478.4119 | 0 | 0 | 2478.4119 | 4.662e-07%
2027 | WA1 | CB WA1 | Tier-1 | Non-HFTD---8 | 3--2 | 7.9261 | 417 | 100% | 35.576 | 87.53% | 0% | 12.47% | 1.5414 | 0 | 0 | 1.5414 | 0 | 1.4026 | 7.8112 | 0.17957 | 1.4026 | 7.8112 | 0.17957 | 1.5565 | 8.6682 | 0.17957 | 4.333% | 0.024123 | 0.022929 | 1474.761 | 154.3788 | 361.2267 | 959.1555 | 1484.3394 | 0 | 0 | 1484.3394 | 5.083e-05%
2027 | 1152 | CB 1152 | Tier-1 | Non-HFTD---17 | 1--2 | 0.225 | 0 | 100% | 1.2601 | 88.07% | 0% | 11.93% | 0.054936 | 0 | 0 | 0.054936 | 0 | 0.049991 | 0.22174 | 0.22545 | 0.049991 | 0.22174 | 0.22545 | 0.055476 | 0.24607 | 0.22545 | 4.36% | 0.0009632 | 0.00091552 | 1308.2728 | 166.1488 | 97.0862 | 1045.0378 | 1316.4 | 0 | 0 | 1316.4 | 1.812e-06%
2027 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 24.1038 | 1376 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 705.149 | 23.7544 | 29.685 | 705.149 | 23.7544 | 29.685 | 782.5163 | 26.3606 | 29.685 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2027 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 6.7626 | 86 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 132.7651 | 6.6645 | 19.9212 | 132.7651 | 6.6645 | 19.9212 | 147.3318 | 7.3957 | 19.9212 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2027 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.56254 | 0 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.5825 | 0.55438 | 10.0697 | 5.5825 | 0.55438 | 10.0697 | 6.195 | 0.61521 | 10.0697 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2027 | 948 | 948-5R | Tier-2 | Tier-2---21 | 1--2 | 0.64563 | 19 | 100% | 3.6494 | 90.16% | 0% | 9.838% | 0.16287 | 0 | 0 | 0.16287 | 0 | 0.14821 | 0.63627 | 0.23294 | 0.14821 | 0.63627 | 0.23294 | 0.16447 | 0.70608 | 0.23294 | 4.463% | 0.0023872 | 0.002269 | 1528.7338 | 203.4062 | 386.7322 | 938.5955 | 1536.5665 | 0 | 0 | 1536.5665 | 5.371e-06%
2027 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 4.5924 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 430.0662 | 4.5258 | 95.0255 | 430.0662 | 4.5258 | 95.0255 | 477.252 | 5.0224 | 95.0255 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2027 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 4.4941 | 255 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 410.7886 | 4.429 | 92.7506 | 410.7886 | 4.429 | 92.7506 | 455.8594 | 4.9149 | 92.7506 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2027 | 486 | 486-61R | Tier-1 | Non-HFTD---1 | 4--4 | 8.0996 | 279 | 100% | 415.5682 | 98.69% | 0% | 1.309% | 20.3013 | 0 | 0 | 20.3013 | 0 | 18.4739 | 7.9822 | 2.3144 | 18.4739 | 7.9822 | 2.3144 | 20.5008 | 8.8579 | 2.3144 | 4.885% | 0.031655 | 0.030088 | 13128.0422 | 2294.0601 | 163.567 | 10670.4151 | 13136.9945 | 0 | 0 | 13136.9945 | 0.0006695%
2027 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 8.7188 | 72 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 318.6899 | 8.5923 | 37.09 | 318.6899 | 8.5923 | 37.09 | 353.6559 | 9.5351 | 37.09 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2027 | 116 | 116-12R | Tier-1 | Non-HFTD---6 | 3--3 | 3.2824 | 68 | 100% | 54.5549 | 5.544% | 89.94% | 4.52% | 0.14973 | 0 | 0 | 0.14973 | 0 | 0.13625 | 3.2348 | 0.04212 | 0.13625 | 3.2348 | 0.04212 | 0.1512 | 3.5897 | 0.04212 | 0.2745% | 0.024461 | 0.02325 | 2230.262 | 3.7698 | 1966.9777 | 259.5146 | 2339.9695 | 0 | 0 | 2339.9695 | 4.937e-06%
2027 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 21.0708 | 1905 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 366.9683 | 20.7653 | 17.6722 | 366.9683 | 20.7653 | 17.6722 | 407.2312 | 23.0437 | 17.6722 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2027 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.41228 | 17 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 13.5232 | 0.40631 | 33.2831 | 13.5232 | 0.40631 | 33.2831 | 15.0069 | 0.45089 | 33.2831 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2027 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 8.3421 | 383 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1264.1257 | 8.2211 | 153.766 | 1264.1257 | 8.2211 | 153.766 | 1402.8226 | 9.1231 | 153.766 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2027 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 13.3513 | 1654 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 402.1167 | 13.1577 | 30.5613 | 402.1167 | 13.1577 | 30.5613 | 446.236 | 14.6014 | 30.5613 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2027 | 68 | CB 68 | Tier-1 | Non-HFTD---4 | 3--4 | 1.521 | 13 | 100% | 125.6028 | 97.63% | 1.574% | 0.7918% | 6.0702 | 0 | 0 | 6.0702 | 0 | 5.5238 | 1.499 | 3.6851 | 5.5238 | 1.499 | 3.6851 | 6.1299 | 1.6634 | 3.6851 | 4.833% | 0.015716 | 0.014938 | 7992.034 | 1382.4541 | 1171.7344 | 5437.8454 | 8001.8815 | 0 | 0 | 8001.8815 | 0.0002002%
2027 | 306 | CB 306 | Tier-1 | Non-HFTD---1 | 4--4 | 1.2839 | 275 | 100% | 737.4997 | 97.09% | 2.802% | 0.1119% | 35.4424 | 0 | 0 | 35.4424 | 0 | 32.2521 | 1.2653 | 25.4907 | 32.2521 | 1.2653 | 25.4907 | 35.7908 | 1.4041 | 25.4907 | 4.806% | 0.057753 | 0.054894 | 12769.9388 | 2020.535 | 320.1958 | 10429.208 | 12789.3181 | 0 | 0 | 12789.3181 | 0.001169%
2027 | OS5 | CB OS5 | Tier-1 | Non-HFTD---18 | 1--1 | 1.275 | 40 | 100% | 1.4382 | 31.82% | 0% | 68.18% | 0.022652 | 0 | 0 | 0.022652 | 0 | 0.020613 | 1.2566 | 0.016404 | 0.020613 | 1.2566 | 0.016404 | 0.022874 | 1.3944 | 0.016404 | 1.575% | 0.0036598 | 0.0034786 | 392.9844 | 0.52405 | 147.391 | 245.0693 | 406.9386 | 0 | 0 | 406.9386 | 7.47e-07%
2027 | 394 | 394-422F | Tier-1 | Non-HFTD---2 | 5--3 | 1.6971 | 43 | 100% | 314.1506 | 0.33% | 99.33% | 0.3425% | 0.051318 | 0 | 0 | 0.051318 | 0 | 0.046699 | 1.6725 | 0.027921 | 0.046699 | 1.6725 | 0.027921 | 0.051822 | 1.856 | 0.027921 | 0.01634% | 0.095311 | 0.090593 | 3296.0513 | 5.5188 | 2895.8033 | 394.7292 | 3467.1361 | 0 | 0 | 3467.1361 | 1.692e-06%
2027 | 171 | 171-708R | Tier-1 | Non-HFTD---3 | 4--3 | 12.6172 | 98 | 100% | 144.3815 | 64.32% | 29.9% | 5.783% | 4.597 | 0 | 0 | 4.597 | 0 | 4.1832 | 12.4343 | 0.33642 | 4.1832 | 12.4343 | 0.33642 | 4.6422 | 13.7985 | 0.33642 | 3.184% | 0.084326 | 0.080152 | 1712.186 | 173.3767 | 499.0152 | 1039.7942 | 1743.9994 | 0 | 0 | 1743.9994 | 0.0001516%
2027 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2.1411 | 4 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 19.4852 | 2.11 | 9.2346 | 19.4852 | 2.11 | 9.2346 | 21.6231 | 2.3415 | 9.2346 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2027 | 431 | 431-474 | Tier-1 | Non-HFTD---15 | 2--1 | 1.7021 | 18 | 100% | 2.429 | 35.21% | 0% | 64.79% | 0.04233 | 0 | 0 | 0.04233 | 0 | 0.03852 | 1.6774 | 0.022964 | 0.03852 | 1.6774 | 0.022964 | 0.042746 | 1.8615 | 0.022964 | 1.743% | 0.0053256 | 0.005062 | 456.099 | 0.22237 | 187.4203 | 268.4563 | 471.4893 | 0 | 0 | 471.4893 | 1.396e-06%
2027 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 2.4735 | 122 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 195.062 | 2.4377 | 80.0202 | 195.062 | 2.4377 | 80.0202 | 216.4638 | 2.7051 | 80.0202 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2027 | 476 | 476-6F | Tier-1 | Non-HFTD---10 | 5--1 | 0.074053 | 11 | 100% | 18.587 | 5.339% | 94.33% | 0.3325% | 0.049124 | 0 | 0 | 0.049124 | 0 | 0.044702 | 0.072979 | 0.61253 | 0.044702 | 0.072979 | 0.61253 | 0.049607 | 0.080986 | 0.61253 | 0.2643% | 0.15628 | 0.14854 | 118.9364 | 1.3234 | 95.4058 | 22.2073 | 124.7997 | 0 | 0 | 124.7997 | 1.62e-06%
2027 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 1.7031 | 141 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.2411 | 1.6784 | 2.5269 | 4.2411 | 1.6784 | 2.5269 | 4.7064 | 1.8625 | 2.5269 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2027 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 1.8653 | 473 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 17.4173 | 1.8383 | 9.4747 | 17.4173 | 1.8383 | 9.4747 | 19.3283 | 2.04 | 9.4747 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2027 | BF1 | CB BF1 | Tier-1 | Non-HFTD---9 | 2--3 | 1.6113 | 1 | 100% | 20.8946 | 91.56% | 0% | 8.439% | 0.947 | 0 | 0 | 0.947 | 0 | 0.86175 | 1.588 | 0.54268 | 0.86175 | 1.588 | 0.54268 | 0.9563 | 1.7622 | 0.54268 | 4.532% | 0.0060496 | 0.0057501 | 3453.8829 | 552.2417 | 48.3246 | 2853.3166 | 3469.0626 | 0 | 0 | 3469.0626 | 3.123e-05%
2027 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 3.6322 | 118 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.3274 | 3.5796 | 1.2089 | 4.3274 | 3.5796 | 1.2089 | 4.8022 | 3.9723 | 1.2089 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2027 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 16.0985 | 1221 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 388.0424 | 15.8651 | 24.4589 | 388.0424 | 15.8651 | 24.4589 | 430.6175 | 17.6057 | 24.4589 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2027 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 9.1409 | 907 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 152.8245 | 9.0084 | 16.9647 | 152.8245 | 9.0084 | 16.9647 | 169.592 | 9.9968 | 16.9647 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2027 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 17.9266 | 1368 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1837.8519 | 17.6666 | 104.0295 | 1837.8519 | 17.6666 | 104.0295 | 2039.4967 | 19.605 | 104.0295 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2027 | 297 | 297-828AE | Tier-1 | Non-HFTD---5 | 2--4 | 1.7713 | 112 | 100% | 51.9776 | 97.72% | 0% | 2.278% | 2.5143 | 0 | 0 | 2.5143 | 0 | 2.288 | 1.7456 | 1.3107 | 2.288 | 1.7456 | 1.3107 | 2.539 | 1.9371 | 1.3107 | 4.837% | 0.0062854 | 0.0059743 | 8269.5727 | 1759.1338 | 61.0431 | 6449.3958 | 8279.3842 | 0 | 0 | 8279.3842 | 8.291e-05%
2027 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 10.907 | 490 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 411.7972 | 10.7488 | 38.3109 | 411.7972 | 10.7488 | 38.3109 | 456.9786 | 11.9282 | 38.3109 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2027 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 3.6616 | 65 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 11.4291 | 3.6085 | 3.1673 | 11.4291 | 3.6085 | 3.1673 | 12.683 | 4.0044 | 3.1673 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2027 | 1076 | CB 1076 | Tier-1 | Non-HFTD---9 | 2--3 | 3.9479 | 154 | 100% | 20.7787 | 85.56% | 0% | 14.44% | 0.88007 | 0 | 0 | 0.88007 | 0 | 0.80085 | 3.8906 | 0.20584 | 0.80085 | 3.8906 | 0.20584 | 0.88872 | 4.3175 | 0.20584 | 4.235% | 0.011545 | 0.010974 | 1799.7403 | 1.5108 | 1555.3284 | 242.9011 | 1813.2706 | 0 | 0 | 1813.2706 | 2.902e-05%
2027 | CD4 | CB CD4 | Tier-1 | Non-HFTD---8 | 3--3 | 4.5362 | 259 | 100% | 39.5125 | 6.129% | 86.05% | 7.825% | 0.11988 | 0 | 0 | 0.11988 | 0 | 0.10909 | 4.4704 | 0.024402 | 0.10909 | 4.4704 | 0.024402 | 0.12106 | 4.9609 | 0.024402 | 0.3034% | 0.022929 | 0.021794 | 1723.2234 | 10.1387 | 1416.6051 | 296.4796 | 1807.4647 | 0 | 0 | 1807.4647 | 3.953e-06%
2027 | 412 | CB 412 | Tier-1 | Non-HFTD---1 | 4--5 | 17.7277 | 1039 | 100% | 1311.9921 | 88.37% | 10.81% | 0.8215% | 57.392 | 0 | 0 | 57.392 | 0 | 52.226 | 17.4706 | 2.9894 | 52.226 | 17.4706 | 2.9894 | 57.9561 | 19.3875 | 2.9894 | 4.374% | 0.071433 | 0.067897 | 18366.6483 | 2615.4927 | 2100.6109 | 13650.5447 | 18477.8687 | 0 | 0 | 18477.8687 | 0.001893%
2027 | 45 | 45-15AE | Tier-1 | Non-HFTD---11 | 1--3 | 0.56231 | 24 | 100% | 8.7551 | 92.94% | 0% | 7.056% | 0.4028 | 0 | 0 | 0.4028 | 0 | 0.36654 | 0.55416 | 0.66144 | 0.36654 | 0.55416 | 0.66144 | 0.40676 | 0.61496 | 0.66144 | 4.601% | 0.0022584 | 0.0021466 | 3876.685 | 65.548 | 3228.8334 | 582.3036 | 3890.931 | 0 | 0 | 3890.931 | 1.328e-05%
2027 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 0.80794 | 3 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 30.9346 | 0 | 0 | 30.9346 | 0 | 28.15 | 0.79623 | 35.3543 | 28.15 | 0.79623 | 35.3543 | 31.2386 | 0.88359 | 35.3543 | 4.945% | 0.0036434 | 0.0034631 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171700.5551 | 0 | 0 | 171700.5551 | 0.00102%
2027 | 795 | 795-816R | Tier-2 | Tier-2---13 | 4--4 | 6.4011 | 361 | 100% | 228.7654 | 4.756% | 93.08% | 2.167% | 0.53859 | 0 | 0 | 0.53859 | 0 | 0.49011 | 6.3083 | 0.077693 | 0.49011 | 6.3083 | 0.077693 | 0.54388 | 7.0005 | 0.077693 | 0.2354% | 0.036491 | 0.034684 | 6269.16 | 14.3219 | 5608.3339 | 646.5042 | 6580.116 | 0 | 0 | 6580.116 | 1.776e-05%
2027 | 859 | 859-1064 | Tier-1 | Non-HFTD---7 | 2--3 | 4.2178 | 255 | 100% | 40.2522 | 93.55% | 0% | 6.452% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.6962 | 4.1566 | 0.40806 | 1.6962 | 4.1566 | 0.40806 | 1.8823 | 4.6127 | 0.40806 | 4.631% | 0.011569 | 0.010996 | 3479.3123 | 521.49 | 92.9503 | 2864.872 | 3491.0022 | 0 | 0 | 3491.0022 | 6.147e-05%
2027 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 9.5078 | 505 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 550.9097 | 9.3699 | 58.7956 | 550.9097 | 9.3699 | 58.7956 | 611.3542 | 10.398 | 58.7956 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2027 | 1173 | 1173-70 | Tier-1 | Non-HFTD---9 | 2--3 | 0.44863 | 4 | 100% | 15.3764 | 0.6778% | 97.23% | 2.096% | 0.0051591 | 0 | 0 | 0.0051591 | 0 | 0.0046947 | 0.44212 | 0.010619 | 0.0046947 | 0.44212 | 0.010619 | 0.0052098 | 0.49063 | 0.010619 | 0.03355% | 0.008697 | 0.0082665 | 1768.0079 | 1.6115 | 1488.7681 | 277.6283 | 1859.4579 | 0 | 0 | 1859.4579 | 1.701e-07%
2027 | 386 | CB 386 | Tier-2 | Tier-2---14 | 4--4 | 7.9203 | 582 | 100% | 266.4482 | 58.89% | 39.19% | 1.927% | 7.7666 | 0 | 0 | 7.7666 | 0 | 7.0675 | 7.8054 | 0.90546 | 7.0675 | 7.8054 | 0.90546 | 7.8429 | 8.6618 | 0.90546 | 2.915% | 0.037437 | 0.035584 | 7117.2424 | 561.1032 | 3326.6838 | 3229.4554 | 7269.6317 | 0 | 0 | 7269.6317 | 0.0002561%
2027 | 122 | CB 122 | Tier-1 | Non-HFTD---13 | 2--2 | 2.0557 | 0 | 100% | 8.11 | 77.73% | 0% | 22.27% | 0.31204 | 0 | 0 | 0.31204 | 0 | 0.28395 | 2.0259 | 0.14016 | 0.28395 | 2.0259 | 0.14016 | 0.31511 | 2.2481 | 0.14016 | 3.848% | 0.0070694 | 0.0067195 | 1147.1966 | 45.0636 | 638.2561 | 463.8769 | 1160.5021 | 0 | 0 | 1160.5021 | 1.029e-05%
2027 | 172 | 172-630R | Tier-1 | Non-HFTD---6 | 4--2 | 4.8346 | 15 | 100% | 66.3107 | 6.519% | 90.48% | 2.997% | 0.21398 | 0 | 0 | 0.21398 | 0 | 0.19472 | 4.7645 | 0.040869 | 0.19472 | 4.7645 | 0.040869 | 0.21609 | 5.2873 | 0.040869 | 0.3227% | 0.053137 | 0.050507 | 1247.9203 | 10.8427 | 1030.4852 | 206.5924 | 1308.6726 | 0 | 0 | 1308.6726 | 7.056e-06%
2027 | CS1 | CB CS1 | Tier-1 | Non-HFTD---14 | 3--1 | 6.2901 | 165 | 100% | 6.8922 | 38.03% | 0% | 61.97% | 0.12974 | 0 | 0 | 0.12974 | 0 | 0.11807 | 6.1989 | 0.019046 | 0.11807 | 6.1989 | 0.019046 | 0.13102 | 6.879 | 0.019046 | 1.882% | 0.017311 | 0.016454 | 398.15 | 1.1079 | 168.1623 | 228.8798 | 410.9994 | 0 | 0 | 410.9994 | 4.278e-06%
2027 | 114 | 114-48 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0661 | 157 | 100% | 88.8606 | 4.08% | 91.67% | 4.249% | 0.17946 | 0 | 0 | 0.17946 | 0 | 0.16331 | 5.9781 | 0.027317 | 0.16331 | 5.9781 | 0.027317 | 0.18122 | 6.634 | 0.027317 | 0.202% | 0.02752 | 0.026158 | 3228.8995 | 11.4775 | 2773.9851 | 443.4369 | 3390.1931 | 0 | 0 | 3390.1931 | 5.918e-06%
2027 | 114 | CB 114 | Tier-1 | Non-HFTD---7 | 2--3 | 1.6892 | 172 | 100% | 43.2481 | 88.83% | 8.106% | 3.062% | 1.9017 | 0 | 0 | 1.9017 | 0 | 1.7305 | 1.6647 | 1.0395 | 1.7305 | 1.6647 | 1.0395 | 1.9204 | 1.8474 | 1.0395 | 4.397% | 0.013188 | 0.012535 | 3279.4498 | 356.1869 | 963.7932 | 1959.4698 | 3298.5242 | 0 | 0 | 3298.5242 | 6.271e-05%
2027 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 0.26853 | 62 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.8496 | 0.26464 | 6.9893 | 1.8496 | 0.26464 | 6.9893 | 2.0526 | 0.29367 | 6.9893 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2027 | 390 | 390-15 | Tier-1 | Non-HFTD---2 | 5--3 | 1.561 | 36 | 100% | 260.9963 | 0.6321% | 98.96% | 0.4064% | 0.081661 | 0 | 0 | 0.081661 | 0 | 0.07431 | 1.5383 | 0.048306 | 0.07431 | 1.5383 | 0.048306 | 0.082464 | 1.7071 | 0.048306 | 0.03129% | 0.099654 | 0.094722 | 2619.0141 | 6.4394 | 2346.7211 | 265.8535 | 2754.5446 | 0 | 0 | 2754.5446 | 2.693e-06%
2027 | 257 | 257-29AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.4854 | 75 | 100% | 2.2983 | 19.76% | 0% | 80.24% | 0.022484 | 0 | 0 | 0.022484 | 0 | 0.02046 | 2.4494 | 0.0083532 | 0.02046 | 2.4494 | 0.0083532 | 0.022705 | 2.7181 | 0.0083532 | 0.9783% | 0.006989 | 0.006643 | 328.8485 | 0.19854 | 88.9601 | 239.6899 | 342.5897 | 0 | 0 | 342.5897 | 7.414e-07%
2027 | 189 | CB 189 | Tier-1 | Non-HFTD---7 | 2--4 | 1.6267 | 68 | 100% | 36.5503 | 96.65% | 0% | 3.352% | 1.7486 | 0 | 0 | 1.7486 | 0 | 1.5912 | 1.6031 | 0.99255 | 1.5912 | 1.6031 | 0.99255 | 1.7658 | 1.779 | 0.99255 | 4.784% | 0.0052996 | 0.0050373 | 6896.7976 | 807.5104 | 1754.8536 | 4334.4335 | 6908.8371 | 0 | 0 | 6908.8371 | 5.766e-05%
2027 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 13.4125 | 974 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 73.1226 | 13.218 | 5.532 | 73.1226 | 13.218 | 5.532 | 81.1454 | 14.6683 | 5.532 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2027 | 310 | 310-9R | Tier-1 | Non-HFTD---13 | 1--3 | 1.5318 | 84 | 100% | 7.8805 | 85.45% | 0% | 14.55% | 0.33331 | 0 | 0 | 0.33331 | 0 | 0.30331 | 1.5096 | 0.20092 | 0.30331 | 1.5096 | 0.20092 | 0.33659 | 1.6752 | 0.20092 | 4.23% | 0.0044784 | 0.0042567 | 1759.6775 | 1.0284 | 1521.6386 | 237.0105 | 1773.015 | 0 | 0 | 1773.015 | 1.099e-05%
2027 | 69 | CB 69 | Tier-1 | Non-HFTD---5 | 2--3 | 1.1767 | 12 | 100% | 50.7962 | 92.2% | 5.783% | 2.017% | 2.3183 | 0 | 0 | 2.3183 | 0 | 2.1096 | 1.1597 | 1.8191 | 2.1096 | 1.1597 | 1.8191 | 2.3411 | 1.2869 | 1.8191 | 4.564% | 0.011719 | 0.011139 | 4334.4449 | 720.874 | 567.5626 | 3046.0083 | 4352.0516 | 0 | 0 | 4352.0516 | 7.645e-05%
2027 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 6.1356 | 334 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 98.5708 | 6.0466 | 16.3017 | 98.5708 | 6.0466 | 16.3017 | 109.3858 | 6.7101 | 16.3017 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2027 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 2.0289 | 257 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 30.0435 | 1.9995 | 15.0253 | 30.0435 | 1.9995 | 15.0253 | 33.3398 | 2.2189 | 15.0253 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2027 | 242 | 242-1411F | Tier-1 | Non-HFTD---1 | 5--4 | 0.27213 | 21 | 100% | 861.0308 | 0.3297% | 99.65% | 0.02489% | 0.14053 | 0 | 0 | 0.14053 | 0 | 0.12788 | 0.26819 | 0.47682 | 0.12788 | 0.26819 | 0.47682 | 0.14191 | 0.29761 | 0.47682 | 0.01632% | 0.09372 | 0.08908 | 9187.308 | 16.4683 | 8354.5754 | 816.2643 | 9664.1858 | 0 | 0 | 9664.1858 | 4.634e-06%
2027 | CA2 | CB CA2 | Tier-1 | Non-HFTD---9 | 2--2 | 0.94321 | 19 | 100% | 20.4637 | 1.406% | 94.71% | 3.883% | 0.014245 | 0 | 0 | 0.014245 | 0 | 0.012963 | 0.92953 | 0.013946 | 0.012963 | 0.92953 | 0.013946 | 0.014385 | 1.0315 | 0.013946 | 0.06961% | 0.013315 | 0.012656 | 1536.8705 | 2.0039 | 1342.2543 | 192.6124 | 1615.7819 | 0 | 0 | 1615.7819 | 4.698e-07%
2027 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 29.2157 | 767 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 375.994 | 28.7921 | 13.0589 | 375.994 | 28.7921 | 13.0589 | 417.2472 | 31.9511 | 13.0589 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2027 | 488 | CB 488 | Tier-1 | Non-HFTD---15 | 1--2 | 1.7068 | 32 | 100% | 3.9951 | 71.83% | 0% | 28.17% | 0.14206 | 0 | 0 | 0.14206 | 0 | 0.12927 | 1.682 | 0.076852 | 0.12927 | 1.682 | 0.076852 | 0.14345 | 1.8666 | 0.076852 | 3.556% | 0.0047686 | 0.0045326 | 837.8017 | 0.17757 | 623.2495 | 214.3746 | 850.0916 | 0 | 0 | 850.0916 | 4.684e-06%
2027 | 56 | 56-669F | Tier-1 | Non-HFTD---4 | 2--4 | 0.57918 | 1 | 100% | 107.608 | 0.09989% | 99.43% | 0.4717% | 0.0053209 | 0 | 0 | 0.0053209 | 0 | 0.004842 | 0.57078 | 0.0084831 | 0.004842 | 0.57078 | 0.0084831 | 0.0053732 | 0.6334 | 0.0084831 | 0.004945% | 0.012314 | 0.011705 | 8738.387 | 10.1815 | 7924.2222 | 803.9833 | 9193.0088 | 0 | 0 | 9193.0088 | 1.755e-07%
2027 | 308 | 308-485AE | Tier-2 | Tier-2---15 | 4--3 | 1.6722 | 57 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.217 | 0 | 0 | 0.217 | 0 | 0.19746 | 1.6479 | 0.11982 | 0.19746 | 1.6479 | 0.11982 | 0.21913 | 1.8287 | 0.11982 | 0.1374% | 0.034738 | 0.033018 | 4547.6785 | 25.2626 | 4047.4864 | 474.9295 | 4777.9399 | 0 | 0 | 4777.9399 | 7.156e-06%
2027 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.77126 | 73 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 35.3002 | 0.76007 | 46.4431 | 35.3002 | 0.76007 | 46.4431 | 39.1733 | 0.84347 | 46.4431 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2027 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 1.5712 | 55 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 20.502 | 1.5484 | 13.2405 | 20.502 | 1.5484 | 13.2405 | 22.7514 | 1.7183 | 13.2405 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2027 | 40 | CB 40 | Tier-1 | Non-HFTD---6 | 3--3 | 7.115 | 166 | 100% | 69.5172 | 93.23% | 0% | 6.766% | 3.2083 | 0 | 0 | 3.2083 | 0 | 2.9195 | 7.0118 | 0.41637 | 2.9195 | 7.0118 | 0.41637 | 3.2398 | 7.7812 | 0.41637 | 4.615% | 0.021321 | 0.020266 | 3260.5047 | 598.6862 | 390.1907 | 2271.6278 | 3271.993 | 0 | 0 | 3271.993 | 0.0001058%
2027 | 137 | 137-34AE | Tier-1 | Non-HFTD---16 | 2--1 | 3.2265 | 148 | 100% | 3.1884 | 24.97% | 0% | 75.03% | 0.039416 | 0 | 0 | 0.039416 | 0 | 0.035868 | 3.1797 | 0.01128 | 0.035868 | 3.1797 | 0.01128 | 0.039803 | 3.5286 | 0.01128 | 1.236% | 0.0099752 | 0.0094814 | 319.6366 | 0.18045 | 101.6106 | 217.8455 | 332.1254 | 0 | 0 | 332.1254 | 1.3e-06%
2027 | 275 | 275-48F | Tier-1 | Non-HFTD---3 | 3--4 | 3.4754 | 51 | 100% | 122.1483 | 5.775% | 92.83% | 1.397% | 0.34918 | 0 | 0 | 0.34918 | 0 | 0.31775 | 3.425 | 0.092774 | 0.31775 | 3.425 | 0.092774 | 0.35261 | 3.8008 | 0.092774 | 0.2859% | 0.024465 | 0.023254 | 4992.7367 | 48.2186 | 4344.9921 | 599.526 | 5237.7319 | 0 | 0 | 5237.7319 | 1.151e-05%
2027 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 2.9135 | 351 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 225.6484 | 2.8712 | 78.5897 | 225.6484 | 2.8712 | 78.5897 | 250.406 | 3.1862 | 78.5897 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2027 | NC3 | CB NC3 | Tier-1 | Non-HFTD---18 | 1--1 | 1.3062 | 16 | 100% | 1.3141 | 19.33% | 0% | 80.67% | 0.012576 | 0 | 0 | 0.012576 | 0 | 0.011444 | 1.2873 | 0.0088904 | 0.011444 | 1.2873 | 0.0088904 | 0.0127 | 1.4285 | 0.0088904 | 0.9571% | 0.004054 | 0.0038533 | 324.1367 | 12.2073 | 35.4768 | 276.4527 | 337.7533 | 0 | 0 | 337.7533 | 4.147e-07%
2027 | 341 | 341-1155F | Tier-1 | Non-HFTD---1 | 3--5 | 4.5127 | 433 | 100% | 374.3613 | 99.24% | 0% | 0.7589% | 18.3903 | 0 | 0 | 18.3903 | 0 | 16.7349 | 4.4472 | 3.763 | 16.7349 | 4.4472 | 3.763 | 18.571 | 4.9352 | 3.763 | 4.912% | 0.015477 | 0.014711 | 24187.611 | 4353.0066 | 31.6958 | 19802.9086 | 24197.1702 | 0 | 0 | 24197.1702 | 0.0006064%
2027 | BN1 | CB BN1 | Tier-1 | Non-HFTD---4 | 4--4 | 10.2073 | 521 | 100% | 173.8031 | 96.37% | 0% | 3.629% | 8.291 | 0 | 0 | 8.291 | 0 | 7.5447 | 10.0593 | 0.75002 | 7.5447 | 10.0593 | 0.75002 | 8.3725 | 11.163 | 0.75002 | 4.77% | 0.028851 | 0.027423 | 6024.1621 | 939.3966 | 90.5041 | 4994.2615 | 6035.548 | 0 | 0 | 6035.548 | 0.0002734%
2027 | 255 | 255-1080R | Tier-1 | Non-HFTD---18 | 2--1 | 2.5939 | 84 | 100% | 2.1745 | 29.65% | 0% | 70.35% | 0.031915 | 0 | 0 | 0.031915 | 0 | 0.029042 | 2.5563 | 0.011361 | 0.029042 | 2.5563 | 0.011361 | 0.032229 | 2.8368 | 0.011361 | 1.468% | 0.006657 | 0.0063275 | 326.6462 | 0.17291 | 117.7275 | 208.7459 | 338.6134 | 0 | 0 | 338.6134 | 1.052e-06%
2027 | 454 | 454-47R | Tier-1 | Non-HFTD---17 | 1--2 | 0.27501 | 6 | 100% | 0.77526 | 68.13% | 0% | 31.87% | 0.026144 | 0 | 0 | 0.026144 | 0 | 0.023791 | 0.27102 | 0.087782 | 0.023791 | 0.27102 | 0.087782 | 0.026401 | 0.30076 | 0.087782 | 3.372% | 0.0008848 | 0.000841 | 876.1933 | 0.21014 | 622.2981 | 253.6851 | 890.7368 | 0 | 0 | 890.7368 | 8.621e-07%
2027 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.94526 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 161.8413 | 0.93155 | 173.7332 | 161.8413 | 0.93155 | 173.7332 | 179.5981 | 1.0338 | 173.7332 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2027 | ES4 | CB ES4 | Tier-1 | Non-HFTD---10 | 4--1 | 15.6208 | 619 | 100% | 17.8102 | 40.04% | 0% | 59.96% | 0.35302 | 0 | 0 | 0.35302 | 0 | 0.32125 | 15.3943 | 0.020868 | 0.32125 | 15.3943 | 0.020868 | 0.35649 | 17.0833 | 0.020868 | 1.982% | 0.043584 | 0.041426 | 408.6447 | 3.4145 | 166.1409 | 239.0894 | 421.4043 | 0 | 0 | 421.4043 | 1.164e-05%
2027 | SR1 | CB SR1 | Tier-1 | Non-HFTD---12 | 4--1 | 11.5445 | 296 | 100% | 12.5988 | 40.76% | 0% | 59.24% | 0.25419 | 0 | 0 | 0.25419 | 0 | 0.23131 | 11.3771 | 0.020331 | 0.23131 | 11.3771 | 0.020331 | 0.25669 | 12.6254 | 0.020331 | 2.018% | 0.032342 | 0.030741 | 389.5505 | 31.2637 | 84.0563 | 274.2304 | 401.5686 | 0 | 0 | 401.5686 | 8.382e-06%
2027 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 17.63 | 253 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 21.2889 | 17.3743 | 1.2253 | 21.2889 | 17.3743 | 1.2253 | 23.6247 | 19.2806 | 1.2253 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2027 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 4.3521 | 411 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 140.9108 | 4.289 | 32.8542 | 140.9108 | 4.289 | 32.8542 | 156.3712 | 4.7595 | 32.8542 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2027 | 280 | 280-24AE | Tier-2 | Tier-2---12 | 4--4 | 2.1642 | 148 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.56941 | 0 | 0 | 0.56941 | 0 | 0.51815 | 2.1329 | 0.24294 | 0.51815 | 2.1329 | 0.24294 | 0.575 | 2.3669 | 0.24294 | 0.1557% | 0.037093 | 0.035257 | 9861.3901 | 49.7133 | 8813.1546 | 998.5222 | 10358.7999 | 0 | 0 | 10358.7999 | 1.878e-05%
2027 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 9.9068 | 758 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 81.859 | 9.7632 | 8.3845 | 81.859 | 9.7632 | 8.3845 | 90.8403 | 10.8344 | 8.3845 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2027 | 1072 | 1072-6 | Tier-1 | Non-HFTD---1 | 3--4 | 0.23504 | 5 | 100% | 193.6121 | 0.3692% | 99.58% | 0.05199% | 0.035387 | 0 | 0 | 0.035387 | 0 | 0.032202 | 0.23163 | 0.13902 | 0.032202 | 0.23163 | 0.13902 | 0.035735 | 0.25704 | 0.13902 | 0.01828% | 0.01694 | 0.016102 | 11429.1521 | 20.5352 | 10413.4738 | 995.1431 | 12022.16 | 0 | 0 | 12022.16 | 1.167e-06%
2027 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 7.8127 | 466 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 869.0928 | 7.6994 | 112.8782 | 869.0928 | 7.6994 | 112.8782 | 964.4476 | 8.5441 | 112.8782 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2027 | CD1 | CB CD1 | Tier-1 | Non-HFTD---7 | 3--3 | 1.308 | 51 | 100% | 43.6009 | 1.546% | 95.78% | 2.676% | 0.033356 | 0 | 0 | 0.033356 | 0 | 0.030354 | 1.289 | 0.023548 | 0.030354 | 1.289 | 0.023548 | 0.033684 | 1.4305 | 0.023548 | 0.0765% | 0.014488 | 0.01377 | 3009.5292 | 3.7078 | 2622.1215 | 383.7 | 3163.8368 | 0 | 0 | 3163.8368 | 1.1e-06%
2027 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 0.049053 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.09892 | 0.048342 | 2.0463 | 0.09892 | 0.048342 | 2.0463 | 0.10977 | 0.053646 | 2.0463 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2027 | 434 | CB 434 | Tier-1 | Non-HFTD---11 | 1--4 | 0.56686 | 54 | 100% | 12.9164 | 95.4% | 0% | 4.605% | 0.60992 | 0 | 0 | 0.60992 | 0 | 0.55502 | 0.55864 | 0.99353 | 0.55502 | 0.55864 | 0.99353 | 0.61592 | 0.61993 | 0.99353 | 4.722% | 0.0024398 | 0.002319 | 5294.056 | 339.8058 | 2981.8904 | 1972.3599 | 5306.7514 | 0 | 0 | 5306.7514 | 2.011e-05%
2027 | 60 | 60-603F | Tier-1 | Non-HFTD---3 | 4--4 | 6.0002 | 140 | 100% | 169.5135 | 9.049% | 88.6% | 2.35% | 0.75926 | 0 | 0 | 0.75926 | 0 | 0.69092 | 5.9132 | 0.11684 | 0.69092 | 5.9132 | 0.11684 | 0.76672 | 6.562 | 0.11684 | 0.4479% | 0.032694 | 0.031076 | 5184.8494 | 70.8257 | 4426.3803 | 687.6434 | 5430.4326 | 0 | 0 | 5430.4326 | 2.504e-05%
2027 | 282 | 282-565F | Tier-1 | Non-HFTD---6 | 4--3 | 0.85098 | 17 | 100% | 89.9778 | 0.4154% | 98.82% | 0.7661% | 0.018499 | 0 | 0 | 0.018499 | 0 | 0.016834 | 0.83864 | 0.020073 | 0.016834 | 0.83864 | 0.020073 | 0.018681 | 0.93065 | 0.020073 | 0.02056% | 0.032683 | 0.031065 | 2753.0459 | 5.5294 | 2228.0176 | 519.4989 | 2895.8231 | 0 | 0 | 2895.8231 | 6.1e-07%
2027 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 1.4693 | 17 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 91.1498 | 1.448 | 62.9494 | 91.1498 | 1.448 | 62.9494 | 101.1506 | 1.6069 | 62.9494 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2027 | 38 | 38-11 | Tier-1 | Non-HFTD---10 | 4--2 | 9.7832 | 399 | 100% | 25.7057 | 75.43% | 0% | 24.57% | 0.95975 | 0 | 0 | 0.95975 | 0 | 0.87336 | 9.6413 | 0.090585 | 0.87336 | 9.6413 | 0.090585 | 0.96919 | 10.6991 | 0.090585 | 3.734% | 0.028609 | 0.027193 | 898.5174 | 56.9208 | 481.0436 | 360.553 | 910.0159 | 0 | 0 | 910.0159 | 3.165e-05%
2027 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 5.8841 | 510 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 68.7275 | 5.7988 | 11.8521 | 68.7275 | 5.7988 | 11.8521 | 76.2681 | 6.435 | 11.8521 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2027 | 43 | 43-445 | Tier-1 | Non-HFTD---10 | 4--2 | 11.0882 | 259 | 100% | 17.7138 | 50.11% | 0% | 49.89% | 0.43939 | 0 | 0 | 0.43939 | 0 | 0.39984 | 10.9275 | 0.036591 | 0.39984 | 10.9275 | 0.036591 | 0.44371 | 12.1264 | 0.036591 | 2.481% | 0.033392 | 0.031739 | 530.477 | 16.8718 | 186.6503 | 326.9548 | 544.2593 | 0 | 0 | 544.2593 | 1.449e-05%
2027 | 297 | CB 297 | Tier-2 | Tier-2---19 | 1--3 | 0.42898 | 9 | 100% | 7.4286 | 94.8% | 0% | 5.203% | 0.34859 | 0 | 0 | 0.34859 | 0 | 0.31721 | 0.42276 | 0.75033 | 0.31721 | 0.42276 | 0.75033 | 0.35201 | 0.46914 | 0.75033 | 4.692% | 0.0019588 | 0.0018618 | 3792.4284 | 350.5573 | 1464.3094 | 1977.5617 | 3802.7036 | 0 | 0 | 3802.7036 | 1.15e-05%
2027 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 11.5801 | 478 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 460.7021 | 11.4122 | 40.3693 | 460.7021 | 11.4122 | 40.3693 | 511.2492 | 12.6643 | 40.3693 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2027 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 6.0637 | 149 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 48.0153 | 5.9757 | 8.035 | 48.0153 | 5.9757 | 8.035 | 53.2834 | 6.6314 | 8.035 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2027 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 19.582 | 1188 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1192.3964 | 19.2981 | 61.7884 | 1192.3964 | 19.2981 | 61.7884 | 1323.2233 | 21.4154 | 61.7884 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2027 | 1071 | 1071-226F | Tier-1 | Non-HFTD---9 | 1--4 | 0.36818 | 42 | 100% | 15.0528 | 98.32% | 0% | 1.683% | 0.73257 | 0 | 0 | 0.73257 | 0 | 0.66663 | 0.36284 | 1.8372 | 0.66663 | 0.36284 | 1.8372 | 0.73977 | 0.40265 | 1.8372 | 4.867% | 0.0017068 | 0.0016223 | 8819.3233 | 1269.9582 | 917.792 | 6631.5731 | 8827.0536 | 0 | 0 | 8827.0536 | 2.416e-05%
2027 | 331 | CB 331 | Tier-2 | Tier-2---14 | 2--5 | 2.8949 | 3 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 12.8498 | 0 | 0 | 12.8498 | 0 | 11.6932 | 2.8529 | 4.0987 | 11.6932 | 2.8529 | 4.0987 | 12.9761 | 3.1659 | 4.0987 | 4.919% | 0.010352 | 0.0098396 | 25232.8512 | 3536.4388 | 3219.2744 | 18477.138 | 25240.9927 | 0 | 0 | 25240.9927 | 0.0004237%
2027 | 920 | CB 920 | Tier-1 | Non-HFTD---1 | 1--5 | 0.96496 | 63 | 100% | 251.9037 | 99.78% | 0% | 0.2231% | 12.4414 | 0 | 0 | 12.4414 | 0 | 11.3215 | 0.95097 | 11.9052 | 11.3215 | 0.95097 | 11.9052 | 12.5637 | 1.0553 | 11.9052 | 4.939% | 0.0036978 | 0.0035148 | 68122.5856 | 11982.8045 | 3000.2837 | 53139.4975 | 68130.5015 | 0 | 0 | 68130.5015 | 0.0004103%
2027 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 33.1318 | 3002 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 144.3433 | 32.6514 | 4.4207 | 144.3433 | 32.6514 | 4.4207 | 160.1803 | 36.2339 | 4.4207 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2027 | 243 | 243-14R | Tier-2 | Tier-2---11 | 4--4 | 13.05 | 653 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 5.9029 | 0 | 0 | 5.9029 | 0 | 5.3716 | 12.8608 | 0.41767 | 5.3716 | 12.8608 | 0.41767 | 5.9609 | 14.2719 | 0.41767 | 1.46% | 0.066445 | 0.063156 | 6084.1314 | 280.7794 | 3933.5085 | 1869.8435 | 6307.5143 | 0 | 0 | 6307.5143 | 0.0001947%
2027 | OH1 | CB OH1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2021 | 28 | 100% | 1.3845 | 20.15% | 0% | 79.85% | 0.013811 | 0 | 0 | 0.013811 | 0 | 0.012568 | 1.1846 | 0.010609 | 0.012568 | 1.1846 | 0.010609 | 0.013947 | 1.3146 | 0.010609 | 0.9975% | 0.003942 | 0.0037469 | 351.2235 | 0.21102 | 96.2554 | 254.7571 | 365.8284 | 0 | 0 | 365.8284 | 4.554e-07%
2027 | PH1 | CB PH1 | Tier-1 | Non-HFTD---18 | 1--1 | 0.61361 | 30 | 100% | 0.70429 | 28.38% | 0% | 71.62% | 0.0098948 | 0 | 0 | 0.0098948 | 0 | 0.0090041 | 0.60471 | 0.01489 | 0.0090041 | 0.60471 | 0.01489 | 0.009992 | 0.67106 | 0.01489 | 1.405% | 0.0018738 | 0.001781 | 375.86 | 13.3825 | 50.7092 | 311.7684 | 389.8784 | 0 | 0 | 389.8784 | 3.263e-07%
2027 | 289 | 289-905AE | Tier-1 | Non-HFTD---8 | 3--3 | 4.6523 | 300 | 100% | 40.9452 | 16.44% | 75.92% | 7.645% | 0.33316 | 0 | 0 | 0.33316 | 0 | 0.30317 | 4.5848 | 0.066124 | 0.30317 | 4.5848 | 0.066124 | 0.33643 | 5.0879 | 0.066124 | 0.8137% | 0.0188 | 0.01787 | 2177.8917 | 8.1279 | 1808.1136 | 361.6502 | 2272.6681 | 0 | 0 | 2272.6681 | 1.099e-05%
2027 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 14.3572 | 1792 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 217.2304 | 14.1491 | 15.353 | 217.2304 | 14.1491 | 15.353 | 241.0644 | 15.7015 | 15.353 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2027 | 154 | 154-894R | Tier-1 | Non-HFTD---14 | 3--1 | 8.141 | 246 | 100% | 8.6688 | 30.94% | 0% | 69.06% | 0.13274 | 0 | 0 | 0.13274 | 0 | 0.1208 | 8.0229 | 0.015056 | 0.1208 | 8.0229 | 0.015056 | 0.13405 | 8.9032 | 0.015056 | 1.531% | 0.023715 | 0.022541 | 365.5396 | 2.5977 | 126.4957 | 236.4462 | 378.6872 | 0 | 0 | 378.6872 | 4.377e-06%
2027 | 443 | CB 443 | Tier-2 | Tier-2---17 | 2--4 | 1.7657 | 0 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 3.2669 | 0 | 0 | 3.2669 | 0 | 2.9729 | 1.7401 | 1.7084 | 2.9729 | 1.7401 | 1.7084 | 3.299 | 1.931 | 1.7084 | 4.865% | 0.007405 | 0.0070385 | 9067.8323 | 1863.6752 | 20.0371 | 7184.12 | 9075.9094 | 0 | 0 | 9075.9094 | 0.0001077%
2027 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 4.1521 | 373 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16842 | 4.0919 | 0.04116 | 0.16842 | 4.0919 | 0.04116 | 0.1869 | 4.5409 | 0.04116 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2027 | 707 | CB 707 | Tier-1 | Non-HFTD---9 | 2--3 | 0.76856 | 33 | 100% | 24.2722 | 35% | 62.06% | 2.94% | 0.42051 | 0 | 0 | 0.42051 | 0 | 0.38266 | 0.75742 | 0.50522 | 0.38266 | 0.75742 | 0.50522 | 0.42465 | 0.84052 | 0.50522 | 1.732% | 0.0080484 | 0.00765 | 3015.7851 | 147.2421 | 1865.593 | 1002.95 | 3117.8717 | 0 | 0 | 3117.8717 | 1.387e-05%
2027 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 3.7048 | 795 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 119.8785 | 3.6511 | 32.8339 | 119.8785 | 3.6511 | 32.8339 | 133.0313 | 4.0516 | 32.8339 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2027 | 547 | 547-22R | Tier-1 | Non-HFTD---13 | 2--2 | 3.5843 | 62 | 100% | 7.8544 | 68.58% | 0% | 31.42% | 0.26665 | 0 | 0 | 0.26665 | 0 | 0.24265 | 3.5323 | 0.068694 | 0.24265 | 3.5323 | 0.068694 | 0.26927 | 3.9199 | 0.068694 | 3.395% | 0.010488 | 0.009969 | 748.881 | 11.7437 | 463.65 | 273.4873 | 761.1333 | 0 | 0 | 761.1333 | 8.793e-06%
2027 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 1.532 | 0 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 256.5422 | 1.5098 | 169.9186 | 256.5422 | 1.5098 | 169.9186 | 284.6894 | 1.6754 | 169.9186 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2027 | 452 | CB 452 | Tier-1 | Non-HFTD---10 | 3--2 | 7.2271 | 173 | 100% | 25.8874 | 80.5% | 0% | 19.5% | 1.0316 | 0 | 0 | 1.0316 | 0 | 0.93872 | 7.1223 | 0.1318 | 0.93872 | 7.1223 | 0.1318 | 1.0417 | 7.9038 | 0.1318 | 3.985% | 0.020795 | 0.019766 | 1244.886 | 0.18265 | 1024.2061 | 220.4972 | 1257.5268 | 0 | 0 | 1257.5268 | 3.402e-05%
2027 | 731 | 731-1245F | Tier-1 | Non-HFTD---17 | 1--2 | 0.46347 | 27 | 100% | 1.7231 | 81.35% | 0% | 18.65% | 0.06939 | 0 | 0 | 0.06939 | 0 | 0.063144 | 0.45675 | 0.13825 | 0.063144 | 0.45675 | 0.13825 | 0.070072 | 0.50686 | 0.13825 | 4.027% | 0.0013412 | 0.0012748 | 1284.744 | 169.7674 | 30.9305 | 1084.0462 | 1297.2191 | 0 | 0 | 1297.2191 | 2.288e-06%
2027 | 556 | CB 556 | Tier-1 | Non-HFTD---1 | 2--5 | 1.5472 | 11 | 100% | 422.664 | 99.75% | 0% | 0.2546% | 20.8686 | 0 | 0 | 20.8686 | 0 | 18.9901 | 1.5247 | 12.4548 | 18.9901 | 1.5247 | 12.4548 | 21.0737 | 1.692 | 12.4548 | 4.937% | 0.0069694 | 0.0066244 | 60645.6807 | 39316.7744 | 1050.0285 | 20278.8779 | 60653.7228 | 0 | 0 | 60653.7228 | 0.0006882%
2027 | 723 | CB 723 | Tier-1 | Non-HFTD---10 | 3--2 | 5.7311 | 124 | 100% | 19.8762 | 84.22% | 0% | 15.78% | 0.82858 | 0 | 0 | 0.82858 | 0 | 0.754 | 5.648 | 0.1335 | 0.754 | 5.648 | 0.1335 | 0.83672 | 6.2676 | 0.1335 | 4.169% | 0.01527 | 0.014514 | 1301.6828 | 11.1848 | 1047.4878 | 243.0102 | 1312.3823 | 0 | 0 | 1312.3823 | 2.732e-05%
2027 | 401 | 401-39R | Tier-2 | Tier-2---14 | 4--4 | 0.64865 | 64 | 100% | 323.2323 | 3.193% | 96.7% | 0.1048% | 0.51091 | 0 | 0 | 0.51091 | 0 | 0.46492 | 0.63925 | 0.72729 | 0.46492 | 0.63925 | 0.72729 | 0.51593 | 0.70938 | 0.72729 | 0.1581% | 0.031872 | 0.030295 | 10141.4477 | 77.0794 | 9013.6522 | 1050.7162 | 10652.728 | 0 | 0 | 10652.728 | 1.685e-05%
2027 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 5.3305 | 262 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 99.8502 | 5.2532 | 19.0075 | 99.8502 | 5.2532 | 19.0075 | 110.8055 | 5.8296 | 19.0075 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2027 | EO1 | CB EO1 | Tier-1 | Non-HFTD---10 | 3--2 | 8.4572 | 310 | 100% | 23.8797 | 77.35% | 0% | 22.65% | 0.91436 | 0 | 0 | 0.91436 | 0 | 0.83205 | 8.3346 | 0.099831 | 0.83205 | 8.3346 | 0.099831 | 0.92334 | 9.2491 | 0.099831 | 3.829% | 0.022403 | 0.021294 | 1065.904 | 118.5711 | 123.3524 | 823.9805 | 1078.4747 | 0 | 0 | 1078.4747 | 3.015e-05%
2027 | 416 | 416-21 | Tier-1 | Non-HFTD---9 | 2--3 | 2.1076 | 56 | 100% | 17.0536 | 88.2% | 0% | 11.8% | 0.74451 | 0 | 0 | 0.74451 | 0 | 0.6775 | 2.077 | 0.32619 | 0.6775 | 2.077 | 0.32619 | 0.75183 | 2.3049 | 0.32619 | 4.366% | 0.0069518 | 0.0066077 | 2453.1267 | 2.6942 | 2174.6936 | 275.7389 | 2468.2065 | 0 | 0 | 2468.2065 | 2.455e-05%
2027 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 6.4924 | 212 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 20.217 | 6.3983 | 3.1598 | 20.217 | 6.3983 | 3.1598 | 22.4352 | 7.1003 | 3.1598 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2027 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 11.2661 | 731 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 680.9116 | 11.1028 | 61.3281 | 680.9116 | 11.1028 | 61.3281 | 755.6196 | 12.3209 | 61.3281 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2027 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | 4--5 | 5.5248 | 1388 | 100% | 2371.786 | 97.71% | 2.108% | 0.1806% | 114.7166 | 0 | 0 | 114.7166 | 0 | 104.3906 | 5.4447 | 19.1728 | 104.3906 | 5.4447 | 19.1728 | 115.8441 | 6.0421 | 19.1728 | 4.837% | 0.074138 | 0.070468 | 31991.6747 | 5091.6051 | 638.7369 | 26261.3327 | 32029.8024 | 0 | 0 | 32029.8024 | 0.003783%
2027 | 458 | 458-43F | Tier-1 | Non-HFTD---16 | 2--1 | 1.8401 | 69 | 100% | 2.2689 | 42.12% | 0% | 57.88% | 0.047309 | 0 | 0 | 0.047309 | 0 | 0.043051 | 1.8135 | 0.023739 | 0.043051 | 1.8135 | 0.023739 | 0.047774 | 2.0124 | 0.023739 | 2.085% | 0.0053162 | 0.005053 | 426.7836 | 1.0552 | 196.9069 | 228.8215 | 439.647 | 0 | 0 | 439.647 | 1.56e-06%
2027 | 74 | CB 74 | Tier-1 | Non-HFTD---10 | 3--2 | 6.9906 | 197 | 100% | 19.9911 | 76.58% | 0% | 23.42% | 0.75785 | 0 | 0 | 0.75785 | 0 | 0.68963 | 6.8892 | 0.1001 | 0.68963 | 6.8892 | 0.1001 | 0.7653 | 7.6451 | 0.1001 | 3.791% | 0.019147 | 0.018199 | 1044.0736 | 1.8204 | 811.7883 | 230.4649 | 1056.8053 | 0 | 0 | 1056.8053 | 2.499e-05%
2027 | SC2 | CB SC2 | Tier-1 | Non-HFTD---2 | 4--4 | 7.0339 | 233 | 100% | 261.4516 | 2.208% | 95.93% | 1.858% | 0.28577 | 0 | 0 | 0.28577 | 0 | 0.26005 | 6.9319 | 0.037514 | 0.26005 | 6.9319 | 0.037514 | 0.28858 | 7.6925 | 0.037514 | 0.1093% | 0.037006 | 0.035174 | 7065.0763 | 7.3313 | 6299.5139 | 758.2311 | 7424.8859 | 0 | 0 | 7424.8859 | 9.424e-06%
2027 | 529 | CB 529 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3037 | 55 | 100% | 27.2988 | 93.37% | 0% | 6.628% | 1.2617 | 0 | 0 | 1.2617 | 0 | 1.1482 | 2.2703 | 0.50572 | 1.1482 | 2.2703 | 0.50572 | 1.2741 | 2.5194 | 0.50572 | 4.622% | 0.0089244 | 0.0084826 | 3058.8995 | 429.8777 | 198.033 | 2430.9888 | 3069.4573 | 0 | 0 | 3069.4573 | 4.161e-05%
2027 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | 4--1 | 0.90625 | 0 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.15233 | 0 | 0 | 0.15233 | 0 | 0.13861 | 0.89311 | 0.1552 | 0.13861 | 0.89311 | 0.1552 | 0.15382 | 0.9911 | 0.1552 | 0.8348% | 0.061771 | 0.058714 | 295.3886 | 6.838 | 193.9385 | 94.612 | 308.1774 | 0 | 0 | 308.1774 | 5.023e-06%
2027 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 10.0072 | 279 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 67.1805 | 9.8621 | 6.812 | 67.1805 | 9.8621 | 6.812 | 74.5514 | 10.9442 | 6.812 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2027 | 34 | CB 34 | Tier-1 | Non-HFTD---19 | 1--1 | 0.1034 | 3 | 100% | 0.13232 | 2.437% | 0% | 97.56% | 0.00015964 | 0 | 0 | 0.00015964 | 0 | 0.00014527 | 0.1019 | 0.0014257 | 0.00014527 | 0.1019 | 0.0014257 | 0.00016121 | 0.11308 | 0.0014257 | 0.1206% | 0.0003968 | 0.00037716 | 333.478 | 0.37096 | 36.9115 | 296.1955 | 350.4215 | 0 | 0 | 350.4215 | 5.264e-09%
2027 | 190 | 190-1122F | Tier-1 | Non-HFTD---9 | 1--4 | 0.44692 | 22 | 100% | 22.2623 | 98.77% | 0% | 1.233% | 1.0884 | 0 | 0 | 1.0884 | 0 | 0.99043 | 0.44044 | 2.2487 | 0.99043 | 0.44044 | 2.2487 | 1.0991 | 0.48877 | 2.2487 | 4.889% | 0.001452 | 0.0013801 | 15332.18 | 2415.7745 | 19.2027 | 12897.2028 | 15342.0229 | 0 | 0 | 15342.0229 | 3.589e-05%
2027 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.023485 | 0 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.8337 | 0.023144 | 122.4361 | 2.8337 | 0.023144 | 122.4361 | 3.1446 | 0.025684 | 122.4361 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2027 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 6.8952 | 718 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 38.0091 | 6.7953 | 5.5935 | 38.0091 | 6.7953 | 5.5935 | 42.1794 | 7.5408 | 5.5935 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2027 | 963 | 963-35 | Tier-1 | Non-HFTD---7 | 2--3 | 3.1555 | 180 | 100% | 30.7376 | 94.18% | 0% | 5.818% | 1.433 | 0 | 0 | 1.433 | 0 | 1.304 | 3.1097 | 0.41933 | 1.304 | 3.1097 | 0.41933 | 1.4471 | 3.4509 | 0.41933 | 4.662% | 0.012897 | 0.012259 | 2383.2808 | 325.3782 | 213.264 | 1844.6386 | 2390.5024 | 0 | 0 | 2390.5024 | 4.725e-05%
2027 | 303 | 303-189AE | Tier-1 | Non-HFTD---3 | 4--4 | 8.0475 | 408 | 100% | 171.0034 | 3.397% | 93.81% | 2.795% | 0.28756 | 0 | 0 | 0.28756 | 0 | 0.26167 | 7.9309 | 0.032994 | 0.26167 | 7.9309 | 0.032994 | 0.29038 | 8.801 | 0.032994 | 0.1682% | 0.032667 | 0.03105 | 5234.7139 | 12.8116 | 4649.2999 | 572.6024 | 5498.0656 | 0 | 0 | 5498.0656 | 9.483e-06%
2027 | 1082 | CB 1082 | Tier-1 | Non-HFTD---10 | 3--2 | 1.1544 | 45 | 100% | 15.7927 | 61.51% | 33.76% | 4.733% | 0.48084 | 0 | 0 | 0.48084 | 0 | 0.43756 | 1.1376 | 0.38462 | 0.43756 | 1.1376 | 0.38462 | 0.48556 | 1.2624 | 0.38462 | 3.045% | 0.014222 | 0.013518 | 1110.4405 | 109.3438 | 313.5434 | 687.5533 | 1132.6997 | 0 | 0 | 1132.6997 | 1.586e-05%
2027 | 740 | 740-857F | Tier-1 | Non-HFTD---19 | 1--1 | 0.23295 | 18 | 100% | 0.392 | 20.4% | 0% | 79.6% | 0.0039577 | 0 | 0 | 0.0039577 | 0 | 0.0036014 | 0.22958 | 0.015687 | 0.0036014 | 0.22958 | 0.015687 | 0.0039966 | 0.25477 | 0.015687 | 1.01% | 0.0010222 | 0.0009716 | 383.4881 | 10.7399 | 40.9688 | 331.7794 | 399.386 | 0 | 0 | 399.386 | 1.305e-07%
2027 | 61 | 61-13F | Tier-1 | Non-HFTD---5 | 3--3 | 1.5653 | 221 | 100% | 66.9136 | 1.1% | 96.65% | 2.249% | 0.036446 | 0 | 0 | 0.036446 | 0 | 0.033165 | 1.5426 | 0.021499 | 0.033165 | 1.5426 | 0.021499 | 0.036804 | 1.7119 | 0.021499 | 0.05447% | 0.016091 | 0.015295 | 4158.3434 | 4.7662 | 3732.5049 | 421.0723 | 4372.5181 | 0 | 0 | 4372.5181 | 1.202e-06%
2027 | 159 | 159-1010F | Tier-1 | Non-HFTD---20 | 1--1 | 0.18916 | 14 | 100% | 0.072864 | 14.16% | 0% | 85.84% | 0.00051071 | 0 | 0 | 0.00051071 | 0 | 0.00046474 | 0.18642 | 0.002493 | 0.00046474 | 0.18642 | 0.002493 | 0.00051573 | 0.20687 | 0.002493 | 0.7009% | 0.0003894 | 0.00037012 | 187.1198 | 0.12086 | 41.0868 | 145.9122 | 195.4848 | 0 | 0 | 195.4848 | 1.684e-08%
2027 | 855 | CB 855 | Tier-1 | Non-HFTD---1 | 2--5 | 3.5599 | 173 | 100% | 270.5618 | 99.37% | 0% | 0.6324% | 13.3081 | 0 | 0 | 13.3081 | 0 | 12.1102 | 3.5082 | 3.4519 | 12.1102 | 3.5082 | 3.4519 | 13.4389 | 3.8932 | 3.4519 | 4.919% | 0.01085 | 0.010313 | 24937.4896 | 3437.8657 | 3656.8715 | 17842.7524 | 24945.7025 | 0 | 0 | 24945.7025 | 0.0004389%
2027 | RV1 | CB RV1 | Tier-1 | Non-HFTD---14 | 3--1 | 7.5803 | 408 | 100% | 5.6011 | 21.45% | 0% | 78.55% | 0.059471 | 0 | 0 | 0.059471 | 0 | 0.054118 | 7.4704 | 0.0072444 | 0.054118 | 7.4704 | 0.0072444 | 0.060056 | 8.29 | 0.0072444 | 1.062% | 0.019991 | 0.019001 | 280.18 | 0.1656 | 80.0914 | 199.9231 | 291.6414 | 0 | 0 | 291.6414 | 1.961e-06%
2027 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 7.6085 | 805 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 131.5802 | 7.4982 | 17.5482 | 131.5802 | 7.4982 | 17.5482 | 146.0169 | 8.3209 | 17.5482 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2027 | 777 | 777-10 | Tier-1 | Non-HFTD---19 | 1--2 | 0.1028 | 0 | 100% | 0.21948 | 49.99% | 0% | 50.01% | 0.0054313 | 0 | 0 | 0.0054313 | 0 | 0.0049424 | 0.10131 | 0.048787 | 0.0049424 | 0.10131 | 0.048787 | 0.0054847 | 0.11242 | 0.048787 | 2.475% | 0.0003706 | 0.00035226 | 592.216 | 47.9707 | 27.3549 | 516.8903 | 607.6387 | 0 | 0 | 607.6387 | 1.791e-07%
2027 | 87 | CB 87 | Tier-1 | Non-HFTD---14 | 3--1 | 6.3328 | 197 | 100% | 8.2544 | 42.74% | 0% | 57.26% | 0.17463 | 0 | 0 | 0.17463 | 0 | 0.15891 | 6.241 | 0.025463 | 0.15891 | 6.241 | 0.025463 | 0.17635 | 6.9257 | 0.025463 | 2.116% | 0.018391 | 0.017481 | 448.8306 | 2.7145 | 199.6816 | 246.4345 | 462.2148 | 0 | 0 | 462.2148 | 5.759e-06%
2027 | 363 | CB 363 | Tier-1 | Non-HFTD---5 | 3--4 | 3.2214 | 67 | 100% | 93.3136 | 5.828% | 91.17% | 3.003% | 0.26918 | 0 | 0 | 0.26918 | 0 | 0.24495 | 3.1747 | 0.077157 | 0.24495 | 3.1747 | 0.077157 | 0.27183 | 3.5231 | 0.077157 | 0.2885% | 0.014683 | 0.013956 | 6355.3857 | 6.7587 | 5611.6916 | 736.9354 | 6667.0722 | 0 | 0 | 6667.0722 | 8.877e-06%
2027 | 116 | CB 116 | Tier-1 | Non-HFTD---2 | 4--4 | 7.0256 | 286 | 100% | 265.4697 | 47.19% | 51.3% | 1.507% | 6.2014 | 0 | 0 | 6.2014 | 0 | 5.6432 | 6.9237 | 0.81506 | 5.6432 | 6.9237 | 0.81506 | 6.2624 | 7.6834 | 0.81506 | 2.336% | 0.037029 | 0.035196 | 7169.199 | 559.0648 | 4185.9405 | 2424.1937 | 7366.3596 | 0 | 0 | 7366.3596 | 0.0002045%
2027 | 221 | 221-1249R | Tier-1 | Non-HFTD---2 | 5--2 | 25.1976 | 192 | 100% | 329.3718 | 60.93% | 35.44% | 3.632% | 9.9343 | 0 | 0 | 9.9343 | 0 | 9.0401 | 24.8322 | 0.36405 | 9.0401 | 24.8322 | 0.36405 | 10.032 | 27.5568 | 0.36405 | 3.016% | 0.32343 | 0.30742 | 1018.3674 | 70.1582 | 373.9946 | 574.2146 | 1039.0867 | 0 | 0 | 1039.0867 | 0.0003276%
2027 | 418 | 418-25R | Tier-1 | Non-HFTD---14 | 2--2 | 3.847 | 112 | 100% | 6.5111 | 53.05% | 0% | 46.95% | 0.171 | 0 | 0 | 0.171 | 0 | 0.1556 | 3.7912 | 0.041044 | 0.1556 | 3.7912 | 0.041044 | 0.17268 | 4.2072 | 0.041044 | 2.626% | 0.011457 | 0.01089 | 568.3108 | 3.1871 | 307.4186 | 257.7051 | 582.2048 | 0 | 0 | 582.2048 | 5.639e-06%
2027 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 5.1074 | 166 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 513.522 | 5.0333 | 102.0247 | 513.522 | 5.0333 | 102.0247 | 569.8644 | 5.5856 | 102.0247 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2027 | MNR3 | CB MNR3 | Tier-1 | Non-HFTD---8 | 3--2 | 4.6053 | 258 | 100% | 32.2512 | 24.3% | 64.69% | 11.01% | 0.38795 | 0 | 0 | 0.38795 | 0 | 0.35303 | 4.5385 | 0.077786 | 0.35303 | 4.5385 | 0.077786 | 0.39176 | 5.0364 | 0.077786 | 1.203% | 0.019891 | 0.018906 | 1621.3979 | 77.741 | 1023.8427 | 519.8142 | 1685.3173 | 0 | 0 | 1685.3173 | 1.279e-05%
2027 | 313 | 313-920F | Tier-1 | Non-HFTD---10 | 3--2 | 0.7511 | 67 | 100% | 25.9898 | 2.478% | 94.94% | 2.583% | 0.03188 | 0 | 0 | 0.03188 | 0 | 0.02901 | 0.74021 | 0.039192 | 0.02901 | 0.74021 | 0.039192 | 0.032193 | 0.82142 | 0.039192 | 0.1227% | 0.019352 | 0.018394 | 1342.9879 | 6.3375 | 1055.0399 | 281.6105 | 1411.1947 | 0 | 0 | 1411.1947 | 1.051e-06%
2027 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 19.4272 | 2033 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 191.4311 | 19.1456 | 9.9987 | 191.4311 | 19.1456 | 9.9987 | 212.4345 | 21.2462 | 9.9987 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2027 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 18.9327 | 1474 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 916.1722 | 18.6582 | 49.1028 | 916.1722 | 18.6582 | 49.1028 | 1016.6925 | 20.7054 | 49.1028 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2027 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 11.8401 | 434 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 119.0101 | 11.6685 | 10.1993 | 119.0101 | 11.6685 | 10.1993 | 132.0677 | 12.9487 | 10.1993 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2027 | 533 | 533-7AE | Tier-1 | Non-HFTD---6 | 4--2 | 2.0012 | 69 | 100% | 45.7464 | 11.34% | 84.92% | 3.741% | 0.25674 | 0 | 0 | 0.25674 | 0 | 0.23363 | 1.9722 | 0.11846 | 0.23363 | 1.9722 | 0.11846 | 0.25926 | 2.1885 | 0.11846 | 0.5612% | 0.066097 | 0.062825 | 692.1106 | 12.2731 | 470.7532 | 209.0843 | 724.0677 | 0 | 0 | 724.0677 | 8.466e-06%
2027 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.49562 | 10 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 37.8035 | 0.48843 | 77.3978 | 37.8035 | 0.48843 | 77.3978 | 41.9512 | 0.54202 | 77.3978 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2027 | 397 | 397-550F | Tier-1 | Non-HFTD---16 | 3--1 | 4.9887 | 155 | 100% | 4.542 | 25.73% | 0% | 74.27% | 0.057853 | 0 | 0 | 0.057853 | 0 | 0.052645 | 4.9164 | 0.010708 | 0.052645 | 4.9164 | 0.010708 | 0.058421 | 5.4558 | 0.010708 | 1.274% | 0.013683 | 0.013005 | 331.9512 | 4.2581 | 82.8811 | 244.812 | 344.7902 | 0 | 0 | 344.7902 | 1.908e-06%
2027 | 156 | CB 156 | Tier-1 | Non-HFTD---7 | 2--3 | 3.9841 | 144 | 100% | 34.4406 | 92.43% | 0% | 7.569% | 1.5758 | 0 | 0 | 1.5758 | 0 | 1.4339 | 3.9263 | 0.36521 | 1.4339 | 3.9263 | 0.36521 | 1.5913 | 4.3571 | 0.36521 | 4.575% | 0.012401 | 0.011788 | 2777.1524 | 583.7733 | 709.3221 | 1484.0571 | 2788.0993 | 0 | 0 | 2788.0993 | 5.196e-05%
2027 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 16.0076 | 996 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 940.331 | 15.7755 | 59.6071 | 940.331 | 15.7755 | 59.6071 | 1043.5019 | 17.5063 | 59.6071 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2027 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 7.3674 | 622 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 179.8549 | 7.2606 | 24.7714 | 179.8549 | 7.2606 | 24.7714 | 199.5882 | 8.0572 | 24.7714 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2027 | 255 | 255-43AE | Tier-1 | Non-HFTD---6 | 4--2 | 17.4344 | 666 | 100% | 53.0999 | 77.76% | 0% | 22.24% | 2.0438 | 0 | 0 | 2.0438 | 0 | 1.8598 | 17.1817 | 0.10824 | 1.8598 | 17.1817 | 0.10824 | 2.0639 | 19.0668 | 0.10824 | 3.849% | 0.048441 | 0.046043 | 1096.1851 | 147.1891 | 267.7558 | 681.2403 | 1108.8831 | 0 | 0 | 1108.8831 | 6.74e-05%
2027 | 50 | CB 50 | Tier-1 | Non-HFTD---16 | 2--1 | 3.922 | 170 | 100% | 4.8179 | 39.4% | 0% | 60.6% | 0.093953 | 0 | 0 | 0.093953 | 0 | 0.085496 | 3.8651 | 0.02212 | 0.085496 | 3.8651 | 0.02212 | 0.094876 | 4.2892 | 0.02212 | 1.95% | 0.010946 | 0.010404 | 440.1426 | 0.20072 | 197.6284 | 242.3134 | 454.0341 | 0 | 0 | 454.0341 | 3.098e-06%
2027 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 7.5286 | 403 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 48.3244 | 7.4195 | 6.5132 | 48.3244 | 7.4195 | 6.5132 | 53.6265 | 8.2335 | 6.5132 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2027 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 14.1159 | 1193 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 77.5518 | 13.9112 | 5.5748 | 77.5518 | 13.9112 | 5.5748 | 86.0606 | 15.4376 | 5.5748 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2027 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 17.3068 | 1251 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 239.6285 | 17.0558 | 14.0496 | 239.6285 | 17.0558 | 14.0496 | 265.9199 | 18.9272 | 14.0496 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2027 | 139 | 139-245AE | Tier-1 | Non-HFTD---14 | 2--2 | 3.4127 | 72 | 100% | 5.6722 | 51.84% | 0% | 48.16% | 0.14554 | 0 | 0 | 0.14554 | 0 | 0.13244 | 3.3632 | 0.03938 | 0.13244 | 3.3632 | 0.03938 | 0.14697 | 3.7322 | 0.03938 | 2.566% | 0.010451 | 0.0099339 | 542.7299 | 27.8649 | 162.7078 | 352.1572 | 556.343 | 0 | 0 | 556.343 | 4.799e-06%
2027 | 512 | CB 512 | Tier-1 | Non-HFTD---5 | 2--4 | 0.53466 | 12 | 100% | 72.9923 | 9.966% | 89.3% | 0.7365% | 0.36007 | 0 | 0 | 0.36007 | 0 | 0.32766 | 0.52691 | 0.62186 | 0.32766 | 0.52691 | 0.62186 | 0.36361 | 0.58472 | 0.62186 | 0.4933% | 0.012277 | 0.01167 | 5945.2569 | 37.3623 | 5220.9585 | 686.9361 | 6224.0176 | 0 | 0 | 6224.0176 | 1.187e-05%
2027 | 189 | 189-750 | Tier-2 | Tier-2---21 | 1--2 | 0.37597 | 5 | 100% | 1.7248 | 88.21% | 0% | 11.79% | 0.075309 | 0 | 0 | 0.075309 | 0 | 0.068531 | 0.37052 | 0.18496 | 0.068531 | 0.37052 | 0.18496 | 0.07605 | 0.41117 | 0.18496 | 4.366% | 0.001013 | 0.00096286 | 1702.705 | 2.2891 | 1507.0729 | 193.3431 | 1713.1637 | 0 | 0 | 1713.1637 | 2.483e-06%
2027 | 361 | 361-684F | Tier-1 | Non-HFTD---18 | 2--1 | 0.31534 | 15 | 100% | 0.70004 | 34.6% | 14.74% | 50.66% | 0.011991 | 0 | 0 | 0.011991 | 0 | 0.010911 | 0.31077 | 0.035111 | 0.010911 | 0.31077 | 0.035111 | 0.012108 | 0.34487 | 0.035111 | 1.713% | 0.0069836 | 0.0066379 | 100.2413 | 5.6671 | 18.5544 | 76.0198 | 103.6552 | 0 | 0 | 103.6552 | 3.954e-07%
2027 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 13.7784 | 1046 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 80.9279 | 13.5786 | 5.9599 | 80.9279 | 13.5786 | 5.9599 | 89.8072 | 15.0685 | 5.9599 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2027 | 120 | 120-367F | Tier-1 | Non-HFTD---13 | 2--2 | 0.019508 | 2 | 100% | 8.1563 | 0% | 99.6% | 0.404% | 0 | 0 | 0 | 0 | 0 | 0 | 0.019225 | 0 | 0 | 0.019225 | 0 | 0 | 0.021334 | 0 | 0% | 0.0075852 | 0.0072097 | 1075.2925 | 1.6858 | 978.9966 | 94.6101 | 1131.2914 | 0 | 0 | 1131.2914 | 0%
2027 | 87 | 87-41AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.2464 | 37 | 100% | 0.28157 | 26.88% | 0% | 73.12% | 0.0037471 | 0 | 0 | 0.0037471 | 0 | 0.0034099 | 0.24283 | 0.014042 | 0.0034099 | 0.24283 | 0.014042 | 0.003784 | 0.26947 | 0.014042 | 1.331% | 0.0008986 | 0.00085412 | 313.3426 | 10.7167 | 37.6883 | 264.9376 | 325.2737 | 0 | 0 | 325.2737 | 1.236e-07%
2027 | 321 | 321-1332R | Tier-1 | Non-HFTD---12 | 2--2 | 4.7077 | 80 | 100% | 9.6163 | 68.26% | 0% | 31.74% | 0.32491 | 0 | 0 | 0.32491 | 0 | 0.29566 | 4.6395 | 0.063728 | 0.29566 | 4.6395 | 0.063728 | 0.3281 | 5.1485 | 0.063728 | 3.379% | 0.013392 | 0.012729 | 718.0629 | 3.1766 | 492.4341 | 222.4522 | 729.9331 | 0 | 0 | 729.9331 | 1.071e-05%
2027 | 770 | 770-259R | Tier-2 | Tier-2---17 | 2--3 | 1.5089 | 0 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 2.0515 | 0 | 0 | 2.0515 | 0 | 1.8669 | 1.487 | 1.2554 | 1.8669 | 1.487 | 1.2554 | 2.0717 | 1.6502 | 1.2554 | 4.826% | 0.010605 | 0.01008 | 4008.538 | 787.4023 | 25.9222 | 3195.2135 | 4013.7737 | 0 | 0 | 4013.7737 | 6.765e-05%
2027 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 3.6864 | 237 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 145.709 | 3.6329 | 40.1077 | 145.709 | 3.6329 | 40.1077 | 161.6959 | 4.0315 | 40.1077 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2027 | 371 | CB 371 | Tier-1 | Non-HFTD---18 | 1--1 | 0.65097 | 0 | 100% | 0.79179 | 5.127% | 0% | 94.87% | 0.0020093 | 0 | 0 | 0.0020093 | 0 | 0.0018284 | 0.64153 | 0.0028501 | 0.0018284 | 0.64153 | 0.0028501 | 0.002029 | 0.71192 | 0.0028501 | 0.2538% | 0.0026386 | 0.002508 | 300.0814 | 2.4613 | 27.3455 | 270.2746 | 314.9079 | 0 | 0 | 314.9079 | 6.626e-08%
2027 | 206 | 206-961F | Tier-1 | Non-HFTD---17 | 1--2 | 0.31686 | 31 | 100% | 0.73497 | 72.73% | 0% | 27.27% | 0.026461 | 0 | 0 | 0.026461 | 0 | 0.024079 | 0.31226 | 0.077113 | 0.024079 | 0.31226 | 0.077113 | 0.026721 | 0.34652 | 0.077113 | 3.6% | 0.0009058 | 0.00086096 | 811.4096 | 93.8104 | 38.4901 | 679.1091 | 822.9314 | 0 | 0 | 822.9314 | 8.726e-07%
2027 | 303 | 303-487AE | Tier-1 | Non-HFTD---4 | 3--4 | 1.8256 | 101 | 100% | 106.3501 | 4.982% | 93.81% | 1.206% | 0.26227 | 0 | 0 | 0.26227 | 0 | 0.23866 | 1.7991 | 0.13265 | 0.23866 | 1.7991 | 0.13265 | 0.26484 | 1.9965 | 0.13265 | 0.2466% | 0.016038 | 0.015244 | 6631.1342 | 30.8907 | 5898.0053 | 702.2382 | 6959.2651 | 0 | 0 | 6959.2651 | 8.649e-06%
2027 | 206 | CB 206 | Tier-1 | Non-HFTD---11 | 2--3 | 3.0087 | 131 | 100% | 15.0084 | 86.35% | 0% | 13.65% | 0.64153 | 0 | 0 | 0.64153 | 0 | 0.58379 | 2.9651 | 0.19689 | 0.58379 | 2.9651 | 0.19689 | 0.64784 | 3.2904 | 0.19689 | 4.274% | 0.0084374 | 0.0080197 | 1778.7928 | 21.532 | 1427.2919 | 329.9688 | 1791.4343 | 0 | 0 | 1791.4343 | 2.116e-05%
2027 | MU1 | CB MU1 | Tier-1 | Non-HFTD---8 | 3--2 | 2.842 | 486 | 100% | 27.925 | 4.407% | 87.94% | 7.651% | 0.060913 | 0 | 0 | 0.060913 | 0 | 0.05543 | 2.8008 | 0.019791 | 0.05543 | 2.8008 | 0.019791 | 0.061512 | 3.1081 | 0.019791 | 0.2181% | 0.018888 | 0.017953 | 1478.4806 | 11.8202 | 1223.4645 | 243.1959 | 1552.0837 | 0 | 0 | 1552.0837 | 2.009e-06%
2027 | 489 | 489-19AE | Tier-1 | Non-HFTD---11 | 2--2 | 2.8017 | 45 | 100% | 9.4748 | 79.25% | 0% | 20.75% | 0.37169 | 0 | 0 | 0.37169 | 0 | 0.33824 | 2.7611 | 0.1225 | 0.33824 | 2.7611 | 0.1225 | 0.37535 | 3.064 | 0.1225 | 3.923% | 0.008219 | 0.0078122 | 1152.7879 | 219.8755 | 163.8034 | 769.109 | 1165.2439 | 0 | 0 | 1165.2439 | 1.226e-05%
2027 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 6.825 | 1872 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 21.2363 | 6.7261 | 3.1573 | 21.2363 | 6.7261 | 3.1573 | 23.5663 | 7.464 | 3.1573 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2027 | 143 | 143-33 | Tier-1 | Non-HFTD---13 | 2--2 | 0.11532 | 2 | 100% | 7.5516 | 0.6961% | 97.86% | 1.439% | 0.0026022 | 0 | 0 | 0.0026022 | 0 | 0.002368 | 0.11365 | 0.020836 | 0.002368 | 0.11365 | 0.020836 | 0.0026278 | 0.12612 | 0.020836 | 0.03446% | 0.0064842 | 0.0061632 | 1164.6172 | 2.5226 | 906.0378 | 256.0569 | 1224.8458 | 0 | 0 | 1224.8458 | 8.581e-08%
2027 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 1.2528 | 11 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 87.1243 | 1.2347 | 70.5645 | 87.1243 | 1.2347 | 70.5645 | 96.6834 | 1.3701 | 70.5645 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2027 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 3.3435 | 151 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 386.4725 | 3.2951 | 117.2887 | 386.4725 | 3.2951 | 117.2887 | 428.8754 | 3.6566 | 117.2887 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2027 | 128 | CB 128 | Tier-1 | Non-HFTD---16 | 2--1 | 3.2045 | 22 | 100% | 2.8222 | 5.175% | 0% | 94.82% | 0.0072295 | 0 | 0 | 0.0072295 | 0 | 0.0065787 | 3.1581 | 0.0020832 | 0.0065787 | 3.1581 | 0.0020832 | 0.0073005 | 3.5046 | 0.0020832 | 0.2562% | 0.010647 | 0.01012 | 265.0569 | 1.7417 | 26.7354 | 236.5798 | 278.1462 | 0 | 0 | 278.1462 | 2.384e-07%
2027 | 171 | 171-6R | Tier-1 | Non-HFTD---8 | 4--2 | 2.4529 | 22 | 100% | 40.3404 | 54.29% | 41.19% | 4.517% | 1.0841 | 0 | 0 | 1.0841 | 0 | 0.98653 | 2.4173 | 0.40811 | 0.98653 | 2.4173 | 0.40811 | 1.0948 | 2.6825 | 0.40811 | 2.687% | 0.036438 | 0.034634 | 1107.1099 | 96.9512 | 428.9197 | 581.2391 | 1133.4637 | 0 | 0 | 1133.4637 | 3.575e-05%
2027 | 171 | CB 171 | Tier-1 | Non-HFTD---3 | 4--3 | 2.7693 | 176 | 100% | 113.9192 | 33.8% | 64.29% | 1.906% | 1.9062 | 0 | 0 | 1.9062 | 0 | 1.7346 | 2.7291 | 0.63559 | 1.7346 | 2.7291 | 0.63559 | 1.9249 | 3.0286 | 0.63559 | 1.673% | 0.040057 | 0.038075 | 2843.8994 | 78.1486 | 2158.4913 | 607.2596 | 2941.9394 | 0 | 0 | 2941.9394 | 6.286e-05%
2027 | 159 | 159-38F | Tier-1 | Non-HFTD---16 | 2--1 | 2.7123 | 104 | 100% | 2.2472 | 22.94% | 0% | 77.06% | 0.025514 | 0 | 0 | 0.025514 | 0 | 0.023217 | 2.673 | 0.0086859 | 0.023217 | 2.673 | 0.0086859 | 0.025765 | 2.9663 | 0.0086859 | 1.135% | 0.00712 | 0.0067676 | 315.6205 | 0.4738 | 92.7094 | 222.4373 | 328.2873 | 0 | 0 | 328.2873 | 8.414e-07%
2027 | 392 | CB 392 | Tier-1 | Non-HFTD---2 | 5--4 | 4.5493 | 172 | 100% | 632.789 | 5.96% | 93.57% | 0.4686% | 1.8668 | 0 | 0 | 1.8668 | 0 | 1.6988 | 4.4833 | 0.37891 | 1.6988 | 4.4833 | 0.37891 | 1.8852 | 4.9752 | 0.37891 | 0.295% | 0.10236 | 0.097291 | 6182.1524 | 58.8165 | 5308.8037 | 814.5321 | 6484.9176 | 0 | 0 | 6484.9176 | 6.156e-05%
2027 | 172 | 172-567R | Tier-1 | Non-HFTD---3 | 4--3 | 10.6971 | 130 | 100% | 141.9219 | 62.19% | 32.78% | 5.033% | 4.369 | 0 | 0 | 4.369 | 0 | 3.9758 | 10.542 | 0.37713 | 3.9758 | 10.542 | 0.37713 | 4.412 | 11.6987 | 0.37713 | 3.078% | 0.069555 | 0.066112 | 2040.4331 | 199.3667 | 664.6627 | 1176.4036 | 2080.609 | 0 | 0 | 2080.609 | 0.0001441%
2027 | 475 | CB 475 | Tier-1 | Non-HFTD---5 | 2--4 | 2.5995 | 183 | 100% | 67.5852 | 97.2% | 0% | 2.801% | 3.2518 | 0 | 0 | 3.2518 | 0 | 2.9591 | 2.5618 | 1.1551 | 2.9591 | 2.5618 | 1.1551 | 3.2837 | 2.8428 | 1.1551 | 4.811% | 0.0082144 | 0.0078078 | 8227.6449 | 1225.4309 | 526.326 | 6475.888 | 8239.6468 | 0 | 0 | 8239.6468 | 0.0001072%
2027 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.038118 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.1166 | 0.037565 | 29.7244 | 1.1166 | 0.037565 | 29.7244 | 1.2391 | 0.041687 | 29.7244 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2027 | 95 | 95-37F | Tier-1 | Non-HFTD---20 | 2--1 | 0.088838 | 3 | 100% | 0.46434 | 14.45% | 70.16% | 15.4% | 0.0033212 | 0 | 0 | 0.0033212 | 0 | 0.0030222 | 0.08755 | 0.03452 | 0.0030222 | 0.08755 | 0.03452 | 0.0033538 | 0.097156 | 0.03452 | 0.7152% | 0.0053792 | 0.0051129 | 86.3215 | 1.055 | 63.4057 | 21.8608 | 90.1673 | 0 | 0 | 90.1673 | 1.095e-07%
2027 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 14.7171 | 588 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 18.1939 | 14.5037 | 1.2544 | 18.1939 | 14.5037 | 1.2544 | 20.1901 | 16.095 | 1.2544 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2027 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 8.9137 | 168 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 96.2068 | 8.7844 | 10.952 | 96.2068 | 8.7844 | 10.952 | 106.7624 | 9.7482 | 10.952 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2027 | AM1 | CB AM1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.6244 | 115 | 100% | 3.3578 | 29.51% | 0% | 70.49% | 0.049051 | 0 | 0 | 0.049051 | 0 | 0.044635 | 3.5719 | 0.012496 | 0.044635 | 3.5719 | 0.012496 | 0.049533 | 3.9638 | 0.012496 | 1.461% | 0.0096132 | 0.0091373 | 349.2893 | 0.61104 | 122.8396 | 225.8387 | 362.1114 | 0 | 0 | 362.1114 | 1.618e-06%
2027 | 580 | 580-690AE | Tier-1 | Non-HFTD---19 | 1--3 | 0.067992 | 0 | 100% | 0.50006 | 86.19% | 0% | 13.81% | 0.021335 | 0 | 0 | 0.021335 | 0 | 0.019415 | 0.067007 | 0.28974 | 0.019415 | 0.067007 | 0.28974 | 0.021545 | 0.074358 | 0.28974 | 4.266% | 0.0002812 | 0.00026728 | 1778.3079 | 201.1614 | 323.7794 | 1253.3671 | 1791.0959 | 0 | 0 | 1791.0959 | 7.035e-07%
2027 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 0.99238 | 48 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.83367 | 0.97799 | 0.85243 | 0.83367 | 0.97799 | 0.85243 | 0.92513 | 1.0853 | 0.85243 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2027 | 416 | 416-35F | Tier-1 | Non-HFTD---17 | 1--1 | 0.98558 | 46 | 100% | 1.2958 | 41.8% | 0% | 58.2% | 0.026812 | 0 | 0 | 0.026812 | 0 | 0.024398 | 0.97129 | 0.02512 | 0.024398 | 0.97129 | 0.02512 | 0.027075 | 1.0779 | 0.02512 | 2.069% | 0.0029674 | 0.0028205 | 436.6793 | 1.3522 | 198.3951 | 236.932 | 449.9146 | 0 | 0 | 449.9146 | 8.842e-07%
2027 | 719 | 719-857F | Tier-1 | Non-HFTD---20 | 1--1 | 0.4199 | 8 | 100% | 0.29905 | 18.65% | 0% | 81.35% | 0.0027613 | 0 | 0 | 0.0027613 | 0 | 0.0025127 | 0.41381 | 0.0060721 | 0.0025127 | 0.41381 | 0.0060721 | 0.0027884 | 0.45921 | 0.0060721 | 0.9233% | 0.0010186 | 0.00096818 | 293.5913 | 0.17971 | 76.4595 | 216.9521 | 306.0289 | 0 | 0 | 306.0289 | 9.106e-08%
2027 | 972 | 972-1642 | Tier-2 | Tier-2---16 | 5--2 | 0.038636 | 0 | 100% | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.038076 | 0 | 0 | 0.038076 | 0 | 0 | 0.042254 | 0 | 0% | 0.11047 | 0.105 | 1677.3427 | 1.9611 | 1510.6909 | 164.6906 | 1764.6951 | 0 | 0 | 1764.6951 | 0%
2027 | 199 | 199-39AE | Tier-1 | Non-HFTD---13 | 2--2 | 2.4932 | 59 | 100% | 5.5063 | 65.09% | 0% | 34.91% | 0.17742 | 0 | 0 | 0.17742 | 0 | 0.16145 | 2.457 | 0.065709 | 0.16145 | 2.457 | 0.065709 | 0.17917 | 2.7266 | 0.065709 | 3.222% | 0.0073958 | 0.0070297 | 744.5212 | 70.5063 | 77.1367 | 596.8782 | 758.0554 | 0 | 0 | 758.0554 | 5.851e-06%
2027 | AM2 | CB AM2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.125 | 184 | 100% | 11.1682 | 52.54% | 0% | 47.46% | 0.29045 | 0 | 0 | 0.29045 | 0 | 0.26431 | 7.0217 | 0.037642 | 0.26431 | 7.0217 | 0.037642 | 0.29331 | 7.7921 | 0.037642 | 2.601% | 0.02008 | 0.019086 | 556.1818 | 2.2661 | 303.5202 | 250.3954 | 569.9286 | 0 | 0 | 569.9286 | 9.578e-06%
2027 | RD4 | RD4-48F | Tier-1 | Non-HFTD---16 | 2--1 | 3.5216 | 269 | 100% | 3.4032 | 33.95% | 0% | 66.05% | 0.057196 | 0 | 0 | 0.057196 | 0 | 0.052047 | 3.4706 | 0.014997 | 0.052047 | 3.4706 | 0.014997 | 0.057758 | 3.8514 | 0.014997 | 1.681% | 0.0093526 | 0.0088896 | 363.8725 | 1.432 | 137.6932 | 224.7473 | 376.3882 | 0 | 0 | 376.3882 | 1.886e-06%
2027 | 852 | CB 852 | Tier-1 | Non-HFTD---7 | 1--5 | 0.13314 | 18 | 100% | 34.4559 | 99.59% | 0% | 0.4114% | 1.6986 | 0 | 0 | 1.6986 | 0 | 1.5457 | 0.13121 | 11.7797 | 1.5457 | 0.13121 | 11.7797 | 1.7152 | 0.14561 | 11.7797 | 4.93% | 0.0007638 | 0.00072599 | 45111.1902 | 8830.4114 | 18.3177 | 36262.461 | 45120.855 | 0 | 0 | 45120.855 | 5.601e-05%
2027 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.50061 | 49 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 17.4178 | 0.49335 | 35.3054 | 17.4178 | 0.49335 | 35.3054 | 19.3289 | 0.54748 | 35.3054 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2027 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 6.2775 | 182 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 431.4681 | 6.1865 | 69.7438 | 431.4681 | 6.1865 | 69.7438 | 478.8077 | 6.8652 | 69.7438 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2027 | 180 | CB 180 | Tier-1 | Non-HFTD---13 | 1--3 | 0.94796 | 5 | 100% | 7.7122 | 90.8% | 0% | 9.202% | 0.34662 | 0 | 0 | 0.34662 | 0 | 0.31542 | 0.93421 | 0.33763 | 0.31542 | 0.93421 | 0.33763 | 0.35003 | 1.0367 | 0.33763 | 4.494% | 0.0030172 | 0.0028678 | 2556.0648 | 24.9107 | 2190.1936 | 340.9605 | 2568.3144 | 0 | 0 | 2568.3144 | 1.143e-05%
2027 | 430 | 430-321AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.3352 | 34 | 100% | 0.30658 | 15.66% | 0% | 84.34% | 0.0023773 | 0 | 0 | 0.0023773 | 0 | 0.0021633 | 0.33034 | 0.0065486 | 0.0021633 | 0.33034 | 0.0065486 | 0.0024006 | 0.36659 | 0.0065486 | 0.7754% | 0.0009426 | 0.00089594 | 325.2518 | 3.1534 | 57.757 | 264.3414 | 339.5368 | 0 | 0 | 339.5368 | 7.839e-08%
2027 | HP1 | CB HP1 | Tier-1 | Non-HFTD---10 | 4--1 | 18.2582 | 619 | 100% | 16.6755 | 30.85% | 0% | 69.15% | 0.25463 | 0 | 0 | 0.25463 | 0 | 0.23171 | 17.9934 | 0.012878 | 0.23171 | 17.9934 | 0.012878 | 0.25714 | 19.9676 | 0.012878 | 1.527% | 0.048206 | 0.04582 | 345.9227 | 0.91802 | 123.9165 | 221.0881 | 358.3803 | 0 | 0 | 358.3803 | 8.397e-06%
2027 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 6.9867 | 127 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 64.8175 | 6.8854 | 9.4138 | 64.8175 | 6.8854 | 9.4138 | 71.9292 | 7.6409 | 9.4138 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2027 | 461 | 461-24F | Tier-1 | Non-HFTD---15 | 1--3 | 0.42368 | 9 | 100% | 4.3764 | 89.98% | 0% | 10.02% | 0.19492 | 0 | 0 | 0.19492 | 0 | 0.17737 | 0.41754 | 0.42481 | 0.17737 | 0.41754 | 0.42481 | 0.19683 | 0.46335 | 0.42481 | 4.454% | 0.0015528 | 0.0014759 | 2818.3832 | 300.604 | 715.3571 | 1802.422 | 2833.0954 | 0 | 0 | 2833.0954 | 6.428e-06%
2027 | 504 | 504-287R | Tier-2 | Tier-2---12 | 4--4 | 7.8402 | 264 | 100% | 501.8283 | 98.94% | 0% | 1.063% | 24.5765 | 0 | 0 | 24.5765 | 0 | 22.3643 | 7.7265 | 2.8945 | 22.3643 | 7.7265 | 2.8945 | 24.818 | 8.5742 | 2.8945 | 4.897% | 0.033132 | 0.031492 | 15146.1514 | 2418.4341 | 53.5553 | 12674.162 | 15154.5352 | 0 | 0 | 15154.5352 | 0.0008104%
2027 | SW1 | CB SW1 | Tier-1 | Non-HFTD---17 | 1--1 | 1.5451 | 35 | 100% | 1.6455 | 48.03% | 0% | 51.97% | 0.039125 | 0 | 0 | 0.039125 | 0 | 0.035603 | 1.5227 | 0.023381 | 0.035603 | 1.5227 | 0.023381 | 0.039509 | 1.6898 | 0.023381 | 2.378% | 0.0038896 | 0.0036971 | 423.0612 | 20.0581 | 101.1853 | 301.8178 | 434.5106 | 0 | 0 | 434.5106 | 1.29e-06%
2027 | 245 | CB 245 | Tier-1 | Non-HFTD---2 | 4--4 | 7.1536 | 280 | 100% | 248.3247 | 30.26% | 68.14% | 1.595% | 3.7197 | 0 | 0 | 3.7197 | 0 | 3.3848 | 7.0499 | 0.48012 | 3.3848 | 7.0499 | 0.48012 | 3.7562 | 7.8234 | 0.48012 | 1.498% | 0.044637 | 0.042428 | 5563.1534 | 331.3651 | 3704.159 | 1527.6293 | 5765.2004 | 0 | 0 | 5765.2004 | 0.0001227%
2027 | 74 | 74-24R | Tier-1 | Non-HFTD---12 | 3--2 | 8.6284 | 269 | 100% | 13.7632 | 60.93% | 0% | 39.07% | 0.41507 | 0 | 0 | 0.41507 | 0 | 0.37771 | 8.5033 | 0.044419 | 0.37771 | 8.5033 | 0.044419 | 0.41915 | 9.4363 | 0.044419 | 3.016% | 0.022875 | 0.021743 | 601.6686 | 1.4002 | 380.4228 | 219.8456 | 613.912 | 0 | 0 | 613.912 | 1.369e-05%
2027 | 341 | 341-920 | Tier-1 | Non-HFTD---3 | 4--3 | 12.9709 | 837 | 100% | 161.886 | 95.19% | 0% | 4.806% | 7.6283 | 0 | 0 | 7.6283 | 0 | 6.9416 | 12.7828 | 0.54304 | 6.9416 | 12.7828 | 0.54304 | 7.7032 | 14.1853 | 0.54304 | 4.712% | 0.035928 | 0.034149 | 4505.8945 | 872.5831 | 176.1223 | 3457.1891 | 4517.1713 | 0 | 0 | 4517.1713 | 0.0002516%
2027 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 9.4684 | 622 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 89.8634 | 9.3311 | 9.6305 | 89.8634 | 9.3311 | 9.6305 | 99.723 | 10.3549 | 9.6305 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2027 | GM2 | CB GM2 | Tier-1 | Non-HFTD---2 | 4--3 | 12.8498 | 1166 | 100% | 185.8665 | 95.73% | 0% | 4.266% | 8.8079 | 0 | 0 | 8.8079 | 0 | 8.0151 | 12.6635 | 0.63293 | 8.0151 | 12.6635 | 0.63293 | 8.8945 | 14.0529 | 0.63293 | 4.739% | 0.042423 | 0.040323 | 4381.2884 | 678.342 | 70.1655 | 3632.7808 | 4391.021 | 0 | 0 | 4391.021 | 0.0002905%
2027 | 52 | 52-20R | Tier-1 | Non-HFTD---14 | 2--2 | 3.9289 | 85 | 100% | 5.9584 | 48.34% | 0% | 51.66% | 0.14257 | 0 | 0 | 0.14257 | 0 | 0.12974 | 3.872 | 0.033506 | 0.12974 | 3.872 | 0.033506 | 0.14397 | 4.2968 | 0.033506 | 2.393% | 0.011327 | 0.010766 | 526.0509 | 0.21605 | 278.8999 | 246.935 | 540.204 | 0 | 0 | 540.204 | 4.701e-06%
2027 | 504 | CB 504 | Tier-1 | Non-HFTD---7 | 2--3 | 4.505 | 174 | 100% | 34.4975 | 90.08% | 0% | 9.923% | 1.5382 | 0 | 0 | 1.5382 | 0 | 1.3997 | 4.4397 | 0.31528 | 1.3997 | 4.4397 | 0.31528 | 1.5533 | 4.9268 | 0.31528 | 4.459% | 0.013226 | 0.012571 | 2608.352 | 206.1348 | 1114.8562 | 1287.361 | 2621.8318 | 0 | 0 | 2621.8318 | 5.072e-05%
2027 | 114 | 114-18AE | Tier-1 | Non-HFTD---6 | 3--3 | 4.008 | 263 | 100% | 66.6834 | 4.686% | 91.31% | 4.003% | 0.15468 | 0 | 0 | 0.15468 | 0 | 0.14076 | 3.9499 | 0.035637 | 0.14076 | 3.9499 | 0.035637 | 0.1562 | 4.3832 | 0.035637 | 0.232% | 0.019386 | 0.018426 | 3439.7723 | 23.4352 | 2933.6014 | 482.7357 | 3610.5136 | 0 | 0 | 3610.5136 | 5.101e-06%
2027 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 3.289 | 349 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 27.4714 | 3.2413 | 8.4754 | 27.4714 | 3.2413 | 8.4754 | 30.4855 | 3.597 | 8.4754 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2027 | 171 | 171-704R | Tier-1 | Non-HFTD---6 | 4--2 | 4.9861 | 76 | 100% | 80.6143 | 61.35% | 34.31% | 4.34% | 2.4483 | 0 | 0 | 2.4483 | 0 | 2.2279 | 4.9138 | 0.4534 | 2.2279 | 4.9138 | 0.4534 | 2.4724 | 5.453 | 0.4534 | 3.037% | 0.048088 | 0.045707 | 1676.4044 | 165.028 | 536.4334 | 974.9431 | 1710.1431 | 0 | 0 | 1710.1431 | 8.074e-05%
2027 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 8.351 | 10 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 14.5292 | 8.2299 | 1.7654 | 14.5292 | 8.2299 | 1.7654 | 16.1233 | 9.1329 | 1.7654 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2027 | 59 | 59-465 | Tier-1 | Non-HFTD---6 | 4--3 | 7.5326 | 198 | 100% | 77.379 | 64.48% | 28.11% | 7.401% | 2.4699 | 0 | 0 | 2.4699 | 0 | 2.2476 | 7.4234 | 0.30278 | 2.2476 | 7.4234 | 0.30278 | 2.4942 | 8.2378 | 0.30278 | 3.192% | 0.036127 | 0.034339 | 2141.862 | 301.1171 | 633.9997 | 1206.7452 | 2181.4767 | 0 | 0 | 2181.4767 | 8.145e-05%
2027 | 588 | CB 588 | Tier-1 | Non-HFTD---9 | 1--4 | 0.38598 | 4 | 100% | 21.538 | 98.85% | 0% | 1.146% | 1.0539 | 0 | 0 | 1.0539 | 0 | 0.95905 | 0.38039 | 2.5212 | 0.95905 | 0.38039 | 2.5212 | 1.0643 | 0.42212 | 2.5212 | 4.893% | 0.0014694 | 0.0013967 | 14657.7162 | 2735.8339 | 186.8229 | 11735.0595 | 14666.4638 | 0 | 0 | 14666.4638 | 3.475e-05%
2027 | 1081 | 1081-666F | Tier-1 | Non-HFTD---4 | 3--4 | 5.8293 | 751 | 100% | 169.8745 | 80.26% | 17.52% | 2.222% | 6.7489 | 0 | 0 | 6.7489 | 0 | 6.1415 | 5.7448 | 1.069 | 6.1415 | 5.7448 | 1.069 | 6.8153 | 6.3751 | 1.069 | 3.973% | 0.027363 | 0.026009 | 6208.1833 | 1026.9206 | 1026.1932 | 4155.0696 | 6272.0024 | 0 | 0 | 6272.0024 | 0.0002226%
2027 | 86 | 86-552F | Tier-1 | Non-HFTD---2 | 4--3 | 20.0174 | 1804 | 100% | 186.6357 | 92.7% | 0% | 7.302% | 8.5639 | 0 | 0 | 8.5639 | 0 | 7.793 | 19.7272 | 0.39504 | 7.793 | 19.7272 | 0.39504 | 8.6481 | 21.8916 | 0.39504 | 4.589% | 0.057976 | 0.055107 | 3219.1671 | 590.7148 | 100.2194 | 2528.2329 | 3231.4085 | 0 | 0 | 3231.4085 | 0.0002824%
2027 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 7.8693 | 840 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 432.2395 | 7.7552 | 55.7356 | 432.2395 | 7.7552 | 55.7356 | 479.6638 | 8.6061 | 55.7356 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2027 | 151 | 151-1044F | Tier-1 | Non-HFTD---18 | 1--1 | 1.7676 | 67 | 100% | 0.90758 | 10.2% | 0% | 89.8% | 0.0045835 | 0 | 0 | 0.0045835 | 0 | 0.0041709 | 1.7419 | 0.0023944 | 0.0041709 | 1.7419 | 0.0023944 | 0.0046285 | 1.9331 | 0.0023944 | 0.505% | 0.0041016 | 0.0038986 | 221.2741 | 0.23379 | 40.1127 | 180.9276 | 231.6219 | 0 | 0 | 231.6219 | 1.511e-07%
2027 | 1119 | 1119-9F | Tier-1 | Non-HFTD---7 | 2--3 | 1.7245 | 235 | 100% | 44.0578 | 1.729% | 95.21% | 3.066% | 0.037698 | 0 | 0 | 0.037698 | 0 | 0.034304 | 1.6994 | 0.020186 | 0.034304 | 1.6994 | 0.020186 | 0.038068 | 1.8859 | 0.020186 | 0.08556% | 0.01155 | 0.010978 | 3814.4644 | 11.0382 | 3336.1347 | 467.2915 | 4009.6797 | 0 | 0 | 4009.6797 | 1.243e-06%
2027 | 321 | 321-741 | Tier-1 | Non-HFTD---18 | 1--1 | 1.6644 | 22 | 100% | 1.2108 | 17.09% | 0% | 82.91% | 0.010243 | 0 | 0 | 0.010243 | 0 | 0.0093207 | 1.6403 | 0.0056824 | 0.0093207 | 1.6403 | 0.0056824 | 0.010343 | 1.8203 | 0.0056824 | 0.8459% | 0.0042182 | 0.0040094 | 287.0469 | 0.17908 | 70.6743 | 216.1935 | 299.441 | 0 | 0 | 299.441 | 3.378e-07%
2027 | CMP1 | CB CMP1 | Tier-1 | Non-HFTD---7 | 3--3 | 5.6403 | 486 | 100% | 37.1183 | 89.86% | 0% | 10.14% | 1.6511 | 0 | 0 | 1.6511 | 0 | 1.5025 | 5.5585 | 0.27031 | 1.5025 | 5.5585 | 0.27031 | 1.6674 | 6.1684 | 0.27031 | 4.448% | 0.016556 | 0.015736 | 2241.9834 | 320.7107 | 77.0021 | 1844.2706 | 2253.8174 | 0 | 0 | 2253.8174 | 5.445e-05%
2027 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 8.4553 | 119 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 234.0568 | 8.3327 | 28.0889 | 234.0568 | 8.3327 | 28.0889 | 259.737 | 9.247 | 28.0889 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2027 | 221 | 221-1251R | Tier-1 | Non-HFTD---2 | 5--4 | 16.3418 | 150 | 100% | 1814.8505 | 87.56% | 11.92% | 0.5209% | 78.6628 | 0 | 0 | 78.6628 | 0 | 71.5821 | 16.1049 | 4.4447 | 71.5821 | 16.1049 | 4.4447 | 79.4359 | 17.8719 | 4.4447 | 4.334% | 0.27478 | 0.26118 | 6604.7785 | 826.9947 | 747.1453 | 5030.6385 | 6647.5552 | 0 | 0 | 6647.5552 | 0.002594%
2027 | 1435 | 1435-50 | Tier-1 | Non-HFTD---10 | 3--2 | 8.8248 | 347 | 100% | 15.0882 | 59.27% | 0% | 40.73% | 0.44264 | 0 | 0 | 0.44264 | 0 | 0.40279 | 8.6968 | 0.046315 | 0.40279 | 8.6968 | 0.046315 | 0.44699 | 9.651 | 0.046315 | 2.934% | 0.026149 | 0.024855 | 577.0099 | 71.0904 | 94.7801 | 411.1393 | 589.2502 | 0 | 0 | 589.2502 | 1.46e-05%
2027 | BY2 | CB BY2 | Tier-1 | Non-HFTD---14 | 3--1 | 5.662 | 220 | 100% | 6.8497 | 39.29% | 0% | 60.71% | 0.13321 | 0 | 0 | 0.13321 | 0 | 0.12122 | 5.5799 | 0.021724 | 0.12122 | 5.5799 | 0.021724 | 0.13452 | 6.1921 | 0.021724 | 1.945% | 0.017488 | 0.016622 | 391.6915 | 5.1993 | 144.7113 | 241.7808 | 404.0761 | 0 | 0 | 404.0761 | 4.393e-06%
2027 | 1094 | 1094-8AE | Tier-1 | Non-HFTD---17 | 1--2 | 0.30739 | 2 | 100% | 1.7277 | 85.41% | 0% | 14.59% | 0.073046 | 0 | 0 | 0.073046 | 0 | 0.066471 | 0.30293 | 0.21943 | 0.066471 | 0.30293 | 0.21943 | 0.073764 | 0.33617 | 0.21943 | 4.228% | 0.0010582 | 0.0010058 | 1632.6499 | 227.3238 | 25.8915 | 1379.4346 | 1645.0517 | 0 | 0 | 1645.0517 | 2.409e-06%
2027 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 11.3022 | 644 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 999.3119 | 11.1384 | 89.7179 | 999.3119 | 11.1384 | 89.7179 | 1108.954 | 12.3605 | 89.7179 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2027 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 5.7011 | 351 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 364.787 | 5.6185 | 64.9265 | 364.787 | 5.6185 | 64.9265 | 404.8106 | 6.2349 | 64.9265 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2027 | 184 | CB 184 | Tier-1 | Non-HFTD---6 | 3--3 | 0.49848 | 58 | 100% | 52.4866 | 0.7232% | 98.61% | 0.668% | 0.018789 | 0 | 0 | 0.018789 | 0 | 0.017097 | 0.49126 | 0.034803 | 0.017097 | 0.49126 | 0.034803 | 0.018973 | 0.54516 | 0.034803 | 0.0358% | 0.015821 | 0.015038 | 3317.5286 | 5.4671 | 2617.7865 | 694.2749 | 3489.0489 | 0 | 0 | 3489.0489 | 6.196e-07%
2027 | 1049 | CB 1049 | Tier-1 | Non-HFTD---14 | 3--1 | 5.6832 | 256 | 100% | 5.616 | 24.5% | 0% | 75.5% | 0.068108 | 0 | 0 | 0.068108 | 0 | 0.061977 | 5.6008 | 0.011066 | 0.061977 | 5.6008 | 0.011066 | 0.068777 | 6.2153 | 0.011066 | 1.213% | 0.016475 | 0.015659 | 340.8813 | 1.1864 | 100.8318 | 238.863 | 354.2843 | 0 | 0 | 354.2843 | 2.246e-06%
2027 | 1418 | CB 1418 | Tier-1 | Non-HFTD---8 | 3--3 | 6.1513 | 238 | 100% | 37.4539 | 88.02% | 0% | 11.98% | 1.6319 | 0 | 0 | 1.6319 | 0 | 1.485 | 6.0621 | 0.24496 | 1.485 | 6.0621 | 0.24496 | 1.6479 | 6.7272 | 0.24496 | 4.357% | 0.021901 | 0.020817 | 1710.114 | 123.2993 | 769.7961 | 817.0186 | 1720.7826 | 0 | 0 | 1720.7826 | 5.381e-05%
2027 | 480 | CB 480 | Tier-1 | Non-HFTD---9 | 3--2 | 5.8805 | 429 | 100% | 25.8202 | 85.83% | 0% | 14.17% | 1.097 | 0 | 0 | 1.097 | 0 | 0.99828 | 5.7952 | 0.17226 | 0.99828 | 5.7952 | 0.17226 | 1.1078 | 6.4311 | 0.17226 | 4.249% | 0.015407 | 0.014644 | 1675.8946 | 13.068 | 1380.5081 | 282.3185 | 1688.259 | 0 | 0 | 1688.259 | 3.618e-05%
2027 | BH1 | CB BH1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.0502 | 26 | 100% | 1.0465 | 22.49% | 0% | 77.51% | 0.011651 | 0 | 0 | 0.011651 | 0 | 0.010602 | 1.035 | 0.010244 | 0.010602 | 1.035 | 0.010244 | 0.011765 | 1.1485 | 0.010244 | 1.113% | 0.0030896 | 0.0029367 | 338.7265 | 0.6221 | 97.3891 | 240.7153 | 352.3993 | 0 | 0 | 352.3993 | 3.842e-07%
2027 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 6.7754 | 306 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 58.3418 | 6.6772 | 8.7375 | 58.3418 | 6.6772 | 8.7375 | 64.7429 | 7.4098 | 8.7375 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2027 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 33.4712 | 1327 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2919.5776 | 32.9859 | 88.5099 | 2919.5776 | 32.9859 | 88.5099 | 3239.9069 | 36.605 | 88.5099 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2027 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 4.4727 | 32 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.7703 | 4.4079 | 0.40162 | 1.7703 | 4.4079 | 0.40162 | 1.9645 | 4.8915 | 0.40162 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2027 | 928 | CB 928 | Tier-2 | Tier-2---7 | 4--5 | 3.6036 | 30 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 65.3395 | 0 | 0 | 65.3395 | 0 | 59.4581 | 3.5513 | 16.7424 | 59.4581 | 3.5513 | 16.7424 | 65.9817 | 3.941 | 16.7424 | 3.948% | 0.057199 | 0.054367 | 28934.4603 | 4597.4585 | 5524.6499 | 18812.3519 | 29239.4879 | 0 | 0 | 29239.4879 | 0.002155%
2027 | 223 | 223-47AE | Tier-2 | Tier-2---19 | 1--3 | 1.211 | 4 | 100% | 19.4153 | 96.46% | 0% | 3.541% | 0.92702 | 0 | 0 | 0.92702 | 0 | 0.84358 | 1.1934 | 0.70685 | 0.84358 | 1.1934 | 0.70685 | 0.93613 | 1.3244 | 0.70685 | 4.775% | 0.0044072 | 0.004189 | 4405.3509 | 653.8395 | 200.8811 | 3550.6304 | 4413.4748 | 0 | 0 | 4413.4748 | 3.057e-05%
2027 | 274 | 274-23R | Tier-1 | Non-HFTD---2 | 4--3 | 14.1254 | 479 | 100% | 237.9284 | 4.707% | 91.23% | 4.063% | 0.55433 | 0 | 0 | 0.55433 | 0 | 0.50444 | 13.9205 | 0.036237 | 0.50444 | 13.9205 | 0.036237 | 0.55978 | 15.4479 | 0.036237 | 0.233% | 0.05657 | 0.05377 | 4205.9111 | 11.172 | 3702.6633 | 492.0758 | 4414.6365 | 0 | 0 | 4414.6365 | 1.828e-05%
2027 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 7.8388 | 378 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 408.4997 | 7.7252 | 52.8792 | 408.4997 | 7.7252 | 52.8792 | 453.3194 | 8.5727 | 52.8792 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2027 | 957 | 957-493 | Tier-1 | Non-HFTD---17 | 1--2 | 0.48785 | 55 | 100% | 2.0962 | 82.3% | 0% | 17.7% | 0.085395 | 0 | 0 | 0.085395 | 0 | 0.077708 | 0.48078 | 0.16163 | 0.077708 | 0.48078 | 0.16163 | 0.086234 | 0.53353 | 0.16163 | 4.074% | 0.001752 | 0.0016653 | 1196.4405 | 130.6529 | 183.8941 | 881.8936 | 1207.4687 | 0 | 0 | 1207.4687 | 2.816e-06%
2027 | 298 | 298-42R | Tier-1 | Non-HFTD---15 | 2--2 | 2.2522 | 46 | 100% | 3.8263 | 63.59% | 0% | 36.41% | 0.12045 | 0 | 0 | 0.12045 | 0 | 0.1096 | 2.2196 | 0.04938 | 0.1096 | 2.2196 | 0.04938 | 0.12163 | 2.4631 | 0.04938 | 3.148% | 0.0063514 | 0.006037 | 602.4284 | 45.032 | 128.6085 | 428.7879 | 613.8503 | 0 | 0 | 613.8503 | 3.972e-06%
2027 | 280 | 280-382AE | Tier-1 | Non-HFTD---3 | 4--3 | 4.587 | 113 | 100% | 117.9502 | 9.67% | 87.78% | 2.549% | 0.56458 | 0 | 0 | 0.56458 | 0 | 0.51376 | 4.5205 | 0.11365 | 0.51376 | 4.5205 | 0.11365 | 0.57013 | 5.0164 | 0.11365 | 0.4787% | 0.044174 | 0.041988 | 2670.1025 | 42.9877 | 2159.6326 | 467.4822 | 2795.7093 | 0 | 0 | 2795.7093 | 1.862e-05%
2027 | 504 | 504-40R | Tier-1 | Non-HFTD---1 | 3--5 | 7.4225 | 827 | 100% | 796.3763 | 99.35% | 0% | 0.6476% | 39.1654 | 0 | 0 | 39.1654 | 0 | 35.6399 | 7.3149 | 4.8722 | 35.6399 | 7.3149 | 4.8722 | 39.5503 | 8.1175 | 4.8722 | 4.918% | 0.025961 | 0.024676 | 30675.6364 | 4949.6837 | 226.8975 | 25499.0552 | 30685.9814 | 0 | 0 | 30685.9814 | 0.001292%
2027 | 313 | CB 313 | Tier-1 | Non-HFTD---1 | 3--5 | 1.4046 | 49 | 100% | 413.0978 | 31.58% | 68.15% | 0.2787% | 6.4568 | 0 | 0 | 6.4568 | 0 | 5.8756 | 1.3842 | 4.2448 | 5.8756 | 1.3842 | 4.2448 | 6.5203 | 1.5361 | 4.2448 | 1.563% | 0.023731 | 0.022556 | 17407.518 | 802.6638 | 11509.0826 | 5095.7715 | 18027.8111 | 0 | 0 | 18027.8111 | 0.0002129%
2027 | 412 | 412-23AE | Tier-1 | Non-HFTD---7 | 3--3 | 1.1481 | 46 | 100% | 36.9619 | 12.24% | 85.64% | 2.113% | 0.22399 | 0 | 0 | 0.22399 | 0 | 0.20382 | 1.1314 | 0.18015 | 0.20382 | 1.1314 | 0.18015 | 0.22619 | 1.2556 | 0.18015 | 0.606% | 0.014019 | 0.013325 | 2636.6319 | 50.1124 | 2071.6936 | 514.8259 | 2757.1322 | 0 | 0 | 2757.1322 | 7.386e-06%
2027 | FM2 | CB FM2 | Tier-1 | Non-HFTD---5 | 2--4 | 0.69792 | 11 | 100% | 52.7223 | 13.09% | 85.83% | 1.077% | 0.34171 | 0 | 0 | 0.34171 | 0 | 0.31095 | 0.6878 | 0.4521 | 0.31095 | 0.6878 | 0.4521 | 0.34507 | 0.76326 | 0.4521 | 0.6481% | 0.0078724 | 0.0074827 | 6697.1021 | 78.5971 | 5715.8481 | 902.657 | 7000.2057 | 0 | 0 | 7000.2057 | 1.127e-05%
2027 | 781 | 781-1356R | Tier-1 | Non-HFTD---6 | 3--3 | 1.2461 | 146 | 100% | 45.6239 | 7.996% | 89.78% | 2.228% | 0.18059 | 0 | 0 | 0.18059 | 0 | 0.16433 | 1.228 | 0.13382 | 0.16433 | 1.228 | 0.13382 | 0.18236 | 1.3627 | 0.13382 | 0.3958% | 0.014432 | 0.013718 | 3161.2121 | 4.0758 | 2704.8503 | 452.2859 | 3312.6768 | 0 | 0 | 3312.6768 | 5.955e-06%
2027 | 1435 | 1435-49F | Tier-1 | Non-HFTD---18 | 2--1 | 2.382 | 56 | 100% | 2.1334 | 19.42% | 0% | 80.58% | 0.020506 | 0 | 0 | 0.020506 | 0 | 0.018661 | 2.3475 | 0.0079492 | 0.018661 | 2.3475 | 0.0079492 | 0.020708 | 2.605 | 0.0079492 | 0.9612% | 0.0065472 | 0.0062231 | 325.8446 | 0.86487 | 82.925 | 242.0548 | 339.5187 | 0 | 0 | 339.5187 | 6.762e-07%
2027 | 730 | CB 730 | Tier-1 | Non-HFTD---8 | 3--3 | 6.5873 | 247 | 100% | 39.2172 | 89.21% | 0% | 10.79% | 1.7319 | 0 | 0 | 1.7319 | 0 | 1.576 | 6.4918 | 0.24277 | 1.576 | 6.4918 | 0.24277 | 1.7489 | 7.204 | 0.24277 | 4.416% | 0.017589 | 0.016718 | 2229.6927 | 2.4263 | 1997.325 | 229.9414 | 2242.2171 | 0 | 0 | 2242.2171 | 5.711e-05%
2027 | VS1 | CB VS1 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6964 | 484 | 100% | 11.7597 | 45.03% | 0% | 54.97% | 0.26214 | 0 | 0 | 0.26214 | 0 | 0.23854 | 9.5558 | 0.024963 | 0.23854 | 9.5558 | 0.024963 | 0.26471 | 10.6043 | 0.024963 | 2.229% | 0.026595 | 0.025278 | 442.1842 | 4.4933 | 194.8415 | 242.8495 | 454.8421 | 0 | 0 | 454.8421 | 8.644e-06%
2027 | 570 | CB 570 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3449 | 49 | 100% | 7.1017 | 67.21% | 0% | 32.79% | 0.23626 | 0 | 0 | 0.23626 | 0 | 0.21499 | 2.3109 | 0.093034 | 0.21499 | 2.3109 | 0.093034 | 0.23858 | 2.5644 | 0.093034 | 3.327% | 0.0078126 | 0.0074259 | 909.0044 | 0.23797 | 637.9097 | 270.8567 | 924.5283 | 0 | 0 | 924.5283 | 7.791e-06%
2027 | 718 | 718-483R | Tier-1 | Non-HFTD---14 | 2--2 | 4.2839 | 92 | 100% | 8.2181 | 68.73% | 0% | 31.27% | 0.2796 | 0 | 0 | 0.2796 | 0 | 0.25443 | 4.2218 | 0.060266 | 0.25443 | 4.2218 | 0.060266 | 0.28234 | 4.685 | 0.060266 | 3.402% | 0.013173 | 0.012521 | 623.8598 | 87.3514 | 82.9145 | 453.5939 | 634.0188 | 0 | 0 | 634.0188 | 9.22e-06%
2027 | 305 | CB 305 | Tier-1 | Non-HFTD---1 | 4--5 | 5.6647 | 1678 | 100% | 2786.7739 | 97.11% | 2.732% | 0.1605% | 133.9547 | 0 | 0 | 133.9547 | 0 | 121.8969 | 5.5826 | 21.8351 | 121.8969 | 5.5826 | 21.8351 | 135.2712 | 6.1951 | 21.8351 | 4.807% | 0.073949 | 0.070288 | 37685.1802 | 5958.9331 | 946.9636 | 30779.2836 | 37741.9553 | 0 | 0 | 37741.9553 | 0.004417%
2027 | S1 | CB S1 | Tier-1 | Non-HFTD---12 | 3--1 | 9.143 | 170 | 100% | 10.789 | 35.54% | 0% | 64.46% | 0.18979 | 0 | 0 | 0.18979 | 0 | 0.17271 | 9.0104 | 0.019168 | 0.17271 | 9.0104 | 0.019168 | 0.19166 | 9.999 | 0.019168 | 1.759% | 0.026358 | 0.025053 | 409.3304 | 3.5481 | 148.5276 | 257.2547 | 423.0718 | 0 | 0 | 423.0718 | 6.259e-06%
2027 | CS3 | CB CS3 | Tier-1 | Non-HFTD---12 | 3--1 | 10.2084 | 309 | 100% | 11.962 | 43.21% | 0% | 56.79% | 0.25586 | 0 | 0 | 0.25586 | 0 | 0.23283 | 10.0604 | 0.023143 | 0.23283 | 10.0604 | 0.023143 | 0.25838 | 11.1642 | 0.023143 | 2.139% | 0.027808 | 0.026432 | 430.1588 | 12.7842 | 130.688 | 286.6866 | 442.8806 | 0 | 0 | 442.8806 | 8.437e-06%
2027 | 334 | CB 334 | Tier-2 | Tier-2---17 | 3--4 | 5.1123 | 83 | 100% | 70.5162 | 95.08% | 0% | 4.917% | 3.3189 | 0 | 0 | 3.3189 | 0 | 3.0202 | 5.0382 | 0.59946 | 3.0202 | 5.0382 | 0.59946 | 3.3515 | 5.5909 | 0.59946 | 4.707% | 0.014478 | 0.013762 | 4870.4444 | 330.0733 | 2622.0959 | 1918.2753 | 4882.9165 | 0 | 0 | 4882.9165 | 0.0001094%
2027 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 2.7814 | 123 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 14.2129 | 2.7411 | 5.1851 | 14.2129 | 2.7411 | 5.1851 | 15.7723 | 3.0418 | 5.1851 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2027 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 3.4339 | 113 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 190.3065 | 3.3841 | 56.2355 | 190.3065 | 3.3841 | 56.2355 | 211.1864 | 3.7554 | 56.2355 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2027 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 2.7396 | 163 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 62.4087 | 2.6999 | 23.1152 | 62.4087 | 2.6999 | 23.1152 | 69.256 | 2.9961 | 23.1152 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2027 | GH3 | CB GH3 | Tier-1 | Non-HFTD---14 | 2--1 | 4.7819 | 78 | 100% | 4.974 | 31.67% | 0% | 68.33% | 0.077982 | 0 | 0 | 0.077982 | 0 | 0.070962 | 4.7125 | 0.015058 | 0.070962 | 4.7125 | 0.015058 | 0.078748 | 5.2296 | 0.015058 | 1.568% | 0.013217 | 0.012562 | 376.3479 | 4.2189 | 117.7982 | 254.3308 | 389.7398 | 0 | 0 | 389.7398 | 2.572e-06%
2027 | 105 | 105-239F | Tier-1 | Non-HFTD---15 | 1--3 | 0.26155 | 20 | 100% | 2.4566 | 91.53% | 0% | 8.467% | 0.11131 | 0 | 0 | 0.11131 | 0 | 0.10129 | 0.25776 | 0.39295 | 0.10129 | 0.25776 | 0.39295 | 0.1124 | 0.28604 | 0.39295 | 4.531% | 0.0010678 | 0.0010149 | 2300.6028 | 305.3862 | 246.2943 | 1748.9223 | 2310.7468 | 0 | 0 | 2310.7468 | 3.67e-06%
2027 | 955 | CB 955 | Tier-1 | Non-HFTD---9 | 1--3 | 1.1538 | 14 | 100% | 15.216 | 95.67% | 0% | 4.328% | 0.7206 | 0 | 0 | 0.7206 | 0 | 0.65573 | 1.1371 | 0.57669 | 0.65573 | 1.1371 | 0.57669 | 0.72768 | 1.2618 | 0.57669 | 4.736% | 0.0047456 | 0.0045107 | 3206.3351 | 265.3654 | 1425.9225 | 1515.0472 | 3213.5613 | 0 | 0 | 3213.5613 | 2.376e-05%
2027 | BS1 | CB BS1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.2324 | 4 | 100% | 0.21229 | 51.44% | 0% | 48.56% | 0.0054051 | 0 | 0 | 0.0054051 | 0 | 0.0049186 | 0.22903 | 0.021475 | 0.0049186 | 0.22903 | 0.021475 | 0.0054582 | 0.25416 | 0.021475 | 2.546% | 0.0005254 | 0.00049939 | 404.0635 | 34.0597 | 17.826 | 352.1779 | 414.2829 | 0 | 0 | 414.2829 | 1.782e-07%
2027 | 191 | 191-1050R | Tier-1 | Non-HFTD---7 | 3--3 | 4.7722 | 123 | 100% | 34.1164 | 89.07% | 0% | 10.93% | 1.5041 | 0 | 0 | 1.5041 | 0 | 1.3687 | 4.703 | 0.29104 | 1.3687 | 4.703 | 0.29104 | 1.5189 | 5.219 | 0.29104 | 4.409% | 0.014785 | 0.014053 | 2307.4666 | 326.6145 | 80.7742 | 1900.0778 | 2320.6044 | 0 | 0 | 2320.6044 | 4.96e-05%
2027 | 60 | CB 60 | Tier-1 | Non-HFTD---11 | 2--2 | 2.9972 | 97 | 100% | 10.2312 | 82.34% | 0% | 17.66% | 0.41699 | 0 | 0 | 0.41699 | 0 | 0.37946 | 2.9537 | 0.12847 | 0.37946 | 2.9537 | 0.12847 | 0.42109 | 3.2778 | 0.12847 | 4.076% | 0.0090716 | 0.0086226 | 1127.8283 | 37.9694 | 715.1314 | 374.7275 | 1138.2024 | 0 | 0 | 1138.2024 | 1.375e-05%
2027 | 137 | 137-767F | Tier-1 | Non-HFTD---11 | 2--2 | 2.2822 | 137 | 100% | 10.6804 | 81.68% | 0% | 18.32% | 0.43185 | 0 | 0 | 0.43185 | 0 | 0.39298 | 2.2491 | 0.17473 | 0.39298 | 2.2491 | 0.17473 | 0.43609 | 2.4958 | 0.17473 | 4.043% | 0.0070892 | 0.0067383 | 1506.5775 | 163.4925 | 256.9577 | 1086.1273 | 1520.9482 | 0 | 0 | 1520.9482 | 1.424e-05%
2027 | 41 | 41-43 | Tier-1 | Non-HFTD---10 | 4--2 | 14.0575 | 306 | 100% | 19.885 | 49.34% | 0% | 50.66% | 0.48568 | 0 | 0 | 0.48568 | 0 | 0.44196 | 13.8537 | 0.031902 | 0.44196 | 13.8537 | 0.031902 | 0.49046 | 15.3737 | 0.031902 | 2.442% | 0.039263 | 0.037319 | 506.4606 | 0.58714 | 271.667 | 234.2065 | 519.8217 | 0 | 0 | 519.8217 | 1.602e-05%
2027 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 12.1965 | 1116 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 373.4462 | 12.0196 | 31.0697 | 373.4462 | 12.0196 | 31.0697 | 414.4198 | 13.3384 | 31.0697 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2027 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 0.41023 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.76932 | 0.40428 | 1.9029 | 0.76932 | 0.40428 | 1.9029 | 0.85373 | 0.44864 | 1.9029 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2027 | 380 | 380-27 | Tier-1 | Non-HFTD---10 | 4--2 | 14.4385 | 565 | 100% | 22.878 | 63.4% | 0% | 36.6% | 0.71795 | 0 | 0 | 0.71795 | 0 | 0.65332 | 14.2291 | 0.045915 | 0.65332 | 14.2291 | 0.045915 | 0.72501 | 15.7903 | 0.045915 | 3.138% | 0.038378 | 0.036478 | 596.1298 | 23.7982 | 253.3548 | 318.9768 | 607.4932 | 0 | 0 | 607.4932 | 2.368e-05%
2027 | 936 | 936-188 | Tier-1 | Non-HFTD---4 | 2--4 | 1.8436 | 201 | 100% | 105.8404 | 98.55% | 0% | 1.448% | 5.1632 | 0 | 0 | 5.1632 | 0 | 4.6985 | 1.8169 | 2.586 | 4.6985 | 1.8169 | 2.586 | 5.214 | 2.0162 | 2.586 | 4.878% | 0.0071268 | 0.006774 | 14851.04 | 3722.7452 | 36.3442 | 11091.9506 | 14862.2428 | 0 | 0 | 14862.2428 | 0.0001703%
2027 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 5.3095 | 739 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 408.8067 | 5.2325 | 78.1281 | 408.8067 | 5.2325 | 78.1281 | 453.66 | 5.8066 | 78.1281 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2027 | 169 | 169-35F | Tier-1 | Non-HFTD---20 | 1--1 | 0.08387 | 2 | 100% | 0.038151 | 8.843% | 0% | 91.16% | 0.00016699 | 0 | 0 | 0.00016699 | 0 | 0.00015196 | 0.082654 | 0.0018385 | 0.00015196 | 0.082654 | 0.0018385 | 0.00016863 | 0.091722 | 0.0018385 | 0.4377% | 0.0001782 | 0.00016938 | 214.089 | 0.14685 | 36.6598 | 177.2824 | 224.2524 | 0 | 0 | 224.2524 | 5.507e-09%
2027 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 0.43788 | 83 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 18.2693 | 0.43153 | 42.3361 | 18.2693 | 0.43153 | 42.3361 | 20.2737 | 0.47888 | 42.3361 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2027 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 2.267 | 54 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 40.8246 | 2.2342 | 18.2728 | 40.8246 | 2.2342 | 18.2728 | 45.3038 | 2.4793 | 18.2728 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2027 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.057008 | 0 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.54074 | 0.056181 | 9.6249 | 0.54074 | 0.056181 | 9.6249 | 0.60007 | 0.062345 | 9.6249 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2027 | 344 | CB 344 | Tier-1 | Non-HFTD---14 | 3--1 | 4.5935 | 221 | 100% | 6.1717 | 46.7% | 0% | 53.3% | 0.14267 | 0 | 0 | 0.14267 | 0 | 0.12983 | 4.5269 | 0.028679 | 0.12983 | 4.5269 | 0.028679 | 0.14407 | 5.0236 | 0.028679 | 2.312% | 0.013899 | 0.013211 | 444.0383 | 5.5246 | 196.2264 | 242.2874 | 456.3636 | 0 | 0 | 456.3636 | 4.705e-06%
2027 | 518 | 518-42AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.19057 | 7 | 100% | 0.34431 | 29.34% | 0% | 70.66% | 0.0050004 | 0 | 0 | 0.0050004 | 0 | 0.0045503 | 0.18781 | 0.024228 | 0.0045503 | 0.18781 | 0.024228 | 0.0050495 | 0.20842 | 0.024228 | 1.452% | 0.0008198 | 0.00077922 | 419.9978 | 0.47523 | 148.6345 | 270.8881 | 435.4533 | 0 | 0 | 435.4533 | 1.649e-07%
2027 | FM3 | CB FM3 | Tier-1 | Non-HFTD---3 | 4--3 | 9.8417 | 866 | 100% | 121.1123 | 67.77% | 26.62% | 5.609% | 4.0628 | 0 | 0 | 4.0628 | 0 | 3.6971 | 9.699 | 0.38118 | 3.6971 | 9.699 | 0.38118 | 4.1027 | 10.7631 | 0.38118 | 3.355% | 0.035117 | 0.033379 | 3448.8213 | 613.5911 | 1013.3761 | 1821.8541 | 3506.7114 | 0 | 0 | 3506.7114 | 0.000134%
2027 | 402 | 402-819F | Tier-1 | Non-HFTD---20 | 1--1 | 0.13463 | 13 | 100% | 0.087285 | 16.51% | 0% | 83.49% | 0.00071325 | 0 | 0 | 0.00071325 | 0 | 0.00064905 | 0.13268 | 0.004892 | 0.00064905 | 0.13268 | 0.004892 | 0.00072026 | 0.14723 | 0.004892 | 0.8172% | 0.0003302 | 0.00031386 | 264.3403 | 3.766 | 41.5642 | 219.0101 | 275.834 | 0 | 0 | 275.834 | 2.352e-08%
2027 | HL1 | CB HL1 | Tier-1 | Non-HFTD---12 | 3--1 | 10.6881 | 256 | 100% | 10.8253 | 37.08% | 0% | 62.92% | 0.19871 | 0 | 0 | 0.19871 | 0 | 0.18082 | 10.5331 | 0.017167 | 0.18082 | 10.5331 | 0.017167 | 0.20066 | 11.6888 | 0.017167 | 1.836% | 0.02785 | 0.026472 | 388.6942 | 5.612 | 146.5056 | 236.5767 | 401.4302 | 0 | 0 | 401.4302 | 6.553e-06%
2027 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 6.1881 | 436 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 233.193 | 6.0984 | 38.2385 | 233.193 | 6.0984 | 38.2385 | 258.7784 | 6.7675 | 38.2385 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2027 | 491 | CB 491 | Tier-1 | Non-HFTD---14 | 2--2 | 2.3305 | 61 | 100% | 5.1621 | 58.11% | 0% | 41.89% | 0.14849 | 0 | 0 | 0.14849 | 0 | 0.13513 | 2.2967 | 0.058834 | 0.13513 | 2.2967 | 0.058834 | 0.14995 | 2.5487 | 0.058834 | 2.877% | 0.0082426 | 0.0078346 | 626.2758 | 50.0543 | 81.0381 | 495.1834 | 639.9375 | 0 | 0 | 639.9375 | 4.897e-06%
2027 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.19716 | 0 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.5118 | 0.1943 | 18.0742 | 3.5118 | 0.1943 | 18.0742 | 3.8971 | 0.21562 | 18.0742 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2027 | 214 | CB 214 | Tier-3 | Tier-3---20 | 1--5 | 0.040909 | 0 | 100% | 59.1996 | 99.88% | 0% | 0.1188% | 2.9269 | 0 | 0 | 2.9269 | 0 | 2.6634 | 0.040316 | 66.0642 | 2.6634 | 0.040316 | 66.0642 | 2.9557 | 0.044739 | 66.0642 | 4.944% | 0.0002016 | 0.00019162 | 293649.0501 | 47091.7983 | 966.5627 | 245590.6891 | 293667.224 | 0 | 0 | 293667.224 | 9.652e-05%
2027 | 188 | CB 188 | Tier-1 | Non-HFTD---1 | 4--4 | 10.3012 | 692 | 100% | 378.367 | 98.23% | 0% | 1.765% | 18.3985 | 0 | 0 | 18.3985 | 0 | 16.7424 | 10.1518 | 1.6492 | 16.7424 | 10.1518 | 1.6492 | 18.5793 | 11.2657 | 1.6492 | 4.863% | 0.035993 | 0.034211 | 10512.2388 | 2006.1945 | 714.6271 | 7791.4172 | 10521.9037 | 0 | 0 | 10521.9037 | 0.0006067%
2027 | 178 | CB 178 | Tier-1 | Non-HFTD---1 | 2--5 | 3.4303 | 94 | 100% | 644.514 | 99.63% | 0% | 0.3655% | 31.7868 | 0 | 0 | 31.7868 | 0 | 28.9256 | 3.3806 | 8.5565 | 28.9256 | 3.3806 | 8.5565 | 32.0992 | 3.7515 | 8.5565 | 4.932% | 0.013511 | 0.012843 | 47701.4988 | 11137.324 | 1569.0906 | 34995.0842 | 47710.5792 | 0 | 0 | 47710.5792 | 0.001048%
2027 | 123 | CB 123 | Tier-1 | Non-HFTD---13 | 1--3 | 0.55284 | 1 | 100% | 5.3856 | 82.28% | 0% | 17.72% | 0.21934 | 0 | 0 | 0.21934 | 0 | 0.1996 | 0.54483 | 0.36635 | 0.1996 | 0.54483 | 0.36635 | 0.2215 | 0.6046 | 0.36635 | 4.073% | 0.002683 | 0.0025502 | 2007.2952 | 0.86408 | 1679.9489 | 326.4822 | 2025.8209 | 0 | 0 | 2025.8209 | 7.233e-06%
2027 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 0.14415 | 19 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.2499 | 0.14206 | 15.8378 | 2.2499 | 0.14206 | 15.8378 | 2.4967 | 0.15764 | 15.8378 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2027 | 77 | 77-28R | Tier-1 | Non-HFTD---15 | 1--2 | 1.3614 | 102 | 100% | 2.2554 | 61.57% | 0% | 38.43% | 0.068739 | 0 | 0 | 0.068739 | 0 | 0.062552 | 1.3416 | 0.046624 | 0.062552 | 1.3416 | 0.046624 | 0.069415 | 1.4888 | 0.046624 | 3.048% | 0.003703 | 0.0035197 | 609.0688 | 47.1548 | 109.5378 | 452.3762 | 621.2579 | 0 | 0 | 621.2579 | 2.267e-06%
2027 | 395 | 395-33R | Tier-2 | Tier-2---11 | 4--3 | 0.79815 | 51 | 100% | 396.9757 | 0.1391% | 99.74% | 0.1245% | 0.02734 | 0 | 0 | 0.02734 | 0 | 0.024879 | 0.78658 | 0.03163 | 0.024879 | 0.78658 | 0.03163 | 0.027609 | 0.87288 | 0.03163 | 0.006887% | 0.092102 | 0.087543 | 4310.174 | 6.5289 | 3952.6979 | 350.9472 | 4534.3264 | 0 | 0 | 4534.3264 | 9.016e-07%
2027 | 1039 | CB 1039 | Tier-1 | Non-HFTD---6 | 4--3 | 0.84625 | 23 | 100% | 89.254 | 66.42% | 32.73% | 0.8498% | 2.9347 | 0 | 0 | 2.9347 | 0 | 2.6705 | 0.83398 | 3.2021 | 2.6705 | 0.83398 | 3.2021 | 2.9635 | 0.92548 | 3.2021 | 3.288% | 0.047241 | 0.044903 | 1889.3167 | 183.5723 | 702.9111 | 1002.8332 | 1922.3524 | 0 | 0 | 1922.3524 | 9.677e-05%
2027 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 18.6854 | 1073 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 241.5192 | 18.4145 | 13.1157 | 241.5192 | 18.4145 | 13.1157 | 268.0181 | 20.4348 | 13.1157 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2027 | 416 | 416-29AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.34208 | 11 | 100% | 0.44314 | 13.31% | 0% | 86.69% | 0.0029191 | 0 | 0 | 0.0029191 | 0 | 0.0026564 | 0.33712 | 0.0078796 | 0.0026564 | 0.33712 | 0.0078796 | 0.0029478 | 0.37411 | 0.0078796 | 0.6587% | 0.0012336 | 0.0011725 | 359.222 | 0.32475 | 75.5335 | 283.3638 | 375.4399 | 0 | 0 | 375.4399 | 9.626e-08%
2027 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.0060606 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.2707 | 0.0059727 | 45.3234 | 0.2707 | 0.0059727 | 45.3234 | 0.30041 | 0.006628 | 45.3234 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2027 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.32386 | 75 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 17.7496 | 0.31917 | 55.6122 | 17.7496 | 0.31917 | 55.6122 | 19.6971 | 0.35419 | 55.6122 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2027 | 941 | 941-33F | Tier-1 | Non-HFTD---10 | 3--2 | 9.9011 | 248 | 100% | 24.7891 | 72.11% | 0% | 27.89% | 0.88483 | 0 | 0 | 0.88483 | 0 | 0.80518 | 9.7576 | 0.082519 | 0.80518 | 9.7576 | 0.082519 | 0.89353 | 10.8282 | 0.082519 | 3.569% | 0.028474 | 0.027064 | 870.5979 | 65.8276 | 379.4765 | 425.2938 | 883.243 | 0 | 0 | 883.243 | 2.918e-05%
2027 | 330 | 330-810R | Tier-1 | Non-HFTD---2 | 3--4 | 2.7411 | 85 | 100% | 235.3556 | 4.74% | 94.16% | 1.096% | 0.55218 | 0 | 0 | 0.55218 | 0 | 0.50247 | 2.7013 | 0.18601 | 0.50247 | 2.7013 | 0.18601 | 0.5576 | 2.9977 | 0.18601 | 0.2346% | 0.026057 | 0.024767 | 9032.2679 | 9.3042 | 8071.7191 | 951.2446 | 9480.3546 | 0 | 0 | 9480.3546 | 1.821e-05%
2027 | 795 | 795-821F | Tier-1 | Non-HFTD---6 | 3--3 | 2.1524 | 92 | 100% | 48.0743 | 18.57% | 77.45% | 3.984% | 0.44179 | 0 | 0 | 0.44179 | 0 | 0.40202 | 2.1212 | 0.18953 | 0.40202 | 2.1212 | 0.18953 | 0.44613 | 2.3539 | 0.18953 | 0.919% | 0.024764 | 0.023538 | 1941.2839 | 16.1722 | 1572.1152 | 352.9965 | 2023.6128 | 0 | 0 | 2023.6128 | 1.457e-05%
2027 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.011364 | 0 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.031188 | 0.011199 | 2.7849 | 0.031188 | 0.011199 | 2.7849 | 0.034609 | 0.012428 | 2.7849 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2027 | 340 | 340-378F | Tier-1 | Non-HFTD---1 | 3--4 | 8.3752 | 891 | 100% | 393.7851 | 98.57% | 0% | 1.434% | 19.2129 | 0 | 0 | 19.2129 | 0 | 17.4835 | 8.2537 | 2.1182 | 17.4835 | 8.2537 | 2.1182 | 19.4017 | 9.1593 | 2.1182 | 4.879% | 0.02753 | 0.026167 | 14303.9568 | 3018.559 | 106.2503 | 11179.1475 | 14314.6375 | 0 | 0 | 14314.6375 | 0.0006336%
2027 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 2.3892 | 145 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 193.5126 | 2.3546 | 82.1854 | 193.5126 | 2.3546 | 82.1854 | 214.7444 | 2.6129 | 82.1854 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2027 | 426 | CB 426 | Tier-1 | Non-HFTD---19 | 1--1 | 0.040909 | 5 | 100% | 0.070175 | 3.474% | 0% | 96.53% | 0.00012067 | 0 | 0 | 0.00012067 | 0 | 0.00010981 | 0.040316 | 0.0027237 | 0.00010981 | 0.040316 | 0.0027237 | 0.00012185 | 0.044739 | 0.0027237 | 0.172% | 0.0001956 | 0.00018592 | 358.7676 | 1.9592 | 33.3661 | 323.4423 | 376.8024 | 0 | 0 | 376.8024 | 3.979e-09%
2027 | 310 | 310-1192F | Tier-1 | Non-HFTD---2 | 4--4 | 9.1648 | 499 | 100% | 284.9417 | 1.867% | 95.71% | 2.424% | 0.26335 | 0 | 0 | 0.26335 | 0 | 0.23964 | 9.0319 | 0.026533 | 0.23964 | 9.0319 | 0.026533 | 0.26593 | 10.0228 | 0.026533 | 0.09242% | 0.04251 | 0.040406 | 6702.9643 | 7.4996 | 5968.2158 | 727.249 | 7045.5227 | 0 | 0 | 7045.5227 | 8.684e-06%
2027 | 362 | 362-40F | Tier-1 | Non-HFTD---11 | 2--2 | 1.0875 | 41 | 100% | 13.0284 | 1.16% | 93.92% | 4.92% | 0.0074835 | 0 | 0 | 0.0074835 | 0 | 0.0068099 | 1.0717 | 0.0063541 | 0.0068099 | 1.0717 | 0.0063541 | 0.007557 | 1.1893 | 0.0063541 | 0.05744% | 0.008482 | 0.0080621 | 1536.0068 | 3.2594 | 1317.0481 | 215.6994 | 1615.0705 | 0 | 0 | 1615.0705 | 2.468e-07%
2027 | 191 | CB 191 | Tier-1 | Non-HFTD---11 | 2--2 | 3.2041 | 104 | 100% | 11.195 | 80.08% | 0% | 19.92% | 0.44379 | 0 | 0 | 0.44379 | 0 | 0.40384 | 3.1577 | 0.12789 | 0.40384 | 3.1577 | 0.12789 | 0.44815 | 3.5041 | 0.12789 | 3.964% | 0.009482 | 0.0090126 | 1180.6585 | 96.7187 | 494.004 | 589.9358 | 1192.904 | 0 | 0 | 1192.904 | 1.463e-05%
2027 | 298 | CB 298 | Tier-1 | Non-HFTD---9 | 1--4 | 1.1671 | 125 | 100% | 17.6868 | 96.46% | 0% | 3.539% | 0.84451 | 0 | 0 | 0.84451 | 0 | 0.76849 | 1.1501 | 0.66817 | 0.76849 | 1.1501 | 0.66817 | 0.85281 | 1.2763 | 0.66817 | 4.775% | 0.0035214 | 0.0033471 | 5022.6742 | 642.7129 | 927.2824 | 3452.679 | 5031.9322 | 0 | 0 | 5031.9322 | 2.785e-05%
2027 | 143 | CB 143 | Tier-1 | Non-HFTD---4 | 3--4 | 3.3491 | 132 | 100% | 145.6039 | 54.61% | 44.11% | 1.276% | 3.9361 | 0 | 0 | 3.9361 | 0 | 3.5818 | 3.3005 | 1.0852 | 3.5818 | 3.3005 | 1.0852 | 3.9748 | 3.6626 | 1.0852 | 2.703% | 0.016042 | 0.015248 | 9076.1902 | 871.9142 | 5424.8557 | 2779.4204 | 9290.7228 | 0 | 0 | 9290.7228 | 0.0001298%
2027 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 8.614 | 1088 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 85.0286 | 8.4891 | 10.0162 | 85.0286 | 8.4891 | 10.0162 | 94.3577 | 9.4205 | 10.0162 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2027 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 3.0796 | 180 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 8.6939 | 3.0349 | 2.8646 | 8.6939 | 3.0349 | 2.8646 | 9.6477 | 3.3679 | 2.8646 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2027 | 381 | 381-49 | Tier-1 | Non-HFTD---19 | 1--1 | 0.0083333 | 0 | 100% | 0.029666 | 0.1223% | 0% | 99.88% | 1.7956e-06 | 0 | 0 | 1.7956e-06 | 0 | 1.634e-06 | 0.0082125 | 0.00019896 | 1.634e-06 | 0.0082125 | 0.00019896 | 1.8133e-06 | 0.0091136 | 0.00019896 | 0.006053% | 6.36e-05 | 6.0452e-05 | 466.4424 | 0.35055 | 42.8905 | 423.2013 | 490.704 | 0 | 0 | 490.704 | 5.921e-11%
2027 | 376 | 376-527AE | Tier-1 | Non-HFTD---19 | 1--3 | 0.051894 | 0 | 100% | 0.49148 | 77.98% | 0% | 22.02% | 0.018971 | 0 | 0 | 0.018971 | 0 | 0.017263 | 0.051142 | 0.33756 | 0.017263 | 0.051142 | 0.33756 | 0.019158 | 0.056753 | 0.33756 | 3.86% | 0.0002636 | 0.00025055 | 1864.5025 | 6.946 | 1450.3613 | 407.1952 | 1885.8844 | 0 | 0 | 1885.8844 | 6.256e-07%
2027 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.34621 | 20 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 7.091 | 0.34119 | 20.7831 | 7.091 | 0.34119 | 20.7831 | 7.869 | 0.37863 | 20.7831 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2027 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.87121 | 109 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.9588 | 0.85858 | 6.9403 | 5.9588 | 0.85858 | 6.9403 | 6.6126 | 0.95278 | 6.9403 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2027 | 834 | 834-887AE | Tier-2 | Tier-2---17 | 2--4 | 1.3721 | 178 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 3.435 | 0 | 0 | 3.435 | 0 | 3.1258 | 1.3522 | 2.3115 | 3.1258 | 1.3522 | 2.3115 | 3.4687 | 1.5006 | 2.3115 | 4.883% | 0.0050886 | 0.0048367 | 13824.3748 | 4928.7906 | 56.7151 | 8838.8691 | 13834.1342 | 0 | 0 | 13834.1342 | 0.0001133%
2027 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 2.2803 | 93 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.1871 | 2.2472 | 0.52827 | 1.1871 | 2.2472 | 0.52827 | 1.3174 | 2.4938 | 0.52827 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2027 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | 3--5 | 8.4224 | 554 | 100% | 1585.8519 | 99.67% | 0% | 0.3254% | 78.2443 | 0 | 0 | 78.2443 | 0 | 71.2012 | 8.3003 | 8.5782 | 71.2012 | 8.3003 | 8.5782 | 79.0132 | 9.211 | 8.5782 | 4.934% | 0.026002 | 0.024715 | 60989.6136 | 9907.2213 | 216.3013 | 50866.0909 | 60999.9476 | 0 | 0 | 60999.9476 | 0.00258%
2027 | 418 | CB 418 | Tier-1 | Non-HFTD---8 | 3--2 | 7.4191 | 168 | 100% | 32.4786 | 83.15% | 0% | 16.85% | 1.3368 | 0 | 0 | 1.3368 | 0 | 1.2165 | 7.3115 | 0.16638 | 1.2165 | 7.3115 | 0.16638 | 1.35 | 8.1137 | 0.16638 | 4.116% | 0.022349 | 0.021243 | 1453.2194 | 9.9672 | 1170.7456 | 272.5066 | 1465.9693 | 0 | 0 | 1465.9693 | 4.408e-05%
2027 | SW3 | CB SW3 | Tier-1 | Non-HFTD---10 | 3--2 | 7.1382 | 267 | 100% | 18.2834 | 70.37% | 0% | 29.63% | 0.63685 | 0 | 0 | 0.63685 | 0 | 0.57952 | 7.0347 | 0.08238 | 0.57952 | 7.0347 | 0.08238 | 0.6431 | 7.8066 | 0.08238 | 3.483% | 0.021128 | 0.020082 | 865.3622 | 65.6443 | 230.815 | 568.9028 | 878.7164 | 0 | 0 | 878.7164 | 2.1e-05%
2027 | RV2 | CB RV2 | Tier-1 | Non-HFTD---18 | 1--1 | 0.8741 | 49 | 100% | 0.72292 | 8.676% | 0% | 91.32% | 0.0031046 | 0 | 0 | 0.0031046 | 0 | 0.0028251 | 0.86142 | 0.0032796 | 0.0028251 | 0.86142 | 0.0032796 | 0.0031351 | 0.95594 | 0.0032796 | 0.4295% | 0.0024738 | 0.0023513 | 292.2303 | 0.20082 | 49.5965 | 242.4329 | 306.1286 | 0 | 0 | 306.1286 | 1.024e-07%
2027 | 299 | 299-1153F | Tier-1 | Non-HFTD---11 | 1--4 | 0.33445 | 5 | 100% | 12.6944 | 96.89% | 0% | 3.107% | 0.60885 | 0 | 0 | 0.60885 | 0 | 0.55404 | 0.3296 | 1.6809 | 0.55404 | 0.3296 | 1.6809 | 0.61483 | 0.36577 | 1.6809 | 4.796% | 0.0013374 | 0.0012712 | 9491.8205 | 1360.071 | 891.9808 | 7239.7687 | 9507.1772 | 0 | 0 | 9507.1772 | 2.008e-05%
2027 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 3.4163 | 181 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 101.4086 | 3.3668 | 30.1205 | 101.4086 | 3.3668 | 30.1205 | 112.5349 | 3.7362 | 30.1205 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2027 | 138 | 138-366 | Tier-1 | Non-HFTD---19 | 1--1 | 0.08428 | 0 | 100% | 0.163 | 7.427% | 0% | 92.57% | 0.00059926 | 0 | 0 | 0.00059926 | 0 | 0.00054532 | 0.083058 | 0.0065655 | 0.00054532 | 0.083058 | 0.0065655 | 0.00060515 | 0.092171 | 0.0065655 | 0.3676% | 0.000406 | 0.0003859 | 401.4766 | 0.27966 | 63.5802 | 337.6168 | 420.8318 | 0 | 0 | 420.8318 | 1.976e-08%
2027 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 11.5796 | 1432 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 221.282 | 11.4117 | 19.3908 | 221.282 | 11.4117 | 19.3908 | 245.5605 | 12.6638 | 19.3908 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2027 | 417 | 417-21R | Tier-1 | Non-HFTD---3 | 4--3 | 10.3053 | 362 | 100% | 169.2976 | 37.28% | 58.96% | 3.759% | 3.1239 | 0 | 0 | 3.1239 | 0 | 2.8427 | 10.1559 | 0.27991 | 2.8427 | 10.1559 | 0.27991 | 3.1546 | 11.2701 | 0.27991 | 1.845% | 0.039679 | 0.037715 | 4266.681 | 378.3982 | 2573.6009 | 1314.6819 | 4406.0517 | 0 | 0 | 4406.0517 | 0.000103%
2027 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 8.9743 | 877 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 502.5613 | 8.8441 | 56.8242 | 502.5613 | 8.8441 | 56.8242 | 557.7011 | 9.8145 | 56.8242 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2027 | 144 | 144-445F | Tier-1 | Non-HFTD---7 | 3--3 | 3.6072 | 172 | 100% | 44.172 | 3.542% | 89.64% | 6.821% | 0.077447 | 0 | 0 | 0.077447 | 0 | 0.070476 | 3.5549 | 0.019825 | 0.070476 | 3.5549 | 0.019825 | 0.078208 | 3.945 | 0.019825 | 0.1753% | 0.01688 | 0.016045 | 2616.7604 | 3.9028 | 2254.4176 | 358.4401 | 2748.2088 | 0 | 0 | 2748.2088 | 2.554e-06%
2027 | 286 | 286-1053R | Tier-1 | Non-HFTD---6 | 4--3 | 9.9807 | 1044 | 100% | 76.5163 | 19.5% | 72.04% | 8.463% | 0.73848 | 0 | 0 | 0.73848 | 0 | 0.67201 | 9.836 | 0.068321 | 0.67201 | 9.836 | 0.068321 | 0.74574 | 10.9152 | 0.068321 | 0.9651% | 0.033619 | 0.031955 | 2275.9575 | 19.2195 | 1851.9212 | 404.8167 | 2371.3746 | 0 | 0 | 2371.3746 | 2.435e-05%
2027 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 10.35 | 794 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 192.6453 | 10.2 | 18.8869 | 192.6453 | 10.2 | 18.8869 | 213.7819 | 11.3191 | 18.8869 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2027 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 6.2353 | 475 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 157.9098 | 6.1449 | 25.6979 | 157.9098 | 6.1449 | 25.6979 | 175.2352 | 6.8191 | 25.6979 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2027 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 2.3515 | 10 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 256.8046 | 2.3174 | 110.8143 | 256.8046 | 2.3174 | 110.8143 | 284.9806 | 2.5717 | 110.8143 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2027 | 178 | 178-48 | Tier-1 | Non-HFTD---15 | 1--3 | 0.243 | 28 | 100% | 2.3951 | 91.42% | 0% | 8.578% | 0.10839 | 0 | 0 | 0.10839 | 0 | 0.09863 | 0.23948 | 0.41185 | 0.09863 | 0.23948 | 0.41185 | 0.10945 | 0.26575 | 0.41185 | 4.525% | 0.0008186 | 0.00077808 | 2925.8017 | 435.8246 | 30.2443 | 2459.7328 | 2938.8721 | 0 | 0 | 2938.8721 | 3.574e-06%
2027 | 719 | 719-856F | Tier-1 | Non-HFTD---20 | 1--1 | 0.65096 | 19 | 100% | 0.5127 | 9.051% | 0% | 90.95% | 0.0022971 | 0 | 0 | 0.0022971 | 0 | 0.0020903 | 0.64152 | 0.0032584 | 0.0020903 | 0.64152 | 0.0032584 | 0.0023197 | 0.71191 | 0.0032584 | 0.448% | 0.0018984 | 0.0018044 | 270.0677 | 0.18482 | 46.7574 | 223.1254 | 282.8592 | 0 | 0 | 282.8592 | 7.575e-08%
2027 | 308 | 308-484AE | Tier-1 | Non-HFTD---3 | 4--3 | 4.8747 | 173 | 100% | 121.7186 | 8.654% | 88.76% | 2.589% | 0.52141 | 0 | 0 | 0.52141 | 0 | 0.47448 | 4.804 | 0.098768 | 0.47448 | 4.804 | 0.098768 | 0.52654 | 5.3311 | 0.098768 | 0.4284% | 0.043365 | 0.041218 | 2806.8523 | 43.4645 | 2320.9674 | 442.4205 | 2940.3772 | 0 | 0 | 2940.3772 | 1.719e-05%
2027 | 517 | CB 517 | Tier-1 | Non-HFTD---13 | 2--2 | 2.9201 | 69 | 100% | 8.4391 | 68.2% | 0% | 31.8% | 0.28488 | 0 | 0 | 0.28488 | 0 | 0.25924 | 2.8777 | 0.090085 | 0.25924 | 2.8777 | 0.090085 | 0.28768 | 3.1935 | 0.090085 | 3.376% | 0.010508 | 0.0099879 | 803.1131 | 55.9391 | 225.7298 | 521.4442 | 816.4147 | 0 | 0 | 816.4147 | 9.394e-06%
2027 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | 4--5 | 1.5992 | 53 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 37.535 | 0 | 0 | 37.535 | 0 | 34.1563 | 1.5761 | 21.672 | 34.1563 | 1.5761 | 21.672 | 37.9039 | 1.749 | 21.672 | 3.124% | 0.042337 | 0.040241 | 28377.3086 | 3599.9822 | 10019.8495 | 14757.4769 | 28922.3867 | 0 | 0 | 28922.3867 | 0.001238%
2027 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 1.375 | 64 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 123.3195 | 1.355 | 91.0092 | 123.3195 | 1.355 | 91.0092 | 136.8498 | 1.5037 | 91.0092 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2027 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 2.9682 | 204 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 312.0217 | 2.9252 | 106.6677 | 312.0217 | 2.9252 | 106.6677 | 346.256 | 3.2461 | 106.6677 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2027 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 13.8096 | 550 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 159.8647 | 13.6094 | 11.7466 | 159.8647 | 13.6094 | 11.7466 | 177.4047 | 15.1026 | 11.7466 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2027 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 8.2782 | 241 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 24.4376 | 8.1582 | 2.9955 | 24.4376 | 8.1582 | 2.9955 | 27.1188 | 9.0533 | 2.9955 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2027 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 10.4533 | 579 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 26.069 | 10.3017 | 2.5306 | 26.069 | 10.3017 | 2.5306 | 28.9292 | 11.432 | 2.5306 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2027 | 139 | 139-48 | Tier-1 | Non-HFTD---10 | 3--2 | 5.7198 | 188 | 100% | 22.1253 | 79.12% | 0% | 20.88% | 0.86657 | 0 | 0 | 0.86657 | 0 | 0.78857 | 5.6369 | 0.13989 | 0.78857 | 5.6369 | 0.13989 | 0.87509 | 6.2554 | 0.13989 | 3.917% | 0.020647 | 0.019625 | 1071.5768 | 0.73997 | 864.6922 | 206.1446 | 1083.2264 | 0 | 0 | 1083.2264 | 2.858e-05%
2027 | 595 | 595-500 | Tier-1 | Non-HFTD---1 | 3--4 | 2.1604 | 125 | 100% | 238.2364 | 29.81% | 69.49% | 0.6998% | 3.5151 | 0 | 0 | 3.5151 | 0 | 3.1987 | 2.1291 | 1.5024 | 3.1987 | 2.1291 | 1.5024 | 3.5497 | 2.3627 | 1.5024 | 1.475% | 0.021896 | 0.020812 | 10880.3635 | 1188.0308 | 6831.5625 | 2860.7703 | 11278.0913 | 0 | 0 | 11278.0913 | 0.0001159%
2027 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 4.354 | 0 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 21.107 | 4.2909 | 4.9191 | 21.107 | 4.2909 | 4.9191 | 23.4228 | 4.7616 | 4.9191 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2027 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 11.4604 | 813 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 194.367 | 11.2942 | 17.2094 | 194.367 | 11.2942 | 17.2094 | 215.6925 | 12.5334 | 17.2094 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2027 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 1.1486 | 90 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.4415 | 1.132 | 8.3406 | 9.4415 | 1.132 | 8.3406 | 10.4774 | 1.2562 | 8.3406 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2027 | 493 | 493-478R | Tier-1 | Non-HFTD---8 | 3--3 | 4.1928 | 240 | 100% | 28.2075 | 88.18% | 0% | 11.82% | 1.2312 | 0 | 0 | 1.2312 | 0 | 1.1204 | 4.132 | 0.27114 | 1.1204 | 4.132 | 0.27114 | 1.2433 | 4.5854 | 0.27114 | 4.365% | 0.014664 | 0.013938 | 1923.5642 | 293.7928 | 238.0854 | 1391.686 | 1935.4086 | 0 | 0 | 1935.4086 | 4.06e-05%
2027 | 416 | CB 416 | Tier-1 | Non-HFTD---13 | 1--4 | 0.49546 | 7 | 100% | 7.4419 | 94.25% | 0% | 5.754% | 0.34718 | 0 | 0 | 0.34718 | 0 | 0.31593 | 0.48828 | 0.64703 | 0.31593 | 0.48828 | 0.64703 | 0.35059 | 0.54185 | 0.64703 | 4.665% | 0.0015346 | 0.0014586 | 4849.4324 | 38.4789 | 4361.574 | 449.3795 | 4863.9644 | 0 | 0 | 4863.9644 | 1.145e-05%
2027 | 243 | 243-20R | Tier-1 | Non-HFTD---2 | 4--4 | 10.387 | 501 | 100% | 388.804 | 72.37% | 26.23% | 1.398% | 13.9291 | 0 | 0 | 13.9291 | 0 | 12.6752 | 10.2364 | 1.2383 | 12.6752 | 10.2364 | 1.2383 | 14.0659 | 11.3595 | 1.2383 | 3.583% | 0.058161 | 0.055282 | 6684.9371 | 1057.1463 | 1810.7065 | 3817.0843 | 6781.1116 | 0 | 0 | 6781.1116 | 0.0004593%
2027 | 724 | CB 724 | Tier-1 | Non-HFTD---20 | 1--1 | 0.25037 | 5 | 100% | 0.16085 | 8.868% | 0% | 91.13% | 0.00070607 | 0 | 0 | 0.00070607 | 0 | 0.00064251 | 0.24674 | 0.002604 | 0.00064251 | 0.24674 | 0.002604 | 0.00071301 | 0.27381 | 0.002604 | 0.439% | 0.000606 | 0.000576 | 265.4252 | 0.18201 | 45.5111 | 219.7321 | 278.0222 | 0 | 0 | 278.0222 | 2.328e-08%
2027 | 706 | CB 706 | Tier-1 | Non-HFTD---7 | 2--3 | 1.7864 | 19 | 100% | 32.9411 | 96.6% | 0.3164% | 3.084% | 1.5751 | 0 | 0 | 1.5751 | 0 | 1.4334 | 1.7605 | 0.81419 | 1.4334 | 1.7605 | 0.81419 | 1.5906 | 1.9536 | 0.81419 | 4.782% | 0.010907 | 0.010367 | 3020.124 | 527.3897 | 16.8429 | 2475.8914 | 3025.472 | 0 | 0 | 3025.472 | 5.194e-05%
2027 | 145 | CB 145 | Tier-1 | Non-HFTD---5 | 2--4 | 1.2373 | 52 | 100% | 50.1579 | 64.45% | 33.49% | 2.055% | 1.6003 | 0 | 0 | 1.6003 | 0 | 1.4562 | 1.2193 | 1.1943 | 1.4562 | 1.2193 | 1.1943 | 1.616 | 1.3531 | 1.1943 | 3.19% | 0.0096286 | 0.009152 | 5209.2634 | 427.9347 | 3048.2211 | 1733.1076 | 5305.6973 | 0 | 0 | 5305.6973 | 5.277e-05%
2027 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 10.5116 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 389.3404 | 10.3592 | 37.5841 | 389.3404 | 10.3592 | 37.5841 | 432.0579 | 11.4958 | 37.5841 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2027 | 411 | CB 411 | Tier-1 | Non-HFTD---17 | 1--4 | 0.039773 | 7 | 100% | 0.73685 | 95.5% | 0% | 4.499% | 0.034833 | 0 | 0 | 0.034833 | 0 | 0.031698 | 0.039196 | 0.8087 | 0.031698 | 0.039196 | 0.8087 | 0.035176 | 0.043497 | 0.8087 | 4.727% | 0.000145 | 0.00013782 | 5081.7307 | 456.5916 | 2088.6806 | 2536.4584 | 5093.636 | 0 | 0 | 5093.636 | 1.149e-06%
2027 | 916 | 916-381 | Tier-2 | Tier-2---12 | 4--4 | 1.3913 | 284 | 100% | 590.9122 | 71.07% | 28.73% | 0.1918% | 20.7893 | 0 | 0 | 20.7893 | 0 | 18.918 | 1.3712 | 13.797 | 18.918 | 1.3712 | 13.797 | 20.9936 | 1.5216 | 13.797 | 3.518% | 0.049834 | 0.047367 | 11857.5641 | 1782.085 | 3001.9836 | 7073.4955 | 12036.1866 | 0 | 0 | 12036.1866 | 0.0006856%
2027 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 31.8811 | 2437 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 613.1991 | 31.4188 | 19.5169 | 613.1991 | 31.4188 | 19.5169 | 680.4779 | 34.866 | 19.5169 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2027 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 7.3848 | 136 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 41.8749 | 7.2777 | 5.7538 | 41.8749 | 7.2777 | 5.7538 | 46.4693 | 8.0762 | 5.7538 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2027 | 258 | CB 258 | Tier-1 | Non-HFTD---19 | 1--1 | 0.065341 | 0 | 100% | 0.17536 | 0.484% | 0% | 99.52% | 4.2015e-05 | 0 | 0 | 4.2015e-05 | 0 | 3.8233e-05 | 0.064394 | 0.00059374 | 3.8233e-05 | 0.064394 | 0.00059374 | 4.2428e-05 | 0.071459 | 0.00059374 | 0.02396% | 0.0003514 | 0.00033401 | 499.0252 | 0.67763 | 45.6717 | 452.6758 | 524.8876 | 0 | 0 | 524.8876 | 1.386e-09%
2027 | 63 | 63-797R | Tier-1 | Non-HFTD---1 | 3--5 | 3.9205 | 872 | 100% | 1294.9207 | 95.84% | 3.945% | 0.2104% | 61.435 | 0 | 0 | 61.435 | 0 | 55.905 | 3.8636 | 14.4695 | 55.905 | 3.8636 | 14.4695 | 62.0388 | 4.2875 | 14.4695 | 4.744% | 0.02549 | 0.024229 | 50800.3291 | 10671.1023 | 1938.6345 | 38190.5924 | 50910.264 | 0 | 0 | 50910.264 | 0.002026%
2027 | 366 | CB 366 | Tier-1 | Non-HFTD---5 | 3--4 | 3.4801 | 66 | 100% | 92.421 | 14.77% | 81.62% | 3.609% | 0.67569 | 0 | 0 | 0.67569 | 0 | 0.61487 | 3.4296 | 0.17928 | 0.61487 | 3.4296 | 0.17928 | 0.68233 | 3.8059 | 0.17928 | 0.7311% | 0.016207 | 0.015404 | 5702.6756 | 6.2073 | 5082.696 | 613.7722 | 5955.7953 | 0 | 0 | 5955.7953 | 2.228e-05%
2027 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | 2--4 | 2.8968 | 266 | 100% | 92.0555 | 97.82% | 0% | 2.183% | 4.4573 | 0 | 0 | 4.4573 | 0 | 4.0561 | 2.8548 | 1.4208 | 4.0561 | 2.8548 | 1.4208 | 4.5011 | 3.168 | 1.4208 | 4.842% | 0.0089936 | 0.0085484 | 10235.6661 | 2125.5614 | 107.0953 | 8003.0094 | 10247.3023 | 0 | 0 | 10247.3023 | 0.000147%
2027 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 6.8056 | 633 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 72.0469 | 6.707 | 10.7421 | 72.0469 | 6.707 | 10.7421 | 79.9518 | 7.4428 | 10.7421 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2027 | 1139 | 1139-5 | Tier-1 | Non-HFTD---2 | 5--3 | 0.75514 | 11 | 100% | 335.8565 | 0.3706% | 99.5% | 0.1331% | 0.061619 | 0 | 0 | 0.061619 | 0 | 0.056072 | 0.74419 | 0.075346 | 0.056072 | 0.74419 | 0.075346 | 0.062224 | 0.82584 | 0.075346 | 0.01835% | 0.10416 | 0.099006 | 3224.3672 | 4.3588 | 2910.0555 | 309.953 | 3391.6629 | 0 | 0 | 3391.6629 | 2.032e-06%
2027 | MA2 | CB MA2 | Tier-1 | Non-HFTD---8 | 3--2 | 3.6417 | 126 | 100% | 40.2518 | 2.195% | 91.76% | 6.046% | 0.043733 | 0 | 0 | 0.043733 | 0 | 0.039797 | 3.5889 | 0.011089 | 0.039797 | 3.5889 | 0.011089 | 0.044163 | 3.9827 | 0.011089 | 0.1086% | 0.025041 | 0.023801 | 1607.4358 | 4.4717 | 1386.7821 | 216.182 | 1689.3102 | 0 | 0 | 1689.3102 | 1.442e-06%
2027 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 0.38935 | 10 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 8.1497 | 0.3837 | 21.2397 | 8.1497 | 0.3837 | 21.2397 | 9.0438 | 0.4258 | 21.2397 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2027 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 9.5874 | 639 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 43.4702 | 9.4483 | 4.6008 | 43.4702 | 9.4483 | 4.6008 | 48.2397 | 10.485 | 4.6008 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2027 | 165 | 165-621F | Tier-1 | Non-HFTD---3 | 4--3 | 12.0826 | 329 | 100% | 101.1468 | 91.67% | 0% | 8.335% | 4.5895 | 0 | 0 | 4.5895 | 0 | 4.1764 | 11.9074 | 0.35074 | 4.1764 | 11.9074 | 0.35074 | 4.6346 | 13.2139 | 0.35074 | 4.537% | 0.037528 | 0.03567 | 2695.236 | 312.5984 | 579.2909 | 1803.3467 | 2706.9347 | 0 | 0 | 2706.9347 | 0.0001513%
2027 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 6.5815 | 249 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 55.5708 | 6.4861 | 8.5677 | 55.5708 | 6.4861 | 8.5677 | 61.6679 | 7.1977 | 8.5677 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2027 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 5.9877 | 450 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 240.2011 | 5.9009 | 40.7057 | 240.2011 | 5.9009 | 40.7057 | 266.5555 | 6.5484 | 40.7057 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2027 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 5.0582 | 548 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 65.2597 | 4.9848 | 13.0917 | 65.2597 | 4.9848 | 13.0917 | 72.4198 | 5.5317 | 13.0917 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2027 | MK2 | CB MK2 | Tier-1 | Non-HFTD---14 | 3--1 | 6.9771 | 167 | 100% | 8.3451 | 44.18% | 0% | 55.82% | 0.18252 | 0 | 0 | 0.18252 | 0 | 0.16609 | 6.8759 | 0.024155 | 0.16609 | 6.8759 | 0.024155 | 0.18431 | 7.6303 | 0.024155 | 2.187% | 0.019822 | 0.01884 | 421.0108 | 29.7884 | 90.8373 | 300.3851 | 433.2487 | 0 | 0 | 433.2487 | 6.019e-06%
2027 | 209 | 209-661 | Tier-1 | Non-HFTD---4 | 1--5 | 1.3877 | 115 | 100% | 118.7112 | 99.11% | 0% | 0.8879% | 5.824 | 0 | 0 | 5.824 | 0 | 5.2998 | 1.3676 | 3.8752 | 5.2998 | 1.3676 | 3.8752 | 5.8813 | 1.5177 | 3.8752 | 4.906% | 0.0044254 | 0.0042063 | 26824.9714 | 4214.0457 | 851.0995 | 21759.8261 | 26837.3758 | 0 | 0 | 26837.3758 | 0.0001921%
2027 | 340 | 340-376F | Tier-1 | Non-HFTD---7 | 2--3 | 2.4146 | 200 | 100% | 34.9276 | 95.82% | 0% | 4.178% | 1.6567 | 0 | 0 | 1.6567 | 0 | 1.5076 | 2.3795 | 0.63355 | 1.5076 | 2.3795 | 0.63355 | 1.673 | 2.6406 | 0.63355 | 4.743% | 0.0073482 | 0.0069845 | 4753.2178 | 524.3665 | 2205.6799 | 2023.1714 | 4763.5601 | 0 | 0 | 4763.5601 | 5.463e-05%
2027 | 579 | CB 579 | Tier-1 | Non-HFTD---6 | 3--3 | 1.4538 | 9 | 100% | 49.6621 | 21.66% | 75.14% | 3.198% | 0.53254 | 0 | 0 | 0.53254 | 0 | 0.4846 | 1.4327 | 0.33825 | 0.4846 | 1.4327 | 0.33825 | 0.53777 | 1.5899 | 0.33825 | 1.072% | 0.015297 | 0.01454 | 3246.5274 | 3.0703 | 2897.813 | 345.6441 | 3378.9733 | 0 | 0 | 3378.9733 | 1.756e-05%
2027 | 325 | CB 325 | Tier-1 | Non-HFTD---7 | 1--4 | 1.1091 | 146 | 100% | 43.928 | 97.88% | 0% | 2.116% | 2.1284 | 0 | 0 | 2.1284 | 0 | 1.9368 | 1.093 | 1.772 | 1.9368 | 1.093 | 1.772 | 2.1493 | 1.2129 | 1.772 | 4.845% | 0.0043742 | 0.0041577 | 10042.5141 | 384.3371 | 7501.7135 | 2156.4635 | 10053.582 | 0 | 0 | 10053.582 | 7.019e-05%
2027 | 368 | CB 368 | Tier-1 | Non-HFTD---4 | 3--4 | 3.9384 | 124 | 100% | 110.2844 | 13.26% | 83.59% | 3.156% | 0.72366 | 0 | 0 | 0.72366 | 0 | 0.65852 | 3.8813 | 0.16966 | 0.65852 | 3.8813 | 0.16966 | 0.73077 | 4.3072 | 0.16966 | 0.6562% | 0.016985 | 0.016144 | 6492.9689 | 7.2051 | 5795.9328 | 689.831 | 6786.285 | 0 | 0 | 6786.285 | 2.386e-05%
2027 | 480 | 480-1163R | Tier-1 | Non-HFTD---16 | 2--1 | 3.6682 | 75 | 100% | 3.8801 | 32.98% | 0% | 67.02% | 0.06334 | 0 | 0 | 0.06334 | 0 | 0.057638 | 3.615 | 0.015944 | 0.057638 | 3.615 | 0.015944 | 0.063962 | 4.0117 | 0.015944 | 1.632% | 0.010077 | 0.0095782 | 385.0495 | 0.19419 | 150.4248 | 234.4305 | 398.4891 | 0 | 0 | 398.4891 | 2.089e-06%
2027 | 500 | 500-1531 | Tier-2 | Tier-2---10 | 4--4 | 0.97704 | 34 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 8.56 | 0 | 0 | 8.56 | 0 | 7.7895 | 0.96288 | 8.0898 | 7.7895 | 0.96288 | 8.0898 | 8.6441 | 1.0685 | 8.0898 | 1.069% | 0.071178 | 0.067654 | 11247.1911 | 406.5986 | 8046.836 | 2793.7565 | 11706.3951 | 0 | 0 | 11706.3951 | 0.0002823%
2027 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 2.2354 | 19 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 96.3058 | 2.203 | 43.7154 | 96.3058 | 2.203 | 43.7154 | 106.8723 | 2.4447 | 43.7154 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2027 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 1.5907 | 13 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.2738 | 1.5676 | 2.0884 | 3.2738 | 1.5676 | 2.0884 | 3.633 | 1.7396 | 2.0884 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2027 | 395 | CB 395 | Tier-1 | Non-HFTD---2 | 4--4 | 0.85682 | 57 | 100% | 731.6954 | 0.7674% | 99.15% | 0.08318% | 0.27795 | 0 | 0 | 0.27795 | 0 | 0.25293 | 0.8444 | 0.29954 | 0.25293 | 0.8444 | 0.29954 | 0.28068 | 0.93704 | 0.29954 | 0.03799% | 0.090668 | 0.08618 | 8070.0864 | 11.9063 | 7403.1498 | 655.0303 | 8487.134 | 0 | 0 | 8487.134 | 9.166e-06%
2027 | 508 | 508-1027F | Tier-1 | Non-HFTD---19 | 1--2 | 0.083367 | 2 | 100% | 0.19317 | 84.46% | 0% | 15.54% | 0.0080765 | 0 | 0 | 0.0080765 | 0 | 0.0073495 | 0.082158 | 0.089456 | 0.0073495 | 0.082158 | 0.089456 | 0.0081559 | 0.091172 | 0.089456 | 4.181% | 0.0001954 | 0.00018573 | 988.6113 | 136.442 | 18.1035 | 834.0658 | 996.6104 | 0 | 0 | 996.6104 | 2.663e-07%
2027 | 96 | 96-1041F | Tier-1 | Non-HFTD---13 | 2--2 | 0.096362 | 0 | 100% | 5.6175 | 97.14% | 1.791% | 1.068% | 0.27012 | 0 | 0 | 0.27012 | 0 | 0.2458 | 0.094965 | 2.5883 | 0.2458 | 0.094965 | 2.5883 | 0.27277 | 0.10538 | 2.5883 | 4.808% | 0.005633 | 0.0053542 | 997.2446 | 127.463 | 205.2994 | 664.4822 | 998.7294 | 0 | 0 | 998.7294 | 8.907e-06%
2027 | 531 | 531-36AE | Tier-1 | Non-HFTD---12 | 3--2 | 5.9676 | 195 | 100% | 9.706 | 61.11% | 0% | 38.89% | 0.29361 | 0 | 0 | 0.29361 | 0 | 0.26719 | 5.8811 | 0.045431 | 0.26719 | 5.8811 | 0.045431 | 0.2965 | 6.5264 | 0.045431 | 3.025% | 0.016 | 0.015208 | 606.6092 | 2.6548 | 376.9073 | 227.0471 | 618.894 | 0 | 0 | 618.894 | 9.682e-06%
2027 | 438 | CB 438 | Tier-1 | Non-HFTD---9 | 1--4 | 0.50947 | 74 | 100% | 16.6829 | 97.05% | 0% | 2.95% | 0.80144 | 0 | 0 | 0.80144 | 0 | 0.7293 | 0.50208 | 1.4526 | 0.7293 | 0.50208 | 1.4526 | 0.80932 | 0.55717 | 1.4526 | 4.804% | 0.0021344 | 0.0020287 | 7816.2233 | 299.4615 | 5763.6381 | 1753.1236 | 7828.2327 | 0 | 0 | 7828.2327 | 2.643e-05%
2027 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 1.6328 | 7 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.9193 | 1.6091 | 6.7859 | 10.9193 | 1.6091 | 6.7859 | 12.1173 | 1.7857 | 6.7859 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2027 | 791 | CB 791 | Tier-1 | Non-HFTD---1 | 2--5 | 2.9851 | 216 | 100% | 969.8887 | 99.78% | 0% | 0.2167% | 47.9055 | 0 | 0 | 47.9055 | 0 | 43.5933 | 2.9418 | 14.8187 | 43.5933 | 2.9418 | 14.8187 | 48.3763 | 3.2645 | 14.8187 | 4.939% | 0.010706 | 0.010176 | 90594.693 | 15315.6434 | 490.2766 | 74788.773 | 90604.9145 | 0 | 0 | 90604.9145 | 0.00158%
2027 | 920 | 920-823 | Tier-2 | Tier-2---11 | 4--4 | 3.3104 | 254 | 100% | 458.2189 | 68.35% | 31.14% | 0.5113% | 15.5021 | 0 | 0 | 15.5021 | 0 | 14.1067 | 3.2624 | 4.324 | 14.1067 | 3.2624 | 4.324 | 15.6545 | 3.6203 | 4.324 | 3.383% | 0.054577 | 0.051875 | 8395.8542 | 937.9397 | 2311.5146 | 5146.3999 | 8534.2572 | 0 | 0 | 8534.2572 | 0.0005112%
2027 | 518 | 518-41 | Tier-1 | Non-HFTD---19 | 1--2 | 0.051326 | 0 | 100% | 0.18129 | 60.97% | 0% | 39.03% | 0.0054716 | 0 | 0 | 0.0054716 | 0 | 0.0049791 | 0.050582 | 0.098436 | 0.0049791 | 0.050582 | 0.098436 | 0.0055254 | 0.056131 | 0.098436 | 3.018% | 0.000233 | 0.00022147 | 778.072 | 0.2285 | 501.9934 | 275.8501 | 793.8862 | 0 | 0 | 793.8862 | 1.804e-07%
2027 | 323 | 323-472AE | Tier-1 | Non-HFTD---13 | 2--2 | 2.246 | 49 | 100% | 8.3309 | 80.43% | 0% | 19.57% | 0.33167 | 0 | 0 | 0.33167 | 0 | 0.30181 | 2.2135 | 0.13635 | 0.30181 | 2.2135 | 0.13635 | 0.33493 | 2.4563 | 0.13635 | 3.981% | 0.0064722 | 0.0061518 | 1287.1873 | 162.8063 | 63.3921 | 1060.9888 | 1300.3075 | 0 | 0 | 1300.3075 | 1.094e-05%
2027 | 513 | CB 513 | Tier-1 | Non-HFTD---15 | 2--2 | 1.6305 | 55 | 100% | 4.8584 | 75.25% | 0% | 24.75% | 0.18097 | 0 | 0 | 0.18097 | 0 | 0.16468 | 1.6069 | 0.10248 | 0.16468 | 1.6069 | 0.10248 | 0.18275 | 1.7832 | 0.10248 | 3.725% | 0.005369 | 0.0051032 | 904.9068 | 3.7303 | 679.4251 | 221.7514 | 916.5709 | 0 | 0 | 916.5709 | 5.968e-06%
2027 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 7.5917 | 223 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 454.2842 | 7.4816 | 60.7201 | 454.2842 | 7.4816 | 60.7201 | 504.1272 | 8.3025 | 60.7201 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2027 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 3.4244 | 409 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 154.5381 | 3.3748 | 45.7922 | 154.5381 | 3.3748 | 45.7922 | 171.4936 | 3.745 | 45.7922 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2027 | 365 | 365-34R | Tier-1 | Non-HFTD---4 | 3--4 | 4.1672 | 256 | 100% | 103.0739 | 4.771% | 91.96% | 3.266% | 0.24342 | 0 | 0 | 0.24342 | 0 | 0.22151 | 4.1068 | 0.053938 | 0.22151 | 4.1068 | 0.053938 | 0.24582 | 4.5574 | 0.053938 | 0.2362% | 0.017802 | 0.016921 | 5789.9516 | 7.6245 | 5140.9605 | 641.3666 | 6077.094 | 0 | 0 | 6077.094 | 8.027e-06%
2027 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 1.6259 | 7 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 18.4733 | 1.6024 | 11.5287 | 18.4733 | 1.6024 | 11.5287 | 20.5002 | 1.7782 | 11.5287 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2027 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 3.5953 | 311 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 231.132 | 3.5431 | 65.2337 | 231.132 | 3.5431 | 65.2337 | 256.4912 | 3.9319 | 65.2337 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2027 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 0.60374 | 82 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 12.9796 | 0.59499 | 21.815 | 12.9796 | 0.59499 | 21.815 | 14.4037 | 0.66027 | 21.815 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2027 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | 4--5 | 3.7428 | 1032 | 100% | 2117.8574 | 97.53% | 2.33% | 0.1416% | 102.2432 | 0 | 0 | 102.2432 | 0 | 93.0399 | 3.6885 | 25.2243 | 93.0399 | 3.6885 | 25.2243 | 103.2481 | 4.0932 | 25.2243 | 4.828% | 0.067442 | 0.064104 | 31402.4615 | 4988.1224 | 677.5642 | 25736.7748 | 31442.8757 | 0 | 0 | 31442.8757 | 0.003372%
2027 | SLD1 | CB SLD1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.41002 | 165 | 100% | 0.56022 | 34.73% | 0% | 65.27% | 0.0096313 | 0 | 0 | 0.0096313 | 0 | 0.0087644 | 0.40408 | 0.02169 | 0.0087644 | 0.40408 | 0.02169 | 0.009726 | 0.44841 | 0.02169 | 1.719% | 0.001298 | 0.0012337 | 431.6022 | 16.2295 | 84.9521 | 330.4206 | 446.2726 | 0 | 0 | 446.2726 | 3.176e-07%
2027 | 741 | 741-17 | Tier-1 | Non-HFTD---17 | 1--2 | 0.36707 | 29 | 100% | 0.86307 | 47.7% | 0% | 52.3% | 0.020379 | 0 | 0 | 0.020379 | 0 | 0.018545 | 0.36174 | 0.051265 | 0.018545 | 0.36174 | 0.051265 | 0.02058 | 0.40143 | 0.051265 | 2.361% | 0.0013504 | 0.0012836 | 639.1235 | 0.34753 | 334.6341 | 304.1418 | 656.5303 | 0 | 0 | 656.5303 | 6.72e-07%
2027 | 165 | 165-35R | Tier-1 | Non-HFTD---14 | 3--1 | 5.1646 | 147 | 100% | 6.4032 | 43.37% | 0% | 56.63% | 0.13745 | 0 | 0 | 0.13745 | 0 | 0.12508 | 5.0897 | 0.024575 | 0.12508 | 5.0897 | 0.024575 | 0.1388 | 5.6482 | 0.024575 | 2.147% | 0.014379 | 0.013667 | 445.3099 | 19.5075 | 97.6943 | 328.1081 | 458.4437 | 0 | 0 | 458.4437 | 4.533e-06%
2027 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 0.63484 | 9 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.33334 | 0.62564 | 0.5328 | 0.33334 | 0.62564 | 0.5328 | 0.36991 | 0.69428 | 0.5328 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2027 | 385 | CB 385 | Tier-1 | Non-HFTD---7 | 2--3 | 3.3032 | 122 | 100% | 37.1529 | 92.67% | 0% | 7.33% | 1.7043 | 0 | 0 | 1.7043 | 0 | 1.5509 | 3.2553 | 0.47641 | 1.5509 | 3.2553 | 0.47641 | 1.721 | 3.6125 | 0.47641 | 4.587% | 0.011539 | 0.010968 | 3219.7101 | 608.925 | 454.3214 | 2156.4637 | 3231.9998 | 0 | 0 | 3231.9998 | 5.62e-05%
2027 | 377 | CB 377 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6765 | 756 | 100% | 10.2043 | 38.55% | 0% | 61.45% | 0.19472 | 0 | 0 | 0.19472 | 0 | 0.17719 | 9.5362 | 0.018581 | 0.17719 | 9.5362 | 0.018581 | 0.19663 | 10.5825 | 0.018581 | 1.908% | 0.025969 | 0.024684 | 392.9351 | 0.64012 | 170.596 | 221.699 | 405.5098 | 0 | 0 | 405.5098 | 6.421e-06%
2027 | 1081 | 1081-11 | Tier-1 | Non-HFTD---3 | 4--4 | 7.6814 | 575 | 100% | 174.6854 | 18.55% | 79% | 2.449% | 1.6041 | 0 | 0 | 1.6041 | 0 | 1.4597 | 7.5701 | 0.19282 | 1.4597 | 7.5701 | 0.19282 | 1.6198 | 8.4006 | 0.19282 | 0.9183% | 0.031395 | 0.029841 | 5564.0802 | 104.2628 | 4552.4133 | 907.4041 | 5800.0917 | 0 | 0 | 5800.0917 | 5.29e-05%
2027 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 4.9145 | 243 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 218.5784 | 4.8433 | 45.1303 | 218.5784 | 4.8433 | 45.1303 | 242.5603 | 5.3747 | 45.1303 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2027 | 462 | 462-1034F | Tier-1 | Non-HFTD---13 | 1--3 | 1.0586 | 56 | 100% | 6.6731 | 87.2% | 0% | 12.8% | 0.28803 | 0 | 0 | 0.28803 | 0 | 0.26211 | 1.0432 | 0.25125 | 0.26211 | 1.0432 | 0.25125 | 0.29086 | 1.1577 | 0.25125 | 4.316% | 0.0032472 | 0.0030865 | 2055.0169 | 223.8756 | 449.9011 | 1381.2401 | 2068.7163 | 0 | 0 | 2068.7163 | 9.498e-06%
2027 | SEA1 | SEA1-384F | Tier-1 | Non-HFTD---6 | 3--3 | 6.4007 | 656 | 100% | 54.3248 | 19.85% | 71.87% | 8.289% | 0.53366 | 0 | 0 | 0.53366 | 0 | 0.48562 | 6.3079 | 0.076986 | 0.48562 | 6.3079 | 0.076986 | 0.5389 | 7 | 0.076986 | 0.9823% | 0.028231 | 0.026833 | 1924.322 | 66.4401 | 1300.7116 | 557.1703 | 2004.6487 | 0 | 0 | 2004.6487 | 1.76e-05%
2027 | BA3 | CB BA3 | Tier-1 | Non-HFTD---14 | 3--1 | 7.1958 | 255 | 100% | 7.3804 | 35.46% | 0% | 64.54% | 0.12955 | 0 | 0 | 0.12955 | 0 | 0.11789 | 7.0915 | 0.016624 | 0.11789 | 7.0915 | 0.016624 | 0.13083 | 7.8696 | 0.016624 | 1.755% | 0.019996 | 0.019007 | 369.0877 | 1.4139 | 144.9388 | 222.735 | 381.4929 | 0 | 0 | 381.4929 | 4.272e-06%
2027 | 856 | CB 856 | Tier-1 | Non-HFTD---7 | 1--4 | 1.0902 | 50 | 100% | 37.8514 | 97.97% | 0% | 2.035% | 1.8355 | 0 | 0 | 1.8355 | 0 | 1.6703 | 1.0744 | 1.5547 | 1.6703 | 1.0744 | 1.5547 | 1.8536 | 1.1922 | 1.5547 | 4.849% | 0.0032934 | 0.0031304 | 11493.0959 | 2089.5504 | 861.3967 | 8542.1488 | 11505.2746 | 0 | 0 | 11505.2746 | 6.053e-05%
2027 | 458 | 458-41F | Tier-1 | Non-HFTD---19 | 1--1 | 0.10816 | 6 | 100% | 0.15945 | 9.171% | 0% | 90.83% | 0.00072386 | 0 | 0 | 0.00072386 | 0 | 0.0006587 | 0.10659 | 0.0061797 | 0.0006587 | 0.10659 | 0.0061797 | 0.00073097 | 0.11829 | 0.0061797 | 0.454% | 0.0004004 | 0.00038058 | 398.2281 | 0.27217 | 69.3796 | 328.5763 | 417.065 | 0 | 0 | 417.065 | 2.387e-08%
2027 | 455 | CB 455 | Tier-1 | Non-HFTD---1 | 3--5 | 7.4072 | 584 | 100% | 628.6508 | 99.14% | 0% | 0.8628% | 30.8497 | 0 | 0 | 30.8497 | 0 | 28.0728 | 7.2998 | 3.8457 | 28.0728 | 7.2998 | 3.8457 | 31.1529 | 8.1008 | 3.8457 | 4.907% | 0.025428 | 0.024169 | 24722.9716 | 4556.7235 | 179.5676 | 19986.6805 | 24734.0802 | 0 | 0 | 24734.0802 | 0.001017%
2027 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 12.4373 | 1312 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 297.7228 | 12.257 | 24.2901 | 297.7228 | 12.257 | 24.2901 | 330.3883 | 13.6018 | 24.2901 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2027 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 4.4118 | 225 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.608 | 4.3478 | 0.36983 | 1.608 | 4.3478 | 0.36983 | 1.7844 | 4.8248 | 0.36983 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2027 | 492 | 492-1091F | Tier-1 | Non-HFTD---3 | 4--3 | 5.9958 | 185 | 100% | 120.6396 | 2.917% | 93.65% | 3.431% | 0.17419 | 0 | 0 | 0.17419 | 0 | 0.15851 | 5.9089 | 0.026826 | 0.15851 | 5.9089 | 0.026826 | 0.1759 | 6.5572 | 0.026826 | 0.1444% | 0.031661 | 0.030093 | 3810.4024 | 14.7006 | 3329.9773 | 465.7245 | 4003.0516 | 0 | 0 | 4003.0516 | 5.744e-06%
2027 | 334 | 334-45F | Tier-1 | Non-HFTD---17 | 1--2 | 0.45601 | 12 | 100% | 1.6737 | 78.33% | 0% | 21.67% | 0.06489 | 0 | 0 | 0.06489 | 0 | 0.059049 | 0.4494 | 0.13139 | 0.059049 | 0.4494 | 0.13139 | 0.065528 | 0.49871 | 0.13139 | 3.877% | 0.001477 | 0.0014039 | 1133.158 | 100.5295 | 294.453 | 738.1754 | 1145.9489 | 0 | 0 | 1145.9489 | 2.14e-06%
2027 | 472 | CB 472 | Tier-1 | Non-HFTD---6 | 3--3 | 6.9083 | 465 | 100% | 66.0921 | 92.91% | 0% | 7.09% | 3.0396 | 0 | 0 | 3.0396 | 0 | 2.766 | 6.8081 | 0.40628 | 2.766 | 6.8081 | 0.40628 | 3.0695 | 7.5551 | 0.40628 | 4.599% | 0.020578 | 0.019559 | 3211.8146 | 441.0584 | 309.4932 | 2461.263 | 3223.674 | 0 | 0 | 3223.674 | 0.0001002%
2027 | 86 | 86-1055F | Tier-1 | Non-HFTD---18 | 1--1 | 1.5329 | 61 | 100% | 1.2551 | 16.29% | 0% | 83.71% | 0.010118 | 0 | 0 | 0.010118 | 0 | 0.0092072 | 1.5107 | 0.0060947 | 0.0092072 | 1.5107 | 0.0060947 | 0.010217 | 1.6765 | 0.0060947 | 0.8061% | 0.0041652 | 0.003959 | 301.3402 | 2.7068 | 56.6739 | 241.9595 | 314.4776 | 0 | 0 | 314.4776 | 3.337e-07%
2027 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 11.6815 | 1018 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 298.5256 | 11.5121 | 25.9315 | 298.5256 | 11.5121 | 25.9315 | 331.2791 | 12.7752 | 25.9315 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2027 | 741 | CB 741 | Tier-1 | Non-HFTD---15 | 1--2 | 0.84259 | 34 | 100% | 3.3752 | 76.64% | 0% | 23.36% | 0.12804 | 0 | 0 | 0.12804 | 0 | 0.11651 | 0.83037 | 0.14031 | 0.11651 | 0.83037 | 0.14031 | 0.12929 | 0.92148 | 0.14031 | 3.793% | 0.0030248 | 0.0028751 | 1115.8402 | 4.7202 | 850.5122 | 260.6077 | 1129.4176 | 0 | 0 | 1129.4176 | 4.222e-06%
2027 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 9.3687 | 606 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 558.9371 | 9.2329 | 60.5377 | 558.9371 | 9.2329 | 60.5377 | 620.2624 | 10.2459 | 60.5377 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2027 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 7.9883 | 1120 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 135.7606 | 7.8725 | 17.245 | 135.7606 | 7.8725 | 17.245 | 150.6559 | 8.7362 | 17.245 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2027 | 1161 | 1161-74 | Tier-1 | Non-HFTD---17 | 1--4 | 0.043561 | 3 | 100% | 1.4617 | 95.2% | 0% | 4.803% | 0.06888 | 0 | 0 | 0.06888 | 0 | 0.062679 | 0.042929 | 1.4601 | 0.062679 | 0.042929 | 1.4601 | 0.069557 | 0.047639 | 1.4601 | 4.712% | 0.0002106 | 0.00020018 | 6940.7274 | 1060.6781 | 30.2849 | 5849.7645 | 6958.0894 | 0 | 0 | 6958.0894 | 2.271e-06%
2027 | NO1 | NO1-289F | Tier-1 | Non-HFTD---16 | 2--1 | 2.4969 | 67 | 100% | 2.4755 | 21.95% | 0% | 78.05% | 0.026901 | 0 | 0 | 0.026901 | 0 | 0.024479 | 2.4607 | 0.0099479 | 0.024479 | 2.4607 | 0.0099479 | 0.027165 | 2.7307 | 0.0099479 | 1.087% | 0.0073078 | 0.0069461 | 338.7505 | 0.19894 | 98.3823 | 240.1693 | 352.5191 | 0 | 0 | 352.5191 | 8.871e-07%
2027 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 14.6369 | 1091 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1206.3179 | 14.4247 | 83.6288 | 1206.3179 | 14.4247 | 83.6288 | 1338.6723 | 16.0073 | 83.6288 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%
2027 | 549 | 549-33F | Tier-1 | Non-HFTD---15 | 1--3 | 0.21133 | 8 | 100% | 3.6274 | 94.05% | 0% | 5.95% | 0.16887 | 0 | 0 | 0.16887 | 0 | 0.15367 | 0.20827 | 0.73785 | 0.15367 | 0.20827 | 0.73785 | 0.17053 | 0.23112 | 0.73785 | 4.655% | 0.0007928 | 0.00075356 | 4575.3815 | 900.2459 | 28.5738 | 3646.5618 | 4589.5578 | 0 | 0 | 4589.5578 | 5.569e-06%
2027 | 236 | 236-1567R | Tier-3 | Tier-3---10 | 5--5 | 5.8553 | 557 | 100% | 5332.0037 | 98.07% | 1.841% | 0.0848% | 258.852 | 0 | 0 | 258.852 | 0 | 235.5518 | 5.7704 | 40.821 | 235.5518 | 5.7704 | 40.821 | 261.396 | 6.4035 | 40.821 | 4.855% | 0.18129 | 0.17232 | 29411.5902 | 5307.4744 | 501.4864 | 23602.6294 | 29441.0836 | 0 | 0 | 29441.0836 | 0.008536%
2027 | 430 | 430-639 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8368 | 57 | 100% | 3.1665 | 30.19% | 0% | 69.81% | 0.047328 | 0 | 0 | 0.047328 | 0 | 0.043068 | 2.7957 | 0.015405 | 0.043068 | 2.7957 | 0.015405 | 0.047793 | 3.1024 | 0.015405 | 1.495% | 0.00835 | 0.0079367 | 379.2265 | 7.9045 | 91.3742 | 279.9478 | 393.0127 | 0 | 0 | 393.0127 | 1.561e-06%
2027 | 521 | 521-1819R | Tier-2 | Tier-2---9 | 4--5 | 5.3936 | 438 | 100% | 810.9996 | 89.31% | 10.24% | 0.4457% | 35.8545 | 0 | 0 | 35.8545 | 0 | 32.6271 | 5.3154 | 6.1382 | 32.6271 | 5.3154 | 6.1382 | 36.2069 | 5.8986 | 6.1382 | 4.421% | 0.043667 | 0.041505 | 18572.4528 | 3866.096 | 1843.7459 | 12862.6109 | 18675.813 | 0 | 0 | 18675.813 | 0.001182%
2027 | 1446 | CB 1446 | Tier-1 | Non-HFTD---17 | 1--2 | 0.3625 | 5 | 100% | 1.7782 | 79.62% | 0% | 20.38% | 0.070088 | 0 | 0 | 0.070088 | 0 | 0.063779 | 0.35724 | 0.17853 | 0.063779 | 0.35724 | 0.17853 | 0.070777 | 0.39644 | 0.17853 | 3.941% | 0.0015656 | 0.0014881 | 1135.819 | 136.3299 | 64.1894 | 935.2997 | 1147.8711 | 0 | 0 | 1147.8711 | 2.311e-06%
2027 | 492 | CB 492 | Tier-1 | Non-HFTD---4 | 3--4 | 2.6833 | 129 | 100% | 147.6974 | 50.2% | 48.6% | 1.193% | 3.6704 | 0 | 0 | 3.6704 | 0 | 3.34 | 2.6444 | 1.2631 | 3.34 | 2.6444 | 1.2631 | 3.7065 | 2.9345 | 1.2631 | 2.485% | 0.022696 | 0.021573 | 6507.5812 | 522.8448 | 3980.5377 | 2004.1987 | 6676.3406 | 0 | 0 | 6676.3406 | 0.000121%
2027 | 295 | CB 295 | Tier-1 | Non-HFTD---13 | 1--3 | 0.49829 | 18 | 100% | 6.2908 | 96.1% | 0% | 3.899% | 0.29925 | 0 | 0 | 0.29925 | 0 | 0.27231 | 0.49106 | 0.55454 | 0.27231 | 0.49106 | 0.55454 | 0.30219 | 0.54494 | 0.55454 | 4.757% | 0.0015178 | 0.0014427 | 4144.6515 | 315.6182 | 2064.3478 | 1764.6855 | 4153.0684 | 0 | 0 | 4153.0684 | 9.868e-06%
2027 | 189 | 189-782F | Tier-1 | Non-HFTD---2 | 4--4 | 2.3879 | 104 | 100% | 270.4001 | 65.38% | 34.07% | 0.5513% | 8.7513 | 0 | 0 | 8.7513 | 0 | 7.9636 | 2.3533 | 3.384 | 7.9636 | 2.3533 | 3.384 | 8.8373 | 2.6115 | 3.384 | 3.236% | 0.052115 | 0.049536 | 5188.4869 | 959.5403 | 1630.2236 | 2598.723 | 5282.0256 | 0 | 0 | 5282.0256 | 0.0002886%
2027 | 230 | 230-2067 | Tier-2 | Tier-2---16 | 4--3 | 0.1678 | 13 | 100% | 121.6067 | 92.98% | 6.845% | 0.1786% | 5.5967 | 0 | 0 | 5.5967 | 0 | 5.093 | 0.16537 | 30.7974 | 5.093 | 0.16537 | 30.7974 | 5.6517 | 0.18351 | 30.7974 | 4.602% | 0.054619 | 0.051915 | 2226.4545 | 337.872 | 139.4312 | 1749.1513 | 2234.5983 | 0 | 0 | 2234.5983 | 0.0001846%
2027 | 61 | 61-21F | Tier-1 | Non-HFTD---4 | 3--4 | 1.9962 | 97 | 100% | 113.4454 | 6.678% | 92.1% | 1.219% | 0.37502 | 0 | 0 | 0.37502 | 0 | 0.34126 | 1.9673 | 0.17347 | 0.34126 | 1.9673 | 0.17347 | 0.37871 | 2.1831 | 0.17347 | 0.3306% | 0.016874 | 0.016039 | 6723.0064 | 49.7643 | 5828.0334 | 845.2086 | 7049.7441 | 0 | 0 | 7049.7441 | 1.237e-05%
2027 | 244 | CB 244 | Tier-2 | Tier-2---14 | 4--4 | 5.2595 | 161 | 100% | 295.5508 | 37.5% | 61.39% | 1.106% | 5.4867 | 0 | 0 | 5.4867 | 0 | 4.9928 | 5.1832 | 0.96327 | 4.9928 | 5.1832 | 0.96327 | 5.5406 | 5.7519 | 0.96327 | 1.856% | 0.040668 | 0.038655 | 7267.3331 | 364.4749 | 4618.5636 | 2284.2946 | 7503.8614 | 0 | 0 | 7503.8614 | 0.0001809%
2027 | 210 | CB 210 | Tier-2 | Tier-2---21 | 1--4 | 0.053788 | 0 | 100% | 1.9532 | 96.21% | 0% | 3.789% | 0.093018 | 0 | 0 | 0.093018 | 0 | 0.084645 | 0.053008 | 1.5968 | 0.084645 | 0.053008 | 1.5968 | 0.093932 | 0.058824 | 1.5968 | 4.762% | 0.0002002 | 0.00019029 | 9756.0468 | 905.9131 | 227.6493 | 8622.4844 | 9775.2983 | 0 | 0 | 9775.2983 | 3.067e-06%
2027 | 704 | CB 704 | Tier-1 | Non-HFTD---1 | 2--4 | 1.7828 | 25 | 100% | 194.5689 | 34.09% | 65.2% | 0.715% | 3.2833 | 0 | 0 | 3.2833 | 0 | 2.9877 | 1.7569 | 1.7005 | 2.9877 | 1.7569 | 1.7005 | 3.3155 | 1.9497 | 1.7005 | 1.687% | 0.012532 | 0.011912 | 15525.5161 | 542.8023 | 11295.5697 | 3687.1441 | 16058.4225 | 0 | 0 | 16058.4225 | 0.0001083%
2027 | 390 | 390-346AE | Tier-1 | Non-HFTD---3 | 5--2 | 1.9503 | 17 | 100% | 137.7692 | 30.57% | 68.57% | 0.8554% | 2.085 | 0 | 0 | 2.085 | 0 | 1.8973 | 1.9221 | 0.98712 | 1.8973 | 1.9221 | 0.98712 | 2.1055 | 2.1329 | 0.98712 | 1.513% | 0.10161 | 0.096578 | 1355.8897 | 68.0236 | 798.9805 | 488.8856 | 1404.9131 | 0 | 0 | 1404.9131 | 6.875e-05%
2027 | 972 | 972-1582R | Tier-3 | Tier-3---6 | 5--5 | 11.1523 | 379 | 100% | 8019.1792 | 98.53% | 1.384% | 0.08092% | 391.1329 | 0 | 0 | 391.1329 | 0 | 355.9256 | 10.9906 | 32.3847 | 355.9256 | 10.9906 | 32.3847 | 394.9769 | 12.1964 | 32.3847 | 4.877% | 0.15062 | 0.14317 | 53239.6467 | 8712.3531 | 675.9355 | 43851.3581 | 53280.2737 | 0 | 0 | 53280.2737 | 0.0129%
2027 | 368 | 368-21AE | Tier-1 | Non-HFTD---6 | 3--3 | 3.2028 | 121 | 100% | 50.8163 | 7.913% | 86.7% | 5.382% | 0.19904 | 0 | 0 | 0.19904 | 0 | 0.18112 | 3.1564 | 0.057383 | 0.18112 | 3.1564 | 0.057383 | 0.201 | 3.5027 | 0.057383 | 0.3917% | 0.015098 | 0.01435 | 3365.8095 | 4.0471 | 2936.2763 | 425.4862 | 3527.2237 | 0 | 0 | 3527.2237 | 6.564e-06%
2027 | 393 | CB 393 | Tier-2 | Tier-2---19 | 1--3 | 1.0951 | 18 | 100% | 8.3766 | 93.83% | 0% | 6.171% | 0.38906 | 0 | 0 | 0.38906 | 0 | 0.35404 | 1.0792 | 0.32806 | 0.35404 | 1.0792 | 0.32806 | 0.39288 | 1.1976 | 0.32806 | 4.645% | 0.0030912 | 0.0029382 | 2709.8263 | 11.6903 | 2486.8043 | 211.3317 | 2718.5348 | 0 | 0 | 2718.5348 | 1.283e-05%
2027 | 157 | 157-232R | Tier-3 | Tier-3---11 | 5--4 | 10.9006 | 366 | 100% | 3160.5079 | 95.27% | 4.501% | 0.231% | 149.0426 | 0 | 0 | 149.0426 | 0 | 135.6268 | 10.7426 | 12.6252 | 135.6268 | 10.7426 | 12.6252 | 150.5074 | 11.9212 | 12.6252 | 4.716% | 0.32167 | 0.30575 | 9825.3054 | 1334.764 | 421.9769 | 8068.5645 | 9849.5166 | 0 | 0 | 9849.5166 | 0.004915%
2027 | 545 | 545-885R | Tier-1 | Non-HFTD---7 | 2--3 | 0.51992 | 17 | 100% | 32.7256 | 0.2758% | 98.33% | 1.395% | 0.004467 | 0 | 0 | 0.004467 | 0 | 0.0040649 | 0.51238 | 0.0079334 | 0.0040649 | 0.51238 | 0.0079334 | 0.0045109 | 0.5686 | 0.0079334 | 0.01365% | 0.012213 | 0.011608 | 2679.6164 | 2.9972 | 2417.3334 | 259.2857 | 2818.7803 | 0 | 0 | 2818.7803 | 1.473e-07%
2027 | 493 | 493-480R | Tier-1 | Non-HFTD---13 | 1--4 | 0.16818 | 0 | 100% | 7.2779 | 97.57% | 0% | 2.432% | 0.3515 | 0 | 0 | 0.3515 | 0 | 0.31986 | 0.16574 | 1.9298 | 0.31986 | 0.16574 | 1.9298 | 0.35495 | 0.18393 | 1.9298 | 4.83% | 0.0008656 | 0.00082275 | 8407.9508 | 1265.6364 | 478.0477 | 6664.2667 | 8418.599 | 0 | 0 | 8418.599 | 1.159e-05%
2027 | 974 | 974-23R | Tier-3 | Tier-3---11 | 5--5 | 16.0805 | 638 | 100% | 3492.8626 | 93.69% | 6.037% | 0.2698% | 161.9921 | 0 | 0 | 161.9921 | 0 | 147.4106 | 15.8473 | 9.3019 | 147.4106 | 15.8473 | 9.3019 | 163.5841 | 17.586 | 9.3019 | 4.638% | 0.16472 | 0.15657 | 21204.8226 | 3176.6761 | 1159.8225 | 16868.324 | 21274.471 | 0 | 0 | 21274.471 | 0.005342%
2027 | 524 | 524-1782F | Tier-3 | Tier-3---10 | 4--5 | 8.5739 | 534 | 100% | 5468.1345 | 99.78% | 0.1144% | 0.1099% | 270.0655 | 0 | 0 | 270.0655 | 0 | 245.7559 | 8.4496 | 29.0851 | 245.7559 | 8.4496 | 29.0851 | 272.7197 | 9.3766 | 29.0851 | 4.939% | 0.040404 | 0.038404 | 135337.1336 | 26288.6429 | 296.748 | 108751.7427 | 135352.9439 | 0 | 0 | 135352.9439 | 0.008906%
2027 | DM1 | DM1-9R | Tier-1 | Non-HFTD---8 | 3--3 | 4.0288 | 231 | 100% | 39.7128 | 14.13% | 78.81% | 7.065% | 0.27771 | 0 | 0 | 0.27771 | 0 | 0.25271 | 3.9704 | 0.06365 | 0.25271 | 3.9704 | 0.06365 | 0.28044 | 4.406 | 0.06365 | 0.6993% | 0.022154 | 0.021057 | 1792.5792 | 37.2507 | 1380.9748 | 374.3537 | 1872.7445 | 0 | 0 | 1872.7445 | 9.158e-06%
2027 | 555 | 555-24F | Tier-1 | Non-HFTD---15 | 2--2 | 2.2983 | 36 | 100% | 4.4061 | 53.21% | 0% | 46.79% | 0.11604 | 0 | 0 | 0.11604 | 0 | 0.1056 | 2.265 | 0.046623 | 0.1056 | 2.265 | 0.046623 | 0.11719 | 2.5135 | 0.046623 | 2.634% | 0.008161 | 0.007757 | 539.893 | 26.4554 | 148.5341 | 364.9035 | 553.0495 | 0 | 0 | 553.0495 | 3.827e-06%
2027 | 194 | CB 194 | Tier-1 | Non-HFTD---7 | 3--3 | 5.9897 | 219 | 100% | 41.3648 | 90.26% | 0% | 9.742% | 1.8481 | 0 | 0 | 1.8481 | 0 | 1.6817 | 5.9029 | 0.2849 | 1.6817 | 5.9029 | 0.2849 | 1.8663 | 6.5506 | 0.2849 | 4.468% | 0.018044 | 0.017151 | 2292.4387 | 249.104 | 561.289 | 1482.0457 | 2304.0686 | 0 | 0 | 2304.0686 | 6.094e-05%
2027 | 323 | 323-1134F | Tier-1 | Non-HFTD---17 | 1--1 | 1.1165 | 113 | 100% | 1.8006 | 61.04% | 0% | 38.96% | 0.054404 | 0 | 0 | 0.054404 | 0 | 0.049507 | 1.1003 | 0.044994 | 0.049507 | 1.1003 | 0.044994 | 0.054939 | 1.221 | 0.044994 | 3.021% | 0.0037208 | 0.0035366 | 483.9282 | 45.0171 | 36.2195 | 402.6916 | 493.747 | 0 | 0 | 493.747 | 1.794e-06%
2027 | 488 | 488-32R | Tier-1 | Non-HFTD---15 | 2--1 | 2.7502 | 123 | 100% | 3.7644 | 43.12% | 0% | 56.88% | 0.080348 | 0 | 0 | 0.080348 | 0 | 0.073115 | 2.7103 | 0.026976 | 0.073115 | 2.7103 | 0.026976 | 0.081137 | 3.0077 | 0.026976 | 2.134% | 0.008362 | 0.0079481 | 450.1773 | 0.19268 | 217.3752 | 232.6094 | 463.5125 | 0 | 0 | 463.5125 | 2.65e-06%
2027 | 474 | 474-29 | Tier-1 | Non-HFTD---1 | 2--5 | 1.8853 | 277 | 100% | 1510.7302 | 99.89% | 0% | 0.1058% | 74.702 | 0 | 0 | 74.702 | 0 | 67.9778 | 1.8579 | 36.5882 | 67.9778 | 1.8579 | 36.5882 | 75.4362 | 2.0618 | 36.5882 | 4.945% | 0.010755 | 0.010222 | 140472.931 | 24566.9965 | 189.9323 | 115716.0023 | 140480.6687 | 0 | 0 | 140480.6687 | 0.002463%
2027 | 410 | CB 410 | Tier-1 | Non-HFTD---6 | 3--3 | 6.5019 | 120 | 100% | 46.5416 | 89.87% | 0% | 10.13% | 2.0704 | 0 | 0 | 2.0704 | 0 | 1.884 | 6.4076 | 0.29403 | 1.884 | 6.4076 | 0.29403 | 2.0907 | 7.1107 | 0.29403 | 4.448% | 0.019659 | 0.018686 | 2367.4198 | 207.1663 | 885.4486 | 1274.805 | 2379.9113 | 0 | 0 | 2379.9113 | 6.827e-05%
2027 | 731 | 731-49F | Tier-1 | Non-HFTD---3 | 4--3 | 16.5002 | 1184 | 100% | 102.8304 | 89.72% | 0% | 10.28% | 4.5668 | 0 | 0 | 4.5668 | 0 | 4.1557 | 16.2609 | 0.25556 | 4.1557 | 16.2609 | 0.25556 | 4.6117 | 18.0451 | 0.25556 | 4.441% | 0.046272 | 0.043982 | 2222.3019 | 294.0745 | 219.4482 | 1708.7791 | 2234.2007 | 0 | 0 | 2234.2007 | 0.0001506%
2027 | 116 | 116-31F | Tier-1 | Non-HFTD---4 | 3--4 | 2.0027 | 95 | 100% | 141.4772 | 0.3709% | 98.55% | 1.083% | 0.025973 | 0 | 0 | 0.025973 | 0 | 0.023635 | 1.9736 | 0.011975 | 0.023635 | 1.9736 | 0.011975 | 0.026228 | 2.1902 | 0.011975 | 0.01836% | 0.020781 | 0.019753 | 6807.8774 | 10.0575 | 6163.2276 | 634.5922 | 7161.1021 | 0 | 0 | 7161.1021 | 8.565e-07%
2027 | CD3 | CB CD3 | Tier-1 | Non-HFTD---18 | 1--1 | 1.6606 | 80 | 100% | 1.5668 | 26.18% | 0% | 73.82% | 0.020307 | 0 | 0 | 0.020307 | 0 | 0.018479 | 1.6365 | 0.011292 | 0.018479 | 1.6365 | 0.011292 | 0.020507 | 1.8161 | 0.011292 | 1.296% | 0.0045772 | 0.0043506 | 342.3111 | 1.0113 | 107.5472 | 233.7526 | 355.4703 | 0 | 0 | 355.4703 | 6.697e-07%
2027 | 124 | 124-258R | Tier-1 | Non-HFTD---17 | 1--2 | 0.39356 | 0 | 100% | 1.2499 | 77.42% | 0% | 22.58% | 0.047899 | 0 | 0 | 0.047899 | 0 | 0.043588 | 0.38785 | 0.11238 | 0.043588 | 0.38785 | 0.11238 | 0.04837 | 0.43041 | 0.11238 | 3.832% | 0.0013672 | 0.0012995 | 914.1789 | 6.3342 | 688.3424 | 219.5024 | 924.9284 | 0 | 0 | 924.9284 | 1.58e-06%
2027 | 519 | CB 519 | Tier-1 | Non-HFTD---11 | 2--2 | 3.4237 | 69 | 100% | 14.2981 | 79.95% | 0% | 20.05% | 0.56585 | 0 | 0 | 0.56585 | 0 | 0.51491 | 3.374 | 0.15261 | 0.51491 | 3.374 | 0.15261 | 0.57141 | 3.7442 | 0.15261 | 3.958% | 0.011118 | 0.010568 | 1286.0072 | 5.5356 | 1018.7507 | 261.721 | 1299.4354 | 0 | 0 | 1299.4354 | 1.866e-05%
2027 | 68 | 68-42 | Tier-1 | Non-HFTD---1 | 3--5 | 1.3063 | 338 | 100% | 327.449 | 81.23% | 18.46% | 0.307% | 13.1668 | 0 | 0 | 13.1668 | 0 | 11.9816 | 1.2873 | 9.3073 | 11.9816 | 1.2873 | 9.3073 | 13.2962 | 1.4286 | 9.3073 | 4.021% | 0.015736 | 0.014957 | 20808.6476 | 4091.2697 | 3467.4094 | 13249.9684 | 21012.0249 | 0 | 0 | 21012.0249 | 0.0004342%
2027 | UP1 | UP1-10 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6159 | 428 | 100% | 10.8294 | 44.21% | 0% | 55.79% | 0.23697 | 0 | 0 | 0.23697 | 0 | 0.21564 | 9.4765 | 0.022755 | 0.21564 | 9.4765 | 0.022755 | 0.2393 | 10.5163 | 0.022755 | 2.188% | 0.026285 | 0.024984 | 412.0009 | 20.5611 | 108.9901 | 282.4498 | 423.9721 | 0 | 0 | 423.9721 | 7.814e-06%
2027 | 222 | 222-1990R | Tier-3 | Tier-3---1 | 5--5 | 14.2375 | 394 | 100% | 45106.6402 | 99.63% | 0.3509% | 0.01982% | 2224.501 | 0 | 0 | 2224.501 | 0 | 2024.2656 | 14.031 | 144.2706 | 2024.2656 | 14.031 | 144.2706 | 2246.3633 | 15.5705 | 144.2706 | 4.932% | 0.41211 | 0.39171 | 109452.4885 | 17402.8472 | 400.2043 | 91649.437 | 109473.6205 | 0 | 0 | 109473.6205 | 0.07336%
2027 | EV1 | CB EV1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.3028 | 221 | 100% | 2.6461 | 17.66% | 0% | 82.34% | 0.023125 | 0 | 0 | 0.023125 | 0 | 0.021044 | 3.2549 | 0.0064651 | 0.021044 | 3.2549 | 0.0064651 | 0.023352 | 3.6121 | 0.0064651 | 0.8739% | 0.0091594 | 0.008706 | 288.895 | 0.179 | 72.6151 | 216.101 | 301.2838 | 0 | 0 | 301.2838 | 7.626e-07%
2027 | 496 | 496-21 | Tier-1 | Non-HFTD---20 | 1--1 | 0.33125 | 15 | 100% | 0.3919 | 1.941% | 0% | 98.06% | 0.00037644 | 0 | 0 | 0.00037644 | 0 | 0.00034256 | 0.32645 | 0.0010493 | 0.00034256 | 0.32645 | 0.0010493 | 0.00038014 | 0.36226 | 0.0010493 | 0.09606% | 0.0013684 | 0.0013007 | 286.3902 | 0.21132 | 31.0685 | 255.1103 | 301.0153 | 0 | 0 | 301.0153 | 1.241e-08%
2027 | 130 | CB 130 | Tier-1 | Non-HFTD---11 | 2--3 | 1.9606 | 69 | 100% | 14.2562 | 86.9% | 0% | 13.1% | 0.61324 | 0 | 0 | 0.61324 | 0 | 0.55804 | 1.9322 | 0.28882 | 0.55804 | 1.9322 | 0.28882 | 0.61927 | 2.1442 | 0.28882 | 4.302% | 0.0066204 | 0.0062927 | 2153.3693 | 1.5526 | 1888.1859 | 263.6308 | 2168.0593 | 0 | 0 | 2168.0593 | 2.022e-05%
2027 | 506 | CB 506 | Tier-1 | Non-HFTD---9 | 2--3 | 1.454 | 84 | 100% | 16.1242 | 91.65% | 0% | 8.345% | 0.73154 | 0 | 0 | 0.73154 | 0 | 0.66569 | 1.4329 | 0.46458 | 0.66569 | 1.4329 | 0.46458 | 0.73873 | 1.5901 | 0.46458 | 4.537% | 0.005379 | 0.0051127 | 2997.6192 | 25.0112 | 2618.7739 | 353.8341 | 3010.6465 | 0 | 0 | 3010.6465 | 2.412e-05%
2027 | 180 | 180-1156 | Tier-1 | Non-HFTD---17 | 1--1 | 0.91007 | 24 | 100% | 1.3219 | 52.08% | 0% | 47.92% | 0.034078 | 0 | 0 | 0.034078 | 0 | 0.031011 | 0.89688 | 0.034576 | 0.031011 | 0.89688 | 0.034576 | 0.034413 | 0.99528 | 0.034576 | 2.578% | 0.00285 | 0.0027089 | 463.8363 | 32.8306 | 62.4543 | 368.5515 | 475.4119 | 0 | 0 | 475.4119 | 1.124e-06%
2027 | DM1 | CB DM1 | Tier-1 | Non-HFTD---17 | 1--3 | 0.093371 | 9 | 100% | 1.7967 | 94.23% | 0% | 5.774% | 0.083802 | 0 | 0 | 0.083802 | 0 | 0.076259 | 0.092017 | 0.82874 | 0.076259 | 0.092017 | 0.82874 | 0.084626 | 0.10211 | 0.82874 | 4.664% | 0.000494 | 0.00046955 | 3637.0553 | 614.328 | 456.8195 | 2565.9079 | 3647.9913 | 0 | 0 | 3647.9913 | 2.763e-06%
2027 | 75 | 75-32R | Tier-3 | Tier-3---13 | 3--5 | 2.4181 | 238 | 100% | 1708.3855 | 99.57% | 0.3134% | 0.112% | 84.2054 | 0 | 0 | 84.2054 | 0 | 76.6258 | 2.3831 | 32.1542 | 76.6258 | 2.3831 | 32.1542 | 85.033 | 2.6445 | 32.1542 | 4.929% | 0.014781 | 0.01405 | 115578.2654 | 21738.9456 | 361.961 | 93477.3588 | 115603.867 | 0 | 0 | 115603.867 | 0.002777%
2027 | 497 | CB 497 | Tier-1 | Non-HFTD---4 | 2--4 | 3.432 | 133 | 100% | 116.2654 | 98.23% | 0% | 1.77% | 5.6533 | 0 | 0 | 5.6533 | 0 | 5.1444 | 3.3822 | 1.521 | 5.1444 | 3.3822 | 1.521 | 5.7088 | 3.7533 | 1.521 | 4.862% | 0.012543 | 0.011922 | 9269.494 | 1186.1414 | 3789.5424 | 4293.8102 | 9278.0371 | 0 | 0 | 9278.0371 | 0.0001864%
2027 | SL1 | CB SL1 | Tier-3 | Tier-3---11 | 5--5 | 6.6007 | 891 | 100% | 3361.5705 | 93.71% | 6.129% | 0.1568% | 155.9384 | 0 | 0 | 155.9384 | 0 | 141.9018 | 6.505 | 21.8142 | 141.9018 | 6.505 | 21.8142 | 157.4709 | 7.2187 | 21.8142 | 4.639% | 0.19527 | 0.18561 | 17214.6695 | 3012.3475 | 977.9751 | 13224.3469 | 17271.0216 | 0 | 0 | 17271.0216 | 0.005142%
2027 | GH1 | CB GH1 | Tier-1 | Non-HFTD---16 | 2--1 | 2.2529 | 134 | 100% | 2.7406 | 41.83% | 0% | 58.17% | 0.056751 | 0 | 0 | 0.056751 | 0 | 0.051642 | 2.2202 | 0.02326 | 0.051642 | 2.2202 | 0.02326 | 0.057308 | 2.4638 | 0.02326 | 2.071% | 0.0067936 | 0.0064573 | 403.4022 | 5.1571 | 159.0665 | 239.1785 | 415.6219 | 0 | 0 | 415.6219 | 1.871e-06%
2027 | RI1 | CB RI1 | Tier-1 | Non-HFTD---15 | 2--1 | 3.5895 | 135 | 100% | 4.7586 | 45.3% | 0% | 54.7% | 0.10671 | 0 | 0 | 0.10671 | 0 | 0.097108 | 3.5375 | 0.027451 | 0.097108 | 3.5375 | 0.027451 | 0.10776 | 3.9256 | 0.027451 | 2.243% | 0.010279 | 0.0097704 | 462.9377 | 10.357 | 170.4671 | 282.1136 | 476.1243 | 0 | 0 | 476.1243 | 3.519e-06%
2027 | 284 | CB 284 | Tier-1 | Non-HFTD---4 | 2--4 | 2.2045 | 412 | 100% | 126.8807 | 47.92% | 50.35% | 1.736% | 3.0095 | 0 | 0 | 3.0095 | 0 | 2.7386 | 2.1726 | 1.2605 | 2.7386 | 2.1726 | 1.2605 | 3.0391 | 2.4109 | 1.2605 | 2.372% | 0.01321 | 0.012556 | 9604.8958 | 620.4944 | 5222.3316 | 3762.0699 | 9865.4152 | 0 | 0 | 9865.4152 | 9.924e-05%
2027 | 596 | CB 596 | Tier-2 | Tier-2---14 | 2--5 | 1.4705 | 72 | 100% | 273.3297 | 99.62% | 0% | 0.3838% | 13.4779 | 0 | 0 | 13.4779 | 0 | 12.2647 | 1.4491 | 8.4635 | 12.2647 | 1.4491 | 8.4635 | 13.6104 | 1.6081 | 8.4635 | 4.931% | 0.0060594 | 0.0057595 | 45108.3697 | 6928.3062 | 2440.2235 | 35739.84 | 45117.3849 | 0 | 0 | 45117.3849 | 0.0004445%
2027 | 363 | 363-25 | Tier-1 | Non-HFTD---9 | 2--3 | 0.49474 | 5 | 100% | 16.2298 | 0.2424% | 98% | 1.754% | 0.0019477 | 0 | 0 | 0.0019477 | 0 | 0.0017724 | 0.48757 | 0.0036351 | 0.0017724 | 0.48757 | 0.0036351 | 0.0019668 | 0.54106 | 0.0036351 | 0.012% | 0.0067338 | 0.0064005 | 2410.1955 | 3.3685 | 2072.0386 | 334.7885 | 2535.409 | 0 | 0 | 2535.409 | 6.423e-08%
2027 | 279 | 279-10AE | Tier-1 | Non-HFTD---3 | 4--3 | 13.1186 | 397 | 100% | 166.5714 | 5.911% | 88.12% | 5.969% | 0.4874 | 0 | 0 | 0.4874 | 0 | 0.44353 | 12.9284 | 0.034307 | 0.44353 | 12.9284 | 0.034307 | 0.49219 | 14.3468 | 0.034307 | 0.2926% | 0.054414 | 0.051721 | 3061.1869 | 21.6691 | 2585.1276 | 454.3903 | 3211.1832 | 0 | 0 | 3211.1832 | 1.607e-05%
2027 | SSC1 | CB SSC1 | Tier-2 | Tier-2---18 | 4--3 | 5.0489 | 229 | 100% | 94.186 | 2.003% | 94.63% | 3.363% | 0.093388 | 0 | 0 | 0.093388 | 0 | 0.084982 | 4.9757 | 0.017079 | 0.084982 | 4.9757 | 0.017079 | 0.094305 | 5.5216 | 0.017079 | 0.09915% | 0.031528 | 0.029967 | 2987.3954 | 7.3065 | 2624.9969 | 355.0921 | 3139.8562 | 0 | 0 | 3139.8562 | 3.08e-06%
2027 | 1116 | CB 1116 | Tier-1 | Non-HFTD---11 | 1--4 | 0.18467 | 5 | 100% | 9.3364 | 98.6% | 0% | 1.405% | 0.45566 | 0 | 0 | 0.45566 | 0 | 0.41464 | 0.182 | 2.2783 | 0.41464 | 0.182 | 2.2783 | 0.46014 | 0.20196 | 2.2783 | 4.88% | 0.0007112 | 0.000676 | 13127.6637 | 2116.3329 | 17.0252 | 10994.3055 | 13137.2689 | 0 | 0 | 13137.2689 | 1.503e-05%
2027 | 840 | 840-374 | Tier-2 | Tier-2---13 | 4--3 | 1.3115 | 242 | 100% | 232.5563 | 96.66% | 2.796% | 0.5416% | 11.1274 | 0 | 0 | 11.1274 | 0 | 10.1258 | 1.2925 | 7.8342 | 10.1258 | 1.2925 | 7.8342 | 11.2367 | 1.4343 | 7.8342 | 4.785% | 0.064007 | 0.060838 | 3633.3054 | 565.5328 | 81.8411 | 2985.9315 | 3639.6199 | 0 | 0 | 3639.6199 | 0.0003669%
2027 | 62 | 62-22AE | Tier-1 | Non-HFTD---3 | 4--3 | 8.7206 | 747 | 100% | 149.8506 | 12.38% | 83.65% | 3.975% | 0.91818 | 0 | 0 | 0.91818 | 0 | 0.83553 | 8.5942 | 0.097221 | 0.83553 | 8.5942 | 0.097221 | 0.92721 | 9.5371 | 0.097221 | 0.6127% | 0.035713 | 0.033945 | 4195.99 | 92.2315 | 3243.5589 | 860.1996 | 4387.459 | 0 | 0 | 4387.459 | 3.028e-05%
2027 | 462 | 462-868 | Tier-1 | Non-HFTD---13 | 2--2 | 2.5009 | 25 | 100% | 8.2724 | 79.98% | 0% | 20.02% | 0.32751 | 0 | 0 | 0.32751 | 0 | 0.29803 | 2.4647 | 0.12092 | 0.29803 | 2.4647 | 0.12092 | 0.33073 | 2.7351 | 0.12092 | 3.959% | 0.0067062 | 0.0063742 | 1233.54 | 39.6864 | 767.131 | 426.7227 | 1246.3996 | 0 | 0 | 1246.3996 | 1.08e-05%
2027 | CS4 | CB CS4 | Tier-1 | Non-HFTD---14 | 3--1 | 7.3911 | 183 | 100% | 7.7232 | 38.74% | 0% | 61.26% | 0.14811 | 0 | 0 | 0.14811 | 0 | 0.13478 | 7.284 | 0.018503 | 0.13478 | 7.284 | 0.018503 | 0.14956 | 8.0832 | 0.018503 | 1.918% | 0.019993 | 0.019004 | 386.2931 | 3.2342 | 152.261 | 230.798 | 398.6167 | 0 | 0 | 398.6167 | 4.884e-06%
2027 | 214 | 214-4R | Tier-3 | Tier-3---17 | 4--4 | 3.7494 | 937 | 100% | 400.1895 | 97.86% | 1.359% | 0.7809% | 19.3854 | 0 | 0 | 19.3854 | 0 | 17.6405 | 3.6951 | 4.7741 | 17.6405 | 3.6951 | 4.7741 | 19.576 | 4.1005 | 4.7741 | 4.844% | 0.059676 | 0.056722 | 6706.0819 | 981.7315 | 85.3472 | 5639.0033 | 6713.5561 | 0 | 0 | 6713.5561 | 0.0006393%
2027 | 586 | 586-3 | Tier-1 | Non-HFTD---1 | 3--5 | 4.2473 | 442 | 100% | 516.8084 | 87.93% | 11.54% | 0.527% | 22.4945 | 0 | 0 | 22.4945 | 0 | 20.4697 | 4.1857 | 4.8904 | 20.4697 | 4.1857 | 4.8904 | 22.7156 | 4.645 | 4.8904 | 4.353% | 0.028089 | 0.026699 | 18398.9604 | 3049.2137 | 1855.4913 | 13494.2554 | 18514.6041 | 0 | 0 | 18514.6041 | 0.0007418%
2027 | 166 | 166-462F | Tier-1 | Non-HFTD---14 | 3--1 | 6.8144 | 161 | 100% | 8.466 | 45.81% | 0% | 54.19% | 0.19198 | 0 | 0 | 0.19198 | 0 | 0.17469 | 6.7156 | 0.026013 | 0.17469 | 6.7156 | 0.026013 | 0.19386 | 7.4525 | 0.026013 | 2.268% | 0.020176 | 0.019178 | 419.5983 | 1.4039 | 205.3363 | 212.8581 | 431.4397 | 0 | 0 | 431.4397 | 6.331e-06%
2027 | 235 | CB 235 | Tier-2 | Tier-2---12 | 1--5 | 0.15928 | 0 | 100% | 443.5427 | 99.96% | 0% | 0.03939% | 21.9467 | 0 | 0 | 21.9467 | 0 | 19.9712 | 0.15697 | 127.2288 | 19.9712 | 0.15697 | 127.2288 | 22.1624 | 0.17419 | 127.2288 | 4.948% | 0.0007134 | 0.00067809 | 621730.7449 | 100003.5038 | 3209.2492 | 518517.9918 | 621743.4984 | 0 | 0 | 621743.4984 | 0.0007237%
2027 | 431 | 431-478 | Tier-1 | Non-HFTD---18 | 1--1 | 1.7773 | 17 | 100% | 1.8417 | 28.24% | 0% | 71.76% | 0.025748 | 0 | 0 | 0.025748 | 0 | 0.02343 | 1.7515 | 0.013377 | 0.02343 | 1.7515 | 0.013377 | 0.026001 | 1.9437 | 0.013377 | 1.398% | 0.004891 | 0.0046489 | 376.5557 | 0.20332 | 130.8951 | 245.4573 | 390.6275 | 0 | 0 | 390.6275 | 8.491e-07%
2027 | 531 | CB 531 | Tier-1 | Non-HFTD---6 | 3--3 | 6.3466 | 124 | 100% | 47.6835 | 90.24% | 0% | 9.762% | 2.1299 | 0 | 0 | 2.1299 | 0 | 1.9382 | 6.2546 | 0.30989 | 1.9382 | 6.2546 | 0.30989 | 2.1509 | 6.9408 | 0.30989 | 4.467% | 0.021006 | 0.019967 | 2269.9514 | 122.328 | 1530.9229 | 616.7005 | 2281.4913 | 0 | 0 | 2281.4913 | 7.024e-05%
2027 | 458 | 458-33F | Tier-1 | Non-HFTD---13 | 2--2 | 1.3521 | 11 | 100% | 7.8002 | 76.69% | 0% | 23.31% | 0.29609 | 0 | 0 | 0.29609 | 0 | 0.26944 | 1.3325 | 0.20221 | 0.26944 | 1.3325 | 0.20221 | 0.299 | 1.4787 | 0.20221 | 3.796% | 0.0058714 | 0.0055808 | 1328.509 | 0.80331 | 1043.3685 | 284.3372 | 1344.6396 | 0 | 0 | 1344.6396 | 9.764e-06%
2027 | 1023 | 1023-200R | Tier-2 | Tier-2---5 | 4--5 | 3.7841 | 448 | 100% | 2889.9732 | 99.24% | 0.6691% | 0.08946% | 141.9685 | 0 | 0 | 141.9685 | 0 | 129.1894 | 3.7292 | 34.6426 | 129.1894 | 3.7292 | 34.6426 | 143.3638 | 4.1384 | 34.6426 | 4.912% | 0.083115 | 0.079 | 34770.9454 | 5602.7978 | 215.4265 | 28952.7211 | 34784.6815 | 0 | 0 | 34784.6815 | 0.004682%
2027 | 549 | 549-36F | Tier-1 | Non-HFTD---17 | 1--1 | 0.72155 | 55 | 100% | 1.2095 | 52.11% | 0% | 47.89% | 0.031196 | 0 | 0 | 0.031196 | 0 | 0.028388 | 0.71108 | 0.039922 | 0.028388 | 0.71108 | 0.039922 | 0.031502 | 0.7891 | 0.039922 | 2.579% | 0.002468 | 0.0023458 | 490.0708 | 38.9275 | 37.7198 | 413.4235 | 502.2942 | 0 | 0 | 502.2942 | 1.029e-06%
2027 | 908 | 908-2062F | Tier-2 | Tier-2---16 | 5--2 | 0.11194 | 9 | 100% | 153.3115 | 98.58% | 1.358% | 0.06577% | 7.4809 | 0 | 0 | 7.4809 | 0 | 6.8075 | 0.11032 | 61.709 | 6.8075 | 0.11032 | 61.709 | 7.5544 | 0.12242 | 61.709 | 4.88% | 0.16054 | 0.1526 | 954.9499 | 151.795 | 13.6809 | 789.4741 | 955.6578 | 0 | 0 | 955.6578 | 0.0002467%
2027 | 492 | 492-1090F | Tier-1 | Non-HFTD---8 | 3--2 | 2.9425 | 77 | 100% | 34.6286 | 4.526% | 88.49% | 6.986% | 0.077582 | 0 | 0 | 0.077582 | 0 | 0.070599 | 2.8998 | 0.024346 | 0.070599 | 2.8998 | 0.024346 | 0.078345 | 3.218 | 0.024346 | 0.224% | 0.023375 | 0.022218 | 1481.4265 | 7.0789 | 1228.0468 | 246.3007 | 1555.0841 | 0 | 0 | 1555.0841 | 2.558e-06%
2027 | 445 | 445-894R | Tier-2 | Tier-2---5 | 5--4 | 26.8775 | 335 | 100% | 4421.0024 | 88.12% | 11.51% | 0.3702% | 192.8443 | 0 | 0 | 192.8443 | 0 | 175.4857 | 26.4878 | 6.6252 | 175.4857 | 26.4878 | 6.6252 | 194.7396 | 29.3939 | 6.6252 | 4.362% | 0.63526 | 0.60381 | 6959.394 | 786.5248 | 728.3164 | 5444.5527 | 7002.446 | 0 | 0 | 7002.446 | 0.006359%
2027 | 578 | 578-227AE | Tier-1 | Non-HFTD---2 | 4--4 | 7.3342 | 376 | 100% | 226.1954 | 3.205% | 94.33% | 2.464% | 0.35882 | 0 | 0 | 0.35882 | 0 | 0.32652 | 7.2279 | 0.045176 | 0.32652 | 7.2279 | 0.045176 | 0.36235 | 8.0209 | 0.045176 | 0.1586% | 0.032265 | 0.030668 | 7010.4637 | 18.2304 | 6217.6891 | 774.5442 | 7363.8535 | 0 | 0 | 7363.8535 | 1.183e-05%
2027 | 792 | 792-46 | Tier-1 | Non-HFTD---3 | 4--3 | 5.8164 | 352 | 100% | 104.7877 | 27.86% | 68.25% | 3.891% | 1.4453 | 0 | 0 | 1.4453 | 0 | 1.3152 | 5.7321 | 0.22944 | 1.3152 | 5.7321 | 0.22944 | 1.4595 | 6.361 | 0.22944 | 1.379% | 0.033958 | 0.032277 | 3085.8225 | 12.0566 | 2731.0247 | 342.7413 | 3201.7488 | 0 | 0 | 3201.7488 | 4.766e-05%
2027 | 1406 | 1406-436 | Tier-1 | Non-HFTD---17 | 1--2 | 0.48596 | 64 | 100% | 0.81719 | 51.42% | 0% | 48.58% | 0.020799 | 0 | 0 | 0.020799 | 0 | 0.018927 | 0.47891 | 0.039521 | 0.018927 | 0.47891 | 0.039521 | 0.021004 | 0.53146 | 0.039521 | 2.545% | 0.0015042 | 0.0014297 | 543.2743 | 2.4202 | 289.5714 | 251.2826 | 557.0192 | 0 | 0 | 557.0192 | 6.859e-07%
2027 | SR4 | CB SR4 | Tier-1 | Non-HFTD---16 | 3--1 | 4.8715 | 126 | 100% | 4.8983 | 33.88% | 0% | 66.12% | 0.082138 | 0 | 0 | 0.082138 | 0 | 0.074744 | 4.8009 | 0.015569 | 0.074744 | 4.8009 | 0.015569 | 0.082945 | 5.3277 | 0.015569 | 1.677% | 0.013512 | 0.012844 | 362.5061 | 1.3132 | 137.6442 | 223.5487 | 374.9894 | 0 | 0 | 374.9894 | 2.709e-06%
2027 | 357 | 357-750R | Tier-2 | Tier-2---2 | 5--5 | 8.4165 | 681 | 100% | 11757.6254 | 97.81% | 2.143% | 0.05143% | 569.2326 | 0 | 0 | 569.2326 | 0 | 517.9939 | 8.2945 | 62.4504 | 517.9939 | 8.2945 | 62.4504 | 574.827 | 9.2045 | 62.4504 | 4.841% | 0.171 | 0.16254 | 68756.8371 | 13656.9609 | 1362.3102 | 53737.566 | 68835.4024 | 0 | 0 | 68835.4024 | 0.01877%
2027 | 239 | CB 239 | Tier-3 | Tier-3---20 | 1--5 | 0.039773 | 0 | 100% | 10.6776 | 99.64% | 0% | 0.3633% | 0.52662 | 0 | 0 | 0.52662 | 0 | 0.47922 | 0.039196 | 12.2262 | 0.47922 | 0.039196 | 12.2262 | 0.5318 | 0.043497 | 12.2262 | 4.932% | 0.0001826 | 0.00017356 | 58475.5699 | 8842.2618 | 1906.0953 | 47727.2128 | 58486.6341 | 0 | 0 | 58486.6341 | 1.737e-05%
2027 | 1090 | 1090-74F | Tier-3 | Tier-3---10 | 4--5 | 9.8927 | 660 | 100% | 4990.92 | 99.62% | 0.2191% | 0.1576% | 246.1199 | 0 | 0 | 246.1199 | 0 | 223.9657 | 9.7492 | 22.9727 | 223.9657 | 9.7492 | 22.9727 | 248.5387 | 10.8189 | 22.9727 | 4.931% | 0.045737 | 0.043473 | 109123.1086 | 21034.7206 | 297.6505 | 87790.7376 | 109144.5164 | 0 | 0 | 109144.5164 | 0.008116%
2027 | 374 | 374-708R | Tier-1 | Non-HFTD---18 | 2--1 | 1.5335 | 37 | 100% | 1.7306 | 14.21% | 0% | 85.79% | 0.012174 | 0 | 0 | 0.012174 | 0 | 0.011078 | 1.5113 | 0.0073306 | 0.011078 | 1.5113 | 0.0073306 | 0.012294 | 1.6771 | 0.0073306 | 0.7035% | 0.005207 | 0.0049493 | 332.3667 | 0.21592 | 73.1264 | 259.0243 | 347.2158 | 0 | 0 | 347.2158 | 4.015e-07%
2027 | KR1 | CB KR1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.1231 | 29 | 100% | 0.82769 | 14.7% | 0% | 85.3% | 0.0060217 | 0 | 0 | 0.0060217 | 0 | 0.0054797 | 1.1068 | 0.0049509 | 0.0054797 | 1.1068 | 0.0049509 | 0.0060809 | 1.2282 | 0.0049509 | 0.7275% | 0.0031394 | 0.002984 | 263.645 | 0.16923 | 59.1795 | 204.2962 | 275.357 | 0 | 0 | 275.357 | 1.986e-07%
2027 | 356 | 356-16R | Tier-2 | Tier-2---4 | 4--5 | 5.9928 | 318 | 100% | 5437.4375 | 98.14% | 1.781% | 0.0775% | 264.1505 | 0 | 0 | 264.1505 | 0 | 240.3733 | 5.9059 | 40.7005 | 240.3733 | 5.9059 | 40.7005 | 266.7465 | 6.5539 | 40.7005 | 4.858% | 0.090754 | 0.086262 | 59914.026 | 11488.6365 | 1202.6478 | 47222.7417 | 59972.0203 | 0 | 0 | 59972.0203 | 0.008711%
2027 | 353 | 353-594F | Tier-2 | Tier-2---7 | 5--5 | 1.221 | 97 | 100% | 2215.6498 | 99.93% | 0.02983% | 0.0378% | 109.6005 | 0 | 0 | 109.6005 | 0 | 99.735 | 1.2033 | 82.8832 | 99.735 | 1.2033 | 82.8832 | 110.6776 | 1.3353 | 82.8832 | 4.947% | 0.10216 | 0.097099 | 21688.8427 | 3516.9498 | 6.7126 | 18165.1803 | 21689.6065 | 0 | 0 | 21689.6065 | 0.003614%
2027 | 1030 | 1030-42R | Tier-3 | Tier-3---3 | 5--5 | 16.7214 | 1433 | 100% | 28398.7895 | 98.49% | 1.466% | 0.03945% | 1384.5772 | 0 | 0 | 1384.5772 | 0 | 1259.9464 | 16.4789 | 76.458 | 1259.9464 | 16.4789 | 76.458 | 1398.1847 | 18.287 | 76.458 | 4.875% | 0.28228 | 0.2683 | 100606.2475 | 17857.1529 | 1351.3594 | 81397.7352 | 100685.1242 | 0 | 0 | 100685.1242 | 0.04566%
2027 | 159 | CB 159 | Tier-1 | Non-HFTD---11 | 1--4 | 0.92049 | 19 | 100% | 13.6027 | 95.86% | 0% | 4.138% | 0.64547 | 0 | 0 | 0.64547 | 0 | 0.58737 | 0.90714 | 0.64749 | 0.58737 | 0.90714 | 0.64749 | 0.65181 | 1.0067 | 0.64749 | 4.745% | 0.002652 | 0.0025207 | 5129.2282 | 0.39825 | 4934.7904 | 194.0395 | 5140.2826 | 0 | 0 | 5140.2826 | 2.129e-05%
2027 | 52 | 52-17F | Tier-1 | Non-HFTD---17 | 1--1 | 1.5992 | 58 | 100% | 2.0098 | 43.61% | 0% | 56.39% | 0.043387 | 0 | 0 | 0.043387 | 0 | 0.039482 | 1.576 | 0.025051 | 0.039482 | 1.576 | 0.025051 | 0.043813 | 1.749 | 0.025051 | 2.159% | 0.004336 | 0.0041214 | 463.5235 | 0.19668 | 225.8901 | 237.4367 | 477.1354 | 0 | 0 | 477.1354 | 1.431e-06%
2027 | 73 | 73-678R | Tier-3 | Tier-3---5 | 5--5 | 14.1729 | 547 | 100% | 10591.3769 | 98.31% | 1.605% | 0.08417% | 515.415 | 0 | 0 | 515.415 | 0 | 469.0206 | 13.9674 | 33.5797 | 469.0206 | 13.9674 | 33.5797 | 520.4805 | 15.4999 | 33.5797 | 4.866% | 0.23776 | 0.22599 | 44546.6543 | 7354.6581 | 672.0109 | 36519.9852 | 44585.8514 | 0 | 0 | 44585.8514 | 0.017%
2027 | 445 | 445-39R | Tier-2 | Tier-2---5 | 5--4 | 8.4532 | 208 | 100% | 3678.5807 | 87.54% | 12.33% | 0.1304% | 159.4029 | 0 | 0 | 159.4029 | 0 | 145.0545 | 8.3307 | 17.4121 | 145.0545 | 8.3307 | 17.4121 | 160.9695 | 9.2447 | 17.4121 | 4.333% | 0.48997 | 0.46571 | 7507.8253 | 962.2168 | 887.8643 | 5657.7442 | 7556.5395 | 0 | 0 | 7556.5395 | 0.005257%
2027 | 221 | 221-38AE | Tier-3 | Tier-3---17 | 5--3 | 0.70208 | 149 | 100% | 318.0967 | 33.4% | 66.33% | 0.2755% | 5.2587 | 0 | 0 | 5.2587 | 0 | 4.7854 | 0.6919 | 6.9162 | 4.7854 | 0.6919 | 6.9162 | 5.3104 | 0.76782 | 6.9162 | 1.653% | 0.16917 | 0.1608 | 1880.3284 | 102.8825 | 1057.137 | 720.3088 | 1945.5476 | 0 | 0 | 1945.5476 | 0.0001734%
2027 | 44 | 44-42 | Tier-1 | Non-HFTD---15 | 1--2 | 1.3706 | 57 | 100% | 2.2519 | 52.49% | 0% | 47.51% | 0.058511 | 0 | 0 | 0.058511 | 0 | 0.053245 | 1.3507 | 0.039419 | 0.053245 | 1.3507 | 0.039419 | 0.059086 | 1.4989 | 0.039419 | 2.598% | 0.0039988 | 0.0038009 | 563.136 | 3.0245 | 302.5201 | 257.5915 | 577.0687 | 0 | 0 | 577.0687 | 1.929e-06%
2027 | WY2 | CB WY2 | Tier-1 | Non-HFTD---12 | 3--1 | 6.6059 | 241 | 100% | 9.4104 | 47.5% | 0% | 52.5% | 0.22128 | 0 | 0 | 0.22128 | 0 | 0.20136 | 6.5101 | 0.030931 | 0.20136 | 6.5101 | 0.030931 | 0.22346 | 7.2244 | 0.030931 | 2.351% | 0.019962 | 0.018974 | 471.4249 | 6.182 | 215.7177 | 249.5253 | 484.3131 | 0 | 0 | 484.3131 | 7.297e-06%
2027 | 949 | CB 949 | Tier-1 | Non-HFTD---6 | 4--2 | 14.4241 | 605 | 100% | 45.6408 | 78.87% | 0% | 21.13% | 1.7818 | 0 | 0 | 1.7818 | 0 | 1.6215 | 14.2149 | 0.11407 | 1.6215 | 14.2149 | 0.11407 | 1.7994 | 15.7745 | 0.11407 | 3.904% | 0.046257 | 0.043967 | 986.6878 | 48.1518 | 564.3079 | 374.2281 | 997.5455 | 0 | 0 | 997.5455 | 5.876e-05%
2027 | 256 | 256-539R | Tier-1 | Non-HFTD---12 | 3--2 | 6.8941 | 186 | 100% | 14.3069 | 63.6% | 0% | 36.4% | 0.45041 | 0 | 0 | 0.45041 | 0 | 0.40986 | 6.7941 | 0.060326 | 0.40986 | 6.7941 | 0.060326 | 0.45483 | 7.5396 | 0.060326 | 3.148% | 0.019872 | 0.018888 | 719.955 | 0.45811 | 479.9475 | 239.5495 | 733.603 | 0 | 0 | 733.603 | 1.485e-05%
2027 | 163 | 163-29R | Tier-1 | Non-HFTD---8 | 4--2 | 15.7299 | 388 | 100% | 28.4362 | 60.97% | 0% | 39.03% | 0.85819 | 0 | 0 | 0.85819 | 0 | 0.78094 | 15.5018 | 0.050378 | 0.78094 | 15.5018 | 0.050378 | 0.86663 | 17.2027 | 0.050378 | 3.018% | 0.04406 | 0.041879 | 645.4007 | 34.614 | 206.1861 | 404.6006 | 658.5195 | 0 | 0 | 658.5195 | 2.83e-05%
2027 | 552 | CB 552 | Tier-1 | Non-HFTD---13 | 2--2 | 2.4147 | 53 | 100% | 6.5456 | 63.72% | 0% | 36.28% | 0.20646 | 0 | 0 | 0.20646 | 0 | 0.18788 | 2.3797 | 0.078949 | 0.18788 | 2.3797 | 0.078949 | 0.20849 | 2.6408 | 0.078949 | 3.154% | 0.0083556 | 0.007942 | 783.3785 | 51.1813 | 212.1801 | 520.0172 | 798.1788 | 0 | 0 | 798.1788 | 6.808e-06%
2027 | 1215 | 1215-28R | Tier-3 | Tier-3---14 | 5--3 | 3.06 | 56 | 100% | 2215.156 | 94.69% | 5.226% | 0.08401% | 103.8279 | 0 | 0 | 103.8279 | 0 | 94.482 | 3.0156 | 31.3307 | 94.482 | 3.0156 | 31.3307 | 104.8483 | 3.3465 | 31.3307 | 4.687% | 0.66756 | 0.63451 | 3318.2974 | 455.1438 | 152.4425 | 2710.7111 | 3327.4734 | 0 | 0 | 3327.4734 | 0.003424%
2027 | 550 | CB 550 | Tier-1 | Non-HFTD---9 | 2--3 | 3.4197 | 103 | 100% | 21.1748 | 85.53% | 0% | 14.47% | 0.89644 | 0 | 0 | 0.89644 | 0 | 0.81575 | 3.3701 | 0.24205 | 0.81575 | 3.3701 | 0.24205 | 0.90525 | 3.7399 | 0.24205 | 4.234% | 0.011507 | 0.010938 | 1840.1317 | 37.2939 | 1370.6401 | 432.1977 | 1854.0024 | 0 | 0 | 1854.0024 | 2.956e-05%
2027 | 185 | CB 185 | Tier-2 | Tier-2---12 | 3--4 | 3.8089 | 316 | 100% | 396.8506 | 79.93% | 19.29% | 0.7702% | 15.7025 | 0 | 0 | 15.7025 | 0 | 14.2891 | 3.7536 | 3.8067 | 14.2891 | 3.7536 | 3.8067 | 15.8568 | 4.1655 | 3.8067 | 3.957% | 0.027797 | 0.026421 | 14276.8452 | 1950.4963 | 2483.4015 | 9842.9474 | 14426.0307 | 0 | 0 | 14426.0307 | 0.0005178%
2027 | 548 | 548-14F | Tier-1 | Non-HFTD---17 | 1--1 | 0.7748 | 32 | 100% | 0.90709 | 48.04% | 0% | 51.96% | 0.02157 | 0 | 0 | 0.02157 | 0 | 0.019628 | 0.76356 | 0.025706 | 0.019628 | 0.76356 | 0.025706 | 0.021782 | 0.84734 | 0.025706 | 2.378% | 0.0019874 | 0.001889 | 456.4228 | 1.7166 | 231.3609 | 223.3454 | 468.7738 | 0 | 0 | 468.7738 | 7.113e-07%
2027 | 793 | 793-27AE | Tier-1 | Non-HFTD---6 | 3--3 | 0.72117 | 87 | 100% | 59.5906 | 9.102% | 90.07% | 0.8316% | 0.26849 | 0 | 0 | 0.26849 | 0 | 0.24432 | 0.71072 | 0.34377 | 0.24432 | 0.71072 | 0.34377 | 0.27113 | 0.78869 | 0.34377 | 0.4506% | 0.019759 | 0.018781 | 3015.8385 | 43.8924 | 2491.6172 | 480.3289 | 3158.6011 | 0 | 0 | 3158.6011 | 8.854e-06%
2027 | 777 | 777-101 | Tier-1 | Non-HFTD---15 | 1--2 | 0.41343 | 18 | 100% | 2.4847 | 82.51% | 0% | 17.49% | 0.10148 | 0 | 0 | 0.10148 | 0 | 0.092349 | 0.40744 | 0.22666 | 0.092349 | 0.40744 | 0.22666 | 0.10248 | 0.45214 | 0.22666 | 4.084% | 0.0015556 | 0.0014786 | 1597.2368 | 209.2569 | 51.6598 | 1336.3201 | 1611.7821 | 0 | 0 | 1611.7821 | 3.347e-06%
2027 | 162 | 162-44R | Tier-1 | Non-HFTD---14 | 3--1 | 5.8971 | 114 | 100% | 6.3779 | 35.8% | 0% | 64.2% | 0.11304 | 0 | 0 | 0.11304 | 0 | 0.10286 | 5.8116 | 0.0177 | 0.10286 | 5.8116 | 0.0177 | 0.11415 | 6.4492 | 0.0177 | 1.772% | 0.016132 | 0.015333 | 395.36 | 1.0985 | 160.8009 | 233.4606 | 408.5776 | 0 | 0 | 408.5776 | 3.728e-06%
2027 | LA3 | CB LA3 | Tier-1 | Non-HFTD---10 | 4--1 | 13.6913 | 366 | 100% | 17.5547 | 51.76% | 0% | 48.24% | 0.44975 | 0 | 0 | 0.44975 | 0 | 0.40927 | 13.4928 | 0.030332 | 0.40927 | 13.4928 | 0.030332 | 0.45417 | 14.9732 | 0.030332 | 2.562% | 0.035693 | 0.033927 | 491.8203 | 13.0666 | 197.3637 | 281.39 | 504.1765 | 0 | 0 | 504.1765 | 1.483e-05%
2027 | BRM1 | CB BRM1 | Tier-1 | Non-HFTD---3 | 4--3 | 7.8361 | 151 | 100% | 119.5681 | 4.577% | 89.64% | 5.783% | 0.27092 | 0 | 0 | 0.27092 | 0 | 0.24653 | 7.7225 | 0.031924 | 0.24653 | 7.7225 | 0.031924 | 0.27358 | 8.5698 | 0.031924 | 0.2266% | 0.029242 | 0.027795 | 4088.8876 | 4.6513 | 3568.1907 | 516.0455 | 4292.0808 | 0 | 0 | 4292.0808 | 8.934e-06%
2027 | 1221 | 1221-2095F | Tier-1 | Non-HFTD---9 | 1--4 | 0.44394 | 1 | 100% | 19.6421 | 98.74% | 0% | 1.261% | 0.96002 | 0 | 0 | 0.96002 | 0 | 0.87361 | 0.4375 | 1.9968 | 0.87361 | 0.4375 | 1.9968 | 0.96946 | 0.4855 | 1.9968 | 4.888% | 0.0016714 | 0.0015887 | 11751.8616 | 4301.6259 | 14.6524 | 7435.5833 | 11759.5801 | 0 | 0 | 11759.5801 | 3.166e-05%
2027 | 73 | 73-23R | Tier-3 | Tier-3---9 | 5--5 | 8.2208 | 258 | 100% | 5733.7907 | 98.41% | 1.505% | 0.0877% | 279.3035 | 0 | 0 | 279.3035 | 0 | 254.1624 | 8.1016 | 31.3718 | 254.1624 | 8.1016 | 31.3718 | 282.0485 | 8.9905 | 31.3718 | 4.871% | 0.21349 | 0.20292 | 26857.2697 | 4453.5755 | 373.1893 | 22030.5049 | 26879.5398 | 0 | 0 | 26879.5398 | 0.00921%
2027 | 42 | 42-46 | Tier-1 | Non-HFTD---8 | 4--2 | 17.2654 | 413 | 100% | 44.005 | 69.91% | 0% | 30.09% | 1.5227 | 0 | 0 | 1.5227 | 0 | 1.3856 | 17.015 | 0.081437 | 1.3856 | 17.015 | 0.081437 | 1.5377 | 18.8819 | 0.081437 | 3.46% | 0.051941 | 0.04937 | 847.2081 | 19.5159 | 531.7286 | 295.9636 | 860.4861 | 0 | 0 | 860.4861 | 5.021e-05%
2027 | 1007 | CB 1007 | Tier-1 | Non-HFTD---4 | 1--5 | 0.54489 | 21 | 100% | 183.252 | 99.8% | 0% | 0.2013% | 9.0527 | 0 | 0 | 9.0527 | 0 | 8.2378 | 0.53699 | 15.3409 | 8.2378 | 0.53699 | 15.3409 | 9.1417 | 0.5959 | 15.3409 | 4.94% | 0.0023706 | 0.0022533 | 77301.9362 | 12237.1432 | 2369.9057 | 62694.8873 | 77310.0415 | 0 | 0 | 77310.0415 | 0.0002985%
2027 | 240 | 240-1028R | Tier-2 | Tier-2---9 | 4--5 | 5.5421 | 271 | 100% | 1181.5361 | 98.38% | 1.316% | 0.2998% | 57.5411 | 0 | 0 | 57.5411 | 0 | 52.3616 | 5.4617 | 9.587 | 52.3616 | 5.4617 | 9.587 | 58.1066 | 6.061 | 9.587 | 4.87% | 0.045174 | 0.042938 | 26155.1082 | 4733.8049 | 362.4599 | 21058.8433 | 26177.1159 | 0 | 0 | 26177.1159 | 0.001897%
2027 | 799 | CB 799 | Tier-2 | Tier-2---15 | 1--5 | 1.1328 | 62 | 100% | 176.6165 | 99.47% | 0% | 0.5321% | 8.696 | 0 | 0 | 8.696 | 0 | 7.9132 | 1.1163 | 7.0886 | 7.9132 | 1.1163 | 7.0886 | 8.7815 | 1.2388 | 7.0886 | 4.924% | 0.0045468 | 0.0043217 | 38844.142 | 6076.6634 | 1382.7609 | 31384.7178 | 38854.9056 | 0 | 0 | 38854.9056 | 0.0002868%
2027 | 1243 | 1243-319R | Tier-2 | Tier-2---9 | 4--4 | 3.321 | 126 | 100% | 1178.043 | 99.35% | 0.5195% | 0.1323% | 57.9331 | 0 | 0 | 57.9331 | 0 | 52.7183 | 3.2729 | 16.1077 | 52.7183 | 3.2729 | 16.1077 | 58.5024 | 3.632 | 16.1077 | 4.918% | 0.081051 | 0.077039 | 14534.5899 | 2255.6514 | 66.1042 | 12212.8342 | 14539.5235 | 0 | 0 | 14539.5235 | 0.00191%
2027 | 230 | 230-371AE | Tier-2 | Tier-2---13 | 4--3 | 1.4237 | 112 | 100% | 195.7251 | 81.71% | 17.81% | 0.4804% | 7.9168 | 0 | 0 | 7.9168 | 0 | 7.2041 | 1.4031 | 5.1346 | 7.2041 | 1.4031 | 5.1346 | 7.9946 | 1.557 | 5.1346 | 4.045% | 0.059006 | 0.056085 | 3317.0375 | 438.8452 | 524.5469 | 2353.6453 | 3348.6257 | 0 | 0 | 3348.6257 | 0.0002611%
2027 | 143 | 143-178F | Tier-1 | Non-HFTD---13 | 2--2 | 0.099242 | 3 | 100% | 7.6566 | 35.29% | 63.85% | 0.8587% | 0.13374 | 0 | 0 | 0.13374 | 0 | 0.1217 | 0.097803 | 1.2444 | 0.1217 | 0.097803 | 1.2444 | 0.13506 | 0.10853 | 1.2444 | 1.747% | 0.0064626 | 0.0061427 | 1184.7481 | 68.836 | 601.4916 | 514.4204 | 1224.6747 | 0 | 0 | 1224.6747 | 4.41e-06%
2027 | 167 | 167-32F | Tier-1 | Non-HFTD---17 | 1--2 | 0.70002 | 13 | 100% | 1.7157 | 69.63% | 0% | 30.37% | 0.059132 | 0 | 0 | 0.059132 | 0 | 0.05381 | 0.68987 | 0.078 | 0.05381 | 0.68987 | 0.078 | 0.059713 | 0.76556 | 0.078 | 3.447% | 0.002212 | 0.0021025 | 775.6143 | 118.1037 | 56.1784 | 601.3322 | 787.882 | 0 | 0 | 787.882 | 1.95e-06%
2027 | 558 | CB 558 | Tier-1 | Non-HFTD---5 | 1--4 | 1.6337 | 37 | 100% | 60.2724 | 98.84% | 0% | 1.159% | 2.9489 | 0 | 0 | 2.9489 | 0 | 2.6835 | 1.6101 | 1.6667 | 2.6835 | 1.6101 | 1.6667 | 2.9779 | 1.7867 | 1.6667 | 4.893% | 0.0040546 | 0.0038539 | 14865.197 | 2133.2107 | 1638.7721 | 11093.2142 | 14874.1658 | 0 | 0 | 14874.1658 | 9.724e-05%
2027 | 796 | 796-45 | Tier-1 | Non-HFTD---7 | 2--4 | 1.3418 | 200 | 100% | 28.511 | 97.42% | 0% | 2.579% | 1.3749 | 0 | 0 | 1.3749 | 0 | 1.2511 | 1.3224 | 0.94612 | 1.2511 | 1.3224 | 0.94612 | 1.3884 | 1.4675 | 0.94612 | 4.822% | 0.0051166 | 0.0048633 | 5572.2547 | 765.3252 | 756.2439 | 4050.6857 | 5579.7376 | 0 | 0 | 5579.7376 | 4.534e-05%
2027 | 152 | 152-1716F | Tier-1 | Non-HFTD---15 | 1--2 | 1.3556 | 9 | 100% | 4.2989 | 81.88% | 0% | 18.12% | 0.17424 | 0 | 0 | 0.17424 | 0 | 0.15855 | 1.336 | 0.11868 | 0.15855 | 1.336 | 0.11868 | 0.17595 | 1.4826 | 0.11868 | 4.053% | 0.0035886 | 0.003411 | 1197.9379 | 232.1636 | 50.7211 | 915.0532 | 1209.2431 | 0 | 0 | 1209.2431 | 5.746e-06%
2027 | 212 | 212-880R | Tier-2 | Tier-2---16 | 5--2 | 1.6392 | 98 | 100% | 104.9439 | 97.78% | 1.295% | 0.9224% | 5.0795 | 0 | 0 | 5.0795 | 0 | 4.6223 | 1.6154 | 2.8614 | 4.6223 | 1.6154 | 2.8614 | 5.1294 | 1.7927 | 2.8614 | 4.84% | 0.10736 | 0.10205 | 977.4994 | 110.3734 | 12.634 | 854.492 | 978.6283 | 0 | 0 | 978.6283 | 0.0001675%
2027 | 57 | 57-463AE | Tier-1 | Non-HFTD---6 | 3--3 | 5.4167 | 145 | 100% | 80.983 | 3.172% | 91.7% | 5.126% | 0.12717 | 0 | 0 | 0.12717 | 0 | 0.11573 | 5.3382 | 0.021679 | 0.11573 | 5.3382 | 0.021679 | 0.12842 | 5.9239 | 0.021679 | 0.157% | 0.026238 | 0.024939 | 3086.4535 | 4.1795 | 2701.0745 | 381.1994 | 3242.09 | 0 | 0 | 3242.09 | 4.194e-06%
2027 | 325 | 325-1229F | Tier-1 | Non-HFTD---11 | 1--3 | 1.4292 | 43 | 100% | 10.0499 | 91.61% | 0% | 8.391% | 0.45572 | 0 | 0 | 0.45572 | 0 | 0.4147 | 1.4084 | 0.29444 | 0.4147 | 1.4084 | 0.29444 | 0.4602 | 1.563 | 0.29444 | 4.535% | 0.0038216 | 0.0036324 | 2629.7498 | 120.9525 | 1901.9845 | 606.8128 | 2641.2417 | 0 | 0 | 2641.2417 | 1.503e-05%
2027 | 71 | CB 71 | Tier-1 | Non-HFTD---14 | 2--2 | 4.0099 | 46 | 100% | 7.9324 | 61.9% | 0% | 38.1% | 0.24303 | 0 | 0 | 0.24303 | 0 | 0.22116 | 3.9518 | 0.055964 | 0.22116 | 3.9518 | 0.055964 | 0.24542 | 4.3853 | 0.055964 | 3.064% | 0.012179 | 0.011576 | 651.3036 | 39.9085 | 181.853 | 429.5421 | 664.2281 | 0 | 0 | 664.2281 | 8.014e-06%
2027 | 450 | 450-114F | Tier-1 | Non-HFTD---7 | 1--4 | 0.63728 | 9 | 100% | 28.615 | 98.32% | 0% | 1.684% | 1.3926 | 0 | 0 | 1.3926 | 0 | 1.2672 | 0.62804 | 2.0177 | 1.2672 | 0.62804 | 2.0177 | 1.4063 | 0.69695 | 2.0177 | 4.867% | 0.0023436 | 0.0022276 | 12209.8338 | 1908.2658 | 365.7567 | 9935.8114 | 12220.543 | 0 | 0 | 12220.543 | 4.592e-05%
2027 | 967 | CB 967 | Tier-1 | Non-HFTD---15 | 1--2 | 0.4197 | 13 | 100% | 2.3533 | 86.82% | 0% | 13.18% | 0.10114 | 0 | 0 | 0.10114 | 0 | 0.092032 | 0.41361 | 0.22251 | 0.092032 | 0.41361 | 0.22251 | 0.10213 | 0.45899 | 0.22251 | 4.298% | 0.0017284 | 0.0016428 | 1361.5561 | 162.4621 | 165.1256 | 1033.9684 | 1370.9019 | 0 | 0 | 1370.9019 | 3.335e-06%
2027 | 570 | 570-490F | Tier-1 | Non-HFTD---9 | 2--2 | 0.62502 | 97 | 100% | 15.9869 | 5.745% | 91.56% | 2.699% | 0.045463 | 0 | 0 | 0.045463 | 0 | 0.041371 | 0.61596 | 0.067165 | 0.041371 | 0.61596 | 0.067165 | 0.04591 | 0.68354 | 0.067165 | 0.2844% | 0.009473 | 0.0090041 | 1687.6286 | 16.8664 | 1423.6306 | 247.1317 | 1770.4675 | 0 | 0 | 1770.4675 | 1.499e-06%
2027 | 177 | 177-941AE | Tier-1 | Non-HFTD---1 | 3--5 | 7.2284 | 562 | 100% | 569.5091 | 99.21% | 0% | 0.7896% | 27.9681 | 0 | 0 | 27.9681 | 0 | 25.4506 | 7.1236 | 3.5727 | 25.4506 | 7.1236 | 3.5727 | 28.243 | 7.9052 | 3.5727 | 4.911% | 0.025296 | 0.024043 | 22514.1579 | 5020.4853 | 161.6801 | 17331.9925 | 22523.4155 | 0 | 0 | 22523.4155 | 0.0009223%
2027 | 745 | CB 745 | Tier-1 | Non-HFTD---11 | 1--3 | 0.81894 | 98 | 100% | 9.4012 | 94.7% | 0% | 5.302% | 0.44069 | 0 | 0 | 0.44069 | 0 | 0.40102 | 0.80707 | 0.49688 | 0.40102 | 0.80707 | 0.49688 | 0.44502 | 0.89561 | 0.49688 | 4.688% | 0.003239 | 0.0030787 | 2902.4859 | 435.0401 | 59.2072 | 2408.2386 | 2910.4997 | 0 | 0 | 2910.4997 | 1.453e-05%
2027 | 520 | 520-1525R | Tier-2 | Tier-2---8 | 5--5 | 7.8576 | 547 | 100% | 1632.8033 | 98.29% | 1.436% | 0.2778% | 79.4388 | 0 | 0 | 79.4388 | 0 | 72.2882 | 7.7436 | 9.3352 | 72.2882 | 7.7436 | 9.3352 | 80.2195 | 8.5933 | 9.3352 | 4.865% | 0.099044 | 0.094141 | 16485.7021 | 3352.5642 | 292.1155 | 12841.0224 | 16500.4136 | 0 | 0 | 16500.4136 | 0.00262%
2027 | 972 | 972-32R | Tier-2 | Tier-2---1 | 5--5 | 15.6835 | 1007 | 100% | 22914.3284 | 97.48% | 2.478% | 0.04418% | 1105.6563 | 0 | 0 | 1105.6563 | 0 | 1006.1322 | 15.4561 | 65.0959 | 1006.1322 | 15.4561 | 65.0959 | 1116.5227 | 17.152 | 65.0959 | 4.825% | 0.16607 | 0.15785 | 137978.7753 | 23361.9707 | 3101.1924 | 111515.6122 | 138159.9776 | 0 | 0 | 138159.9776 | 0.03646%
2027 | 1458 | 1458-519 | Tier-2 | Tier-2---17 | 1--5 | 0.057008 | 0 | 100% | 81.0039 | 99.95% | 0% | 0.04716% | 4.0078 | 0 | 0 | 4.0078 | 0 | 3.647 | 0.056181 | 64.916 | 3.647 | 0.056181 | 64.916 | 4.0472 | 0.062345 | 64.916 | 4.948% | 0.000217 | 0.00020626 | 373290.0884 | 60391.7386 | 732.2515 | 312166.0983 | 373299.256 | 0 | 0 | 373299.256 | 0.0001322%
2027 | 927 | CB 927 | Tier-1 | Non-HFTD---4 | 1--5 | 0.68868 | 51 | 100% | 165.3992 | 99.66% | 0% | 0.3413% | 8.1593 | 0 | 0 | 8.1593 | 0 | 7.4249 | 0.67869 | 10.9399 | 7.4249 | 0.67869 | 10.9399 | 8.2395 | 0.75316 | 10.9399 | 4.933% | 0.0030976 | 0.0029443 | 53395.9292 | 14102.6228 | 23.0019 | 39270.3045 | 53405.4192 | 0 | 0 | 53405.4192 | 0.0002691%
2027 | 560 | CB 560 | Tier-1 | Non-HFTD---13 | 1--4 | 0.31572 | 0 | 100% | 8.2251 | 96.67% | 0% | 3.328% | 0.39359 | 0 | 0 | 0.39359 | 0 | 0.35816 | 0.31114 | 1.1511 | 0.35816 | 0.31114 | 1.1511 | 0.39746 | 0.34527 | 1.1511 | 4.785% | 0.0011202 | 0.0010648 | 7342.5228 | 1158.0205 | 22.9992 | 6161.5031 | 7355.2484 | 0 | 0 | 7355.2484 | 1.298e-05%
2027 | 282 | 282-563F | Tier-1 | Non-HFTD---8 | 4--2 | 0.30794 | 17 | 100% | 27.9436 | 22.74% | 76.55% | 0.7188% | 0.31447 | 0 | 0 | 0.31447 | 0 | 0.28617 | 0.30348 | 0.94295 | 0.28617 | 0.30348 | 0.94295 | 0.31756 | 0.33678 | 0.94295 | 1.125% | 0.031532 | 0.029971 | 886.1932 | 32.7578 | 542.1953 | 311.2401 | 921.8518 | 0 | 0 | 921.8518 | 1.037e-05%
2027 | 519 | 519-46R | Tier-1 | Non-HFTD---14 | 3--2 | 4.9682 | 201 | 100% | 7.5925 | 54.37% | 0% | 45.63% | 0.20433 | 0 | 0 | 0.20433 | 0 | 0.18593 | 4.8962 | 0.037975 | 0.18593 | 4.8962 | 0.037975 | 0.20634 | 5.4334 | 0.037975 | 2.691% | 0.013855 | 0.013169 | 548.0015 | 0.18817 | 320.6507 | 227.1626 | 561.0244 | 0 | 0 | 561.0244 | 6.738e-06%
2027 | 1479 | CB 1479 | Tier-1 | Non-HFTD---14 | 3--1 | 5.0797 | 177 | 100% | 5.3828 | 21.29% | 0% | 78.71% | 0.056714 | 0 | 0 | 0.056714 | 0 | 0.051609 | 5.0061 | 0.010309 | 0.051609 | 5.0061 | 0.010309 | 0.057271 | 5.5553 | 0.010309 | 1.054% | 0.016809 | 0.015977 | 320.2293 | 0.28102 | 90.4979 | 229.4503 | 333.3564 | 0 | 0 | 333.3564 | 1.87e-06%
2027 | 157 | CB 157 | Tier-3 | Tier-3---21 | 1--5 | 0.027841 | 0 | 100% | 6.0775 | 99.43% | 0% | 0.5677% | 0.29913 | 0 | 0 | 0.29913 | 0 | 0.2722 | 0.027437 | 9.9209 | 0.2722 | 0.027437 | 9.9209 | 0.30207 | 0.030448 | 9.9209 | 4.922% | 0.0001334 | 0.0001268 | 45558.1567 | 6595.3961 | 1202.8975 | 37759.8631 | 45571.6265 | 0 | 0 | 45571.6265 | 9.864e-06%
2027 | 93 | 93-559R | Tier-1 | Non-HFTD---2 | 3--4 | 6.9136 | 643 | 100% | 194.9296 | 89.74% | 7.915% | 2.344% | 8.6591 | 0 | 0 | 8.6591 | 0 | 7.8797 | 6.8134 | 1.1565 | 7.8797 | 6.8134 | 1.1565 | 8.7442 | 7.561 | 1.1565 | 4.442% | 0.02667 | 0.02535 | 7308.8898 | 1504.7135 | 606.7669 | 5197.4095 | 7347.9399 | 0 | 0 | 7347.9399 | 0.0002855%
2027 | 387 | 387-11 | Tier-2 | Tier-2---7 | 4--5 | 13.7926 | 900 | 100% | 2227.2808 | 89.28% | 10.33% | 0.3978% | 98.4272 | 0 | 0 | 98.4272 | 0 | 89.5674 | 13.5926 | 6.5894 | 89.5674 | 13.5926 | 6.5894 | 99.3945 | 15.084 | 6.5894 | 4.419% | 0.091496 | 0.086967 | 24342.9313 | 4926.9601 | 2390.2403 | 17025.731 | 24478.8821 | 0 | 0 | 24478.8821 | 0.003246%
2027 | 307 | CB 307 | Tier-1 | Non-HFTD---1 | 4--4 | 1.1522 | 360 | 100% | 601.8674 | 89.73% | 10.15% | 0.1197% | 26.7338 | 0 | 0 | 26.7338 | 0 | 24.3274 | 1.1355 | 21.4238 | 24.3274 | 1.1355 | 21.4238 | 26.9966 | 1.2601 | 21.4238 | 4.442% | 0.056404 | 0.053612 | 10670.688 | 1554.5631 | 980.4133 | 8135.7116 | 10727.7391 | 0 | 0 | 10727.7391 | 0.0008816%
2027 | 185 | 185-40AE | Tier-1 | Non-HFTD---9 | 3--2 | 0.21023 | 6 | 100% | 24.1775 | 44.9% | 54.65% | 0.4525% | 0.53732 | 0 | 0 | 0.53732 | 0 | 0.48896 | 0.20718 | 2.3601 | 0.48896 | 0.20718 | 2.3601 | 0.54261 | 0.22991 | 2.3601 | 2.222% | 0.014972 | 0.014231 | 1614.8054 | 161.7474 | 706.6761 | 746.3819 | 1661.1444 | 0 | 0 | 1661.1444 | 1.772e-05%
2027 | 1297 | CB 1297 | Tier-1 | Non-HFTD---13 | 2--2 | 0.36516 | 2 | 100% | 8.4009 | 39.85% | 56.35% | 3.796% | 0.16572 | 0 | 0 | 0.16572 | 0 | 0.15081 | 0.35987 | 0.41906 | 0.15081 | 0.35987 | 0.41906 | 0.16735 | 0.39935 | 0.41906 | 1.973% | 0.0061708 | 0.0058653 | 1361.4021 | 0.82568 | 1230.5774 | 129.999 | 1404.0463 | 0 | 0 | 1404.0463 | 5.465e-06%
2027 | 719 | 719-20AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.2593 | 0 | 100% | 0.25643 | 2.302% | 0% | 97.7% | 0.00029221 | 0 | 0 | 0.00029221 | 0 | 0.00026591 | 0.25554 | 0.0010406 | 0.00026591 | 0.25554 | 0.0010406 | 0.00029508 | 0.28358 | 0.0010406 | 0.114% | 0.0008862 | 0.00084233 | 289.3554 | 0.21272 | 32.3414 | 256.8012 | 304.0775 | 0 | 0 | 304.0775 | 9.636e-09%
2027 | 211 | CB 211 | Tier-2 | Tier-2---21 | 1--2 | 0.010606 | 0 | 100% | 0.037273 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.010452 | 0 | 0 | 0.010452 | 0 | 0 | 0.011599 | 0 | 0% | 5.02e-05 | 4.7715e-05 | 742.4998 | 0.55871 | 67.4492 | 674.4919 | 781.1676 | 0 | 0 | 781.1676 | 0%
2027 | 313 | 313-921F | Tier-1 | Non-HFTD---10 | 3--2 | 0.32122 | 1 | 100% | 17.8162 | 19.43% | 79.61% | 0.9597% | 0.17138 | 0 | 0 | 0.17138 | 0 | 0.15596 | 0.31656 | 0.49266 | 0.15596 | 0.31656 | 0.49266 | 0.17307 | 0.35129 | 0.49266 | 0.962% | 0.018006 | 0.017115 | 989.4465 | 32.4943 | 625.1022 | 331.85 | 1030.9611 | 0 | 0 | 1030.9611 | 5.652e-06%
2027 | 299 | 299-1010AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.44586 | 28 | 100% | 0.3009 | 15.95% | 0% | 84.05% | 0.0023758 | 0 | 0 | 0.0023758 | 0 | 0.002162 | 0.4394 | 0.0049203 | 0.002162 | 0.4394 | 0.0049203 | 0.0023992 | 0.48761 | 0.0049203 | 0.7896% | 0.001182 | 0.0011235 | 254.5679 | 0.31338 | 59.1142 | 195.1403 | 265.7105 | 0 | 0 | 265.7105 | 7.835e-08%
2027 | 313 | 313-550AE | Tier-1 | Non-HFTD---6 | 3--3 | 1.3333 | 153 | 100% | 63.0293 | 35.2% | 63.19% | 1.611% | 1.0982 | 0 | 0 | 1.0982 | 0 | 0.99937 | 1.314 | 0.76056 | 0.99937 | 1.314 | 0.76056 | 1.109 | 1.4582 | 0.76056 | 1.742% | 0.021034 | 0.019993 | 2996.5143 | 172.626 | 1569.8934 | 1253.9949 | 3097.636 | 0 | 0 | 3097.636 | 3.622e-05%
2027 | 546 | 546-525R | Tier-1 | Non-HFTD---6 | 3--3 | 3.3962 | 95 | 100% | 53.674 | 7.451% | 89.14% | 3.414% | 0.19796 | 0 | 0 | 0.19796 | 0 | 0.18014 | 3.347 | 0.053821 | 0.18014 | 3.347 | 0.053821 | 0.1999 | 3.7142 | 0.053821 | 0.3688% | 0.018842 | 0.01791 | 2848.5751 | 3.4959 | 2541.3825 | 303.6966 | 2985.8697 | 0 | 0 | 2985.8697 | 6.528e-06%
2027 | 152 | 152-513AE | Tier-1 | Non-HFTD---12 | 3--2 | 7.8357 | 74 | 100% | 12.0345 | 69.29% | 0% | 30.71% | 0.41277 | 0 | 0 | 0.41277 | 0 | 0.37562 | 7.722 | 0.048642 | 0.37562 | 7.722 | 0.048642 | 0.41683 | 8.5693 | 0.048642 | 3.43% | 0.019541 | 0.018574 | 615.8514 | 13.6547 | 361.2301 | 240.9665 | 625.7005 | 0 | 0 | 625.7005 | 1.361e-05%
2027 | 66 | CB 66 | Tier-1 | Non-HFTD---1 | 4--5 | 7.6461 | 1197 | 100% | 917.8674 | 93.46% | 5.958% | 0.5799% | 42.4641 | 0 | 0 | 42.4641 | 0 | 38.6418 | 7.5352 | 5.1282 | 38.6418 | 7.5352 | 5.1282 | 42.8815 | 8.362 | 5.1282 | 4.626% | 0.036366 | 0.034566 | 25239.7123 | 4508.1978 | 1664.2037 | 19067.3107 | 25325.6439 | 0 | 0 | 25325.6439 | 0.0014%
2027 | 748 | CB 748 | Tier-1 | Non-HFTD---9 | 2--3 | 2.139 | 70 | 100% | 22.3424 | 93.96% | 0% | 6.041% | 1.0391 | 0 | 0 | 1.0391 | 0 | 0.94561 | 2.108 | 0.44857 | 0.94561 | 2.108 | 0.44857 | 1.0494 | 2.3393 | 0.44857 | 4.651% | 0.0077366 | 0.0073536 | 2887.8899 | 430.152 | 52.4027 | 2405.3352 | 2896.9749 | 0 | 0 | 2896.9749 | 3.427e-05%
2027 | 591 | 591-39AE | Tier-1 | Non-HFTD---1 | 4--4 | 8.7941 | 609 | 100% | 863.6817 | 30.54% | 68.77% | 0.684% | 13.0582 | 0 | 0 | 13.0582 | 0 | 11.8828 | 8.6666 | 1.3711 | 11.8828 | 8.6666 | 1.3711 | 13.1866 | 9.6175 | 1.3711 | 1.512% | 0.061092 | 0.058068 | 14137.3023 | 873.1637 | 8965.9062 | 4298.2324 | 14648.6655 | 0 | 0 | 14648.6655 | 0.0004306%
2027 | 130 | 130-692R | Tier-1 | Non-HFTD---8 | 4--2 | 9.1392 | 120 | 100% | 38.8551 | 79.61% | 0% | 20.39% | 1.5312 | 0 | 0 | 1.5312 | 0 | 1.3934 | 9.0067 | 0.15471 | 1.3934 | 9.0067 | 0.15471 | 1.5463 | 9.9949 | 0.15471 | 3.941% | 0.029616 | 0.02815 | 1311.9621 | 5.802 | 1040.3906 | 265.7695 | 1325.8909 | 0 | 0 | 1325.8909 | 5.049e-05%
2027 | 217 | 217-835R | Tier-3 | Tier-3---5 | 5--5 | 18.3176 | 1062 | 100% | 10686.9326 | 98.68% | 1.222% | 0.09479% | 522.0384 | 0 | 0 | 522.0384 | 0 | 475.0478 | 18.052 | 26.3155 | 475.0478 | 18.052 | 26.3155 | 527.1689 | 20.0326 | 26.3155 | 4.885% | 0.28412 | 0.27006 | 37613.7803 | 6234.338 | 401.1019 | 30978.3405 | 37639.5702 | 0 | 0 | 37639.5702 | 0.01721%
2027 | 212 | 212-1177R | Tier-2 | Tier-2---8 | 5--4 | 12.4913 | 405 | 100% | 1738.9252 | 95.43% | 4.096% | 0.4776% | 82.1402 | 0 | 0 | 82.1402 | 0 | 74.7465 | 12.3102 | 6.0719 | 74.7465 | 12.3102 | 6.0719 | 82.9475 | 13.6608 | 6.0719 | 4.724% | 0.15054 | 0.14309 | 11551.4959 | 1436.1291 | 504.7372 | 9610.6296 | 11579.0081 | 0 | 0 | 11579.0081 | 0.002709%
2027 | 75 | CB 75 | Tier-3 | Tier-3---21 | 1--4 | 0.14545 | 0 | 100% | 4.1734 | 97.63% | 0% | 2.371% | 0.20169 | 0 | 0 | 0.20169 | 0 | 0.18353 | 0.14335 | 1.2803 | 0.18353 | 0.14335 | 1.2803 | 0.20367 | 0.15907 | 1.2803 | 4.833% | 0.0006394 | 0.00060775 | 6527.0943 | 953.8716 | 494.2061 | 5079.0166 | 6535.1527 | 0 | 0 | 6535.1527 | 6.651e-06%
2027 | 496 | CB 496 | Tier-1 | Non-HFTD---20 | 1--1 | 0.23769 | 14 | 100% | 0.1626 | 10.49% | 0% | 89.51% | 0.00084466 | 0 | 0 | 0.00084466 | 0 | 0.00076863 | 0.23424 | 0.0032814 | 0.00076863 | 0.23424 | 0.0032814 | 0.00085296 | 0.25994 | 0.0032814 | 0.5195% | 0.0006016 | 0.00057182 | 270.2755 | 0.18203 | 50.3395 | 219.754 | 282.8737 | 0 | 0 | 282.8737 | 2.785e-08%
2027 | 505 | 505-635R | Tier-1 | Non-HFTD---2 | 4--4 | 22.8048 | 2172 | 100% | 591.8183 | 97.36% | 0% | 2.639% | 28.5218 | 0 | 0 | 28.5218 | 0 | 25.9544 | 22.4741 | 1.1549 | 25.9544 | 22.4741 | 1.1549 | 28.8021 | 24.9399 | 1.1549 | 4.819% | 0.06847 | 0.06508 | 8643.5194 | 1351.8242 | 175.5172 | 7116.178 | 8655.4003 | 0 | 0 | 8655.4003 | 0.0009405%
2027 | 835 | CB 835 | Tier-2 | Tier-2---17 | 1--5 | 0.49168 | 174 | 100% | 42.6475 | 99.43% | 0% | 0.5747% | 2.0989 | 0 | 0 | 2.0989 | 0 | 1.91 | 0.48455 | 3.9418 | 1.91 | 0.48455 | 3.9418 | 2.1195 | 0.53771 | 3.9418 | 4.922% | 0.0017112 | 0.0016265 | 24922.574 | 5223.7878 | 17.636 | 19681.1502 | 24930.0337 | 0 | 0 | 24930.0337 | 6.921e-05%
2027 | RD4 | RD4-49F | Tier-1 | Non-HFTD---16 | 2--1 | 3.5175 | 271 | 100% | 3.6354 | 25.76% | 0% | 74.24% | 0.046356 | 0 | 0 | 0.046356 | 0 | 0.042184 | 3.4665 | 0.012169 | 0.042184 | 3.4665 | 0.012169 | 0.046812 | 3.8468 | 0.012169 | 1.275% | 0.010063 | 0.0095647 | 361.2667 | 2.1724 | 105.3352 | 253.7591 | 375.2341 | 0 | 0 | 375.2341 | 1.529e-06%
2027 | 185 | 185-52F | Tier-1 | Non-HFTD---18 | 3--1 | 0.068182 | 8 | 100% | 1.9986 | 0.2921% | 96.1% | 3.61% | 0.00028895 | 0 | 0 | 0.00028895 | 0 | 0.00026294 | 0.067193 | 0.0039132 | 0.00026294 | 0.067193 | 0.0039132 | 0.00029179 | 0.074566 | 0.0039132 | 0.01446% | 0.014577 | 0.013855 | 137.1083 | 0.56754 | 106.8603 | 29.6805 | 144.2278 | 0 | 0 | 144.2278 | 9.528e-09%
2027 | 77 | CB 77 | Tier-1 | Non-HFTD---3 | 4--3 | 15.8875 | 767 | 100% | 119.7495 | 90.14% | 0% | 9.861% | 5.3431 | 0 | 0 | 5.3431 | 0 | 4.8621 | 15.6571 | 0.31054 | 4.8621 | 15.6571 | 0.31054 | 5.3956 | 17.375 | 0.31054 | 4.462% | 0.052353 | 0.049762 | 2287.3297 | 348.85 | 338.2815 | 1600.1982 | 2299.0765 | 0 | 0 | 2299.0765 | 0.0001762%
2027 | 719 | 719-21AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.2376 | 46 | 100% | 2.7569 | 40.49% | 0% | 59.51% | 0.055252 | 0 | 0 | 0.055252 | 0 | 0.050278 | 2.2052 | 0.0228 | 0.050278 | 2.2052 | 0.0228 | 0.055795 | 2.4472 | 0.0228 | 2.004% | 0.006419 | 0.0061013 | 429.4974 | 0.19234 | 197.1085 | 232.1966 | 442.809 | 0 | 0 | 442.809 | 1.822e-06%
2027 | 512 | 512-50AE | Tier-1 | Non-HFTD---5 | 3--3 | 2.2912 | 159 | 100% | 71.8244 | 0.7571% | 97.4% | 1.847% | 0.026916 | 0 | 0 | 0.026916 | 0 | 0.024494 | 2.258 | 0.010847 | 0.024494 | 2.258 | 0.010847 | 0.027181 | 2.5058 | 0.010847 | 0.03748% | 0.016424 | 0.015611 | 4373.1911 | 5.2566 | 3808.805 | 559.1295 | 4599.2133 | 0 | 0 | 4599.2133 | 8.876e-07%
2027 | 144 | 144-29 | Tier-1 | Non-HFTD---11 | 2--3 | 0.17619 | 16 | 100% | 11.682 | 0.1742% | 98.33% | 1.496% | 0.0010071 | 0 | 0 | 0.0010071 | 0 | 0.00091646 | 0.17363 | 0.0052782 | 0.00091646 | 0.17363 | 0.0052782 | 0.001017 | 0.19268 | 0.0052782 | 0.008621% | 0.0067282 | 0.0063952 | 1736.2798 | 2.3848 | 1561.9921 | 171.903 | 1826.5441 | 0 | 0 | 1826.5441 | 3.321e-08%
2027 | 81 | CB 81 | Tier-1 | Non-HFTD---10 | 3--2 | 6.9752 | 310 | 100% | 21.9247 | 77.75% | 0% | 22.25% | 0.84377 | 0 | 0 | 0.84377 | 0 | 0.76782 | 6.874 | 0.1117 | 0.76782 | 6.874 | 0.1117 | 0.85206 | 7.6282 | 0.1117 | 3.848% | 0.01895 | 0.018012 | 1156.9885 | 0.24003 | 922.628 | 234.1205 | 1170.3967 | 0 | 0 | 1170.3967 | 2.782e-05%
2027 | CCB1 | CB CCB1 | Tier-1 | Non-HFTD---17 | 1--3 | 0.10833 | 0 | 100% | 2.0968 | 95.25% | 0% | 4.748% | 0.098863 | 0 | 0 | 0.098863 | 0 | 0.089964 | 0.10676 | 0.84266 | 0.089964 | 0.10676 | 0.84266 | 0.099835 | 0.11848 | 0.84266 | 4.715% | 0.0004866 | 0.00046251 | 4309.0626 | 662.563 | 60.6472 | 3585.8524 | 4319.7167 | 0 | 0 | 4319.7167 | 3.26e-06%
2027 | 714 | 714-549F | Tier-1 | Non-HFTD---5 | 2--4 | 1.7489 | 77 | 100% | 53.2751 | 98.07% | 0% | 1.933% | 2.5861 | 0 | 0 | 2.5861 | 0 | 2.3534 | 1.7235 | 1.3654 | 2.3534 | 1.7235 | 1.3654 | 2.6116 | 1.9126 | 1.3654 | 4.854% | 0.0067848 | 0.006449 | 7852.121 | 1591.0401 | 27.5154 | 6233.5655 | 7860.0249 | 0 | 0 | 7860.0249 | 8.528e-05%
2027 | 907 | 907-1562AE | Tier-3 | Tier-3---6 | 4--5 | 4.1122 | 459 | 100% | 8439.7692 | 97.62% | 2.35% | 0.03436% | 407.8089 | 0 | 0 | 407.8089 | 0 | 371.1005 | 4.0525 | 91.5725 | 371.1005 | 4.0525 | 91.5725 | 411.8168 | 4.4972 | 91.5725 | 4.832% | 0.054867 | 0.052151 | 153823.4412 | 28255.722 | 3280.1961 | 122287.5231 | 154014.4199 | 0 | 0 | 154014.4199 | 0.01345%
2027 | 492 | 492-343R | Tier-1 | Non-HFTD---1 | 3--4 | 3.0856 | 96 | 100% | 272.4272 | 37.19% | 62.03% | 0.7764% | 5.0152 | 0 | 0 | 5.0152 | 0 | 4.5638 | 3.0409 | 1.5008 | 4.5638 | 3.0409 | 1.5008 | 5.0645 | 3.3745 | 1.5008 | 1.841% | 0.024839 | 0.02361 | 10967.6322 | 612.0765 | 6977.3835 | 3378.1722 | 11326.3811 | 0 | 0 | 11326.3811 | 0.0001654%
2027 | 1173 | 1173-69 | Tier-1 | Non-HFTD---20 | 1--1 | 0.44187 | 41 | 100% | 0.23868 | 12.02% | 0% | 87.98% | 0.0014207 | 0 | 0 | 0.0014207 | 0 | 0.0012928 | 0.43546 | 0.0029688 | 0.0012928 | 0.43546 | 0.0029688 | 0.0014347 | 0.48324 | 0.0029688 | 0.5952% | 0.000946 | 0.00089917 | 252.3094 | 0.16703 | 50.503 | 201.6393 | 263.8692 | 0 | 0 | 263.8692 | 4.685e-08%
2027 | LR1 | CB LR1 | Tier-1 | Non-HFTD---3 | 4--3 | 12.453 | 567 | 100% | 104.9912 | 92.12% | 0% | 7.878% | 4.7876 | 0 | 0 | 4.7876 | 0 | 4.3567 | 12.2725 | 0.35499 | 4.3567 | 12.2725 | 0.35499 | 4.8347 | 13.619 | 0.35499 | 4.56% | 0.036685 | 0.034869 | 2861.9797 | 416.4048 | 112.8622 | 2332.7126 | 2873.7222 | 0 | 0 | 2873.7222 | 0.0001579%
2027 | 790 | CB 790 | Tier-2 | Tier-2---10 | 4--4 | 1.346 | 112 | 100% | 864.253 | 62.67% | 37.21% | 0.1185% | 26.812 | 0 | 0 | 26.812 | 0 | 24.3986 | 1.3265 | 18.3932 | 24.3986 | 1.3265 | 18.3932 | 27.0755 | 1.472 | 18.3932 | 3.102% | 0.092624 | 0.088039 | 9330.8076 | 1033.7577 | 3102.9179 | 5194.132 | 9512.1882 | 0 | 0 | 9512.1882 | 0.0008842%
2027 | 1049 | 1049-3F | Tier-1 | Non-HFTD---12 | 3--1 | 7.1382 | 182 | 100% | 8.8963 | 41.1% | 0% | 58.9% | 0.18101 | 0 | 0 | 0.18101 | 0 | 0.16471 | 7.0347 | 0.023414 | 0.16471 | 7.0347 | 0.023414 | 0.18278 | 7.8066 | 0.023414 | 2.035% | 0.019998 | 0.019008 | 444.8634 | 18.6046 | 93.9565 | 332.3023 | 458.5083 | 0 | 0 | 458.5083 | 5.969e-06%
2027 | 79 | 79-1215F | Tier-3 | Tier-3---18 | 5--3 | 0.2301 | 18 | 100% | 324.1263 | 99.58% | 0.3619% | 0.05404% | 15.9775 | 0 | 0 | 15.9775 | 0 | 14.5393 | 0.22676 | 64.117 | 14.5393 | 0.22676 | 64.117 | 16.1345 | 0.25164 | 64.117 | 4.929% | 0.1831 | 0.17404 | 1770.1913 | 278.679 | 8.5105 | 1483.0017 | 1770.5747 | 0 | 0 | 1770.5747 | 0.0005269%
2027 | 222 | 222-1523R | Tier-3 | Tier-3---7 | 5--5 | 12.4352 | 2333 | 100% | 7406.689 | 96.62% | 3.25% | 0.1263% | 354.2524 | 0 | 0 | 354.2524 | 0 | 322.3648 | 12.2549 | 26.3049 | 322.3648 | 12.2549 | 26.3049 | 357.7339 | 13.5995 | 26.3049 | 4.783% | 0.26901 | 0.25569 | 27533.3002 | 4015.4723 | 832.0956 | 22685.7323 | 27581.7128 | 0 | 0 | 27581.7128 | 0.01168%
2027 | 966 | CB 966 | Tier-1 | Non-HFTD---17 | 1--2 | 0.25966 | 0 | 100% | 1.248 | 85.91% | 0% | 14.09% | 0.053072 | 0 | 0 | 0.053072 | 0 | 0.048295 | 0.25589 | 0.18873 | 0.048295 | 0.25589 | 0.18873 | 0.053594 | 0.28397 | 0.18873 | 4.253% | 0.001115 | 0.0010598 | 1119.2714 | 148.4379 | 21.0289 | 949.8046 | 1127.4836 | 0 | 0 | 1127.4836 | 1.75e-06%
2027 | MAG1 | CB MAG1 | Tier-1 | Non-HFTD---8 | 5--1 | 0.88881 | 25 | 100% | 27.4341 | 1.826% | 95.93% | 2.248% | 0.024802 | 0 | 0 | 0.024802 | 0 | 0.022569 | 0.87592 | 0.025766 | 0.022569 | 0.87592 | 0.025766 | 0.025046 | 0.97202 | 0.025766 | 0.09041% | 0.095165 | 0.090455 | 288.2778 | 1.1724 | 249.3442 | 37.7612 | 303.0165 | 0 | 0 | 303.0165 | 8.179e-07%
2027 | 908 | 908-1172R | Tier-2 | Tier-2---2 | 5--5 | 10.1766 | 1359 | 100% | 15766.5188 | 98.33% | 1.627% | 0.04735% | 767.3776 | 0 | 0 | 767.3776 | 0 | 698.3032 | 10.029 | 69.6283 | 698.3032 | 10.029 | 69.6283 | 774.9194 | 11.1294 | 69.6283 | 4.867% | 0.20692 | 0.19668 | 76195.3215 | 14303.1214 | 1151.1077 | 60741.0923 | 76261.7497 | 0 | 0 | 76261.7497 | 0.02531%
2027 | 490 | 490-23 | Tier-1 | Non-HFTD---15 | 1--4 | 0.21625 | 28 | 100% | 4.2948 | 96.52% | 0% | 3.476% | 0.2052 | 0 | 0 | 0.2052 | 0 | 0.18673 | 0.21311 | 0.8762 | 0.18673 | 0.21311 | 0.8762 | 0.20722 | 0.2365 | 0.8762 | 4.778% | 0.0007132 | 0.0006779 | 6021.8257 | 949.5603 | 22.0761 | 5050.1893 | 6032.728 | 0 | 0 | 6032.728 | 6.767e-06%
2027 | 907 | 907-1604 | Tier-3 | Tier-3---19 | 3--2 | 0.01875 | 0 | 100% | 17.8439 | 83.33% | 16.48% | 0.1969% | 0.73601 | 0 | 0 | 0.73601 | 0 | 0.66976 | 0.018478 | 36.2458 | 0.66976 | 0.018478 | 36.2458 | 0.74324 | 0.020506 | 36.2458 | 4.125% | 0.017739 | 0.016861 | 1005.9134 | 134.52 | 136.2349 | 735.1585 | 1014.6476 | 0 | 0 | 1014.6476 | 2.427e-05%
2027 | HC3 | CB HC3 | Tier-1 | Non-HFTD---10 | 4--2 | 12.0409 | 546 | 100% | 24.3902 | 66.04% | 0% | 33.96% | 0.79725 | 0 | 0 | 0.79725 | 0 | 0.72549 | 11.8663 | 0.061139 | 0.72549 | 11.8663 | 0.061139 | 0.80509 | 13.1682 | 0.061139 | 3.269% | 0.035828 | 0.034054 | 680.7657 | 68.4975 | 157.3177 | 454.9505 | 692.8072 | 0 | 0 | 692.8072 | 2.629e-05%
2027 | 362 | 362-47F | Tier-1 | Non-HFTD---3 | 4--3 | 14.5108 | 539 | 100% | 174.2726 | 36.5% | 57.41% | 6.096% | 3.1484 | 0 | 0 | 3.1484 | 0 | 2.865 | 14.3004 | 0.20034 | 2.865 | 14.3004 | 0.20034 | 3.1794 | 15.8694 | 0.20034 | 1.807% | 0.049116 | 0.046685 | 3548.1987 | 294.627 | 1994.8222 | 1258.7495 | 3665.5412 | 0 | 0 | 3665.5412 | 0.0001038%
2027 | 835 | 835-10F | Tier-2 | Tier-2---19 | 1--4 | 0.3653 | 59 | 100% | 12.4137 | 98.83% | 0% | 1.166% | 0.60731 | 0 | 0 | 0.60731 | 0 | 0.55265 | 0.36 | 1.5351 | 0.55265 | 0.36 | 1.5351 | 0.61328 | 0.3995 | 1.5351 | 4.892% | 0.0010446 | 0.00099289 | 11883.6638 | 1899.9347 | 22.1501 | 9961.5789 | 11890.8775 | 0 | 0 | 11890.8775 | 2.003e-05%
2027 | RB1 | CB RB1 | Tier-3 | Tier-3---20 | 1--5 | 0.026705 | 4 | 100% | 29.7534 | 99.88% | 0% | 0.1212% | 1.471 | 0 | 0 | 1.471 | 0 | 1.3386 | 0.026317 | 50.8637 | 1.3386 | 0.026317 | 50.8637 | 1.4855 | 0.029205 | 50.8637 | 4.944% | 0.0001458 | 0.00013858 | 204069.8082 | 32853.3253 | 379.8701 | 170836.6129 | 204082.6843 | 0 | 0 | 204082.6843 | 4.851e-05%
2027 | 907 | 907-1602 | Tier-3 | Tier-3---17 | 3--4 | 0.10398 | 4 | 100% | 257.2419 | 98.67% | 1.294% | 0.04048% | 12.5635 | 0 | 0 | 12.5635 | 0 | 11.4327 | 0.10247 | 111.5711 | 11.4327 | 0.10247 | 111.5711 | 12.687 | 0.11371 | 111.5711 | 4.884% | 0.018131 | 0.017233 | 14188.117 | 2263.0518 | 146.1468 | 11778.9183 | 14197.9773 | 0 | 0 | 14197.9773 | 0.0004143%
2027 | 282 | CB 282 | Tier-2 | Tier-2---15 | 4--3 | 1.0646 | 34 | 100% | 152.5069 | 4.749% | 94.48% | 0.7672% | 0.3585 | 0 | 0 | 0.3585 | 0 | 0.32623 | 1.0491 | 0.31095 | 0.32623 | 1.0491 | 0.31095 | 0.36202 | 1.1642 | 0.31095 | 0.2351% | 0.035573 | 0.033812 | 4287.153 | 11.5968 | 3743.6752 | 531.8809 | 4499.8161 | 0 | 0 | 4499.8161 | 1.182e-05%
2027 | 123 | 123-437 | Tier-1 | Non-HFTD---17 | 1--2 | 0.28887 | 10 | 100% | 1.1053 | 75.1% | 0% | 24.9% | 0.041085 | 0 | 0 | 0.041085 | 0 | 0.037387 | 0.28468 | 0.13133 | 0.037387 | 0.28468 | 0.13133 | 0.041489 | 0.31592 | 0.13133 | 3.717% | 0.0010262 | 0.0009754 | 1077.05 | 100.0793 | 217.6769 | 759.2939 | 1091.0192 | 0 | 0 | 1091.0192 | 1.355e-06%
2027 | LA2 | CB LA2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.183 | 176 | 100% | 12.2214 | 57.22% | 0% | 42.78% | 0.34614 | 0 | 0 | 0.34614 | 0 | 0.31498 | 7.0788 | 0.044496 | 0.31498 | 7.0788 | 0.044496 | 0.34954 | 7.8555 | 0.044496 | 2.832% | 0.020909 | 0.019874 | 584.5039 | 23.2258 | 216.3025 | 344.9757 | 597.5271 | 0 | 0 | 597.5271 | 1.141e-05%
2027 | 206 | 206-1817 | Tier-2 | Tier-2---4 | 4--5 | 11.7296 | 836 | 100% | 2976.5734 | 99.75% | 0% | 0.2502% | 146.9718 | 0 | 0 | 146.9718 | 0 | 133.7423 | 11.5595 | 11.5699 | 133.7423 | 11.5595 | 11.5699 | 148.4162 | 12.8278 | 11.5699 | 4.938% | 0.038208 | 0.036317 | 77904.8627 | 12644.4177 | 94.4539 | 65165.9911 | 77915.0127 | 0 | 0 | 77915.0127 | 0.004847%
2027 | 857 | CB 857 | Tier-1 | Non-HFTD---4 | 2--4 | 2.4864 | 160 | 100% | 134.8206 | 98.53% | 0% | 1.467% | 6.5757 | 0 | 0 | 6.5757 | 0 | 5.9838 | 2.4503 | 2.442 | 5.9838 | 2.4503 | 2.442 | 6.6403 | 2.7192 | 2.442 | 4.877% | 0.0091096 | 0.0086587 | 14799.8335 | 2316.1863 | 406.4843 | 12077.1629 | 14811.1433 | 0 | 0 | 14811.1433 | 0.0002168%
2027 | 1233 | 1233-591R | Tier-3 | Tier-3---12 | 5--5 | 6.4721 | 569 | 100% | 4300.1838 | 98.66% | 1.226% | 0.1146% | 210.0058 | 0 | 0 | 210.0058 | 0 | 191.1024 | 6.3783 | 29.9615 | 191.1024 | 6.3783 | 29.9615 | 212.0697 | 7.0781 | 29.9615 | 4.884% | 0.13142 | 0.12491 | 32721.9695 | 5569.8694 | 365.067 | 26787.0331 | 32744.8122 | 0 | 0 | 32744.8122 | 0.006925%
2027 | 418 | 418-1260 | Tier-1 | Non-HFTD---18 | 2--1 | 2.407 | 55 | 100% | 2.1529 | 26.16% | 0% | 73.84% | 0.027881 | 0 | 0 | 0.027881 | 0 | 0.025372 | 2.3721 | 0.010696 | 0.025372 | 2.3721 | 0.010696 | 0.028155 | 2.6324 | 0.010696 | 1.295% | 0.0068202 | 0.0064826 | 315.6683 | 2.8639 | 87.2806 | 225.5239 | 327.8067 | 0 | 0 | 327.8067 | 9.194e-07%
2027 | ELE1 | CB ELE1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.0237 | 226 | 100% | 2.9214 | 23.25% | 0% | 76.75% | 0.033616 | 0 | 0 | 0.033616 | 0 | 0.03059 | 2.9799 | 0.010266 | 0.03059 | 2.9799 | 0.010266 | 0.033947 | 3.3068 | 0.010266 | 1.151% | 0.0086982 | 0.0082676 | 335.8673 | 0.21618 | 101.3542 | 234.2969 | 349.2925 | 0 | 0 | 349.2925 | 1.109e-06%
2027 | 217 | 217-972R | Tier-2 | Tier-2---8 | 5--4 | 9.5829 | 969 | 100% | 1438.6594 | 90.88% | 8.66% | 0.4639% | 64.7163 | 0 | 0 | 64.7163 | 0 | 58.891 | 9.444 | 6.2358 | 58.891 | 9.444 | 6.2358 | 65.3523 | 10.4802 | 6.2358 | 4.498% | 0.18227 | 0.17325 | 7892.9777 | 1198.2453 | 600.4509 | 6094.2815 | 7930.4807 | 0 | 0 | 7930.4807 | 0.002134%
2027 | 120 | 120-368F | Tier-1 | Non-HFTD---7 | 2--3 | 1.3866 | 191 | 100% | 30.1162 | 0.9946% | 95.55% | 3.451% | 0.014827 | 0 | 0 | 0.014827 | 0 | 0.013493 | 1.3665 | 0.009874 | 0.013493 | 1.3665 | 0.009874 | 0.014973 | 1.5164 | 0.009874 | 0.04923% | 0.011459 | 0.010892 | 2628.1708 | 4.7284 | 2320.4806 | 302.9617 | 2763.6789 | 0 | 0 | 2763.6789 | 4.89e-07%
2027 | 1250 | 1250-27R | Tier-2 | Tier-2---6 | 5--5 | 4.6189 | 484 | 100% | 6418.5082 | 93.04% | 6.917% | 0.04745% | 295.5897 | 0 | 0 | 295.5897 | 0 | 268.9826 | 4.552 | 59.0914 | 268.9826 | 4.552 | 59.0914 | 298.4947 | 5.0514 | 59.0914 | 4.605% | 0.097369 | 0.09255 | 65919.1509 | 13368.0206 | 4366.1577 | 48184.9726 | 66158.2276 | 0 | 0 | 66158.2276 | 0.009747%
2027 | 548 | 548-18F | Tier-1 | Non-HFTD---17 | 1--1 | 1.1802 | 43 | 100% | 1.1676 | 51.97% | 0% | 48.03% | 0.030039 | 0 | 0 | 0.030039 | 0 | 0.027335 | 1.163 | 0.023503 | 0.027335 | 1.163 | 0.023503 | 0.030335 | 1.2907 | 0.023503 | 2.573% | 0.0027166 | 0.0025821 | 429.8188 | 0.57984 | 239.5369 | 189.7021 | 440.5693 | 0 | 0 | 440.5693 | 9.906e-07%
2027 | 215 | CB 215 | Tier-3 | Tier-3---20 | 1--5 | 0.14848 | 8 | 100% | 133.9133 | 99.89% | 0% | 0.1056% | 6.6217 | 0 | 0 | 6.6217 | 0 | 6.0257 | 0.14633 | 41.1781 | 6.0257 | 0.14633 | 41.1781 | 6.6868 | 0.16239 | 41.1781 | 4.945% | 0.0005546 | 0.00052715 | 241459.2274 | 38751.4093 | 725.0579 | 201982.7602 | 241472.5028 | 0 | 0 | 241472.5028 | 0.0002184%
2027 | 157 | 157-189R | Tier-3 | Tier-3---9 | 5--4 | 27.7167 | 1055 | 100% | 5507.0239 | 92.46% | 7.234% | 0.3043% | 252.0471 | 0 | 0 | 252.0471 | 0 | 229.3595 | 27.3148 | 8.3969 | 229.3595 | 27.3148 | 8.3969 | 254.5243 | 30.3118 | 8.3969 | 4.577% | 0.3705 | 0.35216 | 14863.9228 | 1949.0115 | 963.9544 | 11950.9569 | 14922.279 | 0 | 0 | 14922.279 | 0.008312%
2027 | 283 | 283-55R | Tier-3 | Tier-3---9 | 5--5 | 7.2309 | 112 | 100% | 5299.6344 | 98.55% | 1.37% | 0.07601% | 258.5396 | 0 | 0 | 258.5396 | 0 | 235.2675 | 7.126 | 33.0153 | 235.2675 | 7.126 | 33.0153 | 261.0805 | 7.9079 | 33.0153 | 4.878% | 0.20157 | 0.19159 | 26291.5727 | 4431.5745 | 343.4719 | 21516.5263 | 26311.366 | 0 | 0 | 26311.366 | 0.008526%
2027 | 483 | CB 483 | Tier-1 | Non-HFTD---11 | 2--2 | 2.1438 | 53 | 100% | 10.3604 | 90.93% | 0% | 9.069% | 0.46633 | 0 | 0 | 0.46633 | 0 | 0.42436 | 2.1127 | 0.20086 | 0.42436 | 2.1127 | 0.20086 | 0.47092 | 2.3445 | 0.20086 | 4.501% | 0.006517 | 0.0061944 | 1589.7521 | 232.4385 | 19.5086 | 1337.8049 | 1597.2601 | 0 | 0 | 1597.2601 | 1.538e-05%
2027 | 730 | 730-971R | Tier-1 | Non-HFTD---8 | 3--2 | 8.1335 | 250 | 100% | 26.5137 | 79.89% | 0% | 20.11% | 1.0484 | 0 | 0 | 1.0484 | 0 | 0.95407 | 8.0156 | 0.11903 | 0.95407 | 8.0156 | 0.11903 | 1.0588 | 8.8951 | 0.11903 | 3.954% | 0.02251 | 0.021395 | 1177.8833 | 63.4791 | 575.4887 | 538.9155 | 1190.2215 | 0 | 0 | 1190.2215 | 3.457e-05%
2027 | 551 | 551-19 | Tier-1 | Non-HFTD---12 | 3--2 | 6.4676 | 228 | 100% | 15.235 | 68.38% | 0% | 31.62% | 0.51569 | 0 | 0 | 0.51569 | 0 | 0.46927 | 6.3738 | 0.073625 | 0.46927 | 6.3738 | 0.073625 | 0.52076 | 7.0732 | 0.073625 | 3.385% | 0.018991 | 0.018051 | 802.2291 | 3.4308 | 551.779 | 247.0193 | 815.4385 | 0 | 0 | 815.4385 | 1.701e-05%
2027 | 855 | 855-46AE | Tier-2 | Tier-2---15 | 1--5 | 0.25303 | 0 | 100% | 188.5529 | 99.88% | 0% | 0.1171% | 9.3224 | 0 | 0 | 9.3224 | 0 | 8.4833 | 0.24936 | 34.02 | 8.4833 | 0.24936 | 34.02 | 9.4141 | 0.27672 | 34.02 | 4.944% | 0.0010888 | 0.0010349 | 173174.957 | 50966.8705 | 22.9996 | 122185.0869 | 173185.5197 | 0 | 0 | 173185.5197 | 0.0003074%
2027 | 95 | 95-35F | Tier-1 | Non-HFTD---9 | 2--2 | 2.2868 | 190 | 100% | 19.0547 | 69.14% | 22.45% | 8.414% | 0.65213 | 0 | 0 | 0.65213 | 0 | 0.59343 | 2.2536 | 0.26333 | 0.59343 | 2.2536 | 0.26333 | 0.65854 | 2.5009 | 0.26333 | 3.422% | 0.011941 | 0.01135 | 1595.6856 | 179.3204 | 352.6449 | 1063.7203 | 1621.3303 | 0 | 0 | 1621.3303 | 2.15e-05%
2027 | 1030 | 1030-1777 | Tier-3 | Tier-3---5 | 5--5 | 5.7761 | 253 | 100% | 11817.5772 | 98.58% | 1.381% | 0.03413% | 576.6917 | 0 | 0 | 576.6917 | 0 | 524.7816 | 5.6924 | 92.1901 | 524.7816 | 5.6924 | 92.1901 | 582.3594 | 6.3169 | 92.1901 | 4.88% | 0.24629 | 0.2341 | 47981.5879 | 7910.8802 | 628.0436 | 39442.6641 | 48016.9501 | 0 | 0 | 48016.9501 | 0.01902%
2027 | 1215 | CB 1215 | Tier-3 | Tier-3---20 | 1--5 | 0.05303 | 0 | 100% | 21.8223 | 99.66% | 0% | 0.344% | 1.0765 | 0 | 0 | 1.0765 | 0 | 0.97959 | 0.052261 | 18.744 | 0.97959 | 0.052261 | 18.744 | 1.0871 | 0.057995 | 18.744 | 4.933% | 0.0002576 | 0.00024485 | 84713.9519 | 12244.53 | 142.3109 | 72327.111 | 84729.1273 | 0 | 0 | 84729.1273 | 3.55e-05%
2027 | 166 | 166-984F | Tier-1 | Non-HFTD---16 | 2--1 | 5.0462 | 201 | 100% | 4.5392 | 30.05% | 0% | 69.95% | 0.067511 | 0 | 0 | 0.067511 | 0 | 0.061434 | 4.973 | 0.012354 | 0.061434 | 4.973 | 0.012354 | 0.068175 | 5.5186 | 0.012354 | 1.487% | 0.013305 | 0.012647 | 341.1538 | 0.41222 | 122.751 | 217.9905 | 353.5821 | 0 | 0 | 353.5821 | 2.226e-06%
2027 | 564 | CB 564 | Tier-1 | Non-HFTD---5 | 1--5 | 0.65684 | 30 | 100% | 57.5722 | 99.31% | 0% | 0.6931% | 2.8301 | 0 | 0 | 2.8301 | 0 | 2.5753 | 0.64731 | 3.9785 | 2.5753 | 0.64731 | 3.9785 | 2.8579 | 0.71834 | 3.9785 | 4.916% | 0.002902 | 0.0027584 | 19838.8117 | 2914.289 | 1862.4717 | 15062.051 | 19845.9726 | 0 | 0 | 19845.9726 | 9.333e-05%
2027 | 835 | 835-11F | Tier-2 | Tier-2---15 | 1--5 | 1.0576 | 39 | 100% | 139.955 | 99.63% | 0% | 0.3714% | 6.902 | 0 | 0 | 6.902 | 0 | 6.2808 | 1.0422 | 6.0262 | 6.2808 | 1.0422 | 6.0262 | 6.9699 | 1.1566 | 6.0262 | 4.932% | 0.0041866 | 0.0039794 | 33429.2729 | 8048.3513 | 14.1386 | 25366.7829 | 33435.7392 | 0 | 0 | 33435.7392 | 0.0002276%
2027 | 120 | CB 120 | Tier-1 | Non-HFTD---5 | 2--4 | 0.83351 | 54 | 100% | 72.8901 | 46.84% | 52.05% | 1.107% | 1.6901 | 0 | 0 | 1.6901 | 0 | 1.538 | 0.82143 | 1.8723 | 1.538 | 0.82143 | 1.8723 | 1.7067 | 0.91155 | 1.8723 | 2.319% | 0.010618 | 0.010093 | 6864.6422 | 601.3181 | 3453.7454 | 2809.5787 | 7054.6775 | 0 | 0 | 7054.6775 | 5.573e-05%
2027 | 781 | 781-44 | Tier-1 | Non-HFTD---2 | 4--4 | 15.9541 | 1118 | 100% | 408.0386 | 9.644% | 87.69% | 2.666% | 1.9479 | 0 | 0 | 1.9479 | 0 | 1.7725 | 15.7228 | 0.11274 | 1.7725 | 15.7228 | 0.11274 | 1.967 | 17.4479 | 0.11274 | 0.4774% | 0.057288 | 0.054452 | 7122.6331 | 90.5718 | 5991.9403 | 1040.121 | 7457.7922 | 0 | 0 | 7457.7922 | 6.423e-05%
2027 | 222 | 222-1986R | Tier-3 | Tier-3---1 | 5--5 | 21.2556 | 733 | 100% | 79194.3488 | 99.25% | 0.7305% | 0.01724% | 3890.8074 | 0 | 0 | 3890.8074 | 0 | 3540.5817 | 20.9475 | 169.022 | 3540.5817 | 20.9475 | 169.022 | 3929.0461 | 23.2458 | 169.022 | 4.913% | 0.41507 | 0.39452 | 190797.4815 | 33595.3988 | 1245.7209 | 155956.3617 | 190871.7807 | 0 | 0 | 190871.7807 | 0.1283%
2027 | 473 | CB 473 | Tier-1 | Non-HFTD---2 | 5--4 | 8.3298 | 539 | 100% | 543.89 | 19.16% | 79.89% | 0.9474% | 5.1597 | 0 | 0 | 5.1597 | 0 | 4.6953 | 8.209 | 0.57197 | 4.6953 | 8.209 | 0.57197 | 5.2104 | 9.1097 | 0.57197 | 0.9487% | 0.10114 | 0.096132 | 5377.691 | 163.6638 | 4088.0705 | 1125.9566 | 5604.0765 | 0 | 0 | 5604.0765 | 0.0001701%
2027 | 247 | CB 247 | Tier-2 | Tier-2---12 | 4--4 | 3.5733 | 151 | 100% | 379.7423 | 70.28% | 29.01% | 0.71% | 13.2106 | 0 | 0 | 13.2106 | 0 | 12.0215 | 3.5214 | 3.4138 | 12.0215 | 3.5214 | 3.4138 | 13.3405 | 3.9078 | 3.4138 | 3.479% | 0.038566 | 0.036657 | 9846.5066 | 1443.1584 | 2899.0809 | 5504.2673 | 9998.9083 | 0 | 0 | 9998.9083 | 0.0004356%
2027 | 1245 | CB 1245 | Tier-2 | Tier-2---15 | 1--5 | 0.4697 | 0 | 100% | 108.0997 | 99.75% | 0% | 0.2497% | 5.3376 | 0 | 0 | 5.3376 | 0 | 4.8571 | 0.46289 | 10.4931 | 4.8571 | 0.46289 | 10.4931 | 5.39 | 0.51367 | 10.4931 | 4.938% | 0.001637 | 0.001556 | 66035.2637 | 17244.823 | 21.4736 | 48768.9671 | 66043.8516 | 0 | 0 | 66043.8516 | 0.000176%
2027 | 909 | 909-451 | Tier-3 | Tier-3---1 | 5--5 | 20.5957 | 1501 | 100% | 55252.3747 | 99.27% | 0.7029% | 0.02396% | 2715.113 | 0 | 0 | 2715.113 | 0 | 2470.7159 | 20.2971 | 121.7278 | 2470.7159 | 20.2971 | 121.7278 | 2741.797 | 22.524 | 121.7278 | 4.914% | 0.31112 | 0.29572 | 177590.703 | 30501.3074 | 1127.1647 | 145962.2309 | 177657.9267 | 0 | 0 | 177657.9267 | 0.08953%
2027 | GH2 | CB GH2 | Tier-1 | Non-HFTD---16 | 2--1 | 2.462 | 67 | 100% | 2.4391 | 22.32% | 0% | 77.68% | 0.026948 | 0 | 0 | 0.026948 | 0 | 0.024522 | 2.4263 | 0.010107 | 0.024522 | 2.4263 | 0.010107 | 0.027213 | 2.6925 | 0.010107 | 1.105% | 0.0074138 | 0.0070468 | 328.9948 | 6.3654 | 58.4562 | 264.1731 | 342.304 | 0 | 0 | 342.304 | 8.886e-07%
2027 | 355 | 355-6R | Tier-2 | Tier-2---7 | 4--5 | 1.7237 | 249 | 100% | 1698.7097 | 79.94% | 19.99% | 0.07228% | 67.2176 | 0 | 0 | 67.2176 | 0 | 61.1671 | 1.6987 | 36.0084 | 61.1671 | 1.6987 | 36.0084 | 67.8782 | 1.8851 | 36.0084 | 3.957% | 0.074333 | 0.070654 | 22852.699 | 2966.2426 | 4205.6125 | 15680.8438 | 23091.4486 | 0 | 0 | 23091.4486 | 0.002217%
2027 | 702 | 702-30 | Tier-1 | Non-HFTD---3 | 4--3 | 8.6788 | 214 | 100% | 100.3702 | 67.48% | 26.99% | 5.53% | 3.3524 | 0 | 0 | 3.3524 | 0 | 3.0507 | 8.5529 | 0.35668 | 3.0507 | 8.5529 | 0.35668 | 3.3854 | 9.4914 | 0.35668 | 3.34% | 0.033242 | 0.031597 | 3019.3805 | 488.6759 | 847.0105 | 1683.6941 | 3070.5224 | 0 | 0 | 3070.5224 | 0.0001106%
2027 | 205 | 205-369R | Tier-1 | Non-HFTD---2 | 4--4 | 15.9271 | 1706 | 100% | 370.1825 | 97.17% | 0% | 2.827% | 17.8061 | 0 | 0 | 17.8061 | 0 | 16.2033 | 15.6962 | 1.0323 | 16.2033 | 15.6962 | 1.0323 | 17.9811 | 17.4183 | 1.0323 | 4.81% | 0.046634 | 0.044326 | 7938.0395 | 1227.249 | 240.0519 | 6470.7387 | 7949.7244 | 0 | 0 | 7949.7244 | 0.0005872%
2027 | 154 | 154-897F | Tier-1 | Non-HFTD---20 | 1--1 | 0.72155 | 28 | 100% | 0.3167 | 2.18% | 0% | 97.82% | 0.00034168 | 0 | 0 | 0.00034168 | 0 | 0.00031093 | 0.71109 | 0.00043725 | 0.00031093 | 0.71109 | 0.00043725 | 0.00034504 | 0.78911 | 0.00043725 | 0.1079% | 0.002013 | 0.0019134 | 157.3294 | 0.11581 | 17.4095 | 139.8041 | 165.3442 | 0 | 0 | 165.3442 | 1.127e-08%
2027 | 971 | 971-29R | Tier-3 | Tier-3---6 | 5--5 | 3.8006 | 201 | 100% | 8015.4065 | 99.46% | 0.5042% | 0.0309% | 394.6396 | 0 | 0 | 394.6396 | 0 | 359.1166 | 3.7455 | 95.8807 | 359.1166 | 3.7455 | 95.8807 | 398.5181 | 4.1564 | 95.8807 | 4.924% | 0.12171 | 0.11568 | 65856.8143 | 11074.2553 | 300.8602 | 54481.6988 | 65875.1664 | 0 | 0 | 65875.1664 | 0.01301%
2027 | 481 | 481-30 | Tier-1 | Non-HFTD---16 | 2--1 | 3.2669 | 149 | 100% | 2.7763 | 24.5% | 0% | 75.5% | 0.033676 | 0 | 0 | 0.033676 | 0 | 0.030645 | 3.2195 | 0.0095184 | 0.030645 | 3.2195 | 0.0095184 | 0.034007 | 3.5727 | 0.0095184 | 1.213% | 0.0083508 | 0.0079374 | 332.4593 | 0.20057 | 104.1964 | 228.0624 | 345.5304 | 0 | 0 | 345.5304 | 1.111e-06%
2027 | 353 | 353-904R | Tier-2 | Tier-2---3 | 5--5 | 7.0653 | 395 | 100% | 13534.4067 | 99.43% | 0.528% | 0.03951% | 666.1513 | 0 | 0 | 666.1513 | 0 | 606.1886 | 6.9629 | 87.06 | 606.1886 | 6.9629 | 87.06 | 672.6982 | 7.7268 | 87.06 | 4.922% | 0.12577 | 0.11955 | 107611.5055 | 19419.395 | 792.7842 | 87399.3263 | 107643.3078 | 0 | 0 | 107643.3078 | 0.02197%
2027 | 311 | 311-1199 | Tier-2 | Tier-2---20 | 3--2 | 0.4381 | 36 | 100% | 15.6056 | 49.38% | 48.09% | 2.529% | 0.38147 | 0 | 0 | 0.38147 | 0 | 0.34714 | 0.43175 | 0.80403 | 0.34714 | 0.43175 | 0.80403 | 0.38522 | 0.47912 | 0.80403 | 2.444% | 0.018336 | 0.017428 | 851.1013 | 60.6306 | 426.7234 | 363.7473 | 873.5365 | 0 | 0 | 873.5365 | 1.258e-05%
2027 | 188 | 188-12F | Tier-1 | Non-HFTD---19 | 1--2 | 0.24244 | 18 | 100% | 0.37445 | 60.74% | 0% | 39.26% | 0.011258 | 0 | 0 | 0.011258 | 0 | 0.010244 | 0.23893 | 0.042877 | 0.010244 | 0.23893 | 0.042877 | 0.011368 | 0.26514 | 0.042877 | 3.006% | 0.0006558 | 0.00062334 | 570.9839 | 56.1501 | 25.9997 | 488.8341 | 582.659 | 0 | 0 | 582.659 | 3.712e-07%
2027 | 236 | 236-1573R | Tier-3 | Tier-3---7 | 5--5 | 7.1517 | 256 | 100% | 6927.8558 | 97.84% | 2.089% | 0.06679% | 335.5367 | 0 | 0 | 335.5367 | 0 | 305.3339 | 7.048 | 43.3219 | 305.3339 | 7.048 | 43.3219 | 338.8344 | 7.8213 | 43.3219 | 4.843% | 0.18488 | 0.17572 | 37473.1079 | 6448.1569 | 711.4883 | 30313.4626 | 37515.1745 | 0 | 0 | 37515.1745 | 0.01106%
2027 | 777 | 777-263F | Tier-1 | Non-HFTD---17 | 1--2 | 0.28785 | 0 | 100% | 1.1231 | 80.53% | 0% | 19.47% | 0.044774 | 0 | 0 | 0.044774 | 0 | 0.040744 | 0.28368 | 0.14363 | 0.040744 | 0.28368 | 0.14363 | 0.045214 | 0.3148 | 0.14363 | 3.986% | 0.0008638 | 0.00082104 | 1300.2394 | 169.3313 | 25.8272 | 1105.0809 | 1313.4199 | 0 | 0 | 1313.4199 | 1.476e-06%
2027 | 212 | CB 212 | Tier-2 | Tier-2---19 | 1--5 | 0.23902 | 0 | 100% | 22.9809 | 99.09% | 0% | 0.9069% | 1.1272 | 0 | 0 | 1.1272 | 0 | 1.0258 | 0.23555 | 4.3548 | 1.0258 | 0.23555 | 4.3548 | 1.1383 | 0.26139 | 4.3548 | 4.905% | 0.0011646 | 0.001107 | 19732.8401 | 1812.7881 | 561.3991 | 17358.6529 | 19742.1595 | 0 | 0 | 19742.1595 | 3.717e-05%
2027 | 329 | CB 329 | Tier-2 | Tier-2---14 | 3--4 | 2.4417 | 31 | 100% | 215.2852 | 96.83% | 2.614% | 0.5577% | 10.3186 | 0 | 0 | 10.3186 | 0 | 9.3898 | 2.4063 | 3.9022 | 9.3898 | 2.4063 | 3.9022 | 10.4201 | 2.6703 | 3.9022 | 4.793% | 0.026212 | 0.024915 | 8213.1037 | 1191.5515 | 755.5628 | 6265.9894 | 8226.6688 | 0 | 0 | 8226.6688 | 0.0003403%
2027 | 733 | 733-23R | Tier-1 | Non-HFTD---10 | 4--1 | 14.2499 | 708 | 100% | 18.173 | 43.59% | 0% | 56.41% | 0.39211 | 0 | 0 | 0.39211 | 0 | 0.35681 | 14.0432 | 0.025408 | 0.35681 | 14.0432 | 0.025408 | 0.39596 | 15.584 | 0.025408 | 2.158% | 0.039686 | 0.037722 | 457.9176 | 5.4845 | 190.7048 | 261.7282 | 471.3702 | 0 | 0 | 471.3702 | 1.293e-05%
2027 | 138 | 138-358R | Tier-1 | Non-HFTD---8 | 3--3 | 5.9884 | 352 | 100% | 38.8456 | 86.43% | 0% | 13.57% | 1.6618 | 0 | 0 | 1.6618 | 0 | 1.5123 | 5.9016 | 0.25624 | 1.5123 | 5.9016 | 0.25624 | 1.6782 | 6.5491 | 0.25624 | 4.278% | 0.022652 | 0.021531 | 1714.8689 | 4.9224 | 1481.4917 | 228.4549 | 1726.9914 | 0 | 0 | 1726.9914 | 5.48e-05%
2027 | 163 | 163-33R | Tier-1 | Non-HFTD---10 | 4--2 | 10.3481 | 566 | 100% | 25.0426 | 46.21% | 0% | 53.79% | 0.57287 | 0 | 0 | 0.57287 | 0 | 0.5213 | 10.1981 | 0.051118 | 0.5213 | 10.1981 | 0.051118 | 0.5785 | 11.317 | 0.051118 | 2.288% | 0.044418 | 0.042219 | 563.798 | 5.8936 | 264.9054 | 292.999 | 579.5904 | 0 | 0 | 579.5904 | 1.889e-05%
2027 | RD2 | CB RD2 | Tier-1 | Non-HFTD---12 | 3--1 | 8.8002 | 319 | 100% | 9.3441 | 27.56% | 0% | 72.44% | 0.12749 | 0 | 0 | 0.12749 | 0 | 0.11602 | 8.6726 | 0.013377 | 0.11602 | 8.6726 | 0.013377 | 0.12875 | 9.6242 | 0.013377 | 1.364% | 0.026759 | 0.025434 | 349.1931 | 3.0965 | 101.4578 | 244.6387 | 362.3657 | 0 | 0 | 362.3657 | 4.204e-06%
2027 | 505 | 505-1676F | Tier-1 | Non-HFTD---4 | 3--4 | 5.4025 | 268 | 100% | 126.3109 | 97.31% | 0% | 2.687% | 6.0844 | 0 | 0 | 6.0844 | 0 | 5.5367 | 5.3241 | 1.0399 | 5.5367 | 5.3241 | 1.0399 | 6.1442 | 5.9083 | 1.0399 | 4.817% | 0.016119 | 0.015321 | 7836.1516 | 1240.1952 | 66.9195 | 6529.037 | 7847.1186 | 0 | 0 | 7847.1186 | 0.0002006%
2027 | 103 | CB 103 | Tier-1 | Non-HFTD---2 | 4--4 | 10.3631 | 451 | 100% | 251.3079 | 4.044% | 92.91% | 3.046% | 0.50308 | 0 | 0 | 0.50308 | 0 | 0.4578 | 10.2128 | 0.044826 | 0.4578 | 10.2128 | 0.044826 | 0.50803 | 11.3333 | 0.044826 | 0.2002% | 0.044854 | 0.042634 | 5602.7475 | 13.1962 | 4846.1699 | 743.3814 | 5882.7266 | 0 | 0 | 5882.7266 | 1.659e-05%
2027 | 222 | 222-1992R | Tier-3 | Tier-3---18 | 5--2 | 0.78597 | 38 | 100% | 288.7705 | 86.56% | 13.18% | 0.2657% | 12.3725 | 0 | 0 | 12.3725 | 0 | 11.2588 | 0.77458 | 14.5354 | 11.2588 | 0.77458 | 14.5354 | 12.4941 | 0.85956 | 14.5354 | 4.285% | 0.22115 | 0.2102 | 1305.7642 | 167.1535 | 149.2603 | 989.3504 | 1314.9061 | 0 | 0 | 1314.9061 | 0.000408%
2027 | 150 | 150-506 | Tier-1 | Non-HFTD---9 | 1--4 | 0.56136 | 3 | 100% | 17.1377 | 96.67% | 0% | 3.329% | 0.82008 | 0 | 0 | 0.82008 | 0 | 0.74626 | 0.55322 | 1.3489 | 0.74626 | 0.55322 | 1.3489 | 0.82814 | 0.61392 | 1.3489 | 4.785% | 0.0026668 | 0.0025348 | 6426.2995 | 1009.1063 | 19.5009 | 5397.6923 | 6437.4397 | 0 | 0 | 6437.4397 | 2.704e-05%
2027 | 43 | 43-475F | Tier-1 | Non-HFTD---20 | 1--1 | 0.15131 | 3 | 100% | 0.037927 | 13.96% | 0% | 86.04% | 0.00026216 | 0 | 0 | 0.00026216 | 0 | 0.00023856 | 0.14912 | 0.0015998 | 0.00023856 | 0.14912 | 0.0015998 | 0.00026474 | 0.16548 | 0.0015998 | 0.6912% | 0.0002508 | 0.00023839 | 151.2257 | 1.3755 | 25.089 | 124.7612 | 158.0014 | 0 | 0 | 158.0014 | 8.645e-09%
2027 | 237 | 237-28F | Tier-2 | Tier-2---7 | 5--5 | 1.5879 | 37 | 100% | 2530.2255 | 98.83% | 1.116% | 0.05734% | 123.7762 | 0 | 0 | 123.7762 | 0 | 112.6347 | 1.5649 | 71.9758 | 112.6347 | 1.5649 | 71.9758 | 124.9927 | 1.7366 | 71.9758 | 4.892% | 0.10804 | 0.1027 | 23418.4293 | 3729.6319 | 261.331 | 19427.4664 | 23432.7427 | 0 | 0 | 23432.7427 | 0.004082%
2027 | 288 | 288-2380F | Tier-2 | Tier-2---12 | 4--5 | 1.7432 | 394 | 100% | 550.61 | 92.88% | 6.93% | 0.1872% | 25.3153 | 0 | 0 | 25.3153 | 0 | 23.0365 | 1.7179 | 13.4095 | 23.0365 | 1.7179 | 13.4095 | 25.5641 | 1.9064 | 13.4095 | 4.598% | 0.030344 | 0.028842 | 18145.5978 | 2753.5191 | 1169.7879 | 14222.2908 | 18212.8585 | 0 | 0 | 18212.8585 | 0.0008348%
2027 | 1023 | 1023-46AE | Tier-2 | Tier-2---2 | 5--5 | 19.1678 | 2034 | 100% | 9469.9149 | 95.98% | 3.884% | 0.1387% | 449.9058 | 0 | 0 | 449.9058 | 0 | 409.4082 | 18.8899 | 21.6734 | 409.4082 | 18.8899 | 21.6734 | 454.3275 | 20.9625 | 21.6734 | 4.751% | 0.13914 | 0.13225 | 68062.6824 | 10581.9513 | 2429.1867 | 55051.5444 | 68205.2551 | 0 | 0 | 68205.2551 | 0.01484%
2027 | 415 | CB 415 | Tier-1 | Non-HFTD---3 | 3--3 | 5.4938 | 215 | 100% | 126.4207 | 27.6% | 69.15% | 3.246% | 1.7273 | 0 | 0 | 1.7273 | 0 | 1.5719 | 5.4141 | 0.29032 | 1.5719 | 5.4141 | 0.29032 | 1.7443 | 6.0082 | 0.29032 | 1.366% | 0.027526 | 0.026163 | 4592.8064 | 78.3926 | 3704.5785 | 809.8353 | 4765.9683 | 0 | 0 | 4765.9683 | 5.696e-05%
2027 | 358 | 358-1175F | Tier-2 | Tier-2---11 | 5--3 | 0.47553 | 26 | 100% | 599.5834 | 97.21% | 2.746% | 0.04768% | 28.8502 | 0 | 0 | 28.8502 | 0 | 26.2533 | 0.46863 | 56.021 | 26.2533 | 0.46863 | 56.021 | 29.1337 | 0.52005 | 56.021 | 4.812% | 0.14195 | 0.13492 | 4224.0008 | 666.1443 | 106.9445 | 3450.912 | 4230.1466 | 0 | 0 | 4230.1466 | 0.0009514%
2027 | 197 | 197-1155F | Tier-2 | Tier-2---21 | 1--4 | 0.22216 | 17 | 100% | 6.6189 | 96.38% | 0% | 3.621% | 0.31578 | 0 | 0 | 0.31578 | 0 | 0.28735 | 0.21894 | 1.3125 | 0.28735 | 0.21894 | 1.3125 | 0.31888 | 0.24296 | 1.3125 | 4.771% | 0.0010316 | 0.00098054 | 6416.1897 | 1003.77 | 50.6222 | 5361.7975 | 6428.2874 | 0 | 0 | 6428.2874 | 1.041e-05%
2027 | 789 | CB 789 | Tier-1 | Non-HFTD---4 | 2--4 | 2.8581 | 104 | 100% | 122.362 | 98.67% | 0% | 1.333% | 5.9762 | 0 | 0 | 5.9762 | 0 | 5.4383 | 2.8167 | 1.9307 | 5.4383 | 2.8167 | 1.9307 | 6.0349 | 3.1257 | 1.9307 | 4.884% | 0.0078294 | 0.0074418 | 15628.5298 | 2423.9954 | 597.0903 | 12607.4441 | 15639.3767 | 0 | 0 | 15639.3767 | 0.0001971%
2027 | MF1 | CB MF1 | Tier-1 | Non-HFTD---7 | 3--3 | 4.0621 | 96 | 100% | 37.1269 | 4.679% | 88.17% | 7.156% | 0.085991 | 0 | 0 | 0.085991 | 0 | 0.078251 | 4.0032 | 0.019547 | 0.078251 | 4.0032 | 0.019547 | 0.086836 | 4.4424 | 0.019547 | 0.2316% | 0.015706 | 0.014928 | 2363.9287 | 4.6517 | 2018.9493 | 340.3277 | 2481.2767 | 0 | 0 | 2481.2767 | 2.836e-06%
2027 | 522 | 522-38R | Tier-2 | Tier-2---6 | 4--5 | 17.4926 | 1811 | 100% | 5639.8414 | 96.44% | 3.339% | 0.2198% | 269.2374 | 0 | 0 | 269.2374 | 0 | 245.0024 | 17.239 | 14.2121 | 245.0024 | 17.239 | 14.2121 | 271.8835 | 19.1304 | 14.2121 | 4.774% | 0.088602 | 0.084216 | 63653.5146 | 14842.1478 | 2035.9127 | 46775.4541 | 63771.4814 | 0 | 0 | 63771.4814 | 0.008878%
2027 | 255 | CB 255 | Tier-1 | Non-HFTD---8 | 3--3 | 5.8911 | 156 | 100% | 32.2801 | 87.28% | 0% | 12.72% | 1.3946 | 0 | 0 | 1.3946 | 0 | 1.269 | 5.8057 | 0.21858 | 1.269 | 5.8057 | 0.21858 | 1.4083 | 6.4427 | 0.21858 | 4.32% | 0.016748 | 0.015919 | 1927.4491 | 4.4433 | 1678.6079 | 244.3979 | 1940.2212 | 0 | 0 | 1940.2212 | 4.599e-05%
2027 | 1439 | 1439-29 | Tier-1 | Non-HFTD---17 | 1--2 | 0.26119 | 1 | 100% | 0.74654 | 53.38% | 0% | 46.62% | 0.019724 | 0 | 0 | 0.019724 | 0 | 0.017949 | 0.2574 | 0.069731 | 0.017949 | 0.2574 | 0.069731 | 0.019918 | 0.28564 | 0.069731 | 2.642% | 0.0010952 | 0.001041 | 681.6446 | 46.3387 | 108.2949 | 527.0109 | 698.1955 | 0 | 0 | 698.1955 | 6.504e-07%
2027 | 401 | 401-684R | Tier-2 | Tier-2---21 | 4--1 | 0.051326 | 14 | 100% | 1.5961 | 62.42% | 35.57% | 2.007% | 0.049319 | 0 | 0 | 0.049319 | 0 | 0.04488 | 0.050582 | 0.88728 | 0.04488 | 0.050582 | 0.88728 | 0.049804 | 0.056131 | 0.88728 | 3.09% | 0.030395 | 0.028891 | 52.5129 | 8.9983 | 14.8334 | 28.6812 | 53.5406 | 0 | 0 | 53.5406 | 1.626e-06%
2027 | 202 | CB 202 | Tier-2 | Tier-2---16 | 4--3 | 11.6007 | 313 | 100% | 133.9861 | 95.12% | 0% | 4.877% | 6.3088 | 0 | 0 | 6.3088 | 0 | 5.741 | 11.4325 | 0.50216 | 5.741 | 11.4325 | 0.50216 | 6.3709 | 12.6869 | 0.50216 | 4.709% | 0.040966 | 0.038939 | 3270.6344 | 424.6242 | 32.8297 | 2813.1806 | 3278.9415 | 0 | 0 | 3278.9415 | 0.000208%
2027 | 490 | 490-36 | Tier-1 | Non-HFTD---19 | 1--3 | 0.037879 | 3 | 100% | 0.34203 | 90.49% | 0% | 9.512% | 0.01532 | 0 | 0 | 0.01532 | 0 | 0.013941 | 0.03733 | 0.37346 | 0.013941 | 0.03733 | 0.37346 | 0.015471 | 0.041425 | 0.37346 | 4.479% | 0.000149 | 0.00014162 | 2295.4788 | 192.4507 | 911.964 | 1191.0641 | 2306.8493 | 0 | 0 | 2306.8493 | 5.052e-07%
2027 | 343 | 343-20 | Tier-1 | Non-HFTD---14 | 2--1 | 4.3719 | 186 | 100% | 6.0217 | 48.31% | 0% | 51.69% | 0.144 | 0 | 0 | 0.144 | 0 | 0.13103 | 4.3085 | 0.030413 | 0.13103 | 4.3085 | 0.030413 | 0.14541 | 4.7813 | 0.030413 | 2.391% | 0.012386 | 0.011773 | 486.184 | 9.777 | 199.1497 | 277.2573 | 499.2718 | 0 | 0 | 499.2718 | 4.748e-06%
2027 | 350 | 350-2196R | Tier-2 | Tier-2---5 | 5--5 | 34.4453 | 2730 | 100% | 5570.6857 | 96.99% | 2.589% | 0.4237% | 267.4423 | 0 | 0 | 267.4423 | 0 | 243.3688 | 33.9459 | 7.1693 | 243.3688 | 33.9459 | 7.1693 | 270.0707 | 37.6703 | 7.1693 | 4.801% | 0.19915 | 0.18929 | 27972.7323 | 4549.3249 | 680.341 | 22743.0664 | 28016.6156 | 0 | 0 | 28016.6156 | 0.008819%
2027 | 213 | 213-263F | Tier-1 | Non-HFTD---7 | 1--4 | 0.84712 | 152 | 100% | 32.2974 | 98.29% | 0% | 1.706% | 1.5715 | 0 | 0 | 1.5715 | 0 | 1.43 | 0.83483 | 1.7129 | 1.43 | 0.83483 | 1.7129 | 1.5869 | 0.92643 | 1.7129 | 4.866% | 0.0030164 | 0.0028671 | 10707.2735 | 2157.1184 | 1406.2766 | 7143.8786 | 10716.7845 | 0 | 0 | 10716.7845 | 5.182e-05%
2027 | 508 | CB 508 | Tier-1 | Non-HFTD---9 | 2--3 | 2.0923 | 61 | 100% | 20.2639 | 91.46% | 0% | 8.542% | 0.91739 | 0 | 0 | 0.91739 | 0 | 0.83481 | 2.0619 | 0.40487 | 0.83481 | 2.0619 | 0.40487 | 0.9264 | 2.2881 | 0.40487 | 4.527% | 0.0068532 | 0.006514 | 2956.8488 | 100.9812 | 2109.3369 | 746.5307 | 2970.0016 | 0 | 0 | 2970.0016 | 3.025e-05%
2027 | 1030 | 1030-18R | Tier-3 | Tier-3---7 | 5--5 | 3.5275 | 195 | 100% | 6620.9098 | 98.66% | 1.309% | 0.03186% | 323.3397 | 0 | 0 | 323.3397 | 0 | 294.2347 | 3.4763 | 84.6398 | 294.2347 | 3.4763 | 84.6398 | 326.5175 | 3.8577 | 84.6398 | 4.884% | 0.23843 | 0.22663 | 27769.0579 | 4629.9608 | 333.1834 | 22805.9136 | 27788.4525 | 0 | 0 | 27788.4525 | 0.01066%
2027 | 1100 | 1100-1168F | Tier-2 | Tier-2---18 | 4--2 | 0.18447 | 0 | 100% | 54.719 | 98.75% | 1.065% | 0.1855% | 2.6747 | 0 | 0 | 2.6747 | 0 | 2.4339 | 0.1818 | 13.3884 | 2.4339 | 0.1818 | 13.3884 | 2.701 | 0.20174 | 13.3884 | 4.888% | 0.070904 | 0.067394 | 771.7308 | 123.9939 | 6.7126 | 641.0242 | 772.2335 | 0 | 0 | 772.2335 | 8.82e-05%
2027 | 156 | 156-538 | Tier-1 | Non-HFTD---8 | 3--3 | 5.9075 | 140 | 100% | 34.3358 | 87.94% | 0% | 12.06% | 1.4947 | 0 | 0 | 1.4947 | 0 | 1.3601 | 5.8219 | 0.23362 | 1.3601 | 5.8219 | 0.23362 | 1.5094 | 6.4607 | 0.23362 | 4.353% | 0.018674 | 0.01775 | 1838.6947 | 313.0243 | 338.2317 | 1187.4387 | 1850.2417 | 0 | 0 | 1850.2417 | 4.929e-05%
2027 | 300 | 300-484F | Tier-2 | Tier-2---9 | 4--5 | 10.4561 | 132 | 100% | 754.1323 | 92.41% | 6.882% | 0.7076% | 34.4965 | 0 | 0 | 34.4965 | 0 | 31.3913 | 10.3045 | 3.0464 | 31.3913 | 10.3045 | 3.0464 | 34.8355 | 11.4351 | 3.0464 | 4.574% | 0.039922 | 0.037946 | 18890.1433 | 2594.5618 | 1654.6819 | 14640.8997 | 18964.8043 | 0 | 0 | 18964.8043 | 0.001138%
2027 | 1483 | 1483-39 | Tier-1 | Non-HFTD---18 | 1--1 | 1.3201 | 34 | 100% | 1.247 | 34.85% | 0% | 65.15% | 0.021511 | 0 | 0 | 0.021511 | 0 | 0.019575 | 1.3009 | 0.015047 | 0.019575 | 1.3009 | 0.015047 | 0.021723 | 1.4437 | 0.015047 | 1.725% | 0.0033188 | 0.0031545 | 375.7288 | 1.7167 | 143.7713 | 230.2408 | 388.4768 | 0 | 0 | 388.4768 | 7.094e-07%
2027 | 199 | CB 199 | Tier-1 | Non-HFTD---5 | 3--3 | 5.8392 | 182 | 100% | 86.2492 | 95.28% | 0% | 4.716% | 4.068 | 0 | 0 | 4.068 | 0 | 3.7018 | 5.7545 | 0.64329 | 3.7018 | 5.7545 | 0.64329 | 4.108 | 6.3859 | 0.64329 | 4.717% | 0.019491 | 0.018526 | 4425.0322 | 993.0316 | 124.6693 | 3307.3312 | 4435.8997 | 0 | 0 | 4435.8997 | 0.0001341%
2027 | 549 | CB 549 | Tier-1 | Non-HFTD---11 | 2--2 | 3.6668 | 74 | 100% | 10.14 | 74.51% | 0% | 25.49% | 0.37399 | 0 | 0 | 0.37399 | 0 | 0.34033 | 3.6137 | 0.094178 | 0.34033 | 3.6137 | 0.094178 | 0.37767 | 4.0101 | 0.094178 | 3.688% | 0.010939 | 0.010398 | 926.9394 | 30.6503 | 525.5764 | 370.7127 | 939.2439 | 0 | 0 | 939.2439 | 1.233e-05%
2027 | 277 | CB 277 | Tier-1 | Non-HFTD---11 | 1--4 | 0.46136 | 28 | 100% | 9.2421 | 96.22% | 0% | 3.783% | 0.44017 | 0 | 0 | 0.44017 | 0 | 0.40055 | 0.45467 | 0.88097 | 0.40055 | 0.45467 | 0.88097 | 0.4445 | 0.50456 | 0.88097 | 4.763% | 0.0016702 | 0.0015875 | 5533.5154 | 30.682 | 5156.0762 | 346.7572 | 5544.418 | 0 | 0 | 5544.418 | 1.452e-05%
2027 | 1047 | 1047-36F | Tier-1 | Non-HFTD---14 | 3--1 | 7.665 | 358 | 100% | 7.6285 | 33.56% | 0% | 66.44% | 0.12671 | 0 | 0 | 0.12671 | 0 | 0.1153 | 7.5539 | 0.015264 | 0.1153 | 7.5539 | 0.015264 | 0.12795 | 8.3826 | 0.015264 | 1.661% | 0.020747 | 0.01972 | 367.6979 | 0.66227 | 142.6229 | 224.4127 | 380.4213 | 0 | 0 | 380.4213 | 4.178e-06%
2027 | 510 | CB 510 | Tier-1 | Non-HFTD---11 | 2--2 | 0.63409 | 21 | 100% | 12.2941 | 84.64% | 10.34% | 5.026% | 0.51508 | 0 | 0 | 0.51508 | 0 | 0.46871 | 0.6249 | 0.75006 | 0.46871 | 0.6249 | 0.75006 | 0.52014 | 0.69346 | 0.75006 | 4.19% | 0.012771 | 0.012139 | 962.6446 | 60.1151 | 530.8101 | 371.7194 | 970.3456 | 0 | 0 | 970.3456 | 1.699e-05%
2027 | 1434 | 1434-11 | Tier-1 | Non-HFTD---17 | 1--3 | 0.30362 | 1 | 100% | 1.328 | 86.5% | 0% | 13.5% | 0.056858 | 0 | 0 | 0.056858 | 0 | 0.05174 | 0.29922 | 0.17292 | 0.05174 | 0.29922 | 0.17292 | 0.057417 | 0.33205 | 0.17292 | 4.282% | 0.000755 | 0.00071763 | 1758.899 | 88.6139 | 996.9745 | 673.3106 | 1771.2681 | 0 | 0 | 1771.2681 | 1.875e-06%
2027 | 1180 | CB 1180 | Tier-1 | Non-HFTD---7 | 1--4 | 1.2019 | 76 | 100% | 35.2333 | 97.75% | 0% | 2.252% | 1.7048 | 0 | 0 | 1.7048 | 0 | 1.5513 | 1.1845 | 1.3097 | 1.5513 | 1.1845 | 1.3097 | 1.7215 | 1.3144 | 1.3097 | 4.839% | 0.0039062 | 0.0037128 | 9019.8397 | 919.8579 | 4656.5948 | 3443.387 | 9030.4183 | 0 | 0 | 9030.4183 | 5.622e-05%
2027 | 237 | 237-26F | Tier-2 | Tier-2---10 | 5--4 | 2.4644 | 87 | 100% | 663.2151 | 70.89% | 28.72% | 0.399% | 23.271 | 0 | 0 | 23.271 | 0 | 21.1763 | 2.4287 | 8.7192 | 21.1763 | 2.4287 | 8.7192 | 23.4997 | 2.6952 | 8.7192 | 3.509% | 0.10897 | 0.10358 | 6086.0279 | 695.3102 | 1570.8815 | 3819.8362 | 6178.3065 | 0 | 0 | 6178.3065 | 0.0007674%
2027 | 489 | CB 489 | Tier-1 | Non-HFTD---12 | 3--2 | 5.9438 | 160 | 100% | 14.1275 | 73.98% | 0% | 26.02% | 0.51732 | 0 | 0 | 0.51732 | 0 | 0.47075 | 5.8576 | 0.080366 | 0.47075 | 5.8576 | 0.080366 | 0.5224 | 6.5003 | 0.080366 | 3.662% | 0.016022 | 0.015229 | 881.768 | 0.17267 | 673.1395 | 208.4558 | 893.7185 | 0 | 0 | 893.7185 | 1.706e-05%
2027 | 368 | 368-1057F | Tier-1 | Non-HFTD---12 | 2--2 | 1.2491 | 112 | 100% | 9.345 | 62.09% | 27.57% | 10.34% | 0.28721 | 0 | 0 | 0.28721 | 0 | 0.26136 | 1.2309 | 0.21232 | 0.26136 | 1.2309 | 0.21232 | 0.29004 | 1.366 | 0.21232 | 3.073% | 0.01023 | 0.0097236 | 913.4882 | 55.7905 | 466.091 | 391.6067 | 931.523 | 0 | 0 | 931.523 | 9.471e-06%
2027 | 139 | 139-243AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.24791 | 3 | 100% | 0.28248 | 13.18% | 0% | 86.82% | 0.0018428 | 0 | 0 | 0.0018428 | 0 | 0.0016769 | 0.24432 | 0.0068637 | 0.0016769 | 0.24432 | 0.0068637 | 0.0018609 | 0.27112 | 0.0068637 | 0.6524% | 0.000781 | 0.00074234 | 361.6876 | 0.23629 | 76.193 | 285.2582 | 378.0411 | 0 | 0 | 378.0411 | 6.077e-08%
2027 | 189 | 189-783F | Tier-1 | Non-HFTD---17 | 1--2 | 0.44904 | 7 | 100% | 1.922 | 84.88% | 0% | 15.12% | 0.080752 | 0 | 0 | 0.080752 | 0 | 0.073483 | 0.44253 | 0.16605 | 0.073483 | 0.44253 | 0.16605 | 0.081545 | 0.49108 | 0.16605 | 4.201% | 0.0013618 | 0.0012944 | 1411.3883 | 12.6725 | 1141.007 | 257.7088 | 1422.5046 | 0 | 0 | 1422.5046 | 2.663e-06%
2027 | 140 | 140-481R | Tier-1 | Non-HFTD---6 | 3--3 | 5.1055 | 212 | 100% | 76.5519 | 22.22% | 72.37% | 5.415% | 0.84198 | 0 | 0 | 0.84198 | 0 | 0.76619 | 5.0315 | 0.15228 | 0.76619 | 5.0315 | 0.15228 | 0.85025 | 5.5835 | 0.15228 | 1.1% | 0.022011 | 0.020921 | 3477.9247 | 83.6911 | 2703.5551 | 690.6785 | 3618.8026 | 0 | 0 | 3618.8026 | 2.777e-05%
2027 | 358 | 358-33 | Tier-3 | Tier-3---15 | 5--4 | 0.45755 | 58 | 100% | 1344.6436 | 99.66% | 0.3079% | 0.03174% | 66.3338 | 0 | 0 | 66.3338 | 0 | 60.3628 | 0.45092 | 133.8663 | 60.3628 | 0.45092 | 133.8663 | 66.9857 | 0.50039 | 133.8663 | 4.933% | 0.14298 | 0.1359 | 9404.72 | 1885.3527 | 29.6558 | 7489.7115 | 9406.3837 | 0 | 0 | 9406.3837 | 0.002187%
2027 | 214 | 214-536R | Tier-3 | Tier-3---17 | 4--4 | 2.6683 | 454 | 100% | 513.3291 | 98.71% | 0.8845% | 0.4005% | 25.0833 | 0 | 0 | 25.0833 | 0 | 22.8254 | 2.6296 | 8.68 | 22.8254 | 2.6296 | 8.68 | 25.3298 | 2.9182 | 8.68 | 4.886% | 0.053744 | 0.051083 | 9551.4463 | 1436.3496 | 158.5376 | 7956.5591 | 9557.8383 | 0 | 0 | 9557.8383 | 0.0008272%
2027 | 221 | 221-788 | Tier-3 | Tier-3---12 | 5--5 | 3.6174 | 384 | 100% | 4481.9143 | 99.45% | 0.5095% | 0.04337% | 220.6282 | 0 | 0 | 220.6282 | 0 | 200.7686 | 3.565 | 56.3167 | 200.7686 | 3.565 | 56.3167 | 222.7965 | 3.9561 | 56.3167 | 4.923% | 0.18975 | 0.18036 | 23620.3007 | 4014.0972 | 176.6894 | 19429.514 | 23627.1015 | 0 | 0 | 23627.1015 | 0.007276%
2027 | 799 | 799-504R | Tier-2 | Tier-2---15 | 1--5 | 1.3381 | 157 | 100% | 127.4062 | 99.28% | 0% | 0.716% | 6.2614 | 0 | 0 | 6.2614 | 0 | 5.6978 | 1.3187 | 4.3209 | 5.6978 | 1.3187 | 4.3209 | 6.323 | 1.4634 | 4.3209 | 4.915% | 0.0046964 | 0.0044639 | 27128.474 | 7563.5291 | 572.4903 | 18992.4546 | 27138.5902 | 0 | 0 | 27138.5902 | 0.0002065%
2027 | 548 | CB 548 | Tier-1 | Non-HFTD---10 | 2--2 | 3.9959 | 122 | 100% | 15.6121 | 79.23% | 0% | 20.77% | 0.61227 | 0 | 0 | 0.61227 | 0 | 0.55716 | 3.9379 | 0.14148 | 0.55716 | 3.9379 | 0.14148 | 0.61829 | 4.37 | 0.14148 | 3.922% | 0.012194 | 0.011591 | 1280.2923 | 2.5369 | 1024.1977 | 253.5578 | 1294.1425 | 0 | 0 | 1294.1425 | 2.019e-05%
2027 | 212 | 212-638R | Tier-2 | Tier-2---11 | 5--4 | 4.2816 | 41 | 100% | 609.7797 | 99.07% | 0.4924% | 0.4406% | 29.9025 | 0 | 0 | 29.9025 | 0 | 27.2109 | 4.2195 | 6.4488 | 27.2109 | 4.2195 | 6.4488 | 30.1964 | 4.6825 | 6.4488 | 4.904% | 0.10708 | 0.10177 | 5694.8842 | 618.0557 | 46.4103 | 5030.4182 | 5697.6511 | 0 | 0 | 5697.6511 | 0.0009861%
2027 | 524 | 524-27R | Tier-3 | Tier-3---4 | 4--5 | 14.5985 | 959 | 100% | 11317.6942 | 99.77% | 0.1414% | 0.08951% | 558.9321 | 0 | 0 | 558.9321 | 0 | 508.6206 | 14.3868 | 35.3532 | 508.6206 | 14.3868 | 35.3532 | 564.4253 | 15.9653 | 35.3532 | 4.939% | 0.060207 | 0.057227 | 187979.0829 | 37296.5794 | 584.5714 | 150097.9321 | 188001.69 | 0 | 0 | 188001.69 | 0.01843%
2027 | 95 | 95-29R | Tier-1 | Non-HFTD---6 | 4--3 | 9.681 | 422 | 100% | 60.1265 | 25.03% | 65.18% | 9.791% | 0.74481 | 0 | 0 | 0.74481 | 0 | 0.67777 | 9.5407 | 0.07104 | 0.67777 | 9.5407 | 0.07104 | 0.75213 | 10.5874 | 0.07104 | 1.239% | 0.032867 | 0.03124 | 1829.3755 | 34.6804 | 1347.9039 | 446.7912 | 1900.8041 | 0 | 0 | 1900.8041 | 2.456e-05%
2027 | 210 | 210-9R | Tier-2 | Tier-2---13 | 5--2 | 2.7176 | 192 | 100% | 317.7725 | 50.82% | 48.53% | 0.6462% | 7.9945 | 0 | 0 | 7.9945 | 0 | 7.2749 | 2.6782 | 2.7163 | 7.2749 | 2.6782 | 2.7163 | 8.0731 | 2.972 | 2.7163 | 2.516% | 0.31397 | 0.29843 | 1012.1143 | 65.1884 | 453.8469 | 493.0789 | 1038.0342 | 0 | 0 | 1038.0342 | 0.0002636%
2027 | 548 | 548-12F | Tier-1 | Non-HFTD---20 | 1--1 | 0.3271 | 5 | 100% | 0.21703 | 18.87% | 0% | 81.13% | 0.0020269 | 0 | 0 | 0.0020269 | 0 | 0.0018444 | 0.32235 | 0.0057217 | 0.0018444 | 0.32235 | 0.0057217 | 0.0020468 | 0.35772 | 0.0057217 | 0.9339% | 0.0007594 | 0.00072181 | 285.7879 | 6.0125 | 39.2503 | 240.5251 | 297.8631 | 0 | 0 | 297.8631 | 6.684e-08%
2027 | 775 | CB 775 | Tier-1 | Non-HFTD---17 | 1--2 | 0.29205 | 9 | 100% | 1.2409 | 63.86% | 0% | 36.14% | 0.039223 | 0 | 0 | 0.039223 | 0 | 0.035693 | 0.28781 | 0.12401 | 0.035693 | 0.28781 | 0.12401 | 0.039609 | 0.31939 | 0.12401 | 3.161% | 0.0013874 | 0.0013187 | 894.417 | 24.4609 | 451.2287 | 418.7273 | 911.2529 | 0 | 0 | 911.2529 | 1.293e-06%
2027 | 233 | CB 233 | Tier-2 | Tier-2---4 | 4--5 | 18.8384 | 1884 | 100% | 4127.6955 | 98.74% | 0.928% | 0.3343% | 201.7417 | 0 | 0 | 201.7417 | 0 | 183.5822 | 18.5653 | 9.8885 | 183.5822 | 18.5653 | 9.8885 | 203.7244 | 20.6022 | 9.8885 | 4.888% | 0.075451 | 0.071716 | 54706.8242 | 9492.9943 | 1134.8954 | 44078.9345 | 54742.7891 | 0 | 0 | 54742.7891 | 0.006653%
2027 | 1173 | 1173-68 | Tier-1 | Non-HFTD---13 | 1--3 | 1.1887 | 126 | 100% | 6.4999 | 85.9% | 0% | 14.1% | 0.27639 | 0 | 0 | 0.27639 | 0 | 0.25151 | 1.1714 | 0.2147 | 0.25151 | 1.1714 | 0.2147 | 0.27911 | 1.3 | 0.2147 | 4.252% | 0.0037692 | 0.0035826 | 1724.4769 | 400.6816 | 34.3759 | 1289.4193 | 1737.1359 | 0 | 0 | 1737.1359 | 9.114e-06%
2027 | 1174 | CB 1174 | Tier-1 | Non-HFTD---20 | 1--1 | 0.2536 | 0 | 100% | 0.3405 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.24992 | 0 | 0 | 0.24992 | 0 | 0 | 0.27734 | 0 | 0% | 0.0011044 | 0.0010497 | 308.3124 | 0.232 | 28.0073 | 280.0731 | 324.3686 | 0 | 0 | 324.3686 | 0%
2027 | NC4 | CB NC4 | Tier-1 | Non-HFTD---14 | 3--1 | 6.1544 | 189 | 100% | 6.4492 | 25.78% | 0% | 74.22% | 0.082286 | 0 | 0 | 0.082286 | 0 | 0.074879 | 6.0651 | 0.012346 | 0.074879 | 6.0651 | 0.012346 | 0.083095 | 6.7306 | 0.012346 | 1.276% | 0.017682 | 0.016806 | 364.7392 | 1.3706 | 111.4291 | 251.9395 | 378.8379 | 0 | 0 | 378.8379 | 2.713e-06%
2027 | 123 | 123-557 | Tier-1 | Non-HFTD---19 | 1--2 | 0.005303 | 3 | 100% | 0.044985 | 24.83% | 0% | 75.17% | 0.00055285 | 0 | 0 | 0.00055285 | 0 | 0.00050309 | 0.0052261 | 0.096264 | 0.00050309 | 0.0052261 | 0.096264 | 0.00055828 | 0.0057995 | 0.096264 | 1.229% | 6.14e-05 | 5.8361e-05 | 732.6611 | 11.0369 | 166.3248 | 555.2994 | 761.3435 | 0 | 0 | 761.3435 | 1.823e-08%
2027 | 570 | 570-489F | Tier-1 | Non-HFTD---20 | 1--1 | 0.060397 | 11 | 100% | 0.036046 | 6.552% | 0% | 93.45% | 0.0001169 | 0 | 0 | 0.0001169 | 0 | 0.00010638 | 0.059521 | 0.0017872 | 0.00010638 | 0.059521 | 0.0017872 | 0.00011805 | 0.066052 | 0.0017872 | 0.3243% | 0.0001616 | 0.0001536 | 223.0577 | 0.15685 | 33.549 | 189.3518 | 233.913 | 0 | 0 | 233.913 | 3.855e-09%
2027 | 86 | 86-1058F | Tier-1 | Non-HFTD---19 | 1--1 | 0.34811 | 19 | 100% | 0.46174 | 17.14% | 0% | 82.86% | 0.0039179 | 0 | 0 | 0.0039179 | 0 | 0.0035652 | 0.34306 | 0.010392 | 0.0035652 | 0.34306 | 0.010392 | 0.0039564 | 0.38071 | 0.010392 | 0.8485% | 0.0012994 | 0.0012351 | 355.352 | 8.5613 | 36.0451 | 310.7455 | 370.6858 | 0 | 0 | 370.6858 | 1.292e-07%
2027 | 792 | 792-1173F | Tier-1 | Non-HFTD---12 | 3--2 | 0.42482 | 8 | 100% | 9.7258 | 44.88% | 50.38% | 4.732% | 0.21608 | 0 | 0 | 0.21608 | 0 | 0.19663 | 0.41866 | 0.46967 | 0.19663 | 0.41866 | 0.46967 | 0.21821 | 0.46459 | 0.46967 | 2.222% | 0.018988 | 0.018048 | 512.2147 | 5.2953 | 409.626 | 97.2933 | 526.9171 | 0 | 0 | 526.9171 | 7.126e-06%
2027 | 157 | 157-1928R | Tier-3 | Tier-3---11 | 5--4 | 3.1864 | 101 | 100% | 3052.6745 | 99.07% | 0.8703% | 0.06204% | 149.6985 | 0 | 0 | 149.6985 | 0 | 136.2236 | 3.1402 | 43.381 | 136.2236 | 3.1402 | 43.381 | 151.1698 | 3.4847 | 43.381 | 4.904% | 0.2812 | 0.26728 | 10855.7291 | 1703.869 | 84.5376 | 9067.3225 | 10861.0002 | 0 | 0 | 10861.0002 | 0.004937%
2027 | 241 | 241-570 | Tier-1 | Non-HFTD---2 | 5--4 | 18.8601 | 1038 | 100% | 1283.0682 | 34.99% | 64.02% | 0.9973% | 22.221 | 0 | 0 | 22.221 | 0 | 20.2208 | 18.5866 | 1.0879 | 20.2208 | 18.5866 | 1.0879 | 22.4393 | 20.6259 | 1.0879 | 1.732% | 0.15951 | 0.15162 | 8043.669 | 557.5746 | 4862.2355 | 2623.8589 | 8316.0062 | 0 | 0 | 8316.0062 | 0.0007328%
2027 | 1021 | 1021-883R | Tier-3 | Tier-3---16 | 5--4 | 0.68239 | 74 | 100% | 1386.6299 | 99.58% | 0.3809% | 0.03987% | 68.3494 | 0 | 0 | 68.3494 | 0 | 62.197 | 0.67249 | 92.4873 | 62.197 | 0.67249 | 92.4873 | 69.0211 | 0.74628 | 92.4873 | 4.929% | 0.10042 | 0.095448 | 13808.4689 | 2223.2077 | 49.0594 | 11536.2018 | 13811.4949 | 0 | 0 | 13811.4949 | 0.002254%
2027 | 55 | 55-483F | Tier-1 | Non-HFTD---11 | 2--2 | 2.7087 | 114 | 100% | 9.2861 | 71.18% | 0% | 28.82% | 0.32719 | 0 | 0 | 0.32719 | 0 | 0.29774 | 2.6694 | 0.11154 | 0.29774 | 2.6694 | 0.11154 | 0.3304 | 2.9623 | 0.11154 | 3.523% | 0.009502 | 0.0090317 | 977.2747 | 1.1382 | 715.4551 | 260.6814 | 991.9422 | 0 | 0 | 991.9422 | 1.079e-05%
2027 | 456 | 456-5 | Tier-1 | Non-HFTD---1 | 3--5 | 7.8148 | 407 | 100% | 584.4392 | 99.09% | 0% | 0.9055% | 28.6678 | 0 | 0 | 28.6678 | 0 | 26.0873 | 7.7015 | 3.3873 | 26.0873 | 7.7015 | 3.3873 | 28.9495 | 8.5464 | 3.3873 | 4.905% | 0.025435 | 0.024176 | 22978.1161 | 5310.5669 | 175.0323 | 17492.5169 | 22988.9519 | 0 | 0 | 22988.9519 | 0.0009454%
2027 | DM2 | CB DM2 | Tier-1 | Non-HFTD---3 | 3--3 | 4.8831 | 426 | 100% | 93.2156 | 56.52% | 39.8% | 3.676% | 2.608 | 0 | 0 | 2.608 | 0 | 2.3732 | 4.8123 | 0.49315 | 2.3732 | 4.8123 | 0.49315 | 2.6336 | 5.3403 | 0.49315 | 2.798% | 0.024472 | 0.023261 | 3809.0413 | 343.1954 | 1456.0262 | 2009.8197 | 3895.2895 | 0 | 0 | 3895.2895 | 8.6e-05%
2027 | 261 | CB 261 | Tier-1 | Non-HFTD---11 | 2--2 | 1.4223 | 54 | 100% | 8.7767 | 85.72% | 0% | 14.28% | 0.37239 | 0 | 0 | 0.37239 | 0 | 0.33887 | 1.4017 | 0.24176 | 0.33887 | 1.4017 | 0.24176 | 0.37605 | 1.5555 | 0.24176 | 4.243% | 0.0054352 | 0.0051662 | 1614.782 | 193.7429 | 186.2869 | 1234.7522 | 1626.7947 | 0 | 0 | 1626.7947 | 1.228e-05%
2027 | 93 | 93-10R | Tier-1 | Non-HFTD---2 | 4--4 | 9.5466 | 770 | 100% | 302.3321 | 90.71% | 7.303% | 1.988% | 13.575 | 0 | 0 | 13.575 | 0 | 12.353 | 9.4082 | 1.313 | 12.353 | 9.4082 | 1.313 | 13.7084 | 10.4404 | 1.313 | 4.49% | 0.035815 | 0.034042 | 8441.494 | 1852.3748 | 638.1878 | 5950.9314 | 8482.34 | 0 | 0 | 8482.34 | 0.0004477%
2027 | 368 | 368-24 | Tier-1 | Non-HFTD---3 | 3--4 | 6.8786 | 219 | 100% | 131.8203 | 5.447% | 90.51% | 4.044% | 0.35545 | 0 | 0 | 0.35545 | 0 | 0.32346 | 6.7789 | 0.047715 | 0.32346 | 6.7789 | 0.047715 | 0.35894 | 7.5227 | 0.047715 | 0.2696% | 0.025227 | 0.023978 | 5225.4485 | 5.586 | 4642.0429 | 577.8196 | 5482.7545 | 0 | 0 | 5482.7545 | 1.172e-05%
2027 | 715 | CB 715 | Tier-1 | Non-HFTD---5 | 2--4 | 2.2625 | 177 | 100% | 64.2152 | 97.59% | 0% | 2.408% | 3.1021 | 0 | 0 | 3.1021 | 0 | 2.8229 | 2.2297 | 1.2661 | 2.8229 | 2.2297 | 1.2661 | 3.1326 | 2.4743 | 1.2661 | 4.831% | 0.0088918 | 0.0084517 | 7221.8396 | 1455.0968 | 1510.162 | 4256.5807 | 7230.8958 | 0 | 0 | 7230.8958 | 0.0001023%
2027 | 1030 | 1030-20R | Tier-3 | Tier-3---3 | 5--5 | 15.7168 | 1396 | 100% | 25318.462 | 99.14% | 0.8163% | 0.04139% | 1242.5149 | 0 | 0 | 1242.5149 | 0 | 1130.6716 | 15.4889 | 72.9987 | 1130.6716 | 15.4889 | 72.9987 | 1254.7263 | 17.1883 | 72.9987 | 4.908% | 0.28668 | 0.27249 | 88316.4782 | 15740.2144 | 654.513 | 71921.7508 | 88355.9257 | 0 | 0 | 88355.9257 | 0.04097%
2027 | EOS2 | CB EOS2 | Tier-1 | Non-HFTD---10 | 4--2 | 15.5156 | 504 | 100% | 23.2282 | 49.67% | 0% | 50.33% | 0.57106 | 0 | 0 | 0.57106 | 0 | 0.51965 | 15.2906 | 0.033985 | 0.51965 | 15.2906 | 0.033985 | 0.57667 | 16.9682 | 0.033985 | 2.458% | 0.044799 | 0.042581 | 518.4987 | 9.3302 | 225.2181 | 283.9504 | 532.0901 | 0 | 0 | 532.0901 | 1.883e-05%
2027 | 794 | 794-15 | Tier-1 | Non-HFTD---6 | 4--3 | 4.1462 | 121 | 100% | 86.3748 | 7.031% | 89.79% | 3.183% | 0.30062 | 0 | 0 | 0.30062 | 0 | 0.27356 | 4.0861 | 0.066949 | 0.27356 | 4.0861 | 0.066949 | 0.30357 | 4.5344 | 0.066949 | 0.348% | 0.02911 | 0.027669 | 2967.1473 | 28.0705 | 2440.5619 | 498.5149 | 3110.8053 | 0 | 0 | 3110.8053 | 9.913e-06%
2027 | 583 | 583-318F | Tier-1 | Non-HFTD---4 | 2--5 | 2.2297 | 144 | 100% | 153.5608 | 99.44% | 0% | 0.5645% | 7.5583 | 0 | 0 | 7.5583 | 0 | 6.878 | 2.1974 | 3.1301 | 6.878 | 2.1974 | 3.1301 | 7.6326 | 2.4385 | 3.1301 | 4.922% | 0.0076984 | 0.0073173 | 19947.1031 | 4677.56 | 10.2291 | 15259.3139 | 19952.9673 | 0 | 0 | 19952.9673 | 0.0002492%
2027 | 124 | 124-206R | Tier-1 | Non-HFTD---14 | 2--2 | 2.8064 | 55 | 100% | 5.0289 | 52.24% | 0% | 47.76% | 0.13003 | 0 | 0 | 0.13003 | 0 | 0.11833 | 2.7657 | 0.042784 | 0.11833 | 2.7657 | 0.042784 | 0.13131 | 3.0692 | 0.042784 | 2.586% | 0.0096408 | 0.0091636 | 521.6316 | 2.9356 | 277.9653 | 240.7307 | 534.6068 | 0 | 0 | 534.6068 | 4.288e-06%
2027 | 922 | 922-1143F | Tier-1 | Non-HFTD---9 | 2--3 | 2.9475 | 109 | 100% | 20.705 | 88.62% | 0% | 11.38% | 0.9083 | 0 | 0 | 0.9083 | 0 | 0.82654 | 2.9048 | 0.28454 | 0.82654 | 2.9048 | 0.28454 | 0.91722 | 3.2235 | 0.28454 | 4.387% | 0.0096708 | 0.0091921 | 2140.9782 | 289.3821 | 148.841 | 1702.7551 | 2153.6629 | 0 | 0 | 2153.6629 | 2.995e-05%
2027 | 212 | 212-758R | Tier-2 | Tier-2---8 | 5--4 | 9.6756 | 274 | 100% | 1482.4618 | 97.27% | 2.316% | 0.4117% | 71.3804 | 0 | 0 | 71.3804 | 0 | 64.9552 | 9.5353 | 6.8121 | 64.9552 | 9.5353 | 6.8121 | 72.0819 | 10.5815 | 6.8121 | 4.815% | 0.1427 | 0.13564 | 10388.4417 | 1332.9551 | 229.8859 | 8825.6006 | 10403.1976 | 0 | 0 | 10403.1976 | 0.002354%
2027 | 277 | 277-48 | Tier-1 | Non-HFTD---2 | 4--4 | 10.0475 | 283 | 100% | 230.0219 | 5.859% | 91.22% | 2.918% | 0.66709 | 0 | 0 | 0.66709 | 0 | 0.60704 | 9.9019 | 0.061306 | 0.60704 | 9.9019 | 0.061306 | 0.67365 | 10.9883 | 0.061306 | 0.29% | 0.043712 | 0.041548 | 5262.2134 | 55.7509 | 4495.9402 | 710.5223 | 5520.2023 | 0 | 0 | 5520.2023 | 2.2e-05%
2027 | 1073 | 1073-874F | Tier-2 | Tier-2---20 | 3--3 | 1.5256 | 31 | 100% | 40.9949 | 23.55% | 73.64% | 2.81% | 0.47782 | 0 | 0 | 0.47782 | 0 | 0.43481 | 1.5035 | 0.28921 | 0.43481 | 1.5035 | 0.28921 | 0.48252 | 1.6684 | 0.28921 | 1.166% | 0.021565 | 0.020497 | 1901.027 | 61.7007 | 1198.5032 | 640.8231 | 1976.7168 | 0 | 0 | 1976.7168 | 1.576e-05%
2027 | 276 | 276-158R | Tier-1 | Non-HFTD---3 | 4--3 | 15.2584 | 300 | 100% | 188.0595 | 4.698% | 89.13% | 6.174% | 0.43729 | 0 | 0 | 0.43729 | 0 | 0.39793 | 15.0371 | 0.026463 | 0.39793 | 15.0371 | 0.026463 | 0.44159 | 16.687 | 0.026463 | 0.2325% | 0.060308 | 0.057323 | 3118.2966 | 14.6042 | 2673.243 | 430.4493 | 3273.0622 | 0 | 0 | 3273.0622 | 1.442e-05%
2027 | 95 | 95-36F | Tier-1 | Non-HFTD---9 | 3--2 | 3.9422 | 302 | 100% | 25.869 | 56.36% | 33.85% | 9.785% | 0.72172 | 0 | 0 | 0.72172 | 0 | 0.65675 | 3.8851 | 0.16905 | 0.65675 | 3.8851 | 0.16905 | 0.72881 | 4.3113 | 0.16905 | 2.79% | 0.016067 | 0.015272 | 1610.0531 | 145.5142 | 538.7895 | 925.7494 | 1646.6431 | 0 | 0 | 1646.6431 | 2.38e-05%
2027 | 1021 | 1021-25R | Tier-3 | Tier-3---2 | 5--5 | 6.9741 | 649 | 100% | 18825.6899 | 99.7% | 0.2782% | 0.02306% | 929.0645 | 0 | 0 | 929.0645 | 0 | 845.436 | 6.8729 | 123.0094 | 845.436 | 6.8729 | 123.0094 | 938.1953 | 7.627 | 123.0094 | 4.935% | 0.12361 | 0.11749 | 152300.0709 | 28596.6216 | 387.4212 | 123316.0281 | 152323.9639 | 0 | 0 | 152323.9639 | 0.03064%
2027 | 142 | CB 142 | Tier-1 | Non-HFTD---3 | 4--3 | 10.8841 | 244 | 100% | 108.6332 | 57.02% | 36.05% | 6.937% | 3.066 | 0 | 0 | 3.066 | 0 | 2.7901 | 10.7263 | 0.26011 | 2.7901 | 10.7263 | 0.26011 | 3.0962 | 11.9032 | 0.26011 | 2.822% | 0.039142 | 0.037205 | 2775.333 | 244.59 | 1527.2947 | 1003.4483 | 2837.4565 | 0 | 0 | 2837.4565 | 0.0001011%
2027 | 520 | 520-1509R | Tier-2 | Tier-2---5 | 5--4 | 15.3043 | 1539 | 100% | 3413.9118 | 92.72% | 6.994% | 0.2858% | 156.6869 | 0 | 0 | 156.6869 | 0 | 142.5829 | 15.0824 | 9.4536 | 142.5829 | 15.0824 | 9.4536 | 158.2268 | 16.7373 | 9.4536 | 4.59% | 0.28561 | 0.27147 | 11953.1797 | 1649.8318 | 753.7764 | 9549.5714 | 11998.4952 | 0 | 0 | 11998.4952 | 0.005167%
2027 | 723 | 723-377 | Tier-1 | Non-HFTD---19 | 1--1 | 0.093039 | 6 | 100% | 0.11767 | 36.99% | 0% | 63.01% | 0.0021545 | 0 | 0 | 0.0021545 | 0 | 0.0019605 | 0.09169 | 0.021382 | 0.0019605 | 0.09169 | 0.021382 | 0.0021756 | 0.10175 | 0.021382 | 1.831% | 0.0002816 | 0.00026766 | 417.8452 | 1.6299 | 169.7356 | 246.4797 | 431.5565 | 0 | 0 | 431.5565 | 7.105e-08%
2027 | 394 | CB 394 | Tier-1 | Non-HFTD---2 | 4--3 | 0.54963 | 25 | 100% | 400.0096 | 2.606% | 97.29% | 0.1022% | 0.51601 | 0 | 0 | 0.51601 | 0 | 0.46956 | 0.54166 | 0.86689 | 0.46956 | 0.54166 | 0.86689 | 0.52108 | 0.60109 | 0.86689 | 0.129% | 0.091335 | 0.086814 | 4379.6067 | 27.9554 | 3843.5806 | 508.0707 | 4601.7434 | 0 | 0 | 4601.7434 | 1.702e-05%
2027 | 991 | 991-1206R | Tier-2 | Tier-2---4 | 4--5 | 9.2129 | 306 | 100% | 4576.7911 | 99.78% | 0.09876% | 0.1221% | 226.0508 | 0 | 0 | 226.0508 | 0 | 205.7031 | 9.0793 | 22.6562 | 205.7031 | 9.0793 | 22.6562 | 228.2724 | 10.0755 | 22.6562 | 4.939% | 0.063785 | 0.060628 | 71752.9575 | 17377.7181 | 68.9781 | 54306.2613 | 71761.2112 | 0 | 0 | 71761.2112 | 0.007454%
2027 | 210 | 210-394R | Tier-2 | Tier-2---16 | 5--2 | 3.6236 | 252 | 100% | 170.5929 | 70.47% | 28.1% | 1.432% | 5.9509 | 0 | 0 | 5.9509 | 0 | 5.4153 | 3.5711 | 1.5164 | 5.4153 | 3.5711 | 1.5164 | 6.0094 | 3.9629 | 1.5164 | 3.488% | 0.31841 | 0.30265 | 535.7584 | 42.1364 | 121.741 | 371.881 | 543.997 | 0 | 0 | 543.997 | 0.0001962%
2027 | 324 | CB 324 | Tier-1 | Non-HFTD---7 | 1--4 | 1.1407 | 37 | 100% | 29.9941 | 97.06% | 0% | 2.94% | 1.4411 | 0 | 0 | 1.4411 | 0 | 1.3113 | 1.1242 | 1.1665 | 1.3113 | 1.1242 | 1.1665 | 1.4552 | 1.2475 | 1.1665 | 4.804% | 0.0044058 | 0.0041877 | 6807.8599 | 1023.5636 | 2848.5992 | 2935.6971 | 6818.2819 | 0 | 0 | 6818.2819 | 4.752e-05%
2027 | 448 | 448-735R | Tier-3 | Tier-3---18 | 5--2 | 8.2068 | 162 | 100% | 630.7627 | 79.12% | 20.09% | 0.7869% | 24.7041 | 0 | 0 | 24.7041 | 0 | 22.4804 | 8.0878 | 2.7795 | 22.4804 | 8.0878 | 2.7795 | 24.9469 | 8.9752 | 2.7795 | 3.917% | 0.54202 | 0.51519 | 1163.7353 | 117.1961 | 208.0615 | 838.4777 | 1176.3882 | 0 | 0 | 1176.3882 | 0.0008147%
2027 | 78 | 78-782R | Tier-3 | Tier-3---7 | 5--5 | 1.7152 | 35 | 100% | 7202.3158 | 99.51% | 0.4709% | 0.01666% | 354.7762 | 0 | 0 | 354.7762 | 0 | 322.8415 | 1.6903 | 190.9985 | 322.8415 | 1.6903 | 190.9985 | 358.263 | 1.8757 | 190.9985 | 4.926% | 0.33808 | 0.32134 | 21303.7357 | 3625.7073 | 90.139 | 17587.8894 | 21309.1455 | 0 | 0 | 21309.1455 | 0.0117%
2027 | 151 | 151-97 | Tier-1 | Non-HFTD---20 | 1--1 | 0.20303 | 3 | 100% | 0.093775 | 23.98% | 0% | 76.02% | 0.001113 | 0 | 0 | 0.001113 | 0 | 0.0010128 | 0.20009 | 0.005062 | 0.0010128 | 0.20009 | 0.005062 | 0.001124 | 0.22204 | 0.005062 | 1.187% | 0.0004212 | 0.00040035 | 222.6384 | 0.12736 | 68.7596 | 153.7515 | 231.4528 | 0 | 0 | 231.4528 | 3.67e-08%
2027 | 350 | 350-2201R | Tier-3 | Tier-3---4 | 5--5 | 14.5687 | 1159 | 100% | 13521.7454 | 99.28% | 0.6466% | 0.06915% | 664.5359 | 0 | 0 | 664.5359 | 0 | 604.7186 | 14.3575 | 42.1187 | 604.7186 | 14.3575 | 42.1187 | 671.067 | 15.9328 | 42.1187 | 4.915% | 0.1241 | 0.11796 | 108955.4794 | 20355.5322 | 658.7237 | 87941.2235 | 108996.0902 | 0 | 0 | 108996.0902 | 0.02191%
2027 | GS1 | CB GS1 | Tier-1 | Non-HFTD---10 | 3--2 | 1.6765 | 71 | 100% | 15.4311 | 0.9691% | 90.27% | 8.765% | 0.0074024 | 0 | 0 | 0.0074024 | 0 | 0.0067361 | 1.6522 | 0.0040771 | 0.0067361 | 1.6522 | 0.0040771 | 0.0074751 | 1.8334 | 0.0040771 | 0.04797% | 0.019954 | 0.018967 | 773.3185 | 0.96411 | 654.1164 | 118.238 | 813.201 | 0 | 0 | 813.201 | 2.441e-07%
2027 | BK4 | CB BK4 | Tier-1 | Non-HFTD---8 | 3--2 | 2.4461 | 111 | 100% | 27.9552 | 2.318% | 91.59% | 6.093% | 0.032081 | 0 | 0 | 0.032081 | 0 | 0.029193 | 2.4106 | 0.01211 | 0.029193 | 2.4106 | 0.01211 | 0.032396 | 2.6751 | 0.01211 | 0.1148% | 0.017152 | 0.016303 | 1629.8314 | 2.4593 | 1406.2531 | 221.119 | 1712.7417 | 0 | 0 | 1712.7417 | 1.058e-06%
2027 | 95 | 95-1353F | Tier-1 | Non-HFTD---19 | 1--2 | 0.0064394 | 0 | 100% | 0.032887 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.006346 | 0 | 0 | 0.006346 | 0 | 0 | 0.0070423 | 0 | 0% | 4.94e-05 | 4.6955e-05 | 665.7292 | 0.50094 | 60.4753 | 604.753 | 700.399 | 0 | 0 | 700.399 | 0%
2027 | 295 | 295-1203F | Tier-2 | Tier-2---21 | 1--2 | 0.48803 | 33 | 100% | 0.80448 | 60.49% | 0% | 39.51% | 0.02409 | 0 | 0 | 0.02409 | 0 | 0.021921 | 0.48095 | 0.045579 | 0.021921 | 0.48095 | 0.045579 | 0.024326 | 0.53372 | 0.045579 | 2.994% | 0.0013362 | 0.0012701 | 602.062 | 79.8078 | 41.8021 | 480.452 | 614.4487 | 0 | 0 | 614.4487 | 7.944e-07%
2027 | 287 | 287-1118 | Tier-2 | Tier-2---17 | 2--4 | 0.3572 | 93 | 100% | 43.5784 | 73.95% | 25.25% | 0.8076% | 1.5951 | 0 | 0 | 1.5951 | 0 | 1.4515 | 0.35202 | 4.1235 | 1.4515 | 0.35202 | 4.1235 | 1.6108 | 0.39064 | 4.1235 | 3.66% | 0.0072086 | 0.0068518 | 6045.3323 | 731.9415 | 1415.1289 | 3898.2619 | 6127.3544 | 0 | 0 | 6127.3544 | 5.26e-05%
2027 | 858 | 858-14 | Tier-2 | Tier-2---12 | 2--5 | 3.2698 | 298 | 100% | 411.6965 | 99.51% | 0% | 0.4896% | 20.2792 | 0 | 0 | 20.2792 | 0 | 18.4538 | 3.2224 | 5.7267 | 18.4538 | 3.2224 | 5.7267 | 20.4785 | 3.576 | 5.7267 | 4.926% | 0.010043 | 0.0095457 | 40994.194 | 8631.9946 | 63.0219 | 32299.1775 | 41004.6459 | 0 | 0 | 41004.6459 | 0.0006687%
2027 | 1438 | CB 1438 | Tier-1 | Non-HFTD---10 | 4--2 | 13.0695 | 540 | 100% | 23.5165 | 61.83% | 0% | 38.17% | 0.71979 | 0 | 0 | 0.71979 | 0 | 0.655 | 12.88 | 0.050854 | 0.655 | 12.88 | 0.050854 | 0.72686 | 14.2931 | 0.050854 | 3.061% | 0.042229 | 0.040138 | 556.8862 | 44.3045 | 160.7551 | 351.8266 | 567.9549 | 0 | 0 | 567.9549 | 2.374e-05%
2027 | 139 | 139-426F | Tier-1 | Non-HFTD---13 | 1--2 | 1.0122 | 8 | 100% | 7.5054 | 85.27% | 0% | 14.73% | 0.31681 | 0 | 0 | 0.31681 | 0 | 0.28829 | 0.99748 | 0.28902 | 0.28829 | 0.99748 | 0.28902 | 0.31992 | 1.1069 | 0.28902 | 4.221% | 0.0044324 | 0.004213 | 1693.3052 | 0.18763 | 1466.5978 | 226.5198 | 1706.2913 | 0 | 0 | 1706.2913 | 1.045e-05%
2027 | 775 | 775-187AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.53754 | 21 | 100% | 0.5948 | 11.69% | 0% | 88.31% | 0.0034422 | 0 | 0 | 0.0034422 | 0 | 0.0031323 | 0.52974 | 0.0059129 | 0.0031323 | 0.52974 | 0.0059129 | 0.003476 | 0.58786 | 0.0059129 | 0.5787% | 0.0018144 | 0.0017246 | 327.8194 | 2.8623 | 48.4676 | 276.4895 | 342.8956 | 0 | 0 | 342.8956 | 1.135e-07%
2027 | 166 | 166-465F | Tier-1 | Non-HFTD---20 | 1--1 | 0.70302 | 35 | 100% | 0.54405 | 10.51% | 0% | 89.49% | 0.0028298 | 0 | 0 | 0.0028298 | 0 | 0.0025751 | 0.69283 | 0.0037168 | 0.0025751 | 0.69283 | 0.0037168 | 0.0028576 | 0.76884 | 0.0037168 | 0.5201% | 0.0018838 | 0.0017906 | 288.8062 | 0.19448 | 53.8256 | 234.7861 | 302.2662 | 0 | 0 | 302.2662 | 9.332e-08%
2027 | 66 | 66-1213R | Tier-1 | Non-HFTD---1 | 4--5 | 16.7053 | 4693 | 100% | 5312.2676 | 97.77% | 1.999% | 0.2313% | 257.0917 | 0 | 0 | 257.0917 | 0 | 233.9499 | 16.463 | 14.2106 | 233.9499 | 16.463 | 14.2106 | 259.6184 | 18.2693 | 14.2106 | 4.84% | 0.075145 | 0.071425 | 70693.7485 | 12854.9773 | 1446.2382 | 56392.533 | 70775.8701 | 0 | 0 | 70775.8701 | 0.008478%
2027 | 75 | 75-996R | Tier-2 | Tier-2---7 | 4--5 | 10.9093 | 781 | 100% | 2211.1377 | 99.23% | 0.4312% | 0.3416% | 108.6055 | 0 | 0 | 108.6055 | 0 | 98.8295 | 10.7511 | 9.1925 | 98.8295 | 10.7511 | 9.1925 | 109.6728 | 11.9307 | 9.1925 | 4.912% | 0.043997 | 0.041819 | 50256.3267 | 10744.6266 | 373.824 | 39137.876 | 50276.5529 | 0 | 0 | 50276.5529 | 0.003581%
2027 | 534 | CB 534 | Tier-2 | Tier-2---21 | 4--1 | 0.59621 | 0 | 100% | 6.3051 | 35.99% | 54.92% | 9.089% | 0.11233 | 0 | 0 | 0.11233 | 0 | 0.10222 | 0.58757 | 0.17397 | 0.10222 | 0.58757 | 0.17397 | 0.11344 | 0.65203 | 0.17397 | 1.782% | 0.060541 | 0.057544 | 104.1456 | 5.1049 | 50.6919 | 48.3488 | 107.6172 | 0 | 0 | 107.6172 | 3.704e-06%
2027 | 365 | 365-28AE | Tier-1 | Non-HFTD---13 | 2--2 | 0.82505 | 65 | 100% | 5.7486 | 52.15% | 38.57% | 9.281% | 0.14839 | 0 | 0 | 0.14839 | 0 | 0.13503 | 0.81308 | 0.16608 | 0.13503 | 0.81308 | 0.16608 | 0.14985 | 0.90229 | 0.16608 | 2.581% | 0.0083168 | 0.0079051 | 691.2044 | 57.8 | 253.5042 | 379.9002 | 708.4293 | 0 | 0 | 708.4293 | 4.893e-06%
2027 | 731 | CB 731 | Tier-1 | Non-HFTD---9 | 2--3 | 3.6858 | 132 | 100% | 19.0771 | 87.49% | 0% | 12.51% | 0.82616 | 0 | 0 | 0.82616 | 0 | 0.75179 | 3.6324 | 0.20697 | 0.75179 | 3.6324 | 0.20697 | 0.83428 | 4.0309 | 0.20697 | 4.331% | 0.010127 | 0.0096253 | 1883.8631 | 99.1754 | 1064.8601 | 719.8275 | 1896.1392 | 0 | 0 | 1896.1392 | 2.724e-05%
2027 | 1215 | 1215-32R | Tier-3 | Tier-3---7 | 5--4 | 12.1911 | 333 | 100% | 8696.5042 | 96.48% | 3.447% | 0.07747% | 415.3037 | 0 | 0 | 415.3037 | 0 | 377.9207 | 12.0143 | 31.4559 | 377.9207 | 12.0143 | 31.4559 | 419.3853 | 13.3325 | 31.4559 | 4.776% | 0.68132 | 0.6476 | 12764.1579 | 1785.0395 | 391.9912 | 10587.1273 | 12787.588 | 0 | 0 | 12787.588 | 0.0137%
2027 | 162 | CB 162 | Tier-1 | Non-HFTD---13 | 1--3 | 1.571 | 46 | 100% | 8.4433 | 83.96% | 0% | 16.04% | 0.35092 | 0 | 0 | 0.35092 | 0 | 0.31933 | 1.5483 | 0.20625 | 0.31933 | 1.5483 | 0.20625 | 0.35437 | 1.7181 | 0.20625 | 4.156% | 0.0047568 | 0.0045213 | 1774.9918 | 1.6508 | 1507.3568 | 265.9842 | 1789.8161 | 0 | 0 | 1789.8161 | 1.157e-05%
2027 | 288 | CB 288 | Tier-1 | Non-HFTD---3 | 4--3 | 9.475 | 686 | 100% | 139.689 | 50.69% | 44.99% | 4.325% | 3.5048 | 0 | 0 | 3.5048 | 0 | 3.1893 | 9.3377 | 0.34155 | 3.1893 | 9.3377 | 0.34155 | 3.5392 | 10.3622 | 0.34155 | 2.509% | 0.031221 | 0.029676 | 4474.1439 | 310.4337 | 2474.817 | 1688.8931 | 4589.0459 | 0 | 0 | 4589.0459 | 0.0001156%
2027 | 1023 | 1023-89R | Tier-2 | Tier-2---11 | 4--4 | 4.3252 | 245 | 100% | 585.5086 | 87.68% | 11.85% | 0.4758% | 25.4114 | 0 | 0 | 25.4114 | 0 | 23.1241 | 4.2625 | 5.425 | 23.1241 | 4.2625 | 5.425 | 25.6612 | 4.7301 | 5.425 | 4.34% | 0.083403 | 0.079275 | 7020.201 | 994.3035 | 754.0146 | 5271.8829 | 7065.2497 | 0 | 0 | 7065.2497 | 0.000838%
2027 | 520 | 520-1489R | Tier-2 | Tier-2---8 | 5--5 | 17.8309 | 1248 | 100% | 2637.9338 | 96.76% | 2.798% | 0.4462% | 126.3422 | 0 | 0 | 126.3422 | 0 | 114.9697 | 17.5724 | 6.5426 | 114.9697 | 17.5724 | 6.5426 | 127.5839 | 19.5004 | 6.5426 | 4.789% | 0.13822 | 0.13138 | 19085.4238 | 2512.9913 | 492.8345 | 16079.598 | 19117.6636 | 0 | 0 | 19117.6636 | 0.004166%
2027 | OS1 | CB OS1 | Tier-1 | Non-HFTD---12 | 3--2 | 6.9136 | 228 | 100% | 10.0644 | 54.01% | 0% | 45.99% | 0.26907 | 0 | 0 | 0.26907 | 0 | 0.24485 | 6.8134 | 0.035936 | 0.24485 | 6.8134 | 0.035936 | 0.27171 | 7.5609 | 0.035936 | 2.673% | 0.018753 | 0.017825 | 536.6874 | 6.9162 | 271.0663 | 258.705 | 549.5416 | 0 | 0 | 549.5416 | 8.873e-06%
2027 | RD4 | RD4-50F | Tier-1 | Non-HFTD---14 | 2--1 | 4.4805 | 302 | 100% | 5.2842 | 37.48% | 0% | 62.52% | 0.098033 | 0 | 0 | 0.098033 | 0 | 0.089209 | 4.4155 | 0.020203 | 0.089209 | 4.4155 | 0.020203 | 0.098997 | 4.9 | 0.020203 | 1.855% | 0.012567 | 0.011945 | 420.4788 | 12.2717 | 107.7406 | 300.4665 | 434.1695 | 0 | 0 | 434.1695 | 3.233e-06%
2027 | 52 | CB 52 | Tier-1 | Non-HFTD---19 | 1--1 | 0.47123 | 35 | 100% | 0.48161 | 27.86% | 0% | 72.14% | 0.0066407 | 0 | 0 | 0.0066407 | 0 | 0.0060429 | 0.46439 | 0.013012 | 0.0060429 | 0.46439 | 0.013012 | 0.006706 | 0.51535 | 0.013012 | 1.379% | 0.0013064 | 0.0012417 | 368.6562 | 0.20013 | 126.8513 | 241.6047 | 382.5071 | 0 | 0 | 382.5071 | 2.19e-07%
2027 | 533 | CB 533 | Tier-2 | Tier-2---20 | 4--1 | 0.38679 | 0 | 100% | 10.6053 | 3.364% | 93.72% | 2.92% | 0.01766 | 0 | 0 | 0.01766 | 0 | 0.01607 | 0.38118 | 0.042159 | 0.01607 | 0.38118 | 0.042159 | 0.017834 | 0.42301 | 0.042159 | 0.1665% | 0.06013 | 0.057154 | 176.3723 | 1.2595 | 133.5547 | 41.5581 | 185.2484 | 0 | 0 | 185.2484 | 5.824e-07%
2027 | 1434 | 1434-2 | Tier-1 | Non-HFTD---14 | 3--1 | 5.9692 | 171 | 100% | 5.8957 | 43.99% | 0% | 56.01% | 0.12838 | 0 | 0 | 0.12838 | 0 | 0.11682 | 5.8826 | 0.019859 | 0.11682 | 5.8826 | 0.019859 | 0.12964 | 6.528 | 0.019859 | 2.177% | 0.014526 | 0.013807 | 405.8792 | 0.79827 | 195.3366 | 209.7443 | 417.7184 | 0 | 0 | 417.7184 | 4.233e-06%
2027 | 431 | 431-550 | Tier-1 | Non-HFTD---11 | 2--2 | 4.3572 | 164 | 100% | 13.1339 | 75.53% | 0% | 24.47% | 0.49104 | 0 | 0 | 0.49104 | 0 | 0.44684 | 4.294 | 0.10406 | 0.44684 | 4.294 | 0.10406 | 0.49587 | 4.7651 | 0.10406 | 3.739% | 0.012344 | 0.011733 | 1063.9583 | 1.4337 | 819.6558 | 242.8688 | 1077.517 | 0 | 0 | 1077.517 | 1.619e-05%
2027 | 968 | CB 968 | Tier-1 | Non-HFTD---15 | 1--3 | 0.3553 | 3 | 100% | 2.4046 | 84.55% | 0% | 15.45% | 0.10063 | 0 | 0 | 0.10063 | 0 | 0.091574 | 0.35015 | 0.26153 | 0.091574 | 0.35015 | 0.26153 | 0.10162 | 0.38856 | 0.26153 | 4.185% | 0.0014058 | 0.0013362 | 1710.4748 | 127.3956 | 651.9293 | 931.1499 | 1724.2412 | 0 | 0 | 1724.2412 | 3.318e-06%
2027 | IB2 | CB IB2 | Tier-1 | Non-HFTD---16 | 2--1 | 5.2097 | 121 | 100% | 4.5685 | 28.86% | 0% | 71.14% | 0.065256 | 0 | 0 | 0.065256 | 0 | 0.059382 | 5.1341 | 0.011566 | 0.059382 | 5.1341 | 0.011566 | 0.065897 | 5.6974 | 0.011566 | 1.428% | 0.013384 | 0.012721 | 341.3434 | 0.43381 | 119.0194 | 221.8902 | 353.9902 | 0 | 0 | 353.9902 | 2.152e-06%
2027 | 486 | CB 486 | Tier-1 | Non-HFTD---15 | 1--4 | 0.12424 | 11 | 100% | 2.895 | 93.41% | 0% | 6.589% | 0.13386 | 0 | 0 | 0.13386 | 0 | 0.12181 | 0.12244 | 0.99484 | 0.12181 | 0.12244 | 0.99484 | 0.13517 | 0.13587 | 0.99484 | 4.624% | 0.0005584 | 0.00053076 | 5184.3933 | 136.4681 | 4036.8272 | 1011.0981 | 5202.1844 | 0 | 0 | 5202.1844 | 4.414e-06%
2027 | 969 | CB 969 | Tier-1 | Non-HFTD---15 | 1--3 | 0.40417 | 27 | 100% | 3.3526 | 88.46% | 0% | 11.54% | 0.14681 | 0 | 0 | 0.14681 | 0 | 0.13359 | 0.39831 | 0.33541 | 0.13359 | 0.39831 | 0.33541 | 0.14825 | 0.44201 | 0.33541 | 4.379% | 0.0018268 | 0.0017364 | 1835.2417 | 238.0159 | 133.8154 | 1463.4105 | 1846.2677 | 0 | 0 | 1846.2677 | 4.841e-06%
2027 | 366 | 366-559 | Tier-1 | Non-HFTD---7 | 2--3 | 1.0561 | 6 | 100% | 36.9737 | 0.4866% | 97.35% | 2.161% | 0.0089065 | 0 | 0 | 0.0089065 | 0 | 0.0081048 | 1.0407 | 0.0077874 | 0.0081048 | 1.0407 | 0.0077874 | 0.008994 | 1.1549 | 0.0077874 | 0.02409% | 0.0083398 | 0.007927 | 4433.4019 | 5.8876 | 3951.842 | 475.6723 | 4663.1604 | 0 | 0 | 4663.1604 | 2.937e-07%
2027 | 168 | CB 168 | Tier-1 | Non-HFTD---8 | 3--2 | 7.6273 | 374 | 100% | 32.7486 | 82.97% | 0% | 17.03% | 1.345 | 0 | 0 | 1.345 | 0 | 1.2239 | 7.5167 | 0.16283 | 1.2239 | 7.5167 | 0.16283 | 1.3582 | 8.3414 | 0.16283 | 4.107% | 0.023992 | 0.022804 | 1364.9793 | 11.4899 | 1084.5121 | 268.9774 | 1377.084 | 0 | 0 | 1377.084 | 4.435e-05%
2027 | 497 | 497-888F | Tier-1 | Non-HFTD---11 | 1--3 | 0.99355 | 104 | 100% | 9.8083 | 94.15% | 0% | 5.846% | 0.45713 | 0 | 0 | 0.45713 | 0 | 0.41598 | 0.97915 | 0.42484 | 0.41598 | 0.97915 | 0.42484 | 0.46162 | 1.0866 | 0.42484 | 4.661% | 0.0031776 | 0.0030203 | 3086.6864 | 271.9431 | 1260.4115 | 1554.3319 | 3096.0835 | 0 | 0 | 3096.0835 | 1.507e-05%
2027 | 1081 | 1081-38AE | Tier-1 | Non-HFTD---1 | 3--4 | 1.1752 | 119 | 100% | 213.0679 | 78.03% | 21.53% | 0.4327% | 8.23 | 0 | 0 | 8.23 | 0 | 7.4892 | 1.1581 | 6.4667 | 7.4892 | 1.1581 | 6.4667 | 8.3109 | 1.2852 | 6.4667 | 3.863% | 0.01533 | 0.014572 | 13898.3942 | 2058.13 | 2800.8861 | 9039.378 | 14057.3933 | 0 | 0 | 14057.3933 | 0.0002714%
2027 | 242 | 242-776F | Tier-1 | Non-HFTD---6 | 5--2 | 0.6741 | 30 | 100% | 89.0868 | 11.41% | 88.12% | 0.4676% | 0.50321 | 0 | 0 | 0.50321 | 0 | 0.45791 | 0.66433 | 0.68929 | 0.45791 | 0.66433 | 0.68929 | 0.50815 | 0.73722 | 0.68929 | 0.5649% | 0.097933 | 0.093086 | 909.6674 | 12.7136 | 757.5676 | 139.3862 | 951.6351 | 0 | 0 | 951.6351 | 1.659e-05%
2027 | VDN1 | CB VDN1 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0672 | 440 | 100% | 85.5226 | 4.345% | 90.68% | 4.973% | 0.18395 | 0 | 0 | 0.18395 | 0 | 0.1674 | 5.9793 | 0.027996 | 0.1674 | 5.9793 | 0.027996 | 0.18576 | 6.6353 | 0.027996 | 0.2151% | 0.027823 | 0.026446 | 3073.7667 | 13.6612 | 2620.1542 | 439.9513 | 3226.8862 | 0 | 0 | 3226.8862 | 6.066e-06%
2027 | 1094 | 1094-35F | Tier-2 | Tier-2---7 | 3--5 | 5.1365 | 431 | 100% | 2514.2831 | 99.84% | 0% | 0.1648% | 124.2519 | 0 | 0 | 124.2519 | 0 | 113.0675 | 5.0621 | 22.3362 | 113.0675 | 5.0621 | 22.3362 | 125.473 | 5.6175 | 22.3362 | 4.942% | 0.020398 | 0.019388 | 123263.6714 | 20043.0193 | 98.2626 | 103122.3894 | 123274.2511 | 0 | 0 | 123274.2511 | 0.004097%
2027 | 376 | CB 376 | Tier-1 | Non-HFTD---10 | 3--2 | 7.7214 | 137 | 100% | 26.2471 | 76.46% | 0% | 23.54% | 0.99336 | 0 | 0 | 0.99336 | 0 | 0.90394 | 7.6094 | 0.11879 | 0.90394 | 7.6094 | 0.11879 | 1.0031 | 8.4443 | 0.11879 | 3.785% | 0.022473 | 0.021361 | 1167.9296 | 0.21143 | 917.9161 | 249.8021 | 1182.2491 | 0 | 0 | 1182.2491 | 3.276e-05%
2027 | 59 | 59-464AE | Tier-1 | Non-HFTD---14 | 3--2 | 0.95286 | 102 | 100% | 7.4345 | 25.7% | 64.22% | 10.07% | 0.094587 | 0 | 0 | 0.094587 | 0 | 0.086073 | 0.93904 | 0.09166 | 0.086073 | 0.93904 | 0.09166 | 0.095516 | 1.0421 | 0.09166 | 1.272% | 0.014091 | 0.013394 | 527.5962 | 24.004 | 335.1416 | 168.4506 | 548.0102 | 0 | 0 | 548.0102 | 3.119e-06%
2027 | 63 | 63-35AE | Tier-1 | Non-HFTD---1 | 3--4 | 1.9439 | 124 | 100% | 256.4675 | 76.22% | 23.46% | 0.3199% | 9.6762 | 0 | 0 | 9.6762 | 0 | 8.8052 | 1.9158 | 4.5962 | 8.8052 | 1.9158 | 4.5962 | 9.7713 | 2.1259 | 4.5962 | 3.773% | 0.016955 | 0.016116 | 15126.187 | 2259.8593 | 3445.3068 | 9421.0209 | 15313.5135 | 0 | 0 | 15313.5135 | 0.0003191%
2027 | 712 | 712-311F | Tier-1 | Non-HFTD---15 | 1--2 | 0.68958 | 52 | 100% | 2.2762 | 61.21% | 0% | 38.79% | 0.06897 | 0 | 0 | 0.06897 | 0 | 0.062762 | 0.67958 | 0.092353 | 0.062762 | 0.67958 | 0.092353 | 0.069648 | 0.75415 | 0.092353 | 3.03% | 0.002841 | 0.0027004 | 801.2038 | 64.6949 | 121.7914 | 614.7175 | 817.3878 | 0 | 0 | 817.3878 | 2.274e-06%
2027 | VS3 | CB VS3 | Tier-1 | Non-HFTD---10 | 3--2 | 5.5108 | 560 | 100% | 22.658 | 81.41% | 0% | 18.59% | 0.91305 | 0 | 0 | 0.91305 | 0 | 0.83086 | 5.4309 | 0.15299 | 0.83086 | 5.4309 | 0.15299 | 0.92202 | 6.0268 | 0.15299 | 4.03% | 0.016726 | 0.015898 | 1354.6403 | 175.5967 | 54.3376 | 1124.7059 | 1367.7563 | 0 | 0 | 1367.7563 | 3.011e-05%
2027 | 242 | 242-1420F | Tier-1 | Non-HFTD---6 | 5--2 | 1.2443 | 17 | 100% | 89.5601 | 12.52% | 86.49% | 0.9881% | 0.55499 | 0 | 0 | 0.55499 | 0 | 0.50503 | 1.2263 | 0.41184 | 0.50503 | 1.2263 | 0.41184 | 0.56044 | 1.3608 | 0.41184 | 0.6197% | 0.1 | 0.095054 | 895.5638 | 14.9487 | 662.244 | 218.3711 | 936.3641 | 0 | 0 | 936.3641 | 1.83e-05%
2027 | 181 | 181-49 | Tier-1 | Non-HFTD---6 | 4--2 | 0.13883 | 1 | 100% | 64.7664 | 8.121% | 91.5% | 0.3833% | 0.26035 | 0 | 0 | 0.26035 | 0 | 0.23692 | 0.13681 | 1.7317 | 0.23692 | 0.13681 | 1.7317 | 0.26291 | 0.15182 | 1.7317 | 0.402% | 0.078852 | 0.074949 | 821.3685 | 11.8665 | 685.9557 | 123.5464 | 860.6699 | 0 | 0 | 860.6699 | 8.586e-06%
2027 | 100 | 100-1122R | Tier-1 | Non-HFTD---17 | 1--2 | 0.61362 | 11 | 100% | 1.1188 | 52.39% | 0% | 47.61% | 0.029016 | 0 | 0 | 0.029016 | 0 | 0.026404 | 0.60472 | 0.043663 | 0.026404 | 0.60472 | 0.043663 | 0.029301 | 0.67107 | 0.043663 | 2.594% | 0.002205 | 0.0020959 | 507.381 | 49.2152 | 31.6075 | 426.5583 | 519.9599 | 0 | 0 | 519.9599 | 9.568e-07%
2027 | 90 | 90-32 | Tier-1 | Non-HFTD---5 | 3--3 | 3.1322 | 91 | 100% | 76.4194 | 6.097% | 89.87% | 4.029% | 0.23063 | 0 | 0 | 0.23063 | 0 | 0.20987 | 3.0868 | 0.06799 | 0.20987 | 3.0868 | 0.06799 | 0.23289 | 3.4254 | 0.06799 | 0.3018% | 0.016016 | 0.015223 | 4771.4395 | 9.6024 | 4175.1996 | 586.6374 | 5004.776 | 0 | 0 | 5004.776 | 7.605e-06%
2027 | 1483 | 1483-40 | Tier-1 | Non-HFTD---20 | 1--1 | 0.44642 | 20 | 100% | 0.31443 | 22.37% | 0% | 77.63% | 0.0034821 | 0 | 0 | 0.0034821 | 0 | 0.0031687 | 0.43995 | 0.0072023 | 0.0031687 | 0.43995 | 0.0072023 | 0.0035163 | 0.48822 | 0.0072023 | 1.107% | 0.001097 | 0.0010427 | 286.6296 | 0.16743 | 84.3376 | 202.1246 | 298.2171 | 0 | 0 | 298.2171 | 1.148e-07%
2027 | 154 | 154-878R | Tier-1 | Non-HFTD---12 | 3--1 | 10.4622 | 189 | 100% | 14.2275 | 52.45% | 0% | 47.55% | 0.36939 | 0 | 0 | 0.36939 | 0 | 0.33614 | 10.3105 | 0.032601 | 0.33614 | 10.3105 | 0.032601 | 0.37302 | 11.4417 | 0.032601 | 2.596% | 0.028539 | 0.027127 | 498.52 | 0.24282 | 282.6124 | 215.6648 | 510.8648 | 0 | 0 | 510.8648 | 1.218e-05%
2027 | 181 | 181-54F | Tier-1 | Non-HFTD---16 | 3--1 | 1.2006 | 19 | 100% | 2.7236 | 29.54% | 39.02% | 31.44% | 0.039823 | 0 | 0 | 0.039823 | 0 | 0.036238 | 1.1832 | 0.030628 | 0.036238 | 1.1832 | 0.030628 | 0.040214 | 1.313 | 0.030628 | 1.462% | 0.01856 | 0.017641 | 146.7509 | 7.1793 | 49.6425 | 89.929 | 152.1359 | 0 | 0 | 152.1359 | 1.313e-06%
2027 | 449 | 449-13R | Tier-3 | Tier-3---7 | 5--5 | 16.5478 | 1012 | 100% | 6729.9647 | 90.49% | 9.346% | 0.1629% | 301.4563 | 0 | 0 | 301.4563 | 0 | 274.3211 | 16.3078 | 16.8214 | 274.3211 | 16.3078 | 16.8214 | 304.419 | 18.0971 | 16.8214 | 4.479% | 0.28234 | 0.26837 | 23836.2998 | 3539.8627 | 2045.1194 | 18251.3177 | 23954.3367 | 0 | 0 | 23954.3367 | 0.009941%
2027 | 948 | CB 948 | Tier-1 | Non-HFTD---10 | 4--1 | 14.9462 | 579 | 100% | 22.208 | 55.27% | 0% | 44.73% | 0.60752 | 0 | 0 | 0.60752 | 0 | 0.55284 | 14.7295 | 0.037533 | 0.55284 | 14.7295 | 0.037533 | 0.6135 | 16.3456 | 0.037533 | 2.736% | 0.044785 | 0.042569 | 495.8748 | 16.8793 | 215.136 | 263.8595 | 507.4272 | 0 | 0 | 507.4272 | 2.003e-05%
2027 | 506 | 506-844 | Tier-1 | Non-HFTD---10 | 3--2 | 8.7868 | 165 | 100% | 22.4025 | 80.21% | 0% | 19.79% | 0.8895 | 0 | 0 | 0.8895 | 0 | 0.80944 | 8.6594 | 0.093475 | 0.80944 | 8.6594 | 0.093475 | 0.89825 | 9.6094 | 0.093475 | 3.971% | 0.021885 | 0.020802 | 1023.6455 | 1.2121 | 833.0026 | 189.4308 | 1034.1936 | 0 | 0 | 1034.1936 | 2.933e-05%
2027 | 461 | CB 461 | Tier-2 | Tier-2---15 | 2--4 | 2.4203 | 0 | 100% | 101.8709 | 98.65% | 0% | 1.347% | 4.9747 | 0 | 0 | 4.9747 | 0 | 4.5269 | 2.3852 | 1.8979 | 4.5269 | 2.3852 | 1.8979 | 5.0236 | 2.6469 | 1.8979 | 4.883% | 0.0097562 | 0.0092733 | 10441.6529 | 2274.299 | 1515.1673 | 6652.1866 | 10448.9777 | 0 | 0 | 10448.9777 | 0.000164%
2027 | 80 | 80-568F | Tier-1 | Non-HFTD---14 | 3--1 | 9.8088 | 176 | 100% | 8.3283 | 29.18% | 0% | 70.82% | 0.1203 | 0 | 0 | 0.1203 | 0 | 0.10947 | 9.6665 | 0.011325 | 0.10947 | 9.6665 | 0.011325 | 0.12149 | 10.7271 | 0.011325 | 1.445% | 0.025016 | 0.023778 | 332.9159 | 2.3303 | 105.3492 | 225.2364 | 345.194 | 0 | 0 | 345.194 | 3.967e-06%
2027 | BA2 | CB BA2 | Tier-1 | Non-HFTD---14 | 2--1 | 4.4718 | 100 | 100% | 5.2769 | 32.36% | 0% | 67.64% | 0.084525 | 0 | 0 | 0.084525 | 0 | 0.076917 | 4.407 | 0.017453 | 0.076917 | 4.407 | 0.017453 | 0.085356 | 4.8905 | 0.017453 | 1.602% | 0.013379 | 0.012717 | 394.4186 | 8.4721 | 101.3103 | 284.6363 | 408.3123 | 0 | 0 | 408.3123 | 2.787e-06%
2027 | 594 | 594-1379F | Tier-2 | Tier-2---17 | 1--5 | 0.51875 | 39 | 100% | 49.4293 | 99.41% | 0% | 0.5897% | 2.4323 | 0 | 0 | 2.4323 | 0 | 2.2134 | 0.51123 | 4.3295 | 2.2134 | 0.51123 | 4.3295 | 2.4562 | 0.56732 | 4.3295 | 4.921% | 0.0021822 | 0.0020742 | 22651.1445 | 6586.9703 | 15.0709 | 16049.1033 | 22658.1007 | 0 | 0 | 22658.1007 | 8.021e-05%
2027 | WY3 | CB WY3 | Tier-1 | Non-HFTD---20 | 1--1 | 0.49583 | 5 | 100% | 0.64342 | 2.218% | 0% | 97.78% | 0.00070635 | 0 | 0 | 0.00070635 | 0 | 0.00064277 | 0.48864 | 0.0013154 | 0.00064277 | 0.48864 | 0.0013154 | 0.00071329 | 0.54225 | 0.0013154 | 0.1098% | 0.002013 | 0.0019134 | 319.6305 | 0.84233 | 31.6894 | 287.0987 | 335.907 | 0 | 0 | 335.907 | 2.329e-08%
2027 | 460 | CB 460 | Tier-2 | Tier-2---17 | 1--4 | 0.95644 | 7 | 100% | 58.9173 | 99.11% | 0% | 0.8919% | 2.8904 | 0 | 0 | 2.8904 | 0 | 2.6302 | 0.94257 | 2.7905 | 2.6302 | 0.94257 | 2.7905 | 2.9188 | 1.046 | 2.7905 | 4.906% | 0.0037362 | 0.0035513 | 15769.3081 | 2295.5963 | 5550.7252 | 7922.9866 | 15776.6323 | 0 | 0 | 15776.6323 | 9.531e-05%
2027 | RA1 | CB RA1 | Tier-2 | Tier-2---2 | 5--5 | 9.6284 | 485 | 100% | 10517.0624 | 98.31% | 1.619% | 0.07383% | 511.7794 | 0 | 0 | 511.7794 | 0 | 465.7123 | 9.4888 | 49.0801 | 465.7123 | 9.4888 | 49.0801 | 516.8091 | 10.5299 | 49.0801 | 4.866% | 0.14726 | 0.13997 | 71417.5478 | 11306.2901 | 1058.7648 | 59052.4929 | 71480.5261 | 0 | 0 | 71480.5261 | 0.01688%
2027 | LPS1 | CB LPS1 | Tier-1 | Non-HFTD---18 | 2--1 | 2.5019 | 76 | 100% | 1.8545 | 27.68% | 0% | 72.32% | 0.02541 | 0 | 0 | 0.02541 | 0 | 0.023122 | 2.4656 | 0.009378 | 0.023122 | 2.4656 | 0.009378 | 0.025659 | 2.7361 | 0.009378 | 1.37% | 0.006253 | 0.0059435 | 296.5769 | 4.136 | 77.2739 | 215.167 | 307.7467 | 0 | 0 | 307.7467 | 8.379e-07%
2027 | 417 | 417-791AE | Tier-1 | Non-HFTD---4 | 3--4 | 1.9314 | 67 | 100% | 96.2517 | 1.815% | 96.36% | 1.824% | 0.086463 | 0 | 0 | 0.086463 | 0 | 0.07868 | 1.9034 | 0.041337 | 0.07868 | 1.9034 | 0.041337 | 0.087313 | 2.1122 | 0.041337 | 0.08983% | 0.016976 | 0.016136 | 5669.8675 | 7.6795 | 5119.2772 | 542.9108 | 5959.7835 | 0 | 0 | 5959.7835 | 2.851e-06%
2027 | 454 | 454-53F | Tier-2 | Tier-2---13 | 4--3 | 0.73506 | 31 | 100% | 272.5399 | 0.7301% | 99.1% | 0.1654% | 0.098502 | 0 | 0 | 0.098502 | 0 | 0.089635 | 0.7244 | 0.12374 | 0.089635 | 0.7244 | 0.12374 | 0.09947 | 0.80388 | 0.12374 | 0.03614% | 0.073094 | 0.069476 | 3728.6015 | 9.5009 | 3385.0726 | 334.0281 | 3921.3613 | 0 | 0 | 3921.3613 | 3.248e-06%
2027 | 220 | 220-288R | Tier-3 | Tier-3---14 | 5--4 | 7.2415 | 176 | 100% | 2198.6799 | 96.34% | 3.473% | 0.1901% | 104.8478 | 0 | 0 | 104.8478 | 0 | 95.41 | 7.1365 | 13.3693 | 95.41 | 7.1365 | 13.3693 | 105.8782 | 7.9195 | 13.3693 | 4.769% | 0.37523 | 0.35666 | 5859.515 | 816.9998 | 199.3663 | 4843.1489 | 5870.6934 | 0 | 0 | 5870.6934 | 0.003457%
2027 | 438 | 438-45 | Tier-1 | Non-HFTD---15 | 1--3 | 0.46629 | 47 | 100% | 4.5379 | 93.11% | 0% | 6.89% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.19032 | 0.45953 | 0.41417 | 0.19032 | 0.45953 | 0.41417 | 0.2112 | 0.50995 | 0.41417 | 4.609% | 0.0017438 | 0.0016575 | 2602.317 | 452.2709 | 20.4829 | 2129.5632 | 2611.6552 | 0 | 0 | 2611.6552 | 6.897e-06%
2027 | 445 | 445-1325F | Tier-2 | Tier-2---2 | 5--4 | 11.7129 | 151 | 100% | 7250.7229 | 96.11% | 3.805% | 0.08959% | 344.9322 | 0 | 0 | 344.9322 | 0 | 313.8836 | 11.5431 | 27.1924 | 313.8836 | 11.5431 | 27.1924 | 348.3221 | 12.8095 | 27.1924 | 4.757% | 0.57356 | 0.54517 | 12641.5766 | 1855.057 | 431.2255 | 10355.2942 | 12667.2174 | 0 | 0 | 12667.2174 | 0.01137%
2027 | 355 | 355-65R | Tier-2 | Tier-2---21 | 1--2 | 0.0075758 | 0 | 100% | 0.06699 | 46.11% | 0% | 53.89% | 0.0015289 | 0 | 0 | 0.0015289 | 0 | 0.0013913 | 0.0074659 | 0.18635 | 0.0013913 | 0.0074659 | 0.18635 | 0.0015439 | 0.0082851 | 0.18635 | 2.282% | 7.02e-05 | 6.6725e-05 | 954.2713 | 72.5365 | 46.719 | 835.0158 | 981.0548 | 0 | 0 | 981.0548 | 5.042e-08%
2027 | HW1 | CB HW1 | Tier-1 | Non-HFTD---4 | 1--5 | 1.0525 | 61 | 100% | 122.4382 | 99.35% | 0% | 0.6452% | 6.0216 | 0 | 0 | 6.0216 | 0 | 5.4796 | 1.0372 | 5.2831 | 5.4796 | 1.0372 | 5.2831 | 6.0808 | 1.151 | 5.2831 | 4.918% | 0.0031138 | 0.0029597 | 39321.1613 | 6393.1555 | 36.0556 | 32891.9501 | 39334.373 | 0 | 0 | 39334.373 | 0.0001986%
2027 | 448 | 448-47R | Tier-3 | Tier-3---14 | 5--3 | 8.8214 | 157 | 100% | 2612.2711 | 91.91% | 7.885% | 0.2065% | 118.8447 | 0 | 0 | 118.8447 | 0 | 108.1471 | 8.6935 | 12.44 | 108.1471 | 8.6935 | 12.44 | 120.0127 | 9.6473 | 12.44 | 4.549% | 0.62882 | 0.59769 | 4154.2404 | 551.1168 | 295.8527 | 3307.2709 | 4171.7455 | 0 | 0 | 4171.7455 | 0.003919%
2027 | 595 | CB 595 | Tier-1 | Non-HFTD---17 | 1--2 | 0.39361 | 33 | 100% | 1.0072 | 61.92% | 0% | 38.08% | 0.030872 | 0 | 0 | 0.030872 | 0 | 0.028093 | 0.3879 | 0.072423 | 0.028093 | 0.3879 | 0.072423 | 0.031175 | 0.43046 | 0.072423 | 3.065% | 0.0014016 | 0.0013322 | 718.595 | 0.6485 | 467.1224 | 250.8241 | 732.8449 | 0 | 0 | 732.8449 | 1.018e-06%
2027 | 308 | CB 308 | Tier-2 | Tier-2---18 | 4--3 | 2.3447 | 90 | 100% | 77.7948 | 18.36% | 79.79% | 1.851% | 0.70708 | 0 | 0 | 0.70708 | 0 | 0.64343 | 2.3107 | 0.27846 | 0.64343 | 2.3107 | 0.27846 | 0.71403 | 2.5642 | 0.27846 | 0.9089% | 0.037941 | 0.036063 | 2050.437 | 12.1248 | 1817.8081 | 220.5041 | 2137.6123 | 0 | 0 | 2137.6123 | 2.332e-05%
2027 | 445 | 445-18R | Tier-2 | Tier-2---2 | 5--5 | 24.8581 | 458 | 100% | 10619.7967 | 95.69% | 4.18% | 0.1317% | 503.0122 | 0 | 0 | 503.0122 | 0 | 457.7342 | 24.4977 | 18.6848 | 457.7342 | 24.4977 | 18.6848 | 507.9557 | 27.1855 | 18.6848 | 4.737% | 0.6048 | 0.57486 | 17559.3271 | 2475.3162 | 661.1087 | 14422.9022 | 17598.759 | 0 | 0 | 17598.759 | 0.01659%
2027 | 310 | 310-1194F | Tier-1 | Non-HFTD---19 | 1--1 | 0.20307 | 2 | 100% | 0.28675 | 29.07% | 0% | 70.93% | 0.0041261 | 0 | 0 | 0.0041261 | 0 | 0.0037547 | 0.20013 | 0.018761 | 0.0037547 | 0.20013 | 0.018761 | 0.0041666 | 0.22209 | 0.018761 | 1.439% | 0.000692 | 0.00065775 | 414.3715 | 2.4094 | 133.3051 | 278.6571 | 429.678 | 0 | 0 | 429.678 | 1.361e-07%
2027 | 187 | CB 187 | Tier-1 | Non-HFTD---7 | 3--3 | 5.4221 | 206 | 100% | 43.4605 | 90.51% | 0% | 9.49% | 1.9471 | 0 | 0 | 1.9471 | 0 | 1.7719 | 5.3435 | 0.33159 | 1.7719 | 5.3435 | 0.33159 | 1.9663 | 5.9298 | 0.33159 | 4.48% | 0.017469 | 0.016605 | 2487.8091 | 217.7975 | 1012.4115 | 1257.6001 | 2500.1043 | 0 | 0 | 2500.1043 | 6.421e-05%
2027 | 241 | 241-746 | Tier-1 | Non-HFTD---2 | 5--3 | 0.38732 | 13 | 100% | 290.9824 | 9.93% | 90% | 0.07278% | 1.4303 | 0 | 0 | 1.4303 | 0 | 1.3016 | 0.3817 | 3.4099 | 1.3016 | 0.3817 | 3.4099 | 1.4444 | 0.42358 | 3.4099 | 0.4915% | 0.098458 | 0.093584 | 2955.4024 | 47.8838 | 2441.1448 | 466.3738 | 3094.0296 | 0 | 0 | 3094.0296 | 4.717e-05%
2027 | 312 | 312-40F | Tier-2 | Tier-2---20 | 3--2 | 0.089352 | 2 | 100% | 9.4163 | 0.07625% | 99.1% | 0.8244% | 0.00035539 | 0 | 0 | 0.00035539 | 0 | 0.0003234 | 0.088056 | 0.0036727 | 0.0003234 | 0.088056 | 0.0036727 | 0.00035889 | 0.097717 | 0.0036727 | 0.003774% | 0.017172 | 0.016322 | 548.3384 | 0.98367 | 493.2185 | 54.1362 | 576.8729 | 0 | 0 | 576.8729 | 1.172e-08%
2027 | 357 | 357-1147R | Tier-2 | Tier-2---10 | 5--4 | 0.95666 | 49 | 100% | 1251.1758 | 99.06% | 0.8754% | 0.0621% | 61.3526 | 0 | 0 | 61.3526 | 0 | 55.83 | 0.94279 | 59.2179 | 55.83 | 0.94279 | 59.2179 | 61.9555 | 1.0462 | 59.2179 | 4.904% | 0.14287 | 0.1358 | 8757.5771 | 1409.6316 | 71.0463 | 7276.8992 | 8761.8529 | 0 | 0 | 8761.8529 | 0.002023%
2027 | 172 | 172-569R | Tier-1 | Non-HFTD---3 | 5--2 | 17.4465 | 526 | 100% | 174.5806 | 70.22% | 23.82% | 5.957% | 6.0684 | 0 | 0 | 6.0684 | 0 | 5.5221 | 17.1936 | 0.32117 | 5.5221 | 17.1936 | 0.32117 | 6.128 | 19.08 | 0.32117 | 3.476% | 0.12865 | 0.12229 | 1356.9713 | 139.4703 | 376.51 | 840.9911 | 1378.015 | 0 | 0 | 1378.015 | 0.0002001%
2027 | 241 | CB 241 | Tier-2 | Tier-2---11 | 5--4 | 3.3744 | 106 | 100% | 614.4843 | 5.233% | 94.45% | 0.3166% | 1.5918 | 0 | 0 | 1.5918 | 0 | 1.4485 | 3.3255 | 0.43557 | 1.4485 | 3.3255 | 0.43557 | 1.6074 | 3.6903 | 0.43557 | 0.259% | 0.096356 | 0.091586 | 6377.2296 | 31.8975 | 5684.1218 | 661.2103 | 6691.9621 | 0 | 0 | 6691.9621 | 5.249e-05%
2027 | 170 | 170-410R | Tier-1 | Non-HFTD---8 | 5--1 | 12.3119 | 668 | 100% | 29.1667 | 31.01% | 45.41% | 23.57% | 0.44774 | 0 | 0 | 0.44774 | 0 | 0.40744 | 12.1334 | 0.03358 | 0.40744 | 12.1334 | 0.03358 | 0.45214 | 13.4646 | 0.03358 | 1.535% | 0.10336 | 0.098244 | 282.1845 | 8.474 | 122.6089 | 151.1016 | 292.3227 | 0 | 0 | 292.3227 | 1.476e-05%
2027 | 90 | 90-50F | Tier-1 | Non-HFTD---9 | 2--3 | 0.94068 | 4 | 100% | 23.5914 | 2.577% | 94.35% | 3.073% | 0.030095 | 0 | 0 | 0.030095 | 0 | 0.027386 | 0.92704 | 0.029541 | 0.027386 | 0.92704 | 0.029541 | 0.03039 | 1.0288 | 0.029541 | 0.1276% | 0.0077394 | 0.0073563 | 3048.2262 | 3.32 | 2713.4595 | 331.4467 | 3202.8802 | 0 | 0 | 3202.8802 | 9.924e-07%
2027 | 212 | 212-734R | Tier-2 | Tier-2---10 | 5--4 | 17.8821 | 16 | 100% | 1265.9596 | 97.92% | 1.386% | 0.6959% | 61.3606 | 0 | 0 | 61.3606 | 0 | 55.8373 | 17.6228 | 3.1685 | 55.8373 | 17.6228 | 3.1685 | 61.9636 | 19.5563 | 3.1685 | 4.847% | 0.17753 | 0.16875 | 7130.7609 | 660.9769 | 211.9053 | 6257.8788 | 7138.4909 | 0 | 0 | 7138.4909 | 0.002023%
2027 | 453 | CB 453 | Tier-1 | Non-HFTD---8 | 3--3 | 4.5977 | 103 | 100% | 31.0059 | 88.32% | 0% | 11.68% | 1.3556 | 0 | 0 | 1.3556 | 0 | 1.2336 | 4.5311 | 0.27225 | 1.2336 | 4.5311 | 0.27225 | 1.3689 | 5.0282 | 0.27225 | 4.372% | 0.01456 | 0.013839 | 2129.5572 | 0.18709 | 1903.5138 | 225.8563 | 2142.5053 | 0 | 0 | 2142.5053 | 4.47e-05%
2027 | 57 | 57-1291F | Tier-1 | Non-HFTD---8 | 3--3 | 1.8095 | 10 | 100% | 33.0087 | 0.7107% | 94.92% | 4.37% | 0.011612 | 0 | 0 | 0.011612 | 0 | 0.010567 | 1.7833 | 0.0059255 | 0.010567 | 1.7833 | 0.0059255 | 0.011726 | 1.9789 | 0.0059255 | 0.03518% | 0.016049 | 0.015255 | 2056.6925 | 2.488 | 1785.8176 | 268.3869 | 2163.0395 | 0 | 0 | 2163.0395 | 3.829e-07%
2027 | RS1 | CB RS1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.6957 | 45 | 100% | 1.4439 | 25.65% | 0% | 74.35% | 0.018335 | 0 | 0 | 0.018335 | 0 | 0.016685 | 1.6711 | 0.0099844 | 0.016685 | 1.6711 | 0.0099844 | 0.018515 | 1.8544 | 0.0099844 | 1.27% | 0.0049182 | 0.0046747 | 293.5883 | 8.0472 | 47.0121 | 238.5291 | 304.9556 | 0 | 0 | 304.9556 | 6.046e-07%
2027 | 1140 | 1140-8F | Tier-1 | Non-HFTD---3 | 5--2 | 1.0602 | 12 | 100% | 97.4471 | 0.5522% | 98.8% | 0.6432% | 0.026634 | 0 | 0 | 0.026634 | 0 | 0.024237 | 1.0449 | 0.023196 | 0.024237 | 1.0449 | 0.023196 | 0.026896 | 1.1595 | 0.023196 | 0.02733% | 0.10414 | 0.098982 | 935.7622 | 1.7163 | 839.5416 | 94.5043 | 984.2256 | 0 | 0 | 984.2256 | 8.783e-07%
2027 | 75 | 75-2257F | Tier-3 | Tier-3---20 | 1--5 | 0.050947 | 7 | 100% | 17.7969 | 99.34% | 0% | 0.6614% | 0.87512 | 0 | 0 | 0.87512 | 0 | 0.79635 | 0.050208 | 15.8609 | 0.79635 | 0.050208 | 15.8609 | 0.88372 | 0.055717 | 15.8609 | 4.917% | 0.0002804 | 0.00026652 | 63469.7957 | 10131.5901 | 38.1351 | 53300.0705 | 63491.6581 | 0 | 0 | 63491.6581 | 2.886e-05%
2027 | RC1 | CB RC1 | Tier-2 | Tier-2---4 | 4--5 | 3.232 | 294 | 100% | 3739.8748 | 99.14% | 0.8077% | 0.05477% | 183.5272 | 0 | 0 | 183.5272 | 0 | 167.0073 | 3.1851 | 52.4338 | 167.0073 | 3.1851 | 52.4338 | 185.3309 | 3.5346 | 52.4338 | 4.907% | 0.084253 | 0.080083 | 44388.4144 | 8961.6827 | 332.4323 | 35094.2993 | 44408.3511 | 0 | 0 | 44408.3511 | 0.006052%
2027 | 450 | 450-88R | Tier-2 | Tier-2---10 | 4--4 | 3.7312 | 271 | 100% | 894.3745 | 42.96% | 56.7% | 0.3423% | 19.0196 | 0 | 0 | 19.0196 | 0 | 17.3075 | 3.6771 | 4.7068 | 17.3075 | 3.6771 | 4.7068 | 19.2065 | 4.0806 | 4.7068 | 2.127% | 0.082954 | 0.078848 | 10781.5193 | 1210.2197 | 5658.3612 | 3912.9384 | 11101.7801 | 0 | 0 | 11101.7801 | 0.0006272%
2027 | 192 | CB 192 | Tier-1 | Non-HFTD---4 | 3--4 | 4.2902 | 298 | 100% | 109.5816 | 97.38% | 0% | 2.615% | 5.2824 | 0 | 0 | 5.2824 | 0 | 4.8069 | 4.228 | 1.1369 | 4.8069 | 4.228 | 1.1369 | 5.3343 | 4.6919 | 1.1369 | 4.821% | 0.015026 | 0.014282 | 7292.705 | 958.338 | 2325.7233 | 4008.6436 | 7302.6378 | 0 | 0 | 7302.6378 | 0.0001742%
2027 | 320 | 320-1414 | Tier-1 | Non-HFTD---16 | 2--1 | 3.7206 | 70 | 100% | 2.9348 | 21.11% | 0% | 78.89% | 0.030668 | 0 | 0 | 0.030668 | 0 | 0.027907 | 3.6667 | 0.0076111 | 0.027907 | 3.6667 | 0.0076111 | 0.030969 | 4.069 | 0.0076111 | 1.045% | 0.009875 | 0.0093862 | 297.1976 | 1.2363 | 77.5699 | 218.3914 | 309.4077 | 0 | 0 | 309.4077 | 1.011e-06%
2027 | 181 | 181-53F | Tier-1 | Non-HFTD---2 | 4--3 | 1.2419 | 70 | 100% | 294.6229 | 16.95% | 82.71% | 0.3308% | 2.4727 | 0 | 0 | 2.4727 | 0 | 2.2501 | 1.2239 | 1.8385 | 2.2501 | 1.2239 | 1.8385 | 2.497 | 1.3582 | 1.8385 | 0.8393% | 0.081527 | 0.077492 | 3613.7987 | 100.59 | 2747.4951 | 765.7137 | 3770.0887 | 0 | 0 | 3770.0887 | 8.154e-05%
2027 | 555 | 555-21F | Tier-1 | Non-HFTD---19 | 1--3 | 0.052273 | 1 | 100% | 0.45337 | 83.79% | 0% | 16.21% | 0.018804 | 0 | 0 | 0.018804 | 0 | 0.017111 | 0.051515 | 0.33216 | 0.017111 | 0.051515 | 0.33216 | 0.018988 | 0.057167 | 0.33216 | 4.147% | 0.0002394 | 0.00022755 | 1893.7858 | 169.5298 | 576.4627 | 1147.7933 | 1909.7752 | 0 | 0 | 1909.7752 | 6.201e-07%
2027 | 458 | 458-44F | Tier-1 | Non-HFTD---17 | 1--2 | 0.18371 | 11 | 100% | 0.70314 | 61.18% | 0% | 38.82% | 0.021295 | 0 | 0 | 0.021295 | 0 | 0.019378 | 0.18105 | 0.10703 | 0.019378 | 0.18105 | 0.10703 | 0.021504 | 0.20091 | 0.10703 | 3.028% | 0.0008354 | 0.00079405 | 841.684 | 0.51996 | 542.8689 | 298.2952 | 858.6993 | 0 | 0 | 858.6993 | 7.022e-07%
2027 | 311 | 311-1163F | Tier-2 | Tier-2---18 | 3--3 | 0.65624 | 7 | 100% | 46.1951 | 84.69% | 14.76% | 0.5474% | 1.9366 | 0 | 0 | 1.9366 | 0 | 1.7623 | 0.64673 | 2.725 | 1.7623 | 0.64673 | 2.725 | 1.9557 | 0.71769 | 2.725 | 4.192% | 0.018623 | 0.017701 | 2480.5668 | 274.9764 | 742.9932 | 1462.5972 | 2500.341 | 0 | 0 | 2500.341 | 6.386e-05%
2027 | 223 | 223-526R | Tier-1 | Non-HFTD---5 | 2--4 | 2.4396 | 32 | 100% | 76.1007 | 97.65% | 0% | 2.35% | 3.6784 | 0 | 0 | 3.6784 | 0 | 3.3473 | 2.4042 | 1.3923 | 3.3473 | 2.4042 | 1.3923 | 3.7146 | 2.668 | 1.3923 | 4.834% | 0.0098876 | 0.0093982 | 7696.5754 | 1180.4544 | 230.1408 | 6285.9802 | 7705.9964 | 0 | 0 | 7705.9964 | 0.0001213%
2027 | 522 | CB 522 | Tier-2 | Tier-2---9 | 4--5 | 6.96 | 556 | 100% | 1074.3257 | 89.49% | 10.08% | 0.4258% | 47.5925 | 0 | 0 | 47.5925 | 0 | 43.3085 | 6.8591 | 6.314 | 43.3085 | 6.8591 | 6.314 | 48.0602 | 7.6117 | 6.314 | 4.43% | 0.049006 | 0.04658 | 21922.4202 | 3152.3384 | 2334.9737 | 16435.1082 | 22042.3571 | 0 | 0 | 22042.3571 | 0.001569%
2027 | 902 | 902-48 | Tier-1 | Non-HFTD---11 | 2--2 | 3.1718 | 231 | 100% | 11.2569 | 82.99% | 0% | 17.01% | 0.46241 | 0 | 0 | 0.46241 | 0 | 0.42079 | 3.1258 | 0.13462 | 0.42079 | 3.1258 | 0.13462 | 0.46695 | 3.4687 | 0.13462 | 4.108% | 0.0088092 | 0.0083731 | 1277.8565 | 141.3697 | 477.3616 | 659.1252 | 1289.1791 | 0 | 0 | 1289.1791 | 1.525e-05%
2027 | MT1 | CB MT1 | Tier-1 | Non-HFTD---12 | 3--2 | 6.3385 | 192 | 100% | 10.6593 | 55.29% | 0% | 44.71% | 0.29175 | 0 | 0 | 0.29175 | 0 | 0.26549 | 6.2466 | 0.042502 | 0.26549 | 6.2466 | 0.042502 | 0.29462 | 6.9319 | 0.042502 | 2.737% | 0.019313 | 0.018357 | 551.9219 | 0.89395 | 324.0932 | 226.9347 | 564.7715 | 0 | 0 | 564.7715 | 9.621e-06%
2027 | 733 | CB 733 | Tier-1 | Non-HFTD---8 | 3--3 | 5.8684 | 166 | 100% | 28.3507 | 85.6% | 0% | 14.4% | 1.2013 | 0 | 0 | 1.2013 | 0 | 1.0931 | 5.7833 | 0.18902 | 1.0931 | 5.7833 | 0.18902 | 1.2131 | 6.4178 | 0.18902 | 4.237% | 0.016335 | 0.015526 | 1735.6201 | 10.6405 | 1444.5417 | 280.4379 | 1748.6355 | 0 | 0 | 1748.6355 | 3.961e-05%
2027 | 1103 | 1103-13AE | Tier-2 | Tier-2---17 | 1--5 | 0.27027 | 9 | 100% | 94.4662 | 99.77% | 0% | 0.2344% | 4.6651 | 0 | 0 | 4.6651 | 0 | 4.2452 | 0.26635 | 15.9386 | 4.2452 | 0.26635 | 15.9386 | 4.711 | 0.29557 | 15.9386 | 4.938% | 0.001345 | 0.0012784 | 70235.1135 | 11425.6816 | 17.29 | 58792.1418 | 70243.6865 | 0 | 0 | 70243.6865 | 0.0001538%
2027 | 970 | CB 970 | Tier-2 | Tier-2---14 | 1--5 | 0.092045 | 6 | 100% | 251.0066 | 99.97% | 0% | 0.03372% | 12.4206 | 0 | 0 | 12.4206 | 0 | 11.3026 | 0.090711 | 124.6004 | 11.3026 | 0.090711 | 124.6004 | 12.5427 | 0.10066 | 124.6004 | 4.948% | 0.00034 | 0.00032317 | 738254.59 | 119031.8531 | 2302.4993 | 616920.2376 | 738267.5551 | 0 | 0 | 738267.5551 | 0.0004096%
2027 | 523 | CB 523 | Tier-2 | Tier-2---13 | 4--4 | 6.3104 | 290 | 100% | 305.5692 | 37.2% | 61.32% | 1.484% | 5.6264 | 0 | 0 | 5.6264 | 0 | 5.1199 | 6.2189 | 0.82329 | 5.1199 | 6.2189 | 0.82329 | 5.6817 | 6.9012 | 0.82329 | 1.841% | 0.044603 | 0.042395 | 6850.8655 | 637.5043 | 4014.608 | 2198.7533 | 7074.9309 | 0 | 0 | 7074.9309 | 0.0001855%
2027 | 417 | CB 417 | Tier-1 | Non-HFTD---3 | 3--3 | 4.8645 | 180 | 100% | 116.5397 | 41.56% | 55.34% | 3.097% | 2.3977 | 0 | 0 | 2.3977 | 0 | 2.1818 | 4.794 | 0.45512 | 2.1818 | 4.794 | 0.45512 | 2.4212 | 5.32 | 0.45512 | 2.057% | 0.025451 | 0.024191 | 4579.0552 | 115.5393 | 3554.7727 | 908.7432 | 4718.4081 | 0 | 0 | 4718.4081 | 7.907e-05%
2027 | 353 | 353-593F | Tier-2 | Tier-2---7 | 5--5 | 2.0774 | 267 | 100% | 2519.0591 | 99.18% | 0.76% | 0.05848% | 123.6728 | 0 | 0 | 123.6728 | 0 | 112.5405 | 2.0473 | 54.9702 | 112.5405 | 2.0473 | 54.9702 | 124.8882 | 2.2719 | 54.9702 | 4.909% | 0.10537 | 0.10016 | 23906.1611 | 3846.0543 | 163.4883 | 19896.6185 | 23916.3516 | 0 | 0 | 23916.3516 | 0.004078%
2027 | RE1 | CB RE1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.5885 | 32 | 100% | 1.1035 | 28.77% | 0% | 71.23% | 0.015712 | 0 | 0 | 0.015712 | 0 | 0.014298 | 1.5654 | 0.0091336 | 0.014298 | 1.5654 | 0.0091336 | 0.015867 | 1.7372 | 0.0091336 | 1.424% | 0.0036542 | 0.0034733 | 301.9742 | 0.23132 | 105.981 | 195.762 | 313.1767 | 0 | 0 | 313.1767 | 5.181e-07%
2027 | 900 | 900-1166F | Tier-1 | Non-HFTD---7 | 1--4 | 1.1814 | 97 | 100% | 30.0591 | 97.43% | 0% | 2.568% | 1.4497 | 0 | 0 | 1.4497 | 0 | 1.3192 | 1.1643 | 1.1331 | 1.3192 | 1.1643 | 1.1331 | 1.464 | 1.292 | 1.1331 | 4.823% | 0.003966 | 0.0037697 | 7579.2001 | 1157.8569 | 322.158 | 6099.1853 | 7589.3359 | 0 | 0 | 7589.3359 | 4.781e-05%
2027 | 44 | 44-1101F | Tier-1 | Non-HFTD---16 | 2--1 | 2.2459 | 60 | 100% | 2.701 | 28.07% | 0% | 71.93% | 0.037524 | 0 | 0 | 0.037524 | 0 | 0.034146 | 2.2133 | 0.015428 | 0.034146 | 2.2133 | 0.015428 | 0.037892 | 2.4561 | 0.015428 | 1.389% | 0.0069664 | 0.0066216 | 387.7182 | 2.2876 | 121.4718 | 263.9588 | 402.2428 | 0 | 0 | 402.2428 | 1.237e-06%
2027 | 149 | CB 149 | Tier-1 | Non-HFTD---9 | 1--4 | 0.88352 | 8 | 100% | 21.25 | 97.47% | 0% | 2.53% | 1.0253 | 0 | 0 | 1.0253 | 0 | 0.93297 | 0.87071 | 1.0715 | 0.93297 | 0.87071 | 1.0715 | 1.0353 | 0.96624 | 1.0715 | 4.825% | 0.0036132 | 0.0034343 | 5881.2185 | 1195.3712 | 13.6562 | 4672.1912 | 5888.968 | 0 | 0 | 5888.968 | 3.381e-05%
2027 | 79 | 79-679R | Tier-3 | Tier-3---3 | 5--5 | 7.3706 | 429 | 100% | 18448.5828 | 98.9% | 1.079% | 0.02427% | 903.134 | 0 | 0 | 903.134 | 0 | 821.8397 | 7.2638 | 113.1423 | 821.8397 | 7.2638 | 113.1423 | 912.01 | 8.0607 | 113.1423 | 4.895% | 0.3939 | 0.3744 | 46835.416 | 7852.0838 | 464.0518 | 38519.2804 | 46862.3143 | 0 | 0 | 46862.3143 | 0.02978%
2027 | 153 | CB 153 | Tier-1 | Non-HFTD---6 | 4--2 | 14.7847 | 313 | 100% | 50.6159 | 80.4% | 0% | 19.6% | 2.0143 | 0 | 0 | 2.0143 | 0 | 1.833 | 14.5703 | 0.1258 | 1.833 | 14.5703 | 0.1258 | 2.0341 | 16.1689 | 0.1258 | 3.98% | 0.04186 | 0.039788 | 1209.1779 | 2.388 | 984.9183 | 221.8717 | 1221.5227 | 0 | 0 | 1221.5227 | 6.642e-05%
2027 | 545 | 545-47F | Tier-1 | Non-HFTD---4 | 3--4 | 2.6369 | 24 | 100% | 110.9793 | 1.36% | 96.25% | 2.393% | 0.074705 | 0 | 0 | 0.074705 | 0 | 0.067981 | 2.5987 | 0.02616 | 0.067981 | 2.5987 | 0.02616 | 0.07544 | 2.8838 | 0.02616 | 0.06731% | 0.019055 | 0.018112 | 5824.1558 | 6.8519 | 5193.1991 | 624.1048 | 6123.3406 | 0 | 0 | 6123.3406 | 2.464e-06%
2027 | 416 | 416-37F | Tier-1 | Non-HFTD---17 | 1--1 | 1.2439 | 52 | 100% | 1.7227 | 46.57% | 0% | 53.43% | 0.039708 | 0 | 0 | 0.039708 | 0 | 0.036134 | 1.2259 | 0.029476 | 0.036134 | 1.2259 | 0.029476 | 0.040099 | 1.3604 | 0.029476 | 2.305% | 0.0035008 | 0.0033275 | 492.0848 | 1.381 | 245.7278 | 244.9761 | 505.7782 | 0 | 0 | 505.7782 | 1.309e-06%
2027 | 540 | 540-241R | Tier-2 | Tier-2---9 | 4--5 | 1.2638 | 89 | 100% | 833.6308 | 67.75% | 32.17% | 0.07637% | 27.9571 | 0 | 0 | 27.9571 | 0 | 25.4406 | 1.2455 | 20.426 | 25.4406 | 1.2455 | 20.426 | 28.2319 | 1.3822 | 20.426 | 3.354% | 0.047942 | 0.045568 | 17388.4645 | 1898.6352 | 5274.4553 | 10215.374 | 17680.5002 | 0 | 0 | 17680.5002 | 0.0009219%
2027 | 276 | CB 276 | Tier-1 | Non-HFTD---10 | 3--2 | 1.2919 | 18 | 100% | 26.0793 | 53.94% | 42.4% | 3.659% | 0.69637 | 0 | 0 | 0.69637 | 0 | 0.63369 | 1.2731 | 0.49774 | 0.63369 | 1.2731 | 0.49774 | 0.70322 | 1.4128 | 0.49774 | 2.67% | 0.01954 | 0.018573 | 1334.6469 | 19.5495 | 1128.3922 | 186.7052 | 1366.6586 | 0 | 0 | 1366.6586 | 2.296e-05%
2027 | 107 | CB 107 | Tier-1 | Non-HFTD---13 | 2--2 | 1.8139 | 62 | 100% | 5.6413 | 73.95% | 0% | 26.05% | 0.2065 | 0 | 0 | 0.2065 | 0 | 0.18791 | 1.7876 | 0.10512 | 0.18791 | 1.7876 | 0.10512 | 0.20853 | 1.9837 | 0.10512 | 3.66% | 0.005587 | 0.0053104 | 1009.7148 | 3.394 | 755.2275 | 251.0933 | 1023.4136 | 0 | 0 | 1023.4136 | 6.809e-06%
2027 | FM1 | CB FM1 | Tier-1 | Non-HFTD---8 | 3--3 | 4.6271 | 262 | 100% | 36.2346 | 19.67% | 69.95% | 10.38% | 0.35276 | 0 | 0 | 0.35276 | 0 | 0.32101 | 4.56 | 0.070397 | 0.32101 | 4.56 | 0.070397 | 0.35623 | 5.0604 | 0.070397 | 0.9736% | 0.019823 | 0.018842 | 1827.9252 | 40.3343 | 1310.0854 | 477.5055 | 1904.3969 | 0 | 0 | 1904.3969 | 1.163e-05%
2027 | 1418 | 1418-581R | Tier-1 | Non-HFTD---13 | 2--2 | 1.5783 | 24 | 100% | 5.0692 | 77.2% | 0% | 22.8% | 0.19371 | 0 | 0 | 0.19371 | 0 | 0.17627 | 1.5554 | 0.11333 | 0.17627 | 1.5554 | 0.11333 | 0.19561 | 1.726 | 0.11333 | 3.821% | 0.0055174 | 0.0052443 | 918.7654 | 53.7653 | 399.6633 | 465.3367 | 929.6757 | 0 | 0 | 929.6757 | 6.388e-06%
2027 | BK2 | CB BK2 | Tier-1 | Non-HFTD---9 | 3--3 | 1.5103 | 31 | 100% | 25.856 | 1.714% | 93.1% | 5.186% | 0.021942 | 0 | 0 | 0.021942 | 0 | 0.019967 | 1.4884 | 0.013415 | 0.019967 | 1.4884 | 0.013415 | 0.022158 | 1.6517 | 0.013415 | 0.08486% | 0.015094 | 0.014347 | 1712.9776 | 1.9461 | 1498.4147 | 212.6168 | 1800.6564 | 0 | 0 | 1800.6564 | 7.236e-07%
2027 | 1090 | 1090-73F | Tier-3 | Tier-3---10 | 4--5 | 10.606 | 589 | 100% | 5899.0454 | 99.62% | 0.2521% | 0.1275% | 290.8942 | 0 | 0 | 290.8942 | 0 | 264.7098 | 10.4523 | 25.3256 | 264.7098 | 10.4523 | 25.3256 | 293.7531 | 11.5991 | 25.3256 | 4.931% | 0.046754 | 0.044439 | 126173.0725 | 23873.2693 | 324.7773 | 101975.0259 | 126198.0175 | 0 | 0 | 126198.0175 | 0.009593%
2027 | 718 | CB 718 | Tier-1 | Non-HFTD---18 | 2--1 | 1.4828 | 46 | 100% | 2.2312 | 31.13% | 0% | 68.87% | 0.034382 | 0 | 0 | 0.034382 | 0 | 0.031287 | 1.4613 | 0.021411 | 0.031287 | 1.4613 | 0.021411 | 0.03472 | 1.6216 | 0.021411 | 1.541% | 0.0057306 | 0.0054469 | 389.3448 | 10.2878 | 84.1668 | 294.8901 | 403.3088 | 0 | 0 | 403.3088 | 1.134e-06%
2027 | 358 | 358-682F | Tier-3 | Tier-3---3 | 5--5 | 12.5079 | 454 | 100% | 37602.1184 | 98.59% | 1.386% | 0.02088% | 1835.1165 | 0 | 0 | 1835.1165 | 0 | 1669.931 | 12.3266 | 135.4742 | 1669.931 | 12.3266 | 135.4742 | 1853.1519 | 13.679 | 135.4742 | 4.88% | 0.54241 | 0.51556 | 69323.599 | 12097.0224 | 871.8787 | 56354.6979 | 69374.3945 | 0 | 0 | 69374.3945 | 0.06052%
2027 | 176 | 176-194R | Tier-3 | Tier-3---9 | 5--5 | 9.0746 | 469 | 100% | 4934.1603 | 97.7% | 2.178% | 0.1196% | 238.628 | 0 | 0 | 238.628 | 0 | 217.1483 | 8.943 | 24.2813 | 217.1483 | 8.943 | 24.2813 | 240.9733 | 9.9242 | 24.2813 | 4.836% | 0.21542 | 0.20476 | 22904.8386 | 3771.0766 | 447.8074 | 18685.9546 | 22932.2512 | 0 | 0 | 22932.2512 | 0.007869%
2027 | 364 | 364-49R | Tier-1 | Non-HFTD---3 | 4--3 | 10.7492 | 161 | 100% | 138.1668 | 14.34% | 80.38% | 5.28% | 0.98106 | 0 | 0 | 0.98106 | 0 | 0.89275 | 10.5934 | 0.084274 | 0.89275 | 10.5934 | 0.084274 | 0.9907 | 11.7556 | 0.084274 | 0.7101% | 0.035529 | 0.033771 | 3888.8227 | 11.2159 | 3396.2712 | 481.3356 | 4062.2935 | 0 | 0 | 4062.2935 | 3.235e-05%
2027 | 154 | 154-13 | Tier-1 | Non-HFTD---20 | 1--1 | 0.50816 | 9 | 100% | 0.28839 | 3.646% | 0% | 96.35% | 0.00052053 | 0 | 0 | 0.00052053 | 0 | 0.00047368 | 0.50079 | 0.00094586 | 0.00047368 | 0.50079 | 0.00094586 | 0.00052565 | 0.55574 | 0.00094586 | 0.1805% | 0.0014332 | 0.0013623 | 201.2217 | 0.14589 | 24.9499 | 176.1259 | 211.3187 | 0 | 0 | 211.3187 | 1.717e-08%
2027 | 902 | 902-364F | Tier-1 | Non-HFTD---15 | 1--4 | 0.10985 | 8 | 100% | 3.0036 | 96.46% | 0% | 3.536% | 0.14342 | 0 | 0 | 0.14342 | 0 | 0.13051 | 0.10826 | 1.2056 | 0.13051 | 0.10826 | 1.2056 | 0.14483 | 0.12013 | 1.2056 | 4.775% | 0.0004588 | 0.00043609 | 6546.743 | 1491.2109 | 21.0318 | 5034.5003 | 6558.8002 | 0 | 0 | 6558.8002 | 4.73e-06%
2027 | 144 | CB 144 | Tier-1 | Non-HFTD---3 | 3--4 | 4.3479 | 193 | 100% | 116.3493 | 70.7% | 26.46% | 2.846% | 4.0717 | 0 | 0 | 4.0717 | 0 | 3.7052 | 4.2849 | 0.86472 | 3.7052 | 4.2849 | 0.86472 | 4.1117 | 4.755 | 0.86472 | 3.5% | 0.021258 | 0.020206 | 5473.2508 | 269.7276 | 3553.0613 | 1650.4619 | 5556.7709 | 0 | 0 | 5556.7709 | 0.0001343%
2027 | 146 | 146-275R | Tier-1 | Non-HFTD---5 | 2--4 | 0.74015 | 44 | 100% | 50.1764 | 31.43% | 67.56% | 1.005% | 0.78065 | 0 | 0 | 0.78065 | 0 | 0.71038 | 0.72942 | 0.97389 | 0.71038 | 0.72942 | 0.97389 | 0.78832 | 0.80945 | 0.97389 | 1.556% | 0.0089436 | 0.0085009 | 5610.3123 | 271.1706 | 3574.616 | 1764.5257 | 5810.6541 | 0 | 0 | 5810.6541 | 2.574e-05%
2027 | 289 | 289-1559 | Tier-1 | Non-HFTD---15 | 2--2 | 0.52288 | 72 | 100% | 4.417 | 3.139% | 88.74% | 8.122% | 0.0068636 | 0 | 0 | 0.0068636 | 0 | 0.0062458 | 0.51529 | 0.012121 | 0.0062458 | 0.51529 | 0.012121 | 0.0069311 | 0.57183 | 0.012121 | 0.1554% | 0.0072536 | 0.0068945 | 608.9324 | 2.7259 | 506.3554 | 99.851 | 639.6487 | 0 | 0 | 639.6487 | 2.263e-07%
2027 | 138 | CB 138 | Tier-1 | Non-HFTD---17 | 1--2 | 0.18636 | 2 | 100% | 0.7202 | 42.47% | 0% | 57.53% | 0.01514 | 0 | 0 | 0.01514 | 0 | 0.013778 | 0.18366 | 0.075016 | 0.013778 | 0.18366 | 0.075016 | 0.015289 | 0.20381 | 0.075016 | 2.102% | 0.0010424 | 0.0009908 | 690.9099 | 0.2991 | 329.5323 | 361.0785 | 711.6101 | 0 | 0 | 711.6101 | 4.993e-07%
2027 | 1001 | 1001-1820F | Tier-2 | Tier-2---5 | 5--5 | 6.479 | 1292 | 100% | 4222.2471 | 91.41% | 8.486% | 0.103% | 191.0494 | 0 | 0 | 191.0494 | 0 | 173.8523 | 6.385 | 27.2281 | 173.8523 | 6.385 | 27.2281 | 192.927 | 7.0856 | 27.2281 | 4.525% | 0.12846 | 0.1221 | 32868.2878 | 4904.2029 | 2558.3215 | 25405.7635 | 33015.3127 | 0 | 0 | 33015.3127 | 0.0063%
2027 | PL2 | CB PL2 | Tier-1 | Non-HFTD---12 | 3--2 | 9.8748 | 367 | 100% | 14.4457 | 51.29% | 0% | 48.71% | 0.36674 | 0 | 0 | 0.36674 | 0 | 0.33373 | 9.7316 | 0.034293 | 0.33373 | 9.7316 | 0.034293 | 0.37034 | 10.7993 | 0.034293 | 2.539% | 0.027084 | 0.025743 | 533.3741 | 0.1955 | 297.1585 | 236.0201 | 546.9048 | 0 | 0 | 546.9048 | 1.209e-05%
2027 | 209 | CB 209 | Tier-1 | Non-HFTD---15 | 1--3 | 0.2739 | 2 | 100% | 2.9977 | 95.12% | 0% | 4.884% | 0.14114 | 0 | 0 | 0.14114 | 0 | 0.12844 | 0.26993 | 0.4758 | 0.12844 | 0.26993 | 0.4758 | 0.14253 | 0.29955 | 0.4758 | 4.708% | 0.000675 | 0.00064159 | 4441.0443 | 20.5708 | 4119.0788 | 301.3948 | 4452.339 | 0 | 0 | 4452.339 | 4.654e-06%
2027 | 79 | 79-685R | Tier-3 | Tier-3---14 | 5--4 | 3.9579 | 58 | 100% | 2564.7524 | 99.37% | 0.5359% | 0.0899% | 126.1608 | 0 | 0 | 126.1608 | 0 | 114.8046 | 3.9005 | 29.433 | 114.8046 | 3.9005 | 29.433 | 127.4007 | 4.3285 | 29.433 | 4.919% | 0.43155 | 0.41019 | 5943.1342 | 854.3477 | 28.1313 | 5060.6552 | 5945.071 | 0 | 0 | 5945.071 | 0.00416%
2027 | 230 | CB 230 | Tier-2 | Tier-2---14 | 1--5 | 0.62576 | 81 | 100% | 212.8275 | 99.81% | 0% | 0.1866% | 10.5153 | 0 | 0 | 10.5153 | 0 | 9.5688 | 0.61668 | 15.5165 | 9.5688 | 0.61668 | 15.5165 | 10.6186 | 0.68435 | 15.5165 | 4.941% | 0.0025822 | 0.0024544 | 82420.9788 | 12968.0928 | 2517.612 | 66935.274 | 82428.9864 | 0 | 0 | 82428.9864 | 0.0003468%
2027 | 415 | 415-1237R | Tier-1 | Non-HFTD---3 | 4--3 | 9.2329 | 453 | 100% | 133.0958 | 12.64% | 83.05% | 4.312% | 0.83274 | 0 | 0 | 0.83274 | 0 | 0.75778 | 9.0991 | 0.083282 | 0.75778 | 9.0991 | 0.083282 | 0.84093 | 10.0974 | 0.083282 | 0.6257% | 0.037795 | 0.035924 | 3521.4997 | 33.7505 | 3007.5656 | 480.1837 | 3681.7114 | 0 | 0 | 3681.7114 | 2.746e-05%
2027 | 176 | 176-200F | Tier-3 | Tier-3---15 | 5--4 | 1.165 | 81 | 100% | 1635.841 | 89.24% | 10.7% | 0.05535% | 72.2645 | 0 | 0 | 72.2645 | 0 | 65.7597 | 1.1481 | 57.2759 | 65.7597 | 1.1481 | 57.2759 | 72.9747 | 1.2741 | 57.2759 | 4.418% | 0.18529 | 0.17612 | 8828.4206 | 1287.3516 | 863.0873 | 6677.9817 | 8877.8734 | 0 | 0 | 8877.8734 | 0.002383%
2027 | WA6 | CB WA6 | Tier-1 | Non-HFTD---8 | 4--2 | 13.9047 | 410 | 100% | 38.8392 | 75.37% | 0% | 24.63% | 1.4489 | 0 | 0 | 1.4489 | 0 | 1.3185 | 13.7031 | 0.09622 | 1.3185 | 13.7031 | 0.09622 | 1.4632 | 15.2066 | 0.09622 | 3.731% | 0.043551 | 0.041395 | 891.8131 | 93.2124 | 376.5501 | 422.0507 | 903.2543 | 0 | 0 | 903.2543 | 4.778e-05%
2027 | 1235 | CB 1235 | Tier-2 | Tier-2---6 | 4--5 | 20.7706 | 2370 | 100% | 6645.572 | 99.09% | 0.6868% | 0.2213% | 325.9686 | 0 | 0 | 325.9686 | 0 | 296.627 | 20.4694 | 14.4912 | 296.627 | 20.4694 | 14.4912 | 329.1722 | 22.7153 | 14.4912 | 4.905% | 0.082825 | 0.078725 | 80236.4987 | 14594.2716 | 649.5597 | 64992.6674 | 80274.4439 | 0 | 0 | 80274.4439 | 0.01075%
2027 | 284 | 284-660R | Tier-1 | Non-HFTD---5 | 2--4 | 0.21894 | 31 | 100% | 67.7111 | 37.42% | 62.28% | 0.3086% | 1.2541 | 0 | 0 | 1.2541 | 0 | 1.1412 | 0.21576 | 5.2891 | 1.1412 | 0.21576 | 5.2891 | 1.2664 | 0.23944 | 5.2891 | 1.852% | 0.0068676 | 0.0065277 | 9859.4941 | 664.3708 | 5544.4409 | 3650.6824 | 10180.8369 | 0 | 0 | 10180.8369 | 4.136e-05%
2027 | 856 | 856-1141R | Tier-1 | Non-HFTD---7 | 2--3 | 3.289 | 191 | 100% | 34.972 | 93.55% | 0% | 6.449% | 1.6195 | 0 | 0 | 1.6195 | 0 | 1.4737 | 3.2413 | 0.45466 | 1.4737 | 3.2413 | 0.45466 | 1.6354 | 3.5969 | 0.45466 | 4.631% | 0.0095222 | 0.0090509 | 3672.677 | 493.2945 | 440.7828 | 2738.5997 | 3685.0115 | 0 | 0 | 3685.0115 | 5.34e-05%
2027 | 221 | 221-675R | Tier-2 | Tier-2---8 | 5--4 | 7.0073 | 245 | 100% | 2055.424 | 99.51% | 0.3331% | 0.1572% | 101.2446 | 0 | 0 | 101.2446 | 0 | 92.1312 | 6.9057 | 13.3412 | 92.1312 | 6.9057 | 13.3412 | 102.2396 | 7.6634 | 13.3412 | 4.926% | 0.22072 | 0.20979 | 9312.3427 | 1344.1868 | 80.6907 | 7887.4652 | 9314.7205 | 0 | 0 | 9314.7205 | 0.003339%
2027 | 1001 | 1001-1232F | Tier-1 | Non-HFTD---15 | 1--4 | 0.060606 | 13 | 100% | 3.7082 | 98.25% | 0% | 1.746% | 0.18035 | 0 | 0 | 0.18035 | 0 | 0.16412 | 0.059727 | 2.7477 | 0.16412 | 0.059727 | 2.7477 | 0.18212 | 0.06628 | 2.7477 | 4.864% | 0.0002536 | 0.00024105 | 14622.1214 | 2186.2186 | 960.6365 | 11475.2662 | 14635.4188 | 0 | 0 | 14635.4188 | 5.947e-06%
2027 | 789 | 789-15 | Tier-1 | Non-HFTD---1 | 1--5 | 1.1117 | 192 | 100% | 761.9806 | 99.91% | 0% | 0.08626% | 37.6855 | 0 | 0 | 37.6855 | 0 | 34.2933 | 1.0956 | 31.3008 | 34.2933 | 1.0956 | 31.3008 | 38.0559 | 1.2158 | 31.3008 | 4.946% | 0.0041662 | 0.00396 | 182895.8194 | 29633.7506 | 30.7403 | 153231.3285 | 182904.0354 | 0 | 0 | 182904.0354 | 0.001243%
2027 | 854 | CB 854 | Tier-1 | Non-HFTD---15 | 1--3 | 0.2767 | 0 | 100% | 4.0846 | 92.31% | 0% | 7.692% | 0.18664 | 0 | 0 | 0.18664 | 0 | 0.16984 | 0.27269 | 0.62281 | 0.16984 | 0.27269 | 0.62281 | 0.18847 | 0.30261 | 0.62281 | 4.569% | 0.0011248 | 0.0010691 | 3631.4237 | 108.5173 | 2707.56 | 815.3464 | 3645.9705 | 0 | 0 | 3645.9705 | 6.155e-06%
2027 | AM3 | CB AM3 | Tier-1 | Non-HFTD---12 | 4--1 | 11.0803 | 284 | 100% | 10.6772 | 32.41% | 0% | 67.59% | 0.17131 | 0 | 0 | 0.17131 | 0 | 0.15589 | 10.9196 | 0.014276 | 0.15589 | 10.9196 | 0.014276 | 0.173 | 12.1177 | 0.014276 | 1.604% | 0.029862 | 0.028384 | 357.5503 | 0.35634 | 136.7746 | 220.4194 | 370.1352 | 0 | 0 | 370.1352 | 5.649e-06%
2027 | 1073 | 1073-872F | Tier-2 | Tier-2---20 | 3--2 | 0.61936 | 96 | 100% | 17.9659 | 86.84% | 10.72% | 2.434% | 0.7723 | 0 | 0 | 0.7723 | 0 | 0.70278 | 0.61038 | 1.1514 | 0.70278 | 0.61038 | 1.1514 | 0.77989 | 0.67735 | 1.1514 | 4.299% | 0.018584 | 0.017664 | 966.7183 | 136.5279 | 98.6169 | 731.5734 | 973.3425 | 0 | 0 | 973.3425 | 2.547e-05%
2027 | 357 | 357-50R | Tier-3 | Tier-3---4 | 5--5 | 10.8632 | 1095 | 100% | 10432.4887 | 97.04% | 2.884% | 0.07824% | 501.113 | 0 | 0 | 501.113 | 0 | 456.006 | 10.7057 | 42.5946 | 456.006 | 10.7057 | 42.5946 | 506.0379 | 11.8803 | 42.5946 | 4.803% | 0.14913 | 0.14175 | 69957.169 | 13067.3057 | 1874.1098 | 55015.7535 | 70065.0754 | 0 | 0 | 70065.0754 | 0.01652%
2027 | 417 | 417-41 | Tier-1 | Non-HFTD---19 | 1--3 | 0.067056 | 2 | 100% | 0.62272 | 87.14% | 0% | 12.86% | 0.02686 | 0 | 0 | 0.02686 | 0 | 0.024442 | 0.066084 | 0.36987 | 0.024442 | 0.066084 | 0.36987 | 0.027124 | 0.073334 | 0.36987 | 4.313% | 0.0002544 | 0.00024181 | 2447.8133 | 0.23691 | 2161.5664 | 286.0099 | 2464.2099 | 0 | 0 | 2464.2099 | 8.857e-07%
2027 | 750 | CB 750 | Tier-1 | Non-HFTD---4 | 1--5 | 1.0979 | 9 | 100% | 147.1702 | 99.68% | 0% | 0.3223% | 7.2614 | 0 | 0 | 7.2614 | 0 | 6.6078 | 1.082 | 6.1071 | 6.6078 | 1.082 | 6.1071 | 7.3328 | 1.2007 | 6.1071 | 4.934% | 0.0040188 | 0.0038199 | 36620.4268 | 8634.8324 | 1589.051 | 26396.5433 | 36626.5736 | 0 | 0 | 36626.5736 | 0.0002395%
2027 | 547 | CB 547 | Tier-1 | Non-HFTD---9 | 2--3 | 3.8859 | 81 | 100% | 19.4827 | 85.43% | 0% | 14.57% | 0.82389 | 0 | 0 | 0.82389 | 0 | 0.74973 | 3.8296 | 0.19577 | 0.74973 | 3.8296 | 0.19577 | 0.83199 | 4.2498 | 0.19577 | 4.229% | 0.011393 | 0.010829 | 1710.1181 | 8.849 | 1430.5531 | 270.716 | 1723.0928 | 0 | 0 | 1723.0928 | 2.717e-05%
2027 | FB1 | CB FB1 | Tier-2 | Tier-2---11 | 4--4 | 7.7129 | 412 | 100% | 346.5871 | 36.93% | 61.45% | 1.621% | 6.3355 | 0 | 0 | 6.3355 | 0 | 5.7652 | 7.601 | 0.75848 | 5.7652 | 7.601 | 0.75848 | 6.3978 | 8.435 | 0.75848 | 1.828% | 0.04664 | 0.044331 | 7431.1135 | 852.2072 | 4097.3369 | 2481.5694 | 7675.1976 | 0 | 0 | 7675.1976 | 0.0002089%
2027 | 278 | 278-630 | Tier-1 | Non-HFTD---2 | 4--4 | 10.8269 | 311 | 100% | 273.7142 | 5.715% | 91.87% | 2.413% | 0.77427 | 0 | 0 | 0.77427 | 0 | 0.70457 | 10.6699 | 0.066034 | 0.70457 | 10.6699 | 0.066034 | 0.78188 | 11.8406 | 0.066034 | 0.2829% | 0.044769 | 0.042553 | 6113.9234 | 15.3034 | 5481.2841 | 617.3359 | 6414.1279 | 0 | 0 | 6414.1279 | 2.553e-05%
2027 | 1077 | 1077-8R | Tier-1 | Non-HFTD---9 | 2--3 | 2.8041 | 50 | 100% | 24.3832 | 90.75% | 0% | 9.248% | 1.0954 | 0 | 0 | 1.0954 | 0 | 0.99675 | 2.7635 | 0.36069 | 0.99675 | 2.7635 | 0.36069 | 1.1061 | 3.0667 | 0.36069 | 4.492% | 0.0094446 | 0.0089771 | 2581.7093 | 369.621 | 97.6273 | 2114.461 | 2594.143 | 0 | 0 | 2594.143 | 3.612e-05%
2027 | 780 | CB 780 | Tier-1 | Non-HFTD---6 | 3--3 | 4.5818 | 470 | 100% | 78.9953 | 26.13% | 69.84% | 4.031% | 1.0216 | 0 | 0 | 1.0216 | 0 | 0.92962 | 4.5154 | 0.20588 | 0.92962 | 4.5154 | 0.20588 | 1.0316 | 5.0108 | 0.20588 | 1.293% | 0.024043 | 0.022852 | 3285.6386 | 58.4415 | 2545.5101 | 681.687 | 3412.0448 | 0 | 0 | 3412.0448 | 3.369e-05%
2027 | 220 | CB 220 | Tier-3 | Tier-3---21 | 1--2 | 0.011932 | 0 | 100% | 0.033535 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.011759 | 0 | 0 | 0.011759 | 0 | 0 | 0.013049 | 0 | 0% | 4.74e-05 | 4.5054e-05 | 707.4933 | 0.53237 | 64.2692 | 642.6918 | 744.3381 | 0 | 0 | 744.3381 | 0%
2027 | 487 | CB 487 | Tier-1 | Non-HFTD---19 | 1--3 | 0.046212 | 7 | 100% | 0.46682 | 83.57% | 0% | 16.43% | 0.01931 | 0 | 0 | 0.01931 | 0 | 0.017572 | 0.045542 | 0.38584 | 0.017572 | 0.045542 | 0.38584 | 0.0195 | 0.050539 | 0.38584 | 4.136% | 0.0001976 | 0.00018782 | 2362.465 | 321.7419 | 35.2696 | 2005.4535 | 2382.6846 | 0 | 0 | 2382.6846 | 6.368e-07%
2027 | FB2 | CB FB2 | Tier-2 | Tier-2---9 | 4--5 | 5.2678 | 335 | 100% | 1029.5845 | 94.33% | 5.316% | 0.3556% | 48.074 | 0 | 0 | 48.074 | 0 | 43.7467 | 5.1914 | 8.4267 | 43.7467 | 5.1914 | 8.4267 | 48.5465 | 5.761 | 8.4267 | 4.669% | 0.045688 | 0.043427 | 22535.0189 | 4971.8159 | 1116.7336 | 16446.4695 | 22601.5779 | 0 | 0 | 22601.5779 | 0.001585%
2027 | 1073 | 1073-480 | Tier-1 | Non-HFTD---4 | 3--4 | 0.27083 | 8 | 100% | 99.1186 | 2.789% | 97.03% | 0.1826% | 0.13682 | 0 | 0 | 0.13682 | 0 | 0.1245 | 0.26691 | 0.46646 | 0.1245 | 0.26691 | 0.46646 | 0.13816 | 0.29619 | 0.46646 | 0.138% | 0.017172 | 0.016322 | 5772.1746 | 21.6593 | 5192.9171 | 557.5981 | 6064.3945 | 0 | 0 | 6064.3945 | 4.512e-06%
2027 | 400 | CB 400 | Tier-1 | Non-HFTD---10 | 4--2 | 12.2015 | 190 | 100% | 19.3977 | 65.59% | 0% | 34.41% | 0.62975 | 0 | 0 | 0.62975 | 0 | 0.57306 | 12.0246 | 0.047657 | 0.57306 | 12.0246 | 0.047657 | 0.63594 | 13.3439 | 0.047657 | 3.247% | 0.031276 | 0.029728 | 620.2148 | 1.8495 | 419.0813 | 199.284 | 631.3303 | 0 | 0 | 631.3303 | 2.077e-05%
2027 | 521 | 521-32R | Tier-3 | Tier-3---4 | 5--5 | 9.9971 | 609 | 100% | 12241.7135 | 99.38% | 0.5642% | 0.05689% | 602.2012 | 0 | 0 | 602.2012 | 0 | 547.9949 | 9.8522 | 55.6218 | 547.9949 | 9.8522 | 55.6218 | 608.1196 | 10.9331 | 55.6218 | 4.919% | 0.14844 | 0.14109 | 82470.5463 | 14293.5118 | 425.937 | 67751.0975 | 82497.2218 | 0 | 0 | 82497.2218 | 0.01986%
2027 | 286 | CB 286 | Tier-1 | Non-HFTD---2 | 4--3 | 12.3718 | 1211 | 100% | 207.2412 | 65.65% | 29.54% | 4.807% | 6.7349 | 0 | 0 | 6.7349 | 0 | 6.1286 | 12.1924 | 0.50266 | 6.1286 | 12.1924 | 0.50266 | 6.8011 | 13.5302 | 0.50266 | 3.25% | 0.045864 | 0.043593 | 4518.6432 | 500.9662 | 1809.8664 | 2207.8107 | 4599.4713 | 0 | 0 | 4599.4713 | 0.0002221%
2027 | 540 | CB 540 | Tier-2 | Tier-2---17 | 1--5 | 0.93788 | 198 | 100% | 67.245 | 99.24% | 0% | 0.7576% | 3.3034 | 0 | 0 | 3.3034 | 0 | 3.0061 | 0.92428 | 3.2523 | 3.0061 | 0.92428 | 3.2523 | 3.3359 | 1.0257 | 3.2523 | 4.913% | 0.0036022 | 0.0034239 | 18667.7627 | 2802.0205 | 1252.6198 | 14613.1224 | 18675.1274 | 0 | 0 | 18675.1274 | 0.0001089%
2027 | 81 | 81-177AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.11456 | 4 | 100% | 0.23558 | 5.771% | 0% | 94.23% | 0.00067299 | 0 | 0 | 0.00067299 | 0 | 0.00061242 | 0.1129 | 0.0054244 | 0.00061242 | 0.1129 | 0.0054244 | 0.00067961 | 0.12529 | 0.0054244 | 0.2857% | 0.0005608 | 0.00053304 | 420.0857 | 0.29786 | 60.2022 | 359.5856 | 440.7003 | 0 | 0 | 440.7003 | 2.219e-08%
2027 | 235 | 235-899R | Tier-2 | Tier-2---1 | 5--5 | 14.5858 | 915 | 100% | 23678.6611 | 98.37% | 1.593% | 0.04039% | 1152.9446 | 0 | 0 | 1152.9446 | 0 | 1049.1639 | 14.3743 | 72.9889 | 1049.1639 | 14.3743 | 72.9889 | 1164.2757 | 15.9514 | 72.9889 | 4.869% | 0.15496 | 0.14729 | 152800.2562 | 27483.3247 | 2386.7614 | 122930.1701 | 152930.2625 | 0 | 0 | 152930.2625 | 0.03802%
2027 | 453 | 453-41 | Tier-1 | Non-HFTD---15 | 1--3 | 0.43601 | 31 | 100% | 2.6009 | 88.95% | 0% | 11.05% | 0.11451 | 0 | 0 | 0.11451 | 0 | 0.10421 | 0.42968 | 0.24252 | 0.10421 | 0.42968 | 0.24252 | 0.11564 | 0.47683 | 0.24252 | 4.403% | 0.0012658 | 0.0012031 | 2054.725 | 0.17088 | 1848.26 | 206.2942 | 2066.5516 | 0 | 0 | 2066.5516 | 3.776e-06%
2027 | 493 | 493-485F | Tier-1 | Non-HFTD---11 | 1--4 | 0.31738 | 26 | 100% | 12.8826 | 97.53% | 0% | 2.467% | 0.62196 | 0 | 0 | 0.62196 | 0 | 0.56597 | 0.31278 | 1.8095 | 0.56597 | 0.31278 | 1.8095 | 0.62807 | 0.3471 | 1.8095 | 4.828% | 0.0014534 | 0.0013815 | 8863.7485 | 1806.2326 | 712.2066 | 6345.3093 | 8875.1362 | 0 | 0 | 8875.1362 | 2.051e-05%
2027 | 445 | 445-19R | Tier-2 | Tier-2---8 | 5--3 | 11.1993 | 195 | 100% | 1766.7037 | 84.73% | 14.9% | 0.3714% | 74.0952 | 0 | 0 | 74.0952 | 0 | 67.4256 | 11.0369 | 6.1091 | 67.4256 | 11.0369 | 6.1091 | 74.8234 | 12.2478 | 6.1091 | 4.194% | 0.56527 | 0.53729 | 3125.4156 | 351.5514 | 420.2841 | 2353.5801 | 3150.2749 | 0 | 0 | 3150.2749 | 0.002443%
2027 | 702 | CB 702 | Tier-1 | Non-HFTD---5 | 2--4 | 1.5752 | 2 | 100% | 63.7539 | 98.86% | 0% | 1.141% | 3.1198 | 0 | 0 | 3.1198 | 0 | 2.839 | 1.5524 | 1.8288 | 2.839 | 1.5524 | 1.8288 | 3.1505 | 1.7227 | 1.8288 | 4.894% | 0.005363 | 0.0050975 | 11887.738 | 811.1818 | 6774.97 | 4301.5862 | 11894.8026 | 0 | 0 | 11894.8026 | 0.0001029%
2027 | 94 | CB 94 | Tier-1 | Non-HFTD---5 | 2--4 | 3.3957 | 155 | 100% | 70.2599 | 96.42% | 0% | 3.58% | 3.3534 | 0 | 0 | 3.3534 | 0 | 3.0515 | 3.3464 | 0.91187 | 3.0515 | 3.3464 | 0.91187 | 3.3863 | 3.7136 | 0.91187 | 4.773% | 0.011842 | 0.011256 | 5932.9129 | 699.7774 | 1458.5408 | 3774.5947 | 5943.974 | 0 | 0 | 5943.974 | 0.0001106%
2027 | 130 | 130-13F | Tier-1 | Non-HFTD---14 | 3--1 | 5.4246 | 122 | 100% | 6.0639 | 48.34% | 0% | 51.66% | 0.14511 | 0 | 0 | 0.14511 | 0 | 0.13205 | 5.346 | 0.0247 | 0.13205 | 5.346 | 0.0247 | 0.14654 | 5.9325 | 0.0247 | 2.393% | 0.013826 | 0.013142 | 438.5851 | 0.71643 | 229.2325 | 208.6361 | 450.3837 | 0 | 0 | 450.3837 | 4.785e-06%
2027 | 402 | 402-30AE | Tier-1 | Non-HFTD---14 | 2--2 | 4.5258 | 344 | 100% | 8.257 | 62.04% | 0% | 37.96% | 0.25356 | 0 | 0 | 0.25356 | 0 | 0.23073 | 4.4602 | 0.051732 | 0.23073 | 4.4602 | 0.051732 | 0.25605 | 4.9495 | 0.051732 | 3.071% | 0.013009 | 0.012365 | 634.7125 | 33.2198 | 213.4395 | 388.0532 | 647.261 | 0 | 0 | 647.261 | 8.361e-06%
2027 | 289 | 289-906AE | Tier-1 | Non-HFTD---6 | 3--3 | 3.7338 | 241 | 100% | 60.6322 | 6.027% | 88.86% | 5.111% | 0.1809 | 0 | 0 | 0.1809 | 0 | 0.16461 | 3.6796 | 0.044737 | 0.16461 | 3.6796 | 0.044737 | 0.18267 | 4.0833 | 0.044737 | 0.2984% | 0.017149 | 0.0163 | 3535.6115 | 14.9936 | 2922.6536 | 597.9644 | 3708.6407 | 0 | 0 | 3708.6407 | 5.965e-06%
2027 | S2 | CB S2 | Tier-1 | Non-HFTD---14 | 3--1 | 5.3494 | 53 | 100% | 5.7564 | 31.81% | 0% | 68.19% | 0.090637 | 0 | 0 | 0.090637 | 0 | 0.082478 | 5.2718 | 0.015645 | 0.082478 | 5.2718 | 0.015645 | 0.091528 | 5.8503 | 0.015645 | 1.575% | 0.015094 | 0.014346 | 381.3818 | 0.43885 | 143.4346 | 237.5084 | 394.9256 | 0 | 0 | 394.9256 | 2.989e-06%
2027 | 206 | 206-963F | Tier-1 | Non-HFTD---1 | 3--5 | 4.5674 | 335 | 100% | 308.0085 | 98.9% | 0% | 1.099% | 15.0788 | 0 | 0 | 15.0788 | 0 | 13.7215 | 4.5012 | 3.0484 | 13.7215 | 4.5012 | 3.0484 | 15.227 | 4.995 | 3.0484 | 4.896% | 0.014856 | 0.014121 | 20732.6556 | 3229.8813 | 785.6991 | 16717.0751 | 20744.5251 | 0 | 0 | 20744.5251 | 0.0004972%
2027 | 1250 | CB 1250 | Tier-2 | Tier-2---4 | 4--5 | 2.5689 | 77 | 100% | 4075.2359 | 99.93% | 0.04042% | 0.02515% | 201.5919 | 0 | 0 | 201.5919 | 0 | 183.4459 | 2.5317 | 72.4605 | 183.4459 | 2.5317 | 72.4605 | 203.5731 | 2.8094 | 72.4605 | 4.947% | 0.088703 | 0.084312 | 45942.5846 | 7443.6301 | 317.2977 | 38181.6568 | 45944.1535 | 0 | 0 | 45944.1535 | 0.006648%
2027 | 330 | CB 330 | Tier-2 | Tier-2---16 | 4--3 | 3.7435 | 267 | 100% | 124.2501 | 33.35% | 64.03% | 2.615% | 2.0514 | 0 | 0 | 2.0514 | 0 | 1.8667 | 3.6892 | 0.506 | 1.8667 | 3.6892 | 0.506 | 2.0716 | 4.094 | 0.506 | 1.651% | 0.029702 | 0.028232 | 4183.2246 | 10.9263 | 3758.006 | 414.2923 | 4328.4151 | 0 | 0 | 4328.4151 | 6.765e-05%
2027 | 513 | 513-42F | Tier-1 | Non-HFTD---6 | 4--2 | 0.8341 | 183 | 100% | 92.9137 | 5.505% | 93.9% | 0.5996% | 0.25318 | 0 | 0 | 0.25318 | 0 | 0.23039 | 0.822 | 0.28028 | 0.23039 | 0.822 | 0.28028 | 0.25567 | 0.91219 | 0.28028 | 0.2725% | 0.081117 | 0.077102 | 1145.4316 | 12.1451 | 972.7364 | 160.5501 | 1201.7995 | 0 | 0 | 1201.7995 | 8.349e-06%
2027 | 773 | 773-271F | Tier-1 | Non-HFTD---15 | 1--2 | 0.78394 | 74 | 100% | 3.1656 | 79.61% | 0% | 20.39% | 0.12475 | 0 | 0 | 0.12475 | 0 | 0.11352 | 0.77257 | 0.14694 | 0.11352 | 0.77257 | 0.14694 | 0.12597 | 0.85734 | 0.14694 | 3.941% | 0.0028064 | 0.0026675 | 1127.9942 | 136.9584 | 63.692 | 927.3438 | 1139.9718 | 0 | 0 | 1139.9718 | 4.114e-06%
2027 | WT1 | CB WT1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2778 | 28 | 100% | 0.98508 | 16.22% | 0% | 83.78% | 0.0079093 | 0 | 0 | 0.0079093 | 0 | 0.0071974 | 1.2593 | 0.0057154 | 0.0071974 | 1.2593 | 0.0057154 | 0.0079871 | 1.3975 | 0.0057154 | 0.8029% | 0.0033416 | 0.0031762 | 294.7938 | 0.18584 | 70.2523 | 224.3557 | 307.6558 | 0 | 0 | 307.6558 | 2.608e-07%
2027 | 242 | 242-1427F | Tier-2 | Tier-2---20 | 5--1 | 0.17383 | 0 | 100% | 24.991 | 71.07% | 28.66% | 0.2708% | 0.8792 | 0 | 0 | 0.8792 | 0 | 0.80006 | 0.17131 | 4.6702 | 0.80006 | 0.17131 | 4.6702 | 0.88784 | 0.19011 | 4.6702 | 3.518% | 0.096908 | 0.092111 | 257.8839 | 30.0686 | 62.0054 | 165.8099 | 261.7689 | 0 | 0 | 261.7689 | 2.899e-05%
2027 | 397 | 397-39R | Tier-1 | Non-HFTD---15 | 1--2 | 1.061 | 27 | 100% | 3.5401 | 72.89% | 0% | 27.11% | 0.12772 | 0 | 0 | 0.12772 | 0 | 0.11622 | 1.0456 | 0.11115 | 0.11622 | 1.0456 | 0.11115 | 0.12897 | 1.1603 | 0.11115 | 3.608% | 0.003566 | 0.0033895 | 992.7325 | 10.2311 | 685.8367 | 296.6647 | 1006.7508 | 0 | 0 | 1006.7508 | 4.212e-06%
2027 | 1458 | 1458-1131R | Tier-3 | Tier-3---4 | 5--5 | 6.1667 | 157 | 100% | 15987.4265 | 99.09% | 0.8886% | 0.01928% | 784.1928 | 0 | 0 | 784.1928 | 0 | 713.6047 | 6.0773 | 117.422 | 713.6047 | 6.0773 | 117.422 | 791.8998 | 6.744 | 117.422 | 4.905% | 0.15941 | 0.15152 | 100291.8687 | 16592.5373 | 809.2853 | 82890.0461 | 100339.2877 | 0 | 0 | 100339.2877 | 0.02586%
2027 | 244 | 244-33F | Tier-1 | Non-HFTD---6 | 3--3 | 0.17124 | 0 | 100% | 53.967 | 0.1588% | 99.57% | 0.273% | 0.0042415 | 0 | 0 | 0.0042415 | 0 | 0.0038597 | 0.16876 | 0.022871 | 0.0038597 | 0.16876 | 0.022871 | 0.0042832 | 0.18727 | 0.022871 | 0.007859% | 0.025024 | 0.023786 | 2156.591 | 3.3966 | 1906.5038 | 246.6906 | 2268.7233 | 0 | 0 | 2268.7233 | 1.399e-07%
2027 | 498 | CB 498 | Tier-1 | Non-HFTD---11 | 1--4 | 0.40535 | 1 | 100% | 11.9856 | 98.23% | 0% | 1.767% | 0.5828 | 0 | 0 | 0.5828 | 0 | 0.53034 | 0.39947 | 1.3276 | 0.53034 | 0.39947 | 1.3276 | 0.58853 | 0.4433 | 1.3276 | 4.863% | 0.001257 | 0.0011948 | 9535.0565 | 1272.1609 | 1584.4485 | 6678.4471 | 9543.8307 | 0 | 0 | 9543.8307 | 1.922e-05%
2027 | 94 | 94-24F | Tier-2 | Tier-2---18 | 3--3 | 7.7121 | 186 | 100% | 46.367 | 91.68% | 0% | 8.321% | 2.1042 | 0 | 0 | 2.1042 | 0 | 1.9148 | 7.6003 | 0.25194 | 1.9148 | 7.6003 | 0.25194 | 2.1249 | 8.4341 | 0.25194 | 4.538% | 0.020922 | 0.019886 | 2216.1834 | 511.0324 | 89.3586 | 1615.7924 | 2225.7865 | 0 | 0 | 2225.7865 | 6.939e-05%
2027 | 513 | 513-45F | Tier-1 | Non-HFTD---15 | 1--4 | 0.1356 | 13 | 100% | 3.6672 | 98% | 0% | 1.998% | 0.1779 | 0 | 0 | 0.1779 | 0 | 0.16188 | 0.13364 | 1.2114 | 0.16188 | 0.13364 | 1.2114 | 0.17965 | 0.1483 | 1.2114 | 4.851% | 0.0003442 | 0.00032716 | 10654.1784 | 1674.8537 | 49.3768 | 8929.9479 | 10665.2646 | 0 | 0 | 10665.2646 | 5.866e-06%
2027 | 973 | CB 973 | Tier-2 | Tier-2---14 | 1--5 | 0.12822 | 0 | 100% | 310.4015 | 99.93% | 0% | 0.0686% | 15.3543 | 0 | 0 | 15.3543 | 0 | 13.9722 | 0.12636 | 110.5743 | 13.9722 | 0.12636 | 110.5743 | 15.5052 | 0.14022 | 110.5743 | 4.947% | 0.000676 | 0.00064254 | 459173.7618 | 73982.6369 | 1404.1576 | 383786.9672 | 459190.1666 | 0 | 0 | 459190.1666 | 0.0005063%
2027 | 401 | CB 401 | Tier-1 | Non-HFTD---10 | 3--2 | 7.5127 | 142 | 100% | 15.7522 | 74.38% | 0% | 25.62% | 0.58 | 0 | 0 | 0.58 | 0 | 0.52779 | 7.4037 | 0.071287 | 0.52779 | 7.4037 | 0.071287 | 0.5857 | 8.2161 | 0.071287 | 3.682% | 0.020185 | 0.019185 | 780.4068 | 3.5494 | 583.2472 | 193.6101 | 790.8176 | 0 | 0 | 790.8176 | 1.913e-05%
2027 | 190 | CB 190 | Tier-1 | Non-HFTD---5 | 1--4 | 1.1379 | 17 | 100% | 50.7497 | 97.95% | 0% | 2.052% | 2.4606 | 0 | 0 | 2.4606 | 0 | 2.2391 | 1.1214 | 1.9967 | 2.2391 | 1.1214 | 1.9967 | 2.4848 | 1.2444 | 1.9967 | 4.848% | 0.0045876 | 0.0043605 | 11062.3637 | 1434.6717 | 5166.1533 | 4461.5387 | 11074.1836 | 0 | 0 | 11074.1836 | 8.114e-05%
2027 | 43 | CB 43 | Tier-1 | Non-HFTD---13 | 2--2 | 3.2973 | 61 | 100% | 8.3441 | 73.19% | 0% | 26.81% | 0.3023 | 0 | 0 | 0.3023 | 0 | 0.27509 | 3.2495 | 0.084654 | 0.27509 | 3.2495 | 0.084654 | 0.30527 | 3.6061 | 0.084654 | 3.623% | 0.0092432 | 0.0087857 | 902.7245 | 2.8525 | 666.2859 | 233.5861 | 915.3285 | 0 | 0 | 915.3285 | 9.969e-06%
2027 | 147 | CB 147 | Tier-1 | Non-HFTD---5 | 2--4 | 0.60265 | 82 | 100% | 56.2258 | 13.29% | 85.71% | 1% | 0.36979 | 0 | 0 | 0.36979 | 0 | 0.3365 | 0.59391 | 0.56658 | 0.3365 | 0.59391 | 0.56658 | 0.37342 | 0.65908 | 0.56658 | 0.6577% | 0.0071956 | 0.0068394 | 7813.9098 | 108.3524 | 6561.501 | 1144.0564 | 8166.7746 | 0 | 0 | 8166.7746 | 1.219e-05%
2027 | CS2 | CB CS2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.0863 | 160 | 100% | 10.8217 | 49.87% | 0% | 50.13% | 0.26714 | 0 | 0 | 0.26714 | 0 | 0.24309 | 6.9836 | 0.034809 | 0.24309 | 6.9836 | 0.034809 | 0.26976 | 7.7498 | 0.034809 | 2.469% | 0.02081 | 0.01978 | 520.0357 | 1.0415 | 277.8082 | 241.1859 | 533.6123 | 0 | 0 | 533.6123 | 8.809e-06%
2027 | 170 | 170-3R | Tier-1 | Non-HFTD---3 | 4--3 | 7.9656 | 298 | 100% | 134.6076 | 71.34% | 24.69% | 3.975% | 4.7533 | 0 | 0 | 4.7533 | 0 | 4.3254 | 7.8501 | 0.55101 | 4.3254 | 7.8501 | 0.55101 | 4.8 | 8.7114 | 0.55101 | 3.531% | 0.059016 | 0.056095 | 2280.8503 | 250.0057 | 616.1021 | 1414.7425 | 2314.8955 | 0 | 0 | 2314.8955 | 0.0001567%
2027 | 772 | CB 772 | Tier-1 | Non-HFTD---17 | 1--2 | 0.25341 | 97 | 100% | 0.92752 | 78.02% | 0% | 21.98% | 0.035822 | 0 | 0 | 0.035822 | 0 | 0.032597 | 0.24973 | 0.13053 | 0.032597 | 0.24973 | 0.13053 | 0.036174 | 0.27714 | 0.13053 | 3.862% | 0.0009252 | 0.0008794 | 1002.5093 | 43.9741 | 533.3948 | 425.1403 | 1013.9835 | 0 | 0 | 1013.9835 | 1.181e-06%
2027 | 442 | 442-764R | Tier-3 | Tier-3---18 | 5--2 | 2.5085 | 304 | 100% | 474.7376 | 91.31% | 8.325% | 0.3651% | 21.4573 | 0 | 0 | 21.4573 | 0 | 19.5259 | 2.4721 | 7.8984 | 19.5259 | 2.4721 | 7.8984 | 21.6682 | 2.7434 | 7.8984 | 4.52% | 0.35448 | 0.33694 | 1339.2423 | 150.4184 | 101.5124 | 1087.3115 | 1345.3033 | 0 | 0 | 1345.3033 | 0.0007076%
2027 | 386 | 386-25R | Tier-2 | Tier-2---15 | 3--4 | 2.3127 | 96 | 100% | 143.657 | 35.36% | 63.5% | 1.138% | 2.5144 | 0 | 0 | 2.5144 | 0 | 2.2881 | 2.2791 | 1.0039 | 2.2881 | 2.2791 | 1.0039 | 2.5391 | 2.5292 | 1.0039 | 1.75% | 0.019083 | 0.018138 | 7528.0087 | 552.5881 | 4465.4268 | 2509.9939 | 7781.4266 | 0 | 0 | 7781.4266 | 8.292e-05%
2027 | 450 | 450-1851F | Tier-2 | Tier-2---3 | 5--5 | 7.0884 | 662 | 100% | 8274.1225 | 99.23% | 0.7168% | 0.05235% | 406.4189 | 0 | 0 | 406.4189 | 0 | 369.8356 | 6.9857 | 52.9421 | 369.8356 | 6.9857 | 52.9421 | 410.4131 | 7.7521 | 52.9421 | 4.912% | 0.099477 | 0.094553 | 83176.2362 | 24640.5992 | 545.9556 | 57989.6815 | 83209.5529 | 0 | 0 | 83209.5529 | 0.0134%
2027 | 95 | 95-1352F | Tier-1 | Non-HFTD---19 | 1--2 | 0.00625 | 0 | 100% | 0.035566 | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0061594 | 0 | 0 | 0.0061594 | 0 | 0 | 0.0068352 | 0 | 0% | 5.34e-05 | 5.0757e-05 | 666.0341 | 0.50117 | 60.503 | 605.0299 | 700.7197 | 0 | 0 | 700.7197 | 0%
2027 | FL1 | CB FL1 | Tier-1 | Non-HFTD---18 | 1--1 | 0.99262 | 29 | 100% | 0.95174 | 21.32% | 0% | 78.68% | 0.010043 | 0 | 0 | 0.010043 | 0 | 0.009139 | 0.97823 | 0.0093424 | 0.009139 | 0.97823 | 0.0093424 | 0.010142 | 1.0856 | 0.0093424 | 1.055% | 0.0027542 | 0.0026179 | 345.5613 | 0.20459 | 98.3649 | 246.9919 | 359.7211 | 0 | 0 | 359.7211 | 3.312e-07%
2027 | SO1 | CB SO1 | Tier-1 | Non-HFTD---13 | 2--2 | 1.8291 | 60 | 100% | 6.6385 | 81.22% | 0% | 18.78% | 0.26688 | 0 | 0 | 0.26688 | 0 | 0.24286 | 1.8026 | 0.13473 | 0.24286 | 1.8026 | 0.13473 | 0.26951 | 2.0004 | 0.13473 | 4.02% | 0.0053988 | 0.0051316 | 1229.6237 | 149.2052 | 107.0402 | 973.3783 | 1241.6514 | 0 | 0 | 1241.6514 | 8.801e-06%
2027 | 1076 | 1076-37F | Tier-1 | Non-HFTD---10 | 4--2 | 11.6676 | 512 | 100% | 25.756 | 71.52% | 0% | 28.48% | 0.91186 | 0 | 0 | 0.91186 | 0 | 0.82978 | 11.4985 | 0.072164 | 0.82978 | 11.4985 | 0.072164 | 0.92082 | 12.76 | 0.072164 | 3.54% | 0.031216 | 0.029671 | 825.094 | 10.3507 | 561.5168 | 253.2265 | 837.3304 | 0 | 0 | 837.3304 | 3.007e-05%
2027 | 462 | 462-1521F | Tier-1 | Non-HFTD---13 | 1--3 | 0.48601 | 15 | 100% | 6.0831 | 92.48% | 0% | 7.516% | 0.27849 | 0 | 0 | 0.27849 | 0 | 0.25342 | 0.47896 | 0.5291 | 0.25342 | 0.47896 | 0.5291 | 0.28122 | 0.53151 | 0.5291 | 4.578% | 0.0016764 | 0.0015934 | 3628.6943 | 497.4695 | 319.6242 | 2811.6007 | 3642.8968 | 0 | 0 | 3642.8968 | 9.183e-06%
2027 | 239 | 239-2211R | Tier-3 | Tier-3---16 | 5--4 | 2.7707 | 116 | 100% | 1585.1718 | 98.67% | 1.22% | 0.1095% | 77.4227 | 0 | 0 | 77.4227 | 0 | 70.4536 | 2.7305 | 25.8026 | 70.4536 | 2.7305 | 25.8026 | 78.1836 | 3.0301 | 25.8026 | 4.884% | 0.11902 | 0.11313 | 13318.69 | 2119.2722 | 143.2039 | 11056.2139 | 13327.9127 | 0 | 0 | 13327.9127 | 0.002553%
2027 | 230 | 230-181 | Tier-2 | Tier-2---9 | 4--4 | 2.4656 | 168 | 100% | 788.7224 | 98.19% | 1.606% | 0.2041% | 38.335 | 0 | 0 | 38.335 | 0 | 34.8843 | 2.4298 | 14.3567 | 34.8843 | 2.4298 | 14.3567 | 38.7117 | 2.6964 | 14.3567 | 4.86% | 0.063241 | 0.060111 | 12471.6541 | 1938.3166 | 505.8598 | 10027.4777 | 12483.4125 | 0 | 0 | 12483.4125 | 0.001264%
2027 | 448 | 448-724R | Tier-3 | Tier-3---18 | 5--2 | 8.7678 | 229 | 100% | 520.639 | 76.18% | 22.78% | 1.038% | 19.634 | 0 | 0 | 19.634 | 0 | 17.8667 | 8.6406 | 2.0677 | 17.8667 | 8.6406 | 2.0677 | 19.8269 | 9.5887 | 2.0677 | 3.771% | 0.55035 | 0.52311 | 946.0153 | 77.3726 | 193.0689 | 675.5738 | 957.7484 | 0 | 0 | 957.7484 | 0.0006475%
2027 | JU1 | CB JU1 | Tier-3 | Tier-3---15 | 5--4 | 2.6673 | 399 | 100% | 1531.7487 | 97.85% | 2.019% | 0.1357% | 74.1877 | 0 | 0 | 74.1877 | 0 | 67.5098 | 2.6286 | 25.683 | 67.5098 | 2.6286 | 25.683 | 74.9169 | 2.917 | 25.683 | 4.843% | 0.1808 | 0.17185 | 8471.8458 | 1257.0107 | 156.1661 | 7058.669 | 8481.3528 | 0 | 0 | 8481.3528 | 0.002446%
2027 | 490 | CB 490 | Tier-1 | Non-HFTD---17 | 1--3 | 0.11705 | 101 | 100% | 1.7253 | 96.38% | 0% | 3.622% | 0.082308 | 0 | 0 | 0.082308 | 0 | 0.074899 | 0.11535 | 0.64933 | 0.074899 | 0.11535 | 0.64933 | 0.083117 | 0.128 | 0.64933 | 4.771% | 0.0004622 | 0.00043932 | 3732.7377 | 409.8645 | 1089.0962 | 2233.777 | 3739.7782 | 0 | 0 | 3739.7782 | 2.714e-06%
2027 | 439 | 439-42F | Tier-1 | Non-HFTD---13 | 1--5 | 0.094286 | 67 | 100% | 6.5642 | 99.01% | 0% | 0.991% | 0.32171 | 0 | 0 | 0.32171 | 0 | 0.29275 | 0.092919 | 3.1506 | 0.29275 | 0.092919 | 3.1506 | 0.32487 | 0.10311 | 3.1506 | 4.901% | 0.0003618 | 0.00034389 | 18143.2707 | 3639.6892 | 20.3353 | 14483.2462 | 18152.6341 | 0 | 0 | 18152.6341 | 1.061e-05%
2027 | 451 | CB 451 | Tier-1 | Non-HFTD---12 | 3--2 | 5.2964 | 121 | 100% | 9.9548 | 62.07% | 0% | 37.93% | 0.30587 | 0 | 0 | 0.30587 | 0 | 0.27833 | 5.2196 | 0.053325 | 0.27833 | 5.2196 | 0.053325 | 0.30887 | 5.7923 | 0.053325 | 3.073% | 0.01523 | 0.014476 | 653.6494 | 0.18655 | 428.2521 | 225.2107 | 666.5605 | 0 | 0 | 666.5605 | 1.009e-05%
2027 | 381 | 381-450F | Tier-1 | Non-HFTD---19 | 1--2 | 0.24375 | 7 | 100% | 0.50113 | 65.42% | 0% | 34.58% | 0.016228 | 0 | 0 | 0.016228 | 0 | 0.014767 | 0.24022 | 0.061475 | 0.014767 | 0.24022 | 0.061475 | 0.016388 | 0.26657 | 0.061475 | 3.238% | 0.0009906 | 0.00094157 | 505.8881 | 53.5748 | 17.2796 | 435.0337 | 514.9984 | 0 | 0 | 514.9984 | 5.351e-07%
2027 | 1049 | 1049-7F | Tier-1 | Non-HFTD---16 | 2--1 | 3.8161 | 101 | 100% | 4.3969 | 41.77% | 0% | 58.23% | 0.090919 | 0 | 0 | 0.090919 | 0 | 0.082735 | 3.7608 | 0.021999 | 0.082735 | 3.7608 | 0.021999 | 0.091813 | 4.1734 | 0.021999 | 2.068% | 0.010687 | 0.010158 | 411.4223 | 11.17 | 126.457 | 273.7954 | 423.8979 | 0 | 0 | 423.8979 | 2.998e-06%
2027 | 579 | 579-350F | Tier-1 | Non-HFTD---4 | 3--4 | 0.61875 | 18 | 100% | 142.7673 | 2.23% | 97.26% | 0.5133% | 0.15763 | 0 | 0 | 0.15763 | 0 | 0.14344 | 0.60978 | 0.23523 | 0.14344 | 0.60978 | 0.23523 | 0.15918 | 0.67669 | 0.23523 | 0.1104% | 0.016794 | 0.015962 | 8501.2943 | 15.4192 | 7694.6748 | 791.2003 | 8934.1485 | 0 | 0 | 8934.1485 | 5.198e-06%
2027 | 143 | 143-179F | Tier-1 | Non-HFTD---18 | 2--1 | 0.022348 | 1 | 100% | 1.3702 | 64.14% | 33.11% | 2.747% | 0.043505 | 0 | 0 | 0.043505 | 0 | 0.039589 | 0.022024 | 1.7975 | 0.039589 | 0.022024 | 1.7975 | 0.043932 | 0.024441 | 1.7975 | 3.175% | 0.0062356 | 0.0059269 | 219.7357 | 23.4884 | 57.8583 | 138.3889 | 223.8388 | 0 | 0 | 223.8388 | 1.435e-06%
2027 | 55 | 55-479F | Tier-1 | Non-HFTD---17 | 1--1 | 0.60512 | 90 | 100% | 1.2239 | 36.64% | 0% | 63.36% | 0.022196 | 0 | 0 | 0.022196 | 0 | 0.020198 | 0.59634 | 0.033869 | 0.020198 | 0.59634 | 0.033869 | 0.022414 | 0.66177 | 0.033869 | 1.813% | 0.002537 | 0.0024114 | 482.4279 | 2.4251 | 191.0428 | 288.9599 | 498.3473 | 0 | 0 | 498.3473 | 7.319e-07%
2027 | 44 | 44-40AE | Tier-1 | Non-HFTD---17 | 1--2 | 0.95338 | 22 | 100% | 1.9267 | 51.29% | 0% | 48.71% | 0.048912 | 0 | 0 | 0.048912 | 0 | 0.044509 | 0.93956 | 0.047373 | 0.044509 | 0.93956 | 0.047373 | 0.049393 | 1.0426 | 0.047373 | 2.539% | 0.003574 | 0.0033971 | 539.0796 | 43.7572 | 32.3287 | 462.9937 | 552.7554 | 0 | 0 | 552.7554 | 1.613e-06%
2027 | 364 | 364-36 | Tier-1 | Non-HFTD---4 | 3--4 | 7.918 | 167 | 100% | 171.1869 | 2.025% | 94.55% | 3.426% | 0.17156 | 0 | 0 | 0.17156 | 0 | 0.15611 | 7.8032 | 0.020007 | 0.15611 | 7.8032 | 0.020007 | 0.17324 | 8.6593 | 0.020007 | 0.1002% | 0.027309 | 0.025958 | 6268.4256 | 8.2117 | 5535.3679 | 724.846 | 6588.2626 | 0 | 0 | 6588.2626 | 5.657e-06%
2027 | 244 | 244-29 | Tier-1 | Non-HFTD---2 | 4--4 | 20.8303 | 864 | 100% | 494.9076 | 37.84% | 59.66% | 2.496% | 9.2706 | 0 | 0 | 9.2706 | 0 | 8.4361 | 20.5283 | 0.41095 | 8.4361 | 20.5283 | 0.41095 | 9.3617 | 22.7806 | 0.41095 | 1.873% | 0.082271 | 0.078198 | 6015.6074 | 554.6539 | 3442.3851 | 2018.5684 | 6210.3353 | 0 | 0 | 6210.3353 | 0.0003057%
2027 | 793 | 793-46F | Tier-1 | Non-HFTD---10 | 3--2 | 1.1603 | 43 | 100% | 23.4141 | 2.819% | 95.02% | 2.166% | 0.032668 | 0 | 0 | 0.032668 | 0 | 0.029728 | 1.1434 | 0.025998 | 0.029728 | 1.1434 | 0.025998 | 0.032989 | 1.2689 | 0.025998 | 0.1395% | 0.020148 | 0.01915 | 1162.1175 | 4.9845 | 1026.7024 | 130.4306 | 1220.9323 | 0 | 0 | 1220.9323 | 1.077e-06%
2027 | AD1 | CB AD1 | Tier-1 | Non-HFTD---3 | 4--3 | 9.4 | 277 | 100% | 147.8944 | 9.794% | 85.29% | 4.92% | 0.71697 | 0 | 0 | 0.71697 | 0 | 0.65244 | 9.2637 | 0.070429 | 0.65244 | 9.2637 | 0.070429 | 0.72402 | 10.2801 | 0.070429 | 0.4848% | 0.031636 | 0.03007 | 4674.8186 | 81.3578 | 3791.6481 | 801.8126 | 4894.4299 | 0 | 0 | 4894.4299 | 2.364e-05%
2027 | 85 | 85-500F | Tier-1 | Non-HFTD---14 | 2--2 | 3.3993 | 63 | 100% | 4.936 | 60.97% | 0% | 39.03% | 0.14897 | 0 | 0 | 0.14897 | 0 | 0.13556 | 3.35 | 0.040465 | 0.13556 | 3.35 | 0.040465 | 0.15043 | 3.7176 | 0.040465 | 3.018% | 0.0098106 | 0.009325 | 503.1269 | 39.9485 | 81.0918 | 382.0867 | 513.3535 | 0 | 0 | 513.3535 | 4.912e-06%
2027 | 1030 | 1030-1823F | Tier-3 | Tier-3---13 | 5--5 | 0.91593 | 133 | 100% | 2150.9739 | 99.45% | 0.5287% | 0.02497% | 105.8837 | 0 | 0 | 105.8837 | 0 | 96.3527 | 0.90265 | 106.7439 | 96.3527 | 0.90265 | 106.7439 | 106.9243 | 1.0017 | 106.7439 | 4.923% | 0.10605 | 0.1008 | 20281.9888 | 3254.225 | 96.8163 | 16930.9475 | 20287.8367 | 0 | 0 | 20287.8367 | 0.003492%
2027 | 166 | 166-982F | Tier-1 | Non-HFTD---15 | 2--1 | 2.2852 | 49 | 100% | 2.9192 | 42.53% | 0% | 57.47% | 0.061449 | 0 | 0 | 0.061449 | 0 | 0.055918 | 2.2521 | 0.024829 | 0.055918 | 2.2521 | 0.024829 | 0.062053 | 2.4992 | 0.024829 | 2.105% | 0.0065086 | 0.0061864 | 448.512 | 2.7669 | 198.387 | 247.3581 | 461.9366 | 0 | 0 | 461.9366 | 2.026e-06%
2027 | 45 | CB 45 | Tier-1 | Non-HFTD---9 | 2--3 | 1.9805 | 27 | 100% | 25.7276 | 93.88% | 0% | 6.12% | 1.1956 | 0 | 0 | 1.1956 | 0 | 1.088 | 1.9517 | 0.55743 | 1.088 | 1.9517 | 0.55743 | 1.2073 | 2.1659 | 0.55743 | 4.647% | 0.0069006 | 0.006559 | 3728.3111 | 135.5762 | 2690.8224 | 901.9126 | 3740.1941 | 0 | 0 | 3740.1941 | 3.943e-05%
2027 | 96 | 96-47R | Tier-2 | Tier-2---12 | 4--4 | 7.8716 | 546 | 100% | 553.6953 | 88.3% | 10.7% | 0.9975% | 24.2008 | 0 | 0 | 24.2008 | 0 | 22.0224 | 7.7575 | 2.8389 | 22.0224 | 7.7575 | 2.8389 | 24.4386 | 8.6086 | 2.8389 | 4.371% | 0.034749 | 0.033029 | 15934.2283 | 2878.8213 | 1971.4006 | 11084.0065 | 16031.3298 | 0 | 0 | 16031.3298 | 0.0007981%
2027 | 411 | 411-30R | Tier-3 | Tier-3---6 | 5--5 | 24.6051 | 1577 | 100% | 6370.0414 | 98.47% | 1.262% | 0.272% | 310.4797 | 0 | 0 | 310.4797 | 0 | 282.5323 | 24.2484 | 11.6516 | 282.5323 | 24.2484 | 11.6516 | 313.5311 | 26.9089 | 11.6516 | 4.874% | 0.10309 | 0.09799 | 61789.3921 | 12748.9007 | 821.0259 | 48219.4655 | 61838.7577 | 0 | 0 | 61838.7577 | 0.01024%
2027 | MA1 | CB MA1 | Tier-1 | Non-HFTD---3 | 4--3 | 11.2421 | 595 | 100% | 187.6887 | 3.137% | 92.99% | 3.876% | 0.29148 | 0 | 0 | 0.29148 | 0 | 0.26524 | 11.0791 | 0.023941 | 0.26524 | 11.0791 | 0.023941 | 0.29434 | 12.2947 | 0.023941 | 0.1553% | 0.044813 | 0.042595 | 4188.2268 | 5.9858 | 3692.2486 | 489.9924 | 4399.4977 | 0 | 0 | 4399.4977 | 9.612e-06%
2027 | 463 | 463-1137F | Tier-2 | Tier-2---19 | 1--5 | 0.125 | 0 | 100% | 11.7975 | 99.11% | 0% | 0.8934% | 0.57876 | 0 | 0 | 0.57876 | 0 | 0.52666 | 0.12319 | 4.2753 | 0.52666 | 0.12319 | 4.2753 | 0.58445 | 0.1367 | 4.2753 | 4.906% | 0.0005036 | 0.00047867 | 23426.3875 | 4696.5104 | 948.1966 | 17781.6805 | 23437.287 | 0 | 0 | 23437.287 | 1.909e-05%
2027 | 277 | 277-459F | Tier-1 | Non-HFTD---2 | 4--3 | 9.8924 | 276 | 100% | 196.3447 | 7.922% | 88.67% | 3.412% | 0.76992 | 0 | 0 | 0.76992 | 0 | 0.70061 | 9.749 | 0.071866 | 0.70061 | 9.749 | 0.071866 | 0.77748 | 10.8186 | 0.071866 | 0.3921% | 0.04286 | 0.040738 | 4581.0932 | 25.5864 | 3978.2585 | 577.2483 | 4800.7676 | 0 | 0 | 4800.7676 | 2.539e-05%
2027 | WA2 | CB WA2 | Tier-1 | Non-HFTD---12 | 3--2 | 5.65 | 280 | 100% | 10.82 | 65.84% | 0% | 34.16% | 0.35266 | 0 | 0 | 0.35266 | 0 | 0.32091 | 5.5681 | 0.057634 | 0.32091 | 5.5681 | 0.057634 | 0.35612 | 6.179 | 0.057634 | 3.259% | 0.016911 | 0.016074 | 639.8077 | 57.0792 | 90.6841 | 492.0444 | 651.1883 | 0 | 0 | 651.1883 | 1.163e-05%
2027 | 1162 | 1162-324R | Tier-2 | Tier-2---13 | 4--3 | 3.3255 | 24 | 100% | 240.2897 | 88.19% | 10.99% | 0.8202% | 10.4893 | 0 | 0 | 10.4893 | 0 | 9.5451 | 3.2773 | 2.9125 | 9.5451 | 3.2773 | 2.9125 | 10.5924 | 3.6369 | 2.9125 | 4.365% | 0.068658 | 0.065259 | 3499.8056 | 488.3895 | 324.3861 | 2687.0299 | 3521.3352 | 0 | 0 | 3521.3352 | 0.0003459%
2027 | OCA1 | CB OCA1 | Tier-1 | Non-HFTD---14 | 2--2 | 0.66117 | 89 | 100% | 5.9345 | 0.6639% | 92.19% | 7.151% | 0.0019501 | 0 | 0 | 0.0019501 | 0 | 0.0017746 | 0.65158 | 0.0027235 | 0.0017746 | 0.65158 | 0.0027235 | 0.0019693 | 0.72307 | 0.0027235 | 0.03286% | 0.0090824 | 0.0086328 | 653.4036 | 0.7621 | 562.1423 | 90.4992 | 687.2056 | 0 | 0 | 687.2056 | 6.431e-08%
2027 | 289 | 289-907 | Tier-1 | Non-HFTD---7 | 3--3 | 4.268 | 277 | 100% | 40.1087 | 2.57% | 90.18% | 7.252% | 0.051033 | 0 | 0 | 0.051033 | 0 | 0.046439 | 4.2061 | 0.011041 | 0.046439 | 4.2061 | 0.011041 | 0.051534 | 4.6676 | 0.011041 | 0.1272% | 0.017391 | 0.01653 | 2306.2924 | 6.5848 | 1930.5725 | 369.135 | 2423.3119 | 0 | 0 | 2423.3119 | 1.683e-06%
2027 | 399 | CB 399 | Tier-1 | Non-HFTD---10 | 3--2 | 6.1078 | 357 | 100% | 19.1964 | 76.81% | 0% | 23.19% | 0.72985 | 0 | 0 | 0.72985 | 0 | 0.66415 | 6.0192 | 0.11034 | 0.66415 | 6.0192 | 0.11034 | 0.73702 | 6.6797 | 0.11034 | 3.802% | 0.017948 | 0.017059 | 1069.5788 | 24.012 | 698.2984 | 347.2685 | 1082.4967 | 0 | 0 | 1082.4967 | 2.407e-05%
2027 | 154 | 154-876R | Tier-1 | Non-HFTD---12 | 3--2 | 7.2587 | 212 | 100% | 9.9957 | 58.61% | 0% | 41.39% | 0.29001 | 0 | 0 | 0.29001 | 0 | 0.26391 | 7.1535 | 0.036892 | 0.26391 | 7.1535 | 0.036892 | 0.29286 | 7.9384 | 0.036892 | 2.901% | 0.018706 | 0.01778 | 534.3539 | 0.16641 | 333.2928 | 200.8947 | 545.871 | 0 | 0 | 545.871 | 9.564e-06%
2027 | 1482 | CB 1482 | Tier-1 | Non-HFTD---19 | 1--3 | 0.033523 | 3 | 100% | 0.35238 | 81.69% | 0% | 18.31% | 0.014248 | 0 | 0 | 0.014248 | 0 | 0.012966 | 0.033037 | 0.39247 | 0.012966 | 0.033037 | 0.39247 | 0.014388 | 0.036661 | 0.39247 | 4.043% | 0.0001796 | 0.00017071 | 1962.0387 | 0.27038 | 1635.3539 | 326.4145 | 1980.7517 | 0 | 0 | 1980.7517 | 4.699e-07%
2027 | 1023 | CB 1023 | Tier-2 | Tier-2---4 | 4--5 | 3.9246 | 193 | 100% | 3332.7386 | 99.81% | 0.1085% | 0.07978% | 164.66 | 0 | 0 | 164.66 | 0 | 149.8384 | 3.8677 | 38.7406 | 149.8384 | 3.8677 | 38.7406 | 166.2783 | 4.2921 | 38.7406 | 4.941% | 0.082267 | 0.078195 | 40511.3439 | 6478.7378 | 346.66 | 33685.946 | 40515.3153 | 0 | 0 | 40515.3153 | 0.00543%
2027 | JE1 | CB JE1 | Tier-1 | Non-HFTD---18 | 1--1 | 0.96179 | 61 | 100% | 0.75454 | 7.509% | 0% | 92.49% | 0.0028046 | 0 | 0 | 0.0028046 | 0 | 0.0025522 | 0.94784 | 0.0026926 | 0.0025522 | 0.94784 | 0.0026926 | 0.0028322 | 1.0518 | 0.0026926 | 0.3717% | 0.0027018 | 0.0025681 | 279.2739 | 0.19436 | 44.4353 | 234.6442 | 292.7257 | 0 | 0 | 292.7257 | 9.249e-08%
2027 | 840 | 840-308F | Tier-2 | Tier-2---13 | 4--4 | 1.0854 | 15 | 100% | 330.3488 | 99.39% | 0.4551% | 0.1546% | 16.2526 | 0 | 0 | 16.2526 | 0 | 14.7896 | 1.0697 | 13.8262 | 14.7896 | 1.0697 | 13.8262 | 16.4123 | 1.187 | 13.8262 | 4.92% | 0.063249 | 0.060118 | 5222.9719 | 1196.0786 | 20.9413 | 4005.9521 | 5224.6302 | 0 | 0 | 5224.6302 | 0.0005359%
2027 | 157 | 157-273R | Tier-3 | Tier-3---14 | 5--4 | 8.4758 | 338 | 100% | 1867.403 | 95.01% | 4.712% | 0.2778% | 87.8243 | 0 | 0 | 87.8243 | 0 | 79.9189 | 8.3529 | 9.5678 | 79.9189 | 8.3529 | 9.5678 | 88.6875 | 9.2693 | 9.5678 | 4.703% | 0.32295 | 0.30696 | 5782.3142 | 798.5103 | 275.1351 | 4708.6688 | 5797.3391 | 0 | 0 | 5797.3391 | 0.002896%
2027 | 506 | 506-161 | Tier-1 | Non-HFTD---15 | 2--2 | 1.9422 | 104 | 100% | 4.7204 | 74.33% | 0% | 25.67% | 0.17369 | 0 | 0 | 0.17369 | 0 | 0.15806 | 1.9141 | 0.082576 | 0.15806 | 1.9141 | 0.082576 | 0.1754 | 2.1241 | 0.082576 | 3.68% | 0.0058182 | 0.0055302 | 811.3208 | 47.4149 | 332.8733 | 431.0326 | 822.1649 | 0 | 0 | 822.1649 | 5.728e-06%
2027 | 409 | 409-1155R | Tier-1 | Non-HFTD---10 | 2--2 | 4.4515 | 143 | 100% | 15.855 | 79.34% | 0% | 20.66% | 0.62272 | 0 | 0 | 0.62272 | 0 | 0.56666 | 4.387 | 0.12917 | 0.56666 | 4.387 | 0.12917 | 0.62884 | 4.8683 | 0.12917 | 3.928% | 0.012886 | 0.012248 | 1230.387 | 1.5966 | 990.7436 | 238.0468 | 1243.622 | 0 | 0 | 1243.622 | 2.053e-05%
2027 | 86 | CB 86 | Tier-1 | Non-HFTD---17 | 1--3 | 0.28124 | 5 | 100% | 2.0292 | 91.13% | 0% | 8.873% | 0.091533 | 0 | 0 | 0.091533 | 0 | 0.083294 | 0.27716 | 0.30053 | 0.083294 | 0.27716 | 0.30053 | 0.092433 | 0.30757 | 0.30053 | 4.511% | 0.0007966 | 0.00075717 | 2547.343 | 6.272 | 2304.2733 | 236.7977 | 2559.1141 | 0 | 0 | 2559.1141 | 3.018e-06%
2027 | 1434 | 1434-37R | Tier-1 | Non-HFTD---8 | 3--2 | 9.4542 | 300 | 100% | 34.3658 | 81.72% | 0% | 18.28% | 1.3902 | 0 | 0 | 1.3902 | 0 | 1.2651 | 9.3171 | 0.13578 | 1.2651 | 9.3171 | 0.13578 | 1.4039 | 10.3394 | 0.13578 | 4.045% | 0.027694 | 0.026323 | 1240.9281 | 98.0626 | 641.6225 | 501.2431 | 1252.7397 | 0 | 0 | 1252.7397 | 4.584e-05%
2027 | 197 | CB 197 | Tier-2 | Tier-2---21 | 1--4 | 0.097159 | 0 | 100% | 1.9198 | 98.18% | 0% | 1.817% | 0.093305 | 0 | 0 | 0.093305 | 0 | 0.084906 | 0.09575 | 0.88675 | 0.084906 | 0.09575 | 0.88675 | 0.094222 | 0.10626 | 0.88675 | 4.86% | 0.000314 | 0.00029846 | 6114.1 | 461.2612 | 3185.8611 | 2466.9777 | 6119.8844 | 0 | 0 | 6119.8844 | 3.077e-06%
2027 | 326 | 326-26 | Tier-1 | Non-HFTD---17 | 1--3 | 0.27121 | 19 | 100% | 1.9501 | 90.68% | 0% | 9.316% | 0.087536 | 0 | 0 | 0.087536 | 0 | 0.079657 | 0.26728 | 0.29803 | 0.079657 | 0.26728 | 0.29803 | 0.088396 | 0.29661 | 0.29803 | 4.489% | 0.0009188 | 0.00087332 | 2122.4058 | 3.4556 | 1922.3956 | 196.5546 | 2132.7026 | 0 | 0 | 2132.7026 | 2.887e-06%
2027 | 933 | 933-472F | Tier-1 | Non-HFTD---4 | 2--5 | 2.0138 | 194 | 100% | 165.8681 | 99.03% | 0% | 0.973% | 8.1306 | 0 | 0 | 8.1306 | 0 | 7.3987 | 1.9846 | 3.7281 | 7.3987 | 1.9846 | 3.7281 | 8.2105 | 2.2024 | 3.7281 | 4.902% | 0.0078904 | 0.0074998 | 21021.5038 | 4274.6156 | 66.263 | 16680.6253 | 21032.1561 | 0 | 0 | 21032.1561 | 0.0002681%
2027 | 779 | 779-25AE | Tier-1 | Non-HFTD---15 | 1--3 | 0.33084 | 22 | 100% | 3.5318 | 96.75% | 0% | 3.249% | 0.16914 | 0 | 0 | 0.16914 | 0 | 0.15392 | 0.32604 | 0.47208 | 0.15392 | 0.32604 | 0.47208 | 0.17081 | 0.36182 | 0.47208 | 4.789% | 0.0008446 | 0.00080279 | 4181.6044 | 654.541 | 38.406 | 3488.6574 | 4188.6793 | 0 | 0 | 4188.6793 | 5.578e-06%
2027 | BY3 | CB BY3 | Tier-1 | Non-HFTD---12 | 3--1 | 8.1915 | 286 | 100% | 10.3011 | 47.64% | 0% | 52.36% | 0.24292 | 0 | 0 | 0.24292 | 0 | 0.22105 | 8.0727 | 0.027383 | 0.22105 | 8.0727 | 0.027383 | 0.24531 | 8.9584 | 0.027383 | 2.358% | 0.023075 | 0.021933 | 446.413 | 16.8472 | 131.6677 | 297.8981 | 458.5857 | 0 | 0 | 458.5857 | 8.011e-06%
2027 | 215 | 215-1531R | Tier-2 | Tier-2---2 | 5--5 | 8.4597 | 765 | 100% | 12702.4119 | 98.21% | 1.737% | 0.04837% | 617.5408 | 0 | 0 | 617.5408 | 0 | 561.9538 | 8.337 | 67.4045 | 561.9538 | 8.337 | 67.4045 | 623.61 | 9.2518 | 67.4045 | 4.862% | 0.20291 | 0.19287 | 62600.9651 | 10891.2685 | 1005.9666 | 50703.7299 | 62659.1843 | 0 | 0 | 62659.1843 | 0.02036%
2027 | 475 | 475-763F | Tier-1 | Non-HFTD---9 | 2--3 | 2.6615 | 141 | 100% | 16.724 | 89.58% | 0% | 10.42% | 0.74158 | 0 | 0 | 0.74158 | 0 | 0.67483 | 2.6229 | 0.25728 | 0.67483 | 2.6229 | 0.25728 | 0.74887 | 2.9107 | 0.25728 | 4.434% | 0.0076068 | 0.0072303 | 2198.5586 | 311.6157 | 88.9446 | 1797.9982 | 2210.4884 | 0 | 0 | 2210.4884 | 2.445e-05%
2027 | 900 | 900-1119F | Tier-1 | Non-HFTD---15 | 1--4 | 0.064205 | 4 | 100% | 3.0645 | 96.62% | 0% | 3.379% | 0.14657 | 0 | 0 | 0.14657 | 0 | 0.13337 | 0.063274 | 2.1079 | 0.13337 | 0.063274 | 2.1079 | 0.14801 | 0.070216 | 2.1079 | 4.783% | 0.000334 | 0.00031747 | 9175.1794 | 752.0584 | 4282.7612 | 4140.3597 | 9191.3258 | 0 | 0 | 9191.3258 | 4.833e-06%
2027 | TR1 | CB TR1 | Tier-1 | Non-HFTD---5 | 1--5 | 0.82749 | 70 | 100% | 65.5808 | 99.13% | 0% | 0.8721% | 3.2179 | 0 | 0 | 3.2179 | 0 | 2.9283 | 0.81549 | 3.5908 | 2.9283 | 0.81549 | 3.5908 | 3.2496 | 0.90497 | 3.5908 | 4.907% | 0.0027118 | 0.0025776 | 24183.476 | 3920.7975 | 31.6199 | 20231.0587 | 24194.4592 | 0 | 0 | 24194.4592 | 0.0001061%
2027 | 453 | 453-32R | Tier-1 | Non-HFTD---16 | 2--1 | 2.4413 | 131 | 100% | 2.5305 | 33.48% | 0% | 66.52% | 0.04194 | 0 | 0 | 0.04194 | 0 | 0.038165 | 2.4059 | 0.015863 | 0.038165 | 2.4059 | 0.015863 | 0.042353 | 2.6699 | 0.015863 | 1.657% | 0.0069622 | 0.0066176 | 363.4686 | 7.0606 | 101.7102 | 254.6977 | 376.0595 | 0 | 0 | 376.0595 | 1.383e-06%
2027 | 1090 | 1090-636R | Tier-3 | Tier-3---15 | 5--3 | 8.1866 | 142 | 100% | 919.3728 | 93.93% | 5.62% | 0.4487% | 42.7471 | 0 | 0 | 42.7471 | 0 | 38.8993 | 8.0679 | 4.8215 | 38.8993 | 8.0679 | 4.8215 | 43.1673 | 8.9531 | 4.8215 | 4.65% | 0.38465 | 0.36561 | 2390.1852 | 345.5626 | 112.657 | 1931.9657 | 2397.7393 | 0 | 0 | 2397.7393 | 0.00141%
2027 | 908 | 908-2040 | Tier-2 | Tier-2---5 | 5--5 | 5.3209 | 576 | 100% | 3646.8048 | 91.91% | 7.986% | 0.1044% | 165.9128 | 0 | 0 | 165.9128 | 0 | 150.9784 | 5.2437 | 28.7922 | 150.9784 | 5.2437 | 28.7922 | 167.5434 | 5.8191 | 28.7922 | 4.55% | 0.17929 | 0.17042 | 20339.8492 | 3923.1303 | 1491.1287 | 14925.5902 | 20425.5442 | 0 | 0 | 20425.5442 | 0.005471%
2027 | 975 | CB 975 | Tier-3 | Tier-3---16 | 5--4 | 0.46496 | 52 | 100% | 1304.3742 | 99.51% | 0.4601% | 0.0271% | 64.252 | 0 | 0 | 64.252 | 0 | 58.4684 | 0.45822 | 127.5989 | 58.4684 | 0.45822 | 127.5989 | 64.8835 | 0.5085 | 127.5989 | 4.926% | 0.10726 | 0.10195 | 12161.0449 | 1953.4321 | 79.6517 | 10127.9611 | 12164.1301 | 0 | 0 | 12164.1301 | 0.002119%
2027 | 1101 | CB 1101 | Tier-2 | Tier-2---9 | 4--4 | 3.0366 | 17 | 100% | 1133.279 | 99.72% | 0.1529% | 0.1272% | 55.9402 | 0 | 0 | 55.9402 | 0 | 50.9048 | 2.9925 | 17.0106 | 50.9048 | 2.9925 | 17.0106 | 56.49 | 3.3209 | 17.0106 | 4.936% | 0.091579 | 0.087045 | 12374.933 | 1964.2318 | 240.1019 | 10170.5993 | 12376.7382 | 0 | 0 | 12376.7382 | 0.001845%
2027 | 492 | 492-14R | Tier-1 | Non-HFTD---2 | 4--3 | 10.8722 | 597 | 100% | 216.5783 | 3.253% | 93.45% | 3.298% | 0.34878 | 0 | 0 | 0.34878 | 0 | 0.31738 | 10.7146 | 0.029622 | 0.31738 | 10.7146 | 0.029622 | 0.3522 | 11.8901 | 0.029622 | 0.161% | 0.045206 | 0.042969 | 4790.8774 | 21.0243 | 4182.3297 | 587.5234 | 5032.259 | 0 | 0 | 5032.259 | 1.15e-05%
2027 | 76 | 76-49F | Tier-1 | Non-HFTD---15 | 1--2 | 0.71628 | 24 | 100% | 2.5849 | 70.44% | 0% | 29.56% | 0.09013 | 0 | 0 | 0.09013 | 0 | 0.082017 | 0.7059 | 0.11619 | 0.082017 | 0.7059 | 0.11619 | 0.091016 | 0.78335 | 0.11619 | 3.487% | 0.002558 | 0.0024314 | 1010.5197 | 2.3761 | 725.7796 | 282.364 | 1026.0758 | 0 | 0 | 1026.0758 | 2.972e-06%
2027 | 257 | CB 257 | Tier-1 | Non-HFTD---10 | 3--2 | 6.9074 | 160 | 100% | 24.5079 | 76.93% | 0% | 23.07% | 0.93326 | 0 | 0 | 0.93326 | 0 | 0.84926 | 6.8073 | 0.12476 | 0.84926 | 6.8073 | 0.12476 | 0.94243 | 7.5541 | 0.12476 | 3.808% | 0.021535 | 0.020469 | 1138.0399 | 1.5436 | 890.8784 | 245.6179 | 1151.7131 | 0 | 0 | 1151.7131 | 3.078e-05%
2027 | 476 | CB 476 | Tier-2 | Tier-2---2 | 5--5 | 18.0017 | 2125 | 100% | 7260.3217 | 73.64% | 26.17% | 0.1876% | 264.6639 | 0 | 0 | 264.6639 | 0 | 240.8405 | 17.7407 | 13.5756 | 240.8405 | 17.7407 | 13.5756 | 267.265 | 19.6871 | 13.5756 | 3.645% | 0.20125 | 0.19129 | 36075.4158 | 6663.2216 | 8787.8653 | 20624.3289 | 36570.586 | 0 | 0 | 36570.586 | 0.008728%
2027 | 768 | 768-20AE | Tier-1 | Non-HFTD---5 | 1--5 | 0.6589 | 98 | 100% | 67.3049 | 99.42% | 0% | 0.5848% | 3.3121 | 0 | 0 | 3.3121 | 0 | 3.014 | 0.64935 | 4.6415 | 3.014 | 0.64935 | 4.6415 | 3.3447 | 0.72059 | 4.6415 | 4.921% | 0.002811 | 0.0026719 | 23943.3951 | 9554.3263 | 1502.6811 | 12886.3878 | 23950.6874 | 0 | 0 | 23950.6874 | 0.0001092%
2027 | 283 | 283-80F | Tier-3 | Tier-3---19 | 5--1 | 0.033523 | 0 | 100% | 22.6843 | 50.28% | 49.56% | 0.1579% | 0.56461 | 0 | 0 | 0.56461 | 0 | 0.51379 | 0.033037 | 15.552 | 0.51379 | 0.033037 | 15.552 | 0.57016 | 0.036661 | 15.552 | 2.489% | 0.17072 | 0.16227 | 132.8742 | 11.4022 | 53.3449 | 68.1271 | 136.3146 | 0 | 0 | 136.3146 | 1.862e-05%
2027 | PB5 | CB PB5 | Tier-1 | Non-HFTD---6 | 3--3 | 5.8622 | 228 | 100% | 65.9306 | 5.839% | 87.56% | 6.598% | 0.19055 | 0 | 0 | 0.19055 | 0 | 0.17339 | 5.7772 | 0.030014 | 0.17339 | 5.7772 | 0.030014 | 0.19242 | 6.411 | 0.030014 | 0.289% | 0.027149 | 0.025805 | 2428.4558 | 3.0271 | 2101.4761 | 323.9526 | 2547.5406 | 0 | 0 | 2547.5406 | 6.283e-06%
2027 | 135 | CB 135 | Tier-1 | Non-HFTD---20 | 1--1 | 0.62631 | 9 | 100% | 0.56317 | 1.996% | 0% | 98% | 0.00055646 | 0 | 0 | 0.00055646 | 0 | 0.00050637 | 0.61723 | 0.00082039 | 0.00050637 | 0.61723 | 0.00082039 | 0.00056193 | 0.68495 | 0.00082039 | 0.09881% | 0.0020306 | 0.0019301 | 277.341 | 0.20452 | 30.2271 | 246.9094 | 291.496 | 0 | 0 | 291.496 | 1.835e-08%
2027 | 299 | 299-815 | Tier-1 | Non-HFTD---7 | 2--3 | 3.2593 | 209 | 100% | 28.2256 | 91.52% | 0% | 8.482% | 1.2787 | 0 | 0 | 1.2787 | 0 | 1.1636 | 3.212 | 0.36226 | 1.1636 | 3.212 | 0.36226 | 1.2912 | 3.5644 | 0.36226 | 4.53% | 0.010153 | 0.0096506 | 2779.9666 | 384.8777 | 211.0962 | 2183.9927 | 2792.246 | 0 | 0 | 2792.246 | 4.217e-05%
2027 | 307 | 307-1492R | Tier-2 | Tier-2---9 | 4--4 | 1.5443 | 285 | 100% | 744.3133 | 92.56% | 7.329% | 0.1099% | 34.1027 | 0 | 0 | 34.1027 | 0 | 31.033 | 1.5219 | 20.3906 | 31.033 | 1.5219 | 20.3906 | 34.4379 | 1.6889 | 20.3906 | 4.582% | 0.057115 | 0.054288 | 13031.835 | 1966.1148 | 878.6004 | 10187.1199 | 13082.321 | 0 | 0 | 13082.321 | 0.001125%
2027 | 159 | 159-37F | Tier-1 | Non-HFTD---14 | 3--1 | 7.37 | 197 | 100% | 7.089 | 33.87% | 0% | 66.13% | 0.11886 | 0 | 0 | 0.11886 | 0 | 0.10816 | 7.2632 | 0.014892 | 0.10816 | 7.2632 | 0.014892 | 0.12003 | 8.0601 | 0.014892 | 1.677% | 0.019669 | 0.018695 | 360.4176 | 0.40479 | 142.323 | 217.6898 | 372.8294 | 0 | 0 | 372.8294 | 3.92e-06%
2027 | MT3 | CB MT3 | Tier-1 | Non-HFTD---16 | 2--1 | 3.6305 | 161 | 100% | 4.5475 | 41.58% | 0% | 58.42% | 0.093595 | 0 | 0 | 0.093595 | 0 | 0.08517 | 3.5779 | 0.023805 | 0.08517 | 3.5779 | 0.023805 | 0.094514 | 3.9704 | 0.023805 | 2.058% | 0.011697 | 0.011118 | 388.7903 | 0.29705 | 181.7474 | 206.7459 | 400.6191 | 0 | 0 | 400.6191 | 3.086e-06%
2027 | 158 | 158-29 | Tier-1 | Non-HFTD---12 | 4--1 | 16.0678 | 488 | 100% | 14.9816 | 28.99% | 0% | 71.01% | 0.215 | 0 | 0 | 0.215 | 0 | 0.19565 | 15.8348 | 0.012356 | 0.19565 | 15.8348 | 0.012356 | 0.21712 | 17.5722 | 0.012356 | 1.435% | 0.043297 | 0.041154 | 346.0178 | 1.8646 | 116.0528 | 228.1004 | 358.8133 | 0 | 0 | 358.8133 | 7.09e-06%
2027 | 442 | 442-46R | Tier-3 | Tier-3---19 | 5--1 | 0.055682 | 33 | 100% | 88.141 | 1.745% | 98.17% | 0.08447% | 0.076128 | 0 | 0 | 0.076128 | 0 | 0.069276 | 0.054874 | 1.2624 | 0.069276 | 0.054874 | 1.2624 | 0.076876 | 0.060895 | 1.2624 | 0.08637% | 0.35092 | 0.33355 | 251.1714 | 0.81668 | 223.9277 | 26.427 | 264.0236 | 0 | 0 | 264.0236 | 2.51e-06%
2027 | 859 | 859-13F | Tier-1 | Non-HFTD---1 | 4--5 | 10.7166 | 869 | 100% | 1153.8557 | 99.35% | 0% | 0.6497% | 56.7448 | 0 | 0 | 56.7448 | 0 | 51.637 | 10.5613 | 4.8893 | 51.637 | 10.5613 | 4.8893 | 57.3025 | 11.72 | 4.8893 | 4.918% | 0.035677 | 0.033911 | 32341.7236 | 5122.1729 | 819.8446 | 26399.7061 | 32352.6656 | 0 | 0 | 32352.6656 | 0.001871%
2027 | 211 | 211-279R | Tier-2 | Tier-2---10 | 5--3 | 15.3767 | 416 | 100% | 1199.6322 | 89.49% | 9.8% | 0.7134% | 53.1388 | 0 | 0 | 53.1388 | 0 | 48.3556 | 15.1538 | 3.191 | 48.3556 | 15.1538 | 3.191 | 53.6611 | 16.8164 | 3.191 | 4.43% | 0.37314 | 0.35467 | 3215.0069 | 263.9331 | 327.4552 | 2623.6187 | 3232.6094 | 0 | 0 | 3232.6094 | 0.001752%
2027 | SE4 | CB SE4 | Tier-1 | Non-HFTD---12 | 3--2 | 1.139 | 45 | 100% | 13.0711 | 1.917% | 92.58% | 5.504% | 0.012405 | 0 | 0 | 0.012405 | 0 | 0.011288 | 1.1225 | 0.010056 | 0.011288 | 1.1225 | 0.010056 | 0.012526 | 1.2457 | 0.010056 | 0.0949% | 0.021339 | 0.020283 | 612.5496 | 1.2137 | 530.3816 | 80.9543 | 643.8382 | 0 | 0 | 643.8382 | 4.091e-07%
2027 | 340 | CB 340 | Tier-1 | Non-HFTD---7 | 1--5 | 0.42082 | 33 | 100% | 29.3144 | 98.84% | 0% | 1.164% | 1.4342 | 0 | 0 | 1.4342 | 0 | 1.3051 | 0.41471 | 3.1469 | 1.3051 | 0.41471 | 3.1469 | 1.4483 | 0.46022 | 3.1469 | 4.892% | 0.0015836 | 0.0015052 | 18511.2088 | 2537.4844 | 2809.9216 | 13163.8027 | 18522.4306 | 0 | 0 | 18522.4306 | 4.729e-05%
2027 | 507 | 507-1733 | Tier-1 | Non-HFTD---13 | 1--3 | 1.175 | 58 | 100% | 7.2494 | 86.12% | 0% | 13.88% | 0.30903 | 0 | 0 | 0.30903 | 0 | 0.28121 | 1.158 | 0.24284 | 0.28121 | 1.158 | 0.24284 | 0.31207 | 1.2851 | 0.24284 | 4.263% | 0.003877 | 0.0036851 | 1869.8551 | 69.1763 | 1211.0556 | 589.6232 | 1883.3737 | 0 | 0 | 1883.3737 | 1.019e-05%
2027 | 61 | 61-23F | Tier-1 | Non-HFTD---7 | 2--3 | 0.13197 | 28 | 100% | 42.4736 | 0.005397% | 99.75% | 0.2412% | 0.00011347 | 0 | 0 | 0.00011347 | 0 | 0.00010326 | 0.13005 | 0.00079397 | 0.00010326 | 0.13005 | 0.00079397 | 0.00011459 | 0.14432 | 0.00079397 | 0.0002672% | 0.011235 | 0.010679 | 3780.542 | 4.6215 | 3457.7842 | 318.1363 | 3977.4139 | 0 | 0 | 3977.4139 | 3.742e-09%
2027 | 222 | 222-2085 | Tier-3 | Tier-3---3 | 5--5 | 31.2755 | 3127 | 100% | 16772.3082 | 96.7% | 3.181% | 0.1236% | 802.7939 | 0 | 0 | 802.7939 | 0 | 730.5315 | 30.8221 | 23.7016 | 730.5315 | 30.8221 | 23.7016 | 810.6837 | 34.2038 | 23.7016 | 4.786% | 0.35117 | 0.33379 | 47761.3033 | 7204.6408 | 1463.9747 | 39092.6878 | 47843.4976 | 0 | 0 | 47843.4976 | 0.02647%
2027 | 53 | 53-49 | Tier-1 | Non-HFTD---18 | 2--1 | 2.3103 | 59 | 100% | 1.7953 | 15.92% | 0% | 84.08% | 0.014151 | 0 | 0 | 0.014151 | 0 | 0.012878 | 2.2768 | 0.0056561 | 0.012878 | 2.2768 | 0.0056561 | 0.01429 | 2.5266 | 0.0056561 | 0.7883% | 0.0061878 | 0.0058815 | 290.1286 | 0.18355 | 68.3602 | 221.5848 | 302.8317 | 0 | 0 | 302.8317 | 4.667e-07%
2027 | 589 | CB 589 | Tier-1 | Non-HFTD---4 | 2--5 | 1.6411 | 159 | 100% | 115.513 | 99.19% | 0% | 0.8071% | 5.6717 | 0 | 0 | 5.6717 | 0 | 5.1612 | 1.6173 | 3.1912 | 5.1612 | 1.6173 | 3.1912 | 5.7275 | 1.7948 | 3.1912 | 4.91% | 0.0061356 | 0.0058319 | 18826.6917 | 3852.5482 | 1417.3063 | 13556.8372 | 18834.6054 | 0 | 0 | 18834.6054 | 0.000187%
2027 | 504 | 504-2501R | Tier-2 | Tier-2---9 | 3--5 | 5.5121 | 308 | 100% | 733.6834 | 99.51% | 0% | 0.4917% | 36.1388 | 0 | 0 | 36.1388 | 0 | 32.8858 | 5.4322 | 6.0539 | 32.8858 | 5.4322 | 6.0539 | 36.4939 | 6.0282 | 6.0539 | 4.926% | 0.021593 | 0.020524 | 33978.4661 | 5431.2856 | 538.4348 | 28008.7457 | 33987.1667 | 0 | 0 | 33987.1667 | 0.001192%
2027 | 342 | 342-521AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.2639 | 79 | 100% | 2.959 | 30.71% | 0% | 69.29% | 0.044974 | 0 | 0 | 0.044974 | 0 | 0.040926 | 2.231 | 0.018344 | 0.040926 | 2.231 | 0.018344 | 0.045416 | 2.4758 | 0.018344 | 1.52% | 0.0073744 | 0.0070094 | 401.2552 | 3.7445 | 126.7331 | 270.7777 | 415.7354 | 0 | 0 | 415.7354 | 1.483e-06%
2027 | 851 | CB 851 | Tier-1 | Non-HFTD---4 | 1--5 | 0.77311 | 72 | 100% | 102.5522 | 99.44% | 0% | 0.5561% | 5.0481 | 0 | 0 | 5.0481 | 0 | 4.5937 | 0.7619 | 6.0293 | 4.5937 | 0.7619 | 6.0293 | 5.0977 | 0.84549 | 6.0293 | 4.922% | 0.0031694 | 0.0030125 | 32356.9802 | 6963.0193 | 3626.5901 | 21767.3707 | 32366.3506 | 0 | 0 | 32366.3506 | 0.0001665%
2027 | 1073 | CB 1073 | Tier-1 | Non-HFTD---3 | 4--4 | 6.1307 | 211 | 100% | 166.0602 | 6.113% | 91.74% | 2.147% | 0.50246 | 0 | 0 | 0.50246 | 0 | 0.45723 | 6.0418 | 0.075678 | 0.45723 | 6.0418 | 0.075678 | 0.50739 | 6.7047 | 0.075678 | 0.3026% | 0.033742 | 0.032072 | 4921.469 | 22.1347 | 4284.5904 | 614.7439 | 5162.102 | 0 | 0 | 5162.102 | 1.657e-05%
2027 | 289 | CB 289 | Tier-1 | Non-HFTD---6 | 3--3 | 4.3732 | 707 | 100% | 64.7389 | 39.27% | 55.62% | 5.104% | 1.2585 | 0 | 0 | 1.2585 | 0 | 1.1452 | 4.3097 | 0.26573 | 1.1452 | 4.3097 | 0.26573 | 1.2709 | 4.7826 | 0.26573 | 1.944% | 0.018234 | 0.017332 | 3550.4112 | 114.2687 | 2547.3845 | 888.758 | 3662.6956 | 0 | 0 | 3662.6956 | 4.15e-05%
2027 | 207 | 207-101R | Tier-1 | Non-HFTD---8 | 4--2 | 11.3577 | 523 | 100% | 42.8651 | 83.69% | 0% | 16.31% | 1.7758 | 0 | 0 | 1.7758 | 0 | 1.6159 | 11.1931 | 0.14437 | 1.6159 | 11.1931 | 0.14437 | 1.7932 | 12.4211 | 0.14437 | 4.143% | 0.032633 | 0.031017 | 1313.5599 | 147.1403 | 219.5178 | 946.9018 | 1324.7172 | 0 | 0 | 1324.7172 | 5.856e-05%
2027 | 129 | CB 129 | Tier-1 | Non-HFTD---16 | 2--1 | 2.6926 | 56 | 100% | 3.1821 | 23.64% | 0% | 76.36% | 0.037241 | 0 | 0 | 0.037241 | 0 | 0.033888 | 2.6536 | 0.012771 | 0.033888 | 2.6536 | 0.012771 | 0.037607 | 2.9447 | 0.012771 | 1.17% | 0.009111 | 0.00866 | 349.2616 | 7.9358 | 58.2971 | 283.0287 | 363.1501 | 0 | 0 | 363.1501 | 1.228e-06%
2027 | 1117 | 1117-1121F | Tier-1 | Non-HFTD---4 | 2--4 | 0.2763 | 27 | 100% | 101.5663 | 18.17% | 81.65% | 0.1832% | 0.91333 | 0 | 0 | 0.91333 | 0 | 0.83112 | 0.27229 | 3.0523 | 0.83112 | 0.27229 | 3.0523 | 0.92231 | 0.30217 | 3.0523 | 0.8992% | 0.007029 | 0.0066811 | 14449.6047 | 439.553 | 10775.9849 | 3234.0669 | 15065.4048 | 0 | 0 | 15065.4048 | 3.012e-05%
2027 | 462 | CB 462 | Tier-2 | Tier-2---19 | 2--4 | 2.1019 | 19 | 100% | 42.4238 | 96.69% | 0% | 3.313% | 2.0304 | 0 | 0 | 2.0304 | 0 | 1.8476 | 2.0714 | 0.89199 | 1.8476 | 2.0714 | 0.89199 | 2.0504 | 2.2986 | 0.89199 | 4.786% | 0.0069768 | 0.0066314 | 6080.6996 | 1110.385 | 1800.7984 | 3169.5162 | 6091.1906 | 0 | 0 | 6091.1906 | 6.696e-05%
2027 | 323 | 323-471 | Tier-1 | Non-HFTD---8 | 4--2 | 9.5176 | 267 | 100% | 28.3599 | 75.43% | 0% | 24.57% | 1.059 | 0 | 0 | 1.059 | 0 | 0.96363 | 9.3796 | 0.10274 | 0.96363 | 9.3796 | 0.10274 | 1.0694 | 10.4088 | 0.10274 | 3.734% | 0.03033 | 0.028828 | 935.0577 | 152.0048 | 120.2204 | 662.8324 | 947.0204 | 0 | 0 | 947.0204 | 3.492e-05%
2027 | 452 | 452-1403 | Tier-2 | Tier-2---15 | 1--5 | 0.20947 | 25 | 100% | 137.227 | 99.9% | 0% | 0.1049% | 6.7856 | 0 | 0 | 6.7856 | 0 | 6.1748 | 0.20643 | 29.912 | 6.1748 | 0.20643 | 29.912 | 6.8523 | 0.22908 | 29.912 | 4.945% | 0.0007938 | 0.00075451 | 172873.5238 | 28023.5372 | 18.7375 | 144831.2491 | 172882.965 | 0 | 0 | 172882.965 | 0.0002238%
2027 | 732 | CB 732 | Tier-1 | Non-HFTD---2 | 4--3 | 16.7686 | 825 | 100% | 213.1572 | 94.97% | 0% | 5.028% | 10.0208 | 0 | 0 | 10.0208 | 0 | 9.1188 | 16.5254 | 0.5518 | 9.1188 | 16.5254 | 0.5518 | 10.1192 | 18.3386 | 0.5518 | 4.701% | 0.049818 | 0.047352 | 4278.701 | 526.9055 | 864.1827 | 2887.6129 | 4289.9048 | 0 | 0 | 4289.9048 | 0.0003304%
2027 | 1233 | 1233-259R | Tier-3 | Tier-3---16 | 5--4 | 4.8975 | 146 | 100% | 1558.5389 | 98.56% | 1.214% | 0.2225% | 76.0395 | 0 | 0 | 76.0395 | 0 | 69.195 | 4.8265 | 14.3365 | 69.195 | 4.8265 | 14.3365 | 76.7869 | 5.356 | 14.3365 | 4.879% | 0.12749 | 0.12118 | 12225.1388 | 1994.1014 | 166.7691 | 10064.2683 | 12234.2836 | 0 | 0 | 12234.2836 | 0.002508%
2027 | 783 | CB 783 | Tier-1 | Non-HFTD---4 | 3--4 | 1.3273 | 6 | 100% | 129.217 | 41.62% | 57.78% | 0.5927% | 2.6624 | 0 | 0 | 2.6624 | 0 | 2.4227 | 1.308 | 1.8522 | 2.4227 | 1.308 | 1.8522 | 2.6885 | 1.4515 | 1.8522 | 2.06% | 0.014816 | 0.014083 | 8721.335 | 243.3525 | 6978.51 | 1499.4724 | 8986.4721 | 0 | 0 | 8986.4721 | 8.78e-05%
2027 | 341 | 341-1157F | Tier-1 | Non-HFTD---7 | 2--4 | 2.6621 | 96 | 100% | 34.4267 | 96.63% | 0% | 3.372% | 1.6467 | 0 | 0 | 1.6467 | 0 | 1.4984 | 2.6235 | 0.57115 | 1.4984 | 2.6235 | 0.57115 | 1.6628 | 2.9114 | 0.57115 | 4.783% | 0.0066766 | 0.0063461 | 5156.3263 | 996.266 | 92.4403 | 4067.62 | 5165.3804 | 0 | 0 | 5165.3804 | 5.43e-05%
2027 | 430 | CB 430 | Tier-1 | Non-HFTD---19 | 1--2 | 0.045833 | 1 | 100% | 0.27806 | 60.51% | 0% | 39.49% | 0.0083278 | 0 | 0 | 0.0083278 | 0 | 0.0075782 | 0.045169 | 0.16778 | 0.0075782 | 0.045169 | 0.16778 | 0.0084097 | 0.050125 | 0.16778 | 2.995% | 0.0002042 | 0.00019409 | 1361.6908 | 10.8448 | 808.9488 | 541.8972 | 1389.698 | 0 | 0 | 1389.698 | 2.746e-07%
2027 | 1023 | 1023-48R | Tier-2 | Tier-2---5 | 5--5 | 16.5267 | 1228 | 100% | 3773.8473 | 97.39% | 2.337% | 0.2725% | 181.93 | 0 | 0 | 181.93 | 0 | 165.5538 | 16.287 | 10.1648 | 165.5538 | 16.287 | 10.1648 | 183.718 | 18.074 | 10.1648 | 4.821% | 0.12816 | 0.12182 | 29445.7307 | 4617.189 | 643.444 | 24185.0978 | 29485.7528 | 0 | 0 | 29485.7528 | 0.005999%
2027 | 322 | 322-32R | Tier-1 | Non-HFTD---19 | 1--2 | 0.064394 | 4 | 100% | 0.50266 | 78.22% | 0% | 21.78% | 0.019462 | 0 | 0 | 0.019462 | 0 | 0.01771 | 0.06346 | 0.27907 | 0.01771 | 0.06346 | 0.27907 | 0.019653 | 0.070423 | 0.27907 | 3.872% | 0.0003072 | 0.00029199 | 1636.2621 | 0.9533 | 1308.036 | 327.2728 | 1654.824 | 0 | 0 | 1654.824 | 6.418e-07%
2027 | 518 | 518-39 | Tier-1 | Non-HFTD---17 | 1--2 | 0.84644 | 38 | 100% | 1.403 | 67.89% | 0% | 32.11% | 0.047151 | 0 | 0 | 0.047151 | 0 | 0.042907 | 0.83417 | 0.051437 | 0.042907 | 0.83417 | 0.051437 | 0.047614 | 0.92569 | 0.051437 | 3.361% | 0.002089 | 0.0019856 | 671.6292 | 2.198 | 463.1642 | 206.267 | 682.8598 | 0 | 0 | 682.8598 | 1.555e-06%
2027 | 991 | 991-1 | Tier-2 | Tier-2---12 | 4--5 | 1.2636 | 42 | 100% | 626.8618 | 65.87% | 33.98% | 0.153% | 20.4388 | 0 | 0 | 20.4388 | 0 | 18.5991 | 1.2453 | 14.9352 | 18.5991 | 1.2453 | 14.9352 | 20.6397 | 1.3819 | 14.9352 | 3.261% | 0.034773 | 0.033051 | 18027.4627 | 3649.7735 | 5561.6241 | 8816.0652 | 18347.8976 | 0 | 0 | 18347.8976 | 0.000674%
2027 | 152 | 152-1713F | Tier-1 | Non-HFTD---12 | 3--2 | 5.262 | 136 | 100% | 9.6728 | 69.07% | 0% | 30.93% | 0.33072 | 0 | 0 | 0.33072 | 0 | 0.30095 | 5.1857 | 0.058036 | 0.30095 | 5.1857 | 0.058036 | 0.33397 | 5.7546 | 0.058036 | 3.419% | 0.013625 | 0.01295 | 709.9482 | 124.6406 | 78.4846 | 506.823 | 721.3825 | 0 | 0 | 721.3825 | 1.091e-05%
2027 | 576 | CB 576 | Tier-2 | Tier-2---12 | 4--4 | 0.64527 | 28 | 100% | 417.7025 | 78.37% | 21.49% | 0.1463% | 16.2034 | 0 | 0 | 16.2034 | 0 | 14.7448 | 0.63591 | 23.187 | 14.7448 | 0.63591 | 23.187 | 16.3626 | 0.70568 | 23.187 | 3.879% | 0.047237 | 0.044899 | 8842.622 | 1103.3667 | 1857.3002 | 5881.9552 | 8942.2431 | 0 | 0 | 8942.2431 | 0.0005343%
2027 | IB1 | CB IB1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.2845 | 58 | 100% | 2.8974 | 41.24% | 0% | 58.76% | 0.059153 | 0 | 0 | 0.059153 | 0 | 0.053829 | 3.2369 | 0.01663 | 0.053829 | 3.2369 | 0.01663 | 0.059735 | 3.592 | 0.01663 | 2.042% | 0.0077878 | 0.0074023 | 372.0428 | 0.3241 | 172.327 | 199.3917 | 383.4268 | 0 | 0 | 383.4268 | 1.951e-06%
2027 | 1021 | 1021-92 | Tier-3 | Tier-3---15 | 5--4 | 0.46834 | 30 | 100% | 794.3626 | 99.6% | 0.3592% | 0.04176% | 39.1633 | 0 | 0 | 39.1633 | 0 | 35.6381 | 0.46155 | 77.2141 | 35.6381 | 0.46155 | 77.2141 | 39.5482 | 0.51219 | 77.2141 | 4.93% | 0.099013 | 0.094112 | 8022.7784 | 1292.1342 | 24.8963 | 6705.7479 | 8024.4536 | 0 | 0 | 8024.4536 | 0.001291%
2027 | 776 | CB 776 | Tier-2 | Tier-2---18 | 3--3 | 2.6153 | 52 | 100% | 55.0677 | 92.66% | 4.028% | 3.312% | 2.5258 | 0 | 0 | 2.5258 | 0 | 2.2984 | 2.5774 | 0.89175 | 2.2984 | 2.5774 | 0.89175 | 2.5506 | 2.8602 | 0.89175 | 4.587% | 0.014982 | 0.01424 | 3675.6367 | 654.2376 | 129.2917 | 2892.1074 | 3689.6867 | 0 | 0 | 3689.6867 | 8.329e-05%
2027 | 157 | 157-204R | Tier-3 | Tier-3---11 | 5--4 | 13.2184 | 329 | 100% | 3876.1334 | 98.99% | 0.834% | 0.1804% | 189.9223 | 0 | 0 | 189.9223 | 0 | 172.8267 | 13.0268 | 13.2671 | 172.8267 | 13.0268 | 13.2671 | 191.7888 | 14.456 | 13.2671 | 4.9% | 0.32777 | 0.31154 | 11825.9094 | 1771.5346 | 144.6692 | 9909.7056 | 11832.1568 | 0 | 0 | 11832.1568 | 0.006263%
2027 | 449 | CB 449 | Tier-3 | Tier-3---20 | 1--5 | 0.054356 | 0 | 100% | 7.8127 | 98.22% | 0% | 1.784% | 0.37983 | 0 | 0 | 0.37983 | 0 | 0.34564 | 0.053568 | 6.4524 | 0.34564 | 0.053568 | 6.4524 | 0.38356 | 0.059445 | 6.4524 | 4.862% | 0.0002642 | 0.00025112 | 29571.2422 | 4082.6639 | 218.8037 | 25269.7746 | 29598.7157 | 0 | 0 | 29598.7157 | 1.253e-05%
2027 | 702 | 702-27R | Tier-1 | Non-HFTD---3 | 4--3 | 12.2498 | 298 | 100% | 127.2983 | 14.57% | 79% | 6.429% | 0.91821 | 0 | 0 | 0.91821 | 0 | 0.83556 | 12.0722 | 0.069213 | 0.83556 | 12.0722 | 0.069213 | 0.92723 | 13.3967 | 0.069213 | 0.7213% | 0.039338 | 0.03739 | 3236.0467 | 32.4645 | 2654.2302 | 549.352 | 3380.0157 | 0 | 0 | 3380.0157 | 3.028e-05%
2027 | 442 | 442-509R | Tier-3 | Tier-3---15 | 5--3 | 4.9693 | 856 | 100% | 852.9261 | 84.92% | 14.72% | 0.3553% | 35.855 | 0 | 0 | 35.855 | 0 | 32.6276 | 4.8973 | 6.6624 | 32.6276 | 4.8973 | 6.6624 | 36.2074 | 5.4346 | 6.6624 | 4.204% | 0.36954 | 0.35125 | 2308.0588 | 278.8986 | 306.2936 | 1722.8667 | 2326.1793 | 0 | 0 | 2326.1793 | 0.001182%
2027 | 192 | 192-657AE | Tier-1 | Non-HFTD---4 | 2--4 | 1.8044 | 96 | 100% | 94.561 | 98.93% | 0% | 1.074% | 4.6305 | 0 | 0 | 4.6305 | 0 | 4.2137 | 1.7782 | 2.3696 | 4.2137 | 1.7782 | 2.3696 | 4.676 | 1.9733 | 2.3696 | 4.897% | 0.006219 | 0.0059112 | 15205.1851 | 2854.2403 | 2013.1644 | 10337.7804 | 15213.6876 | 0 | 0 | 15213.6876 | 0.0001527%
2027 | 357 | 357-1299R | Tier-3 | Tier-3---9 | 5--5 | 2.7532 | 52 | 100% | 5098.7328 | 99.68% | 0.2892% | 0.03002% | 251.5816 | 0 | 0 | 251.5816 | 0 | 228.9358 | 2.7133 | 84.3759 | 228.9358 | 2.7133 | 84.3759 | 254.0541 | 3.011 | 84.3759 | 4.934% | 0.2409 | 0.22898 | 21164.9633 | 3980.007 | 56.5395 | 17128.4168 | 21168.4818 | 0 | 0 | 21168.4818 | 0.008296%
2027 | 52 | 52-18F | Tier-1 | Non-HFTD---12 | 2--2 | 3.9165 | 42 | 100% | 11.6184 | 68.06% | 0% | 31.94% | 0.39141 | 0 | 0 | 0.39141 | 0 | 0.35617 | 3.8597 | 0.09228 | 0.35617 | 3.8597 | 0.09228 | 0.39525 | 4.2832 | 0.09228 | 3.369% | 0.012594 | 0.011971 | 922.5162 | 0.22173 | 654.6115 | 267.6829 | 937.8622 | 0 | 0 | 937.8622 | 1.291e-05%
2027 | 940 | 940-391 | Tier-1 | Non-HFTD---18 | 1--1 | 1.8076 | 25 | 100% | 1.1106 | 27.65% | 0% | 72.35% | 0.015203 | 0 | 0 | 0.015203 | 0 | 0.013834 | 1.7814 | 0.0077658 | 0.013834 | 1.7814 | 0.0077658 | 0.015352 | 1.9769 | 0.0077658 | 1.369% | 0.004339 | 0.0041242 | 255.964 | 0.14879 | 87.5462 | 168.2691 | 265.6079 | 0 | 0 | 265.6079 | 5.013e-07%
2027 | 1081 | CB 1081 | Tier-1 | Non-HFTD---2 | 4--4 | 9.8183 | 503 | 100% | 237.9505 | 29.91% | 67.53% | 2.553% | 3.5234 | 0 | 0 | 3.5234 | 0 | 3.2062 | 9.676 | 0.33136 | 3.2062 | 9.676 | 0.33136 | 3.558 | 10.7376 | 0.33136 | 1.481% | 0.036958 | 0.035128 | 6438.4369 | 198.6995 | 5359.42 | 880.3174 | 6673.437 | 0 | 0 | 6673.437 | 0.0001162%
2027 | 203 | 203-21R | Tier-1 | Non-HFTD---4 | 3--4 | 2.1493 | 204 | 100% | 165.9937 | 4.67% | 94.37% | 0.9641% | 0.38369 | 0 | 0 | 0.38369 | 0 | 0.34915 | 2.1181 | 0.16484 | 0.34915 | 2.1181 | 0.16484 | 0.38746 | 2.3505 | 0.16484 | 0.2311% | 0.023296 | 0.022143 | 7125.2936 | 41.2792 | 6274.0075 | 810.0069 | 7479.0361 | 0 | 0 | 7479.0361 | 1.265e-05%
2027 | 510 | 510-49R | Tier-1 | Non-HFTD---1 | 3--4 | 2.222 | 211 | 100% | 240.5874 | 27.72% | 71.76% | 0.5245% | 3.301 | 0 | 0 | 3.301 | 0 | 3.0039 | 2.1898 | 1.3718 | 3.0039 | 2.1898 | 1.3718 | 3.3335 | 2.43 | 1.3718 | 1.372% | 0.018276 | 0.017371 | 13164.1155 | 585.4029 | 9744.1726 | 2834.54 | 13659.6467 | 0 | 0 | 13659.6467 | 0.0001089%
2027 | MOR1 | CB MOR1 | Tier-2 | Tier-2---4 | 5--5 | 3.55 | 303 | 100% | 5119.7141 | 98.56% | 1.393% | 0.05121% | 249.7665 | 0 | 0 | 249.7665 | 0 | 227.2841 | 3.4985 | 64.9659 | 227.2841 | 3.4985 | 64.9659 | 252.2212 | 3.8824 | 64.9659 | 4.879% | 0.12647 | 0.12021 | 40481.7763 | 7026.0973 | 519.7061 | 32935.973 | 40512.2177 | 0 | 0 | 40512.2177 | 0.008236%
2027 | 240 | 240-1044 | Tier-3 | Tier-3---16 | 4--4 | 2.7573 | 100 | 100% | 791.3356 | 98.7% | 1.112% | 0.1837% | 38.6637 | 0 | 0 | 38.6637 | 0 | 35.1835 | 2.7174 | 12.9477 | 35.1835 | 2.7174 | 12.9477 | 39.0437 | 3.0155 | 12.9477 | 4.886% | 0.076308 | 0.072531 | 10370.2289 | 1768.6676 | 147.2931 | 8454.2683 | 10377.2245 | 0 | 0 | 10377.2245 | 0.001275%
2027 | 362 | CB 362 | Tier-1 | Non-HFTD---5 | 3--3 | 4.5676 | 102 | 100% | 90.5945 | 20.96% | 74.63% | 4.416% | 0.93975 | 0 | 0 | 0.93975 | 0 | 0.85516 | 4.5014 | 0.18998 | 0.85516 | 4.5014 | 0.18998 | 0.94899 | 4.9953 | 0.18998 | 1.037% | 0.019673 | 0.018699 | 4605.0162 | 4.0643 | 4102.7241 | 498.2277 | 4794.5791 | 0 | 0 | 4794.5791 | 3.099e-05%
2027 | OS4 | CB OS4 | Tier-1 | Non-HFTD---16 | 2--1 | 2.4284 | 86 | 100% | 3.0117 | 33.83% | 0% | 66.17% | 0.050427 | 0 | 0 | 0.050427 | 0 | 0.045888 | 2.3932 | 0.019174 | 0.045888 | 2.3932 | 0.019174 | 0.050923 | 2.6558 | 0.019174 | 1.674% | 0.0070618 | 0.0067122 | 426.4805 | 1.5389 | 161.7401 | 263.2015 | 441.1779 | 0 | 0 | 441.1779 | 1.663e-06%
2027 | NTL1 | CB NTL1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.6614 | 519 | 100% | 2.8418 | 23.91% | 0% | 76.09% | 0.033635 | 0 | 0 | 0.033635 | 0 | 0.030607 | 3.6083 | 0.0084824 | 0.030607 | 3.6083 | 0.0084824 | 0.033965 | 4.0042 | 0.0084824 | 1.184% | 0.0099992 | 0.0095042 | 284.2073 | 4.5526 | 60.82 | 218.8347 | 295.4693 | 0 | 0 | 295.4693 | 1.109e-06%
2027 | 1297 | 1297-34F | Tier-1 | Non-HFTD---4 | 2--4 | 2.0714 | 47 | 100% | 97.1169 | 3.668% | 94.54% | 1.791% | 0.17635 | 0 | 0 | 0.17635 | 0 | 0.16047 | 2.0413 | 0.078613 | 0.16047 | 2.0413 | 0.078613 | 0.17808 | 2.2653 | 0.078613 | 0.1816% | 0.012533 | 0.011912 | 7749.0176 | 8.2538 | 6940.7523 | 800.0115 | 8137.7662 | 0 | 0 | 8137.7662 | 5.815e-06%
2027 | 232 | 232-40AE | Tier-2 | Tier-2---19 | 2--3 | 0.081438 | 6 | 100% | 11.4297 | 0.4523% | 98.58% | 0.9661% | 0.0025592 | 0 | 0 | 0.0025592 | 0 | 0.0023289 | 0.080257 | 0.029017 | 0.0023289 | 0.080257 | 0.029017 | 0.0025844 | 0.089063 | 0.029017 | 0.02239% | 0.0059544 | 0.0056597 | 1919.5436 | 3.4341 | 1729.7945 | 186.3149 | 2019.0571 | 0 | 0 | 2019.0571 | 8.439e-08%
2027 | 1482 | 1482-28 | Tier-1 | Non-HFTD---14 | 2--2 | 3.2782 | 104 | 100% | 5.0457 | 55.06% | 0% | 44.94% | 0.13753 | 0 | 0 | 0.13753 | 0 | 0.12515 | 3.2307 | 0.038737 | 0.12515 | 3.2307 | 0.038737 | 0.13888 | 3.5852 | 0.038737 | 2.726% | 0.0090634 | 0.0086148 | 556.7146 | 0.18825 | 329.2696 | 227.2568 | 569.7429 | 0 | 0 | 569.7429 | 4.535e-06%
2027 | 971 | 971-388R | Tier-3 | Tier-3---4 | 5--5 | 17.9011 | 1159 | 100% | 11267.961 | 98.98% | 0.9235% | 0.09902% | 552.0609 | 0 | 0 | 552.0609 | 0 | 502.3679 | 17.6416 | 28.4764 | 502.3679 | 17.6416 | 28.4764 | 557.4865 | 19.5772 | 28.4764 | 4.899% | 0.17642 | 0.16769 | 63870.0886 | 10985.172 | 547.8169 | 52337.0996 | 63904.0993 | 0 | 0 | 63904.0993 | 0.0182%
2027 | 1525 | CB 1525 | Tier-2 | Tier-2---13 | 4--4 | 6.2326 | 240 | 100% | 259.6903 | 35.49% | 63.12% | 1.387% | 4.5624 | 0 | 0 | 4.5624 | 0 | 4.1518 | 6.1422 | 0.67594 | 4.1518 | 6.1422 | 0.67594 | 4.6073 | 6.8161 | 0.67594 | 1.757% | 0.050512 | 0.048011 | 5141.181 | 367.2769 | 3050.2081 | 1723.6959 | 5313.8944 | 0 | 0 | 5313.8944 | 0.0001505%
2027 | 176 | 176-1845R | Tier-3 | Tier-3---11 | 5--5 | 7.3522 | 280 | 100% | 3401.0234 | 97.74% | 2.113% | 0.1474% | 164.5455 | 0 | 0 | 164.5455 | 0 | 149.7342 | 7.2456 | 20.6654 | 149.7342 | 7.2456 | 20.6654 | 166.1626 | 8.0406 | 20.6654 | 4.838% | 0.20978 | 0.19939 | 16212.4883 | 2568.5055 | 309.8495 | 13334.1334 | 16231.572 | 0 | 0 | 16231.572 | 0.005426%
2027 | 505 | CB 505 | Tier-1 | Non-HFTD---9 | 2--3 | 2.4237 | 236 | 100% | 21.0176 | 91.98% | 0% | 8.019% | 0.95694 | 0 | 0 | 0.95694 | 0 | 0.8708 | 2.3885 | 0.36458 | 0.8708 | 2.3885 | 0.36458 | 0.96634 | 2.6506 | 0.36458 | 4.553% | 0.0074238 | 0.0070563 | 2831.1077 | 271.0214 | 968.8336 | 1591.2527 | 2842.9314 | 0 | 0 | 2842.9314 | 3.156e-05%
2027 | 550 | 550-665R | Tier-1 | Non-HFTD---14 | 2--2 | 4.5705 | 162 | 100% | 7.2973 | 61.93% | 0% | 38.07% | 0.22372 | 0 | 0 | 0.22372 | 0 | 0.20358 | 4.5042 | 0.045198 | 0.20358 | 4.5042 | 0.045198 | 0.22592 | 4.9984 | 0.045198 | 3.066% | 0.01349 | 0.012822 | 540.9468 | 37.0768 | 158.5779 | 345.2921 | 551.6702 | 0 | 0 | 551.6702 | 7.377e-06%
2027 | 92 | CB 92 | Tier-1 | Non-HFTD---6 | 3--3 | 2.9091 | 147 | 100% | 46.3322 | 87.55% | 8.668% | 3.778% | 2.008 | 0 | 0 | 2.008 | 0 | 1.8272 | 2.8669 | 0.63735 | 1.8272 | 2.8669 | 0.63735 | 2.0277 | 3.1815 | 0.63735 | 4.334% | 0.013793 | 0.013111 | 3359.0098 | 253.9545 | 2011.5361 | 1093.5193 | 3380.7821 | 0 | 0 | 3380.7821 | 6.622e-05%
2027 | 403 | 403-9F | Tier-1 | Non-HFTD---20 | 1--1 | 0.82969 | 47 | 100% | 0.45165 | 12.22% | 0% | 87.78% | 0.0027327 | 0 | 0 | 0.0027327 | 0 | 0.0024867 | 0.81766 | 0.0030412 | 0.0024867 | 0.81766 | 0.0030412 | 0.0027595 | 0.90737 | 0.0030412 | 0.605% | 0.0021892 | 0.0020808 | 206.3063 | 0.33556 | 40.449 | 165.5217 | 215.737 | 0 | 0 | 215.737 | 9.011e-08%
2027 | 330 | 330-44R | Tier-1 | Non-HFTD---19 | 1--2 | 0.010227 | 0 | 100% | 0.13525 | 15.38% | 0% | 84.62% | 0.0010298 | 0 | 0 | 0.0010298 | 0 | 0.00093708 | 0.010079 | 0.092974 | 0.00093708 | 0.010079 | 0.092974 | 0.0010399 | 0.011185 | 0.092974 | 0.7614% | 0.0001638 | 0.00015569 | 825.6908 | 0.52574 | 190.4747 | 634.6904 | 862.0768 | 0 | 0 | 862.0768 | 3.396e-08%
2027 | 465 | CB 465 | Tier-1 | Non-HFTD---11 | 1--3 | 0.51648 | 20 | 100% | 9.9117 | 96.03% | 0% | 3.967% | 0.47116 | 0 | 0 | 0.47116 | 0 | 0.42875 | 0.50899 | 0.84236 | 0.42875 | 0.50899 | 0.84236 | 0.47579 | 0.56483 | 0.84236 | 4.754% | 0.0023928 | 0.0022744 | 4142.2995 | 915.7141 | 14.9285 | 3211.6569 | 4150.8578 | 0 | 0 | 4150.8578 | 1.554e-05%
2027 | VS2 | CB VS2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.0479 | 620 | 100% | 11.3625 | 51.95% | 0% | 48.05% | 0.29219 | 0 | 0 | 0.29219 | 0 | 0.26589 | 6.9457 | 0.038281 | 0.26589 | 6.9457 | 0.038281 | 0.29506 | 7.7078 | 0.038281 | 2.572% | 0.020771 | 0.019743 | 547.0307 | 29.9029 | 126.8526 | 390.2752 | 560.7192 | 0 | 0 | 560.7192 | 9.635e-06%
2027 | 765 | 765-53 | Tier-1 | Non-HFTD---11 | 1--4 | 0.22367 | 0 | 100% | 10.2799 | 97.92% | 0% | 2.076% | 0.49829 | 0 | 0 | 0.49829 | 0 | 0.45344 | 0.22043 | 2.057 | 0.45344 | 0.22043 | 2.057 | 0.50318 | 0.24462 | 2.057 | 4.847% | 0.0009128 | 0.00086762 | 11261.9019 | 1681.3147 | 2761.922 | 6818.6652 | 11274.0796 | 0 | 0 | 11274.0796 | 1.643e-05%
2027 | 256 | 256-46AE | Tier-1 | Non-HFTD---14 | 3--1 | 4.8671 | 108 | 100% | 5.4684 | 29.52% | 0% | 70.48% | 0.079899 | 0 | 0 | 0.079899 | 0 | 0.072707 | 4.7965 | 0.015158 | 0.072707 | 4.7965 | 0.015158 | 0.080684 | 5.3228 | 0.015158 | 1.461% | 0.01432 | 0.013611 | 381.8681 | 0.20253 | 137.1678 | 244.4977 | 395.8848 | 0 | 0 | 395.8848 | 2.635e-06%
2027 | 76 | 76-266F | Tier-1 | Non-HFTD---19 | 1--1 | 0.21686 | 20 | 100% | 0.3287 | 26.14% | 0% | 73.86% | 0.0042534 | 0 | 0 | 0.0042534 | 0 | 0.0038706 | 0.21371 | 0.018111 | 0.0038706 | 0.21371 | 0.018111 | 0.0042953 | 0.23716 | 0.018111 | 1.294% | 0.0008422 | 0.00080051 | 390.2914 | 7.9469 | 80.8159 | 301.5286 | 405.3035 | 0 | 0 | 405.3035 | 1.403e-07%
2027 | 1480 | 1480-26F | Tier-1 | Non-HFTD---18 | 1--1 | 1.1896 | 35 | 100% | 1.5754 | 25.22% | 0% | 74.78% | 0.019667 | 0 | 0 | 0.019667 | 0 | 0.017897 | 1.1724 | 0.015265 | 0.017897 | 1.1724 | 0.015265 | 0.019861 | 1.301 | 0.015265 | 1.248% | 0.0040818 | 0.0038798 | 385.9459 | 1.0392 | 118.4615 | 266.4452 | 400.9759 | 0 | 0 | 400.9759 | 6.486e-07%
2027 | WY1 | CB WY1 | Tier-1 | Non-HFTD---20 | 1--1 | 0.1875 | 0 | 100% | 0.14453 | 1.564% | 0% | 98.44% | 0.00011192 | 0 | 0 | 0.00011192 | 0 | 0.00010185 | 0.18479 | 0.00055117 | 0.00010185 | 0.18479 | 0.00055117 | 0.00011302 | 0.20506 | 0.00055117 | 0.07744% | 0.0005 | 0.00047525 | 289.0698 | 0.75643 | 26.8687 | 261.4447 | 303.8884 | 0 | 0 | 303.8884 | 3.691e-09%
2027 | 797 | CB 797 | Tier-1 | Non-HFTD---5 | 1--5 | 0.92273 | 13 | 100% | 65.0189 | 98.85% | 0% | 1.151% | 3.1814 | 0 | 0 | 3.1814 | 0 | 2.895 | 0.90935 | 3.1836 | 2.895 | 0.90935 | 3.1836 | 3.2127 | 1.0091 | 3.1836 | 4.893% | 0.0039484 | 0.003753 | 16467.148 | 2087.333 | 3503.3467 | 10876.4683 | 16477.0185 | 0 | 0 | 16477.0185 | 0.0001049%
2027 | WA5 | CB WA5 | Tier-1 | Non-HFTD---8 | 4--2 | 14.9795 | 462 | 100% | 31.7966 | 66.36% | 0% | 33.64% | 1.0444 | 0 | 0 | 1.0444 | 0 | 0.95039 | 14.7623 | 0.064379 | 0.95039 | 14.7623 | 0.064379 | 1.0547 | 16.382 | 0.064379 | 3.285% | 0.046317 | 0.044024 | 686.5028 | 95.2087 | 167.8003 | 423.4938 | 698.531 | 0 | 0 | 698.531 | 3.444e-05%
2027 | 322 | 322-822F | Tier-1 | Non-HFTD---18 | 1--1 | 1.136 | 22 | 100% | 0.86968 | 23.9% | 0% | 76.1% | 0.010288 | 0 | 0 | 0.010288 | 0 | 0.0093621 | 1.1195 | 0.0083628 | 0.0093621 | 1.1195 | 0.0083628 | 0.010389 | 1.2423 | 0.0083628 | 1.183% | 0.0028306 | 0.0026905 | 307.242 | 6.8624 | 53.816 | 246.5637 | 319.4186 | 0 | 0 | 319.4186 | 3.393e-07%
2027 | 365 | 365-648R | Tier-1 | Non-HFTD---7 | 3--3 | 3.785 | 254 | 100% | 37.1137 | 20.26% | 73.09% | 6.654% | 0.37221 | 0 | 0 | 0.37221 | 0 | 0.33871 | 3.7301 | 0.090803 | 0.33871 | 3.7301 | 0.090803 | 0.37587 | 4.1394 | 0.090803 | 1.003% | 0.015525 | 0.014757 | 2390.5758 | 8.2255 | 2060.9087 | 321.4416 | 2489.8485 | 0 | 0 | 2489.8485 | 1.227e-05%
2027 | 402 | 402-820F | Tier-1 | Non-HFTD---11 | 2--3 | 2.1513 | 197 | 100% | 12.3895 | 88.33% | 0% | 11.67% | 0.54174 | 0 | 0 | 0.54174 | 0 | 0.49297 | 2.1201 | 0.23252 | 0.49297 | 2.1201 | 0.23252 | 0.54706 | 2.3528 | 0.23252 | 4.373% | 0.0060732 | 0.0057726 | 2040.0308 | 5.8898 | 1788.8383 | 245.3027 | 2052.4249 | 0 | 0 | 2052.4249 | 1.786e-05%
2027 | MV1 | CB MV1 | Tier-1 | Non-HFTD---4 | 3--4 | 5.3483 | 429 | 100% | 150.3384 | 97.79% | 0% | 2.21% | 7.2773 | 0 | 0 | 7.2773 | 0 | 6.6222 | 5.2708 | 1.2564 | 6.6222 | 5.2708 | 1.2564 | 7.3488 | 5.849 | 1.2564 | 4.841% | 0.014765 | 0.014034 | 10182.3567 | 1618.5344 | 97.4794 | 8466.3429 | 10194.0779 | 0 | 0 | 10194.0779 | 0.00024%
2027 | 315 | 315-1192F | Tier-2 | Tier-2---19 | 1--4 | 0.39659 | 8 | 100% | 14.6681 | 98.1% | 0% | 1.899% | 0.71228 | 0 | 0 | 0.71228 | 0 | 0.64817 | 0.39084 | 1.6584 | 0.64817 | 0.39084 | 1.6584 | 0.71928 | 0.43372 | 1.6584 | 4.856% | 0.0015284 | 0.0014527 | 9597.0285 | 5451.7396 | 23.5265 | 4121.7625 | 9606.5199 | 0 | 0 | 9606.5199 | 2.349e-05%
2027 | NO3 | CB NO3 | Tier-1 | Non-HFTD---16 | 2--1 | 3.3623 | 80 | 100% | 3.2681 | 33.34% | 0% | 66.66% | 0.053939 | 0 | 0 | 0.053939 | 0 | 0.049084 | 3.3135 | 0.014813 | 0.049084 | 3.3135 | 0.014813 | 0.054469 | 3.6771 | 0.014813 | 1.65% | 0.008886 | 0.0084461 | 367.7794 | 0.18447 | 144.8976 | 222.6973 | 380.5463 | 0 | 0 | 380.5463 | 1.779e-06%
2027 | 325 | 325-1220R | Tier-1 | Non-HFTD---8 | 4--2 | 21.6898 | 393 | 100% | 37.7086 | 59.54% | 0% | 40.46% | 1.1113 | 0 | 0 | 1.1113 | 0 | 1.0113 | 21.3753 | 0.047312 | 1.0113 | 21.3753 | 0.047312 | 1.1223 | 23.7206 | 0.047312 | 2.947% | 0.060023 | 0.057052 | 628.2334 | 4.0248 | 373.6526 | 250.5559 | 641.471 | 0 | 0 | 641.471 | 3.665e-05%
2027 | 166 | CB 166 | Tier-1 | Non-HFTD---10 | 3--2 | 5.1707 | 175 | 100% | 21.6566 | 82.43% | 0% | 17.57% | 0.88364 | 0 | 0 | 0.88364 | 0 | 0.8041 | 5.0957 | 0.1578 | 0.8041 | 5.0957 | 0.1578 | 0.89233 | 5.6548 | 0.1578 | 4.08% | 0.015112 | 0.014364 | 1433.0361 | 0.84572 | 1200.0855 | 232.1049 | 1446.1491 | 0 | 0 | 1446.1491 | 2.914e-05%
2027 | 94 | 94-41 | Tier-1 | Non-HFTD---2 | 4--4 | 13.5683 | 315 | 100% | 189.6711 | 96.69% | 0% | 3.312% | 9.0777 | 0 | 0 | 9.0777 | 0 | 8.2606 | 13.3716 | 0.61777 | 8.2606 | 13.3716 | 0.61777 | 9.1669 | 14.8387 | 0.61777 | 4.786% | 0.03601 | 0.034228 | 5267.1204 | 1003.7798 | 888.4702 | 3374.8704 | 5276.2062 | 0 | 0 | 5276.2062 | 0.0002994%
2027 | 88 | CB 88 | Tier-1 | Non-HFTD---6 | 4--3 | 10.0387 | 412 | 100% | 58.8668 | 89.39% | 0% | 10.61% | 2.6047 | 0 | 0 | 2.6047 | 0 | 2.3702 | 9.8931 | 0.23958 | 2.3702 | 9.8931 | 0.23958 | 2.6303 | 10.9785 | 0.23958 | 4.425% | 0.033053 | 0.031417 | 1780.9916 | 215.4092 | 736.244 | 829.3384 | 1790.8352 | 0 | 0 | 1790.8352 | 8.589e-05%
2027 | 387 | CB 387 | Tier-1 | Non-HFTD---2 | 4--4 | 6.7638 | 316 | 100% | 522.65 | 70.14% | 28.94% | 0.9137% | 18.1467 | 0 | 0 | 18.1467 | 0 | 16.5133 | 6.6658 | 2.4773 | 16.5133 | 6.6658 | 2.4773 | 18.3251 | 7.3971 | 2.4773 | 3.472% | 0.067633 | 0.064286 | 7727.6908 | 947.907 | 2193.816 | 4585.9679 | 7847.8494 | 0 | 0 | 7847.8494 | 0.0005984%
2027 | 365 | CB 365 | Tier-1 | Non-HFTD---3 | 4--3 | 10.8739 | 264 | 100% | 153.8294 | 16.84% | 79.11% | 4.05% | 1.282 | 0 | 0 | 1.282 | 0 | 1.1666 | 10.7162 | 0.10886 | 1.1666 | 10.7162 | 0.10886 | 1.2946 | 11.892 | 0.10886 | 0.8334% | 0.031529 | 0.029968 | 4879.0131 | 4.4935 | 4354.8547 | 519.6649 | 5090.3229 | 0 | 0 | 5090.3229 | 4.228e-05%
2027 | 161 | 161-989F | Tier-1 | Non-HFTD---17 | 1--2 | 0.19681 | 27 | 100% | 0.82181 | 77.98% | 0% | 22.02% | 0.031721 | 0 | 0 | 0.031721 | 0 | 0.028866 | 0.19396 | 0.14883 | 0.028866 | 0.19396 | 0.14883 | 0.032033 | 0.21524 | 0.14883 | 3.86% | 0.0006838 | 0.00064995 | 1201.8318 | 151.5 | 35.0825 | 1015.2493 | 1215.615 | 0 | 0 | 1215.615 | 1.046e-06%
2027 | 404 | CB 404 | Tier-1 | Non-HFTD---15 | 1--3 | 0.3267 | 6 | 100% | 3.4322 | 87.98% | 0% | 12.02% | 0.14946 | 0 | 0 | 0.14946 | 0 | 0.13601 | 0.32197 | 0.42243 | 0.13601 | 0.32197 | 0.42243 | 0.15093 | 0.35729 | 0.42243 | 4.355% | 0.0014236 | 0.0013531 | 2410.8954 | 1.0401 | 2142.2971 | 267.5582 | 2425.9921 | 0 | 0 | 2425.9921 | 4.929e-06%
2027 | 471 | CB 471 | Tier-1 | Non-HFTD---1 | 4--5 | 9.5888 | 824 | 100% | 3808.7328 | 99.83% | 0% | 0.1692% | 188.2133 | 0 | 0 | 188.2133 | 0 | 171.2715 | 9.4498 | 18.1244 | 171.2715 | 9.4498 | 18.1244 | 190.0631 | 10.4866 | 18.1244 | 4.942% | 0.030567 | 0.029054 | 124601.1385 | 20145.8945 | 297.3105 | 104157.9336 | 124612.117 | 0 | 0 | 124612.117 | 0.006207%
2027 | 900 | CB 900 | Tier-1 | Non-HFTD---19 | 1--3 | 0.042803 | 42 | 100% | 0.53356 | 93.68% | 0% | 6.317% | 0.024743 | 0 | 0 | 0.024743 | 0 | 0.022516 | 0.042182 | 0.53377 | 0.022516 | 0.042182 | 0.53377 | 0.024986 | 0.046811 | 0.53377 | 4.637% | 0.0001684 | 0.00016006 | 3168.3903 | 480.3966 | 18.1813 | 2669.8125 | 3178.8134 | 0 | 0 | 3178.8134 | 8.159e-07%
2027 | 263 | CB 263 | Tier-1 | Non-HFTD---13 | 1--2 | 1.1358 | 53 | 100% | 5.0642 | 81.76% | 0% | 18.24% | 0.20495 | 0 | 0 | 0.20495 | 0 | 0.1865 | 1.1193 | 0.16662 | 0.1865 | 1.1193 | 0.16662 | 0.20696 | 1.2421 | 0.16662 | 4.047% | 0.0045504 | 0.0043252 | 1112.9117 | 144.2639 | 21.0571 | 947.5907 | 1123.4851 | 0 | 0 | 1123.4851 | 6.758e-06%
2027 | 716 | CB 716 | Tier-1 | Non-HFTD---17 | 1--2 | 0.23504 | 15 | 100% | 1.616 | 79.4% | 0% | 20.6% | 0.063516 | 0 | 0 | 0.063516 | 0 | 0.057798 | 0.23163 | 0.24953 | 0.057798 | 0.23163 | 0.24953 | 0.06414 | 0.25704 | 0.24953 | 3.93% | 0.0010432 | 0.00099156 | 1549.1257 | 170.2187 | 205.5076 | 1173.3993 | 1565.7446 | 0 | 0 | 1565.7446 | 2.095e-06%
2027 | LV2 | CB LV2 | Tier-1 | Non-HFTD---10 | 3--2 | 9.3228 | 280 | 100% | 15.9867 | 57.43% | 0% | 42.57% | 0.4545 | 0 | 0 | 0.4545 | 0 | 0.41359 | 9.1876 | 0.045016 | 0.41359 | 9.1876 | 0.045016 | 0.45897 | 10.1956 | 0.045016 | 2.843% | 0.026716 | 0.025394 | 598.3883 | 38.8763 | 209.6571 | 349.8549 | 611.653 | 0 | 0 | 611.653 | 1.499e-05%
2027 | FRD1 | CB FRD1 | Tier-1 | Non-HFTD---20 | 1--1 | 0.72899 | 27 | 100% | 0.37361 | 16.66% | 0% | 83.34% | 0.0030815 | 0 | 0 | 0.0030815 | 0 | 0.0028041 | 0.71842 | 0.0039032 | 0.0028041 | 0.71842 | 0.0039032 | 0.0031118 | 0.79724 | 0.0039032 | 0.8248% | 0.001599 | 0.0015198 | 233.6497 | 0.89583 | 52.0165 | 180.7373 | 243.7901 | 0 | 0 | 243.7901 | 1.016e-07%
2027 | 217 | CB 217 | Tier-3 | Tier-3---20 | 1--5 | 0.034091 | 0 | 100% | 26.6678 | 99.71% | 0% | 0.2895% | 1.3162 | 0 | 0 | 1.3162 | 0 | 1.1978 | 0.033597 | 35.6511 | 1.1978 | 0.033597 | 35.6511 | 1.3292 | 0.037283 | 35.6511 | 4.936% | 0.000134 | 0.00012737 | 199013.7941 | 31841.1986 | 716.7689 | 166455.8266 | 199043.8026 | 0 | 0 | 199043.8026 | 4.34e-05%
2027 | PL4 | CB PL4 | Tier-1 | Non-HFTD---12 | 3--1 | 10.2286 | 356 | 100% | 13.8266 | 47.94% | 0% | 52.06% | 0.3281 | 0 | 0 | 0.3281 | 0 | 0.29857 | 10.0803 | 0.029619 | 0.29857 | 10.0803 | 0.029619 | 0.33133 | 11.1863 | 0.029619 | 2.373% | 0.027903 | 0.026522 | 495.5242 | 0.19412 | 260.9853 | 234.3448 | 508.9589 | 0 | 0 | 508.9589 | 1.082e-05%
2027 | 222 | 222-1503R | Tier-3 | Tier-3---15 | 5--4 | 2.6021 | 595 | 100% | 1359.3953 | 95.15% | 4.696% | 0.1502% | 64.0292 | 0 | 0 | 64.0292 | 0 | 58.2657 | 2.5644 | 22.721 | 58.2657 | 2.5644 | 22.721 | 64.6584 | 2.8458 | 22.721 | 4.71% | 0.23465 | 0.22303 | 5793.3484 | 808.274 | 260.6182 | 4724.4562 | 5807.9691 | 0 | 0 | 5807.9691 | 0.002111%
2027 | 454 | 454-45AE | Tier-1 | Non-HFTD---2 | 4--4 | 4.39 | 160 | 100% | 491.7858 | 41.61% | 57.78% | 0.6067% | 10.13 | 0 | 0 | 10.13 | 0 | 9.2181 | 4.3264 | 2.1307 | 9.2181 | 4.3264 | 2.1307 | 10.2295 | 4.801 | 2.1307 | 2.06% | 0.084004 | 0.079846 | 5854.3004 | 713.107 | 3089.276 | 2051.9175 | 6032.3112 | 0 | 0 | 6032.3112 | 0.000334%
2027 | 329 | 329-215F | Tier-1 | Non-HFTD---6 | 3--3 | 1.3032 | 53 | 100% | 64.9248 | 1.785% | 96.02% | 2.2% | 0.05735 | 0 | 0 | 0.05735 | 0 | 0.052188 | 1.2843 | 0.040635 | 0.052188 | 1.2843 | 0.040635 | 0.057914 | 1.4252 | 0.040635 | 0.08833% | 0.021703 | 0.020628 | 2991.5676 | 12.9271 | 2341.0516 | 637.589 | 3144.5818 | 0 | 0 | 3144.5818 | 1.891e-06%
2027 | 155 | 155-40 | Tier-1 | Non-HFTD---16 | 2--1 | 4.411 | 109 | 100% | 3.7492 | 25.26% | 0% | 74.74% | 0.046886 | 0 | 0 | 0.046886 | 0 | 0.042666 | 4.347 | 0.0098149 | 0.042666 | 4.347 | 0.0098149 | 0.047347 | 4.8239 | 0.0098149 | 1.251% | 0.012188 | 0.011585 | 307.6104 | 0.55017 | 96.2898 | 210.7705 | 319.5829 | 0 | 0 | 319.5829 | 1.546e-06%
2027 | 326 | 326-35R | Tier-1 | Non-HFTD---2 | 4--4 | 13.9548 | 334 | 100% | 586.1826 | 18.71% | 79.88% | 1.411% | 5.4284 | 0 | 0 | 5.4284 | 0 | 4.9398 | 13.7524 | 0.35919 | 4.9398 | 13.7524 | 0.35919 | 5.4818 | 15.2613 | 0.35919 | 0.9261% | 0.07497 | 0.071259 | 7818.9373 | 361.909 | 5822.8865 | 1634.1418 | 8149.9516 | 0 | 0 | 8149.9516 | 0.000179%
2027 | 1233 | 1233-589R | Tier-3 | Tier-3---16 | 5--4 | 3.2034 | 92 | 100% | 1386.4905 | 98.92% | 0.9396% | 0.1432% | 67.8881 | 0 | 0 | 67.8881 | 0 | 61.7773 | 3.1569 | 19.5689 | 61.7773 | 3.1569 | 19.5689 | 68.5553 | 3.5033 | 19.5689 | 4.896% | 0.11751 | 0.11169 | 11798.9753 | 1859.8108 | 96.407 | 9842.7575 | 11805.6289 | 0 | 0 | 11805.6289 | 0.002239%
2027 | 701 | 701-48AE | Tier-1 | Non-HFTD---4 | 3--4 | 3.0439 | 162 | 100% | 111.3526 | 1.512% | 96.4% | 2.091% | 0.083358 | 0 | 0 | 0.083358 | 0 | 0.075855 | 2.9998 | 0.025287 | 0.075855 | 2.9998 | 0.025287 | 0.084177 | 3.3289 | 0.025287 | 0.07486% | 0.014184 | 0.013482 | 7850.7987 | 18.6835 | 7007.5279 | 824.5872 | 8253.4683 | 0 | 0 | 8253.4683 | 2.749e-06%
2027 | 170 | 170-46 | Tier-1 | Non-HFTD---6 | 5--2 | 14.4293 | 566 | 100% | 63.3107 | 39.69% | 47.72% | 12.59% | 1.2437 | 0 | 0 | 1.2437 | 0 | 1.1318 | 14.2201 | 0.07959 | 1.1318 | 14.2201 | 0.07959 | 1.2559 | 15.7803 | 0.07959 | 1.964% | 0.099838 | 0.094896 | 634.1343 | 13.2723 | 434.6906 | 186.1714 | 654.0524 | 0 | 0 | 654.0524 | 4.101e-05%
2027 | 61 | CB 61 | Tier-1 | Non-HFTD---3 | 4--4 | 8.4142 | 700 | 100% | 184.2595 | 17.6% | 78.77% | 3.63% | 1.6051 | 0 | 0 | 1.6051 | 0 | 1.4606 | 8.2922 | 0.17615 | 1.4606 | 8.2922 | 0.17615 | 1.6209 | 9.202 | 0.17615 | 0.8711% | 0.035306 | 0.033559 | 5218.8994 | 61.45 | 4296.865 | 860.5843 | 5442.858 | 0 | 0 | 5442.858 | 5.293e-05%
2027 | 708 | CB 708 | Tier-1 | Non-HFTD---11 | 2--2 | 0.79432 | 18 | 100% | 12.3602 | 94.92% | 0.8388% | 4.245% | 0.58072 | 0 | 0 | 0.58072 | 0 | 0.52845 | 0.7828 | 0.67508 | 0.52845 | 0.7828 | 0.67508 | 0.58643 | 0.86869 | 0.67508 | 4.698% | 0.0077752 | 0.0073903 | 1589.6964 | 132.6057 | 705.9862 | 751.1045 | 1593.9055 | 0 | 0 | 1593.9055 | 1.915e-05%
2027 | SW2 | CB SW2 | Tier-1 | Non-HFTD---14 | 3--1 | 6.287 | 115 | 100% | 6.1621 | 30.27% | 0% | 69.73% | 0.092335 | 0 | 0 | 0.092335 | 0 | 0.084023 | 6.1958 | 0.013561 | 0.084023 | 6.1958 | 0.013561 | 0.093242 | 6.8756 | 0.013561 | 1.498% | 0.016864 | 0.016029 | 365.4058 | 0.34604 | 132.8123 | 232.2474 | 378.6748 | 0 | 0 | 378.6748 | 3.045e-06%
2027 | EO2 | CB EO2 | Tier-1 | Non-HFTD---14 | 3--1 | 8.4316 | 236 | 100% | 6.9651 | 27.51% | 0% | 72.49% | 0.094861 | 0 | 0 | 0.094861 | 0 | 0.086322 | 8.3093 | 0.010389 | 0.086322 | 8.3093 | 0.010389 | 0.095793 | 9.221 | 0.010389 | 1.362% | 0.021169 | 0.020122 | 329.0193 | 1.1923 | 105.9838 | 221.8432 | 341.4396 | 0 | 0 | 341.4396 | 3.128e-06%
2027 | 95 | 95-34 | Tier-1 | Non-HFTD---9 | 2--3 | 1.5831 | 108 | 100% | 20.4353 | 56.35% | 39.11% | 4.547% | 0.56998 | 0 | 0 | 0.56998 | 0 | 0.51867 | 1.5602 | 0.33245 | 0.51867 | 1.5602 | 0.33245 | 0.57558 | 1.7313 | 0.33245 | 2.789% | 0.0092856 | 0.008826 | 2200.7529 | 196.7754 | 835.923 | 1168.0545 | 2250.7837 | 0 | 0 | 2250.7837 | 1.88e-05%
2027 | 341 | 341-1179 | Tier-1 | Non-HFTD---9 | 1--4 | 1.0375 | 44 | 100% | 16.5229 | 96.72% | 0% | 3.284% | 0.79103 | 0 | 0 | 0.79103 | 0 | 0.71982 | 1.0225 | 0.70401 | 0.71982 | 1.0225 | 0.70401 | 0.7988 | 1.1346 | 0.70401 | 4.787% | 0.002784 | 0.0026462 | 5934.9652 | 1118.6399 | 28.4603 | 4787.865 | 5945.1152 | 0 | 0 | 5945.1152 | 2.609e-05%
2027 | EO3 | CB EO3 | Tier-1 | Non-HFTD---3 | 4--3 | 14.1508 | 390 | 100% | 120.8831 | 92.52% | 0% | 7.481% | 5.5361 | 0 | 0 | 5.5361 | 0 | 5.0378 | 13.9456 | 0.36124 | 5.0378 | 13.9456 | 0.36124 | 5.5905 | 15.4757 | 0.36124 | 4.58% | 0.038956 | 0.037028 | 3103.0517 | 661.6926 | 179.4344 | 2261.9247 | 3115.1408 | 0 | 0 | 3115.1408 | 0.0001826%
2027 | 234 | CB 234 | Tier-2 | Tier-2---4 | 4--5 | 11.0316 | 1008 | 100% | 3294.853 | 98.88% | 0.9043% | 0.2189% | 161.2634 | 0 | 0 | 161.2634 | 0 | 146.7475 | 10.8717 | 13.4981 | 146.7475 | 10.8717 | 13.4981 | 162.8483 | 12.0645 | 13.4981 | 4.894% | 0.044658 | 0.042447 | 73779.6805 | 13525.886 | 881.4848 | 59372.3097 | 73822.8352 | 0 | 0 | 73822.8352 | 0.005318%
2027 | 759 | 759-13AE | Tier-1 | Non-HFTD---10 | 4--2 | 14.8888 | 631 | 100% | 22.2365 | 59.69% | 0% | 40.31% | 0.65701 | 0 | 0 | 0.65701 | 0 | 0.59787 | 14.6729 | 0.040747 | 0.59787 | 14.6729 | 0.040747 | 0.66347 | 16.2828 | 0.040747 | 2.955% | 0.039311 | 0.037365 | 565.6533 | 37.0216 | 132.6301 | 396.0016 | 577.5278 | 0 | 0 | 577.5278 | 2.167e-05%
2027 | 266 | CB 266 | Tier-1 | Non-HFTD---7 | 2--4 | 1.4792 | 31 | 100% | 30.6273 | 96.93% | 0% | 3.069% | 1.4695 | 0 | 0 | 1.4695 | 0 | 1.3372 | 1.4577 | 0.91736 | 1.3372 | 1.4577 | 0.91736 | 1.484 | 1.6177 | 0.91736 | 4.798% | 0.005299 | 0.0050367 | 5779.8249 | 166.0393 | 4572.2436 | 1041.5419 | 5789.0623 | 0 | 0 | 5789.0623 | 4.846e-05%
2027 | 1481 | 1481-5AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.032977 | 0 | 100% | 0.036092 | 1.509% | 0% | 98.49% | 2.6963e-05 | 0 | 0 | 2.6963e-05 | 0 | 2.4536e-05 | 0.032499 | 0.00075497 | 2.4536e-05 | 0.032499 | 0.00075497 | 2.7228e-05 | 0.036065 | 0.00075497 | 0.07471% | 0.0001132 | 0.0001076 | 318.8351 | 0.53572 | 31.4788 | 286.8206 | 335.1888 | 0 | 0 | 335.1888 | 8.891e-10%
2027 | 239 | 239-2215R | Tier-3 | Tier-3---10 | 5--5 | 12.0589 | 952 | 100% | 6268.6569 | 98.24% | 1.63% | 0.1302% | 304.8369 | 0 | 0 | 304.8369 | 0 | 277.3974 | 11.884 | 23.342 | 277.3974 | 11.884 | 23.342 | 307.8328 | 13.1879 | 23.342 | 4.863% | 0.15408 | 0.14645 | 40685.5389 | 6831.4863 | 640.4954 | 33213.5572 | 40722.8328 | 0 | 0 | 40722.8328 | 0.01005%
2027 | 321 | CB 321 | Tier-1 | Non-HFTD---9 | 3--2 | 5.2511 | 131 | 100% | 22.0824 | 85.16% | 0% | 14.84% | 0.9309 | 0 | 0 | 0.9309 | 0 | 0.8471 | 5.175 | 0.16369 | 0.8471 | 5.175 | 0.16369 | 0.94005 | 5.7427 | 0.16369 | 4.216% | 0.014142 | 0.013442 | 1561.434 | 63.0678 | 966.4548 | 531.9115 | 1573.4991 | 0 | 0 | 1573.4991 | 3.07e-05%
2027 | 286 | 286-989AE | Tier-1 | Non-HFTD---3 | 4--3 | 10.8825 | 1225 | 100% | 139.8716 | 4.025% | 90.57% | 5.409% | 0.2787 | 0 | 0 | 0.2787 | 0 | 0.25361 | 10.7247 | 0.023647 | 0.25361 | 10.7247 | 0.023647 | 0.28144 | 11.9014 | 0.023647 | 0.1993% | 0.03669 | 0.034874 | 3812.2742 | 15.0936 | 3277.8049 | 519.3757 | 4002.8176 | 0 | 0 | 4002.8176 | 9.19e-06%
2027 | 303 | CB 303 | Tier-1 | Non-HFTD---2 | 4--4 | 12.3992 | 651 | 100% | 349.915 | 18.7% | 78.58% | 2.715% | 3.2397 | 0 | 0 | 3.2397 | 0 | 2.9481 | 12.2194 | 0.24126 | 2.9481 | 12.2194 | 0.24126 | 3.2716 | 13.5601 | 0.24126 | 0.9259% | 0.047695 | 0.045334 | 7336.5129 | 14.6418 | 6603.3249 | 718.5462 | 7647.1195 | 0 | 0 | 7647.1195 | 0.0001068%
2027 | 409 | 409-38R | Tier-1 | Non-HFTD---14 | 2--2 | 3.0827 | 145 | 100% | 5.3106 | 56.43% | 0% | 43.57% | 0.14833 | 0 | 0 | 0.14833 | 0 | 0.13498 | 3.038 | 0.044429 | 0.13498 | 3.038 | 0.044429 | 0.14979 | 3.3713 | 0.044429 | 2.793% | 0.008986 | 0.0085412 | 590.983 | 1.708 | 347.574 | 241.701 | 604.394 | 0 | 0 | 604.394 | 4.891e-06%
2027 | 43 | 43-443 | Tier-1 | Non-HFTD---19 | 1--1 | 0.15364 | 0 | 100% | 0.25601 | 33.72% | 0% | 66.28% | 0.0042726 | 0 | 0 | 0.0042726 | 0 | 0.003888 | 0.15142 | 0.025677 | 0.003888 | 0.15142 | 0.025677 | 0.0043145 | 0.16803 | 0.025677 | 1.669% | 0.0005224 | 0.00049654 | 490.0579 | 1.5926 | 186.4105 | 302.0548 | 506.9745 | 0 | 0 | 506.9745 | 1.409e-07%
2027 | 221 | 221-6R | Tier-2 | Tier-2---5 | 5--5 | 6.0572 | 6 | 100% | 3904.259 | 99.88% | 0.03221% | 0.0896% | 193.0254 | 0 | 0 | 193.0254 | 0 | 175.6505 | 5.9694 | 29.4253 | 175.6505 | 5.9694 | 29.4253 | 194.9225 | 6.6243 | 29.4253 | 4.944% | 0.21604 | 0.20535 | 18071.9767 | 2732.2517 | 50.2734 | 15289.4517 | 18073.1232 | 0 | 0 | 18073.1232 | 0.006365%
2027 | 287 | 287-20 | Tier-1 | Non-HFTD---7 | 2--4 | 0.66515 | 101 | 100% | 45.5594 | 6.137% | 92.85% | 1.013% | 0.13841 | 0 | 0 | 0.13841 | 0 | 0.12595 | 0.65551 | 0.19215 | 0.12595 | 0.65551 | 0.19215 | 0.13977 | 0.72743 | 0.19215 | 0.3038% | 0.0081382 | 0.0077354 | 5598.2146 | 73.7618 | 4770.4937 | 753.9592 | 5871.8642 | 0 | 0 | 5871.8642 | 4.564e-06%
2027 | 73 | 73-1164 | Tier-3 | Tier-3---13 | 5--4 | 1.3216 | 209 | 100% | 2448.8293 | 98.64% | 1.317% | 0.04316% | 119.5679 | 0 | 0 | 119.5679 | 0 | 108.8052 | 1.3025 | 83.5379 | 108.8052 | 1.3025 | 83.5379 | 120.743 | 1.4454 | 83.5379 | 4.883% | 0.18614 | 0.17693 | 13155.649 | 2050.8097 | 155.9445 | 10948.8948 | 13164.97 | 0 | 0 | 13164.97 | 0.003943%
2027 | 295 | 295-1201F | Tier-1 | Non-HFTD---19 | 1--2 | 0.16193 | 31 | 100% | 0.61619 | 77.51% | 0% | 22.49% | 0.023641 | 0 | 0 | 0.023641 | 0 | 0.021513 | 0.15958 | 0.13481 | 0.021513 | 0.15958 | 0.13481 | 0.023874 | 0.17709 | 0.13481 | 3.837% | 0.0006544 | 0.00062201 | 941.6139 | 118.3874 | 26.4172 | 796.8092 | 952.6431 | 0 | 0 | 952.6431 | 7.796e-07%
2027 | 249 | CB 249 | Tier-3 | Tier-3---16 | 4--4 | 3.6983 | 174 | 100% | 826.9208 | 97.04% | 2.672% | 0.2884% | 39.7207 | 0 | 0 | 39.7207 | 0 | 36.1453 | 3.6447 | 9.9173 | 36.1453 | 3.6447 | 9.9173 | 40.1111 | 4.0446 | 9.9173 | 4.803% | 0.05906 | 0.056137 | 14001.3211 | 2124.344 | 445.6547 | 11431.3225 | 14022.9085 | 0 | 0 | 14022.9085 | 0.00131%
2027 | 122 | 122-196 | Tier-1 | Non-HFTD---17 | 1--3 | 0.094697 | 0 | 100% | 0.86843 | 83.21% | 0% | 16.79% | 0.035772 | 0 | 0 | 0.035772 | 0 | 0.032552 | 0.093324 | 0.3488 | 0.032552 | 0.093324 | 0.3488 | 0.036123 | 0.10356 | 0.3488 | 4.119% | 0.0004458 | 0.00042373 | 1948.0311 | 75.668 | 1186.0682 | 686.2949 | 1965.0602 | 0 | 0 | 1965.0602 | 1.18e-06%
2027 | AD3 | CB AD3 | Tier-1 | Non-HFTD---6 | 3--3 | 5.5978 | 142 | 100% | 83.3741 | 10.35% | 84.58% | 5.071% | 0.4273 | 0 | 0 | 0.4273 | 0 | 0.38884 | 5.5166 | 0.070485 | 0.38884 | 5.5166 | 0.070485 | 0.4315 | 6.1219 | 0.070485 | 0.5125% | 0.020729 | 0.019703 | 4022.177 | 22.235 | 3421.9761 | 577.9659 | 4209.9556 | 0 | 0 | 4209.9556 | 1.409e-05%
2027 | 580 | CB 580 | Tier-1 | Non-HFTD---10 | 3--2 | 6.6564 | 112 | 100% | 16.6854 | 65.67% | 0% | 34.33% | 0.54239 | 0 | 0 | 0.54239 | 0 | 0.49356 | 6.5599 | 0.075239 | 0.49356 | 6.5599 | 0.075239 | 0.54772 | 7.2797 | 0.075239 | 3.251% | 0.021036 | 0.019994 | 793.1967 | 20.8991 | 418.7736 | 353.524 | 807.3777 | 0 | 0 | 807.3777 | 1.789e-05%
2027 | 283 | 283-71F | Tier-3 | Tier-3---13 | 5--4 | 5.1553 | 296 | 100% | 2013.5901 | 87.8% | 12.03% | 0.1689% | 87.5136 | 0 | 0 | 87.5136 | 0 | 79.6362 | 5.0806 | 15.6746 | 79.6362 | 5.0806 | 15.6746 | 88.3736 | 5.638 | 15.6746 | 4.346% | 0.19011 | 0.1807 | 10591.4545 | 1521.6606 | 1147.6649 | 7922.129 | 10658.7421 | 0 | 0 | 10658.7421 | 0.002886%
2027 | 381 | CB 381 | Tier-1 | Non-HFTD---5 | 1--4 | 0.78239 | 13 | 100% | 47.7165 | 98.4% | 0% | 1.604% | 2.3241 | 0 | 0 | 2.3241 | 0 | 2.1149 | 0.77104 | 2.7429 | 2.1149 | 0.77104 | 2.7429 | 2.3469 | 0.85564 | 2.7429 | 4.871% | 0.0039148 | 0.003721 | 12188.7447 | 1325.9661 | 5588.321 | 5274.4577 | 12198.9235 | 0 | 0 | 12198.9235 | 7.664e-05%
2027 | 781 | 781-1359 | Tier-1 | Non-HFTD---6 | 3--3 | 1.9735 | 131 | 100% | 56.4656 | 0.6389% | 97.32% | 2.039% | 0.017858 | 0 | 0 | 0.017858 | 0 | 0.016251 | 1.9448 | 0.0083558 | 0.016251 | 1.9448 | 0.0083558 | 0.018034 | 2.1582 | 0.0083558 | 0.03163% | 0.015735 | 0.014956 | 3588.4458 | 5.6419 | 3219.1315 | 363.6723 | 3774.1303 | 0 | 0 | 3774.1303 | 5.889e-07%
2027 | 198 | CB 198 | Tier-1 | Non-HFTD---7 | 2--3 | 2.6296 | 53 | 100% | 42.3989 | 95.29% | 0% | 4.712% | 1.9999 | 0 | 0 | 1.9999 | 0 | 1.8198 | 2.5914 | 0.70225 | 1.8198 | 2.5914 | 0.70225 | 2.0195 | 2.8758 | 0.70225 | 4.717% | 0.0090942 | 0.008644 | 4662.1866 | 881.6219 | 964.9735 | 2815.5912 | 4673.6267 | 0 | 0 | 4673.6267 | 6.595e-05%
2027 | 486 | 486-91 | Tier-1 | Non-HFTD---11 | 2--3 | 1.6947 | 55 | 100% | 14.7921 | 90.67% | 0% | 9.328% | 0.66391 | 0 | 0 | 0.66391 | 0 | 0.60414 | 1.6701 | 0.36174 | 0.60414 | 1.6701 | 0.36174 | 0.67043 | 1.8534 | 0.36174 | 4.488% | 0.0056232 | 0.0053449 | 2630.5487 | 105.0428 | 1762.2852 | 763.2207 | 2643.3281 | 0 | 0 | 2643.3281 | 2.189e-05%
2027 | 159 | 159-31R | Tier-1 | Non-HFTD---10 | 4--1 | 15.0642 | 475 | 100% | 17.9248 | 42.9% | 0% | 57.1% | 0.38062 | 0 | 0 | 0.38062 | 0 | 0.34636 | 14.8458 | 0.023331 | 0.34636 | 14.8458 | 0.023331 | 0.38437 | 16.4747 | 0.023331 | 2.123% | 0.041101 | 0.039067 | 436.1117 | 0.91666 | 205.6006 | 229.5944 | 449.0806 | 0 | 0 | 449.0806 | 1.255e-05%
2027 | 403 | 403-11F | Tier-1 | Non-HFTD---19 | 1--1 | 0.092612 | 1 | 100% | 0.13674 | 49.73% | 0% | 50.27% | 0.003366 | 0 | 0 | 0.003366 | 0 | 0.003063 | 0.091269 | 0.033561 | 0.003063 | 0.091269 | 0.033561 | 0.0033991 | 0.10128 | 0.033561 | 2.462% | 0.0002772 | 0.00026348 | 493.2752 | 2.7743 | 252.0099 | 238.491 | 506.1886 | 0 | 0 | 506.1886 | 1.11e-07%
2027 | 142 | 142-33 | Tier-1 | Non-HFTD---3 | 4--3 | 9.6922 | 296 | 100% | 118.7124 | 20.51% | 73.88% | 5.606% | 1.2055 | 0 | 0 | 1.2055 | 0 | 1.0969 | 9.5517 | 0.11484 | 1.0969 | 9.5517 | 0.11484 | 1.2173 | 10.5997 | 0.11484 | 1.015% | 0.037439 | 0.035585 | 3170.8556 | 82.1006 | 2482.6954 | 606.0595 | 3302.112 | 0 | 0 | 3302.112 | 3.975e-05%
2027 | 1049 | 1049-4F | Tier-1 | Non-HFTD---15 | 2--2 | 1.9534 | 56 | 100% | 3.7141 | 55.35% | 0% | 44.65% | 0.10175 | 0 | 0 | 0.10175 | 0 | 0.092592 | 1.925 | 0.048099 | 0.092592 | 1.925 | 0.048099 | 0.10275 | 2.1363 | 0.048099 | 2.74% | 0.0062142 | 0.0059066 | 597.6775 | 50.3489 | 47.6467 | 499.6819 | 611.5765 | 0 | 0 | 611.5765 | 3.355e-06%
2027 | 313 | 313-923F | Tier-1 | Non-HFTD---8 | 3--2 | 2.539 | 201 | 100% | 37.7797 | 19.84% | 75.48% | 4.681% | 0.37105 | 0 | 0 | 0.37105 | 0 | 0.33765 | 2.5022 | 0.13494 | 0.33765 | 2.5022 | 0.13494 | 0.3747 | 2.7767 | 0.13494 | 0.9821% | 0.024714 | 0.023491 | 1528.6511 | 49.341 | 1018.188 | 461.1221 | 1592.4645 | 0 | 0 | 1592.4645 | 1.224e-05%
2027 | 353 | CB 353 | Tier-2 | Tier-2---19 | 1--5 | 0.043939 | 2 | 100% | 7.5897 | 98.6% | 0% | 1.398% | 0.37044 | 0 | 0 | 0.37044 | 0 | 0.33709 | 0.043302 | 7.7846 | 0.33709 | 0.043302 | 7.7846 | 0.37408 | 0.048053 | 7.7846 | 4.881% | 0.0001926 | 0.00018307 | 39406.3406 | 6139.512 | 737.3483 | 32529.4803 | 39435.0274 | 0 | 0 | 39435.0274 | 1.222e-05%
2027 | 413 | CB 413 | Tier-1 | Non-HFTD---14 | 2--2 | 2.979 | 41 | 100% | 5.219 | 51.24% | 0% | 48.76% | 0.13238 | 0 | 0 | 0.13238 | 0 | 0.12046 | 2.9358 | 0.041032 | 0.12046 | 2.9358 | 0.041032 | 0.13368 | 3.2579 | 0.041032 | 2.537% | 0.0095502 | 0.0090775 | 546.4762 | 31.366 | 184.439 | 330.6712 | 560.3522 | 0 | 0 | 560.3522 | 4.365e-06%
2027 | 731 | 731-1247F | Tier-1 | Non-HFTD---8 | 3--2 | 8.847 | 410 | 100% | 26.8816 | 80.57% | 0% | 19.43% | 1.0721 | 0 | 0 | 1.0721 | 0 | 0.97557 | 8.7187 | 0.11189 | 0.97557 | 8.7187 | 0.11189 | 1.0826 | 9.6753 | 0.11189 | 3.988% | 0.023379 | 0.022222 | 1149.7989 | 119.8828 | 215.3653 | 814.5508 | 1161.4348 | 0 | 0 | 1161.4348 | 3.535e-05%
2027 | 581 | CB 581 | Tier-1 | Non-HFTD---14 | 2--2 | 4.2623 | 254 | 100% | 6.6929 | 56.27% | 0% | 43.73% | 0.18643 | 0 | 0 | 0.18643 | 0 | 0.16965 | 4.2005 | 0.040388 | 0.16965 | 4.2005 | 0.040388 | 0.18826 | 4.6614 | 0.040388 | 2.786% | 0.012283 | 0.011675 | 544.875 | 36.9163 | 103.2062 | 404.7526 | 557.283 | 0 | 0 | 557.283 | 6.148e-06%
2027 | 560 | 560-46F | Tier-1 | Non-HFTD---9 | 1--4 | 0.47552 | 5 | 100% | 21.1791 | 98.55% | 0% | 1.446% | 1.0332 | 0 | 0 | 1.0332 | 0 | 0.9402 | 0.46863 | 2.0063 | 0.9402 | 0.46863 | 2.0063 | 1.0434 | 0.52004 | 2.0063 | 4.878% | 0.0016054 | 0.0015259 | 13192.414 | 3248.8863 | 1203.2389 | 8740.2887 | 13202.348 | 0 | 0 | 13202.348 | 3.407e-05%
2027 | 206 | 206-974 | Tier-1 | Non-HFTD---1 | 4--5 | 8.7475 | 717 | 100% | 1943.6719 | 99.69% | 0% | 0.3117% | 95.9119 | 0 | 0 | 95.9119 | 0 | 87.2785 | 8.6207 | 10.1243 | 87.2785 | 8.6207 | 10.1243 | 96.8545 | 9.5665 | 10.1243 | 4.935% | 0.028958 | 0.027525 | 67119.4507 | 10907.8418 | 251.1395 | 55960.4695 | 67130.3452 | 0 | 0 | 67130.3452 | 0.003163%
2027 | 430 | 430-42F | Tier-1 | Non-HFTD---16 | 2--1 | 4.3551 | 171 | 100% | 4.6808 | 37.11% | 0% | 62.89% | 0.085984 | 0 | 0 | 0.085984 | 0 | 0.078245 | 4.292 | 0.01823 | 0.078245 | 4.292 | 0.01823 | 0.086829 | 4.7629 | 0.01823 | 1.837% | 0.013 | 0.012357 | 360.0482 | 4.7005 | 126.5075 | 228.8402 | 371.8404 | 0 | 0 | 371.8404 | 2.835e-06%
2027 | CG2 | CB CG2 | Tier-1 | Non-HFTD---2 | 4--4 | 8.5261 | 945 | 100% | 237.5736 | 92.58% | 4.849% | 2.57% | 10.8874 | 0 | 0 | 10.8874 | 0 | 9.9074 | 8.4025 | 1.1791 | 9.9074 | 8.4025 | 1.1791 | 10.9944 | 9.3244 | 1.1791 | 4.583% | 0.033669 | 0.032002 | 7056.2378 | 1251.7365 | 402.879 | 5401.6224 | 7083.5019 | 0 | 0 | 7083.5019 | 0.000359%
2027 | RA3 | CB RA3 | Tier-2 | Tier-2---10 | 5--4 | 5.0727 | 240 | 100% | 916.1972 | 69.5% | 30.07% | 0.4286% | 31.5185 | 0 | 0 | 31.5185 | 0 | 28.6814 | 4.9991 | 5.7373 | 28.6814 | 4.9991 | 5.7373 | 31.8282 | 5.5476 | 5.7373 | 3.44% | 0.12911 | 0.12272 | 7096.3625 | 800.779 | 1887.9363 | 4407.6471 | 7209.0875 | 0 | 0 | 7209.0875 | 0.001039%
2027 | 67 | CB 67 | Tier-3 | Tier-3---20 | 1--5 | 0.043939 | 0 | 100% | 10.8761 | 99.3% | 0% | 0.7025% | 0.53458 | 0 | 0 | 0.53458 | 0 | 0.48646 | 0.043302 | 11.2341 | 0.48646 | 0.043302 | 11.2341 | 0.53984 | 0.048053 | 11.2341 | 4.915% | 0.0002312 | 0.00021976 | 47041.8645 | 6931.4997 | 675.7608 | 39434.604 | 47059.0744 | 0 | 0 | 47059.0744 | 1.763e-05%
2027 | VS4 | CB VS4 | Tier-1 | Non-HFTD---12 | 3--1 | 6.475 | 300 | 100% | 8.974 | 52.07% | 0% | 47.93% | 0.23131 | 0 | 0 | 0.23131 | 0 | 0.21049 | 6.3812 | 0.032985 | 0.21049 | 6.3812 | 0.032985 | 0.23358 | 7.0813 | 0.032985 | 2.578% | 0.018085 | 0.017189 | 496.2256 | 31.5583 | 87.8288 | 376.8384 | 508.6116 | 0 | 0 | 508.6116 | 7.628e-06%
2027 | 403 | CB 403 | Tier-1 | Non-HFTD---11 | 1--3 | 1.3608 | 12 | 100% | 10.6218 | 92.93% | 0% | 7.069% | 0.48861 | 0 | 0 | 0.48861 | 0 | 0.44463 | 1.341 | 0.33156 | 0.44463 | 1.341 | 0.33156 | 0.49341 | 1.4882 | 0.33156 | 4.6% | 0.0034798 | 0.0033075 | 3052.4178 | 0.16237 | 2856.2333 | 196.0221 | 3063.6555 | 0 | 0 | 3063.6555 | 1.611e-05%
2027 | 168 | 168-702F | Tier-1 | Non-HFTD---5 | 3--3 | 4.9932 | 515 | 100% | 86.0496 | 96.13% | 0% | 3.875% | 4.0944 | 0 | 0 | 4.0944 | 0 | 3.7259 | 4.9208 | 0.75716 | 3.7259 | 4.9208 | 0.75716 | 4.1346 | 5.4607 | 0.75716 | 4.758% | 0.018904 | 0.017968 | 4551.8785 | 998.3577 | 182.1089 | 3371.4119 | 4561.0641 | 0 | 0 | 4561.0641 | 0.000135%
2027 | 520 | 520-1936 | Tier-3 | Tier-3---20 | 1--5 | 0.1358 | 0 | 100% | 63.7111 | 99.77% | 0% | 0.2279% | 3.1465 | 0 | 0 | 3.1465 | 0 | 2.8633 | 0.13383 | 21.3955 | 2.8633 | 0.13383 | 21.3955 | 3.1774 | 0.14851 | 21.3955 | 4.939% | 0.0006668 | 0.00063379 | 95547.5888 | 14906.0915 | 19.7801 | 80621.7172 | 95558.9285 | 0 | 0 | 95558.9285 | 0.0001038%
2027 | 1022 | 1022-17F | Tier-3 | Tier-3---4 | 5--5 | 4.5633 | 493 | 100% | 9800.6792 | 99.62% | 0.3456% | 0.03348% | 483.2946 | 0 | 0 | 483.2946 | 0 | 439.7915 | 4.4971 | 97.7945 | 439.7915 | 4.4971 | 97.7945 | 488.0444 | 4.9905 | 97.7945 | 4.931% | 0.10945 | 0.10403 | 89544.6442 | 15809.5952 | 285.6325 | 73449.4165 | 89562.3218 | 0 | 0 | 89562.3218 | 0.01594%
2027 | 58 | 58-753F | Tier-1 | Non-HFTD---9 | 2--2 | 0.24597 | 0 | 100% | 17.6789 | 0.1407% | 99.04% | 0.8181% | 0.001231 | 0 | 0 | 0.001231 | 0 | 0.0011202 | 0.24241 | 0.004621 | 0.0011202 | 0.24241 | 0.004621 | 0.0012431 | 0.269 | 0.004621 | 0.006963% | 0.011461 | 0.010893 | 1542.5838 | 1.9521 | 1400.9815 | 139.6502 | 1622.8053 | 0 | 0 | 1622.8053 | 4.059e-08%
2027 | 68 | 68-27 | Tier-1 | Non-HFTD---5 | 3--3 | 1.0051 | 139 | 100% | 64.4638 | 96.08% | 2.916% | 1.004% | 3.0659 | 0 | 0 | 3.0659 | 0 | 2.7899 | 0.99054 | 2.8165 | 2.7899 | 0.99054 | 2.8165 | 3.096 | 1.0992 | 2.8165 | 4.756% | 0.014207 | 0.013503 | 4537.5974 | 1115.6501 | 119.135 | 3302.8124 | 4546.8608 | 0 | 0 | 4546.8608 | 0.0001011%
2027 | 64 | 64-13F | Tier-1 | Non-HFTD---13 | 2--2 | 0.11307 | 9 | 100% | 5.341 | 32.14% | 65.84% | 2.014% | 0.084982 | 0 | 0 | 0.084982 | 0 | 0.077333 | 0.11143 | 0.69401 | 0.077333 | 0.11143 | 0.69401 | 0.085818 | 0.12365 | 0.69401 | 1.591% | 0.0078982 | 0.0075072 | 676.2339 | 52.8868 | 355.4216 | 267.9254 | 700.1306 | 0 | 0 | 700.1306 | 2.802e-06%
2027 | 571 | 571-33 | Tier-1 | Non-HFTD---8 | 3--2 | 4.3138 | 257 | 100% | 41.773 | 16.82% | 74.21% | 8.975% | 0.34775 | 0 | 0 | 0.34775 | 0 | 0.31645 | 4.2512 | 0.074437 | 0.31645 | 4.2512 | 0.074437 | 0.35117 | 4.7177 | 0.074437 | 0.8325% | 0.024717 | 0.023494 | 1690.0234 | 1.9728 | 1442.354 | 245.6966 | 1763.2343 | 0 | 0 | 1763.2343 | 1.147e-05%
2027 | 520 | 520-1045R | Tier-2 | Tier-2---5 | 5--4 | 8.7312 | 1277 | 100% | 2978.814 | 97.34% | 2.471% | 0.184% | 143.536 | 0 | 0 | 143.536 | 0 | 130.6158 | 8.6046 | 15.1797 | 130.6158 | 8.6046 | 15.1797 | 144.9467 | 9.5487 | 15.1797 | 4.819% | 0.26824 | 0.25496 | 11105.2066 | 1577.7553 | 240.9549 | 9286.4963 | 11120.5631 | 0 | 0 | 11120.5631 | 0.004733%
2027 | 171 | 171-567 | Tier-1 | Non-HFTD---6 | 4--3 | 4.0096 | 49 | 100% | 70.6554 | 57.12% | 38.82% | 4.06% | 1.9978 | 0 | 0 | 1.9978 | 0 | 1.8179 | 3.9515 | 0.46006 | 1.8179 | 3.9515 | 0.46006 | 2.0174 | 4.385 | 0.46006 | 2.827% | 0.041203 | 0.039164 | 1714.7945 | 149.6855 | 670.7195 | 894.3894 | 1753.0872 | 0 | 0 | 1753.0872 | 6.588e-05%
2027 | 712 | CB 712 | Tier-1 | Non-HFTD---17 | 1--2 | 0.30758 | 18 | 100% | 1.8273 | 79.32% | 0% | 20.68% | 0.071744 | 0 | 0 | 0.071744 | 0 | 0.065286 | 0.30312 | 0.21538 | 0.065286 | 0.30312 | 0.21538 | 0.072449 | 0.33637 | 0.21538 | 3.926% | 0.0012852 | 0.0012216 | 1421.816 | 151.1232 | 223.9631 | 1046.7297 | 1437.1307 | 0 | 0 | 1437.1307 | 2.366e-06%
2027 | 154 | CB 154 | Tier-1 | Non-HFTD---8 | 3--2 | 8.8996 | 202 | 100% | 34.1288 | 84.46% | 0% | 15.54% | 1.4268 | 0 | 0 | 1.4268 | 0 | 1.2984 | 8.7706 | 0.14804 | 1.2984 | 8.7706 | 0.14804 | 1.4408 | 9.7329 | 0.14804 | 4.181% | 0.024087 | 0.022895 | 1416.8753 | 0.16572 | 1216.6491 | 200.0605 | 1428.3445 | 0 | 0 | 1428.3445 | 4.705e-05%
2027 | 100 | CB 100 | Tier-1 | Non-HFTD---14 | 2--1 | 3.145 | 12 | 100% | 5.5173 | 52.94% | 0% | 47.06% | 0.14457 | 0 | 0 | 0.14457 | 0 | 0.13156 | 3.0994 | 0.042445 | 0.13156 | 3.0994 | 0.042445 | 0.14599 | 3.4395 | 0.042445 | 2.62% | 0.011123 | 0.010572 | 496.0224 | 30.1785 | 97.473 | 368.3709 | 508.18 | 0 | 0 | 508.18 | 4.767e-06%
2027 | 176 | 176-164R | Tier-3 | Tier-3---11 | 5--5 | 6.2526 | 373 | 100% | 4184.7467 | 98.1% | 1.799% | 0.1047% | 203.2012 | 0 | 0 | 203.2012 | 0 | 184.9104 | 6.162 | 30.0083 | 184.9104 | 6.162 | 30.0083 | 205.1983 | 6.8381 | 30.0083 | 4.856% | 0.20727 | 0.19701 | 20189.7554 | 3207.9265 | 321.2591 | 16660.5698 | 20209.7732 | 0 | 0 | 20209.7732 | 0.006701%
2027 | 902 | CB 902 | Tier-1 | Non-HFTD---6 | 3--3 | 7.7576 | 271 | 100% | 88.9578 | 94.13% | 0% | 5.869% | 4.145 | 0 | 0 | 4.145 | 0 | 3.7719 | 7.6451 | 0.49337 | 3.7719 | 7.6451 | 0.49337 | 4.1857 | 8.4839 | 0.49337 | 4.659% | 0.02472 | 0.023497 | 3598.5877 | 613.2964 | 680.9324 | 2304.3589 | 3609.5869 | 0 | 0 | 3609.5869 | 0.0001367%
2027 | 57 | 57-736 | Tier-1 | Non-HFTD---4 | 3--4 | 1.4816 | 0 | 100% | 116.8924 | 0.4896% | 98.37% | 1.142% | 0.028331 | 0 | 0 | 0.028331 | 0 | 0.025781 | 1.4601 | 0.017656 | 0.025781 | 1.4601 | 0.017656 | 0.028609 | 1.6203 | 0.017656 | 0.02424% | 0.015165 | 0.014415 | 7707.8351 | 8.3652 | 6936.4124 | 763.0575 | 8107.2772 | 0 | 0 | 8107.2772 | 9.342e-07%
2027 | 1081 | 1081-668F | Tier-1 | Non-HFTD---7 | 2--3 | 0.89998 | 110 | 100% | 32.9591 | 15.19% | 83.12% | 1.695% | 0.24782 | 0 | 0 | 0.24782 | 0 | 0.22551 | 0.88694 | 0.25426 | 0.22551 | 0.88694 | 0.25426 | 0.25026 | 0.98425 | 0.25426 | 0.7519% | 0.013304 | 0.012645 | 2477.4214 | 66.1914 | 1948.4509 | 462.7791 | 2586.8423 | 0 | 0 | 2586.8423 | 8.172e-06%
2027 | 553 | 553-27R | Tier-1 | Non-HFTD---1 | 4--4 | 16.2339 | 1091 | 100% | 504.2652 | 97.83% | 0% | 2.166% | 24.4204 | 0 | 0 | 24.4204 | 0 | 22.2223 | 15.9985 | 1.389 | 22.2223 | 15.9985 | 1.389 | 24.6604 | 17.7538 | 1.389 | 4.843% | 0.054721 | 0.052013 | 9215.1363 | 1913.347 | 158.4888 | 7143.3005 | 9225.5318 | 0 | 0 | 9225.5318 | 0.0008053%
2027 | 157 | 157-207R | Tier-3 | Tier-3---16 | 2--5 | 2.0208 | 0 | 100% | 719.0865 | 99.89% | 0% | 0.1123% | 35.5548 | 0 | 0 | 35.5548 | 0 | 32.3544 | 1.9915 | 16.246 | 32.3544 | 1.9915 | 16.246 | 35.9042 | 2.21 | 16.246 | 4.944% | 0.0095404 | 0.0090682 | 75372.7824 | 10925.518 | 1399.5436 | 63047.7208 | 75377.1909 | 0 | 0 | 75377.1909 | 0.001172%
2027 | 1242 | 1242-127AE | Tier-2 | Tier-2---21 | 1--4 | 0.052273 | 0 | 100% | 2.4589 | 98.62% | 0% | 1.38% | 0.12004 | 0 | 0 | 0.12004 | 0 | 0.10923 | 0.051515 | 2.1204 | 0.10923 | 0.051515 | 2.1204 | 0.12122 | 0.057167 | 2.1204 | 4.882% | 0.0001786 | 0.00016976 | 13767.9144 | 2205.6945 | 17.2653 | 11544.9546 | 13777.8124 | 0 | 0 | 13777.8124 | 3.958e-06%
2027 | 352 | CB 352 | Tier-2 | Tier-2---18 | 4--2 | 0.125 | 29 | 100% | 87.8741 | 99.22% | 0.6237% | 0.1541% | 4.3159 | 0 | 0 | 4.3159 | 0 | 3.9274 | 0.12319 | 31.8818 | 3.9274 | 0.12319 | 31.8818 | 4.3584 | 0.1367 | 31.8818 | 4.911% | 0.066856 | 0.063546 | 1314.3831 | 210.4244 | 8.2251 | 1095.7336 | 1314.9155 | 0 | 0 | 1314.9155 | 0.0001423%
2027 | 157 | 157-165R | Tier-3 | Tier-3---18 | 5--2 | 4.8606 | 118 | 100% | 418.5676 | 87.71% | 11.66% | 0.6303% | 18.1719 | 0 | 0 | 18.1719 | 0 | 16.5362 | 4.7901 | 3.4521 | 16.5362 | 4.7901 | 3.4521 | 18.3505 | 5.3157 | 3.4521 | 4.341% | 0.28262 | 0.26863 | 1481.042 | 148.6168 | 162.2497 | 1170.1755 | 1490.5243 | 0 | 0 | 1490.5243 | 0.0005992%
2027 | 771 | CB 771 | Tier-1 | Non-HFTD---9 | 2--3 | 3.289 | 51 | 100% | 24.0595 | 89.94% | 0% | 10.06% | 1.0712 | 0 | 0 | 1.0712 | 0 | 0.97476 | 3.2413 | 0.30073 | 0.97476 | 3.2413 | 0.30073 | 1.0817 | 3.5969 | 0.30073 | 4.452% | 0.012612 | 0.011987 | 1907.7243 | 292.4297 | 438.977 | 1176.3177 | 1917.7151 | 0 | 0 | 1917.7151 | 3.532e-05%
2027 | 350 | CB 350 | Tier-2 | Tier-2---15 | 1--5 | 0.13314 | 1 | 100% | 133.5736 | 99.92% | 0% | 0.07821% | 6.6067 | 0 | 0 | 6.6067 | 0 | 6.012 | 0.13121 | 45.8187 | 6.012 | 0.13121 | 45.8187 | 6.6717 | 0.14561 | 45.8187 | 4.946% | 0.0004644 | 0.00044141 | 287626.1215 | 46100.7705 | 2192.4832 | 239332.8678 | 287637.8364 | 0 | 0 | 287637.8364 | 0.0002179%
2027 | GA3 | CB GA3 | Tier-1 | Non-HFTD---12 | 3--2 | 8.5176 | 228 | 100% | 14.7076 | 61.7% | 0% | 38.3% | 0.44919 | 0 | 0 | 0.44919 | 0 | 0.40876 | 8.3941 | 0.048696 | 0.40876 | 8.3941 | 0.048696 | 0.45361 | 9.3151 | 0.048696 | 3.054% | 0.024925 | 0.023691 | 590.0826 | 58.8012 | 95.7567 | 435.5246 | 601.8522 | 0 | 0 | 601.8522 | 1.481e-05%
2027 | 176 | 176-161R | Tier-3 | Tier-3---5 | 5--5 | 10.6068 | 603 | 100% | 11523.3049 | 98.77% | 1.172% | 0.05875% | 563.3817 | 0 | 0 | 563.3817 | 0 | 512.6697 | 10.453 | 49.0451 | 512.6697 | 10.453 | 49.0451 | 568.9186 | 11.5999 | 49.0451 | 4.889% | 0.22417 | 0.21307 | 51404.5427 | 8329.9408 | 608.281 | 42466.321 | 51437.4981 | 0 | 0 | 51437.4981 | 0.01858%
2027 | 532 | 532-762 | Tier-1 | Non-HFTD---17 | 1--3 | 0.099583 | 5 | 100% | 0.90806 | 87.96% | 0% | 12.04% | 0.039537 | 0 | 0 | 0.039537 | 0 | 0.035978 | 0.098139 | 0.3666 | 0.035978 | 0.098139 | 0.3666 | 0.039926 | 0.10891 | 0.3666 | 4.354% | 0.0003776 | 0.00035891 | 2404.8082 | 35.439 | 1925.6662 | 443.703 | 2419.8862 | 0 | 0 | 2419.8862 | 1.304e-06%
2027 | 375 | CB 375 | Tier-1 | Non-HFTD---20 | 1--1 | 0.5411 | 62 | 100% | 0.68134 | 5.392% | 0% | 94.61% | 0.0018184 | 0 | 0 | 0.0018184 | 0 | 0.0016547 | 0.53326 | 0.003103 | 0.0016547 | 0.53326 | 0.003103 | 0.0018363 | 0.59177 | 0.003103 | 0.2669% | 0.0021338 | 0.0020282 | 319.3093 | 0.25077 | 44.5114 | 274.5471 | 335.0417 | 0 | 0 | 335.0417 | 5.996e-08%
2027 | 404 | 404-6AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.6847 | 111 | 100% | 2.5254 | 19.87% | 0% | 80.13% | 0.024835 | 0 | 0 | 0.024835 | 0 | 0.022599 | 2.6458 | 0.0085416 | 0.022599 | 2.6458 | 0.0085416 | 0.025079 | 2.9361 | 0.0085416 | 0.9834% | 0.0075878 | 0.0072122 | 332.8242 | 1.9467 | 79.6777 | 251.1998 | 346.7135 | 0 | 0 | 346.7135 | 8.19e-07%
2027 | 180 | 180-13 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1185 | 117 | 100% | 4.6843 | 83.08% | 0% | 16.92% | 0.19265 | 0 | 0 | 0.19265 | 0 | 0.17531 | 1.1023 | 0.15904 | 0.17531 | 1.1023 | 0.15904 | 0.19454 | 1.2233 | 0.15904 | 4.113% | 0.0036268 | 0.0034473 | 1291.5815 | 151.5131 | 169.6594 | 970.409 | 1302.96 | 0 | 0 | 1302.96 | 6.353e-06%
2027 | TM1 | CB TM1 | Tier-1 | Non-HFTD---7 | 1--5 | 0.014962 | 3 | 100% | 38.7396 | 99.8% | 0% | 0.1958% | 1.9139 | 0 | 0 | 1.9139 | 0 | 1.7416 | 0.014745 | 118.112 | 1.7416 | 0.014745 | 118.112 | 1.9327 | 0.016363 | 118.112 | 4.94% | 0.0001408 | 0.00013383 | 275139.3146 | 43811.8165 | 68.1712 | 231259.327 | 275167.3683 | 0 | 0 | 275167.3683 | 6.311e-05%
2027 | 279 | CB 279 | Tier-1 | Non-HFTD---6 | 3--3 | 4.4104 | 176 | 100% | 90.028 | 19.61% | 77.19% | 3.194% | 0.87403 | 0 | 0 | 0.87403 | 0 | 0.79536 | 4.3465 | 0.18299 | 0.79536 | 4.3465 | 0.18299 | 0.88262 | 4.8234 | 0.18299 | 0.9708% | 0.028282 | 0.026882 | 3183.1813 | 17.4479 | 2800.4627 | 365.2707 | 3316.4414 | 0 | 0 | 3316.4414 | 2.882e-05%
2027 | 450 | CB 450 | Tier-1 | Non-HFTD---13 | 1--3 | 0.74978 | 8 | 100% | 5.2749 | 90.32% | 0% | 9.679% | 0.23583 | 0 | 0 | 0.23583 | 0 | 0.21461 | 0.73891 | 0.29044 | 0.21461 | 0.73891 | 0.29044 | 0.23815 | 0.81998 | 0.29044 | 4.471% | 0.0022246 | 0.0021145 | 2371.1556 | 0.17269 | 2162.5037 | 208.4792 | 2383.1075 | 0 | 0 | 2383.1075 | 7.777e-06%
2027 | 79 | 79-668R | Tier-3 | Tier-3---15 | 5--3 | 9.2899 | 568 | 100% | 1606.9068 | 70.93% | 28.63% | 0.4437% | 56.416 | 0 | 0 | 56.416 | 0 | 51.3378 | 9.1552 | 5.6075 | 51.3378 | 9.1552 | 5.6075 | 56.9704 | 10.1597 | 5.6075 | 3.511% | 0.43999 | 0.41821 | 3652.1539 | 351.9998 | 935.9584 | 2364.1956 | 3707.4514 | 0 | 0 | 3707.4514 | 0.00186%
2027 | 1022 | 1022-26R | Tier-3 | Tier-3---15 | 4--4 | 0.38903 | 18 | 100% | 694.7204 | 99.22% | 0.7469% | 0.03547% | 34.1196 | 0 | 0 | 34.1196 | 0 | 31.0484 | 0.38339 | 80.9832 | 31.0484 | 0.38339 | 80.9832 | 34.4549 | 0.42546 | 80.9832 | 4.911% | 0.092662 | 0.088075 | 7497.376 | 1200.1947 | 49.8675 | 6247.3138 | 7500.4309 | 0 | 0 | 7500.4309 | 0.001125%
2027 | 450 | 450-113F | Tier-1 | Non-HFTD---17 | 1--4 | 0.057576 | 2 | 100% | 1.4984 | 95.09% | 0% | 4.911% | 0.070528 | 0 | 0 | 0.070528 | 0 | 0.06418 | 0.056741 | 1.1311 | 0.06418 | 0.056741 | 1.1311 | 0.071221 | 0.062966 | 1.1311 | 4.707% | 0.0002576 | 0.00024485 | 5816.7432 | 904.3973 | 28.2827 | 4884.0631 | 5831.6186 | 0 | 0 | 5831.6186 | 2.326e-06%
2027 | 95 | CB 95 | Tier-1 | Non-HFTD---9 | 2--3 | 1.4153 | 129 | 100% | 22.4303 | 86.17% | 9.176% | 4.655% | 0.95673 | 0 | 0 | 0.95673 | 0 | 0.87061 | 1.3948 | 0.62418 | 0.87061 | 1.3948 | 0.62418 | 0.96614 | 1.5478 | 0.62418 | 4.265% | 0.0095064 | 0.0090358 | 2359.4915 | 219.0536 | 893.0827 | 1247.3552 | 2376.4865 | 0 | 0 | 2376.4865 | 3.155e-05%
2027 | 361 | 361-686F | Tier-1 | Non-HFTD---5 | 3--4 | 4.0396 | 99 | 100% | 90.6744 | 3.585% | 93.42% | 2.993% | 0.16092 | 0 | 0 | 0.16092 | 0 | 0.14644 | 3.981 | 0.036784 | 0.14644 | 3.981 | 0.036784 | 0.1625 | 4.4178 | 0.036784 | 0.1775% | 0.016667 | 0.015842 | 5440.2244 | 15.7061 | 4798.4721 | 626.0462 | 5713.382 | 0 | 0 | 5713.382 | 5.307e-06%
2027 | 250 | 250-288F | Tier-1 | Non-HFTD---19 | 1--2 | 0.046023 | 0 | 100% | 0.22194 | 49.89% | 0% | 50.11% | 0.0054814 | 0 | 0 | 0.0054814 | 0 | 0.004988 | 0.045355 | 0.10998 | 0.004988 | 0.045355 | 0.10998 | 0.0055353 | 0.050332 | 0.10998 | 2.47% | 0.0002572 | 0.00024447 | 862.9068 | 69.1562 | 40.6738 | 753.0767 | 885.4234 | 0 | 0 | 885.4234 | 1.808e-07%
2027 | 275 | 275-45 | Tier-1 | Non-HFTD---4 | 3--4 | 1.1627 | 21 | 100% | 157.581 | 0.4262% | 99.03% | 0.5451% | 0.033242 | 0 | 0 | 0.033242 | 0 | 0.03025 | 1.1458 | 0.026401 | 0.03025 | 1.1458 | 0.026401 | 0.033569 | 1.2715 | 0.026401 | 0.0211% | 0.018421 | 0.017509 | 8554.512 | 15.6556 | 7786.8024 | 752.0539 | 8998.114 | 0 | 0 | 8998.114 | 1.096e-06%
2027 | 231 | 231-1635R | Tier-2 | Tier-2---4 | 5--5 | 29.745 | 3637 | 100% | 5142.095 | 98.68% | 0.901% | 0.4182% | 251.176 | 0 | 0 | 251.176 | 0 | 228.5667 | 29.3138 | 7.7973 | 228.5667 | 29.3138 | 7.7973 | 253.6445 | 32.53 | 7.7973 | 4.885% | 0.11648 | 0.11071 | 44146.87 | 7752.1946 | 471.7485 | 35922.9269 | 44177.1988 | 0 | 0 | 44177.1988 | 0.008283%
2027 | 72 | CB 72 | Tier-1 | Non-HFTD---11 | 2--2 | 3.7652 | 140 | 100% | 12.136 | 75.45% | 0% | 24.55% | 0.45323 | 0 | 0 | 0.45323 | 0 | 0.41243 | 3.7106 | 0.11115 | 0.41243 | 3.7106 | 0.11115 | 0.45768 | 4.1177 | 0.11115 | 3.735% | 0.012052 | 0.011455 | 1006.99 | 15.7502 | 686.9496 | 304.2902 | 1019.8666 | 0 | 0 | 1019.8666 | 1.495e-05%
2027 | 41 | CB 41 | Tier-1 | Non-HFTD---9 | 3--2 | 4.8292 | 112 | 100% | 23.8741 | 85.94% | 0% | 14.06% | 1.0156 | 0 | 0 | 1.0156 | 0 | 0.92417 | 4.7591 | 0.19419 | 0.92417 | 4.7591 | 0.19419 | 1.0256 | 5.2813 | 0.19419 | 4.254% | 0.013957 | 0.013266 | 1710.5248 | 0.97502 | 1486.9644 | 222.5854 | 1723.0513 | 0 | 0 | 1723.0513 | 3.349e-05%
2027 | 407 | CB 407 | Tier-1 | Non-HFTD---14 | 3--1 | 5.0112 | 98 | 100% | 5.6418 | 32.16% | 0% | 67.84% | 0.089806 | 0 | 0 | 0.089806 | 0 | 0.081722 | 4.9386 | 0.016548 | 0.081722 | 4.9386 | 0.016548 | 0.090689 | 5.4804 | 0.016548 | 1.592% | 0.014713 | 0.013984 | 383.4683 | 0.85569 | 142.8953 | 239.7173 | 397.0166 | 0 | 0 | 397.0166 | 2.961e-06%
2027 | 373 | CB 373 | Tier-1 | Non-HFTD---19 | 1--1 | 0.33921 | 6 | 100% | 0.39748 | 23.53% | 0% | 76.47% | 0.0046292 | 0 | 0 | 0.0046292 | 0 | 0.0042125 | 0.33429 | 0.012601 | 0.0042125 | 0.33429 | 0.012601 | 0.0046747 | 0.37097 | 0.012601 | 1.165% | 0.0010574 | 0.0010051 | 375.899 | 0.2163 | 114.5547 | 261.128 | 390.8691 | 0 | 0 | 390.8691 | 1.527e-07%
2027 | 182 | 182-2252R | Tier-2 | Tier-2---5 | 5--5 | 3.4226 | 354 | 100% | 4229.9446 | 99.22% | 0.7256% | 0.05893% | 207.7395 | 0 | 0 | 207.7395 | 0 | 189.0401 | 3.3729 | 56.0461 | 189.0401 | 3.3729 | 56.0461 | 209.7812 | 3.743 | 56.0461 | 4.911% | 0.11307 | 0.10747 | 37409.5665 | 6099.6348 | 248.5113 | 31061.4203 | 37424.8513 | 0 | 0 | 37424.8513 | 0.00685%
2027 | 158 | CB 158 | Tier-1 | Non-HFTD---16 | 2--1 | 4.6192 | 158 | 100% | 4.5058 | 34.28% | 0% | 65.72% | 0.076457 | 0 | 0 | 0.076457 | 0 | 0.069575 | 4.5522 | 0.015284 | 0.069575 | 4.5522 | 0.015284 | 0.077208 | 5.0517 | 0.015284 | 1.697% | 0.012279 | 0.011672 | 366.9398 | 1.1795 | 141.5538 | 224.2064 | 379.4985 | 0 | 0 | 379.4985 | 2.521e-06%
2027 | 356 | CB 356 | Tier-2 | Tier-2---19 | 1--5 | 0.016856 | 5 | 100% | 6.8062 | 99.1% | 0% | 0.8997% | 0.33387 | 0 | 0 | 0.33387 | 0 | 0.30382 | 0.016612 | 18.2896 | 0.30382 | 0.016612 | 18.2896 | 0.33716 | 0.018434 | 18.2896 | 4.905% | 0.0001262 | 0.00011995 | 53931.5569 | 8525.3907 | 930.8819 | 44475.2842 | 53956.8259 | 0 | 0 | 53956.8259 | 1.101e-05%
2027 | 326 | CB 326 | Tier-1 | Non-HFTD---8 | 3--3 | 5.6661 | 124 | 100% | 30.5714 | 87.97% | 0% | 12.03% | 1.3312 | 0 | 0 | 1.3312 | 0 | 1.2114 | 5.584 | 0.21694 | 1.2114 | 5.584 | 0.21694 | 1.3443 | 6.1966 | 0.21694 | 4.354% | 0.015429 | 0.014666 | 1981.3749 | 14.2383 | 1678.7619 | 288.3747 | 1993.7895 | 0 | 0 | 1993.7895 | 4.39e-05%
2027 | 448 | 448-1234R | Tier-3 | Tier-3---15 | 5--3 | 3.0297 | 15 | 100% | 1211.6194 | 97.39% | 2.475% | 0.1351% | 58.4097 | 0 | 0 | 58.4097 | 0 | 53.1521 | 2.9858 | 17.8017 | 53.1521 | 2.9858 | 17.8017 | 58.9838 | 3.3134 | 17.8017 | 4.821% | 0.62101 | 0.59027 | 1951.0598 | 272.2597 | 44.6636 | 1634.1365 | 1953.7118 | 0 | 0 | 1953.7118 | 0.001926%
2027 | 86 | 86-553F | Tier-1 | Not Applicable | Not Applicable | 0.0223 | 0 | 100% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.021977 | 0 | 0 | 0.021977 | 0 | 0 | 0.024388 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2027 | 221 | 221-1235F | Tier-3 | Tier-3---18 | 5--2 | 0.0489 | 0 | 100% | 236.1769 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.048191 | 0 | 0 | 0.048191 | 0 | 0 | 0.053478 | 0 | 0% | 0.16409 | 0.15597 | 1439.2989 | 2.105 | 1306.2711 | 130.9227 | 1514.2545 | 0 | 0 | 1514.2545 | 0%
2027 | 1234 | 1234-732R | Tier-2 | Not Applicable | Not Applicable | 0.5958 | 0 | 100% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.58716 | 0 | 0 | 0.58716 | 0 | 0 | 0.65158 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2028 | 1153 | CB 1153 | Tier-1 | Non-HFTD---19 | 1--2 | 0.09697 | 1 | 100% | 0.54442 | 68.22% | 0% | 31.78% | 0.018384 | 0 | 0 | 0.018384 | 0 | 0.015958 | 0.091161 | 0.17506 | 0.015958 | 0.091161 | 0.17506 | 0.018656 | 0.10657 | 0.17506 | 3.377% | 0.0005088 | 0.00048361 | 1070.015 | 113.1086 | 30.893 | 926.0134 | 1087.7256 | 0 | 0 | 1087.7256 | 6.062e-07%
2028 | 217 | 217-983R | Tier-3 | Tier-3---5 | 5--5 | 6.8811 | 261 | 100% | 10116.9629 | 99.05% | 0.91% | 0.0405% | 496.0298 | 0 | 0 | 496.0298 | 0 | 430.5862 | 6.4689 | 66.5626 | 430.5862 | 6.4689 | 66.5626 | 503.3602 | 7.5622 | 66.5626 | 4.903% | 0.2438 | 0.23173 | 41497.7937 | 6529.9576 | 349.4347 | 34618.4014 | 41518.3345 | 0 | 0 | 41518.3345 | 0.01636%
2028 | 509 | 509-1227R | Tier-1 | Non-HFTD---13 | 2--2 | 2.0561 | 86 | 100% | 6.8178 | 77.37% | 0% | 22.63% | 0.26111 | 0 | 0 | 0.26111 | 0 | 0.22666 | 1.9329 | 0.11726 | 0.22666 | 1.9329 | 0.11726 | 0.26497 | 2.2596 | 0.11726 | 3.83% | 0.0063694 | 0.0060541 | 1070.3915 | 53.8343 | 522.4019 | 494.1553 | 1083.0058 | 0 | 0 | 1083.0058 | 8.61e-06%
2028 | 142 | 142-8R | Tier-1 | Non-HFTD---8 | 3--2 | 6.7481 | 216 | 100% | 40.8893 | 6.402% | 80.66% | 12.94% | 0.12957 | 0 | 0 | 0.12957 | 0 | 0.11247 | 6.3439 | 0.017729 | 0.11247 | 6.3439 | 0.017729 | 0.13148 | 7.4161 | 0.017729 | 0.3169% | 0.027724 | 0.026352 | 1474.8579 | 5.0539 | 1173.9231 | 295.8809 | 1546.7485 | 0 | 0 | 1546.7485 | 4.273e-06%
2028 | DV1 | CB DV1 | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 0 | 100% | 15.4911 | 99.81% | 0% | 0.1868% | 0.76538 | 0 | 0 | 0.76538 | 0 | 0.6644 | 0.032227 | 20.6162 | 0.6644 | 0.032227 | 20.6162 | 0.77669 | 0.037674 | 20.6162 | 4.941% | 0.000145 | 0.00013782 | 106835.191 | 17155.6704 | 250.2479 | 89429.2727 | 106845.5825 | 0 | 0 | 106845.5825 | 2.524e-05%
2028 | 391 | CB 391 | Tier-1 | Non-HFTD---2 | 4--4 | 0.66137 | 36 | 100% | 550.2041 | 0.5245% | 99.39% | 0.08518% | 0.14286 | 0 | 0 | 0.14286 | 0 | 0.12401 | 0.62176 | 0.19945 | 0.12401 | 0.62176 | 0.19945 | 0.14497 | 0.72684 | 0.19945 | 0.02597% | 0.089115 | 0.084704 | 6174.0912 | 11.3908 | 5617.0317 | 545.6688 | 6493.938 | 0 | 0 | 6493.938 | 4.711e-06%
2028 | 84 | CB 84 | Tier-1 | Non-HFTD---12 | 3--2 | 6.597 | 272 | 100% | 11.1569 | 60.04% | 0% | 39.96% | 0.33156 | 0 | 0 | 0.33156 | 0 | 0.28781 | 6.2018 | 0.046408 | 0.28781 | 6.2018 | 0.046408 | 0.33646 | 7.25 | 0.046408 | 2.972% | 0.018717 | 0.01779 | 596.0964 | 9.118 | 324.3476 | 262.6307 | 608.5026 | 0 | 0 | 608.5026 | 1.093e-05%
2028 | 325 | 325-25 | Tier-1 | Non-HFTD---13 | 1--3 | 1.2847 | 29 | 100% | 8.3612 | 88.04% | 0% | 11.96% | 0.36437 | 0 | 0 | 0.36437 | 0 | 0.31629 | 1.2077 | 0.2619 | 0.31629 | 1.2077 | 0.2619 | 0.36975 | 1.4118 | 0.2619 | 4.358% | 0.0037654 | 0.003579 | 2220.5219 | 1.0278 | 1973.9755 | 245.5186 | 2234.3551 | 0 | 0 | 2234.3551 | 1.202e-05%
2028 | 221 | 221-1466 | Tier-3 | Not Applicable | Not Applicable | 0.6294 | 0 | 100% | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0.5917 | 0 | 0 | 0.5917 | 0 | 0 | 0.6917 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2028 | 390 | CB 390 | Tier-1 | Non-HFTD---2 | 5--4 | 1.4761 | 48 | 100% | 555.1958 | 4.119% | 95.66% | 0.2245% | 1.1319 | 0 | 0 | 1.1319 | 0 | 0.98254 | 1.3877 | 0.70805 | 0.98254 | 1.3877 | 0.70805 | 1.1486 | 1.6222 | 0.70805 | 0.2039% | 0.093583 | 0.088951 | 5932.6308 | 27.2019 | 5249.9711 | 655.4577 | 6228.8647 | 0 | 0 | 6228.8647 | 3.733e-05%
2028 | 445 | 445-1315 | Tier-2 | Tier-2---19 | 1--5 | 0.080871 | 0 | 100% | 26.2494 | 99.59% | 0% | 0.4079% | 1.294 | 0 | 0 | 1.294 | 0 | 1.1233 | 0.076027 | 14.7752 | 1.1233 | 0.076027 | 14.7752 | 1.3132 | 0.088877 | 14.7752 | 4.93% | 0.000636 | 0.00060452 | 41272.5846 | 5558.0973 | 1215.1763 | 34499.311 | 41281.3528 | 0 | 0 | 41281.3528 | 4.267e-05%
2028 | 520 | 520-1527R | Tier-3 | Tier-3---7 | 5--5 | 10.7038 | 1013 | 100% | 6763.0006 | 96.72% | 3.176% | 0.1068% | 323.7803 | 0 | 0 | 323.7803 | 0 | 281.0624 | 10.0626 | 27.9313 | 281.0624 | 10.0626 | 27.9313 | 328.5651 | 11.7633 | 27.9313 | 4.788% | 0.27105 | 0.25763 | 24951.4497 | 4456.278 | 731.2619 | 19763.9099 | 24994.1011 | 0 | 0 | 24994.1011 | 0.01068%
2028 | 93 | CB 93 | Tier-1 | Non-HFTD---3 | 3--4 | 6.2065 | 398 | 100% | 117.8522 | 49.76% | 46.78% | 3.462% | 2.9028 | 0 | 0 | 2.9028 | 0 | 2.5198 | 5.8347 | 0.43186 | 2.5198 | 5.8347 | 0.43186 | 2.9457 | 6.8209 | 0.43186 | 2.463% | 0.023557 | 0.022391 | 5002.7692 | 337.5468 | 2573.6674 | 2091.555 | 5133.6638 | 0 | 0 | 5133.6638 | 9.572e-05%
2028 | 733 | 733-20AE | Tier-1 | Non-HFTD---8 | 3--2 | 9.4582 | 571 | 100% | 39.7294 | 85.07% | 0% | 14.93% | 1.6731 | 0 | 0 | 1.6731 | 0 | 1.4523 | 8.8916 | 0.16334 | 1.4523 | 8.8916 | 0.16334 | 1.6978 | 10.3944 | 0.16334 | 4.211% | 0.026087 | 0.024795 | 1522.9809 | 217.8105 | 467.7091 | 837.4613 | 1534.8195 | 0 | 0 | 1534.8195 | 5.517e-05%
2028 | 233 | 233-123R | Tier-2 | Tier-2---4 | 4--5 | 15.066 | 1487 | 100% | 3035.8045 | 98.84% | 0.8219% | 0.339% | 148.5278 | 0 | 0 | 148.5278 | 0 | 128.9318 | 14.1635 | 9.1031 | 128.9318 | 14.1635 | 9.1031 | 150.7228 | 16.5573 | 9.1031 | 4.893% | 0.06125 | 0.058219 | 49563.8317 | 7938.6753 | 487.1368 | 41138.0196 | 49593.7962 | 0 | 0 | 49593.7962 | 0.004898%
2028 | 307 | 307-1538F | Tier-2 | Tier-2---7 | 5--5 | 2.2173 | 257 | 100% | 2407.2332 | 91.07% | 8.863% | 0.06623% | 108.5181 | 0 | 0 | 108.5181 | 0 | 94.2008 | 2.0845 | 45.1917 | 94.2008 | 2.0845 | 45.1917 | 110.1218 | 2.4368 | 45.1917 | 4.508% | 0.10098 | 0.09598 | 23839.1374 | 3538.2875 | 1900.5414 | 18400.3085 | 23949.9932 | 0 | 0 | 23949.9932 | 0.003579%
2028 | 1085 | CB 1085 | Tier-1 | Non-HFTD---4 | 2--4 | 0.4608 | 15 | 100% | 121.8151 | 29.33% | 70.28% | 0.3892% | 1.7686 | 0 | 0 | 1.7686 | 0 | 1.5352 | 0.43319 | 3.5439 | 1.5352 | 0.43319 | 3.5439 | 1.7947 | 0.50641 | 3.5439 | 1.452% | 0.009242 | 0.0087845 | 13180.5987 | 392.6277 | 10019.0268 | 2768.9443 | 13665.6902 | 0 | 0 | 13665.6902 | 5.832e-05%
2028 | 299 | CB 299 | Tier-1 | Non-HFTD---11 | 1--3 | 0.95907 | 13 | 100% | 9.1156 | 92.89% | 0% | 7.105% | 0.41916 | 0 | 0 | 0.41916 | 0 | 0.36386 | 0.90163 | 0.40356 | 0.36386 | 0.90163 | 0.40356 | 0.42536 | 1.054 | 0.40356 | 4.598% | 0.0028978 | 0.0027544 | 3145.7096 | 173.9595 | 1876.4075 | 1095.3426 | 3157.3492 | 0 | 0 | 3157.3492 | 1.382e-05%
2028 | 732 | 732-15R | Tier-1 | Non-HFTD---1 | 3--5 | 5.2317 | 420 | 100% | 342.6373 | 98.93% | 0% | 1.067% | 16.7796 | 0 | 0 | 16.7796 | 0 | 14.5658 | 4.9183 | 2.9615 | 14.5658 | 4.9183 | 2.9615 | 17.0275 | 5.7495 | 2.9615 | 4.897% | 0.02096 | 0.019923 | 16347.0441 | 3636.1945 | 124.2963 | 12586.5533 | 16356.1285 | 0 | 0 | 16356.1285 | 0.0005533%
2028 | 1119 | 1119-6F | Tier-1 | Non-HFTD---11 | 1--4 | 0.65508 | 30 | 100% | 14.1126 | 96.32% | 0% | 3.68% | 0.67286 | 0 | 0 | 0.67286 | 0 | 0.58409 | 0.61584 | 0.94845 | 0.58409 | 0.61584 | 0.94845 | 0.68281 | 0.71992 | 0.94845 | 4.768% | 0.002277 | 0.0021643 | 6197.8946 | 838.8203 | 861.0344 | 4498.0399 | 6209.7735 | 0 | 0 | 6209.7735 | 2.219e-05%
2028 | 256 | CB 256 | Tier-1 | Non-HFTD---11 | 2--2 | 3.543 | 127 | 100% | 11.4393 | 77.87% | 0% | 22.13% | 0.44094 | 0 | 0 | 0.44094 | 0 | 0.38277 | 3.3308 | 0.11492 | 0.38277 | 3.3308 | 0.11492 | 0.44746 | 3.8937 | 0.11492 | 3.855% | 0.011638 | 0.011062 | 982.9441 | 22.1853 | 662.0367 | 298.7221 | 994.2718 | 0 | 0 | 994.2718 | 1.454e-05%
2028 | 572 | CB 572 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1793 | 12 | 100% | 3.33 | 52.2% | 0% | 47.8% | 0.086046 | 0 | 0 | 0.086046 | 0 | 0.074694 | 1.1087 | 0.067373 | 0.074694 | 1.1087 | 0.067373 | 0.087318 | 1.296 | 0.067373 | 2.584% | 0.0045428 | 0.0043179 | 733.0269 | 0.26885 | 414.4483 | 318.3098 | 751.2737 | 0 | 0 | 751.2737 | 2.837e-06%
2028 | 901 | 901-1124 | Tier-1 | Non-HFTD---1 | 2--5 | 2.1134 | 202 | 100% | 225.4814 | 99.29% | 0% | 0.709% | 11.0822 | 0 | 0 | 11.0822 | 0 | 9.6201 | 1.9868 | 4.842 | 9.6201 | 1.9868 | 4.842 | 11.246 | 2.3226 | 4.842 | 4.915% | 0.0087544 | 0.0083211 | 25756.3496 | 4178.6743 | 36.5656 | 21541.1098 | 25765.8596 | 0 | 0 | 25765.8596 | 0.0003654%
2028 | 183 | 183-440 | Tier-2 | Tier-2---12 | 3--5 | 3.165 | 217 | 100% | 471.2015 | 74.37% | 25.17% | 0.4626% | 17.3463 | 0 | 0 | 17.3463 | 0 | 15.0577 | 2.9754 | 5.0607 | 15.0577 | 2.9754 | 5.0607 | 17.6026 | 3.4783 | 5.0607 | 3.681% | 0.025335 | 0.024081 | 18598.5411 | 2255.9959 | 4325.0411 | 12017.5041 | 18846.7923 | 0 | 0 | 18846.7923 | 0.000572%
2028 | 973 | 973-1226R | Tier-3 | Tier-3---10 | 5--5 | 8.4832 | 262 | 100% | 5177.8696 | 97.32% | 2.585% | 0.09195% | 249.4435 | 0 | 0 | 249.4435 | 0 | 216.5332 | 7.975 | 27.1514 | 216.5332 | 7.975 | 27.1514 | 253.1298 | 9.3229 | 27.1514 | 4.817% | 0.13989 | 0.13297 | 37012.5952 | 5797.6214 | 879.9001 | 30335.0736 | 37064.1939 | 0 | 0 | 37064.1939 | 0.008226%
2028 | 546 | 546-14R | Tier-1 | Non-HFTD---1 | 3--4 | 3.7622 | 61 | 100% | 227.2127 | 1.45% | 97.43% | 1.118% | 0.16304 | 0 | 0 | 0.16304 | 0 | 0.14153 | 3.5368 | 0.040017 | 0.14153 | 3.5368 | 0.040017 | 0.16545 | 4.1346 | 0.040017 | 0.07176% | 0.020679 | 0.019656 | 10987.501 | 12.3302 | 9969.5471 | 1005.6237 | 11551.4115 | 0 | 0 | 11551.4115 | 5.377e-06%
2028 | 73 | 73-1130R | Tier-3 | Tier-3---9 | 5--5 | 12.0339 | 277 | 100% | 6201.607 | 97.29% | 2.601% | 0.1104% | 298.6566 | 0 | 0 | 298.6566 | 0 | 259.2534 | 11.3131 | 22.9162 | 259.2534 | 11.3131 | 22.9162 | 303.0701 | 13.2251 | 22.9162 | 4.816% | 0.2182 | 0.2074 | 28421.9762 | 4506.0463 | 681.7619 | 23234.168 | 28462.107 | 0 | 0 | 28462.107 | 0.009849%
2028 | CTL1 | CTL1-3R | Tier-3 | Tier-3---14 | 5--4 | 6.8671 | 1649 | 100% | 2064.0334 | 78.9% | 20.86% | 0.2358% | 80.612 | 0 | 0 | 80.612 | 0 | 69.9765 | 6.4557 | 10.8394 | 69.9765 | 6.4557 | 10.8394 | 81.8033 | 7.5468 | 10.8394 | 3.906% | 0.42513 | 0.40409 | 4855.055 | 599.2986 | 919.5646 | 3336.1917 | 4908.4041 | 0 | 0 | 4908.4041 | 0.002658%
2028 | 1250 | 1250-677R | Tier-2 | Tier-2---3 | 5--5 | 9.4852 | 776 | 100% | 11748.9088 | 99.26% | 0.6837% | 0.05427% | 577.2793 | 0 | 0 | 577.2793 | 0 | 501.116 | 8.9171 | 56.1973 | 501.116 | 8.9171 | 56.1973 | 585.8104 | 10.4242 | 56.1973 | 4.913% | 0.11659 | 0.11081 | 100775.3023 | 17114.8267 | 643.0906 | 83017.3851 | 100814.0313 | 0 | 0 | 100814.0313 | 0.01904%
2028 | 200 | CB 200 | Tier-2 | Tier-2---9 | 4--5 | 13.8235 | 537 | 100% | 1342.6559 | 29.9% | 69.37% | 0.7369% | 19.8694 | 0 | 0 | 19.8694 | 0 | 17.2479 | 12.9955 | 1.3272 | 17.2479 | 12.9955 | 1.3272 | 20.163 | 15.1918 | 1.3272 | 1.48% | 0.060261 | 0.057278 | 22280.6766 | 968.7431 | 14863.6506 | 6448.2829 | 23094.1132 | 0 | 0 | 23094.1132 | 0.0006552%
2028 | 280 | CB 280 | Tier-2 | Tier-2---14 | 4--4 | 4.0675 | 139 | 100% | 310.7968 | 16.09% | 83.08% | 0.8251% | 2.4753 | 0 | 0 | 2.4753 | 0 | 2.1488 | 3.8238 | 0.56194 | 2.1488 | 3.8238 | 0.56194 | 2.5119 | 4.4701 | 0.56194 | 0.7965% | 0.042409 | 0.04031 | 7328.4886 | 170.2669 | 5820.5339 | 1337.6878 | 7648.7329 | 0 | 0 | 7648.7329 | 8.163e-05%
2028 | 322 | CB 322 | Tier-1 | Non-HFTD---8 | 3--3 | 6.9822 | 212 | 100% | 42.0776 | 89.49% | 0% | 10.51% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.618 | 6.564 | 0.2465 | 1.618 | 6.564 | 0.2465 | 1.8915 | 7.6733 | 0.2465 | 4.43% | 0.018945 | 0.018007 | 2221.0419 | 151.6209 | 1083.6314 | 985.7895 | 2233.1993 | 0 | 0 | 2233.1993 | 6.147e-05%
2028 | 56 | CB 56 | Tier-1 | Non-HFTD---3 | 3--4 | 3.7124 | 66 | 100% | 122.2122 | 9.667% | 86.95% | 3.388% | 0.58481 | 0 | 0 | 0.58481 | 0 | 0.50766 | 3.49 | 0.14546 | 0.50766 | 3.49 | 0.14546 | 0.59346 | 4.0798 | 0.14546 | 0.4785% | 0.023301 | 0.022147 | 5245.0232 | 5.0181 | 4537.7925 | 702.2126 | 5491.767 | 0 | 0 | 5491.767 | 1.929e-05%
2028 | 80 | 80-564 | Tier-1 | Non-HFTD---8 | 3--2 | 9.7153 | 219 | 100% | 31.4137 | 77.77% | 0% | 22.23% | 1.2093 | 0 | 0 | 1.2093 | 0 | 1.0498 | 9.1334 | 0.11494 | 1.0498 | 9.1334 | 0.11494 | 1.2272 | 10.677 | 0.11494 | 3.85% | 0.028026 | 0.026639 | 1120.8843 | 9.0416 | 839.8211 | 272.0216 | 1133.8606 | 0 | 0 | 1133.8606 | 3.988e-05%
2028 | 835 | 835-35F | Tier-2 | Tier-2---19 | 1--5 | 0.074242 | 8 | 100% | 6.7153 | 99.02% | 0% | 0.9775% | 0.32916 | 0 | 0 | 0.32916 | 0 | 0.28573 | 0.069795 | 4.0938 | 0.28573 | 0.069795 | 4.0938 | 0.33402 | 0.081592 | 4.0938 | 4.902% | 0.0003154 | 0.00029979 | 21291.4086 | 3424.4375 | 20.5737 | 17846.3975 | 21302.2477 | 0 | 0 | 21302.2477 | 1.085e-05%
2028 | 480 | 480-32 | Tier-1 | Non-HFTD---10 | 3--2 | 7.1091 | 262 | 100% | 17.2812 | 70.33% | 0% | 29.67% | 0.60164 | 0 | 0 | 0.60164 | 0 | 0.52226 | 6.6833 | 0.078145 | 0.52226 | 6.6833 | 0.078145 | 0.61053 | 7.8128 | 0.078145 | 3.481% | 0.019568 | 0.018599 | 883.1465 | 0.19748 | 644.9364 | 238.0126 | 896.7913 | 0 | 0 | 896.7913 | 1.984e-05%
2028 | 461 | 461-644R | Tier-1 | Non-HFTD---17 | 1--3 | 0.27861 | 0 | 100% | 1.9699 | 87.49% | 0% | 12.51% | 0.085309 | 0 | 0 | 0.085309 | 0 | 0.074054 | 0.26192 | 0.28273 | 0.074054 | 0.26192 | 0.28273 | 0.08657 | 0.30619 | 0.28273 | 4.331% | 0.0008654 | 0.00082256 | 2276.3126 | 196.7287 | 798.4144 | 1281.1695 | 2291.1467 | 0 | 0 | 2291.1467 | 2.813e-06%
2028 | 442 | 442-525 | Tier-3 | Tier-3---18 | 5--2 | 4.5645 | 666 | 100% | 526.1263 | 57.95% | 41.57% | 0.4783% | 15.0927 | 0 | 0 | 15.0927 | 0 | 13.1015 | 4.2911 | 3.0532 | 13.1015 | 4.2911 | 3.0532 | 15.3158 | 5.0164 | 3.0532 | 2.869% | 0.36155 | 0.34365 | 1455.1925 | 118.5768 | 543.1524 | 793.4634 | 1487.0575 | 0 | 0 | 1487.0575 | 0.0004977%
2028 | 171 | 171-34 | Tier-1 | Non-HFTD---6 | 4--3 | 4.3813 | 60 | 100% | 81.2035 | 44.67% | 51.64% | 3.687% | 1.7955 | 0 | 0 | 1.7955 | 0 | 1.5586 | 4.1188 | 0.37842 | 1.5586 | 4.1188 | 0.37842 | 1.8221 | 4.815 | 0.37842 | 2.211% | 0.043687 | 0.041525 | 1858.7395 | 129.5883 | 851.5868 | 877.5644 | 1912.2988 | 0 | 0 | 1912.2988 | 5.921e-05%
2028 | 70 | CB 70 | Tier-1 | Non-HFTD---12 | 3--2 | 6.5709 | 60 | 100% | 14.3505 | 72.4% | 0% | 27.6% | 0.51431 | 0 | 0 | 0.51431 | 0 | 0.44645 | 6.1773 | 0.072274 | 0.44645 | 6.1773 | 0.072274 | 0.52191 | 7.2213 | 0.072274 | 3.584% | 0.016758 | 0.015928 | 856.3389 | 1.8915 | 630.9279 | 223.5195 | 868.6465 | 0 | 0 | 868.6465 | 1.696e-05%
2028 | 357 | CB 357 | Tier-3 | Tier-3---10 | 5--5 | 5.0178 | 378 | 100% | 6110.8546 | 96.01% | 3.933% | 0.05986% | 290.409 | 0 | 0 | 290.409 | 0 | 252.094 | 4.7172 | 53.4412 | 252.094 | 4.7172 | 53.4412 | 294.7007 | 5.5145 | 53.4412 | 4.752% | 0.12773 | 0.12141 | 47841.0693 | 7695.9209 | 1866.6974 | 38278.451 | 47940.553 | 0 | 0 | 47940.553 | 0.009577%
2028 | 1434 | 1434-10AE | Tier-1 | Non-HFTD---10 | 3--2 | 6.6536 | 200 | 100% | 17.6762 | 78.96% | 0% | 21.04% | 0.69087 | 0 | 0 | 0.69087 | 0 | 0.59972 | 6.255 | 0.095878 | 0.59972 | 6.255 | 0.095878 | 0.70108 | 7.3122 | 0.095878 | 3.908% | 0.017501 | 0.016634 | 1010.0366 | 133.2202 | 327.76 | 549.0563 | 1021.1043 | 0 | 0 | 1021.1043 | 2.278e-05%
2028 | 55 | 55-484F | Tier-1 | Non-HFTD---20 | 1--1 | 0.58822 | 21 | 100% | 0.44013 | 10.92% | 0% | 89.08% | 0.0023797 | 0 | 0 | 0.0023797 | 0 | 0.0020657 | 0.55298 | 0.0037356 | 0.0020657 | 0.55298 | 0.0037356 | 0.0024149 | 0.64645 | 0.0037356 | 0.5407% | 0.0015886 | 0.00151 | 277.0544 | 0.1857 | 52.6811 | 224.1876 | 289.9068 | 0 | 0 | 289.9068 | 7.847e-08%
2028 | 719 | CB 719 | Tier-1 | Non-HFTD---8 | 3--3 | 5.0596 | 131 | 100% | 28.3767 | 85.41% | 0% | 14.59% | 1.1998 | 0 | 0 | 1.1998 | 0 | 1.0415 | 4.7566 | 0.21896 | 1.0415 | 4.7566 | 0.21896 | 1.2175 | 5.5605 | 0.21896 | 4.228% | 0.015223 | 0.01447 | 1864.0191 | 0.59716 | 1614.3662 | 249.0557 | 1878.1781 | 0 | 0 | 1878.1781 | 3.956e-05%
2028 | 91 | 91-7F | Tier-2 | Tier-2---9 | 4--5 | 7.7339 | 601 | 100% | 1295.9906 | 95.98% | 3.603% | 0.4176% | 61.5723 | 0 | 0 | 61.5723 | 0 | 53.4487 | 7.2706 | 7.3513 | 53.4487 | 7.2706 | 7.3513 | 62.4822 | 8.4995 | 7.3513 | 4.751% | 0.034038 | 0.032353 | 38075.0405 | 8008.4456 | 1355.7745 | 28710.8203 | 38154.7637 | 0 | 0 | 38154.7637 | 0.00203%
2028 | 1079 | 1079-9 | Tier-2 | Tier-2---15 | 3--3 | 8.0419 | 234 | 100% | 117.3021 | 94.99% | 0% | 5.009% | 5.5156 | 0 | 0 | 5.5156 | 0 | 4.7879 | 7.5602 | 0.63331 | 4.7879 | 7.5602 | 0.63331 | 5.5971 | 8.8379 | 0.63331 | 4.702% | 0.027256 | 0.025907 | 4303.7498 | 1020.4795 | 248.6707 | 3034.5996 | 4314.9761 | 0 | 0 | 4314.9761 | 0.0001819%
2028 | 217 | 217-48AE | Tier-2 | Tier-2---8 | 5--4 | 15.1559 | 814 | 100% | 2727.5845 | 87.85% | 11.78% | 0.3693% | 118.6108 | 0 | 0 | 118.6108 | 0 | 102.9619 | 14.248 | 7.2264 | 102.9619 | 14.248 | 7.2264 | 120.3637 | 16.6561 | 7.2264 | 4.349% | 0.20236 | 0.19234 | 13478.9252 | 1980.0515 | 1403.044 | 10095.8296 | 13564.2138 | 0 | 0 | 13564.2138 | 0.003911%
2028 | 67 | 67-45R | Tier-3 | Tier-3---15 | 5--4 | 10.2425 | 356 | 100% | 1627.9508 | 92.79% | 6.809% | 0.4053% | 74.7699 | 0 | 0 | 74.7699 | 0 | 64.9052 | 9.6289 | 6.7406 | 64.9052 | 9.6289 | 6.7406 | 75.8749 | 11.2564 | 6.7406 | 4.593% | 0.20887 | 0.19854 | 7793.9219 | 1114.9846 | 483.0899 | 6195.8475 | 7823.2046 | 0 | 0 | 7823.2046 | 0.002466%
2028 | 292 | CB 292 | Tier-2 | Tier-2---18 | 4--3 | 0.81042 | 169 | 100% | 94.6686 | 66.47% | 32.93% | 0.6021% | 3.115 | 0 | 0 | 3.115 | 0 | 2.704 | 0.76187 | 3.5491 | 2.704 | 0.76187 | 3.5491 | 3.161 | 0.89064 | 3.5491 | 3.29% | 0.048129 | 0.045747 | 1966.9754 | 205.7428 | 558.5001 | 1202.7325 | 2001.3198 | 0 | 0 | 2001.3198 | 0.0001027%
2028 | 448 | 448-9R | Tier-3 | Tier-3---9 | 5--4 | 17.7839 | 395 | 100% | 5644.8109 | 93.43% | 6.384% | 0.1906% | 261.0474 | 0 | 0 | 261.0474 | 0 | 226.6062 | 16.7187 | 13.5541 | 226.6062 | 16.7187 | 13.5541 | 264.9052 | 19.5443 | 13.5541 | 4.625% | 0.54394 | 0.51701 | 10377.639 | 1411.4395 | 624.4235 | 8341.776 | 10413.1713 | 0 | 0 | 10413.1713 | 0.008608%
2028 | 262 | CB 262 | Tier-1 | Non-HFTD---13 | 1--2 | 1.333 | 30 | 100% | 8.1125 | 88.1% | 0% | 11.9% | 0.35378 | 0 | 0 | 0.35378 | 0 | 0.30711 | 1.2531 | 0.24508 | 0.30711 | 1.2531 | 0.24508 | 0.35901 | 1.4649 | 0.24508 | 4.361% | 0.004918 | 0.0046746 | 1649.5582 | 174.8972 | 367.1245 | 1107.5365 | 1659.7811 | 0 | 0 | 1659.7811 | 1.167e-05%
2028 | 372 | CB 372 | Tier-1 | Non-HFTD---18 | 2--1 | 2.0544 | 108 | 100% | 2.0256 | 27.04% | 0% | 72.96% | 0.027112 | 0 | 0 | 0.027112 | 0 | 0.023535 | 1.9313 | 0.012186 | 0.023535 | 1.9313 | 0.012186 | 0.027513 | 2.2577 | 0.012186 | 1.339% | 0.0057966 | 0.0055097 | 349.4394 | 0.28023 | 117.0886 | 232.0705 | 362.7165 | 0 | 0 | 362.7165 | 8.941e-07%
2028 | 221 | 221-35 | Tier-2 | Tier-2---10 | 5--3 | 0.64962 | 16 | 100% | 710.3273 | 99.46% | 0.4791% | 0.06249% | 34.9708 | 0 | 0 | 34.9708 | 0 | 30.3569 | 0.61071 | 49.7076 | 30.3569 | 0.61071 | 49.7076 | 35.4876 | 0.71393 | 49.7076 | 4.923% | 0.17281 | 0.16425 | 4110.5569 | 625.546 | 25.6711 | 3459.3398 | 4111.7163 | 0 | 0 | 4111.7163 | 0.001153%
2028 | DV1 | DV1-3R | Tier-3 | Tier-3---11 | 5--5 | 7.3926 | 440 | 100% | 3719.4004 | 95.17% | 4.691% | 0.1427% | 175.211 | 0 | 0 | 175.211 | 0 | 152.0946 | 6.9498 | 21.8848 | 152.0946 | 6.9498 | 21.8848 | 177.8003 | 8.1244 | 21.8848 | 4.711% | 0.19421 | 0.1846 | 19151.2388 | 2981.992 | 820.0711 | 15349.1757 | 19199.4477 | 0 | 0 | 19199.4477 | 0.005778%
2028 | 178 | 178-968AE | Tier-2 | Tier-2---18 | 3--3 | 6.2909 | 231 | 100% | 47.6106 | 91.21% | 0% | 8.789% | 2.1496 | 0 | 0 | 2.1496 | 0 | 1.866 | 5.9141 | 0.31552 | 1.866 | 5.9141 | 0.31552 | 2.1814 | 6.9136 | 0.31552 | 4.515% | 0.018466 | 0.017552 | 2578.2566 | 462.9869 | 204.7374 | 1910.5323 | 2590.057 | 0 | 0 | 2590.057 | 7.089e-05%
2028 | 81 | 81-193AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.28938 | 8 | 100% | 0.44576 | 14.6% | 0% | 85.4% | 0.0032221 | 0 | 0 | 0.0032221 | 0 | 0.002797 | 0.27204 | 0.010282 | 0.002797 | 0.27204 | 0.010282 | 0.0032698 | 0.31802 | 0.010282 | 0.7228% | 0.0011408 | 0.0010843 | 390.747 | 0.25109 | 87.3722 | 303.1238 | 408.1247 | 0 | 0 | 408.1247 | 1.063e-07%
2028 | 170 | 170-42 | Tier-1 | Non-HFTD---10 | 4--2 | 2.6307 | 74 | 100% | 23.9542 | 86.3% | 7.76% | 5.937% | 1.0233 | 0 | 0 | 1.0233 | 0 | 0.88831 | 2.4731 | 0.35919 | 0.88831 | 2.4731 | 0.35919 | 1.0384 | 2.8911 | 0.35919 | 4.272% | 0.037594 | 0.035733 | 637.182 | 77.2313 | 106.2759 | 453.6748 | 641.7271 | 0 | 0 | 641.7271 | 3.375e-05%
2028 | 233 | 233-86F | Tier-2 | Tier-2---8 | 5--5 | 17.4522 | 914 | 100% | 2341.6741 | 85.9% | 13.6% | 0.4998% | 99.5721 | 0 | 0 | 99.5721 | 0 | 86.435 | 16.4069 | 5.2682 | 86.435 | 16.4069 | 5.2682 | 101.0435 | 19.1798 | 5.2682 | 4.252% | 0.1204 | 0.11444 | 19449.7342 | 2690.1535 | 2433.0497 | 14326.531 | 19592.5279 | 0 | 0 | 19592.5279 | 0.003284%
2028 | 521 | CB 521 | Tier-2 | Tier-2---20 | 3--1 | 0.41062 | 17 | 100% | 12.2832 | 16.79% | 81.3% | 1.905% | 0.1021 | 0 | 0 | 0.1021 | 0 | 0.088634 | 0.38602 | 0.22961 | 0.088634 | 0.38602 | 0.22961 | 0.10361 | 0.45127 | 0.22961 | 0.8313% | 0.025917 | 0.024634 | 473.952 | 7.4349 | 392.0671 | 74.45 | 494.4894 | 0 | 0 | 494.4894 | 3.367e-06%
2028 | 72 | 72-12F | Tier-1 | Non-HFTD---19 | 1--1 | 0.23446 | 7 | 100% | 0.35888 | 36.92% | 0% | 63.08% | 0.0065581 | 0 | 0 | 0.0065581 | 0 | 0.0056929 | 0.22042 | 0.025828 | 0.0056929 | 0.22042 | 0.025828 | 0.0066551 | 0.25767 | 0.025828 | 1.827% | 0.0007194 | 0.00068379 | 498.8599 | 8.4651 | 162.404 | 327.9909 | 515.2486 | 0 | 0 | 515.2486 | 2.163e-07%
2028 | 792 | 792-1172F | Tier-1 | Non-HFTD---14 | 3--1 | 5.2345 | 273 | 100% | 6.3558 | 40.89% | 0% | 59.11% | 0.12864 | 0 | 0 | 0.12864 | 0 | 0.11167 | 4.9209 | 0.022693 | 0.11167 | 4.9209 | 0.022693 | 0.13055 | 5.7526 | 0.022693 | 2.024% | 0.014697 | 0.013969 | 432.4678 | 0.27436 | 199.5532 | 232.6402 | 445.7806 | 0 | 0 | 445.7806 | 4.242e-06%
2028 | 452 | 452-37AE | Tier-1 | Non-HFTD---5 | 1--5 | 0.40967 | 44 | 100% | 90.6209 | 99.66% | 0% | 0.3391% | 4.4705 | 0 | 0 | 4.4705 | 0 | 3.8807 | 0.38513 | 10.0763 | 3.8807 | 0.38513 | 10.0763 | 4.5366 | 0.45022 | 10.0763 | 4.933% | 0.0017838 | 0.0016955 | 50802.159 | 10626.9011 | 18.8338 | 40156.424 | 50811.1291 | 0 | 0 | 50811.1291 | 0.0001474%
2028 | 90 | 90-24 | Tier-1 | Non-HFTD---7 | 2--3 | 0.60288 | 19 | 100% | 27.778 | 1.28% | 96.39% | 2.335% | 0.017597 | 0 | 0 | 0.017597 | 0 | 0.015275 | 0.56677 | 0.026951 | 0.015275 | 0.56677 | 0.026951 | 0.017857 | 0.66256 | 0.026951 | 0.06335% | 0.0071986 | 0.0068423 | 3858.8091 | 4.7029 | 3414.9982 | 439.108 | 4057.1958 | 0 | 0 | 4057.1958 | 5.803e-07%
2028 | 275 | CB 275 | Tier-1 | Non-HFTD---2 | 3--4 | 3.0089 | 148 | 100% | 206.6235 | 45.85% | 53.34% | 0.8107% | 4.6895 | 0 | 0 | 4.6895 | 0 | 4.0708 | 2.8286 | 1.4391 | 4.0708 | 2.8286 | 1.4391 | 4.7588 | 3.3067 | 1.4391 | 2.27% | 0.025053 | 0.023813 | 8247.3894 | 358.5021 | 5488.4618 | 2400.4254 | 8479.9674 | 0 | 0 | 8479.9674 | 0.0001546%
2028 | 42 | CB 42 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3775 | 32 | 100% | 5.9866 | 70.69% | 0% | 29.31% | 0.20948 | 0 | 0 | 0.20948 | 0 | 0.18184 | 2.235 | 0.081358 | 0.18184 | 2.235 | 0.081358 | 0.21257 | 2.6128 | 0.081358 | 3.499% | 0.00755 | 0.0071763 | 792.9237 | 22.0026 | 447.2899 | 323.6312 | 805.0273 | 0 | 0 | 805.0273 | 6.908e-06%
2028 | 249 | 249-24R | Tier-3 | Tier-3---12 | 5--5 | 15.5693 | 654 | 100% | 3753.23 | 95.85% | 3.876% | 0.273% | 178.0768 | 0 | 0 | 178.0768 | 0 | 154.5823 | 14.6367 | 10.5613 | 154.5823 | 14.6367 | 10.5613 | 180.7085 | 17.1105 | 10.5613 | 4.745% | 0.10094 | 0.09594 | 37183.961 | 6704.4922 | 1334.1553 | 29145.3135 | 37264.3032 | 0 | 0 | 37264.3032 | 0.005872%
2028 | 246 | 246-34R | Tier-3 | Tier-3---12 | 4--5 | 12.821 | 928 | 100% | 3387.0058 | 94.54% | 5.197% | 0.2577% | 158.5107 | 0 | 0 | 158.5107 | 0 | 137.5976 | 12.053 | 11.416 | 137.5976 | 12.053 | 11.416 | 160.8532 | 14.0901 | 11.416 | 4.68% | 0.070488 | 0.066999 | 48050.8143 | 8360.4537 | 2387.5887 | 37302.7719 | 48187.325 | 0 | 0 | 48187.325 | 0.005227%
2028 | 525 | CB 525 | Tier-1 | Non-HFTD---5 | 2--4 | 0.53731 | 44 | 100% | 72.1571 | 17.62% | 81.53% | 0.8516% | 0.62936 | 0 | 0 | 0.62936 | 0 | 0.54632 | 0.50513 | 1.0816 | 0.54632 | 0.50513 | 1.0816 | 0.63866 | 0.5905 | 1.0816 | 0.8722% | 0.0072554 | 0.0068963 | 9945.2959 | 206.1053 | 8187.2341 | 1551.9565 | 10371.9649 | 0 | 0 | 10371.9649 | 2.075e-05%
2028 | 306 | 306-961 | Tier-1 | Non-HFTD---8 | 4--2 | 0.25951 | 21 | 100% | 44.8989 | 37.41% | 62.22% | 0.3782% | 0.83134 | 0 | 0 | 0.83134 | 0 | 0.72165 | 0.24396 | 2.958 | 0.72165 | 0.24396 | 2.958 | 0.84362 | 0.2852 | 2.958 | 1.852% | 0.052982 | 0.050359 | 847.4364 | 49.5718 | 468.5847 | 329.2799 | 875.061 | 0 | 0 | 875.061 | 2.741e-05%
2028 | 287 | CB 287 | Tier-1 | Non-HFTD---4 | 3--4 | 2.9707 | 127 | 100% | 114.6676 | 71.93% | 25.48% | 2.591% | 4.0827 | 0 | 0 | 4.0827 | 0 | 3.5441 | 2.7927 | 1.269 | 3.5441 | 2.7927 | 1.269 | 4.1431 | 3.2647 | 1.269 | 3.56% | 0.015966 | 0.015175 | 7182.079 | 404.9612 | 4312.5318 | 2464.586 | 7287.0718 | 0 | 0 | 7287.0718 | 0.0001346%
2028 | 1094 | CB 1094 | Tier-1 | Non-HFTD---9 | 1--5 | 0.38073 | 5 | 100% | 25.2689 | 98.73% | 0% | 1.267% | 1.235 | 0 | 0 | 1.235 | 0 | 1.072 | 0.35792 | 2.9951 | 1.072 | 0.35792 | 2.9951 | 1.2532 | 0.41841 | 2.9951 | 4.887% | 0.001448 | 0.0013763 | 17450.9081 | 2431.0189 | 2381.051 | 12638.8381 | 17462.4248 | 0 | 0 | 17462.4248 | 4.072e-05%
2028 | 1438 | 1438-333F | Tier-1 | Non-HFTD---20 | 1--1 | 0.44675 | 30 | 100% | 0.3138 | 20.87% | 0% | 79.13% | 0.0032416 | 0 | 0 | 0.0032416 | 0 | 0.0028139 | 0.41999 | 0.0067 | 0.0028139 | 0.41999 | 0.0067 | 0.0032895 | 0.49097 | 0.0067 | 1.033% | 0.0012552 | 0.0011931 | 249.9971 | 2.9701 | 52.7852 | 194.2418 | 260.2993 | 0 | 0 | 260.2993 | 1.069e-07%
2028 | 489 | 489-33 | Tier-1 | Non-HFTD---20 | 1--1 | 1.3928 | 37 | 100% | 0.5266 | 10.19% | 0% | 89.81% | 0.002657 | 0 | 0 | 0.002657 | 0 | 0.0023065 | 1.3094 | 0.0017615 | 0.0023065 | 1.3094 | 0.0017615 | 0.0026963 | 1.5307 | 0.0017615 | 0.5046% | 0.0028464 | 0.0027055 | 185.0048 | 0.12502 | 33.9508 | 150.929 | 193.6574 | 0 | 0 | 193.6574 | 8.762e-08%
2028 | 80 | 80-575R | Tier-1 | Non-HFTD---15 | 1--2 | 1.7536 | 42 | 100% | 3.3604 | 69.22% | 0% | 30.78% | 0.11514 | 0 | 0 | 0.11514 | 0 | 0.099946 | 1.6486 | 0.060625 | 0.099946 | 1.6486 | 0.060625 | 0.11684 | 1.9272 | 0.060625 | 3.426% | 0.0044504 | 0.0042301 | 755.0854 | 6.5404 | 504.3875 | 244.1574 | 767.1901 | 0 | 0 | 767.1901 | 3.797e-06%
2028 | 178 | 178-983AE | Tier-1 | Non-HFTD---9 | 1--5 | 0.24788 | 9 | 100% | 24.3065 | 99.32% | 0% | 0.6782% | 1.195 | 0 | 0 | 1.195 | 0 | 1.0373 | 0.23303 | 4.4515 | 1.0373 | 0.23303 | 4.4515 | 1.2127 | 0.27242 | 4.4515 | 4.916% | 0.00085 | 0.00080793 | 28595.879 | 4615.9311 | 22.2023 | 23957.7456 | 28605.9786 | 0 | 0 | 28605.9786 | 3.941e-05%
2028 | 1001 | 1001-1231F | Tier-2 | Tier-2---15 | 3--3 | 0.094697 | 7 | 100% | 117.1572 | 99.03% | 0.8725% | 0.09309% | 5.7433 | 0 | 0 | 5.7433 | 0 | 4.9855 | 0.089025 | 56.0018 | 4.9855 | 0.089025 | 56.0018 | 5.8282 | 0.10407 | 56.0018 | 4.902% | 0.025088 | 0.023847 | 4669.7772 | 753.5538 | 37.9946 | 3878.2287 | 4672.1255 | 0 | 0 | 4672.1255 | 0.0001894%
2028 | 1448 | CB 1448 | Tier-1 | Non-HFTD---15 | 1--3 | 0.55455 | 52 | 100% | 4.2012 | 88.77% | 0% | 11.23% | 0.18461 | 0 | 0 | 0.18461 | 0 | 0.16026 | 0.52133 | 0.3074 | 0.16026 | 0.52133 | 0.3074 | 0.18734 | 0.60944 | 0.3074 | 4.394% | 0.002261 | 0.0021491 | 1858.0978 | 176.4132 | 558.9214 | 1122.7631 | 1868.9599 | 0 | 0 | 1868.9599 | 6.088e-06%
2028 | 973 | 973-530AE | Tier-3 | Tier-3---17 | 5--3 | 0.03428 | 0 | 100% | 388.0062 | 6.476% | 93.52% | 0.007746% | 1.2438 | 0 | 0 | 1.2438 | 0 | 1.0797 | 0.032227 | 33.5039 | 1.0797 | 0.032227 | 33.5039 | 1.2622 | 0.037674 | 33.5039 | 0.3206% | 0.10542 | 0.1002 | 3680.7214 | 42.8472 | 3148.1936 | 489.6807 | 3859.9917 | 0 | 0 | 3859.9917 | 4.102e-05%
2028 | 740 | 740-856F | Tier-1 | Non-HFTD---16 | 2--1 | 2.888 | 214 | 100% | 2.9768 | 34.05% | 0% | 65.95% | 0.050176 | 0 | 0 | 0.050176 | 0 | 0.043556 | 2.715 | 0.016042 | 0.043556 | 2.715 | 0.016042 | 0.050917 | 3.1739 | 0.016042 | 1.686% | 0.0078388 | 0.0074508 | 379.746 | 4.2927 | 127.0305 | 248.4227 | 392.788 | 0 | 0 | 392.788 | 1.655e-06%
2028 | 578 | 578-242F | Tier-1 | Non-HFTD---3 | 3--4 | 2.7303 | 60 | 100% | 101.2493 | 1.118% | 96.96% | 1.921% | 0.056018 | 0 | 0 | 0.056018 | 0 | 0.048628 | 2.5667 | 0.018945 | 0.048628 | 2.5667 | 0.018945 | 0.056846 | 3.0005 | 0.018945 | 0.05533% | 0.017989 | 0.017099 | 5628.2774 | 9.7279 | 4959.9632 | 658.5863 | 5918.1099 | 0 | 0 | 5918.1099 | 1.847e-06%
2028 | 506 | 506-160AE | Tier-1 | Non-HFTD---19 | 1--2 | 0.047538 | 2 | 100% | 0.28387 | 86.74% | 0% | 13.26% | 0.012188 | 0 | 0 | 0.012188 | 0 | 0.01058 | 0.04469 | 0.23675 | 0.01058 | 0.04469 | 0.23675 | 0.012368 | 0.052244 | 0.23675 | 4.294% | 0.0001712 | 0.00016273 | 1658.1166 | 166.0816 | 438.3656 | 1053.6695 | 1669.5667 | 0 | 0 | 1669.5667 | 4.019e-07%
2028 | 57 | CB 57 | Tier-1 | Non-HFTD---2 | 4--4 | 7.9972 | 102 | 100% | 246.5725 | 13.42% | 83.87% | 2.714% | 1.6375 | 0 | 0 | 1.6375 | 0 | 1.4215 | 7.5182 | 0.18907 | 1.4215 | 7.5182 | 0.18907 | 1.6617 | 8.7888 | 0.18907 | 0.6641% | 0.034392 | 0.03269 | 7169.3891 | 7.2057 | 6458.1009 | 704.0825 | 7492.6625 | 0 | 0 | 7492.6625 | 5.4e-05%
2028 | 781 | CB 781 | Tier-1 | Non-HFTD---4 | 3--4 | 3.2938 | 134 | 100% | 155.4252 | 25.13% | 72.94% | 1.931% | 1.9333 | 0 | 0 | 1.9333 | 0 | 1.6782 | 3.0965 | 0.54197 | 1.6782 | 3.0965 | 0.54197 | 1.9618 | 3.6198 | 0.54197 | 1.244% | 0.021159 | 0.020111 | 7345.7215 | 11.4899 | 6707.1006 | 627.1309 | 7632.1422 | 0 | 0 | 7632.1422 | 6.375e-05%
2028 | 57 | 57-1292F | Tier-1 | Non-HFTD---9 | 2--2 | 0.68467 | 37 | 100% | 21.0439 | 0.2676% | 97.17% | 2.561% | 0.0027876 | 0 | 0 | 0.0027876 | 0 | 0.0024198 | 0.64366 | 0.0037594 | 0.0024198 | 0.64366 | 0.0037594 | 0.0028288 | 0.75245 | 0.0037594 | 0.01325% | 0.012624 | 0.011999 | 1666.9469 | 1.8812 | 1483.5097 | 181.556 | 1753.5256 | 0 | 0 | 1753.5256 | 9.192e-08%
2028 | 907 | 907-2820R | Tier-3 | Tier-3---10 | 4--5 | 2.4583 | 117 | 100% | 6348.4755 | 99.98% | 0.008026% | 0.01607% | 314.1738 | 0 | 0 | 314.1738 | 0 | 272.7233 | 2.3111 | 118.007 | 272.7233 | 2.3111 | 118.007 | 318.8167 | 2.7017 | 118.007 | 4.949% | 0.082479 | 0.078396 | 76970.9977 | 15788.3869 | 6.9606 | 61175.6502 | 76971.9637 | 0 | 0 | 76971.9637 | 0.01036%
2028 | 723 | 723-793F | Tier-1 | Non-HFTD---20 | 1--1 | 0.16136 | 30 | 100% | 0.15365 | 52.88% | 0% | 47.12% | 0.004022 | 0 | 0 | 0.004022 | 0 | 0.0034914 | 0.1517 | 0.023015 | 0.0034914 | 0.1517 | 0.023015 | 0.0040815 | 0.17734 | 0.023015 | 2.618% | 0.0004994 | 0.00047468 | 307.6774 | 26.5 | 14.647 | 266.5305 | 315.2275 | 0 | 0 | 315.2275 | 1.326e-07%
2028 | 1039 | 1039-13 | Tier-2 | Tier-2---3 | 5--5 | 16.5898 | 1848 | 100% | 15957.1711 | 97.45% | 2.471% | 0.0752% | 769.7688 | 0 | 0 | 769.7688 | 0 | 668.2095 | 15.5961 | 42.8447 | 668.2095 | 15.5961 | 42.8447 | 781.1445 | 18.232 | 42.8447 | 4.824% | 0.1351 | 0.12841 | 118113.2514 | 24651.3232 | 2725.8666 | 90736.0616 | 118269.8643 | 0 | 0 | 118269.8643 | 0.02538%
2028 | 474 | 474-22AE | Tier-1 | Non-HFTD---1 | 4--5 | 9.6011 | 965 | 100% | 6435.9834 | 99.89% | 0% | 0.1146% | 318.2162 | 0 | 0 | 318.2162 | 0 | 276.2324 | 9.026 | 30.604 | 276.2324 | 9.026 | 30.604 | 322.9188 | 10.5515 | 30.604 | 4.944% | 0.046635 | 0.044327 | 138007.5774 | 24328.5202 | 121.2373 | 113557.8199 | 138015.8115 | 0 | 0 | 138015.8115 | 0.01049%
2028 | 185 | 185-51F | Tier-2 | Tier-2---7 | 4--5 | 8.9873 | 712 | 100% | 1723.9707 | 91.93% | 7.724% | 0.3493% | 78.4468 | 0 | 0 | 78.4468 | 0 | 68.097 | 8.449 | 8.0598 | 68.097 | 8.449 | 8.0598 | 79.6061 | 9.8769 | 8.0598 | 4.55% | 0.048222 | 0.045835 | 35751.0066 | 6382.5174 | 2576.5393 | 26791.9499 | 35901.3238 | 0 | 0 | 35901.3238 | 0.002587%
2028 | NO1 | CB NO1 | Tier-1 | Non-HFTD---20 | 1--1 | 0.16004 | 5 | 100% | 0.11186 | 6.282% | 0% | 93.72% | 0.00034784 | 0 | 0 | 0.00034784 | 0 | 0.00030195 | 0.15046 | 0.0020069 | 0.00030195 | 0.15046 | 0.0020069 | 0.00035298 | 0.17589 | 0.0020069 | 0.311% | 0.0004254 | 0.00040434 | 262.9516 | 0.18543 | 38.9048 | 223.8613 | 275.7853 | 0 | 0 | 275.7853 | 1.147e-08%
2028 | PE1 | CB PE1 | Tier-3 | Tier-3---13 | 5--4 | 6.7553 | 1558 | 100% | 3027.5479 | 94.73% | 5.109% | 0.164% | 141.961 | 0 | 0 | 141.961 | 0 | 123.2314 | 6.3507 | 19.4044 | 123.2314 | 6.3507 | 19.4044 | 144.0589 | 7.424 | 19.4044 | 4.689% | 0.24168 | 0.22972 | 12527.0623 | 1785.3868 | 582.212 | 10159.4635 | 12561.4639 | 0 | 0 | 12561.4639 | 0.004681%
2028 | 1160 | CB 1160 | Tier-2 | Tier-2---22 | 4--1 | 0.16307 | 3 | 100% | 2.3826 | 9.042% | 83.57% | 7.391% | 0.010664 | 0 | 0 | 0.010664 | 0 | 0.0092569 | 0.1533 | 0.060384 | 0.0092569 | 0.1533 | 0.060384 | 0.010821 | 0.17921 | 0.060384 | 0.4476% | 0.059368 | 0.05643 | 40.1318 | 0.36722 | 29.4839 | 10.2807 | 42.0328 | 0 | 0 | 42.0328 | 3.517e-07%
2028 | 448 | 448-1196F | Tier-3 | Tier-3---20 | 1--5 | 0.038636 | 0 | 100% | 16.696 | 99.41% | 0% | 0.5907% | 0.82157 | 0 | 0 | 0.82157 | 0 | 0.71318 | 0.036322 | 19.6348 | 0.71318 | 0.036322 | 19.6348 | 0.83371 | 0.042461 | 19.6348 | 4.921% | 0.0002432 | 0.00023116 | 68651.2414 | 9671.9172 | 309.329 | 58669.9952 | 68672.3598 | 0 | 0 | 68672.3598 | 2.709e-05%
2028 | 536 | CB 536 | Tier-2 | Tier-2---18 | 4--2 | 1.5002 | 51 | 100% | 54.1099 | 76.19% | 21.99% | 1.82% | 2.0408 | 0 | 0 | 2.0408 | 0 | 1.7715 | 1.4103 | 1.2561 | 1.7715 | 1.4103 | 1.2561 | 2.0709 | 1.6487 | 1.2561 | 3.772% | 0.063476 | 0.060334 | 852.4497 | 102.6719 | 151.462 | 598.3157 | 863.0188 | 0 | 0 | 863.0188 | 6.73e-05%
2028 | 252 | 252-277F | Tier-1 | Non-HFTD---15 | 1--2 | 0.90889 | 30 | 100% | 3.3511 | 64.95% | 0% | 35.05% | 0.10774 | 0 | 0 | 0.10774 | 0 | 0.093522 | 0.85445 | 0.10945 | 0.093522 | 0.85445 | 0.10945 | 0.10933 | 0.99886 | 0.10945 | 3.215% | 0.0037008 | 0.0035176 | 905.5022 | 85.5311 | 154.0815 | 665.8897 | 922.0312 | 0 | 0 | 922.0312 | 3.553e-06%
2028 | 1286 | CB 1286 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1557 | 55 | 100% | 2.6947 | 57.45% | 0% | 42.55% | 0.076626 | 0 | 0 | 0.076626 | 0 | 0.066516 | 1.0864 | 0.061225 | 0.066516 | 1.0864 | 0.061225 | 0.077758 | 1.27 | 0.061225 | 2.844% | 0.0043234 | 0.0041094 | 623.2816 | 31.002 | 192.2211 | 400.0585 | 637.0941 | 0 | 0 | 637.0941 | 2.527e-06%
2028 | 161 | 161-974F | Tier-1 | Non-HFTD---15 | 1--2 | 1.2625 | 35 | 100% | 2.9871 | 73.28% | 0% | 26.72% | 0.10836 | 0 | 0 | 0.10836 | 0 | 0.094063 | 1.1869 | 0.07925 | 0.094063 | 1.1869 | 0.07925 | 0.10996 | 1.3875 | 0.07925 | 3.628% | 0.0046736 | 0.0044423 | 639.1485 | 67.3315 | 71.5481 | 500.2689 | 648.0412 | 0 | 0 | 648.0412 | 3.573e-06%
2028 | 770 | 770-250R | Tier-1 | Non-HFTD---13 | 1--3 | 0.94323 | 92 | 100% | 8.2742 | 91.72% | 0% | 8.276% | 0.37568 | 0 | 0 | 0.37568 | 0 | 0.32611 | 0.88673 | 0.36777 | 0.32611 | 0.88673 | 0.36777 | 0.38123 | 1.0366 | 0.36777 | 4.54% | 0.003255 | 0.0030939 | 2542.0097 | 485.388 | 24.5872 | 2032.0344 | 2552.9659 | 0 | 0 | 2552.9659 | 1.239e-05%
2028 | 182 | 182-2240F | Tier-2 | Tier-2---2 | 5--5 | 13.8138 | 967 | 100% | 11917.1989 | 94.29% | 5.651% | 0.05821% | 556.2232 | 0 | 0 | 556.2232 | 0 | 482.838 | 12.9864 | 37.1803 | 482.838 | 12.9864 | 37.1803 | 564.4431 | 15.1812 | 37.1803 | 4.667% | 0.1455 | 0.1383 | 81902.6703 | 23758.3803 | 4446.6021 | 53697.6879 | 82146.1822 | 0 | 0 | 82146.1822 | 0.01834%
2028 | 188 | 188-11F | Tier-2 | Tier-2---7 | 3--5 | 5.0004 | 427 | 100% | 2209.344 | 99.86% | 0% | 0.1429% | 109.2062 | 0 | 0 | 109.2062 | 0 | 94.7981 | 4.7008 | 20.1662 | 94.7981 | 4.7008 | 20.1662 | 110.8201 | 5.4953 | 20.1662 | 4.943% | 0.019333 | 0.018376 | 114277.2032 | 24326.824 | 78.3726 | 89872.0066 | 114285.7081 | 0 | 0 | 114285.7081 | 0.003601%
2028 | 175 | CB 175 | Tier-2 | Tier-2---10 | 5--4 | 2.8512 | 275 | 100% | 1236.5075 | 84.14% | 15.66% | 0.203% | 51.5004 | 0 | 0 | 51.5004 | 0 | 44.7057 | 2.6804 | 16.6788 | 44.7057 | 2.6804 | 16.6788 | 52.2615 | 3.1334 | 16.6788 | 4.165% | 0.16723 | 0.15895 | 7393.9644 | 1133.6762 | 1185.8912 | 5074.397 | 7455.0304 | 0 | 0 | 7455.0304 | 0.001698%
2028 | 591 | 591-1594R | Tier-2 | Tier-2---12 | 4--4 | 3.0667 | 69 | 100% | 519.9571 | 96.32% | 3.27% | 0.4047% | 24.792 | 0 | 0 | 24.792 | 0 | 21.5211 | 2.883 | 7.4648 | 21.5211 | 2.883 | 7.4648 | 25.1584 | 3.3703 | 7.4648 | 4.768% | 0.047196 | 0.04486 | 11017.0212 | 2112.3756 | 330.6194 | 8574.0262 | 11038.1069 | 0 | 0 | 11038.1069 | 0.0008175%
2028 | 909 | 909-805R | Tier-2 | Tier-2---1 | 5--5 | 13.4184 | 1026 | 100% | 32313.161 | 99.26% | 0.708% | 0.02831% | 1587.725 | 0 | 0 | 1587.725 | 0 | 1378.2488 | 12.6146 | 109.2582 | 1378.2488 | 12.6146 | 109.2582 | 1611.1885 | 14.7466 | 109.2582 | 4.914% | 0.28921 | 0.27489 | 111728.904 | 24066.0497 | 703.1475 | 86959.7068 | 111771.744 | 0 | 0 | 111771.744 | 0.05236%
2028 | 524 | CB 524 | Tier-3 | Tier-3---17 | 3--5 | 3.4998 | 176 | 100% | 481.3309 | 94.25% | 5.298% | 0.4514% | 22.456 | 0 | 0 | 22.456 | 0 | 19.4933 | 3.2901 | 5.9247 | 19.4933 | 3.2901 | 5.9247 | 22.7878 | 3.8462 | 5.9247 | 4.665% | 0.018139 | 0.017241 | 26536.2736 | 4900.6821 | 2268.1123 | 19367.4792 | 26615.7308 | 0 | 0 | 26615.7308 | 0.0007405%
2028 | 972 | 972-1590F | Tier-3 | Tier-3---2 | 5--5 | 20.6608 | 1532 | 100% | 23409.1539 | 98.39% | 1.548% | 0.05965% | 1140.1279 | 0 | 0 | 1140.1279 | 0 | 989.7054 | 19.4232 | 50.9548 | 989.7054 | 19.4232 | 50.9548 | 1156.9769 | 22.7059 | 50.9548 | 4.87% | 0.17603 | 0.16732 | 132982.6796 | 26774.8666 | 1933.0349 | 104274.7781 | 133093.9956 | 0 | 0 | 133093.9956 | 0.0376%
2028 | 908 | 908-2055F | Tier-3 | Tier-3---2 | 5--5 | 11.56 | 909 | 100% | 22564.0783 | 99.08% | 0.8792% | 0.03652% | 1106.6937 | 0 | 0 | 1106.6937 | 0 | 960.6823 | 10.8676 | 88.3987 | 960.6823 | 10.8676 | 88.3987 | 1123.0485 | 12.7044 | 88.3987 | 4.905% | 0.20355 | 0.19347 | 110854.0623 | 21094.0064 | 955.5801 | 88804.4759 | 110906.9288 | 0 | 0 | 110906.9288 | 0.03649%
2028 | 441 | 441-23R | Tier-3 | Tier-3---11 | 5--4 | 5.1261 | 362 | 100% | 3518.0204 | 97.45% | 2.468% | 0.07959% | 169.706 | 0 | 0 | 169.706 | 0 | 147.3159 | 4.8191 | 30.5692 | 147.3159 | 4.8191 | 30.5692 | 172.214 | 5.6336 | 30.5692 | 4.824% | 0.54783 | 0.52071 | 6421.7327 | 899.4842 | 135.0433 | 5387.2052 | 6430.2517 | 0 | 0 | 6430.2517 | 0.005596%
2028 | 450 | 450-1854 | Tier-2 | Tier-2---9 | 4--4 | 2.1386 | 164 | 100% | 1132.2887 | 95.25% | 4.625% | 0.1242% | 53.3866 | 0 | 0 | 53.3866 | 0 | 46.343 | 2.0105 | 23.0506 | 46.343 | 2.0105 | 23.0506 | 54.1755 | 2.3503 | 23.0506 | 4.715% | 0.079085 | 0.07517 | 14317.3642 | 2563.412 | 613.0615 | 11140.8906 | 14352.7731 | 0 | 0 | 14352.7731 | 0.00176%
2028 | 353 | 353-1429R | Tier-2 | Tier-2---6 | 5--5 | 5.9518 | 999 | 100% | 9221.8022 | 97.49% | 2.457% | 0.05523% | 445.0117 | 0 | 0 | 445.0117 | 0 | 386.2992 | 5.5952 | 69.0406 | 386.2992 | 5.5952 | 69.0406 | 451.5881 | 6.5409 | 69.0406 | 4.826% | 0.12141 | 0.1154 | 75954.4937 | 16555.9174 | 1751.4473 | 57647.129 | 76053.8635 | 0 | 0 | 76053.8635 | 0.01467%
2028 | 1438 | 1438-331F | Tier-1 | Non-HFTD---19 | 1--1 | 0.11725 | 0 | 100% | 0.12483 | 14.96% | 0% | 85.04% | 0.00092462 | 0 | 0 | 0.00092462 | 0 | 0.00080263 | 0.11023 | 0.0072813 | 0.00080263 | 0.11023 | 0.0072813 | 0.00093828 | 0.12886 | 0.0072813 | 0.7407% | 0.000355 | 0.00033743 | 351.6369 | 0.225 | 79.7806 | 271.6313 | 367.2091 | 0 | 0 | 367.2091 | 3.049e-08%
2028 | 161 | 161-991F | Tier-1 | Non-HFTD---12 | 3--1 | 9.0516 | 207 | 100% | 10.7177 | 44.4% | 0% | 55.6% | 0.23557 | 0 | 0 | 0.23557 | 0 | 0.20449 | 8.5094 | 0.024031 | 0.20449 | 8.5094 | 0.024031 | 0.23905 | 9.9476 | 0.024031 | 2.198% | 0.025268 | 0.024017 | 424.1613 | 21.5449 | 118.7087 | 283.9078 | 436.4423 | 0 | 0 | 436.4423 | 7.768e-06%
2028 | 445 | 445-897R | Tier-2 | Tier-2---10 | 5--3 | 1.0659 | 30 | 100% | 1351.7747 | 97.24% | 2.711% | 0.04647% | 65.0678 | 0 | 0 | 65.0678 | 0 | 56.4831 | 1.0021 | 56.3672 | 56.4831 | 1.0021 | 56.3672 | 66.0294 | 1.1714 | 56.3672 | 4.814% | 0.75637 | 0.71893 | 1787.1928 | 255.4993 | 53.1623 | 1478.5313 | 1789.7592 | 0 | 0 | 1789.7592 | 0.002146%
2028 | 236 | 236-1563R | Tier-3 | Tier-3---13 | 5--4 | 3.7138 | 186 | 100% | 2260.6624 | 98.61% | 1.288% | 0.1052% | 110.3442 | 0 | 0 | 110.3442 | 0 | 95.786 | 3.4914 | 27.4349 | 95.786 | 3.4914 | 27.4349 | 111.9749 | 4.0815 | 27.4349 | 4.881% | 0.17215 | 0.16363 | 13131.72 | 2138.3841 | 138.0778 | 10855.258 | 13141.245 | 0 | 0 | 13141.245 | 0.003639%
2028 | 713 | 713-169 | Tier-1 | Non-HFTD---19 | 1--1 | 0.36193 | 0 | 100% | 0.56535 | 24.4% | 0% | 75.6% | 0.0068286 | 0 | 0 | 0.0068286 | 0 | 0.0059277 | 0.34025 | 0.017421 | 0.0059277 | 0.34025 | 0.017421 | 0.0069295 | 0.39776 | 0.017421 | 1.208% | 0.0014716 | 0.0013988 | 384.1744 | 11.8523 | 47.4609 | 324.8612 | 399.2994 | 0 | 0 | 399.2994 | 2.252e-07%
2028 | 176 | 176-197F | Tier-3 | Tier-3---5 | 5--5 | 13.767 | 1106 | 100% | 13172.958 | 96.8% | 3.124% | 0.0728% | 631.2162 | 0 | 0 | 631.2162 | 0 | 547.9368 | 12.9424 | 42.3366 | 547.9368 | 12.9424 | 42.3366 | 640.5444 | 15.1298 | 42.3366 | 4.792% | 0.23242 | 0.22091 | 56678.2637 | 12110.4711 | 1632.9775 | 42934.8152 | 56772.6237 | 0 | 0 | 56772.6237 | 0.02082%
2028 | 92 | 92-619F | Tier-2 | Tier-2---14 | 3--4 | 3.3373 | 77 | 100% | 202.8689 | 46.88% | 52.08% | 1.034% | 4.708 | 0 | 0 | 4.708 | 0 | 4.0869 | 3.1374 | 1.3026 | 4.0869 | 3.1374 | 1.3026 | 4.7776 | 3.6677 | 1.3026 | 2.321% | 0.015617 | 0.014844 | 12990.5937 | 1279.3739 | 6200.2786 | 5510.9412 | 13349.9397 | 0 | 0 | 13349.9397 | 0.0001553%
2028 | 1021 | 1021-1748F | Tier-3 | Tier-3---2 | 5--5 | 17.727 | 1516 | 100% | 35156.1224 | 99.02% | 0.9436% | 0.03662% | 1723.1698 | 0 | 0 | 1723.1698 | 0 | 1495.8237 | 16.6652 | 89.7573 | 1495.8237 | 16.6652 | 89.7573 | 1748.6349 | 19.4818 | 89.7573 | 4.901% | 0.16564 | 0.15744 | 212249.5403 | 39094.5522 | 1887.9434 | 171267.0447 | 212357.8902 | 0 | 0 | 212357.8902 | 0.05682%
2028 | 231 | CB 231 | Tier-2 | Tier-2---7 | 4--5 | 8.6068 | 720 | 100% | 2499.974 | 99.29% | 0.4807% | 0.2332% | 122.8653 | 0 | 0 | 122.8653 | 0 | 106.6551 | 8.0913 | 13.1815 | 106.6551 | 8.0913 | 13.1815 | 124.681 | 9.4588 | 13.1815 | 4.915% | 0.037573 | 0.035713 | 66537.1573 | 11726.385 | 695.1024 | 54115.6699 | 66561.8947 | 0 | 0 | 66561.8947 | 0.004052%
2028 | 928 | 928-20 | Tier-2 | Tier-2---20 | 4--2 | 0.15818 | 49 | 100% | 27.1749 | 93.08% | 6.522% | 0.4024% | 1.252 | 0 | 0 | 1.252 | 0 | 1.0868 | 0.1487 | 7.3087 | 1.0868 | 0.1487 | 7.3087 | 1.2705 | 0.17384 | 7.3087 | 4.607% | 0.044362 | 0.042166 | 612.5656 | 93.209 | 34.6926 | 484.664 | 614.7746 | 0 | 0 | 614.7746 | 4.129e-05%
2028 | AD2 | CB AD2 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3572 | 43 | 100% | 40.3722 | 2.888% | 92.69% | 4.427% | 0.057707 | 0 | 0 | 0.057707 | 0 | 0.050093 | 2.216 | 0.022605 | 0.050093 | 2.216 | 0.022605 | 0.05856 | 2.5905 | 0.022605 | 0.1429% | 0.011539 | 0.010968 | 3498.6997 | 6.8788 | 3053.1148 | 438.7061 | 3675.6431 | 0 | 0 | 3675.6431 | 1.903e-06%
2028 | 90 | 90-44AE | Tier-1 | Non-HFTD---4 | 3--4 | 3.5829 | 134 | 100% | 101.3703 | 11.74% | 85.7% | 2.562% | 0.58913 | 0 | 0 | 0.58913 | 0 | 0.51141 | 3.3683 | 0.15183 | 0.51141 | 3.3683 | 0.15183 | 0.59784 | 3.9376 | 0.15183 | 0.5812% | 0.015099 | 0.014352 | 6713.5305 | 6.5653 | 6082.8987 | 624.0665 | 7022.1078 | 0 | 0 | 7022.1078 | 1.943e-05%
2028 | 239 | 239-89R | Tier-3 | Tier-3---17 | 4--4 | 2.8193 | 63 | 100% | 376.4251 | 98.76% | 0.8388% | 0.4045% | 18.4014 | 0 | 0 | 18.4014 | 0 | 15.9736 | 2.6504 | 6.0268 | 15.9736 | 2.6504 | 6.0268 | 18.6733 | 3.0984 | 6.0268 | 4.888% | 0.064786 | 0.061579 | 5810.3033 | 876.5504 | 280.4988 | 4653.254 | 5814.0653 | 0 | 0 | 5814.0653 | 0.0006068%
2028 | EOS3 | CB EOS3 | Tier-1 | Non-HFTD---11 | 2--3 | 2.4386 | 83 | 100% | 14.1826 | 87.38% | 0% | 12.62% | 0.61345 | 0 | 0 | 0.61345 | 0 | 0.53251 | 2.2925 | 0.23228 | 0.53251 | 2.2925 | 0.23228 | 0.62251 | 2.68 | 0.23228 | 4.325% | 0.0075404 | 0.0071672 | 1880.8804 | 242.4617 | 179.6503 | 1458.7683 | 1893.2412 | 0 | 0 | 1893.2412 | 2.023e-05%
2028 | 392 | 392-23F | Tier-1 | Non-HFTD---2 | 5--3 | 2.6426 | 50 | 100% | 466.525 | 0.9229% | 98.62% | 0.4561% | 0.21313 | 0 | 0 | 0.21313 | 0 | 0.18501 | 2.4843 | 0.074471 | 0.18501 | 2.4843 | 0.074471 | 0.21628 | 2.9042 | 0.074471 | 0.04568% | 0.10259 | 0.097512 | 4547.4707 | 15.3107 | 3769.5708 | 762.5892 | 4782.1075 | 0 | 0 | 4782.1075 | 7.028e-06%
2028 | 949 | 949-22R | Tier-1 | Non-HFTD---12 | 3--2 | 5.1989 | 436 | 100% | 9.2316 | 56.06% | 0% | 43.94% | 0.25619 | 0 | 0 | 0.25619 | 0 | 0.22239 | 4.8875 | 0.045502 | 0.22239 | 4.8875 | 0.045502 | 0.25998 | 5.7135 | 0.045502 | 2.775% | 0.016401 | 0.015589 | 562.8643 | 27.9703 | 168.0106 | 366.8833 | 575.7433 | 0 | 0 | 575.7433 | 8.448e-06%
2028 | 245 | 245-486 | Tier-1 | Non-HFTD---2 | 4--4 | 4.3474 | 192 | 100% | 294.2309 | 35.69% | 63.39% | 0.9197% | 5.1981 | 0 | 0 | 5.1981 | 0 | 4.5123 | 4.087 | 1.1041 | 4.5123 | 4.087 | 1.1041 | 5.2749 | 4.7777 | 1.1041 | 1.767% | 0.039483 | 0.037529 | 7452.0521 | 531.8785 | 4332.7245 | 2587.4492 | 7701.6294 | 0 | 0 | 7701.6294 | 0.0001714%
2028 | 452 | 452-39AE | Tier-1 | Non-HFTD---1 | 2--5 | 1.292 | 196 | 100% | 261.2424 | 99.61% | 0% | 0.3884% | 12.8813 | 0 | 0 | 12.8813 | 0 | 11.1818 | 1.2146 | 9.2059 | 11.1818 | 1.2146 | 9.2059 | 13.0716 | 1.4199 | 9.2059 | 4.931% | 0.0055772 | 0.0053011 | 46841.1346 | 13719.2411 | 19.0906 | 33102.8029 | 46850.6095 | 0 | 0 | 46850.6095 | 0.0004248%
2028 | 233 | 233-81F | Tier-2 | Tier-2---12 | 3--5 | 4.0824 | 476 | 100% | 447.7794 | 94.96% | 4.349% | 0.694% | 21.0474 | 0 | 0 | 21.0474 | 0 | 18.2705 | 3.8378 | 4.7606 | 18.2705 | 3.8378 | 4.7606 | 21.3584 | 4.4865 | 4.7606 | 4.7% | 0.02204 | 0.020949 | 20316.8521 | 3103.6732 | 873.0875 | 16340.0914 | 20370.2068 | 0 | 0 | 20370.2068 | 0.0006941%
2028 | 231 | 231-1136R | Tier-2 | Tier-2---7 | 4--5 | 13.2557 | 1044 | 100% | 2730.9177 | 98.3% | 1.373% | 0.325% | 132.8848 | 0 | 0 | 132.8848 | 0 | 115.3527 | 12.4617 | 9.2566 | 115.3527 | 12.4617 | 9.2566 | 134.8486 | 14.5678 | 9.2566 | 4.866% | 0.054655 | 0.051949 | 49966.8413 | 8713.2838 | 1199.3075 | 40054.25 | 50011.031 | 0 | 0 | 50011.031 | 0.004382%
2028 | 474 | CB 474 | Tier-1 | Non-HFTD---1 | 3--5 | 4.6676 | 497 | 100% | 794.8798 | 99.6% | 0% | 0.3957% | 39.1908 | 0 | 0 | 39.1908 | 0 | 34.0202 | 4.388 | 7.753 | 34.0202 | 4.388 | 7.753 | 39.77 | 5.1296 | 7.753 | 4.93% | 0.016088 | 0.015291 | 49409.4676 | 7937.2559 | 481.7871 | 40990.4246 | 49419.6498 | 0 | 0 | 49419.6498 | 0.001292%
2028 | 164 | CB 164 | Tier-1 | Non-HFTD---13 | 1--2 | 1.583 | 41 | 100% | 5.3562 | 79.49% | 0% | 20.51% | 0.21076 | 0 | 0 | 0.21076 | 0 | 0.18295 | 1.4882 | 0.12294 | 0.18295 | 1.4882 | 0.12294 | 0.21388 | 1.7397 | 0.12294 | 3.935% | 0.0047404 | 0.0045058 | 1129.913 | 8.1525 | 869.9018 | 251.8587 | 1141.9803 | 0 | 0 | 1141.9803 | 6.95e-06%
2028 | 1106 | CB 1106 | Tier-2 | Tier-2---7 | 4--5 | 1.2773 | 61 | 100% | 1646.9837 | 34.54% | 65.41% | 0.04829% | 28.1563 | 0 | 0 | 28.1563 | 0 | 24.4415 | 1.2008 | 20.355 | 24.4415 | 1.2008 | 20.355 | 28.5724 | 1.4037 | 20.355 | 1.71% | 0.070774 | 0.067271 | 23270.9618 | 1321.744 | 13847.343 | 8101.8748 | 24064.3118 | 0 | 0 | 24064.3118 | 0.0009285%
2028 | 441 | 441-27R | Tier-3 | Tier-3---9 | 5--4 | 7.3796 | 119 | 100% | 4750.1268 | 98% | 1.916% | 0.08125% | 230.4346 | 0 | 0 | 230.4346 | 0 | 200.0322 | 6.9376 | 28.8332 | 200.0322 | 6.9376 | 28.8332 | 233.8399 | 8.1101 | 28.8332 | 4.851% | 0.55752 | 0.52992 | 8520.0828 | 1214.2934 | 144.8205 | 7160.9689 | 8528.9458 | 0 | 0 | 8528.9458 | 0.007599%
2028 | DS1 | CB DS1 | Tier-1 | Non-HFTD---12 | 3--2 | 1.7008 | 75 | 100% | 13.0351 | 8.296% | 84.41% | 7.29% | 0.053527 | 0 | 0 | 0.053527 | 0 | 0.046465 | 1.5989 | 0.02906 | 0.046465 | 1.5989 | 0.02906 | 0.054318 | 1.8691 | 0.02906 | 0.4106% | 0.014723 | 0.013994 | 885.347 | 9.9559 | 707.4464 | 167.9447 | 927.6291 | 0 | 0 | 927.6291 | 1.765e-06%
2028 | 182 | 182-2254R | Tier-2 | Tier-2---11 | 5--4 | 0.87803 | 17 | 100% | 655.8009 | 99.14% | 0.7615% | 0.1019% | 32.1819 | 0 | 0 | 32.1819 | 0 | 27.936 | 0.82544 | 33.8438 | 27.936 | 0.82544 | 33.8438 | 32.6575 | 0.96495 | 33.8438 | 4.907% | 0.10223 | 0.097167 | 6415.1442 | 1053.2232 | 42.7228 | 5319.1982 | 6418.0287 | 0 | 0 | 6418.0287 | 0.001061%
2028 | 554 | CB 554 | Tier-1 | Non-HFTD---15 | 1--2 | 0.48106 | 1 | 100% | 2.8878 | 78.27% | 0% | 21.73% | 0.11188 | 0 | 0 | 0.11188 | 0 | 0.09712 | 0.45225 | 0.21475 | 0.09712 | 0.45225 | 0.21475 | 0.11353 | 0.52868 | 0.21475 | 3.874% | 0.0020388 | 0.0019379 | 1416.4094 | 124.7784 | 373.0089 | 918.622 | 1432.4394 | 0 | 0 | 1432.4394 | 3.689e-06%
2028 | 452 | 452-717 | Tier-2 | Tier-2---19 | 1--5 | 0.29487 | 27 | 100% | 24.802 | 99.04% | 0% | 0.9608% | 1.2159 | 0 | 0 | 1.2159 | 0 | 1.0555 | 0.2772 | 3.8076 | 1.0555 | 0.2772 | 3.8076 | 1.2339 | 0.32405 | 3.8076 | 4.902% | 0.000973 | 0.00092484 | 25490.2561 | 9086.828 | 25.5586 | 16377.8695 | 25503.0101 | 0 | 0 | 25503.0101 | 4.01e-05%
2028 | 250 | 250-47 | Tier-1 | Non-HFTD---19 | 1--2 | 0.076894 | 8 | 100% | 0.26608 | 73.81% | 0% | 26.19% | 0.009721 | 0 | 0 | 0.009721 | 0 | 0.0084384 | 0.072288 | 0.11673 | 0.0084384 | 0.072288 | 0.11673 | 0.0098646 | 0.084506 | 0.11673 | 3.653% | 0.0002818 | 0.00026785 | 944.2218 | 112.5399 | 22.9232 | 808.7588 | 957.1024 | 0 | 0 | 957.1024 | 3.206e-07%
2028 | 195 | CB 195 | Tier-1 | Non-HFTD---1 | 4--4 | 2.8899 | 388 | 100% | 363.2496 | 59.46% | 39.93% | 0.6035% | 10.6919 | 0 | 0 | 10.6919 | 0 | 9.2812 | 2.7168 | 3.4162 | 9.2812 | 2.7168 | 3.4162 | 10.8499 | 3.176 | 3.4162 | 2.943% | 0.029402 | 0.027947 | 12354.4195 | 1165.0324 | 4745.6591 | 6443.728 | 12615.2346 | 0 | 0 | 12615.2346 | 0.0003526%
2028 | 597 | CB 597 | Tier-2 | Tier-2---14 | 1--5 | 1.0557 | 113 | 100% | 218.0489 | 99.66% | 0% | 0.3378% | 10.757 | 0 | 0 | 10.757 | 0 | 9.3377 | 0.99245 | 9.4088 | 9.3377 | 0.99245 | 9.4088 | 10.9159 | 1.1602 | 9.4088 | 4.933% | 0.0040332 | 0.0038336 | 54063.4858 | 8115.5826 | 4098.4737 | 41849.4295 | 54072.9953 | 0 | 0 | 54072.9953 | 0.0003547%
2028 | OT2 | CB OT2 | Tier-1 | Non-HFTD---8 | 3--3 | 3.4801 | 92 | 100% | 45.4213 | 3.226% | 91.33% | 5.441% | 0.072536 | 0 | 0 | 0.072536 | 0 | 0.062966 | 3.2717 | 0.019246 | 0.062966 | 3.2717 | 0.019246 | 0.073608 | 3.8246 | 0.019246 | 0.1597% | 0.024647 | 0.023427 | 1842.8901 | 7.4819 | 1565.7674 | 269.6408 | 1935.7675 | 0 | 0 | 1935.7675 | 2.392e-06%
2028 | 968 | 968-476F | Tier-2 | Tier-2---17 | 3--3 | 2.5405 | 13 | 100% | 62.492 | 96.91% | 0.773% | 2.32% | 2.9977 | 0 | 0 | 2.9977 | 0 | 2.6022 | 2.3884 | 1.0895 | 2.6022 | 2.3884 | 1.0895 | 3.042 | 2.792 | 1.0895 | 4.797% | 0.015315 | 0.014557 | 4080.3921 | 1049.3579 | 36.5623 | 2994.4719 | 4086.964 | 0 | 0 | 4086.964 | 9.885e-05%
2028 | RA1 | RA1-402R | Tier-3 | Tier-3---4 | 5--5 | 3.8122 | 504 | 100% | 9339.3378 | 99.33% | 0.6459% | 0.02826% | 459.1808 | 0 | 0 | 459.1808 | 0 | 398.5988 | 3.5838 | 111.2217 | 398.5988 | 3.5838 | 111.2217 | 465.9666 | 4.1895 | 111.2217 | 4.917% | 0.12948 | 0.12307 | 72130.9155 | 12817.7406 | 426.7116 | 58886.4633 | 72156.2385 | 0 | 0 | 72156.2385 | 0.01514%
2028 | 971 | 971-1973R | Tier-3 | Tier-3---4 | 5--5 | 10.9521 | 993 | 100% | 15148.7962 | 99.05% | 0.8967% | 0.0506% | 742.7622 | 0 | 0 | 742.7622 | 0 | 644.766 | 10.2961 | 62.6226 | 644.766 | 10.2961 | 62.6226 | 753.7388 | 12.0362 | 62.6226 | 4.903% | 0.14704 | 0.13976 | 103024.8612 | 19745.1245 | 859.0693 | 82420.6674 | 103075.6848 | 0 | 0 | 103075.6848 | 0.02449%
2028 | 723 | 723-792F | Tier-1 | Non-HFTD---19 | 1--1 | 0.2026 | 9 | 100% | 0.19474 | 41.11% | 0% | 58.89% | 0.0039627 | 0 | 0 | 0.0039627 | 0 | 0.0034399 | 0.19047 | 0.01806 | 0.0034399 | 0.19047 | 0.01806 | 0.0040213 | 0.22266 | 0.01806 | 2.035% | 0.0005522 | 0.00052487 | 352.6648 | 19.2157 | 47.4573 | 285.9917 | 363.4808 | 0 | 0 | 363.4808 | 1.307e-07%
2028 | 161 | CB 161 | Tier-1 | Non-HFTD---11 | 1--3 | 0.78239 | 11 | 100% | 13.2728 | 94.99% | 0% | 5.009% | 0.62409 | 0 | 0 | 0.62409 | 0 | 0.54175 | 0.73552 | 0.73656 | 0.54175 | 0.73552 | 0.73656 | 0.63332 | 0.85983 | 0.73656 | 4.702% | 0.002891 | 0.0027479 | 4591.0843 | 3.1452 | 4363.6333 | 224.3059 | 4603.061 | 0 | 0 | 4603.061 | 2.058e-05%
2028 | 342 | 342-514F | Tier-1 | Non-HFTD---16 | 2--1 | 4.5697 | 173 | 100% | 4.6383 | 28.46% | 0% | 71.54% | 0.065351 | 0 | 0 | 0.065351 | 0 | 0.056728 | 4.296 | 0.013205 | 0.056728 | 4.296 | 0.013205 | 0.066316 | 5.0221 | 0.013205 | 1.409% | 0.013236 | 0.012581 | 350.4217 | 5.7925 | 88.2778 | 256.3514 | 363.4765 | 0 | 0 | 363.4765 | 2.155e-06%
2028 | 334 | 334-21 | Tier-1 | Non-HFTD---2 | 5--3 | 7.2951 | 196 | 100% | 378.2145 | 89.09% | 9.517% | 1.396% | 16.6786 | 0 | 0 | 16.6786 | 0 | 14.4782 | 6.8581 | 2.1111 | 14.4782 | 6.8581 | 2.1111 | 16.9251 | 8.0172 | 2.1111 | 4.41% | 0.11474 | 0.10906 | 3296.3029 | 544.604 | 266.9039 | 2484.795 | 3315.0355 | 0 | 0 | 3315.0355 | 0.00055%
2028 | 314 | CB 314 | Tier-1 | Non-HFTD---1 | 3--4 | 1.0947 | 32 | 100% | 255.5795 | 52.94% | 46.78% | 0.2824% | 6.6973 | 0 | 0 | 6.6973 | 0 | 5.8137 | 1.0291 | 5.6493 | 5.8137 | 1.0291 | 5.6493 | 6.7962 | 1.203 | 5.6493 | 2.62% | 0.021433 | 0.020372 | 11924.6916 | 952.6976 | 5630.0979 | 5341.896 | 12216.954 | 0 | 0 | 12216.954 | 0.0002209%
2028 | 1138 | CB 1138 | Tier-2 | Tier-2---10 | 5--4 | 7.6676 | 440 | 100% | 765.4961 | 75% | 24.28% | 0.7274% | 28.4174 | 0 | 0 | 28.4174 | 0 | 24.6681 | 7.2083 | 3.4222 | 24.6681 | 7.2083 | 3.4222 | 28.8373 | 8.4266 | 3.4222 | 3.712% | 0.11418 | 0.10853 | 6704.4211 | 1031.4722 | 1538.2078 | 4134.7411 | 6791.7244 | 0 | 0 | 6791.7244 | 0.0009371%
2028 | 771 | 771-274AE | Tier-1 | Non-HFTD---19 | 1--2 | 0.13125 | 10 | 100% | 0.57016 | 61.28% | 0% | 38.72% | 0.017295 | 0 | 0 | 0.017295 | 0 | 0.015013 | 0.12339 | 0.12167 | 0.015013 | 0.12339 | 0.12167 | 0.01755 | 0.14424 | 0.12167 | 3.033% | 0.0006212 | 0.00059045 | 917.8285 | 52.5226 | 272.2512 | 593.0547 | 936.3367 | 0 | 0 | 936.3367 | 5.703e-07%
2028 | 248 | CB 248 | Tier-2 | Tier-2---9 | 3--5 | 4.4809 | 284 | 100% | 962.1527 | 99.5% | 0% | 0.4991% | 47.3889 | 0 | 0 | 47.3889 | 0 | 41.1366 | 4.2125 | 9.7654 | 41.1366 | 4.2125 | 9.7654 | 48.0892 | 4.9244 | 9.7654 | 4.925% | 0.01881 | 0.017879 | 51150.5838 | 8615.1388 | 24.4667 | 42510.9782 | 51163.8787 | 0 | 0 | 51163.8787 | 0.001563%
2028 | 545 | 545-874R | Tier-1 | Non-HFTD---4 | 3--4 | 3.5507 | 93 | 100% | 149.8608 | 5.982% | 92.24% | 1.775% | 0.44376 | 0 | 0 | 0.44376 | 0 | 0.38521 | 3.338 | 0.1154 | 0.38521 | 3.338 | 0.1154 | 0.45032 | 3.9022 | 0.1154 | 0.2961% | 0.020584 | 0.019565 | 7280.5198 | 7.5721 | 6605.319 | 667.6287 | 7636.9922 | 0 | 0 | 7636.9922 | 1.463e-05%
2028 | 562 | CB 562 | Tier-1 | Non-HFTD---1 | 2--5 | 1.5066 | 1 | 100% | 385.0598 | 99.74% | 0% | 0.2579% | 19.0113 | 0 | 0 | 19.0113 | 0 | 16.503 | 1.4164 | 11.6514 | 16.503 | 1.4164 | 11.6514 | 19.2922 | 1.6558 | 11.6514 | 4.937% | 0.0064962 | 0.0061746 | 59274.622 | 37636.7204 | 2222.5751 | 19415.3265 | 59282.5839 | 0 | 0 | 59282.5839 | 0.0006269%
2028 | 256 | 256-39AE | Tier-1 | Non-HFTD---18 | 1--1 | 1.2698 | 44 | 100% | 1.0609 | 19.16% | 0% | 80.84% | 0.010061 | 0 | 0 | 0.010061 | 0 | 0.0087334 | 1.1938 | 0.0073157 | 0.0087334 | 1.1938 | 0.0073157 | 0.010209 | 1.3955 | 0.0073157 | 0.9484% | 0.0034328 | 0.0032629 | 309.0347 | 0.18799 | 81.9019 | 226.9448 | 322.0452 | 0 | 0 | 322.0452 | 3.318e-07%
2028 | 352 | 352-27R | Tier-3 | Tier-3---2 | 5--5 | 13.0331 | 1634 | 100% | 18614.1823 | 99.36% | 0.5928% | 0.04664% | 915.5099 | 0 | 0 | 915.5099 | 0 | 794.7222 | 12.2525 | 64.8623 | 794.7222 | 12.2525 | 64.8623 | 929.0394 | 14.3233 | 64.8623 | 4.918% | 0.11814 | 0.11229 | 157566.7738 | 32189.8213 | 867.9223 | 124509.0302 | 157619.2477 | 0 | 0 | 157619.2477 | 0.03019%
2028 | 855 | 855-45 | Tier-1 | Non-HFTD---20 | 1--1 | 0.17043 | 1 | 100% | 0.068838 | 3.968% | 0% | 96.03% | 0.00013522 | 0 | 0 | 0.00013522 | 0 | 0.00011738 | 0.16022 | 0.00073263 | 0.00011738 | 0.16022 | 0.00073263 | 0.00013722 | 0.1873 | 0.00073263 | 0.1964% | 0.0003944 | 0.00037488 | 174.5396 | 0.12612 | 22.1525 | 152.261 | 183.2685 | 0 | 0 | 183.2685 | 4.459e-09%
2028 | 524 | 524-46R | Tier-3 | Tier-3---4 | 5--5 | 12.3091 | 646 | 100% | 13710.9533 | 98.99% | 0.9557% | 0.05722% | 671.8177 | 0 | 0 | 671.8177 | 0 | 583.1815 | 11.5718 | 50.3967 | 583.1815 | 11.5718 | 50.3967 | 681.7459 | 13.5276 | 50.3967 | 4.9% | 0.18916 | 0.17979 | 72484.9745 | 13906.2618 | 666.7027 | 57912.0099 | 72523.2103 | 0 | 0 | 72523.2103 | 0.02215%
2028 | 288 | 288-18 | Tier-1 | Non-HFTD---1 | 3--5 | 5.4562 | 1025 | 100% | 1717.8671 | 96.12% | 3.649% | 0.229% | 81.7367 | 0 | 0 | 81.7367 | 0 | 70.9528 | 5.1294 | 13.8326 | 70.9528 | 5.1294 | 13.8326 | 82.9446 | 5.9963 | 13.8326 | 4.758% | 0.026137 | 0.024843 | 65724.9856 | 11143.2146 | 2230.6061 | 52351.1649 | 65857.7245 | 0 | 0 | 65857.7245 | 0.002695%
2028 | 452 | 452-47 | Tier-1 | Non-HFTD---11 | 2--3 | 1.7508 | 32 | 100% | 8.9597 | 85.97% | 0% | 14.03% | 0.3813 | 0 | 0 | 0.3813 | 0 | 0.33099 | 1.6459 | 0.2011 | 0.33099 | 1.6459 | 0.2011 | 0.38693 | 1.9241 | 0.2011 | 4.256% | 0.0051162 | 0.0048629 | 1751.2376 | 0.18482 | 1527.9269 | 223.1259 | 1764.0292 | 0 | 0 | 1764.0292 | 1.257e-05%
2028 | 69 | 69-45F | Tier-1 | Non-HFTD---4 | 2--4 | 0.32272 | 10 | 100% | 106.7813 | 2.696% | 97.13% | 0.1713% | 0.14248 | 0 | 0 | 0.14248 | 0 | 0.12368 | 0.30338 | 0.40767 | 0.12368 | 0.30338 | 0.40767 | 0.14458 | 0.35466 | 0.40767 | 0.1334% | 0.008264 | 0.0078549 | 12921.2611 | 83.6052 | 11175.4926 | 1662.1634 | 13576.0339 | 0 | 0 | 13576.0339 | 4.698e-06%
2028 | ALV1 | CB ALV1 | Tier-1 | Non-HFTD---9 | 2--3 | 1.8195 | 145 | 100% | 23.1135 | 96.16% | 0% | 3.841% | 1.1002 | 0 | 0 | 1.1002 | 0 | 0.95502 | 1.7105 | 0.55832 | 0.95502 | 1.7105 | 0.55832 | 1.1164 | 1.9996 | 0.55832 | 4.76% | 0.0050056 | 0.0047578 | 4617.5342 | 724.8553 | 33.5047 | 3859.1742 | 4626.7717 | 0 | 0 | 4626.7717 | 3.628e-05%
2028 | 60 | 60-574 | Tier-1 | Non-HFTD---13 | 2--2 | 3.014 | 84 | 100% | 8.5311 | 71.96% | 0% | 28.04% | 0.3039 | 0 | 0 | 0.3039 | 0 | 0.2638 | 2.8335 | 0.093101 | 0.2638 | 2.8335 | 0.093101 | 0.30839 | 3.3124 | 0.093101 | 3.562% | 0.0093494 | 0.0088866 | 912.477 | 24.9805 | 528.1696 | 359.327 | 925.7996 | 0 | 0 | 925.7996 | 1.002e-05%
2028 | 703 | CB 703 | Tier-1 | Non-HFTD---13 | 2--2 | 0.13314 | 1 | 100% | 6.8734 | 94.98% | 2.252% | 2.765% | 0.32316 | 0 | 0 | 0.32316 | 0 | 0.28053 | 0.12517 | 2.2412 | 0.28053 | 0.12517 | 2.2412 | 0.32794 | 0.14632 | 2.2412 | 4.702% | 0.0055408 | 0.0052665 | 1240.5052 | 28.6229 | 1027.2685 | 184.6138 | 1243.7466 | 0 | 0 | 1243.7466 | 1.066e-05%
2028 | 229 | CB 229 | Tier-1 | Non-HFTD---15 | 1--3 | 0.16098 | 0 | 100% | 2.744 | 94.71% | 0% | 5.287% | 0.12865 | 0 | 0 | 0.12865 | 0 | 0.11168 | 0.15134 | 0.73791 | 0.11168 | 0.15134 | 0.73791 | 0.13055 | 0.17692 | 0.73791 | 4.688% | 0.0005864 | 0.00055737 | 4679.4778 | 389.4263 | 2294.1086 | 1995.9429 | 4692.3613 | 0 | 0 | 4692.3613 | 4.242e-06%
2028 | 230 | 230-1606R | Tier-2 | Tier-2---11 | 4--4 | 2.6869 | 346 | 100% | 536.3838 | 78.97% | 20.71% | 0.32% | 20.9668 | 0 | 0 | 20.9668 | 0 | 18.2006 | 2.5259 | 7.2055 | 18.2006 | 2.5259 | 7.2055 | 21.2767 | 2.9529 | 7.2055 | 3.909% | 0.062818 | 0.059709 | 8538.6965 | 1090.1965 | 1630.9842 | 5817.5158 | 8632.2204 | 0 | 0 | 8632.2204 | 0.0006914%
2028 | 532 | CB 532 | Tier-1 | Non-HFTD---10 | 3--2 | 5.6968 | 88 | 100% | 16.397 | 75.87% | 0% | 24.13% | 0.61579 | 0 | 0 | 0.61579 | 0 | 0.53455 | 5.3555 | 0.099812 | 0.53455 | 5.3555 | 0.099812 | 0.62489 | 6.2607 | 0.099812 | 3.756% | 0.016027 | 0.015234 | 1023.0743 | 0.6764 | 795.5841 | 226.8138 | 1035.9312 | 0 | 0 | 1035.9312 | 2.031e-05%
2028 | 572 | 572-493F | Tier-1 | Non-HFTD---20 | 1--1 | 0.20172 | 3 | 100% | 0.12336 | 2.076% | 0% | 97.92% | 0.00012676 | 0 | 0 | 0.00012676 | 0 | 0.00011003 | 0.18964 | 0.00058022 | 0.00011003 | 0.18964 | 0.00058022 | 0.00012863 | 0.22169 | 0.00058022 | 0.1027% | 0.000542 | 0.00051517 | 227.6098 | 0.16771 | 24.9717 | 202.4705 | 239.2172 | 0 | 0 | 239.2172 | 4.18e-09%
2028 | 456 | CB 456 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0005 | 145 | 100% | 54.2335 | 91.66% | 0% | 8.342% | 2.4606 | 0 | 0 | 2.4606 | 0 | 2.136 | 5.6411 | 0.37865 | 2.136 | 5.6411 | 0.37865 | 2.497 | 6.5945 | 0.37865 | 4.537% | 0.018506 | 0.01759 | 2930.6543 | 41.8221 | 2453.6064 | 435.2259 | 2943.3855 | 0 | 0 | 2943.3855 | 8.114e-05%
2028 | 237 | 237-2R | Tier-3 | Tier-3---2 | 5--5 | 16.7242 | 1062 | 100% | 30894.1234 | 99.11% | 0.8492% | 0.03898% | 1515.6765 | 0 | 0 | 1515.6765 | 0 | 1315.706 | 15.7225 | 83.6832 | 1315.706 | 15.7225 | 83.6832 | 1538.0753 | 18.3797 | 83.6832 | 4.906% | 0.18156 | 0.17257 | 170161.3668 | 36497.0865 | 1351.4865 | 132312.7938 | 170240.0741 | 0 | 0 | 170240.0741 | 0.04998%
2028 | 176 | 176-1836R | Tier-2 | Tier-2---11 | 5--3 | 1.5242 | 73 | 100% | 404.4817 | 67.64% | 32.12% | 0.2398% | 13.5424 | 0 | 0 | 13.5424 | 0 | 11.7557 | 1.4329 | 8.204 | 11.7557 | 1.4329 | 8.204 | 13.7425 | 1.6751 | 8.204 | 3.348% | 0.10638 | 0.10111 | 3802.2631 | 510.8459 | 1145.0457 | 2146.3715 | 3866.3442 | 0 | 0 | 3866.3442 | 0.0004466%
2028 | 445 | 445-17R | Tier-2 | Tier-2---8 | 5--3 | 3.4282 | 109 | 100% | 1603.5562 | 88.72% | 11.16% | 0.1231% | 70.4231 | 0 | 0 | 70.4231 | 0 | 61.1318 | 3.2228 | 18.9684 | 61.1318 | 3.2228 | 18.9684 | 71.4638 | 3.7675 | 18.9684 | 4.392% | 0.53426 | 0.50782 | 3001.4248 | 392.7995 | 299.0437 | 2309.5816 | 3019.055 | 0 | 0 | 3019.055 | 0.002322%
2028 | 314 | 314-13F | Tier-1 | Non-HFTD---6 | 3--3 | 0.47273 | 5 | 100% | 74.5408 | 76.13% | 23.46% | 0.4094% | 2.809 | 0 | 0 | 2.809 | 0 | 2.4384 | 0.44441 | 5.4868 | 2.4384 | 0.44441 | 5.4868 | 2.8505 | 0.51952 | 5.4868 | 3.768% | 0.019129 | 0.018182 | 3896.6601 | 485.4254 | 838.4338 | 2572.801 | 3945.1005 | 0 | 0 | 3945.1005 | 9.263e-05%
2028 | 80 | CB 80 | Tier-1 | Non-HFTD---7 | 3--3 | 5.2693 | 48 | 100% | 44.4535 | 89.11% | 0% | 10.89% | 1.9609 | 0 | 0 | 1.9609 | 0 | 1.7021 | 4.9537 | 0.34361 | 1.7021 | 4.9537 | 0.34361 | 1.9898 | 5.7909 | 0.34361 | 4.411% | 0.017052 | 0.016208 | 2606.9684 | 6.287 | 2311.46 | 289.2215 | 2621.7513 | 0 | 0 | 2621.7513 | 6.466e-05%
2028 | 315 | 315-485AE | Tier-2 | Tier-2---14 | 2--5 | 1.6445 | 445 | 100% | 209.8559 | 99.5% | 0% | 0.498% | 10.3361 | 0 | 0 | 10.3361 | 0 | 8.9724 | 1.546 | 5.8037 | 8.9724 | 1.546 | 5.8037 | 10.4889 | 1.8073 | 5.8037 | 4.925% | 0.00637 | 0.0060547 | 32944.4153 | 11783.7746 | 42.3107 | 21118.3299 | 32952.9592 | 0 | 0 | 32952.9592 | 0.0003408%
2028 | 212 | 212-799R | Tier-2 | Tier-2---10 | 5--4 | 5.2246 | 110 | 100% | 1038.8005 | 97.12% | 2.539% | 0.3416% | 49.9395 | 0 | 0 | 49.9395 | 0 | 43.3507 | 4.9116 | 8.8261 | 43.3507 | 4.9116 | 8.8261 | 50.6775 | 5.7418 | 8.8261 | 4.807% | 0.12493 | 0.11875 | 8315.0604 | 1068.4402 | 194.8254 | 7051.7948 | 8327.5336 | 0 | 0 | 8327.5336 | 0.001647%
2028 | 57 | 57-1295F | Tier-1 | Non-HFTD---14 | 3--1 | 0.73143 | 22 | 100% | 5.7785 | 18.72% | 64.33% | 16.95% | 0.053541 | 0 | 0 | 0.053541 | 0 | 0.046477 | 0.68762 | 0.067592 | 0.046477 | 0.68762 | 0.067592 | 0.054332 | 0.80383 | 0.067592 | 0.9266% | 0.013816 | 0.013132 | 418.2342 | 0.34202 | 329.9664 | 87.9258 | 435.938 | 0 | 0 | 435.938 | 1.766e-06%
2028 | 1434 | CB 1434 | Tier-1 | Non-HFTD---13 | 2--2 | 2.2678 | 40 | 100% | 5.9882 | 73.95% | 0% | 26.05% | 0.21921 | 0 | 0 | 0.21921 | 0 | 0.19029 | 2.132 | 0.089255 | 0.19029 | 2.132 | 0.089255 | 0.22245 | 2.4923 | 0.089255 | 3.661% | 0.0060046 | 0.0057074 | 997.2619 | 1.3501 | 754.0153 | 241.8966 | 1010.7891 | 0 | 0 | 1010.7891 | 7.229e-06%
2028 | 499 | CB 499 | Tier-2 | Tier-2---19 | 2--3 | 1.9464 | 59 | 100% | 19.4193 | 94.64% | 0% | 5.361% | 0.90973 | 0 | 0 | 0.90973 | 0 | 0.7897 | 1.8298 | 0.43158 | 0.7897 | 1.8298 | 0.43158 | 0.92317 | 2.1391 | 0.43158 | 4.685% | 0.00687 | 0.0065299 | 2826.6853 | 293.3494 | 758.4761 | 1774.8598 | 2834.5765 | 0 | 0 | 2834.5765 | 3e-05%
2028 | 548 | 548-17F | Tier-1 | Non-HFTD---4 | 2--4 | 2.5892 | 226 | 100% | 104.2118 | 98.1% | 0% | 1.901% | 5.0604 | 0 | 0 | 5.0604 | 0 | 4.3928 | 2.4341 | 1.8047 | 4.3928 | 2.4341 | 1.8047 | 5.1352 | 2.8455 | 1.8047 | 4.856% | 0.010934 | 0.010393 | 9530.6409 | 2004.1168 | 69.3119 | 7457.2122 | 9540.0775 | 0 | 0 | 9540.0775 | 0.0001669%
2028 | 254 | CB 254 | Tier-1 | Non-HFTD---17 | 1--2 | 0.16193 | 0 | 100% | 0.87557 | 85.54% | 0% | 14.46% | 0.037073 | 0 | 0 | 0.037073 | 0 | 0.032182 | 0.15223 | 0.2114 | 0.032182 | 0.15223 | 0.2114 | 0.037621 | 0.17796 | 0.2114 | 4.234% | 0.0005892 | 0.00056003 | 1486.0267 | 199.9018 | 58.8156 | 1227.3092 | 1497.2186 | 0 | 0 | 1497.2186 | 1.223e-06%
2028 | 58 | 58-756F | Tier-1 | Non-HFTD---11 | 2--2 | 0.3534 | 9 | 100% | 14.7362 | 1.289% | 96.53% | 2.184% | 0.009405 | 0 | 0 | 0.009405 | 0 | 0.0081642 | 0.33223 | 0.024574 | 0.0081642 | 0.33223 | 0.024574 | 0.009544 | 0.38838 | 0.024574 | 0.06382% | 0.012057 | 0.01146 | 1222.212 | 3.1244 | 1076.1922 | 142.8953 | 1285.0415 | 0 | 0 | 1285.0415 | 3.101e-07%
2028 | 186 | 186-940R | Tier-1 | Non-HFTD---1 | 4--4 | 2.8176 | 388 | 100% | 708.016 | 27.23% | 72.48% | 0.2936% | 9.5427 | 0 | 0 | 9.5427 | 0 | 8.2837 | 2.6488 | 3.1273 | 8.2837 | 2.6488 | 3.1273 | 9.6838 | 3.0965 | 3.1273 | 1.348% | 0.051585 | 0.049032 | 13725.1247 | 759.9823 | 9159.4783 | 3805.6641 | 14245.2769 | 0 | 0 | 14245.2769 | 0.0003147%
2028 | 168 | 168-703F | Tier-1 | Non-HFTD---15 | 2--1 | 1.968 | 106 | 100% | 2.7691 | 40.41% | 0% | 59.59% | 0.055392 | 0 | 0 | 0.055392 | 0 | 0.048084 | 1.8501 | 0.02599 | 0.048084 | 1.8501 | 0.02599 | 0.056211 | 2.1628 | 0.02599 | 2% | 0.0058996 | 0.0056076 | 469.3702 | 3.0577 | 197.5515 | 268.7611 | 483.9359 | 0 | 0 | 483.9359 | 1.827e-06%
2028 | 57 | 57-1296F | Tier-1 | Non-HFTD---6 | 3--3 | 4.3852 | 419 | 100% | 54.2561 | 82.4% | 11.86% | 5.738% | 2.2131 | 0 | 0 | 2.2131 | 0 | 1.9211 | 4.1225 | 0.466 | 1.9211 | 4.1225 | 0.466 | 2.2458 | 4.8193 | 0.466 | 4.079% | 0.026297 | 0.024995 | 2063.1894 | 274.7024 | 258.9091 | 1529.5779 | 2082.0976 | 0 | 0 | 2082.0976 | 7.298e-05%
2028 | 190 | 190-1868R | Tier-1 | Non-HFTD---11 | 1--4 | 0.48108 | 19 | 100% | 12.0699 | 97.67% | 0% | 2.333% | 0.58352 | 0 | 0 | 0.58352 | 0 | 0.50654 | 0.45226 | 1.12 | 0.50654 | 0.45226 | 1.12 | 0.59215 | 0.5287 | 1.12 | 4.835% | 0.0015928 | 0.001514 | 7577.7716 | 422.4158 | 4765.8195 | 2389.5362 | 7586.9772 | 0 | 0 | 7586.9772 | 1.924e-05%
2028 | 1139 | CB 1139 | Tier-1 | Non-HFTD---17 | 1--3 | 0.21402 | 0 | 100% | 1.9809 | 88.52% | 0% | 11.48% | 0.086804 | 0 | 0 | 0.086804 | 0 | 0.075351 | 0.2012 | 0.37452 | 0.075351 | 0.2012 | 0.37452 | 0.088086 | 0.2352 | 0.37452 | 4.382% | 0.0008862 | 0.00084233 | 2235.3083 | 105.1437 | 1355.0151 | 775.1495 | 2248.667 | 0 | 0 | 2248.667 | 2.862e-06%
2028 | LA1 | CB LA1 | Tier-1 | Non-HFTD---12 | 4--1 | 10.8148 | 231 | 100% | 14.2144 | 47.91% | 0% | 52.09% | 0.33709 | 0 | 0 | 0.33709 | 0 | 0.29262 | 10.167 | 0.028781 | 0.29262 | 10.167 | 0.028781 | 0.34207 | 11.8853 | 0.028781 | 2.371% | 0.029769 | 0.028295 | 477.4907 | 3.6261 | 230.2568 | 243.6078 | 490.4441 | 0 | 0 | 490.4441 | 1.112e-05%
2028 | 417 | 417-44AE | Tier-1 | Non-HFTD---5 | 2--4 | 0.70607 | 9 | 100% | 68.544 | 0.1089% | 99.12% | 0.7728% | 0.0036964 | 0 | 0 | 0.0036964 | 0 | 0.0032087 | 0.66378 | 0.004834 | 0.0032087 | 0.66378 | 0.004834 | 0.003751 | 0.77596 | 0.004834 | 0.005393% | 0.0129 | 0.012261 | 5313.5687 | 6.798 | 4793.3964 | 513.3743 | 5589.9865 | 0 | 0 | 5589.9865 | 1.219e-07%
2028 | 1077 | CB 1077 | Tier-1 | Non-HFTD---8 | 3--2 | 8.2547 | 281 | 100% | 27.171 | 78.66% | 0% | 21.34% | 1.058 | 0 | 0 | 1.058 | 0 | 0.91838 | 7.7603 | 0.11834 | 0.91838 | 7.7603 | 0.11834 | 1.0736 | 9.0718 | 0.11834 | 3.894% | 0.023107 | 0.021963 | 1175.8656 | 180.5721 | 140.8614 | 854.4321 | 1188.933 | 0 | 0 | 1188.933 | 3.489e-05%
2028 | 738 | CB 738 | Tier-1 | Non-HFTD---17 | 1--2 | 0.53655 | 33 | 100% | 2.031 | 77.55% | 0% | 22.45% | 0.077964 | 0 | 0 | 0.077964 | 0 | 0.067678 | 0.50441 | 0.13417 | 0.067678 | 0.50441 | 0.13417 | 0.079116 | 0.58967 | 0.13417 | 3.839% | 0.0021108 | 0.0020063 | 962.2085 | 113.8791 | 22.5007 | 825.8287 | 973.4589 | 0 | 0 | 973.4589 | 2.571e-06%
2028 | 578 | CB 578 | Tier-1 | Non-HFTD---3 | 3--4 | 4.9491 | 87 | 100% | 140.4916 | 12.05% | 84.92% | 3.035% | 0.83787 | 0 | 0 | 0.83787 | 0 | 0.72732 | 4.6526 | 0.15633 | 0.72732 | 4.6526 | 0.15633 | 0.85025 | 5.439 | 0.15633 | 0.5964% | 0.025495 | 0.024233 | 5510.5967 | 5.2725 | 4912.3512 | 592.973 | 5763.0011 | 0 | 0 | 5763.0011 | 2.763e-05%
2028 | 442 | 442-728R | Tier-3 | Tier-3---5 | 5--5 | 22.2475 | 1918 | 100% | 11572.221 | 88.48% | 11.4% | 0.1243% | 506.8142 | 0 | 0 | 506.8142 | 0 | 439.9478 | 20.9149 | 21.0352 | 439.9478 | 20.9149 | 21.0352 | 514.3039 | 24.4497 | 21.0352 | 4.38% | 0.35802 | 0.3403 | 32323.0144 | 5419.0959 | 3368.3532 | 23535.5653 | 32516.9947 | 0 | 0 | 32516.9947 | 0.01671%
2028 | BN2 | CB BN2 | Tier-1 | Non-HFTD---1 | 4--5 | 10.1083 | 520 | 100% | 1098.8312 | 99.36% | 0% | 0.6449% | 54.0413 | 0 | 0 | 54.0413 | 0 | 46.9114 | 9.5029 | 4.9366 | 46.9114 | 9.5029 | 4.9366 | 54.84 | 11.109 | 4.9366 | 4.918% | 0.034221 | 0.032527 | 32110.0379 | 7492.6936 | 90.1662 | 24527.178 | 32120.8227 | 0 | 0 | 32120.8227 | 0.001782%
2028 | 582 | CB 582 | Tier-1 | Non-HFTD---17 | 1--2 | 0.3354 | 8 | 100% | 1.2456 | 82.48% | 0% | 17.52% | 0.050855 | 0 | 0 | 0.050855 | 0 | 0.044146 | 0.31531 | 0.14001 | 0.044146 | 0.31531 | 0.14001 | 0.051607 | 0.3686 | 0.14001 | 4.083% | 0.0009004 | 0.00085583 | 1383.3541 | 0.23444 | 1162.7176 | 220.4021 | 1395.9743 | 0 | 0 | 1395.9743 | 1.677e-06%
2028 | 431 | 431-48AE | Tier-1 | Non-HFTD---18 | 1--1 | 1.1947 | 55 | 100% | 1.4033 | 31.02% | 0% | 68.98% | 0.021548 | 0 | 0 | 0.021548 | 0 | 0.018705 | 1.1231 | 0.016654 | 0.018705 | 1.1231 | 0.016654 | 0.021867 | 1.313 | 0.016654 | 1.536% | 0.0035406 | 0.0033653 | 396.3532 | 0.23934 | 147.5741 | 248.5398 | 410.5915 | 0 | 0 | 410.5915 | 7.106e-07%
2028 | 595 | 595-1454F | Tier-2 | Tier-2---15 | 3--4 | 1.3606 | 113 | 100% | 124.9246 | 83.27% | 16% | 0.7306% | 5.1495 | 0 | 0 | 5.1495 | 0 | 4.4701 | 1.2791 | 3.4947 | 4.4701 | 1.2791 | 3.4947 | 5.2256 | 1.4953 | 3.4947 | 4.122% | 0.018776 | 0.017847 | 6653.3471 | 1471.8841 | 978.4778 | 4202.9852 | 6711.3017 | 0 | 0 | 6711.3017 | 0.0001698%
2028 | UP2 | CB UP2 | Tier-1 | Non-HFTD---12 | 3--2 | 6.268 | 169 | 100% | 9.6733 | 51.85% | 0% | 48.15% | 0.24825 | 0 | 0 | 0.24825 | 0 | 0.2155 | 5.8925 | 0.036572 | 0.2155 | 5.8925 | 0.036572 | 0.25192 | 6.8884 | 0.036572 | 2.566% | 0.018016 | 0.017125 | 536.9147 | 0.19455 | 301.8547 | 234.8654 | 550.3792 | 0 | 0 | 550.3792 | 8.186e-06%
2028 | 214 | 214-613R | Tier-3 | Tier-3---14 | 5--3 | 5.4881 | 1424 | 100% | 1721.769 | 85.69% | 14.07% | 0.2459% | 73.0294 | 0 | 0 | 73.0294 | 0 | 63.3943 | 5.1593 | 12.2873 | 63.3943 | 5.1593 | 12.2873 | 74.1087 | 6.0313 | 12.2873 | 4.242% | 0.43289 | 0.41146 | 3977.4025 | 528.7899 | 507.0028 | 2941.6099 | 4007.0485 | 0 | 0 | 4007.0485 | 0.002408%
2028 | 79 | 79-660R | Tier-3 | Tier-3---14 | 5--3 | 7.564 | 793 | 100% | 2087.0386 | 97.47% | 2.263% | 0.2704% | 100.6913 | 0 | 0 | 100.6913 | 0 | 87.4066 | 7.1109 | 12.2919 | 87.4066 | 7.1109 | 12.2919 | 102.1793 | 8.3128 | 12.2919 | 4.825% | 0.45747 | 0.43483 | 4562.1181 | 605.8757 | 102.8461 | 3853.3963 | 4568.1369 | 0 | 0 | 4568.1369 | 0.00332%
2028 | 39 | CB 39 | Tier-1 | Non-HFTD---19 | 1--1 | 0.092003 | 0 | 100% | 0.12086 | 14.55% | 0% | 85.45% | 0.00087056 | 0 | 0 | 0.00087056 | 0 | 0.0007557 | 0.086492 | 0.0087372 | 0.0007557 | 0.086492 | 0.0087372 | 0.00088342 | 0.10111 | 0.0087372 | 0.7203% | 0.000339 | 0.00032222 | 356.5086 | 8.0102 | 30.562 | 317.9364 | 372.373 | 0 | 0 | 372.373 | 2.871e-08%
2028 | 313 | 313-548AE | Tier-1 | Non-HFTD---12 | 3--2 | 0.1225 | 4 | 100% | 14.2935 | 9.237% | 90.04% | 0.7189% | 0.065357 | 0 | 0 | 0.065357 | 0 | 0.056734 | 0.11516 | 0.49266 | 0.056734 | 0.11516 | 0.49266 | 0.066323 | 0.13462 | 0.49266 | 0.4573% | 0.017367 | 0.016507 | 823.0292 | 13.4104 | 588.2213 | 221.3976 | 861.9315 | 0 | 0 | 861.9315 | 2.155e-06%
2028 | 366 | 366-48 | Tier-1 | Non-HFTD---5 | 3--4 | 2.5229 | 51 | 100% | 85.178 | 1.803% | 95.42% | 2.781% | 0.076004 | 0 | 0 | 0.076004 | 0 | 0.065976 | 2.3718 | 0.027818 | 0.065976 | 2.3718 | 0.027818 | 0.077127 | 2.7726 | 0.027818 | 0.08923% | 0.013571 | 0.012899 | 6276.6562 | 7.3618 | 5560.2911 | 709.0033 | 6597.6387 | 0 | 0 | 6597.6387 | 2.506e-06%
2028 | 1140 | CB 1140 | Tier-1 | Non-HFTD---2 | 4--4 | 0.29399 | 56 | 100% | 668.0984 | 0.02919% | 99.94% | 0.02644% | 0.0096542 | 0 | 0 | 0.0096542 | 0 | 0.0083805 | 0.27638 | 0.030323 | 0.0083805 | 0.27638 | 0.030323 | 0.0097969 | 0.32309 | 0.030323 | 0.001445% | 0.087146 | 0.082832 | 7666.4439 | 10.8548 | 7025.307 | 630.2821 | 8065.5793 | 0 | 0 | 8065.5793 | 3.184e-07%
2028 | 35 | 35-297AE | Tier-1 | Non-HFTD---11 | 2--2 | 0.30568 | 35 | 100% | 10.2793 | 20.26% | 76.41% | 3.337% | 0.10307 | 0 | 0 | 0.10307 | 0 | 0.089471 | 0.28737 | 0.31134 | 0.089471 | 0.28737 | 0.31134 | 0.10459 | 0.33594 | 0.31134 | 1.003% | 0.0071058 | 0.0067541 | 1446.6053 | 46.2284 | 897.7038 | 502.6731 | 1506.6811 | 0 | 0 | 1506.6811 | 3.399e-06%
2028 | 449 | 449-16R | Tier-3 | Tier-3---15 | 5--4 | 2.4038 | 65 | 100% | 1495.5065 | 96.97% | 2.927% | 0.1006% | 71.7862 | 0 | 0 | 71.7862 | 0 | 62.3151 | 2.2598 | 27.5755 | 62.3151 | 2.2598 | 27.5755 | 72.8471 | 2.6417 | 27.5755 | 4.8% | 0.23738 | 0.22563 | 6300.0313 | 977.5714 | 169.5858 | 5152.8741 | 6309.9651 | 0 | 0 | 6309.9651 | 0.002367%
2028 | 208 | CB 208 | Tier-1 | Non-HFTD---13 | 1--3 | 0.50053 | 7 | 100% | 7.9912 | 93.78% | 0% | 6.225% | 0.37094 | 0 | 0 | 0.37094 | 0 | 0.322 | 0.47055 | 0.6843 | 0.322 | 0.47055 | 0.6843 | 0.37642 | 0.55008 | 0.6843 | 4.642% | 0.0017112 | 0.0016265 | 4669.9217 | 68.1319 | 3989.8459 | 611.9439 | 4685.0604 | 0 | 0 | 4685.0604 | 1.223e-05%
2028 | 307 | 307-234R | Tier-2 | Tier-2---4 | 5--5 | 4.6394 | 937 | 100% | 4762.848 | 95.55% | 4.384% | 0.07015% | 225.2596 | 0 | 0 | 225.2596 | 0 | 195.54 | 4.3615 | 44.8328 | 195.54 | 4.3615 | 44.8328 | 228.5885 | 5.0987 | 44.8328 | 4.73% | 0.11001 | 0.10456 | 43295.9421 | 6736.6432 | 1761.8167 | 34797.4822 | 43396.3748 | 0 | 0 | 43396.3748 | 0.007428%
2028 | 171 | 171-568 | Tier-1 | Non-HFTD---8 | 4--2 | 1.7236 | 45 | 100% | 31.0781 | 60.02% | 35.24% | 4.741% | 0.92333 | 0 | 0 | 0.92333 | 0 | 0.80151 | 1.6204 | 0.49464 | 0.80151 | 1.6204 | 0.49464 | 0.93698 | 1.8943 | 0.49464 | 2.971% | 0.032551 | 0.03094 | 954.7509 | 88.4522 | 317.464 | 548.8347 | 974.6293 | 0 | 0 | 974.6293 | 3.045e-05%
2028 | 581 | 581-49 | Tier-1 | Non-HFTD---9 | 2--3 | 2.7263 | 67 | 100% | 15.9576 | 84.86% | 0% | 15.14% | 0.67032 | 0 | 0 | 0.67032 | 0 | 0.58188 | 2.563 | 0.22703 | 0.58188 | 2.563 | 0.22703 | 0.68023 | 2.9962 | 0.22703 | 4.201% | 0.0089802 | 0.0085357 | 1776.972 | 49.0609 | 1234.3778 | 493.5333 | 1790.9809 | 0 | 0 | 1790.9809 | 2.21e-05%
2028 | 156 | 156-529AE | Tier-1 | Non-HFTD---18 | 2--1 | 1.9048 | 13 | 100% | 2.0617 | 40.76% | 0% | 59.24% | 0.041597 | 0 | 0 | 0.041597 | 0 | 0.036109 | 1.7907 | 0.020165 | 0.036109 | 1.7907 | 0.020165 | 0.042211 | 2.0933 | 0.020165 | 2.018% | 0.0054304 | 0.0051616 | 379.6623 | 1.8858 | 164.6049 | 213.1716 | 391.3754 | 0 | 0 | 391.3754 | 1.372e-06%
2028 | 920 | 920-1342R | Tier-3 | Tier-3---12 | 4--5 | 6.3664 | 344 | 100% | 3406.6458 | 99.34% | 0.5402% | 0.1203% | 167.5153 | 0 | 0 | 167.5153 | 0 | 145.4142 | 5.9851 | 24.296 | 145.4142 | 5.9851 | 24.296 | 169.9908 | 6.9966 | 24.296 | 4.917% | 0.068604 | 0.065208 | 49656.3753 | 10714.8381 | 249.0111 | 38692.5261 | 49673.4543 | 0 | 0 | 49673.4543 | 0.005524%
2028 | 236 | 236-1561R | Tier-3 | Tier-3---13 | 5--4 | 5.1765 | 273 | 100% | 2823.5781 | 97.26% | 2.617% | 0.1213% | 135.9404 | 0 | 0 | 135.9404 | 0 | 118.0052 | 4.8665 | 24.2487 | 118.0052 | 4.8665 | 24.2487 | 137.9494 | 5.6889 | 24.2487 | 4.814% | 0.17766 | 0.16886 | 15893.5317 | 2548.7171 | 379.7854 | 12965.0293 | 15916.1933 | 0 | 0 | 15916.1933 | 0.004483%
2028 | 1090 | 1090-70F | Tier-2 | Tier-2---15 | 2--5 | 0.64526 | 41 | 100% | 140.8367 | 88.02% | 11.68% | 0.2956% | 6.1362 | 0 | 0 | 6.1362 | 0 | 5.3266 | 0.60661 | 8.781 | 5.3266 | 0.60661 | 8.781 | 6.2269 | 0.70913 | 8.781 | 4.357% | 0.0083 | 0.0078891 | 16968.2749 | 2406.7786 | 1862.2717 | 12699.2245 | 17074.1431 | 0 | 0 | 17074.1431 | 0.0002023%
2028 | 315 | CB 315 | Tier-2 | Tier-2---19 | 1--4 | 0.68764 | 56 | 100% | 10.7713 | 97.26% | 0% | 2.741% | 0.51856 | 0 | 0 | 0.51856 | 0 | 0.45015 | 0.64645 | 0.69633 | 0.45015 | 0.64645 | 0.69633 | 0.52622 | 0.75571 | 0.69633 | 4.814% | 0.0017586 | 0.0016715 | 6124.9072 | 776.0019 | 1213.3331 | 4135.5722 | 6133.6511 | 0 | 0 | 6133.6511 | 1.71e-05%
2028 | 900 | 900-1118F | Tier-1 | Non-HFTD---15 | 1--3 | 0.4102 | 22 | 100% | 3.8209 | 95.13% | 0% | 4.872% | 0.17992 | 0 | 0 | 0.17992 | 0 | 0.15618 | 0.38563 | 0.405 | 0.15618 | 0.38563 | 0.405 | 0.18258 | 0.4508 | 0.405 | 4.709% | 0.0011032 | 0.0010486 | 3463.4496 | 535.7058 | 23.7271 | 2904.0167 | 3472.2375 | 0 | 0 | 3472.2375 | 5.933e-06%
2028 | CG1 | CB CG1 | Tier-1 | Non-HFTD---1 | 4--4 | 8.3125 | 886 | 100% | 278.5213 | 94.12% | 3.851% | 2.028% | 12.9764 | 0 | 0 | 12.9764 | 0 | 11.2643 | 7.8146 | 1.4414 | 11.2643 | 7.8146 | 1.4414 | 13.1681 | 9.1354 | 1.4414 | 4.659% | 0.029972 | 0.028488 | 9292.8406 | 1535.1687 | 384.8682 | 7372.8037 | 9321.2885 | 0 | 0 | 9321.2885 | 0.0004279%
2028 | 212 | 212-725R | Tier-3 | Tier-3---10 | 5--5 | 11.8649 | 1839 | 100% | 4887.8267 | 99.15% | 0.7265% | 0.1225% | 239.8933 | 0 | 0 | 239.8933 | 0 | 208.243 | 11.1542 | 18.6694 | 208.243 | 11.1542 | 18.6694 | 243.4385 | 13.0394 | 18.6694 | 4.908% | 0.13941 | 0.13251 | 35061.0556 | 5196.5846 | 230.3548 | 29634.1163 | 35076.5573 | 0 | 0 | 35076.5573 | 0.007911%
2028 | 143 | 143-147F | Tier-1 | Non-HFTD---9 | 2--3 | 0.3229 | 0 | 100% | 25.6591 | 1.387% | 97.22% | 1.391% | 0.017616 | 0 | 0 | 0.017616 | 0 | 0.015292 | 0.30356 | 0.050374 | 0.015292 | 0.30356 | 0.050374 | 0.017876 | 0.35487 | 0.050374 | 0.06865% | 0.0072518 | 0.0068928 | 3538.3122 | 10.6062 | 3051.6105 | 476.0955 | 3720.0242 | 0 | 0 | 3720.0242 | 5.809e-07%
2028 | 175 | 175-24R | Tier-2 | Tier-2---8 | 5--4 | 4.8509 | 338 | 100% | 2651.4354 | 70.65% | 29.24% | 0.1064% | 92.7259 | 0 | 0 | 92.7259 | 0 | 80.4921 | 4.5604 | 17.6503 | 80.4921 | 4.5604 | 17.6503 | 94.0962 | 5.3311 | 17.6503 | 3.497% | 0.17491 | 0.16625 | 15158.7512 | 2441.7081 | 4085.9178 | 8631.1253 | 15390.4469 | 0 | 0 | 15390.4469 | 0.003058%
2028 | 216 | 216-1859F | Tier-3 | Tier-3---4 | 5--5 | 8.4771 | 468 | 100% | 14041.2877 | 99.19% | 0.7753% | 0.03948% | 689.3805 | 0 | 0 | 689.3805 | 0 | 598.4272 | 7.9694 | 75.0911 | 598.4272 | 7.9694 | 75.0911 | 699.5682 | 9.3163 | 75.0911 | 4.91% | 0.15704 | 0.14927 | 89409.7821 | 15986.4383 | 636.9074 | 72786.4365 | 89447.7216 | 0 | 0 | 89447.7216 | 0.02273%
2028 | 908 | 908-1236 | Tier-2 | Tier-2---2 | 5--5 | 5.4265 | 797 | 100% | 11763.9311 | 98.8% | 1.165% | 0.03327% | 575.3384 | 0 | 0 | 575.3384 | 0 | 499.4312 | 5.1015 | 97.8998 | 499.4312 | 5.1015 | 97.8998 | 583.8408 | 5.9637 | 97.8998 | 4.891% | 0.1877 | 0.17841 | 62673.98 | 12802.8477 | 668.2172 | 49202.9151 | 62713.0821 | 0 | 0 | 62713.0821 | 0.01897%
2028 | 946 | CB 946 | Tier-1 | Non-HFTD---10 | 3--2 | 9.2432 | 373 | 100% | 21.7172 | 73.55% | 0% | 26.45% | 0.79062 | 0 | 0 | 0.79062 | 0 | 0.68631 | 8.6896 | 0.078981 | 0.68631 | 8.6896 | 0.078981 | 0.8023 | 10.1582 | 0.078981 | 3.641% | 0.025949 | 0.024665 | 836.9106 | 3.7986 | 613.2175 | 219.8946 | 848.4404 | 0 | 0 | 848.4404 | 2.607e-05%
2028 | 515 | CB 515 | Tier-1 | Non-HFTD---14 | 2--2 | 3.1625 | 51 | 100% | 7.211 | 59.11% | 0% | 40.89% | 0.21099 | 0 | 0 | 0.21099 | 0 | 0.18316 | 2.9731 | 0.061604 | 0.18316 | 2.9731 | 0.061604 | 0.21411 | 3.4756 | 0.061604 | 2.926% | 0.011304 | 0.010745 | 637.9041 | 25.5438 | 265.137 | 347.2233 | 651.4877 | 0 | 0 | 651.4877 | 6.958e-06%
2028 | 67 | 67-24R | Tier-3 | Tier-3---13 | 5--4 | 13.6103 | 643 | 100% | 2610.8 | 93.6% | 6.065% | 0.3401% | 120.9575 | 0 | 0 | 120.9575 | 0 | 104.999 | 12.795 | 8.2062 | 104.999 | 12.795 | 8.2062 | 122.745 | 14.9575 | 8.2062 | 4.633% | 0.2194 | 0.20854 | 11899.5856 | 1685.3261 | 658.8049 | 9555.4545 | 11939.276 | 0 | 0 | 11939.276 | 0.003989%
2028 | 521 | 521-18R | Tier-3 | Tier-3---6 | 4--5 | 12.5093 | 872 | 100% | 8713.0173 | 99.36% | 0.5424% | 0.09583% | 428.5416 | 0 | 0 | 428.5416 | 0 | 372.002 | 11.76 | 31.6328 | 372.002 | 11.76 | 31.6328 | 434.8746 | 13.7476 | 31.6328 | 4.918% | 0.071321 | 0.067791 | 122165.8816 | 19717.7113 | 666.3639 | 101781.8064 | 122206.4886 | 0 | 0 | 122206.4886 | 0.01413%
2028 | 235 | 235-897R | Tier-2 | Tier-2---5 | 5--5 | 6.6053 | 288 | 100% | 4375.0381 | 88.63% | 11.27% | 0.1058% | 191.9337 | 0 | 0 | 191.9337 | 0 | 166.611 | 6.2097 | 26.8309 | 166.611 | 6.2097 | 26.8309 | 194.7701 | 7.2592 | 26.8309 | 4.387% | 0.1179 | 0.11206 | 37108.0419 | 5823.2573 | 3860.2589 | 27424.5257 | 37327.8331 | 0 | 0 | 37327.8331 | 0.006329%
2028 | 481 | CB 481 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8417 | 224 | 100% | 2.6593 | 32.47% | 0% | 67.53% | 0.042738 | 0 | 0 | 0.042738 | 0 | 0.037099 | 2.6714 | 0.013887 | 0.037099 | 2.6714 | 0.013887 | 0.043369 | 3.1229 | 0.013887 | 1.607% | 0.0074788 | 0.0071086 | 355.573 | 8.8932 | 83.5025 | 263.1773 | 368.0784 | 0 | 0 | 368.0784 | 1.409e-06%
2028 | RB1 | RB1-433R | Tier-3 | Tier-3---10 | 5--5 | 6.3644 | 324 | 100% | 5946.5075 | 99.32% | 0.6164% | 0.06772% | 292.3383 | 0 | 0 | 292.3383 | 0 | 253.7687 | 5.9831 | 42.414 | 253.7687 | 5.9831 | 42.414 | 296.6585 | 6.9944 | 42.414 | 4.916% | 0.15284 | 0.14528 | 38906.0871 | 6569.4535 | 216.2572 | 32120.3764 | 38919.9489 | 0 | 0 | 38919.9489 | 0.00964%
2028 | 58 | 58-522 | Tier-1 | Non-HFTD---8 | 2--3 | 0.66855 | 23 | 100% | 27.7406 | 11.51% | 86.26% | 2.232% | 0.15806 | 0 | 0 | 0.15806 | 0 | 0.13721 | 0.6285 | 0.2183 | 0.13721 | 0.6285 | 0.2183 | 0.16039 | 0.73473 | 0.2183 | 0.5698% | 0.012983 | 0.01234 | 2136.6878 | 9.4433 | 1891.1628 | 236.0817 | 2235.1536 | 0 | 0 | 2235.1536 | 5.212e-06%
2028 | 85 | CB 85 | Tier-1 | Non-HFTD---6 | 3--3 | 6.3067 | 296 | 100% | 49.3225 | 92.1% | 0% | 7.898% | 2.2486 | 0 | 0 | 2.2486 | 0 | 1.952 | 5.9289 | 0.32923 | 1.952 | 5.9289 | 0.32923 | 2.2819 | 6.9309 | 0.32923 | 4.559% | 0.02128 | 0.020227 | 2317.7858 | 252.1431 | 971.833 | 1093.8096 | 2327.3193 | 0 | 0 | 2327.3193 | 7.415e-05%
2028 | 79 | 79-785 | Tier-3 | Tier-3---3 | 5--5 | 13.604 | 899 | 100% | 18780.9285 | 97.14% | 2.812% | 0.0448% | 903.1022 | 0 | 0 | 903.1022 | 0 | 783.9515 | 12.7891 | 61.2982 | 783.9515 | 12.7891 | 61.2982 | 916.4483 | 14.9506 | 61.2982 | 4.809% | 0.38023 | 0.36141 | 49393.626 | 8845.5666 | 1277.0593 | 39271.0002 | 49467.0991 | 0 | 0 | 49467.0991 | 0.02978%
2028 | 396 | 396-699R | Tier-2 | Tier-2---5 | 5--5 | 20.4475 | 1782 | 100% | 3136.9517 | 88.18% | 11.4% | 0.4202% | 136.9258 | 0 | 0 | 136.9258 | 0 | 118.8605 | 19.2227 | 6.1833 | 118.8605 | 19.2227 | 6.1833 | 138.9493 | 22.4716 | 6.1833 | 4.365% | 0.15664 | 0.14888 | 20026.8881 | 3486.3931 | 2134.8995 | 14405.5955 | 20150.1614 | 0 | 0 | 20150.1614 | 0.004515%
2028 | 130 | 130-14F | Tier-1 | Non-HFTD---17 | 1--1 | 0.84125 | 47 | 100% | 1.0142 | 40.98% | 0% | 59.02% | 0.020571 | 0 | 0 | 0.020571 | 0 | 0.017857 | 0.79086 | 0.022579 | 0.017857 | 0.79086 | 0.022579 | 0.020875 | 0.92452 | 0.022579 | 2.028% | 0.002514 | 0.0023896 | 403.4011 | 3.3646 | 167.0213 | 233.0153 | 415.8008 | 0 | 0 | 415.8008 | 6.783e-07%
2028 | 361 | CB 361 | Tier-1 | Non-HFTD---5 | 2--4 | 1.65 | 12 | 100% | 72.0528 | 3.654% | 93.91% | 2.433% | 0.13032 | 0 | 0 | 0.13032 | 0 | 0.11312 | 1.5512 | 0.072929 | 0.11312 | 1.5512 | 0.072929 | 0.13224 | 1.8133 | 0.072929 | 0.1809% | 0.010387 | 0.0098725 | 6937.0919 | 7.1268 | 6176.303 | 753.6622 | 7285.1607 | 0 | 0 | 7285.1607 | 4.297e-06%
2028 | 310 | 310-719F | Tier-1 | Non-HFTD---3 | 3--4 | 3.2121 | 143 | 100% | 124.5147 | 2.263% | 95.99% | 1.745% | 0.13948 | 0 | 0 | 0.13948 | 0 | 0.12108 | 3.0197 | 0.040097 | 0.12108 | 3.0197 | 0.040097 | 0.14154 | 3.5301 | 0.040097 | 0.112% | 0.025632 | 0.024363 | 4857.7828 | 6.9446 | 4370.4656 | 480.3726 | 5105.0406 | 0 | 0 | 5105.0406 | 4.6e-06%
2028 | 1283 | CB 1283 | Tier-1 | Non-HFTD---15 | 1--3 | 0.69583 | 17 | 100% | 4.6015 | 87.53% | 0% | 12.47% | 0.19938 | 0 | 0 | 0.19938 | 0 | 0.17307 | 0.65415 | 0.26457 | 0.17307 | 0.65415 | 0.26457 | 0.20232 | 0.76471 | 0.26457 | 4.333% | 0.002425 | 0.002305 | 1897.5339 | 258.5117 | 88.6838 | 1550.3385 | 1909.8545 | 0 | 0 | 1909.8545 | 6.575e-06%
2028 | 518 | CB 518 | Tier-1 | Non-HFTD---11 | 2--3 | 2.5012 | 35 | 100% | 15.0618 | 85.82% | 0% | 14.18% | 0.63981 | 0 | 0 | 0.63981 | 0 | 0.55539 | 2.3513 | 0.2362 | 0.55539 | 2.3513 | 0.2362 | 0.64926 | 2.7487 | 0.2362 | 4.248% | 0.008289 | 0.0078787 | 1817.08 | 17.4829 | 1476.3748 | 323.2224 | 1830.5026 | 0 | 0 | 1830.5026 | 2.11e-05%
2028 | 1458 | 1458-601R | Tier-3 | Tier-3---2 | 5--5 | 15.4477 | 850 | 100% | 37077.302 | 99.36% | 0.615% | 0.02874% | 1823.5109 | 0 | 0 | 1823.5109 | 0 | 1582.9263 | 14.5224 | 108.9986 | 1582.9263 | 14.5224 | 108.9986 | 1850.4589 | 16.9769 | 108.9986 | 4.918% | 0.20421 | 0.1941 | 181561.9083 | 39229.4205 | 1054.6776 | 141277.8102 | 181622.7804 | 0 | 0 | 181622.7804 | 0.06013%
2028 | 76 | CB 76 | Tier-1 | Non-HFTD---17 | 1--2 | 0.68485 | 11 | 100% | 2.0654 | 56.67% | 0% | 43.33% | 0.057942 | 0 | 0 | 0.057942 | 0 | 0.050298 | 0.64383 | 0.078122 | 0.050298 | 0.64383 | 0.078122 | 0.058798 | 0.75265 | 0.078122 | 2.805% | 0.0027636 | 0.0026268 | 747.3661 | 2.0048 | 442.1787 | 303.1826 | 764.2293 | 0 | 0 | 764.2293 | 1.911e-06%
2028 | 209 | 209-1769F | Tier-2 | Tier-2---6 | 5--5 | 31.9017 | 2321 | 100% | 8462.8018 | 99.74% | 0% | 0.2593% | 417.8226 | 0 | 0 | 417.8226 | 0 | 362.6973 | 29.9908 | 12.0936 | 362.6973 | 29.9908 | 12.0936 | 423.9973 | 35.0596 | 12.0936 | 4.937% | 0.11169 | 0.10616 | 75768.5529 | 12314.8084 | 115.8328 | 63337.9117 | 75778.7828 | 0 | 0 | 75778.7828 | 0.01378%
2028 | 169 | CB 169 | Tier-1 | Non-HFTD---19 | 1--2 | 0.17503 | 9 | 100% | 0.4733 | 37.59% | 0% | 62.41% | 0.008807 | 0 | 0 | 0.008807 | 0 | 0.0076451 | 0.16455 | 0.046461 | 0.0076451 | 0.16455 | 0.046461 | 0.0089372 | 0.19236 | 0.046461 | 1.861% | 0.0007436 | 0.00070679 | 636.5041 | 14.2067 | 190.1326 | 432.1648 | 657.1913 | 0 | 0 | 657.1913 | 2.904e-07%
2028 | 415 | 415-33 | Tier-1 | Non-HFTD---3 | 4--3 | 9.518 | 398 | 100% | 139.7786 | 20.17% | 75.04% | 4.79% | 1.3955 | 0 | 0 | 1.3955 | 0 | 1.2114 | 8.9479 | 0.13538 | 1.2114 | 8.9479 | 0.13538 | 1.4161 | 10.4602 | 0.13538 | 0.9983% | 0.039288 | 0.037343 | 3557.7759 | 167.3493 | 2542.2057 | 848.2208 | 3705.6889 | 0 | 0 | 3705.6889 | 4.602e-05%
2028 | QN1 | CB QN1 | Tier-1 | Non-HFTD---12 | 2--2 | 2.5479 | 232 | 100% | 9.4771 | 20.58% | 60.74% | 18.68% | 0.096528 | 0 | 0 | 0.096528 | 0 | 0.083793 | 2.3953 | 0.034982 | 0.083793 | 2.3953 | 0.034982 | 0.097955 | 2.8001 | 0.034982 | 1.019% | 0.01229 | 0.011681 | 771.15 | 21.6223 | 474.8473 | 274.6805 | 803.0463 | 0 | 0 | 803.0463 | 3.183e-06%
2028 | 535 | CB 535 | Tier-2 | Tier-2---16 | 4--3 | 0.31174 | 0 | 100% | 111.4983 | 4.585% | 95.12% | 0.2939% | 0.25308 | 0 | 0 | 0.25308 | 0 | 0.21969 | 0.29307 | 0.74961 | 0.21969 | 0.29307 | 0.74961 | 0.25682 | 0.3426 | 0.74961 | 0.227% | 0.059698 | 0.056743 | 1867.7052 | 14.9488 | 1426.0626 | 426.6938 | 1960.5113 | 0 | 0 | 1960.5113 | 8.346e-06%
2028 | 72 | 72-16 | Tier-1 | Non-HFTD---14 | 2--1 | 4.3345 | 108 | 100% | 6.3445 | 45.63% | 0% | 54.37% | 0.1433 | 0 | 0 | 0.1433 | 0 | 0.12439 | 4.0748 | 0.030527 | 0.12439 | 4.0748 | 0.030527 | 0.14542 | 4.7635 | 0.030527 | 2.259% | 0.012945 | 0.012305 | 490.0991 | 5.3198 | 229.2157 | 255.5636 | 503.9765 | 0 | 0 | 503.9765 | 4.725e-06%
2028 | 246 | CB 246 | Tier-2 | Tier-2---7 | 4--5 | 11.0435 | 650 | 100% | 1438.4419 | 90% | 9.47% | 0.5268% | 64.0848 | 0 | 0 | 64.0848 | 0 | 55.6298 | 10.382 | 5.3583 | 55.6298 | 10.382 | 5.3583 | 65.0319 | 12.1367 | 5.3583 | 4.455% | 0.066431 | 0.063143 | 21653.0415 | 4674.1804 | 2209.0046 | 14769.8565 | 21765.7701 | 0 | 0 | 21765.7701 | 0.002113%
2028 | 197 | 197-1157F | Tier-2 | Tier-2---18 | 3--3 | 0.44794 | 76 | 100% | 63.1655 | 1.305% | 98.13% | 0.5601% | 0.040803 | 0 | 0 | 0.040803 | 0 | 0.03542 | 0.42111 | 0.08411 | 0.03542 | 0.42111 | 0.08411 | 0.041406 | 0.49229 | 0.08411 | 0.0646% | 0.01787 | 0.016985 | 3534.7635 | 11.6765 | 2974.4275 | 548.6595 | 3716.4442 | 0 | 0 | 3716.4442 | 1.346e-06%
2028 | 230 | 230-133AE | Tier-2 | Tier-2---6 | 5--5 | 11.3506 | 1480 | 100% | 6388.6939 | 98.26% | 1.615% | 0.1229% | 310.7459 | 0 | 0 | 310.7459 | 0 | 269.7477 | 10.6707 | 25.2793 | 269.7477 | 10.6707 | 25.2793 | 315.3382 | 12.4742 | 25.2793 | 4.864% | 0.095565 | 0.090834 | 66852.0974 | 10704.3112 | 1013.9772 | 55133.809 | 66912.5857 | 0 | 0 | 66912.5857 | 0.01025%
2028 | 355 | 355-41R | Tier-2 | Tier-2---6 | 4--5 | 6.2962 | 610 | 100% | 7500.5861 | 98.5% | 1.439% | 0.05987% | 365.7128 | 0 | 0 | 365.7128 | 0 | 317.4625 | 5.9191 | 53.6337 | 317.4625 | 5.9191 | 53.6337 | 371.1173 | 6.9195 | 53.6337 | 4.876% | 0.092253 | 0.087687 | 81304.346 | 12979.0487 | 1073.0006 | 67252.2967 | 81367.8246 | 0 | 0 | 81367.8246 | 0.01206%
2028 | 353 | 353-900F | Tier-2 | Tier-2---8 | 5--5 | 0.99152 | 180 | 100% | 1991.3582 | 88.69% | 11.27% | 0.03442% | 87.4279 | 0 | 0 | 87.4279 | 0 | 75.8931 | 0.93213 | 81.4193 | 75.8931 | 0.93213 | 81.4193 | 88.7199 | 1.0897 | 81.4193 | 4.39% | 0.10085 | 0.09586 | 19745.2341 | 2847.6968 | 2035.1188 | 14862.4185 | 19861.49 | 0 | 0 | 19861.49 | 0.002883%
2028 | 298 | 298-384 | Tier-1 | Non-HFTD---19 | 1--2 | 0.022348 | 0 | 100% | 0.1467 | 75.48% | 0% | 24.52% | 0.0054809 | 0 | 0 | 0.0054809 | 0 | 0.0047578 | 0.02101 | 0.22645 | 0.0047578 | 0.02101 | 0.22645 | 0.0055619 | 0.024561 | 0.22645 | 3.736% | 0.0001034 | 9.8282e-05 | 1418.7583 | 113.2285 | 410.6318 | 894.898 | 1436.8769 | 0 | 0 | 1436.8769 | 1.807e-07%
2028 | 728 | 728-1570F | Tier-2 | Tier-2---19 | 1--5 | 0.074417 | 14 | 100% | 33.2807 | 99.79% | 0% | 0.2133% | 1.6439 | 0 | 0 | 1.6439 | 0 | 1.427 | 0.069959 | 20.3976 | 1.427 | 0.069959 | 20.3976 | 1.6682 | 0.081783 | 20.3976 | 4.939% | 0.0003472 | 0.00033001 | 95854.6419 | 22304.1965 | 20.1049 | 73530.3404 | 95865.2904 | 0 | 0 | 95865.2904 | 5.421e-05%
2028 | 176 | CB 176 | Tier-1 | Non-HFTD---10 | 4--1 | 0.063306 | 6 | 100% | 15.5544 | 4.631% | 94.88% | 0.4893% | 0.035657 | 0 | 0 | 0.035657 | 0 | 0.030953 | 0.059514 | 0.52009 | 0.030953 | 0.059514 | 0.52009 | 0.036184 | 0.069573 | 0.52009 | 0.2292% | 0.032585 | 0.030972 | 477.3549 | 3.466 | 417.7975 | 56.0913 | 501.0632 | 0 | 0 | 501.0632 | 1.176e-06%
2028 | 44 | CB 44 | Tier-1 | Non-HFTD---9 | 3--2 | 5.4639 | 138 | 100% | 25.8658 | 84.4% | 0% | 15.6% | 1.0806 | 0 | 0 | 1.0806 | 0 | 0.93804 | 5.1366 | 0.18262 | 0.93804 | 5.1366 | 0.18262 | 1.0966 | 6.0047 | 0.18262 | 4.178% | 0.016291 | 0.015485 | 1587.7136 | 11.2067 | 1294.5636 | 281.9434 | 1600.6131 | 0 | 0 | 1600.6131 | 3.563e-05%
2028 | 358 | CB 358 | Tier-3 | Tier-3---15 | 5--4 | 0.31499 | 10 | 100% | 861.4334 | 18.88% | 81.11% | 0.0161% | 8.0496 | 0 | 0 | 8.0496 | 0 | 6.9875 | 0.29613 | 23.5965 | 6.9875 | 0.29613 | 23.5965 | 8.1685 | 0.34617 | 23.5965 | 0.9344% | 0.1387 | 0.13184 | 6210.6059 | 197.9224 | 4526.0062 | 1486.6772 | 6472.9843 | 0 | 0 | 6472.9843 | 0.0002654%
2028 | 907 | 907-1716R | Tier-3 | Tier-3---2 | 4--5 | 12.7815 | 1624 | 100% | 27066.4552 | 99.19% | 0.7771% | 0.02941% | 1328.9846 | 0 | 0 | 1328.9846 | 0 | 1153.6452 | 12.0159 | 96.01 | 1153.6452 | 12.0159 | 96.01 | 1348.6244 | 14.0467 | 96.01 | 4.91% | 0.088049 | 0.083691 | 307401.4891 | 65823.1334 | 2297.2385 | 239281.1172 | 307530.5948 | 0 | 0 | 307530.5948 | 0.04382%
2028 | 1166 | 1166-15R | Tier-3 | Tier-3---11 | 5--5 | 5.0748 | 159 | 100% | 3965.2217 | 98.26% | 1.658% | 0.07833% | 192.8712 | 0 | 0 | 192.8712 | 0 | 167.4248 | 4.7708 | 35.0936 | 167.4248 | 4.7708 | 35.0936 | 195.7215 | 5.5771 | 35.0936 | 4.864% | 0.19397 | 0.18436 | 20442.8701 | 3274.5374 | 313.5505 | 16854.7822 | 20461.351 | 0 | 0 | 20461.351 | 0.00636%
2028 | 759 | CB 759 | Tier-1 | Non-HFTD---11 | 2--2 | 3.6532 | 193 | 100% | 13.6768 | 80.97% | 0% | 19.03% | 0.5482 | 0 | 0 | 0.5482 | 0 | 0.47587 | 3.4344 | 0.13856 | 0.47587 | 3.4344 | 0.13856 | 0.5563 | 4.0148 | 0.13856 | 4.008% | 0.010883 | 0.010344 | 1256.7154 | 15.5947 | 944.7873 | 296.3334 | 1269.1674 | 0 | 0 | 1269.1674 | 1.808e-05%
2028 | 325 | 325-1227F | Tier-1 | Non-HFTD---13 | 1--4 | 0.24205 | 4 | 100% | 7.4492 | 97.14% | 0% | 2.857% | 0.3582 | 0 | 0 | 0.3582 | 0 | 0.31094 | 0.22755 | 1.3665 | 0.31094 | 0.22755 | 1.3665 | 0.36349 | 0.26601 | 1.3665 | 4.809% | 0.000908 | 0.00086305 | 8203.9485 | 1304.1799 | 23.899 | 6875.8695 | 8216.1539 | 0 | 0 | 8216.1539 | 1.181e-05%
2028 | 203 | CB 203 | Tier-2 | Tier-2---13 | 4--4 | 6.2051 | 618 | 100% | 195.752 | 9.583% | 88.23% | 2.187% | 0.9286 | 0 | 0 | 0.9286 | 0 | 0.80609 | 5.8334 | 0.13818 | 0.80609 | 5.8334 | 0.13818 | 0.94233 | 6.8193 | 0.13818 | 0.4744% | 0.03541 | 0.033657 | 5528.1246 | 34.2367 | 4807.7085 | 686.1793 | 5788.4276 | 0 | 0 | 5788.4276 | 3.062e-05%
2028 | 794 | 794-1002 | Tier-1 | Non-HFTD---4 | 3--4 | 1.1659 | 43 | 100% | 176.6639 | 5.845% | 93.67% | 0.4796% | 0.51118 | 0 | 0 | 0.51118 | 0 | 0.44374 | 1.096 | 0.40486 | 0.44374 | 1.096 | 0.40486 | 0.51873 | 1.2813 | 0.40486 | 0.2894% | 0.021091 | 0.020047 | 8376.1891 | 42.6247 | 7445.0358 | 888.5286 | 8786.9043 | 0 | 0 | 8786.9043 | 1.686e-05%
2028 | NVS1 | CB NVS1 | Tier-2 | Tier-2---12 | 4--5 | 10.0271 | 878 | 100% | 638.0788 | 99.02% | 0% | 0.9838% | 31.2742 | 0 | 0 | 31.2742 | 0 | 27.148 | 9.4265 | 2.88 | 27.148 | 9.4265 | 2.88 | 31.7363 | 11.0197 | 2.88 | 4.901% | 0.029239 | 0.027792 | 21822.7187 | 3513.3113 | 81.7568 | 18227.6506 | 21833.8993 | 0 | 0 | 21833.8993 | 0.001031%
2028 | 795 | CB 795 | Tier-1 | Non-HFTD---12 | 3--2 | 0.64564 | 34 | 100% | 12.7544 | 93.94% | 1.477% | 4.587% | 0.59306 | 0 | 0 | 0.59306 | 0 | 0.51481 | 0.60697 | 0.84817 | 0.51481 | 0.60697 | 0.84817 | 0.60182 | 0.70956 | 0.84817 | 4.65% | 0.020541 | 0.019524 | 620.9301 | 28.9913 | 416.0915 | 175.8474 | 622.891 | 0 | 0 | 622.891 | 1.956e-05%
2028 | 74 | 74-35R | Tier-1 | Non-HFTD---5 | 2--4 | 1.7629 | 93 | 100% | 50.9295 | 97.64% | 0% | 2.355% | 2.4616 | 0 | 0 | 2.4616 | 0 | 2.1369 | 1.6573 | 1.2894 | 2.1369 | 1.6573 | 1.2894 | 2.498 | 1.9374 | 1.2894 | 4.833% | 0.0071104 | 0.0067584 | 7162.6834 | 1136.9423 | 64.4037 | 5961.3374 | 7171.4683 | 0 | 0 | 7171.4683 | 8.118e-05%
2028 | 444 | CB 444 | Tier-2 | Tier-2---16 | 4--2 | 0.43141 | 4 | 100% | 117.4434 | 97.68% | 1.947% | 0.3705% | 5.6787 | 0 | 0 | 5.6787 | 0 | 4.9295 | 0.40557 | 12.1544 | 4.9295 | 0.40557 | 12.1544 | 5.7626 | 0.47412 | 12.1544 | 4.835% | 0.081621 | 0.07758 | 1438.8937 | 193.307 | 35.5972 | 1209.9894 | 1440.6306 | 0 | 0 | 1440.6306 | 0.0001873%
2028 | 247 | 247-48 | Tier-2 | Tier-2---16 | 3--3 | 0.44811 | 21 | 100% | 105.2026 | 98.18% | 1.532% | 0.2854% | 5.1129 | 0 | 0 | 5.1129 | 0 | 4.4383 | 0.42126 | 10.5357 | 4.4383 | 0.42126 | 10.5357 | 5.1885 | 0.49246 | 10.5357 | 4.86% | 0.026216 | 0.024918 | 4012.9756 | 640.3206 | 51.944 | 3320.7111 | 4016.7732 | 0 | 0 | 4016.7732 | 0.0001686%
2028 | 322 | 322-821F | Tier-1 | Non-HFTD---10 | 4--2 | 12.5641 | 239 | 100% | 18.5107 | 56.59% | 0% | 43.41% | 0.51854 | 0 | 0 | 0.51854 | 0 | 0.45013 | 11.8115 | 0.038109 | 0.45013 | 11.8115 | 0.038109 | 0.5262 | 13.8078 | 0.038109 | 2.801% | 0.033072 | 0.031435 | 559.7082 | 23.5182 | 196.1441 | 340.0459 | 572.3609 | 0 | 0 | 572.3609 | 1.71e-05%
2028 | 206 | 206-1105 | Tier-2 | Tier-2---9 | 3--5 | 4.2677 | 342 | 100% | 1279.0443 | 99.78% | 0% | 0.2159% | 63.176 | 0 | 0 | 63.176 | 0 | 54.8409 | 4.012 | 13.6691 | 54.8409 | 4.012 | 13.6691 | 64.1096 | 4.6901 | 13.6691 | 4.939% | 0.014019 | 0.013325 | 91236.4892 | 14837.9635 | 119.2359 | 76279.2897 | 91246.7455 | 0 | 0 | 91246.7455 | 0.002083%
2028 | 204 | CB 204 | Tier-2 | Tier-2---9 | 4--4 | 14.6288 | 344 | 100% | 1059.5314 | 80.82% | 18.41% | 0.7661% | 42.3888 | 0 | 0 | 42.3888 | 0 | 36.7962 | 13.7525 | 2.6756 | 36.7962 | 13.7525 | 2.6756 | 43.0152 | 16.0768 | 2.6756 | 4.001% | 0.068524 | 0.065132 | 15462.1941 | 1952.7232 | 2912.9931 | 10596.4779 | 15616.619 | 0 | 0 | 15616.619 | 0.001398%
2028 | 1073 | 1073-886F | Tier-2 | Tier-2---20 | 3--2 | 0.11231 | 26 | 100% | 27.0781 | 12.75% | 86.83% | 0.4178% | 0.17092 | 0 | 0 | 0.17092 | 0 | 0.14837 | 0.10558 | 1.4053 | 0.14837 | 0.10558 | 1.4053 | 0.17345 | 0.12343 | 1.4053 | 0.6312% | 0.016776 | 0.015946 | 1614.0782 | 34.779 | 1276.2143 | 303.0849 | 1687.417 | 0 | 0 | 1687.417 | 5.636e-06%
2028 | 546 | 546-12 | Tier-1 | Non-HFTD---11 | 2--2 | 0.83025 | 13 | 100% | 14.4143 | 0.3875% | 96.68% | 2.928% | 0.0027652 | 0 | 0 | 0.0027652 | 0 | 0.0024004 | 0.78052 | 0.0030753 | 0.0024004 | 0.78052 | 0.0030753 | 0.002806 | 0.91244 | 0.0030753 | 0.01918% | 0.01256 | 0.011939 | 1147.5972 | 1.952 | 997.2808 | 148.3644 | 1207.13 | 0 | 0 | 1207.13 | 9.119e-08%
2028 | 266 | 266-485F | Tier-2 | Tier-2---21 | 1--4 | 0.18886 | 56 | 100% | 3.9025 | 97.35% | 0% | 2.654% | 0.18805 | 0 | 0 | 0.18805 | 0 | 0.16324 | 0.17754 | 0.91943 | 0.16324 | 0.17754 | 0.91943 | 0.19083 | 0.20755 | 0.91943 | 4.819% | 0.000646 | 0.00061402 | 6041.0896 | 954.7948 | 18.9693 | 5067.3254 | 6049.4401 | 0 | 0 | 6049.4401 | 6.201e-06%
2028 | RB1 | RB1-427R | Tier-3 | Tier-3---7 | 5--5 | 12.6949 | 1154 | 100% | 6920.124 | 97.57% | 2.306% | 0.1195% | 334.2371 | 0 | 0 | 334.2371 | 0 | 290.1396 | 11.9345 | 24.311 | 290.1396 | 11.9345 | 24.311 | 339.1765 | 13.9516 | 24.311 | 4.83% | 0.15381 | 0.14619 | 44992.7829 | 7465.1678 | 918.5464 | 36609.0687 | 45049.6194 | 0 | 0 | 45049.6194 | 0.01102%
2028 | 859 | CB 859 | Tier-1 | Non-HFTD---13 | 1--4 | 0.2674 | 5 | 100% | 6.3536 | 96.15% | 0% | 3.853% | 0.30239 | 0 | 0 | 0.30239 | 0 | 0.26249 | 0.25138 | 1.0442 | 0.26249 | 0.25138 | 1.0442 | 0.30686 | 0.29387 | 1.0442 | 4.759% | 0.0009722 | 0.00092408 | 6535.3261 | 323.1257 | 4329.0086 | 1883.1918 | 6548.4396 | 0 | 0 | 6548.4396 | 9.972e-06%
2028 | 376 | 376-491R | Tier-1 | Non-HFTD---10 | 2--2 | 4.3338 | 110 | 100% | 15.387 | 85.15% | 0% | 14.85% | 0.64853 | 0 | 0 | 0.64853 | 0 | 0.56297 | 4.0742 | 0.13818 | 0.56297 | 4.0742 | 0.13818 | 0.65811 | 4.7627 | 0.13818 | 4.215% | 0.011779 | 0.011196 | 1306.2651 | 20.6652 | 1016.2338 | 269.3662 | 1316.3691 | 0 | 0 | 1316.3691 | 2.139e-05%
2028 | 216 | 216-220R | Tier-3 | Tier-3---20 | 1--5 | 0.052462 | 7 | 100% | 71.2816 | 99.9% | 0% | 0.09987% | 3.5249 | 0 | 0 | 3.5249 | 0 | 3.0599 | 0.04932 | 62.0412 | 3.0599 | 0.04932 | 62.0412 | 3.577 | 0.057655 | 62.0412 | 4.945% | 0.000285 | 0.00027089 | 250110.7129 | 40302.5833 | 22.6906 | 209785.4391 | 250123.7212 | 0 | 0 | 250123.7212 | 0.0001162%
2028 | 310 | 310-718F | Tier-1 | Non-HFTD---17 | 1--3 | 0.087462 | 0 | 100% | 0.81802 | 90.7% | 0% | 9.303% | 0.036725 | 0 | 0 | 0.036725 | 0 | 0.03188 | 0.082223 | 0.38772 | 0.03188 | 0.082223 | 0.38772 | 0.037268 | 0.09612 | 0.38772 | 4.49% | 0.000254 | 0.00024143 | 3220.5537 | 0.90818 | 2943.8401 | 275.8054 | 3236.1564 | 0 | 0 | 3236.1564 | 1.211e-06%
2028 | 548 | 548-15F | Tier-1 | Non-HFTD---11 | 2--3 | 1.8856 | 63 | 100% | 14.762 | 91.23% | 0% | 8.768% | 0.66665 | 0 | 0 | 0.66665 | 0 | 0.57869 | 1.7727 | 0.32645 | 0.57869 | 1.7727 | 0.32645 | 0.6765 | 2.0723 | 0.32645 | 4.516% | 0.005445 | 0.0051755 | 2711.1073 | 395.5509 | 80.5547 | 2235.0017 | 2723.487 | 0 | 0 | 2723.487 | 2.198e-05%
2028 | 1022 | 1022-322R | Tier-3 | Tier-3---10 | 5--5 | 3.6661 | 275 | 100% | 5072.1995 | 99.16% | 0.7912% | 0.04875% | 248.9649 | 0 | 0 | 248.9649 | 0 | 216.1178 | 3.4465 | 62.7064 | 216.1178 | 3.4465 | 62.7064 | 252.6441 | 4.029 | 62.7064 | 4.908% | 0.10587 | 0.10063 | 47911.5964 | 8502.7198 | 346.5755 | 39062.3011 | 47932.5548 | 0 | 0 | 47932.5548 | 0.00821%
2028 | 463 | 463-1229 | Tier-2 | Tier-2---9 | 5--4 | 11.4998 | 62 | 100% | 1378.3182 | 99.02% | 0.574% | 0.4088% | 67.5562 | 0 | 0 | 67.5562 | 0 | 58.6432 | 10.8109 | 5.4244 | 58.6432 | 10.8109 | 5.4244 | 68.5546 | 12.6381 | 5.4244 | 4.901% | 0.096723 | 0.091935 | 14250.1892 | 3311.1583 | 71.0827 | 10867.9482 | 14257.4826 | 0 | 0 | 14257.4826 | 0.002228%
2028 | 296 | 296-68F | Tier-2 | Tier-2---21 | 1--2 | 0.92708 | 47 | 100% | 3.2301 | 78.97% | 0% | 21.03% | 0.12626 | 0 | 0 | 0.12626 | 0 | 0.1096 | 0.87155 | 0.12576 | 0.1096 | 0.87155 | 0.12576 | 0.12813 | 1.0189 | 0.12576 | 3.909% | 0.0027146 | 0.0025802 | 1189.8836 | 223.7824 | 100.9033 | 865.1979 | 1202.9164 | 0 | 0 | 1202.9164 | 4.164e-06%
2028 | 327 | CB 327 | Tier-3 | Tier-3---16 | 4--5 | 0.87727 | 18 | 100% | 1456.7095 | 99.79% | 0.1579% | 0.0494% | 71.9576 | 0 | 0 | 71.9576 | 0 | 62.4639 | 0.82472 | 75.7391 | 62.4639 | 0.82472 | 75.7391 | 73.021 | 0.96411 | 75.7391 | 4.94% | 0.076966 | 0.073157 | 18926.5639 | 3241.7353 | 24.8136 | 15660.0149 | 18928.6074 | 0 | 0 | 18928.6074 | 0.002373%
2028 | 1406 | 1406-19F | Tier-1 | Non-HFTD---11 | 3--2 | 5.6559 | 78 | 100% | 15.0674 | 83.86% | 0% | 16.14% | 0.62542 | 0 | 0 | 0.62542 | 0 | 0.54291 | 5.3171 | 0.10211 | 0.54291 | 5.3171 | 0.10211 | 0.63467 | 6.2157 | 0.10211 | 4.151% | 0.013569 | 0.012898 | 1110.3933 | 84.7049 | 427.6552 | 598.0332 | 1119.7291 | 0 | 0 | 1119.7291 | 2.062e-05%
2028 | BT1 | CB BT1 | Tier-1 | Non-HFTD---17 | 1--1 | 1.1276 | 81 | 100% | 1.503 | 53.13% | 0% | 46.87% | 0.03953 | 0 | 0 | 0.03953 | 0 | 0.034315 | 1.0601 | 0.032371 | 0.034315 | 1.0601 | 0.032371 | 0.040115 | 1.2392 | 0.032371 | 2.63% | 0.0030182 | 0.0028688 | 497.9935 | 40.6456 | 38.8309 | 418.5169 | 510.1485 | 0 | 0 | 510.1485 | 1.304e-06%
2028 | 509 | CB 509 | Tier-1 | Non-HFTD---10 | 3--2 | 10.0667 | 447 | 100% | 23.3118 | 74.78% | 0% | 25.22% | 0.86292 | 0 | 0 | 0.86292 | 0 | 0.74907 | 9.4637 | 0.079152 | 0.74907 | 9.4637 | 0.079152 | 0.87567 | 11.0631 | 0.079152 | 3.702% | 0.027199 | 0.025853 | 857.0759 | 12.4778 | 585.3688 | 259.2293 | 868.3324 | 0 | 0 | 868.3324 | 2.846e-05%
2028 | 567 | CB 567 | Tier-1 | Non-HFTD---7 | 1--4 | 0.56364 | 51 | 100% | 37.3049 | 99.02% | 0% | 0.9826% | 1.8284 | 0 | 0 | 1.8284 | 0 | 1.5872 | 0.52988 | 2.9954 | 1.5872 | 0.52988 | 2.9954 | 1.8555 | 0.61943 | 2.9954 | 4.901% | 0.0023798 | 0.002262 | 15675.6634 | 2324.2738 | 1292.524 | 12058.8657 | 15683.6852 | 0 | 0 | 15683.6852 | 6.03e-05%
2028 | 900 | 900-1163F | Tier-1 | Non-HFTD---19 | 1--1 | 0.24072 | 21 | 100% | 0.28819 | 42.17% | 0% | 57.83% | 0.0060154 | 0 | 0 | 0.0060154 | 0 | 0.0052218 | 0.2263 | 0.023075 | 0.0052218 | 0.2263 | 0.023075 | 0.0061043 | 0.26455 | 0.023075 | 2.087% | 0.0008402 | 0.00079861 | 343.0068 | 17.2218 | 58.4349 | 267.35 | 353.3375 | 0 | 0 | 353.3375 | 1.984e-07%
2028 | 1180 | 1180-9 | Tier-1 | Non-HFTD---15 | 2--2 | 2.6981 | 65 | 100% | 4.0697 | 57.31% | 0% | 42.69% | 0.11546 | 0 | 0 | 0.11546 | 0 | 0.10023 | 2.5365 | 0.039514 | 0.10023 | 2.5365 | 0.039514 | 0.11717 | 2.9652 | 0.039514 | 2.837% | 0.00751 | 0.0071383 | 541.9067 | 54.2911 | 113.8438 | 373.7718 | 553.9532 | 0 | 0 | 553.9532 | 3.807e-06%
2028 | NO2 | CB NO2 | Tier-1 | Non-HFTD---12 | 3--1 | 8.0842 | 188 | 100% | 8.9476 | 36.78% | 0% | 63.22% | 0.16292 | 0 | 0 | 0.16292 | 0 | 0.14142 | 7.6 | 0.018609 | 0.14142 | 7.6 | 0.018609 | 0.16533 | 8.8845 | 0.018609 | 1.821% | 0.022313 | 0.021209 | 401.0024 | 0.19075 | 170.5339 | 230.2778 | 414.204 | 0 | 0 | 414.204 | 5.372e-06%
2028 | 35 | 35-2 | Tier-1 | Non-HFTD---5 | 2--4 | 0.48065 | 5 | 100% | 55.5571 | 6.064% | 93.16% | 0.7781% | 0.16677 | 0 | 0 | 0.16677 | 0 | 0.14477 | 0.45186 | 0.32038 | 0.14477 | 0.45186 | 0.32038 | 0.16923 | 0.52823 | 0.32038 | 0.3002% | 0.0075196 | 0.0071474 | 7388.3078 | 76.3747 | 6138.5143 | 1173.4188 | 7749.742 | 0 | 0 | 7749.742 | 5.499e-06%
2028 | 462 | 462-1523F | Tier-1 | Non-HFTD---13 | 1--3 | 0.86758 | 18 | 100% | 5.2887 | 89.35% | 0% | 10.65% | 0.2339 | 0 | 0 | 0.2339 | 0 | 0.20304 | 0.81561 | 0.24895 | 0.20304 | 0.81561 | 0.24895 | 0.23736 | 0.95346 | 0.24895 | 4.423% | 0.0023366 | 0.0022209 | 2263.4326 | 314.0218 | 110.4125 | 1838.9983 | 2275.9905 | 0 | 0 | 2275.9905 | 7.713e-06%
2028 | 973 | 973-626R | Tier-3 | Tier-3---7 | 5--5 | 10.906 | 208 | 100% | 6521.7236 | 98.03% | 1.864% | 0.1053% | 316.4676 | 0 | 0 | 316.4676 | 0 | 274.7145 | 10.2528 | 26.7942 | 274.7145 | 10.2528 | 26.7942 | 321.1444 | 11.9856 | 26.7942 | 4.853% | 0.1523 | 0.14476 | 42821.6164 | 7446.1094 | 721.9925 | 34653.5145 | 42865.5348 | 0 | 0 | 42865.5348 | 0.01044%
2028 | 190 | 190-1125F | Tier-1 | Non-HFTD---17 | 1--4 | 0.044508 | 0 | 100% | 1.3314 | 97.57% | 0% | 2.433% | 0.064301 | 0 | 0 | 0.064301 | 0 | 0.055818 | 0.041842 | 1.334 | 0.055818 | 0.041842 | 1.334 | 0.065251 | 0.048913 | 1.334 | 4.83% | 0.0001574 | 0.00014961 | 8458.7881 | 1300.024 | 20.0108 | 7138.7533 | 8469.5078 | 0 | 0 | 8469.5078 | 2.12e-06%
2028 | 63 | CB 63 | Tier-1 | Non-HFTD---1 | 3--4 | 2.7163 | 250 | 100% | 198.805 | 36.18% | 62.9% | 0.9206% | 3.5599 | 0 | 0 | 3.5599 | 0 | 3.0903 | 2.5536 | 1.2102 | 3.0903 | 2.5536 | 1.2102 | 3.6125 | 2.9852 | 1.2102 | 1.791% | 0.019218 | 0.018267 | 10344.6205 | 564.0493 | 6645.6212 | 3134.95 | 10688.4616 | 0 | 0 | 10688.4616 | 0.0001174%
2028 | 325 | 325-22R | Tier-1 | Non-HFTD---12 | 3--2 | 8.3706 | 226 | 100% | 13.8312 | 56.1% | 0% | 43.9% | 0.38407 | 0 | 0 | 0.38407 | 0 | 0.3334 | 7.8692 | 0.042368 | 0.3334 | 7.8692 | 0.042368 | 0.38975 | 9.1992 | 0.042368 | 2.777% | 0.024153 | 0.022957 | 572.6603 | 37.8929 | 176.6374 | 358.13 | 585.7531 | 0 | 0 | 585.7531 | 1.267e-05%
2028 | 1219 | CB 1219 | Tier-1 | Non-HFTD---19 | 1--1 | 0.23918 | 9 | 100% | 0.3441 | 26.91% | 0% | 73.09% | 0.0045828 | 0 | 0 | 0.0045828 | 0 | 0.0039781 | 0.22486 | 0.017692 | 0.0039781 | 0.22486 | 0.017692 | 0.0046505 | 0.26286 | 0.017692 | 1.332% | 0.0008074 | 0.00076743 | 426.1824 | 17.8119 | 34.3349 | 374.0356 | 442.4055 | 0 | 0 | 442.4055 | 1.511e-07%
2028 | 239 | 239-2217R | Tier-3 | Tier-3---16 | 4--4 | 4.9148 | 696 | 100% | 1029.5673 | 69.27% | 30.42% | 0.3032% | 35.3035 | 0 | 0 | 35.3035 | 0 | 30.6457 | 4.6204 | 6.6327 | 30.6457 | 4.6204 | 6.6327 | 35.8252 | 5.4013 | 6.6327 | 3.429% | 0.073205 | 0.069582 | 14064.0898 | 1546.1618 | 3996.6336 | 8521.2943 | 14289.1505 | 0 | 0 | 14289.1505 | 0.001164%
2028 | 1166 | CB 1166 | Tier-3 | Tier-3---20 | 1--5 | 0.085985 | 0 | 100% | 70.8201 | 99.8% | 0% | 0.2033% | 3.4985 | 0 | 0 | 3.4985 | 0 | 3.0369 | 0.080834 | 37.5694 | 3.0369 | 0.080834 | 37.5694 | 3.5502 | 0.094496 | 37.5694 | 4.94% | 0.0005142 | 0.00048875 | 137728.7598 | 21906.6699 | 136.7435 | 115685.3465 | 137743.3449 | 0 | 0 | 137743.3449 | 0.0001154%
2028 | LJ3 | CB LJ3 | Tier-1 | Non-HFTD---14 | 3--1 | 5.2941 | 292 | 100% | 6.3096 | 39.49% | 0% | 60.51% | 0.12333 | 0 | 0 | 0.12333 | 0 | 0.10705 | 4.977 | 0.02151 | 0.10705 | 4.977 | 0.02151 | 0.12515 | 5.8181 | 0.02151 | 1.955% | 0.014718 | 0.013989 | 428.7031 | 0.52088 | 190.8463 | 237.3358 | 442.2133 | 0 | 0 | 442.2133 | 4.067e-06%
2028 | 286 | 286-990AE | Tier-1 | Non-HFTD---6 | 3--3 | 4.5934 | 275 | 100% | 50.0124 | 5.334% | 88.41% | 6.257% | 0.13205 | 0 | 0 | 0.13205 | 0 | 0.11463 | 4.3182 | 0.026546 | 0.11463 | 4.3182 | 0.026546 | 0.13401 | 5.0481 | 0.026546 | 0.264% | 0.018547 | 0.017629 | 2696.5813 | 3.2353 | 2292.3777 | 400.9683 | 2829.5225 | 0 | 0 | 2829.5225 | 4.355e-06%
2028 | 210 | 210-392R | Tier-2 | Tier-2---10 | 5--3 | 10.6016 | 377 | 100% | 1037.8957 | 85.73% | 13.64% | 0.6245% | 44.0457 | 0 | 0 | 44.0457 | 0 | 38.2345 | 9.9665 | 3.8363 | 38.2345 | 9.9665 | 3.8363 | 44.6966 | 11.651 | 3.8363 | 4.244% | 0.34771 | 0.33049 | 2984.984 | 285.5851 | 372.7528 | 2326.6461 | 3007.1634 | 0 | 0 | 3007.1634 | 0.001452%
2028 | 1250 | 1250-8R | Tier-2 | Tier-2---4 | 4--5 | 4.2055 | 350 | 100% | 3684.9802 | 98.15% | 1.772% | 0.07391% | 179.0398 | 0 | 0 | 179.0398 | 0 | 155.4182 | 3.9536 | 39.3108 | 155.4182 | 3.9536 | 39.3108 | 181.6856 | 4.6218 | 39.3108 | 4.859% | 0.092289 | 0.08772 | 39928.877 | 6438.64 | 665.159 | 32825.0781 | 39967.2577 | 0 | 0 | 39967.2577 | 0.005904%
2028 | 700 | 700-259F | Tier-1 | Non-HFTD---18 | 2--1 | 0.55551 | 19 | 100% | 1.7805 | 42.11% | 22.63% | 35.26% | 0.037115 | 0 | 0 | 0.037115 | 0 | 0.032218 | 0.52224 | 0.061693 | 0.032218 | 0.52224 | 0.061693 | 0.037663 | 0.6105 | 0.061693 | 2.085% | 0.0075412 | 0.0071679 | 236.1005 | 16.7944 | 50.0362 | 169.27 | 243.2182 | 0 | 0 | 243.2182 | 1.224e-06%
2028 | 311 | 311-14R | Tier-2 | Tier-2---14 | 3--4 | 0.75338 | 24 | 100% | 278.652 | 16.28% | 83.57% | 0.1501% | 2.2455 | 0 | 0 | 2.2455 | 0 | 1.9492 | 0.70825 | 2.7522 | 1.9492 | 0.70825 | 2.7522 | 2.2787 | 0.82795 | 2.7522 | 0.8058% | 0.018935 | 0.017998 | 14715.9264 | 335.1634 | 11691.6167 | 2689.1463 | 15357.5365 | 0 | 0 | 15357.5365 | 7.405e-05%
2028 | 222 | 222-2013R | Tier-3 | Tier-3---7 | 5--5 | 13.7044 | 1323 | 100% | 7426.9759 | 96.05% | 3.813% | 0.1383% | 353.11 | 0 | 0 | 353.11 | 0 | 306.5225 | 12.8835 | 23.7919 | 306.5225 | 12.8835 | 23.7919 | 358.3282 | 15.0609 | 23.7919 | 4.754% | 0.27927 | 0.26545 | 26594.1155 | 4003.6011 | 918.5637 | 21671.9506 | 26648.8357 | 0 | 0 | 26648.8357 | 0.01164%
2028 | SC1 | CB SC1 | Tier-1 | Non-HFTD---2 | 4--4 | 7.9705 | 397 | 100% | 245.1307 | 1.784% | 95.78% | 2.439% | 0.21643 | 0 | 0 | 0.21643 | 0 | 0.18787 | 7.4931 | 0.025073 | 0.18787 | 7.4931 | 0.025073 | 0.21963 | 8.7595 | 0.025073 | 0.08829% | 0.040226 | 0.038235 | 6093.8082 | 6.9984 | 5431.9692 | 654.8405 | 6405.5002 | 0 | 0 | 6405.5002 | 7.137e-06%
2028 | 381 | 381-48 | Tier-1 | Non-HFTD---13 | 2--2 | 2.1998 | 102 | 100% | 7.9134 | 78.55% | 0% | 21.45% | 0.30769 | 0 | 0 | 0.30769 | 0 | 0.26709 | 2.068 | 0.12915 | 0.26709 | 2.068 | 0.12915 | 0.31223 | 2.4176 | 0.12915 | 3.888% | 0.0068838 | 0.0065431 | 1149.5636 | 150.1274 | 123.1813 | 876.2549 | 1162.4055 | 0 | 0 | 1162.4055 | 1.015e-05%
2028 | CHA1 | CB CHA1 | Tier-1 | Non-HFTD---10 | 3--2 | 4.0496 | 334 | 100% | 19.2146 | 44.26% | 40.89% | 14.85% | 0.42097 | 0 | 0 | 0.42097 | 0 | 0.36543 | 3.807 | 0.095988 | 0.36543 | 3.807 | 0.095988 | 0.42719 | 4.4505 | 0.095988 | 2.191% | 0.016682 | 0.015856 | 1151.8035 | 79.964 | 473.8867 | 597.9528 | 1185.238 | 0 | 0 | 1185.238 | 1.388e-05%
2028 | 279 | 279-11AE | Tier-1 | Non-HFTD---2 | 4--3 | 13.9777 | 317 | 100% | 201.506 | 3.082% | 92.11% | 4.808% | 0.30745 | 0 | 0 | 0.30745 | 0 | 0.26689 | 13.1404 | 0.02031 | 0.26689 | 13.1404 | 0.02031 | 0.31199 | 15.3613 | 0.02031 | 0.1526% | 0.055223 | 0.052489 | 3648.9772 | 5.6056 | 3185.2795 | 458.092 | 3833.1507 | 0 | 0 | 3833.1507 | 1.014e-05%
2028 | 162 | 162-19F | Tier-1 | Non-HFTD---12 | 4--2 | 10.1582 | 296 | 100% | 15.1555 | 52.93% | 0% | 47.07% | 0.39707 | 0 | 0 | 0.39707 | 0 | 0.34468 | 9.5497 | 0.036093 | 0.34468 | 9.5497 | 0.036093 | 0.40293 | 11.1637 | 0.036093 | 2.62% | 0.029254 | 0.027806 | 518.0585 | 22.6254 | 158.6224 | 336.8107 | 530.7581 | 0 | 0 | 530.7581 | 1.309e-05%
2028 | PL6 | CB PL6 | Tier-1 | Non-HFTD---12 | 4--1 | 10.6356 | 602 | 100% | 11.6399 | 35.44% | 0% | 64.56% | 0.20418 | 0 | 0 | 0.20418 | 0 | 0.17724 | 9.9985 | 0.017726 | 0.17724 | 9.9985 | 0.017726 | 0.20719 | 11.6884 | 0.017726 | 1.754% | 0.029655 | 0.028187 | 392.5082 | 0.9255 | 157.6202 | 233.9625 | 405.7056 | 0 | 0 | 405.7056 | 6.733e-06%
2028 | 288 | 288-149R | Tier-2 | Tier-2---12 | 3--5 | 4.8645 | 919 | 100% | 481.2843 | 94.31% | 4.95% | 0.7414% | 22.4677 | 0 | 0 | 22.4677 | 0 | 19.5034 | 4.5732 | 4.2647 | 19.5034 | 4.5732 | 4.2647 | 22.7997 | 5.3461 | 4.2647 | 4.668% | 0.02124 | 0.020188 | 22659.7646 | 3469.9036 | 1191.7456 | 17998.1154 | 22726.928 | 0 | 0 | 22726.928 | 0.0007409%
2028 | LJ4 | CB LJ4 | Tier-1 | Non-HFTD---16 | 2--1 | 2.5968 | 116 | 100% | 3.329 | 11.7% | 0% | 88.3% | 0.019278 | 0 | 0 | 0.019278 | 0 | 0.016735 | 2.4413 | 0.0068548 | 0.016735 | 2.4413 | 0.0068548 | 0.019563 | 2.8539 | 0.0068548 | 0.5791% | 0.0094594 | 0.0089912 | 351.9241 | 0.35466 | 68.6606 | 282.9088 | 368.1074 | 0 | 0 | 368.1074 | 6.357e-07%
2028 | 44 | 44-41 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2296 | 47 | 100% | 1.0965 | 21.81% | 0% | 78.19% | 0.011837 | 0 | 0 | 0.011837 | 0 | 0.010275 | 1.1559 | 0.0088893 | 0.010275 | 1.1559 | 0.0088893 | 0.012012 | 1.3513 | 0.0088893 | 1.079% | 0.0032776 | 0.0031154 | 334.5534 | 0.42375 | 95.3401 | 238.7896 | 348.1766 | 0 | 0 | 348.1766 | 3.903e-07%
2028 | 450 | 450-1853F | Tier-2 | Tier-2---10 | 4--4 | 1.1027 | 145 | 100% | 792.2018 | 92.77% | 7.138% | 0.09408% | 36.3781 | 0 | 0 | 36.3781 | 0 | 31.5786 | 1.0366 | 30.4627 | 31.5786 | 1.0366 | 30.4627 | 36.9157 | 1.2118 | 30.4627 | 4.592% | 0.075291 | 0.071564 | 10521.8374 | 1586.5914 | 691.3436 | 8243.9024 | 10561.4641 | 0 | 0 | 10561.4641 | 0.0012%
2028 | 59 | CB 59 | Tier-1 | Non-HFTD---5 | 2--4 | 0.80076 | 2 | 100% | 54.4254 | 99.08% | 0.2847% | 0.6369% | 2.6692 | 0 | 0 | 2.6692 | 0 | 2.3171 | 0.75279 | 3.078 | 2.3171 | 0.75279 | 3.078 | 2.7087 | 0.88002 | 3.078 | 4.904% | 0.0099342 | 0.0094425 | 5478.5927 | 848.4383 | 1089.8599 | 3540.2945 | 5481.2223 | 0 | 0 | 5481.2223 | 8.802e-05%
2028 | 131 | CB 131 | Tier-1 | Non-HFTD---15 | 2--2 | 1.6525 | 6 | 100% | 3.9586 | 65.37% | 0% | 34.63% | 0.1281 | 0 | 0 | 0.1281 | 0 | 0.11119 | 1.5535 | 0.071576 | 0.11119 | 1.5535 | 0.071576 | 0.12999 | 1.8161 | 0.071576 | 3.236% | 0.0054554 | 0.0051854 | 725.6284 | 55.3628 | 156.9776 | 513.288 | 738.7144 | 0 | 0 | 738.7144 | 4.224e-06%
2028 | 442 | 442-16R | Tier-3 | Tier-3---14 | 5--3 | 10.8114 | 954 | 100% | 1834.9376 | 96.09% | 3.534% | 0.3793% | 87.2753 | 0 | 0 | 87.2753 | 0 | 75.7606 | 10.1638 | 7.454 | 75.7606 | 10.1638 | 7.454 | 88.565 | 11.8816 | 7.454 | 4.756% | 0.45792 | 0.43525 | 4007.1227 | 501.0309 | 121.8682 | 3384.2237 | 4015.2885 | 0 | 0 | 4015.2885 | 0.002878%
2028 | 321 | 321-740AE | Tier-1 | Non-HFTD---14 | 3--1 | 5.658 | 154 | 100% | 5.6044 | 24.77% | 0% | 75.23% | 0.068724 | 0 | 0 | 0.068724 | 0 | 0.059657 | 5.3191 | 0.011216 | 0.059657 | 5.3191 | 0.011216 | 0.06974 | 6.2181 | 0.011216 | 1.226% | 0.016283 | 0.015477 | 344.189 | 0.80306 | 105.0413 | 238.3446 | 357.6731 | 0 | 0 | 357.6731 | 2.266e-06%
2028 | 780 | 780-468R | Tier-1 | Non-HFTD---4 | 3--4 | 1.3398 | 27 | 100% | 132.1756 | 2.152% | 97.23% | 0.6129% | 0.14083 | 0 | 0 | 0.14083 | 0 | 0.12225 | 1.2596 | 0.097058 | 0.12225 | 1.2596 | 0.097058 | 0.14291 | 1.4724 | 0.097058 | 0.1065% | 0.014295 | 0.013588 | 9246.1513 | 26.0626 | 8234.6389 | 985.4497 | 9717.3064 | 0 | 0 | 9717.3064 | 4.644e-06%
2028 | 75 | 75-41 | Tier-3 | Tier-3---13 | 3--5 | 2.6099 | 102 | 100% | 1937.5846 | 99.86% | 0.04507% | 0.0969% | 95.7743 | 0 | 0 | 95.7743 | 0 | 83.1383 | 2.4535 | 33.885 | 83.1383 | 2.4535 | 33.885 | 97.1896 | 2.8682 | 33.885 | 4.943% | 0.0163 | 0.015493 | 118871.6769 | 26474.373 | 152.913 | 92244.3909 | 118880.4654 | 0 | 0 | 118880.4654 | 0.003158%
2028 | 775 | 775-185 | Tier-1 | Non-HFTD---16 | 2--1 | 2.1559 | 84 | 100% | 2.4124 | 31.06% | 0% | 68.94% | 0.037091 | 0 | 0 | 0.037091 | 0 | 0.032197 | 2.0267 | 0.015886 | 0.032197 | 2.0267 | 0.015886 | 0.037639 | 2.3693 | 0.015886 | 1.538% | 0.0065622 | 0.0062374 | 367.6213 | 10.1886 | 93.1395 | 264.2932 | 380.8197 | 0 | 0 | 380.8197 | 1.223e-06%
2028 | 1406 | CB 1406 | Tier-1 | Non-HFTD---17 | 1--3 | 0.036742 | 0 | 100% | 0.71787 | 90.65% | 0% | 9.349% | 0.032213 | 0 | 0 | 0.032213 | 0 | 0.027963 | 0.034542 | 0.80953 | 0.027963 | 0.034542 | 0.80953 | 0.032689 | 0.04038 | 0.80953 | 4.487% | 0.0001864 | 0.00017717 | 3851.2388 | 0.27092 | 3523.903 | 327.0649 | 3869.9891 | 0 | 0 | 3869.9891 | 1.062e-06%
2028 | 458 | CB 458 | Tier-1 | Non-HFTD---20 | 1--1 | 0.51493 | 1 | 100% | 0.4923 | 10.29% | 0% | 89.71% | 0.0025064 | 0 | 0 | 0.0025064 | 0 | 0.0021757 | 0.48409 | 0.0044944 | 0.0021757 | 0.48409 | 0.0044944 | 0.0025434 | 0.5659 | 0.0044944 | 0.5091% | 0.0016434 | 0.0015621 | 299.5635 | 3.6595 | 33.8007 | 262.1032 | 313.5596 | 0 | 0 | 313.5596 | 8.265e-08%
2028 | 252 | 252-129 | Tier-2 | Tier-2---18 | 3--3 | 4.6668 | 14 | 100% | 49.4853 | 86.66% | 6.71% | 6.626% | 2.1229 | 0 | 0 | 2.1229 | 0 | 1.8428 | 4.3873 | 0.42003 | 1.8428 | 4.3873 | 0.42003 | 2.1542 | 5.1288 | 0.42003 | 4.29% | 0.02391 | 0.022726 | 2069.6845 | 324.0484 | 134.0961 | 1611.54 | 2084.0584 | 0 | 0 | 2084.0584 | 7e-05%
2028 | 172 | 172-615R | Tier-1 | Non-HFTD---6 | 4--2 | 6.2257 | 251 | 100% | 65.0211 | 31.38% | 63.15% | 5.469% | 1.0101 | 0 | 0 | 1.0101 | 0 | 0.8768 | 5.8528 | 0.14981 | 0.8768 | 5.8528 | 0.14981 | 1.025 | 6.842 | 0.14981 | 1.553% | 0.053579 | 0.050927 | 1213.547 | 17.4537 | 970.9978 | 225.0954 | 1256.9124 | 0 | 0 | 1256.9124 | 3.331e-05%
2028 | 45 | 45-16 | Tier-1 | Non-HFTD---11 | 2--2 | 2.7608 | 126 | 100% | 10.6609 | 86.29% | 0% | 13.71% | 0.45536 | 0 | 0 | 0.45536 | 0 | 0.39528 | 2.5954 | 0.1523 | 0.39528 | 2.5954 | 0.1523 | 0.46209 | 3.0341 | 0.1523 | 4.271% | 0.0075584 | 0.0071843 | 1410.4753 | 328.5278 | 122.7581 | 959.1895 | 1420.5468 | 0 | 0 | 1420.5468 | 1.502e-05%
2028 | 233 | 233-41R | Tier-2 | Tier-2---9 | 4--5 | 10.1081 | 575 | 100% | 718.991 | 97.57% | 1.357% | 1.072% | 34.7253 | 0 | 0 | 34.7253 | 0 | 30.1439 | 9.5027 | 3.1722 | 30.1439 | 9.5027 | 3.1722 | 35.2385 | 11.1087 | 3.1722 | 4.83% | 0.044487 | 0.042285 | 16161.8225 | 2695.2374 | 377.2862 | 13089.2989 | 16182.2721 | 0 | 0 | 16182.2721 | 0.001145%
2028 | 83 | CB 83 | Tier-1 | Non-HFTD---11 | 2--2 | 5.2235 | 109 | 100% | 14.2823 | 84.51% | 0% | 15.49% | 0.59746 | 0 | 0 | 0.59746 | 0 | 0.51863 | 4.9106 | 0.10562 | 0.51863 | 4.9106 | 0.10562 | 0.60629 | 5.7405 | 0.10562 | 4.183% | 0.012231 | 0.011626 | 1167.6768 | 4.647 | 975.6795 | 187.3504 | 1177.0966 | 0 | 0 | 1177.0966 | 1.97e-05%
2028 | HL3 | CB HL3 | Tier-1 | Non-HFTD---12 | 3--1 | 8.2549 | 102 | 100% | 9.4251 | 40.92% | 0% | 59.08% | 0.19092 | 0 | 0 | 0.19092 | 0 | 0.16573 | 7.7605 | 0.021356 | 0.16573 | 7.7605 | 0.021356 | 0.19374 | 9.0721 | 0.021356 | 2.026% | 0.021995 | 0.020907 | 428.5039 | 2.1065 | 186.5448 | 239.8526 | 441.6875 | 0 | 0 | 441.6875 | 6.296e-06%
2028 | 240 | 240-2006R | Tier-3 | Tier-3---12 | 4--5 | 12.1512 | 539 | 100% | 3742.5721 | 99.07% | 0.7558% | 0.1785% | 183.5266 | 0 | 0 | 183.5266 | 0 | 159.313 | 11.4233 | 13.9463 | 159.313 | 11.4233 | 13.9463 | 186.2387 | 13.354 | 13.9463 | 4.904% | 0.06999 | 0.066526 | 53472.8025 | 8543.8289 | 386.3377 | 44542.6358 | 53498.8189 | 0 | 0 | 53498.8189 | 0.006052%
2028 | 197 | 197-1150F | Tier-2 | Tier-2---15 | 3--4 | 1.3604 | 2 | 100% | 183.5383 | 99.34% | 0.09556% | 0.5689% | 9.0248 | 0 | 0 | 9.0248 | 0 | 7.8341 | 1.2789 | 6.1255 | 7.8341 | 1.2789 | 6.1255 | 9.1582 | 1.4951 | 6.1255 | 4.917% | 0.021777 | 0.020699 | 8428.1597 | 1361.8326 | 10.8364 | 7055.4907 | 8431.076 | 0 | 0 | 8431.076 | 0.0002976%
2028 | 524 | 524-69R | Tier-3 | Tier-3---1 | 5--5 | 34.1718 | 1855 | 100% | 40375.3309 | 99.03% | 0.9107% | 0.05596% | 1979.2587 | 0 | 0 | 1979.2587 | 0 | 1718.1256 | 32.125 | 53.4826 | 1718.1256 | 32.125 | 53.4826 | 2008.5084 | 37.5544 | 53.4826 | 4.902% | 0.27264 | 0.25914 | 148092.4418 | 24296.9603 | 1265.0887 | 122530.3927 | 148166.9965 | 0 | 0 | 148166.9965 | 0.06527%
2028 | 1173 | CB 1173 | Tier-1 | Non-HFTD---15 | 1--2 | 1.1624 | 51 | 100% | 2.9682 | 59.25% | 0% | 40.75% | 0.087048 | 0 | 0 | 0.087048 | 0 | 0.075563 | 1.0927 | 0.069151 | 0.075563 | 1.0927 | 0.069151 | 0.088334 | 1.2774 | 0.069151 | 2.933% | 0.0040836 | 0.0038815 | 726.8498 | 0.22289 | 457.5433 | 269.0836 | 742.276 | 0 | 0 | 742.276 | 2.871e-06%
2028 | 493 | CB 493 | Tier-1 | Non-HFTD---17 | 1--2 | 0.20795 | 11 | 100% | 1.0505 | 81.53% | 0% | 18.47% | 0.042395 | 0 | 0 | 0.042395 | 0 | 0.036801 | 0.1955 | 0.18824 | 0.036801 | 0.1955 | 0.18824 | 0.043021 | 0.22854 | 0.18824 | 4.036% | 0.0008612 | 0.00081857 | 1219.8489 | 9.8539 | 955.0049 | 254.9902 | 1231.585 | 0 | 0 | 1231.585 | 1.398e-06%
2028 | 1090 | CB 1090 | Tier-2 | Tier-2---7 | 3--5 | 4.8975 | 156 | 100% | 1414.5114 | 99.62% | 0.1678% | 0.2113% | 69.7529 | 0 | 0 | 69.7529 | 0 | 60.5501 | 4.6042 | 13.1512 | 60.5501 | 4.6042 | 13.1512 | 70.7837 | 5.3823 | 13.1512 | 4.931% | 0.025114 | 0.023871 | 56324.0689 | 9092.3637 | 116.2348 | 47115.4703 | 56335.1879 | 0 | 0 | 56335.1879 | 0.0023%
2028 | 153 | 153-1119R | Tier-1 | Non-HFTD---13 | 2--2 | 2.4303 | 39 | 100% | 8.0116 | 75.45% | 0% | 24.55% | 0.2992 | 0 | 0 | 0.2992 | 0 | 0.25972 | 2.2848 | 0.11368 | 0.25972 | 2.2848 | 0.11368 | 0.30362 | 2.6709 | 0.11368 | 3.735% | 0.0073252 | 0.0069626 | 1093.6986 | 0.20207 | 849.5472 | 243.9493 | 1107.6839 | 0 | 0 | 1107.6839 | 9.866e-06%
2028 | 323 | CB 323 | Tier-1 | Non-HFTD---11 | 1--4 | 0.54113 | 18 | 100% | 12.9162 | 95.89% | 0% | 4.106% | 0.6131 | 0 | 0 | 0.6131 | 0 | 0.53221 | 0.50871 | 1.0462 | 0.53221 | 0.50871 | 1.0462 | 0.62216 | 0.59469 | 1.0462 | 4.747% | 0.0019678 | 0.0018704 | 6563.758 | 128.289 | 5536.1599 | 899.3092 | 6577.7919 | 0 | 0 | 6577.7919 | 2.022e-05%
2028 | TM1 | TM1-10R | Tier-3 | Tier-3---12 | 5--5 | 3.3899 | 476 | 100% | 3782.8568 | 99.48% | 0.4537% | 0.066% | 186.2783 | 0 | 0 | 186.2783 | 0 | 161.7017 | 3.1869 | 50.7401 | 161.7017 | 3.1869 | 50.7401 | 189.0311 | 3.7255 | 50.7401 | 4.924% | 0.093421 | 0.088796 | 40492.6609 | 6371.8092 | 167.7468 | 33953.1049 | 40503.6201 | 0 | 0 | 40503.6201 | 0.006143%
2028 | 146 | CB 146 | Tier-1 | Non-HFTD---15 | 2--2 | 0.18561 | 0 | 100% | 2.7748 | 92.6% | 1.913% | 5.483% | 0.12719 | 0 | 0 | 0.12719 | 0 | 0.11041 | 0.17449 | 0.63278 | 0.11041 | 0.17449 | 0.63278 | 0.12907 | 0.20398 | 0.63278 | 4.584% | 0.0054076 | 0.0051399 | 513.1328 | 60.6904 | 208.0736 | 244.3689 | 515.1093 | 0 | 0 | 515.1093 | 4.194e-06%
2028 | DR1 | CB DR1 | Tier-1 | Non-HFTD---10 | 3--2 | 5.4435 | 420 | 100% | 21.3264 | 25.84% | 59.63% | 14.53% | 0.27278 | 0 | 0 | 0.27278 | 0 | 0.23679 | 5.1175 | 0.046271 | 0.23679 | 5.1175 | 0.046271 | 0.27681 | 5.9824 | 0.046271 | 1.279% | 0.019541 | 0.018574 | 1091.3677 | 40.6433 | 651.42 | 399.3043 | 1133.5175 | 0 | 0 | 1133.5175 | 8.995e-06%
2028 | 414 | CB 414 | Tier-1 | Non-HFTD---2 | 4--3 | 16.8574 | 578 | 100% | 223.669 | 40.12% | 54.98% | 4.902% | 4.4417 | 0 | 0 | 4.4417 | 0 | 3.8556 | 15.8477 | 0.24329 | 3.8556 | 15.8477 | 0.24329 | 4.5073 | 18.5261 | 0.24329 | 1.986% | 0.060264 | 0.057281 | 3711.4858 | 297.0369 | 2040.8852 | 1373.5637 | 3827.2303 | 0 | 0 | 3827.2303 | 0.0001465%
2028 | 443 | 443-218R | Tier-1 | Non-HFTD---3 | 5--2 | 2.5293 | 0 | 100% | 96.9814 | 95.91% | 2.964% | 1.126% | 4.6043 | 0 | 0 | 4.6043 | 0 | 3.9968 | 2.3778 | 1.6809 | 3.9968 | 2.3778 | 1.6809 | 4.6723 | 2.7797 | 1.6809 | 4.748% | 0.096176 | 0.091415 | 1008.3738 | 175.6292 | 24.7239 | 808.0207 | 1010.5213 | 0 | 0 | 1010.5213 | 0.0001518%
2028 | 442 | 442-780 | Tier-3 | Tier-3---19 | 5--1 | 1.4734 | 170 | 100% | 141.3846 | 51% | 48.51% | 0.49% | 3.5693 | 0 | 0 | 3.5693 | 0 | 3.0984 | 1.3852 | 2.2368 | 3.0984 | 1.3852 | 2.2368 | 3.6221 | 1.6193 | 2.2368 | 2.525% | 0.34601 | 0.32888 | 408.6195 | 29.4314 | 178.8179 | 200.3702 | 419.0465 | 0 | 0 | 419.0465 | 0.0001177%
2028 | 702 | 702-25 | Tier-1 | Non-HFTD---4 | 2--4 | 0.91362 | 18 | 100% | 105.79 | 16.96% | 82.58% | 0.4592% | 0.88821 | 0 | 0 | 0.88821 | 0 | 0.77103 | 0.8589 | 0.89769 | 0.77103 | 0.8589 | 0.89769 | 0.90134 | 1.0041 | 0.89769 | 0.8396% | 0.0085112 | 0.0080899 | 12429.5062 | 105.0973 | 10920.6101 | 1403.7989 | 12967.0151 | 0 | 0 | 12967.0151 | 2.929e-05%
2028 | TY1 | CB TY1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.27729 | 7 | 100% | 0.35043 | 36.25% | 0% | 63.75% | 0.0062889 | 0 | 0 | 0.0062889 | 0 | 0.0054592 | 0.26068 | 0.020942 | 0.0054592 | 0.26068 | 0.020942 | 0.0063818 | 0.30474 | 0.020942 | 1.795% | 0.0008392 | 0.00079766 | 417.5792 | 9.9722 | 115.9508 | 291.6562 | 431.4417 | 0 | 0 | 431.4417 | 2.074e-07%
2028 | 1243 | 1243-45R | Tier-2 | Tier-2---7 | 4--5 | 4.2257 | 174 | 100% | 1878.3826 | 99.05% | 0.8285% | 0.1244% | 92.0939 | 0 | 0 | 92.0939 | 0 | 79.9435 | 3.9726 | 20.1236 | 79.9435 | 3.9726 | 20.1236 | 93.4549 | 4.644 | 20.1236 | 4.903% | 0.087615 | 0.083278 | 21438.9544 | 3365.8931 | 151.2586 | 17921.8028 | 21449.5937 | 0 | 0 | 21449.5937 | 0.003037%
2028 | 64 | CB 64 | Tier-1 | Non-HFTD---4 | 3--4 | 3.6049 | 136 | 100% | 105.4157 | 32.05% | 65.74% | 2.205% | 1.6724 | 0 | 0 | 1.6724 | 0 | 1.4517 | 3.389 | 0.42837 | 1.4517 | 3.389 | 0.42837 | 1.6971 | 3.9618 | 0.42837 | 1.586% | 0.017938 | 0.01705 | 5876.6069 | 242.5487 | 3978.8464 | 1655.2117 | 6084.5618 | 0 | 0 | 6084.5618 | 5.515e-05%
2028 | 278 | 278-22R | Tier-1 | Non-HFTD---2 | 4--3 | 15.5778 | 433 | 100% | 285.1665 | 5.51% | 90.91% | 3.576% | 0.77782 | 0 | 0 | 0.77782 | 0 | 0.6752 | 14.6447 | 0.046105 | 0.6752 | 14.6447 | 0.046105 | 0.78931 | 17.1199 | 0.046105 | 0.2728% | 0.058535 | 0.055637 | 4871.7604 | 23.1046 | 4253.0091 | 595.6468 | 5111.491 | 0 | 0 | 5111.491 | 2.565e-05%
2028 | 356 | 356-30AE | Tier-3 | Tier-3---6 | 5--5 | 20.8132 | 1063 | 100% | 9294.6751 | 95.41% | 4.438% | 0.1505% | 438.9762 | 0 | 0 | 438.9762 | 0 | 381.0599 | 19.5665 | 19.4751 | 381.0599 | 19.5665 | 19.4751 | 445.4634 | 22.8735 | 19.4751 | 4.723% | 0.14106 | 0.13408 | 65892.3901 | 11916.7444 | 2728.2388 | 51247.4069 | 66049.8398 | 0 | 0 | 66049.8398 | 0.01448%
2028 | 312 | 312-14F | Tier-2 | Tier-2---14 | 3--4 | 0.8655 | 53 | 100% | 202.1236 | 0.1514% | 99.59% | 0.26% | 0.015143 | 0 | 0 | 0.015143 | 0 | 0.013145 | 0.81366 | 0.016156 | 0.013145 | 0.81366 | 0.016156 | 0.015367 | 0.95118 | 0.016156 | 0.007492% | 0.018868 | 0.017934 | 10712.5091 | 15.0624 | 9630.1858 | 1067.2609 | 11269.5492 | 0 | 0 | 11269.5492 | 4.994e-07%
2028 | 41 | 41-44AE | Tier-1 | Non-HFTD---15 | 2--2 | 2.7028 | 103 | 100% | 4.0717 | 49.31% | 0% | 50.69% | 0.099392 | 0 | 0 | 0.099392 | 0 | 0.086279 | 2.541 | 0.033955 | 0.086279 | 2.541 | 0.033955 | 0.10086 | 2.9704 | 0.033955 | 2.441% | 0.0078416 | 0.0074534 | 519.2383 | 3.8166 | 257.6774 | 257.7443 | 532.9441 | 0 | 0 | 532.9441 | 3.278e-06%
2028 | 247 | 247-46 | Tier-3 | Tier-3---16 | 4--5 | 6.4578 | 311 | 100% | 1360.3328 | 92.51% | 7.186% | 0.3009% | 62.2952 | 0 | 0 | 62.2952 | 0 | 54.0763 | 6.071 | 8.9074 | 54.0763 | 6.071 | 8.9074 | 63.2158 | 7.097 | 8.9074 | 4.579% | 0.045228 | 0.04299 | 30076.9614 | 4522.9768 | 2007.8493 | 23546.1352 | 30194.2294 | 0 | 0 | 30194.2294 | 0.002054%
2028 | 791 | 791-419F | Tier-2 | Tier-2---5 | 5--5 | 5.507 | 474 | 100% | 3349.7594 | 92.58% | 7.304% | 0.116% | 153.5102 | 0 | 0 | 153.5102 | 0 | 133.2569 | 5.1771 | 25.7396 | 133.2569 | 5.1771 | 25.7396 | 155.7788 | 6.0521 | 25.7396 | 4.583% | 0.11325 | 0.10765 | 29577.718 | 5038.7125 | 1957.3259 | 22581.6795 | 29692.0073 | 0 | 0 | 29692.0073 | 0.005062%
2028 | 598 | CB 598 | Tier-1 | Non-HFTD---9 | 1--4 | 0.66591 | 21 | 100% | 17.2197 | 95.45% | 0% | 4.551% | 0.81358 | 0 | 0 | 0.81358 | 0 | 0.70624 | 0.62602 | 1.1281 | 0.70624 | 0.62602 | 1.1281 | 0.82561 | 0.73183 | 1.1281 | 4.725% | 0.0027812 | 0.0026435 | 6191.4698 | 926.9749 | 243.7416 | 5020.7533 | 6206.1445 | 0 | 0 | 6206.1445 | 2.683e-05%
2028 | 211 | 211-312R | Tier-2 | Tier-2---8 | 5--3 | 18.1587 | 322 | 100% | 1809.5147 | 84.26% | 15.08% | 0.6521% | 75.477 | 0 | 0 | 75.477 | 0 | 65.5189 | 17.071 | 3.838 | 65.5189 | 17.071 | 3.838 | 76.5924 | 19.9562 | 3.838 | 4.171% | 0.39031 | 0.37099 | 4636.1485 | 511.795 | 635.8046 | 3488.549 | 4674.1392 | 0 | 0 | 4674.1392 | 0.002489%
2028 | 357 | 357-45R | Tier-3 | Tier-3---8 | 5--5 | 11.815 | 984 | 100% | 17696.7525 | 97.47% | 2.478% | 0.04808% | 853.8638 | 0 | 0 | 853.8638 | 0 | 741.2094 | 11.1073 | 66.732 | 741.2094 | 11.1073 | 66.732 | 866.4823 | 12.9845 | 66.732 | 4.825% | 0.18538 | 0.1762 | 95462.1405 | 19005.7771 | 2236.2758 | 74220.0876 | 95587.7082 | 0 | 0 | 95587.7082 | 0.02816%
2028 | 516 | CB 516 | Tier-1 | Non-HFTD---13 | 2--2 | 1.9939 | 56 | 100% | 4.9777 | 55.1% | 0% | 44.9% | 0.13576 | 0 | 0 | 0.13576 | 0 | 0.11785 | 1.8745 | 0.062869 | 0.11785 | 1.8745 | 0.062869 | 0.13777 | 2.1913 | 0.062869 | 2.727% | 0.0070882 | 0.0067373 | 702.2584 | 0.23727 | 415.5749 | 286.4462 | 718.68 | 0 | 0 | 718.68 | 4.477e-06%
2028 | 205 | 205-1550 | Tier-2 | Tier-2---15 | 2--4 | 2.7852 | 227 | 100% | 124.0064 | 98.52% | 0% | 1.478% | 6.0476 | 0 | 0 | 6.0476 | 0 | 5.2497 | 2.6184 | 2.0049 | 5.2497 | 2.6184 | 2.0049 | 6.137 | 3.0609 | 2.0049 | 4.877% | 0.008789 | 0.0083539 | 14109.2738 | 2221.4405 | 309.7116 | 11578.1217 | 14120.1329 | 0 | 0 | 14120.1329 | 0.0001994%
2028 | HV1 | CB HV1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2047 | 174 | 100% | 1.373 | 42.97% | 0% | 57.03% | 0.029203 | 0 | 0 | 0.029203 | 0 | 0.02535 | 1.1326 | 0.022383 | 0.02535 | 1.1326 | 0.022383 | 0.029634 | 1.324 | 0.022383 | 2.127% | 0.0035008 | 0.0033275 | 392.1896 | 29.8125 | 41.3066 | 321.0705 | 403.8379 | 0 | 0 | 403.8379 | 9.63e-07%
2028 | 522 | 522-34 | Tier-2 | Tier-2---16 | 4--3 | 1.8014 | 103 | 100% | 112.7117 | 43.02% | 55.81% | 1.165% | 2.4004 | 0 | 0 | 2.4004 | 0 | 2.0837 | 1.6935 | 1.2305 | 2.0837 | 1.6935 | 1.2305 | 2.4359 | 1.9797 | 1.2305 | 2.13% | 0.030009 | 0.028524 | 3755.9309 | 247.8638 | 2031.3846 | 1476.6825 | 3867.3753 | 0 | 0 | 3867.3753 | 7.916e-05%
2028 | 361 | 361-45R | Tier-1 | Non-HFTD---5 | 3--4 | 2.965 | 64 | 100% | 74.9226 | 4.739% | 91.81% | 3.451% | 0.17574 | 0 | 0 | 0.17574 | 0 | 0.15255 | 2.7874 | 0.05473 | 0.15255 | 2.7874 | 0.05473 | 0.17833 | 3.2585 | 0.05473 | 0.2346% | 0.01487 | 0.014134 | 5038.4415 | 12.6045 | 4395.9502 | 629.8868 | 5288.3992 | 0 | 0 | 5288.3992 | 5.795e-06%
2028 | 368 | 368-1054F | Tier-1 | Non-HFTD---5 | 2--4 | 0.47745 | 4 | 100% | 80.991 | 0.1968% | 99.37% | 0.4288% | 0.0078897 | 0 | 0 | 0.0078897 | 0 | 0.0068488 | 0.44885 | 0.015258 | 0.0068488 | 0.44885 | 0.015258 | 0.0080063 | 0.52471 | 0.015258 | 0.009741% | 0.0067372 | 0.0064037 | 12021.4569 | 14.7322 | 10791.9159 | 1214.8087 | 12646.2765 | 0 | 0 | 12646.2765 | 2.602e-07%
2028 | LM3 | CB LM3 | Tier-1 | Non-HFTD---16 | 2--1 | 3.229 | 148 | 100% | 2.8437 | 17.95% | 0% | 82.05% | 0.025272 | 0 | 0 | 0.025272 | 0 | 0.021938 | 3.0356 | 0.0072268 | 0.021938 | 3.0356 | 0.0072268 | 0.025645 | 3.5486 | 0.0072268 | 0.8887% | 0.0089108 | 0.0084697 | 319.1341 | 1.177 | 75.099 | 242.8581 | 332.7702 | 0 | 0 | 332.7702 | 8.334e-07%
2028 | 308 | 308-464 | Tier-1 | Non-HFTD---3 | 4--3 | 3.726 | 137 | 100% | 187.2147 | 5.297% | 93.54% | 1.164% | 0.49085 | 0 | 0 | 0.49085 | 0 | 0.42609 | 3.5028 | 0.12164 | 0.42609 | 3.5028 | 0.12164 | 0.49811 | 4.0948 | 0.12164 | 0.2622% | 0.040091 | 0.038106 | 4669.7896 | 26.7777 | 4109.7012 | 533.3108 | 4900.101 | 0 | 0 | 4900.101 | 1.619e-05%
2028 | 155 | CB 155 | Tier-1 | Non-HFTD---7 | 2--3 | 4.6852 | 45 | 100% | 44.4963 | 94.43% | 0% | 5.571% | 2.0799 | 0 | 0 | 2.0799 | 0 | 1.8054 | 4.4046 | 0.4099 | 1.8054 | 4.4046 | 0.4099 | 2.1106 | 5.149 | 0.4099 | 4.674% | 0.013451 | 0.012786 | 3307.9312 | 28.3316 | 2967.8681 | 311.7315 | 3317.529 | 0 | 0 | 3317.529 | 6.859e-05%
2028 | 970 | 970-1341R | Tier-3 | Tier-3---4 | 5--5 | 4.3966 | 74 | 100% | 12961.6134 | 99.66% | 0.3199% | 0.02218% | 639.405 | 0 | 0 | 639.405 | 0 | 555.0452 | 4.1332 | 134.2887 | 555.0452 | 4.1332 | 134.2887 | 648.8541 | 4.8318 | 134.2887 | 4.933% | 0.12497 | 0.11878 | 103720.1236 | 23825.8597 | 477.209 | 79417.0549 | 103738.6021 | 0 | 0 | 103738.6021 | 0.02109%
2028 | 244 | 244-32F | Tier-1 | Non-HFTD---6 | 3--3 | 0.80758 | 17 | 100% | 51.191 | 8.266% | 90.61% | 1.12% | 0.20945 | 0 | 0 | 0.20945 | 0 | 0.18182 | 0.7592 | 0.23949 | 0.18182 | 0.7592 | 0.23949 | 0.21255 | 0.88752 | 0.23949 | 0.4092% | 0.026609 | 0.025291 | 1923.8516 | 6.2615 | 1678.6755 | 238.9145 | 2015.76 | 0 | 0 | 2015.76 | 6.907e-06%
2028 | 730 | 730-1079 | Tier-1 | Non-HFTD---10 | 4--2 | 13.1661 | 615 | 100% | 24.9152 | 67.14% | 0% | 32.86% | 0.8281 | 0 | 0 | 0.8281 | 0 | 0.71885 | 12.3774 | 0.058077 | 0.71885 | 12.3774 | 0.058077 | 0.84034 | 14.4693 | 0.058077 | 3.324% | 0.039453 | 0.0375 | 631.5134 | 48.4936 | 242.245 | 340.7748 | 642.3187 | 0 | 0 | 642.3187 | 2.731e-05%
2028 | 908 | 908-1370R | Tier-2 | Tier-2---8 | 5--4 | 5.8533 | 590 | 100% | 1466.2762 | 91.81% | 7.905% | 0.289% | 66.6334 | 0 | 0 | 66.6334 | 0 | 57.8421 | 5.5026 | 10.5117 | 57.8421 | 5.5026 | 10.5117 | 67.6181 | 6.4327 | 10.5117 | 4.544% | 0.1878 | 0.17851 | 7807.4644 | 1287.0292 | 565.6485 | 5954.7867 | 7840.781 | 0 | 0 | 7840.781 | 0.002197%
2028 | 397 | CB 397 | Tier-1 | Non-HFTD---10 | 3--2 | 5.8458 | 263 | 100% | 18.3403 | 77.93% | 0% | 22.07% | 0.70752 | 0 | 0 | 0.70752 | 0 | 0.61417 | 5.4957 | 0.11176 | 0.61417 | 5.4957 | 0.11176 | 0.71798 | 6.4245 | 0.11176 | 3.858% | 0.016356 | 0.015546 | 1121.3207 | 1.3088 | 889.4625 | 230.5495 | 1134.2064 | 0 | 0 | 1134.2064 | 2.333e-05%
2028 | 221 | 221-1230F | Tier-3 | Tier-3---12 | 4--5 | 3.8686 | 160 | 100% | 3690.9623 | 99.91% | 0% | 0.09183% | 182.5349 | 0 | 0 | 182.5349 | 0 | 158.4522 | 3.6368 | 43.5687 | 158.4522 | 3.6368 | 43.5687 | 185.2324 | 4.2515 | 43.5687 | 4.945% | 0.035843 | 0.034069 | 102975.2444 | 15309.4662 | 8.5902 | 87657.1879 | 102980.169 | 0 | 0 | 102980.169 | 0.006019%
2028 | 1250 | 1250-671R | Tier-2 | Tier-2---6 | 4--5 | 2.001 | 355 | 100% | 6815.4278 | 94.54% | 5.441% | 0.023% | 318.9315 | 0 | 0 | 318.9315 | 0 | 276.8533 | 1.8811 | 147.1755 | 276.8533 | 1.8811 | 147.1755 | 323.6447 | 2.199 | 147.1755 | 4.68% | 0.09205 | 0.087494 | 74040.4971 | 12900.0912 | 3770.1984 | 57370.2075 | 74251.1661 | 0 | 0 | 74251.1661 | 0.01052%
2028 | OK1 | CB OK1 | Tier-3 | Tier-3---7 | 5--5 | 7.3438 | 745 | 100% | 6915.6819 | 99% | 0.9206% | 0.07911% | 338.9042 | 0 | 0 | 338.9042 | 0 | 294.1909 | 6.9039 | 42.6123 | 294.1909 | 6.9039 | 42.6123 | 343.9125 | 8.0707 | 42.6123 | 4.901% | 0.20255 | 0.19252 | 34143.1528 | 5850.2009 | 285.3534 | 28007.5985 | 34160.9278 | 0 | 0 | 34160.9278 | 0.01118%
2028 | EN1 | CB EN1 | Tier-1 | Non-HFTD---6 | 4--3 | 9.5242 | 860 | 100% | 70.8621 | 16.44% | 73.67% | 9.888% | 0.57673 | 0 | 0 | 0.57673 | 0 | 0.50064 | 8.9537 | 0.055914 | 0.50064 | 8.9537 | 0.055914 | 0.58525 | 10.467 | 0.055914 | 0.8139% | 0.03227 | 0.030673 | 2195.9128 | 34.015 | 1636.754 | 525.1438 | 2291.4685 | 0 | 0 | 2291.4685 | 1.902e-05%
2028 | 551 | CB 551 | Tier-1 | Non-HFTD---17 | 1--3 | 0.22538 | 1 | 100% | 2.2115 | 88.35% | 0% | 11.65% | 0.096715 | 0 | 0 | 0.096715 | 0 | 0.083955 | 0.21188 | 0.39623 | 0.083955 | 0.21188 | 0.39623 | 0.098145 | 0.2477 | 0.39623 | 4.373% | 0.000778 | 0.00073949 | 2842.6003 | 2.9889 | 2524.6412 | 314.9702 | 2859.8501 | 0 | 0 | 2859.8501 | 3.189e-06%
2028 | 196 | CB 196 | Tier-2 | Tier-2---15 | 3--4 | 0.59317 | 34 | 100% | 134.4699 | 3.142% | 96.54% | 0.3137% | 0.20915 | 0 | 0 | 0.20915 | 0 | 0.18155 | 0.55764 | 0.32557 | 0.18155 | 0.55764 | 0.32557 | 0.21224 | 0.65189 | 0.32557 | 0.1555% | 0.019464 | 0.018501 | 6908.5051 | 30.9312 | 5935.5679 | 942.006 | 7256.9805 | 0 | 0 | 7256.9805 | 6.897e-06%
2028 | CA1 | CB CA1 | Tier-1 | Non-HFTD---8 | 3--2 | 4.8453 | 343 | 100% | 26.9004 | 5.027% | 82.43% | 12.54% | 0.066943 | 0 | 0 | 0.066943 | 0 | 0.058111 | 4.5551 | 0.012757 | 0.058111 | 4.5551 | 0.012757 | 0.067932 | 5.3249 | 0.012757 | 0.2489% | 0.01864 | 0.017718 | 1443.1369 | 5.8286 | 1152.8354 | 284.4728 | 1514.514 | 0 | 0 | 1514.514 | 2.208e-06%
2028 | 908 | 908-1372R | Tier-2 | Tier-2---2 | 5--5 | 3.7273 | 332 | 100% | 7960.2903 | 98.35% | 1.621% | 0.03193% | 387.5225 | 0 | 0 | 387.5225 | 0 | 336.3948 | 3.504 | 96.0033 | 336.3948 | 3.504 | 96.0033 | 393.2494 | 4.0962 | 96.0033 | 4.868% | 0.17701 | 0.16825 | 44971.6131 | 9357.4907 | 670.8421 | 34943.2804 | 45010.3176 | 0 | 0 | 45010.3176 | 0.01278%
2028 | 1436 | CB 1436 | Tier-1 | Non-HFTD---13 | 1--3 | 0.38731 | 13 | 100% | 5.4228 | 92.93% | 0% | 7.074% | 0.24944 | 0 | 0 | 0.24944 | 0 | 0.21653 | 0.36411 | 0.59468 | 0.21653 | 0.36411 | 0.59468 | 0.25312 | 0.42565 | 0.59468 | 4.6% | 0.0017518 | 0.0016651 | 3095.5311 | 14.7451 | 2805.6585 | 275.1275 | 3106.9346 | 0 | 0 | 3106.9346 | 8.226e-06%
2028 | 153 | 153-581F | Tier-1 | Non-HFTD---12 | 3--1 | 7.8703 | 195 | 100% | 9.378 | 55.57% | 0% | 44.43% | 0.25798 | 0 | 0 | 0.25798 | 0 | 0.22394 | 7.3989 | 0.030267 | 0.22394 | 7.3989 | 0.030267 | 0.26179 | 8.6494 | 0.030267 | 2.751% | 0.019874 | 0.01889 | 471.8682 | 14.7491 | 216.5363 | 240.5828 | 482.7857 | 0 | 0 | 482.7857 | 8.507e-06%
2028 | 1297 | 1297-35F | Tier-1 | Non-HFTD---5 | 2--3 | 1.8046 | 25 | 100% | 50.4009 | 3.614% | 93.45% | 2.939% | 0.090151 | 0 | 0 | 0.090151 | 0 | 0.078257 | 1.6965 | 0.046129 | 0.078257 | 1.6965 | 0.046129 | 0.091484 | 1.9832 | 0.046129 | 0.1789% | 0.011686 | 0.011107 | 4313.0011 | 4.498 | 3844.9239 | 463.5793 | 4529.4966 | 0 | 0 | 4529.4966 | 2.973e-06%
2028 | 521 | 521-14R | Tier-3 | Tier-3---5 | 5--5 | 12.6964 | 992 | 100% | 11350.2874 | 96.69% | 3.233% | 0.07621% | 543.2489 | 0 | 0 | 543.2489 | 0 | 471.5754 | 11.9359 | 39.5089 | 471.5754 | 11.9359 | 39.5089 | 551.277 | 13.9532 | 39.5089 | 4.786% | 0.27097 | 0.25755 | 41888.3276 | 6522.016 | 1245.0082 | 34121.3033 | 41960.5084 | 0 | 0 | 41960.5084 | 0.01791%
2028 | 364 | CB 364 | Tier-1 | Non-HFTD---3 | 3--4 | 4.5699 | 87 | 100% | 99.5129 | 18.42% | 77.53% | 4.054% | 0.90733 | 0 | 0 | 0.90733 | 0 | 0.78762 | 4.2961 | 0.18333 | 0.78762 | 4.2961 | 0.18333 | 0.92074 | 5.0222 | 0.18333 | 0.9118% | 0.019381 | 0.018422 | 5134.505 | 5.0746 | 4604.1532 | 525.2772 | 5352.6459 | 0 | 0 | 5352.6459 | 2.992e-05%
2028 | 591 | CB 591 | Tier-1 | Non-HFTD---1 | 4--4 | 9.3315 | 487 | 100% | 1060.5472 | 90.24% | 9.188% | 0.5739% | 47.3724 | 0 | 0 | 47.3724 | 0 | 41.1223 | 8.7725 | 4.6876 | 41.1223 | 8.7725 | 4.6876 | 48.0725 | 10.2552 | 4.6876 | 4.467% | 0.066615 | 0.063317 | 15920.6417 | 3763.87 | 1847.5145 | 10309.2572 | 16001.5783 | 0 | 0 | 16001.5783 | 0.001562%
2028 | 320 | CB 320 | Tier-1 | Non-HFTD---13 | 1--3 | 0.72523 | 16 | 100% | 4.9303 | 88.31% | 0% | 11.69% | 0.21551 | 0 | 0 | 0.21551 | 0 | 0.18708 | 0.68179 | 0.2744 | 0.18708 | 0.68179 | 0.2744 | 0.2187 | 0.79701 | 0.2744 | 4.371% | 0.002136 | 0.0020303 | 2308.1856 | 59.5018 | 1700.6421 | 548.0417 | 2322.2409 | 0 | 0 | 2322.2409 | 7.107e-06%
2028 | 770 | CB 770 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3017 | 137 | 100% | 5.4599 | 68.13% | 0% | 31.87% | 0.18414 | 0 | 0 | 0.18414 | 0 | 0.15985 | 2.1639 | 0.073871 | 0.15985 | 2.1639 | 0.073871 | 0.18686 | 2.5296 | 0.073871 | 3.373% | 0.008087 | 0.0076867 | 675.1471 | 60.111 | 111.1789 | 503.8571 | 686.3515 | 0 | 0 | 686.3515 | 6.072e-06%
2028 | 777 | 777-268F | Tier-1 | Non-HFTD---19 | 1--3 | 0.02803 | 0 | 100% | 0.57885 | 94.54% | 0% | 5.457% | 0.027089 | 0 | 0 | 0.027089 | 0 | 0.023515 | 0.026351 | 0.89237 | 0.023515 | 0.026351 | 0.89237 | 0.02749 | 0.030805 | 0.89237 | 4.68% | 0.0001222 | 0.00011615 | 4736.8697 | 723.3986 | 27.1305 | 3986.3407 | 4750.3318 | 0 | 0 | 4750.3318 | 8.933e-07%
2028 | 58 | 58-754F | Tier-1 | Non-HFTD---4 | 3--4 | 2.4574 | 37 | 100% | 111.5609 | 10.85% | 87.5% | 1.644% | 0.5994 | 0 | 0 | 0.5994 | 0 | 0.52032 | 2.3102 | 0.22522 | 0.52032 | 2.3102 | 0.22522 | 0.60826 | 2.7007 | 0.22522 | 0.5373% | 0.017828 | 0.016946 | 6257.4815 | 6.3235 | 5703.0525 | 548.1055 | 6547.9864 | 0 | 0 | 6547.9864 | 1.977e-05%
2028 | 781 | 781-43AE | Tier-1 | Non-HFTD---18 | 2--1 | 0.15072 | 4 | 100% | 1.2651 | 4.138% | 85.16% | 10.71% | 0.002591 | 0 | 0 | 0.002591 | 0 | 0.0022492 | 0.14169 | 0.015873 | 0.0022492 | 0.14169 | 0.015873 | 0.0026293 | 0.16564 | 0.015873 | 0.2048% | 0.011135 | 0.010584 | 113.6153 | 0.81972 | 89.1208 | 23.6748 | 119.2873 | 0 | 0 | 119.2873 | 8.544e-08%
2028 | 221 | 221-37AE | Tier-3 | Tier-3---11 | 5--5 | 7.7195 | 976 | 100% | 3934.7733 | 97.03% | 2.838% | 0.1358% | 188.9786 | 0 | 0 | 188.9786 | 0 | 164.0457 | 7.2571 | 22.6048 | 164.0457 | 7.2571 | 22.6048 | 191.7713 | 8.4836 | 22.6048 | 4.803% | 0.19925 | 0.18939 | 19747.6238 | 2983.7057 | 579.4204 | 16184.4978 | 19778.2099 | 0 | 0 | 19778.2099 | 0.006232%
2028 | 482 | 482-382F | Tier-1 | Non-HFTD---15 | 2--2 | 2.7703 | 50 | 100% | 4.259 | 56.74% | 0% | 43.26% | 0.11962 | 0 | 0 | 0.11962 | 0 | 0.10384 | 2.6043 | 0.039871 | 0.10384 | 2.6043 | 0.039871 | 0.12139 | 3.0445 | 0.039871 | 2.809% | 0.0074466 | 0.007078 | 571.9423 | 0.18618 | 346.992 | 224.7641 | 584.8278 | 0 | 0 | 584.8278 | 3.945e-06%
2028 | 1201 | 1201-282F | Tier-2 | Tier-2---17 | 2--4 | 1.7013 | 9 | 100% | 70.6534 | 98.66% | 0% | 1.337% | 3.4506 | 0 | 0 | 3.4506 | 0 | 2.9953 | 1.5994 | 1.8728 | 2.9953 | 1.5994 | 1.8728 | 3.5016 | 1.8697 | 1.8728 | 4.884% | 0.0070442 | 0.0066955 | 10030.0143 | 2447.2684 | 423.376 | 7159.37 | 10036.9961 | 0 | 0 | 10036.9961 | 0.0001138%
2028 | SK1 | CB SK1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.026705 | 0 | 100% | 0.041248 | 11.22% | 0% | 88.78% | 0.00022901 | 0 | 0 | 0.00022901 | 0 | 0.00019879 | 0.025105 | 0.0079185 | 0.00019879 | 0.025105 | 0.0079185 | 0.00023239 | 0.029348 | 0.0079185 | 0.5552% | 0.0001128 | 0.00010722 | 365.6737 | 6.7467 | 30.4931 | 328.4339 | 382.5813 | 0 | 0 | 382.5813 | 7.552e-09%
2028 | 971 | 971-2050R | Tier-3 | Tier-3---2 | 5--5 | 20.7013 | 1682 | 100% | 28484.5838 | 98.91% | 1.035% | 0.05308% | 1394.6521 | 0 | 0 | 1394.6521 | 0 | 1210.6489 | 19.4613 | 62.208 | 1210.6489 | 19.4613 | 62.208 | 1415.2624 | 22.7505 | 62.208 | 4.896% | 0.18464 | 0.1755 | 154268.7538 | 28980.1168 | 1504.6624 | 123783.9747 | 154356.1301 | 0 | 0 | 154356.1301 | 0.04599%
2028 | 237 | 237-1761R | Tier-3 | Tier-3---12 | 5--5 | 7.4915 | 117 | 100% | 3634.1464 | 99.4% | 0.4942% | 0.1098% | 178.8037 | 0 | 0 | 178.8037 | 0 | 155.2133 | 7.0428 | 22.0387 | 155.2133 | 7.0428 | 22.0387 | 181.4461 | 8.2331 | 22.0387 | 4.92% | 0.14935 | 0.14196 | 24332.6951 | 3910.2644 | 110.1562 | 20312.2745 | 24340.349 | 0 | 0 | 24340.349 | 0.005896%
2028 | 140 | 140-496 | Tier-1 | Non-HFTD---5 | 3--4 | 2.3094 | 156 | 100% | 76.0759 | 10.21% | 86.85% | 2.935% | 0.38454 | 0 | 0 | 0.38454 | 0 | 0.33381 | 2.1711 | 0.15375 | 0.33381 | 2.1711 | 0.15375 | 0.39022 | 2.538 | 0.15375 | 0.5055% | 0.01454 | 0.01382 | 5232.251 | 43.4645 | 4467.4961 | 721.2904 | 5476.9106 | 0 | 0 | 5476.9106 | 1.268e-05%
2028 | 462 | 462-1035F | Tier-1 | Non-HFTD---19 | 1--2 | 0.022159 | 4 | 100% | 0.24779 | 73.53% | 0% | 26.47% | 0.0090189 | 0 | 0 | 0.0090189 | 0 | 0.007829 | 0.020832 | 0.37582 | 0.007829 | 0.020832 | 0.37582 | 0.0091522 | 0.024353 | 0.37582 | 3.64% | 0.0001494 | 0.000142 | 1658.5735 | 0.33035 | 1259.4318 | 398.8113 | 1681.4368 | 0 | 0 | 1681.4368 | 2.974e-07%
2028 | 471 | 471-36F | Tier-2 | Tier-2---4 | 4--5 | 3.9252 | 376 | 100% | 4253.6671 | 94.96% | 4.983% | 0.06005% | 199.9388 | 0 | 0 | 199.9388 | 0 | 173.5599 | 3.6901 | 47.034 | 173.5599 | 3.6901 | 47.034 | 202.8935 | 4.3138 | 47.034 | 4.7% | 0.093079 | 0.088471 | 45699.6343 | 7333.0142 | 2085.1053 | 36281.5148 | 45819.647 | 0 | 0 | 45819.647 | 0.006593%
2028 | 911 | CB 911 | Tier-2 | Tier-2---14 | 1--5 | 0.9375 | 47 | 100% | 193.6033 | 99.75% | 0% | 0.253% | 9.5591 | 0 | 0 | 9.5591 | 0 | 8.2979 | 0.88134 | 9.4151 | 8.2979 | 0.88134 | 9.4151 | 9.7004 | 1.0303 | 9.4151 | 4.937% | 0.0040632 | 0.0038621 | 47647.9856 | 7461.2719 | 1706.7058 | 38480.0078 | 47654.2641 | 0 | 0 | 47654.2641 | 0.0003152%
2028 | 452 | 452-38AE | Tier-2 | Tier-2---4 | 2--5 | 2.7653 | 360 | 100% | 2823.7515 | 99.93% | 0% | 0.06613% | 139.6833 | 0 | 0 | 139.6833 | 0 | 121.2542 | 2.5997 | 46.6416 | 121.2542 | 2.5997 | 46.6416 | 141.7475 | 3.0391 | 46.6416 | 4.947% | 0.011395 | 0.010831 | 247801.8355 | 52326.7791 | 24.6712 | 195450.3852 | 247810.3694 | 0 | 0 | 247810.3694 | 0.004606%
2028 | 516 | 516-7F | Tier-1 | Non-HFTD---19 | 1--1 | 0.27315 | 23 | 100% | 0.35341 | 11.58% | 0% | 88.42% | 0.0020258 | 0 | 0 | 0.0020258 | 0 | 0.0017585 | 0.25679 | 0.006848 | 0.0017585 | 0.25679 | 0.006848 | 0.0020557 | 0.30019 | 0.006848 | 0.5732% | 0.0009896 | 0.00094061 | 357.1201 | 0.2376 | 70.0389 | 286.8436 | 373.5645 | 0 | 0 | 373.5645 | 6.68e-08%
2028 | 520 | 520-1904 | Tier-3 | Tier-3---13 | 4--5 | 7.6936 | 531 | 100% | 2084.5359 | 96.48% | 3.265% | 0.2521% | 99.5552 | 0 | 0 | 99.5552 | 0 | 86.4204 | 7.2327 | 11.9485 | 86.4204 | 7.2327 | 11.9485 | 101.0265 | 8.4552 | 11.9485 | 4.776% | 0.05278 | 0.050167 | 39495.106 | 6591.0687 | 1215.4691 | 31688.5681 | 39567.4502 | 0 | 0 | 39567.4502 | 0.003283%
2028 | 330 | 330-8R | Tier-1 | Non-HFTD---2 | 4--4 | 9.8311 | 664 | 100% | 217.2506 | 11.57% | 85.07% | 3.362% | 1.2444 | 0 | 0 | 1.2444 | 0 | 1.0803 | 9.2422 | 0.11688 | 1.0803 | 9.2422 | 0.11688 | 1.2628 | 10.8042 | 0.11688 | 0.5728% | 0.044939 | 0.042715 | 4834.3005 | 5.4086 | 4300.9723 | 527.9196 | 5056.9268 | 0 | 0 | 5056.9268 | 4.104e-05%
2028 | 411 | 411-47R | Tier-2 | Tier-2---9 | 4--5 | 14.6036 | 803 | 100% | 1350.4062 | 95.97% | 3.342% | 0.6845% | 64.1539 | 0 | 0 | 64.1539 | 0 | 55.6898 | 13.7289 | 4.0564 | 55.6898 | 13.7289 | 4.0564 | 65.102 | 16.0492 | 4.0564 | 4.751% | 0.063274 | 0.060142 | 21342.1296 | 4038.9634 | 957.9305 | 16345.2356 | 21386.8765 | 0 | 0 | 21386.8765 | 0.002116%
2028 | 329 | 329-793F | Tier-1 | Non-HFTD---14 | 3--1 | 0.54544 | 10 | 100% | 8.6222 | 27.32% | 66.37% | 6.318% | 0.11658 | 0 | 0 | 0.11658 | 0 | 0.1012 | 0.51277 | 0.19736 | 0.1012 | 0.51277 | 0.19736 | 0.11831 | 0.59943 | 0.19736 | 1.352% | 0.019245 | 0.018293 | 448.0142 | 14.326 | 282.864 | 150.8242 | 464.9726 | 0 | 0 | 464.9726 | 3.845e-06%
2028 | 90 | 90-49 | Tier-1 | Non-HFTD---11 | 2--3 | 0.38809 | 7 | 100% | 11.9536 | 0.3922% | 96.08% | 3.526% | 0.0023207 | 0 | 0 | 0.0023207 | 0 | 0.0020145 | 0.36484 | 0.0055216 | 0.0020145 | 0.36484 | 0.0055216 | 0.002355 | 0.42651 | 0.0055216 | 0.01941% | 0.0065452 | 0.0062212 | 1826.3158 | 2.1347 | 1619.3491 | 204.832 | 1921.0534 | 0 | 0 | 1921.0534 | 7.653e-08%
2028 | 702 | 702-448F | Tier-1 | Non-HFTD---19 | 1--3 | 0.029545 | 0 | 100% | 0.36733 | 90.03% | 0% | 9.967% | 0.016371 | 0 | 0 | 0.016371 | 0 | 0.014211 | 0.027776 | 0.51163 | 0.014211 | 0.027776 | 0.51163 | 0.016613 | 0.03247 | 0.51163 | 4.457% | 0.0001214 | 0.00011539 | 3025.8156 | 1.795 | 2741.9742 | 282.0463 | 3041.5218 | 0 | 0 | 3041.5218 | 5.398e-07%
2028 | 151 | CB 151 | Tier-1 | Non-HFTD---16 | 2--1 | 2.8715 | 54 | 100% | 3.6088 | 37.51% | 0% | 62.49% | 0.067008 | 0 | 0 | 0.067008 | 0 | 0.058167 | 2.6995 | 0.021547 | 0.058167 | 2.6995 | 0.021547 | 0.067998 | 3.1558 | 0.021547 | 1.857% | 0.0086214 | 0.0081946 | 418.5864 | 20.5993 | 55.0518 | 342.9354 | 432.2085 | 0 | 0 | 432.2085 | 2.21e-06%
2028 | 442 | 442-758F | Tier-3 | Tier-3---18 | 5--2 | 1.1019 | 43 | 100% | 549.9829 | 98.93% | 0.9134% | 0.161% | 26.9317 | 0 | 0 | 26.9317 | 0 | 23.3784 | 1.0359 | 22.5684 | 23.3784 | 1.0359 | 22.5684 | 27.3297 | 1.211 | 22.5684 | 4.897% | 0.35119 | 0.3338 | 1566.0749 | 220.1383 | 11.599 | 1334.3376 | 1566.9511 | 0 | 0 | 1566.9511 | 0.0008881%
2028 | 974 | CB 974 | Tier-2 | Tier-2---12 | 1--5 | 0.11723 | 0 | 100% | 334.3039 | 99.93% | 0% | 0.06503% | 16.5373 | 0 | 0 | 16.5373 | 0 | 14.3554 | 0.11021 | 130.2523 | 14.3554 | 0.11021 | 130.2523 | 16.7817 | 0.12884 | 130.2523 | 4.947% | 0.0006326 | 0.00060129 | 528460.2237 | 85326.4466 | 346.0244 | 442787.7527 | 528478.122 | 0 | 0 | 528478.122 | 0.0005453%
2028 | 136 | CB 136 | Tier-1 | Non-HFTD---11 | 2--2 | 3.5625 | 63 | 100% | 14.7465 | 75.99% | 0% | 24.01% | 0.55467 | 0 | 0 | 0.55467 | 0 | 0.48149 | 3.3491 | 0.14377 | 0.48149 | 3.3491 | 0.14377 | 0.56287 | 3.9152 | 0.14377 | 3.761% | 0.012814 | 0.012179 | 1150.8466 | 68.1179 | 481.9548 | 600.7739 | 1165.2384 | 0 | 0 | 1165.2384 | 1.829e-05%
2028 | AG1 | CB AG1 | Tier-1 | Non-HFTD---6 | 3--3 | 2.6702 | 142 | 100% | 54.2692 | 2.264% | 94.2% | 3.533% | 0.060827 | 0 | 0 | 0.060827 | 0 | 0.052802 | 2.5103 | 0.021034 | 0.052802 | 2.5103 | 0.021034 | 0.061726 | 2.9346 | 0.021034 | 0.1121% | 0.01771 | 0.016834 | 3064.2572 | 3.3404 | 2723.0059 | 337.911 | 3220.2238 | 0 | 0 | 3220.2238 | 2.006e-06%
2028 | 58 | 58-110F | Tier-1 | Non-HFTD---3 | 4--3 | 6.2108 | 237 | 100% | 93.5151 | 11.61% | 83.8% | 4.592% | 0.53721 | 0 | 0 | 0.53721 | 0 | 0.46634 | 5.8388 | 0.079869 | 0.46634 | 5.8388 | 0.079869 | 0.54515 | 6.8256 | 0.079869 | 0.5745% | 0.033104 | 0.031465 | 2824.9053 | 53.6585 | 2259.5047 | 511.7421 | 2954.947 | 0 | 0 | 2954.947 | 1.772e-05%
2028 | 53 | CB 53 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2979 | 50 | 100% | 0.88951 | 10.17% | 0% | 89.83% | 0.0044771 | 0 | 0 | 0.0044771 | 0 | 0.0038864 | 1.2202 | 0.0031852 | 0.0038864 | 1.2202 | 0.0031852 | 0.0045433 | 1.4264 | 0.0031852 | 0.5033% | 0.0032354 | 0.0030752 | 274.9306 | 0.18584 | 50.3908 | 224.354 | 287.7926 | 0 | 0 | 287.7926 | 1.476e-07%
2028 | 1448 | 1448-368 | Tier-1 | Non-HFTD---11 | 2--3 | 2.0286 | 23 | 100% | 14.0801 | 87.11% | 0% | 12.89% | 0.60712 | 0 | 0 | 0.60712 | 0 | 0.52702 | 1.9071 | 0.27635 | 0.52702 | 1.9071 | 0.27635 | 0.61609 | 2.2294 | 0.27635 | 4.312% | 0.0077936 | 0.0074078 | 1806.6243 | 178.7989 | 575.1368 | 1052.6887 | 1818.7529 | 0 | 0 | 1818.7529 | 2.002e-05%
2028 | 351 | 351-819R | Tier-2 | Tier-2---1 | 5--5 | 12.622 | 987 | 100% | 23517.4275 | 99.25% | 0.716% | 0.03401% | 1155.3817 | 0 | 0 | 1155.3817 | 0 | 1002.9466 | 11.8659 | 84.5231 | 1002.9466 | 11.8659 | 84.5231 | 1172.456 | 13.8714 | 84.5231 | 4.913% | 0.14376 | 0.13664 | 163589.7091 | 37860.9824 | 1092.4816 | 124636.245 | 163653.6055 | 0 | 0 | 163653.6055 | 0.0381%
2028 | 242 | 242-1413F | Tier-1 | Non-HFTD---2 | 5--3 | 1.8794 | 86 | 100% | 367.3537 | 8.271% | 91.36% | 0.3661% | 1.5041 | 0 | 0 | 1.5041 | 0 | 1.3056 | 1.7668 | 0.73899 | 1.3056 | 1.7668 | 0.73899 | 1.5263 | 2.0654 | 0.73899 | 0.4094% | 0.10056 | 0.095586 | 3652.9198 | 53.8188 | 2967.9065 | 631.1945 | 3827.4209 | 0 | 0 | 3827.4209 | 4.96e-05%
2028 | 186 | CB 186 | Tier-1 | Non-HFTD---5 | 3--4 | 4.111 | 213 | 100% | 92.3894 | 96.63% | 0% | 3.367% | 4.4193 | 0 | 0 | 4.4193 | 0 | 3.8363 | 3.8648 | 0.99262 | 3.8363 | 3.8648 | 0.99262 | 4.4846 | 4.518 | 0.99262 | 4.783% | 0.015082 | 0.014336 | 6125.6456 | 905.7849 | 2088.3006 | 3131.5601 | 6136.3851 | 0 | 0 | 6136.3851 | 0.0001457%
2028 | 570 | 570-491F | Tier-1 | Non-HFTD---20 | 1--1 | 0.70831 | 56 | 100% | 0.50055 | 7.694% | 0% | 92.31% | 0.0019065 | 0 | 0 | 0.0019065 | 0 | 0.001655 | 0.66588 | 0.0024854 | 0.001655 | 0.66588 | 0.0024854 | 0.0019347 | 0.77843 | 0.0024854 | 0.3809% | 0.001908 | 0.0018136 | 262.3439 | 0.27517 | 41.617 | 220.4517 | 274.9549 | 0 | 0 | 274.9549 | 6.287e-08%
2028 | 546 | CB 546 | Tier-1 | Non-HFTD---1 | 4--4 | 7.344 | 174 | 100% | 334.1605 | 5.89% | 92.51% | 1.604% | 0.97427 | 0 | 0 | 0.97427 | 0 | 0.84573 | 6.9041 | 0.1225 | 0.84573 | 6.9041 | 0.1225 | 0.98867 | 8.0709 | 0.1225 | 0.2916% | 0.030456 | 0.028948 | 10971.9113 | 11.4011 | 9971.8641 | 988.6462 | 11509.6495 | 0 | 0 | 11509.6495 | 3.213e-05%
2028 | EOS1 | CB EOS1 | Tier-1 | Non-HFTD---6 | 4--2 | 17.8417 | 865 | 100% | 70.9236 | 82.85% | 0% | 17.15% | 2.9086 | 0 | 0 | 2.9086 | 0 | 2.5248 | 16.7729 | 0.15053 | 2.5248 | 16.7729 | 0.15053 | 2.9515 | 19.6078 | 0.15053 | 4.101% | 0.050825 | 0.048309 | 1395.4534 | 210.0698 | 229.3399 | 956.0438 | 1407.9183 | 0 | 0 | 1407.9183 | 9.591e-05%
2028 | 515 | 515-49R | Tier-1 | Non-HFTD---17 | 1--2 | 0.3564 | 2 | 100% | 0.93866 | 50.3% | 0% | 49.7% | 0.023373 | 0 | 0 | 0.023373 | 0 | 0.020289 | 0.33505 | 0.060555 | 0.020289 | 0.33505 | 0.060555 | 0.023718 | 0.39168 | 0.060555 | 2.49% | 0.0014364 | 0.0013653 | 653.4775 | 1.8578 | 348.3582 | 303.2615 | 670.3899 | 0 | 0 | 670.3899 | 7.708e-07%
2028 | 78 | 78-26R | Tier-3 | Tier-3---5 | 5--5 | 6.3703 | 516 | 100% | 14526.7268 | 98.56% | 1.412% | 0.03052% | 708.6971 | 0 | 0 | 708.6971 | 0 | 615.1953 | 5.9887 | 102.7255 | 615.1953 | 5.9887 | 102.7255 | 719.1703 | 7.0009 | 102.7255 | 4.879% | 0.34567 | 0.32856 | 42024.2818 | 6675.4461 | 542.9403 | 34805.8954 | 42055.8613 | 0 | 0 | 42055.8613 | 0.02337%
2028 | 1001 | 1001-1140R | Tier-2 | Tier-2---10 | 5--4 | 1.3333 | 233 | 100% | 1005.6854 | 94.09% | 5.81% | 0.1042% | 46.8371 | 0 | 0 | 46.8371 | 0 | 40.6576 | 1.2535 | 32.4361 | 40.6576 | 1.2535 | 32.4361 | 47.5292 | 1.4653 | 32.4361 | 4.657% | 0.097832 | 0.09299 | 10279.6968 | 1573.4563 | 574.8933 | 8131.3471 | 10311.3601 | 0 | 0 | 10311.3601 | 0.001545%
2028 | 67 | 67-34R | Tier-3 | Tier-3---11 | 5--5 | 20.3065 | 1258 | 100% | 4180.1374 | 93.8% | 5.869% | 0.3284% | 194.0937 | 0 | 0 | 194.0937 | 0 | 168.4859 | 19.0901 | 8.8258 | 168.4859 | 19.0901 | 8.8258 | 196.962 | 22.3166 | 8.8258 | 4.643% | 0.24743 | 0.23519 | 16893.949 | 2506.1553 | 940.0965 | 13447.6972 | 16948.4725 | 0 | 0 | 16948.4725 | 0.0064%
2028 | 76 | 76-272 | Tier-1 | Non-HFTD---15 | 1--2 | 1.5693 | 60 | 100% | 2.4692 | 55.93% | 0% | 44.07% | 0.068363 | 0 | 0 | 0.068363 | 0 | 0.059344 | 1.4753 | 0.040226 | 0.059344 | 1.4753 | 0.040226 | 0.069373 | 1.7246 | 0.040226 | 2.769% | 0.0043474 | 0.0041322 | 567.9648 | 0.63038 | 337.7103 | 229.6241 | 580.9991 | 0 | 0 | 580.9991 | 2.254e-06%
2028 | 65 | CB 65 | Tier-1 | Non-HFTD---2 | 3--4 | 6.2999 | 644 | 100% | 189.2656 | 62.06% | 35.57% | 2.376% | 5.814 | 0 | 0 | 5.814 | 0 | 5.0469 | 5.9225 | 0.85216 | 5.0469 | 5.9225 | 0.85216 | 5.8999 | 6.9235 | 0.85216 | 3.072% | 0.027671 | 0.026302 | 6839.7543 | 634.4467 | 2950.5287 | 3254.7788 | 6974.9036 | 0 | 0 | 6974.9036 | 0.0001917%
2028 | 374 | CB 374 | Tier-1 | Non-HFTD---8 | 4--2 | 13.2841 | 373 | 100% | 28.091 | 64.57% | 0% | 35.43% | 0.89782 | 0 | 0 | 0.89782 | 0 | 0.77936 | 12.4884 | 0.062407 | 0.77936 | 12.4884 | 0.062407 | 0.91108 | 14.599 | 0.062407 | 3.196% | 0.037158 | 0.035318 | 755.9952 | 0.21604 | 512.3714 | 243.4078 | 769.9451 | 0 | 0 | 769.9451 | 2.961e-05%
2028 | 393 | 393-14R | Tier-2 | Tier-2---10 | 5--4 | 2.6388 | 132 | 100% | 924.8041 | 18.79% | 81.02% | 0.1888% | 8.6004 | 0 | 0 | 8.6004 | 0 | 7.4657 | 2.4807 | 3.0095 | 7.4657 | 2.4807 | 3.0095 | 8.7275 | 2.9 | 3.0095 | 0.93% | 0.10079 | 0.095804 | 9175.2809 | 449.6615 | 6823.2178 | 1902.4016 | 9563.3384 | 0 | 0 | 9563.3384 | 0.0002836%
2028 | 703 | 703-279R | Tier-1 | Non-HFTD---2 | 4--4 | 8.8328 | 321 | 100% | 201.9742 | 33.23% | 63.5% | 3.273% | 3.3219 | 0 | 0 | 3.3219 | 0 | 2.8836 | 8.3037 | 0.34727 | 2.8836 | 8.3037 | 0.34727 | 3.371 | 9.7071 | 0.34727 | 1.645% | 0.030988 | 0.029454 | 6517.9035 | 105.9052 | 5595.0681 | 816.9302 | 6744.5585 | 0 | 0 | 6744.5585 | 0.0001095%
2028 | 274 | CB 274 | Tier-1 | Non-HFTD---4 | 3--4 | 0.089394 | 2 | 100% | 104.8089 | 0.2793% | 99.62% | 0.1033% | 0.014491 | 0 | 0 | 0.014491 | 0 | 0.012579 | 0.084039 | 0.14968 | 0.012579 | 0.084039 | 0.14968 | 0.014705 | 0.098243 | 0.14968 | 0.01383% | 0.014981 | 0.014239 | 6996.2133 | 9.5886 | 6367.3875 | 619.2371 | 7359.5434 | 0 | 0 | 7359.5434 | 4.779e-07%
2028 | 51 | 51-861R | Tier-1 | Non-HFTD---16 | 2--1 | 3.5 | 123 | 100% | 2.9058 | 18.9% | 0% | 81.1% | 0.027191 | 0 | 0 | 0.027191 | 0 | 0.023604 | 3.2904 | 0.0071736 | 0.023604 | 3.2904 | 0.0071736 | 0.027593 | 3.8465 | 0.0071736 | 0.9358% | 0.0093474 | 0.0088847 | 310.8674 | 0.1897 | 81.668 | 229.0098 | 323.9963 | 0 | 0 | 323.9963 | 8.967e-07%
2028 | 157 | 157-257R | Tier-3 | Tier-3---14 | 5--4 | 23.0074 | 900 | 100% | 2061.1876 | 81.54% | 17.79% | 0.6678% | 83.1948 | 0 | 0 | 83.1948 | 0 | 72.2185 | 21.6293 | 3.3389 | 72.2185 | 21.6293 | 3.3389 | 84.4243 | 25.2849 | 3.3389 | 4.036% | 0.36686 | 0.3487 | 5618.4522 | 584.3287 | 907.0207 | 4127.1028 | 5672.464 | 0 | 0 | 5672.464 | 0.002743%
2028 | 454 | CB 454 | Tier-1 | Non-HFTD---11 | 3--2 | 5.108 | 105 | 100% | 14.4703 | 77.76% | 0% | 22.24% | 0.557 | 0 | 0 | 0.557 | 0 | 0.48351 | 4.802 | 0.10069 | 0.48351 | 4.802 | 0.10069 | 0.56523 | 5.6136 | 0.10069 | 3.849% | 0.014027 | 0.013332 | 1031.6351 | 0.20077 | 822.8982 | 208.5361 | 1043.582 | 0 | 0 | 1043.582 | 1.837e-05%
2028 | 761 | CB 761 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3415 | 77 | 100% | 36.3819 | 95.87% | 0% | 4.131% | 1.7265 | 0 | 0 | 1.7265 | 0 | 1.4987 | 2.2012 | 0.68086 | 1.4987 | 2.2012 | 0.68086 | 1.752 | 2.5733 | 0.68086 | 4.746% | 0.0090226 | 0.008576 | 4032.309 | 532.6165 | 590.1313 | 2909.5613 | 4040.9834 | 0 | 0 | 4040.9834 | 5.693e-05%
2028 | 209 | 209-660R | Tier-1 | Non-HFTD---13 | 1--3 | 0.73613 | 58 | 100% | 6.8017 | 90.67% | 0% | 9.327% | 0.30528 | 0 | 0 | 0.30528 | 0 | 0.265 | 0.69203 | 0.38294 | 0.265 | 0.69203 | 0.38294 | 0.30979 | 0.80899 | 0.38294 | 4.488% | 0.0025076 | 0.0023835 | 2712.4478 | 81.1565 | 1987.9733 | 643.318 | 2725.6234 | 0 | 0 | 2725.6234 | 1.007e-05%
2028 | 400 | 400-1019 | Tier-1 | Non-HFTD---12 | 4--1 | 14.5055 | 252 | 100% | 13.8376 | 46.13% | 0% | 53.87% | 0.31594 | 0 | 0 | 0.31594 | 0 | 0.27426 | 13.6366 | 0.020112 | 0.27426 | 13.6366 | 0.020112 | 0.32061 | 15.9414 | 0.020112 | 2.283% | 0.036477 | 0.034671 | 379.3524 | 0.8422 | 189.3108 | 189.1995 | 389.9959 | 0 | 0 | 389.9959 | 1.042e-05%
2028 | 545 | 545-50F | Tier-1 | Non-HFTD---4 | 3--4 | 3.0186 | 22 | 100% | 135.8264 | 1.065% | 96.96% | 1.972% | 0.071585 | 0 | 0 | 0.071585 | 0 | 0.062141 | 2.8378 | 0.021898 | 0.062141 | 2.8378 | 0.021898 | 0.072643 | 3.3174 | 0.021898 | 0.0527% | 0.019507 | 0.018541 | 6963.0284 | 7.5673 | 6209.716 | 745.7451 | 7321.7871 | 0 | 0 | 7321.7871 | 2.361e-06%
2028 | 859 | 859-42R | Tier-2 | Tier-2---3 | 4--5 | 17.8147 | 1731 | 100% | 8606.9717 | 99.86% | 0% | 0.1411% | 425.4439 | 0 | 0 | 425.4439 | 0 | 369.313 | 16.7476 | 22.0516 | 369.313 | 16.7476 | 22.0516 | 431.7311 | 19.5782 | 22.0516 | 4.943% | 0.067132 | 0.063809 | 128210.0534 | 20875.9672 | 105.3382 | 107228.748 | 128219.4758 | 0 | 0 | 128219.4758 | 0.01403%
2028 | GN1 | CB GN1 | Tier-1 | Non-HFTD---6 | 3--3 | 4.8692 | 151 | 100% | 90.3459 | 4.418% | 91.44% | 4.142% | 0.1976 | 0 | 0 | 0.1976 | 0 | 0.17153 | 4.5775 | 0.037472 | 0.17153 | 4.5775 | 0.037472 | 0.20052 | 5.3511 | 0.037472 | 0.2187% | 0.024571 | 0.023355 | 3676.9336 | 12.2101 | 3193.0279 | 471.6956 | 3859.9596 | 0 | 0 | 3859.9596 | 6.516e-06%
2028 | 449 | 449-683 | Tier-3 | Tier-3---18 | 5--3 | 1.6021 | 38 | 100% | 625.3129 | 96.7% | 3.156% | 0.1473% | 29.9305 | 0 | 0 | 29.9305 | 0 | 25.9816 | 1.5061 | 17.2507 | 25.9816 | 1.5061 | 17.2507 | 30.3728 | 1.7607 | 17.2507 | 4.786% | 0.34581 | 0.32869 | 1808.2683 | 247.0492 | 45.475 | 1515.7441 | 1811.3792 | 0 | 0 | 1811.3792 | 0.000987%
2028 | 511 | CB 511 | Tier-1 | Non-HFTD---4 | 3--4 | 2.4116 | 87 | 100% | 163.9412 | 95.95% | 3.193% | 0.8556% | 7.7866 | 0 | 0 | 7.7866 | 0 | 6.7592 | 2.2671 | 2.9814 | 6.7592 | 2.2671 | 2.9814 | 7.9016 | 2.6503 | 2.9814 | 4.75% | 0.019336 | 0.018379 | 8478.4598 | 1002.8854 | 2208.1517 | 5267.4227 | 8496.3346 | 0 | 0 | 8496.3346 | 0.0002568%
2028 | 403 | 403-15F | Tier-1 | Non-HFTD---17 | 1--2 | 0.21288 | 44 | 100% | 1.6081 | 91.84% | 0% | 8.156% | 0.073108 | 0 | 0 | 0.073108 | 0 | 0.063462 | 0.20013 | 0.31711 | 0.063462 | 0.20013 | 0.31711 | 0.074188 | 0.23395 | 0.31711 | 4.546% | 0.001071 | 0.001018 | 1501.4701 | 224.8932 | 11.1242 | 1265.4527 | 1507.8474 | 0 | 0 | 1507.8474 | 2.411e-06%
2028 | 155 | 155-1236R | Tier-1 | Non-HFTD---8 | 2--3 | 4.1822 | 117 | 100% | 27.9773 | 89.48% | 0% | 10.52% | 1.2392 | 0 | 0 | 1.2392 | 0 | 1.0757 | 3.9317 | 0.27359 | 1.0757 | 3.9317 | 0.27359 | 1.2575 | 4.5962 | 0.27359 | 4.429% | 0.01302 | 0.012376 | 2148.7604 | 291.0687 | 669.5809 | 1188.1108 | 2160.534 | 0 | 0 | 2160.534 | 4.086e-05%
2028 | 52 | 52-16F | Tier-1 | Non-HFTD---19 | 1--1 | 0.61587 | 22 | 100% | 0.6475 | 11.64% | 0% | 88.36% | 0.0037321 | 0 | 0 | 0.0037321 | 0 | 0.0032397 | 0.57898 | 0.0055955 | 0.0032397 | 0.57898 | 0.0055955 | 0.0037872 | 0.67683 | 0.0055955 | 0.5764% | 0.001922 | 0.0018269 | 336.889 | 0.24654 | 66.1207 | 270.5218 | 352.3906 | 0 | 0 | 352.3906 | 1.231e-07%
2028 | 239 | 239-2213R | Tier-3 | Tier-3---15 | 5--4 | 5.4023 | 497 | 100% | 1116.4705 | 96.46% | 3.23% | 0.3121% | 53.3076 | 0 | 0 | 53.3076 | 0 | 46.2745 | 5.0787 | 9.1115 | 46.2745 | 5.0787 | 9.1115 | 54.0954 | 5.937 | 9.1115 | 4.775% | 0.1294 | 0.123 | 8627.7496 | 1319.6651 | 288.3985 | 7019.686 | 8643.666 | 0 | 0 | 8643.666 | 0.001758%
2028 | 857 | 857-60 | Tier-1 | Non-HFTD---11 | 1--4 | 0.99317 | 41 | 100% | 13.5992 | 95.18% | 0% | 4.819% | 0.64072 | 0 | 0 | 0.64072 | 0 | 0.55619 | 0.93368 | 0.59569 | 0.55619 | 0.93368 | 0.59569 | 0.65019 | 1.0915 | 0.59569 | 4.711% | 0.0028286 | 0.0026886 | 4807.7559 | 729.0888 | 145.8859 | 3932.7813 | 4819.8226 | 0 | 0 | 4819.8226 | 2.113e-05%
2028 | 597 | 597-595 | Tier-2 | Tier-2---1 | 5--5 | 17.4555 | 1680 | 100% | 18774.394 | 95.55% | 4.388% | 0.06321% | 887.9695 | 0 | 0 | 887.9695 | 0 | 770.8154 | 16.4099 | 46.9725 | 770.8154 | 16.4099 | 46.9725 | 901.092 | 19.1834 | 46.9725 | 4.73% | 0.15307 | 0.14549 | 122655.7075 | 27181.9194 | 4937.1438 | 90536.6442 | 122940.0104 | 0 | 0 | 122940.0104 | 0.02928%
2028 | 242 | 242-1426F | Tier-2 | Tier-2---10 | 5--4 | 3.42 | 209 | 100% | 960.3446 | 65.96% | 33.81% | 0.2324% | 31.3551 | 0 | 0 | 31.3551 | 0 | 27.2182 | 3.2152 | 8.4656 | 27.2182 | 3.2152 | 8.4656 | 31.8184 | 3.7586 | 8.4656 | 3.265% | 0.10724 | 0.10194 | 8954.7461 | 1188.9727 | 2793.8383 | 4971.9351 | 9113.4933 | 0 | 0 | 9113.4933 | 0.001034%
2028 | 553 | CB 553 | Tier-1 | Non-HFTD---5 | 2--3 | 3.1561 | 136 | 100% | 49.0638 | 94.65% | 0% | 5.347% | 2.2988 | 0 | 0 | 2.2988 | 0 | 1.9955 | 2.967 | 0.67256 | 1.9955 | 2.967 | 0.67256 | 2.3328 | 3.4685 | 0.67256 | 4.685% | 0.011308 | 0.010749 | 4338.7071 | 494.3233 | 1109.1201 | 2735.2637 | 4350.7882 | 0 | 0 | 4350.7882 | 7.581e-05%
2028 | 175 | 175-90R | Tier-3 | Tier-3---9 | 5--5 | 11.9254 | 907 | 100% | 5741.4949 | 96.86% | 2.992% | 0.1472% | 275.2829 | 0 | 0 | 275.2829 | 0 | 238.9635 | 11.211 | 21.315 | 238.9635 | 11.211 | 21.315 | 279.3511 | 13.1058 | 21.315 | 4.795% | 0.20491 | 0.19477 | 28019.3198 | 4481.7022 | 744.6531 | 22792.9645 | 28065.1231 | 0 | 0 | 28065.1231 | 0.009078%
2028 | 1047 | 1047-35F | Tier-1 | Non-HFTD---15 | 1--2 | 1.687 | 51 | 100% | 2.3448 | 49.08% | 0% | 50.92% | 0.056963 | 0 | 0 | 0.056963 | 0 | 0.049447 | 1.5859 | 0.031179 | 0.049447 | 1.5859 | 0.031179 | 0.057805 | 1.854 | 0.031179 | 2.429% | 0.004654 | 0.0044236 | 503.8208 | 0.79361 | 266.8776 | 236.1496 | 517.1817 | 0 | 0 | 517.1817 | 1.878e-06%
2028 | 217 | 217-837R | Tier-3 | Tier-3---12 | 5--5 | 12.6807 | 909 | 100% | 3657.1834 | 94.66% | 5.124% | 0.2164% | 171.362 | 0 | 0 | 171.362 | 0 | 148.7534 | 11.9212 | 12.4781 | 148.7534 | 11.9212 | 12.4781 | 173.8944 | 13.936 | 12.4781 | 4.686% | 0.14269 | 0.13563 | 25630.0196 | 4247.0317 | 1289.9429 | 20093.0451 | 25701.3071 | 0 | 0 | 25701.3071 | 0.005651%
2028 | 450 | 450-50R | Tier-2 | Tier-2---11 | 4--4 | 0.51918 | 36 | 100% | 537.0702 | 32.53% | 67.41% | 0.0594% | 8.6479 | 0 | 0 | 8.6479 | 0 | 7.507 | 0.48808 | 15.3806 | 7.507 | 0.48808 | 15.3806 | 8.7757 | 0.57057 | 15.3806 | 1.61% | 0.071801 | 0.068247 | 7480.0024 | 403.5755 | 4618.5943 | 2457.8325 | 7742.8291 | 0 | 0 | 7742.8291 | 0.0002852%
2028 | 85 | 85-498F | Tier-1 | Non-HFTD---13 | 1--3 | 0.76871 | 66 | 100% | 5.1045 | 87.99% | 0% | 12.01% | 0.22234 | 0 | 0 | 0.22234 | 0 | 0.193 | 0.72267 | 0.26707 | 0.193 | 0.72267 | 0.26707 | 0.22562 | 0.8448 | 0.26707 | 4.356% | 0.002808 | 0.002669 | 1817.8549 | 381.7426 | 31.0024 | 1405.1099 | 1829.2212 | 0 | 0 | 1829.2212 | 7.332e-06%
2028 | 971 | 971-381R | Tier-2 | Tier-2---15 | 1--5 | 0.075568 | 0 | 100% | 191.8954 | 99.94% | 0% | 0.06293% | 9.4928 | 0 | 0 | 9.4928 | 0 | 8.2404 | 0.071042 | 115.9939 | 8.2404 | 0.071042 | 115.9939 | 9.6331 | 0.083049 | 115.9939 | 4.947% | 0.0003802 | 0.00036138 | 504722.2701 | 81534.2634 | 28.852 | 423159.1547 | 504738.8106 | 0 | 0 | 504738.8106 | 0.000313%
2028 | 441 | 441-279R | Tier-3 | Tier-3---18 | 5--2 | 2.1594 | 50 | 100% | 582.1633 | 91.34% | 8.391% | 0.2732% | 26.3202 | 0 | 0 | 26.3202 | 0 | 22.8477 | 2.0301 | 11.2545 | 22.8477 | 2.0301 | 11.2545 | 26.7092 | 2.3732 | 11.2545 | 4.521% | 0.53527 | 0.50877 | 1087.6056 | 130.7987 | 72.799 | 884.0079 | 1092.5132 | 0 | 0 | 1092.5132 | 0.0008679%
2028 | 79 | 79-808R | Tier-3 | Tier-3---3 | 5--5 | 10.6674 | 427 | 100% | 19978.3255 | 99.23% | 0.7353% | 0.0338% | 981.3213 | 0 | 0 | 981.3213 | 0 | 851.8508 | 10.0284 | 84.9436 | 851.8508 | 10.0284 | 84.9436 | 995.8233 | 11.7233 | 84.9436 | 4.912% | 0.44563 | 0.42357 | 44831.6641 | 7188.3432 | 299.9404 | 37343.3805 | 44849.6205 | 0 | 0 | 44849.6205 | 0.03236%
2028 | RD1 | CB RD1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.1822 | 221 | 100% | 3.8065 | 31.86% | 0% | 68.14% | 0.060024 | 0 | 0 | 0.060024 | 0 | 0.052105 | 2.9916 | 0.017417 | 0.052105 | 2.9916 | 0.017417 | 0.060911 | 3.4972 | 0.017417 | 1.577% | 0.009563 | 0.0090896 | 398.0431 | 3.9878 | 128.2654 | 265.7899 | 412.1688 | 0 | 0 | 412.1688 | 1.979e-06%
2028 | 64 | 64-14F | Tier-1 | Non-HFTD---3 | 4--3 | 8.9328 | 168 | 100% | 111.7051 | 4.553% | 91.33% | 4.117% | 0.25173 | 0 | 0 | 0.25173 | 0 | 0.21852 | 8.3977 | 0.026021 | 0.21852 | 8.3977 | 0.026021 | 0.25545 | 9.817 | 0.026021 | 0.2254% | 0.030765 | 0.029242 | 3630.8929 | 16.1011 | 3147.9882 | 466.8035 | 3811.3735 | 0 | 0 | 3811.3735 | 8.301e-06%
2028 | 240 | 240-1148 | Tier-3 | Tier-3---17 | 4--4 | 3.4333 | 108 | 100% | 376.72 | 96.88% | 2.523% | 0.5996% | 18.0654 | 0 | 0 | 18.0654 | 0 | 15.6819 | 3.2277 | 4.8586 | 15.6819 | 3.2277 | 4.8586 | 18.3323 | 3.7732 | 4.8586 | 4.795% | 0.037482 | 0.035627 | 10050.6383 | 1533.8365 | 215.1786 | 8301.6232 | 10066.9823 | 0 | 0 | 10066.9823 | 0.0005957%
2028 | 470 | 470-47R | Tier-3 | Tier-3---2 | 5--5 | 24.3072 | 930 | 100% | 16740.3912 | 99.37% | 0.5365% | 0.09319% | 823.4313 | 0 | 0 | 823.4313 | 0 | 714.7921 | 22.8512 | 31.2803 | 714.7921 | 22.8512 | 31.2803 | 835.6001 | 26.7133 | 31.2803 | 4.919% | 0.16225 | 0.15422 | 103174.1084 | 18151.9385 | 504.5592 | 84517.6107 | 103207.9428 | 0 | 0 | 103207.9428 | 0.02715%
2028 | 448 | 448-714R | Tier-3 | Tier-3---14 | 5--3 | 11.8164 | 264 | 100% | 2119.752 | 55.7% | 43.96% | 0.3458% | 58.4428 | 0 | 0 | 58.4428 | 0 | 50.7321 | 11.1086 | 4.5669 | 50.7321 | 11.1086 | 4.5669 | 59.3064 | 12.9861 | 4.5669 | 2.757% | 0.46343 | 0.44049 | 4574.0639 | 348.1722 | 1808.8383 | 2417.0534 | 4679.5943 | 0 | 0 | 4679.5943 | 0.001927%
2028 | 971 | 971-383R | Tier-3 | Tier-3---4 | 5--5 | 9.7066 | 444 | 100% | 14770.5962 | 98.43% | 1.528% | 0.03956% | 719.68 | 0 | 0 | 719.68 | 0 | 624.7291 | 9.1252 | 68.462 | 624.7291 | 9.1252 | 68.462 | 730.3154 | 10.6675 | 68.462 | 4.872% | 0.13837 | 0.13152 | 106747.8715 | 18250.5069 | 1553.2478 | 86944.1168 | 106835.0414 | 0 | 0 | 106835.0414 | 0.02373%
2028 | 410 | 410-50R | Tier-1 | Non-HFTD---1 | 4--5 | 11.9653 | 1104 | 100% | 1314.3326 | 99.38% | 0% | 0.6151% | 64.6593 | 0 | 0 | 64.6593 | 0 | 56.1285 | 11.2486 | 4.9898 | 56.1285 | 11.2486 | 4.9898 | 65.6148 | 13.1497 | 4.9898 | 4.92% | 0.044038 | 0.041858 | 29845.69 | 7721.7282 | 133.8501 | 21990.1116 | 29855.2499 | 0 | 0 | 29855.2499 | 0.002132%
2028 | 215 | 215-38R | Tier-3 | Tier-3---10 | 5--5 | 6.4307 | 367 | 100% | 5434.8155 | 98.92% | 1.009% | 0.07406% | 266.1091 | 0 | 0 | 266.1091 | 0 | 231 | 6.0455 | 38.21 | 231 | 6.0455 | 38.21 | 270.0416 | 7.0673 | 38.21 | 4.896% | 0.12528 | 0.11908 | 43381.3494 | 7513.7468 | 468.0295 | 35399.5731 | 43405.8232 | 0 | 0 | 43405.8232 | 0.008775%
2028 | 60 | 60-576F | Tier-1 | Non-HFTD---16 | 2--1 | 2.3228 | 78 | 100% | 2.6375 | 57.75% | 0% | 42.25% | 0.075392 | 0 | 0 | 0.075392 | 0 | 0.065445 | 2.1836 | 0.029971 | 0.065445 | 2.1836 | 0.029971 | 0.076506 | 2.5527 | 0.029971 | 2.858% | 0.0059106 | 0.005618 | 446.2382 | 1.1181 | 268.8191 | 176.301 | 456.0577 | 0 | 0 | 456.0577 | 2.486e-06%
2028 | 516 | 516-5F | Tier-1 | Non-HFTD---18 | 1--1 | 1.126 | 37 | 100% | 1.2452 | 18.96% | 0% | 81.04% | 0.011684 | 0 | 0 | 0.011684 | 0 | 0.010142 | 1.0585 | 0.0095814 | 0.010142 | 1.0585 | 0.0095814 | 0.011856 | 1.2374 | 0.0095814 | 0.9383% | 0.0037102 | 0.0035265 | 335.6145 | 0.20467 | 88.3256 | 247.0843 | 349.7795 | 0 | 0 | 349.7795 | 3.853e-07%
2028 | 276 | 276-228 | Tier-1 | Non-HFTD---2 | 4--3 | 17.7437 | 786 | 100% | 290.9914 | 11.65% | 84% | 4.346% | 1.6788 | 0 | 0 | 1.6788 | 0 | 1.4573 | 16.6809 | 0.087363 | 1.4573 | 16.6809 | 0.087363 | 1.7036 | 19.5001 | 0.087363 | 0.5769% | 0.065634 | 0.062385 | 4433.5468 | 54.5858 | 3672.1531 | 706.8079 | 4637.5265 | 0 | 0 | 4637.5265 | 5.536e-05%
2028 | 442 | 442-729 | Tier-3 | Tier-3---15 | 5--3 | 2.7701 | 39 | 100% | 704.6091 | 96.62% | 3.132% | 0.2514% | 33.6979 | 0 | 0 | 33.6979 | 0 | 29.252 | 2.6041 | 11.2329 | 29.252 | 2.6041 | 11.2329 | 34.1959 | 3.0443 | 11.2329 | 4.782% | 0.36059 | 0.34274 | 1954.0299 | 229.5782 | 101.2201 | 1623.2315 | 1957.4733 | 0 | 0 | 1957.4733 | 0.001111%
2028 | 141 | CB 141 | Tier-1 | Non-HFTD---13 | 2--2 | 0.62292 | 9 | 100% | 7.7413 | 92.75% | 0.6935% | 6.554% | 0.35542 | 0 | 0 | 0.35542 | 0 | 0.30853 | 0.5856 | 0.52686 | 0.30853 | 0.5856 | 0.52686 | 0.36068 | 0.68458 | 0.52686 | 4.591% | 0.0076852 | 0.0073048 | 1007.3001 | 119.4264 | 208.7958 | 679.0778 | 1011.1018 | 0 | 0 | 1011.1018 | 1.172e-05%
2028 | 160 | 160-20R | Tier-1 | Non-HFTD---10 | 3--2 | 5.9633 | 134 | 100% | 17.1087 | 69.24% | 0% | 30.76% | 0.58642 | 0 | 0 | 0.58642 | 0 | 0.50905 | 5.6061 | 0.090803 | 0.50905 | 5.6061 | 0.090803 | 0.59508 | 6.5536 | 0.090803 | 3.428% | 0.018715 | 0.017789 | 914.1502 | 3.7049 | 637.1365 | 273.3088 | 928.792 | 0 | 0 | 928.792 | 1.934e-05%
2028 | 730 | 730-835 | Tier-1 | Non-HFTD---6 | 3--3 | 4.7612 | 180 | 100% | 55.2599 | 94.32% | 0% | 5.676% | 2.5801 | 0 | 0 | 2.5801 | 0 | 2.2397 | 4.476 | 0.50038 | 2.2397 | 4.476 | 0.50038 | 2.6182 | 5.2325 | 0.50038 | 4.669% | 0.01382 | 0.013136 | 3998.6627 | 454.843 | 1618.098 | 1925.7217 | 4010.4832 | 0 | 0 | 4010.4832 | 8.508e-05%
2028 | 378 | CB 378 | Tier-1 | Non-HFTD---18 | 1--1 | 0.98752 | 1 | 100% | 1.1196 | 10.82% | 0% | 89.18% | 0.0059945 | 0 | 0 | 0.0059945 | 0 | 0.0052036 | 0.92837 | 0.0056051 | 0.0052036 | 0.92837 | 0.0056051 | 0.0060831 | 1.0853 | 0.0056051 | 0.5354% | 0.0033556 | 0.0031895 | 333.65 | 5.5607 | 29.9513 | 298.138 | 349.1463 | 0 | 0 | 349.1463 | 1.977e-07%
2028 | 1458 | 1458-1075F | Tier-3 | Tier-3---20 | 1--5 | 0.03428 | 4 | 100% | 58.2342 | 99.94% | 0% | 0.06312% | 2.8808 | 0 | 0 | 2.8808 | 0 | 2.5007 | 0.032227 | 77.5965 | 2.5007 | 0.032227 | 77.5965 | 2.9233 | 0.037674 | 77.5965 | 4.947% | 0.00013 | 0.00012356 | 447955.3838 | 72658.276 | 116.4548 | 375180.6529 | 447970.1088 | 0 | 0 | 447970.1088 | 9.5e-05%
2028 | 409 | CB 409 | Tier-1 | Non-HFTD---8 | 3--2 | 6.5118 | 143 | 100% | 29.0295 | 85.38% | 0% | 14.62% | 1.2269 | 0 | 0 | 1.2269 | 0 | 1.065 | 6.1217 | 0.17398 | 1.065 | 6.1217 | 0.17398 | 1.245 | 7.1564 | 0.17398 | 4.226% | 0.017884 | 0.016999 | 1623.1908 | 7.6402 | 1361.7978 | 253.7528 | 1635.548 | 0 | 0 | 1635.548 | 4.046e-05%
2028 | 149 | 149-129R | Tier-1 | Non-HFTD---13 | 2--2 | 0.15038 | 7 | 100% | 5.3596 | 91.52% | 2.339% | 6.145% | 0.24279 | 0 | 0 | 0.24279 | 0 | 0.21076 | 0.14137 | 1.4908 | 0.21076 | 0.14137 | 1.4908 | 0.24638 | 0.16526 | 1.4908 | 4.53% | 0.007042 | 0.0066934 | 761.089 | 113.4886 | 18.657 | 628.9434 | 764.452 | 0 | 0 | 764.452 | 8.006e-06%
2028 | 140 | CB 140 | Tier-1 | Non-HFTD---5 | 3--4 | 3.3106 | 54 | 100% | 74.8313 | 17.08% | 79.52% | 3.4% | 0.63266 | 0 | 0 | 0.63266 | 0 | 0.54919 | 3.1123 | 0.17646 | 0.54919 | 3.1123 | 0.17646 | 0.64201 | 3.6383 | 0.17646 | 0.8455% | 0.014532 | 0.013812 | 5149.556 | 4.4743 | 4651.9396 | 493.1422 | 5371.9295 | 0 | 0 | 5371.9295 | 2.086e-05%
2028 | 296 | CB 296 | Tier-2 | Tier-2---19 | 1--5 | 0.44716 | 96 | 100% | 39.5699 | 99.22% | 0% | 0.7837% | 1.9434 | 0 | 0 | 1.9434 | 0 | 1.687 | 0.42037 | 4.013 | 1.687 | 0.42037 | 4.013 | 1.9721 | 0.49142 | 4.013 | 4.911% | 0.0016582 | 0.0015761 | 23863.1595 | 3322.2329 | 3363.4423 | 17177.4843 | 23872.899 | 0 | 0 | 23872.899 | 6.408e-05%
2028 | 172 | CB 172 | Tier-1 | Non-HFTD---8 | 4--2 | 4.7581 | 37 | 100% | 28.3098 | 70.45% | 18.79% | 10.75% | 0.98726 | 0 | 0 | 0.98726 | 0 | 0.85701 | 4.4731 | 0.19159 | 0.85701 | 4.4731 | 0.19159 | 1.0019 | 5.2291 | 0.19159 | 3.487% | 0.048261 | 0.045872 | 586.5969 | 29.8676 | 317.2028 | 239.5265 | 595.6234 | 0 | 0 | 595.6234 | 3.256e-05%
2028 | 444 | 444-43R | Tier-2 | Tier-2---5 | 5--5 | 20.6063 | 130 | 100% | 3413.8137 | 97.67% | 1.995% | 0.3352% | 165.0466 | 0 | 0 | 165.0466 | 0 | 143.2712 | 19.372 | 7.3958 | 143.2712 | 19.372 | 7.3958 | 167.4857 | 22.6461 | 7.3958 | 4.835% | 0.2124 | 0.20189 | 16072.3576 | 2078.7289 | 404.7694 | 13588.8592 | 16091.8592 | 0 | 0 | 16091.8592 | 0.005443%
2028 | 514 | CB 514 | Tier-1 | Non-HFTD---3 | 4--3 | 20.4863 | 910 | 100% | 180.2752 | 92.03% | 0% | 7.975% | 8.212 | 0 | 0 | 8.212 | 0 | 7.1285 | 19.2592 | 0.37014 | 7.1285 | 19.2592 | 0.37014 | 8.3334 | 22.5142 | 0.37014 | 4.555% | 0.058723 | 0.055816 | 3069.9453 | 628.347 | 399.7755 | 2041.8228 | 3082.6949 | 0 | 0 | 3082.6949 | 0.0002708%
2028 | 48 | CB 48 | Tier-1 | Non-HFTD---18 | 2--1 | 1.5148 | 3 | 100% | 1.5208 | 11.23% | 0% | 88.77% | 0.0084538 | 0 | 0 | 0.0084538 | 0 | 0.0073384 | 1.4241 | 0.0051531 | 0.0073384 | 1.4241 | 0.0051531 | 0.0085787 | 1.6648 | 0.0051531 | 0.5559% | 0.0049642 | 0.0047185 | 306.3449 | 5.7261 | 24.7034 | 275.9155 | 320.507 | 0 | 0 | 320.507 | 2.788e-07%
2028 | 181 | CB 181 | Tier-1 | Non-HFTD---15 | 1--2 | 0.7286 | 20 | 100% | 2.8335 | 82.32% | 0% | 17.68% | 0.11546 | 0 | 0 | 0.11546 | 0 | 0.10023 | 0.68496 | 0.14633 | 0.10023 | 0.68496 | 0.14633 | 0.11717 | 0.80072 | 0.14633 | 4.075% | 0.0024946 | 0.0023711 | 1135.8594 | 18.9687 | 837.4512 | 279.4394 | 1146.3163 | 0 | 0 | 1146.3163 | 3.808e-06%
2028 | 1030 | 1030-1728R | Tier-3 | Tier-3---9 | 5--5 | 2.6777 | 105 | 100% | 5124.1587 | 98.26% | 1.711% | 0.02883% | 249.2335 | 0 | 0 | 249.2335 | 0 | 216.3509 | 2.5173 | 85.9462 | 216.3509 | 2.5173 | 85.9462 | 252.9167 | 2.9427 | 85.9462 | 4.864% | 0.23544 | 0.22379 | 21764.1991 | 3692.5677 | 344.0629 | 17727.5685 | 21783.9158 | 0 | 0 | 21783.9158 | 0.008219%
2028 | BW1 | CB BW1 | Tier-1 | Non-HFTD---11 | 1--3 | 1.0872 | 45 | 100% | 8.712 | 88.19% | 0% | 11.81% | 0.3803 | 0 | 0 | 0.3803 | 0 | 0.33013 | 1.0221 | 0.32301 | 0.33013 | 1.0221 | 0.32301 | 0.38592 | 1.1948 | 0.32301 | 4.365% | 0.0039232 | 0.003729 | 2220.6335 | 316.4948 | 49.7388 | 1854.3999 | 2234.2939 | 0 | 0 | 2234.2939 | 1.254e-05%
2028 | 406 | CB 406 | Tier-1 | Non-HFTD---12 | 3--2 | 5.5205 | 205 | 100% | 8.8138 | 58.69% | 0% | 41.31% | 0.25605 | 0 | 0 | 0.25605 | 0 | 0.22227 | 5.1898 | 0.042827 | 0.22227 | 5.1898 | 0.042827 | 0.25983 | 6.0669 | 0.042827 | 2.905% | 0.014645 | 0.01392 | 601.8164 | 0.6689 | 372.8417 | 228.3057 | 614.7641 | 0 | 0 | 614.7641 | 8.443e-06%
2028 | 241 | 241-820AE | Tier-1 | Non-HFTD---2 | 5--3 | 3.04 | 97 | 100% | 286.7702 | 14.9% | 84.42% | 0.6786% | 2.1155 | 0 | 0 | 2.1155 | 0 | 1.8364 | 2.8579 | 0.64258 | 1.8364 | 2.8579 | 0.64258 | 2.1468 | 3.3409 | 0.64258 | 0.7377% | 0.10624 | 0.10098 | 2699.1913 | 103.9208 | 2115.2903 | 479.9802 | 2818.8105 | 0 | 0 | 2818.8105 | 6.976e-05%
2028 | 1162 | 1162-329R | Tier-2 | Tier-2---13 | 4--3 | 3.4321 | 22 | 100% | 206.5878 | 96.62% | 2.592% | 0.7875% | 9.8805 | 0 | 0 | 9.8805 | 0 | 8.577 | 3.2265 | 2.6583 | 8.577 | 3.2265 | 2.6583 | 10.0266 | 3.7718 | 2.6583 | 4.783% | 0.070019 | 0.066553 | 2950.4371 | 449.0329 | 64.8259 | 2436.5783 | 2955.6292 | 0 | 0 | 2955.6292 | 0.0003258%
2028 | 96 | CB 96 | Tier-1 | Non-HFTD---7 | 2--3 | 0.84791 | 78 | 100% | 37.3393 | 43.85% | 54.05% | 2.092% | 0.81053 | 0 | 0 | 0.81053 | 0 | 0.70359 | 0.79712 | 0.88267 | 0.70359 | 0.79712 | 0.88267 | 0.82251 | 0.93184 | 0.88267 | 2.171% | 0.0084764 | 0.0080568 | 4405.0953 | 227.7051 | 3027.1235 | 1150.2667 | 4533.9014 | 0 | 0 | 4533.9014 | 2.673e-05%
2028 | 145 | 145-633 | Tier-1 | Non-HFTD---11 | 2--2 | 0.17216 | 0 | 100% | 10.3552 | 34.57% | 64.03% | 1.397% | 0.1772 | 0 | 0 | 0.1772 | 0 | 0.15382 | 0.16185 | 0.9504 | 0.15382 | 0.16185 | 0.9504 | 0.17982 | 0.1892 | 0.9504 | 1.711% | 0.0067068 | 0.0063748 | 1543.9807 | 37.6917 | 1219.1738 | 287.1152 | 1596.5913 | 0 | 0 | 1596.5913 | 5.843e-06%
2028 | 178 | 178-982 | Tier-2 | Tier-2---21 | 1--1 | 1.1551 | 19 | 100% | 0.95479 | 13.38% | 0% | 86.62% | 0.0063254 | 0 | 0 | 0.0063254 | 0 | 0.0054908 | 1.0859 | 0.0050564 | 0.0054908 | 1.0859 | 0.0050564 | 0.0064188 | 1.2694 | 0.0050564 | 0.6625% | 0.0033454 | 0.0031798 | 285.4035 | 0.62363 | 58.6739 | 226.106 | 298.2775 | 0 | 0 | 298.2775 | 2.086e-07%
2028 | NO1 | NO1-288F | Tier-1 | Non-HFTD---18 | 1--1 | 1.0576 | 14 | 100% | 0.81031 | 11.55% | 0% | 88.45% | 0.0046337 | 0 | 0 | 0.0046337 | 0 | 0.0040223 | 0.99423 | 0.0040457 | 0.0040223 | 0.99423 | 0.0040457 | 0.0047021 | 1.1623 | 0.0040457 | 0.5718% | 0.002839 | 0.0026985 | 285.4227 | 0.18996 | 55.9053 | 229.3274 | 298.5697 | 0 | 0 | 298.5697 | 1.528e-07%
2028 | 712 | 712-26 | Tier-1 | Non-HFTD---19 | 1--2 | 0.16006 | 32 | 100% | 0.49531 | 70.46% | 0% | 29.54% | 0.017274 | 0 | 0 | 0.017274 | 0 | 0.014995 | 0.15047 | 0.099654 | 0.014995 | 0.15047 | 0.099654 | 0.017529 | 0.1759 | 0.099654 | 3.488% | 0.0005438 | 0.00051688 | 910.8315 | 103.0746 | 31.4131 | 776.3438 | 924.8457 | 0 | 0 | 924.8457 | 5.696e-07%
2028 | 78 | CB 78 | Tier-3 | Tier-3---20 | 1--5 | 0.036174 | 0 | 100% | 25.281 | 99.56% | 0% | 0.4423% | 1.2459 | 0 | 0 | 1.2459 | 0 | 1.0815 | 0.034007 | 31.8018 | 1.0815 | 0.034007 | 31.8018 | 1.2643 | 0.039755 | 31.8018 | 4.928% | 0.0002122 | 0.0002017 | 119137.3955 | 18702.2941 | 125.3011 | 100309.8003 | 119164.835 | 0 | 0 | 119164.835 | 4.108e-05%
2028 | 532 | 532-763 | Tier-1 | Non-HFTD---2 | 5--4 | 6.6682 | 237 | 100% | 872.9353 | 22.07% | 77.46% | 0.4675% | 9.5372 | 0 | 0 | 9.5372 | 0 | 8.2789 | 6.2688 | 1.3207 | 8.2789 | 6.2688 | 1.3207 | 9.6781 | 7.3283 | 1.3207 | 1.093% | 0.10819 | 0.10283 | 8068.6143 | 305.6113 | 5713.7599 | 2049.2431 | 8396.0666 | 0 | 0 | 8396.0666 | 0.0003145%
2028 | 138 | 138-360F | Tier-1 | Non-HFTD---17 | 1--2 | 0.59812 | 11 | 100% | 1.3988 | 40.66% | 0% | 59.34% | 0.02815 | 0 | 0 | 0.02815 | 0 | 0.024436 | 0.56229 | 0.043457 | 0.024436 | 0.56229 | 0.043457 | 0.028566 | 0.65733 | 0.043457 | 2.012% | 0.0024168 | 0.0022972 | 578.7745 | 0.25845 | 266.504 | 312.012 | 596.6618 | 0 | 0 | 596.6618 | 9.283e-07%
2028 | 1435 | 1435-1075F | Tier-1 | Non-HFTD---15 | 2--2 | 2.7231 | 121 | 100% | 4.6893 | 70.05% | 0% | 29.95% | 0.1626 | 0 | 0 | 0.1626 | 0 | 0.14114 | 2.56 | 0.055134 | 0.14114 | 2.56 | 0.055134 | 0.165 | 2.9927 | 0.055134 | 3.467% | 0.0067656 | 0.0064307 | 693.1065 | 136.0595 | 69.2928 | 487.7542 | 703.9175 | 0 | 0 | 703.9175 | 5.362e-06%
2028 | 1202 | 1202-9 | Tier-2 | Tier-2---17 | 2--4 | 3.468 | 67 | 100% | 73.4421 | 96.84% | 0% | 3.16% | 3.5205 | 0 | 0 | 3.5205 | 0 | 3.056 | 3.2602 | 0.93737 | 3.056 | 3.2602 | 0.93737 | 3.5725 | 3.8112 | 0.93737 | 4.794% | 0.01182 | 0.011235 | 6213.48 | 1453.8319 | 498.5132 | 4261.1349 | 6223.7055 | 0 | 0 | 6223.7055 | 0.0001161%
2028 | 221 | 221-344R | Tier-3 | Tier-3---13 | 5--4 | 11.5724 | 1453 | 100% | 2735.9283 | 96.11% | 3.605% | 0.2871% | 130.1577 | 0 | 0 | 130.1577 | 0 | 112.9854 | 10.8792 | 10.3855 | 112.9854 | 10.8792 | 10.3855 | 132.0812 | 12.7179 | 10.3855 | 4.757% | 0.2115 | 0.20103 | 12935.7823 | 1776.6901 | 423.0574 | 10736.0349 | 12962.0007 | 0 | 0 | 12962.0007 | 0.004292%
2028 | 274 | 274-40 | Tier-1 | Non-HFTD---3 | 4--3 | 7.8386 | 296 | 100% | 130.2262 | 2.649% | 92.8% | 4.548% | 0.17075 | 0 | 0 | 0.17075 | 0 | 0.14822 | 7.3691 | 0.020114 | 0.14822 | 7.3691 | 0.020114 | 0.17328 | 8.6146 | 0.020114 | 0.1311% | 0.037195 | 0.035354 | 3501.1361 | 5.6164 | 3059.4974 | 436.0223 | 3678.638 | 0 | 0 | 3678.638 | 5.631e-06%
2028 | 270 | CB 270 | Tier-1 | Non-HFTD---5 | 3--4 | 2.0546 | 375 | 100% | 71.4588 | 15.92% | 82.32% | 1.76% | 0.56317 | 0 | 0 | 0.56317 | 0 | 0.48887 | 1.9315 | 0.25311 | 0.48887 | 1.9315 | 0.25311 | 0.5715 | 2.2579 | 0.25311 | 0.7881% | 0.0142 | 0.013497 | 5032.3124 | 129.2561 | 3832.2088 | 1070.8475 | 5252.6589 | 0 | 0 | 5252.6589 | 1.857e-05%
2028 | 563 | CB 563 | Tier-1 | Non-HFTD---11 | 1--4 | 0.17481 | 35 | 100% | 10.231 | 98.75% | 0% | 1.252% | 0.50009 | 0 | 0 | 0.50009 | 0 | 0.43411 | 0.16434 | 2.6416 | 0.43411 | 0.16434 | 2.6416 | 0.50748 | 0.19211 | 2.6416 | 4.888% | 0.0006932 | 0.00065889 | 14759.0669 | 2171.1529 | 3891.2279 | 8696.6862 | 14768.6918 | 0 | 0 | 14768.6918 | 1.649e-05%
2028 | 700 | CB 700 | Tier-1 | Non-HFTD---13 | 1--3 | 0.40907 | 7 | 100% | 6.7901 | 95.69% | 0% | 4.313% | 0.32161 | 0 | 0 | 0.32161 | 0 | 0.27918 | 0.38457 | 0.72596 | 0.27918 | 0.38457 | 0.72596 | 0.32636 | 0.44956 | 0.72596 | 4.736% | 0.0015946 | 0.0015157 | 4258.1661 | 656.9619 | 50.5505 | 3550.6537 | 4267.7311 | 0 | 0 | 4267.7311 | 1.061e-05%
2028 | 157 | 157-81R | Tier-3 | Tier-3---3 | 5--5 | 27.7907 | 1435 | 100% | 18749.5963 | 97% | 2.901% | 0.09453% | 900.3079 | 0 | 0 | 900.3079 | 0 | 781.526 | 26.126 | 29.9137 | 781.526 | 26.126 | 29.9137 | 913.6128 | 30.5416 | 29.9137 | 4.802% | 0.38414 | 0.36512 | 48809.8885 | 7659.8047 | 1292.0303 | 39858.0535 | 48886.0197 | 0 | 0 | 48886.0197 | 0.02969%
2028 | 189 | 189-645 | Tier-1 | Non-HFTD---11 | 2--3 | 1.8176 | 78 | 100% | 13.5881 | 92.26% | 0% | 7.743% | 0.62053 | 0 | 0 | 0.62053 | 0 | 0.53866 | 1.7087 | 0.31524 | 0.53866 | 1.7087 | 0.31524 | 0.6297 | 1.9975 | 0.31524 | 4.567% | 0.0052774 | 0.0050162 | 2574.7796 | 257.5393 | 821.9251 | 1495.3153 | 2585.1626 | 0 | 0 | 2585.1626 | 2.046e-05%
2028 | 368 | 368-403F | Tier-1 | Non-HFTD---11 | 2--2 | 0.42387 | 9 | 100% | 10.4781 | 1.466% | 94.68% | 3.85% | 0.0076023 | 0 | 0 | 0.0076023 | 0 | 0.0065993 | 0.39848 | 0.016561 | 0.0065993 | 0.39848 | 0.016561 | 0.0077146 | 0.46583 | 0.016561 | 0.07255% | 0.0067636 | 0.0064288 | 1549.1827 | 1.6714 | 1373.0792 | 174.432 | 1628.6783 | 0 | 0 | 1628.6783 | 2.507e-07%
2028 | 719 | 719-28 | Tier-1 | Non-HFTD---19 | 1--3 | 0.011364 | 0 | 100% | 0.19101 | 81.43% | 0% | 18.57% | 0.0076988 | 0 | 0 | 0.0076988 | 0 | 0.0066831 | 0.010683 | 0.62558 | 0.0066831 | 0.010683 | 0.62558 | 0.0078126 | 0.012489 | 0.62558 | 4.031% | 7.58e-05 | 7.2048e-05 | 2519.9154 | 0.35219 | 2094.389 | 425.1743 | 2544.2902 | 0 | 0 | 2544.2902 | 2.539e-07%
2028 | 62 | CB 62 | Tier-1 | Non-HFTD---5 | 3--4 | 1.8229 | 124 | 100% | 88.5913 | 17.86% | 80.39% | 1.758% | 0.78309 | 0 | 0 | 0.78309 | 0 | 0.67977 | 1.7137 | 0.39666 | 0.67977 | 1.7137 | 0.39666 | 0.79466 | 2.0034 | 0.39666 | 0.8839% | 0.016405 | 0.015593 | 5400.2599 | 65.1821 | 4479.0088 | 856.069 | 5631.2734 | 0 | 0 | 5631.2734 | 2.582e-05%
2028 | 88 | 88-27F | Tier-1 | Non-HFTD---15 | 1--3 | 0.14678 | 11 | 100% | 2.2245 | 92.57% | 0% | 7.426% | 0.10194 | 0 | 0 | 0.10194 | 0 | 0.088488 | 0.13799 | 0.64127 | 0.088488 | 0.13799 | 0.64127 | 0.10344 | 0.16131 | 0.64127 | 4.582% | 0.0008056 | 0.00076572 | 2761.3126 | 412.5963 | 52.951 | 2295.7652 | 2771.9912 | 0 | 0 | 2771.9912 | 3.361e-06%
2028 | 309 | 309-15F | Tier-1 | Non-HFTD---12 | 3--1 | 8.7252 | 163 | 100% | 10.1949 | 53% | 0% | 47% | 0.26747 | 0 | 0 | 0.26747 | 0 | 0.23219 | 8.2025 | 0.028307 | 0.23219 | 8.2025 | 0.028307 | 0.27143 | 9.5888 | 0.028307 | 2.624% | 0.023995 | 0.022807 | 424.8851 | 7.9838 | 195.2064 | 221.6949 | 435.2844 | 0 | 0 | 435.2844 | 8.82e-06%
2028 | 161 | 161-975F | Tier-1 | Non-HFTD---13 | 2--2 | 3.2134 | 83 | 100% | 8.5862 | 76.7% | 0% | 23.3% | 0.32599 | 0 | 0 | 0.32599 | 0 | 0.28298 | 3.021 | 0.093673 | 0.28298 | 3.021 | 0.093673 | 0.33081 | 3.5315 | 0.093673 | 3.797% | 0.0085198 | 0.0080981 | 1007.7888 | 0.42746 | 792.7442 | 214.6171 | 1020.0168 | 0 | 0 | 1020.0168 | 1.075e-05%
2028 | 90 | CB 90 | Tier-1 | Non-HFTD---9 | 2--3 | 0.018939 | 0 | 100% | 16.6741 | 2.335% | 97.48% | 0.1839% | 0.019272 | 0 | 0 | 0.019272 | 0 | 0.016729 | 0.017805 | 0.93959 | 0.016729 | 0.017805 | 0.93959 | 0.019557 | 0.020814 | 0.93959 | 0.1156% | 0.0049876 | 0.0047407 | 3343.1051 | 4.348 | 3056.2234 | 282.5337 | 3513.1416 | 0 | 0 | 3513.1416 | 6.355e-07%
2028 | 183 | CB 183 | Tier-1 | Non-HFTD---4 | 3--4 | 2.7093 | 99 | 100% | 128.8021 | 22.66% | 75.77% | 1.57% | 1.4445 | 0 | 0 | 1.4445 | 0 | 1.2539 | 2.547 | 0.4923 | 1.2539 | 2.547 | 0.4923 | 1.4658 | 2.9775 | 0.4923 | 1.121% | 0.022326 | 0.021221 | 5769.2045 | 129.7649 | 4423.5742 | 1215.8654 | 6001.5822 | 0 | 0 | 6001.5822 | 4.763e-05%
2028 | 854 | 854-607F | Tier-1 | Non-HFTD---13 | 1--5 | 0.039394 | 11 | 100% | 5.4805 | 98.61% | 0% | 1.386% | 0.26752 | 0 | 0 | 0.26752 | 0 | 0.23223 | 0.037034 | 6.2706 | 0.23223 | 0.037034 | 6.2706 | 0.27148 | 0.043293 | 6.2706 | 4.881% | 0.000262 | 0.00024903 | 20917.8697 | 3367.0159 | 28.8837 | 17521.9701 | 20932.9704 | 0 | 0 | 20932.9704 | 8.822e-06%
2028 | 445 | 445-1311R | Tier-3 | Tier-3---5 | 5--5 | 13.2995 | 388 | 100% | 9632.5907 | 94.96% | 4.965% | 0.07823% | 452.7685 | 0 | 0 | 452.7685 | 0 | 393.0326 | 12.5028 | 31.4355 | 393.0326 | 12.5028 | 31.4355 | 459.4596 | 14.616 | 31.4355 | 4.7% | 0.53792 | 0.51129 | 17907.0399 | 2661.5807 | 811.6698 | 14433.7894 | 17954.067 | 0 | 0 | 17954.067 | 0.01493%
2028 | 54 | CB 54 | Tier-1 | Non-HFTD---11 | 2--2 | 2.685 | 55 | 100% | 9.0518 | 74.11% | 0% | 25.89% | 0.33207 | 0 | 0 | 0.33207 | 0 | 0.28826 | 2.5242 | 0.1142 | 0.28826 | 2.5242 | 0.1142 | 0.33697 | 2.9508 | 0.1142 | 3.669% | 0.0079966 | 0.0076008 | 1131.9509 | 0.54614 | 863.4862 | 267.9186 | 1147.2119 | 0 | 0 | 1147.2119 | 1.095e-05%
2028 | 353 | 353-902F | Tier-2 | Tier-2---11 | 5--3 | 0.57917 | 50 | 100% | 465.1006 | 62.84% | 37.09% | 0.07221% | 14.4673 | 0 | 0 | 14.4673 | 0 | 12.5585 | 0.54448 | 23.0654 | 12.5585 | 0.54448 | 23.0654 | 14.6811 | 0.6365 | 23.0654 | 3.111% | 0.098854 | 0.093961 | 4704.9245 | 482.7247 | 1590.8556 | 2631.3442 | 4795.9754 | 0 | 0 | 4795.9754 | 0.0004771%
2028 | 51 | CB 51 | Tier-1 | Non-HFTD---14 | 3--1 | 5.1357 | 233 | 100% | 6.4086 | 44.95% | 0% | 55.05% | 0.14259 | 0 | 0 | 0.14259 | 0 | 0.12378 | 4.828 | 0.025638 | 0.12378 | 4.828 | 0.025638 | 0.1447 | 5.644 | 0.025638 | 2.225% | 0.014079 | 0.013382 | 455.1864 | 0.18855 | 227.3695 | 227.6283 | 468.236 | 0 | 0 | 468.236 | 4.702e-06%
2028 | 946 | 946-25F | Tier-1 | Non-HFTD---20 | 1--1 | 0.62441 | 13 | 100% | 0.39407 | 18.79% | 0% | 81.21% | 0.0036656 | 0 | 0 | 0.0036656 | 0 | 0.003182 | 0.58701 | 0.0054207 | 0.003182 | 0.58701 | 0.0054207 | 0.0037198 | 0.68622 | 0.0054207 | 0.9302% | 0.0015836 | 0.0015052 | 248.8471 | 0.15206 | 65.1198 | 183.5753 | 259.3713 | 0 | 0 | 259.3713 | 1.209e-07%
2028 | NO1 | NO1-287F | Tier-1 | Non-HFTD---18 | 2--1 | 1.8949 | 50 | 100% | 1.6275 | 20.71% | 0% | 79.29% | 0.016687 | 0 | 0 | 0.016687 | 0 | 0.014486 | 1.7814 | 0.0081316 | 0.014486 | 1.7814 | 0.0081316 | 0.016934 | 2.0825 | 0.0081316 | 1.025% | 0.0051894 | 0.0049325 | 313.6146 | 0.1871 | 87.5499 | 225.8776 | 326.5639 | 0 | 0 | 326.5639 | 5.503e-07%
2028 | 205 | CB 205 | Tier-1 | Non-HFTD---7 | 3--3 | 5.2694 | 405 | 100% | 38.7792 | 89.82% | 0% | 10.18% | 1.7242 | 0 | 0 | 1.7242 | 0 | 1.4967 | 4.9537 | 0.30214 | 1.4967 | 4.9537 | 0.30214 | 1.7497 | 5.791 | 0.30214 | 4.446% | 0.016219 | 0.015416 | 2391.0005 | 150.1089 | 1253.224 | 987.6676 | 2403.6753 | 0 | 0 | 2403.6753 | 5.686e-05%
2028 | 296 | 296-66F | Tier-2 | Tier-2---21 | 1--3 | 0.14451 | 7 | 100% | 2.284 | 90.58% | 0% | 9.421% | 0.10241 | 0 | 0 | 0.10241 | 0 | 0.088895 | 0.13585 | 0.65436 | 0.088895 | 0.13585 | 0.65436 | 0.10392 | 0.15881 | 0.65436 | 4.484% | 0.0006178 | 0.00058722 | 3696.9667 | 843.8145 | 35.5403 | 2817.6118 | 3715.1054 | 0 | 0 | 3715.1054 | 3.377e-06%
2028 | 1458 | 1458-1061 | Tier-2 | Tier-2---5 | 5--5 | 2.3455 | 224 | 100% | 4370.0987 | 98.67% | 1.293% | 0.03403% | 213.4501 | 0 | 0 | 213.4501 | 0 | 185.2886 | 2.205 | 84.031 | 185.2886 | 2.205 | 84.031 | 216.6045 | 2.5777 | 84.031 | 4.884% | 0.14228 | 0.13523 | 30715.3399 | 7020.373 | 365.5776 | 23329.3893 | 30736.5608 | 0 | 0 | 30736.5608 | 0.007039%
2028 | EN2 | CB EN2 | Tier-1 | Non-HFTD---8 | 3--3 | 5.9322 | 649 | 100% | 45.2165 | 53.61% | 36.84% | 9.55% | 1.2 | 0 | 0 | 1.2 | 0 | 1.0417 | 5.5768 | 0.18679 | 1.0417 | 5.5768 | 0.18679 | 1.2177 | 6.5194 | 0.18679 | 2.654% | 0.022788 | 0.02166 | 1984.2222 | 155.0903 | 804.1172 | 1025.0147 | 2032.1547 | 0 | 0 | 2032.1547 | 3.957e-05%
2028 | 504 | 504-1563 | Tier-1 | Non-HFTD---1 | 3--5 | 9.2025 | 702 | 100% | 1424.1907 | 99.61% | 0% | 0.3928% | 70.2205 | 0 | 0 | 70.2205 | 0 | 60.956 | 8.6512 | 7.0459 | 60.956 | 8.6512 | 7.0459 | 71.2583 | 10.1134 | 7.0459 | 4.931% | 0.028304 | 0.026903 | 50317.6471 | 8145.1206 | 368.3302 | 41804.1963 | 50327.94 | 0 | 0 | 50327.94 | 0.002316%
2028 | 380 | CB 380 | Tier-1 | Non-HFTD---6 | 3--3 | 6.7373 | 225 | 100% | 65.1412 | 93.43% | 0% | 6.569% | 3.0127 | 0 | 0 | 3.0127 | 0 | 2.6152 | 6.3338 | 0.4129 | 2.6152 | 6.3338 | 0.4129 | 3.0572 | 7.4043 | 0.4129 | 4.625% | 0.019847 | 0.018864 | 3282.237 | 399.2549 | 1245.0692 | 1637.9129 | 3293.4656 | 0 | 0 | 3293.4656 | 9.935e-05%
2028 | 792 | 792-47R | Tier-1 | Non-HFTD---1 | 4--4 | 7.7364 | 716 | 100% | 393.985 | 1.678% | 96.94% | 1.378% | 0.32719 | 0 | 0 | 0.32719 | 0 | 0.28402 | 7.273 | 0.039052 | 0.28402 | 7.273 | 0.039052 | 0.33203 | 8.5022 | 0.039052 | 0.08305% | 0.039069 | 0.037135 | 10084.4423 | 11.8059 | 9078.6124 | 994.0241 | 10600.8076 | 0 | 0 | 10600.8076 | 1.079e-05%
2028 | 599 | 599-19R | Tier-2 | Tier-2---1 | 5--5 | 27.9316 | 2565 | 100% | 25743.4561 | 99.4% | 0.5253% | 0.0786% | 1266.6062 | 0 | 0 | 1266.6062 | 0 | 1099.4968 | 26.2586 | 41.8719 | 1099.4968 | 26.2586 | 41.8719 | 1285.3243 | 30.6966 | 41.8719 | 4.92% | 0.15161 | 0.14411 | 169796.7072 | 27439.4443 | 825.3004 | 141531.9625 | 169850.1033 | 0 | 0 | 169850.1033 | 0.04177%
2028 | 56 | 56-670F | Tier-1 | Non-HFTD---6 | 3--3 | 1.1852 | 40 | 100% | 49.2251 | 0.5924% | 97.4% | 2.005% | 0.014434 | 0 | 0 | 0.014434 | 0 | 0.01253 | 1.1142 | 0.011245 | 0.01253 | 1.1142 | 0.011245 | 0.014647 | 1.3025 | 0.011245 | 0.02932% | 0.014208 | 0.013505 | 3464.6013 | 3.8619 | 3012.3419 | 448.3975 | 3643.9615 | 0 | 0 | 3643.9615 | 4.76e-07%
2028 | 133 | CB 133 | Tier-1 | Non-HFTD---14 | 3--2 | 6.2032 | 134 | 100% | 8.7184 | 49.78% | 0% | 50.22% | 0.21483 | 0 | 0 | 0.21483 | 0 | 0.18648 | 5.8316 | 0.031978 | 0.18648 | 5.8316 | 0.031978 | 0.218 | 6.8173 | 0.031978 | 2.464% | 0.017124 | 0.016276 | 509.131 | 1.8919 | 270.3959 | 236.8432 | 522.4469 | 0 | 0 | 522.4469 | 7.084e-06%
2028 | 434 | 434-301 | Tier-2 | Tier-2---17 | 1--5 | 0.75759 | 163 | 100% | 70.6497 | 99.53% | 0% | 0.466% | 3.4809 | 0 | 0 | 3.4809 | 0 | 3.0216 | 0.71221 | 4.2426 | 3.0216 | 0.71221 | 4.2426 | 3.5323 | 0.83258 | 4.2426 | 4.927% | 0.003157 | 0.0030007 | 22378.7351 | 3567.4996 | 150.7709 | 18660.4646 | 22384.166 | 0 | 0 | 22384.166 | 0.0001148%
2028 | 176 | 176-1834R | Tier-3 | Tier-3---5 | 5--5 | 13.5415 | 913 | 100% | 10068.5168 | 97.13% | 2.784% | 0.0867% | 484.0866 | 0 | 0 | 484.0866 | 0 | 420.2187 | 12.7304 | 33.0092 | 420.2187 | 12.7304 | 33.0092 | 491.2405 | 14.8819 | 33.0092 | 4.808% | 0.23205 | 0.22056 | 43390.2136 | 8541.7295 | 1179.6329 | 33668.8511 | 43455.0714 | 0 | 0 | 43455.0714 | 0.01596%
2028 | 163 | CB 163 | Tier-1 | Non-HFTD---6 | 4--2 | 19.7841 | 299 | 100% | 56.8724 | 88.67% | 0% | 11.33% | 2.4962 | 0 | 0 | 2.4962 | 0 | 2.1669 | 18.5991 | 0.11651 | 2.1669 | 18.5991 | 0.11651 | 2.5331 | 21.7425 | 0.11651 | 4.389% | 0.038275 | 0.03638 | 1485.8961 | 18.0474 | 1223.2724 | 244.5763 | 1494.6629 | 0 | 0 | 1494.6629 | 8.232e-05%
2028 | 482 | 482-381F | Tier-1 | Non-HFTD---18 | 1--1 | 1.6901 | 145 | 100% | 1.247 | 13.37% | 0% | 86.63% | 0.0082507 | 0 | 0 | 0.0082507 | 0 | 0.0071622 | 1.5889 | 0.0045077 | 0.0071622 | 1.5889 | 0.0045077 | 0.0083727 | 1.8574 | 0.0045077 | 0.6617% | 0.0044034 | 0.0041854 | 283.1864 | 0.18461 | 60.1392 | 222.8626 | 295.9628 | 0 | 0 | 295.9628 | 2.721e-07%
2028 | 463 | CB 463 | Tier-2 | Tier-2---17 | 2--5 | 1.5028 | 87 | 100% | 99.9729 | 99.18% | 0% | 0.8185% | 4.9082 | 0 | 0 | 4.9082 | 0 | 4.2606 | 1.4128 | 3.0157 | 4.2606 | 1.4128 | 3.0157 | 4.9807 | 1.6516 | 3.0157 | 4.909% | 0.0053474 | 0.0050827 | 18695.6146 | 4709.0355 | 4354.0593 | 9632.5197 | 18703.5841 | 0 | 0 | 18703.5841 | 0.0001619%
2028 | 230 | 230-127AE | Tier-2 | Tier-2---7 | 5--5 | 10.5112 | 1091 | 100% | 2000.4654 | 94.98% | 4.641% | 0.3747% | 94.056 | 0 | 0 | 94.056 | 0 | 81.6467 | 9.8816 | 8.2625 | 81.6467 | 9.8816 | 8.2625 | 95.4459 | 11.5517 | 8.2625 | 4.702% | 0.093988 | 0.089336 | 21284.2191 | 3269.4209 | 921.4772 | 17093.321 | 21339.8191 | 0 | 0 | 21339.8191 | 0.003102%
2028 | 454 | 454-1814 | Tier-2 | Tier-2---20 | 4--2 | 0.095455 | 38 | 100% | 39.0262 | 97.23% | 2.586% | 0.1833% | 1.8783 | 0 | 0 | 1.8783 | 0 | 1.6305 | 0.089737 | 18.1696 | 1.6305 | 0.089737 | 18.1696 | 1.9061 | 0.1049 | 18.1696 | 4.813% | 0.072066 | 0.068499 | 541.534 | 85.8986 | 12.987 | 442.6484 | 542.315 | 0 | 0 | 542.315 | 6.194e-05%
2028 | 124 | CB 124 | Tier-1 | Non-HFTD---15 | 1--2 | 0.95 | 6 | 100% | 3.2925 | 66.24% | 0% | 33.76% | 0.10796 | 0 | 0 | 0.10796 | 0 | 0.093713 | 0.8931 | 0.10493 | 0.093713 | 0.8931 | 0.10493 | 0.10955 | 1.044 | 0.10493 | 3.279% | 0.0040986 | 0.0038957 | 803.3242 | 53.1781 | 266.286 | 483.8601 | 817.4481 | 0 | 0 | 817.4481 | 3.56e-06%
2028 | 701 | CB 701 | Tier-1 | Non-HFTD---2 | 4--3 | 17.7385 | 540 | 100% | 193.6018 | 45.82% | 47.23% | 6.946% | 4.3911 | 0 | 0 | 4.3911 | 0 | 3.8118 | 16.676 | 0.22858 | 3.8118 | 16.676 | 0.22858 | 4.456 | 19.4944 | 0.22858 | 2.268% | 0.065404 | 0.062166 | 2960.1098 | 147.5713 | 1958.5218 | 854.0167 | 3043.6312 | 0 | 0 | 3043.6312 | 0.0001448%
2028 | 213 | 213-262F | Tier-1 | Non-HFTD---19 | 1--2 | 0.083756 | 5 | 100% | 0.16168 | 79.23% | 0% | 20.77% | 0.0063411 | 0 | 0 | 0.0063411 | 0 | 0.0055044 | 0.078739 | 0.069907 | 0.0055044 | 0.078739 | 0.069907 | 0.0064348 | 0.092047 | 0.069907 | 3.922% | 0.0001976 | 0.00018782 | 818.194 | 104.1852 | 22.3943 | 691.6145 | 827.0423 | 0 | 0 | 827.0423 | 2.091e-07%
2028 | 1139 | 1139-4F | Tier-2 | Tier-2---11 | 5--3 | 4.1474 | 89 | 100% | 472.1771 | 0.2595% | 99.27% | 0.4712% | 0.060646 | 0 | 0 | 0.060646 | 0 | 0.052645 | 3.899 | 0.013502 | 0.052645 | 3.899 | 0.013502 | 0.061542 | 4.5579 | 0.013502 | 0.01284% | 0.11231 | 0.10675 | 4204.4022 | 7.5405 | 3803.8802 | 392.9815 | 4422.7903 | 0 | 0 | 4422.7903 | 2e-06%
2028 | 237 | CB 237 | Tier-2 | Tier-2---8 | 5--5 | 0.84619 | 36 | 100% | 2111.5746 | 99.54% | 0.4259% | 0.03207% | 104.0443 | 0 | 0 | 104.0443 | 0 | 90.3172 | 0.7955 | 113.5349 | 90.3172 | 0.7955 | 113.5349 | 105.5818 | 0.92995 | 113.5349 | 4.927% | 0.10923 | 0.10382 | 19331.9134 | 3573.3415 | 106.8159 | 15651.756 | 19336.5241 | 0 | 0 | 19336.5241 | 0.003431%
2028 | 451 | 451-38F | Tier-1 | Non-HFTD---17 | 1--1 | 1.3801 | 116 | 100% | 1.6743 | 45.15% | 0% | 54.85% | 0.037424 | 0 | 0 | 0.037424 | 0 | 0.032486 | 1.2975 | 0.025038 | 0.032486 | 1.2975 | 0.025038 | 0.037977 | 1.5168 | 0.025038 | 2.235% | 0.004114 | 0.0039104 | 406.98 | 0.16796 | 204.0476 | 202.7644 | 418.6042 | 0 | 0 | 418.6042 | 1.234e-06%
2028 | 230 | 230-1008R | Tier-2 | Tier-2---16 | 4--3 | 0.76383 | 10 | 100% | 171.5883 | 99.37% | 0.4538% | 0.1789% | 8.4399 | 0 | 0 | 8.4399 | 0 | 7.3264 | 0.71807 | 10.2028 | 7.3264 | 0.71807 | 10.2028 | 8.5646 | 0.83944 | 10.2028 | 4.919% | 0.055697 | 0.05294 | 3080.7564 | 492.3345 | 31.2554 | 2557.1665 | 3081.7716 | 0 | 0 | 3081.7716 | 0.0002783%
2028 | 480 | 480-35 | Tier-1 | Non-HFTD---10 | 4--1 | 16.4336 | 1010 | 100% | 19.5827 | 39.21% | 0% | 60.79% | 0.38007 | 0 | 0 | 0.38007 | 0 | 0.32992 | 15.4492 | 0.021355 | 0.32992 | 15.4492 | 0.021355 | 0.38569 | 18.0603 | 0.021355 | 1.941% | 0.047129 | 0.044796 | 415.5112 | 23.8764 | 99.4507 | 292.1841 | 428.6657 | 0 | 0 | 428.6657 | 1.253e-05%
2028 | 719 | 719-33 | Tier-1 | Non-HFTD---16 | 2--1 | 4.6088 | 110 | 100% | 4.0499 | 25.39% | 0% | 74.61% | 0.050892 | 0 | 0 | 0.050892 | 0 | 0.044178 | 4.3327 | 0.010196 | 0.044178 | 4.3327 | 0.010196 | 0.051644 | 5.065 | 0.010196 | 1.257% | 0.012955 | 0.012314 | 312.6002 | 0.17551 | 100.5469 | 211.8778 | 324.7469 | 0 | 0 | 324.7469 | 1.678e-06%
2028 | 83 | 83-622F | Tier-1 | Non-HFTD---18 | 2--1 | 3.0943 | 66 | 100% | 1.5636 | 25.94% | 0% | 74.06% | 0.020078 | 0 | 0 | 0.020078 | 0 | 0.017429 | 2.909 | 0.0059914 | 0.017429 | 2.909 | 0.0059914 | 0.020375 | 3.4006 | 0.0059914 | 1.284% | 0.00696 | 0.0066155 | 224.6568 | 1.1983 | 66.8397 | 156.6188 | 233.3214 | 0 | 0 | 233.3214 | 6.621e-07%
2028 | 240 | 240-2004R | Tier-3 | Tier-3---12 | 5--5 | 19.7983 | 1084 | 100% | 4437.6588 | 97.91% | 1.769% | 0.321% | 215.0731 | 0 | 0 | 215.0731 | 0 | 186.6975 | 18.6124 | 10.0308 | 186.6975 | 18.6124 | 10.0308 | 218.2515 | 21.7581 | 10.0308 | 4.847% | 0.095775 | 0.091035 | 46334.0144 | 8309.1897 | 777.0534 | 37247.7713 | 46384.4455 | 0 | 0 | 46384.4455 | 0.007092%
2028 | 1079 | CB 1079 | Tier-1 | Non-HFTD---9 | 2--3 | 2.5269 | 152 | 100% | 15.9736 | 90.06% | 0% | 9.938% | 0.71212 | 0 | 0 | 0.71212 | 0 | 0.61816 | 2.3755 | 0.26023 | 0.61816 | 2.3755 | 0.26023 | 0.72264 | 2.777 | 0.26023 | 4.458% | 0.0072148 | 0.0068577 | 2214.0112 | 265.8554 | 1002.265 | 945.8908 | 2225.4696 | 0 | 0 | 2225.4696 | 2.348e-05%
2028 | 207 | CB 207 | Tier-1 | Non-HFTD---7 | 2--3 | 2.9445 | 104 | 100% | 36.13 | 94.58% | 0% | 5.421% | 1.6915 | 0 | 0 | 1.6915 | 0 | 1.4683 | 2.7682 | 0.53043 | 1.4683 | 2.7682 | 0.53043 | 1.7165 | 3.236 | 0.53043 | 4.682% | 0.0090126 | 0.0085665 | 4008.8284 | 146.4393 | 2915.0578 | 947.3313 | 4020.1468 | 0 | 0 | 4020.1468 | 5.578e-05%
2028 | 1418 | 1418-31R | Tier-1 | Non-HFTD---15 | 1--2 | 0.66439 | 18 | 100% | 2.7275 | 78.81% | 0% | 21.19% | 0.1064 | 0 | 0 | 0.1064 | 0 | 0.092359 | 0.6246 | 0.14787 | 0.092359 | 0.6246 | 0.14787 | 0.10797 | 0.73016 | 0.14787 | 3.901% | 0.0024528 | 0.0023314 | 1112.0026 | 74.6408 | 441.9379 | 595.4239 | 1124.2767 | 0 | 0 | 1124.2767 | 3.509e-06%
2028 | 300 | 300-483F | Tier-2 | Tier-2---12 | 3--5 | 5.4324 | 19 | 100% | 458.7821 | 99.48% | 0% | 0.5194% | 22.5918 | 0 | 0 | 22.5918 | 0 | 19.6111 | 5.107 | 3.8401 | 19.6111 | 5.107 | 3.8401 | 22.9256 | 5.9701 | 3.8401 | 4.924% | 0.018397 | 0.017486 | 24937.8732 | 4596.9105 | 11.7655 | 20329.1971 | 24944.6182 | 0 | 0 | 24944.6182 | 0.000745%
2028 | 431 | 431-46AE | Tier-1 | Non-HFTD---14 | 2--1 | 4.3178 | 34 | 100% | 5.4602 | 36.55% | 0% | 63.45% | 0.098795 | 0 | 0 | 0.098795 | 0 | 0.085761 | 4.0592 | 0.021128 | 0.085761 | 4.0592 | 0.021128 | 0.10026 | 4.7452 | 0.021128 | 1.809% | 0.012491 | 0.011873 | 437.1166 | 0.2108 | 184.9596 | 251.9462 | 451.5597 | 0 | 0 | 451.5597 | 3.258e-06%
2028 | 350 | 350-41R | Tier-2 | Tier-2---3 | 5--5 | 16.422 | 1638 | 100% | 11201.3889 | 98.88% | 1.023% | 0.1021% | 548.2325 | 0 | 0 | 548.2325 | 0 | 475.9015 | 15.4383 | 30.826 | 475.9015 | 15.4383 | 30.826 | 556.3343 | 18.0476 | 30.826 | 4.894% | 0.12896 | 0.12258 | 86857.3846 | 16955.532 | 989.3213 | 68912.5314 | 86908.2599 | 0 | 0 | 86908.2599 | 0.01808%
2028 | BO1 | CB BO1 | Tier-1 | Non-HFTD---18 | 2--1 | 1.7728 | 43 | 100% | 1.9101 | 28.77% | 0% | 71.23% | 0.027199 | 0 | 0 | 0.027199 | 0 | 0.02361 | 1.6666 | 0.014167 | 0.02361 | 1.6666 | 0.014167 | 0.0276 | 1.9482 | 0.014167 | 1.424% | 0.0052326 | 0.0049736 | 365.037 | 0.49286 | 127.5995 | 236.9446 | 378.5787 | 0 | 0 | 378.5787 | 8.969e-07%
2028 | 545 | CB 545 | Tier-1 | Non-HFTD---5 | 3--3 | 1.9879 | 35 | 100% | 70.9796 | 19.97% | 77.85% | 2.177% | 0.7018 | 0 | 0 | 0.7018 | 0 | 0.60921 | 1.8688 | 0.32599 | 0.60921 | 1.8688 | 0.32599 | 0.71217 | 2.1846 | 0.32599 | 0.9887% | 0.015929 | 0.01514 | 4456.0552 | 3.8159 | 4082.19 | 370.0493 | 4641.7637 | 0 | 0 | 4641.7637 | 2.314e-05%
2028 | 150 | 150-434AE | Tier-1 | Non-HFTD---9 | 1--4 | 1.1161 | 6 | 100% | 24.5324 | 96.53% | 0% | 3.474% | 1.1722 | 0 | 0 | 1.1722 | 0 | 1.0175 | 1.0492 | 0.96976 | 1.0175 | 1.0492 | 0.96976 | 1.1895 | 1.2266 | 0.96976 | 4.778% | 0.0042426 | 0.0040326 | 5782.3912 | 1118.2339 | 22.284 | 4641.8732 | 5792.8535 | 0 | 0 | 5792.8535 | 3.865e-05%
2028 | 144 | 144-442F | Tier-1 | Non-HFTD---5 | 3--4 | 3.5848 | 126 | 100% | 88.4511 | 1.673% | 95.65% | 2.673% | 0.073245 | 0 | 0 | 0.073245 | 0 | 0.063582 | 3.3701 | 0.018866 | 0.063582 | 3.3701 | 0.018866 | 0.074328 | 3.9397 | 0.018866 | 0.08281% | 0.015509 | 0.014741 | 5703.2117 | 6.9384 | 5087.8182 | 608.4551 | 5995.254 | 0 | 0 | 5995.254 | 2.415e-06%
2028 | 990 | 990-713 | Tier-2 | Tier-2---17 | 3--3 | 0.065909 | 13 | 100% | 85.9224 | 0.4524% | 99.5% | 0.04623% | 0.01924 | 0 | 0 | 0.01924 | 0 | 0.016701 | 0.061961 | 0.26955 | 0.016701 | 0.061961 | 0.26955 | 0.019524 | 0.072433 | 0.26955 | 0.02239% | 0.017823 | 0.01694 | 4820.9793 | 10.6403 | 4200.4141 | 609.9249 | 5070.9099 | 0 | 0 | 5070.9099 | 6.345e-07%
2028 | 160 | CB 160 | Tier-1 | Non-HFTD---7 | 2--3 | 3.6716 | 129 | 100% | 31.5499 | 92.29% | 0% | 7.71% | 1.4413 | 0 | 0 | 1.4413 | 0 | 1.2512 | 3.4517 | 0.36248 | 1.2512 | 3.4517 | 0.36248 | 1.4626 | 4.035 | 0.36248 | 4.568% | 0.01025 | 0.0097426 | 3078.0386 | 0.58515 | 2859.7845 | 217.6689 | 3090.397 | 0 | 0 | 3090.397 | 4.753e-05%
2028 | 390 | 390-18 | Tier-1 | Non-HFTD---2 | 5--3 | 3.9404 | 129 | 100% | 318.8449 | 16.58% | 82.54% | 0.8771% | 2.617 | 0 | 0 | 2.617 | 0 | 2.2717 | 3.7043 | 0.61325 | 2.2717 | 3.7043 | 0.61325 | 2.6556 | 4.3304 | 0.61325 | 0.8208% | 0.10878 | 0.1034 | 2931.0773 | 106.6158 | 2119.5636 | 704.8979 | 3058.4114 | 0 | 0 | 3058.4114 | 8.63e-05%
2028 | GA1 | CB GA1 | Tier-1 | Non-HFTD---14 | 3--1 | 7.5047 | 189 | 100% | 7.2576 | 27.71% | 0% | 72.29% | 0.099541 | 0 | 0 | 0.099541 | 0 | 0.086408 | 7.0552 | 0.012247 | 0.086408 | 7.0552 | 0.012247 | 0.10101 | 8.2476 | 0.012247 | 1.372% | 0.021919 | 0.020834 | 331.1033 | 2.6119 | 98.6514 | 229.84 | 343.5687 | 0 | 0 | 343.5687 | 3.282e-06%
2028 | 1243 | CB 1243 | Tier-2 | Tier-2---7 | 3--5 | 5.0473 | 319 | 100% | 1438.3629 | 99.75% | 0% | 0.2509% | 71.0203 | 0 | 0 | 71.0203 | 0 | 61.6503 | 4.745 | 12.9927 | 61.6503 | 4.745 | 12.9927 | 72.0699 | 5.5469 | 12.9927 | 4.938% | 0.019586 | 0.018616 | 73438.3162 | 12301.3098 | 66.4142 | 61070.5923 | 73447.9127 | 0 | 0 | 73447.9127 | 0.002342%
2028 | 473 | 473-36R | Tier-1 | Non-HFTD---1 | 5--4 | 14.9443 | 562 | 100% | 1339.2067 | 0.8137% | 98.49% | 0.6935% | 0.53941 | 0 | 0 | 0.53941 | 0 | 0.46825 | 14.0491 | 0.033329 | 0.46825 | 14.0491 | 0.033329 | 0.54739 | 16.4236 | 0.033329 | 0.04028% | 0.11477 | 0.10909 | 11668.3486 | 17.7885 | 10476.9993 | 1173.5608 | 12271.0665 | 0 | 0 | 12271.0665 | 1.779e-05%
2028 | HC4 | CB HC4 | Tier-1 | Non-HFTD---8 | 3--2 | 6.4726 | 321 | 100% | 33.1006 | 83.29% | 0% | 16.71% | 1.3646 | 0 | 0 | 1.3646 | 0 | 1.1846 | 6.0849 | 0.19468 | 1.1846 | 6.0849 | 0.19468 | 1.3848 | 7.1133 | 0.19468 | 4.123% | 0.021599 | 0.02053 | 1532.5221 | 272.5227 | 181.5019 | 1078.4974 | 1545.8612 | 0 | 0 | 1545.8612 | 4.5e-05%
2028 | 555 | 555-2F | Tier-1 | Non-HFTD---17 | 1--2 | 0.42273 | 2 | 100% | 0.84765 | 38.63% | 0% | 61.37% | 0.016208 | 0 | 0 | 0.016208 | 0 | 0.014069 | 0.39741 | 0.035403 | 0.014069 | 0.39741 | 0.035403 | 0.016447 | 0.46458 | 0.035403 | 1.912% | 0.0015912 | 0.0015124 | 532.7136 | 32.3462 | 37.5358 | 462.8316 | 549.7399 | 0 | 0 | 549.7399 | 5.345e-07%
2028 | 281 | CB 281 | Tier-2 | Tier-2---16 | 4--3 | 6.8986 | 157 | 100% | 131.3229 | 1.145% | 96.36% | 2.498% | 0.07445 | 0 | 0 | 0.07445 | 0 | 0.064627 | 6.4854 | 0.009965 | 0.064627 | 6.4854 | 0.009965 | 0.07555 | 7.5815 | 0.009965 | 0.05669% | 0.046838 | 0.04452 | 2803.7555 | 3.8846 | 2517.4341 | 282.4368 | 2948.0968 | 0 | 0 | 2948.0968 | 2.455e-06%
2028 | 305 | 305-32R | Tier-1 | Non-HFTD---1 | 4--5 | 7.0648 | 1685 | 100% | 4233.8665 | 96.93% | 2.943% | 0.1312% | 203.133 | 0 | 0 | 203.133 | 0 | 176.3327 | 6.6416 | 26.5497 | 176.3327 | 6.6416 | 26.5497 | 206.1349 | 7.7641 | 26.5497 | 4.798% | 0.080233 | 0.076262 | 52769.5087 | 8342.6927 | 1399.583 | 43027.233 | 52853.9991 | 0 | 0 | 52853.9991 | 0.006699%
2028 | MK1 | CB MK1 | Tier-1 | Non-HFTD---14 | 3--1 | 6.0093 | 122 | 100% | 7.4473 | 44.14% | 0% | 55.86% | 0.16271 | 0 | 0 | 0.16271 | 0 | 0.14125 | 5.6493 | 0.025002 | 0.14125 | 5.6493 | 0.025002 | 0.16512 | 6.6041 | 0.025002 | 2.185% | 0.016865 | 0.01603 | 441.5759 | 36.2896 | 78.2242 | 327.062 | 454.4219 | 0 | 0 | 454.4219 | 5.366e-06%
2028 | 532 | 532-1293F | Tier-1 | Non-HFTD---17 | 1--2 | 0.79053 | 19 | 100% | 1.3366 | 55.6% | 0% | 44.4% | 0.036789 | 0 | 0 | 0.036789 | 0 | 0.031935 | 0.74318 | 0.042971 | 0.031935 | 0.74318 | 0.042971 | 0.037333 | 0.86879 | 0.042971 | 2.752% | 0.0023122 | 0.0021977 | 578.0789 | 32.7375 | 145.1444 | 400.197 | 591.4446 | 0 | 0 | 591.4446 | 1.213e-06%
2028 | 357 | 357-2049F | Tier-3 | Tier-3---8 | 5--5 | 7.806 | 514 | 100% | 16869.708 | 98.79% | 1.184% | 0.02933% | 824.9167 | 0 | 0 | 824.9167 | 0 | 716.0815 | 7.3385 | 97.5793 | 716.0815 | 7.3385 | 97.5793 | 837.1074 | 8.5787 | 97.5793 | 4.89% | 0.18286 | 0.17381 | 92253.2607 | 17311.1307 | 1006.4282 | 73935.7018 | 92311.5642 | 0 | 0 | 92311.5642 | 0.0272%
2028 | 177 | 177-955 | Tier-2 | Tier-2---5 | 5--5 | 4.7979 | 602 | 100% | 2963.4059 | 78.23% | 21.66% | 0.1106% | 114.7532 | 0 | 0 | 114.7532 | 0 | 99.6133 | 4.5105 | 22.0848 | 99.6133 | 4.5105 | 22.0848 | 116.449 | 5.2728 | 22.0848 | 3.872% | 0.11726 | 0.11145 | 25272.526 | 4724.2579 | 4965.7102 | 15582.5579 | 25559.0608 | 0 | 0 | 25559.0608 | 0.003784%
2028 | VO1 | CB VO1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.214 | 26 | 100% | 1.1072 | 22.13% | 0% | 77.87% | 0.012131 | 0 | 0 | 0.012131 | 0 | 0.01053 | 1.1413 | 0.0092265 | 0.01053 | 1.1413 | 0.0092265 | 0.01231 | 1.3342 | 0.0092265 | 1.096% | 0.003819 | 0.00363 | 289.9083 | 0.16986 | 84.6753 | 205.0631 | 301.6643 | 0 | 0 | 301.6643 | 4e-07%
2028 | WA4 | CB WA4 | Tier-1 | Non-HFTD---10 | 3--2 | 7.4043 | 239 | 100% | 23.9832 | 78.04% | 0% | 21.96% | 0.92645 | 0 | 0 | 0.92645 | 0 | 0.80422 | 6.9608 | 0.11554 | 0.80422 | 6.9608 | 0.11554 | 0.94015 | 8.1373 | 0.11554 | 3.863% | 0.022554 | 0.021438 | 1063.3699 | 52.777 | 527.6231 | 482.9698 | 1075.5315 | 0 | 0 | 1075.5315 | 3.055e-05%
2028 | 299 | 299-1011 | Tier-1 | Non-HFTD---5 | 2--3 | 4.203 | 102 | 100% | 54.9991 | 94.1% | 0% | 5.9% | 2.5618 | 0 | 0 | 2.5618 | 0 | 2.2238 | 3.9512 | 0.56282 | 2.2238 | 3.9512 | 0.56282 | 2.5997 | 4.6191 | 0.56282 | 4.658% | 0.013194 | 0.012541 | 4168.5545 | 546.6465 | 589.0831 | 3032.8249 | 4181.3634 | 0 | 0 | 4181.3634 | 8.448e-05%
2028 | 463 | 463-1136F | Tier-2 | Tier-2---18 | 4--2 | 0.58561 | 1 | 100% | 88.0149 | 97.35% | 2.233% | 0.4157% | 4.2413 | 0 | 0 | 4.2413 | 0 | 3.6818 | 0.55053 | 6.6877 | 3.6818 | 0.55053 | 6.6877 | 4.304 | 0.64357 | 6.6877 | 4.819% | 0.060434 | 0.057442 | 1456.3858 | 230.2642 | 26.4999 | 1199.6216 | 1458.3947 | 0 | 0 | 1458.3947 | 0.0001399%
2028 | 441 | 441-30R | Tier-3 | Tier-3---9 | 5--4 | 5.7333 | 62 | 100% | 5348.8774 | 98.57% | 1.364% | 0.06326% | 260.9896 | 0 | 0 | 260.9896 | 0 | 226.556 | 5.3899 | 42.0335 | 226.556 | 5.3899 | 42.0335 | 264.8465 | 6.3008 | 42.0335 | 4.879% | 0.55519 | 0.52771 | 9634.2631 | 1376.8977 | 118.4218 | 8138.9436 | 9641.4258 | 0 | 0 | 9641.4258 | 0.008606%
2028 | 700 | 700-255 | Tier-1 | Non-HFTD---9 | 2--2 | 1.2451 | 22 | 100% | 16.4031 | 90.17% | 3.905% | 5.929% | 0.7321 | 0 | 0 | 0.7321 | 0 | 0.63551 | 1.1705 | 0.54293 | 0.63551 | 1.1705 | 0.54293 | 0.74292 | 1.3683 | 0.54293 | 4.463% | 0.010214 | 0.009708 | 1606.0068 | 234.45 | 79.4931 | 1292.0638 | 1614.2322 | 0 | 0 | 1614.2322 | 2.414e-05%
2028 | 321 | 321-646 | Tier-1 | Non-HFTD---18 | 2--1 | 1.9246 | 24 | 100% | 2.1274 | 32.02% | 0% | 67.98% | 0.033717 | 0 | 0 | 0.033717 | 0 | 0.029269 | 1.8093 | 0.016177 | 0.029269 | 1.8093 | 0.016177 | 0.034215 | 2.1151 | 0.016177 | 1.585% | 0.0057906 | 0.005504 | 367.3897 | 7.7909 | 93.4102 | 266.1885 | 380.3966 | 0 | 0 | 380.3966 | 1.112e-06%
2028 | 740 | CB 740 | Tier-1 | Non-HFTD---10 | 4--2 | 12.6747 | 722 | 100% | 25.6721 | 66.02% | 0% | 33.98% | 0.839 | 0 | 0 | 0.839 | 0 | 0.7283 | 11.9155 | 0.061123 | 0.7283 | 11.9155 | 0.061123 | 0.8514 | 13.9293 | 0.061123 | 3.268% | 0.034483 | 0.032776 | 744.476 | 0.22301 | 514.3039 | 229.9491 | 757.6491 | 0 | 0 | 757.6491 | 2.767e-05%
2028 | 308 | 308-486AE | Tier-2 | Tier-2---16 | 4--3 | 3.6318 | 154 | 100% | 164.6778 | 2.383% | 96.2% | 1.419% | 0.19428 | 0 | 0 | 0.19428 | 0 | 0.16865 | 3.4142 | 0.049396 | 0.16865 | 3.4142 | 0.049396 | 0.19715 | 3.9913 | 0.049396 | 0.118% | 0.040279 | 0.038285 | 4088.4689 | 19.0997 | 3634.8848 | 434.4844 | 4296.3129 | 0 | 0 | 4296.3129 | 6.407e-06%
2028 | SW4 | CB SW4 | Tier-1 | Non-HFTD---16 | 2--1 | 3.3697 | 89 | 100% | 2.7806 | 34.41% | 0% | 65.59% | 0.047357 | 0 | 0 | 0.047357 | 0 | 0.041109 | 3.1679 | 0.012977 | 0.041109 | 3.1679 | 0.012977 | 0.048056 | 3.7033 | 0.012977 | 1.703% | 0.0083328 | 0.0079203 | 333.6959 | 7.2394 | 91.3226 | 235.1339 | 345.095 | 0 | 0 | 345.095 | 1.562e-06%
2028 | 1090 | 1090-1734 | Tier-3 | Tier-3---16 | 2--5 | 2.1343 | 23 | 100% | 730.5479 | 99.24% | 0.5863% | 0.172% | 35.8879 | 0 | 0 | 35.8879 | 0 | 31.153 | 2.0064 | 15.5267 | 31.153 | 2.0064 | 15.5267 | 36.4183 | 2.3455 | 15.5267 | 4.912% | 0.01345 | 0.012784 | 54317.4438 | 9020.2507 | 362.2329 | 44934.9602 | 54338.8933 | 0 | 0 | 54338.8933 | 0.001183%
2028 | 166 | 166-463F | Tier-1 | Non-HFTD---19 | 1--1 | 0.081818 | 8 | 100% | 0.15952 | 10.72% | 0% | 89.28% | 0.0008462 | 0 | 0 | 0.0008462 | 0 | 0.00073456 | 0.076917 | 0.0095499 | 0.00073456 | 0.076917 | 0.0095499 | 0.0008587 | 0.089917 | 0.0095499 | 0.5305% | 0.0003874 | 0.00036822 | 411.7579 | 0.27663 | 77.5231 | 333.9581 | 430.9033 | 0 | 0 | 430.9033 | 2.79e-08%
2028 | BK1 | CB BK1 | Tier-1 | Non-HFTD---8 | 3--3 | 3.8556 | 133 | 100% | 44.2018 | 7.123% | 86.74% | 6.139% | 0.15584 | 0 | 0 | 0.15584 | 0 | 0.13528 | 3.6247 | 0.037322 | 0.13528 | 3.6247 | 0.037322 | 0.15814 | 4.2373 | 0.037322 | 0.3526% | 0.021968 | 0.02088 | 2012.1178 | 13.6327 | 1683.8934 | 314.5917 | 2109.4411 | 0 | 0 | 2109.4411 | 5.139e-06%
2028 | 908 | 908-30 | Tier-2 | Tier-2---10 | 5--4 | 1.5403 | 228 | 100% | 847.524 | 96.52% | 3.329% | 0.1488% | 40.4933 | 0 | 0 | 40.4933 | 0 | 35.1509 | 1.4481 | 24.2745 | 35.1509 | 1.4481 | 24.2745 | 41.0917 | 1.6928 | 24.2745 | 4.778% | 0.16572 | 0.15752 | 5114.069 | 791.8811 | 161.7983 | 4160.3897 | 5123.3319 | 0 | 0 | 5123.3319 | 0.001335%
2028 | 501 | 501-786 | Tier-2 | Tier-2---14 | 2--5 | 1.0739 | 170 | 100% | 204.0835 | 99.63% | 0% | 0.368% | 10.065 | 0 | 0 | 10.065 | 0 | 8.737 | 1.0096 | 8.6543 | 8.737 | 1.0096 | 8.6543 | 10.2137 | 1.1802 | 8.6543 | 4.932% | 0.0050324 | 0.0047833 | 40553.9202 | 6567.6362 | 21.2746 | 33965.0094 | 40561.693 | 0 | 0 | 40561.693 | 0.0003319%
2028 | 381 | 381-451F | Tier-1 | Non-HFTD---10 | 3--2 | 6.7813 | 160 | 100% | 23.3181 | 88.11% | 0% | 11.89% | 1.017 | 0 | 0 | 1.017 | 0 | 0.88285 | 6.3751 | 0.13848 | 0.88285 | 6.3751 | 0.13848 | 1.0321 | 7.4526 | 0.13848 | 4.362% | 0.018659 | 0.017735 | 1249.6956 | 131.9022 | 309.5549 | 808.2386 | 1257.4325 | 0 | 0 | 1257.4325 | 3.354e-05%
2028 | WA3 | CB WA3 | Tier-1 | Non-HFTD---8 | 4--2 | 13.982 | 461 | 100% | 27.563 | 70.26% | 0% | 29.74% | 0.95857 | 0 | 0 | 0.95857 | 0 | 0.8321 | 13.1445 | 0.063304 | 0.8321 | 13.1445 | 0.063304 | 0.97274 | 15.3661 | 0.063304 | 3.478% | 0.039294 | 0.037349 | 701.463 | 20.3909 | 425.071 | 256.0011 | 712.3281 | 0 | 0 | 712.3281 | 3.161e-05%
2028 | 821 | CB 821 | Tier-1 | Non-HFTD---8 | 4--2 | 11.9876 | 611 | 100% | 39.8764 | 81.44% | 0% | 18.56% | 1.6076 | 0 | 0 | 1.6076 | 0 | 1.3955 | 11.2696 | 0.12383 | 1.3955 | 11.2696 | 0.12383 | 1.6314 | 13.1743 | 0.12383 | 4.032% | 0.03208 | 0.030492 | 1243.0135 | 29.5845 | 853.3576 | 360.0714 | 1255.025 | 0 | 0 | 1255.025 | 5.301e-05%
2028 | 454 | 454-49F | Tier-2 | Tier-2---13 | 4--3 | 1.5199 | 92 | 100% | 292.9743 | 76.06% | 23.59% | 0.3558% | 11.0299 | 0 | 0 | 11.0299 | 0 | 9.5746 | 1.4288 | 6.7011 | 9.5746 | 1.4288 | 6.7011 | 11.1929 | 1.6703 | 6.7011 | 3.765% | 0.077203 | 0.073382 | 3794.8464 | 847.9473 | 816.929 | 2129.9701 | 3842.1656 | 0 | 0 | 3842.1656 | 0.0003637%
2028 | 196 | 196-43F | Tier-2 | Tier-2---17 | 3--4 | 0.2589 | 52 | 100% | 93.7651 | 5.14% | 94.59% | 0.2662% | 0.23855 | 0 | 0 | 0.23855 | 0 | 0.20708 | 0.24339 | 0.8508 | 0.20708 | 0.24339 | 0.8508 | 0.24208 | 0.28453 | 0.8508 | 0.2544% | 0.017356 | 0.016497 | 5402.3367 | 48.5246 | 4687.8466 | 665.9656 | 5669.2187 | 0 | 0 | 5669.2187 | 7.867e-06%
2028 | 1215 | 1215-12R | Tier-3 | Tier-3---9 | 5--4 | 8.3178 | 81 | 100% | 6147.2839 | 97.88% | 2.045% | 0.07292% | 297.8447 | 0 | 0 | 297.8447 | 0 | 258.5486 | 7.8195 | 33.0644 | 258.5486 | 7.8195 | 33.0644 | 302.2462 | 9.1411 | 33.0644 | 4.845% | 0.69907 | 0.66447 | 8793.5219 | 1246.9976 | 166.0142 | 7380.5102 | 8803.2228 | 0 | 0 | 8803.2228 | 0.009822%
2028 | 243 | CB 243 | Tier-2 | Tier-2---14 | 4--4 | 3.2755 | 98 | 100% | 284.2808 | 92.1% | 7.127% | 0.7733% | 12.9602 | 0 | 0 | 12.9602 | 0 | 11.2503 | 3.0793 | 3.6535 | 11.2503 | 3.0793 | 3.6535 | 13.1517 | 3.5998 | 3.6535 | 4.559% | 0.039288 | 0.037343 | 7235.7813 | 1297.464 | 840.9216 | 5097.3957 | 7265.5523 | 0 | 0 | 7265.5523 | 0.0004274%
2028 | 789 | 789-4R | Tier-2 | Tier-2---3 | 4--5 | 12.3028 | 1609 | 100% | 10274.0059 | 99.92% | 0% | 0.08426% | 508.1348 | 0 | 0 | 508.1348 | 0 | 441.0941 | 11.5659 | 38.1375 | 441.0941 | 11.5659 | 38.1375 | 515.644 | 13.5207 | 38.1375 | 4.946% | 0.050279 | 0.047791 | 204338.276 | 36517.9453 | 193.5463 | 167626.7844 | 204347.2427 | 0 | 0 | 204347.2427 | 0.01676%
2028 | 558 | 558-301R | Tier-1 | Non-HFTD---1 | 2--5 | 2.4663 | 84 | 100% | 286.6551 | 99.35% | 0% | 0.6493% | 14.0973 | 0 | 0 | 14.0973 | 0 | 12.2374 | 2.3186 | 5.2779 | 12.2374 | 2.3186 | 5.2779 | 14.3056 | 2.7105 | 5.2779 | 4.918% | 0.010369 | 0.0098561 | 27644.3313 | 6740.2704 | 35.1226 | 20868.9383 | 27653.6787 | 0 | 0 | 27653.6787 | 0.0004649%
2028 | 214 | 214-1122R | Tier-3 | Tier-3---3 | 5--5 | 19.9074 | 1772 | 100% | 26281.1502 | 98.91% | 1.048% | 0.04591% | 1286.6839 | 0 | 0 | 1286.6839 | 0 | 1116.9255 | 18.7149 | 59.681 | 1116.9255 | 18.7149 | 59.681 | 1305.6986 | 21.878 | 59.681 | 4.896% | 0.26918 | 0.25585 | 97635.635 | 15575.0756 | 943.7834 | 81116.776 | 97691.265 | 0 | 0 | 97691.265 | 0.04243%
2028 | 242 | CB 242 | Tier-2 | Tier-2---11 | 5--3 | 3.397 | 63 | 100% | 406.8184 | 64.36% | 35.02% | 0.6193% | 12.9611 | 0 | 0 | 12.9611 | 0 | 11.2511 | 3.1935 | 3.5231 | 11.2511 | 3.1935 | 3.5231 | 13.1527 | 3.7333 | 3.5231 | 3.186% | 0.1014 | 0.096385 | 4011.826 | 391.3486 | 1462.3995 | 2158.0779 | 4086.281 | 0 | 0 | 4086.281 | 0.0004274%
2028 | 1006 | 1006-829F | Tier-2 | Tier-2---15 | 1--5 | 0.47178 | 3 | 100% | 114.5301 | 99.76% | 0% | 0.2395% | 5.6557 | 0 | 0 | 5.6557 | 0 | 4.9095 | 0.44352 | 11.0693 | 4.9095 | 0.44352 | 11.0693 | 5.7392 | 0.51848 | 11.0693 | 4.938% | 0.0022112 | 0.0021017 | 51795.4298 | 10544.9933 | 12.8959 | 41237.5406 | 51801.8888 | 0 | 0 | 51801.8888 | 0.0001865%
2028 | 975 | 975-22R | Tier-3 | Tier-3---7 | 5--5 | 1.6544 | 27 | 100% | 6417.0381 | 80.3% | 19.69% | 0.01691% | 255.0589 | 0 | 0 | 255.0589 | 0 | 221.4077 | 1.5553 | 142.3605 | 221.4077 | 1.5553 | 142.3605 | 258.8282 | 1.8181 | 142.3605 | 3.975% | 0.19669 | 0.18696 | 32624.3404 | 6032.7065 | 5987.0676 | 20604.5664 | 32959.0914 | 0 | 0 | 32959.0914 | 0.008411%
2028 | 350 | 350-2188R | Tier-2 | Tier-2---5 | 5--5 | 22.0576 | 2114 | 100% | 3602.0119 | 95.48% | 4.084% | 0.4314% | 170.2488 | 0 | 0 | 170.2488 | 0 | 147.7871 | 20.7363 | 7.127 | 147.7871 | 20.7363 | 7.127 | 172.7648 | 24.241 | 7.127 | 4.726% | 0.15121 | 0.14373 | 23821.2544 | 3643.7972 | 896.9251 | 19280.5321 | 23877.2694 | 0 | 0 | 23877.2694 | 0.005614%
2028 | 94 | 94-16F | Tier-1 | Non-HFTD---15 | 2--2 | 2.6851 | 41 | 100% | 4.4816 | 61.07% | 0% | 38.93% | 0.13547 | 0 | 0 | 0.13547 | 0 | 0.1176 | 2.5242 | 0.046587 | 0.1176 | 2.5242 | 0.046587 | 0.13747 | 2.9509 | 0.046587 | 3.023% | 0.007584 | 0.0072086 | 590.9306 | 44.9122 | 129.254 | 416.7645 | 602.9122 | 0 | 0 | 602.9122 | 4.467e-06%
2028 | 511 | 511-831 | Tier-1 | Non-HFTD---5 | 2--3 | 0.15682 | 10 | 100% | 45.7736 | 11.2% | 88.5% | 0.2943% | 0.25387 | 0 | 0 | 0.25387 | 0 | 0.22037 | 0.14742 | 1.4948 | 0.22037 | 0.14742 | 1.4948 | 0.25762 | 0.17234 | 1.4948 | 0.5546% | 0.011273 | 0.010715 | 4060.4617 | 56.9583 | 3419.2148 | 584.2885 | 4248.229 | 0 | 0 | 4248.229 | 8.372e-06%
2028 | 521 | 521-27R | Tier-2 | Tier-2---3 | 4--5 | 10.1674 | 862 | 100% | 5618.6229 | 98.78% | 1.092% | 0.1294% | 274.726 | 0 | 0 | 274.726 | 0 | 238.4801 | 9.5584 | 24.9499 | 238.4801 | 9.5584 | 24.9499 | 278.7859 | 11.1738 | 24.9499 | 4.89% | 0.063668 | 0.060516 | 88249.328 | 16011.7412 | 1005.788 | 71231.7988 | 88305.4429 | 0 | 0 | 88305.4429 | 0.009059%
2028 | 571 | 571-49F | Tier-1 | Non-HFTD---11 | 2--2 | 4.1737 | 180 | 100% | 14.8937 | 75.79% | 0% | 24.21% | 0.55872 | 0 | 0 | 0.55872 | 0 | 0.48501 | 3.9237 | 0.12361 | 0.48501 | 3.9237 | 0.12361 | 0.56698 | 4.5868 | 0.12361 | 3.751% | 0.013087 | 0.01244 | 1138.0185 | 7.555 | 852.2014 | 278.2621 | 1152.3692 | 0 | 0 | 1152.3692 | 1.842e-05%
2028 | 161 | 161-610R | Tier-1 | Non-HFTD---8 | 4--2 | 15.3086 | 353 | 100% | 29.9374 | 67.56% | 0% | 32.44% | 1.0012 | 0 | 0 | 1.0012 | 0 | 0.86908 | 14.3916 | 0.060388 | 0.86908 | 14.3916 | 0.060388 | 1.016 | 16.8239 | 0.060388 | 3.344% | 0.041579 | 0.039521 | 720.0082 | 5.3968 | 475.6596 | 238.9517 | 732.172 | 0 | 0 | 732.172 | 3.302e-05%
2028 | PB1 | CB PB1 | Tier-1 | Non-HFTD---3 | 4--3 | 6.9699 | 84 | 100% | 137.6037 | 3.283% | 92.37% | 4.346% | 0.2236 | 0 | 0 | 0.2236 | 0 | 0.1941 | 6.5524 | 0.029622 | 0.1941 | 6.5524 | 0.029622 | 0.2269 | 7.6598 | 0.029622 | 0.1625% | 0.031616 | 0.030051 | 4352.3713 | 4.764 | 3790.0764 | 557.531 | 4571.5929 | 0 | 0 | 4571.5929 | 7.373e-06%
2028 | 257 | 257-31AE | Tier-1 | Non-HFTD---14 | 2--1 | 4.2349 | 159 | 100% | 5.7719 | 39.09% | 0% | 60.91% | 0.11168 | 0 | 0 | 0.11168 | 0 | 0.096944 | 3.9812 | 0.024351 | 0.096944 | 3.9812 | 0.024351 | 0.11333 | 4.6541 | 0.024351 | 1.935% | 0.012621 | 0.011996 | 457.3241 | 0.20961 | 204.0654 | 253.0491 | 471.8311 | 0 | 0 | 471.8311 | 3.683e-06%
2028 | 351 | CB 351 | Tier-2 | Tier-2---3 | 5--5 | 6.7335 | 568 | 100% | 14599.7352 | 99.66% | 0.3054% | 0.03279% | 720.2429 | 0 | 0 | 720.2429 | 0 | 625.2178 | 6.3302 | 98.7681 | 625.2178 | 6.3302 | 98.7681 | 730.8867 | 7.4 | 98.7681 | 4.933% | 0.12463 | 0.11847 | 117140.1184 | 26730.0261 | 377.3251 | 90032.7671 | 117160.7487 | 0 | 0 | 117160.7487 | 0.02375%
2028 | 137 | CB 137 | Tier-1 | Non-HFTD---18 | 1--1 | 0.9422 | 16 | 100% | 0.70761 | 22.42% | 0% | 77.58% | 0.0078535 | 0 | 0 | 0.0078535 | 0 | 0.0068174 | 0.88577 | 0.0076966 | 0.0068174 | 0.88577 | 0.0076966 | 0.0079696 | 1.0355 | 0.0076966 | 1.11% | 0.0024496 | 0.0023283 | 288.869 | 0.16863 | 85.1261 | 203.5742 | 300.5396 | 0 | 0 | 300.5396 | 2.59e-07%
2028 | 520 | CB 520 | Tier-2 | Tier-2---21 | 1--5 | 0.0058712 | 6 | 100% | 1.7668 | 97.86% | 0% | 2.14% | 0.085586 | 0 | 0 | 0.085586 | 0 | 0.074294 | 0.0055195 | 13.4602 | 0.074294 | 0.0055195 | 13.4602 | 0.08685 | 0.0064524 | 13.4602 | 4.844% | 7.36e-05 | 6.9957e-05 | 24005.4522 | 5429.4966 | 1707.34 | 16868.6156 | 24032.1992 | 0 | 0 | 24032.1992 | 2.822e-06%
2028 | 120 | 120-360F | Tier-1 | Non-HFTD---9 | 2--3 | 0.90587 | 65 | 100% | 24.5458 | 1.164% | 95.41% | 3.43% | 0.014138 | 0 | 0 | 0.014138 | 0 | 0.012273 | 0.85161 | 0.014412 | 0.012273 | 0.85161 | 0.014412 | 0.014347 | 0.99555 | 0.014412 | 0.0576% | 0.010414 | 0.0098981 | 2357.0882 | 2.378 | 2024.3177 | 330.3924 | 2478.4119 | 0 | 0 | 2478.4119 | 4.662e-07%
2028 | WA1 | CB WA1 | Tier-1 | Non-HFTD---8 | 3--2 | 7.9261 | 417 | 100% | 35.576 | 87.53% | 0% | 12.47% | 1.5414 | 0 | 0 | 1.5414 | 0 | 1.338 | 7.4513 | 0.17957 | 1.338 | 7.4513 | 0.17957 | 1.5642 | 8.7107 | 0.17957 | 4.333% | 0.024123 | 0.022929 | 1474.761 | 154.3788 | 361.2267 | 959.1555 | 1484.3394 | 0 | 0 | 1484.3394 | 5.083e-05%
2028 | 1152 | CB 1152 | Tier-1 | Non-HFTD---17 | 1--2 | 0.225 | 0 | 100% | 1.2601 | 88.07% | 0% | 11.93% | 0.054936 | 0 | 0 | 0.054936 | 0 | 0.047688 | 0.21152 | 0.22545 | 0.047688 | 0.21152 | 0.22545 | 0.055748 | 0.24727 | 0.22545 | 4.36% | 0.0009632 | 0.00091552 | 1308.2728 | 166.1488 | 97.0862 | 1045.0378 | 1316.4 | 0 | 0 | 1316.4 | 1.812e-06%
2028 | 356 | 356-19R | Tier-3 | Tier-3---8 | 5--5 | 24.1038 | 1376 | 100% | 16012.7864 | 97.76% | 2.145% | 0.09187% | 774.9006 | 0 | 0 | 774.9006 | 0 | 672.6642 | 22.66 | 29.685 | 672.6642 | 22.66 | 29.685 | 786.3521 | 26.4898 | 29.685 | 4.839% | 0.16775 | 0.15945 | 95453.8626 | 17291.24 | 1933.3613 | 76229.2613 | 95565.0716 | 0 | 0 | 95565.0716 | 0.02555%
2028 | 79 | 79-799R | Tier-3 | Tier-3---14 | 5--3 | 6.7626 | 86 | 100% | 3034.8235 | 97.12% | 2.752% | 0.1275% | 145.8979 | 0 | 0 | 145.8979 | 0 | 126.6489 | 6.3575 | 19.9212 | 126.6489 | 6.3575 | 19.9212 | 148.054 | 7.432 | 19.9212 | 4.807% | 0.77068 | 0.73253 | 3937.8445 | 548.6205 | 97.3974 | 3291.8266 | 3943.7498 | 0 | 0 | 3943.7498 | 0.004811%
2028 | 1215 | 1215-10R | Tier-3 | Tier-3---18 | 5--1 | 0.56254 | 0 | 100% | 157.8878 | 78.49% | 21.24% | 0.2654% | 6.1347 | 0 | 0 | 6.1347 | 0 | 5.3253 | 0.52885 | 10.0697 | 5.3253 | 0.52885 | 10.0697 | 6.2253 | 0.61823 | 10.0697 | 3.885% | 0.66566 | 0.63271 | 237.1916 | 27.6889 | 39.523 | 169.9797 | 239.848 | 0 | 0 | 239.848 | 0.0002023%
2028 | 948 | 948-5R | Tier-2 | Tier-2---21 | 1--2 | 0.64563 | 19 | 100% | 3.6494 | 90.16% | 0% | 9.838% | 0.16287 | 0 | 0 | 0.16287 | 0 | 0.14138 | 0.60696 | 0.23294 | 0.14138 | 0.60696 | 0.23294 | 0.16528 | 0.70954 | 0.23294 | 4.463% | 0.0023872 | 0.002269 | 1528.7338 | 203.4062 | 386.7322 | 938.5955 | 1536.5665 | 0 | 0 | 1536.5665 | 5.371e-06%
2028 | 79 | 79-676R | Tier-3 | Tier-3---5 | 5--5 | 4.5924 | 373 | 100% | 9714.1464 | 98.29% | 1.686% | 0.02874% | 472.6073 | 0 | 0 | 472.6073 | 0 | 410.2539 | 4.3173 | 95.0255 | 410.2539 | 4.3173 | 95.0255 | 479.5915 | 5.047 | 95.0255 | 4.865% | 0.38409 | 0.36508 | 25291.2629 | 4345.6054 | 407.8419 | 20537.8155 | 25313.8415 | 0 | 0 | 25313.8415 | 0.01558%
2028 | 351 | 351-871R | Tier-3 | Tier-3---6 | 5--5 | 4.4941 | 255 | 100% | 9144.3124 | 99.73% | 0.2371% | 0.03256% | 451.4229 | 0 | 0 | 451.4229 | 0 | 391.8645 | 4.2249 | 92.7506 | 391.8645 | 4.2249 | 92.7506 | 458.094 | 4.939 | 92.7506 | 4.937% | 0.11468 | 0.109 | 79737.0821 | 12866.5749 | 173.3661 | 66697.1411 | 79748.2799 | 0 | 0 | 79748.2799 | 0.01489%
2028 | 486 | 486-61R | Tier-1 | Non-HFTD---1 | 4--4 | 8.0996 | 279 | 100% | 415.5682 | 98.69% | 0% | 1.309% | 20.3013 | 0 | 0 | 20.3013 | 0 | 17.6228 | 7.6144 | 2.3144 | 17.6228 | 7.6144 | 2.3144 | 20.6013 | 8.9014 | 2.3144 | 4.885% | 0.031655 | 0.030088 | 13128.0422 | 2294.0601 | 163.567 | 10670.4151 | 13136.9945 | 0 | 0 | 13136.9945 | 0.0006695%
2028 | 974 | 974-715R | Tier-3 | Tier-3---6 | 5--5 | 8.7188 | 72 | 100% | 7107.1697 | 99.55% | 0.3981% | 0.05413% | 350.214 | 0 | 0 | 350.214 | 0 | 304.0085 | 8.1965 | 37.09 | 304.0085 | 8.1965 | 37.09 | 355.3895 | 9.5818 | 37.09 | 4.928% | 0.14069 | 0.13372 | 50517.2415 | 8114.8836 | 271.1921 | 42131.1659 | 50529.1387 | 0 | 0 | 50529.1387 | 0.01155%
2028 | 116 | 116-12R | Tier-1 | Non-HFTD---6 | 3--3 | 3.2824 | 68 | 100% | 54.5549 | 5.544% | 89.94% | 4.52% | 0.14973 | 0 | 0 | 0.14973 | 0 | 0.12997 | 3.0857 | 0.04212 | 0.12997 | 3.0857 | 0.04212 | 0.15194 | 3.6073 | 0.04212 | 0.2745% | 0.024461 | 0.02325 | 2230.262 | 3.7698 | 1966.9777 | 259.5146 | 2339.9695 | 0 | 0 | 2339.9695 | 4.937e-06%
2028 | 788 | CB 788 | Tier-2 | Tier-2---2 | 5--5 | 21.0708 | 1905 | 100% | 8569.0681 | 95.07% | 4.755% | 0.1724% | 403.2679 | 0 | 0 | 403.2679 | 0 | 350.0629 | 19.8087 | 17.6722 | 350.0629 | 19.8087 | 17.6722 | 409.2275 | 23.1566 | 17.6722 | 4.706% | 0.14181 | 0.13479 | 60426.1463 | 13184.7767 | 2801.9092 | 44439.4605 | 60581.2081 | 0 | 0 | 60581.2081 | 0.0133%
2028 | 350 | 350-2182R | Tier-2 | Tier-2---13 | 4--3 | 0.41228 | 17 | 100% | 302.428 | 99.27% | 0.6612% | 0.06922% | 14.8608 | 0 | 0 | 14.8608 | 0 | 12.9002 | 0.38759 | 33.2831 | 12.9002 | 0.38759 | 33.2831 | 15.0805 | 0.4531 | 33.2831 | 4.914% | 0.068991 | 0.065576 | 4383.5865 | 700.445 | 25.9827 | 3657.1588 | 4385.2539 | 0 | 0 | 4385.2539 | 0.0004901%
2028 | 237 | 237-1765R | Tier-3 | Tier-3---1 | 5--5 | 8.3421 | 383 | 100% | 28249.2525 | 99.34% | 0.6358% | 0.01982% | 1389.1699 | 0 | 0 | 1389.1699 | 0 | 1205.8901 | 7.8424 | 153.766 | 1205.8901 | 7.8424 | 153.766 | 1409.6992 | 9.1678 | 153.766 | 4.918% | 0.25909 | 0.24626 | 109034.6893 | 21935.6413 | 634.4252 | 86464.6228 | 109071.9184 | 0 | 0 | 109071.9184 | 0.04581%
2028 | 521 | 521-700R | Tier-2 | Tier-2---3 | 4--5 | 13.3513 | 1654 | 100% | 9012.5446 | 99.05% | 0.8425% | 0.1052% | 441.8931 | 0 | 0 | 441.8931 | 0 | 383.592 | 12.5516 | 30.5613 | 383.592 | 12.5516 | 30.5613 | 448.4235 | 14.6729 | 30.5613 | 4.903% | 0.074421 | 0.070737 | 121102.821 | 22486.5784 | 1104.4304 | 97511.8122 | 121162.5896 | 0 | 0 | 121162.5896 | 0.01457%
2028 | 68 | CB 68 | Tier-1 | Non-HFTD---4 | 3--4 | 1.521 | 13 | 100% | 125.6028 | 97.63% | 1.574% | 0.7918% | 6.0702 | 0 | 0 | 6.0702 | 0 | 5.2694 | 1.4299 | 3.6851 | 5.2694 | 1.4299 | 3.6851 | 6.1599 | 1.6716 | 3.6851 | 4.833% | 0.015716 | 0.014938 | 7992.034 | 1382.4541 | 1171.7344 | 5437.8454 | 8001.8815 | 0 | 0 | 8001.8815 | 0.0002002%
2028 | 306 | CB 306 | Tier-1 | Non-HFTD---1 | 4--4 | 1.2839 | 275 | 100% | 737.4997 | 97.09% | 2.802% | 0.1119% | 35.4424 | 0 | 0 | 35.4424 | 0 | 30.7663 | 1.207 | 25.4907 | 30.7663 | 1.207 | 25.4907 | 35.9662 | 1.411 | 25.4907 | 4.806% | 0.057753 | 0.054894 | 12769.9388 | 2020.535 | 320.1958 | 10429.208 | 12789.3181 | 0 | 0 | 12789.3181 | 0.001169%
2028 | OS5 | CB OS5 | Tier-1 | Non-HFTD---18 | 1--1 | 1.275 | 40 | 100% | 1.4382 | 31.82% | 0% | 68.18% | 0.022652 | 0 | 0 | 0.022652 | 0 | 0.019663 | 1.1987 | 0.016404 | 0.019663 | 1.1987 | 0.016404 | 0.022986 | 1.4013 | 0.016404 | 1.575% | 0.0036598 | 0.0034786 | 392.9844 | 0.52405 | 147.391 | 245.0693 | 406.9386 | 0 | 0 | 406.9386 | 7.47e-07%
2028 | 394 | 394-422F | Tier-1 | Non-HFTD---2 | 5--3 | 1.6971 | 43 | 100% | 314.1506 | 0.33% | 99.33% | 0.3425% | 0.051318 | 0 | 0 | 0.051318 | 0 | 0.044547 | 1.5955 | 0.027921 | 0.044547 | 1.5955 | 0.027921 | 0.052076 | 1.8651 | 0.027921 | 0.01634% | 0.095311 | 0.090593 | 3296.0513 | 5.5188 | 2895.8033 | 394.7292 | 3467.1361 | 0 | 0 | 3467.1361 | 1.692e-06%
2028 | 171 | 171-708R | Tier-1 | Non-HFTD---3 | 4--3 | 12.6172 | 98 | 100% | 144.3815 | 64.32% | 29.9% | 5.783% | 4.597 | 0 | 0 | 4.597 | 0 | 3.9905 | 11.8614 | 0.33642 | 3.9905 | 11.8614 | 0.33642 | 4.6649 | 13.8662 | 0.33642 | 3.184% | 0.084326 | 0.080152 | 1712.186 | 173.3767 | 499.0152 | 1039.7942 | 1743.9994 | 0 | 0 | 1743.9994 | 0.0001516%
2028 | 928 | 928-19 | Tier-2 | Tier-2---11 | 4--4 | 2.1411 | 4 | 100% | 434.8834 | 99.47% | 0.2691% | 0.2608% | 21.4127 | 0 | 0 | 21.4127 | 0 | 18.5876 | 2.0128 | 9.2346 | 18.5876 | 2.0128 | 9.2346 | 21.7291 | 2.353 | 9.2346 | 4.924% | 0.051756 | 0.049194 | 8402.5377 | 1782.5381 | 20.2893 | 6599.7102 | 8404.8564 | 0 | 0 | 8404.8564 | 0.0007061%
2028 | 431 | 431-474 | Tier-1 | Non-HFTD---15 | 2--1 | 1.7021 | 18 | 100% | 2.429 | 35.21% | 0% | 64.79% | 0.04233 | 0 | 0 | 0.04233 | 0 | 0.036745 | 1.6001 | 0.022964 | 0.036745 | 1.6001 | 0.022964 | 0.042956 | 1.8706 | 0.022964 | 1.743% | 0.0053256 | 0.005062 | 456.099 | 0.22237 | 187.4203 | 268.4563 | 471.4893 | 0 | 0 | 471.4893 | 1.396e-06%
2028 | 971 | 971-371R | Tier-3 | Tier-3---12 | 5--5 | 2.4735 | 122 | 100% | 4351.5062 | 99.52% | 0.4473% | 0.03668% | 214.3571 | 0 | 0 | 214.3571 | 0 | 186.0759 | 2.3254 | 80.0202 | 186.0759 | 2.3254 | 80.0202 | 217.5249 | 2.7184 | 80.0202 | 4.926% | 0.11668 | 0.1109 | 37295.5774 | 6189.1534 | 149.4964 | 30956.9275 | 37304.9774 | 0 | 0 | 37304.9774 | 0.007069%
2028 | 476 | 476-6F | Tier-1 | Non-HFTD---10 | 5--1 | 0.074053 | 11 | 100% | 18.587 | 5.339% | 94.33% | 0.3325% | 0.049124 | 0 | 0 | 0.049124 | 0 | 0.042643 | 0.069617 | 0.61253 | 0.042643 | 0.069617 | 0.61253 | 0.04985 | 0.081383 | 0.61253 | 0.2643% | 0.15628 | 0.14854 | 118.9364 | 1.3234 | 95.4058 | 22.2073 | 124.7997 | 0 | 0 | 124.7997 | 1.62e-06%
2028 | 1094 | 1094-7 | Tier-2 | Tier-2---17 | 2--4 | 1.7031 | 141 | 100% | 95.3301 | 98.77% | 0% | 1.235% | 4.6606 | 0 | 0 | 4.6606 | 0 | 4.0457 | 1.601 | 2.5269 | 4.0457 | 1.601 | 2.5269 | 4.7294 | 1.8716 | 2.5269 | 4.889% | 0.0065074 | 0.0061853 | 14649.4839 | 2335.884 | 162.0699 | 12151.53 | 14658.9042 | 0 | 0 | 14658.9042 | 0.0001537%
2028 | 980 | CB 980 | Tier-2 | Tier-2---12 | 2--5 | 1.8653 | 473 | 100% | 387.8494 | 99.7% | 0% | 0.3041% | 19.1402 | 0 | 0 | 19.1402 | 0 | 16.6149 | 1.7536 | 9.4747 | 16.6149 | 1.7536 | 9.4747 | 19.423 | 2.05 | 9.4747 | 4.935% | 0.0069124 | 0.0065702 | 56109.2292 | 24867.9549 | 702.1092 | 30539.1651 | 56118.1149 | 0 | 0 | 56118.1149 | 0.0006312%
2028 | BF1 | CB BF1 | Tier-1 | Non-HFTD---9 | 2--3 | 1.6113 | 1 | 100% | 20.8946 | 91.56% | 0% | 8.439% | 0.947 | 0 | 0 | 0.947 | 0 | 0.82206 | 1.5148 | 0.54268 | 0.82206 | 1.5148 | 0.54268 | 0.96099 | 1.7708 | 0.54268 | 4.532% | 0.0060496 | 0.0057501 | 3453.8829 | 552.2417 | 48.3246 | 2853.3166 | 3469.0626 | 0 | 0 | 3469.0626 | 3.123e-05%
2028 | 396 | CB 396 | Tier-2 | Tier-2---11 | 5--4 | 3.6322 | 118 | 100% | 669.8148 | 14.34% | 85.25% | 0.4034% | 4.7554 | 0 | 0 | 4.7554 | 0 | 4.128 | 3.4147 | 1.2089 | 4.128 | 3.4147 | 1.2089 | 4.8257 | 3.9918 | 1.2089 | 0.71% | 0.10036 | 0.095392 | 6674.121 | 193.8927 | 5213.8843 | 1266.344 | 6971.8435 | 0 | 0 | 6971.8435 | 0.0001568%
2028 | 788 | 788-34R | Tier-2 | Tier-2---6 | 5--5 | 16.0985 | 1221 | 100% | 9132.2366 | 94.33% | 5.547% | 0.1209% | 426.4266 | 0 | 0 | 426.4266 | 0 | 370.166 | 15.1342 | 24.4589 | 370.166 | 15.1342 | 24.4589 | 432.7283 | 17.692 | 24.4589 | 4.669% | 0.12404 | 0.1179 | 73621.1831 | 18327.6204 | 3867.2587 | 51426.3041 | 73838.4724 | 0 | 0 | 73838.4724 | 0.01406%
2028 | 230 | 230-2060R | Tier-2 | Tier-2---4 | 4--5 | 9.1409 | 907 | 100% | 3473.4554 | 97.68% | 2.135% | 0.1887% | 167.9415 | 0 | 0 | 167.9415 | 0 | 145.7841 | 8.5934 | 16.9647 | 145.7841 | 8.5934 | 16.9647 | 170.4233 | 10.0458 | 16.9647 | 4.835% | 0.088414 | 0.084038 | 39286.0822 | 6237.3116 | 786.318 | 32262.4526 | 39333.6151 | 0 | 0 | 39333.6151 | 0.005538%
2028 | 908 | 908-2038R | Tier-2 | Tier-2---1 | 5--5 | 17.9266 | 1368 | 100% | 41258.5742 | 98.89% | 1.078% | 0.03081% | 2019.6477 | 0 | 0 | 2019.6477 | 0 | 1753.1858 | 16.8528 | 104.0295 | 1753.1858 | 16.8528 | 104.0295 | 2049.4942 | 19.7011 | 104.0295 | 4.895% | 0.23053 | 0.21912 | 178970.5163 | 35360.8505 | 1780.0078 | 141829.658 | 179073.8915 | 0 | 0 | 179073.8915 | 0.0666%
2028 | 297 | 297-828AE | Tier-1 | Non-HFTD---5 | 2--4 | 1.7713 | 112 | 100% | 51.9776 | 97.72% | 0% | 2.278% | 2.5143 | 0 | 0 | 2.5143 | 0 | 2.1826 | 1.6652 | 1.3107 | 2.1826 | 1.6652 | 1.3107 | 2.5514 | 1.9466 | 1.3107 | 4.837% | 0.0062854 | 0.0059743 | 8269.5727 | 1759.1338 | 61.0431 | 6449.3958 | 8279.3842 | 0 | 0 | 8279.3842 | 8.291e-05%
2028 | 73 | 73-683R | Tier-3 | Tier-3---7 | 5--5 | 10.907 | 490 | 100% | 9288.0329 | 98.43% | 1.494% | 0.07761% | 452.5311 | 0 | 0 | 452.5311 | 0 | 392.8265 | 10.2536 | 38.3109 | 392.8265 | 10.2536 | 38.3109 | 459.2187 | 11.9866 | 38.3109 | 4.872% | 0.22716 | 0.21591 | 40887.9849 | 6381.0644 | 580.3589 | 33926.5617 | 40921.4543 | 0 | 0 | 40921.4543 | 0.01492%
2028 | 212 | 212-743R | Tier-2 | Tier-2---13 | 5--3 | 3.6616 | 65 | 100% | 261.4279 | 97.06% | 2.12% | 0.8249% | 12.5596 | 0 | 0 | 12.5596 | 0 | 10.9026 | 3.4422 | 3.1673 | 10.9026 | 3.4422 | 3.1673 | 12.7452 | 4.024 | 3.1673 | 4.804% | 0.11654 | 0.11078 | 2243.1612 | 251.3274 | 45.2431 | 1946.5907 | 2246.6012 | 0 | 0 | 2246.6012 | 0.0004142%
2028 | 1076 | CB 1076 | Tier-1 | Non-HFTD---9 | 2--3 | 3.9479 | 154 | 100% | 20.7787 | 85.56% | 0% | 14.44% | 0.88007 | 0 | 0 | 0.88007 | 0 | 0.76396 | 3.7114 | 0.20584 | 0.76396 | 3.7114 | 0.20584 | 0.89307 | 4.3387 | 0.20584 | 4.235% | 0.011545 | 0.010974 | 1799.7403 | 1.5108 | 1555.3284 | 242.9011 | 1813.2706 | 0 | 0 | 1813.2706 | 2.902e-05%
2028 | CD4 | CB CD4 | Tier-1 | Non-HFTD---8 | 3--3 | 4.5362 | 259 | 100% | 39.5125 | 6.129% | 86.05% | 7.825% | 0.11988 | 0 | 0 | 0.11988 | 0 | 0.10406 | 4.2644 | 0.024402 | 0.10406 | 4.2644 | 0.024402 | 0.12165 | 4.9852 | 0.024402 | 0.3034% | 0.022929 | 0.021794 | 1723.2234 | 10.1387 | 1416.6051 | 296.4796 | 1807.4647 | 0 | 0 | 1807.4647 | 3.953e-06%
2028 | 412 | CB 412 | Tier-1 | Non-HFTD---1 | 4--5 | 17.7277 | 1039 | 100% | 1311.9921 | 88.37% | 10.81% | 0.8215% | 57.392 | 0 | 0 | 57.392 | 0 | 49.82 | 16.6658 | 2.9894 | 49.82 | 16.6658 | 2.9894 | 58.2402 | 19.4825 | 2.9894 | 4.374% | 0.071433 | 0.067897 | 18366.6483 | 2615.4927 | 2100.6109 | 13650.5447 | 18477.8687 | 0 | 0 | 18477.8687 | 0.001893%
2028 | 45 | 45-15AE | Tier-1 | Non-HFTD---11 | 1--3 | 0.56231 | 24 | 100% | 8.7551 | 92.94% | 0% | 7.056% | 0.4028 | 0 | 0 | 0.4028 | 0 | 0.34965 | 0.52863 | 0.66144 | 0.34965 | 0.52863 | 0.66144 | 0.40875 | 0.61797 | 0.66144 | 4.601% | 0.0022584 | 0.0021466 | 3876.685 | 65.548 | 3228.8334 | 582.3036 | 3890.931 | 0 | 0 | 3890.931 | 1.328e-05%
2028 | 452 | 452-1404F | Tier-2 | Tier-2---12 | 1--5 | 0.80794 | 3 | 100% | 625.5425 | 99.9% | 0% | 0.09615% | 30.9346 | 0 | 0 | 30.9346 | 0 | 26.8532 | 0.75955 | 35.3543 | 26.8532 | 0.75955 | 35.3543 | 31.3917 | 0.88792 | 35.3543 | 4.945% | 0.0036434 | 0.0034631 | 171691.9583 | 40882.2121 | 22.2295 | 130787.5168 | 171700.5551 | 0 | 0 | 171700.5551 | 0.00102%
2028 | 795 | 795-816R | Tier-2 | Tier-2---13 | 4--4 | 6.4011 | 361 | 100% | 228.7654 | 4.756% | 93.08% | 2.167% | 0.53859 | 0 | 0 | 0.53859 | 0 | 0.46753 | 6.0177 | 0.077693 | 0.46753 | 6.0177 | 0.077693 | 0.54655 | 7.0348 | 0.077693 | 0.2354% | 0.036491 | 0.034684 | 6269.16 | 14.3219 | 5608.3339 | 646.5042 | 6580.116 | 0 | 0 | 6580.116 | 1.776e-05%
2028 | 859 | 859-1064 | Tier-1 | Non-HFTD---7 | 2--3 | 4.2178 | 255 | 100% | 40.2522 | 93.55% | 0% | 6.452% | 1.8639 | 0 | 0 | 1.8639 | 0 | 1.618 | 3.9651 | 0.40806 | 1.618 | 3.9651 | 0.40806 | 1.8915 | 4.6353 | 0.40806 | 4.631% | 0.011569 | 0.010996 | 3479.3123 | 521.49 | 92.9503 | 2864.872 | 3491.0022 | 0 | 0 | 3491.0022 | 6.147e-05%
2028 | 79 | 79-658R | Tier-3 | Tier-3---5 | 5--5 | 9.5078 | 505 | 100% | 12321.0759 | 99.26% | 0.6823% | 0.05367% | 605.4043 | 0 | 0 | 605.4043 | 0 | 525.5304 | 8.9383 | 58.7956 | 525.5304 | 8.9383 | 58.7956 | 614.3511 | 10.4489 | 58.7956 | 4.914% | 0.46655 | 0.44346 | 26408.7945 | 4377.4606 | 177.0739 | 21854.26 | 26418.917 | 0 | 0 | 26418.917 | 0.01996%
2028 | 1173 | 1173-70 | Tier-1 | Non-HFTD---9 | 2--3 | 0.44863 | 4 | 100% | 15.3764 | 0.6778% | 97.23% | 2.096% | 0.0051591 | 0 | 0 | 0.0051591 | 0 | 0.0044785 | 0.42175 | 0.010619 | 0.0044785 | 0.42175 | 0.010619 | 0.0052354 | 0.49304 | 0.010619 | 0.03355% | 0.008697 | 0.0082665 | 1768.0079 | 1.6115 | 1488.7681 | 277.6283 | 1859.4579 | 0 | 0 | 1859.4579 | 1.701e-07%
2028 | 386 | CB 386 | Tier-2 | Tier-2---14 | 4--4 | 7.9203 | 582 | 100% | 266.4482 | 58.89% | 39.19% | 1.927% | 7.7666 | 0 | 0 | 7.7666 | 0 | 6.7419 | 7.4459 | 0.90546 | 6.7419 | 7.4459 | 0.90546 | 7.8814 | 8.7043 | 0.90546 | 2.915% | 0.037437 | 0.035584 | 7117.2424 | 561.1032 | 3326.6838 | 3229.4554 | 7269.6317 | 0 | 0 | 7269.6317 | 0.0002561%
2028 | 122 | CB 122 | Tier-1 | Non-HFTD---13 | 2--2 | 2.0557 | 0 | 100% | 8.11 | 77.73% | 0% | 22.27% | 0.31204 | 0 | 0 | 0.31204 | 0 | 0.27087 | 1.9325 | 0.14016 | 0.27087 | 1.9325 | 0.14016 | 0.31665 | 2.2592 | 0.14016 | 3.848% | 0.0070694 | 0.0067195 | 1147.1966 | 45.0636 | 638.2561 | 463.8769 | 1160.5021 | 0 | 0 | 1160.5021 | 1.029e-05%
2028 | 172 | 172-630R | Tier-1 | Non-HFTD---6 | 4--2 | 4.8346 | 15 | 100% | 66.3107 | 6.519% | 90.48% | 2.997% | 0.21398 | 0 | 0 | 0.21398 | 0 | 0.18575 | 4.545 | 0.040869 | 0.18575 | 4.545 | 0.040869 | 0.21715 | 5.3132 | 0.040869 | 0.3227% | 0.053137 | 0.050507 | 1247.9203 | 10.8427 | 1030.4852 | 206.5924 | 1308.6726 | 0 | 0 | 1308.6726 | 7.056e-06%
2028 | CS1 | CB CS1 | Tier-1 | Non-HFTD---14 | 3--1 | 6.2901 | 165 | 100% | 6.8922 | 38.03% | 0% | 61.97% | 0.12974 | 0 | 0 | 0.12974 | 0 | 0.11263 | 5.9133 | 0.019046 | 0.11263 | 5.9133 | 0.019046 | 0.13166 | 6.9128 | 0.019046 | 1.882% | 0.017311 | 0.016454 | 398.15 | 1.1079 | 168.1623 | 228.8798 | 410.9994 | 0 | 0 | 410.9994 | 4.278e-06%
2028 | 114 | 114-48 | Tier-1 | Non-HFTD---6 | 3--3 | 6.0661 | 157 | 100% | 88.8606 | 4.08% | 91.67% | 4.249% | 0.17946 | 0 | 0 | 0.17946 | 0 | 0.15578 | 5.7027 | 0.027317 | 0.15578 | 5.7027 | 0.027317 | 0.18211 | 6.6665 | 0.027317 | 0.202% | 0.02752 | 0.026158 | 3228.8995 | 11.4775 | 2773.9851 | 443.4369 | 3390.1931 | 0 | 0 | 3390.1931 | 5.918e-06%
2028 | 114 | CB 114 | Tier-1 | Non-HFTD---7 | 2--3 | 1.6892 | 172 | 100% | 43.2481 | 88.83% | 8.106% | 3.062% | 1.9017 | 0 | 0 | 1.9017 | 0 | 1.6508 | 1.588 | 1.0395 | 1.6508 | 1.588 | 1.0395 | 1.9298 | 1.8564 | 1.0395 | 4.397% | 0.013188 | 0.012535 | 3279.4498 | 356.1869 | 963.7932 | 1959.4698 | 3298.5242 | 0 | 0 | 3298.5242 | 6.271e-05%
2028 | 288 | 288-2375R | Tier-2 | Tier-2---19 | 2--4 | 0.26853 | 62 | 100% | 41.8014 | 98.23% | 1.253% | 0.5152% | 2.0326 | 0 | 0 | 2.0326 | 0 | 1.7644 | 0.25245 | 6.9893 | 1.7644 | 0.25245 | 6.9893 | 2.0626 | 0.29511 | 6.9893 | 4.862% | 0.0067116 | 0.0063794 | 6228.2316 | 993.1951 | 116.6696 | 5118.3669 | 6233.9673 | 0 | 0 | 6233.9673 | 6.703e-05%
2028 | 390 | 390-15 | Tier-1 | Non-HFTD---2 | 5--3 | 1.561 | 36 | 100% | 260.9963 | 0.6321% | 98.96% | 0.4064% | 0.081661 | 0 | 0 | 0.081661 | 0 | 0.070887 | 1.4675 | 0.048306 | 0.070887 | 1.4675 | 0.048306 | 0.082868 | 1.7155 | 0.048306 | 0.03129% | 0.099654 | 0.094722 | 2619.0141 | 6.4394 | 2346.7211 | 265.8535 | 2754.5446 | 0 | 0 | 2754.5446 | 2.693e-06%
2028 | 257 | 257-29AE | Tier-1 | Non-HFTD---16 | 2--1 | 2.4854 | 75 | 100% | 2.2983 | 19.76% | 0% | 80.24% | 0.022484 | 0 | 0 | 0.022484 | 0 | 0.019518 | 2.3365 | 0.0083532 | 0.019518 | 2.3365 | 0.0083532 | 0.022816 | 2.7314 | 0.0083532 | 0.9783% | 0.006989 | 0.006643 | 328.8485 | 0.19854 | 88.9601 | 239.6899 | 342.5897 | 0 | 0 | 342.5897 | 7.414e-07%
2028 | 189 | CB 189 | Tier-1 | Non-HFTD---7 | 2--4 | 1.6267 | 68 | 100% | 36.5503 | 96.65% | 0% | 3.352% | 1.7486 | 0 | 0 | 1.7486 | 0 | 1.5179 | 1.5293 | 0.99255 | 1.5179 | 1.5293 | 0.99255 | 1.7744 | 1.7878 | 0.99255 | 4.784% | 0.0052996 | 0.0050373 | 6896.7976 | 807.5104 | 1754.8536 | 4334.4335 | 6908.8371 | 0 | 0 | 6908.8371 | 5.766e-05%
2028 | 220 | 220-294R | Tier-3 | Tier-3---14 | 5--3 | 13.4125 | 974 | 100% | 1925.8876 | 84.29% | 15.28% | 0.4298% | 80.3557 | 0 | 0 | 80.3557 | 0 | 69.754 | 12.6091 | 5.532 | 69.754 | 12.6091 | 5.532 | 81.5432 | 14.7402 | 5.532 | 4.172% | 0.44397 | 0.422 | 4337.8466 | 467.6186 | 600.0435 | 3270.1845 | 4373.3345 | 0 | 0 | 4373.3345 | 0.00265%
2028 | 310 | 310-9R | Tier-1 | Non-HFTD---13 | 1--3 | 1.5318 | 84 | 100% | 7.8805 | 85.45% | 0% | 14.55% | 0.33331 | 0 | 0 | 0.33331 | 0 | 0.28934 | 1.4401 | 0.20092 | 0.28934 | 1.4401 | 0.20092 | 0.33824 | 1.6835 | 0.20092 | 4.23% | 0.0044784 | 0.0042567 | 1759.6775 | 1.0284 | 1521.6386 | 237.0105 | 1773.015 | 0 | 0 | 1773.015 | 1.099e-05%
2028 | 69 | CB 69 | Tier-1 | Non-HFTD---5 | 2--3 | 1.1767 | 12 | 100% | 50.7962 | 92.2% | 5.783% | 2.017% | 2.3183 | 0 | 0 | 2.3183 | 0 | 2.0124 | 1.1063 | 1.8191 | 2.0124 | 1.1063 | 1.8191 | 2.3526 | 1.2932 | 1.8191 | 4.564% | 0.011719 | 0.011139 | 4334.4449 | 720.874 | 567.5626 | 3046.0083 | 4352.0516 | 0 | 0 | 4352.0516 | 7.645e-05%
2028 | 214 | 214-583R | Tier-3 | Tier-3---13 | 4--5 | 6.1356 | 334 | 100% | 2208.3134 | 99.09% | 0.6816% | 0.2244% | 108.3212 | 0 | 0 | 108.3212 | 0 | 94.0298 | 5.7681 | 16.3017 | 94.0298 | 5.7681 | 16.3017 | 109.922 | 6.743 | 16.3017 | 4.905% | 0.070413 | 0.066928 | 31362.296 | 5124.9033 | 314.6524 | 25922.7404 | 31377.0932 | 0 | 0 | 31377.0932 | 0.003572%
2028 | 175 | 175-94R | Tier-2 | Tier-2---10 | 5--4 | 2.0289 | 257 | 100% | 836.2457 | 79.76% | 20.09% | 0.1547% | 33.0153 | 0 | 0 | 33.0153 | 0 | 28.6595 | 1.9074 | 15.0253 | 28.6595 | 1.9074 | 15.0253 | 33.5032 | 2.2298 | 15.0253 | 3.948% | 0.16555 | 0.15736 | 5051.3061 | 703.4026 | 913.3417 | 3434.5618 | 5104.5538 | 0 | 0 | 5104.5538 | 0.001089%
2028 | 242 | 242-1411F | Tier-1 | Non-HFTD---1 | 5--4 | 0.27213 | 21 | 100% | 861.0308 | 0.3297% | 99.65% | 0.02489% | 0.14053 | 0 | 0 | 0.14053 | 0 | 0.12199 | 0.25583 | 0.47682 | 0.12199 | 0.25583 | 0.47682 | 0.1426 | 0.29907 | 0.47682 | 0.01632% | 0.09372 | 0.08908 | 9187.308 | 16.4683 | 8354.5754 | 816.2643 | 9664.1858 | 0 | 0 | 9664.1858 | 4.634e-06%
2028 | CA2 | CB CA2 | Tier-1 | Non-HFTD---9 | 2--2 | 0.94321 | 19 | 100% | 20.4637 | 1.406% | 94.71% | 3.883% | 0.014245 | 0 | 0 | 0.014245 | 0 | 0.012366 | 0.88671 | 0.013946 | 0.012366 | 0.88671 | 0.013946 | 0.014456 | 1.0366 | 0.013946 | 0.06961% | 0.013315 | 0.012656 | 1536.8705 | 2.0039 | 1342.2543 | 192.6124 | 1615.7819 | 0 | 0 | 1615.7819 | 4.698e-07%
2028 | 448 | 448-744R | Tier-3 | Tier-3---7 | 5--5 | 29.2157 | 767 | 100% | 9104.5616 | 91.68% | 8.126% | 0.1928% | 413.1864 | 0 | 0 | 413.1864 | 0 | 358.6727 | 27.4657 | 13.0589 | 358.6727 | 27.4657 | 13.0589 | 419.2925 | 32.1077 | 13.0589 | 4.538% | 0.49442 | 0.46994 | 18414.705 | 2487.6549 | 1363.4523 | 14563.5979 | 18494.4792 | 0 | 0 | 18494.4792 | 0.01363%
2028 | 488 | CB 488 | Tier-1 | Non-HFTD---15 | 1--2 | 1.7068 | 32 | 100% | 3.9951 | 71.83% | 0% | 28.17% | 0.14206 | 0 | 0 | 0.14206 | 0 | 0.12331 | 1.6045 | 0.076852 | 0.12331 | 1.6045 | 0.076852 | 0.14415 | 1.8757 | 0.076852 | 3.556% | 0.0047686 | 0.0045326 | 837.8017 | 0.17757 | 623.2495 | 214.3746 | 850.0916 | 0 | 0 | 850.0916 | 4.684e-06%
2028 | 56 | 56-669F | Tier-1 | Non-HFTD---4 | 2--4 | 0.57918 | 1 | 100% | 107.608 | 0.09989% | 99.43% | 0.4717% | 0.0053209 | 0 | 0 | 0.0053209 | 0 | 0.0046189 | 0.54449 | 0.0084831 | 0.0046189 | 0.54449 | 0.0084831 | 0.0053996 | 0.63651 | 0.0084831 | 0.004945% | 0.012314 | 0.011705 | 8738.387 | 10.1815 | 7924.2222 | 803.9833 | 9193.0088 | 0 | 0 | 9193.0088 | 1.755e-07%
2028 | 308 | 308-485AE | Tier-2 | Tier-2---15 | 4--3 | 1.6722 | 57 | 100% | 157.9773 | 2.775% | 96.6% | 0.6237% | 0.217 | 0 | 0 | 0.217 | 0 | 0.18837 | 1.572 | 0.11982 | 0.18837 | 1.572 | 0.11982 | 0.2202 | 1.8377 | 0.11982 | 0.1374% | 0.034738 | 0.033018 | 4547.6785 | 25.2626 | 4047.4864 | 474.9295 | 4777.9399 | 0 | 0 | 4777.9399 | 7.156e-06%
2028 | 1118 | 1118-1718F | Tier-2 | Tier-2---10 | 5--4 | 0.77126 | 73 | 100% | 788.3757 | 99.4% | 0.5205% | 0.07536% | 38.792 | 0 | 0 | 38.792 | 0 | 33.674 | 0.72506 | 46.4431 | 33.674 | 0.72506 | 46.4431 | 39.3653 | 0.8476 | 46.4431 | 4.921% | 0.10781 | 0.10247 | 7312.7208 | 1401.0432 | 30.5742 | 5881.1034 | 7314.9902 | 0 | 0 | 7314.9902 | 0.001279%
2028 | 1242 | 1242-1084 | Tier-2 | Tier-2---12 | 2--5 | 1.5712 | 55 | 100% | 456.1931 | 99.77% | 0% | 0.2285% | 22.53 | 0 | 0 | 22.53 | 0 | 19.5575 | 1.4771 | 13.2405 | 19.5575 | 1.4771 | 13.2405 | 22.8629 | 1.7267 | 13.2405 | 4.939% | 0.005996 | 0.0056992 | 76082.9136 | 21423.4088 | 20.55 | 54638.9547 | 76091.9678 | 0 | 0 | 76091.9678 | 0.000743%
2028 | 40 | CB 40 | Tier-1 | Non-HFTD---6 | 3--3 | 7.115 | 166 | 100% | 69.5172 | 93.23% | 0% | 6.766% | 3.2083 | 0 | 0 | 3.2083 | 0 | 2.785 | 6.6888 | 0.41637 | 2.785 | 6.6888 | 0.41637 | 3.2557 | 7.8193 | 0.41637 | 4.615% | 0.021321 | 0.020266 | 3260.5047 | 598.6862 | 390.1907 | 2271.6278 | 3271.993 | 0 | 0 | 3271.993 | 0.0001058%
2028 | 137 | 137-34AE | Tier-1 | Non-HFTD---16 | 2--1 | 3.2265 | 148 | 100% | 3.1884 | 24.97% | 0% | 75.03% | 0.039416 | 0 | 0 | 0.039416 | 0 | 0.034216 | 3.0332 | 0.01128 | 0.034216 | 3.0332 | 0.01128 | 0.039998 | 3.5459 | 0.01128 | 1.236% | 0.0099752 | 0.0094814 | 319.6366 | 0.18045 | 101.6106 | 217.8455 | 332.1254 | 0 | 0 | 332.1254 | 1.3e-06%
2028 | 275 | 275-48F | Tier-1 | Non-HFTD---3 | 3--4 | 3.4754 | 51 | 100% | 122.1483 | 5.775% | 92.83% | 1.397% | 0.34918 | 0 | 0 | 0.34918 | 0 | 0.30311 | 3.2672 | 0.092774 | 0.30311 | 3.2672 | 0.092774 | 0.35434 | 3.8194 | 0.092774 | 0.2859% | 0.024465 | 0.023254 | 4992.7367 | 48.2186 | 4344.9921 | 599.526 | 5237.7319 | 0 | 0 | 5237.7319 | 1.151e-05%
2028 | 1021 | 1021-855 | Tier-3 | Tier-3---10 | 5--5 | 2.9135 | 351 | 100% | 5034.3753 | 99.51% | 0.4541% | 0.0405% | 247.9689 | 0 | 0 | 247.9689 | 0 | 215.2532 | 2.7389 | 78.5897 | 215.2532 | 2.7389 | 78.5897 | 251.6334 | 3.2019 | 78.5897 | 4.926% | 0.10909 | 0.10369 | 46149.2476 | 7426.785 | 192.1999 | 38530.2627 | 46161.1355 | 0 | 0 | 46161.1355 | 0.008177%
2028 | NC3 | CB NC3 | Tier-1 | Non-HFTD---18 | 1--1 | 1.3062 | 16 | 100% | 1.3141 | 19.33% | 0% | 80.67% | 0.012576 | 0 | 0 | 0.012576 | 0 | 0.010917 | 1.228 | 0.0088904 | 0.010917 | 1.228 | 0.0088904 | 0.012762 | 1.4355 | 0.0088904 | 0.9571% | 0.004054 | 0.0038533 | 324.1367 | 12.2073 | 35.4768 | 276.4527 | 337.7533 | 0 | 0 | 337.7533 | 4.147e-07%
2028 | 341 | 341-1155F | Tier-1 | Non-HFTD---1 | 3--5 | 4.5127 | 433 | 100% | 374.3613 | 99.24% | 0% | 0.7589% | 18.3903 | 0 | 0 | 18.3903 | 0 | 15.9639 | 4.2424 | 3.763 | 15.9639 | 4.2424 | 3.763 | 18.662 | 4.9594 | 3.763 | 4.912% | 0.015477 | 0.014711 | 24187.611 | 4353.0066 | 31.6958 | 19802.9086 | 24197.1702 | 0 | 0 | 24197.1702 | 0.0006064%
2028 | BN1 | CB BN1 | Tier-1 | Non-HFTD---4 | 4--4 | 10.2073 | 521 | 100% | 173.8031 | 96.37% | 0% | 3.629% | 8.291 | 0 | 0 | 8.291 | 0 | 7.1971 | 9.5959 | 0.75002 | 7.1971 | 9.5959 | 0.75002 | 8.4135 | 11.2178 | 0.75002 | 4.77% | 0.028851 | 0.027423 | 6024.1621 | 939.3966 | 90.5041 | 4994.2615 | 6035.548 | 0 | 0 | 6035.548 | 0.0002734%
2028 | 255 | 255-1080R | Tier-1 | Non-HFTD---18 | 2--1 | 2.5939 | 84 | 100% | 2.1745 | 29.65% | 0% | 70.35% | 0.031915 | 0 | 0 | 0.031915 | 0 | 0.027704 | 2.4386 | 0.011361 | 0.027704 | 2.4386 | 0.011361 | 0.032387 | 2.8507 | 0.011361 | 1.468% | 0.006657 | 0.0063275 | 326.6462 | 0.17291 | 117.7275 | 208.7459 | 338.6134 | 0 | 0 | 338.6134 | 1.052e-06%
2028 | 454 | 454-47R | Tier-1 | Non-HFTD---17 | 1--2 | 0.27501 | 6 | 100% | 0.77526 | 68.13% | 0% | 31.87% | 0.026144 | 0 | 0 | 0.026144 | 0 | 0.022695 | 0.25854 | 0.087782 | 0.022695 | 0.25854 | 0.087782 | 0.02653 | 0.30223 | 0.087782 | 3.372% | 0.0008848 | 0.000841 | 876.1933 | 0.21014 | 622.2981 | 253.6851 | 890.7368 | 0 | 0 | 890.7368 | 8.621e-07%
2028 | 222 | 222-1988R | Tier-3 | Tier-3---11 | 5--4 | 0.94526 | 9 | 100% | 3619.4356 | 99.27% | 0.7155% | 0.01673% | 177.8502 | 0 | 0 | 177.8502 | 0 | 154.3856 | 0.88864 | 173.7332 | 154.3856 | 0.88864 | 173.7332 | 180.4785 | 1.0388 | 173.7332 | 4.914% | 0.34461 | 0.32755 | 10502.9479 | 1679.8132 | 68.5397 | 8754.595 | 10506.9529 | 0 | 0 | 10506.9529 | 0.005865%
2028 | ES4 | CB ES4 | Tier-1 | Non-HFTD---10 | 4--1 | 15.6208 | 619 | 100% | 17.8102 | 40.04% | 0% | 59.96% | 0.35302 | 0 | 0 | 0.35302 | 0 | 0.30645 | 14.6851 | 0.020868 | 0.30645 | 14.6851 | 0.020868 | 0.35824 | 17.1671 | 0.020868 | 1.982% | 0.043584 | 0.041426 | 408.6447 | 3.4145 | 166.1409 | 239.0894 | 421.4043 | 0 | 0 | 421.4043 | 1.164e-05%
2028 | SR1 | CB SR1 | Tier-1 | Non-HFTD---12 | 4--1 | 11.5445 | 296 | 100% | 12.5988 | 40.76% | 0% | 59.24% | 0.25419 | 0 | 0 | 0.25419 | 0 | 0.22065 | 10.853 | 0.020331 | 0.22065 | 10.853 | 0.020331 | 0.25795 | 12.6873 | 0.020331 | 2.018% | 0.032342 | 0.030741 | 389.5505 | 31.2637 | 84.0563 | 274.2304 | 401.5686 | 0 | 0 | 401.5686 | 8.382e-06%
2028 | 204 | 204-32R | Tier-2 | Tier-2---11 | 4--4 | 17.63 | 253 | 100% | 490.4615 | 96.36% | 1.259% | 2.378% | 23.3948 | 0 | 0 | 23.3948 | 0 | 20.3082 | 16.5739 | 1.2253 | 20.3082 | 16.5739 | 1.2253 | 23.7405 | 19.3751 | 1.2253 | 4.77% | 0.087106 | 0.082794 | 5630.6279 | 747.5355 | 75.2 | 4807.8924 | 5641.2939 | 0 | 0 | 5641.2939 | 0.0007715%
2028 | 75 | 75-2259F | Tier-3 | Tier-3---12 | 3--5 | 4.3521 | 411 | 100% | 3135.4576 | 99.77% | 0.1421% | 0.08717% | 154.8494 | 0 | 0 | 154.8494 | 0 | 134.4194 | 4.0914 | 32.8542 | 134.4194 | 4.0914 | 32.8542 | 157.1378 | 4.7829 | 32.8542 | 4.939% | 0.020337 | 0.019331 | 154171.9995 | 31533.3232 | 223.914 | 122414.7623 | 154190.404 | 0 | 0 | 154190.404 | 0.005106%
2028 | 280 | 280-24AE | Tier-2 | Tier-2---12 | 4--4 | 2.1642 | 148 | 100% | 365.7885 | 3.145% | 96.42% | 0.4381% | 0.56941 | 0 | 0 | 0.56941 | 0 | 0.49428 | 2.0346 | 0.24294 | 0.49428 | 2.0346 | 0.24294 | 0.57782 | 2.3785 | 0.24294 | 0.1557% | 0.037093 | 0.035257 | 9861.3901 | 49.7133 | 8813.1546 | 998.5222 | 10358.7999 | 0 | 0 | 10358.7999 | 1.878e-05%
2028 | 411 | 411-1873R | Tier-2 | Tier-2---7 | 4--5 | 9.9068 | 758 | 100% | 1857.5393 | 97.83% | 1.797% | 0.3696% | 89.9563 | 0 | 0 | 89.9563 | 0 | 78.0879 | 9.3134 | 8.3845 | 78.0879 | 9.3134 | 8.3845 | 91.2856 | 10.8875 | 8.3845 | 4.843% | 0.04682 | 0.044503 | 39673.886 | 7004.2078 | 901.7535 | 31767.9247 | 39718.6459 | 0 | 0 | 39718.6459 | 0.002966%
2028 | 1072 | 1072-6 | Tier-1 | Non-HFTD---1 | 3--4 | 0.23504 | 5 | 100% | 193.6121 | 0.3692% | 99.58% | 0.05199% | 0.035387 | 0 | 0 | 0.035387 | 0 | 0.030718 | 0.22096 | 0.13902 | 0.030718 | 0.22096 | 0.13902 | 0.03591 | 0.2583 | 0.13902 | 0.01828% | 0.01694 | 0.016102 | 11429.1521 | 20.5352 | 10413.4738 | 995.1431 | 12022.16 | 0 | 0 | 12022.16 | 1.167e-06%
2028 | 215 | 215-1534R | Tier-2 | Tier-2---1 | 5--5 | 7.8127 | 466 | 100% | 19489.7064 | 99% | 0.9737% | 0.02962% | 955.0614 | 0 | 0 | 955.0614 | 0 | 829.0555 | 7.3447 | 112.8782 | 829.0555 | 7.3447 | 112.8782 | 969.1753 | 8.586 | 112.8782 | 4.9% | 0.1982 | 0.18839 | 98331.2515 | 17803.4226 | 882.3499 | 79645.479 | 98382.6286 | 0 | 0 | 98382.6286 | 0.03149%
2028 | CD1 | CB CD1 | Tier-1 | Non-HFTD---7 | 3--3 | 1.308 | 51 | 100% | 43.6009 | 1.546% | 95.78% | 2.676% | 0.033356 | 0 | 0 | 0.033356 | 0 | 0.028955 | 1.2296 | 0.023548 | 0.028955 | 1.2296 | 0.023548 | 0.033849 | 1.4375 | 0.023548 | 0.0765% | 0.014488 | 0.01377 | 3009.5292 | 3.7078 | 2622.1215 | 383.7 | 3163.8368 | 0 | 0 | 3163.8368 | 1.1e-06%
2028 | 1073 | 1073-887F | Tier-2 | Tier-2---21 | 3--1 | 0.049053 | 4 | 100% | 6.3934 | 34.35% | 64.55% | 1.103% | 0.10871 | 0 | 0 | 0.10871 | 0 | 0.094363 | 0.046115 | 2.0463 | 0.094363 | 0.046115 | 2.0463 | 0.11031 | 0.053909 | 2.0463 | 1.7% | 0.016639 | 0.015815 | 384.2398 | 21.9164 | 213.9745 | 148.3489 | 397.3768 | 0 | 0 | 397.3768 | 3.585e-06%
2028 | 434 | CB 434 | Tier-1 | Non-HFTD---11 | 1--4 | 0.56686 | 54 | 100% | 12.9164 | 95.4% | 0% | 4.605% | 0.60992 | 0 | 0 | 0.60992 | 0 | 0.52945 | 0.5329 | 0.99353 | 0.52945 | 0.5329 | 0.99353 | 0.61894 | 0.62297 | 0.99353 | 4.722% | 0.0024398 | 0.002319 | 5294.056 | 339.8058 | 2981.8904 | 1972.3599 | 5306.7514 | 0 | 0 | 5306.7514 | 2.011e-05%
2028 | 60 | 60-603F | Tier-1 | Non-HFTD---3 | 4--4 | 6.0002 | 140 | 100% | 169.5135 | 9.049% | 88.6% | 2.35% | 0.75926 | 0 | 0 | 0.75926 | 0 | 0.65909 | 5.6408 | 0.11684 | 0.65909 | 5.6408 | 0.11684 | 0.77048 | 6.5941 | 0.11684 | 0.4479% | 0.032694 | 0.031076 | 5184.8494 | 70.8257 | 4426.3803 | 687.6434 | 5430.4326 | 0 | 0 | 5430.4326 | 2.504e-05%
2028 | 282 | 282-565F | Tier-1 | Non-HFTD---6 | 4--3 | 0.85098 | 17 | 100% | 89.9778 | 0.4154% | 98.82% | 0.7661% | 0.018499 | 0 | 0 | 0.018499 | 0 | 0.016059 | 0.80001 | 0.020073 | 0.016059 | 0.80001 | 0.020073 | 0.018773 | 0.93522 | 0.020073 | 0.02056% | 0.032683 | 0.031065 | 2753.0459 | 5.5294 | 2228.0176 | 519.4989 | 2895.8231 | 0 | 0 | 2895.8231 | 6.1e-07%
2028 | 1458 | 1458-1058F | Tier-3 | Tier-3---13 | 5--5 | 1.4693 | 17 | 100% | 2365.6896 | 85.54% | 14.42% | 0.04244% | 100.1661 | 0 | 0 | 100.1661 | 0 | 86.9507 | 1.3813 | 62.9494 | 86.9507 | 1.3813 | 62.9494 | 101.6464 | 1.6147 | 62.9494 | 4.234% | 0.13833 | 0.13149 | 17101.412 | 2623.0697 | 2234.5189 | 12243.8234 | 17230.2132 | 0 | 0 | 17230.2132 | 0.003303%
2028 | 38 | 38-11 | Tier-1 | Non-HFTD---10 | 4--2 | 9.7832 | 399 | 100% | 25.7057 | 75.43% | 0% | 24.57% | 0.95975 | 0 | 0 | 0.95975 | 0 | 0.83313 | 9.1972 | 0.090585 | 0.83313 | 9.1972 | 0.090585 | 0.97394 | 10.7516 | 0.090585 | 3.734% | 0.028609 | 0.027193 | 898.5174 | 56.9208 | 481.0436 | 360.553 | 910.0159 | 0 | 0 | 910.0159 | 3.165e-05%
2028 | 921 | 921-800F | Tier-2 | Tier-2---7 | 4--5 | 5.8841 | 510 | 100% | 1991.7107 | 76.61% | 23.16% | 0.2301% | 75.5258 | 0 | 0 | 75.5258 | 0 | 65.5614 | 5.5316 | 11.8521 | 65.5614 | 5.5316 | 11.8521 | 76.642 | 6.4665 | 11.8521 | 3.792% | 0.065336 | 0.062102 | 30484.0304 | 5417.7742 | 6386.3527 | 18679.9035 | 30855.4164 | 0 | 0 | 30855.4164 | 0.002491%
2028 | 43 | 43-445 | Tier-1 | Non-HFTD---10 | 4--2 | 11.0882 | 259 | 100% | 17.7138 | 50.11% | 0% | 49.89% | 0.43939 | 0 | 0 | 0.43939 | 0 | 0.38142 | 10.4241 | 0.036591 | 0.38142 | 10.4241 | 0.036591 | 0.44589 | 12.1859 | 0.036591 | 2.481% | 0.033392 | 0.031739 | 530.477 | 16.8718 | 186.6503 | 326.9548 | 544.2593 | 0 | 0 | 544.2593 | 1.449e-05%
2028 | 297 | CB 297 | Tier-2 | Tier-2---19 | 1--3 | 0.42898 | 9 | 100% | 7.4286 | 94.8% | 0% | 5.203% | 0.34859 | 0 | 0 | 0.34859 | 0 | 0.30259 | 0.40328 | 0.75033 | 0.30259 | 0.40328 | 0.75033 | 0.35374 | 0.47144 | 0.75033 | 4.692% | 0.0019588 | 0.0018618 | 3792.4284 | 350.5573 | 1464.3094 | 1977.5617 | 3802.7036 | 0 | 0 | 3802.7036 | 1.15e-05%
2028 | 1166 | 1166-342R | Tier-3 | Tier-3---5 | 5--5 | 11.5801 | 478 | 100% | 10322.642 | 99.08% | 0.8619% | 0.05733% | 506.2736 | 0 | 0 | 506.2736 | 0 | 439.4785 | 10.8865 | 40.3693 | 439.4785 | 10.8865 | 40.3693 | 513.7554 | 12.7264 | 40.3693 | 4.904% | 0.21878 | 0.20795 | 47183.5693 | 7440.5956 | 374.9584 | 39368.0153 | 47206.1577 | 0 | 0 | 47206.1577 | 0.0167%
2028 | 441 | CB 441 | Tier-3 | Tier-3---15 | 5--3 | 6.0637 | 149 | 100% | 1133.0808 | 94.08% | 5.666% | 0.2577% | 52.7648 | 0 | 0 | 52.7648 | 0 | 45.8033 | 5.7004 | 8.035 | 45.8033 | 5.7004 | 8.035 | 53.5446 | 6.6639 | 8.035 | 4.657% | 0.54555 | 0.51854 | 2076.9658 | 210.0359 | 105.6276 | 1761.3022 | 2083.3735 | 0 | 0 | 2083.3735 | 0.00174%
2028 | 1030 | 1030-989R | Tier-3 | Tier-3---3 | 5--5 | 19.582 | 1188 | 100% | 26696.2161 | 99.16% | 0.796% | 0.04527% | 1310.3453 | 0 | 0 | 1310.3453 | 0 | 1137.4651 | 18.409 | 61.7884 | 1137.4651 | 18.409 | 61.7884 | 1329.7097 | 21.5204 | 61.7884 | 4.908% | 0.30703 | 0.29183 | 86951.1078 | 14407.8405 | 617.0271 | 71926.2402 | 86989.2036 | 0 | 0 | 86989.2036 | 0.04321%
2028 | 1071 | 1071-226F | Tier-1 | Non-HFTD---9 | 1--4 | 0.36818 | 42 | 100% | 15.0528 | 98.32% | 0% | 1.683% | 0.73257 | 0 | 0 | 0.73257 | 0 | 0.63592 | 0.34613 | 1.8372 | 0.63592 | 0.34613 | 1.8372 | 0.7434 | 0.40463 | 1.8372 | 4.867% | 0.0017068 | 0.0016223 | 8819.3233 | 1269.9582 | 917.792 | 6631.5731 | 8827.0536 | 0 | 0 | 8827.0536 | 2.416e-05%
2028 | 331 | CB 331 | Tier-2 | Tier-2---14 | 2--5 | 2.8949 | 3 | 100% | 261.2105 | 99.38% | 0% | 0.6196% | 12.8498 | 0 | 0 | 12.8498 | 0 | 11.1545 | 2.7215 | 4.0987 | 11.1545 | 2.7215 | 4.0987 | 13.0397 | 3.1814 | 4.0987 | 4.919% | 0.010352 | 0.0098396 | 25232.8512 | 3536.4388 | 3219.2744 | 18477.138 | 25240.9927 | 0 | 0 | 25240.9927 | 0.0004237%
2028 | 920 | CB 920 | Tier-1 | Non-HFTD---1 | 1--5 | 0.96496 | 63 | 100% | 251.9037 | 99.78% | 0% | 0.2231% | 12.4414 | 0 | 0 | 12.4414 | 0 | 10.8 | 0.90716 | 11.9052 | 10.8 | 0.90716 | 11.9052 | 12.6253 | 1.0605 | 11.9052 | 4.939% | 0.0036978 | 0.0035148 | 68122.5856 | 11982.8045 | 3000.2837 | 53139.4975 | 68130.5015 | 0 | 0 | 68130.5015 | 0.0004103%
2028 | 220 | 220-298R | Tier-3 | Tier-3---11 | 5--4 | 33.1318 | 3002 | 100% | 3585.6314 | 89.37% | 10.06% | 0.5685% | 158.6214 | 0 | 0 | 158.6214 | 0 | 137.6937 | 31.1472 | 4.4207 | 137.6937 | 31.1472 | 4.4207 | 160.9655 | 36.4115 | 4.4207 | 4.424% | 0.50177 | 0.47693 | 7145.9975 | 838.8497 | 642.3981 | 5664.7497 | 7185.5575 | 0 | 0 | 7185.5575 | 0.005231%
2028 | 243 | 243-14R | Tier-2 | Tier-2---11 | 4--4 | 13.05 | 653 | 100% | 404.2589 | 29.5% | 68.39% | 2.113% | 5.9029 | 0 | 0 | 5.9029 | 0 | 5.1241 | 12.2683 | 0.41767 | 5.1241 | 12.2683 | 0.41767 | 5.9901 | 14.3418 | 0.41767 | 1.46% | 0.066445 | 0.063156 | 6084.1314 | 280.7794 | 3933.5085 | 1869.8435 | 6307.5143 | 0 | 0 | 6307.5143 | 0.0001947%
2028 | OH1 | CB OH1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.2021 | 28 | 100% | 1.3845 | 20.15% | 0% | 79.85% | 0.013811 | 0 | 0 | 0.013811 | 0 | 0.011989 | 1.1301 | 0.010609 | 0.011989 | 1.1301 | 0.010609 | 0.014015 | 1.3211 | 0.010609 | 0.9975% | 0.003942 | 0.0037469 | 351.2235 | 0.21102 | 96.2554 | 254.7571 | 365.8284 | 0 | 0 | 365.8284 | 4.554e-07%
2028 | PH1 | CB PH1 | Tier-1 | Non-HFTD---18 | 1--1 | 0.61361 | 30 | 100% | 0.70429 | 28.38% | 0% | 71.62% | 0.0098948 | 0 | 0 | 0.0098948 | 0 | 0.0085893 | 0.57685 | 0.01489 | 0.0085893 | 0.57685 | 0.01489 | 0.010041 | 0.67435 | 0.01489 | 1.405% | 0.0018738 | 0.001781 | 375.86 | 13.3825 | 50.7092 | 311.7684 | 389.8784 | 0 | 0 | 389.8784 | 3.263e-07%
2028 | 289 | 289-905AE | Tier-1 | Non-HFTD---8 | 3--3 | 4.6523 | 300 | 100% | 40.9452 | 16.44% | 75.92% | 7.645% | 0.33316 | 0 | 0 | 0.33316 | 0 | 0.2892 | 4.3736 | 0.066124 | 0.2892 | 4.3736 | 0.066124 | 0.33808 | 5.1128 | 0.066124 | 0.8137% | 0.0188 | 0.01787 | 2177.8917 | 8.1279 | 1808.1136 | 361.6502 | 2272.6681 | 0 | 0 | 2272.6681 | 1.099e-05%
2028 | 520 | 520-35R | Tier-3 | Tier-3---9 | 5--5 | 14.3572 | 1792 | 100% | 4997.7942 | 96.49% | 3.313% | 0.193% | 238.7183 | 0 | 0 | 238.7183 | 0 | 207.223 | 13.4972 | 15.353 | 207.223 | 13.4972 | 15.353 | 242.246 | 15.7784 | 15.353 | 4.776% | 0.28544 | 0.27131 | 17509.0395 | 2720.8213 | 525.8469 | 14262.3712 | 17541.0048 | 0 | 0 | 17541.0048 | 0.007872%
2028 | 154 | 154-894R | Tier-1 | Non-HFTD---14 | 3--1 | 8.141 | 246 | 100% | 8.6688 | 30.94% | 0% | 69.06% | 0.13274 | 0 | 0 | 0.13274 | 0 | 0.11523 | 7.6533 | 0.015056 | 0.11523 | 7.6533 | 0.015056 | 0.13471 | 8.9468 | 0.015056 | 1.531% | 0.023715 | 0.022541 | 365.5396 | 2.5977 | 126.4957 | 236.4462 | 378.6872 | 0 | 0 | 378.6872 | 4.377e-06%
2028 | 443 | CB 443 | Tier-2 | Tier-2---17 | 2--4 | 1.7657 | 0 | 100% | 67.1473 | 98.29% | 0% | 1.71% | 3.2669 | 0 | 0 | 3.2669 | 0 | 2.8359 | 1.66 | 1.7084 | 2.8359 | 1.66 | 1.7084 | 3.3152 | 1.9405 | 1.7084 | 4.865% | 0.007405 | 0.0070385 | 9067.8323 | 1863.6752 | 20.0371 | 7184.12 | 9075.9094 | 0 | 0 | 9075.9094 | 0.0001077%
2028 | 311 | 311-43 | Tier-2 | Tier-2---15 | 3--4 | 4.1521 | 373 | 100% | 159.8581 | 2.339% | 95.81% | 1.853% | 0.18508 | 0 | 0 | 0.18508 | 0 | 0.16067 | 3.9034 | 0.04116 | 0.16067 | 3.9034 | 0.04116 | 0.18782 | 4.5631 | 0.04116 | 0.1158% | 0.027937 | 0.026554 | 5722.0498 | 17.0566 | 5016.8041 | 688.1891 | 6013.0719 | 0 | 0 | 6013.0719 | 6.103e-06%
2028 | 707 | CB 707 | Tier-1 | Non-HFTD---9 | 2--3 | 0.76856 | 33 | 100% | 24.2722 | 35% | 62.06% | 2.94% | 0.42051 | 0 | 0 | 0.42051 | 0 | 0.36503 | 0.72252 | 0.50522 | 0.36503 | 0.72252 | 0.50522 | 0.42673 | 0.84464 | 0.50522 | 1.732% | 0.0080484 | 0.00765 | 3015.7851 | 147.2421 | 1865.593 | 1002.95 | 3117.8717 | 0 | 0 | 3117.8717 | 1.387e-05%
2028 | 1001 | 1001-1130R | Tier-2 | Tier-2---5 | 5--5 | 3.7048 | 795 | 100% | 2758.283 | 96.49% | 3.415% | 0.0991% | 131.7366 | 0 | 0 | 131.7366 | 0 | 114.3559 | 3.4829 | 32.8339 | 114.3559 | 3.4829 | 32.8339 | 133.6834 | 4.0715 | 32.8339 | 4.776% | 0.10617 | 0.10091 | 25980.7036 | 4080.9848 | 853.5333 | 21046.1854 | 26028.2544 | 0 | 0 | 26028.2544 | 0.004344%
2028 | 547 | 547-22R | Tier-1 | Non-HFTD---13 | 2--2 | 3.5843 | 62 | 100% | 7.8544 | 68.58% | 0% | 31.42% | 0.26665 | 0 | 0 | 0.26665 | 0 | 0.23147 | 3.3696 | 0.068694 | 0.23147 | 3.3696 | 0.068694 | 0.27059 | 3.9391 | 0.068694 | 3.395% | 0.010488 | 0.009969 | 748.881 | 11.7437 | 463.65 | 273.4873 | 761.1333 | 0 | 0 | 761.1333 | 8.793e-06%
2028 | 78 | 78-35R | Tier-3 | Tier-3---10 | 2--5 | 1.532 | 0 | 100% | 5696.3358 | 99.98% | 0% | 0.01771% | 281.9187 | 0 | 0 | 281.9187 | 0 | 244.7238 | 1.4402 | 169.9186 | 244.7238 | 1.4402 | 169.9186 | 286.0849 | 1.6837 | 169.9186 | 4.949% | 0.008188 | 0.0077827 | 695693.1861 | 112288.7116 | 42.5016 | 583361.9729 | 695699.6035 | 0 | 0 | 695699.6035 | 0.009297%
2028 | 452 | CB 452 | Tier-1 | Non-HFTD---10 | 3--2 | 7.2271 | 173 | 100% | 25.8874 | 80.5% | 0% | 19.5% | 1.0316 | 0 | 0 | 1.0316 | 0 | 0.89547 | 6.7942 | 0.1318 | 0.89547 | 6.7942 | 0.1318 | 1.0468 | 7.9425 | 0.1318 | 3.985% | 0.020795 | 0.019766 | 1244.886 | 0.18265 | 1024.2061 | 220.4972 | 1257.5268 | 0 | 0 | 1257.5268 | 3.402e-05%
2028 | 731 | 731-1245F | Tier-1 | Non-HFTD---17 | 1--2 | 0.46347 | 27 | 100% | 1.7231 | 81.35% | 0% | 18.65% | 0.06939 | 0 | 0 | 0.06939 | 0 | 0.060235 | 0.4357 | 0.13825 | 0.060235 | 0.4357 | 0.13825 | 0.070416 | 0.50934 | 0.13825 | 4.027% | 0.0013412 | 0.0012748 | 1284.744 | 169.7674 | 30.9305 | 1084.0462 | 1297.2191 | 0 | 0 | 1297.2191 | 2.288e-06%
2028 | 556 | CB 556 | Tier-1 | Non-HFTD---1 | 2--5 | 1.5472 | 11 | 100% | 422.664 | 99.75% | 0% | 0.2546% | 20.8686 | 0 | 0 | 20.8686 | 0 | 18.1153 | 1.4545 | 12.4548 | 18.1153 | 1.4545 | 12.4548 | 21.177 | 1.7003 | 12.4548 | 4.937% | 0.0069694 | 0.0066244 | 60645.6807 | 39316.7744 | 1050.0285 | 20278.8779 | 60653.7228 | 0 | 0 | 60653.7228 | 0.0006882%
2028 | 723 | CB 723 | Tier-1 | Non-HFTD---10 | 3--2 | 5.7311 | 124 | 100% | 19.8762 | 84.22% | 0% | 15.78% | 0.82858 | 0 | 0 | 0.82858 | 0 | 0.71926 | 5.3878 | 0.1335 | 0.71926 | 5.3878 | 0.1335 | 0.84083 | 6.2984 | 0.1335 | 4.169% | 0.01527 | 0.014514 | 1301.6828 | 11.1848 | 1047.4878 | 243.0102 | 1312.3823 | 0 | 0 | 1312.3823 | 2.732e-05%
2028 | 401 | 401-39R | Tier-2 | Tier-2---14 | 4--4 | 0.64865 | 64 | 100% | 323.2323 | 3.193% | 96.7% | 0.1048% | 0.51091 | 0 | 0 | 0.51091 | 0 | 0.4435 | 0.6098 | 0.72729 | 0.4435 | 0.6098 | 0.72729 | 0.51846 | 0.71286 | 0.72729 | 0.1581% | 0.031872 | 0.030295 | 10141.4477 | 77.0794 | 9013.6522 | 1050.7162 | 10652.728 | 0 | 0 | 10652.728 | 1.685e-05%
2028 | 449 | 449-6R | Tier-3 | Tier-3---14 | 5--4 | 5.3305 | 262 | 100% | 2320.0162 | 95.55% | 4.318% | 0.1352% | 109.7271 | 0 | 0 | 109.7271 | 0 | 95.2503 | 5.0112 | 19.0075 | 95.2503 | 5.0112 | 19.0075 | 111.3487 | 5.8582 | 19.0075 | 4.73% | 0.24779 | 0.23552 | 9362.9076 | 1355.2687 | 401.1593 | 7606.4796 | 9384.6196 | 0 | 0 | 9384.6196 | 0.003618%
2028 | EO1 | CB EO1 | Tier-1 | Non-HFTD---10 | 3--2 | 8.4572 | 310 | 100% | 23.8797 | 77.35% | 0% | 22.65% | 0.91436 | 0 | 0 | 0.91436 | 0 | 0.79372 | 7.9506 | 0.099831 | 0.79372 | 7.9506 | 0.099831 | 0.92787 | 9.2944 | 0.099831 | 3.829% | 0.022403 | 0.021294 | 1065.904 | 118.5711 | 123.3524 | 823.9805 | 1078.4747 | 0 | 0 | 1078.4747 | 3.015e-05%
2028 | 416 | 416-21 | Tier-1 | Non-HFTD---9 | 2--3 | 2.1076 | 56 | 100% | 17.0536 | 88.2% | 0% | 11.8% | 0.74451 | 0 | 0 | 0.74451 | 0 | 0.64629 | 1.9813 | 0.32619 | 0.64629 | 1.9813 | 0.32619 | 0.75552 | 2.3162 | 0.32619 | 4.366% | 0.0069518 | 0.0066077 | 2453.1267 | 2.6942 | 2174.6936 | 275.7389 | 2468.2065 | 0 | 0 | 2468.2065 | 2.455e-05%
2028 | 210 | 210-172R | Tier-2 | Tier-2---11 | 5--2 | 6.4924 | 212 | 100% | 498.1496 | 90.1% | 9.186% | 0.7154% | 22.2168 | 0 | 0 | 22.2168 | 0 | 19.2857 | 6.1035 | 3.1598 | 19.2857 | 6.1035 | 3.1598 | 22.5452 | 7.1351 | 3.1598 | 4.46% | 0.32588 | 0.30975 | 1528.6439 | 130.0935 | 126.0496 | 1272.5007 | 1536.5263 | 0 | 0 | 1536.5263 | 0.0007326%
2028 | 73 | 73-1163 | Tier-3 | Tier-3---4 | 5--5 | 11.2661 | 731 | 100% | 15337.1849 | 98.56% | 1.393% | 0.04595% | 748.2657 | 0 | 0 | 748.2657 | 0 | 649.5434 | 10.5913 | 61.3281 | 649.5434 | 10.5913 | 61.3281 | 759.3236 | 12.3813 | 61.3281 | 4.879% | 0.22506 | 0.21392 | 68145.9431 | 11285.6081 | 934.2701 | 55926.0649 | 68197.0126 | 0 | 0 | 68197.0126 | 0.02468%
2028 | 305 | 305-35R | Tier-1 | Non-HFTD---1 | 4--5 | 5.5248 | 1388 | 100% | 2371.786 | 97.71% | 2.108% | 0.1806% | 114.7166 | 0 | 0 | 114.7166 | 0 | 99.5815 | 5.1939 | 19.1728 | 99.5815 | 5.1939 | 19.1728 | 116.4119 | 6.0717 | 19.1728 | 4.837% | 0.074138 | 0.070468 | 31991.6747 | 5091.6051 | 638.7369 | 26261.3327 | 32029.8024 | 0 | 0 | 32029.8024 | 0.003783%
2028 | 458 | 458-43F | Tier-1 | Non-HFTD---16 | 2--1 | 1.8401 | 69 | 100% | 2.2689 | 42.12% | 0% | 57.88% | 0.047309 | 0 | 0 | 0.047309 | 0 | 0.041068 | 1.7299 | 0.023739 | 0.041068 | 1.7299 | 0.023739 | 0.048008 | 2.0223 | 0.023739 | 2.085% | 0.0053162 | 0.005053 | 426.7836 | 1.0552 | 196.9069 | 228.8215 | 439.647 | 0 | 0 | 439.647 | 1.56e-06%
2028 | 74 | CB 74 | Tier-1 | Non-HFTD---10 | 3--2 | 6.9906 | 197 | 100% | 19.9911 | 76.58% | 0% | 23.42% | 0.75785 | 0 | 0 | 0.75785 | 0 | 0.65786 | 6.5718 | 0.1001 | 0.65786 | 6.5718 | 0.1001 | 0.76905 | 7.6826 | 0.1001 | 3.791% | 0.019147 | 0.018199 | 1044.0736 | 1.8204 | 811.7883 | 230.4649 | 1056.8053 | 0 | 0 | 1056.8053 | 2.499e-05%
2028 | SC2 | CB SC2 | Tier-1 | Non-HFTD---2 | 4--4 | 7.0339 | 233 | 100% | 261.4516 | 2.208% | 95.93% | 1.858% | 0.28577 | 0 | 0 | 0.28577 | 0 | 0.24807 | 6.6126 | 0.037514 | 0.24807 | 6.6126 | 0.037514 | 0.28999 | 7.7302 | 0.037514 | 0.1093% | 0.037006 | 0.035174 | 7065.0763 | 7.3313 | 6299.5139 | 758.2311 | 7424.8859 | 0 | 0 | 7424.8859 | 9.424e-06%
2028 | 529 | CB 529 | Tier-1 | Non-HFTD---7 | 2--3 | 2.3037 | 55 | 100% | 27.2988 | 93.37% | 0% | 6.628% | 1.2617 | 0 | 0 | 1.2617 | 0 | 1.0953 | 2.1658 | 0.50572 | 1.0953 | 2.1658 | 0.50572 | 1.2804 | 2.5318 | 0.50572 | 4.622% | 0.0089244 | 0.0084826 | 3058.8995 | 429.8777 | 198.033 | 2430.9888 | 3069.4573 | 0 | 0 | 3069.4573 | 4.161e-05%
2028 | 1161 | CB 1161 | Tier-2 | Tier-2---20 | 4--1 | 0.90625 | 0 | 100% | 18.2465 | 16.87% | 78.76% | 4.376% | 0.15233 | 0 | 0 | 0.15233 | 0 | 0.13223 | 0.85197 | 0.1552 | 0.13223 | 0.85197 | 0.1552 | 0.15458 | 0.99596 | 0.1552 | 0.8348% | 0.061771 | 0.058714 | 295.3886 | 6.838 | 193.9385 | 94.612 | 308.1774 | 0 | 0 | 308.1774 | 5.023e-06%
2028 | 212 | 212-1204R | Tier-2 | Tier-2---8 | 5--4 | 10.0072 | 279 | 100% | 1570.3762 | 94.97% | 4.642% | 0.3849% | 73.8258 | 0 | 0 | 73.8258 | 0 | 64.0856 | 9.4078 | 6.812 | 64.0856 | 9.4078 | 6.812 | 74.9168 | 10.9978 | 6.812 | 4.701% | 0.19221 | 0.18269 | 8170.2767 | 1029.897 | 370.2708 | 6770.1089 | 8191.6669 | 0 | 0 | 8191.6669 | 0.002435%
2028 | 34 | CB 34 | Tier-1 | Non-HFTD---19 | 1--1 | 0.1034 | 3 | 100% | 0.13232 | 2.437% | 0% | 97.56% | 0.00015964 | 0 | 0 | 0.00015964 | 0 | 0.00013858 | 0.097202 | 0.0014257 | 0.00013858 | 0.097202 | 0.0014257 | 0.000162 | 0.11363 | 0.0014257 | 0.1206% | 0.0003968 | 0.00037716 | 333.478 | 0.37096 | 36.9115 | 296.1955 | 350.4215 | 0 | 0 | 350.4215 | 5.264e-09%
2028 | 190 | 190-1122F | Tier-1 | Non-HFTD---9 | 1--4 | 0.44692 | 22 | 100% | 22.2623 | 98.77% | 0% | 1.233% | 1.0884 | 0 | 0 | 1.0884 | 0 | 0.9448 | 0.42015 | 2.2487 | 0.9448 | 0.42015 | 2.2487 | 1.1045 | 0.49116 | 2.2487 | 4.889% | 0.001452 | 0.0013801 | 15332.18 | 2415.7745 | 19.2027 | 12897.2028 | 15342.0229 | 0 | 0 | 15342.0229 | 3.589e-05%
2028 | 909 | 909-812 | Tier-2 | Tier-2---17 | 1--5 | 0.023485 | 0 | 100% | 62.9838 | 99.88% | 0% | 0.1185% | 3.114 | 0 | 0 | 3.114 | 0 | 2.7032 | 0.022078 | 122.4361 | 2.7032 | 0.022078 | 122.4361 | 3.16 | 0.02581 | 122.4361 | 4.944% | 0.0001786 | 0.00016976 | 352652.9396 | 56837.6366 | 442.6032 | 295372.6998 | 352674.6938 | 0 | 0 | 352674.6938 | 0.0001027%
2028 | 239 | 239-2207R | Tier-3 | Tier-3---16 | 4--4 | 6.8952 | 718 | 100% | 860.3234 | 98.08% | 1.495% | 0.4234% | 41.7689 | 0 | 0 | 41.7689 | 0 | 36.2581 | 6.4822 | 5.5935 | 36.2581 | 6.4822 | 5.5935 | 42.3861 | 7.5778 | 5.5935 | 4.855% | 0.078224 | 0.074352 | 10998.2588 | 1887.5765 | 146.4219 | 8964.2604 | 11009.2492 | 0 | 0 | 11009.2492 | 0.001377%
2028 | 963 | 963-35 | Tier-1 | Non-HFTD---7 | 2--3 | 3.1555 | 180 | 100% | 30.7376 | 94.18% | 0% | 5.818% | 1.433 | 0 | 0 | 1.433 | 0 | 1.2439 | 2.9665 | 0.41933 | 1.2439 | 2.9665 | 0.41933 | 1.4542 | 3.4679 | 0.41933 | 4.662% | 0.012897 | 0.012259 | 2383.2808 | 325.3782 | 213.264 | 1844.6386 | 2390.5024 | 0 | 0 | 2390.5024 | 4.725e-05%
2028 | 303 | 303-189AE | Tier-1 | Non-HFTD---3 | 4--4 | 8.0475 | 408 | 100% | 171.0034 | 3.397% | 93.81% | 2.795% | 0.28756 | 0 | 0 | 0.28756 | 0 | 0.24962 | 7.5655 | 0.032994 | 0.24962 | 7.5655 | 0.032994 | 0.2918 | 8.8442 | 0.032994 | 0.1682% | 0.032667 | 0.03105 | 5234.7139 | 12.8116 | 4649.2999 | 572.6024 | 5498.0656 | 0 | 0 | 5498.0656 | 9.483e-06%
2028 | 1082 | CB 1082 | Tier-1 | Non-HFTD---10 | 3--2 | 1.1544 | 45 | 100% | 15.7927 | 61.51% | 33.76% | 4.733% | 0.48084 | 0 | 0 | 0.48084 | 0 | 0.4174 | 1.0852 | 0.38462 | 0.4174 | 1.0852 | 0.38462 | 0.48794 | 1.2686 | 0.38462 | 3.045% | 0.014222 | 0.013518 | 1110.4405 | 109.3438 | 313.5434 | 687.5533 | 1132.6997 | 0 | 0 | 1132.6997 | 1.586e-05%
2028 | 740 | 740-857F | Tier-1 | Non-HFTD---19 | 1--1 | 0.23295 | 18 | 100% | 0.392 | 20.4% | 0% | 79.6% | 0.0039577 | 0 | 0 | 0.0039577 | 0 | 0.0034355 | 0.219 | 0.015687 | 0.0034355 | 0.219 | 0.015687 | 0.0040162 | 0.25601 | 0.015687 | 1.01% | 0.0010222 | 0.0009716 | 383.4881 | 10.7399 | 40.9688 | 331.7794 | 399.386 | 0 | 0 | 399.386 | 1.305e-07%
2028 | 61 | 61-13F | Tier-1 | Non-HFTD---5 | 3--3 | 1.5653 | 221 | 100% | 66.9136 | 1.1% | 96.65% | 2.249% | 0.036446 | 0 | 0 | 0.036446 | 0 | 0.031637 | 1.4715 | 0.021499 | 0.031637 | 1.4715 | 0.021499 | 0.036984 | 1.7203 | 0.021499 | 0.05447% | 0.016091 | 0.015295 | 4158.3434 | 4.7662 | 3732.5049 | 421.0723 | 4372.5181 | 0 | 0 | 4372.5181 | 1.202e-06%
2028 | 159 | 159-1010F | Tier-1 | Non-HFTD---20 | 1--1 | 0.18916 | 14 | 100% | 0.072864 | 14.16% | 0% | 85.84% | 0.00051071 | 0 | 0 | 0.00051071 | 0 | 0.00044333 | 0.17783 | 0.002493 | 0.00044333 | 0.17783 | 0.002493 | 0.00051826 | 0.20788 | 0.002493 | 0.7009% | 0.0003894 | 0.00037012 | 187.1198 | 0.12086 | 41.0868 | 145.9122 | 195.4848 | 0 | 0 | 195.4848 | 1.684e-08%
2028 | 855 | CB 855 | Tier-1 | Non-HFTD---1 | 2--5 | 3.5599 | 173 | 100% | 270.5618 | 99.37% | 0% | 0.6324% | 13.3081 | 0 | 0 | 13.3081 | 0 | 11.5523 | 3.3466 | 3.4519 | 11.5523 | 3.3466 | 3.4519 | 13.5048 | 3.9122 | 3.4519 | 4.919% | 0.01085 | 0.010313 | 24937.4896 | 3437.8657 | 3656.8715 | 17842.7524 | 24945.7025 | 0 | 0 | 24945.7025 | 0.0004389%
2028 | RV1 | CB RV1 | Tier-1 | Non-HFTD---14 | 3--1 | 7.5803 | 408 | 100% | 5.6011 | 21.45% | 0% | 78.55% | 0.059471 | 0 | 0 | 0.059471 | 0 | 0.051625 | 7.1262 | 0.0072444 | 0.051625 | 7.1262 | 0.0072444 | 0.06035 | 8.3306 | 0.0072444 | 1.062% | 0.019991 | 0.019001 | 280.18 | 0.1656 | 80.0914 | 199.9231 | 291.6414 | 0 | 0 | 291.6414 | 1.961e-06%
2028 | 1233 | 1233-587R | Tier-3 | Tier-3---13 | 5--5 | 7.6085 | 805 | 100% | 2983.7291 | 97.9% | 1.929% | 0.1696% | 144.5958 | 0 | 0 | 144.5958 | 0 | 125.5186 | 7.1528 | 17.5482 | 125.5186 | 7.1528 | 17.5482 | 146.7327 | 8.3617 | 17.5482 | 4.846% | 0.13489 | 0.12821 | 22120.1137 | 3552.0723 | 402.3722 | 18165.6692 | 22144.283 | 0 | 0 | 22144.283 | 0.004768%
2028 | 777 | 777-10 | Tier-1 | Non-HFTD---19 | 1--2 | 0.1028 | 0 | 100% | 0.21948 | 49.99% | 0% | 50.01% | 0.0054313 | 0 | 0 | 0.0054313 | 0 | 0.0047147 | 0.09664 | 0.048787 | 0.0047147 | 0.09664 | 0.048787 | 0.0055116 | 0.11297 | 0.048787 | 2.475% | 0.0003706 | 0.00035226 | 592.216 | 47.9707 | 27.3549 | 516.8903 | 607.6387 | 0 | 0 | 607.6387 | 1.791e-07%
2028 | 87 | CB 87 | Tier-1 | Non-HFTD---14 | 3--1 | 6.3328 | 197 | 100% | 8.2544 | 42.74% | 0% | 57.26% | 0.17463 | 0 | 0 | 0.17463 | 0 | 0.15159 | 5.9535 | 0.025463 | 0.15159 | 5.9535 | 0.025463 | 0.17721 | 6.9597 | 0.025463 | 2.116% | 0.018391 | 0.017481 | 448.8306 | 2.7145 | 199.6816 | 246.4345 | 462.2148 | 0 | 0 | 462.2148 | 5.759e-06%
2028 | 363 | CB 363 | Tier-1 | Non-HFTD---5 | 3--4 | 3.2214 | 67 | 100% | 93.3136 | 5.828% | 91.17% | 3.003% | 0.26918 | 0 | 0 | 0.26918 | 0 | 0.23367 | 3.0285 | 0.077157 | 0.23367 | 3.0285 | 0.077157 | 0.27316 | 3.5403 | 0.077157 | 0.2885% | 0.014683 | 0.013956 | 6355.3857 | 6.7587 | 5611.6916 | 736.9354 | 6667.0722 | 0 | 0 | 6667.0722 | 8.877e-06%
2028 | 116 | CB 116 | Tier-1 | Non-HFTD---2 | 4--4 | 7.0256 | 286 | 100% | 265.4697 | 47.19% | 51.3% | 1.507% | 6.2014 | 0 | 0 | 6.2014 | 0 | 5.3832 | 6.6048 | 0.81506 | 5.3832 | 6.6048 | 0.81506 | 6.2931 | 7.721 | 0.81506 | 2.336% | 0.037029 | 0.035196 | 7169.199 | 559.0648 | 4185.9405 | 2424.1937 | 7366.3596 | 0 | 0 | 7366.3596 | 0.0002045%
2028 | 221 | 221-1249R | Tier-1 | Non-HFTD---2 | 5--2 | 25.1976 | 192 | 100% | 329.3718 | 60.93% | 35.44% | 3.632% | 9.9343 | 0 | 0 | 9.9343 | 0 | 8.6237 | 23.6883 | 0.36405 | 8.6237 | 23.6883 | 0.36405 | 10.0811 | 27.6919 | 0.36405 | 3.016% | 0.32343 | 0.30742 | 1018.3674 | 70.1582 | 373.9946 | 574.2146 | 1039.0867 | 0 | 0 | 1039.0867 | 0.0003276%
2028 | 418 | 418-25R | Tier-1 | Non-HFTD---14 | 2--2 | 3.847 | 112 | 100% | 6.5111 | 53.05% | 0% | 46.95% | 0.171 | 0 | 0 | 0.171 | 0 | 0.14844 | 3.6165 | 0.041044 | 0.14844 | 3.6165 | 0.041044 | 0.17352 | 4.2278 | 0.041044 | 2.626% | 0.011457 | 0.01089 | 568.3108 | 3.1871 | 307.4186 | 257.7051 | 582.2048 | 0 | 0 | 582.2048 | 5.639e-06%
2028 | 971 | CB 971 | Tier-2 | Tier-2---3 | 5--5 | 5.1074 | 166 | 100% | 11456.6981 | 99.51% | 0.4569% | 0.03477% | 564.3183 | 0 | 0 | 564.3183 | 0 | 489.8651 | 4.8014 | 102.0247 | 489.8651 | 4.8014 | 102.0247 | 572.6579 | 5.6129 | 102.0247 | 4.926% | 0.12528 | 0.11908 | 91451.3672 | 15599.0846 | 567.0446 | 75285.238 | 91474.7827 | 0 | 0 | 91474.7827 | 0.01861%
2028 | MNR3 | CB MNR3 | Tier-1 | Non-HFTD---8 | 3--2 | 4.6053 | 258 | 100% | 32.2512 | 24.3% | 64.69% | 11.01% | 0.38795 | 0 | 0 | 0.38795 | 0 | 0.33677 | 4.3294 | 0.077786 | 0.33677 | 4.3294 | 0.077786 | 0.39368 | 5.0611 | 0.077786 | 1.203% | 0.019891 | 0.018906 | 1621.3979 | 77.741 | 1023.8427 | 519.8142 | 1685.3173 | 0 | 0 | 1685.3173 | 1.279e-05%
2028 | 313 | 313-920F | Tier-1 | Non-HFTD---10 | 3--2 | 0.7511 | 67 | 100% | 25.9898 | 2.478% | 94.94% | 2.583% | 0.03188 | 0 | 0 | 0.03188 | 0 | 0.027674 | 0.70611 | 0.039192 | 0.027674 | 0.70611 | 0.039192 | 0.032351 | 0.82545 | 0.039192 | 0.1227% | 0.019352 | 0.018394 | 1342.9879 | 6.3375 | 1055.0399 | 281.6105 | 1411.1947 | 0 | 0 | 1411.1947 | 1.051e-06%
2028 | 1138 | 1138-6R | Tier-2 | Tier-2---5 | 5--5 | 19.4272 | 2033 | 100% | 4663.8779 | 91.12% | 8.567% | 0.3106% | 210.367 | 0 | 0 | 210.367 | 0 | 182.6123 | 18.2636 | 9.9987 | 182.6123 | 18.2636 | 9.9987 | 213.4758 | 21.3503 | 9.9987 | 4.511% | 0.17153 | 0.16304 | 27190.5644 | 4666.2669 | 2170.5181 | 20353.7794 | 27316.2731 | 0 | 0 | 27316.2731 | 0.006937%
2028 | 354 | 354-1706R | Tier-2 | Tier-2---1 | 5--5 | 18.9327 | 1474 | 100% | 20510.2592 | 99.17% | 0.7728% | 0.06052% | 1006.7977 | 0 | 0 | 1006.7977 | 0 | 873.9661 | 17.7987 | 49.1028 | 873.9661 | 17.7987 | 49.1028 | 1021.6763 | 20.8069 | 49.1028 | 4.909% | 0.13939 | 0.13249 | 147143.8192 | 29557.6672 | 1212.8556 | 116373.2964 | 147207.6742 | 0 | 0 | 147207.6742 | 0.0332%
2028 | 212 | 212-773R | Tier-2 | Tier-2---5 | 5--4 | 11.8401 | 434 | 100% | 2758.5667 | 95.78% | 3.96% | 0.2633% | 130.7823 | 0 | 0 | 130.7823 | 0 | 113.5276 | 11.1309 | 10.1993 | 113.5276 | 11.1309 | 10.1993 | 132.715 | 13.0122 | 10.1993 | 4.741% | 0.19881 | 0.18897 | 13875.2805 | 1871.421 | 507.3138 | 11496.5456 | 13905.797 | 0 | 0 | 13905.797 | 0.004313%
2028 | 533 | 533-7AE | Tier-1 | Non-HFTD---6 | 4--2 | 2.0012 | 69 | 100% | 45.7464 | 11.34% | 84.92% | 3.741% | 0.25674 | 0 | 0 | 0.25674 | 0 | 0.22287 | 1.8813 | 0.11846 | 0.22287 | 1.8813 | 0.11846 | 0.26053 | 2.1993 | 0.11846 | 0.5612% | 0.066097 | 0.062825 | 692.1106 | 12.2731 | 470.7532 | 209.0843 | 724.0677 | 0 | 0 | 724.0677 | 8.466e-06%
2028 | 357 | 357-2047F | Tier-2 | Tier-2---10 | 5--4 | 0.49562 | 10 | 100% | 878.9304 | 95.49% | 4.482% | 0.03213% | 41.5429 | 0 | 0 | 41.5429 | 0 | 36.0619 | 0.46593 | 77.3978 | 36.0619 | 0.46593 | 77.3978 | 42.1568 | 0.54468 | 77.3978 | 4.727% | 0.14128 | 0.13429 | 6221.0361 | 965.311 | 255.5825 | 5000.1426 | 6235.6624 | 0 | 0 | 6235.6624 | 0.00137%
2028 | 397 | 397-550F | Tier-1 | Non-HFTD---16 | 3--1 | 4.9887 | 155 | 100% | 4.542 | 25.73% | 0% | 74.27% | 0.057853 | 0 | 0 | 0.057853 | 0 | 0.05022 | 4.6899 | 0.010708 | 0.05022 | 4.6899 | 0.010708 | 0.058707 | 5.4825 | 0.010708 | 1.274% | 0.013683 | 0.013005 | 331.9512 | 4.2581 | 82.8811 | 244.812 | 344.7902 | 0 | 0 | 344.7902 | 1.908e-06%
2028 | 156 | CB 156 | Tier-1 | Non-HFTD---7 | 2--3 | 3.9841 | 144 | 100% | 34.4406 | 92.43% | 0% | 7.569% | 1.5758 | 0 | 0 | 1.5758 | 0 | 1.3679 | 3.7454 | 0.36521 | 1.3679 | 3.7454 | 0.36521 | 1.5991 | 4.3785 | 0.36521 | 4.575% | 0.012401 | 0.011788 | 2777.1524 | 583.7733 | 709.3221 | 1484.0571 | 2788.0993 | 0 | 0 | 2788.0993 | 5.196e-05%
2028 | 236 | 236-1569R | Tier-3 | Tier-3---8 | 5--5 | 16.0076 | 996 | 100% | 21222.9131 | 98.36% | 1.585% | 0.05121% | 1033.3462 | 0 | 0 | 1033.3462 | 0 | 897.0119 | 15.0487 | 59.6071 | 897.0119 | 15.0487 | 59.6071 | 1048.6171 | 17.5921 | 59.6071 | 4.869% | 0.21435 | 0.20374 | 99012.7753 | 16128.7388 | 1444.5093 | 81439.5272 | 99097.1397 | 0 | 0 | 99097.1397 | 0.03408%
2028 | 175 | 175-2024R | Tier-2 | Tier-2---5 | 5--5 | 7.3674 | 622 | 100% | 4029.0085 | 99.1% | 0.8147% | 0.08289% | 197.6458 | 0 | 0 | 197.6458 | 0 | 171.5694 | 6.9261 | 24.7714 | 171.5694 | 6.9261 | 24.7714 | 200.5666 | 8.0967 | 24.7714 | 4.906% | 0.19114 | 0.18168 | 21078.6803 | 4664.0587 | 153.3837 | 16261.2378 | 21088.5336 | 0 | 0 | 21088.5336 | 0.006518%
2028 | 255 | 255-43AE | Tier-1 | Non-HFTD---6 | 4--2 | 17.4344 | 666 | 100% | 53.0999 | 77.76% | 0% | 22.24% | 2.0438 | 0 | 0 | 2.0438 | 0 | 1.7741 | 16.3901 | 0.10824 | 1.7741 | 16.3901 | 0.10824 | 2.074 | 19.1603 | 0.10824 | 3.849% | 0.048441 | 0.046043 | 1096.1851 | 147.1891 | 267.7558 | 681.2403 | 1108.8831 | 0 | 0 | 1108.8831 | 6.74e-05%
2028 | 50 | CB 50 | Tier-1 | Non-HFTD---16 | 2--1 | 3.922 | 170 | 100% | 4.8179 | 39.4% | 0% | 60.6% | 0.093953 | 0 | 0 | 0.093953 | 0 | 0.081557 | 3.6871 | 0.02212 | 0.081557 | 3.6871 | 0.02212 | 0.095341 | 4.3102 | 0.02212 | 1.95% | 0.010946 | 0.010404 | 440.1426 | 0.20072 | 197.6284 | 242.3134 | 454.0341 | 0 | 0 | 454.0341 | 3.098e-06%
2028 | 920 | 920-735AE | Tier-2 | Tier-2---7 | 4--5 | 7.5286 | 403 | 100% | 1554.328 | 69.02% | 30.62% | 0.3611% | 53.1046 | 0 | 0 | 53.1046 | 0 | 46.0982 | 7.0777 | 6.5132 | 46.0982 | 7.0777 | 6.5132 | 53.8893 | 8.2739 | 6.5132 | 3.417% | 0.068691 | 0.065291 | 22627.8919 | 3439.8789 | 6367.8103 | 12820.2027 | 22992.947 | 0 | 0 | 22992.947 | 0.001751%
2028 | 211 | 211-771R | Tier-3 | Tier-3---14 | 5--4 | 14.1159 | 1193 | 100% | 1890.633 | 91.06% | 8.49% | 0.4466% | 85.223 | 0 | 0 | 85.223 | 0 | 73.9791 | 13.2704 | 5.5748 | 73.9791 | 13.2704 | 5.5748 | 86.4824 | 15.5132 | 5.5748 | 4.508% | 0.3743 | 0.35578 | 5051.0602 | 491.5059 | 380.0774 | 4179.4769 | 5074.5675 | 0 | 0 | 5074.5675 | 0.00281%
2028 | 1234 | CB 1234 | Tier-3 | Tier-3---10 | 5--5 | 17.3068 | 1251 | 100% | 6311.4919 | 84.29% | 15.54% | 0.1769% | 263.3319 | 0 | 0 | 263.3319 | 0 | 228.5893 | 16.2701 | 14.0496 | 228.5893 | 16.2701 | 14.0496 | 267.2235 | 19.0199 | 14.0496 | 4.172% | 0.11961 | 0.11369 | 52765.4948 | 7251.4549 | 7797.694 | 37716.3459 | 53197.2441 | 0 | 0 | 53197.2441 | 0.008684%
2028 | 139 | 139-245AE | Tier-1 | Non-HFTD---14 | 2--2 | 3.4127 | 72 | 100% | 5.6722 | 51.84% | 0% | 48.16% | 0.14554 | 0 | 0 | 0.14554 | 0 | 0.12634 | 3.2083 | 0.03938 | 0.12634 | 3.2083 | 0.03938 | 0.14769 | 3.7505 | 0.03938 | 2.566% | 0.010451 | 0.0099339 | 542.7299 | 27.8649 | 162.7078 | 352.1572 | 556.343 | 0 | 0 | 556.343 | 4.799e-06%
2028 | 512 | CB 512 | Tier-1 | Non-HFTD---5 | 2--4 | 0.53466 | 12 | 100% | 72.9923 | 9.966% | 89.3% | 0.7365% | 0.36007 | 0 | 0 | 0.36007 | 0 | 0.31257 | 0.50263 | 0.62186 | 0.31257 | 0.50263 | 0.62186 | 0.3654 | 0.58758 | 0.62186 | 0.4933% | 0.012277 | 0.01167 | 5945.2569 | 37.3623 | 5220.9585 | 686.9361 | 6224.0176 | 0 | 0 | 6224.0176 | 1.187e-05%
2028 | 189 | 189-750 | Tier-2 | Tier-2---21 | 1--2 | 0.37597 | 5 | 100% | 1.7248 | 88.21% | 0% | 11.79% | 0.075309 | 0 | 0 | 0.075309 | 0 | 0.065373 | 0.35345 | 0.18496 | 0.065373 | 0.35345 | 0.18496 | 0.076422 | 0.41318 | 0.18496 | 4.366% | 0.001013 | 0.00096286 | 1702.705 | 2.2891 | 1507.0729 | 193.3431 | 1713.1637 | 0 | 0 | 1713.1637 | 2.483e-06%
2028 | 361 | 361-684F | Tier-1 | Non-HFTD---18 | 2--1 | 0.31534 | 15 | 100% | 0.70004 | 34.6% | 14.74% | 50.66% | 0.011991 | 0 | 0 | 0.011991 | 0 | 0.010409 | 0.29645 | 0.035111 | 0.010409 | 0.29645 | 0.035111 | 0.012168 | 0.34656 | 0.035111 | 1.713% | 0.0069836 | 0.0066379 | 100.2413 | 5.6671 | 18.5544 | 76.0198 | 103.6552 | 0 | 0 | 103.6552 | 3.954e-07%
2028 | 217 | 217-41AE | Tier-2 | Tier-2---8 | 5--4 | 13.7784 | 1046 | 100% | 2013.5966 | 89.22% | 10.31% | 0.4697% | 88.9331 | 0 | 0 | 88.9331 | 0 | 77.1998 | 12.9531 | 5.9599 | 77.1998 | 12.9531 | 5.9599 | 90.2474 | 15.1423 | 5.9599 | 4.417% | 0.19664 | 0.1869 | 10240.1297 | 1454.7861 | 960.9628 | 7824.3807 | 10297.5917 | 0 | 0 | 10297.5917 | 0.002933%
2028 | 120 | 120-367F | Tier-1 | Non-HFTD---13 | 2--2 | 0.019508 | 2 | 100% | 8.1563 | 0% | 99.6% | 0.404% | 0 | 0 | 0 | 0 | 0 | 0 | 0.018339 | 0 | 0 | 0.018339 | 0 | 0 | 0.021439 | 0 | 0% | 0.0075852 | 0.0072097 | 1075.2925 | 1.6858 | 978.9966 | 94.6101 | 1131.2914 | 0 | 0 | 1131.2914 | 0%
2028 | 87 | 87-41AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.2464 | 37 | 100% | 0.28157 | 26.88% | 0% | 73.12% | 0.0037471 | 0 | 0 | 0.0037471 | 0 | 0.0032528 | 0.23164 | 0.014042 | 0.0032528 | 0.23164 | 0.014042 | 0.0038025 | 0.27079 | 0.014042 | 1.331% | 0.0008986 | 0.00085412 | 313.3426 | 10.7167 | 37.6883 | 264.9376 | 325.2737 | 0 | 0 | 325.2737 | 1.236e-07%
2028 | 321 | 321-1332R | Tier-1 | Non-HFTD---12 | 2--2 | 4.7077 | 80 | 100% | 9.6163 | 68.26% | 0% | 31.74% | 0.32491 | 0 | 0 | 0.32491 | 0 | 0.28204 | 4.4257 | 0.063728 | 0.28204 | 4.4257 | 0.063728 | 0.32971 | 5.1737 | 0.063728 | 3.379% | 0.013392 | 0.012729 | 718.0629 | 3.1766 | 492.4341 | 222.4522 | 729.9331 | 0 | 0 | 729.9331 | 1.071e-05%
2028 | 770 | 770-259R | Tier-2 | Tier-2---17 | 2--3 | 1.5089 | 0 | 100% | 42.5113 | 97.49% | 0.5175% | 1.991% | 2.0515 | 0 | 0 | 2.0515 | 0 | 1.7809 | 1.4185 | 1.2554 | 1.7809 | 1.4185 | 1.2554 | 2.0819 | 1.6583 | 1.2554 | 4.826% | 0.010605 | 0.01008 | 4008.538 | 787.4023 | 25.9222 | 3195.2135 | 4013.7737 | 0 | 0 | 4013.7737 | 6.765e-05%
2028 | 354 | 354-24AE | Tier-2 | Tier-2---4 | 4--5 | 3.6864 | 237 | 100% | 3653.654 | 88.54% | 11.39% | 0.07412% | 160.1222 | 0 | 0 | 160.1222 | 0 | 138.9965 | 3.4656 | 40.1077 | 138.9965 | 3.4656 | 40.1077 | 162.4885 | 4.0513 | 40.1077 | 4.383% | 0.080555 | 0.076567 | 45356.2427 | 6500.1683 | 4749.3039 | 34106.7705 | 45627.0334 | 0 | 0 | 45627.0334 | 0.00528%
2028 | 371 | CB 371 | Tier-1 | Non-HFTD---18 | 1--1 | 0.65097 | 0 | 100% | 0.79179 | 5.127% | 0% | 94.87% | 0.0020093 | 0 | 0 | 0.0020093 | 0 | 0.0017442 | 0.61198 | 0.0028501 | 0.0017442 | 0.61198 | 0.0028501 | 0.002039 | 0.71541 | 0.0028501 | 0.2538% | 0.0026386 | 0.002508 | 300.0814 | 2.4613 | 27.3455 | 270.2746 | 314.9079 | 0 | 0 | 314.9079 | 6.626e-08%
2028 | 206 | 206-961F | Tier-1 | Non-HFTD---17 | 1--2 | 0.31686 | 31 | 100% | 0.73497 | 72.73% | 0% | 27.27% | 0.026461 | 0 | 0 | 0.026461 | 0 | 0.02297 | 0.29788 | 0.077113 | 0.02297 | 0.29788 | 0.077113 | 0.026852 | 0.34822 | 0.077113 | 3.6% | 0.0009058 | 0.00086096 | 811.4096 | 93.8104 | 38.4901 | 679.1091 | 822.9314 | 0 | 0 | 822.9314 | 8.726e-07%
2028 | 303 | 303-487AE | Tier-1 | Non-HFTD---4 | 3--4 | 1.8256 | 101 | 100% | 106.3501 | 4.982% | 93.81% | 1.206% | 0.26227 | 0 | 0 | 0.26227 | 0 | 0.22766 | 1.7163 | 0.13265 | 0.22766 | 1.7163 | 0.13265 | 0.26614 | 2.0063 | 0.13265 | 0.2466% | 0.016038 | 0.015244 | 6631.1342 | 30.8907 | 5898.0053 | 702.2382 | 6959.2651 | 0 | 0 | 6959.2651 | 8.649e-06%
2028 | 206 | CB 206 | Tier-1 | Non-HFTD---11 | 2--3 | 3.0087 | 131 | 100% | 15.0084 | 86.35% | 0% | 13.65% | 0.64153 | 0 | 0 | 0.64153 | 0 | 0.55689 | 2.8285 | 0.19689 | 0.55689 | 2.8285 | 0.19689 | 0.65101 | 3.3065 | 0.19689 | 4.274% | 0.0084374 | 0.0080197 | 1778.7928 | 21.532 | 1427.2919 | 329.9688 | 1791.4343 | 0 | 0 | 1791.4343 | 2.116e-05%
2028 | MU1 | CB MU1 | Tier-1 | Non-HFTD---8 | 3--2 | 2.842 | 486 | 100% | 27.925 | 4.407% | 87.94% | 7.651% | 0.060913 | 0 | 0 | 0.060913 | 0 | 0.052877 | 2.6718 | 0.019791 | 0.052877 | 2.6718 | 0.019791 | 0.061814 | 3.1233 | 0.019791 | 0.2181% | 0.018888 | 0.017953 | 1478.4806 | 11.8202 | 1223.4645 | 243.1959 | 1552.0837 | 0 | 0 | 1552.0837 | 2.009e-06%
2028 | 489 | 489-19AE | Tier-1 | Non-HFTD---11 | 2--2 | 2.8017 | 45 | 100% | 9.4748 | 79.25% | 0% | 20.75% | 0.37169 | 0 | 0 | 0.37169 | 0 | 0.32265 | 2.6339 | 0.1225 | 0.32265 | 2.6339 | 0.1225 | 0.37719 | 3.0791 | 0.1225 | 3.923% | 0.008219 | 0.0078122 | 1152.7879 | 219.8755 | 163.8034 | 769.109 | 1165.2439 | 0 | 0 | 1165.2439 | 1.226e-05%
2028 | 214 | 214-17AE | Tier-3 | Tier-3---17 | 4--4 | 6.825 | 1872 | 100% | 484.0355 | 97.4% | 1.48% | 1.12% | 23.3369 | 0 | 0 | 23.3369 | 0 | 20.258 | 6.4162 | 3.1573 | 20.258 | 6.4162 | 3.1573 | 23.6818 | 7.5006 | 3.1573 | 4.821% | 0.071957 | 0.068395 | 6726.7702 | 920.7038 | 92.7705 | 5713.2959 | 6735.8769 | 0 | 0 | 6735.8769 | 0.0007696%
2028 | 143 | 143-33 | Tier-1 | Non-HFTD---13 | 2--2 | 0.11532 | 2 | 100% | 7.5516 | 0.6961% | 97.86% | 1.439% | 0.0026022 | 0 | 0 | 0.0026022 | 0 | 0.0022589 | 0.10841 | 0.020836 | 0.0022589 | 0.10841 | 0.020836 | 0.0026407 | 0.12674 | 0.020836 | 0.03446% | 0.0064842 | 0.0061632 | 1164.6172 | 2.5226 | 906.0378 | 256.0569 | 1224.8458 | 0 | 0 | 1224.8458 | 8.581e-08%
2028 | 182 | 182-2250 | Tier-2 | Tier-2---8 | 5--5 | 1.2528 | 11 | 100% | 1939.2132 | 99.74% | 0.2126% | 0.04638% | 95.7424 | 0 | 0 | 95.7424 | 0 | 83.1107 | 1.1778 | 70.5645 | 83.1107 | 1.1778 | 70.5645 | 97.1573 | 1.3769 | 70.5645 | 4.937% | 0.10496 | 0.099761 | 18476.2986 | 2987.5542 | 36.178 | 15452.5664 | 18478.7907 | 0 | 0 | 18478.7907 | 0.003157%
2028 | 973 | 973-1245R | Tier-3 | Tier-3---6 | 5--5 | 3.3435 | 151 | 100% | 8620.1106 | 99.53% | 0.4446% | 0.0227% | 424.7015 | 0 | 0 | 424.7015 | 0 | 368.6686 | 3.1433 | 117.2887 | 368.6686 | 3.1433 | 117.2887 | 430.9777 | 3.6745 | 117.2887 | 4.927% | 0.12039 | 0.11443 | 71603.6913 | 12270.708 | 387.9577 | 58945.0256 | 71621.1173 | 0 | 0 | 71621.1173 | 0.01401%
2028 | 128 | CB 128 | Tier-1 | Non-HFTD---16 | 2--1 | 3.2045 | 22 | 100% | 2.8222 | 5.175% | 0% | 94.82% | 0.0072295 | 0 | 0 | 0.0072295 | 0 | 0.0062757 | 3.0126 | 0.0020832 | 0.0062757 | 3.0126 | 0.0020832 | 0.0073363 | 3.5217 | 0.0020832 | 0.2562% | 0.010647 | 0.01012 | 265.0569 | 1.7417 | 26.7354 | 236.5798 | 278.1462 | 0 | 0 | 278.1462 | 2.384e-07%
2028 | 171 | 171-6R | Tier-1 | Non-HFTD---8 | 4--2 | 2.4529 | 22 | 100% | 40.3404 | 54.29% | 41.19% | 4.517% | 1.0841 | 0 | 0 | 1.0841 | 0 | 0.94108 | 2.306 | 0.40811 | 0.94108 | 2.306 | 0.40811 | 1.1001 | 2.6957 | 0.40811 | 2.687% | 0.036438 | 0.034634 | 1107.1099 | 96.9512 | 428.9197 | 581.2391 | 1133.4637 | 0 | 0 | 1133.4637 | 3.575e-05%
2028 | 171 | CB 171 | Tier-1 | Non-HFTD---3 | 4--3 | 2.7693 | 176 | 100% | 113.9192 | 33.8% | 64.29% | 1.906% | 1.9062 | 0 | 0 | 1.9062 | 0 | 1.6547 | 2.6034 | 0.63559 | 1.6547 | 2.6034 | 0.63559 | 1.9343 | 3.0434 | 0.63559 | 1.673% | 0.040057 | 0.038075 | 2843.8994 | 78.1486 | 2158.4913 | 607.2596 | 2941.9394 | 0 | 0 | 2941.9394 | 6.286e-05%
2028 | 159 | 159-38F | Tier-1 | Non-HFTD---16 | 2--1 | 2.7123 | 104 | 100% | 2.2472 | 22.94% | 0% | 77.06% | 0.025514 | 0 | 0 | 0.025514 | 0 | 0.022148 | 2.5499 | 0.0086859 | 0.022148 | 2.5499 | 0.0086859 | 0.025891 | 2.9808 | 0.0086859 | 1.135% | 0.00712 | 0.0067676 | 315.6205 | 0.4738 | 92.7094 | 222.4373 | 328.2873 | 0 | 0 | 328.2873 | 8.414e-07%
2028 | 392 | CB 392 | Tier-1 | Non-HFTD---2 | 5--4 | 4.5493 | 172 | 100% | 632.789 | 5.96% | 93.57% | 0.4686% | 1.8668 | 0 | 0 | 1.8668 | 0 | 1.6205 | 4.2768 | 0.37891 | 1.6205 | 4.2768 | 0.37891 | 1.8944 | 4.9996 | 0.37891 | 0.295% | 0.10236 | 0.097291 | 6182.1524 | 58.8165 | 5308.8037 | 814.5321 | 6484.9176 | 0 | 0 | 6484.9176 | 6.156e-05%
2028 | 172 | 172-567R | Tier-1 | Non-HFTD---3 | 4--3 | 10.6971 | 130 | 100% | 141.9219 | 62.19% | 32.78% | 5.033% | 4.369 | 0 | 0 | 4.369 | 0 | 3.7926 | 10.0564 | 0.37713 | 3.7926 | 10.0564 | 0.37713 | 4.4336 | 11.756 | 0.37713 | 3.078% | 0.069555 | 0.066112 | 2040.4331 | 199.3667 | 664.6627 | 1176.4036 | 2080.609 | 0 | 0 | 2080.609 | 0.0001441%
2028 | 475 | CB 475 | Tier-1 | Non-HFTD---5 | 2--4 | 2.5995 | 183 | 100% | 67.5852 | 97.2% | 0% | 2.801% | 3.2518 | 0 | 0 | 3.2518 | 0 | 2.8227 | 2.4437 | 1.1551 | 2.8227 | 2.4437 | 1.1551 | 3.2998 | 2.8568 | 1.1551 | 4.811% | 0.0082144 | 0.0078078 | 8227.6449 | 1225.4309 | 526.326 | 6475.888 | 8239.6468 | 0 | 0 | 8239.6468 | 0.0001072%
2028 | CTL1 | CB CTL1 | Tier-3 | Tier-3---19 | 5--1 | 0.038118 | 4 | 100% | 27.4807 | 90.21% | 9.514% | 0.2799% | 1.2271 | 0 | 0 | 1.2271 | 0 | 1.0652 | 0.035835 | 29.7244 | 1.0652 | 0.035835 | 29.7244 | 1.2452 | 0.041891 | 29.7244 | 4.465% | 0.42111 | 0.40027 | 65.2572 | 9.1588 | 5.9813 | 50.1171 | 65.5901 | 0 | 0 | 65.5901 | 4.046e-05%
2028 | 95 | 95-37F | Tier-1 | Non-HFTD---20 | 2--1 | 0.088838 | 3 | 100% | 0.46434 | 14.45% | 70.16% | 15.4% | 0.0033212 | 0 | 0 | 0.0033212 | 0 | 0.002883 | 0.083517 | 0.03452 | 0.002883 | 0.083517 | 0.03452 | 0.0033703 | 0.097632 | 0.03452 | 0.7152% | 0.0053792 | 0.0051129 | 86.3215 | 1.055 | 63.4057 | 21.8608 | 90.1673 | 0 | 0 | 90.1673 | 1.095e-07%
2028 | 444 | 444-9R | Tier-2 | Tier-2---11 | 5--3 | 14.7171 | 588 | 100% | 571.2373 | 70.71% | 27.93% | 1.361% | 19.9936 | 0 | 0 | 19.9936 | 0 | 17.3558 | 13.8355 | 1.2544 | 17.3558 | 13.8355 | 1.2544 | 20.2891 | 16.1739 | 1.2544 | 3.5% | 0.1488 | 0.14143 | 3839.0169 | 360.2149 | 1019.4785 | 2459.3235 | 3897.5795 | 0 | 0 | 3897.5795 | 0.0006593%
2028 | 212 | 212-886R | Tier-2 | Tier-2---8 | 5--4 | 8.9137 | 168 | 100% | 2163.5248 | 98.72% | 1.034% | 0.2463% | 105.7234 | 0 | 0 | 105.7234 | 0 | 91.7748 | 8.3797 | 10.952 | 91.7748 | 8.3797 | 10.952 | 107.2858 | 9.796 | 10.952 | 4.887% | 0.18767 | 0.17838 | 11528.3958 | 1549.2528 | 106.6411 | 9872.5019 | 11536.0822 | 0 | 0 | 11536.0822 | 0.003486%
2028 | AM1 | CB AM1 | Tier-1 | Non-HFTD---16 | 2--1 | 3.6244 | 115 | 100% | 3.3578 | 29.51% | 0% | 70.49% | 0.049051 | 0 | 0 | 0.049051 | 0 | 0.042579 | 3.4073 | 0.012496 | 0.042579 | 3.4073 | 0.012496 | 0.049775 | 3.9832 | 0.012496 | 1.461% | 0.0096132 | 0.0091373 | 349.2893 | 0.61104 | 122.8396 | 225.8387 | 362.1114 | 0 | 0 | 362.1114 | 1.618e-06%
2028 | 580 | 580-690AE | Tier-1 | Non-HFTD---19 | 1--3 | 0.067992 | 0 | 100% | 0.50006 | 86.19% | 0% | 13.81% | 0.021335 | 0 | 0 | 0.021335 | 0 | 0.01852 | 0.06392 | 0.28974 | 0.01852 | 0.06392 | 0.28974 | 0.02165 | 0.074723 | 0.28974 | 4.266% | 0.0002812 | 0.00026728 | 1778.3079 | 201.1614 | 323.7794 | 1253.3671 | 1791.0959 | 0 | 0 | 1791.0959 | 7.035e-07%
2028 | 308 | 308-563AE | Tier-2 | Tier-2---18 | 4--3 | 0.99238 | 48 | 100% | 95.5263 | 19.37% | 79.9% | 0.729% | 0.91613 | 0 | 0 | 0.91613 | 0 | 0.79526 | 0.93294 | 0.85243 | 0.79526 | 0.93294 | 0.85243 | 0.92967 | 1.0906 | 0.85243 | 0.959% | 0.03316 | 0.031518 | 2880.805 | 126.6132 | 2111.1435 | 643.0484 | 3001.7645 | 0 | 0 | 3001.7645 | 3.021e-05%
2028 | 416 | 416-35F | Tier-1 | Non-HFTD---17 | 1--1 | 0.98558 | 46 | 100% | 1.2958 | 41.8% | 0% | 58.2% | 0.026812 | 0 | 0 | 0.026812 | 0 | 0.023274 | 0.92654 | 0.02512 | 0.023274 | 0.92654 | 0.02512 | 0.027208 | 1.0831 | 0.02512 | 2.069% | 0.0029674 | 0.0028205 | 436.6793 | 1.3522 | 198.3951 | 236.932 | 449.9146 | 0 | 0 | 449.9146 | 8.842e-07%
2028 | 719 | 719-857F | Tier-1 | Non-HFTD---20 | 1--1 | 0.4199 | 8 | 100% | 0.29905 | 18.65% | 0% | 81.35% | 0.0027613 | 0 | 0 | 0.0027613 | 0 | 0.0023969 | 0.39475 | 0.0060721 | 0.0023969 | 0.39475 | 0.0060721 | 0.0028021 | 0.46146 | 0.0060721 | 0.9233% | 0.0010186 | 0.00096818 | 293.5913 | 0.17971 | 76.4595 | 216.9521 | 306.0289 | 0 | 0 | 306.0289 | 9.106e-08%
2028 | 972 | 972-1642 | Tier-2 | Tier-2---16 | 5--2 | 0.038636 | 0 | 100% | 185.3011 | 0% | 99.96% | 0.04171% | 0 | 0 | 0 | 0 | 0 | 0 | 0.036322 | 0 | 0 | 0.036322 | 0 | 0 | 0.042461 | 0 | 0% | 0.11047 | 0.105 | 1677.3427 | 1.9611 | 1510.6909 | 164.6906 | 1764.6951 | 0 | 0 | 1764.6951 | 0%
2028 | 199 | 199-39AE | Tier-1 | Non-HFTD---13 | 2--2 | 2.4932 | 59 | 100% | 5.5063 | 65.09% | 0% | 34.91% | 0.17742 | 0 | 0 | 0.17742 | 0 | 0.15401 | 2.3439 | 0.065709 | 0.15401 | 2.3439 | 0.065709 | 0.18004 | 2.74 | 0.065709 | 3.222% | 0.0073958 | 0.0070297 | 744.5212 | 70.5063 | 77.1367 | 596.8782 | 758.0554 | 0 | 0 | 758.0554 | 5.851e-06%
2028 | AM2 | CB AM2 | Tier-1 | Non-HFTD---12 | 3--2 | 7.125 | 184 | 100% | 11.1682 | 52.54% | 0% | 47.46% | 0.29045 | 0 | 0 | 0.29045 | 0 | 0.25213 | 6.6982 | 0.037642 | 0.25213 | 6.6982 | 0.037642 | 0.29475 | 7.8302 | 0.037642 | 2.601% | 0.02008 | 0.019086 | 556.1818 | 2.2661 | 303.5202 | 250.3954 | 569.9286 | 0 | 0 | 569.9286 | 9.578e-06%
2028 | RD4 | RD4-48F | Tier-1 | Non-HFTD---16 | 2--1 | 3.5216 | 269 | 100% | 3.4032 | 33.95% | 0% | 66.05% | 0.057196 | 0 | 0 | 0.057196 | 0 | 0.04965 | 3.3107 | 0.014997 | 0.04965 | 3.3107 | 0.014997 | 0.058041 | 3.8702 | 0.014997 | 1.681% | 0.0093526 | 0.0088896 | 363.8725 | 1.432 | 137.6932 | 224.7473 | 376.3882 | 0 | 0 | 376.3882 | 1.886e-06%
2028 | 852 | CB 852 | Tier-1 | Non-HFTD---7 | 1--5 | 0.13314 | 18 | 100% | 34.4559 | 99.59% | 0% | 0.4114% | 1.6986 | 0 | 0 | 1.6986 | 0 | 1.4745 | 0.12517 | 11.7797 | 1.4745 | 0.12517 | 11.7797 | 1.7237 | 0.14632 | 11.7797 | 4.93% | 0.0007638 | 0.00072599 | 45111.1902 | 8830.4114 | 18.3177 | 36262.461 | 45120.855 | 0 | 0 | 45120.855 | 5.601e-05%
2028 | 1458 | 1458-1056 | Tier-2 | Tier-2---11 | 5--3 | 0.50061 | 49 | 100% | 427.4478 | 90.46% | 9.431% | 0.1062% | 19.1407 | 0 | 0 | 19.1407 | 0 | 16.6154 | 0.47062 | 35.3054 | 16.6154 | 0.47062 | 35.3054 | 19.4236 | 0.55016 | 35.3054 | 4.478% | 0.13508 | 0.12839 | 3164.5032 | 465.473 | 268.1729 | 2430.8573 | 3180.2204 | 0 | 0 | 3180.2204 | 0.0006312%
2028 | 222 | 222-1433R | Tier-3 | Tier-3---5 | 5--5 | 6.2775 | 182 | 100% | 9617.9712 | 99.59% | 0.3681% | 0.03974% | 474.1478 | 0 | 0 | 474.1478 | 0 | 411.5912 | 5.9015 | 69.7438 | 411.5912 | 5.9015 | 69.7438 | 481.1548 | 6.8989 | 69.7438 | 4.93% | 0.37266 | 0.35421 | 25809.0958 | 4058.0923 | 86.1531 | 21664.8505 | 25814.5777 | 0 | 0 | 25814.5777 | 0.01564%
2028 | 180 | CB 180 | Tier-1 | Non-HFTD---13 | 1--3 | 0.94796 | 5 | 100% | 7.7122 | 90.8% | 0% | 9.202% | 0.34662 | 0 | 0 | 0.34662 | 0 | 0.30089 | 0.89118 | 0.33763 | 0.30089 | 0.89118 | 0.33763 | 0.35174 | 1.0418 | 0.33763 | 4.494% | 0.0030172 | 0.0028678 | 2556.0648 | 24.9107 | 2190.1936 | 340.9605 | 2568.3144 | 0 | 0 | 2568.3144 | 1.143e-05%
2028 | 430 | 430-321AE | Tier-1 | Non-HFTD---20 | 1--1 | 0.3352 | 34 | 100% | 0.30658 | 15.66% | 0% | 84.34% | 0.0023773 | 0 | 0 | 0.0023773 | 0 | 0.0020636 | 0.31512 | 0.0065486 | 0.0020636 | 0.31512 | 0.0065486 | 0.0024124 | 0.36838 | 0.0065486 | 0.7754% | 0.0009426 | 0.00089594 | 325.2518 | 3.1534 | 57.757 | 264.3414 | 339.5368 | 0 | 0 | 339.5368 | 7.839e-08%
2028 | HP1 | CB HP1 | Tier-1 | Non-HFTD---10 | 4--1 | 18.2582 | 619 | 100% | 16.6755 | 30.85% | 0% | 69.15% | 0.25463 | 0 | 0 | 0.25463 | 0 | 0.22104 | 17.1645 | 0.012878 | 0.22104 | 17.1645 | 0.012878 | 0.2584 | 20.0655 | 0.012878 | 1.527% | 0.048206 | 0.04582 | 345.9227 | 0.91802 | 123.9165 | 221.0881 | 358.3803 | 0 | 0 | 358.3803 | 8.397e-06%
2028 | 212 | 212-888R | Tier-2 | Tier-2---8 | 5--4 | 6.9867 | 127 | 100% | 1471.0622 | 97.82% | 1.883% | 0.2988% | 71.2291 | 0 | 0 | 71.2291 | 0 | 61.8315 | 6.5682 | 9.4138 | 61.8315 | 6.5682 | 9.4138 | 72.2817 | 7.6783 | 9.4138 | 4.842% | 0.13116 | 0.12466 | 11216.1087 | 1520.4174 | 191.4206 | 9504.2707 | 11228.8506 | 0 | 0 | 11228.8506 | 0.002349%
2028 | 461 | 461-24F | Tier-1 | Non-HFTD---15 | 1--3 | 0.42368 | 9 | 100% | 4.3764 | 89.98% | 0% | 10.02% | 0.19492 | 0 | 0 | 0.19492 | 0 | 0.1692 | 0.3983 | 0.42481 | 0.1692 | 0.3983 | 0.42481 | 0.1978 | 0.46562 | 0.42481 | 4.454% | 0.0015528 | 0.0014759 | 2818.3832 | 300.604 | 715.3571 | 1802.422 | 2833.0954 | 0 | 0 | 2833.0954 | 6.428e-06%
2028 | 504 | 504-287R | Tier-2 | Tier-2---12 | 4--4 | 7.8402 | 264 | 100% | 501.8283 | 98.94% | 0% | 1.063% | 24.5765 | 0 | 0 | 24.5765 | 0 | 21.334 | 7.3705 | 2.8945 | 21.334 | 7.3705 | 2.8945 | 24.9397 | 8.6162 | 2.8945 | 4.897% | 0.033132 | 0.031492 | 15146.1514 | 2418.4341 | 53.5553 | 12674.162 | 15154.5352 | 0 | 0 | 15154.5352 | 0.0008104%
2028 | SW1 | CB SW1 | Tier-1 | Non-HFTD---17 | 1--1 | 1.5451 | 35 | 100% | 1.6455 | 48.03% | 0% | 51.97% | 0.039125 | 0 | 0 | 0.039125 | 0 | 0.033963 | 1.4526 | 0.023381 | 0.033963 | 1.4526 | 0.023381 | 0.039703 | 1.6981 | 0.023381 | 2.378% | 0.0038896 | 0.0036971 | 423.0612 | 20.0581 | 101.1853 | 301.8178 | 434.5106 | 0 | 0 | 434.5106 | 1.29e-06%
2028 | 245 | CB 245 | Tier-1 | Non-HFTD---2 | 4--4 | 7.1536 | 280 | 100% | 248.3247 | 30.26% | 68.14% | 1.595% | 3.7197 | 0 | 0 | 3.7197 | 0 | 3.2289 | 6.7251 | 0.48012 | 3.2289 | 6.7251 | 0.48012 | 3.7746 | 7.8618 | 0.48012 | 1.498% | 0.044637 | 0.042428 | 5563.1534 | 331.3651 | 3704.159 | 1527.6293 | 5765.2004 | 0 | 0 | 5765.2004 | 0.0001227%
2028 | 74 | 74-24R | Tier-1 | Non-HFTD---12 | 3--2 | 8.6284 | 269 | 100% | 13.7632 | 60.93% | 0% | 39.07% | 0.41507 | 0 | 0 | 0.41507 | 0 | 0.36031 | 8.1116 | 0.044419 | 0.36031 | 8.1116 | 0.044419 | 0.42121 | 9.4825 | 0.044419 | 3.016% | 0.022875 | 0.021743 | 601.6686 | 1.4002 | 380.4228 | 219.8456 | 613.912 | 0 | 0 | 613.912 | 1.369e-05%
2028 | 341 | 341-920 | Tier-1 | Non-HFTD---3 | 4--3 | 12.9709 | 837 | 100% | 161.886 | 95.19% | 0% | 4.806% | 7.6283 | 0 | 0 | 7.6283 | 0 | 6.6218 | 12.1939 | 0.54304 | 6.6218 | 12.1939 | 0.54304 | 7.741 | 14.2548 | 0.54304 | 4.712% | 0.035928 | 0.034149 | 4505.8945 | 872.5831 | 176.1223 | 3457.1891 | 4517.1713 | 0 | 0 | 4517.1713 | 0.0002516%
2028 | 520 | 520-45 | Tier-2 | Tier-2---8 | 5--5 | 9.4684 | 622 | 100% | 2044.6463 | 97.57% | 2.13% | 0.298% | 98.7525 | 0 | 0 | 98.7525 | 0 | 85.7236 | 8.9012 | 9.6305 | 85.7236 | 8.9012 | 9.6305 | 100.2118 | 10.4057 | 9.6305 | 4.83% | 0.10446 | 0.099291 | 19573.1854 | 2561.9074 | 366.8903 | 16644.3877 | 19597.9361 | 0 | 0 | 19597.9361 | 0.003256%
2028 | GM2 | CB GM2 | Tier-1 | Non-HFTD---2 | 4--3 | 12.8498 | 1166 | 100% | 185.8665 | 95.73% | 0% | 4.266% | 8.8079 | 0 | 0 | 8.8079 | 0 | 7.6459 | 12.0801 | 0.63293 | 7.6459 | 12.0801 | 0.63293 | 8.9381 | 14.1218 | 0.63293 | 4.739% | 0.042423 | 0.040323 | 4381.2884 | 678.342 | 70.1655 | 3632.7808 | 4391.021 | 0 | 0 | 4391.021 | 0.0002905%
2028 | 52 | 52-20R | Tier-1 | Non-HFTD---14 | 2--2 | 3.9289 | 85 | 100% | 5.9584 | 48.34% | 0% | 51.66% | 0.14257 | 0 | 0 | 0.14257 | 0 | 0.12376 | 3.6936 | 0.033506 | 0.12376 | 3.6936 | 0.033506 | 0.14468 | 4.3179 | 0.033506 | 2.393% | 0.011327 | 0.010766 | 526.0509 | 0.21605 | 278.8999 | 246.935 | 540.204 | 0 | 0 | 540.204 | 4.701e-06%
2028 | 504 | CB 504 | Tier-1 | Non-HFTD---7 | 2--3 | 4.505 | 174 | 100% | 34.4975 | 90.08% | 0% | 9.923% | 1.5382 | 0 | 0 | 1.5382 | 0 | 1.3352 | 4.2351 | 0.31528 | 1.3352 | 4.2351 | 0.31528 | 1.5609 | 4.9509 | 0.31528 | 4.459% | 0.013226 | 0.012571 | 2608.352 | 206.1348 | 1114.8562 | 1287.361 | 2621.8318 | 0 | 0 | 2621.8318 | 5.072e-05%
2028 | 114 | 114-18AE | Tier-1 | Non-HFTD---6 | 3--3 | 4.008 | 263 | 100% | 66.6834 | 4.686% | 91.31% | 4.003% | 0.15468 | 0 | 0 | 0.15468 | 0 | 0.13428 | 3.7679 | 0.035637 | 0.13428 | 3.7679 | 0.035637 | 0.15697 | 4.4047 | 0.035637 | 0.232% | 0.019386 | 0.018426 | 3439.7723 | 23.4352 | 2933.6014 | 482.7357 | 3610.5136 | 0 | 0 | 3610.5136 | 5.101e-06%
2028 | 221 | 221-782R | Tier-3 | Tier-3---17 | 5--3 | 3.289 | 349 | 100% | 618.0174 | 98.68% | 0.7939% | 0.5237% | 30.1888 | 0 | 0 | 30.1888 | 0 | 26.2058 | 3.092 | 8.4754 | 26.2058 | 3.092 | 8.4754 | 30.6349 | 3.6146 | 8.4754 | 4.885% | 0.2472 | 0.23496 | 2500.0604 | 358.786 | 17.1966 | 2124.0778 | 2501.7759 | 0 | 0 | 2501.7759 | 0.0009955%
2028 | 171 | 171-704R | Tier-1 | Non-HFTD---6 | 4--2 | 4.9861 | 76 | 100% | 80.6143 | 61.35% | 34.31% | 4.34% | 2.4483 | 0 | 0 | 2.4483 | 0 | 2.1253 | 4.6875 | 0.4534 | 2.1253 | 4.6875 | 0.4534 | 2.4845 | 5.4797 | 0.4534 | 3.037% | 0.048088 | 0.045707 | 1676.4044 | 165.028 | 536.4334 | 974.9431 | 1710.1431 | 0 | 0 | 1710.1431 | 8.074e-05%
2028 | 444 | 444-15R | Tier-2 | Tier-2---13 | 5--3 | 8.351 | 10 | 100% | 333.8465 | 96.62% | 2.31% | 1.072% | 15.9664 | 0 | 0 | 15.9664 | 0 | 13.8599 | 7.8508 | 1.7654 | 13.8599 | 7.8508 | 1.7654 | 16.2024 | 9.1776 | 1.7654 | 4.783% | 0.14886 | 0.14149 | 2242.6726 | 267.3076 | 49.2808 | 1926.0842 | 2246.6232 | 0 | 0 | 2246.6232 | 0.0005265%
2028 | 59 | 59-465 | Tier-1 | Non-HFTD---6 | 4--3 | 7.5326 | 198 | 100% | 77.379 | 64.48% | 28.11% | 7.401% | 2.4699 | 0 | 0 | 2.4699 | 0 | 2.1441 | 7.0814 | 0.30278 | 2.1441 | 7.0814 | 0.30278 | 2.5064 | 8.2782 | 0.30278 | 3.192% | 0.036127 | 0.034339 | 2141.862 | 301.1171 | 633.9997 | 1206.7452 | 2181.4767 | 0 | 0 | 2181.4767 | 8.145e-05%
2028 | 588 | CB 588 | Tier-1 | Non-HFTD---9 | 1--4 | 0.38598 | 4 | 100% | 21.538 | 98.85% | 0% | 1.146% | 1.0539 | 0 | 0 | 1.0539 | 0 | 0.91487 | 0.36286 | 2.5212 | 0.91487 | 0.36286 | 2.5212 | 1.0695 | 0.42419 | 2.5212 | 4.893% | 0.0014694 | 0.0013967 | 14657.7162 | 2735.8339 | 186.8229 | 11735.0595 | 14666.4638 | 0 | 0 | 14666.4638 | 3.475e-05%
2028 | 1081 | 1081-666F | Tier-1 | Non-HFTD---4 | 3--4 | 5.8293 | 751 | 100% | 169.8745 | 80.26% | 17.52% | 2.222% | 6.7489 | 0 | 0 | 6.7489 | 0 | 5.8585 | 5.4801 | 1.069 | 5.8585 | 5.4801 | 1.069 | 6.8487 | 6.4063 | 1.069 | 3.973% | 0.027363 | 0.026009 | 6208.1833 | 1026.9206 | 1026.1932 | 4155.0696 | 6272.0024 | 0 | 0 | 6272.0024 | 0.0002226%
2028 | 86 | 86-552F | Tier-1 | Non-HFTD---2 | 4--3 | 20.0174 | 1804 | 100% | 186.6357 | 92.7% | 0% | 7.302% | 8.5639 | 0 | 0 | 8.5639 | 0 | 7.434 | 18.8184 | 0.39504 | 7.434 | 18.8184 | 0.39504 | 8.6904 | 21.9989 | 0.39504 | 4.589% | 0.057976 | 0.055107 | 3219.1671 | 590.7148 | 100.2194 | 2528.2329 | 3231.4085 | 0 | 0 | 3231.4085 | 0.0002824%
2028 | 236 | 236-1535R | Tier-3 | Tier-3---4 | 5--5 | 7.8693 | 840 | 100% | 9719.0421 | 98.73% | 1.209% | 0.05836% | 474.9956 | 0 | 0 | 474.9956 | 0 | 412.3272 | 7.3979 | 55.7356 | 412.3272 | 7.3979 | 55.7356 | 482.0151 | 8.6483 | 55.7356 | 4.887% | 0.12847 | 0.12211 | 75651.1712 | 14020.5397 | 863.9874 | 60766.6441 | 75701.1003 | 0 | 0 | 75701.1003 | 0.01566%
2028 | 151 | 151-1044F | Tier-1 | Non-HFTD---18 | 1--1 | 1.7676 | 67 | 100% | 0.90758 | 10.2% | 0% | 89.8% | 0.0045835 | 0 | 0 | 0.0045835 | 0 | 0.0039788 | 1.6617 | 0.0023944 | 0.0039788 | 1.6617 | 0.0023944 | 0.0046512 | 1.9425 | 0.0023944 | 0.505% | 0.0041016 | 0.0038986 | 221.2741 | 0.23379 | 40.1127 | 180.9276 | 231.6219 | 0 | 0 | 231.6219 | 1.511e-07%
2028 | 1119 | 1119-9F | Tier-1 | Non-HFTD---7 | 2--3 | 1.7245 | 235 | 100% | 44.0578 | 1.729% | 95.21% | 3.066% | 0.037698 | 0 | 0 | 0.037698 | 0 | 0.032724 | 1.6212 | 0.020186 | 0.032724 | 1.6212 | 0.020186 | 0.038255 | 1.8952 | 0.020186 | 0.08556% | 0.01155 | 0.010978 | 3814.4644 | 11.0382 | 3336.1347 | 467.2915 | 4009.6797 | 0 | 0 | 4009.6797 | 1.243e-06%
2028 | 321 | 321-741 | Tier-1 | Non-HFTD---18 | 1--1 | 1.6644 | 22 | 100% | 1.2108 | 17.09% | 0% | 82.91% | 0.010243 | 0 | 0 | 0.010243 | 0 | 0.0088913 | 1.5647 | 0.0056824 | 0.0088913 | 1.5647 | 0.0056824 | 0.010394 | 1.8292 | 0.0056824 | 0.8459% | 0.0042182 | 0.0040094 | 287.0469 | 0.17908 | 70.6743 | 216.1935 | 299.441 | 0 | 0 | 299.441 | 3.378e-07%
2028 | CMP1 | CB CMP1 | Tier-1 | Non-HFTD---7 | 3--3 | 5.6403 | 486 | 100% | 37.1183 | 89.86% | 0% | 10.14% | 1.6511 | 0 | 0 | 1.6511 | 0 | 1.4333 | 5.3025 | 0.27031 | 1.4333 | 5.3025 | 0.27031 | 1.6755 | 6.1986 | 0.27031 | 4.448% | 0.016556 | 0.015736 | 2241.9834 | 320.7107 | 77.0021 | 1844.2706 | 2253.8174 | 0 | 0 | 2253.8174 | 5.445e-05%
2028 | 449 | 449-693R | Tier-3 | Tier-3---9 | 5--5 | 8.4553 | 119 | 100% | 5260.7056 | 98.77% | 1.153% | 0.07468% | 257.2092 | 0 | 0 | 257.2092 | 0 | 223.2743 | 7.9488 | 28.0889 | 223.2743 | 7.9488 | 28.0889 | 261.0102 | 9.2923 | 28.0889 | 4.889% | 0.26107 | 0.24815 | 20150.463 | 3063.9091 | 212.3063 | 16874.2476 | 20163.3414 | 0 | 0 | 20163.3414 | 0.008482%
2028 | 221 | 221-1251R | Tier-1 | Non-HFTD---2 | 5--4 | 16.3418 | 150 | 100% | 1814.8505 | 87.56% | 11.92% | 0.5209% | 78.6628 | 0 | 0 | 78.6628 | 0 | 68.2845 | 15.363 | 4.4447 | 68.2845 | 15.363 | 4.4447 | 79.8253 | 17.9595 | 4.4447 | 4.334% | 0.27478 | 0.26118 | 6604.7785 | 826.9947 | 747.1453 | 5030.6385 | 6647.5552 | 0 | 0 | 6647.5552 | 0.002594%
2028 | 1435 | 1435-50 | Tier-1 | Non-HFTD---10 | 3--2 | 8.8248 | 347 | 100% | 15.0882 | 59.27% | 0% | 40.73% | 0.44264 | 0 | 0 | 0.44264 | 0 | 0.38424 | 8.2962 | 0.046315 | 0.38424 | 8.2962 | 0.046315 | 0.44918 | 9.6983 | 0.046315 | 2.934% | 0.026149 | 0.024855 | 577.0099 | 71.0904 | 94.7801 | 411.1393 | 589.2502 | 0 | 0 | 589.2502 | 1.46e-05%
2028 | BY2 | CB BY2 | Tier-1 | Non-HFTD---14 | 3--1 | 5.662 | 220 | 100% | 6.8497 | 39.29% | 0% | 60.71% | 0.13321 | 0 | 0 | 0.13321 | 0 | 0.11563 | 5.3228 | 0.021724 | 0.11563 | 5.3228 | 0.021724 | 0.13517 | 6.2224 | 0.021724 | 1.945% | 0.017488 | 0.016622 | 391.6915 | 5.1993 | 144.7113 | 241.7808 | 404.0761 | 0 | 0 | 404.0761 | 4.393e-06%
2028 | 1094 | 1094-8AE | Tier-1 | Non-HFTD---17 | 1--2 | 0.30739 | 2 | 100% | 1.7277 | 85.41% | 0% | 14.59% | 0.073046 | 0 | 0 | 0.073046 | 0 | 0.063408 | 0.28897 | 0.21943 | 0.063408 | 0.28897 | 0.21943 | 0.074125 | 0.33781 | 0.21943 | 4.228% | 0.0010582 | 0.0010058 | 1632.6499 | 227.3238 | 25.8915 | 1379.4346 | 1645.0517 | 0 | 0 | 1645.0517 | 2.409e-06%
2028 | 214 | 214-647R | Tier-3 | Tier-3---8 | 5--5 | 11.3022 | 644 | 100% | 22354.3085 | 99.24% | 0.73% | 0.02701% | 1098.1613 | 0 | 0 | 1098.1613 | 0 | 953.2756 | 10.6253 | 89.7179 | 953.2756 | 10.6253 | 89.7179 | 1114.3901 | 12.421 | 89.7179 | 4.913% | 0.23844 | 0.22663 | 93753.9152 | 14837.2709 | 625.983 | 78290.6613 | 93790.8777 | 0 | 0 | 93790.8777 | 0.03621%
2028 | 1458 | 1458-565R | Tier-3 | Tier-3---6 | 5--5 | 5.7011 | 351 | 100% | 8159.9793 | 99.25% | 0.7112% | 0.04348% | 400.8709 | 0 | 0 | 400.8709 | 0 | 347.982 | 5.3596 | 64.9265 | 347.982 | 5.3596 | 64.9265 | 406.795 | 6.2655 | 64.9265 | 4.913% | 0.15819 | 0.15036 | 51582.9513 | 8279.4207 | 334.7207 | 42968.8099 | 51603.2234 | 0 | 0 | 51603.2234 | 0.01322%
2028 | 184 | CB 184 | Tier-1 | Non-HFTD---6 | 3--3 | 0.49848 | 58 | 100% | 52.4866 | 0.7232% | 98.61% | 0.668% | 0.018789 | 0 | 0 | 0.018789 | 0 | 0.01631 | 0.46863 | 0.034803 | 0.01631 | 0.46863 | 0.034803 | 0.019066 | 0.54783 | 0.034803 | 0.0358% | 0.015821 | 0.015038 | 3317.5286 | 5.4671 | 2617.7865 | 694.2749 | 3489.0489 | 0 | 0 | 3489.0489 | 6.196e-07%
2028 | 1049 | CB 1049 | Tier-1 | Non-HFTD---14 | 3--1 | 5.6832 | 256 | 100% | 5.616 | 24.5% | 0% | 75.5% | 0.068108 | 0 | 0 | 0.068108 | 0 | 0.059122 | 5.3428 | 0.011066 | 0.059122 | 5.3428 | 0.011066 | 0.069114 | 6.2458 | 0.011066 | 1.213% | 0.016475 | 0.015659 | 340.8813 | 1.1864 | 100.8318 | 238.863 | 354.2843 | 0 | 0 | 354.2843 | 2.246e-06%
2028 | 1418 | CB 1418 | Tier-1 | Non-HFTD---8 | 3--3 | 6.1513 | 238 | 100% | 37.4539 | 88.02% | 0% | 11.98% | 1.6319 | 0 | 0 | 1.6319 | 0 | 1.4166 | 5.7828 | 0.24496 | 1.4166 | 5.7828 | 0.24496 | 1.656 | 6.7602 | 0.24496 | 4.357% | 0.021901 | 0.020817 | 1710.114 | 123.2993 | 769.7961 | 817.0186 | 1720.7826 | 0 | 0 | 1720.7826 | 5.381e-05%
2028 | 480 | CB 480 | Tier-1 | Non-HFTD---9 | 3--2 | 5.8805 | 429 | 100% | 25.8202 | 85.83% | 0% | 14.17% | 1.097 | 0 | 0 | 1.097 | 0 | 0.9523 | 5.5283 | 0.17226 | 0.9523 | 5.5283 | 0.17226 | 1.1132 | 6.4626 | 0.17226 | 4.249% | 0.015407 | 0.014644 | 1675.8946 | 13.068 | 1380.5081 | 282.3185 | 1688.259 | 0 | 0 | 1688.259 | 3.618e-05%
2028 | BH1 | CB BH1 | Tier-1 | Non-HFTD---18 | 1--1 | 1.0502 | 26 | 100% | 1.0465 | 22.49% | 0% | 77.51% | 0.011651 | 0 | 0 | 0.011651 | 0 | 0.010114 | 0.98729 | 0.010244 | 0.010114 | 0.98729 | 0.010244 | 0.011823 | 1.1542 | 0.010244 | 1.113% | 0.0030896 | 0.0029367 | 338.7265 | 0.6221 | 97.3891 | 240.7153 | 352.3993 | 0 | 0 | 352.3993 | 3.842e-07%
2028 | 387 | 387-15 | Tier-3 | Tier-3---16 | 4--5 | 6.7754 | 306 | 100% | 1455.0528 | 89.01% | 10.72% | 0.2619% | 64.1128 | 0 | 0 | 64.1128 | 0 | 55.6541 | 6.3695 | 8.7375 | 55.6541 | 6.3695 | 8.7375 | 65.0603 | 7.4461 | 8.7375 | 4.406% | 0.072601 | 0.069007 | 20041.7181 | 3328.5132 | 2008.3795 | 14704.8254 | 20156.3764 | 0 | 0 | 20156.3764 | 0.002114%
2028 | 237 | 237-30R | Tier-3 | Tier-3---1 | 5--5 | 33.4712 | 1327 | 100% | 65515.492 | 98.93% | 1.038% | 0.03019% | 3208.3751 | 0 | 0 | 3208.3751 | 0 | 2785.0787 | 31.4663 | 88.5099 | 2785.0787 | 31.4663 | 88.5099 | 3255.7888 | 36.7844 | 88.5099 | 4.897% | 0.49249 | 0.46811 | 133030.3773 | 22547.6539 | 1250.7985 | 109231.9249 | 133104.3812 | 0 | 0 | 133104.3812 | 0.1058%
2028 | 1299 | CB 1299 | Tier-2 | Tier-2---19 | 3--3 | 4.4727 | 32 | 100% | 41.7756 | 94.08% | 0% | 5.924% | 1.9454 | 0 | 0 | 1.9454 | 0 | 1.6887 | 4.2048 | 0.40162 | 1.6887 | 4.2048 | 0.40162 | 1.9742 | 4.9155 | 0.40162 | 4.657% | 0.014997 | 0.014255 | 2785.5246 | 467.5235 | 44.8169 | 2273.1842 | 2794.1175 | 0 | 0 | 2794.1175 | 6.415e-05%
2028 | 928 | CB 928 | Tier-2 | Tier-2---7 | 4--5 | 3.6036 | 30 | 100% | 1655.0106 | 79.76% | 20.12% | 0.1245% | 65.3395 | 0 | 0 | 65.3395 | 0 | 56.719 | 3.3877 | 16.7424 | 56.719 | 3.3877 | 16.7424 | 66.3051 | 3.9603 | 16.7424 | 3.948% | 0.057199 | 0.054367 | 28934.4603 | 4597.4585 | 5524.6499 | 18812.3519 | 29239.4879 | 0 | 0 | 29239.4879 | 0.002155%
2028 | 223 | 223-47AE | Tier-2 | Tier-2---19 | 1--3 | 1.211 | 4 | 100% | 19.4153 | 96.46% | 0% | 3.541% | 0.92702 | 0 | 0 | 0.92702 | 0 | 0.80472 | 1.1384 | 0.70685 | 0.80472 | 1.1384 | 0.70685 | 0.94072 | 1.3309 | 0.70685 | 4.775% | 0.0044072 | 0.004189 | 4405.3509 | 653.8395 | 200.8811 | 3550.6304 | 4413.4748 | 0 | 0 | 4413.4748 | 3.057e-05%
2028 | 274 | 274-23R | Tier-1 | Non-HFTD---2 | 4--3 | 14.1254 | 479 | 100% | 237.9284 | 4.707% | 91.23% | 4.063% | 0.55433 | 0 | 0 | 0.55433 | 0 | 0.4812 | 13.2793 | 0.036237 | 0.4812 | 13.2793 | 0.036237 | 0.56253 | 15.5236 | 0.036237 | 0.233% | 0.05657 | 0.05377 | 4205.9111 | 11.172 | 3702.6633 | 492.0758 | 4414.6365 | 0 | 0 | 4414.6365 | 1.828e-05%
2028 | 972 | 972-942R | Tier-3 | Tier-3---6 | 5--5 | 7.8388 | 378 | 100% | 9149.6836 | 99.12% | 0.8301% | 0.05344% | 448.9075 | 0 | 0 | 448.9075 | 0 | 389.681 | 7.3693 | 52.8792 | 389.681 | 7.3693 | 52.8792 | 455.5415 | 8.6148 | 52.8792 | 4.906% | 0.14195 | 0.13492 | 64459.3584 | 11777.4052 | 488.1508 | 52193.8024 | 64489.0192 | 0 | 0 | 64489.0192 | 0.0148%
2028 | 957 | 957-493 | Tier-1 | Non-HFTD---17 | 1--2 | 0.48785 | 55 | 100% | 2.0962 | 82.3% | 0% | 17.7% | 0.085395 | 0 | 0 | 0.085395 | 0 | 0.074129 | 0.45863 | 0.16163 | 0.074129 | 0.45863 | 0.16163 | 0.086657 | 0.53614 | 0.16163 | 4.074% | 0.001752 | 0.0016653 | 1196.4405 | 130.6529 | 183.8941 | 881.8936 | 1207.4687 | 0 | 0 | 1207.4687 | 2.816e-06%
2028 | 298 | 298-42R | Tier-1 | Non-HFTD---15 | 2--2 | 2.2522 | 46 | 100% | 3.8263 | 63.59% | 0% | 36.41% | 0.12045 | 0 | 0 | 0.12045 | 0 | 0.10455 | 2.1173 | 0.04938 | 0.10455 | 2.1173 | 0.04938 | 0.12223 | 2.4752 | 0.04938 | 3.148% | 0.0063514 | 0.006037 | 602.4284 | 45.032 | 128.6085 | 428.7879 | 613.8503 | 0 | 0 | 613.8503 | 3.972e-06%
2028 | 280 | 280-382AE | Tier-1 | Non-HFTD---3 | 4--3 | 4.587 | 113 | 100% | 117.9502 | 9.67% | 87.78% | 2.549% | 0.56458 | 0 | 0 | 0.56458 | 0 | 0.4901 | 4.3122 | 0.11365 | 0.4901 | 4.3122 | 0.11365 | 0.57293 | 5.041 | 0.11365 | 0.4787% | 0.044174 | 0.041988 | 2670.1025 | 42.9877 | 2159.6326 | 467.4822 | 2795.7093 | 0 | 0 | 2795.7093 | 1.862e-05%
2028 | 504 | 504-40R | Tier-1 | Non-HFTD---1 | 3--5 | 7.4225 | 827 | 100% | 796.3763 | 99.35% | 0% | 0.6476% | 39.1654 | 0 | 0 | 39.1654 | 0 | 33.9981 | 6.9779 | 4.8722 | 33.9981 | 6.9779 | 4.8722 | 39.7441 | 8.1573 | 4.8722 | 4.918% | 0.025961 | 0.024676 | 30675.6364 | 4949.6837 | 226.8975 | 25499.0552 | 30685.9814 | 0 | 0 | 30685.9814 | 0.001292%
2028 | 313 | CB 313 | Tier-1 | Non-HFTD---1 | 3--5 | 1.4046 | 49 | 100% | 413.0978 | 31.58% | 68.15% | 0.2787% | 6.4568 | 0 | 0 | 6.4568 | 0 | 5.6049 | 1.3204 | 4.2448 | 5.6049 | 1.3204 | 4.2448 | 6.5522 | 1.5436 | 4.2448 | 1.563% | 0.023731 | 0.022556 | 17407.518 | 802.6638 | 11509.0826 | 5095.7715 | 18027.8111 | 0 | 0 | 18027.8111 | 0.0002129%
2028 | 412 | 412-23AE | Tier-1 | Non-HFTD---7 | 3--3 | 1.1481 | 46 | 100% | 36.9619 | 12.24% | 85.64% | 2.113% | 0.22399 | 0 | 0 | 0.22399 | 0 | 0.19443 | 1.0793 | 0.18015 | 0.19443 | 1.0793 | 0.18015 | 0.2273 | 1.2617 | 0.18015 | 0.606% | 0.014019 | 0.013325 | 2636.6319 | 50.1124 | 2071.6936 | 514.8259 | 2757.1322 | 0 | 0 | 2757.1322 | 7.386e-06%
2028 | FM2 | CB FM2 | Tier-1 | Non-HFTD---5 | 2--4 | 0.69792 | 11 | 100% | 52.7223 | 13.09% | 85.83% | 1.077% | 0.34171 | 0 | 0 | 0.34171 | 0 | 0.29663 | 0.65611 | 0.4521 | 0.29663 | 0.65611 | 0.4521 | 0.34676 | 0.767 | 0.4521 | 0.6481% | 0.0078724 | 0.0074827 | 6697.1021 | 78.5971 | 5715.8481 | 902.657 | 7000.2057 | 0 | 0 | 7000.2057 | 1.127e-05%
2028 | 781 | 781-1356R | Tier-1 | Non-HFTD---6 | 3--3 | 1.2461 | 146 | 100% | 45.6239 | 7.996% | 89.78% | 2.228% | 0.18059 | 0 | 0 | 0.18059 | 0 | 0.15676 | 1.1714 | 0.13382 | 0.15676 | 1.1714 | 0.13382 | 0.18326 | 1.3694 | 0.13382 | 0.3958% | 0.014432 | 0.013718 | 3161.2121 | 4.0758 | 2704.8503 | 452.2859 | 3312.6768 | 0 | 0 | 3312.6768 | 5.955e-06%
2028 | 1435 | 1435-49F | Tier-1 | Non-HFTD---18 | 2--1 | 2.382 | 56 | 100% | 2.1334 | 19.42% | 0% | 80.58% | 0.020506 | 0 | 0 | 0.020506 | 0 | 0.017801 | 2.2393 | 0.0079492 | 0.017801 | 2.2393 | 0.0079492 | 0.02081 | 2.6178 | 0.0079492 | 0.9612% | 0.0065472 | 0.0062231 | 325.8446 | 0.86487 | 82.925 | 242.0548 | 339.5187 | 0 | 0 | 339.5187 | 6.762e-07%
2028 | 730 | CB 730 | Tier-1 | Non-HFTD---8 | 3--3 | 6.5873 | 247 | 100% | 39.2172 | 89.21% | 0% | 10.79% | 1.7319 | 0 | 0 | 1.7319 | 0 | 1.5034 | 6.1927 | 0.24277 | 1.5034 | 6.1927 | 0.24277 | 1.7575 | 7.2393 | 0.24277 | 4.416% | 0.017589 | 0.016718 | 2229.6927 | 2.4263 | 1997.325 | 229.9414 | 2242.2171 | 0 | 0 | 2242.2171 | 5.711e-05%
2028 | VS1 | CB VS1 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6964 | 484 | 100% | 11.7597 | 45.03% | 0% | 54.97% | 0.26214 | 0 | 0 | 0.26214 | 0 | 0.22755 | 9.1156 | 0.024963 | 0.22755 | 9.1156 | 0.024963 | 0.26601 | 10.6563 | 0.024963 | 2.229% | 0.026595 | 0.025278 | 442.1842 | 4.4933 | 194.8415 | 242.8495 | 454.8421 | 0 | 0 | 454.8421 | 8.644e-06%
2028 | 570 | CB 570 | Tier-1 | Non-HFTD---13 | 2--2 | 2.3449 | 49 | 100% | 7.1017 | 67.21% | 0% | 32.79% | 0.23626 | 0 | 0 | 0.23626 | 0 | 0.20508 | 2.2044 | 0.093034 | 0.20508 | 2.2044 | 0.093034 | 0.23975 | 2.577 | 0.093034 | 3.327% | 0.0078126 | 0.0074259 | 909.0044 | 0.23797 | 637.9097 | 270.8567 | 924.5283 | 0 | 0 | 924.5283 | 7.791e-06%
2028 | 718 | 718-483R | Tier-1 | Non-HFTD---14 | 2--2 | 4.2839 | 92 | 100% | 8.2181 | 68.73% | 0% | 31.27% | 0.2796 | 0 | 0 | 0.2796 | 0 | 0.24271 | 4.0273 | 0.060266 | 0.24271 | 4.0273 | 0.060266 | 0.28373 | 4.7079 | 0.060266 | 3.402% | 0.013173 | 0.012521 | 623.8598 | 87.3514 | 82.9145 | 453.5939 | 634.0188 | 0 | 0 | 634.0188 | 9.22e-06%
2028 | 305 | CB 305 | Tier-1 | Non-HFTD---1 | 4--5 | 5.6647 | 1678 | 100% | 2786.7739 | 97.11% | 2.732% | 0.1605% | 133.9547 | 0 | 0 | 133.9547 | 0 | 116.2814 | 5.3254 | 21.8351 | 116.2814 | 5.3254 | 21.8351 | 135.9343 | 6.2255 | 21.8351 | 4.807% | 0.073949 | 0.070288 | 37685.1802 | 5958.9331 | 946.9636 | 30779.2836 | 37741.9553 | 0 | 0 | 37741.9553 | 0.004417%
2028 | S1 | CB S1 | Tier-1 | Non-HFTD---12 | 3--1 | 9.143 | 170 | 100% | 10.789 | 35.54% | 0% | 64.46% | 0.18979 | 0 | 0 | 0.18979 | 0 | 0.16475 | 8.5953 | 0.019168 | 0.16475 | 8.5953 | 0.019168 | 0.1926 | 10.048 | 0.019168 | 1.759% | 0.026358 | 0.025053 | 409.3304 | 3.5481 | 148.5276 | 257.2547 | 423.0718 | 0 | 0 | 423.0718 | 6.259e-06%
2028 | CS3 | CB CS3 | Tier-1 | Non-HFTD---12 | 3--1 | 10.2084 | 309 | 100% | 11.962 | 43.21% | 0% | 56.79% | 0.25586 | 0 | 0 | 0.25586 | 0 | 0.2221 | 9.5969 | 0.023143 | 0.2221 | 9.5969 | 0.023143 | 0.25964 | 11.2189 | 0.023143 | 2.139% | 0.027808 | 0.026432 | 430.1588 | 12.7842 | 130.688 | 286.6866 | 442.8806 | 0 | 0 | 442.8806 | 8.437e-06%
2028 | 334 | CB 334 | Tier-2 | Tier-2---17 | 3--4 | 5.1123 | 83 | 100% | 70.5162 | 95.08% | 0% | 4.917% | 3.3189 | 0 | 0 | 3.3189 | 0 | 2.881 | 4.8061 | 0.59946 | 2.881 | 4.8061 | 0.59946 | 3.368 | 5.6183 | 0.59946 | 4.707% | 0.014478 | 0.013762 | 4870.4444 | 330.0733 | 2622.0959 | 1918.2753 | 4882.9165 | 0 | 0 | 4882.9165 | 0.0001094%
2028 | 91 | CB 91 | Tier-2 | Tier-2---12 | 3--5 | 2.7814 | 123 | 100% | 337.7351 | 93.43% | 6.078% | 0.496% | 15.6188 | 0 | 0 | 15.6188 | 0 | 13.5581 | 2.6148 | 5.1851 | 13.5581 | 2.6148 | 5.1851 | 15.8496 | 3.0567 | 5.1851 | 4.625% | 0.015476 | 0.01471 | 21823.4311 | 3984.4333 | 1811.7057 | 16027.292 | 21898.15 | 0 | 0 | 21898.15 | 0.000515%
2028 | 1105 | 1105-1479 | Tier-2 | Tier-2---4 | 5--5 | 3.4339 | 113 | 100% | 4228.0435 | 99.92% | 0.03248% | 0.04256% | 209.1311 | 0 | 0 | 209.1311 | 0 | 181.5394 | 3.2282 | 56.2355 | 181.5394 | 3.2282 | 56.2355 | 212.2217 | 3.7738 | 56.2355 | 4.946% | 0.10556 | 0.10034 | 40053.0076 | 8992.3794 | 12.7012 | 31047.927 | 40054.5729 | 0 | 0 | 40054.5729 | 0.006896%
2028 | 215 | 215-1544R | Tier-2 | Tier-2---8 | 5--4 | 2.7396 | 163 | 100% | 1412.4296 | 98.09% | 1.785% | 0.1216% | 68.582 | 0 | 0 | 68.582 | 0 | 59.5336 | 2.5755 | 23.1152 | 59.5336 | 2.5755 | 23.1152 | 69.5955 | 3.0108 | 23.1152 | 4.856% | 0.10891 | 0.10352 | 12968.9923 | 2539.663 | 210.0651 | 10219.2641 | 12981.8719 | 0 | 0 | 12981.8719 | 0.002262%
2028 | GH3 | CB GH3 | Tier-1 | Non-HFTD---14 | 2--1 | 4.7819 | 78 | 100% | 4.974 | 31.67% | 0% | 68.33% | 0.077982 | 0 | 0 | 0.077982 | 0 | 0.067693 | 4.4954 | 0.015058 | 0.067693 | 4.4954 | 0.015058 | 0.079134 | 5.2552 | 0.015058 | 1.568% | 0.013217 | 0.012562 | 376.3479 | 4.2189 | 117.7982 | 254.3308 | 389.7398 | 0 | 0 | 389.7398 | 2.572e-06%
2028 | 105 | 105-239F | Tier-1 | Non-HFTD---15 | 1--3 | 0.26155 | 20 | 100% | 2.4566 | 91.53% | 0% | 8.467% | 0.11131 | 0 | 0 | 0.11131 | 0 | 0.09662 | 0.24589 | 0.39295 | 0.09662 | 0.24589 | 0.39295 | 0.11295 | 0.28744 | 0.39295 | 4.531% | 0.0010678 | 0.0010149 | 2300.6028 | 305.3862 | 246.2943 | 1748.9223 | 2310.7468 | 0 | 0 | 2310.7468 | 3.67e-06%
2028 | 955 | CB 955 | Tier-1 | Non-HFTD---9 | 1--3 | 1.1538 | 14 | 100% | 15.216 | 95.67% | 0% | 4.328% | 0.7206 | 0 | 0 | 0.7206 | 0 | 0.62552 | 1.0847 | 0.57669 | 0.62552 | 1.0847 | 0.57669 | 0.73125 | 1.268 | 0.57669 | 4.736% | 0.0047456 | 0.0045107 | 3206.3351 | 265.3654 | 1425.9225 | 1515.0472 | 3213.5613 | 0 | 0 | 3213.5613 | 2.376e-05%
2028 | BS1 | CB BS1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.2324 | 4 | 100% | 0.21229 | 51.44% | 0% | 48.56% | 0.0054051 | 0 | 0 | 0.0054051 | 0 | 0.004692 | 0.21848 | 0.021475 | 0.004692 | 0.21848 | 0.021475 | 0.005485 | 0.25541 | 0.021475 | 2.546% | 0.0005254 | 0.00049939 | 404.0635 | 34.0597 | 17.826 | 352.1779 | 414.2829 | 0 | 0 | 414.2829 | 1.782e-07%
2028 | 191 | 191-1050R | Tier-1 | Non-HFTD---7 | 3--3 | 4.7722 | 123 | 100% | 34.1164 | 89.07% | 0% | 10.93% | 1.5041 | 0 | 0 | 1.5041 | 0 | 1.3057 | 4.4863 | 0.29104 | 1.3057 | 4.4863 | 0.29104 | 1.5264 | 5.2445 | 0.29104 | 4.409% | 0.014785 | 0.014053 | 2307.4666 | 326.6145 | 80.7742 | 1900.0778 | 2320.6044 | 0 | 0 | 2320.6044 | 4.96e-05%
2028 | 60 | CB 60 | Tier-1 | Non-HFTD---11 | 2--2 | 2.9972 | 97 | 100% | 10.2312 | 82.34% | 0% | 17.66% | 0.41699 | 0 | 0 | 0.41699 | 0 | 0.36198 | 2.8176 | 0.12847 | 0.36198 | 2.8176 | 0.12847 | 0.42316 | 3.2938 | 0.12847 | 4.076% | 0.0090716 | 0.0086226 | 1127.8283 | 37.9694 | 715.1314 | 374.7275 | 1138.2024 | 0 | 0 | 1138.2024 | 1.375e-05%
2028 | 137 | 137-767F | Tier-1 | Non-HFTD---11 | 2--2 | 2.2822 | 137 | 100% | 10.6804 | 81.68% | 0% | 18.32% | 0.43185 | 0 | 0 | 0.43185 | 0 | 0.37487 | 2.1455 | 0.17473 | 0.37487 | 2.1455 | 0.17473 | 0.43823 | 2.5081 | 0.17473 | 4.043% | 0.0070892 | 0.0067383 | 1506.5775 | 163.4925 | 256.9577 | 1086.1273 | 1520.9482 | 0 | 0 | 1520.9482 | 1.424e-05%
2028 | 41 | 41-43 | Tier-1 | Non-HFTD---10 | 4--2 | 14.0575 | 306 | 100% | 19.885 | 49.34% | 0% | 50.66% | 0.48568 | 0 | 0 | 0.48568 | 0 | 0.4216 | 13.2155 | 0.031902 | 0.4216 | 13.2155 | 0.031902 | 0.49286 | 15.4491 | 0.031902 | 2.442% | 0.039263 | 0.037319 | 506.4606 | 0.58714 | 271.667 | 234.2065 | 519.8217 | 0 | 0 | 519.8217 | 1.602e-05%
2028 | 521 | 521-1856R | Tier-3 | Tier-3---6 | 5--5 | 12.1965 | 1116 | 100% | 8477.8617 | 97.79% | 2.104% | 0.1048% | 410.3866 | 0 | 0 | 410.3866 | 0 | 356.2423 | 11.4659 | 31.0697 | 356.2423 | 11.4659 | 31.0697 | 416.4513 | 13.4038 | 31.0697 | 4.841% | 0.15411 | 0.14648 | 55012.684 | 8678.1991 | 1054.7005 | 45279.7844 | 55075.953 | 0 | 0 | 55075.953 | 0.01353%
2028 | 223 | 223-536R | Tier-2 | Tier-2---19 | 1--4 | 0.41023 | 5 | 100% | 17.3686 | 98.33% | 0% | 1.666% | 0.84542 | 0 | 0 | 0.84542 | 0 | 0.73388 | 0.38565 | 1.9029 | 0.73388 | 0.38565 | 1.9029 | 0.85792 | 0.45084 | 1.9029 | 4.868% | 0.0018852 | 0.0017919 | 9213.1285 | 1446.4962 | 15.3355 | 7751.2969 | 9221.1221 | 0 | 0 | 9221.1221 | 2.788e-05%
2028 | 380 | 380-27 | Tier-1 | Non-HFTD---10 | 4--2 | 14.4385 | 565 | 100% | 22.878 | 63.4% | 0% | 36.6% | 0.71795 | 0 | 0 | 0.71795 | 0 | 0.62323 | 13.5736 | 0.045915 | 0.62323 | 13.5736 | 0.045915 | 0.72856 | 15.8677 | 0.045915 | 3.138% | 0.038378 | 0.036478 | 596.1298 | 23.7982 | 253.3548 | 318.9768 | 607.4932 | 0 | 0 | 607.4932 | 2.368e-05%
2028 | 936 | 936-188 | Tier-1 | Non-HFTD---4 | 2--4 | 1.8436 | 201 | 100% | 105.8404 | 98.55% | 0% | 1.448% | 5.1632 | 0 | 0 | 5.1632 | 0 | 4.482 | 1.7332 | 2.586 | 4.482 | 1.7332 | 2.586 | 5.2395 | 2.0261 | 2.586 | 4.878% | 0.0071268 | 0.006774 | 14851.04 | 3722.7452 | 36.3442 | 11091.9506 | 14862.2428 | 0 | 0 | 14862.2428 | 0.0001703%
2028 | 907 | 907-1702R | Tier-3 | Tier-3---6 | 4--5 | 5.3095 | 739 | 100% | 9100.5582 | 99.73% | 0.2344% | 0.03926% | 449.2449 | 0 | 0 | 449.2449 | 0 | 389.9738 | 4.9915 | 78.1281 | 389.9738 | 4.9915 | 78.1281 | 455.8839 | 5.8351 | 78.1281 | 4.936% | 0.061079 | 0.058055 | 148997.4926 | 27594.5733 | 329.8343 | 121073.085 | 149018.7269 | 0 | 0 | 149018.7269 | 0.01481%
2028 | 169 | 169-35F | Tier-1 | Non-HFTD---20 | 1--1 | 0.08387 | 2 | 100% | 0.038151 | 8.843% | 0% | 91.16% | 0.00016699 | 0 | 0 | 0.00016699 | 0 | 0.00014496 | 0.078846 | 0.0018385 | 0.00014496 | 0.078846 | 0.0018385 | 0.00016946 | 0.092172 | 0.0018385 | 0.4377% | 0.0001782 | 0.00016938 | 214.089 | 0.14685 | 36.6598 | 177.2824 | 224.2524 | 0 | 0 | 224.2524 | 5.507e-09%
2028 | 1001 | 1001-1814AE | Tier-2 | Tier-2---11 | 5--3 | 0.43788 | 83 | 100% | 409.0622 | 99.15% | 0.7717% | 0.07851% | 20.0764 | 0 | 0 | 20.0764 | 0 | 17.4277 | 0.41165 | 42.3361 | 17.4277 | 0.41165 | 42.3361 | 20.3731 | 0.48122 | 42.3361 | 4.908% | 0.094213 | 0.089549 | 4341.8958 | 702.528 | 31.2092 | 3608.1586 | 4343.8182 | 0 | 0 | 4343.8182 | 0.000662%
2028 | 542 | CB 542 | Tier-2 | Tier-2---9 | 4--5 | 2.267 | 54 | 100% | 949.4775 | 95.45% | 4.414% | 0.1311% | 44.8628 | 0 | 0 | 44.8628 | 0 | 38.9439 | 2.1313 | 18.2728 | 38.9439 | 2.1313 | 18.2728 | 45.5258 | 2.4915 | 18.2728 | 4.725% | 0.053515 | 0.050866 | 17742.4015 | 2646.628 | 1293.2242 | 13802.5493 | 17784.4002 | 0 | 0 | 17784.4002 | 0.001479%
2028 | 354 | CB 354 | Tier-2 | Tier-2---19 | 1--5 | 0.057008 | 0 | 100% | 12.0695 | 99.46% | 0% | 0.538% | 0.59423 | 0 | 0 | 0.59423 | 0 | 0.51583 | 0.053593 | 9.6249 | 0.51583 | 0.053593 | 9.6249 | 0.60301 | 0.062651 | 9.6249 | 4.923% | 0.0002126 | 0.00020208 | 56770.8652 | 8857.5448 | 1365.0187 | 46548.3017 | 56786.7697 | 0 | 0 | 56786.7697 | 1.96e-05%
2028 | 344 | CB 344 | Tier-1 | Non-HFTD---14 | 3--1 | 4.5935 | 221 | 100% | 6.1717 | 46.7% | 0% | 53.3% | 0.14267 | 0 | 0 | 0.14267 | 0 | 0.12385 | 4.3184 | 0.028679 | 0.12385 | 4.3184 | 0.028679 | 0.14478 | 5.0483 | 0.028679 | 2.312% | 0.013899 | 0.013211 | 444.0383 | 5.5246 | 196.2264 | 242.2874 | 456.3636 | 0 | 0 | 456.3636 | 4.705e-06%
2028 | 518 | 518-42AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.19057 | 7 | 100% | 0.34431 | 29.34% | 0% | 70.66% | 0.0050004 | 0 | 0 | 0.0050004 | 0 | 0.0043406 | 0.17916 | 0.024228 | 0.0043406 | 0.17916 | 0.024228 | 0.0050743 | 0.20944 | 0.024228 | 1.452% | 0.0008198 | 0.00077922 | 419.9978 | 0.47523 | 148.6345 | 270.8881 | 435.4533 | 0 | 0 | 435.4533 | 1.649e-07%
2028 | FM3 | CB FM3 | Tier-1 | Non-HFTD---3 | 4--3 | 9.8417 | 866 | 100% | 121.1123 | 67.77% | 26.62% | 5.609% | 4.0628 | 0 | 0 | 4.0628 | 0 | 3.5267 | 9.2522 | 0.38118 | 3.5267 | 9.2522 | 0.38118 | 4.1228 | 10.8159 | 0.38118 | 3.355% | 0.035117 | 0.033379 | 3448.8213 | 613.5911 | 1013.3761 | 1821.8541 | 3506.7114 | 0 | 0 | 3506.7114 | 0.000134%
2028 | 402 | 402-819F | Tier-1 | Non-HFTD---20 | 1--1 | 0.13463 | 13 | 100% | 0.087285 | 16.51% | 0% | 83.49% | 0.00071325 | 0 | 0 | 0.00071325 | 0 | 0.00061915 | 0.12656 | 0.004892 | 0.00061915 | 0.12656 | 0.004892 | 0.00072379 | 0.14795 | 0.004892 | 0.8172% | 0.0003302 | 0.00031386 | 264.3403 | 3.766 | 41.5642 | 219.0101 | 275.834 | 0 | 0 | 275.834 | 2.352e-08%
2028 | HL1 | CB HL1 | Tier-1 | Non-HFTD---12 | 3--1 | 10.6881 | 256 | 100% | 10.8253 | 37.08% | 0% | 62.92% | 0.19871 | 0 | 0 | 0.19871 | 0 | 0.17249 | 10.0479 | 0.017167 | 0.17249 | 10.0479 | 0.017167 | 0.20164 | 11.7461 | 0.017167 | 1.836% | 0.02785 | 0.026472 | 388.6942 | 5.612 | 146.5056 | 236.5767 | 401.4302 | 0 | 0 | 401.4302 | 6.553e-06%
2028 | 470 | 470-40AE | Tier-2 | Tier-2---4 | 4--5 | 6.1881 | 436 | 100% | 5264.9688 | 98.33% | 1.599% | 0.07273% | 256.2599 | 0 | 0 | 256.2599 | 0 | 222.4503 | 5.8174 | 38.2385 | 222.4503 | 5.8174 | 38.2385 | 260.047 | 6.8007 | 38.2385 | 4.867% | 0.091034 | 0.086528 | 57835.1917 | 10044.8198 | 839.6266 | 46950.7453 | 57885.5342 | 0 | 0 | 57885.5342 | 0.008451%
2028 | 491 | CB 491 | Tier-1 | Non-HFTD---14 | 2--2 | 2.3305 | 61 | 100% | 5.1621 | 58.11% | 0% | 41.89% | 0.14849 | 0 | 0 | 0.14849 | 0 | 0.1289 | 2.1909 | 0.058834 | 0.1289 | 2.1909 | 0.058834 | 0.15069 | 2.5612 | 0.058834 | 2.877% | 0.0082426 | 0.0078346 | 626.2758 | 50.0543 | 81.0381 | 495.1834 | 639.9375 | 0 | 0 | 639.9375 | 4.897e-06%
2028 | 445 | 445-1323 | Tier-2 | Tier-2---18 | 3--3 | 0.19716 | 0 | 100% | 78.5439 | 99.26% | 0.525% | 0.2138% | 3.8592 | 0 | 0 | 3.8592 | 0 | 3.35 | 0.18535 | 18.0742 | 3.35 | 0.18535 | 18.0742 | 3.9162 | 0.21668 | 18.0742 | 4.913% | 0.025445 | 0.024185 | 3086.8349 | 448.9544 | 15.5572 | 2622.3233 | 3088.0226 | 0 | 0 | 3088.0226 | 0.0001273%
2028 | 214 | CB 214 | Tier-3 | Tier-3---20 | 1--5 | 0.040909 | 0 | 100% | 59.1996 | 99.88% | 0% | 0.1188% | 2.9269 | 0 | 0 | 2.9269 | 0 | 2.5407 | 0.038459 | 66.0642 | 2.5407 | 0.038459 | 66.0642 | 2.9702 | 0.044959 | 66.0642 | 4.944% | 0.0002016 | 0.00019162 | 293649.0501 | 47091.7983 | 966.5627 | 245590.6891 | 293667.224 | 0 | 0 | 293667.224 | 9.652e-05%
2028 | 188 | CB 188 | Tier-1 | Non-HFTD---1 | 4--4 | 10.3012 | 692 | 100% | 378.367 | 98.23% | 0% | 1.765% | 18.3985 | 0 | 0 | 18.3985 | 0 | 15.9711 | 9.6842 | 1.6492 | 15.9711 | 9.6842 | 1.6492 | 18.6704 | 11.3209 | 1.6492 | 4.863% | 0.035993 | 0.034211 | 10512.2388 | 2006.1945 | 714.6271 | 7791.4172 | 10521.9037 | 0 | 0 | 10521.9037 | 0.0006067%
2028 | 178 | CB 178 | Tier-1 | Non-HFTD---1 | 2--5 | 3.4303 | 94 | 100% | 644.514 | 99.63% | 0% | 0.3655% | 31.7868 | 0 | 0 | 31.7868 | 0 | 27.593 | 3.2248 | 8.5565 | 27.593 | 3.2248 | 8.5565 | 32.2566 | 3.7699 | 8.5565 | 4.932% | 0.013511 | 0.012843 | 47701.4988 | 11137.324 | 1569.0906 | 34995.0842 | 47710.5792 | 0 | 0 | 47710.5792 | 0.001048%
2028 | 123 | CB 123 | Tier-1 | Non-HFTD---13 | 1--3 | 0.55284 | 1 | 100% | 5.3856 | 82.28% | 0% | 17.72% | 0.21934 | 0 | 0 | 0.21934 | 0 | 0.1904 | 0.51973 | 0.36635 | 0.1904 | 0.51973 | 0.36635 | 0.22258 | 0.60757 | 0.36635 | 4.073% | 0.002683 | 0.0025502 | 2007.2952 | 0.86408 | 1679.9489 | 326.4822 | 2025.8209 | 0 | 0 | 2025.8209 | 7.233e-06%
2028 | 1458 | 1458-456F | Tier-2 | Tier-2---16 | 4--3 | 0.14415 | 19 | 100% | 167.5686 | 29.81% | 70.17% | 0.01889% | 2.4724 | 0 | 0 | 2.4724 | 0 | 2.1462 | 0.13551 | 15.8378 | 2.1462 | 0.13551 | 15.8378 | 2.509 | 0.15842 | 15.8378 | 1.475% | 0.091761 | 0.087218 | 1826.1497 | 89.9148 | 1141.6591 | 594.5758 | 1892.9043 | 0 | 0 | 1892.9043 | 8.153e-05%
2028 | 77 | 77-28R | Tier-1 | Non-HFTD---15 | 1--2 | 1.3614 | 102 | 100% | 2.2554 | 61.57% | 0% | 38.43% | 0.068739 | 0 | 0 | 0.068739 | 0 | 0.05967 | 1.2798 | 0.046624 | 0.05967 | 1.2798 | 0.046624 | 0.069755 | 1.4961 | 0.046624 | 3.048% | 0.003703 | 0.0035197 | 609.0688 | 47.1548 | 109.5378 | 452.3762 | 621.2579 | 0 | 0 | 621.2579 | 2.267e-06%
2028 | 395 | 395-33R | Tier-2 | Tier-2---11 | 4--3 | 0.79815 | 51 | 100% | 396.9757 | 0.1391% | 99.74% | 0.1245% | 0.02734 | 0 | 0 | 0.02734 | 0 | 0.023733 | 0.75034 | 0.03163 | 0.023733 | 0.75034 | 0.03163 | 0.027744 | 0.87716 | 0.03163 | 0.006887% | 0.092102 | 0.087543 | 4310.174 | 6.5289 | 3952.6979 | 350.9472 | 4534.3264 | 0 | 0 | 4534.3264 | 9.016e-07%
2028 | 1039 | CB 1039 | Tier-1 | Non-HFTD---6 | 4--3 | 0.84625 | 23 | 100% | 89.254 | 66.42% | 32.73% | 0.8498% | 2.9347 | 0 | 0 | 2.9347 | 0 | 2.5475 | 0.79556 | 3.2021 | 2.5475 | 0.79556 | 3.2021 | 2.978 | 0.93002 | 3.2021 | 3.288% | 0.047241 | 0.044903 | 1889.3167 | 183.5723 | 702.9111 | 1002.8332 | 1922.3524 | 0 | 0 | 1922.3524 | 9.677e-05%
2028 | 908 | 908-1368R | Tier-2 | Tier-2---5 | 5--5 | 18.6854 | 1073 | 100% | 5570.7929 | 96.25% | 3.531% | 0.2207% | 265.4096 | 0 | 0 | 265.4096 | 0 | 230.3929 | 17.5661 | 13.1157 | 230.3929 | 17.5661 | 13.1157 | 269.3319 | 20.535 | 13.1157 | 4.764% | 0.23644 | 0.22474 | 23560.7485 | 3807.7086 | 754.5572 | 18998.4826 | 23606.7777 | 0 | 0 | 23606.7777 | 0.008752%
2028 | 416 | 416-29AE | Tier-1 | Non-HFTD---19 | 1--1 | 0.34208 | 11 | 100% | 0.44314 | 13.31% | 0% | 86.69% | 0.0029191 | 0 | 0 | 0.0029191 | 0 | 0.002534 | 0.32159 | 0.0078796 | 0.002534 | 0.32159 | 0.0078796 | 0.0029623 | 0.37594 | 0.0078796 | 0.6587% | 0.0012336 | 0.0011725 | 359.222 | 0.32475 | 75.5335 | 283.3638 | 375.4399 | 0 | 0 | 375.4399 | 9.626e-08%
2028 | 283 | CB 283 | Tier-3 | Tier-3---21 | 1--5 | 0.0060606 | 1 | 100% | 6.0451 | 99.41% | 0% | 0.5857% | 0.29748 | 0 | 0 | 0.29748 | 0 | 0.25823 | 0.0056976 | 45.3234 | 0.25823 | 0.0056976 | 45.3234 | 0.30188 | 0.0066605 | 45.3234 | 4.921% | 7.6e-05 | 7.2238e-05 | 79541.4151 | 12489.5349 | 411.7525 | 66640.1278 | 79565.6757 | 0 | 0 | 79565.6757 | 9.81e-06%
2028 | 1105 | 1105-1483 | Tier-2 | Tier-2---11 | 4--4 | 0.32386 | 75 | 100% | 417.0013 | 94.5% | 5.418% | 0.08666% | 19.5054 | 0 | 0 | 19.5054 | 0 | 16.9319 | 0.30446 | 55.6122 | 16.9319 | 0.30446 | 55.6122 | 19.7936 | 0.35592 | 55.6122 | 4.678% | 0.063819 | 0.06066 | 6534.1451 | 1004.5674 | 285.3302 | 5244.2475 | 6552.8754 | 0 | 0 | 6552.8754 | 0.0006432%
2028 | 941 | 941-33F | Tier-1 | Non-HFTD---10 | 3--2 | 9.9011 | 248 | 100% | 24.7891 | 72.11% | 0% | 27.89% | 0.88483 | 0 | 0 | 0.88483 | 0 | 0.76809 | 9.3081 | 0.082519 | 0.76809 | 9.3081 | 0.082519 | 0.89791 | 10.8812 | 0.082519 | 3.569% | 0.028474 | 0.027064 | 870.5979 | 65.8276 | 379.4765 | 425.2938 | 883.243 | 0 | 0 | 883.243 | 2.918e-05%
2028 | 330 | 330-810R | Tier-1 | Non-HFTD---2 | 3--4 | 2.7411 | 85 | 100% | 235.3556 | 4.74% | 94.16% | 1.096% | 0.55218 | 0 | 0 | 0.55218 | 0 | 0.47932 | 2.5769 | 0.18601 | 0.47932 | 2.5769 | 0.18601 | 0.56034 | 3.0124 | 0.18601 | 0.2346% | 0.026057 | 0.024767 | 9032.2679 | 9.3042 | 8071.7191 | 951.2446 | 9480.3546 | 0 | 0 | 9480.3546 | 1.821e-05%
2028 | 795 | 795-821F | Tier-1 | Non-HFTD---6 | 3--3 | 2.1524 | 92 | 100% | 48.0743 | 18.57% | 77.45% | 3.984% | 0.44179 | 0 | 0 | 0.44179 | 0 | 0.3835 | 2.0235 | 0.18953 | 0.3835 | 2.0235 | 0.18953 | 0.44832 | 2.3655 | 0.18953 | 0.919% | 0.024764 | 0.023538 | 1941.2839 | 16.1722 | 1572.1152 | 352.9965 | 2023.6128 | 0 | 0 | 2023.6128 | 1.457e-05%
2028 | 1233 | CB 1233 | Tier-3 | Tier-3---21 | 1--4 | 0.011364 | 0 | 100% | 0.76155 | 90.92% | 0% | 9.083% | 0.034272 | 0 | 0 | 0.034272 | 0 | 0.029751 | 0.010683 | 2.7849 | 0.029751 | 0.010683 | 2.7849 | 0.034779 | 0.012489 | 2.7849 | 4.5% | 0.0001248 | 0.00011862 | 6102.1444 | 830.5531 | 104.2913 | 5167.3 | 6131.0101 | 0 | 0 | 6131.0101 | 1.13e-06%
2028 | 340 | 340-378F | Tier-1 | Non-HFTD---1 | 3--4 | 8.3752 | 891 | 100% | 393.7851 | 98.57% | 0% | 1.434% | 19.2129 | 0 | 0 | 19.2129 | 0 | 16.678 | 7.8735 | 2.1182 | 16.678 | 7.8735 | 2.1182 | 19.4968 | 9.2042 | 2.1182 | 4.879% | 0.02753 | 0.026167 | 14303.9568 | 3018.559 | 106.2503 | 11179.1475 | 14314.6375 | 0 | 0 | 14314.6375 | 0.0006336%
2028 | 353 | 353-901F | Tier-2 | Tier-2---4 | 5--5 | 2.3892 | 145 | 100% | 4555.6189 | 94.3% | 5.656% | 0.04182% | 212.6544 | 0 | 0 | 212.6544 | 0 | 184.5979 | 2.2461 | 82.1854 | 184.5979 | 2.2461 | 82.1854 | 215.797 | 2.6257 | 82.1854 | 4.668% | 0.10618 | 0.10093 | 42903.6289 | 8030.1734 | 2213.8729 | 32659.5826 | 43030.9365 | 0 | 0 | 43030.9365 | 0.007013%
2028 | 426 | CB 426 | Tier-1 | Non-HFTD---19 | 1--1 | 0.040909 | 5 | 100% | 0.070175 | 3.474% | 0% | 96.53% | 0.00012067 | 0 | 0 | 0.00012067 | 0 | 0.00010475 | 0.038459 | 0.0027237 | 0.00010475 | 0.038459 | 0.0027237 | 0.00012245 | 0.044959 | 0.0027237 | 0.172% | 0.0001956 | 0.00018592 | 358.7676 | 1.9592 | 33.3661 | 323.4423 | 376.8024 | 0 | 0 | 376.8024 | 3.979e-09%
2028 | 310 | 310-1192F | Tier-1 | Non-HFTD---2 | 4--4 | 9.1648 | 499 | 100% | 284.9417 | 1.867% | 95.71% | 2.424% | 0.26335 | 0 | 0 | 0.26335 | 0 | 0.2286 | 8.6158 | 0.026533 | 0.2286 | 8.6158 | 0.026533 | 0.26724 | 10.072 | 0.026533 | 0.09242% | 0.04251 | 0.040406 | 6702.9643 | 7.4996 | 5968.2158 | 727.249 | 7045.5227 | 0 | 0 | 7045.5227 | 8.684e-06%
2028 | 362 | 362-40F | Tier-1 | Non-HFTD---11 | 2--2 | 1.0875 | 41 | 100% | 13.0284 | 1.16% | 93.92% | 4.92% | 0.0074835 | 0 | 0 | 0.0074835 | 0 | 0.0064962 | 1.0224 | 0.0063541 | 0.0064962 | 1.0224 | 0.0063541 | 0.0075941 | 1.1951 | 0.0063541 | 0.05744% | 0.008482 | 0.0080621 | 1536.0068 | 3.2594 | 1317.0481 | 215.6994 | 1615.0705 | 0 | 0 | 1615.0705 | 2.468e-07%
2028 | 191 | CB 191 | Tier-1 | Non-HFTD---11 | 2--2 | 3.2041 | 104 | 100% | 11.195 | 80.08% | 0% | 19.92% | 0.44379 | 0 | 0 | 0.44379 | 0 | 0.38524 | 3.0122 | 0.12789 | 0.38524 | 3.0122 | 0.12789 | 0.45035 | 3.5213 | 0.12789 | 3.964% | 0.009482 | 0.0090126 | 1180.6585 | 96.7187 | 494.004 | 589.9358 | 1192.904 | 0 | 0 | 1192.904 | 1.463e-05%
2028 | 298 | CB 298 | Tier-1 | Non-HFTD---9 | 1--4 | 1.1671 | 125 | 100% | 17.6868 | 96.46% | 0% | 3.539% | 0.84451 | 0 | 0 | 0.84451 | 0 | 0.73309 | 1.0972 | 0.66817 | 0.73309 | 1.0972 | 0.66817 | 0.85699 | 1.2826 | 0.66817 | 4.775% | 0.0035214 | 0.0033471 | 5022.6742 | 642.7129 | 927.2824 | 3452.679 | 5031.9322 | 0 | 0 | 5031.9322 | 2.785e-05%
2028 | 143 | CB 143 | Tier-1 | Non-HFTD---4 | 3--4 | 3.3491 | 132 | 100% | 145.6039 | 54.61% | 44.11% | 1.276% | 3.9361 | 0 | 0 | 3.9361 | 0 | 3.4168 | 3.1485 | 1.0852 | 3.4168 | 3.1485 | 1.0852 | 3.9943 | 3.6806 | 1.0852 | 2.703% | 0.016042 | 0.015248 | 9076.1902 | 871.9142 | 5424.8557 | 2779.4204 | 9290.7228 | 0 | 0 | 9290.7228 | 0.0001298%
2028 | 230 | 230-1586R | Tier-2 | Tier-2---7 | 4--5 | 8.614 | 1088 | 100% | 2072.8837 | 91.06% | 8.635% | 0.3% | 93.4394 | 0 | 0 | 93.4394 | 0 | 81.1115 | 8.098 | 10.0162 | 81.1115 | 8.098 | 10.0162 | 94.8202 | 9.4667 | 10.0162 | 4.508% | 0.084625 | 0.080436 | 24494.9333 | 3610.2418 | 2037.5267 | 18847.1648 | 24608.9164 | 0 | 0 | 24608.9164 | 0.003081%
2028 | 520 | 520-22R | Tier-2 | Tier-2---14 | 4--4 | 3.0796 | 180 | 100% | 258.296 | 74.72% | 24.53% | 0.7505% | 9.5538 | 0 | 0 | 9.5538 | 0 | 8.2934 | 2.8951 | 2.8646 | 8.2934 | 2.8951 | 2.8646 | 9.695 | 3.3844 | 2.8646 | 3.699% | 0.036011 | 0.034228 | 7172.7783 | 1320.6919 | 1869.4908 | 3982.5956 | 7267.1983 | 0 | 0 | 7267.1983 | 0.0003151%
2028 | 381 | 381-49 | Tier-1 | Non-HFTD---19 | 1--1 | 0.0083333 | 0 | 100% | 0.029666 | 0.1223% | 0% | 99.88% | 1.7956e-06 | 0 | 0 | 1.7956e-06 | 0 | 1.5587e-06 | 0.0078342 | 0.00019896 | 1.5587e-06 | 0.0078342 | 0.00019896 | 1.8222e-06 | 0.0091582 | 0.00019896 | 0.006053% | 6.36e-05 | 6.0452e-05 | 466.4424 | 0.35055 | 42.8905 | 423.2013 | 490.704 | 0 | 0 | 490.704 | 5.921e-11%
2028 | 376 | 376-527AE | Tier-1 | Non-HFTD---19 | 1--3 | 0.051894 | 0 | 100% | 0.49148 | 77.98% | 0% | 22.02% | 0.018971 | 0 | 0 | 0.018971 | 0 | 0.016468 | 0.048786 | 0.33756 | 0.016468 | 0.048786 | 0.33756 | 0.019251 | 0.057031 | 0.33756 | 3.86% | 0.0002636 | 0.00025055 | 1864.5025 | 6.946 | 1450.3613 | 407.1952 | 1885.8844 | 0 | 0 | 1885.8844 | 6.256e-07%
2028 | 1243 | 1243-38R | Tier-2 | Tier-2---16 | 4--3 | 0.34621 | 20 | 100% | 158.2514 | 99.48% | 0.3681% | 0.155% | 7.7925 | 0 | 0 | 7.7925 | 0 | 6.7644 | 0.32547 | 20.7831 | 6.7644 | 0.32547 | 20.7831 | 7.9076 | 0.38048 | 20.7831 | 4.924% | 0.072591 | 0.068997 | 2180.0532 | 345.5554 | 6.6981 | 1827.7997 | 2180.6472 | 0 | 0 | 2180.6472 | 0.000257%
2028 | 981 | CB 981 | Tier-2 | Tier-2---15 | 1--5 | 0.87121 | 109 | 100% | 132.7571 | 99.65% | 0% | 0.354% | 6.5482 | 0 | 0 | 6.5482 | 0 | 5.6843 | 0.81903 | 6.9403 | 5.6843 | 0.81903 | 6.9403 | 6.645 | 0.95745 | 6.9403 | 4.932% | 0.0030076 | 0.0028587 | 44140.5414 | 6652.1756 | 3087.2085 | 34401.1573 | 44148.6786 | 0 | 0 | 44148.6786 | 0.0002159%
2028 | 834 | 834-887AE | Tier-2 | Tier-2---17 | 2--4 | 1.3721 | 178 | 100% | 70.3467 | 98.64% | 0% | 1.356% | 3.435 | 0 | 0 | 3.435 | 0 | 2.9818 | 1.29 | 2.3115 | 2.9818 | 1.29 | 2.3115 | 3.4857 | 1.508 | 2.3115 | 4.883% | 0.0050886 | 0.0048367 | 13824.3748 | 4928.7906 | 56.7151 | 8838.8691 | 13834.1342 | 0 | 0 | 13834.1342 | 0.0001133%
2028 | 522 | 522-36 | Tier-2 | Tier-2---16 | 4--3 | 2.2803 | 93 | 100% | 116.9577 | 22.53% | 76.17% | 1.295% | 1.3046 | 0 | 0 | 1.3046 | 0 | 1.1324 | 2.1437 | 0.52827 | 1.1324 | 2.1437 | 0.52827 | 1.3238 | 2.506 | 0.52827 | 1.115% | 0.031092 | 0.029553 | 3761.7134 | 135.7107 | 2618.1163 | 1007.8864 | 3913.4717 | 0 | 0 | 3913.4717 | 4.302e-05%
2028 | 206 | 206-953R | Tier-1 | Non-HFTD---1 | 3--5 | 8.4224 | 554 | 100% | 1585.8519 | 99.67% | 0% | 0.3254% | 78.2443 | 0 | 0 | 78.2443 | 0 | 67.9211 | 7.9179 | 8.5782 | 67.9211 | 7.9179 | 8.5782 | 79.4006 | 9.2561 | 8.5782 | 4.934% | 0.026002 | 0.024715 | 60989.6136 | 9907.2213 | 216.3013 | 50866.0909 | 60999.9476 | 0 | 0 | 60999.9476 | 0.00258%
2028 | 418 | CB 418 | Tier-1 | Non-HFTD---8 | 3--2 | 7.4191 | 168 | 100% | 32.4786 | 83.15% | 0% | 16.85% | 1.3368 | 0 | 0 | 1.3368 | 0 | 1.1605 | 6.9747 | 0.16638 | 1.1605 | 6.9747 | 0.16638 | 1.3566 | 8.1535 | 0.16638 | 4.116% | 0.022349 | 0.021243 | 1453.2194 | 9.9672 | 1170.7456 | 272.5066 | 1465.9693 | 0 | 0 | 1465.9693 | 4.408e-05%
2028 | SW3 | CB SW3 | Tier-1 | Non-HFTD---10 | 3--2 | 7.1382 | 267 | 100% | 18.2834 | 70.37% | 0% | 29.63% | 0.63685 | 0 | 0 | 0.63685 | 0 | 0.55282 | 6.7107 | 0.08238 | 0.55282 | 6.7107 | 0.08238 | 0.64626 | 7.8448 | 0.08238 | 3.483% | 0.021128 | 0.020082 | 865.3622 | 65.6443 | 230.815 | 568.9028 | 878.7164 | 0 | 0 | 878.7164 | 2.1e-05%
2028 | RV2 | CB RV2 | Tier-1 | Non-HFTD---18 | 1--1 | 0.8741 | 49 | 100% | 0.72292 | 8.676% | 0% | 91.32% | 0.0031046 | 0 | 0 | 0.0031046 | 0 | 0.002695 | 0.82174 | 0.0032796 | 0.002695 | 0.82174 | 0.0032796 | 0.0031505 | 0.96062 | 0.0032796 | 0.4295% | 0.0024738 | 0.0023513 | 292.2303 | 0.20082 | 49.5965 | 242.4329 | 306.1286 | 0 | 0 | 306.1286 | 1.024e-07%
2028 | 299 | 299-1153F | Tier-1 | Non-HFTD---11 | 1--4 | 0.33445 | 5 | 100% | 12.6944 | 96.89% | 0% | 3.107% | 0.60885 | 0 | 0 | 0.60885 | 0 | 0.52852 | 0.31442 | 1.6809 | 0.52852 | 0.31442 | 1.6809 | 0.61785 | 0.36756 | 1.6809 | 4.796% | 0.0013374 | 0.0012712 | 9491.8205 | 1360.071 | 891.9808 | 7239.7687 | 9507.1772 | 0 | 0 | 9507.1772 | 2.008e-05%
2028 | 221 | 221-824 | Tier-3 | Tier-3---13 | 5--4 | 3.4163 | 181 | 100% | 2324.2215 | 96.86% | 3.03% | 0.1069% | 111.4397 | 0 | 0 | 111.4397 | 0 | 96.7369 | 3.2117 | 30.1205 | 96.7369 | 3.2117 | 30.1205 | 113.0865 | 3.7545 | 30.1205 | 4.795% | 0.18396 | 0.17486 | 12634.0691 | 1992.2766 | 356.0024 | 10285.7901 | 12654.7103 | 0 | 0 | 12654.7103 | 0.003675%
2028 | 138 | 138-366 | Tier-1 | Non-HFTD---19 | 1--1 | 0.08428 | 0 | 100% | 0.163 | 7.427% | 0% | 92.57% | 0.00059926 | 0 | 0 | 0.00059926 | 0 | 0.0005202 | 0.079232 | 0.0065655 | 0.0005202 | 0.079232 | 0.0065655 | 0.00060812 | 0.092623 | 0.0065655 | 0.3676% | 0.000406 | 0.0003859 | 401.4766 | 0.27966 | 63.5802 | 337.6168 | 420.8318 | 0 | 0 | 420.8318 | 1.976e-08%
2028 | 234 | 234-48R | Tier-2 | Tier-2---4 | 4--5 | 11.5796 | 1432 | 100% | 4939.3793 | 99.46% | 0.3916% | 0.1518% | 243.1707 | 0 | 0 | 243.1707 | 0 | 211.088 | 10.886 | 19.3908 | 211.088 | 10.886 | 19.3908 | 246.7643 | 12.7258 | 19.3908 | 4.923% | 0.047931 | 0.045559 | 103051.0115 | 20615.902 | 443.8608 | 81991.2487 | 103080.1738 | 0 | 0 | 103080.1738 | 0.008019%
2028 | 417 | 417-21R | Tier-1 | Non-HFTD---3 | 4--3 | 10.3053 | 362 | 100% | 169.2976 | 37.28% | 58.96% | 3.759% | 3.1239 | 0 | 0 | 3.1239 | 0 | 2.7117 | 9.688 | 0.27991 | 2.7117 | 9.688 | 0.27991 | 3.17 | 11.3254 | 0.27991 | 1.845% | 0.039679 | 0.037715 | 4266.681 | 378.3982 | 2573.6009 | 1314.6819 | 4406.0517 | 0 | 0 | 4406.0517 | 0.000103%
2028 | 355 | CB 355 | Tier-2 | Tier-2---3 | 5--5 | 8.9743 | 877 | 100% | 11288.3525 | 98.84% | 1.109% | 0.05403% | 552.2734 | 0 | 0 | 552.2734 | 0 | 479.4093 | 8.4367 | 56.8242 | 479.4093 | 8.4367 | 56.8242 | 560.435 | 9.8626 | 56.8242 | 4.892% | 0.1048 | 0.099616 | 107709.793 | 22403.5173 | 1198.9113 | 84107.3644 | 107775.044 | 0 | 0 | 107775.044 | 0.01821%
2028 | 144 | 144-445F | Tier-1 | Non-HFTD---7 | 3--3 | 3.6072 | 172 | 100% | 44.172 | 3.542% | 89.64% | 6.821% | 0.077447 | 0 | 0 | 0.077447 | 0 | 0.067229 | 3.3912 | 0.019825 | 0.067229 | 3.3912 | 0.019825 | 0.078591 | 3.9643 | 0.019825 | 0.1753% | 0.01688 | 0.016045 | 2616.7604 | 3.9028 | 2254.4176 | 358.4401 | 2748.2088 | 0 | 0 | 2748.2088 | 2.554e-06%
2028 | 286 | 286-1053R | Tier-1 | Non-HFTD---6 | 4--3 | 9.9807 | 1044 | 100% | 76.5163 | 19.5% | 72.04% | 8.463% | 0.73848 | 0 | 0 | 0.73848 | 0 | 0.64105 | 9.3829 | 0.068321 | 0.64105 | 9.3829 | 0.068321 | 0.7494 | 10.9687 | 0.068321 | 0.9651% | 0.033619 | 0.031955 | 2275.9575 | 19.2195 | 1851.9212 | 404.8167 | 2371.3746 | 0 | 0 | 2371.3746 | 2.435e-05%
2028 | 175 | 175-64R | Tier-3 | Tier-3---11 | 5--5 | 10.35 | 794 | 100% | 4385.4004 | 97.52% | 2.308% | 0.1684% | 211.7013 | 0 | 0 | 211.7013 | 0 | 183.7705 | 9.7301 | 18.8869 | 183.7705 | 9.7301 | 18.8869 | 214.8298 | 11.3746 | 18.8869 | 4.827% | 0.20232 | 0.19231 | 21675.2228 | 3768.1363 | 445.824 | 17461.2625 | 21703.178 | 0 | 0 | 21703.178 | 0.006981%
2028 | 1233 | 1233-585R | Tier-3 | Tier-3---12 | 5--5 | 6.2353 | 475 | 100% | 3561.9587 | 98.42% | 1.457% | 0.1235% | 173.5298 | 0 | 0 | 173.5298 | 0 | 150.6352 | 5.8618 | 25.6979 | 150.6352 | 5.8618 | 25.6979 | 176.0942 | 6.8525 | 25.6979 | 4.872% | 0.12988 | 0.12345 | 27424.4063 | 4490.301 | 369.0567 | 22565.0486 | 27446.9828 | 0 | 0 | 27446.9828 | 0.005722%
2028 | 909 | 909-453R | Tier-2 | Tier-2---3 | 2--5 | 2.3515 | 10 | 100% | 5703.0403 | 99.97% | 0% | 0.03309% | 282.2071 | 0 | 0 | 282.2071 | 0 | 244.9741 | 2.2107 | 110.8143 | 244.9741 | 2.2107 | 110.8143 | 286.3776 | 2.5843 | 110.8143 | 4.948% | 0.0097928 | 0.0093081 | 582370.7512 | 94031.5141 | 664.3163 | 487674.9208 | 582380.7865 | 0 | 0 | 582380.7865 | 0.009306%
2028 | 178 | 178-48 | Tier-1 | Non-HFTD---15 | 1--3 | 0.243 | 28 | 100% | 2.3951 | 91.42% | 0% | 8.578% | 0.10839 | 0 | 0 | 0.10839 | 0 | 0.094086 | 0.22844 | 0.41185 | 0.094086 | 0.22844 | 0.41185 | 0.10999 | 0.26705 | 0.41185 | 4.525% | 0.0008186 | 0.00077808 | 2925.8017 | 435.8246 | 30.2443 | 2459.7328 | 2938.8721 | 0 | 0 | 2938.8721 | 3.574e-06%
2028 | 719 | 719-856F | Tier-1 | Non-HFTD---20 | 1--1 | 0.65096 | 19 | 100% | 0.5127 | 9.051% | 0% | 90.95% | 0.0022971 | 0 | 0 | 0.0022971 | 0 | 0.001994 | 0.61197 | 0.0032584 | 0.001994 | 0.61197 | 0.0032584 | 0.002331 | 0.7154 | 0.0032584 | 0.448% | 0.0018984 | 0.0018044 | 270.0677 | 0.18482 | 46.7574 | 223.1254 | 282.8592 | 0 | 0 | 282.8592 | 7.575e-08%
2028 | 308 | 308-484AE | Tier-1 | Non-HFTD---3 | 4--3 | 4.8747 | 173 | 100% | 121.7186 | 8.654% | 88.76% | 2.589% | 0.52141 | 0 | 0 | 0.52141 | 0 | 0.45262 | 4.5827 | 0.098768 | 0.45262 | 4.5827 | 0.098768 | 0.52912 | 5.3572 | 0.098768 | 0.4284% | 0.043365 | 0.041218 | 2806.8523 | 43.4645 | 2320.9674 | 442.4205 | 2940.3772 | 0 | 0 | 2940.3772 | 1.719e-05%
2028 | 517 | CB 517 | Tier-1 | Non-HFTD---13 | 2--2 | 2.9201 | 69 | 100% | 8.4391 | 68.2% | 0% | 31.8% | 0.28488 | 0 | 0 | 0.28488 | 0 | 0.2473 | 2.7452 | 0.090085 | 0.2473 | 2.7452 | 0.090085 | 0.28909 | 3.2091 | 0.090085 | 3.376% | 0.010508 | 0.0099879 | 803.1131 | 55.9391 | 225.7298 | 521.4442 | 816.4147 | 0 | 0 | 816.4147 | 9.394e-06%
2028 | 590 | CB 590 | Tier-1 | Non-HFTD---1 | 4--5 | 1.5992 | 53 | 100% | 1201.4044 | 63.12% | 36.78% | 0.1021% | 37.535 | 0 | 0 | 37.535 | 0 | 32.5828 | 1.5034 | 21.672 | 32.5828 | 1.5034 | 21.672 | 38.0897 | 1.7575 | 21.672 | 3.124% | 0.042337 | 0.040241 | 28377.3086 | 3599.9822 | 10019.8495 | 14757.4769 | 28922.3867 | 0 | 0 | 28922.3867 | 0.001238%
2028 | 907 | CB 907 | Tier-3 | Tier-3---13 | 3--5 | 1.375 | 64 | 100% | 2742.2838 | 99.83% | 0.1274% | 0.03844% | 135.5179 | 0 | 0 | 135.5179 | 0 | 117.6384 | 1.2926 | 91.0092 | 117.6384 | 1.2926 | 91.0092 | 137.5206 | 1.5111 | 91.0092 | 4.942% | 0.023668 | 0.022497 | 115862.6602 | 23455.2181 | 132.6973 | 92274.7448 | 115872.6663 | 0 | 0 | 115872.6663 | 0.004469%
2028 | 1021 | 1021-1760R | Tier-3 | Tier-3---6 | 5--5 | 2.9682 | 204 | 100% | 7055.7157 | 98.18% | 1.793% | 0.03106% | 342.8861 | 0 | 0 | 342.8861 | 0 | 297.6475 | 2.7904 | 106.6677 | 297.6475 | 2.7904 | 106.6677 | 347.9533 | 3.262 | 106.6677 | 4.86% | 0.10829 | 0.10293 | 65155.0235 | 11761.6096 | 1070.3945 | 52323.0195 | 65216.9272 | 0 | 0 | 65216.9272 | 0.01131%
2028 | 240 | 240-2032R | Tier-3 | Tier-3---12 | 5--5 | 13.8096 | 550 | 100% | 3665.7351 | 96.82% | 2.929% | 0.2538% | 175.6782 | 0 | 0 | 175.6782 | 0 | 152.5001 | 12.9824 | 11.7466 | 152.5001 | 12.9824 | 11.7466 | 178.2744 | 15.1766 | 11.7466 | 4.792% | 0.12278 | 0.1167 | 29856.9037 | 4756.4874 | 803.6507 | 24296.7656 | 29906.3959 | 0 | 0 | 29906.3959 | 0.005793%
2028 | 67 | 67-37R | Tier-3 | Tier-3---17 | 5--3 | 8.2782 | 241 | 100% | 622.3042 | 87.18% | 11.98% | 0.8373% | 26.8549 | 0 | 0 | 26.8549 | 0 | 23.3118 | 7.7824 | 2.9955 | 23.3118 | 7.7824 | 2.9955 | 27.2518 | 9.0977 | 2.9955 | 4.315% | 0.20095 | 0.191 | 3096.8174 | 368.9872 | 339.0656 | 2388.7646 | 3117.4933 | 0 | 0 | 3117.4933 | 0.0008856%
2028 | 520 | 520-1902R | Tier-2 | Tier-2---9 | 4--4 | 10.4533 | 579 | 100% | 748.333 | 77.34% | 21.7% | 0.962% | 28.6477 | 0 | 0 | 28.6477 | 0 | 24.868 | 9.8271 | 2.5306 | 24.868 | 9.8271 | 2.5306 | 29.071 | 11.488 | 2.5306 | 3.828% | 0.058932 | 0.056015 | 12698.2886 | 2074.7299 | 2551.2719 | 8072.2868 | 12848.1568 | 0 | 0 | 12848.1568 | 0.0009447%
2028 | 139 | 139-48 | Tier-1 | Non-HFTD---10 | 3--2 | 5.7198 | 188 | 100% | 22.1253 | 79.12% | 0% | 20.88% | 0.86657 | 0 | 0 | 0.86657 | 0 | 0.75224 | 5.3772 | 0.13989 | 0.75224 | 5.3772 | 0.13989 | 0.87938 | 6.286 | 0.13989 | 3.917% | 0.020647 | 0.019625 | 1071.5768 | 0.73997 | 864.6922 | 206.1446 | 1083.2264 | 0 | 0 | 1083.2264 | 2.858e-05%
2028 | 595 | 595-500 | Tier-1 | Non-HFTD---1 | 3--4 | 2.1604 | 125 | 100% | 238.2364 | 29.81% | 69.49% | 0.6998% | 3.5151 | 0 | 0 | 3.5151 | 0 | 3.0514 | 2.031 | 1.5024 | 3.0514 | 2.031 | 1.5024 | 3.5671 | 2.3743 | 1.5024 | 1.475% | 0.021896 | 0.020812 | 10880.3635 | 1188.0308 | 6831.5625 | 2860.7703 | 11278.0913 | 0 | 0 | 11278.0913 | 0.0001159%
2028 | 1090 | 1090-639R | Tier-3 | Tier-3---18 | 5--2 | 4.354 | 0 | 100% | 509.5021 | 91.97% | 7.519% | 0.512% | 23.1948 | 0 | 0 | 23.1948 | 0 | 20.1346 | 4.0932 | 4.9191 | 20.1346 | 4.0932 | 4.9191 | 23.5376 | 4.785 | 4.9191 | 4.552% | 0.37006 | 0.35174 | 1376.8236 | 183.1657 | 83.207 | 1110.4509 | 1382.5822 | 0 | 0 | 1382.5822 | 0.0007649%
2028 | 599 | CB 599 | Tier-2 | Tier-2---4 | 4--5 | 11.4604 | 813 | 100% | 4323.2442 | 99.81% | 0% | 0.1903% | 213.5933 | 0 | 0 | 213.5933 | 0 | 185.4129 | 10.7739 | 17.2094 | 185.4129 | 10.7739 | 17.2094 | 216.7498 | 12.5949 | 17.2094 | 4.941% | 0.043095 | 0.040961 | 100319.859 | 21711.3429 | 465.9724 | 78142.5437 | 100329.8016 | 0 | 0 | 100329.8016 | 0.007044%
2028 | 183 | 183-439 | Tier-2 | Tier-2---14 | 3--5 | 1.1486 | 90 | 100% | 316.4778 | 66.23% | 33.5% | 0.2671% | 10.3754 | 0 | 0 | 10.3754 | 0 | 9.0065 | 1.0798 | 8.3406 | 9.0065 | 1.0798 | 8.3406 | 10.5287 | 1.2623 | 8.3406 | 3.278% | 0.018422 | 0.01751 | 17179.1509 | 1863.06 | 5259.1597 | 10056.9311 | 17481.2723 | 0 | 0 | 17481.2723 | 0.0003421%
2028 | 493 | 493-478R | Tier-1 | Non-HFTD---8 | 3--3 | 4.1928 | 240 | 100% | 28.2075 | 88.18% | 0% | 11.82% | 1.2312 | 0 | 0 | 1.2312 | 0 | 1.0687 | 3.9417 | 0.27114 | 1.0687 | 3.9417 | 0.27114 | 1.2494 | 4.6079 | 0.27114 | 4.365% | 0.014664 | 0.013938 | 1923.5642 | 293.7928 | 238.0854 | 1391.686 | 1935.4086 | 0 | 0 | 1935.4086 | 4.06e-05%
2028 | 416 | CB 416 | Tier-1 | Non-HFTD---13 | 1--4 | 0.49546 | 7 | 100% | 7.4419 | 94.25% | 0% | 5.754% | 0.34718 | 0 | 0 | 0.34718 | 0 | 0.30137 | 0.46578 | 0.64703 | 0.30137 | 0.46578 | 0.64703 | 0.35231 | 0.54451 | 0.64703 | 4.665% | 0.0015346 | 0.0014586 | 4849.4324 | 38.4789 | 4361.574 | 449.3795 | 4863.9644 | 0 | 0 | 4863.9644 | 1.145e-05%
2028 | 243 | 243-20R | Tier-1 | Non-HFTD---2 | 4--4 | 10.387 | 501 | 100% | 388.804 | 72.37% | 26.23% | 1.398% | 13.9291 | 0 | 0 | 13.9291 | 0 | 12.0913 | 9.7648 | 1.2383 | 12.0913 | 9.7648 | 1.2383 | 14.1349 | 11.4152 | 1.2383 | 3.583% | 0.058161 | 0.055282 | 6684.9371 | 1057.1463 | 1810.7065 | 3817.0843 | 6781.1116 | 0 | 0 | 6781.1116 | 0.0004593%
2028 | 724 | CB 724 | Tier-1 | Non-HFTD---20 | 1--1 | 0.25037 | 5 | 100% | 0.16085 | 8.868% | 0% | 91.13% | 0.00070607 | 0 | 0 | 0.00070607 | 0 | 0.00061291 | 0.23537 | 0.002604 | 0.00061291 | 0.23537 | 0.002604 | 0.0007165 | 0.27515 | 0.002604 | 0.439% | 0.000606 | 0.000576 | 265.4252 | 0.18201 | 45.5111 | 219.7321 | 278.0222 | 0 | 0 | 278.0222 | 2.328e-08%
2028 | 706 | CB 706 | Tier-1 | Non-HFTD---7 | 2--3 | 1.7864 | 19 | 100% | 32.9411 | 96.6% | 0.3164% | 3.084% | 1.5751 | 0 | 0 | 1.5751 | 0 | 1.3673 | 1.6794 | 0.81419 | 1.3673 | 1.6794 | 0.81419 | 1.5984 | 1.9632 | 0.81419 | 4.782% | 0.010907 | 0.010367 | 3020.124 | 527.3897 | 16.8429 | 2475.8914 | 3025.472 | 0 | 0 | 3025.472 | 5.194e-05%
2028 | 145 | CB 145 | Tier-1 | Non-HFTD---5 | 2--4 | 1.2373 | 52 | 100% | 50.1579 | 64.45% | 33.49% | 2.055% | 1.6003 | 0 | 0 | 1.6003 | 0 | 1.3891 | 1.1632 | 1.1943 | 1.3891 | 1.1632 | 1.1943 | 1.6239 | 1.3597 | 1.1943 | 3.19% | 0.0096286 | 0.009152 | 5209.2634 | 427.9347 | 3048.2211 | 1733.1076 | 5305.6973 | 0 | 0 | 5305.6973 | 5.277e-05%
2028 | 524 | 524-50R | Tier-3 | Tier-3---7 | 5--5 | 10.5116 | 525 | 100% | 8801.877 | 98.2% | 1.718% | 0.0819% | 427.853 | 0 | 0 | 427.853 | 0 | 371.4043 | 9.8819 | 37.5841 | 371.4043 | 9.8819 | 37.5841 | 434.1758 | 11.5521 | 37.5841 | 4.861% | 0.18313 | 0.17407 | 48062.3901 | 8095.7209 | 755.2397 | 39211.4295 | 48107.4292 | 0 | 0 | 48107.4292 | 0.01411%
2028 | 411 | CB 411 | Tier-1 | Non-HFTD---17 | 1--4 | 0.039773 | 7 | 100% | 0.73685 | 95.5% | 0% | 4.499% | 0.034833 | 0 | 0 | 0.034833 | 0 | 0.030238 | 0.03739 | 0.8087 | 0.030238 | 0.03739 | 0.8087 | 0.035348 | 0.04371 | 0.8087 | 4.727% | 0.000145 | 0.00013782 | 5081.7307 | 456.5916 | 2088.6806 | 2536.4584 | 5093.636 | 0 | 0 | 5093.636 | 1.149e-06%
2028 | 916 | 916-381 | Tier-2 | Tier-2---12 | 4--4 | 1.3913 | 284 | 100% | 590.9122 | 71.07% | 28.73% | 0.1918% | 20.7893 | 0 | 0 | 20.7893 | 0 | 18.0464 | 1.308 | 13.797 | 18.0464 | 1.308 | 13.797 | 21.0965 | 1.5291 | 13.797 | 3.518% | 0.049834 | 0.047367 | 11857.5641 | 1782.085 | 3001.9836 | 7073.4955 | 12036.1866 | 0 | 0 | 12036.1866 | 0.0006856%
2028 | 350 | 350-2192R | Tier-2 | Tier-2---2 | 5--5 | 31.8811 | 2437 | 100% | 13871.6222 | 98.14% | 1.698% | 0.1643% | 673.8553 | 0 | 0 | 673.8553 | 0 | 584.9503 | 29.9714 | 19.5169 | 584.9503 | 29.9714 | 19.5169 | 683.8136 | 35.0369 | 19.5169 | 4.858% | 0.18928 | 0.17991 | 73287.5708 | 12530.2712 | 1204.2381 | 59553.0615 | 73358.6632 | 0 | 0 | 73358.6632 | 0.02222%
2028 | 198 | 198-37R | Tier-2 | Tier-2---9 | 4--5 | 7.3848 | 136 | 100% | 973.0999 | 95.53% | 4.02% | 0.4464% | 46.017 | 0 | 0 | 46.017 | 0 | 39.9458 | 6.9425 | 5.7538 | 39.9458 | 6.9425 | 5.7538 | 46.6971 | 8.1158 | 5.7538 | 4.729% | 0.030671 | 0.029153 | 31727.0349 | 12880.9235 | 1667.8732 | 17178.2382 | 31800.8328 | 0 | 0 | 31800.8328 | 0.001517%
2028 | 258 | CB 258 | Tier-1 | Non-HFTD---19 | 1--1 | 0.065341 | 0 | 100% | 0.17536 | 0.484% | 0% | 99.52% | 4.2015e-05 | 0 | 0 | 4.2015e-05 | 0 | 3.6472e-05 | 0.061427 | 0.00059374 | 3.6472e-05 | 0.061427 | 0.00059374 | 4.2636e-05 | 0.071809 | 0.00059374 | 0.02396% | 0.0003514 | 0.00033401 | 499.0252 | 0.67763 | 45.6717 | 452.6758 | 524.8876 | 0 | 0 | 524.8876 | 1.386e-09%
2028 | 63 | 63-797R | Tier-1 | Non-HFTD---1 | 3--5 | 3.9205 | 872 | 100% | 1294.9207 | 95.84% | 3.945% | 0.2104% | 61.435 | 0 | 0 | 61.435 | 0 | 53.3296 | 3.6856 | 14.4695 | 53.3296 | 3.6856 | 14.4695 | 62.3429 | 4.3086 | 14.4695 | 4.744% | 0.02549 | 0.024229 | 50800.3291 | 10671.1023 | 1938.6345 | 38190.5924 | 50910.264 | 0 | 0 | 50910.264 | 0.002026%
2028 | 366 | CB 366 | Tier-1 | Non-HFTD---5 | 3--4 | 3.4801 | 66 | 100% | 92.421 | 14.77% | 81.62% | 3.609% | 0.67569 | 0 | 0 | 0.67569 | 0 | 0.58654 | 3.2716 | 0.17928 | 0.58654 | 3.2716 | 0.17928 | 0.68567 | 3.8246 | 0.17928 | 0.7311% | 0.016207 | 0.015404 | 5702.6756 | 6.2073 | 5082.696 | 613.7722 | 5955.7953 | 0 | 0 | 5955.7953 | 2.228e-05%
2028 | 299 | 299-814AE | Tier-1 | Non-HFTD---4 | 2--4 | 2.8968 | 266 | 100% | 92.0555 | 97.82% | 0% | 2.183% | 4.4573 | 0 | 0 | 4.4573 | 0 | 3.8692 | 2.7233 | 1.4208 | 3.8692 | 2.7233 | 1.4208 | 4.5231 | 3.1836 | 1.4208 | 4.842% | 0.0089936 | 0.0085484 | 10235.6661 | 2125.5614 | 107.0953 | 8003.0094 | 10247.3023 | 0 | 0 | 10247.3023 | 0.000147%
2028 | 232 | CB 232 | Tier-2 | Tier-2---7 | 4--5 | 6.8056 | 633 | 100% | 1642.5971 | 97.37% | 2.323% | 0.3027% | 79.1736 | 0 | 0 | 79.1736 | 0 | 68.7279 | 6.398 | 10.7421 | 68.7279 | 6.398 | 10.7421 | 80.3437 | 7.4793 | 10.7421 | 4.82% | 0.029023 | 0.027587 | 56595.6114 | 8878.7373 | 1490.4163 | 46226.4579 | 56673.0008 | 0 | 0 | 56673.0008 | 0.002611%
2028 | 1139 | 1139-5 | Tier-1 | Non-HFTD---2 | 5--3 | 0.75514 | 11 | 100% | 335.8565 | 0.3706% | 99.5% | 0.1331% | 0.061619 | 0 | 0 | 0.061619 | 0 | 0.053489 | 0.70991 | 0.075346 | 0.053489 | 0.70991 | 0.075346 | 0.062529 | 0.82989 | 0.075346 | 0.01835% | 0.10416 | 0.099006 | 3224.3672 | 4.3588 | 2910.0555 | 309.953 | 3391.6629 | 0 | 0 | 3391.6629 | 2.032e-06%
2028 | MA2 | CB MA2 | Tier-1 | Non-HFTD---8 | 3--2 | 3.6417 | 126 | 100% | 40.2518 | 2.195% | 91.76% | 6.046% | 0.043733 | 0 | 0 | 0.043733 | 0 | 0.037963 | 3.4236 | 0.011089 | 0.037963 | 3.4236 | 0.011089 | 0.04438 | 4.0022 | 0.011089 | 0.1086% | 0.025041 | 0.023801 | 1607.4358 | 4.4717 | 1386.7821 | 216.182 | 1689.3102 | 0 | 0 | 1689.3102 | 1.442e-06%
2028 | 452 | 452-1405 | Tier-2 | Tier-2---15 | 1--5 | 0.38935 | 10 | 100% | 181.2174 | 99.84% | 0% | 0.161% | 8.9558 | 0 | 0 | 8.9558 | 0 | 7.7742 | 0.36602 | 21.2397 | 7.7742 | 0.36602 | 21.2397 | 9.0882 | 0.42789 | 21.2397 | 4.942% | 0.001513 | 0.0014381 | 119773.5584 | 22556.6664 | 21.4776 | 97195.4144 | 119783.5982 | 0 | 0 | 119783.5982 | 0.0002953%
2028 | 212 | 212-739R | Tier-3 | Tier-3---15 | 5--4 | 9.5874 | 639 | 100% | 998.7912 | 96.62% | 2.787% | 0.5903% | 47.7702 | 0 | 0 | 47.7702 | 0 | 41.4677 | 9.0131 | 4.6008 | 41.4677 | 9.0131 | 4.6008 | 48.4762 | 10.5364 | 4.6008 | 4.783% | 0.13097 | 0.12449 | 7626.107 | 884.6687 | 208.746 | 6532.6923 | 7639.5217 | 0 | 0 | 7639.5217 | 0.001575%
2028 | 165 | 165-621F | Tier-1 | Non-HFTD---3 | 4--3 | 12.0826 | 329 | 100% | 101.1468 | 91.67% | 0% | 8.335% | 4.5895 | 0 | 0 | 4.5895 | 0 | 3.984 | 11.3589 | 0.35074 | 3.984 | 11.3589 | 0.35074 | 4.6573 | 13.2786 | 0.35074 | 4.537% | 0.037528 | 0.03567 | 2695.236 | 312.5984 | 579.2909 | 1803.3467 | 2706.9347 | 0 | 0 | 2706.9347 | 0.0001513%
2028 | 240 | CB 240 | Tier-2 | Tier-2---9 | 4--5 | 6.5815 | 249 | 100% | 1263.0316 | 97.68% | 1.949% | 0.3739% | 61.0677 | 0 | 0 | 61.0677 | 0 | 53.0108 | 6.1873 | 8.5677 | 53.0108 | 6.1873 | 8.5677 | 61.9702 | 7.233 | 8.5677 | 4.835% | 0.048511 | 0.046109 | 26036.1977 | 5428.7987 | 694.0612 | 19913.3378 | 26067.6956 | 0 | 0 | 26067.6956 | 0.002014%
2028 | 79 | 79-714R | Tier-3 | Tier-3---9 | 5--4 | 5.9877 | 450 | 100% | 5536.6205 | 96.31% | 3.618% | 0.06787% | 263.9613 | 0 | 0 | 263.9613 | 0 | 229.1356 | 5.6291 | 40.7057 | 229.1356 | 5.6291 | 40.7057 | 267.8621 | 6.5805 | 40.7057 | 4.768% | 0.37772 | 0.35902 | 14658.165 | 2258.9978 | 483.8289 | 11915.3383 | 14686.3013 | 0 | 0 | 14686.3013 | 0.008704%
2028 | 520 | 520-10R | Tier-2 | Tier-2---7 | 4--5 | 5.0582 | 548 | 100% | 1478.7446 | 97.97% | 1.759% | 0.2664% | 71.715 | 0 | 0 | 71.715 | 0 | 62.2533 | 4.7552 | 13.0917 | 62.2533 | 4.7552 | 13.0917 | 72.7748 | 5.5589 | 13.0917 | 4.85% | 0.046043 | 0.043764 | 32116.3215 | 6760.2491 | 666.312 | 24689.7604 | 32150.2042 | 0 | 0 | 32150.2042 | 0.002365%
2028 | MK2 | CB MK2 | Tier-1 | Non-HFTD---14 | 3--1 | 6.9771 | 167 | 100% | 8.3451 | 44.18% | 0% | 55.82% | 0.18252 | 0 | 0 | 0.18252 | 0 | 0.15844 | 6.5591 | 0.024155 | 0.15844 | 6.5591 | 0.024155 | 0.18521 | 7.6677 | 0.024155 | 2.187% | 0.019822 | 0.01884 | 421.0108 | 29.7884 | 90.8373 | 300.3851 | 433.2487 | 0 | 0 | 433.2487 | 6.019e-06%
2028 | 209 | 209-661 | Tier-1 | Non-HFTD---4 | 1--5 | 1.3877 | 115 | 100% | 118.7112 | 99.11% | 0% | 0.8879% | 5.824 | 0 | 0 | 5.824 | 0 | 5.0556 | 1.3046 | 3.8752 | 5.0556 | 1.3046 | 3.8752 | 5.9101 | 1.5251 | 3.8752 | 4.906% | 0.0044254 | 0.0042063 | 26824.9714 | 4214.0457 | 851.0995 | 21759.8261 | 26837.3758 | 0 | 0 | 26837.3758 | 0.0001921%
2028 | 340 | 340-376F | Tier-1 | Non-HFTD---7 | 2--3 | 2.4146 | 200 | 100% | 34.9276 | 95.82% | 0% | 4.178% | 1.6567 | 0 | 0 | 1.6567 | 0 | 1.4381 | 2.2699 | 0.63355 | 1.4381 | 2.2699 | 0.63355 | 1.6812 | 2.6536 | 0.63355 | 4.743% | 0.0073482 | 0.0069845 | 4753.2178 | 524.3665 | 2205.6799 | 2023.1714 | 4763.5601 | 0 | 0 | 4763.5601 | 5.463e-05%
2028 | 579 | CB 579 | Tier-1 | Non-HFTD---6 | 3--3 | 1.4538 | 9 | 100% | 49.6621 | 21.66% | 75.14% | 3.198% | 0.53254 | 0 | 0 | 0.53254 | 0 | 0.46228 | 1.3667 | 0.33825 | 0.46228 | 1.3667 | 0.33825 | 0.54041 | 1.5977 | 0.33825 | 1.072% | 0.015297 | 0.01454 | 3246.5274 | 3.0703 | 2897.813 | 345.6441 | 3378.9733 | 0 | 0 | 3378.9733 | 1.756e-05%
2028 | 325 | CB 325 | Tier-1 | Non-HFTD---7 | 1--4 | 1.1091 | 146 | 100% | 43.928 | 97.88% | 0% | 2.116% | 2.1284 | 0 | 0 | 2.1284 | 0 | 1.8476 | 1.0427 | 1.772 | 1.8476 | 1.0427 | 1.772 | 2.1599 | 1.2189 | 1.772 | 4.845% | 0.0043742 | 0.0041577 | 10042.5141 | 384.3371 | 7501.7135 | 2156.4635 | 10053.582 | 0 | 0 | 10053.582 | 7.019e-05%
2028 | 368 | CB 368 | Tier-1 | Non-HFTD---4 | 3--4 | 3.9384 | 124 | 100% | 110.2844 | 13.26% | 83.59% | 3.156% | 0.72366 | 0 | 0 | 0.72366 | 0 | 0.62818 | 3.7025 | 0.16966 | 0.62818 | 3.7025 | 0.16966 | 0.73435 | 4.3283 | 0.16966 | 0.6562% | 0.016985 | 0.016144 | 6492.9689 | 7.2051 | 5795.9328 | 689.831 | 6786.285 | 0 | 0 | 6786.285 | 2.386e-05%
2028 | 480 | 480-1163R | Tier-1 | Non-HFTD---16 | 2--1 | 3.6682 | 75 | 100% | 3.8801 | 32.98% | 0% | 67.02% | 0.06334 | 0 | 0 | 0.06334 | 0 | 0.054983 | 3.4485 | 0.015944 | 0.054983 | 3.4485 | 0.015944 | 0.064276 | 4.0313 | 0.015944 | 1.632% | 0.010077 | 0.0095782 | 385.0495 | 0.19419 | 150.4248 | 234.4305 | 398.4891 | 0 | 0 | 398.4891 | 2.089e-06%
2028 | 500 | 500-1531 | Tier-2 | Tier-2---10 | 4--4 | 0.97704 | 34 | 100% | 800.5503 | 21.6% | 78.32% | 0.07823% | 8.56 | 0 | 0 | 8.56 | 0 | 7.4307 | 0.91852 | 8.0898 | 7.4307 | 0.91852 | 8.0898 | 8.6865 | 1.0738 | 8.0898 | 1.069% | 0.071178 | 0.067654 | 11247.1911 | 406.5986 | 8046.836 | 2793.7565 | 11706.3951 | 0 | 0 | 11706.3951 | 0.0002823%
2028 | 1100 | 1100-1172R | Tier-2 | Tier-2---7 | 4--5 | 2.2354 | 19 | 100% | 2144.9788 | 99.68% | 0.2699% | 0.05437% | 105.8322 | 0 | 0 | 105.8322 | 0 | 91.8692 | 2.1015 | 43.7154 | 91.8692 | 2.1015 | 43.7154 | 107.3962 | 2.4567 | 43.7154 | 4.934% | 0.080798 | 0.076798 | 26547.4908 | 6276.7564 | 58.3505 | 20212.3839 | 26551.9736 | 0 | 0 | 26551.9736 | 0.00349%
2028 | 1162 | CB 1162 | Tier-2 | Tier-2---18 | 4--2 | 1.5907 | 13 | 100% | 75.2008 | 96.65% | 1.975% | 1.378% | 3.5976 | 0 | 0 | 3.5976 | 0 | 3.123 | 1.4954 | 2.0884 | 3.123 | 1.4954 | 2.0884 | 3.6508 | 1.7482 | 2.0884 | 4.784% | 0.064214 | 0.061035 | 1171.1044 | 178.0938 | 26.2712 | 966.7394 | 1173.1495 | 0 | 0 | 1173.1495 | 0.0001186%
2028 | 395 | CB 395 | Tier-1 | Non-HFTD---2 | 4--4 | 0.85682 | 57 | 100% | 731.6954 | 0.7674% | 99.15% | 0.08318% | 0.27795 | 0 | 0 | 0.27795 | 0 | 0.24128 | 0.8055 | 0.29954 | 0.24128 | 0.8055 | 0.29954 | 0.28206 | 0.94163 | 0.29954 | 0.03799% | 0.090668 | 0.08618 | 8070.0864 | 11.9063 | 7403.1498 | 655.0303 | 8487.134 | 0 | 0 | 8487.134 | 9.166e-06%
2028 | 508 | 508-1027F | Tier-1 | Non-HFTD---19 | 1--2 | 0.083367 | 2 | 100% | 0.19317 | 84.46% | 0% | 15.54% | 0.0080765 | 0 | 0 | 0.0080765 | 0 | 0.0070109 | 0.078373 | 0.089456 | 0.0070109 | 0.078373 | 0.089456 | 0.0081958 | 0.091619 | 0.089456 | 4.181% | 0.0001954 | 0.00018573 | 988.6113 | 136.442 | 18.1035 | 834.0658 | 996.6104 | 0 | 0 | 996.6104 | 2.663e-07%
2028 | 96 | 96-1041F | Tier-1 | Non-HFTD---13 | 2--2 | 0.096362 | 0 | 100% | 5.6175 | 97.14% | 1.791% | 1.068% | 0.27012 | 0 | 0 | 0.27012 | 0 | 0.23448 | 0.09059 | 2.5883 | 0.23448 | 0.09059 | 2.5883 | 0.27411 | 0.1059 | 2.5883 | 4.808% | 0.005633 | 0.0053542 | 997.2446 | 127.463 | 205.2994 | 664.4822 | 998.7294 | 0 | 0 | 998.7294 | 8.907e-06%
2028 | 531 | 531-36AE | Tier-1 | Non-HFTD---12 | 3--2 | 5.9676 | 195 | 100% | 9.706 | 61.11% | 0% | 38.89% | 0.29361 | 0 | 0 | 0.29361 | 0 | 0.25488 | 5.6102 | 0.045431 | 0.25488 | 5.6102 | 0.045431 | 0.29795 | 6.5584 | 0.045431 | 3.025% | 0.016 | 0.015208 | 606.6092 | 2.6548 | 376.9073 | 227.0471 | 618.894 | 0 | 0 | 618.894 | 9.682e-06%
2028 | 438 | CB 438 | Tier-1 | Non-HFTD---9 | 1--4 | 0.50947 | 74 | 100% | 16.6829 | 97.05% | 0% | 2.95% | 0.80144 | 0 | 0 | 0.80144 | 0 | 0.6957 | 0.47895 | 1.4526 | 0.6957 | 0.47895 | 1.4526 | 0.81329 | 0.5599 | 1.4526 | 4.804% | 0.0021344 | 0.0020287 | 7816.2233 | 299.4615 | 5763.6381 | 1753.1236 | 7828.2327 | 0 | 0 | 7828.2327 | 2.643e-05%
2028 | 1162 | 1162-363 | Tier-2 | Tier-2---13 | 4--3 | 1.6328 | 7 | 100% | 247.9994 | 97.75% | 1.792% | 0.4608% | 11.9994 | 0 | 0 | 11.9994 | 0 | 10.4162 | 1.535 | 6.7859 | 10.4162 | 1.535 | 6.7859 | 12.1767 | 1.7944 | 6.7859 | 4.838% | 0.064829 | 0.06162 | 3825.4385 | 595.791 | 56.0143 | 3173.6332 | 3829.9274 | 0 | 0 | 3829.9274 | 0.0003957%
2028 | 791 | CB 791 | Tier-1 | Non-HFTD---1 | 2--5 | 2.9851 | 216 | 100% | 969.8887 | 99.78% | 0% | 0.2167% | 47.9055 | 0 | 0 | 47.9055 | 0 | 41.5851 | 2.8063 | 14.8187 | 41.5851 | 2.8063 | 14.8187 | 48.6134 | 3.2805 | 14.8187 | 4.939% | 0.010706 | 0.010176 | 90594.693 | 15315.6434 | 490.2766 | 74788.773 | 90604.9145 | 0 | 0 | 90604.9145 | 0.00158%
2028 | 920 | 920-823 | Tier-2 | Tier-2---11 | 4--4 | 3.3104 | 254 | 100% | 458.2189 | 68.35% | 31.14% | 0.5113% | 15.5021 | 0 | 0 | 15.5021 | 0 | 13.4569 | 3.1121 | 4.324 | 13.4569 | 3.1121 | 4.324 | 15.7312 | 3.6381 | 4.324 | 3.383% | 0.054577 | 0.051875 | 8395.8542 | 937.9397 | 2311.5146 | 5146.3999 | 8534.2572 | 0 | 0 | 8534.2572 | 0.0005112%
2028 | 518 | 518-41 | Tier-1 | Non-HFTD---19 | 1--2 | 0.051326 | 0 | 100% | 0.18129 | 60.97% | 0% | 39.03% | 0.0054716 | 0 | 0 | 0.0054716 | 0 | 0.0047497 | 0.048251 | 0.098436 | 0.0047497 | 0.048251 | 0.098436 | 0.0055524 | 0.056406 | 0.098436 | 3.018% | 0.000233 | 0.00022147 | 778.072 | 0.2285 | 501.9934 | 275.8501 | 793.8862 | 0 | 0 | 793.8862 | 1.804e-07%
2028 | 323 | 323-472AE | Tier-1 | Non-HFTD---13 | 2--2 | 2.246 | 49 | 100% | 8.3309 | 80.43% | 0% | 19.57% | 0.33167 | 0 | 0 | 0.33167 | 0 | 0.28791 | 2.1115 | 0.13635 | 0.28791 | 2.1115 | 0.13635 | 0.33657 | 2.4684 | 0.13635 | 3.981% | 0.0064722 | 0.0061518 | 1287.1873 | 162.8063 | 63.3921 | 1060.9888 | 1300.3075 | 0 | 0 | 1300.3075 | 1.094e-05%
2028 | 513 | CB 513 | Tier-1 | Non-HFTD---15 | 2--2 | 1.6305 | 55 | 100% | 4.8584 | 75.25% | 0% | 24.75% | 0.18097 | 0 | 0 | 0.18097 | 0 | 0.15709 | 1.5329 | 0.10248 | 0.15709 | 1.5329 | 0.10248 | 0.18364 | 1.7919 | 0.10248 | 3.725% | 0.005369 | 0.0051032 | 904.9068 | 3.7303 | 679.4251 | 221.7514 | 916.5709 | 0 | 0 | 916.5709 | 5.968e-06%
2028 | 1166 | 1166-18R | Tier-3 | Tier-3---5 | 5--5 | 7.5917 | 223 | 100% | 10108.4901 | 99.77% | 0.1963% | 0.03345% | 499.2208 | 0 | 0 | 499.2208 | 0 | 433.3562 | 7.137 | 60.7201 | 433.3562 | 7.137 | 60.7201 | 506.5984 | 8.3432 | 60.7201 | 4.939% | 0.21365 | 0.20307 | 47313.4054 | 8461.5455 | 93.1732 | 38758.6866 | 47319.0655 | 0 | 0 | 47319.0655 | 0.01646%
2028 | 454 | 454-48F | Tier-2 | Tier-2---4 | 4--5 | 3.4244 | 409 | 100% | 3441.1661 | 99.7% | 0.2542% | 0.04705% | 169.8246 | 0 | 0 | 169.8246 | 0 | 147.4188 | 3.2193 | 45.7922 | 147.4188 | 3.2193 | 45.7922 | 172.3343 | 3.7634 | 45.7922 | 4.935% | 0.085487 | 0.081255 | 40253.7717 | 13127.3131 | 90.5163 | 27035.9424 | 40260.0869 | 0 | 0 | 40260.0869 | 0.0056%
2028 | 365 | 365-34R | Tier-1 | Non-HFTD---4 | 3--4 | 4.1672 | 256 | 100% | 103.0739 | 4.771% | 91.96% | 3.266% | 0.24342 | 0 | 0 | 0.24342 | 0 | 0.21131 | 3.9176 | 0.053938 | 0.21131 | 3.9176 | 0.053938 | 0.24702 | 4.5797 | 0.053938 | 0.2362% | 0.017802 | 0.016921 | 5789.9516 | 7.6245 | 5140.9605 | 641.3666 | 6077.094 | 0 | 0 | 6077.094 | 8.027e-06%
2028 | 1242 | 1242-1079R | Tier-2 | Tier-2---12 | 2--5 | 1.6259 | 7 | 100% | 411.5414 | 99.65% | 0% | 0.3468% | 20.3007 | 0 | 0 | 20.3007 | 0 | 17.6223 | 1.5286 | 11.5287 | 17.6223 | 1.5286 | 11.5287 | 20.6007 | 1.7869 | 11.5287 | 4.933% | 0.0067316 | 0.0063984 | 61135.7492 | 25086.0386 | 163.5766 | 35886.134 | 61146.7898 | 0 | 0 | 61146.7898 | 0.0006694%
2028 | RA2 | CB RA2 | Tier-2 | Tier-2---4 | 5--5 | 3.5953 | 311 | 100% | 5229.9021 | 98.11% | 1.831% | 0.05575% | 253.995 | 0 | 0 | 253.995 | 0 | 220.4842 | 3.3799 | 65.2337 | 220.4842 | 3.3799 | 65.2337 | 257.7485 | 3.9512 | 65.2337 | 4.857% | 0.12706 | 0.12077 | 41161.4683 | 9548.3144 | 685.7088 | 30927.4452 | 41201.919 | 0 | 0 | 41201.919 | 0.008376%
2028 | 450 | 450-1850 | Tier-2 | Tier-2---13 | 4--3 | 0.60374 | 82 | 100% | 296.7138 | 97.11% | 2.719% | 0.1664% | 14.2636 | 0 | 0 | 14.2636 | 0 | 12.3817 | 0.56758 | 21.815 | 12.3817 | 0.56758 | 21.815 | 14.4744 | 0.6635 | 21.815 | 4.807% | 0.073712 | 0.070064 | 4025.2898 | 636.7638 | 101.4909 | 3287.0352 | 4031.3382 | 0 | 0 | 4031.3382 | 0.0004704%
2028 | 307 | 307-1684R | Tier-1 | Non-HFTD---1 | 4--5 | 3.7428 | 1032 | 100% | 2117.8574 | 97.53% | 2.33% | 0.1416% | 102.2432 | 0 | 0 | 102.2432 | 0 | 88.7538 | 3.5186 | 25.2243 | 88.7538 | 3.5186 | 25.2243 | 103.7542 | 4.1133 | 25.2243 | 4.828% | 0.067442 | 0.064104 | 31402.4615 | 4988.1224 | 677.5642 | 25736.7748 | 31442.8757 | 0 | 0 | 31442.8757 | 0.003372%
2028 | SLD1 | CB SLD1 | Tier-1 | Non-HFTD---19 | 1--1 | 0.41002 | 165 | 100% | 0.56022 | 34.73% | 0% | 65.27% | 0.0096313 | 0 | 0 | 0.0096313 | 0 | 0.0083606 | 0.38546 | 0.02169 | 0.0083606 | 0.38546 | 0.02169 | 0.0097736 | 0.45061 | 0.02169 | 1.719% | 0.001298 | 0.0012337 | 431.6022 | 16.2295 | 84.9521 | 330.4206 | 446.2726 | 0 | 0 | 446.2726 | 3.176e-07%
2028 | 741 | 741-17 | Tier-1 | Non-HFTD---17 | 1--2 | 0.36707 | 29 | 100% | 0.86307 | 47.7% | 0% | 52.3% | 0.020379 | 0 | 0 | 0.020379 | 0 | 0.017691 | 0.34508 | 0.051265 | 0.017691 | 0.34508 | 0.051265 | 0.020681 | 0.4034 | 0.051265 | 2.361% | 0.0013504 | 0.0012836 | 639.1235 | 0.34753 | 334.6341 | 304.1418 | 656.5303 | 0 | 0 | 656.5303 | 6.72e-07%
2028 | 165 | 165-35R | Tier-1 | Non-HFTD---14 | 3--1 | 5.1646 | 147 | 100% | 6.4032 | 43.37% | 0% | 56.63% | 0.13745 | 0 | 0 | 0.13745 | 0 | 0.11932 | 4.8552 | 0.024575 | 0.11932 | 4.8552 | 0.024575 | 0.13948 | 5.6758 | 0.024575 | 2.147% | 0.014379 | 0.013667 | 445.3099 | 19.5075 | 97.6943 | 328.1081 | 458.4437 | 0 | 0 | 458.4437 | 4.533e-06%
2028 | 1525 | 1525-23R | Tier-2 | Tier-2---20 | 4--1 | 0.63484 | 9 | 100% | 8.268 | 89.5% | 6.947% | 3.548% | 0.36631 | 0 | 0 | 0.36631 | 0 | 0.31798 | 0.59681 | 0.5328 | 0.31798 | 0.59681 | 0.5328 | 0.37173 | 0.69768 | 0.5328 | 4.43% | 0.032823 | 0.031198 | 251.8988 | 39.1664 | 14.7185 | 198.0139 | 253.2756 | 0 | 0 | 253.2756 | 1.208e-05%
2028 | 385 | CB 385 | Tier-1 | Non-HFTD---7 | 2--3 | 3.3032 | 122 | 100% | 37.1529 | 92.67% | 0% | 7.33% | 1.7043 | 0 | 0 | 1.7043 | 0 | 1.4794 | 3.1054 | 0.47641 | 1.4794 | 3.1054 | 0.47641 | 1.7295 | 3.6302 | 0.47641 | 4.587% | 0.011539 | 0.010968 | 3219.7101 | 608.925 | 454.3214 | 2156.4637 | 3231.9998 | 0 | 0 | 3231.9998 | 5.62e-05%
2028 | 377 | CB 377 | Tier-1 | Non-HFTD---12 | 3--1 | 9.6765 | 756 | 100% | 10.2043 | 38.55% | 0% | 61.45% | 0.19472 | 0 | 0 | 0.19472 | 0 | 0.16903 | 9.0969 | 0.018581 | 0.16903 | 9.0969 | 0.018581 | 0.1976 | 10.6344 | 0.018581 | 1.908% | 0.025969 | 0.024684 | 392.9351 | 0.64012 | 170.596 | 221.699 | 405.5098 | 0 | 0 | 405.5098 | 6.421e-06%
2028 | 1081 | 1081-11 | Tier-1 | Non-HFTD---3 | 4--4 | 7.6814 | 575 | 100% | 174.6854 | 18.55% | 79% | 2.449% | 1.6041 | 0 | 0 | 1.6041 | 0 | 1.3924 | 7.2213 | 0.19282 | 1.3924 | 7.2213 | 0.19282 | 1.6278 | 8.4418 | 0.19282 | 0.9183% | 0.031395 | 0.029841 | 5564.0802 | 104.2628 | 4552.4133 | 907.4041 | 5800.0917 | 0 | 0 | 5800.0917 | 5.29e-05%
2028 | 222 | 222-2063 | Tier-3 | Tier-3---9 | 5--5 | 4.9145 | 243 | 100% | 4859.7765 | 99.85% | 0.09452% | 0.05485% | 240.1996 | 0 | 0 | 240.1996 | 0 | 208.5089 | 4.6202 | 45.1303 | 208.5089 | 4.6202 | 45.1303 | 243.7493 | 5.401 | 45.1303 | 4.943% | 0.23776 | 0.22599 | 20439.7717 | 3158.5726 | 17.2561 | 17263.9431 | 20441.3617 | 0 | 0 | 20441.3617 | 0.007921%
2028 | 462 | 462-1034F | Tier-1 | Non-HFTD---13 | 1--3 | 1.0586 | 56 | 100% | 6.6731 | 87.2% | 0% | 12.8% | 0.28803 | 0 | 0 | 0.28803 | 0 | 0.25003 | 0.99516 | 0.25125 | 0.25003 | 0.99516 | 0.25125 | 0.29229 | 1.1634 | 0.25125 | 4.316% | 0.0032472 | 0.0030865 | 2055.0169 | 223.8756 | 449.9011 | 1381.2401 | 2068.7163 | 0 | 0 | 2068.7163 | 9.498e-06%
2028 | SEA1 | SEA1-384F | Tier-1 | Non-HFTD---6 | 3--3 | 6.4007 | 656 | 100% | 54.3248 | 19.85% | 71.87% | 8.289% | 0.53366 | 0 | 0 | 0.53366 | 0 | 0.46325 | 6.0173 | 0.076986 | 0.46325 | 6.0173 | 0.076986 | 0.54154 | 7.0343 | 0.076986 | 0.9823% | 0.028231 | 0.026833 | 1924.322 | 66.4401 | 1300.7116 | 557.1703 | 2004.6487 | 0 | 0 | 2004.6487 | 1.76e-05%
2028 | BA3 | CB BA3 | Tier-1 | Non-HFTD---14 | 3--1 | 7.1958 | 255 | 100% | 7.3804 | 35.46% | 0% | 64.54% | 0.12955 | 0 | 0 | 0.12955 | 0 | 0.11246 | 6.7648 | 0.016624 | 0.11246 | 6.7648 | 0.016624 | 0.13147 | 7.9081 | 0.016624 | 1.755% | 0.019996 | 0.019007 | 369.0877 | 1.4139 | 144.9388 | 222.735 | 381.4929 | 0 | 0 | 381.4929 | 4.272e-06%
2028 | 856 | CB 856 | Tier-1 | Non-HFTD---7 | 1--4 | 1.0902 | 50 | 100% | 37.8514 | 97.97% | 0% | 2.035% | 1.8355 | 0 | 0 | 1.8355 | 0 | 1.5933 | 1.0249 | 1.5547 | 1.5933 | 1.0249 | 1.5547 | 1.8626 | 1.1981 | 1.5547 | 4.849% | 0.0032934 | 0.0031304 | 11493.0959 | 2089.5504 | 861.3967 | 8542.1488 | 11505.2746 | 0 | 0 | 11505.2746 | 6.053e-05%
2028 | 458 | 458-41F | Tier-1 | Non-HFTD---19 | 1--1 | 0.10816 | 6 | 100% | 0.15945 | 9.171% | 0% | 90.83% | 0.00072386 | 0 | 0 | 0.00072386 | 0 | 0.00062836 | 0.10168 | 0.0061797 | 0.00062836 | 0.10168 | 0.0061797 | 0.00073456 | 0.11887 | 0.0061797 | 0.454% | 0.0004004 | 0.00038058 | 398.2281 | 0.27217 | 69.3796 | 328.5763 | 417.065 | 0 | 0 | 417.065 | 2.387e-08%
2028 | 455 | CB 455 | Tier-1 | Non-HFTD---1 | 3--5 | 7.4072 | 584 | 100% | 628.6508 | 99.14% | 0% | 0.8628% | 30.8497 | 0 | 0 | 30.8497 | 0 | 26.7796 | 6.9636 | 3.8457 | 26.7796 | 6.9636 | 3.8457 | 31.3056 | 8.1405 | 3.8457 | 4.907% | 0.025428 | 0.024169 | 24722.9716 | 4556.7235 | 179.5676 | 19986.6805 | 24734.0802 | 0 | 0 | 24734.0802 | 0.001017%
2028 | 470 | CB 470 | Tier-2 | Tier-2---6 | 5--5 | 12.4373 | 1312 | 100% | 6922.0493 | 95.49% | 4.388% | 0.1268% | 327.1728 | 0 | 0 | 327.1728 | 0 | 284.0073 | 11.6923 | 24.2901 | 284.0073 | 11.6923 | 24.2901 | 332.0078 | 13.6685 | 24.2901 | 4.727% | 0.114 | 0.10835 | 60721.6484 | 13514.2063 | 2573.4965 | 44633.9456 | 60864.4088 | 0 | 0 | 60864.4088 | 0.01079%
2028 | 523 | 523-31AE | Tier-2 | Tier-2---14 | 4--4 | 4.4118 | 225 | 100% | 305.199 | 11.7% | 87.21% | 1.095% | 1.767 | 0 | 0 | 1.767 | 0 | 1.5339 | 4.1475 | 0.36983 | 1.5339 | 4.1475 | 0.36983 | 1.7931 | 4.8485 | 0.36983 | 0.579% | 0.037419 | 0.035567 | 8156.1707 | 205.0688 | 6422.8624 | 1528.2395 | 8531.2451 | 0 | 0 | 8531.2451 | 5.827e-05%
2028 | 492 | 492-1091F | Tier-1 | Non-HFTD---3 | 4--3 | 5.9958 | 185 | 100% | 120.6396 | 2.917% | 93.65% | 3.431% | 0.17419 | 0 | 0 | 0.17419 | 0 | 0.15121 | 5.6367 | 0.026826 | 0.15121 | 5.6367 | 0.026826 | 0.17677 | 6.5893 | 0.026826 | 0.1444% | 0.031661 | 0.030093 | 3810.4024 | 14.7006 | 3329.9773 | 465.7245 | 4003.0516 | 0 | 0 | 4003.0516 | 5.744e-06%
2028 | 334 | 334-45F | Tier-1 | Non-HFTD---17 | 1--2 | 0.45601 | 12 | 100% | 1.6737 | 78.33% | 0% | 21.67% | 0.06489 | 0 | 0 | 0.06489 | 0 | 0.056329 | 0.4287 | 0.13139 | 0.056329 | 0.4287 | 0.13139 | 0.065849 | 0.50115 | 0.13139 | 3.877% | 0.001477 | 0.0014039 | 1133.158 | 100.5295 | 294.453 | 738.1754 | 1145.9489 | 0 | 0 | 1145.9489 | 2.14e-06%
2028 | 472 | CB 472 | Tier-1 | Non-HFTD---6 | 3--3 | 6.9083 | 465 | 100% | 66.0921 | 92.91% | 0% | 7.09% | 3.0396 | 0 | 0 | 3.0396 | 0 | 2.6386 | 6.4945 | 0.40628 | 2.6386 | 6.4945 | 0.40628 | 3.0845 | 7.5921 | 0.40628 | 4.599% | 0.020578 | 0.019559 | 3211.8146 | 441.0584 | 309.4932 | 2461.263 | 3223.674 | 0 | 0 | 3223.674 | 0.0001002%
2028 | 86 | 86-1055F | Tier-1 | Non-HFTD---18 | 1--1 | 1.5329 | 61 | 100% | 1.2551 | 16.29% | 0% | 83.71% | 0.010118 | 0 | 0 | 0.010118 | 0 | 0.0087831 | 1.4411 | 0.0060947 | 0.0087831 | 1.4411 | 0.0060947 | 0.010268 | 1.6847 | 0.0060947 | 0.8061% | 0.0041652 | 0.003959 | 301.3402 | 2.7068 | 56.6739 | 241.9595 | 314.4776 | 0 | 0 | 314.4776 | 3.337e-07%
2028 | 214 | 214-1135R | Tier-3 | Tier-3---6 | 4--5 | 11.6815 | 1018 | 100% | 6666.9216 | 99.41% | 0.4702% | 0.123% | 328.055 | 0 | 0 | 328.055 | 0 | 284.7731 | 10.9818 | 25.9315 | 284.7731 | 10.9818 | 25.9315 | 332.9031 | 12.8378 | 25.9315 | 4.921% | 0.090777 | 0.086284 | 73442.8498 | 12678.0578 | 384.6507 | 60380.1413 | 73465.5376 | 0 | 0 | 73465.5376 | 0.01082%
2028 | 741 | CB 741 | Tier-1 | Non-HFTD---15 | 1--2 | 0.84259 | 34 | 100% | 3.3752 | 76.64% | 0% | 23.36% | 0.12804 | 0 | 0 | 0.12804 | 0 | 0.11114 | 0.79212 | 0.14031 | 0.11114 | 0.79212 | 0.14031 | 0.12993 | 0.92599 | 0.14031 | 3.793% | 0.0030248 | 0.0028751 | 1115.8402 | 4.7202 | 850.5122 | 260.6077 | 1129.4176 | 0 | 0 | 1129.4176 | 4.222e-06%
2028 | 236 | CB 236 | Tier-2 | Tier-2---1 | 5--5 | 9.3687 | 606 | 100% | 12711.1878 | 97.62% | 2.333% | 0.04724% | 614.2258 | 0 | 0 | 614.2258 | 0 | 533.188 | 8.8075 | 60.5377 | 533.188 | 8.8075 | 60.5377 | 623.3029 | 10.2961 | 60.5377 | 4.832% | 0.1419 | 0.13487 | 89580.6366 | 15500.694 | 2015.4718 | 72064.4708 | 89691.6894 | 0 | 0 | 89691.6894 | 0.02025%
2028 | 221 | 221-23R | Tier-3 | Tier-3---11 | 5--5 | 7.9883 | 1120 | 100% | 3270.2376 | 92.16% | 7.656% | 0.1816% | 149.1897 | 0 | 0 | 149.1897 | 0 | 129.5064 | 7.5098 | 17.245 | 129.5064 | 7.5098 | 17.245 | 151.3944 | 8.779 | 17.245 | 4.562% | 0.19945 | 0.18957 | 16396.4914 | 2639.7901 | 1189.9448 | 12566.7565 | 16463.4153 | 0 | 0 | 16463.4153 | 0.00492%
2028 | 1161 | 1161-74 | Tier-1 | Non-HFTD---17 | 1--4 | 0.043561 | 3 | 100% | 1.4617 | 95.2% | 0% | 4.803% | 0.06888 | 0 | 0 | 0.06888 | 0 | 0.059792 | 0.040951 | 1.4601 | 0.059792 | 0.040951 | 1.4601 | 0.069897 | 0.047873 | 1.4601 | 4.712% | 0.0002106 | 0.00020018 | 6940.7274 | 1060.6781 | 30.2849 | 5849.7645 | 6958.0894 | 0 | 0 | 6958.0894 | 2.271e-06%
2028 | NO1 | NO1-289F | Tier-1 | Non-HFTD---16 | 2--1 | 2.4969 | 67 | 100% | 2.4755 | 21.95% | 0% | 78.05% | 0.026901 | 0 | 0 | 0.026901 | 0 | 0.023351 | 2.3474 | 0.0099479 | 0.023351 | 2.3474 | 0.0099479 | 0.027298 | 2.7441 | 0.0099479 | 1.087% | 0.0073078 | 0.0069461 | 338.7505 | 0.19894 | 98.3823 | 240.1693 | 352.5191 | 0 | 0 | 352.5191 | 8.871e-07%
2028 | 237 | 237-17R | Tier-2 | Tier-2---1 | 5--5 | 14.6369 | 1091 | 100% | 27080.7376 | 98.89% | 1.071% | 0.0369% | 1325.6439 | 0 | 0 | 1325.6439 | 0 | 1150.7453 | 13.7601 | 83.6288 | 1150.7453 | 13.7601 | 83.6288 | 1345.2344 | 16.0858 | 83.6288 | 4.895% | 0.15539 | 0.1477 | 174274.8137 | 31991.9545 | 1838.789 | 140444.0702 | 174375.3733 | 0 | 0 | 174375.3733 | 0.04371%