## LSPGC Table 2-1
Section No. | Section Title | Name | Title | Phone Number | Email
1 | Executive Summary | Cameron Fredkin | COO | 636-489-8892 | cfredkin@lspower.com
2 | Responsible Person | Rituraj Yadav | Associate Manager, Wildfire Mitigation | 208-281-8255 | ryadav@lspower.com
3 | Overview of WMP | Ross Hohlt | Director, Asset Management | 636-534-3319 | rhohlt@lspower.com
4 | Overview of the Service Territory | James Rekowski | Associate Project Manager | 636-534-3341 | jrekowski@lspower.com
5 | Risk Methodology and Assessment | Rituraj Yadav | Associate Manager, Wildfire Mitigation | 208-281-8255 | ryadav@lspower.com
6 | Wildfire Mitigation Strategy Development | Rituraj Yadav | Associate Manager, Wildfire Mitigation | 208-281-8255 | ryadav@lspower.com
7 | Public Safety Power Shutoff | Ross Hohlt | Director, Asset Management | 636-534-3319 | rhohlt@lspower.com
8 | Grid Design, Operations, and Maintenance | Rituraj Yadav | Associate Manager, Wildfire Mitigation | 208-281-8255 | ryadav@lspower.com
9 | Vegetation Management and Inspections | Greg Smith | Senior Manager, Vegetation Management | 806-513-6002 | gsmith@lspower.com
10 | Situational Awareness and Forecasting | Rituraj Yadav | Associate Manager, Wildfire Mitigation | 208-281-8255 | ryadav@lspower.com
11 | Emergency Preparedness, Collaboration, and Public Awareness | Heath Holt | Senior Health, Safety, and Environmental Manager | 512-982-5668 | hholt@lspower.com
12 | Enterprise Systems | Rituraj Yadav | Associate Manager, Wildfire Mitigation | 208-281-8255 | ryadav@lspower.com
13 | Lessons Learned | James Rekowski | Associate Project Manager | 636-534-3341 | jrekowski@lspower.com

## LSPGC Table 3-1
Activity ID | Previous Activity ID | ACTIVITY DESCRIPTION | WMP INITIATIVE CATEGORY | WMP INITIATIVE
ENT-01 |  | Centralize vegetation data and integrate inspection workflows for energized substation | Enterprise Systems | Substation Vegetation Management
ENT-02 |  | Maintain SCADA and operational telemetry for substation oversight | Enterprise Systems | Grid Monitoring
ENT-03 |  | Develop basic dashboards for inspection trends and risk prioritization | Enterprise Systems | Risk Assessment
EP-01 |  | Update System Restoration Plan to include Fern Road Substation | Emergency Preparedness, Collaboration and Public Awareness | Emergency Preparedness and Recovery Plan
EP-02 |  | Establish wildfire-specific communication protocols | Emergency Preparedness, Collaboration and Public Awareness | Public Outreach, Communication, and Engagement
EP-03 | LSP-09 | Initiate and maintain annual outreach with local fire/emergency agencies near energized assets | Emergency Preparedness, Collaboration and Public Awareness | External Collaboration and Coordination
GD-01 |  | Investigate advanced protection system enhancements for potential inclusion in project design | Grid Design, Operations, and Maintenance | Grid Operations and Procedures
GD-02 | LSP-02 | Monthly Substation Inspections | Grid Design, Operations, and Maintenance | Asset Inspections
GD-03 |  | Dissolved Gas Analysis Test at energized transformers | Grid Design, Operations, and Maintenance | Equipment Maintenance and Repair
GD-04 | LSP-03 | Use Maximo to manage assets, inspections, and maintenance | Grid Design, Operations, and Maintenance | Work Orders (Asset Management)
GD-05 |  | Review Emergency Operations Plan and update annually | Grid Design, Operations, and Maintenance | Grid Operations and Procedures
GD-06 |  | Create and rollout HFTD safety training | Grid Design, Operations, and Maintenance | Workforce Planning (Asset Management)
SAF-01 | LSP-06 | Install perimeter cameras at substations | Situational Awareness and Forecasting | Grid Monitoring Systems
SAF-02 |  | Complete ignition sensor feasibility study at energized assets | Situational Awareness and Forecasting | Ignition Detection Systems
SAF-03 |  | Install weather stations at planned project sites | Situational Awareness and Forecasting | Environmental Monitoring Systems
SAF-04 |  | Calibrate weather stations semi-annually | Situational Awareness and Forecasting | Weather Station Maintenance and Calibration
SAF-05 |  | Expand weather forecasting capability at planned project sites. | Situational Awareness and Forecasting | Weather Forecasting
VM-01 |  | Application of current Vegetation Management standards to future Transmission Line asset | Vegetation Management and inspections | Integrated Vegetation Management
VM-02 |  | Applications of current Wood and Slash Management standards to future Transmission Line assets | Vegetation Management and inspections | Wood and Slash Management
VM-03 |  | Development of construction fire safety plan for Transmission Line vegetation activities | Vegetation Management and inspections | Workforce Planning
VM-04 |  | Conduct inspections | Vegetation Management and inspections | Defensible Space
VM-05 |  | Transmission Annual MVCD System Inspections | Vegetation Management and inspections | Vegetation Management Inspections
VM-06 |  | Detailed Ground Vegetation Evaluations | Vegetation Management and inspections | Vegetation Management Inspections
VM-07 |  | Pole clearing activities | Vegetation Management and inspections | Pole clearing

## Table 3-1
Priority | Risk | Risk Driver | x% of ignitions in HFTD | Topographical and Climatological Risk Factors
1 | Equipment / facility failure or damage | Transformer | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Anchor/guy | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Capacitor bank | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Conductor | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Connector device | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Insulator and bushing | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Lightning arrestor | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Pole | N/A | HFTD, heat, humidity, wind, precipitation
2 | Equipment / facility failure or damage | Switch | N/A | HFTD, heat, humidity, wind, precipitation
3 | Contact from object | 3rd party contact | N/A | HFTD, heat, humidity, wind, precipitation
3 | Contact from object | Aircraft vehicle contact | N/A | HFTD, heat, humidity, wind, precipitation
3 | Contact from object | Animal contact | N/A | HFTD, heat, humidity, wind, precipitation
3 | Contact from object | Ballon contact | N/A | HFTD, heat, humidity, wind, precipitation
3 | Contact from object | Land vehicle contact | N/A | HFTD, heat, humidity, wind, precipitation
3 | Contamination | Contamination | N/A | HFTD, heat, humidity, wind, precipitation
3 | Lightning | Lightning | N/A | HFTD, heat, humidity, wind, precipitation
3 | Vandalism/ theft | Vandalism/ theft | N/A | HFTD, heat, humidity, wind, precipitation
3 | Vegetation contact | Blow-in | N/A | HFTD, heat, humidity, wind, precipitation
3 | Wire-to-wire contact | Wire-to-wire contact | N/A | HFTD, heat, humidity, wind, precipitation
-- | Contact from object | Other contact from object | N/A | N/A
-- | Contact from object | Unknown | N/A | N/A
-- | Dig-in | Dig-in | N/A | N/A
-- | Equipment / facility failure or damage | Cross arm | N/A | N/A
-- | Equipment / facility failure or damage | Cutout | N/A | N/A
-- | Equipment / facility failure or damage | Fuse | N/A | N/A
-- | Equipment / facility failure or damage | Other | N/A | N/A
-- | Equipment / facility failure or damage | Recloser | N/A | N/A
-- | Equipment / facility failure or damage | Relay | N/A | N/A
-- | Equipment / facility failure or damage | Sectionalizer | N/A | N/A
-- | Equipment / facility failure or damage | Splice | N/A | N/A
-- | Equipment / facility failure or damage | Tap | N/A | N/A
-- | Equipment / facility failure or damage | Tie wire | N/A | N/A
-- | Equipment / facility failure or damage | Unknown | N/A | N/A
-- | Equipment / facility failure or damage | Voltage regulator/booster | N/A | N/A
-- | Protective device operation | Protective device operation | N/A | N/A
-- | Unknown | Unknown | N/A | N/A
-- | Vegetation contact | Fall-in (branch failure) | N/A | N/A
-- | Vegetation contact | Fall-in (root failure) | N/A | N/A
-- | Vegetation contact | Fall-in (trunk failure) | N/A | N/A
-- | Vegetation contact | Grow-in | N/A | N/A

## Table 3-2
Performance Metric | Assumption that underlies the use of the metric | Mitigation Section associated with the Performance Metric (state “WMP” if the metric applies to entire plan)
None | N/A | N/A

## Table 3-3
Year of WMP Cycle | Spend (thousands $USD)
2026 | Projected = 108
2027 | Projected = 154
2028 | Projected = 534

## Table 4-1
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | Total
Area served (sq. mi.) | N/A | N/A | N/A | N/A
Number of customers served | N/A | N/A | N/A | N/A
Overhead transmission lines (circuit miles) | 0 | 0 | 14.3 | 14.3
Overhead distribution lines (circuit miles) | 0 | 0 | 0 | 0
Underground transmission lines (circuit miles) | 0 | 0 | 29.2 | 29.2
Underground distribution lines (circuit miles) | 0 | 0 | 0 | 0

## Table 4-2
Ignition Date | Fire Name | Official Cause | Fire Size (acres) | No. of Fatalities | No. of Structures Destroyed and Damaged | Financial Loss (US$) | Lesson(s) Learned
None | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Table 4-3
Entry # | Circuit ID | Name of Circuit | Dates of Outages | Number of Customers Hours of PSPS per Outage | Measures Taken, or Planned to Be Taken, to Reduce the Need for and Impact of Future PSPS of Circuit | Estimated Annual Decline in Deenergization and Deenergization Impact on Customers
None | N/A | N/A | N/A | N/A | N/A | N/A

## Table 5-1
Assumption | Justification | Limitation | Applicable Models
The utility risk model does not currently evaluate the effect of adopting mitigation measures on risk reduction. Risk reduction effects of each mitigation measure are evaluated qualitatively. | As LSPGC currently only has one substation energized, it does not have sufficient operational history to quantitatively evaluate the effects of various mitigation measures on risk reduction. | N/A | N/A
The likelihood of ignition is not explicitly considered. Conservatively, ignitions are assumed to occur equally for all currently energized substations, future substations and overhead transmission lines per unit-mile. | LSPGC only recently energized 1 substation (Orchard) and thus has no ignition history (e.g., equipment failure rates, hazard vegetations fault rates). | N/A | Wildfire Risk Model
Burn likelihood is not explicitly considered. Conservatively, all ignitions are assumed to result in a wildfire incident. | LSPGC only recently energized 1 substation (Orchard) and thus has no ignition history or wildfire history. | N/A | Wildfire Risk Model
Static wind conditions based on probabilistic historical data are assumed across the analytical domain by unique Protected Service Area. | Static wind conditions, at landscape scales, are considered standard practice for understanding landscape-scale wildfire behavior modelling for baseline conditions. | Local weather conditions may result in localized severe fire weather conditions. However, the locations where this may be under-conservative will depend on topographic conditions. | Fire Intensity model and Fire Spread Model
Fuels are assumed to be continuous and uniform for the scale of the input data (i.e., 30m resolution) | This is standard practice for wildfire modelling inputs. | N/A | Fire Intensity Model and Fire Spread Model.
Fire characteristics at a point only depends on the conditions at that point (point-functional model). This means that there are certain non-local phenomena like: · Increase of ROS due to a concave front. · Fire interaction between different parts of the same fire or a different one. | This is standard practice for wildfire modelling inputs. | N/A | Fire Intensity Model and Fire Spread Model.
Fire spread is assumed to be elliptical (Rothermel model) although there are several variations such as double ellipse, oval, egg-shape, etc. | This is standard practice for wildfire modelling inputs. | N/A | Fire Intensity Model and Fire Spread Model.
Weather is given hourly and is assumed to remain constant during that time. There is no interpolation in time to compute the evolution of weather between hours. | This is standard practice for wildfire modelling inputs. | N/A | Fire Intensity Model and Fire Spread Model.
Fire is not coupled with the atmosphere in any way. This may seem like a major limitation in the model as wind is a main contribution to fire spread. Coupling of fire and atmospheric conditions is currently in the realm of research, with high levels of uncertainty. | This is standard practice for wildfire modelling inputs. | N/A | Fire Intensity Model and Fire Spread Model.
Gusts are not considered in the model | This is standard practice for wildfire modelling inputs. | N/A | Fire Intensity and Fire Spread Model.
No interaction between slope and wind other than creating an effective or equivalent wind. This means that fire is assumed to have an elliptical shape no matter the alignment of wind and slope. | This is standard practice for wildfire modelling inputs. | N/A | Fire Intensity Model and Fire Spread Model.
Spotting is only considered for crown fires | This is the current limitation of fire behavior models | N/A | Fire Intensity Model and Fire Spread Model.

## Table 5-2
Scenario ID | Design Scenario | Purpose
WL1 | Wind Load Condition 3 | Used in Fire Intensity and Fire Spread models.
WC2 | Weather Condition 2
VC1 | Vegetation Condition 1

## Table 5-3
Scenario ID | Extreme-Event Scenario | Purpose
N/A | N/A | N/A

## Table 5-4
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
R1 | Overall utility risk | WL1, WC2, VC1 | Wildfire risk (R2) | See related models | Overall utility risk at a substation or by unit-mile. | Unitless
R2 | Wildfire risk | WL1, WC2, VC1 | Wildfire Consequence (IRC3) | See related models | Wildfire risk at a substation or unit-mile | Unitless
IRC2 | Wildfire consequence | WL1, WC2, VC1 | Wildfire hazard intensity (FRC5) Wildfire exposure potential (FRC6) Wildfire vulnerability (FRC7) | See related models | Consequence score from 0-6 at a resolution of 30m | Unitless
FRC5 | Wildfire hazard intensity | WL1, WC2, VC1 | Topography Sustained wind speeds Vegetation | LANDFIRE Weather model LANDFIRE | Intensity of a fire at a 30m x 30m grid | Unitless
FRC6 | Wildfire exposure potential | WL1, WC2, VC1 | Topography Sustained wind speeds Vegetation Assets-at-Risk | LANDFIRE Weather model LANDFIRE Microsoft, DHS | Number, extent and type of assets exposed (structures, critical facilities and infrastructure) at a 30m resolution | Unitless
FRC7 | Wildfire vulnerability | WL1, WC2, VC1 | Structures | Microsoft | Spacing of structures | Feet

## Table 5-5
Risk Ranking | Circuit, Segment, or Span ID | Overall Utility Risk Score | Wildfire Risk Score | Outage Program Risk Score | Top Risk Contributors | Total Miles | Version of Risk Model Used
1 | Fern ST | 5 | 5 | N/A | N/A | N/A | N/A
2 | Manning ST | 0.11831 | 0.11831 | N/A | N/A | N/A | N/A
3 | Manning UM-12 | 0.078769 | 0.078769 | N/A | N/A | 0.3 | N/A
4 | Manning UM-11 | 0.026037 | 0.026037 | N/A | N/A | 1 | N/A
5 | Manning UM-3 | 0.019119 | 0.019119 | N/A | N/A | 1 | N/A
6 | Manning UM-2 | 0.017639 | 0.017639 | N/A | N/A | 1 | N/A
7 | Manning UM-1 | 0.014291 | 0.014291 | N/A | N/A | 1 | N/A
8 | Collinsville UM-1 | 0.014251 | 0.014251 | N/A | N/A | 0.8 | N/A
9 | Collinsville ST | 0.0035612 | 0.0035612 | N/A | N/A | N/A | N/A
10 | POSB UM-1 | 0.00315 | 0.00315 | N/A | N/A | 1 | N/A
11 | POSB UM-2 | 0.0028561 | 0.0028561 | N/A | N/A | 0.8 | N/A
12 | POSB UM-3 | 0.0016957 | 0.0016957 | N/A | N/A | 0.03 | N/A
13 | Manning UM-4 | 0 | 0 | N/A | N/A | 1 | N/A
14 | Manning UM-5 | 0 | 0 | N/A | N/A | 1.1 | N/A
15 | Manning UM-6 | 0 | 0 | N/A | N/A | 1 | N/A
16 | Manning UM-7 | 0 | 0 | N/A | N/A | 1 | N/A
17 | Manning UM-8 | 0 | 0 | N/A | N/A | 1 | N/A
18 | Manning UM-9 | 0 | 0 | N/A | N/A | 1 | N/A
19 | Manning UM-10 | 0 | 0 | N/A | N/A | 1 | N/A
20 | Orchard ST | 0 | 0 | N/A | N/A | N/A | N/A

## Table 5-6
Key Risk Assessment Area | Proposed Improvement | Type of Improvement | Expected Value Add | Timeframe and Key Milestones
RA-1-A. Risk Event Tracking | As LSPGC has only recently energized one substation (Orchard), it does not have any operational history to identify wildfire risk drivers (e.g., sources of ignitions, faults, etc.) | LSPGC plans to develop and implement a system for collecting data on wildfire risk drivers and near miss events to help better inform potential initiating events for wildfires and ultimately identify mitigations measures to reduce those events. | LSPGC anticipates the benefit of collecting wildfire risk event drivers and near misses will help increase awareness and understanding of potential sources of initiating events for wildfires due to its equipment, identify potential mitigation measures to reduce the likelihood of those events, and eventually use the data to inform the “ignition likelihood” component of the quantified risk assessment | 2026: Full deployment for logging risk drivers and near-miss events at Orchard Substations by end of Q4. 2027: Use collected data to enhance ignition likelihood decision making; develop QA/QC standards and internal reporting by end of Q2. 2028: Evaluate tracking system performance and integrate findings into mitigation strategies and 2029 WMP planning.
RA-1-B. Wildfire Incident Tracking | As LSPGC has only recently energized one substation (Orchard), it does not have any operational history that have led to wildfire incidents or near miss events. | LSPGC plans to develop and implement a system for collecting data on wildfire/fire incidents and near miss events to help better inform the potential for catastrophic wildfires across its equipment locations, and the associated technical and programmatic areas of improvement for these types of events. | LSPGC anticipates the benefit of collecting wildfire/fire incident details and near misses will help increase awareness and understanding of the potential for catastrophic wildfires due to its equipment and operational practices, identify potential mitigation measures to reduce the likelihood of catastrophic events, and eventually use the data to better inform the “burn likelihood” component of the quantified risk assessment. | 2026: Launch incident classification and data capture process across all operational sites by end of Q4. 2027: Correlate incident data with mitigation effectiveness and environmental factors by end of Q2. 2028: Use data to inform wildfire and emergency planning updates by end of Q4.

## Table 6-1
Priority | Circuit Segment and/or Span ID | Length (miles) | Overall Utility Risk | Wildfire Risk | Outage Program Risk | Percent of Overall Utility Risk | Associated Risk Drivers
1 | Fern Substation | N/A Substation Only | 5 | 5 | N/A | 94% | Transformer Failure Other Equipment Failures
2 | Manning Substation | Substation and 4.3 miles OH | 0.118 | 0.118 | N/A | 5% | Transformer Failure Other Equipment Failures Contract to Energized Equipment by Foreign Objects

## Table 6-2
Stakeholder | Stakeholder Point of Contact | Electrical Corporation Point of Contact | Stakeholder Role | Engagement Methods | Mitigation Initiative Activity | Level of Engagement for Mitigation Initiative Activity
LSPGC Business Leadership | Director, Asset Management | Associate Manager, Wildfire Mitigation | •Provides guidance and decision making on wildfire mitigation near and long-term planning •Informed on wildfire mitigation execution status •Informed and provides guidance on strategy/risk prioritization methodologies | Monthly Internal Meetings | All | Internal
Office of Energy Infrastructure Safety (OEIS or Energy Safety) | OEIS Deputy Director, Director of OEIS | Principal Manager, Regulatory Affairs & Compliance - State Regulatory Relations | •Defines WMP requirements • Participates and provides guidance in working groups • Reviews wildfire mitigation plan submissions and provides feedback, areas for continuous improvement, and issues approval or denial of plan | •Written comments •Ad hoc meetings | All | Local
Local Fire Agencies (includes Cal FIRE) | Various California Fire Chiefs | LSPGC Health, Safety, and Environmental Manager | Consulted | Ad hoc meetings | All | Local

## Table 6-3
Initiative Activity | Initiative Activity Section # | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness- Outage Program Risk | Cost-Benefit Score - Overall Risk | Cost-Benefit Score - Wildfire Risk | Cost-Benefit Score – Outage Program Risk | % HFRA Covered | Expected % Risk Reduction52 | Model(s) Used to Calculate Risk Impact
Not applicable

## Table 6-4
Circuit, Segment, or Span ID | Initial Overall Utility Risk | 2026 Initiative Activities | 2026 Overall Utility Risk | 2027 Initiative Activities | 2027 Overall Utility Risk | 2028 Initiatives Activities | 2028 Overall Utility Risk
N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Table 8-1
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | Target Unit | 2026 Target / Status | % Planned in HFTD for 2026 | % Planned in HFRA for 2026 | % Risk Reduction for 2026 | 2027 Target / Status | % Planned in HFTD for 2027 | % Planned in HFRA for 2027 | % Risk Reduction for 2027 | 2028 Target / Status | % Planned in HFTD for 2028 | % Planned in HFRA for 2028 | % Risk Reduction for 2028 | Three-year total | Section; Page number
Grid Design and System Hardening | Qualitative | Investigate advanced protection system enhancements for potential inclusion in project design (GD-01) | N/A | N/A | Begin review and investigation | 0 | 0 | N/A | Complete investigation | 0% | 0 | N/A | Implement design if applicable | 0% | 0% | N/A | N/A | 8.2.8; 66
Asset Inspections | Quantitative | Monthly Substation Inspections (GD-02) | N/A | # of inspections | 21 | 50% | N/A | 67% | 24 | 50% | N/A | 67% | 24 | 50% | N/A | 67% | 69 | 8.3.2; 69
Equipment Maintenance and Repair | Quantitative | Dissolved Gas Analysis Test at energized transformers (GD-03) | N/A | # of inspections | Q4 / 3 | N/A | N/A | N/A | Q4 / 6 | 50% | N/A | N/A | Q4 / 6 | N/A | N/A | N/A | 15 | 8.4.11; 80
Work Orders | Qualitative | Use Maximo to manage assets, inspections, and maintenance (GD-04) | N/A | N/A | initial system configuration | N/A | N/A | N/A | Expanded asset coverage | N/A | N/A | N/A | QA/QC reporting enhancement | N/A | N/A | N/A | N/A | 8.6; 89
Grid Operations and Procedures | Qualitative | Review Emergency Operations Plan and update annually (GD-05) | N/A | N/A | Q4 / Annual Update | N/A | N/A | N/A | Q4 / Annual Update | N/A | N/A | N/A | Q4 / Annual Update | N/A | N/A | N/A | N/A | 8.7.2; 92
Workforce Planning | Qualitative | Create and rollout HFTD safety training (GD-06) | N/A | N/A | Creation; Q2/2026 | N/A | N/A | N/A | Rollout; Q1,2027 | N/A | N/A | N/A | Maintained | N/A | N/A | N/A | N/A | 8.6;89

## Table 8-2
Type | Inspection Activity (Program) | Frequency or Trigger (Note 1) | Method of Inspection (Note 2) | Governing Standards & Operating Procedures | Cumulative Quarterly Target 2026, Q1 | Cumulative Quarterly Target 2026, Q2 | Cumulative Quarterly Target 2026, Q3 | Cumulative Quarterly Target 2026, Q4 | Cumulative Quarterly Target 2027, Q1 | Cumulative Quarterly Target 2027, Q2 | Cumulative Quarterly Target 2027, Q3 | Cumulative Quarterly Target 2027, Q4 | Cumulative Quarterly Target 2028, Q1 | Cumulative Quarterly Target 2028, Q2 | Cumulative Quarterly Target 2028, Q3 | Cumulative Quarterly Target 2028, Q4 | % of HFRA and HFTD Covered Annually by Inspection Type | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Transmission | Inspection | Annual | Ground, Aerial | GO 165, LS Power Grid maintenance plan Appendix one, Rev. 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | N/A | N/A | N/A | N/A
Substation | Detailed | Monthly | Ground | GO 165, LS Power Grid maintenance plan | 3 | 9 | 15 | 21 | 6 | 12 | 18 | 24 | 6 | 12 | 18 | 24 | 50% | N/A | N/A | N/A

## Table 8-3
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Asset Inspections | GD-02 | QA | Validate that asset inspections are performed according to the LSPGC Maintenance Plan and that results are documented completely and accurately.
Equipment Maintenance and Repair | GD-03 | QA | Confirm that Dissolved Gas Analysis (DGA) testing is performed annually in accordance with the LSPGC Maintenance Plan.
Workforce Planning | GD-06 | QA | Verify that all LSPGC Field Operations personnel accessing facilities in Tier 2+ HFTD complete HFTD Safety Training once the training is implemented.

## Table 8-4
Initiative/ Activity Being Audited | Type of Audit | Population /Sample Unit | 2026 Population Size | 2026: Sample Size | 2027: Population Size | 2027: Sample Size | 2028: Population Size | 2028: Sample Size | Percent of Sample in the HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Asset Inspections | Field | Total # of inspections per year | 21 | 1 | 24 | 2 | 24 | 2 | 50% | 95%/2% | 100% | 100% | 100%
Equipment Maintenance and Repair | Field | # of Dissolved Gas Analysis Test performed. | 3 | 3 | 6 | 6 | 6 | 6 | 50% | N/A | 100% | 100% | 100%
Grid Operations and Procedures | Desktop | # of LSPGC Field Operations staff accessing Tier 2+ HFTD sites annually | 9 | 9 | 9 | 9 | 9 | 9 | 100% of those accessing HFTD facilities | N/A | 100% completion of HFTD Safety Training prior to access | 100% completion of HFTD Safety Training prior to access | 100% completion of HFTD Safety Training prior to access

## LSPGC Table 8-1
Initiative/ Activity Being Audited | Program type | Applicable procedure | Revision and effective dates
Asset Inspections | QA | LSPGC Maintenance Plan | 2.0, 12/20/2024
Equipment Maintenance and Repair | QA | STATCOMs service agreement | 1.0, 03/12/2025
Grid Operations and Procedures | QA | LSPGC Emergency Operations Plan | 1.0, 07/02/2024

## LSPGC Table 8-2
Initiative/ Activity Being Audited | Quality Program Type | Sample Unit | Pass Criteria | Fail Criteria | Pass Rate Calculation
Asset Inspections | Field | Total number of inspections per year | Field conditions are consistent with inspection report and inspection report is consistent with inspection program procedures | Inspection report inconsistent with procedures or field conditions inconsistent with inspection report | Number of inspections passed/total inspections audited
Equipment Maintenance and Repair | Field | # dissolved gas analysis test performed in a calendar year | Field records confirm maintenance completed per service agreement | Maintenance activity not performed or documentation incomplete | Number of maintenance items passed ÷ total audited
Workforce Planning | Desktop | LSPGC Field Operations staff accessing Tier 2+ HFTD sites | Records confirm completion of required HFTD Safety Training | Missing or incomplete HFTD training records for personnel with Tier 2+ access | Number of personnel records passed ÷ total records audited

## LSPGC Table 8-3
Priority | Risk Level | Response
1 | Immediate safety, reliability, or fire risk with potential for significant impact | Address immediately
2 | Moderate to low safety or reliability risk | (1) six months for nonconformances that create a fire risk located in Tier 3 of the High Fire-Threat District; (2) 12 months for nonconformances that create a fire risk located in Tier 2 of the High Fire-Threat District; (3) 12 months for nonconformances that compromise worker safety; and (4) 59 months for all other Level 2 nonconformances.
3 | Low impact or acceptable, non-emergency condition | Take action (re-inspect, re-evaluate, or repair) as appropriate

## Table 8-5
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | N/A | N/A | N/A | N/A
HFTD Tier 2 | N/A | N/A | N/A | N/A
HFTD Tier 3 | N/A | N/A | N/A | N/A

## Table 8-6
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | N/A | N/A | N/A | N/A
Priority 2 | N/A | N/A | N/A | N/A
Priority 3 | N/A | N/A | N/A | N/A

## Table 8-7
Circuit ID | Number of outages in past three years | Cumulative outage duration | Cumulative number of customers impacted by outages
None | N/A | N/A | N/A

## LSPGC Table 8-4
Job Title | Qualifications | Training
Supervisor, Field Operations | • 5+ years of experience in utility field operations or equivalent • Requires completion of a technical or vocational training program as a substation or relay technician • Relevant prior experience with an electric utility or testing services contractor • Knowledge of substation equipment maintenance tasks • Familiarity of specialized technical software and test equipment utilized for substation maintenance activities | • Hazard Communication • Portable Fire Extinguishers • Emergency Action Plan • NERC CIP
Substation Operator | • Requires completion of a technical or vocational training program as a substation or relay technician • Relevant prior experience with an electric utility or testing services contractor • Knowledge of substation equipment maintenance tasks • Familiarity of specialized technical software and test equipment utilized for substation maintenance activities | • Hazard Communication • Portable Fire Extinguishers • Emergency Action Plan • NERC CIP
Relay Technician | • Requires completion of a technical or vocational training program as a substation or relay technician • 5+ years of relevant experience with an electric utility or testing services contractor • Knowledge of substation equipment maintenance tasks • Familiarity of specialized technical software and test equipment utilized for substation maintenance activities • Thorough understanding of protective relaying, communication, metering, and SCADA systems | • Hazard Communication • Portable Fire Extinguishers • Emergency Action Plan • NERC CIP

## LSPGC Table 8-5
Job Title | Qualifications | Training
Manager, Transmission Lines | • 5+ years experience in transmission line engineering, maintenance, or project management • Project and contractor oversight experience | • Hazard Communication • Portable Fire Extinguishers • Emergency Action Plan
Transmission Line Inspector | •TBD | • Hazard Communication • Portable Fire Extinguishers • Emergency Action Plan

## LSPGC Table 8-6
Job Title | Qualifications | Training
Principal Engineer | • Bachelor of Science in Engineering • Expertise in substation, transmission, or protection system design | • Varies
Senior Manager, System Protection | • 5 – 10+ years of protection engineering experience • Strong knowledge of NERC/CIP compliance | • NERC CIP • Hazard Communication • Portable Fire Extinguishers •Emergency Action Plan
Transmission Line Engineer | • BS Electrical or Civil Engineering • Familiarity with wildfire hardening strategies and CPUC General Orders 95/165 | • Pole loading and clearance design software training
Substation Engineer | • BS Electrical Engineering • Familiarity with grounding, insulation coordination, and substation hardening techniques | • Varies
Sr. Manager, Health, Safety, and Environmental | • BS in safety, health sciences, or related field • Licensed Paramedic with field response experience • Utility/industrial safety management background • Knowledge of wildfire risk and field safety in utility environments | • Hazard Communication • Portable Fire Extinguishers • Emergency Action Plan
Associate Manager, Wildfire Mitigation | • Experience in risk modeling, GIS mapping, or fuels assessment • Familiarity with OEIS, CPUC, and CAL FIRE requirements | • Hazard Communication • Portable Fire Extinguishers • Emergency Action Plan

## Table 9-1
Initiative | Quantitative or Qualitative | Activity (Tracking ID) | Previous Tracking ID, if applicable | Target Unit | 2026 Total/Status | % Risk reduction for2026 | 2027 Total/Status | % Risk reduction for 2027 | 2028 Total/Status | % Risk reduction 2028 | Three-year Total | Section; Page Number
Integrated Vegetation Management | Qualitative | Application of current Vegetation Management standards to future Transmission Line assets (VM-01) | n/a | n/a | Gap analysis complete | n/a | Solution analysis complete | n/a | Implementation based on energization timelines | n/a | n/a | 9.7.1, 110
Wood and Slash Management | Qualitative | Applications of current Wood and Slash Management standards to future Transmission Line assets (VM-02) | n/a | n/a | Gap analysis complete | n/a | Solution analysis complete | n/a | Implementation based on energization timelines | n/a | n/a | 9.5.2; 108
Workforce Planning | Qualitative | Development of construction fire safety plan for Transmission Line vegetation activities (VM-03) | n/a | n/a | Gap analysis complete | n/a | Solution analysis complete | n/a | Implementation based on energization timelines | n/a | n/a | 9.13; 120

## Table 9-2
Activity (Program) | Tracking ID | Previous Tracking ID, if applicable | Target Unit | Cml Qtrly Target 2026, Q1 | Cml Qtrly Target 2026, Q2 | Cml Qtrly Target 2026, Q3 | Cml Qtrly Target 2026, Q4 | Cml Qtrly Target 2027, Q1 | Cml Qtrly Target 2027, Q2 | Cml Qtrly Target 2027, Q3 | Cml Qtrly Target 2027, Q4 | Cml Qtrly Target 2028, Q1 | Cml Qtrly Target 2028, Q2 | Cml Qtrly Target 2028, Q3 | Cml Qtrly Target 2028, Q4 | % HFTD Covered in 2026 | % Risk Reduction for 2026 | % Risk Reduction for 2027 | % Risk Reduction for 2028 | Three- Year Total | Activity Timeline Target | Section; Page Number
Defensible Space | VM-04 | LSP-04 | Number of substations inspected | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 50% | n/a | n/a | n/a | 23 | 90 days | 9.6; 109
Transmission Annual MVCD System Inspections | VM-05 | n/a | Circuit miles inspected | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 9.2.1.1; 101
Transmission Detailed Ground Vegetation Evaluations | VM-06 | n/a | Circuit miles inspected | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 9.2.2.1; 103
Pole clearing | VM-07 | n/a | Poles | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 9.4; 106

## Table 9-3
Type | Inspection Activity (Program) | Area Inspected | Frequency
Transmission | Annual MVCD System Inspections | Territory-wide | 12 months NTE 18 months
Transmission | Detailed Ground Vegetation Evaluations | Territory-wide | As triggered
Transmission | Emergency/Storm Event Inspections | Event-based | Event-based

## Table 9-4
Partnering Agency/ Organization | Activities | Objectives | Electrical Corporation Role | Anticipated Accomplishments
N/A | N/A | N/A | N/A | N/A

## Table 9-5
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Defensible Space Inspections | VM-04 | QA | To ensure defensible space inspections are according to procedure and to remedy any non-conformance.

## Table 9-6
Initiative/ Activity Being Audited | Population /Sample Unit | 2026: Population Size | 2026: Sample Size | 2026: % of Sample in HFTD | 2027: Population Size | 2027: Sample Size | 2027: % of Sample in HFTD | 2028: Population Size | 2028: Sample Size | 2028: % of Sample in HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Defensible Space Inspection | Substation | 2 | 1 | 100% | 2 | 1 | 100% | 2 | 1 | 100% | 100%/0% | 100% | 100% | 100%

## LSPGC Table 9-1
Priority | Risk Level | Response
1 | Immediate safety, reliability, or fire risk with potential for significant impact | Address as soon as possible
2 | Moderate to low safety or reliability risk | Address within 3 months
3 | Low impact or acceptable, non-emergency condition | Address or re-evaluate within 12 months

## Table 9-7
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | N/A | N/A | N/A | N/A
HFTD Tier 2 | N/A | N/A | N/A | N/A
HFTD Tier 3 | N/A | N/A | N/A | N/A

## Table 9-8
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | N/A | N/A | N/A | N/A
Priority 2 | N/A | N/A | N/A | N/A
Priority 3 | N/A | N/A | N/A | N/A

## Table 9-9
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | # of Electrical Corporation Employees with Min Quals | # of Electrical Corporation Employees with Special Certifications | # of Contracted Employees with Min Quals | # of Contractor Employees with Applicable Certifications | Total # of Employees | Reference to Electrical Corporation Training/Qualification Programs
Licensed herbicide applicators | QAL or QAC | Qualified Applicators License or Qualified Applicators Certificate | 0 | 0 | TBD | TBD | TBD | N/A

## Table 10-1
Initiative | Quantitative or Qualitative | Activity | Previous Tracking ID, if applicable | Target Unit | 2026 | % risk reduction for 2026 | 2027 Total/Status | % risk reduction for 2027 | 2028 Total/Status | % risk reduction for 2028 | Three- year total | Section; Page number
| Target | (tracking ID #) |  |  | End of year total/Completion
Date
Environmental Monitoring Systems | Quantitative | Install weather stations at planned project sites (SAF-03) | N/A | Weather stations | 0 | N/A | 1 | N/A | 4 | N/A | 5 | 10.2.3; 131
Environmental Monitoring Systems | Qualitative | Integrate weather stations feed from energized site as a standard feed into the operations center. (SAF-03) | N/A | N/A | In progress; July 2026 | N/A | Completed; October 2027 | N/A | Completed; October 2027 | N/A | N/A | 10.2; 127
Grid Monitoring Systems | Quantitative | Install perimeter cameras at substations (SAF-01) | LSP-06 | # of cameras installed | 0 | N/A | 0 | N/A | TBD based on final design | N/A | TBD | 10.4; 138
Grid Monitoring Systems | Qualitative | Install perimeter cameras from energized site as standard feed into the operations center. (SAF-01) | LSP-06 | N/A | In progress; July 2026 | N/A | Completed; July 2027 | N/A | Completed; July 2027 | N/A | N/A | 10.3; 132
Ignition Detection Systems | Qualitative | Complete ignition sensor feasibility study at HFTD energized assets (SAF-02) | N/A | N/A | Start; Q3 2026 | N/A | Completed; End of Q4 2027 | N/A | Completed; End of Q4 2027 | N/A | N/A | 10.4; 138
Ignition Detection Systems | Quantitative | Install integrated fire-detection systems in STATCOM buildings (SAF-02) | N/A | # of detections systems | 1 | N/A | 0 | N/A | 0 | N/A | 1 | 10.4; 138
Weather Station Maintenance and Calibration | Quantitative | Calibrate weather stations semi-annually (SAF-04) | N/A | # of weather stations | 2 | N/A | 2 | N/A | 2 | N/A | 6 | 10.5.5; 140
Weather Station Maintenance and Calibration | Qualitative | Follow manufacturer calibration procedures and document compliance (SAF-04) | N/A | N/A | Procedure followed | N/A | Procedure followed | N/A | Procedure followed | N/A | 6 | 10.5.5; 145
[5 empty] | and documented |  | and documented |  | and documented
Weather Forecasting | Quantitative | Expand weather forecasting capability at planned project sites. (SAF-05) | N/A | # of weather stations | 0 | N/A | 0 | N/A | 4 | N/A | 4 | 10.5.4; 145
Weather Forecasting | Qualitative | Integrate weather-forecasting support tool into operations (SAF-05) | N/A | N/A | In progress; Q2 2026 | N/A | Completed; Q2 2027 | N/A | Completed; Q2 2027 | N/A | N/A | 10.5; 142

## Table 10-2
System | Measurement/ Observation | Frequency | Purpose and Integration
Weather Stations | wind speed, wind direction, wind gusts, humidity, and temperature | 24/7 per site | Purpose: to monitor environmental conditions at each facility. Integration: weather stations are included in station design and installed during initial station construction. Testing and calibration is done during commissioning of each site.
Fire Detection Systems (Substation Buildings) | heat/smoke | 24/7 | Real-time detection of potential fire activity inside substation buildings

## Table 10-3
System | Measurement/ Observation | Frequency | Purpose and Integration
Orchard Substation EMS (SCADA-based via AspenTech OSI EMS) | Transformer oil and winding temperatures Breaker status and alarms SOE logging SACADA analog/digital values | Continuous (real-time) | Provides centralized real-time visibility, control, and alarming for critical substation assets. Integrated with LSPGC’s Primary and Backup Transmission Control Centers.

## Table 10-4
Detection System | Capabilities | Companion Technologies | Contribution to Fire Detection and Confirmation
High-Definition Surveillance Cameras | Real-time and post-event viewing of substation grounds | Weather station alerts, alarm logs | Allow TSOs to detect visible smoke/flame activity and assess severity
Fire Alarm Systems | Detects heat/smoke/flame in control house enclosures | Surveillance cameras | Notifies TSOs of fire activity in buildings; visually confirmed
SCADA Transformer Monitoring | Continuous tracking of temperature readings for early fault indicators | EMS/SCADA, alarm thresholds | Alerts operators to overheating that may precede ignition

## Table 10-5
Feature Group | Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
N/A | N/A | N/A | LSPGC does not calculate its own FPI | N/A | N/A | N/A | N/A

## Table 11-1
Initiative | Activity (tracking ID #) | Previous Tracking ID, if applicable | 2026 End of year total/Completion Date | 2027 Status | 2028 Status | Section; Page number
Emergency Preparedness and Recovery Plan | Update System Restoration Plan to include Fern Road Substation (EP-01) | N/A | Finalize; Q1 2026 | Maintained; Q1 2027 | Maintained; 2028 | 11.2.1.1.; 199
Public Outreach, Communication, and Engagement | Establish wildfire-specific communication protocols (EP-02) | N/A | Framework Drafted: Q4 2026 | Completed: Q3 2027 | Maintained; 2028 | 11.3.1; 206
External Collaboration and Coordination | Initiate and maintain annual outreach with local fire/emergency agencies near energized assets (EP-03) | N/A | Started: Q2 2026 | Ongoing; 2027 | Ongoing; 2028 | 11.3.2; 210

## Table 11-2
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
N/A | N/A | N/A

## Table 11-3
Public Safety Partner Group | Name of Entity | Key Protocols | Frequency of Prearranged Communication Review and Update
Local Fire Agencies | Shasta County Fire Dept | Coordination during permitting, emergency site access, wildfire | Annually
CPUC | CPUC | Regulatory reporting and fire-related incident notifications | Annually
PG&E (interconnecting utility) | PG&E | Incident coordination, PSPS-related information relay | Annually
CAISO | CAISO | Event-based notification of grid-impacting conditions | Annually

## Table 11-4
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Emergency communication process still evolving | Continue development of formal protocols | Strategy: Update the existing the Emergency Operations Plan to include planned sites upon energization. Target timeline: Q4 2026
Local public safety contact lists not fully developed | Expand contact lists as additional assets become operational | Strategy: Create an internal regional and local fire agencies contact list around existing construction and planned future sites. Target timeline: Q4 2026

## Table 11-5
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Local County Resource Management Agency | LSPGC currently doesn't have any activity with Tribal Agency, CSO, or fire safe council. | N/A | N/A
Local Fire Safe Council | LSPGC currently doesn't have any activity with Tribal Agency, CSO, or fire safe council. | N/A | N/A
Local County Resource Conservation District | LSPGC currently doesn't have any activity with Tribal Agency, CSO, or fire safe council. | N/A | N/A
Regional Forest and Fire Capacity Program (RFFCP) Grantee | LSPGC currently doesn't have any activity with Tribal Agency, CSO, or fire safe council. | N/A | N/A

## Table 11-6
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
Emerging Collaboration Framework | As a newly operational transmission operator with a limited public-facing presence to date, LSPGC has had few formal collaboration opportunities with local agencies and fire councils. | Strategy: Develop and publish web-based informational materials outlining LSPGC’s wildfire mitigation approach and infrastructure footprint. Assign a wildfire planning liaison and initiate outreach meetings with local agencies in regions where construction is active or planned. Timeline: Web materials online by Q4 2026; Internal engagement begins Q1 2027.

## Table 11-7
Name of County, City, or Tribal Agency or Civil Society Organization(e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
None | N/A | N/A | N/A

## Table 11-8
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
None | N/A | N/A

## Table 11-9
Stakeholder Group/Target Community | Event Type | Method(s) for Communicating | Means to Verify Message Receipt | Interests or Concerns Before, During, and After Wildfire and PSPS events
None | N/A | N/A | N/A | N/A

## Table 11-10
Target Community | Interests or Concerns Before, During, and After Wildfire and PSPS events
None | N/A

## Table 11-11
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
None | N/A | N/A

## Table 12-1
Initiative | Activity (tracking ID #) | Previous Tracking ID, if applicable | 2026 End of year total/Completion Date | 2027 Total/Status | 2028 Total/Status | Section ; Page number
Asset Management | Use Maximo to manage assets, inspections, and maintenance (GD-04) | N/A | Initial system configuration | Expanded asset coverage | QA/QC and reporting enhancements | 12.2; 171
Vegetation Management | Centralize vegetation data and integrate inspection workflows (ENT-01) | N/A | System setup and data population | Reporting and contractor access | Audit and tracking features enabled | 12.2; 172
Grid Monitoring | Maintain SCADA and operational telemetry for substation oversight (ENT-02) | N/A | Baseline alarms mapped | Monitoring workflows in use | System validated against commitments | 12.2; 172
Ignition Detection | Research and complete evaluation of potential ignition detection capabilities at HFTD energized assets (SAF-02) | N/A | Review available technologies | Assess feasibility and applicability | Inform long-term strategy and planning | 10.4; 132
Weather Forecasting | Use StormGeo and RAWS data for operational awareness (SAF-05) | N/A | Data feeds configured | Alerts routed to key personnel | Used to inform operational readiness | 10.5.4; 139
Risk Assessment | Develop basic dashboards for inspection trends and risk prioritization (ENT-03) | N/A | Planning and baseline development | Data inputs aligned to initiatives | Dashboards used in internal reviews | 12.2; 172

## Table 13-1
ID # | Year of Lesson Learned | Subject | Category and Source of Lesson Learned | Description of Lesson Learned | Proposed WMP Improvement | Timeline for Implementation | Reference
1 | 2024 | Vegetation management in substation defensible space area | Construction period inspections and contractor input | Defensible space in HFTD is not one-size fits all and needs to consider safety, terrain features and project design | Create formal Substation Defensible Space Procedure | Q1 2026 | Substation Defensible Space Procedure one finalized
2 | 2023 | Contractor construction fire prevention plan improvements | Emergency Preparedness | Contractor CFPP drafts were routinely underwhelming and required many iterations of feedback before approval | Create CFPP template requirements to be provided to contractors for future major projects | Q4 2026 | CFPP requirements document once drafted

## Table 13-2
Discontinued Initiative Activity (Tracking ID) | Rationale for Discontinuation | Lessons Learned | Replacement Activities (include page # where discussed)
N/A – No discontinued activities to report during 2023–2025. LSPGC became operational in March 2025