## BVES Table 2-1
WMP Section | Name | Title | Email | Phone Number
1. Executive Summary | Paul Marconi | President, Treasurer, & Secretary | Paul.Marconi@bvesinc.com | 909-202-9539
2. Responsible Persons | Paul Marconi | President, Treasurer, & Secretary | Paul.Marconi@bvesinc.com | 909-202-9539
3. Overview of WMP | Paul Marconi | President, Treasurer, & Secretary | Paul.Marconi@bvesinc.com | 909-202-9539
4. Overview of the Service Territory | Tom Chou | Utility Engineer & Wildfire Mitigation Supervisor | Tom.Chou@bvesinc.com | 909-273-8009
5. Risk Methodology and Assessment | Alexis Ravnik | Electric Distribution Systems Engineer | Alexis.Ravnik@bvesinc.com | 909-649-5379
6. Wildfire Mitigation Strategy Development | Tom Chou | Utility Engineer & Wildfire Mitigation Supervisor | Tom.Chou@bvesinc.com | 909-273-8009
7. Public Safety Power Shutoff | Sean Matlock | Energy Resource Manager & Assistant Corporate Secretary | Sean.Matlock@bvesinc.com | 909-522-1913
8. Grid Design, Operations, and Maintenance | Tom Chou | Utility Engineer & Wildfire Mitigation Supervisor | Tom.Chou@bvesinc.com | 909-273-8009
9. Vegetation Management and Inspections | Jared Hennen | Wildfire Mitigation and Reliability Engineer | Jared.Hennen@bvesinc.com | 909-255-2948
10. Situational Awareness and Forecasting | Tom Chou | Utility Engineer & Wildfire Mitigation Supervisor | Tom.Chou@bvesinc.com | 909-273-8009
11. Emergency Preparedness, Collaboration, and Public Awareness | Paul Marconi | President, Treasurer, & Secretary | Paul.Marconi@bvesinc.com | 909-202-9539
12. Enterprise Systems | Tom Chou | Utility Engineer & Wildfire Mitigation Supervisor | Tom.Chou@bvesinc.com | 909-273-8009
13. Lessons Learned | Paul Marconi | President, Treasurer, & Secretary | Paul.Marconi@bvesinc.com | 909-202-9539

## Table 3-1
Priority | Risk | Risk Driver | x% of ignitions in HFTD | Topographical and Climatological Risk Factors
Medium | Contact from object | Animal contact | 1.7% | Service area mostly WUI
Medium | Contact from object | Balloon contact | 0.3% | None
High | Contact from object | Land vehicle contact | 8.6% | None
Medium | Contact from object | Aircraft vehicle contact | 0.3% | Airport in close proximity to facilities
Medium | Contact from object | 3rd party contact | 1.6% | None
Medium | Contact from object | Other contact from object | 0.4% | None
Low | Contact from object | Unknown | 0% | None
High | Vegetation contact | Fall-in (branch failure) | 6.9% | Heavy vegetation
High | Vegetation contact | Fall-in (trunk failure) | 9.7% | Heavy vegetation
Low | Vegetation contact | Fall-in (root failure) | 0% | Heavy vegetation
High | Vegetation contact | Blow-in | 9.6% | Heavy vegetation
Medium | Vegetation contact | Grow-in | 1% | Heavy vegetation
Low | Equipment / facility failure or damage | Anchor/guy | 0% | None
Low | Equipment / facility failure or damage | Capacitor bank | 0.1% | None
Medium | Equipment / facility failure or damage | Conductor | 1.7% | None
High | Equipment / facility failure or damage | Connector device | 7.5% | None
Low | Equipment / facility failure or damage | Cross arm | 0.1% | None
High | Equipment / facility failure or damage | Fuse | 11.9% | None
Medium | Equipment / facility failure or damage | Cutout | 2.3% | None
Low | Equipment / facility failure or damage | Insulator and bushing | 0.2% | Lightning storms
Low | Equipment / facility failure or damage | Lightning arrestor | 0.1% | Lightning storms
Medium | Equipment / facility failure or damage | Pole | 0.4% | None
Medium | Equipment / facility failure or damage | Recloser | 0.7% | None
Low | Equipment / facility failure or damage | Relay | 0% | None
Medium | Equipment / facility failure or damage | Sectionalizer | 1.3% | None
Medium | Equipment / facility failure or damage | Splice | 0.3% | None
Medium | Equipment / facility failure or damage | Switch | 0.5% | None
Low | Equipment / facility failure or damage | Tap | 0% | None
Low | Equipment / facility failure or damage | Tie wire | 0.1% | None
High | Equipment / facility failure or damage | Transformer | 3.4% | None
Medium | Equipment / facility failure or damage | Voltage regulator/booster | 0.5% | None
Medium | Equipment / facility failure or damage | Unknown | 1% | None
High | Equipment / facility failure or damage | Other | 2.7% | None
High | Wire-to-wire contact | Wire-to-wire contact | 3.3% | High winds
Low | Contamination | Contamination | 0% | None
Low | Protective device operation | Protective device operation | 0% | None
Low | Vandalism/ theft | Vandalism/ theft | 0.2% | None
High | Lightning | Lightning | 21.4% | Lightning storms
Low | Unknown | Unknown | 0% | None
Medium | Dig-in | Dig-in | 0.5% | None

## Table 3-2
Performance Metric | Assumption that underlies the use of the metric | Section associated with the Performance Metric (state “WMP” if the metric applies to entire plan)
None | N/A | N/A

## BVES Table 3-1
UTILITY INITIATIVE TRACKING ID | UTILITY INITIATIVE NAME | WMP INITIATIVE CATEGORY | WMP INITIATIVE
EP_1 | Emergency preparedness and recovery plan | Emergency Preparedness and Community Outreach | Emergency preparedness and recovery plan
EP_2 | External collaboration and coordination | Emergency Preparedness and Community Outreach | External collaboration and coordination
EP_3 | Public communication, outreach, and education | Emergency Preparedness and Community Outreach | Public communication, outreach, and education
EP_4 | Customer support in wildfire and PSPS emergencies | Emergency Preparedness and Community Outreach | Customer support in wildfire and PSPS emergencies
ENT_1 | Asset management and inspection enterprise system(s) | Enterprise Systems | Summary of Enterprise Systems
ENT_2 | Vegetation management enterprise system | Enterprise Systems | Summary of Enterprise Systems
GD_1 | Covered Conductor Replacement Project (Reconductor) | Grid Design, Operations, and Maintenance | Covered conductor installation
GD_10 | Fuse TripSaver Automation | Grid Design, Operations, and Maintenance | Installation of system automation equipment
GD_11 | Non-Exempt Surge Arrester Replacement | Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions
GD_12 | Tree Attachment Removal Project | Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions
GD_13 | Safety and Technical Upgrades to Lake Substation | Grid Design, Operations, and Maintenance | Other technologies and systems not listed above
GD_14 | Partial Safety and Technical Upgrades to Village Substation | Grid Design, Operations, and Maintenance | Other technologies and systems not listed above
GD_15 | Equipment maintenance and repair | Grid Design, Operations, and Maintenance | Equipment maintenance and repair
GD_16 | Asset Quality assurance / quality control | Grid Design, Operations, and Maintenance | Quality assurance / quality control
GD_17 | Asset Open work orders | Grid Design, Operations, and Maintenance | Work orders
GD_18 | Equipment Settings to Reduce Wildfire Risk | Grid Design, Operations, and Maintenance | Equipment Settings to Reduce Wildfire Risk
GD_19 | Grid Response Procedures and Notifications | Grid Design, Operations, and Maintenance | Grid Response Procedures and Notifications
GD_2 | Minor Undergrounding Upgrades Projects | Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment
GD_20 | Personnel Work Procedures and Training in Conditions of Elevated Fire Risk | Grid Design, Operations, and Maintenance | Personnel Work Procedures and Training in Conditions of Elevated Fire Risk
GD_21 | Asset Workforce Planning | Grid Design, Operations, and Maintenance | Workforce Planning
GD_22 | Detailed Inspections | Grid Design, Operations, and Maintenance | Asset inspections
GD_23 | Patrol Inspections | Grid Design, Operations, and Maintenance | Asset inspections
GD_24 | UAV Thermography Inspections | Grid Design, Operations, and Maintenance | Asset inspections
GD_25 | UAV HD Photography/Videography Inspections | Grid Design, Operations, and Maintenance | Asset inspections
GD_26 | Third-Party Ground Patrol Inspections | Grid Design, Operations, and Maintenance | Asset inspections
GD_27 | Intrusive Pole Inspections | Grid Design, Operations, and Maintenance | Asset inspections
GD_28 | Substation inspections | Grid Design, Operations, and Maintenance | Asset inspections
GD_3 | Covered Conductor Replacement Project (Pole Assessment) | Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements
GD_4 | Evacuation Route Hardening Project | Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements
GD_5 | Traditional overhead hardening | Grid Design, Operations, and Maintenance | Traditional overhead hardening
GD_6 | Bear Valley Solar Energy Project | Grid Design, Operations, and Maintenance | Microgrids
GD_7 | Bear Valley Energy Storage Project | Grid Design, Operations, and Maintenance | Microgrids
GD_8 | Switch and Field Device Automation | Grid Design, Operations, and Maintenance | Installation of system automation equipment
GD_9 | Capacitor Bank Upgrade Project | Grid Design, Operations, and Maintenance | Installation of system automation equipment
RMA_1 | Risk Methodology and Assessment | Risk Methodology and Assessment | Risk Methodology and Assessment
SAF_1 | Advanced weather monitoring and weather stations | Situational Awareness and Forecasting | Environmental monitoring systems
SAF_2 | Install Fault Indicators | Situational Awareness and Forecasting | Grid monitoring systems
SAF_3 | Online Diagnostic System | Situational Awareness and Forecasting | Grid monitoring systems
SAF_4 | Autonomous Monitoring of Power Line Infrastructure | Situational Awareness and Forecasting | Ignition detection systems
SAF_5 | ALERT Wildfire Cameras | Situational Awareness and Forecasting | Ignition detection systems
SAF_6 | Weather forecasting | Situational Awareness and Forecasting | Weather forecasting
SAF_7 | Fire potential index | Situational Awareness and Forecasting | Fire potential index
VM_1 | Detailed Inspections | Vegetation Management and Inspection | Vegetation management inspections
VM_10 | Pole clearing | Vegetation Management and Inspection | Pole clearing
VM_11 | Wood and slash management | Vegetation Management and Inspection | Wood and slash management
VM_12 | Substation defensible space | Vegetation Management and Inspection | Defensible space
VM_13 | Emergency response vegetation management | Vegetation Management and Inspection | Activities based on weather conditions
VM_14 | Post-fire service restoration | Vegetation Management and Inspection | Post-fire service restoration
VM_15 | Vegetation Management Quality assurance / quality control | Vegetation Management and Inspection | Quality assurance / quality control
VM_16 | Vegetation Management Open work orders | Vegetation Management and Inspection | Work orders
VM_17 | Vegetation Management Workforce planning | Vegetation Management and Inspection | Workforce Planning
VM_2 | Patrol Inspections | Vegetation Management and Inspection | Vegetation management inspections
VM_3 | UAV HD Photography/Videography Inspections | Vegetation Management and Inspection | Vegetation management inspections
VM_4 | LiDAR Inspections | Vegetation Management and Inspection | Vegetation management inspections
VM_5 | Third-Party Ground Patrol Inspections | Vegetation Management and Inspection | Vegetation management inspections
VM_6 | Substation inspections | Vegetation Management and Inspection | Vegetation management inspections
VM_7 | Satellite Imaging Inspections | Vegetation Management and Inspection | Vegetation management inspections
VM_8 | Fall-in Mitigation and High-risk Species | Vegetation Management and Inspection | Pruning and Removal
VM_9 | Clearance | Vegetation Management and Inspection | Pruning and Removal
WMSD_1 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy Development

## Table 3-3
Year of WMP Cycle | Spend (thousands $USD)
2026 | 17085
2027 | 44391
2028 | 18774

## Table 4-1
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | Total
Area served (sq. mi.) | 30.6 | 1.4 | 0 | 32
Number of customers served | 24786 | 1 | 0 | 24787
Overhead transmission lines (circuit miles) | 0 | 0 | 0 | 0
Overhead distribution lines (circuit miles) | 203.93 | 1.56 | 0 | 205.49
Underground transmission lines (circuit miles) | 0 | 0 | 0 | 0
Underground distribution lines (circuit miles) | 62.03 | 0 | 0 | 62.03

## Table 4-2
Ignition Date | Fire Name | Official Cause | Fire Size (acres) | No. of Fatalities | No. of Structures Destroyed and Damaged | Financial Loss (US$) | Lesson(s) Learned
None | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Table 4-3
Entry # | Circuit ID | Name of Circuit | Dates of Outages | Number of Customers Hours of PSPS per Outage | Measures Taken, or Planned to Be Taken, to Reduce the Need for and Impact of Future PSPS of Circuit | Estimated Annual Decline in PSPS Events and PSPS Impact on Customers
None | N/A | N/A | N/A | N/A | N/A | N/A

## Table 5-1
Assumption | Justification | Limitation | Applicable Models
The model evaluates each mitigation measure in isolation of other mitigation measures to calculate risk benefit. | N/A | N/A | Risk Register Model
Currently BVES utilizes SME evaluation of likelihood and consequence instead of raw data input. SME’s evaluate data sources such as outage log, LiDAR surveys, asset hardening, etc. in developing their evaluations. While the data is largely standardized and consistent, the input to the model from the data can fluctuate somewhat due to the inherent subjectivity of the SME’s interpretation of the data. | N/A | N/A | Risk Register Model
Because the determination of likelihood and consequence is by SME evaluation, stability of the assumptions is susceptible to instability when SMEs change. | N/A | N/A | Risk Register Model
The physical framework development is based on an idealized situation in steady state spread which may not fit some extreme behavior of fires. | N/A | N/A | WFA-E
Fuels are assumed to be continuous and uniform for the scale of the input (typically between 10-to-30-meter (m) resolution). | N/A | N/A | WFA-E
Fire characteristics at a point only depends on the conditions at that point (point-functional model). This means that there are certain non-local phenomena like: · Increase of ROS due to a concave front. · Fire interaction between different parts of the same fire or a different one. | N/A | N/A | WFA-E
Fire spread is assumed to be elliptical although there are several variations such as double ellipse, oval, egg-shape, etc. | N/A | N/A | WFA-E
Weather is given hourly and is assumed to remain constant during that time. There is no interpolation in time to compute evolution of weather between hours. | N/A | N/A | WFA-E
Reliability of weather inputs in the mid-range forecast (2 to 5 days). | N/A | N/A | WFA-E
Fire is not coupled with the atmosphere in any way. This may seem like a major limitation in the model as wind is a main contribution to fire spread and at present many models (especially physical ones) try to couple wind and fire. The main reasons for us not to consider the coupling is: · It would make it unfeasible to run millions of simulations considering the coupling effect. · Empirical and semi-empirical models have been developed using an average wind speed as an input, so it is not clear that considering more granular wind at the front is advisable. | N/A | N/A | WFA-E
Fire is always assumed to be fully developed. Fire acceleration, flashover, or decay is not considered. | N/A | N/A | WFA-E
Atmospheric instability which may have a deep impact on ROS (beer 1991) is not considered in the model. | N/A | N/A | WFA-E
Gusts are not considered in the model. | N/A | N/A | WFA-E
No interaction between slope and wind other than creating an effective or equivalent wind. This means that fire is assumed to have an elliptical shape no matter the alignment of wind and slope. | N/A | N/A | WFA-E
Models have been developed with scares empirical data. The abundance of today’s fire data sources, however, is allowing us to better adjust models to observed fire patterns. | N/A | N/A | WFA-E
Fuel array description of the vegetation may not perfectly describe fuel characteristics. | N/A | N/A | WFA-E
Spotting is only considered in surface fires. | N/A | N/A | WFA-E

## Table 5-2
Scenario ID | Design Scenario | Purpose
WL1 | Wind Load Condition 1 | Used in the WFA FireSight models.
WL2 | Wind Load Condition 2
WC2 | Weather Condition 2,
VC1 | Vegetation Condition 1
VC3 | Vegetation Condition 3

## Table 5-3
Scenario ID | Extreme-Event Scenario | Purpose
ES1 | 2030 Climate Conditions (mostly concerned with fuel levels and moisture) | Assess if climate change, as well as any resulting changes in wildfire consequence, may influence BVES’s existing grid hardening strategy.

## Table 5-4
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
R1 | Overall Utility Risk | Wind Load Condition 1, Wind Load Condition 2, Weather Condition 2, Vegetation Condition 1, Vegetation Condition 3 | Wildfire Risk (R2) Outage Program Risk (R3) | Current: BVES Risk Register Model, Fire Safety Circuit Matrix, and Technosylva WFA Future: DIREXYON and Technosylva WFA | Overall utility risk at the circuit or at the risk mitigation initiative. | Unitless
R2 | Wildfire Risk | Wind Load Condition 3, Weather Condition 2, Vegetation Condition 1, Vegetation Condition 3 | Wildfire Likelihood (IRC1) Wildfire Consequence (IRC3) | Current: BVES Risk Register Model, Fire Safety Circuit Matrix, and Technosylva WFA Future: DIREXYON and Technosylva WFA | Wildfire risk at the circuit or at the risk mitigation initiative. | Unitless
R3 | Outage Program Risk | Wind Load Condition 2, Weather Condition 1, Vegetation Condition 1 | PSPS Likelihood (IRC4) PSPS Consequence (IRC5) PEDS Outage Likelihood (IRC6) [Deferred to a future update] PEDS Outage Consequence (IRC7) [Deferred to a future update] | Current: BVES Risk Register Model, Fire Safety Circuit Matrix, Technosylva WFA, and Technosylva RAVE Future: DIREXYON, Technosylva WFA, and Technosylva RAVE | Outage program risk at the circuit or at the risk mitigation initiative. | Unitless
R4 | PSPS Risk | Wind Load Condition 2, Weather Condition 1, Vegetation Condition 1 | PSPS Likelihood (IRC4) PSPS Consequence (IRC5) | Current: BVES Risk Register Model, Fire Safety Circuit Matrix, Technosylva WFA, and Technosylva RAVE Future: DIREXYON, Technosylva WFA, and Technosylva RAVE | PSPS risk at the circuit level or at the risk mitigation initiative level. | Unitless
R5 | PEDS Outage Risk | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update.
IRC1 | Wildfire Likelihood | Wind Load Condition 3, Weather Condition 2, Vegetation Condition 1, Vegetation Condition 3 | Burn Likelihood (FRC4) Ignition Likelihood (IRC2) | Current: BVES Risk Register Model, Fire Safety Circuit Matrix, and Technosylva WFA Future: DIREXYON and Technosylva WFA | Wildfire Likelihood per circuit. | Unitless
IRC2 | Ignition Likelihood | Wind Load Condition 3, Weather Condition 2, Vegetation Condition 1, Vegetation Condition 3 | Equipment Caused Ignition Likelihood (FRC1) Contact from Vegetation Ignition Likelihood (FRC2) Contact from Object Ignition Likelihood (FRC3) | Current: Fire Safety Circuit Matrix and Technosylva WFA Future: DIREXYON and Technosylva WFA | Ignition Likelihood per circuit. | Unitless
IRC3 | Wildfire Consequence | Wind Load Condition 3, Weather Condition 2, Vegetation Condition 1, Vegetation Condition 3 | Wildfire Hazard Intensity (FRC5) Wildfire Exposure Potential (FRC6) Wildfire Vulnerability (FRC7) | Current: Technosylva WFA Future: DIREXYON and Technosylva WFA | Wildfire Consequence per circuit. | Unitless
IRC4 | PSPS Likelihood | Wind Load Condition 2, Weather Condition 1, Vegetation Condition 1 | Wildfire Likelihood (IRC1) | Current: Technosylva WFA Future: DIREXYON and Technosylva WFA | PSPS Likelihood per circuit. | Unitless
IRC5 | PSPS Consequence | Wind Load Condition 2, Weather Condition 1, Vegetation Condition 1 | Wildfire Exposure Potential (FRC6) Wildfire Vulnerability (FRC7) PSPS Exposure Potential (FRC8) PSPS Vulnerability (FRC9) | Current: Technosylva RAVE Future: DIREXYON, Technosylva WFA, and Technosylva RAVE | AFN customers and buildings impacted per circuit level | Customers per circuit Buildings per circuit
IRC6 | PEDS Outage Likelihood | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update.
IRC7 | PEDS Outage Consequence | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update.
FRC1 | Equipment Caused Ignition Likelihood | Wind Load Condition 2, Weather Condition 1, Vegetation Condition 1 | Distribution Asset Data, Historical Outages and Ignitions | Current: None Future: DIREXYON | Likelihood of ignition caused by equipment at the asset level. | Annualized ignition probability of ignition
FRC2 | Contact from Vegetation Ignition Likelihood | Wind Load Condition 2, Weather Condition 1, Vegetation Condition 1 | Distribution Asset Data, Historical Outages and Ignitions | Current: None Future: DIREXYON | Likelihood of ignition from vegetation contact at the asset level. | Annualized ignition probability of ignition
FRC3 | Contact from Object Ignition Likelihood | Wind Load Condition 2, Weather Condition 1, Vegetation Condition 1 | Distribution Asset Data, Historical Outages and Ignitions | Current: None Future: DIREXYON | Likelihood of ignition from object contact at the asset level. | Annualized ignition probability of ignition
FRC4 | Burn Likelihood | Wind Load Condition 3, Weather Condition 1, Vegetation Condition 1, Vegetation Condition 3 | Vegetation | Current: Technosylva WFA Future: DIREXYON and Technosylva WFA | 100m x 100m pixel destructive potential classification | Unitless
FRC5 | Wildfire Hazard Intensity | Wind Load Condition 3, Weather Condition 1, Vegetation Condition 1, Vegetation Condition 3 | Sustained Wind Speeds Vegetation | Current: Technosylva WFA Future: DIREXYON and Technosylva WFA | 100m x 100m pixel destructive potential classification | Unitless
FRC6 | Wildfire Exposure Potential | Wind Load Condition 3, Weather Condition 1, Vegetation Condition 1, Vegetation Condition 3 | Topography | Current: Technosylva WFA Future: DIREXYON and Technosylva WFA | 100m x 100m pixel destructive potential classification | Unitless
FRC7 | Wildfire Vulnerability | Wind Load Condition 3, Weather Condition 1, Vegetation Condition 1, Vegetation Condition 3 | Customer demographics and AFN population | Current: Technosylva WFA and Technosylva RAVE Future: DIREXYON, Technosylva WFA, and Technosylva RAVE | AFN population per circuit | Customers per circuit
FRC8 | PSPS Exposure Likelihood | Wind Load Condition 3, Weather Condition 1, Vegetation Condition 1, Vegetation Condition 3 | Customer demographics, AFN population, and building locations | Current: Technosylva RAVE Future: DIREXYON, Technosylva WFA, and Technosylva RAVE | AFN customers and buildings impacted per circuit level | Customers per circuit Buildings per circuit
FRC9 | Vulnerability of Community to PSPS (PSPS Vulnerability) | Wind Load Condition 3, Weather Condition 1, Vegetation Condition 1, Vegetation Condition 3 | Customer demographics, AFN population, and building locations | Current: Technosylva RAVE Future: DIREXYON, Technosylva WFA, and Technosylva RAVE | AFN customers and buildings impacted per circuit level | Customers per circuit Buildings per circuit
FRC10 | PEDS Outage Exposure Likelihood | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update.
FRC11 | PEDS Outage Vulnerability | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update. | NA - Deferred to a future update.

## Table 5-5
SUPPORT COLUMNS: DO NOT REPORT IN WMP FINAL DELIVERABLE
Risk Ranking | Circuit | Overall Utility Risk Score | Wildfire Risk Score | Outage Program Risk Score | Top Risk Contributors | Total Miles | Version of Risk Model Used | Wildfire Risk Score [Fire Safety Circuit Matrix] | Normalized Wildfire Risk Score [Fire Safety Circuit Matrix] | Wildfire Risk Score [FireSight] | Normalized Wildfire Risk Score [FireSight] | PSPS Risk Score
1 | Boulder | #REF! | #REF! | 0.51 | Overhead Bare Wire Length | 17.4862 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.51
2 | Shay | #REF! | #REF! | 0.88 | None | 17.2997 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.88
3 | Holcomb | #REF! | #REF! | 0.49 | Overhead Bare Wire Length | 13.2573 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.49
4 | Goldmine | #REF! | #REF! | 0.54 | Overhead Bare Wire Length | 13.169 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.54
5 | Clubview | #REF! | #REF! | 0.55 | Overhead Bare Wire Length | 10.1605 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.55
6 | Baldwin | #REF! | #REF! | 0.42 | Overhead Bare Wire Length | 8.2681 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.42
7 | North Shore | #REF! | #REF! | 0.31 | Overhead Bare Wire Length | 15.7376 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.31
8 | Pioneer | #REF! | #REF! | 0.26 | Overhead Bare Wire Length | 16.3837 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.26
9 | Sunrise | #REF! | #REF! | 0.58 | Overhead Bare Wire Length | 7.5783 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.58
10 | Radford | #REF! | #REF! | 0.28 | Overhead Bare Wire Length | 3.1268 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.28
11 | Erwin Lake | #REF! | #REF! | 0.62 | None | 21.9088 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.62
12 | Eagle | #REF! | #REF! | 0.57 | Overhead Bare Wire Length | 6.612 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.57
13 | Sunset | #REF! | #REF! | 0.48 | Overhead Bare Wire Length | 10.306 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.48
14 | Interlacken | #REF! | #REF! | 0.57 | Overhead Bare Wire Length | 5.5165 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.57
15 | Castle Glen | #REF! | #REF! | 0.52 | Overhead Bare Wire Length | 6.8544 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.52
16 | Garstin | #REF! | #REF! | 0.55 | Overhead Bare Wire Length | 5.3368 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.55
17 | Paradise | #REF! | #REF! | 0.47 | Overhead Bare Wire Length | 9.7581 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.47
18 | Country Club | #REF! | #REF! | 0.44 | Overhead Bare Wire Length | 3.1728 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.44
19 | Georgia | #REF! | #REF! | 0.48 | Overhead Bare Wire Length | 4.7543 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.48
20 | Lagonita | #REF! | #REF! | 0.39 | Overhead Bare Wire Length | 6.7483 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.39
21 | Pump House | #REF! | #REF! | 0.48 | Overhead Bare Wire Length | 0.63614 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.48
22 | Harnish | #REF! | #REF! | 0.35 | Overhead Bare Wire Length | 1.5276 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0.35
23 | Lift | #REF! | #REF! | 0 | Overhead Bare Wire Length | 0.011312 | Fire Safety Circuit Matrix | #REF! | #REF! | #REF! | #REF! | 0
weighted average by line
|  | Fox Farm | [5 empty] | Underground
|  | Skyline | [5 empty] | Not used
|  | Geronimo | [5 empty] | Underground

## Table 5-6
Key Risk Assessment Area | Proposed Improvement | Type of Improvement | Expected Value Add | Timeframe and Key Milestones
RA-1, risk assessment methodology | RA-1-A. Complete Integration of Direxyon and Technosylva Models | Programmatic: Training and process improvements on WFA-E use. | To improve data-driven decision making processes. | Pilot system, 2025–2026 Integrate system 2026–2027
RA-1, risk assessment methodology | RA-1-B. Develop verification and validation documentation for ignition models. | Technical: Inclusion of additional assets (i.e., arresters and connectors), refinement of vegetation treatment (i.e., separate asset instead of included in the pole asset), and refinement to the PSPS probability calculations. | Produce reliable quantitatively derived risk components and display them in a manner that is useful to decision makers. | Q4 2025 Implementation
RA-1, risk assessment methodology | RA-1-C. Develop verification and validation documentation for ignition models. | Technical: Inclusion of PEDS risk components. | Produce reliable quantitatively derived risk components and display them in a manner that is useful to decision makers. | Q4 2026 Implementation
RA-2, Design Basis | RA-2-A. Develop wildfire mitigation programs and procedures to support use of integrated models. | Programmatic: Establish data transfer, quality control, and periodicity between BVES, Technosylva, and DIREXYON. | Establish internal quality control standards and guidelines. | Q4 2025 Implementation
RA-3 Risk Presentation | RA-3. Risk Presentation | Technical and Programmatic: Complete the development of overall risk enterprise system and processes for control and use of system. Additionally, conduct staff training on system. | Produce reliable quantitatively derived risk components and display them in a manner that is useful to decision makers. | Q4 2025 Implementation

## Table 6-1
Priority | Circuit | Length (miles) | Overall Utility Risk | Wildfire Risk | Outage Program Risk | Percent of Overall Utility Risk | Associated Risk Drivers
1 | Baldwin | 8.2681 | #REF! | #REF! | 0.42 | #REF! | Conductor failure
2 | Boulder | 17.4862 | #REF! | #REF! | 0.51 | #REF! | Conductor failure
3 | Eagle | 6.612 | #REF! | #REF! | 0.57 | #REF! | Conductor failure
4 | Castle Glen | 6.8544 | #REF! | #REF! | 0.52 | #REF! | Conductor failure
5 | Clubview | 10.1605 | #REF! | #REF! | 0.55 | #REF! | Conductor failure
6 | Erwin Lake | 21.9088 | #REF! | #REF! | 0.62 | #REF! | None
7 | Country Club | 3.1728 | #REF! | #REF! | 0.44 | #REF! | Conductor failure
8 | Interlacken | 5.5165 | #REF! | #REF! | 0.57 | #REF! | Conductor failure
9 | Georgia | 4.7543 | #REF! | #REF! | 0.48 | #REF! | Conductor failure
10 | North Shore | 15.7376 | #REF! | #REF! | 0.31 | #REF! | Conductor failure
11 | Goldmine | 13.169 | #REF! | #REF! | 0.54 | #REF! | Conductor failure
12 | Holcomb | 13.2573 | #REF! | #REF! | 0.49 | #REF! | Conductor failure
13 | Harnish | 1.5276 | #REF! | #REF! | 0.35 | #REF! | Conductor failure
14 | Lagonita | 6.7483 | #REF! | #REF! | 0.39 | #REF! | Conductor failure
15 | Garstin | 5.3368 | #REF! | #REF! | 0.55 | #REF! | Conductor failure
16 | Radford | 3.1268 | #REF! | #REF! | 0.28 | #REF! | Conductor failure
17 | Paradise | 9.7581 | #REF! | #REF! | 0.47 | #REF! | Conductor failure
18 | Pump House | 0.63614 | #REF! | #REF! | 0.48 | #REF! | Conductor failure
19 | Shay | 17.2997 | #REF! | #REF! | 0.88 | #REF! | None
20 | Lift | 0.011312 | #REF! | #REF! | 0 | #REF! | Conductor failure
21 | Pioneer | 16.3837 | #REF! | #REF! | 0.26 | #REF! | Conductor failure
22 | Sunrise | 7.5783 | #REF! | #REF! | 0.58 | #REF! | Conductor failure
23 | Sunset | 10.306 | #REF! | #REF! | 0.48 | #REF! | Conductor failure

## Table 6-2
Stakeholder | Stakeholder Point of Contact | Electrical Corporation Point of Contact | Stakeholder Role | Engagement Methods | Mitigation Initiative Activity | Level of Engagement for Mitigation Initiative Activity
Sheriff’s Department Big Bear Lake Patrol Station | Sherriff | Paul Marconi | • Evacuation Routes – decision maker • PSPS Coordination - informed | • Quarterly public meetings • Phone calls as needed | • Emergency preparedness and recovery plan (EP_1) • External collaboration and coordination (EP_2) • Public communication, outreach, and education (EP_3) | Local
Big Bear Fire Department | Fire Chief | Paul Marconi | • Policy - consulted • Coordinate emergency response - consulted • Wildfire mitigation – decision maker | • Quarterly meetings • Phone calls as needed | • Emergency preparedness and recovery plan (EP_1) • External collaboration and coordination (EP_2) • Public communication, outreach, and education (EP_3) • Wildfire Mitigation Strategy Development (WMSD_1) • Emergency response vegetation management (VM_13) • Post-fire service restoration (VM_14) • Fall-in Mitigation and High-risk Species (VM_8) • Clearance (VM_9) | Local
San Bernadino County | Big Bear Lake Representative for County Supervisor 3rd District | Paul Marconi | • Policy - consulted • Communication - informed | • Bi-annual meetings • Phone calls as needed | • Emergency preparedness and recovery plan (EP_1) • External collaboration and coordination (EP_2) • Public communication, outreach, and education (EP_3) • Wildfire Mitigation Strategy Development (WMSD_1) | Local
Cal Trans | Transportation Engineer | Tom Chou | • Grid hardening coordination - informed • PSPS coordination - informed • Permitting – decision maker | • Quarterly meetings • Phone calls as needed | • Emergency preparedness and recovery plan (EP_1) • External collaboration and coordination (EP_2) • Public communication, outreach, and education (EP_3) | Local
City of Big Bear Lake | City Manager Director of Public Service/City Engineer | Paul Marconi | • Policy – consulted • Permitting – consulted • Communication – consulted | • Quarterly public meetings • Phone calls as needed | • Emergency preparedness and recovery plan (EP_1) • External collaboration and coordination (EP_2) • Public communication, outreach, and education (EP_3) • Wildfire Mitigation Strategy Development (WMSD_1) | Local
Mountaintop San Bernadino US Forrest Service | District Ranger | Paul Marconi | • Grid hardening coordination – consulted • Vegetation management – consulted • Permitting – decision maker | • Phone calls as needed | • Emergency preparedness and recovery plan (EP_1) • External collaboration and coordination (EP_2) • Public communication, outreach, and education (EP_3) • Pole clearing (VM_10) • Wood and slash management (VM_11) • Emergency response vegetation management (VM_13) • Post-fire service restoration (VM_14) • Fall-in Mitigation and High-risk Species (VM_8) • Clearance (VM_9) • Wildfire Mitigation Strategy Development (WMSD_1) | Federal

## Table 6-3
Initiative Activity | Initiative Activity Section # | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness – Outage Program Risk | Cost-Benefit Score – Overall Risk | Cost-Benefit Score – Wildfire Risk | Cost-Benefit Score – Outage Program Risk | % HFRA Covered | Expected % Risk Reduction52 | Model(s) Used to Calculate Risk Impact
ENT_1: Asset management and inspection enterprise system(s) | 12.2 | 4.93% | 3.115% | 6.744% | 0.72054 | 0.64414 | 0.79695 | NA | 4.93% | Risk Register
ENT_2: Vegetation management enterprise system | 12.2 | 4.93% | 3.115% | 6.744% | 0.72054 | 0.64414 | 0.79695 | NA | 4.93% | Risk Register
EP_1: Emergency preparedness and recovery plan | 11.2 | 4.93% | 3.115% | 6.744% | 3.8327 | 3.4263 | 4.2391 | NA | 4.93% | Risk Register
EP_2: External collaboration and coordination | 11.1, 12.1 | 4.93% | 3.115% | 6.744% | 1.0194 | 0.91128 | 1.1275 | NA | 4.93% | Risk Register
EP_3: Public communication, outreach, and education | 11.1, 12.1 | 4.93% | 3.115% | 6.744% | 0.32024 | 0.28628 | 0.3542 | NA | 4.93% | Risk Register
EP_4: Customer support in wildfire and PSPS emergencies | 11.1, 12.1 | 4.93% | 3.115% | 6.744% | 5.1102 | 4.5683 | 5.6521 | NA | 4.93% | Risk Register
GD_1: Covered Conductor Replacement Project (Reconductor) | 8.2.1, 8.4.4, 8.4.9 | 5.843% | 5.536% | 6.151% | 0.22088 | 0.27017 | 0.17158 | 38% | 5.843% | Risk Register
GD_10: Fuse TripSaver Automation | 8.2.8, 8.4.5 | 2.516% | 3.676% | 1.355% | 2.3033 | 3.8052 | 0.80148 | 20% | 2.516% | Risk Register
GD_11: Non-Exempt Surge Arrester Replacement | 8.2.10 | 5.101% | 3.458% | 6.744% | 0.59467 | 0.56244 | 0.6269 | 100% | 5.101% | Risk Register
GD_12: Tree Attachment Removal Project | 8.2.10 | 5.339% | 5.559% | 5.12% | 1.2243 | 1.6042 | 0.84441 | 100% | 5.339% | Risk Register
GD_13: Safety and Technical Upgrades to Lake Substation | 8.2.12 | 5.698% | 4.652% | 6.744% | 0.033487 | 0.036626 | 0.030347 | 100% | 5.698% | Risk Register
GD_14: Partial Safety and Technical Upgrades to Village Substation | 8.2.12 | 5.698% | 4.652% | 6.744% | 0.038431 | 0.042034 | 0.034828 | 100% | 5.698% | Risk Register
GD_15: Equipment maintenance and repair | 8.4.3 | 5.551% | 4.34% | 6.761% | 0.028273 | 0.029914 | 0.026632 | 100% | 5.551% | Risk Register
GD_16: Asset Quality assurance / quality control | 8.5.4 | 5.609% | 4.475% | 6.744% | 1.9136 | 2.0562 | 1.771 | NA | 5.609% | Risk Register
GD_17: Asset Open work orders | 8.6 | 5.085% | 3.427% | 6.744% | 1.6276 | 1.532 | 1.7231 | NA | 5.085% | Risk Register
GD_18: Equipment Settings to Reduce Wildfire Risk | 8.7.1 | 7.626% | 8.507% | 6.744% | 0.71808 | 0.98836 | 0.44779 | 100% | 7.626% | Risk Register
GD_19: Grid Response Procedures and Notifications | 8.7.2 | 4.93% | 3.115% | 6.744% | 3.2024 | 2.8628 | 3.542 | NA | 4.93% | Risk Register
GD_2: Minor Undergrounding Upgrades Projects | 8.2.2 | 4.93% | 3.115% | 6.744% | 0.18893 | 0.1689 | 0.20897 | 100% | 4.93% | Risk Register
GD_20: Personnel Work Procedures and Training in Conditions of Elevated Fire Risk | 8.7.3 | 4.93% | 3.115% | 6.744% | 7.2054 | 6.4414 | 7.9695 | NA | 4.93% | Risk Register
GD_21: Asset Workforce Planning | 8.7.4 | 4.93% | 3.115% | 6.744% | 4.4341 | 3.9639 | 4.9043 | NA | 4.93% | Risk Register
GD_22: Detailed inspections | 8.3.1 | 5.698% | 4.652% | 6.744% | 2.345 | 2.5649 | 2.1252 | 100% | 5.698% | Risk Register
GD_23: Patrol Inspections | 8.3.2 | 5.698% | 4.652% | 6.744% | 1.005 | 1.0992 | 0.9108 | 100% | 5.698% | Risk Register
GD_24: UAV Thermography Inspections | 8.3.3 | 5.698% | 4.652% | 6.744% | 0.22425 | 0.24527 | 0.20323 | 100% | 5.698% | Risk Register
GD_25: UAV HD Photography/Videography Inspections | 8.3.4, 8.4.7 | 5.698% | 4.652% | 6.744% | 0.22425 | 0.24527 | 0.20323 | 100% | 5.698% | Risk Register
GD_26: 3rd Party Ground Patrol Inspections | 8.3.5 | 5.698% | 4.652% | 6.744% | 0.55804 | 0.61035 | 0.50572 | 100% | 5.698% | Risk Register
GD_27: Intrussive Pole Inspections | 8.3.6 | 5.698% | 4.652% | 6.744% | 1.8513 | 2.0249 | 1.6778 | 100% | 5.698% | Risk Register
GD_28: Substation inspections | 8.3.7 | 5.698% | 4.652% | 6.744% | 0.31978 | 0.34976 | 0.2898 | 100% | 5.698% | Risk Register
GD_3: Covered Conductor Replacement Project (Pole Assessment) | 8.2.3, 8.4.6, 8.4.7 | 5.843% | 5.536% | 6.151% | 0.51538 | 0.6304 | 0.40036 | 38% | 5.843% | Risk Register
GD_4: Evacuation Route Hardening Project | 8.2.3, 8.4.6, 8.4.7 | 5.559% | 5.559% | NA | 1.9892 | 1.9892 | NA | 31% | 5.559% | Risk Register
GD_5: Traditional overhead hardening | 8.2.5, 8.4.1, 8.4.2, 8.4.11 | 5.698% | 4.652% | 6.744% | 0.08647 | 0.094576 | 0.078363 | 100% | 5.698% | Risk Register
GD_6: Solar Energy Project | 8.2.7 | 18.05% | NA | 18.05% | 0.010914 | NA | 0.010914 | 100% | 18.05% | Risk Register
GD_7: Energy Storage Project | 8.2.7 | 18.05% | NA | 18.05% | 0.015481 | NA | 0.015481 | 100% | 18.05% | Risk Register
GD_8: Switch and Field Device Automation | 8.2.8, 8.4.8 | 6.126% | 4.412% | 7.84% | 0.63282 | 0.62791 | 0.63772 | 22% | 6.126% | Risk Register
GD_9: Capacitor Bank Upgrade Project | 8.2.8, 8.4.1 | 3.767% | 5.163% | 2.371% | 0.64257 | 1.018 | 0.26716 | 100% | 3.767% | Risk Register
RMA_1: Risk Methodology and Assessment | 5.7 | 6.472% | 3.461% | 9.484% | 0.52036 | 0.40556 | 0.63515 | 100% | 6.472% | Risk Register
SAF_1: Advanced weather monitoring and weather stations | 10.2 | 5.542% | 4.34% | 6.744% | 2.8918 | 3.0633 | 2.7203 | 100% | 5.542% | Risk Register
SAF_2: Install Fault Indicators | 10.3 | 5.085% | 3.427% | 6.744% | 3.6927 | 3.4758 | 3.9095 | 100% | 5.085% | Risk Register
SAF_3: Online Diagnostic System | 10.3 | 5.542% | 4.34% | 6.744% | 2.6657 | 2.8238 | 2.5076 | 100% | 5.542% | Risk Register
SAF_4: Autonomous Monitoring of Power Line Infrastructure | 10.4 | 5.706% | 4.652% | 6.761% | 0.097823 | 0.10687 | 0.088775 | 100% | 5.706% | Risk Register
SAF_5: ALERT Wildfire Cameras | 10.4 | 4.93% | 3.115% | 6.744% | 3.78 | 3.38 | 4.18 | 100% | 4.93% | Risk Register
SAF_6: Weather forecasting | 10.5 | 4.93% | 3.115% | 6.744% | 0.32795 | 0.29317 | 0.36272 | 100% | 4.93% | Risk Register
SAF_7: Fire potential index | 10.6 | 7.068% | 4.652% | 9.484% | 0.78683 | 0.72678 | 0.84687 | 100% | 7.068% | Risk Register
VM_1: Detailed inspections | 9.2.1 | 5.698% | 4.652% | 6.744% | 2.345 | 2.5649 | 2.1252 | 100% | 5.698% | Risk Register
VM_10: Pole clearing | 9.4 | 5.551% | 4.34% | 6.761% | 0.10853 | 0.11483 | 0.10223 | 100% | 5.551% | Risk Register
VM_11: Wood and slash management | 9.5 | 5.706% | 4.652% | 6.761% | 0.012592 | 0.013757 | 0.011427 | 100% | 5.706% | Risk Register
VM_12: Substation defensible space | 9.6 | 4.938% | 3.115% | 6.761% | 1.9241 | 1.7177 | 2.1306 | 100% | 4.938% | Risk Register
VM_13: Emergency response vegetation management | 9.9 | 3.984% | 1.225% | 6.744% | 0.60811 | 0.29332 | 0.92289 | NA | 3.984% | Risk Register
VM_14: Post-fire service restoration | 9.1 | 4.93% | 3.115% | 6.744% | 5.5426 | 4.9549 | 6.1304 | NA | 4.93% | Risk Register
VM_15: Vegetation Management Quality assurance / quality control | 9.11 | 4.93% | 3.115% | 6.744% | 0.45891 | 0.41025 | 0.50757 | NA | 4.93% | Risk Register
VM_16: Vegetation Management Open work orders | 9.12 | 4.93% | 3.115% | 6.744% | 0.68523 | 0.61257 | 0.75789 | NA | 4.93% | Risk Register
VM_17: Vegetation Management Workforce planning | 9.13 | 4.93% | 3.115% | 6.744% | 3.6792 | 3.2891 | 4.0693 | NA | 4.93% | Risk Register
VM_2: Patrol Inspections | 9.2.2 | 5.698% | 4.652% | 6.744% | 1.005 | 1.0992 | 0.9108 | 100% | 5.698% | Risk Register
VM_3: UAV HD Photography/Videography Inspections | 9.2.3 | 5.698% | 4.652% | 6.744% | 0.22425 | 0.24527 | 0.20323 | 100% | 5.698% | Risk Register
VM_4: LiDAR inspections | 9.2.4 | 5.698% | 4.652% | 6.744% | 0.29636 | 0.32415 | 0.26858 | 100% | 5.698% | Risk Register
VM_5: 3rd Party Ground Patrol Inspections | 9.2.5 | 5.698% | 4.652% | 6.744% | 0.55804 | 0.61035 | 0.50572 | 100% | 5.698% | Risk Register
VM_6: Substation inspections | 9.2.6 | 5.698% | 4.652% | 6.744% | 2.6056 | 2.8499 | 2.3613 | 100% | 5.698% | Risk Register
VM_7: Satellite Imaging Inspections | 9.2.7 | 5.698% | 4.652% | 6.744% | 0.87939 | 0.96184 | 0.79695 | 100% | 5.698% | Risk Register
VM_8: Fall-in Mitigation and High-risk Species | 9.3 | 9.192% | 11.62% | 6.761% | 0.13477 | 0.20228 | 0.067252 | 100% | 9.192% | Risk Register
VM_9: Clearance | 9.3 | 9.192% | 11.62% | 6.761% | 0.032631 | 0.048979 | 0.016284 | 100% | 9.192% | Risk Register
WMSD_1: Wildfire Mitigation Strategy Development | 6 | 5.101% | 3.458% | 6.744% | 0.80419 | 0.7606 | 0.84778 | NA | 5.101% | Risk Register

## Table 6-4
Circuit | 2025 Overall Utility Risk | 2026 Initiative Activities | 2026 Overall Utility Risk | 2027 Initiative Activities | 2027 Overall Utility Risk | 2028 Initiatives Activities | 2028 Overall Utility Risk
Boulder | #REF! | GD_1: Covered Conductor Replacement Project (Reconductor) GD_3: Covered Conductor Replacement Project (Pole Assessment) | #REF! | None | #REF! | GD_1: Covered Conductor Replacement Project (Reconductor) GD_3: Covered Conductor Replacement Project (Pole Assessment) | #REF!
Goldmine | #REF! | None | #REF! | None | #REF! | None | #REF!
North Shore | #REF! | None | #REF! | GD_1: Covered Conductor Replacement Project (Reconductor) GD_3: Covered Conductor Replacement Project (Pole Assessment) | #REF! | GD_1: Covered Conductor Replacement Project (Reconductor) GD_3: Covered Conductor Replacement Project (Pole Assessment) | #REF!
Clubview | #REF! | None | #REF! | None | #REF! | GD_1: Covered Conductor Replacement Project (Reconductor) GD_3: Covered Conductor Replacement Project (Pole Assessment) | #REF!
Pioneer | #REF! | None | #REF! | GD_1: Covered Conductor Replacement Project (Reconductor) GD_3: Covered Conductor Replacement Project (Pole Assessment) | #REF! | None | #REF!
Holcomb | #REF! | GD_1: Covered Conductor Replacement Project (Reconductor) GD_3: Covered Conductor Replacement Project (Pole Assessment) | #REF! | None | #REF! | None | #REF!
Sunset | #REF! | None | #REF! | None | #REF! | None | #REF!
Lagonita | #REF! | None | #REF! | None | #REF! | None | #REF!
Sunrise | #REF! | None | #REF! | None | #REF! | None | #REF!
Eagle | #REF! | None | #REF! | None | #REF! | None | #REF!
Castle Glen | #REF! | None | #REF! | None | #REF! | None | #REF!
Paradise | #REF! | None | #REF! | None | #REF! | None | #REF!
Interlacken | #REF! | None | #REF! | None | #REF! | None | #REF!
Harnish | #REF! | None | #REF! | None | #REF! | None | #REF!
Radford | #REF! | None | #REF! | None | #REF! | None | #REF!
Lift | #REF! | None | #REF! | None | #REF! | None | #REF!
Garstin | #REF! | None | #REF! | None | #REF! | None | #REF!
Georgia | #REF! | None | #REF! | None | #REF! | None | #REF!
Country Club | #REF! | None | #REF! | None | #REF! | None | #REF!
Baldwin | #REF! | None | #REF! | None | #REF! | None | #REF!
Pump House | #REF! | None | #REF! | None | #REF! | None | #REF!
Shay | #REF! | None | #REF! | None | #REF! | None | #REF!
Erwin Lake | #REF! | None | #REF! | None | #REF! | None | #REF!

## Table 8-1
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | Target Unit | [2026] Target/Status | % Planned in HFTD for [2026] | % Planned in HFRA for [2026] | % Risk Reduction for [2026] | [2027] Total/Status | % Planned in HFTD for [2027] | % Planned in HFRA for [2027] | % Risk Reduction for [2027] | [2028] Total/Status | % Planned in HFTD for [2028] | % Planned in HFRA for [2028] | % Risk Reduction for [2028] | Three-year total | Section; Page number
Covered conductor installation | Quantitative | Covered Conductor Replacement Project (Reconductor) (GD_1) | GD_1 | Circuit Miles Replaced | 8 | 100% | 100% | 4.43% | 10 | 100% | 100% | 5.54% | 10 | 100% | 100% | 5.54% | 28 | 8.2.1; p. 116
Undergrounding of electric lines and/or equipment | Qualitative | Minor Undergrounding Upgrades Projects (GD_2) | GD_3 | Initiate Underground Projects as needed (% of Assigned Budget) | 100% | 100% | 100% | 3.12% | 100% | 100% | 100% | 3.12% | 100% | 100% | 100% | 3.12% | 100% | 8.2.2; p. 119
Distribution pole replacements and reinforcements | Quantitative | Covered Conductor Replacement Project (Pole Assessment) (GD_3) | GD_4 | # of Poles Replaced or Reinforced | 125 | 100% | 100% | 4.43% | 150 | 100% | 100% | 5.54% | 150 | 100% | 100% | 5.54% | 425 | 8.2.3; p. 120
Distribution pole replacements and reinforcements | Quantitative | Evacuation Route Hardening Project (GD_4) | GD_6 | # of Poles Hardened with Wire Mesh Wrap | 500 | 100% | 100% | 5.56% | 500 | 100% | 100% | 5.56% | 500 | 100% | 100% | 5.56% | 1500 | 8.2.3; p. 120
Traditional overhead hardening | Qualitative | Traditional overhead hardening (GD_5) | GD_8 | % of Assigned Budget | 100% | 100% | 100% | 4.65% | 100% | 100% | 100% | 4.65% | 100% | 100% | 100% | 4.65% | 100% | 8.2.5; p. 124
Microgrids | Qualitative | Bear Valley Solar Energy Project (GD_6) | GD_10 | % of Project Completed | N/A | N/A | N/A | N/A | 100% | 100% | 100% | 18.05% | N/A | N/A | N/A | N/A | 100% | 8.2.7; p. 126
Microgrids | Qualitative | Bear Valley Energy Storage Project (GD_7) | GD_11 | % of Project Completed | N/A | N/A | N/A | N/A | 100% | 100% | 100% | 18.05% | N/A | N/A | N/A | N/A | 100% | 8.2.7; p. 126
Installation of system automation equipment | Quantitative | Switch and Field Device Automation (GD_8) | GD_12 | # of switches connected to SCADA | 10 | 100% | 100% | 4.41% | 10 | 100% | 100% | 4.41% | 10 | 100% | 100% | 4.41% | 30 | 8.2.8; p. 128
Installation of system automation equipment | Quantitative | Capacitor Bank Upgrade Project (GD_9) | GD_14 | # of units replaced | 6 | 100% | 100% | 5.16% | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 6 | 8.2.8; p. 128
Installation of system automation equipment | Quantitative | Fuse TripSaver Automation (GD_10) | GD_15 | # of TripSavers connected to SCADA | 10 | 100% | 100% | 3.68% | 10 | 100% | 100% | 3.68% | 10 | 100% | 100% | 3.68% | 30 | 8.2.8; p. 128
Other grid topology improvements to minimize risk of ignitions | Quantitative | Non-Exempt Surge Arrester Replacement (GD_11) |  | # of Non-exempt surge arresters replaced | 58 | 100% | 100% | 3.46% | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 58 | 8.2.10; p. 133
Other grid topology improvements to minimize risk of ignitions | Quantitative | Tree Attachment Removal Project (GD_12) | GD_19 | # of Tree Attachments Removed | 100 | 100% | 100% | 5.559% | 100 | 100% | 100% | 5.559% | 45 | 100% | 100% | 2.502% | 245 | 8.2.10; p. 133
Other technologies and systems not listed above | Qualitative | Safety and Technical Upgrades to Lake Substation (GD_13) | GD_23 | % of Project Completed | 50% | 100% | 100% | 0 | 50% | 100% | 100% | 4.65% | N/A | N/A | N/A | N/A | 100% | 8.2.12; p. 136
Other technologies and systems not listed above | Qualitative | Partial Safety and Technical Upgrades to Village Substation (GD_14) | GD_24 | % of Project Completed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100% | 100% | 100% | 4.65% | 100% | 8.2.12; p. 136
Equipment maintenance and repair | Qualitative | Equipment maintenance and repair (GD_15) | GD_33 | % of Assigned Budget | 100% | 100% | 100% | 4.34% | 100% | 100% | 100% | 4.34% | 100% | 100% | 100% | 4.34% | 100% | 8.4.1; p. 147
Quality assurance / quality control | Quantitative | Asset Quality assurance / quality control (GD_16) | GD_35 | Number of Asset QCs on WMP Work | 20 | 100% | 100% | 4.48% | 20 | 100% | 100% | 4.48% | 20 | 100% | 100% | 4.48% | 60 | 8.5;p.155
Work orders | Quantitative | Asset Open work orders (GD_17) | GD_36 | 90% or more of work orders compelted on schedule for the year | 90% | 100% | 100% | 3.43% | 90% | 100% | 100% | 3.43% | 90% | 100% | 100% | 3.43% | 90% | 8.6;p.162
Equipment Settings to Reduce Wildfire Risk | Qualitative | Equipment Settings to Reduce Wildfire Risk (GD_18) | GD_37 | % of EPSS Plan Achieved | 100% | 100% | 100% | 8.51% | 100% | 100% | 100% | 8.51% | 100% | 100% | 100% | 8.51% | 100% | 8.7.1; p. 164
Grid Response Procedures and Notifications | Qualitative | Grid Response Procedures and Notifications (GD_19) | GD_38 | Review Grid Procedures and Update Annually | Performed annually | 100% | 100% | 3.12% | Performed annually | 100% | 100% | 3.12% | Performed annually | 100% | 100% | 3.12% | N/A | 8.7.2; p. 169
Personnel Work Procedures and Training in Conditions of Elevated Fire Risk | Qualitative | Personnel Work Procedures and Training in Conditions of Elevated Fire Risk (GD_20) | GD_20 | Conduct Training and Review Procdures for Elevated Fire Risk Conditions | Performed annually | 100% | 100% | 3.12% | Performed annually | 100% | 100% | 3.12% | Performed annually | 100% | 100% | 3.12% | N/A | 8.7.3; p. 171
Workforce Planning | Qualitative | Asset Workforce Planning (GD_21) | GD_21 | Evaluate annually workforce training and adequacy | Performed annually | 100% | 100% | 4.65% | Performed annually | 100% | 100% | 4.65% | Performed annually | 100% | 100% | 4.65% | N/A | 8.8; p. 172
Asset Inspection | Quantitative | Detail Inspection (GD_22) | GD_22 | Circuit Miles Inspected | 55 | 100% | 100% | 4.65% | 55 | 100% | 100% | 4.65% | 55 | 100% | 100% | 4.65% | 165 | 8.3.1; p. 141
Asset Inspection | Quantitative | Patrol Inspections (GD_23) | GD_23 | Circuit Miles Inspected | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 615 | 8.3.2; p. 142
Asset Inspection | Quantitative | UAV Thermography Inspections (GD_24) | GD_24 | Circuit Miles Inspected | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 615 | 8.3.3; p. 143
Asset Inspection |  | UAV HD Photography/Videography Inspections (GD_25) | GD_25 | Circuit Miles Inspected | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 615 | 8.3.4; p. 143
Asset Inspection | Quantitative | Third-Party Ground Patrol Inspections (GD_26 | GD_26 | Circuit Miles Inspected | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 205 | 100% | 100% | 4.65% | 615 | 8.3.5; p. 145
Asset Inspection | Quantitative | Intrusive Pole Inspections (GD_27) | GD_27 | # of Poles Tested | 850 | 100% | 100% | 4.65% | 850 | 100% | 100% | 4.65% | 850 | 100% | 100% | 4.65% | 2550 | 8.3.6; p. 146
Asset Inspection | Quantitative | Substation inspections (GD_28) | GD_28 | # of Substations Inspected | 144 | 100% | 100% | 4.65% | 144 | 100% | 100% | 4.65% | 144 | 100% | 100% | 4.65% | 432 | 8.3.7; p. 147
Transmission pole/tower replacements and reinforcements | N/A | BVES currently does not have any projects under this initiative | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8.2.4; p. 124
Emerging grid hardening technology installations and pilots | N/A | BVES currently does not have any projects under this initiative | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8.2.6; p. 126
Line removals (in HFTD) | N/A | BVES currently does not have any projects under this initiative | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8.2.9; p. 133
Other grid topology improvements to mitigate or reduce PSPS events | N/A | BVES currently does not have any projects under this initiative | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8.2.11; p. 135

## Table 8-2
Type | Inspection Activity (Program) | Frequency or Trigger (Note 1) | Method of Inspection (Note 2) | Governing Standards & Operating Procedures | Cumulative Quarterly Target Year 1, Q1 | Cumulative Quarterly Target Year 1, Q2 | Cumulative Quarterly Target Year 1, Q3 | Cumulative Quarterly Target Year 1, Q4 | Cumulative Quarterly Target Year 2, Q1 | Cumulative Quarterly Target Year 2, Q2 | Cumulative Quarterly Target Year 2, Q3 | Cumulative Quarterly Target Year 2, Q4 | Cumulative Quarterly Target Year 3, Q1 | Cumulative Quarterly Target Year 3, Q2 | Cumulative Quarterly Target Year 3, Q3 | Cumulative Quarterly Target Year 3, Q4 | % of HFRA and HFTD Covered Annually by Inspectio n Type | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Transmission | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Distribution | Detailed | 5 years Cycle | Ground Inspections | GO 165 & GO 95 (Rule18) | 10 | 25 | 40 | 55 | 10 | 25 | 40 | 55 | 10 | 25 | 40 | 55 | 20 | 1% (Asset) | 5% (Asset) | 15% (Asset)
Distribution | Patrol | Annual | Ground Inspections | GO 165 & GO 95 (Rule18) | 52 | 102 | 153 | 205 | 52 | 102 | 153 | 205 | 52 | 102 | 153 | 205 | 100 | 1% (Asset) | 5% (Asset) | 10% (Asset)
Distribution | UAV Thermography Inspection | Annual | Drone Inspection | GO 165 & GO 95 (Rule18) | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 100 | 1% (Asset) | 5% (Asset) | 15% (Asset)
Distribution | UAV HD Photography/Videography | Annual | Drone Inspection | GO 165 & GO 95 (Rule18) | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 100 | 1% (Asset) | 10% (Asset) | 15% (Asset)
Distribution | Third-Party Ground Patrol | Annual | Ground Inspections | GO 165 & GO 95 (Rule18) | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 100 | 1% (Asset) | 10% (Asset) | 20% (Asset)
Distribution | Intrusive Inspection | Per GO 165 | Ground Inspections | GO 165 & GO 95 (Rule18) | 0 | 0 | 850 | 850 | 0 | 0 | 850 | 850 | 0 | 0 | 850 | 850 | 10 | 1% (Asset) | 15% (Asset) | 10% (Asset)
Substation | Substation Inspection | Monthly | Ground Inspections | GO 174 | 36 | 72 | 108 | 144 | 36 | 72 | 108 | 144 | 36 | 72 | 108 | 144 | 100 | 1% (Asset) | 5% (Asset) | 15% (Asset)

## Table 8-3
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Covered Conductor Replacement Project | GD_1 & GD_3 | QC | Ensure that new construction meets BVES standards.
Tree Attachment Removal Project | GD_12 | QC | Ensure that the tree attachment was removed and the new construction meets BVES standards.
Grid Design | GD_16 | QA | Ensure that the correct material was used and that constructions meets BVES standards.
UAV Thermography | GD_24 | QA/QC | Ensure that the inspection findings are correct.
UAV HD Photography | GD_25 | QA/QC | Ensure that the inspection findings are correct.
Third-Party Ground Patrol | GD_26 | QC | Ensure that the inspection findings are correct.
Substation Inspection | GD_28 | QA | Ensure that the inspections are being completed to BVES standards.
Detailed Inspection | GD_22 | QA | To ensure that the field inspector is following BVES procedures for detailed inspections.
Patrol Inspection | GD_23 | QA | To ensure that the field inspector is following BVES procedures for patrol inspections.

## Table 8-4
Initiative/ Activity Being Audited | Type of Audit | Population /Sample Unit | 2026: Population Size | 2026: Sample Size | 2027: Population Size | 2027: Sample Size | 2028: Population Size | 2028: Sample Size | Percent of Sample in the HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Covered Conductor Installation | Field | Circuit Miles | 8 | 8 | 10 | 10 | 10 | 10 | 100% | N/A | 90% | 90% | 90%
Tree Attachment Removal Project | Field | Asset Inspection | 100 | 100 | 100 | 100 | 45 | 45 | 100% | N/A | 90% | 90% | 90%
Grid Design | Desktop | Circuit Miles | 8 | 8 | 10 | 10 | 10 | 10 | 100% | N/A | 90% | 90% | 90%
UAV Thermography | Desktop/Field | Circuit Mile | 205 | 205 | 205 | 205 | 205 | 205 | 100% | N/A | 90% | 90% | 90%
UAV HD Photography | Desktop/Field | Asset Inspection | 205 | 205 | 205 | 205 | 205 | 205 | 100% | N/A | 90% | 90% | 90%
Third-Party Ground Patrol | Field | Asset Inspection | 205 | 205 | 205 | 205 | 205 | 205 | 100% | N/A | 90% | 90% | 90%
Substation Inspection | Field | Asset Inspection | 156 | 156 | 156 | 156 | 156 | 156 | 100% | N/A | 90% | 90% | 90%
Detailed Inspection | Desktop/Field | # of Field Inspector | 1 | 1 | 1 | 1 | 1 | 1 | 100% | N/A | 90% | 90% | 90%
Patrol Inspection | Desktop/Field | # of Field Inspector | 1 | 1 | 1 | 1 | 1 | 1 | 100% | N/A | 90% | 90% | 90%

## Table 8-5
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 0 | 0 | 0 | 0
HFTD Tier 2 | 0 | 0 | 0 | 0
HFTD Tier 3 | 0 | 0 | 0 | 0

## Table 8-6
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 0 | 0 | 0 | 0
Priority 3 | 0 | 0 | 0 | 0

## Table 8-7
Circuit/Circuit Segment ID | Circuit/Circuit Segment Name | Circuit/Circuit Segment Length (overhead circuit miles) | Number of Outages in Past Three Years | Cumulative Outage Duration (minutes) | Cumulative Number of Customers Impacted by Outages
Baldwin | Baldwin | 8.94 | 8 | 424 | 116359
Shay | Shay | 17.17 | 3 | 150 | 31599
Interlaken | Interlaken | 6.45 | 4 | 329 | 9325
Clubview | Clubview | 10.18 | 2 | 478 | 8895
Erwin Lake | Erwin Lake | 21.83 | 4 | 333 | 8618
Goldmine | Goldmine | 13.2 | 3 | 368 | 7371
North Shore | North Shore | 15.83 | 3 | 262 | 5920
Sunset | Sunset | 10.67 | 1 | 341 | 5514
Boulder | Boulder | 17.23 | 6 | 356 | 5025
Radford | Radford | 3 | 2 | 50 | 3437

## Table 9-1
Initiative | Quantitative or Qualitative | Activity (Tracking ID) | Previous Tracking ID, if applicable | Target Unit | 2026 Target/Status | % Risk Reduction for 2026 | 2027 Target/Status | % Risk Reduction for 2027 | 2028 Target/Status | % Risk Reduction for 2028 | Three-Year Total | Section; Page Number
Pruning and Removal | Quantitative | Fall-in mitigation and high-risk species (VM_ 8) | VM_10 & VM_12 | # of trees remediated or removed to prevent fall-in | 88 | 11.62% | 88 | 11.62% | 88 | 11.62% | 216 | 9.3; p.201
Pruning and Removal | Quantitative | Clearance (VM_9) | VM_9 | Circuit Miles Cleared | 72 | 11.62% | 72 | 11.62% | 72 | 11.62% | 216 | 9.3; p.201
Pole clearing | Quantitative | Pole clearing (VM_ 10) | VM_7 | # of Poles Cleared | 70 | 4.34% | 70 | 4.34% | 70 | 4.34% | 210 | 9.4; p.206
Wood and slash management | Qualitative | Wood and slash management (VM_11) | VM_8 | Wood & slash removed per VM Contract | N/A | 4.652% | N/A | 4.65% | N/A | 4.65% | N/A | 9.5; p.207
Defensible space | Quantitative | Defensible space (VM_12) | VM_11 | # of Substations Cleared | 13 | 3.115% | 13 | 3.12% | 13 | 3.12% | 39 | 9.6; p.208
Activities based on weather conditions | Qualitative | Activities based on weather conditions (VM_13) | VM_14 | Review Vegetation Management Emergency Response Procedures Annually | N/A | 1.225% | N/A | 1.22% | N/A | 1.22% | N/A | 9.9; p.211
Post-fire service restoration | Qualitative | Post-fire service restoration (VM_14) | N/A | Review Post-fire service restoration procedures annually | N/A | 3.115% | N/A | 3.12% | N/A | 3.12% | N/A | 9.10; p.213
Quality assurance / quality control | Quantitative | Quality assurance/ quality control (VM_15) | VM_16 | # of VM QCs Performed | 72 | 3.115% | 72 | 3.12% | 72 | 3.12% | 216 | 9.11; p.213
Work orders | Qualitative | Work orders (VM_16) | VM_17 | 90% or more of work orders completed on schedule for the year | N/A | 3.115% | N/A | 3.12% | N/A | 3.12% | N/A | 9.12; p.221
Workforce Planning | Qualitative | Workforce planning (VM_17) | VM_18 | Evaluate annually workforce training and adequacy | N/A | 3.115% | N/A | 3.12% | N/A | 3.12% | N/A | 9.13; p.223
Integrated vegetation management | BVES does not have any programs under this initiative | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 9.13; p.223

## Table 9-2
Activity (Program) | Tracking ID | Previous Tracking ID, if applicable | Target Unit | Cumulativ e (Cml.) Quarterly Target Year 1, Q1 | Cml. Quarterly Target Year 1, Q2 | Cml. Quarterly Target Year 1, Q3 | Cml. Quarterly Target Year 1, Q4 | Cml. Quarterly Target Year 2, Q1 | Cml. Quarterly Target Year 2, Q2 | Cml. Quarterly Target Year 2, Q3 | Cml. Quarterly Target Year 2, Q4 | Cml. Quarterly Target Year 3, Q1 | Cml. Quarterly Target Year 3, Q2 | Cml. Quarterly Target Year 3, Q3 | Cml. Quarterly Target Year 3, Q4 | % HFTD Covered in 2026 | 2026 Total | % Risk Reduction for 2026 | % Risk Reduction for 2027 | % Risk Reduction for 2028 | Three-Year Total | Activity Timeline Target | Section; Page Number
Detailed Inspections | VM_1 | VM_1 | Circuit Miles Inspected | 10 | 25 | 40 | 55 | 10 | 25 | 40 | 55 | 10 | 25 | 40 | 55 | 26% | 55 | 4.652% | 4.652% | 4.652% | 165 | 7 days | 9.2.1; p.184
Patrol inspection | VM_2 | VM_2 | Circuit Miles Inspected | 52 | 102 | 153 | 205 | 52 | 102 | 153 | 205 | 52 | 102 | 153 | 205 | 100% | 205 | 4.652% | 4.652% | 4.652% | 615 | 7 day | 9.2.1; p.184
UAV HD Photography.Videography | VM_3 | VM_3 | Circuit Miles Inspected | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 100% | 205 | 4.652% | 4.652% | 4.652% | 615 | 30 day | 9.2.1; p.184
LiDAR Inspection | VM_4 | VM_4 | Circuit Miles Inspected | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 100% | 205 | 4.652% | 4.652% | 4.652% | 615 | 30 day | 9.2.1; p.184
Third-Party Ground Patrol | VM_5 | VM_5 | Circuit Miles Inspected | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 0 | 0 | 205 | 205 | 100% | 205 | 4.652% | 4.652% | 4.652% | 615 | 30 day | 9.2.1; p.184
Substation Inspection | VM_6 | VM_6 | # of Substations Inspected | 36 | 72 | 108 | 144 | 36 | 72 | 108 | 144 | 36 | 72 | 108 | 144 | 100% | 144 | 4.652% | 4.652% | 4.652% | 432 | 30 day | 9.2.1; p.184
Satellite imagining inspection | VM_7 | VM_19 | Inspection of Entire Service Area | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 100% | 1 | 4.652% | 4.652% | 4.652% | 3 | 30 day | 8

## Table 9-3
Type | Inspection Activity (Program) | Area Inspected | Frequency
Distribution | Detailed Inspection | Entire Service Area | Five-year cycle of entire service area. Higher risk circuits every 3 years.
Distribution | Patrol inspection | Entire Service Area | Annual survey of entire service area
Distribution | UAV HD Photography / Videography | Entire Service Area | Annual survey of entire service area
Distribution | LiDAR Inspection | Entire Service Area | Annual survey of entire service area
Distribution | Third-Party Ground Patrol | Entire Service Area | Annual survey of entire service area
Distribution | Substation Inspection | Entire Service Area | Monthly inspections of all in-service substations
Distribution | Satellite imagining inspection | Entire Service Area | Annual survey of entire service area

## Table 9-4
Partnering Agency/ Organization | Activities | Objectives | Electrical Corporation Role | Anticipated Accomplishments
No Current Partnerships Exist | N/A | N/A | N/A | N/A

## Table 9-5
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Detailed Inspection | VM_1 | QA | To ensure that the field inspector is following BVES procedures for detailed inspections.
Patrol Inspection | VM_2 | QA | To ensure that the field inspector is following BVES procedures for patrol inspections.
UAV HD Photography | VM_3 | QC | To ensure contractor inspectors are identifying and flagging possible defect on assets.
LiDAR Inspection | VM_4 | QC | To ensure that all possible encroachments are properly identified.
Third-Party Ground Patrol | VM_5 | QC | To ensure contractor inspectors are identifying and flagging possible defect on assets.
Substation Inspection | VM_6 | QA | To ensure that inspectors are conducting all inspection up to BVES standards.
Satellite Imaging | VM_7 | QC | To ensure that all possible encroachments are properly identified.
Fall-in Mitigation and High Risk Species | VM_8 | QC | To ensure that contractors completed trimming around assets to BVES standards.
Clearance | VM_9 | QC | To ensure that contractors completed trimming around assets to BVES standards.
Substation Defensible Space | VM_12 | QC | To ensure that contractors completed defensible space work around substations to BVES standards.

## Table 9-6
Initiative/ Activity Being Audited | Population /Sample Unit | 2026: Population Size | 2026: Sample Size | 2026: % of Sample in HFTD | 2027: Population Size | 2027: Sample Size | 2027: % of Sample in HFTD | 2028: Population Size | [Year 3}: Sample Size | 2028: % of Sample in HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Detailed Inspection | # of Field Inspector | 1 | 1 | N/A | 1 | 1 | N/A | 1 | 1 | N/A | N/A | 90% | 90% | 90%
Patrol Inspection | # of Field Inspector | 1 | 1 | N/A | 1 | 1 | N/A | 1 | 1 | N/A | N/A | 90% | 90% | 90%
UAV HD Photography | Circuit Mile | 205 | 205 | 100% | 205 | 205 | 100% | 205 | 205 | 100% | N/A | 90% | 90% | 90%
LiDAR Inspection | Circuit Mile | 205 | 205 | 100% | 205 | 205 | 100% | 205 | 205 | 100% | N/A | 90% | 90% | 90%
Third-Party Ground Patrol | Circuit Mile | 205 | 205 | 100% | 205 | 205 | 100% | 205 | 205 | 100% | N/A | 90% | 90% | 90%
Substation Inspection | Substations Inspections | 156 | 156 | 100% | 156 | 156 | 100% | 156 | 156 | 100% | N/A | 90% | 90% | 90%
Satellite Imaging | Circuit Mile | 205 | 205 | 100% | 205 | 205 | 100% | 205 | 205 | 100% | N/A | 90% | 90% | 90%
Fall-in Mitigation and High-Risk Species | Circuit Mile | 72 | 72 | 100% | 72 | 72 | 100% | 72 | 72 | 100% | N/A | 90% | 90% | 90%
Clearance | Circuit Mile | 72 | 72 | 100% | 72 | 72 | 100% | 72 | 72 | 100% | N/A | 90% | 90% | 90%
Substation Defensible Space | Substations Defensible Space Work | 13 | 13 | 100% | 13 | 13 | 100% | 13 | 13 | 100% | N/A | 90% | 90% | 90%

## Table 9-7
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 0 | 0 | 0 | 0
HFTD Tier 2 | 44 | 0 | 0 | 0
HFTD Tier 3 | 0 | 0 | 0 | 0

## Table 9-8
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 44 | 0 | 0 | 0
Priority 3 | 0 | 0 | 0 | 0

## Table 9-9
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | # of Electrical Corporation Employees with Min Quals | # of Electrical Corporation Employees with Special Certifications | # of Contracted Employees with Min Quals | # of Contractor Employees with Applicable Certifications | Total # of Employees | Reference to Electrical Corporation Training / Qualification Programs
Forester | One year of arboriculture experience or degree in relevant field | ISA Certified Arborist | 0 | ISA Certified Arborist Utility Specialist-1 | 1 | 1 | 1 | N/A
Tree Trim General Foreman/Supervisor (Contractor) | 5 years of line clearance tree pruning experience in a Foreman role Line clearance Certification Current California Driver License General Computer knowledge | Line‐clearance qualified tree‐trimmer | 0 | N/A | 3 | 0 | 3 | N/A
Tree Trim Groundsman | One year of arboriculture experience or degree in relevant field | Strong work ethic Current California Driver License (Class B permit) General computer skills | 0 | N/A | 6 | 0 | 6 | N/A
Geospatial Lead Analyst | 8 years of GIS and Remote Sensing Experience Strong Quality Control and Detail Advanced Knowledge of LiDAR Sensors and Data Advanced GIS Skills and Problem Solving | ASPRS Certified Remote Sensing Technologist | 0 | N/A | 1 | 0 | 1 | N/A
Geospatial Technician | Solid Understand of GIS and Remote Sensing Science Strong Attention to Detail Strong Computer Skills Work Independently | N/A | 0 | N/A | 1 | 0 | 1 | N/A
Utility Systems Specialist Inspector/Lead Inspector | Overhead Distribution and/or Transmission distribution inspection experience (2-year min) Identification of all overhead equipment Current Driver License Computer and GIS mapping experience | NESC and ANSI Inspection experience (1-year min) Red Cross FA/CPR certified Wildfire Training Registered | 0 | N/A | 2 | 0 | 2 | N/A
Field Inspector | Three years of Journeyman Lineman or above experience. Experience inspecting overhead and underground facilities. Class C California Driver’s License | IBEW Journeyman Lineman Registered | 1 | N/A | 0 | 0 | 1 | N/A
Utility Engineer & Wildfire Mitigation Supervisor | Bachelor’s Degree in an engineering field or a technical discipline required. Eight years of planning, construction, or engineering experience including four years of administrative and supervisory experience. Utility experience preferred. Work experience in an area with strong compliance regimes. Experience interacting with utility regulators and knowledge of regulatory processes preferred | Professional Engineer license in California required. If not held, must obtain within 2 years of employment | 1 | N/A | 0 | 0 | 1 | N/A
Wildfire Mitigation and Reliability Engineer | Bachelor of Science degree in Engineering, Mathematics, Physics, or other related technical discipline. Prior electric utility experience preferred. Understanding of statistical analysis and probabilistic methods preferred. | N/A | 1 | N/A | 0 | 0 | 1 | N/A

## Table 10-1
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID, if applicable | Target Unit | 2026 End of Year Total / Completion Date | % Risk Reduction for 2026 | 2027 Total / Status | % Risk Reduction for 2027 | 2028 Total / Status | % Risk Reduction for 2028 | Three- Year Total | Section; Page number
Environmental monitoring systems | Quantitative | Advanced weather monitoring and weather stations (SAF_1) | SAF_1 | Number of Weather Stations Serviced | 20 | 4.34% | 20 | 4.34% | 20 | 4.34% | 60 | 10.2; p.229
Environmental monitoring systems | Qualitative | Integrate Environmental Monitoring Network as a standard feed into the Distribution Management Center. Advanced weather monitoring and weather stations (SAF_1) | SAF_1 | N/A | In progress; October 2026 | N/A | Completed; October 2027 | N/A | Completed; October 2027 | N/A | N/A | 10.2; p.229
Grid monitoring systems | Quantitative | Fault Indicator Serviced (SAF_2) | SAF_2 | % of Installed FI's Serviced | 100% | 3.43% | 100% | 3.43% | 100% | 3.43% | 3 | 10.3; p.231
Grid monitoring systems | Qualitative | Integrate FIs as a standard feed into the Distribution Management Center. Fault Indicators (SAF_2) | SAF_2 | N/A | In progress; October 2026 | N/A | In progress; October 2027 | N/A | Completed; October 2028 | N/A | N/A | 10.3; p.231
Grid monitoring systems | Quantitative | Online Diagnostic System (SAF_3) | SAF_3 | Number of circuits installed on per year. | 1 | 4.34% | N/A | N/A | N/A | N/A | 1 | 10.3; p.231
Grid monitoring systems | Qualitative | Conduct annual review and evaluation of Online Diagnostic system database of system detections. Online Diagnostic System (SAF_3) | SAF_3 | N/A | Annual review and evaluation completed; December 2026 | N/A | Annual review and evaluation completed; December 2027 | N/A | Annual review and evaluation completed; December 2028 | N/A | N/A | 10.3; p.231
Ignition detection systems | Quantitative | Autonomous Monitoring of Power Line Infrastructure (SAF_4) | SAF_4 | % of Installed Sensors Serviced | 100% | 4.65% | 100% | 4.65% | 100% | 4.65% | 3 | 10.4; p.235
Ignition detection systems | Qualitative | Integrate issue as a standard feed into the Distribution Management Center. Autonomous Monitoring of Power Line Infrastructure (SAF_4) | SAF_4 | N/A | In progress; October 2026 | N/A | Completed; October 2027 | N/A | Completed; October 2027 | N/A | N/A | 10.4; p.235
Ignition detection systems | Quantitative | ALERTWildfire Cameras (SAF_5) | SAF_5 | Number of ALERTWildfire Cameras Evaluated by BVES in Operability and Coverage Review | 15 | 3.12% | 15 | 3.12% | 15 | 3.12% | 45 | 10.4; p.235
Ignition detection systems | Qualitative | Provide assistance as requested by ALERT Wildfire Consortium to maintain, upgrade, and/or expand ALERT Wildfire Cameras covering BVES Service Area. ALERTWildfire Cameras (SAF_5) | SAF_5 | N/A | In progress; October 2026 | N/A | In progress; October 2027 | N/A | Completed; October 2028 | N/A | N/A | 10.4; p.235
Weather forecasting | Quantitative | Weather forecasting (SAF_6) | SAF_6 | Percent Time Each Year Weather Stations are Operational | 85% | 4.34% | 85% | 4.34% | 85% | 4.34% | 85% | 10.5; p.241
Weather forecasting | Qualitative | Maintain WFA-E Capability and Weather Consultant Coverage for Each Year. Weather forecasting (SAF_6) | SAF_6 | N/A | Completed annual review of WFA-E Capability and Weather Consultant Coverage; December 2026 | N/A | Completed annual review of WFA-E Capability and Weather Consultant Coverage; December 2026 | N/A | Completed annual review of WFA-E Capability and Weather Consultant Coverage; December 2026 | N/A | N/A | 10.5; p.241
Fire potential index | Quantitative | Fire potential index (SAF_7) | SAF_7 | FPI Model Domain Size in Mi^2 | 3168 | 4.65% | 3168 | 4.65% | 3168 | 4.65% | 9504 | 10.6; p.244
Fire potential index | Qualitative | Integrate FPI as a standard feed into the Distribution Management Center. Fire potential index (SAF_7) | SAF_7 | N/A | In progress; October 2026 | N/A | Completed; October 2027 | N/A | Completed; October 2027 | N/A | N/A | 10.6; p.244

## Table 10-2
System | Measurement/ Observation | Frequency | Purpose and Integration
Weather stations | Air Temperature Wind Velocity & Direction (Steady & Gust) Relative Humidity Barometric Pressure Precipitation | 60 observations/hour | Improved weather monitoring and forecasting Model Validation SCADA Connected

## Table 10-3
System | Measurement/ Observation | Frequency | Purpose and Integration
Fault Indicators Serviced | Indication of fault on an electrical line or circuit | Real-Time | Allow for BVES to reduce risk of ignition or spark by reducing time to locate and isolate fault. BVES has installed 162 on the system and 60 are connected to SCADA.
EGM Meta-Alert System | Fault Monitoring due fire, grounding, or third-party impact Electrical current, voltage Waveform, harmonics | Real-Time | Real-time monitoring of Baldwin, North Shore, Boulder Circuits

## Table 10-4
Detection System | Capabilities | Companion Technologies | Contribution to Fire Detection and Confirmation
HD Cameras (ALERTWildfire HD Cameras) | Continuous Monitoring During Hazardous Conditions 15 cameras in 7 Key Locations Across BVES service Territory | Technosylva – Fire Growth Potential Software | Visual Awareness in areas adjacent to electrical assets. Immediate fire alert
Fire Spread Modeling | BVES is utilizing Technosylva’s FireCast and FireSim Applications to predict fire spread and consequence outputs such as fire perimeter size, structures impacted, and populations affected | N/A | Capability to forecast consequences that wildfire will have on a particular area
GreenGrid iSIU System | Physical Asset Condition, and Ignition Monitoring | N/A | Real-time monitoring of Radford, Boulder and North Shore circuits

## Table 10-5
Feature Group | Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
Fuels | Fuel Complexity | Surface | Fuel model complex is a measure of the fuel model loads and age present in the territory. | LANDFIRE enhanced with Technosylva proprietary fuels data | quarterly | 30 m | N/A
Fuels | Live Fuel Moisture Content | Surface | Live Fuel Moisture Content - Herbaceous and Woody | Proprietary machine learning dataset created by Technosylva | annually | 2 km | Daily
Terrain | Terrain Difficulty | Surface | Index to quantify difficulty in fire suppression efforts based on Accessibility, Penetrability, and Fireline Opening indexes | Technosylva proprietary index. | annually | 30 m | N/A
Weather | Dead Fuel Moisture Content | Surface | Dead Fuel Moisture Content | WRF with Nelson Dead Fuel Moisture Model | daily | 2 km | 1 hr
Weather | Wind Speed | 10 m | Hourly snapshot of the wind at 10 meters above ground level across the territory | WRF | daily | 2 km | 1 hr
Weather | Wind Gust | 10 m | Sudden increase in wind speed. Technosyvla estimates wind gust magnitudes through a machine learning-based parameterization scheme. | WRF with Technosylva proprietary algorithm | daily | 2 km | 1 hr
Hotspots | Fire Activity | Surface | Satellite detected hotspot data from 2012 to 2022 was used to train ML algorithms to be used in real-time estimation of FPI. | VIIRS with Technosylva proprietary algorithm | On model update | hexel level 8 (0.78 mi) | 3 hr

## Table 11-1
Initiative | Activity (Tracking ID #) | Previous Tracking ID, if applicable | 2026 End of Year Total/Completion Date | 2027 Status | 2028 Status | Section; Page number
Emergency preparedness and recovery plan | Review and Update as needed PSPS and EDRP each year (Tracking ID: EP_1) | EP_1 | 100% Completed by December 31, 2026 | 100% Completed by December 31, 2027 | 100% Completed by December 31, 2028 | 11.2; p. 250
External collaboration and coordination | Conduct Stakeholder Briefs quarterly and Annual Tabletop Exercise (Tracking ID: EP_2) | EP_2 | Annual Table Top Exercise completed by June 30, 2026 Stakeholder Briefs completed by August 31, 2026 | Annual Table Top Exercise completed by June 30, 2027 Stakeholder Briefs completed by August 31, 2027 | Annual Table Top Exercise completed by June 30, 2028 Stakeholder Briefs completed by August 31, 2028 | 11.3; p. 262
Public communication, outreach, and education | Achieve satisfactory outreach evaluation on semi-annual PSPS and wildfire customer survey. (Satisfactory is >60% overall.)(Tracking ID: EP_3) | EP_3 | 100% Completed by December 31, 2026 | 100% Completed by December 31, 2027 | 100% Completed by December 31, 2028 | 11.4; p. 268
Customer support in wildfire and PSPS emergencies | Review procedures for Customer support in wildfire and PSPS emergencies annually (Tracking ID: EP_4) | EP_5 | 100% Completed by December 31, 2026 | 100% Completed by December 31, 2027 | 100% Completed by December 31, 2028 | 11.5; p. 285

## Table 11-2
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Bear Valley has never invoked a PSPS so its direct experience is non-existent. | Continue to work with other IOUs to gain knowledge and best practices from their direct experiences. | Strategy: Participate in AFN Council and Joint IOU WMP sessions. Also, review other IOU PSPS reports and attend workshops on PSPS when offered. Target timeline: This is ongoing and Bear Valley should target all of these activities each year.
Limited coordination with Local Government and Agencies | Work with Local Government and Agencies to gain their input to Bear Valley's EDRP and PSPS. | Strategy: Conduct a workshop for EDRP and PSPS with Local Government and Agencies and provide an opportunity for them to edit the EDRP and PSPS. Provide final copies of these documents to Local Government and Agencies. Target timeline: Conduct coordination strategy for PSPS in 2026 and conduct coordination strategy for EDRP in 2027.

## Table 11-3
Public Safety Partner Group | Name of Entity | Key Protocols | Frequency of Prearranged Communication Review and Update
Fire | Local County Fire Department | • Communication capabilities (staffing, resources, technologies) • Methods for information exchange • Backup systems & data management strategy • Common alerting protocols & messaging • Predefined emergency contacts (See BVES Emergency Plan) | Annually (around April – May)
Law Enforcement | County Sheriff’s Office | • Real-time emergency alerts & PSPS activation notifications • Coordination on public safety response • Information sharing through secured channels (See Section X, Emergency Plan) | Annually (around April – May)
Office of Emergency Services | County & State OES Agencies | • Multi-agency coordination & data-sharing • Situational reports on wildfire threats & grid stability • PSPS debrief meetings (See Section Y, Emergency Plan) | Quarterly
Regulatory & Government | CPUC & Energy Safety | • PSPS notifications & compliance reporting • Emergency operations monitoring • Performance evaluation of emergency communication protocols (See Section Z, Emergency Plan) | As needed
Interconnected Electrical Corporations | Neighboring Utility Companies | • Mutual aid coordination • Load balancing & resource-sharing agreements • PSPS grid impact assessments (See Section A, Emergency Plan) | Annually and during potential events

## Table 11-4
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Limited feedback on wildfire & PSPS emergency plan | Less than 10% of state & local government stakeholders have participated in emergency plan review. | Strategy: Host a 0.5-day workshop with state & local agencies to review emergency preparedness strategies. Solicit verbal & written comments from stakeholders. Assign liaison for follow-up engagement. Target Timeline: By end of 2026
Inconsistent notification receipt across agencies | More than 50% of government partners have independent & non-standardized communication systems. | Strategy: Develop a multi-channel alert system that includes text, email, & secondary confirmation methods. Conduct a survey of public safety partners to align notification preferences with BVES’s capabilities. Target Timeline: By end of 2027.

## Table 11-5
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
San Bernardino County Third District Supervisor | WMP and PSPS | Meeting with County Supervisor Rowe | Conducted virtual meeting on at 10:30 am January 21, 2025
Big Bear Mountain Mutual Aid Association (MMAA) | WMP and PSPS | Group presentation with Q&A | Briefed MMAA at 9:00 am on February 11, 2025
Utility Wildfire General Order Scope Discussion | WMP | IOU and PU Coordination Meeting | Virtual Brief December 13, 2024
BVES PSPS Working and Planning Group, Stakeholder Meeting | PSPS | Briefing to Local Stakeholders | Virtual Brief December 12, 2024
Inland Empire Fire Safe Alliance Meeting | WMP | Meeting with Fire Fighting Agencies, USFS, other local community stakeholders | Virtual Brief November 13, 2024
PSPS Working Group Meeting + Microgrid Workshop - Central Region - AND- Inland Empire & Northern Region | PSPS | Meeting Utilities & Local Government & Agencies | Virtual Brief November 7, 2024
Statewide Access and Functional Needs/Joint IOU Meeting | PSPS | Meeting | Roundtable discussion September 17, 2024
Collaborative Council / Joint access functional needs | PSPS | Meeting | Virtual meeting September 9, 2024
BVES and Big Bear Fire Department Coordination Meeting | WMP | Meeting` | Coordination and upcoming projects discussion on July 29, 2024
CUEA Annual Conference | WMP and PSPS | Conference | Conference briefs on May 10, 2024
CMUA Annual Wildfire Mitigation Plan Roundtable | WMP and PSPS | Conference | Conference briefs on December 6, 2023

## Table 11-6
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
Limited coordination with Local Government and Agencies | Work with Local Government and Agencies to gain their input to Bear Valley's WMP Initiative. | Strategy: Conduct a workshop for WMP Initiatives with Local Government and Agencies and provide an opportunity for them to review proposed initiatives. Target timeline: Conduct coordination workshop for WMP Initiatives in 2026 and conduct WMP Initiative review in 2027.

## Table 11-7
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
None | N/A | N/A | N/A

## Table 11-8
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
None | N/A | N/A

## Table 11-9
Stakeholder Group/Target Community | Event Type | Method(s) for Communicating | Means to Verify Message Receipt | Interests or Concerns Before, During, and After Wildfire and PSPS events
General Public | Wildfire | TV, radio, newspapers, website updates, and social media (See Section 6.3, PSPS Plan Appendix G) | Customer response tracking, outage website analytics, media monitoring | Real-time outage updates, restoration estimates, safety guidance
General Public | Wildfire-related outage | Automated alerts via phone, SMS, IVR, email (See Section 6.3, PSPS Plan Appendix G) | Customer response tracking, outage website analytics, media monitoring | Real-time outage updates, restoration estimates, safety guidance
General Public | PSPS-related outage | Hourly messaging via automated alerts and social media (See Section 6.3, PSPS Plan Appendix G) | Customer response tracking, outage website analytics, media monitoring | Real-time outage updates, restoration estimates, safety guidance
General Public | Restoration of service | Notifications for restoration timelines via automated alerts (See Section 6.3, PSPS Plan Appendix G) | Customer response tracking, outage website analytics, media monitoring | Timely updates on service restoration, customer support access
Priority Essential Services | Wildfire | Direct outreach to service providers, priority notification list, dedicated call lines (See Section 6.3, PSPS Plan Appendix G) | Response confirmation from critical infrastructure facilities, status reports | Advance warning for power disruptions, continuity planning, emergency backup needs
Priority Essential Services | Wildfire-related outage | Response confirmation from critical infrastructure facilities, status reports (See Section 6.4, PSPS Plan Appendix G) | Response confirmation from critical infrastructure facilities, status reports | Advance warning for power disruptions, continuity planning, emergency backup needs
Priority Essential Services | PSPS-related outage | Direct communication via emergency coordination meetings, priority call lines (See Section 6.4, PSPS Plan Appendix G) | Response confirmation from critical infrastructure facilities, status reports | Advance warning for power disruptions, continuity planning, emergency backup needs
Priority Essential Services | Restoration of service | Dedicated restoration updates through direct outreach and emergency contacts (See Section 6.4, PSPS Plan Appendix G) | Response confirmation from critical infrastructure facilities, status reports | Timely restoration of service for critical operations
AFN Populations | All event types | Text-to-speech messages, large-font alerts, coordination with disability advocacy groups (See Section 6.3, PSPS Plan Appendix G) | Follow-up calls, coordination with AFN service providers, CRC check-ins | Ensuring accessibility of messages, timely assistance, medical equipment support
Populations with Limited English Proficiency | All event types | Translated messages in multiple languages, multilingual call center support (See Section 6.3, PSPS Plan Appendix G) | Community feedback channels, multilingual helpline logs | Availability of translated materials, culturally appropriate outreach
People in Remote Areas | All event types | Radio-based notifications, in-person alerts from local emergency teams (See Section 6.3, PSPS Plan Appendix G) | Local emergency teams confirm receipt through direct interaction | Reliable communication in areas with low connectivity, emergency preparedness support

## Table 11-10
Target Community | Interests or Concerns Before, During, and After Wildfire and PSPS events
Populations with Limited English Proficiency | Limited access to wildfire risk information, need for multilingual emergency alerts, culturally appropriate outreach, and assistance in understanding PSPS notifications (See Section 6.3, PSPS Plan Appendix G).
People in Remote Areas | Challenges with internet connectivity, reliance on radio-based alerts, and limited access to Community Resource Centers (CRCs) during PSPS activations (See Section 6.3, PSPS Plan Appendix G).
Elderly Residents | Concerns about mobility limitations, access to emergency transportation, medical device power needs, and difficulty receiving real-time alerts (See Section 6.3, PSPS Plan Appendix G).
People with Limited Technology Access | Barriers to receiving digital alerts and emergency notifications, reliance on landline calls, printed notices, and in-person community support (See Section 6.3, PSPS Plan Appendix G).
AFN Populations (People with Disabilities, Medical Needs, or Other Functional Limitations) | Require personalized notifications, early warning for power-dependent medical devices, access to backup power resources, and targeted outreach through support organizations (See Section 6.3, PSPS Plan Appendix G).
Essential Service Providers (Hospitals, Fire Departments, Water Systems, etc.) | Require early warning for PSPS events, direct coordination with BVES emergency teams, and access to power continuity planning resources (See Section 6.3, PSPS Plan Appendix G).

## Table 11-11
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Limited feedback on wildfire & PSPS emergency plan | Less than 10% of state & local government stakeholders have been able to provide feedback on emergency preparedness planning | Strategy: Host a 1.5-day workshop with state & local agencies to review emergency preparedness strategies. Solicit verbal & written comments from stakeholders. Assign liaison for follow-up engagement. (See Section 7, PSPS Plan Appendix G) Target Timeline: By end of 2026
Low participation from AFN communities in outreach programs | Many AFN residents are unaware of BVES wildfire & PSPS preparedness programs due to outreach gaps in language access & accessibility limitations | Strategy: Expand multilingual messaging & alternative formats (e.g., large print, ASL videos, braille). Strengthen AFN partnerships with CBOs & advocacy groups. Conduct targeted outreach via CRCs & AFN service networks. (See BVES AFN Plan, Section 5.2) Target Timeline: By end of 2026
Inefficiencies in real-time emergency alert delivery | Some customers report delays in receiving emergency alerts via SMS, IVR, & automated calls during PSPS events, especially in low-signal rural areas | Strategy: Upgrade mass notification system to enhance alert speed & reliability. Implement radio-based emergency notifications for remote areas. Conduct PSPS notification performance testing & system audits. (See Section 6.3, PSPS Plan Appendix G) Target Timeline: By end of 2027
Limited awareness of vegetation management efforts | Many customers do not understand how vegetation management reduces wildfire risk, leading to public concerns about tree-trimming activities | Strategy: Launch a Vegetation Management Awareness Campaign through social media, direct mail, & community meetings. Enhance transparency in vegetation clearing schedules & create a public GIS mapping tool showing planned tree-trimming areas. (See Section 6.3, PSPS Plan Appendix G) Target Timeline: By end of 2027
Barriers to outreach in remote communities | Remote-area residents face connectivity challenges & rely heavily on radio, in-person outreach, & satellite-based messaging | Strategy: Expand satellite-based emergency alerts & establish mobile outreach teams for door-to-door notifications in high-risk rural areas. Partner with local radio stations to provide real-time PSPS updates & safety messaging. (See Section 6.3, PSPS Plan Appendix G) Target Timeline: By end of 2027
Populations with Limited English Proficiency | All event types | Translated messages in multiple languages, multilingual call center support (See Section 6.3, PSPS Plan) Target Timeline: By end of 2028
People in Remote Areas | All event types | Radio-based notifications, in-person alerts from local emergency teams (See Section 6.3, PSPS Plan) Target Timeline: By end of 2028

## Table 12-1
Initiative | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | 2026 End of Year Total / Completion Date | 2027 Total / Status | 2028 Total / Status | Section; Page number
Asset management and inspection enterprise system(s) | Conduct Annual Usefulness and Impact of Enterprise System Survey and Take Corrective Action on Results (ENT_1) | GD_34 | 100% Completed by December 31, 2026 | 100% Completed by December 31, 2027 | 100% Completed by December 31, 2028 | 12; p. 291
Vegetation management enterprise system | Conduct Annual Usefulness and Impact of Enterprise System Survey and Take Corrective Action on Results (ENT_2) | VM_15 | 100% Completed by December 31, 2026 | 100% Completed by December 31, 2027 | 100% Completed by December 31, 2028 | 12; p. 291
Grid Monitoring enterprise system | Develop and implement automatic SCADA alerts plan for staff. Grid Response Procedures and Notifications (GD_19) | GD_38 | Automatic SCADA alert plan developed; December 2026 | Automatic SCADA alert plan implemented; December 2027 | N/A | 8.7.2; p. 169
Ignition Detection enterprise system | Develop and implement automatic iSIU system alerts plan for staff. Autonomous Monitoring of Power Line Infrastructure (SAF_4) | SAF_7 | Automatic iSIU system alert plan developed; December 2026 | Automatic iSIU system alert plan implemented; December 2027 | N/A | 10.4.1; p. 235
Environmental Monitoring enterprise system | Develop and implement automatic weather station network alerts plan for staff. Advanced weather monitoring and weather stations (SAF_1) | SAF_1 | Automatic weather station network alert plan developed; December 2026 | Automatic weather station alert plan implemented; December 2027 | N/A | 10.2.1; p. 229
Risk Assessment enterprise system | Complete Integration of Direxyon and Technosylva Models - Risk Methodology and Assessment (RMA_1) | RMA_1 | System integration started; January 2026 | System integration completed; December 2027 | N/A | 5.7; p. 66

## Table 13-1
ID # | Year of Lesson Learned | Subject | Category and Source of Lesson Learned | Description of Lesson Learned | Proposed WMP Improvement | Timeline for Implementation | Reference
1 | 2020-2023 | Permitting | Grid Design, Operations, and Maintenance | The permitting process with the US Forrest Service is a lengthy and challenging process/ | The USFS has a very heavy workload in addition to its permitting work and has a very small staff to accomplish the workload. Additionally, the USFS has many permit requests to process and does not necessarily have the internal capability to determine which requests need to be processed as a high priority. Therefore, it is beneficial engage the USFS staff early and frequently to emphasize the priority of the project; especially, wildfire mitigation initiatives. | Situational. Currently, BVES does not have any projects requiring significant USFS permitting. | Radford Line Replacement Project
2 | 2024 | Fire Potential Index (FPI) | Situational Awareness and Forecasting | Implementation of FPI has provided BVES more granularity in evaluating operational actions to mitigate wildfire risk. | Circulating FPI to staff every day raises the situational awareness on the wildfire risk for the day and helps drive the right operational decisions each day to ensure the distribution system is operated in a safe manner. | Currently implements. BVES will continue to review its effectiveness each year as an ongoing effort. | 2026-2028 WMP Section 10.6
3 | 2023 | Supply Chain | Grid Design, Operations, and Maintenance | Procurement lead time for large and technically advanced electrical equipment (substation transformers, intelligent switchgear and reclosers, capacitor banks, etc.) is extremely lengthy (15-18 months). | Procurement of electrical equipment must be performed as soon as feasible due to the long lead times. When this is coupled with permitting time and GRC approval time, a project can easily extend out to 3-5 years. | Currently implemented in BVES's planning process. | N/A
4 | 2023 | Risk based planning | Risk Methodology and Assessment and Wildfire Mitigation Strategy | By transitioning to risk models that provide risk analysis at the segment level, BVES is now able to prioritize its grid hardening efforts in its highest risk spots with significant precision. | Utilize Technosylva's FireSight model to prioritize WMP initiatives. | BVES has transitioned to utilizing quantitative risk modeling (Technosylva's FireSight) in prioritizing WMP Initiatives. | 2026-2028 WMP Section 6
5 | 2023-2024 | Community engagement | Emergency Preparedness, Collaboration, and Community outreach | Apply findings from public safety partners and community coordination throughout the year to inform future planning | Drawing upon lessons learned from other California utilities, BVES has increased its community engagement activities over 2021 from 2020 as well as engaging more broadly with the direct public safety partners within the service area. | Ongoing | 2026-2028 WMP Section 11
6 | 2023-2024 | PSPS Preparation | Emergency Preparedness, Collaboration, and Community outreach | The feedback from Drills and Table Top Exercises are vital to the advancement of BVES programs, specifically those related to PSPS | Drills and Table Top Exercises have led to enhancements for training PSPS response teams by (1) Elevated exercise complexity with interactive elements to simulate real-world scenarios; (2) Role-specific training and action cards for individual practice and training; and (3) Backup training to bolster operational readiness and response capability | Ongoing | 2026-2028 WMP Section 11
7 | 2023-2024 | PSPS Response | Emergency Preparedness, Collaboration, and Community outreach | Lessons learned from other IOUs is leading to improved PSPS Response | IOUs have collectively reported that utilities made strides to enhance collaboration with Public Safety Partners | 2026-2028 WMP | 2026-2028 WMP Section 11
8 | 2023-2024 | PSPS Customer Impact Mitigation | Emergency Preparedness, Collaboration, and Community outreach | Lessons learned from other IOUs is leading to improved PSPS Response | Reduce customer burden for the access and functional needs (AFN) population and disadvantaged communities (DACs), through improved notification systems and Community Resource Centers (CRCs). Additional CRC amenities considered with a focus on additional charging units. | 2026-2028 WMP | 2026-2028 WMP Section 11
9 | 2023-2024 | PSPS Communication and Notification Improvements | Emergency Preparedness, Collaboration, and Community outreach | Lessons learned from other IOUs is leading to improved PSPS Response | Addressing concerns regarding excessive or inaccurate notifications to customers and Public Safety Partners. Customers report being frustrated with too much communication. Allow customers to select notification options. | 2026-2028 WMP | 2026-2028 WMP Section 11
10 | 2023-2024 | PSPS Operational Coordination and Standardization | Emergency Preparedness, Collaboration, and Community outreach | Lessons learned from other IOUs is leading to improved PSPS Response | Standardizing naming conventions and processes across different operational aspects to minimize confusion and errors. During tabletop exercises, participants reported confusion in the naming convention. Ensure simple naming conventions when disseminating information. Consider colors/numbers and clear/concise naming. Consider using an unfamiliar audience to see if they can understand the convention. | 2026-2028 WMP | 2026-2028 WMP Section 11
11 | 2023-2024 | PSPS Situational Awareness and Training | Emergency Preparedness, Collaboration, and Community outreach | Lessons learned from other IOUs is leading to improved PSPS Response | Providing further training and standardization to ensure all personnel are proficient in hosting operational briefings and calls. During tabletop exercises, participants reported confusion in the naming convention. Adopt a standard template and memo for communication per topic and customer group. Conduct position-specific training to improve situational awareness, especially regarding scope changes during PSPS events. | 2026-2028 WMP | 2026-2028 WMP Section 11
12 | 2023 | Covered Conductor Working Group | Grid Design, Operations, and Maintenance | The utilities agree that it is helpful to share information, practices, and data across the utilities as this can lead to improvements in reducing wildfire risk, safety incidents, and the impacts of PSPS, and improvements with other utility objectives. Several shared discussions of materials and procedures have helped improved BVES’s covered conductor program. | Covered conductors working group reports have provided an excellent technical basis for making grid design and maintenance decisions. | Ongoing | 2026-2028 WMP Section 8
13 | 2023-2024 | Risk Model Working Group | Risk Methodology and Assessment | The Risk Model Working Group has provided BVES with significant amount of detailed information concerning Risk Modeling especially from the other Utilities. | The information gained can help shape how BVES uses its risk modeling resources and makes decisions moving forward. | Ongoing | RMWG Reports
14 | 2023 | Utility Vegetation Management Best Practices for Wildfire Safety | Vegetation Management and Inspection | The meeting on Utility Vegetation Management Best Practices for Wildfire Safety has provided BVES with beneficial insight into considerations for vegetation management program improvements. | The information gained can help shape how BVES implements its vegetation management and inspection programs. | Ongoing | Meeting report.

## Table 13-2
Discontinued Activity (Tracking ID) | Rationale for Discontinuation | Lessons Learned | Replacement Activities (include page # where discussed)
None | N/A | N/A | N/A