## Table of Tables
Section | Required Tables Name | PGE Tables Names
2 |  | Table PG&E-2‑1: WMP Section Program Owners
3.2 |  | Table PG&E-3.2‑1: List Of Objectives, Risk Drivers, Targets and Metrics
3.4 | Table 3-1: List Of Wildfire Risk Drivers To Prioritize
3.5 | Table 3-2: Self-Identified Performance Metrics Table
3.6 | Table 3-3: Summary Of Projected WMP Expenditures
4.1 | Table 4-1: High-Level Service Territory Components
4.2 | Table 4-2: Catastrophic PG&E Wildfires
4.2 |  | Table PG&E‑4.2‑1: Causes and Lessons Learned From Catastrophic Wildfires
4.3 | Table 4-3: Frequently Deenergized Circuits
5.2 |  | Table PG&E-5.2-1: Addressing Key Likelihood and Consequences In Risk Models
5.2.2.2 |  | Table PG&E-5.2.2.2-2: Critical Customer Weightings
5.2.2.3 |  | Table PG&E-5.2.2.3-1: Wdrm V4 Mitigation Composites
5.2.3 | Table 5-1: Risk Modeling Assumptions and Limitations
5.3.1 | Table 5-2: Summary Of Design Scenarios
5.3.2 | Table 5-3: Summary Of Extreme-Event Scenarios
5.4 | Table 5-4: Summary Of Risk Models
5.5.2 | Table 5-5: Summary Of Top-Risk Circuits, Segments, Or Spans
5.7 | Table 5-6: Utility Risk Assessment Improvement Plan
6.1.2 | Table 6-1: List Of Prioritized Areas In An Electrical Corporations Service Territory Based On Overall Utility Risk
6.1.3 |  | Table PG&E-6.1.3-1: Migration Effectiveness Alone and In Combination
6.1.3.2 |  | Table PG&E-6.1.3.2-1: Distribution Risk Areas
6.1.3.2 |  | Table PG&E-6.1.3.2-2: Transmission Risk Areas
6.1.3.4 | Table 6-2: Stakeholder Roles and Responsibilities In The Decision-Making Process
6.2.1.2 | Table 6-3: Risk Impact Of Activities
6.2.1.2 |  | Table PG&E-6.2.1.2-1: Contingency Table for EPSS Effectiveness Calculation
6.2.1.2 |  | Table PG&E-6.2.1.2-2: Example Calculations for Undergrounding and Covered Conductor Installation
6.2.1.2 |  | Table PG&E-6.2.1.2-3: Example Calculations for Backlog Tags
6.2.1.2 |  | Table PG&E-6.2.1.2-4: Example Calculations for Pole Clearing, Distribution Routine Patrols, and Breakaway Connector Installation
6.2.1.2 |  | Table PG&E-6.2.1.2-5: Example Calculations for Pole Clearing, Distribution Routine Patrols, and Breakaway Connector Installation
6.2.1.3 | Table 6-4: Summary Of Risk Reduction For Top-Risk Circuits
7 |  | Table PG&E‑7‑1: PSPS Event Statistics
8.1.2 | Table 8-1: Grid Design, Operation, and Maintenance Targets By Year
8.2.1 |  | Table PG&E-8.2.1-1: Mitigation Effectiveness Assessment – Failure Mode Examples
8.2.1 |  | Table PG&E-8.2.1-2: Ignition Mitigation Effectiveness Ratings For Three Example Mitigations
8.2.1 |  | Table PG&E-8.2.1-3: Ignition Mitigation Effectiveness Representative Blended Average Values
8.2.1 |  | Table PG&E-8.2.1-4 : Covered Conductor and Undergrounding Impacts On The Likelihood Of Ignition
8.2.1 |  | Table PG&E-8.2.1-5: Covered Conductor And Undergrounding Risk Reduction Trend Analysis
8.2.7.2 |  | Table PG&E-8.2.7.2: PSPS Impacts Avoided After Temporary Microgrid Deployment
8.3 | Table 8-2: Asset Inspection Frequency, Method, and Criteria
8.3 |  | Table PG&E-8.3-1: Asset Inspection Frequency, Method, and Criteria
8.3.8.3 |  | Table PG&E-8.3.8.3-1: 2024 HFTD HFRA Aerial Inspection Find Rate By Notification Priority
8.3.15.1 |  | Table PG&E-8.3.15.1-1: Substation and Switchyard Drone Inspection Find Rate By Year and Notification Priority
8.4 |  | Table PG&E-8.4-1: Equipment Maintenance and Repair
8.5.1 | Table 8-3: Grid Design, Asset Inspections, and Maintenance QA and QC Program Objectives
8.5.1 | Table 8-4: Grid Design, Asset Inspections, and Maintenance QA and QC Activity Targets
8.5.2 |  | Table PG&E-8.5.2-1: QA/QC Guidance Documents
8.5.3 |  | Table PG&E-8.5.3-1: QA/QC Sampling Plan
8.5.4 |  | Table PG&E-8.5.4-1: Pass Rate Calculation
8.6 | Table 8-5-1: Transmission: Number Of Past Due Asset Work Orders Categorized By Age (As Of December 31, 2024)
8.6 | Table 8-6-1: Transmission: Number Of Past Due Asset Work Orders Categorized By Priority Level (As Of January 29, 2024)
8.6 | Table 8-5-2: Distribution: Number Of Past Due Asset Work Orders Categorized By Age and HFTD Tier (As Of September 30, 2024)
8.6 | Table 8-6-2: Distribution: Number Of Past Due Asset Work Orders Categorized By Priority Level (As Of September 30, 2024)
8.6 | Table 8-5-3: Substation: Number Of Past Due Asset Work Orders Categorized By Age (As Of January 1, 2025)
8.6 | Table 8-6-3: Substation: Number Of Past Due Asset Work Orders Categorized By Priority Level (As Of January 1, 2025Er Of Past Due Asset Work Orders Categorized By Priority Level
8.6.2 |  | Table PG&E-8.6.2-1: Annual Forecasted Creations and Completions Volume
8.6.2 |  | Table PG&E-8.6.2-2: Electric Notifications Priority Levels
8.7.1 | Table 8-7: Top Ten Impacted Circuits From Changes To Epss In The Past Three Years
8.7.1.1 |  | Table PG&E-8.7.1.1-1: Wildfire Risk Levels
8.7.1.1 |  | Table PG&E-8.7.1.1-2: Summary Of Epss Capable Miles
8.8.1 |  | Table PG&E-8.8.1-1: Workforce Planning, Asset Inspections
8.8.2 |  | Table PG&E-8.8.1-2: Workforce Planning, Grid Hardening
8.8.3 |  | Table PG&E-8.8.1-3: Workforce Planning, Risk Event Inspection
9.1.2 | Table 9-1: Vegetation Management Targets By Year (Non-Inspection Targets)
9.1.2 | Table 9-2: Vegetation Inspections and Pole Clearing Targets By Year
9.2 | Table 9-3: Vegetation Management Inspection Frequency, Method, and Criteria
9.2.1.3 |  | Table PG&E-9.2.1.3-1: Radial Clearances, Per Go 95, Appendix E
9.2.3.3 |  | Table PG&E-9.2.3.3-1: PG&E Minimum Clearance Distances
9.2.3.3 |  | Table PG&E-9.2.3.3-2: CPUC Minimum Clearance Distance Requirements and Recommendations
9.2.3.3 |  | Table PG&E-9.2.3.3-3: Nerc Minimum Vegetation Clearance Distance (Mvcd) In Feet
9.8 | Table 9-4: Partnerships In Vegetation Management
9.11.1 | Table 9-5: Vegetation Management QA and QC Program
9.11.1 | Table 9-6: Vegetation Management QA and QC Activity Targets
9.12.3 | Table 9-7: Number Of Past Due Vegetation Management Work Orders Categorized By Age and HFTD Tier
9.12.3 | Table 9-8: Number Of Past Due Vegetation Management Work Orders Categorized By Age and Priority Levels
9.13.2 |  | Table PG&E 9.13.2-1: PG&E VMI Basic Web Based Courses
9.13 | Table 9-9: Vegetation Management Qualifications and Training
10.1.2 | Table 10-1: Situational Awareness Targets By Year
10.2.1 | Table 10-2: Environmental Monitoring Systems
10.3.1 | Table 10-3: Grid Operation Monitoring Systems
10.4.1 | Table 10-4: Fire Detection Systems Currently Deployed
10.5.1 |  | Table PG&E-10.5-1: PG&E Operational Mesoscale Modeling System Development
10.5.1 |  | Table PG&E‑10.5.1‑1: Weather Variables
10.6.1 | Table 10-5: Fire Potential Features
10.6.1 |  | Table PG&E-10.6.1-1: Fpi Class Breakpoints
10.6.1 |  | Table PG&E-10.6.1-2: Fire Consequence Distribution By Class Breakpoints
10.6.1 |  | Table PG&E-10.6.1-3: Fpi Model Skill Score Comparison
10.6.1 |  | Table PG&E-10.6.1-4: Fpi Model Features
11.1.1 | Table 11-1: Emergency Preparedness and Community Outreach Targets By Year
11.2.1 | Table 11-2: Key Gaps and Limitations In Integrating Wildfire- and PSPS Specific Strategies Into Emergency Plan
11.3.1 | Table 11-3: High-Level Communication Protocols, Procedures, and Systems With Public Safety Partners
11.3.1 | Table 11-4: Key Gaps and Limitations In Communication Coordination With Public Safety Partners
11.3.2 | Table 11-5: Collaboration In Local and Regional Wildfire Mitigation Planning
11.3.2 | Table 11-6: Key Gaps and Limitations In Collaborating On Local and Regional Wildfire Mitigation Planning
11.3.3 | Table 11-7: Collaboration With Tribal Agencies
11.3.3 | Table 11-8: Key Gaps and Limitations In Collaborating With Tribal Agencies
11.4.1 | Table 11-9: Protocols For Emergency Communication To Stakeholder Groups
11.4.3 | Table 11-10: List Of Target Communities
11.4.3 |  | Table PG&E-11.4.3-1: PG&E’S Public Communication, Outreach, and Education Awareness Programs
11.4.4 |  | Table PG&E-11.4.4-1: Identifying Afn Customers
11.4.6 | Table 11-11: Key Gaps and Limitations In Public Emergency Communication Strategy
12.1.1 | Table 12-1: Enterprise Systems Targets
13.1 | Table 13-1: Lessons Learned
13.2 |  | Table PG&E-13.2-1: Working Groups and Lessons Learned
13.3 | Table 13-2: Lessons Learned From Discontinued Activities
13.3 |  | Table PG&E-13.3-1: Completed WMP Activities
13.3 |  | Table PG&E-13.3-1: Completed WMP Activities
ACI PG&E-25U-01 |  | Table ACI‑PG&E‑25U‑01‑1: Correlation Between Sub Models And Outage Models
ACI PG&E-25U-04 |  | Table ACI‑PG&E‑25U‑04‑2: Comparison Of Risk Models Percentile Groupings Used In Distribution Inspection Planning
ACI PG&E-25U-04 |  | Table ACI‑PG&E‑25U‑04‑1: Inspection Scenario Summary
ACI PG&E-25U-05 |  | Table ACI‑PG&E‑25U‑05‑2: Risk Reduction Calculation Per Wdrm V4
ACI PG&E-25U-05 |  | Table ACI‑PG&E‑25U‑05‑1: IONA Program 2024 Results Summary
RN-26-04-01 |  | TABLE PG&E-RN-PGE-26-04-01: Updated Gh 12 And Gh 14 Targets
RN-26-04-02 |  | TABLE PG&E-RN-PGE-26-04-02 Adjustments To Gh‑12 Targets
RN-26-05-01 |  | TABLE PG&E-RN-PGE-26-05-01 Original And Revised Gh‑04 Targets
RN-26-05-02 |  | TABLE PG&E-RN-PGE-26-05-02 Gh‑04 Target Breakdown
RN-26-05-03 |  | TABLE PG&E-RN-PGE-26-05-03 Gh‑12 Target Breakdown
RN-26-07-01 |  | TABLE PG&E-RN-PGE-26-07-01 Test Inspection Targets
RN-26-07-02 |  | TABLE PG&E-RN-PGE-26-07-02 Inspection Program Find Rates
RN-26-08-01 |  | TABLE PG&E-RN-PGE-26-08-01 Wood Management Benchmarking Target (Vm 23) Timeline And Milestones
RN-26-08-02 |  | TABLE PG&E-RN-PGE-26-08-02 Workforce Planning – Vegetation Management Target (Vm 24) Timeline And Milestones
RN-26-08-03 |  | TABLE PG&E-RN-PGE-26-08-03 Integrated Vegetation Management Benchmarking Target (Vm 25) Timeline And Milestones
RN-26-08-04 |  | TABLE PG&E-RN-PGE-26-08-04 Vm Critical Datasets Data Quality Remediation (Vegetation Management) Target (Es 01) Timeline And Milestones
RN-26-09-01 |  | TABLE PG&E-RN-PGE-26-09-01 Program Consolidation Timeline And Milestones

## Table PG&E-2‑1
TABLE PG&E-2‑1:
WMP SECTION PROGRAM OWNERS
Section | Title | Program Owner
Section 1 | Executive Summary | Andy Abranches, Senior Director, Wildfire Risk Management
Section 2 | Responsible Persons | Andy Abranches, Senior Director, Wildfire Risk Management
Section 3 | Sections 3.1 – 3.5: Overview of the WMP | Andy Abranches, Senior Director, Wildfire Risk Management
| Section 3.6: Projected Expenditures | Kristin Manz, Vice President (VP), Finance and Planning
| Section 3.7: Climate Change | Andy Abranches, Senior Director, Wildfire Risk Management
Section 4 | Section 4.1: Service Territory | Jadwindar Singh, Senior Director, Electric Asset Knowledge Management and Analytics
| Section 4.2: Catastrophic Wildfire History | Andy Abranches, Senior Director, Wildfire Risk Management
| Section 4.3: Frequently Deenergized Circuits | Mark Quinlan, Senior Vice President (SVP), Wildfire, Emergency and Operations
Section 5 | Risk Methodology and Assessment | Andy Abranches, Senior Director, Wildfire Risk Management
Section 6 | Wildfire Mitigation Strategy Development | Andy Abranches, Senior Director, Wildfire Risk Management
Section 7 | PSPS | Mark Quinlan, SVP, Wildfire and Emergency Operations
Section 8 | Grid Design, Operations, and Maintenance | Martin Wyspianski, VP, Electric Asset Management
Section 9 | VM and Inspections | Angela Sanford, VP, Vegetation Management
Section 10 | Situational Awareness and Forecasting | Scott Strenfel, Senior Director, Meteorology and Fire Science
Section 11 | Emergency Preparedness, Collaboration, and Public Awareness | Angie Gibson, VP, Emergency Preparedness and Response
Section 12 | Enterprise Systems | Tahir Paroo, Senior Director, IT Grid Systems and Smart Meter Operations
Section 13 | Lessons Learned, Working Group Meetings, and Discontinued Initiative Activities | Andy Abranches, Senior Director, Wildfire Risk Management

## Table PG&E 3.2-1
TABLE PG&E-3.2‑1:
LIST OF OBJECTIVES, RISK DRIVERS, TARGETS AND METRICS
Category | PG&E Target Name | Target Number | Objective #1 & 2 |  |  | Objective #3 | Objective #4 | PG&E Performance Metric
|  |  | Reduce Wildfire Risk Associated With PG&E’s Electrical Infrastructure |  |  | Reduce Customer Impact from Wildfire Mitigation Activities | Mature Enterprise Systems to Support Risk Reduction Efforts
|  |  | Vegetation Contact | Equipment Failure | Contact From Object
Grid Design, Operations, and Maintenance | System Hardening – Undergrounding | GH‑04 | X | X | X | X |  | See Quarterly Data Report (QDR) Tables 5 and 6 for performance metrics(a)
| Overhead Hardening – Distribution | GH‑12 | X | X | X
| Line Removal Enabled by Remote Grid – Distribution(b) | GH‑14 | X | X | X | X
| System Hardening Distribution Quality Assurance | GM‑10D |  | X
| System Hardening Distribution Quality Control | GM‑11D |  | X
| System Hardening – Transmission Shunt Splices | GH‑06 |  | X
| System Hardening – Transmission Conductor Segment Replacement | GH‑11 |  | X
| Service Breakaway Connectors | GM‑14 | X |  | X
| Proactive Avian Abatement Feasibility Study – Transmission | GH‑13 |  |  | X
| Detailed Inspection – Transmission | AI‑04 |  | X
| Infrared Inspections – Transmission | AI‑06 |  | X
| Aerial Scan Inspections – Distribution(b) | AI‑07A | X | X
| Detailed Inspections – Distribution | AI-07D | X | X
| Evaluate / create new method(s) to improve accuracy of Asset Inventory Data | ES-02 |  | X
| Asset Inspections Distribution Quality Assurance | GM‑01D |  | X
| Asset Inspections Transmission Quality Assurance | GM‑01T |  | X
| Open Tag Reduction – Distribution Backlog | GM‑03 |  | X
| Asset Inspections Distribution Quality Control | GM‑09D |  | X
| Asset Inspection Transmission Quality Control | GM‑09T |  | X
| Open Tag Reduction Distribution Backlog Quality Assurance | GM‑12D |  | X
| Open Tag Reduction Distribution Backlog Quality Control | GM‑13D |  | X
| Workforce Planning – Distribution Asset Inspection | GM‑15 |  | X
| Updates on EPSS Reliability Study | GM‑07 | X | X | X
| Integration of continuous grid monitoring technologies | ES‑05 | X | X | X |  |  | See QDR Table 10 for performance metrics(a)
| Continue sharing PSPS lessons learned | PS‑10 | X | X | X
| Access and Functional Needs (AFN) Customer Support During PSPS Emergencies | PS‑12 |  |  |  | X
Vegetation Management and Inspections | Vegetation Management Critical Datasets Data Quality Remediation | ES‑01 | X |  |  |  |  | See QDR Tables 5 and 6 for performance metrics(a)
| Pole Clearing Program - Compliance (c) | VM‑02C | X | X
| Pole Clearing Program - Risk Reduction (c) | VM-02R | X | X
| Substation Inspections – Distribution | VM‑05 | X
| Substation Inspections – Transmission | VM‑06 | X
| Substation Inspections – Power Generation | VM‑07 | X
| Vegetation Management Quality Assurance – Distribution | VM‑08D | X
| Vegetation Management Quality Assurance – Transmission | VM‑08T | X
| Routine Transmission – Ground | VM‑13 | X
| Transmission Hazard Patrol (Second Patrol, Tree Mortality) | VM‑14 | X
| Integrated Vegetation Management Benchmarking | VM‑25 | X
| Distribution Routine Patrol | VM‑16 | X
| Distribution Hazard Patrol | VM‑17 | X
| Vegetation Management Quality Control – Distribution Routine | VM‑22D | X
| Vegetation Management Quality Control – Pole Clearing | VM‑22P | X
| Vegetation Management Quality Control – Transmission Routine | VM‑22T | X
| Wood Management Benchmarking | VM‑23 | X
| Workforce Planning – Vegetation Management | VM‑24 | X
| Mitigation of Legacy Tree Removal Inventory (TRI)(b) | VM‑26 | X
Emergency Preparedness | Community Engagement – Outreach to HFRA Infrastructure Customers | CO‑04 |  |  |  | X |  | See QDR Table 10 for performance metrics(a)
| Community Engagement – Outage Preparedness Campaign | CO‑05 |  |  |  | X
| Common Operating Picture Technology | EP‑07 |  |  |  | X
Situational Awareness and Forecasting | Line Sensor – Installations | SA‑02 |  |  |  |  | X | See QDR Tables 4 and 10 for performance metrics(a)
| Evaluate camera AI system performance and new functionalities. | SA‑08 |  |  |  |  | X
| Distribution Fault Anticipation (DFA) Installations | SA‑10 |  |  |  |  | X
| EFD – Installations | SA‑11 |  | X |  |  | X
| Live Fuel Moisture Data Collection | SA‑12 |  |  |  |  | X
| Weather Station Network Evaluation | SA‑13 |  |  |  |  | X
| SmartMeter devices next generation capability evaluation | SA‑14 |  |  |  |  | X
| Weekly uptime of Wildfire Cameras | SA‑15 |  |  |  |  | X
| Weather Model Verification Tool | SA‑16 |  |  |  |  | X
| Weather Model Enhancements leveraging AI‑ML | SA‑17 |  |  |  |  | X
| Weather Station Network Health | SA‑18 |  |  |  |  | X
| Weather Station Network Optimization | SA‑19 |  |  |  |  | X
Enterprise Systems | Grid Monitoring Sensor Systems Efficacy Assessment | ES‑03 | X | X | X |  | X | Not Applicable
| Operate and Maintain Weather Data Systems | ES‑04 | X | X |  |  | X
_______________
(a) Attainment metrics (where applicable) are available on QDR Table 1
(b) PG&E set new targets in our Revision Notice response, specifically for Critical Issues RN-PGE-26-04, RN-PGE-26-05, RN-PGE-26-06, and RN-PGE-26-09. See 2026-2028 WMP Revision Notice Response R0 for additional information.
(c) Pole Clearing Program Target (VM-02) is split into Pole Clearing Program - Compliance (VM-02C) and Pole Clearing Program - Risk Reduction (VM-02R) in response to Critical Issue RN-PGE-26-10. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table 3-1
TABLE 3-1:
LIST OF WILDFIRE RISK DRIVERS TO PRIORITIZE (a)
Priority | Risk | Risk Driver | Risk Sub‑Driver | x% of Ignitions in HFTD/HFRA)[i] | Topographical and Climatological Risk Factors
1 | Wildfire | Vegetation contact | Vegetation – Branch | 12.5% | Extreme weather, wind
1 | Wildfire | Vegetation Contact | Vegetation – Trunk | 14.4% | Extreme weather, wind
1 | Wildfire | Vegetation Contact | Vegetation – Other | 6.9% | Extreme weather, wind
2 | Wildfire | Equipment failure | Anchor/guy | 0.1% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Capacitor bank | 2.4% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Conductor | 12.1% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Connector device | 5.7% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Cross arm | 1.7% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Fuse | 3.4% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Cutout | See “Fuse” | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Insulator and bushing | 1.5% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Lightning arrestor | 0.7% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Pole | 4% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Recloser | 1.1% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Relay | See “Sectionalized” | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Sectionalized | >0.1% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Splice | See “Conductor” | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Switch | 1% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Transformer | 1.7% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Voltage Regulator | 0.6% | Extreme weather, heat, wind
2 | Wildfire | Equipment failure | Other – Equipment failure | 1.5% | Extreme weather, heat, wind
3 | Wildfire | Contact from object | Animal Contact | 9.6% | N/A
3 | Wildfire | Contact from object | Balloon Contact | 1.7% | Wind
3 | Wildfire | Contact from object | Land Vehicle Contact | 5.6% | N/A
3 | Wildfire | Contact from object | Aircraft Vehicle Contact | See “Other – Contact from object” | N/A
3 | Wildfire | Contact from object | Third Party Contact | See “Other – Contact from object” | N/A
3 | Wildfire | Contact from object | Other – Contact from object | 3.7% | N/A
4 | Wildfire | Wire‑to‑Wire contact | N/A | 1.5% | Heat, Wind
4 | Wildfire | Contamination | N/A | 2.1% | Precipitation, heat, wind
4 | Wildfire | Protective device operation | N/A | See “Utility work/ operation” | N/A
4 | Wildfire | Vandalism/theft | N/A | 0.1% | N/A
4 | Wildfire | Utility work/operation | N/A | 0.3% | N/A
4 | Wildfire | Lightning | N/A | See “All Other” | Precipitation, lightning
4 | Wildfire | Unknown | N/A | 2.8% | N/A
4 | Wildfire | Dig-in | N/A | See “All Other” | N/A
4 | Wildfire | All Other | N/A | 1.4% | N/A
_______________
(a) Updated based on Substantive Errata filing on April 18, 2025 in accordance with Energy Safety issuance of Revision Notice at 21.
(i) The percentage of ignition in HFTD/HFRA is based on 2015‑2024 data.

## Table 3-2
TABLE 3-2:
SELF-IDENTIFIED PERFORMANCE METRICS TABLE
Performance Metric | Assumption that Underlies Use of the Metric | Section Associated With Performance Metric
Weather‑Normalized CPUC‑Reportable Fire Ignitions Rate in R3+ Conditions (Rolling 365 days) | (1) The metric focuses on ignitions occurring in elevated wildfire risk conditions as measured by the FPI of R3 and above; historical ignitions occurring in R3+ conditions result in the most consequential fires; (2) The rolling metric addresses the issue of considerable swings during the first half of the year when the number of R3 days is low (often 0) | WMP

## Table 3-3
TABLE 3-3:
SUMMARY OF PROJECTED WMP EXPENDITURES
Year | Projected Spend
(Thousands of Dollars)(a)
2026 | 5409896
2027 | 6298656
2028 | 6779101
(a) Adjusted in response to Critical Issues RN-PGE-26-04 and RN-PGE-26-05. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table 4-1
TABLE 4-1:
HIGH-LEVEL SERVICE TERRITORY COMPONENTS
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non‑HFTD | Total
Area Served (Sq. Mi.) | 31907 | 6141 | 34693 | 72741
Number of Electric Customer Accounts Served | 361698 | 170740 | 5225042 | 5757480
Overhead Transmission Lines (Circuit Miles) | 4149 | 1273 | 12430 | 17852
Overhead Distribution Lines (Circuit Miles) | 17771 | 6754 | 55241 | 79766
Underground Transmission Lines (Circuit Miles) | 11 | 1 | 171 | 183
Underground Distribution Lines (Circuit Miles) | 2491 | 1063 | 25544 | 29098

## Table 4-2
TABLE 4-2:
CATASTROPHIC PG&E WILDFIRES
Ignition Date | Fire Name(a) | Fire Size (acres) | No. of Fatalities | No. of Structures Destroyed and Damaged | Financial Loss (in millions, USD)(b)
2015-09-09 | Butte | 70868 | 2 | 965 | 71
2017-08-29 | Railroad | 12407 | – | – | 3
2017-10-08 | Nuns Complex | 56556 | 3 | 1527 | 47
2017-10-08 | Cherokee | 8500 | – | 7 | 1.4
2017-10-08 | Atlas | 51624 | 6 | 903 | 47
2017-10-08 | Cascade | 9989 | 4 | 274 | 7.75
2017-10-08 | Redwood Valley | 36523 | 9 | 584 | 23
2017-10-08 | La Porte | 6151 | – | 76 | 7.75
2017-10-09 | Pocket | 17357 | – | 8 | 47
2018-11-08 | Camp | 153336 | 85 | 19558 | 16650
2019-10-23 | Kinkade | 77758 | – | 434 | 950
2020-09-27 | Zogg | 56338 | 4 | 231 | 375
2021-07-13 | Dixie | 963309 | 1 | 1405 | 1150
2022-09-06 | Mosquito(b) | 76788 | – | 91 | Unknown
2024-06-17 | Sites(b) | 19195 | – | – | Unknown
_______________
(a) Data in this table comes from the CAL FIRE website (excluding financial loss). Financial loss information provided by CAL FIRE was combined for the Cascade and LaPorte Fires and the Nuns Complex, Atlas, and Pocket Fires. For those individual fires, the total financial loss is divided evenly.
(b) USFS is continuing to investigate the Mosquito Fire and CAL FIRE is investigating the Sites Fire. They have not designated an official cause of ignition for either fire.

## Table PG&E‑4.2‑1
TABLE PG&E‑4.2‑1:
CAUSES AND LESSONS LEARNED FROM CATASTROPHIC WILDFIRES
Fire Name: Butte Fire
Date of Ignition | 2015-09-09
Cause Based on Available Information | According to CAL FIRE, a gray pine contacted a PG&E powerline which ignited part of the tree. Embers from the contact with the conductor dropped into the fuels below the conductor, which ignited the wildland fire. Two gray pines on the outer edge of the pine stand had been previously removed, which left the interior gray pine that contacted the conductor more exposed to the sun and the powerlines.
Lessons Learned | At the time of the Butte Fire, PG&E did not have a process in place for evaluating specific lessons learned from individual fires. Since then, PG&E improved employee and contractor training for VM to mitigate wildfire and ensure safe work practices.
Fire Name: Railroad Fire
Date of Ignition | 2017-08-29
Cause Based on Available Information According to the USFS | According to the USFS, a contractor was hired by USFS to remove a dead cedar tree adjacent to PG&E’s powerlines in Madera County. After several cuts to the tree, it fell at an angle and hit PG&E’s powerlines. After the tree hit the powerlines, the vegetation beneath the powerlines ignited. Given the presence of the downed lines, the crew could not safely attempt to put out the fire. Without immediate suppression efforts, the fire spread into the surrounding forest.
Lessons Learned | At the time of the Railroad Fire, PG&E did not have a process in place for evaluating specific lessons learned from individual fires. Upon review, the Railroad Fire did not result from an issue relating to PG&E’s electric system. PG&E sent a crew to the area to mitigate a hazard tree to prevent a potential wildfire from occurring. The fire resulted from VM work that could have been performed more safely.
After the Railroad Fire, PG&E improved its VM training and employee and contractor training regarding work outdoors in any forest, brush, or grass‑covered land. In 2021, we implemented Safe Work Practices that outline safe work processes that contractors must adhere to when performing tree work. If tree work cannot be performed pursuant to the safe work practices outlined because of abnormal conditions, contractors are required to stop work to reevaluate how to perform the work safely.
Fire Name: October 2017 Wildfires
Date of Ignition | Various (see details below for each fire)
Cause Based on Available Information According to the USFS | Vegetation contact and equipment failures in high winds caused these fires. Cherokee – On October 8, 2017, PG&E observed that branches from a green, healthy California White Oak/Valley Oak tree had broken in Oroville. The troubleman who responded reported that one branch was found on the ground lying on top of a downed conductor. Another broken branch was suspended in the air, hanging on another branch, and touching a conductor that remained intact.
Adobe – According to CAL FIRE, the Adobe Fire in Kenwood was one of six incidents constituting the “Nuns Fire,” which ignited on October 8, 2017. When PG&E was granted access to the incident location, PG&E observed a green eucalyptus tree had fallen and was lying on three of three conductors of a 12 kilovolts (kV) primary tap line on the ground. The eucalyptus tree was rooted approximately 60 feet from the distribution conductors.
Nuns – According to CAL FIRE, the Nuns Fire, which started on October 8, 2017 in Glen Ellen, consisted of six different fires: Nuns, Adobe, Norrbom, Pressley, Partrick and Oakmont. When PG&E was granted access to the incident site, PG&E observed that the top section of a green, healthy Alder tree had broken and was lying on the ground near one of three conductors of a downed open wire secondary service in Glen Ellen. Over a week later, two healthy Douglas Fir trees also came down on primary distribution conductors, and steel messenger cables supporting the telephone and Community Antenna Television conductors approximately 0.4 miles downstream from the initial ignition location.
Sulphur – According to CAL FIRE, the Sulphur Fire started on October 8, 2017 in Clearlake Oaks. PG&E identified two poles that had broken. The top section of one pole had broken and fallen to the ground, and the pole one span to the west burned at the base and fell to the ground. This resulted in a wire down event.
La Porte – According to CAL FIRE, the La Porte Fire started on October 9, 2017 in Bangor, Butte County. PG&E understands that CAL FIRE collected a section of conductor and a tree branch prior to releasing the incident location. After CAL FIRE released the incident location on October 13, 2017, PG&E accessed the site and was able to identify broken oak tree branches and a downed conductor at the incident location.
Pressley – According to CAL FIRE, the Pressley Fire started on October 9, 2017 “east of Rohnert Park” in Sonoma County. Per CAL FIRE, this is one of the six fires that were included in the vegetation‑caused “Nuns Fire.”
Norrbom – According to CAL FIRE, the Norrbom Fire was one of six incidents that make up the Nuns Fire, which ignited on October 8, 2017. On June 8, 2018, CAL FIRE issued a press release stating that the Norrbom fire was caused by a tree falling and contacting PG&E power lines. It is possible CAL FIRE was referring to a location on Gehricke Road, Sonoma, at which a black oak tree was found lying on downed conductors.
Redwood Valley – According to CAL FIRE, the Redwood Valley Fire location was first observed on October 9, 2017. According to the CAL FIRE Investigation Report, a CAL FIRE employee reported a small vegetation fire on the east side of Hawn Creek Road. A PG&E troubleman recalled seeing one of three phases down near the incident location later in the day.
Cascade – CAL FIRE determined the Cascade Fire, which occurred in Yuba County on October 8, 2017, was started by sagging power lines coming into contact during heavy winds. PG&E observed that the primary conductors were in place and appeared to be in working order at the time that CAL FIRE requested possession of the equipment. The secondary service line appeared to be damaged at mid‑span, but there was no apparent damage to other PG&E facilities.
Partrick – According to CAL FIRE, this fire occurred in Napa on October 8, 2017. When PG&E was granted access to the incident location, PG&E observed that a 20‑inch diameter Coast Live Oak tree, approximately 50 feet tall and rooted approximately 40 feet uphill from distribution conductors had broken above its base. One of the two phases on a 12 kV tap line was on the ground. According to CAL FIRE, the Partrick Fire was one of six ignitions that were part of the “Nuns Fire.”
Atlas – According to CAL FIRE, the Atlas Fire started in two locations in Napa on October 8, 2017. When PG&E was granted access to the first incident location, PG&E observed a broken tree limb and broken field‑phase primary insulator on a 12 kV circuit. A green, healthy tree limb fell from a California White Oak/Valley Oak that was rooted approximately 15 feet from the distribution conductors. When PG&E was granted access to the second incident location, PG&E observed a California Black Oak tree that had broken at the base and was lying on the ground. The base of the California Black Oak tree was burnt and rooted approximately 20 feet from the distribution conductors.
Lobo – According to CAL FIRE, the Lobo Fire ignited on October 9, 2017, near Nevada City. CAL FIRE removed both a Ponderosa Pine tree and distribution conductors at the incident location before releasing the incident location. Prior to CAL FIRE removing the tree, PG&E employees who assisted with the evidence collection reported briefly observing the pine tree resting on the conductors. PG&E does not know how the tree came to rest on the conductors because CAL FIRE removed the tree prior to PG&E having an opportunity to inspect the tree.
Oakmont – According to CAL FIRE’s website, the Oakmont Fire started late on October 14, 2017. However, according to PG&E records, a PG&E troubleman who was at the Oakmont incident location to assist CAL FIRE on the evening of October 13, 2017 reported that there was already a quarter‑acre grass fire with CAL FIRE on site working to contain the fire. When PG&E was granted access to the incident location on October 18, PG&E observed that a green, healthy Douglas Fir tree had uprooted and fallen onto other trees. Two of two phases of the 12 kV circuit were down on another tree, but the tree was still standing and not on fire.
Pocket – According to CAL FIRE’s website, the Pocket Fire started on October 9, 2017, in Geyserville. When PG&E accessed the incident location on October 17, 2017, PG&E observed that a top section of a California White Oak/Valley Oak tree had broken. At least one conductor of a 12 kV circuit was on the ground. The California White Oak/Valley Oak was rooted approximately 15 feet from the distribution conductors.
Lessons Learned | At the time of the October 2017 Wildfires, PG&E did not have a process in place for evaluating specific lessons learned from individual fires. For purposes of this response, we address the October 2017 wildfires collectively because they occurred over a relatively short period of time during significant high wind events. The identified ignitions primarily resulted from: (1) vegetation contact with electrical facilities; and/or (2) equipment failure.
PG&E hired an independent firm to undertake a Root Cause Analysis (RCA) of each of the October 2017 wildfires to identify gaps that can be closed to reduce the risk of future catastrophic wildfires. Envista Forensics completed the RCA and published its report in July 2022. (c) PG&E responded to the Envista findings in August 2022. (d) PG&E agreed with the majority of the recommendations contained in that report, and referenced the work done by the Company since 2017 in the areas of risk assessment and mapping, situational awareness and forecasting, grid design and system hardening, asset management and inspections, VM and inspections, grid operations and protocols, data governance, emergency protocols, and PSPS.
Fire Name: Camp Fire
Date of Ignition | 2018-11-08
Cause Based on Available Information | CAL FIRE investigators determined the cause of the Camp Fire was electrical arcing between an energized jumper conductor (power line) and the steel tower structure. Investigators determined a “C hook” that linked an insulator string connected to the jumper conductor to the transposition arm of a PG&E tower failed, allowing the energized jumper conductor to contact the steel tower structure. The ensuing electrical arcing between the jumper conductor and steel tower structure caused the aluminum strands of the conductor and a portion of the steel tower structure to melt. The molten aluminum and steel fell to the brush‑covered ground at the base of the steel tower structure. This molten metal ignited the dry brush, which resulted in the fire. The broken “C hook” that led to the arcing showed substantial wear with age. The ignition occurred on a red flag warning day.
Lessons Learned | The lessons learned from the Camp Fire include: (1) the need for rigorous equipment inspections and maintenance; and (2) the need to use risk modeling to prioritize inspection and maintenance work so that maintenance is performed in the highest risk area for wildfires. In the enhanced inspection process, wear on C‑Hooks and other equipment was specifically addressed.
Fire Name: Kincade Fire
Date of Ignition | 2019-10-23
Cause Based on Available Information | The Kincade Fire ignited in the Geysers geothermal area in Sonoma County. According to CAL FIRE, a jumper cable on the Geysers #9 Lakeville 230 kV transmission line broke and arced upon failure toward the associated steel tower. CAL FIRE concluded this arcing ignited the vegetation below and ignited the fire.
The portion of the transmission line connected to the broken jumper remained energized at the time of the incident though it had not served load to the neighboring Calpine‑owned geothermal facility for several years. During the fire investigation, it was also determined that, following Calpine’s request to remove the connection between the line and the Calpine‑owned facility, the jumper cable had been configured as “open”—i.e., electrically connected at only one end, rather than both ends. According to CAL FIRE, due to this configuration, the jumper cables may have had a greater range of movement, potentially increasing the wear on the jumper cable at issue to the point that it failed during a wind event.
Lessons Learned | There were two primary lessons learned from the Kincade Fire: (1) the need to provide additional guidance on how to routinely evaluate whether facilities in the field are idle and need to be de‑energized and/or removed; and (2) the need to provide additional guidance on the proper construction of open jumpers in order to prevent any undesired outcomes that may result from jumper conductor length or movement.
Fire Name: Zogg Fire
Date of Ignition | 2020-09-27
Cause Based on Available Information | According to CAL FIRE, a gray pine near Zogg Mine Road in unincorporated Shasta County failed and struck PG&E powerlines. This contact resulted in an ignition of the vegetation beneath the powerlines. The ignition occurred on a RFW Day and quickly spread beyond the area of origin.
The trees in the area where the ignition occurred had been inspected in 2018, 2019, and 2020. Photographs of the subject tree from PG&E’s July 2019 Light Detection and Ranging (LiDAR) indicate the subject tree had a green canopy and appeared healthy, according to CAL FIRE’s arborist expert.
Lessons Learned | Our analysis of the Zogg Fire led us to further evaluate the propensity for tree‑related outages and overstrike tree potential, specifically during certain weather conditions such as RFW days, and to pilot programs to perform more detailed inspections of potential strike trees on routine VM patrols.
Fire Name: Dixie Fire
Date of Ignition | 2021-07-13
Cause Based on Available Information | According to CAL FIRE, the Dixie Fire ignited in the Feather River Canyon when a tree failed and fell onto an overhead distribution line. As a result of the tree contact, fuses on two of the conductors operated, but the third fuse did not operate, and that line remained energized. The contact between the tree and the energized line eventually led to an ignition. CAL FIRE notes that at the time of the failure, the tree that contacted PG&E’s powerlines was alive, vital, and growing vertically. Post‑fire inspection suggested the tree had previous damage and decay that contributed to its failure.
Lessons Learned | Even on non‑RFW days and/or days with no weather or wind events, an ignition can occur when vegetation or other objects contact an energized powerline.
Outages in HFTD areas whose cause cannot be quickly ascertained may call for a more expedited response time even if there is not a known safety hazard, especially during summer months during times of drought.
Fire Name: Mosquito Fire
Date of Ignition | 2022-09-06
Cause Based on Available Information | The cause of the Mosquito Fire is currently under investigation.
Lessons Learned | There are currently no lessons learned from this ignition because its cause is still under investigation.
Fire Name: Sites
Date of Ignition | 2024-06-17
Cause Based on Available Information | The cause of the Sites Fire is currently under investigation.
Lessons Learned | There are currently no lessons learned from this ignition because its cause is still under investigation.

## Table-4-3
TABLE 4-3:
FREQUENTLY DEENERGIZED CIRCUITS
Entry # | Circuit ID | Name of Circuit | Dates of Outages | Numbers of Customers Hours of PSPS per Outage | Measures Taken, or Planned to Be Taken, to Reduce the Need for an Impact of Future PSPS of Circuit | Estimated Annual Decline in PSPS Events and PSPS Impact on Customers (Customer hours)
1 | 152101101 | ALLEGHANY 1101 | 2019-10-09 | 78196 | · 1.3 OH hardening miles in scope for 2026; | 77,784 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 18513 | · 4.4 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 100496 | · 0.3 miles in scope for undergrounding in 2028;
|  |  | 2020-09-07 | 59913 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-09-27 | 34140 | · Mitigated by Temporary Generation;
|  |  | 2020-10-14 | 156
|  |  | 2020-10-25 | 64061
2 | 152101102 | ALLEGHANY 1102 | 2019-10-09 | 9611 | · 0.4 OH hardening miles completed in 2021; | 13,678 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 6415 | · 10.6 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 21576 | · 2.6 miles in scope for undergrounding in 2026;
|  |  | 2020-09-07 | 6269 | · 21.2 miles in scope for undergrounding in 2027;
|  |  | 2020-09-27 | 3111
|  |  | 2020-10-25 | 11230
3 | 163561101 | ALPINE 1101 | 2019-10-09 | 3184 | · Mitigated by PSPS Protocols; | 12,381 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 7437
|  |  | 2019-10-26 | 26037
|  |  | 2020-09-07 | 11735
|  |  | 2020-09-27 | 5472
|  |  | 2020-10-25 | 13664
4 | 163561102 | ALPINE 1102 | 2019-10-09 | 1468 | · Mitigated by PSPS Protocols; | 13,047 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 8131
|  |  | 2019-10-26 | 28571
|  |  | 2020-09-07 | 12878
|  |  | 2020-09-27 | 5959
|  |  | 2020-10-25 | 14942
5 | 103261103 | ANDERSON 1103 | 2019-10-09 | 56117 | · 3 OH hardening miles in scope for 2025; | 20,516 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 15846 | · 3.7 miles undergrounded in 2023;
|  |  | 2019-11-20 | 4616 | · 2 Sectionalizing devices added or replaced;
|  |  | 2020-10-21 | 7020
|  |  | 2020-10-25 | 12569
|  |  | 2021-08-17 | 1757
|  |  | 2021-10-11 | 1834
6 | 42861101 | ANNAPOLIS 1101 | 2019-10-09 | 8905 | · Mitigated by PSPS Protocols; | 8,290 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 212
|  |  | 2019-10-26 | 18954
|  |  | 2020-10-25 | 5090
7 | 153661103 | APPLE HILL 1103 | 2019-10-09 | 76224 | · Mitigated by PSPS Protocols; | 45,186 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 28319
|  |  | 2019-10-26 | 64291
|  |  | 2020-09-07 | 46548
|  |  | 2020-09-27 | 23710
|  |  | 2020-10-25 | 58808
8 | 153661104 | APPLE HILL 1104 | 2019-10-09 | 112983 | · 1.3 OH hardening miles completed in 2019; 0 OH hardening miles in scope for 2025; | 81,877 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 53916 | · 5.4 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 164280
|  |  | 2020-09-07 | 87994
|  |  | 2020-09-27 | 51303
|  |  | 2020-10-25 | 114032
9 | 153662102 | APPLE HILL 2102 | 2019-10-09 | 257324 | · 0.7 OH hardening miles completed in 2019; 1.3 OH hardening miles completed in 2021; 0.1 OH hardening miles completed in 2024; 4.5 OH hardening miles in scope for 2025; | 223,489 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 104497 | · 7.4 miles undergrounded in 2024; 42.6 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 454605 | · 3 Sectionalizing devices added or replaced;
|  |  | 2020-09-07 | 164352
|  |  | 2020-09-27 | 103919
|  |  | 2020-10-25 | 247448
10 | 62081101 | ARBUCKLE 1101 | 2020-10-25 | 71 | · 1 Sectionalizing device added or replaced; | 51 fewer customer hours of PSPS per year
|  |  | 2021-08-17 | 65
|  |  | 2021-09-20 | 29
|  |  | 2021-10-11 | 97
|  |  | 2024-07-02 | 77
|  |  | 2024-10-17 | 738
|  |  | 2024-11-05 | 681
11 | 62081104 | ARBUCKLE 1104 | 2019-10-09 | 24724 | · Mitigated by PSPS Protocols; | 6,744 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 848
|  |  | 2019-11-20 | 298
|  |  | 2020-10-25 | 323
|  |  | 2021-08-17 | 265
|  |  | 2021-09-20 | 126
|  |  | 2021-10-11 | 391
12 | 103191101 | BANGOR 1101 | 2019-06-08 | 35466 | · 0.3 OH hardening miles completed in 2022; 0.1 OH hardening miles completed in 2024; | 82,821 fewer customer hours of PSPS per year
|  |  | 2019-09-23 | 45008 | · 1.3 miles undergrounded in 2022; 0.1 miles undergrounded in 2023;
|  |  | 2019-09-25 | 32868 | · 6 Sectionalizing devices added or replaced;
|  |  | 2019-10-09 | 149385
|  |  | 2019-10-23 | 60930
|  |  | 2019-10-26 | 212970
|  |  | 2020-09-07 | 10467
|  |  | 2020-09-27 | 8706
|  |  | 2020-10-14 | 4213
|  |  | 2020-10-25 | 102961
13 | 152701107 | BELL 1107 | 2019-10-09 | 38881 | · 2 Sectionalizing devices added or replaced; | 16,132 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 22050
|  |  | 2019-10-26 | 37564
14 | 152701108 | BELL 1108 | 2019-10-09 | 105914 | · 12.4 OH hardening miles completed in 2024; 3.1 OH hardening miles in scope for 2025; | 57,506 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 18645 | · 7.6 miles undergrounded in 2024; 0.5 miles in scope for undergrounding in 2025; 3.7 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 73845 | · 2 Sectionalizing devices added or replaced;
|  |  | 2020-10-25 | 37260
15 | 103751101 | BIG BEND 1101 | 2019-09-23 | 3322 | · 5.1 OH hardening miles completed in 2019; 0.1 OH hardening miles completed in 2023; 2.3 OH hardening miles in scope for 2026; | 6,395 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 2384 | · 0.7 miles in scope for undergrounding in 2026;
|  |  | 2019-10-05 | 2445
|  |  | 2019-10-09 | 12165
|  |  | 2019-10-23 | 4884
|  |  | 2019-10-26 | 18472
|  |  | 2020-09-07 | 9622
|  |  | 2020-09-27 | 8422
|  |  | 2020-10-14 | 10894
|  |  | 2020-10-21 | 7666
|  |  | 2020-10-25 | 11106
|  |  | 2021-08-17 | 9805
|  |  | 2021-10-11 | 8038
|  |  | 2023-08-30 | 3285
|  |  | 2024-07-02 | 9667
2737
|  |  | 2024-10-17 | 6471
|  |  | 2024-11-05 | 8445
16 | 103751102 | BIG BEND 1102 | 2019-09-23 | 7203 | · 1.7 OH hardening miles completed in 2019; 26.8 OH hardening miles completed in 2020; 2.5 OH hardening miles completed in 2021; 0 OH hardening miles completed in 2023; | 15,263 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 5067 | · 11.2 miles undergrounded in 2021; 10.8 miles undergrounded in 2022; 0.1 miles undergrounded in 2023;
|  |  | 2019-10-05 | 5360
|  |  | 2019-10-09 | 23522
|  |  | 2019-10-23 | 9861
|  |  | 2019-10-26 | 31174
|  |  | 2020-09-07 | 0
|  |  | 2020-09-27 | 301
|  |  | 2020-10-14 | 3677
|  |  | 2020-10-21 | 2427
|  |  | 2020-10-25 | 3555
17 | 152301101 | BONNIE NOOK 1101 | 2019-10-09 | 30733 | · 6 miles undergrounded in 2024; 7.7 miles in scope for undergrounding in 2025; 4.6 miles in scope for undergrounding in 2026; | 33,584 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 11381
|  |  | 2019-10-26 | 48418
|  |  | 2020-09-07 | 18377
|  |  | 2020-09-27 | 9219
|  |  | 2020-10-25 | 24031
18 | 152301102 | BONNIE NOOK 1102 | 2019-10-09 | 31323 | · Mitigated by PSPS Protocols; | 11,257 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 11900
|  |  | 2019-10-26 | 49320
|  |  | 2020-09-07 | 20519
|  |  | 2020-09-27 | 10440
|  |  | 2020-10-25 | 25587
19 | 192461102 | BRIDGEVILLE 1102 | 2019-10-09 | 6281 | · Mitigated by PSPS Protocols; | 6,514 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 9689
|  |  | 2020-09-07 | 12422
|  |  | 2020-10-14 | 634
|  |  | 2020-10-25 | 6627
20 | 152921101 | BROWNS VALLEY 1101 | 2019-09-23 | 9496 | · Sectionalization Planned; | 21,190 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 6693
|  |  | 2019-10-09 | 24883
|  |  | 2019-10-23 | 12796
|  |  | 2019-10-26 | 36492
|  |  | 2020-10-25 | 2475
21 | 152481102 | BRUNSWICK 1102 | 2019-09-25 | 14179 | · Mitigated by PSPS Protocols; | 75,905 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 67190
|  |  | 2019-10-23 | 33509
|  |  | 2019-10-26 | 84131
|  |  | 2020-09-07 | 58945
|  |  | 2020-09-27 | 6188
|  |  | 2020-10-25 | 71508
22 | 152481103 | BRUNSWICK 1103 | 2019-10-09 | 162922 | · 14.9 OH hardening miles completed in 2020; 13.5 OH hardening miles completed in 2021; 0.8 OH hardening miles completed in 2022; | 132,716 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 77827 | · 0.1 miles undergrounded in 2022;
|  |  | 2019-10-26 | 109071 | · 5 Sectionalizing devices added or replaced;
|  |  | 2020-09-07 | 138163 | · Mitigated by Temporary Generation;
|  |  | 2020-10-25 | 124002
23 | 152481104 | BRUNSWICK 1104 | 2019-10-09 | 138781 | · 3 Sectionalizing devices added or replaced; | 102,200 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 43169 | · Mitigated by Temporary Generation;
|  |  | 2019-10-26 | 86839
|  |  | 2020-09-07 | 108079
|  |  | 2020-10-25 | 94112
24 | 152481105 | BRUNSWICK 1105 | 2019-09-25 | 50916 | · 10.6 OH hardening miles completed in 2019; | 199,581 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 217975 | · 3 Sectionalizing devices added or replaced;
|  |  | 2019-10-23 | 90595 | · 4,184 customers mitigated by Temporary Generation;
|  |  | 2019-10-26 | 182978
|  |  | 2020-09-07 | 149243
|  |  | 2020-09-27 | 41777
|  |  | 2020-10-25 | 174742
25 | 152481106 | BRUNSWICK 1106 | 2019-09-25 | 55070 | · 0.1 miles undergrounded in 2023; | 263,579 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 301249 | · 8 Sectionalizing devices added or replaced;
|  |  | 2019-10-23 | 131169
|  |  | 2019-10-26 | 237528
|  |  | 2020-09-07 | 200021
|  |  | 2020-09-27 | 6918
|  |  | 2020-10-25 | 232470
26 | 152481107 | BRUNSWICK 1107 | 2019-10-09 | 141356 | · 2 Sectionalizing devices added or replaced; | 115,687 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 52503 | · Mitigated by Temporary Generation;
|  |  | 2019-10-26 | 124347
|  |  | 2020-09-07 | 115081
|  |  | 2020-10-25 | 91924
27 | 152481110 | BRUNSWICK 1110 | 2019-10-09 | 154669 | · 0 miles undergrounded in 2022; | 123,961 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 41942 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-10-26 | 159221 | · Mitigated by Temporary Generation;
|  |  | 2020-09-07 | 115933
|  |  | 2020-10-25 | 96507
28 | 102211101 | BUCKS CREEK 1101 | 2019-09-25 | 44 | · 13.1 OH hardening miles completed in 2019; 0.1 OH hardening miles completed in 2023; | 455 fewer customer hours of PSPS per year
|  |  | 2019-10-05 | 59 | · 1.5 miles undergrounded in 2023; 2.4 miles undergrounded in 2024;
|  |  | 2019-10-09 | 259
|  |  | 2019-10-26 | 464
|  |  | 2020-09-07 | 277
|  |  | 2020-09-27 | 137
|  |  | 2020-10-14 | 182
|  |  | 2020-10-21 | 119
|  |  | 2020-10-25 | 278
29 | 102211102 | BUCKS CREEK 1102 | 2019-10-09 | 10329 | · 1.9 OH hardening miles in scope for 2025; 2.1 OH hardening miles in scope for 2026; | 10,599 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 13928 | · 14.8 miles undergrounded in 2024; 9 miles in scope for undergrounding in 2025; 3.4 miles in scope for undergrounding in 2026;
|  |  | 2020-09-07 | 5527
|  |  | 2020-09-27 | 3930
|  |  | 2020-10-21 | 1329
|  |  | 2020-10-25 | 7354
30 | 102211103 | BUCKS CREEK 1103 | 2019-10-09 | 20491 | · 1.4 OH hardening miles in scope for 2025; | 23,140 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 30353 | · 0 miles in scope for undergrounding in 2025;
|  |  | 2020-09-07 | 20826
|  |  | 2020-09-27 | 12173
|  |  | 2020-10-21 | 3818
|  |  | 2020-10-25 | 21630
|  |  | 2021-08-17 | 13514
|  |  | 2021-10-11 | 10669
|  |  | 2024-10-17 | 6315
|  |  | 2024-11-05 | 74
31 | 103081105 | BUTTE 1105 | 2019-06-08 | 2910 | · 1.4 OH hardening miles completed in 2019; 0.3 OH hardening miles completed in 2024; | 20,404 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 3150 | · 4 Sectionalizing devices added or replaced;
|  |  | 2019-10-05 | 2833
|  |  | 2019-10-09 | 25000
|  |  | 2019-10-23 | 5597
|  |  | 2019-10-26 | 21191
|  |  | 2020-09-07 | 12023
|  |  | 2020-09-27 | 9214
|  |  | 2020-10-14 | 10484
|  |  | 2020-10-21 | 1066
|  |  | 2020-10-25 | 7718
|  |  | 2021-08-17 | 1029
32 | 255451102 | CAL WATER 1102 | 2019-10-09 | 69472 | · 1 Sectionalizing device added or replaced; | 17,852 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 485
|  |  | 2019-10-26 | 476
|  |  | 2020-09-07 | 221
|  |  | 2020-12-03 | 236
|  |  | 2021-01-18 | 327
|  |  | 2021-10-14 | 190
33 | 162211101 | CALAVERAS CEMENT 1101 | 2019-10-09 | 104531 | · 10.7 miles in scope for undergrounding in 2027; | 78,224 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 17062 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 191257
|  |  | 2020-10-25 | 40307
34 | 42711101 | CALISTOGA 1101 | 2019-09-25 | 13441 | · 5.4 OH hardening miles completed in 2019; 4.4 OH hardening miles in scope for 2025; 4.4 OH hardening miles in scope for 2026; 4 OH hardening miles in scope for 2027; | 115,662 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 89080 | · 3 miles in scope for undergrounding in 2025; 0.5 miles in scope for undergrounding in 2026; 10 miles in scope for undergrounding in 2027;
|  |  | 2019-10-23 | 45358 | · 6 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 156759 | · Mitigated by Temporary Generation;
|  |  | 2019-11-20 | 39148
|  |  | 2020-09-07 | 96678
|  |  | 2020-09-27 | 3228
|  |  | 2020-10-14 | 57976
|  |  | 2020-10-25 | 62900
|  |  | 2021-08-17 | 32531
|  |  | 2021-10-11 | 2780
|  |  | 2023-09-20 | 71
|  |  | 2024-07-02 | 335
|  |  | 2024-10-17 | 7480
|  |  | 2024-11-05 | 11256
35 | 42711102 | CALISTOGA 1102 | 2019-10-09 | 64376 | · 0.1 OH hardening miles completed in 2022; 3.4 OH hardening miles in scope for 2025; | 63,411 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 17139 | · 1.7 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 61701 | · 5 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 28052 | · Mitigated by Temporary Generation;
|  |  | 2020-09-07 | 39348
|  |  | 2020-10-14 | 26871
|  |  | 2020-10-25 | 38128
|  |  | 2021-08-17 | 23868
|  |  | 2024-10-17 | 436
|  |  | 2024-11-05 | 441
36 | 48011144 | CALPINE 1144 | 2019-10-23 | 4583 | · Mitigated by PSPS Protocols; | 1,011 fewer customer hours of PSPS per year
|  |  | 2021-08-17 | 558
|  |  | 2021-10-11 | 1190
|  |  | 2024-07-02 | 604
|  |  | 2024-10-17 | 1265
|  |  | 2024-11-05 | 374
37 | 48011146 | CALPINE 1146 | 2021-08-17 | 37 |  | No customer hours decline of PSPS per year
|  |  | 2021-10-11 | 79
|  |  | 2024-07-02 | 40
|  |  | 2024-10-17 | 63
|  |  | 2024-11-05 | 47
38 | 103321101 | CEDAR CREEK 1101 | 2019-10-09 | 46560 | · Mitigated by PSPS Protocols; | 12,635 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 79756
|  |  | 2019-11-20 | 14241
|  |  | 2020-09-07 | 29373
|  |  | 2020-10-14 | 32320
|  |  | 2020-10-21 | 29200
|  |  | 2020-10-25 | 34057
|  |  | 2021-08-17 | 21635
|  |  | 2023-08-30 | 13453
|  |  | 2024-09-30 | 12064
39 | 103201101 | CHALLENGE 1101 | 2019-10-09 | 43425 | · Mitigated by PSPS Protocols; | 24,038 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 19203
|  |  | 2019-10-26 | 50761
|  |  | 2020-09-07 | 0
|  |  | 2020-09-27 | 14298
|  |  | 2020-10-14 | 28678
|  |  | 2020-10-25 | 32359
40 | 103201102 | CHALLENGE 1102 | 2019-09-23 | 15751 | · Sectionalization Planned; · 14.0 miles in scope for undergrounding in 2028; | 33,423 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 10986
|  |  | 2019-10-09 | 54295
|  |  | 2019-10-23 | 23051
|  |  | 2019-10-26 | 48320
|  |  | 2020-09-07 | 18498
|  |  | 2020-09-27 | 16712
|  |  | 2020-10-14 | 17318
|  |  | 2020-10-25 | 41728
41 | 103091101 | CLARK ROAD 1101 | 2019-06-08 | 175 | · Mitigated by PSPS Protocols; | 603 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 172
|  |  | 2019-10-05 | 186
|  |  | 2019-10-09 | 875
|  |  | 2019-10-23 | 357
|  |  | 2019-10-26 | 646
42 | 103091102 | CLARK ROAD 1102 | 2019-06-08 | 15151 | · 0.1 OH hardening miles completed in 2019; 1 OH hardening miles completed in 2024; | 45,967 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 19146 | · 15.9 miles undergrounded in 2023; 7.9 miles undergrounded in 2024; 0.9 miles in scope for undergrounding in 2025;
|  |  | 2019-10-05 | 14634 | · 3 Sectionalizing devices added or replaced;
|  |  | 2019-10-09 | 62960
|  |  | 2019-10-23 | 27869
|  |  | 2019-10-26 | 58976
|  |  | 2020-09-07 | 57840
|  |  | 2020-09-27 | 24166
|  |  | 2020-10-14 | 38057
|  |  | 2020-10-21 | 26409
|  |  | 2020-10-25 | 31405
|  |  | 2021-08-17 | 15618
|  |  | 2021-10-11 | 14463
|  |  | 2023-08-30 | 2419
|  |  | 2024-09-30 | 2894
|  |  | 2024-11-05 | 4438
43 | 42821102 | CLOVERDALE 1102 | 2019-10-09 | 102234 | · 28.9 miles in scope for undergrounding in 2027; | 47,037 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 44239 | · 1 Motorized Switch Operator (MSO) device(s) replaced;
|  |  | 2019-10-26 | 247235 | · 4 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 377 | · Sectionalization Planned;
|  |  | 2020-10-14 | 1743
|  |  | 2020-10-25 | 16934
|  |  | 2021-08-17 | 1524
|  |  | 2021-10-11 | 1075
|  |  | 2024-10-17 | 4462
|  |  | 2024-11-05 | 3703
44 | 152471101 | COLUMBIA HILL 1101 | 2019-10-09 | 78055 | · 8.1 OH hardening miles completed in 2019; 0.4 OH hardening miles completed in 2020; 0.7 OH hardening miles in scope for 2025; 5.1 OH hardening miles in scope for 2026; | 69,437 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 53171 | · 0.7 miles undergrounded in 2020; 1.9 miles in scope for undergrounding in 2025; 1 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 100191
|  |  | 2020-09-07 | 53492
|  |  | 2020-09-27 | 4900
|  |  | 2020-10-14 | 661
|  |  | 2020-10-25 | 63788
45 | 103331101 | CORNING 1101 | 2019-10-09 | 56178 | · 1 Sectionalizing device added or replaced; | 35,470 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 41034
|  |  | 2020-10-25 | 25514
|  |  | 2021-08-17 | 33332
|  |  | 2021-09-20 | 9255
|  |  | 2021-10-11 | 28251
|  |  | 2023-08-30 | 12315
|  |  | 2023-09-20 | 13329
|  |  | 2024-07-02 | 22844
|  |  | 2024-10-17 | 22958
|  |  | 2024-11-05 | 23184
46 | 103331102 | CORNING 1102 | 2019-10-09 | 19137 | · 0.3 OH hardening miles completed in 2024; 4.4 OH hardening miles in scope for 2026; | 12,258 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 21210 | · 21.9 miles undergrounded in 2023; 7.8 miles undergrounded in 2024; 0.1 miles in scope for undergrounding in 2025;
|  |  | 2020-10-21 | 3295 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-10-25 | 8325 | · Mitigated by Temporary Generation;
|  |  | 2021-08-17 | 11609
|  |  | 2021-09-20 | 3707
|  |  | 2021-10-11 | 10916
|  |  | 2023-08-30 | 4467
|  |  | 2023-09-20 | 4969
|  |  | 2024-07-02 | 7470
|  |  | 2024-10-17 | 12461
|  |  | 2024-11-05 | 7840
47 | 63121101 | CORTINA 1101 | 2019-10-09 | 4724 | · 1 Sectionalizing device added or replaced; | 1,227 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 503 | · Mitigated by Temporary Generation;
|  |  | 2019-11-20 | 185
|  |  | 2020-10-25 | 187
|  |  | 2021-08-17 | 181
|  |  | 2021-09-20 | 80
|  |  | 2021-10-11 | 255
|  |  | 2024-07-02 | 204
|  |  | 2024-10-17 | 748
|  |  | 2024-11-05 | 573
48 | 102931103 | COTTONWOOD 1103 | 2019-10-09 | 124597 | · 4 Sectionalizing devices added or replaced; | 59,893 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 127617
|  |  | 2019-11-20 | 38755
|  |  | 2020-10-25 | 73369
|  |  | 2021-08-17 | 86526
|  |  | 2021-10-11 | 19347
49 | 102251101 | CRESTA 1101 | 2021-08-17 | 41 | · Mitigated by PSPS Protocols; | No customer hours decline of PSPS per year
|  |  | 2021-10-11 | 29
|  |  | 2024-09-30 | 76
|  |  | 2024-10-17 | 110
|  |  | 2024-11-05 | 159
50 | 103351101 | DESCHUTES 1101 | 2019-10-09 | 67881 | · Sectionalization Planned; | 28,742 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 104235
|  |  | 2019-11-20 | 18782
|  |  | 2020-09-07 | 769
|  |  | 2020-09-27 | 2491
|  |  | 2020-10-14 | 12938
|  |  | 2020-10-21 | 27670
|  |  | 2020-10-25 | 41392
|  |  | 2021-08-17 | 6278
|  |  | 2021-10-11 | 2085
51 | 103351104 | DESCHUTES 1104 | 2019-10-09 | 106469 | · 4.2 OH hardening miles completed in 2021; 33.1 OH hardening miles completed in 2022; 6.4 OH hardening miles completed in 2024; 4.5 OH hardening miles in scope for 2025; | 19,080 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 128780 | · 0.2 miles undergrounded in 2022; 0.1 miles undergrounded in 2023;
|  |  | 2019-11-20 | 13534 | · 6 Sectionalizing devices added or replaced;
|  |  | 2020-10-21 | 60492
|  |  | 2020-10-25 | 70941
|  |  | 2021-08-17 | 13209
|  |  | 2021-10-11 | 2591
52 | 152261103 | DIAMOND SPRINGS 1103 | 2019-10-09 | 68747 | · 4 Sectionalizing devices added or replaced; | 53,516 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 38293
|  |  | 2019-10-26 | 101731
|  |  | 2020-09-27 | 11774
|  |  | 2020-10-25 | 34555
53 | 152261104 | DIAMOND SPRINGS 1104 | 2019-10-09 | 22637 | · 1 Sectionalizing device added or replaced; | 17,543 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 10128
|  |  | 2019-10-26 | 26804
|  |  | 2020-10-25 | 10604
54 | 152261105 | DIAMOND SPRINGS 1105 | 2019-10-09 | 116283 | · 0.3 OH hardening miles completed in 2022; 0.8 OH hardening miles completed in 2023; | 95,007 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 73681
|  |  | 2019-10-26 | 124053
|  |  | 2020-10-25 | 66010
55 | 152261106 | DIAMOND SPRINGS 1106 | 2019-10-09 | 111745 | · 0.1 OH hardening miles completed in 2022; | 92,978 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 56893 | · 1.3 miles undergrounded in 2022;
|  |  | 2019-10-26 | 157004 | · 5 Sectionalizing devices added or replaced;
|  |  | 2020-09-07 | 2290
|  |  | 2020-09-27 | 35288
|  |  | 2020-10-25 | 58254
56 | 152261107 | DIAMOND SPRINGS 1107 | 2019-10-09 | 52696 | · 5.2 OH hardening miles completed in 2021; 2.2 OH hardening miles completed in 2022; | 41,240 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 30522 | · 1 miles undergrounded in 2022; 1.3 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 58688 | · 4 Sectionalizing devices added or replaced;
|  |  | 2020-10-25 | 28319
57 | 153741101 | DOBBINS 1101 | 2019-09-23 | 17114 | · 1 Sectionalizing device added or replaced; | 40,948 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 12843
|  |  | 2019-10-09 | 50343
|  |  | 2019-10-23 | 22040
|  |  | 2019-10-26 | 76842
|  |  | 2020-09-07 | 32407
|  |  | 2020-09-27 | 8454
|  |  | 2020-10-14 | 25928
|  |  | 2020-10-25 | 40515
58 | 152321101 | DRUM 1101 | 2019-10-09 | 12035 | · 1.8 OH hardening miles in scope for 2026; | 12,568 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 3931 | · 0.3 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 21452
|  |  | 2020-09-07 | 7375
|  |  | 2020-09-27 | 3773
|  |  | 2020-10-25 | 9797
59 | 43071101 | DUNBAR 1101 | 2019-10-09 | 168801 | · 0.4 OH hardening miles completed in 2021; 0 OH hardening miles completed in 2024; | 164,383 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 79555 | · 0.2 miles undergrounded in 2023; 2.3 miles undergrounded in 2024; 0.9 miles in scope for undergrounding in 2025; 0.7 miles in scope for undergrounding in 2026; 1.1 miles in scope for undergrounding in 2027;
|  |  | 2019-10-26 | 332300 | · 12 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 3525 | · Sectionalization Planned;
|  |  | 2020-09-07 | 82844
|  |  | 2020-10-14 | 8935
|  |  | 2020-10-25 | 158153
|  |  | 2021-08-17 | 2593
|  |  | 2024-10-17 | 8828
|  |  | 2024-11-05 | 7741
60 | 43071103 | DUNBAR 1103 | 2019-10-09 | 107806 | · 10 Sectionalizing devices added or replaced; | No customer hours decline of PSPS per year
|  |  | 2019-10-23 | 7889 | · Sectionalization Planned;
|  |  | 2019-10-26 | 221167
|  |  | 2019-11-20 | 4289
|  |  | 2020-09-07 | 9800
|  |  | 2020-10-14 | 14738
|  |  | 2020-10-25 | 49217
|  |  | 2021-08-17 | 4455
|  |  | 2024-10-17 | 4735
|  |  | 2024-11-05 | 4660
61 | 63811103 | DUNNIGAN 1103 | 2024-07-02 | 332 | · 1 Sectionalizing device added or replaced; | No customer hours decline of PSPS per year
|  |  | 2024-10-17 | 563
|  |  | 2024-11-05 | 416
62 | 152762101 | EL DORADO PH 2101 | 2019-10-09 | 277624 | · 14.3 OH hardening miles completed in 2019; 20.5 OH hardening miles completed in 2020; 18.2 OH hardening miles completed in 2021; 6.3 OH hardening miles completed in 2022; 1.6 OH hardening miles completed in 2023; | 243,772 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 104267 | · 13.1 miles undergrounded in 2022; 3.1 miles undergrounded in 2023; 6.2 miles in scope for undergrounding in 2026; 2.1 miles in scope for undergrounding in 2028
|  |  | 2019-10-26 | 398332
|  |  | 2020-09-07 | 171375
|  |  | 2020-09-27 | 87825
|  |  | 2020-10-14 | 7
|  |  | 2020-10-25 | 269585
63 | 152762102 | EL DORADO PH 2102 | 2019-10-09 | 91893 | · 14.5 OH hardening miles completed in 2020; 0.2 OH hardening miles completed in 2021; · 0.1 miles in scope for undergrounded in 2028; | 41,559 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 34940
|  |  | 2019-10-26 | 55080
|  |  | 2020-09-07 | 53023
|  |  | 2020-09-27 | 34534
|  |  | 2020-10-25 | 75169
64 | 162161101 | ELECTRA 1101 | 2019-10-09 | 74912 | · 0 OH hardening miles completed in 2024; 0.9 OH hardening miles in scope for 2025; | 42,004 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 32668 | · 6.2 miles undergrounded in 2024; 15.3 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 152174 | · 3 Sectionalizing devices added or replaced;
|  |  | 2020-10-25 | 34861
65 | 102781101 | ELK CREEK 1101 | 2019-10-09 | 32230 | · 0.9 OH hardening miles completed in 2023; 1 OH hardening miles in scope for 2025; 9.3 OH hardening miles in scope for 2026; | No customer hours decline of PSPS per year
|  |  | 2019-11-20 | 20196 | · 16 miles undergrounded in 2023; 0.8 miles in scope for undergrounding in 2025;
|  |  | 2020-10-21 | 1778 | · Mitigated by Temporary Generation;
|  |  | 2020-10-25 | 25353
|  |  | 2021-08-17 | 35996
|  |  | 2021-10-11 | 30140
|  |  | 2023-08-30 | 14650
|  |  | 2024-09-30 | 7084
|  |  | 2024-10-17 | 44570
|  |  | 2024-11-05 | 30279
66 | 42751113 | FITCH MOUNTAIN 1113 | 2019-10-09 | 142253 | · 14.3 OH hardening miles completed in 2020; 4.7 OH hardening miles completed in 2021; | 112,527 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 24247 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 271424
|  |  | 2020-10-25 | 17273
67 | 152181101 | FORESTHILL 1101 | 2019-09-25 | 24766 | · 0 OH hardening miles in scope for 2025; | 60,424 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 135732 | · 13.5 miles undergrounded in 2024; 5.4 miles in scope for undergrounding in 2025; 0.5 miles in scope for undergrounding in 2026;
|  |  | 2019-10-23 | 52586
|  |  | 2019-10-26 | 90429
|  |  | 2020-09-07 | 80506
|  |  | 2020-09-27 | 43873
|  |  | 2020-10-25 | 99506
68 | 152181102 | FORESTHILL 1102 | 2019-09-25 | 5335 | · 7.7 OH hardening miles in scope for 2026; | 12,137 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 25151 | · 27.9 miles in scope for undergrounding in 2026;
|  |  | 2019-10-23 | 9767
|  |  | 2019-10-26 | 20969
|  |  | 2020-09-07 | 15645
|  |  | 2020-09-27 | 8020
|  |  | 2020-10-25 | 18530
69 | 192321122 | FORT SEWARD 1122 | 2019-10-09 | 2510 | · 1 Sectionalizing device added or replaced; | 1,902 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 5824
|  |  | 2020-09-07 | 0
|  |  | 2020-10-14 | 833
|  |  | 2020-10-25 | 2152
70 | 163451701 | FROGTOWN 1701 | 2019-10-09 | 52566 | · 0.2 OH hardening miles completed in 2019; 0.6 OH hardening miles completed in 2021; | 37,254 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 38221
|  |  | 2019-10-26 | 48807
|  |  | 2020-09-07 | 43995
|  |  | 2020-10-25 | 54979
71 | 42561102 | FULTON 1102 | 2019-10-09 | 40785 | · 1 MSO device(s) replaced; | 35,685 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 21399 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 86394
|  |  | 2020-10-25 | 15519
72 | 42561107 | FULTON 1107 | 2019-09-25 | 1756 | · 0.2 OH hardening miles completed in 2019; 1.4 OH hardening miles completed in 2020; 0.1 OH hardening miles completed in 2021; 2.6 OH hardening miles completed in 2022; | 33,930 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 36497 | · 0.6 miles undergrounded in 2020; 1.8 miles undergrounded in 2022;
|  |  | 2019-10-23 | 18332 | · 4 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 102265
|  |  | 2019-11-20 | 10423
|  |  | 2020-10-25 | 19028
73 | 42891101 | GEYSERVILLE 1101 | 2019-10-09 | 78017 | · 6 Sectionalizing devices added or replaced; | 73,446 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 53450
|  |  | 2019-10-26 | 158008
|  |  | 2020-10-25 | 3689
|  |  | 2021-08-17 | 621
74 | 42891102 | GEYSERVILLE 1102 | 2019-10-09 | 64311 | · 1 OH hardening miles completed in 2019; | 55,458 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 147569 | · 15 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 45747 | · Mitigated by Temporary Generation;
|  |  | 2020-10-14 | 2672
|  |  | 2020-10-25 | 26055
|  |  | 2021-08-17 | 6301
|  |  | 2021-10-11 | 798
|  |  | 2024-10-17 | 7181
|  |  | 2024-11-05 | 6095
75 | 103401101 | GIRVAN 1101 | 2019-10-09 | 59223 | · 11 OH hardening miles completed in 2020; | 7,446 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 68183 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-11-20 | 31486 | · 20.6 miles in scope for undergrounding in 2028
|  |  | 2020-10-21 | 17916
|  |  | 2020-10-25 | 32931
|  |  | 2021-08-17 | 33507
|  |  | 2021-10-11 | 28541
|  |  | 2023-08-30 | 5554
|  |  | 2024-09-30 | 8552
|  |  | 2024-10-17 | 20493
76 | 102601101 | GLENN 1101 | 2019-10-09 | 2015 | · Mitigated by PSPS Protocols; | 989 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 2352
|  |  | 2019-11-20 | 41
|  |  | 2020-10-25 | 138
|  |  | 2021-08-17 | 122
|  |  | 2021-09-20 | 52
|  |  | 2021-10-11 | 153
|  |  | 2023-08-30 | 70
|  |  | 2024-09-30 | 1443
|  |  | 2024-10-17 | 5050
|  |  | 2024-11-05 | 3473
77 | 152031101 | GRASS VALLEY 1101 | 2019-10-09 | 39947 | · 2 Sectionalizing devices added or replaced; | 15,364 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 17947
|  |  | 2019-10-26 | 27623
|  |  | 2020-10-25 | 14310
78 | 152031103 | GRASS VALLEY 1103 | 2019-10-09 | 82777 | · Mitigated by PSPS Protocols; | 50,760 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 36034
|  |  | 2019-10-26 | 86402
|  |  | 2020-10-25 | 60023
79 | 24101103 | HALF MOON BAY 1103 | 2019-10-09 | 112024 | · 0 OH hardening miles in scope for 2026; | 105,000 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 8599 | · 2.5 miles undergrounded in 2022; 3.6 miles undergrounded in 2023; 0.9 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 234750 | · 10 Sectionalizing devices added or replaced;
|  |  | 2020-10-14 | 30831 | · Sectionalization Planned;
|  |  | 2020-10-25 | 44470
80 | 152241101 | HALSEY 1101 | 2019-10-09 | 129128 | · 0.5 OH hardening miles completed in 2019; | 66,685 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 40079
|  |  | 2019-10-26 | 87891
|  |  | 2020-10-25 | 64868
81 | 152241102 | HALSEY 1102 | 2019-10-09 | 96342 | · 7 Sectionalizing devices added or replaced; | 70,538 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 23673
|  |  | 2019-10-26 | 136983
|  |  | 2020-10-25 | 45787
82 | 152691103 | HIGGINS 1103 | 2019-10-09 | 112805 | · 2 Sectionalizing devices added or replaced; | 54,238 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 50691
|  |  | 2019-10-26 | 85858
|  |  | 2020-10-25 | 70050
83 | 152691104 | HIGGINS 1104 | 2019-10-09 | 149709 | · Mitigated by PSPS Protocols; | 91,682 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 66293
|  |  | 2019-10-26 | 100720
|  |  | 2020-10-25 | 121939
84 | 152691107 | HIGGINS 1107 | 2019-10-09 | 73272 | · Mitigated by PSPS Protocols; | 46,900 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 38048
|  |  | 2019-10-26 | 50600
|  |  | 2020-10-25 | 65534
85 | 152691109 | HIGGINS 1109 | 2019-10-09 | 93368 | · 0.1 miles undergrounded in 2022; | 57,851 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 39247 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 85700
|  |  | 2020-10-25 | 37600
86 | 152691110 | HIGGINS 1110 | 2019-10-09 | 66836 | · 1.6 OH hardening miles completed in 2019; | 45,683 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 33457 | · 3 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 69095
|  |  | 2020-10-25 | 45679
87 | 43361102 | HIGHLANDS 1102 | 2019-10-09 | 156931 | · 1.5 OH hardening miles completed in 2022; 0.1 OH hardening miles completed in 2023; 2.1 OH hardening miles completed in 2024; 8.7 OH hardening miles in scope for 2025; 1.2 OH hardening miles in scope for 2026; 6 OH hardening miles in scope for 2027; | 57,165 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 315310 | · 5.6 miles in scope for undergrounding in 2026; 0.8 miles in scope for undergrounding in 2027;
|  |  | 2019-11-20 | 39366 | · Sectionalization Planned;
|  |  | 2020-10-25 | 1129
|  |  | 2021-08-17 | 439
|  |  | 2021-10-11 | 451
|  |  | 2024-10-17 | 1281
|  |  | 2024-11-05 | 991
88 | 43361103 | HIGHLANDS 1103 | 2019-10-09 | 125687 | · 24.4 OH hardening miles in scope for 2026; | 117,715 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 221114 | · 0.7 miles in scope for undergrounding in 2026;
|  |  | 2019-11-20 | 55872 | · 2 Sectionalizing devices added or replaced;
|  |  | 2020-10-14 | 2278 | · Sectionalization Planned;
|  |  | 2020-10-25 | 95940 | · Mitigated by Temporary Generation;
|  |  | 2021-08-17 | 57173
|  |  | 2021-09-20 | 596
|  |  | 2021-10-11 | 30228
|  |  | 2023-08-30 | 571
|  |  | 2023-09-20 | 573
|  |  | 2024-07-02 | 1059
|  |  | 2024-10-17 | 2278
|  |  | 2024-11-05 | 3476
89 | 43361104 | HIGHLANDS 1104 | 2019-10-09 | 126140 | · 0.5 OH hardening miles in scope for 2026; | 59,339 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 101115 | •Mitigated by Temporary Generation;
|  |  | 2019-11-20 | 33229
|  |  | 2020-10-25 | 13
90 | 42251101 | HOPLAND 1101 | 2019-10-09 | 70929 | · Sectionalization Planned; | 47,856 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 3959
|  |  | 2019-10-26 | 122001
|  |  | 2019-11-20 | 4093
|  |  | 2020-10-25 | 2496
91 | 103441101 | JESSUP 1101 | 2019-10-09 | 82677 | · 4 Sectionalizing devices added or replaced; | 56,260 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 187117 | · Sectionalization Planned;
|  |  | 2019-11-20 | 48026
|  |  | 2020-10-21 | 34241
|  |  | 2020-10-25 | 46550
|  |  | 2021-08-17 | 41934
|  |  | 2023-08-30 | 2347
|  |  | 2024-09-30 | 9211
92 | 103441102 | JESSUP 1102 | 2019-10-09 | 101752 | · 0 OH hardening miles completed in 2023; 2 OH hardening miles in scope for 2025; | 55,280 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 208837 | · 23.8 miles undergrounded in 2023; 0.3 miles undergrounded in 2024;
|  |  | 2019-11-20 | 31145 | · 2 Sectionalizing devices added or replaced;
|  |  | 2020-10-21 | 22346
|  |  | 2020-10-25 | 49559
|  |  | 2021-08-17 | 64550
|  |  | 2021-10-11 | 2385
|  |  | 2024-09-30 | 10499
93 | 103441103 | JESSUP 1103 | 2019-10-09 | 79749 | · 1.5 OH hardening miles in scope for 2025; | 53,984 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 138784 | · 1.7 miles undergrounded in 2023;
|  |  | 2019-11-20 | 6621 | · 3 Sectionalizing devices added or replaced;
|  |  | 2020-10-21 | 2148
|  |  | 2020-10-25 | 4685
|  |  | 2021-08-17 | 3084
94 | 103221101 | KANAKA 1101 | 2019-09-23 | 14630 | · 6.6 OH hardening miles completed in 2021; 1.1 OH hardening miles completed in 2022; 0.2 OH hardening miles completed in 2023; 1.4 OH hardening miles completed in 2024; 0.5 OH hardening miles in scope for 2025; | 17,710 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 8656 | · 1.5 miles undergrounded in 2020; 2.9 miles undergrounded in 2022; 0.1 miles undergrounded in 2023;
|  |  | 2019-10-05 | 10689 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-10-09 | 42316
|  |  | 2019-10-23 | 15575
|  |  | 2019-10-26 | 59338
|  |  | 2019-11-20 | 691
|  |  | 2020-09-07 | 0
|  |  | 2020-10-14 | 15175
|  |  | 2020-10-25 | 18733
|  |  | 2021-10-11 | 266
95 | 253911102 | LAMONT 1102 | 2019-10-09 | 158 | · Mitigated by PSPS Protocols; | 235 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 179
|  |  | 2019-10-26 | 182
|  |  | 2020-09-07 | 86
|  |  | 2020-12-03 | 92
|  |  | 2021-01-18 | 128
|  |  | 2021-10-11 | 113
96 | 153701104 | LINCOLN 1104 | 2019-10-09 | 37676 | · 2.6 OH hardening miles completed in 2023; 2 OH hardening miles in scope for 2025; | 23,107 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 4655 | · 8.7 miles undergrounded in 2023; 2.2 miles undergrounded in 2024;
|  |  | 2019-10-26 | 55247 | · 2 Sectionalizing devices added or replaced;
97 | 103142102 | LOGAN CREEK 2102 | 2019-10-09 | 24078 | · 1 Sectionalizing device added or replaced; | 5,650 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 421
|  |  | 2019-11-20 | 67
|  |  | 2020-10-25 | 253
|  |  | 2021-08-17 | 184
|  |  | 2021-10-11 | 241
|  |  | 2023-08-30 | 118
|  |  | 2024-09-30 | 497
|  |  | 2024-10-17 | 3978
|  |  | 2024-11-05 | 2647
98 | 192411101 | LOW GAP 1101 | 2019-10-09 | 13584 | · 2.5 OH hardening miles completed in 2020; | 12,571 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 34489 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-09-07 | 25309
|  |  | 2020-10-14 | 4107
|  |  | 2020-10-25 | 14781
99 | 43351103 | LUCERNE 1103 | 2019-10-09 | 125809 | · 0.9 OH hardening miles in scope for 2025; | 97,476 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 22
|  |  | 2019-10-26 | 195495
|  |  | 2020-10-25 | 68577
100 | 63172101 | MADISON 2101 | 2019-10-09 | 31941 | · 1 MSO device(s) replaced; | 15,208 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 30755 | · 10 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 8857
|  |  | 2020-10-14 | 423
|  |  | 2020-10-21 | 72
|  |  | 2020-10-25 | 246
|  |  | 2021-08-17 | 5219
|  |  | 2021-09-20 | 93
|  |  | 2021-10-11 | 7927
|  |  | 2023-08-30 | 260
|  |  | 2024-07-02 | 1853
|  |  | 2024-10-17 | 843
|  |  | 2024-11-05 | 9346
101 | 163011101 | MARTELL 1101 | 2019-10-09 | 96151 | · 0.1 OH hardening miles completed in 2019; | 60,390 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 15164 | · 10 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 111440
|  |  | 2020-10-25 | 18805
102 | 62881105 | MAXWELL 1105 | 2019-10-09 | 1777 | · Mitigated by PSPS Protocols; | 1,502 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 2073
|  |  | 2020-10-25 | 1412
|  |  | 2021-08-17 | 1028
|  |  | 2021-09-20 | 517
|  |  | 2021-10-11 | 1511
|  |  | 2023-08-30 | 606
|  |  | 2024-10-17 | 2545
|  |  | 2024-11-05 | 1900
103 | 43141101 | MIDDLETOWN 1101 | 2019-10-09 | 119475 | · 5.2 OH hardening miles completed in 2019; 0.4 OH hardening miles completed in 2021; 13.6 OH hardening miles completed in 2022; 0.3 OH hardening miles completed in 2023; 5.5 OH hardening miles in scope for 2025; 4.1 OH hardening miles in scope for 2026; 4.4 OH hardening miles in scope for 2027; | 88,163 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 10976 | · 3.2 miles undergrounded in 2022; 6.2 miles undergrounded in 2023; 0.9 miles undergrounded in 2024; 2.1 miles in scope for undergrounding in 2025; 6.4 miles in scope for undergrounding in 2026; 9.2 miles in scope for undergrounding in 2027;
|  |  | 2019-10-26 | 192974 | · 8 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 53955 | · Mitigated by Temporary Generation;
|  |  | 2020-09-07 | 3056
|  |  | 2020-09-27 | 1884
|  |  | 2020-10-14 | 2662
|  |  | 2020-10-25 | 91395
|  |  | 2021-08-17 | 31680
|  |  | 2021-10-11 | 16100
|  |  | 2024-07-02 | 3087
|  |  | 2024-10-17 | 17420
|  |  | 2024-11-05 | 11547
104 | 43141102 | MIDDLETOWN 1102 | 2019-10-09 | 115134 | · 1.1 OH hardening miles completed in 2022; 0.7 OH hardening miles in scope for 2026; 1.4 OH hardening miles in scope for 2027; | 104,636 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 222958 | · 0.6 miles undergrounded in 2022; 2 miles in scope for undergrounding in 2027;
|  |  | 2019-11-20 | 50112 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-10-25 | 109871 | · 2 customers mitigated by Temporary Generation;
|  |  | 2021-08-17 | 15041
|  |  | 2021-10-11 | 72178
105 | 43141103 | MIDDLETOWN 1103 | 2019-10-09 | 9151 | · 1.4 OH hardening miles completed in 2021; 5.7 OH hardening miles completed in 2022; 3.8 OH hardening miles completed in 2023; | No customer hours decline of PSPS per year
|  |  | 2019-10-26 | 14150 | · 6.8 miles undergrounded in 2022; 4.1 miles undergrounded in 2023;
|  |  | 2019-11-20 | 4113
|  |  | 2020-10-25 | 6986
|  |  | 2021-10-11 | 158
|  |  | 2024-11-05 | 284
106 | 43302103 | MONROE 2103 | 2019-10-09 | 7444 | · 1 Sectionalizing device added or replaced; | No customer hours decline of PSPS per year
|  |  | 2019-10-23 | 257
|  |  | 2019-10-26 | 797
107 | 43302107 | MONROE 2107 | 2019-10-09 | 97063 | · 1 Sectionalizing device added or replaced; | 24,208 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 2357
|  |  | 2019-10-26 | 5464
108 | 43051101 | MONTICELLO 1101 | 2019-06-08 | 15175 | · 27.3 OH hardening miles completed in 2020; 5.7 OH hardening miles in scope for 2026; | 48,639 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 201 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-10-09 | 70868
|  |  | 2019-10-23 | 759
|  |  | 2019-10-26 | 141652
|  |  | 2019-11-20 | 39735
|  |  | 2020-10-14 | 22000
|  |  | 2020-10-25 | 50212
|  |  | 2021-08-17 | 20845
|  |  | 2021-09-20 | 62
|  |  | 2021-10-11 | 38041
|  |  | 2024-07-02 | 105
|  |  | 2024-10-17 | 21954
|  |  | 2024-11-05 | 49908
109 | 152282101 | MOUNTAIN QUARRIES 2101 | 2019-10-09 | 210483 | · •1.7 OH hardening miles completed in 2021; 0 OH hardening miles completed in 2022; 0.1 OH hardening miles completed in 2023; 18.5 OH hardening miles completed in 2024; 29.1 OH hardening miles in scope for 2025; | 133,472 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 56223 | · 3.1 miles undergrounded in 2022; 4.1 miles undergrounded in 2023; 0.5 miles undergrounded in 2024; 2 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 307894
|  |  | 2020-09-07 | 65716
|  |  | 2020-09-27 | 4625
|  |  | 2020-10-25 | 83968
110 | 153132101 | NARROWS 2101 | 2019-09-23 | 9152 | · Sectionalization Planned; | 13,879 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 7011
|  |  | 2019-10-09 | 28589
|  |  | 2019-10-23 | 12304
|  |  | 2019-10-26 | 46887
|  |  | 2020-10-25 | 4787
111 | 153132102 | NARROWS 2102 | 2019-09-23 | 61626 | · 5.4 OH hardening miles in scope for 2026; | 121,649 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 49853 | · Sectionalization Planned;
|  |  | 2019-10-09 | 155311
|  |  | 2019-10-23 | 87311
|  |  | 2019-10-26 | 123474
|  |  | 2020-10-25 | 88733
112 | 153132105 | NARROWS 2105 | 2019-09-23 | 75682 | · 5 Sectionalizing devices added or replaced; | 148,144 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 54916
|  |  | 2019-10-09 | 220383
|  |  | 2019-10-23 | 127879
|  |  | 2019-10-26 | 182604
|  |  | 2020-10-25 | 110466
113 | 102041104 | NOTRE DAME 1104 | 2019-06-08 | 3590 | · 0.2 OH hardening miles completed in 2024; 3.8 OH hardening miles in scope for 2025; 6 OH hardening miles in scope for 2026; | 24,939 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 2852 | · 7.2 miles in scope for undergrounding in 2025; 5.7 miles in scope for undergrounding in 2026;
|  |  | 2019-10-05 | 3685 | · 3 Sectionalizing devices added or replaced;
|  |  | 2019-10-09 | 39448
|  |  | 2019-10-23 | 5335
|  |  | 2019-10-26 | 10107
|  |  | 2020-09-07 | 9729
|  |  | 2020-09-27 | 7287
|  |  | 2020-10-14 | 9269
|  |  | 2020-10-25 | 9671
114 | 163541102 | OLETA 1102 | 2019-10-09 | 71572 | · 3 Sectionalizing devices added or replaced; | 32,399 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 11976
|  |  | 2019-10-26 | 63854
115 | 103521103 | OREGON TRAIL 1103 | 2019-10-09 | 76936 | · 22.1 OH hardening miles completed in 2022; 20.4 OH hardening miles completed in 2023; 1.2 OH hardening miles completed in 2024; 0.2 OH hardening miles in scope for 2025; | 22,642 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 154515 | · 7.7 miles undergrounded in 2022; 0.6 miles undergrounded in 2023; 10.1 miles undergrounded in 2024; 4.3 miles in scope for undergrounding in 2025;
|  |  | 2019-11-20 | 3434
|  |  | 2020-10-14 | 9625
|  |  | 2020-10-21 | 52053
|  |  | 2020-10-25 | 65110
|  |  | 2021-08-17 | 45290
116 | 103521104 | OREGON TRAIL 1104 | 2019-10-09 | 59532 | · Mitigated by PSPS Protocols; | No customer hours decline of PSPS per year
|  |  | 2019-10-26 | 49718
|  |  | 2019-11-20 | 577
|  |  | 2020-10-21 | 19029
|  |  | 2020-10-25 | 29881
|  |  | 2021-08-17 | 8477
117 | 103031101 | ORO FINO 1101 | 2019-06-08 | 46164 | · Mitigated by PSPS Protocols; | 155,117 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 73066
|  |  | 2019-10-05 | 33543
|  |  | 2019-10-09 | 138570
|  |  | 2019-10-23 | 59933
|  |  | 2019-10-26 | 83528
|  |  | 2020-09-07 | 91055
|  |  | 2020-09-27 | 78859
|  |  | 2020-10-14 | 115950
|  |  | 2020-10-21 | 27366
|  |  | 2020-10-25 | 111512
|  |  | 2021-08-17 | 51734
118 | 103031102 | ORO FINO 1102 | 2019-06-08 | 38971 | · 0 OH hardening miles in scope for 2025; | 152,622 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 45665 | · 8.2 miles in scope for undergrounding in 2025; 14.1 miles in scope for undergrounding in 2026;
|  |  | 2019-10-05 | 28584 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-10-09 | 118941 | · Sectionalization Planned;
|  |  | 2019-10-23 | 53928
|  |  | 2019-10-26 | 139124
|  |  | 2020-09-07 | 124091
|  |  | 2020-09-27 | 72938
|  |  | 2020-10-14 | 100001
|  |  | 2020-10-21 | 29965
|  |  | 2020-10-25 | 94365
|  |  | 2021-08-17 | 26551
|  |  | 2024-10-17 | 16100
119 | 102521104 | OROVILLE 1104 | 2019-06-08 | 15841 | · Mitigated by PSPS Protocols; | 8,105 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 16297
|  |  | 2019-10-09 | 283
120 | 103461101 | PANORAMA 1101 | 2019-10-09 | 31962 | · 1.6 miles undergrounded in 2023; | 28,510 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 20026 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 18760 | · Sectionalization Planned;
|  |  | 2020-10-21 | 17476
|  |  | 2020-10-25 | 22045
|  |  | 2021-08-17 | 20579
|  |  | 2021-10-11 | 22082
121 | 103461102 | PANORAMA 1102 | 2019-10-09 | 13706 | · 2 Sectionalizing devices added or replaced; | 9,040 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 20047 | · Sectionalization Planned;
|  |  | 2019-11-20 | 5314
|  |  | 2020-10-14 | 1398
|  |  | 2020-10-21 | 938
|  |  | 2020-10-25 | 2441
|  |  | 2021-08-17 | 547
|  |  | 2021-10-11 | 3372
122 | 102831103 | PARADISE 1103 | 2019-06-08 | 11860 | · 0.5 OH hardening miles completed in 2019; | 12,459 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 10515 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-10-05 | 10503
|  |  | 2019-10-09 | 49180
|  |  | 2019-10-23 | 23305
|  |  | 2019-10-26 | 79090
|  |  | 2020-09-07 | 2695
|  |  | 2020-09-27 | 8216
|  |  | 2020-10-14 | 11217
|  |  | 2020-10-21 | 3046
|  |  | 2020-10-25 | 22109
123 | 102831104 | PARADISE 1104 | 2019-06-08 | 10921 | · 7.1 OH hardening miles completed in 2019; 0.1 OH hardening miles completed in 2023; | 32,887 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 12119 | · 2.3 miles undergrounded in 2023; 0.1 miles undergrounded in 2024;
|  |  | 2019-10-05 | 10764
|  |  | 2019-10-09 | 46912
|  |  | 2019-10-23 | 19879
|  |  | 2019-10-26 | 76543
|  |  | 2020-09-07 | 76292
|  |  | 2020-09-27 | 61405
|  |  | 2020-10-14 | 82377
|  |  | 2020-10-21 | 21273
|  |  | 2020-10-25 | 85835
|  |  | 2021-08-17 | 23513
124 | 102831105 | PARADISE 1105 | 2019-09-25 | 16366 | · 3.2 OH hardening miles completed in 2019; | 31,552 fewer customer hours of PSPS per year
|  |  | 2019-10-05 | 14620 | · Mitigated by Temporary Generation;
|  |  | 2019-10-09 | 60859
|  |  | 2019-10-23 | 26002
|  |  | 2019-10-26 | 94065
|  |  | 2020-09-07 | 57899
|  |  | 2020-09-27 | 46551
|  |  | 2020-10-14 | 58435
|  |  | 2020-10-21 | 15916
|  |  | 2020-10-25 | 61012
|  |  | 2021-08-17 | 16111
|  |  | 2024-10-17 | 849
125 | 102831106 | PARADISE 1106 | 2019-09-25 | 3113 | · 0.9 OH hardening miles completed in 2019; | 22,672 fewer customer hours of PSPS per year
|  |  | 2019-10-05 | 3550
|  |  | 2019-10-09 | 16542
|  |  | 2019-10-23 | 6832
|  |  | 2019-10-26 | 26596
|  |  | 2020-09-07 | 15584
|  |  | 2020-09-27 | 13721
|  |  | 2020-10-14 | 17635
|  |  | 2020-10-21 | 4892
|  |  | 2020-10-25 | 12527
|  |  | 2021-08-17 | 1952
126 | 152201101 | PIKE CITY 1101 | 2019-10-09 | 24785 | · 2.7 OH hardening miles in scope for 2026; | 20,662 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 18434 | · 29.7 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 44172 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-09-07 | 16344
|  |  | 2020-09-27 | 7968
|  |  | 2020-10-25 | 27124
127 | 152201102 | PIKE CITY 1102 | 2019-10-09 | 1916 | · Mitigated by PSPS Protocols; | 1,572 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 1097
|  |  | 2019-10-26 | 2878
|  |  | 2020-09-07 | 1540
|  |  | 2020-09-27 | 471
|  |  | 2020-10-25 | 1664
128 | 163751101 | PINE GROVE 1101 | 2019-10-09 | 65466 | · Mitigated by PSPS Protocols; | 41,151 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 30860
|  |  | 2019-10-26 | 76816
|  |  | 2020-10-25 | 27896
129 | 163751102 | PINE GROVE 1102 | 2019-10-09 | 281441 | · 2.9 OH hardening miles completed in 2019; 5.3 OH hardening miles completed in 2020; 4.6 OH hardening miles completed in 2021; 1.3 OH hardening miles completed in 2022; 0.1 OH hardening miles completed in 2023; | 138,364 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 94715 | · 0 miles undergrounded in 2022; 0.1 miles undergrounded in 2023;
|  |  | 2019-10-26 | 260315 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-09-07 | 127452 | · Mitigated by Temporary Generation;
|  |  | 2020-09-27 | 60831
|  |  | 2020-10-25 | 98330
130 | 103732101 | PIT NO 3 2101 | 2020-09-07 | 5183 | · 0.1 OH hardening miles completed in 2024; | 2,206 fewer customer hours of PSPS per year
|  |  | 2020-10-21 | 932 | · 5.8 miles in scope for undergrounding in 2025;
|  |  | 2020-10-25 | 5817
|  |  | 2024-09-30 | 679
131 | 103501101 | PIT NO 7 1101 | 2019-10-09 | 141 | · Mitigated by PSPS Protocols; | 125 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 229
|  |  | 2020-09-07 | 75
|  |  | 2020-10-14 | 86
|  |  | 2020-10-21 | 82
|  |  | 2020-10-25 | 93
|  |  | 2021-08-17 | 56
132 | 153081109 | PLACERVILLE 1109 | 2019-10-09 | 34760 | · 1 Sectionalizing device added or replaced; | 26,100 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 20894 | · Mitigated by Temporary Generation;
|  |  | 2019-10-26 | 44463
|  |  | 2020-09-07 | 18633
|  |  | 2020-09-27 | 8804
|  |  | 2020-10-25 | 25952
133 | 153081110 | PLACERVILLE 1110 | 2019-10-09 | 67339 | · 5 Sectionalizing devices added or replaced; | 48,644 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 14605 | · Mitigated by Temporary Generation;
|  |  | 2019-10-26 | 102478
|  |  | 2020-09-27 | 19866
|  |  | 2020-10-25 | 75968
134 | 153081111 | PLACERVILLE 1111 | 2019-10-09 | 40560 | · 10 Sectionalizing devices added or replaced; | 40,806 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 25424 | · Mitigated by Temporary Generation;
|  |  | 2019-10-26 | 36729
|  |  | 2020-09-07 | 34246
|  |  | 2020-09-27 | 17175
|  |  | 2020-10-25 | 51763
135 | 153081112 | PLACERVILLE 1112 | 2019-10-09 | 79290 | · 8.1 OH hardening miles in scope for 2025; | 89,043 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 52922 | · 0.1 miles undergrounded in 2022; 5.9 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 113225 | · 6 Sectionalizing devices added or replaced;
|  |  | 2020-09-07 | 73668 | · Mitigated by Temporary Generation;
|  |  | 2020-09-27 | 38641
|  |  | 2020-10-25 | 99600
136 | 153082106 | PLACERVILLE 2106 | 2019-10-09 | 292538 | · 12.6 OH hardening miles in scope for 2025; 12.6 OH hardening miles in scope for 2026; | 226,274 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 138898 | · 0.2 miles undergrounded in 2022; 1.3 miles undergrounded in 2023; 1 miles undergrounded in 2024; 19.1 miles in scope for undergrounding in 2025; 45.8 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 373230 | · 11 Sectionalizing devices added or replaced;
|  |  | 2020-09-07 | 187716 | · Mitigated by Temporary Generation;
|  |  | 2020-09-27 | 101250
|  |  | 2020-10-25 | 289522
137 | 42281105 | POTTER VALLEY P H 1105 | 2019-10-09 | 47006 | · 1.6 OH hardening miles completed in 2022; 7.8 OH hardening miles completed in 2023; 21.1 OH hardening miles in scope for 2025; 0.8 OH hardening miles in scope for 2026; | 26,109 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 1665 | · 0.1 miles undergrounded in 2022; 1.9 miles undergrounded in 2023; 2.2 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 75247 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-10-25 | 3859 | · Sectionalization Planned;
138 | 43291104 | PUEBLO 1104 | 2019-10-09 | 99885 | · 2 Sectionalizing devices added or replaced; | 14,902 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 56010
|  |  | 2019-11-20 | 16166
|  |  | 2020-10-14 | 12631
|  |  | 2020-10-25 | 12594
|  |  | 2021-08-17 | 4644
|  |  | 2021-10-11 | 1111
|  |  | 2024-10-17 | 1592
|  |  | 2024-11-05 | 10087
139 | 43291105 | PUEBLO 1105 | 2019-10-09 | 104599 | · 1.3 OH hardening miles completed in 2019; | 21,888 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 44964 | · 4 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 7906
|  |  | 2020-10-14 | 20463
|  |  | 2020-10-25 | 22802
|  |  | 2021-08-17 | 2399
|  |  | 2021-10-11 | 3549
|  |  | 2024-10-17 | 4227
|  |  | 2024-11-05 | 5287
140 | 43292102 | PUEBLO 2102 | 2019-10-09 | 21951 | · 2 OH hardening miles completed in 2021; | No customer hours decline of PSPS per year
|  |  | 2019-10-23 | 2194 | · 10 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 35771
|  |  | 2019-11-20 | 6560
|  |  | 2020-09-07 | 1289
|  |  | 2020-10-14 | 3271
|  |  | 2020-10-25 | 19136
|  |  | 2021-08-17 | 1575
|  |  | 2024-10-17 | 3324
|  |  | 2024-11-05 | 6766
141 | 43292103 | PUEBLO 2103 | 2019-10-09 | 212204 | · 6 Sectionalizing devices added or replaced; | 824 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 4343
|  |  | 2019-10-26 | 71413
|  |  | 2019-11-20 | 5394
|  |  | 2020-09-07 | 843
|  |  | 2020-10-14 | 1688
|  |  | 2020-10-25 | 28961
|  |  | 2021-08-17 | 5218
|  |  | 2024-10-17 | 10822
|  |  | 2024-11-05 | 20216
142 | 63681102 | PUTAH CREEK 1102 | 2019-06-08 | 3151 | · 26.6 OH hardening miles completed in 2022; 1.7 OH hardening miles completed in 2023; | 10,254 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 25239 | · 0.4 miles undergrounded in 2022;
|  |  | 2019-10-26 | 30475 | · 2 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 228
|  |  | 2020-10-25 | 4573
|  |  | 2021-08-17 | 2775
|  |  | 2021-10-11 | 9251
|  |  | 2024-07-02 | 4353
|  |  | 2024-10-17 | 11946
|  |  | 2024-11-05 | 9103
143 | 63681105 | PUTAH CREEK 1105 | 2019-10-09 | 15722 | · 3 Sectionalizing devices added or replaced; | 4,161 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 3874
|  |  | 2021-08-17 | 200
|  |  | 2021-09-20 | 81
|  |  | 2021-10-11 | 1261
|  |  | 2024-10-17 | 1541
|  |  | 2024-11-05 | 1396
144 | 103541101 | RED BLUFF 1101 | 2019-10-09 | 78442 | · 3 Sectionalizing devices added or replaced; | 34,152 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 22841
|  |  | 2019-11-20 | 15094
|  |  | 2020-10-25 | 4931
|  |  | 2021-08-17 | 27821
|  |  | 2021-10-11 | 19897
|  |  | 2024-10-17 | 1844
145 | 103541103 | RED BLUFF 1103 | 2019-10-09 | 120138 | · Sectionalization Planned; | 22,868 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 5487
|  |  | 2019-11-20 | 5766
|  |  | 2021-08-17 | 5828
|  |  | 2021-10-11 | 5344
|  |  | 2024-10-17 | 4396
146 | 103541104 | RED BLUFF 1104 | 2019-10-09 | 79713 | · 2 Sectionalizing devices added or replaced; | 41,978 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 32177
|  |  | 2019-11-20 | 24361
|  |  | 2021-08-17 | 35844
|  |  | 2021-10-11 | 26074
147 | 103541105 | RED BLUFF 1105 | 2019-10-09 | 98920 | · 1 Sectionalizing device added or replaced; | 42,563 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 23248
|  |  | 2019-11-20 | 23444
|  |  | 2021-08-17 | 40861
|  |  | 2024-10-17 | 6473
148 | 43191101 | REDBUD 1101 | 2019-10-09 | 107092 | · 1.4 OH hardening miles completed in 2019; 1.3 OH hardening miles completed in 2023; 0.3 OH hardening miles completed in 2024; 0.7 OH hardening miles in scope for 2025; | 35,819 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 185303 | · 4.9 miles undergrounded in 2023; 26.8 miles undergrounded in 2024; 7.7 miles in scope for undergrounding in 2025; 1.1 miles in scope for undergrounding in 2026;
|  |  | 2019-11-20 | 252 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-10-25 | 54800
|  |  | 2021-08-17 | 13921
|  |  | 2021-10-11 | 3578
|  |  | 2024-10-17 | 25454
|  |  | 2024-11-05 | 18946
149 | 43321101 | RINCON 1101 | 2019-10-09 | 174633 | · 5 Sectionalizing devices added or replaced; | 77,036 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 101866 | · Sectionalization Planned;
|  |  | 2019-10-26 | 350862
|  |  | 2019-11-20 | 59829
|  |  | 2020-09-07 | 113221
|  |  | 2020-10-25 | 78293
|  |  | 2021-08-17 | 433
|  |  | 2024-10-17 | 1840
|  |  | 2024-11-05 | 1743
150 | 43321102 | RINCON 1102 | 2019-10-09 | 190276 | · 1 Sectionalizing device added or replaced; | 82,038 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 116908
|  |  | 2019-10-26 | 426715
|  |  | 2020-09-07 | 137932
151 | 43321103 | RINCON 1103 | 2019-09-25 | 1632 | · 0.2 OH hardening miles completed in 2019; 0.3 OH hardening miles completed in 2022; 0.1 OH hardening miles completed in 2023; | 41,693 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 87646 | · 1.5 miles undergrounded in 2021;
|  |  | 2019-10-23 | 55916 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-10-26 | 187249
|  |  | 2019-11-20 | 55906
|  |  | 2020-09-07 | 62907
|  |  | 2020-10-14 | 806
|  |  | 2020-10-25 | 9507
|  |  | 2021-08-17 | 4534
|  |  | 2024-10-17 | 480
|  |  | 2024-11-05 | 12576
152 | 43321104 | RINCON 1104 | 2019-10-09 | 231090 | · 0.1 OH hardening miles completed in 2022; | 68,820 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 95919 | · 1.3 miles undergrounded in 2021;
|  |  | 2019-10-26 | 364319 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-09-07 | 74824
153 | 163692101 | SALT SPRINGS 2101 | 2019-10-09 | 9696 | · Mitigated by PSPS Protocols; | 18,259 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 10224
|  |  | 2019-10-26 | 36349
|  |  | 2020-09-07 | 16302
|  |  | 2020-09-27 | 7543
|  |  | 2020-10-25 | 18928
154 | 163692102 | SALT SPRINGS 2102 | 2019-10-09 | 95826 | · 1.2 OH hardening miles completed in 2020; 0.1 OH hardening miles completed in 2021; | 118,024 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 55614 | · 1 MSO device(s) replaced;
|  |  | 2019-10-26 | 192633
|  |  | 2020-09-07 | 80926
|  |  | 2020-09-27 | 36899
|  |  | 2020-10-25 | 96954
155 | 42151104 | SANTA ROSA A 1104 | 2019-10-09 | 158923 | · 1 MSO device(s) replaced; | 85,793 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 58181 | · 3 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 229380
|  |  | 2019-11-20 | 10949
|  |  | 2020-09-07 | 14763
|  |  | 2020-10-25 | 21428
156 | 258131101 | SCE TEHACHAPI 1101 | 2020-12-03 | 66 | · Mitigated by PSPS Protocols; | 60 fewer customer hours of PSPS per year
|  |  | 2021-01-18 | 91
|  |  | 2021-09-20 | 43
|  |  | 2021-10-14 | 39
157 | 152431101 | SHADY GLEN 1101 | 2019-10-09 | 108135 | · 1.4 OH hardening miles completed in 2021; 1.5 OH hardening miles in scope for 2025; 2.6 OH hardening miles in scope for 2026; | 26,833 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 46852 | · 0.1 miles undergrounded in 2021; 3.2 miles undergrounded in 2022; 4.6 miles in scope for undergrounding in 2025; 10 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 72725
|  |  | 2020-09-07 | 851
|  |  | 2020-10-25 | 54136
158 | 152431102 | SHADY GLEN 1102 | 2019-10-09 | 45382 | · 1.5 OH hardening miles completed in 2019; 2.4 OH hardening miles in scope for 2026; | 20,064 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 18186 | · 37.4 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 74269 | · Sectionalization Planned;
|  |  | 2020-09-07 | 28507
|  |  | 2020-09-27 | 8212
|  |  | 2020-10-25 | 31937
159 | 153652109 | SHINGLE SPRINGS 2109 | 2019-10-09 | 203534 | · 0.8 OH hardening miles completed in 2021; 18.3 OH hardening miles completed in 2022; 2.6 OH hardening miles completed in 2023; | 86,342 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 13687 | · 6.6 miles undergrounded in 2022; 4.1 miles undergrounded in 2023;
|  |  | 2019-10-26 | 168349 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-10-25 | 37212
160 | 43432102 | SILVERADO 2102 | 2019-10-09 | 81486 | · 1.3 OH hardening miles completed in 2021; 2.2 OH hardening miles completed in 2022; | 15,574 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 20873 | · 2 MSO device(s) replaced;
|  |  | 2019-10-26 | 63424 | · 8 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 30136
|  |  | 2020-09-07 | 13039
|  |  | 2020-10-14 | 31679
|  |  | 2020-10-25 | 28127
|  |  | 2021-08-17 | 3287
|  |  | 2021-10-11 | 11341
|  |  | 2024-10-17 | 15251
|  |  | 2024-11-05 | 15577
161 | 43432103 | SILVERADO 2103 | 2019-10-09 | 41574 | · 6 Sectionalizing devices added or replaced; | No customer hours decline of PSPS per year
|  |  | 2019-10-23 | 344
|  |  | 2019-10-26 | 37376
|  |  | 2019-11-20 | 8867
|  |  | 2020-09-07 | 90
|  |  | 2020-10-25 | 15350
|  |  | 2021-08-17 | 63
|  |  | 2024-10-17 | 542
|  |  | 2024-11-05 | 587
162 | 43432104 | SILVERADO 2104 | 2019-10-09 | 156415 | · 6.2 OH hardening miles completed in 2019; 3.5 OH hardening miles completed in 2020; 1.5 OH hardening miles completed in 2021; 1.9 OH hardening miles completed in 2022; 3.7 OH hardening miles in scope for 2026; | 534 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 55229 | · 1 miles undergrounded in 2019; 5.3 miles undergrounded in 2022; 41.1 miles in scope for undergrounding in 2025; 21.8 miles in scope for undergrounding in 2026; 19.9 miles in scope for undergrounding in 2028
|  |  | 2019-10-26 | 141810 | · 11 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 69542 | · Mitigated by Temporary Generation;
|  |  | 2020-09-07 | 98486
|  |  | 2020-10-14 | 50863
|  |  | 2020-10-25 | 107917
|  |  | 2021-08-17 | 39184
|  |  | 2021-10-11 | 27161
|  |  | 2024-10-17 | 97343
|  |  | 2024-11-05 | 71955
163 | 43432105 | SILVERADO 2105 | 2019-10-09 | 113765 | · 3.4 OH hardening miles completed in 2019; 1.8 OH hardening miles completed in 2020; 0.7 OH hardening miles completed in 2022; 6.8 OH hardening miles in scope for 2025; 4.3 OH hardening miles in scope for 2026; | No customer hours decline of PSPS per year
|  |  | 2019-10-23 | 7866 | · 0.2 miles undergrounded in 2023; 4.4 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 65419 | · 16 Sectionalizing devices added or replaced;
|  |  | 2019-11-20 | 26518
|  |  | 2020-09-07 | 6489
|  |  | 2020-10-14 | 7837
|  |  | 2020-10-25 | 22496
|  |  | 2024-10-17 | 900
|  |  | 2024-11-05 | 607
164 | 153791101 | SMARTVILLE 1101 | 2019-09-23 | 4063 | · Mitigated by PSPS Protocols; | 11,936 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 3009
|  |  | 2019-10-09 | 11624
|  |  | 2019-10-23 | 5886
|  |  | 2019-10-26 | 23163
165 | 42721102 | SONOMA 1102 | 2019-10-09 | 147903 | · 2 Sectionalizing devices added or replaced; | 40,523 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 7601
|  |  | 2019-10-26 | 11133
|  |  | 2020-10-14 | 4728
|  |  | 2020-10-25 | 7953
|  |  | 2024-10-17 | 4273
|  |  | 2024-11-05 | 4250
166 | 42721103 | SONOMA 1103 | 2019-10-09 | 100464 | · 3 Sectionalizing devices added or replaced; | 25,067 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 8206
|  |  | 2019-10-26 | 14206
|  |  | 2020-10-14 | 12995
|  |  | 2020-10-25 | 14360
|  |  | 2021-08-17 | 644
|  |  | 2024-10-17 | 5184
|  |  | 2024-11-05 | 5378
167 | 42721106 | SONOMA 1106 | 2019-10-09 | 119347 | · 2 Sectionalizing devices added or replaced; | 34,080 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 4116
|  |  | 2019-10-26 | 6094
|  |  | 2020-10-14 | 4020
|  |  | 2020-10-25 | 4018
|  |  | 2024-10-17 | 314
|  |  | 2024-11-05 | 294
168 | 152251101 | SPAULDING 1101 | 2019-10-09 | 12740 | · Mitigated by PSPS Protocols; | 7,648 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 17933
|  |  | 2020-09-07 | 6259
|  |  | 2020-09-27 | 1395
|  |  | 2020-10-25 | 8308
169 | 162821701 | STANISLAUS 1701 | 2019-10-09 | 73947 | · 3.8 OH hardening miles completed in 2023; 18.2 OH hardening miles in scope for 2025; 8.6 OH hardening miles in scope for 2026; 1.8 OH hardening miles in scope for 2027; | 94,855 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 45372 | · 4.1 miles undergrounded in 2023; 3.4 miles in scope for undergrounding in 2025; 14.9 miles in scope for undergrounding in 2026; 9.4 miles in scope for undergrounding in 2027;
|  |  | 2019-10-26 | 149345
|  |  | 2020-09-07 | 95359
|  |  | 2020-10-25 | 79059
170 | 162821702 | STANISLAUS 1702 | 2019-10-09 | 121951 | · 1.5 OH hardening miles completed in 2022; 3.6 OH hardening miles completed in 2023; 0.1 OH hardening miles completed in 2024; 0.2 OH hardening miles in scope for 2025; | 165,955 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 113080 | · 0.1 miles undergrounded in 2022; 9.8 miles undergrounded in 2023; 2.6 miles undergrounded in 2024; 9.3 miles in scope for undergrounding in 2025; 10.7 miles in scope for undergrounding in 2026;
|  |  | 2019-10-26 | 413871 | · 1 MSO device(s) replaced;
|  |  | 2020-09-07 | 185912
|  |  | 2020-10-25 | 221223
171 | 103561101 | STILLWATER 1101 | 2019-10-09 | 42184 | · 1.7 OH hardening miles completed in 2021; 0.1 OH hardening miles completed in 2022; | No customer hours decline of PSPS per year
|  |  | 2019-10-26 | 33778
|  |  | 2020-10-14 | 1502
|  |  | 2020-10-21 | 11475
|  |  | 2020-10-25 | 19870
|  |  | 2021-08-17 | 20058
|  |  | 2024-09-30 | 5724
|  |  | 2024-10-17 | 28699
172 | 103561102 | STILLWATER 1102 | 2019-10-09 | 72898 | · 2.8 OH hardening miles completed in 2021; | 9,045 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 73134
|  |  | 2020-10-14 | 31542
|  |  | 2020-10-21 | 22027
|  |  | 2020-10-25 | 50313
|  |  | 2021-08-17 | 60790
|  |  | 2024-09-30 | 12522
|  |  | 2024-10-17 | 33975
173 | 102971111 | SYCAMORE CREEK 1111 | 2019-10-05 | 7593 | · 8.2 OH hardening miles completed in 2024; | 38,540 fewer customer hours of PSPS per year
|  |  | 2019-10-09 | 48050 | · 20.5 miles in scope for undergrounding in 2025; 6.8 miles in scope for undergrounding in 2026;
|  |  | 2019-10-23 | 14581 | · 3 Sectionalizing devices added or replaced;
|  |  | 2019-10-26 | 28042
|  |  | 2020-09-27 | 16637
|  |  | 2020-10-14 | 23580
|  |  | 2020-10-25 | 25120
|  |  | 2021-10-11 | 19812
174 | 252931102 | TEJON 1102 | 2019-10-09 | 18827 | · 5 miles undergrounded in 2024; 11 miles in scope for undergrounding in 2025; 10.3 miles in scope for undergrounding in 2026; | 5,428 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 24746 | · Mitigated by Temporary Generation;
|  |  | 2020-09-07 | 12121
|  |  | 2020-12-03 | 12445
|  |  | 2021-09-20 | 10941
|  |  | 2021-10-11 | 16676
|  |  | 2021-10-14 | 9563
|  |  | 2024-11-05 | 16468
175 | 252931103 | TEJON 1103 | 2019-10-09 | 571 | · 1 Sectionalizing device added or replaced; | 663 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 550
|  |  | 2019-10-26 | 627
|  |  | 2020-09-07 | 276
|  |  | 2020-12-03 | 37
|  |  | 2021-01-18 | 51
|  |  | 2021-10-11 | 335
|  |  | 2021-10-14 | 207
176 | 161380201 | TIGER CREEK 0201 | 2019-10-09 | 333 | · 4.3 miles in scope for undergrounding in 2026; | 485 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 277 | 1 Sectionalizing device added or replaced;
|  |  | 2019-10-26 | 1238
|  |  | 2020-09-07 | 465
|  |  | 2020-09-27 | 242
|  |  | 2020-10-25 | 640
177 | 103571105 | TYLER 1105 | 2019-10-09 | 81905 | · 2 Sectionalizing devices added or replaced; | 45,828 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 77505
|  |  | 2019-11-20 | 11540
|  |  | 2020-10-25 | 6067
|  |  | 2021-08-17 | 17215
|  |  | 2021-09-20 | 2412
|  |  | 2021-10-11 | 13023
|  |  | 2024-10-17 | 13814
178 | 42871101 | UPPER LAKE 1101 | 2019-10-09 | 72814 | · 0.4 OH hardening miles completed in 2019; 1.1 OH hardening miles completed in 2022; 0.2 OH hardening miles completed in 2023; 1.4 OH hardening miles completed in 2024; 4.7 OH hardening miles in scope for 2025; 0.6 OH hardening miles in scope for 2026; 1.5 OH hardening miles in scope for 2027; | 52,998 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 230 | · 5.6 miles undergrounded in 2023; 0.9 miles undergrounded in 2024; 0 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 120918 | · 1 Sectionalizing device added or replaced;
|  |  | 2020-10-25 | 18030
179 | 63601104 | VACAVILLE 1104 | 2019-10-09 | 80875 | · 1.7 OH hardening miles completed in 2021; 8.2 OH hardening miles completed in 2022; 0 OH hardening miles completed in 2023; 0 OH hardening miles completed in 2024; | No customer hours decline of PSPS per year
|  |  | 2019-10-26 | 137659 | · 2.7 miles undergrounded in 2022; 1.5 miles undergrounded in 2023; 2 miles undergrounded in 2024; 0.2 miles in scope for undergrounding in 2025;
|  |  | 2020-10-25 | 1313 | · 2 Sectionalizing devices added or replaced;
|  |  | 2021-08-17 | 452
|  |  | 2021-09-20 | 721
|  |  | 2021-10-11 | 5280
|  |  | 2024-10-17 | 6203
|  |  | 2024-11-05 | 9416
180 | 63601108 | VACAVILLE 1108 | 2019-10-09 | 53488 | · 13.1 OH hardening miles completed in 2020; | No customer hours decline of PSPS per year
|  |  | 2019-10-26 | 32269 | · 0.4 miles undergrounded in 2024;
|  |  | 2019-11-20 | 2011 | · 1 MSO device(s) replaced;
|  |  | 2020-10-25 | 5522 | · 2 Sectionalizing devices added or replaced;
|  |  | 2021-08-17 | 6276
|  |  | 2021-09-20 | 371
|  |  | 2021-10-11 | 10092
|  |  | 2024-07-02 | 1342
|  |  | 2024-10-17 | 39287
|  |  | 2024-11-05 | 34685
181 | 13751102 | VASCO 1102 | 2019-10-26 | 18197 | · 2 Sectionalizing devices added or replaced; | 6,559 fewer customer hours of PSPS per year
|  |  | 2020-10-25 | 7744
|  |  | 2021-10-11 | 4068
|  |  | 2024-07-20 | 69
|  |  | 2024-10-17 | 8265
|  |  | 2024-11-05 | 4209
182 | 102541101 | VOLTA 1101 | 2019-10-09 | 98284 | · 37 OH hardening miles completed in 2022; 4 OH hardening miles completed in 2023; 7.6 OH hardening miles completed in 2024; | 70,614 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 23077 | · 3.7 miles undergrounded in 2022; 2 miles undergrounded in 2023; 0.5 miles in scope for underground in 2028
|  |  | 2019-10-26 | 121646 | · Mitigated by Temporary Generation;
|  |  | 2019-11-20 | 38140
|  |  | 2020-09-07 | 51351
|  |  | 2020-09-27 | 25032
|  |  | 2020-10-14 | 56698
|  |  | 2020-10-25 | 53642
|  |  | 2021-08-17 | 48059
|  |  | 2021-10-11 | 18504
|  |  | 2024-10-17 | 321
183 | 102541102 | VOLTA 1102 | 2019-10-09 | 153174 | · 9.3 OH hardening miles completed in 2019; 26.2 OH hardening miles completed in 2020; | 204,768 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 283684 | · Mitigated by Temporary Generation;
|  |  | 2019-11-20 | 72933
|  |  | 2020-09-07 | 108020
|  |  | 2020-09-27 | 42145
|  |  | 2020-10-14 | 111580
|  |  | 2020-10-25 | 92283
|  |  | 2021-08-17 | 105499
184 | 152491101 | WEIMAR 1101 | 2019-10-09 | 97087 | · 0.6 OH hardening miles completed in 2019; | 8,395 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 36718
|  |  | 2019-10-26 | 74319
|  |  | 2020-09-07 | 1100
|  |  | 2020-10-25 | 47995
185 | 152491102 | WEIMAR 1102 | 2019-10-09 | 31898 | · Mitigated by PSPS Protocols; | 5,115 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 13950
|  |  | 2019-10-26 | 28953
|  |  | 2020-10-25 | 27282
186 | 163201101 | WEST POINT 1101 | 2019-10-09 | 110847 | · 4.3 OH hardening miles completed in 2020; | 83,618 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 41286 | · 12.6 miles in scope for undergrounding in 2025; 4 miles in scope for undergrounding in 2026; 3.6 miles in scope for undergrounding in 2027;
|  |  | 2019-10-26 | 162372
|  |  | 2020-09-07 | 63404
|  |  | 2020-09-27 | 31632
|  |  | 2020-10-25 | 80011
187 | 163201102 | WEST POINT 1102 | 2019-10-09 | 210745 | · 0.7 OH hardening miles in scope for 2025; 4.6 OH hardening miles in scope for 2026; | 139,248 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 68381 | · 3.5 miles undergrounded in 2024; 10.6 miles in scope for undergrounding in 2025; 3.5 miles in scope for undergrounding in 2026; 3.4 miles in scope for undergrounding in 2028
|  |  | 2019-10-26 | 240224 | · 7 Sectionalizing devices added or replaced;
|  |  | 2020-09-07 | 106168
|  |  | 2020-09-27 | 52062
|  |  | 2020-10-25 | 128078
188 | 152811105 | WHEATLAND 1105 | 2019-10-09 | 10611 | · 1 Sectionalizing device added or replaced; | 7,068 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 4633
|  |  | 2019-10-26 | 13026
189 | 103601101 | WHITMORE 1101 | 2019-10-09 | 33670 | · 2 Sectionalizing devices added or replaced; | 11,979 fewer customer hours of PSPS per year
|  |  | 2019-10-26 | 57941
|  |  | 2019-11-20 | 5653
|  |  | 2020-09-07 | 13271
|  |  | 2020-10-25 | 22208
|  |  | 2021-08-17 | 4855
|  |  | 2023-08-30 | 8663
|  |  | 2024-09-30 | 1191
190 | 152271102 | WISE 1102 | 2019-10-09 | 104144 | · Mitigated by PSPS Protocols; | 41,070 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 15696
|  |  | 2019-10-26 | 94608
191 | 24251101 | WOODSIDE 1101 | 2019-10-09 | 44030 | · 1 OH hardening miles completed in 2019; 0.2 OH hardening miles completed in 2023; | 22,927 fewer customer hours of PSPS per year
|  |  | 2019-10-23 | 4820 | · 0.5 miles undergrounded in 2023; 0.7 miles in scope for undergrounding in 2025;
|  |  | 2019-10-26 | 70922 | · 2 Sectionalizing devices added or replaced;
|  |  | 2020-10-14 | 3118
|  |  | 2020-10-25 | 26809
192 | 102911102 | WYANDOTTE 1102 | 2019-06-08 | 1796 | · Mitigated by PSPS Protocols; | 5,509 fewer customer hours of PSPS per year
|  |  | 2019-09-23 | 503
|  |  | 2019-09-25 | 460
|  |  | 2019-10-09 | 15419
|  |  | 2019-10-23 | 771
|  |  | 2019-10-26 | 3088
193 | 102911103 | WYANDOTTE 1103 | 2019-06-08 | 23663 | · 0.1 OH hardening miles completed in 2022; | 38,506 fewer customer hours of PSPS per year
|  |  | 2019-09-23 | 29842 | · 23.6 miles undergrounded in 2021; 26.8 miles undergrounded in 2022; 0.4 miles undergrounded in 2023;
|  |  | 2019-09-25 | 21022 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-10-05 | 11848
|  |  | 2019-10-09 | 99086
|  |  | 2019-10-23 | 40466
|  |  | 2019-10-26 | 79165
|  |  | 2019-11-20 | 3832
|  |  | 2020-09-07 | 0
|  |  | 2020-09-27 | 495
|  |  | 2020-10-21 | 759
|  |  | 2020-10-25 | 15213
194 | 102911105 | WYANDOTTE 1105 | 2019-09-23 | 6017 | · 9.1 OH hardening miles completed in 2023; 0.2 OH hardening miles completed in 2024; 0.1 OH hardening miles in scope for 2025; | 14,015 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 4082 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-10-05 | 4037
|  |  | 2019-10-09 | 20115
|  |  | 2019-10-23 | 8076
|  |  | 2019-10-26 | 13574
|  |  | 2020-09-07 | 9
|  |  | 2020-09-27 | 33
|  |  | 2020-10-14 | 46
|  |  | 2020-10-21 | 30
|  |  | 2020-10-25 | 44
195 | 102911106 | WYANDOTTE 1106 | 2019-06-08 | 2154 | · Mitigated by PSPS Protocols; | 11,563 fewer customer hours of PSPS per year
|  |  | 2019-09-23 | 3691
|  |  | 2019-09-25 | 2202
|  |  | 2019-10-09 | 29882
|  |  | 2019-10-23 | 202
|  |  | 2019-10-26 | 8122
196 | 102911107 | WYANDOTTE 1107 | 2019-06-08 | 32379 | · 3 Sectionalizing devices added or replaced; | 32,214 fewer customer hours of PSPS per year
|  |  | 2019-09-23 | 35533 | · Sectionalization Planned;
|  |  | 2019-09-25 | 23953
|  |  | 2019-10-09 | 123146
|  |  | 2019-10-23 | 47501
|  |  | 2019-10-26 | 110339
|  |  | 2020-09-07 | 2089
|  |  | 2020-09-27 | 12365
|  |  | 2020-10-25 | 35278
197 | 102911109 | WYANDOTTE 1109 | 2019-06-08 | 36441 | · 0.9 OH hardening miles completed in 2021; 0.1 OH hardening miles completed in 2022; 0.1 OH hardening miles completed in 2023; | 104,546 fewer customer hours of PSPS per year
|  |  | 2019-09-23 | 50854 | · 0.9 miles undergrounded in 2022;
|  |  | 2019-09-25 | 34854 | · 3 Sectionalizing devices added or replaced;
|  |  | 2019-10-09 | 157280
|  |  | 2019-10-23 | 58607
|  |  | 2019-10-26 | 102045
198 | 102911110 | WYANDOTTE 1110 | 2019-09-23 | 31411 | · 0.4 OH hardening miles completed in 2024; | 7,046 fewer customer hours of PSPS per year
|  |  | 2019-09-25 | 21961 | · 5.6 miles undergrounded in 2023; 5.3 miles undergrounded in 2024;
|  |  | 2019-10-09 | 116578 | · 1 Sectionalizing device added or replaced;
|  |  | 2019-10-23 | 43574
|  |  | 2019-10-26 | 62361
199 | ETL.6220 | BRIDGEVILLE‑GARBERVILLE 60 KV | 2019-10-26 | – | · OH Hardening Completed in 20231; OH Hardening Planned in 2025; | See Footnote(b)
|  |  | 2020-09-07 | – | · Sectionalizing Capable;
|  |  | 2020-10-14 | – | · Mitigated by Islanding;
|  |  | 2020-10-25 | – | · 1,442 Transmission Tags Completed;
· 38.1 ROW Expansion miles completed;
200 | ETL.1180 | BUTT VALLEY‑CARIBOU 115 KV | 2020-09-07 | – | · 159 Transmission Tags Completed; | See Footnote(b)
|  |  | 2020-09-27 | – | · 7.4 ROW Expansion miles completed;
|  |  | 2020-10-14 | –
|  |  | 2020-10-21 | –
|  |  | 2020-10-25 | –
201 | ETL.3190 | CARIBOU‑PALERMO 115 KV | 2019-10-09 | ‑– | · 299 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
202 | ETL.4440 | CARIBOU‑TABLE MOUNTAIN 230 KV | 2020-09-07 | – | · Mitigated by Islanding; | See Footnote(b)
|  |  | 2020-09-27 | – | · 1,389 Transmission Tags Completed;
|  |  | 2020-10-14 | – | · 9.7 ROW Expansion miles completed;
|  |  | 2020-10-21 | –
|  |  | 2020-10-25 | –
203 | ETL.6300 | CARIBOU‑WESTWOOD 60 KV | 2020-09-07 | 403 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2020-10-14 | – | · 845 Transmission Tags Completed;
|  |  | 2020-10-21 | – | · 18.7 ROW Expansion miles completed;
|  |  | 2020-10-25 | –
204 | ETL.6320 | CENTERVILLE‑TABLE MOUNTAIN 60 KV | 2019-06-08 | 137 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-09-25 | – | · 352 Transmission Tags Completed;
|  |  | 2019-10-05 | – | · 21.5 ROW Expansion miles completed;
|  |  | 2019-10-09 | –
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
205 | ETL.6330 | CENTERVILLE‑TABLE MOUNTAIN‑OROVILLE 60 KV | 2019-06-08 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-09-25 | – | · 560 Transmission Tags Completed;
|  |  | 2019-10-05 | – | · 25.6 ROW Expansion miles completed;
|  |  | 2019-10-09 | –
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
206 | ETL.6470 | COLGATE‑ALLEGHANY 60 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-23 | – | · 1,679 Transmission Tags Completed;
|  |  | 2019-10-26 | – | · 24.6 ROW Expansion miles completed;
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
207 | ETL.6480 | COLGATE‑CHALLENGE 60 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-23 | – | · 362 Transmission Tags Completed;
|  |  | 2019-10-26 | – | · 13.1 ROW Expansion miles completed;
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
208 | ETL.6490 | COLGATE‑GRASS VALLEY 60 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-23 | – | · 611 Transmission Tags Completed;
|  |  | 2019-10-26 | – | · 13.2 ROW Expansion miles completed;
209 | ETL.6500 | COLGATE‑PALERMO 60 KV | 2019-06-08 | – | · OH Hardening Completed in 20231; OH Hardening Planned in 2025; | See Footnote(b)
|  |  | 2019-09-23 | – | · Sectionalizing Capable;
|  |  | 2019-09-25 | – | · 753 Transmission Tags Completed;
|  |  | 2019-10-09 | –
|  |  | 2019-10-26 | –
210 | ETL.6520 | COLGATE‑SMARTVILLE #2 60 KV | 2019-09-23 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-09-25 | – | · 415 Transmission Tags Completed;
|  |  | 2019-10-09 | –
|  |  | 2019-10-26 | –
211 | ETL.6650 | COTTONWOOD‑BENTON #2 60 KV | 2019-10-09 | – | · 364 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-26 | –
|  |  | 2019-11-20 | –
212 | ETL.6690 | DEER CREEK‑DRUM 60 KV | 2019-10-09 | – | · 440 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | – | · 6.2 ROW Expansion miles completed;
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
213 | ETL.6720 | DESABLA‑CENTERVILLE 60 KV | 2019-06-08 | 13 | · 425 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-09-25 | – | · 5.9 ROW Expansion miles completed;
|  |  | 2019-10-05 | –
|  |  | 2019-10-09 | –
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
214 | ETL.6760 | DRUM‑GRASS VALLEY‑WEIMAR 60 KV | 2018-10-14 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-09 | – | · 1,745 Transmission Tags Completed;
|  |  | 2019-10-23 | 68
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
215 | ETL.4393 | DRUM‑HIGGINS 115 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-23 | – | · 821 Transmission Tags Completed;
|  |  | 2019-10-26 | – | · 27.3 ROW Expansion miles completed;
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
216 | ETL.1420 | DRUM‑RIO OSO #1 115 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-23 | – | · 921 Transmission Tags Completed;
|  |  | 2019-10-26 | – | · 62.7 ROW Expansion miles completed;
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
217 | ETL.1430 | DRUM‑RIO OSO #2 115 KV | 2019-10-09 | – | · 508 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | – | · 62.8 ROW Expansion miles completed;
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
218 | ETL.1470 | EAGLE ROCK‑CORTINA 115 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-26 | – | · 398 Transmission Tags Completed;
|  |  | 2019-11-20 | 25
219 | ETL.1480 | EAGLE ROCK‑REDBUD 115 KV | 2019-10-09 | 43 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-26 | – | · 419 Transmission Tags Completed;
|  |  | 2019-11-20 | –
220 | ETL.1530 | EL DORADO‑MISSOURI FLAT #1 115 KV | 2019-10-09 | 38 | · 359 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | – | · 8.4 ROW Expansion miles completed;
|  |  | 2019-10-26 | –
|  |  | 2020-10-25 | –
221 | ETL.1540 | EL DORADO‑MISSOURI FLAT #2 115 KV | 2019-10-09 | – | · 100 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | – | · 8.4 ROW Expansion miles completed;
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
222 | ETL.6722 | FORKS OF THE BUTTE TAP 60 KV | 2019-06-08 | 13 | · 37 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-09-25 | –
|  |  | 2019-10-05 | –
223 | ETL.6870 | FRENCH MEADOWS‑MIDDLE FORK 60 KV | 2018-10-14 | 51 | · 732 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-09 | – | · 13.2 ROW Expansion miles completed;
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-09-27 | –
|  |  | 2020-10-25 | –
224 | ETL.6880 | FULTON‑CALISTOGA 60 KV | 2018-10-14 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-23 | – | · 1,032 Transmission Tags Completed;
|  |  | 2019-10-26 | – | · 50.6 ROW Expansion miles completed;
|  |  | 2019-11-20 | –
|  |  | 2020-10-25 | –
|  |  | 2021-08-17 | –
225 | ETL.6890 | FULTON‑HOPLAND 60 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-23 | – | · 880 Transmission Tags Completed;
|  |  | 2019-10-26 | –
226 | ETL.2823 | FULTON‑LAKEVILLE‑IGNACIO 230 KV | 2019-10-23 | – | · 6 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-26 | –
|  |  | 2019-11-20 | –
227 | ETL.7290 | KILARC‑CEDAR CREEK 60 KV | 2019-10-09 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-26 | – | · 662 Transmission Tags Completed;
|  |  | 2019-11-20 | – | · 13.5 ROW Expansion miles completed;
|  |  | 2020-09-07 | –
|  |  | 2020-10-14 | –
|  |  | 2020-10-21 | –
|  |  | 2020-10-25 | –
|  |  | 2023-08-30 | –
|  |  | 2024-09-30 | –
228 | ETL.3505 | KM GREEN 115 KV TAP | 2020-09-07 | 53 | · 51 Transmission Tags Completed; | See Footnote(b)
|  |  | 2020-09-27 | –
|  |  | 2020-10-25 | –
229 | ETL.8405 | MIDDLE FORK #1 60 KV | 2018-10-14 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-09-25 | – | · 579 Transmission Tags Completed;
|  |  | 2019-10-09 | – | · 9.4 ROW Expansion miles completed;
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-09-27 | –
|  |  | 2020-10-25 | –
230 | ETL.5140 | MIDDLE FORK‑GOLD HILL 230 KV | 2019-10-09 | – | · 1,176 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-09-27 | –
|  |  | 2020-10-25 | –
231 | ETL.6721 | ORO FINO TAP 60 KV | 2019-06-08 | – | · 77 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-09-25 | –
|  |  | 2019-10-05 | –
232 | ETL.7730 | PALERMO‑OROVILLE #1 60 KV | 2019-06-08 | 174 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-09-23 | – | · 83 Transmission Tags Completed;
|  |  | 2019-09-25 | –
|  |  | 2019-10-09 | –
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
233 | ETL.7740 | PALERMO‑OROVILLE #2 60 KV | 2019-06-08 | 53 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-09-23 | – | · 159 Transmission Tags Completed;
|  |  | 2019-09-25 | –
234 | ETL.3500 | SALT SPRINGS‑TIGER CREEK 115 KV | 2019-10-26 | 92 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2020-09-07 | – | · 423 Transmission Tags Completed;
|  |  | 2020-09-27 | – | · 19.6 ROW Expansion miles completed;
|  |  | 2020-10-25 | –
235 | ETL.7980 | SMARTVILLE‑MARYSVILLE 60 KV | 2019-09-23 | 82 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-09 | – | · 273 Transmission Tags Completed;
|  |  | 2019-10-26 | –
236 | ETL.8000 | SMARTVILLE‑NICOLAUS #2 60 KV | 2019-09-23 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-09 | 42 | · 90 Transmission Tags Completed;
|  |  | 2019-10-26 | –
237 | ETL.5780 | TIGER CREEK‑ELECTRA 230KV | 2019-10-09 | 45 | · 271 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
238 | ETL.5790 | TIGER CREEK‑VALLEY SPRINGS 230 KV | 2019-10-09 | – | · 323 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
239 | ETL.7560 | WEIMAR #1 60 KV | 2018-10-14 | 16 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-09-25 | – | · 669 Transmission Tags Completed;
|  |  | 2019-10-09 | – | · 14.0 ROW Expansion miles completed;
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
240 | ETL.8340 | WEIMAR‑HALSEY 60 KV | 2019-10-09 | – | · 271 Transmission Tags Completed; | See Footnote(b)
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
241 | ETL.8350 | WEST POINT‑VALLEY SPRINGS 60 KV | 2018-10-14 | 13 | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-09 | – | · Mitigated by Islanding;
|  |  | 2019-10-23 | – | · 611 Transmission Tags Completed;
|  |  | 2019-10-26 | – | · 21.6 ROW Expansion miles completed;
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
242 | ETL.4220 | WOODLEAF‑PALERMO 115 KV | 2019-09-25 | – | · Sectionalizing Capable; | See Footnote(b)
|  |  | 2019-10-05 | – | · 672 Transmission Tags Completed; and
|  |  | 2019-10-09 | – | · 19.6 ROW Expansion miles completed.
|  |  | 2019-10-23 | –
|  |  | 2019-10-26 | –
|  |  | 2020-09-07 | –
|  |  | 2020-10-25 | –
_______________
(a) Transmission OH hardening not measured in miles due to the hardening by mitigation taken by the installation of a shunt splice device.
(b) The most significant customer impacts of transmission PSPS occur on the distribution circuits fed by these transmission lines, and are not well‑represented by the small number of customers fed directly from transmission lines. The customer‑hours mitigated for downstream distribution customers are captured in the rows corresponding to each distribution circuit, instead of the rows corresponding to upstream transmission lines.

## Table PG&E-5.2-1
TABLE PG&E 5.2-1:
ADDRESSING KEY LIKELIHOOD AND CONSEQUENCES IN RISK MODELS
Factor | How Key Factors Addressed in PG&E’s Risk Models
Equipment/Assets | Threats to equipment and assets are considered in the LoRE analysis and quantification
Topography | LoRE and CoRE both use topographical data sets as they influence the threats and hazards to assets and the conditions for fire propagation
Weather | Hazards to assets and equipment due to weather are considered in the LoRE analysis and quantification. Weather also influences the CoRE assessment of wildfire propagation.
Vegetation | Hazard to assets in the probability of vegetation failures that can cause ignitions (LoRE analysis and quantification). Fuels quantification of vegetation is a key variable in the assessment of fire propagation.
Climate Change | Secondary input to hazards, threats with LoRE and fire propagation in CoRE. Not currently directly modeled.
Social Vulnerability | Demographic data used as an input for egress impact adjustment to CoRE.
Physical Vulnerability | Demographic data used as an input for egress impact adjustment to CoRE.
Access Capacities | Demographic data used as an input for egress impact adjustment to CoRE.

## Table PG&E-5.2.2.2-2
TABLE PG&E 5.2.2.2 2: CRITICAL CUSTOMER WEIGHTINGS
Customer Type | Customer Weighting | Customer Category
Extreme | 100 | CC1
Significant | 5 | Life Support, Medical Baseline & Low Income, Life Support & Low Income
Elevated | 2 | CC2, CC3, CE1, CE2, CE3, EE, PR1, SC1, SC2, SC3, SE1, SE2, SE3, TE1, TE2, TT1, TT2, Medical Baseline, ‑Self‑Identified Vulnerable, ‑‑Self‑Identified Disabled, Low Income
Regular Customer | 1 | Regular Customer

## Table PG&E‑5.2.2.3‑1
TABLE PG&E‑5.2.2.3‑1:
WDRM V4 MITIGATION COMPOSITES
Event Probability Model | All Composite | System Hardening | Vegetation Management
Animal – Bird | ü | ü | ×
Animal – Squirrel | ü | ü | ×
Animal – Other | ü | ü | ×
Capacitor Bank | ü | ü | ×
Dynamic Protection Device (DPD) | ü | ü | ×
Fuse | ü | ü | ×
Primary Conductor – Line Slap | ü | ü | ×
Primary Conductor – Wire Down | ü | ü | ×
Primary Conductor – Other | ü | ü | ×
Secondary Conductor | ü | ü | ×
Support Structure – Electrical | ü | × | ×
Support Structure – Equipment | ü | ü | ×
Switch | ü | ü | ×
Third Party – Balloon | ü | ü | ×
Third Party – Vehicle | ü | ü | ×
Third Party – Other | ü | ü | ×
Transformer – Failure | ü | ü | ×
Transformer – Leaking | ü | × | ×
Vegetation – Branch | ü | ü | ü
Vegetation – Trunk | ü | ü | ü
Vegetation – Other | ü | ü | ü
Voltage Regulator | ü | ü | ×
Other Equipment | ü | ü | ×

## Table 5-1
TABLE 5‑1:
RISK MODELING ASSUMPTIONS AND LIMITATIONS(a)
Assumption | Rationale/Justification | Limitation | Applicable Model
It is assumed that events from June‑November, the typical timing of fire seasons, are representative of all events capable of producing wildfire risk | If the training data for the WDRM included events caused by winter storms, icing, and other causal processes not compatible with ignition and wildfire spread, the pattern of model predictions would be influenced by events that contribute little or no wildfire risk. To avoid exposing the model to misleading data, the training events are restricted to June through November. | We assume that wildfires are possible outside of the typical fire season and that ignitions and wildfires occurring outside of the typical fire season would have the same relationship with the model covariates as the ones the model is already trained on. | Overall Utility Risk
Ignition/Wildfire Risk (WDRM/WTRM)
Ignition Likelihood
Ignition/WFC
Equipment Likelihood of Ignition
Contact from Object Likelihood of Ignition
The WDRM v4 is an “observational model” that uses the pattern of past outages and ignitions to predict their future. | The core assumption of such an approach is that the correlations and causal processes that have governed past outages and ignitions will continue to govern them in the future. | N/A | WDRM
Ignition Likelihood
Equipment Likelihood of Ignition
Contact from Object Likelihood of Ignition
ML tools, like feature generation, model regularization, and the preferential use of out of sample performance metrics, are well suited to the prediction of ignition probability and risk. | The key features of the ML tools are the primary output of the WDRM v4. | N/A | Ignition/Wildfire Risk (WDRM)
Ignition Likelihood
Equipment Likelihood of Ignition
Contact from Object Likelihood of Ignition
WTRM builds on assumptions used by the Transmission Operational Assessment (OA) Model. PG&E identified 47 components through a Failure Modes and Effects Analysis which could result in a wildfire ignition if they failed. These 47 components were divided into 9 asset groups and asset specific datasets are assigned to each one. | While the scope of the WTRM exceeds that of the OA Model in terms of incorporating other hazards, the asset group types remain a proxy for a collection of components that share similar: (1) life cycles, (2) sensitivities to threats and hazards, and (3) Asset Management strategies. | N/A | Ignition/Wildfire Risk (WTRM v2)
Where age data is unavailable from system of records, a logic is used to determine the most conservative age of the asset. | Age data is required for each component for the WTRM to compute an annual failure rate. | Some equipment risk could potentially be overestimated due to equipment using assumed age. | Ignition/Wildfire Risk (WTRM v2)
Circuits operating outside their rated capacity or in abnormal configuration do not have an increased ignition risk. | In July 2024 during an intense heat event, PG&E saw a significant uptick in fire risk exposure and associated ignition events. PG&E did an analysis that found that conductors and connectors under high heat stress, both external (due to extended heat) and internal (due to load) could be one of the contributing factors. | While the distribution (WDRM v4) probability of failure model does include the risk for abnormal circuits, it does not currently identify circuits that are operating within the rated capacity and circuits that are operating outside their rated capacity or circuits in abnormal configuration. PG&E is currently investigating if there is a correlation between circuit condition and higher outage and ignition events. PG&E is collecting data to determine the degree of risk introduced by circuit configuration in the HFTD/HFRA. | WDRM v4
Critical Customer Weightings are based on high level SME judgement. | The assignment of a critical weighting factor to our customers is a subjective process that will continually be reviewed and potentially updated. There has been limited industry research and therefore no industry standard on how different customers are impacted by PSPS events or loss of power. PG&E will continue to work with the industry and Investor‑Owned Utility (IOU) partners to better reflect customer risks in our PSPS consequence model. The current weighting system was developed internally to provide a simple differentiation of customer category types. | The distribution of customer risk (and PSPS risk reduction) is partly driven by the type of customers and their critical weighting score. Significant changes to the critical customer weighting could potentially impact Circuit Protection Zone risk ranking and prioritization initiatives | PSPS Risk
PSPS Consequence
PSPS Likelihood
Vulnerability of Community to PSPS
PSPS safety consequence is based off 50 percent PG&E PSPS planned and 50 percent unplanned long duration outages across the United States (U.S.) | PSPS represented as a non‑zero safety risk is reasonable. However, PG&E providing advanced notification for a planned de‑energization reduces the safety impact of the outage and should not be treated as an unplanned outage. Given that historical records show no safety impacts, PG&E included unplanned long duration outages across the U.S. (i.e., 2033 NE Blackout, 2011 SW Blackout, 2012 Superstorm Sandy, etc.) at 50 percent, respectively. | The safety consequence of PSPS should not include unplanned outages as it does not accurately represent PSPS itself. | PSPS Risk
Safety accounts for 50 percent of our MAVF PSPS Risk. PSPS events are relatively new and there is minimal SIF data to include in the risk analysis. For this reason, other large external national events (i.e., 2003 NE Blackout, 2011 SW Blackout, 2012 Superstorm Sandy, etc.) were considered in evaluating safety risks associated with PSPS events. |  |  | PSPS Consequence
PSPS Likelihood
Vulnerability of Community to PSPS
EPSS Consequence assumes that the duration will be the same for outages that occur both with and without EPSS enabled. | Analysis of outages supports the expectation that the duration of an outage will be the same whether or not EPSS is enabled. | As future operational EPSS data becomes available, analysis may discover differences in duration for EPSS enabled outages | EPSS Risk
EPSS Consequence
EPSS Likelihood of a fault is independent of whether or not EPSS is enabled. | No known causal mechanism that would cause the fault rate to change when EPSS is enabled. | As future operational EPSS data become available a causal mechanism may be discovered. | EPSS Risk
EPSS Likelihood
EPSS Value of Service (VOS) is specific to customer class based on the outputs of the interruption cost estimation calculator | Interruption cost estimation calculator inputs are based on PG&E customer characteristics and historic SAIFI, SAIDI, CAIDI metrics | VOS is based on 2016 data, escalated to 2024 values | EPSS Risk
EPSS Consequence
Baseline Risk in the Enterprise Wildfire Risk Model is calibrated to historical performance. | Baseline wildfire risk needs to be calibrated against all other risks within the Company. As such, historical years’ performance is used to calculate risk score | Changes in wildfire risk has been dynamic. Baseline risk scores based on historical performance may not be reflective of current performance. | Enterprise Risk Model (b)
The FPI and IPW models are observational models that learn the pattern of historical fires, outages, and ignitions together with the conditions under which they occurred to predict future fires, outages, and ignitions. | The rationale of such an approach is that the correlations and causal processes that drive historical fires, outages and ignitions will continue to drive them in the future. | Fires, ignitions and outages of the future may be driven by processes that have not been accounted for in the models. | FPI/IPW(c)
The FPI and IPW models are driven predominantly by weather model forecasts. | Weather is an important driver of fires, outages, and ignitions. | Weather model forecasts, while skillful and well validated, are not a perfect representation of the future state of the atmosphere. | FPI/IPW(c)
ML methods, such as feature creation, classification and regression, model sampling, and use of the out of sample performance metrics, are well suited to the prediction of fire, outage, and ignition probability and risk. | The rationale of ML is that it allows the skillful explanation of future fires, outages, and ignitions by using large amounts of data and sophisticated algorithms. | ML models are limited by the amount of data available and the sophistication of the current state‑of‑the‑art algorithms. | FPI/IPW(c)
_______________
(a) Updated based on Substantive Errata filing on April 18, 2025 in accordance with Energy Safety's issuance of Revision Notice at 21.
(b) The Enterprise Risk Model is used to calibrate all the wildfire, PSPS, and EPSS risk models listed in Table 5‑4 above for the purpose of calculating overall utility risk.
(c) The FPI/IPW models are operational models and, therefore, do not appear in Table 5‑4 below.

## Table 5-2
TABLE 5‑2:
SUMMARY OF DESIGN SCENARIOS
Scenario ID | Design Scenario | Purpose
OP1 | Weather 1 | Operational models (FPI, IPW)
Weather 2
Wind Load 1
Wind Load 2
Vegetation 1
OP2 | Wind Load 1 | OA Operational Model
Wind Load 2
Wind Load 3
Wind Load 4
Weather 1
Weather 2
Vegetation 1
PL1 | Weather 2 | WDRM Planning Model
Wind Load 1
Wind Load 2
Vegetation 3
PL2 | Weather 2 | WTRM Planning Model
Wind Load 1
Wind Load 2
Wind Load 3
Wind Load 4
Vegetation 3

## Table 5-3
PG&E is not completing Table 5‑3 above as we do not directly account for extreme event scenarios as articulated in the WMP Guidelines in risk modeling.

## Table 5-4
TABLE 5‑4:
PG&E RISK MODELS
ID | Risk Component | Design Scenario | Key Inputs | Source of Inputs | Key Outputs | Units
UR | Overall Utility Risk | PL1 | Outage Program Risk and Ignition/Wildfire Risk | Ignition Likelihood | Circuit Segment Level Risk | Dollars ($)
Ignition WFC
PSPS Likelihood
PSPS Consequence
PEDS (EPSS) Likelihood
PEDS (EPSS) Consequence
WFR | Ignition/Wildfire Risk (WDRM/WTRM) | PL1 | Ignition Probability | Ignition Likelihood | Circuit Segment Risk | Dollars ($)
|  |  | Ignition Consequence | Ignition/WFC
OP R | Outage Program Risk | PL1 | PSPS Risk | PSPS Likelihood | Circuit Segment Risk | Dollars ($)
|  |  | PEDS (EPSS) Risk | PSPS Consequence
PEDS (EPSS) Likelihood
PEDS (EPSS) Consequence
PSPS R | PSPS Risk | PL1 | PSPS Consequence | Historical Meteorology Data | SPID Risk | Dollars ($)
|  |  | PSPS Likelihood | Historical PSPS enablement | Circuit segment Risk
|  |  |  | Customer Impacts | Circuit Risk
PEDS R | PEDS (EPSS) Risk | PL1 | PEDS (EPSS) Likelihood | Distribution Event Probability Models | Circuit Segment Risk | Dollars ($)
|  |  | PEDS (EPSS) Consequence | Customer Impacts
PI | Ignition Likelihood | PL1 | Equipment models ignition probability | Equipment Likelihood of Ignition | Circuit Segment Likelihood of Ignition | Ignitions/year
|  |  | Contact from object models ignition probability | Contact from Object Likelihood of Ignition
PEDS L | PEDS (EPSS) Likelihood | PL1 | Equipment models outage probability | Equipment Likelihood of Outage | Circuit Segment Likelihood of Outage | Ignitions/year
|  |  | Contact from object models outage probability | Contact from Object Likelihood of Outage
WFC | Ignition/WFC | PL1 | Wildfire Hazard Intensity | Technosylva | Pixel (100 m x 100 m) consequence | MAVF
|  |  | Wildfire Exposure Potential | FPI
|  |  | Wildfire Vulnerability | Visible Infrared Imaging Radiometer Suite (VIIRS)
Burn Probability
PSPS C | PSPS Consequence | PL1 | PSPS event data | Historical Meteorology Data | SPID Consequence | Dollars ($)
|  |  | Customer data |  | Circuit segment Consequence
Circuit Consequence
PEDS C | PEDS (EPSS) Consequence | PL1 | Customer impacts | CMI | Circuit Segment Consequence | Dollars ($)
EQI | Equipment Likelihood of Ignition | PL1 | Equipment subset likelihood of ignition models | Distribution Asset Data, Historical Outages and Ignitions, PSPS Damages and Hazards, Meteorological data, National Land Cover Database, LANDFIRE surface fuels, HFTD, Vegetation LiDAR, FPI, Real‑Time Mesoscale Analysis | 100 meter x 100 meter pixel Annual probability of ignition | Ignitions/year
CFOI | Contact from Object Likelihood of Ignition | PL1 | Contract from object sub model | Distribution Asset Data, Historical Outages and Ignitions, PSPS Damages and Hazards, Meteorological data, National Land Cover Database, LANDFIRE surface fuels, HFTD, Vegetation LiDAR, FPI, Real‑Time Mesoscale Analysis | 100 meter x 100 meter pixel Annual probability of ignition | Ignitions/year
BP | Burn Probability | PL1 | Rate of Spread | Technosylva | 100m x 100m pixel destructive potential classification | % of days
Flame Length
WHI | Wildfire Hazard Intensity | PL1 | Rate of Spread | Technosylva | 100m x 100m pixel destructive potential classification | % of days
Flame Length
WEP | Wildfire Exposure Potential | PL1 | VIIRS | VIIRS | 100m x 100m pixel destructive potential classification | % of days
|  |  | FPI | FPI
|  |  | Terrain Difficulty Index | Technosylva
WFV | Wildfire Vulnerability | PL1 | AFN | AFN | Customer demographics by circuit segment | Counts/circuit segment
|  |  | FPI | FPI
PSPS L | PSPS Likelihood | PL1 | Historical Meteorology | Weather Data | PSPS event counts by circuit segment | Events/Year
PSPS V | Vulnerability of Community to PSPS | PL1 | Customer Demographic data | AFN | Demographic counts per circuit segment | Counts/circuit segment
PEDS L | PEDS (EPSS) Likelihood | PL1 | Distribution Event Probability Models | Probability of outage models | Probability of outage | Outages/Year
PEDS V | Vulnerability of Community to PEDS (EPSS) | PL1 | Customer Demographic data | AFN | Demographic counts per circuit segment | Counts/circuit segment

## Table 5-5A
TABLE 5‑5A:
SUMMARY OF TOP RISK CIRCUIT SEGMENTS BY OVERALL UTILITY RISK(a)
Risk Ranking | Circuit, Segment, or Span ID | Overall Utility Risk Score | Wildfire Risk Score | Outage Program Risk Score | Top Risk Contributors | Total Miles | Version of Risk Model Used
1 | CLAYTON 2212681608 | 99.7013 | 92.6037 | 7.0976 | Wildfire | 33.2215 | WDRM v4
2 | BALCH NO 1 1101105414 | 91.5229 | 91.5131 | 0.0098458 | Wildfire | 7.4477 | WDRM v4
3 | CLOVERDALE 1102672 | 80.9024 | 78.7264 | 2.176 | Wildfire | 22.4533 | WDRM v4
4 | PLACERVILLE 21067522 | 72.8321 | 67.696 | 5.1361 | Wildfire | 73.5317 | WDRM v4
5 | PLACERVILLE 210611132 | 67.324 | 62.2574 | 5.0666 | Wildfire | 44.4736 | WDRM v4
6 | MIDDLETOWN 1101644756 | 66.8951 | 65.0459 | 1.8492 | Wildfire | 15.2593 | WDRM v4
7 | STANISLAUS 1701CB | 64.2834 | 62.1173 | 2.1661 | Wildfire | 38.5242 | WDRM v4
8 | EL DORADO PH 210119752 | 61.3359 | 55.4086 | 5.9273 | Wildfire | 41.5804 | WDRM v4
9 | CALPINE 1144CB | 60.6956 | 58.9532 | 1.7424 | Wildfire | 26.7587 | WDRM v4
10 | ALLEGHANY 1102CB | 60.0599 | 59.7834 | 0.27645 | Wildfire | 18.792 | WDRM v4
11 | MARIPOSA 210237282 | 59.3946 | 57.7906 | 1.604 | Wildfire | 53.2532 | WDRM v4
12 | BIG BEND 1101CB | 57.5444 | 51.6681 | 5.8763 | Wildfire | 23.51 | WDRM v4
13 | WEST POINT 11024788 | 57.4156 | 54.6136 | 2.8021 | Wildfire | 74.2727 | WDRM v4
14 | CALAVERAS CEMENT 1101544800 | 57.3184 | 57.0604 | 0.25802 | Wildfire | 23.5406 | WDRM v4
15 | CALAVERAS CEMENT 1101502 | 56.1338 | 54.458 | 1.6758 | Wildfire | 37.9251 | WDRM v4
16 | CORNING 110185152 | 54.4345 | 48.2352 | 6.1993 | Wildfire & PSPS | 25.5236 | WDRM v4
17 | CURTIS 17048140 | 54.0429 | 51.7497 | 2.2932 | Wildfire | 38.0418 | WDRM v4
18 | COLUMBIA HILL 1101CB | 53.4681 | 50.684 | 2.784 | Wildfire | 47.9377 | WDRM v4
19 | TEMPLETON 2113A12 | 53.4192 | 53.0356 | 0.38359 | Wildfire | 41.3599 | WDRM v4
20 | FORT ROSS 112170288 | 52.9255 | 52.6791 | 0.24643 | Wildfire | 25.013 | WDRM v4
21 | BIG BEND 1101641808 | 52.57 | 47.0195 | 5.5505 | Wildfire & PSPS | 29.532 | WDRM v4
22 | MARIPOSA 2101752630 | 51.4021 | 51.3695 | 0.032589 | Wildfire | 19.2425 | WDRM v4
23 | SILVERADO 2104633600 | 50.5596 | 44.9826 | 5.577 | Wildfire & PSPS | 25.0577 | WDRM v4
24 | VACAVILLE 110838316 | 49.3106 | 47.764 | 1.5466 | Wildfire | 15.7285 | WDRM v4
25 | APPLE HILL 110497086 | 49.1966 | 46.843 | 2.3536 | Wildfire | 28.4004 | WDRM v4
26 | APPLE HILL 21029722 | 48.5389 | 46.5058 | 2.0331 | Wildfire | 40.0897 | WDRM v4
27 | MIDDLETOWN 1101548 | 48.4984 | 41.3425 | 7.1559 | Wildfire & PSPS | 31.27 | WDRM v4
28 | PINE GROVE 11026080 | 48.1154 | 46.5222 | 1.5931 | Wildfire | 34.8802 | WDRM v4
29 | HIGHLANDS 1102628 | 46.8557 | 46.5809 | 0.27478 | Wildfire | 19.3754 | WDRM v4
30 | PLACERVILLE 21069712 | 46.2948 | 43.8896 | 2.4052 | Wildfire | 26.1562 | WDRM v4
31 | HARTLEY 1101698 | 46.1802 | 45.9563 | 0.22392 | Wildfire | 21.2775 | WDRM v4
32 | PUEBLO 2103678 | 45.963 | 42.0971 | 3.8658 | Wildfire | 36.7092 | WDRM v4
33 | MARTELL 110191216 | 45.6481 | 45.3977 | 0.25043 | Wildfire | 41.5937 | WDRM v4
34 | REDBUD 1101323962 | 45.5277 | 36.441 | 9.0867 | Wildfire & PSPS | 16.9079 | WDRM v4
35 | MOLINO 1102318 | 45.412 | 44.6383 | 0.77372 | Wildfire | 27.7967 | WDRM v4
36 | HIGHLANDS 1103520 | 44.295 | 41.366 | 2.929 | Wildfire | 48.0022 | WDRM v4
37 | COARSEGOLD 210410110 | 43.9578 | 41.5037 | 2.4541 | Wildfire | 52.3108 | WDRM v4
38 | AUBERRY 1101R2578 | 43.6409 | 40.7536 | 2.8873 | Wildfire | 47.5091 | WDRM v4
39 | MARIPOSA 210237288 | 43.5691 | 42.7023 | 0.86674 | Wildfire | 87.0249 | WDRM v4
40 | FROGTOWN 170113412 | 43.5543 | 37.8631 | 5.6911 | Wildfire | 43.0363 | WDRM v4
41 | ELECTRA 1101CB | 43.215 | 41.7064 | 1.5086 | Wildfire | 23.973 | WDRM v4
42 | CORNING 11021622 | 42.7053 | 41.3156 | 1.3897 | Wildfire | 35.3851 | WDRM v4
43 | DIAMOND SPRINGS 110676088 | 42.3199 | 41.9075 | 0.4124 | Wildfire | 34.243 | WDRM v4
44 | BONNIE NOOK 1102CB | 41.8552 | 35.1003 | 6.7549 | Wildfire & PSPS | 30.1758 | WDRM v4
45 | BRUNSWICK 11021010 | 41.6777 | 40.6525 | 1.0252 | Wildfire | 47.0869 | WDRM v4
46 | CURTIS 170390320 | 41.0182 | 39.6973 | 1.3209 | Wildfire | 32.1089 | WDRM v4
47 | MARIPOSA 210110070 | 40.9066 | 40.8295 | 0.077089 | Wildfire | 26.2826 | WDRM v4
48 | GIRVAN 11011330 | 40.5343 | 35.9333 | 4.601 | Wildfire & PSPS | 25.9983 | WDRM v4
49 | APPLE HILL 110413512 | 40.3039 | 32.9483 | 7.3557 | Wildfire & PSPS | 31.275 | WDRM v4
50 | DIAMOND SPRINGS 11057722 | 40.1837 | 39.017 | 1.1667 | Wildfire | 62.1778 | WDRM v4
51 | BALCH NO 1 1101406582 | 40.1094 | 40.1094 | 0 | Wildfire | 3.7849 | WDRM v4
52 | MOUNTAIN QUARRIES 21011130 | 39.6503 | 38.0279 | 1.6224 | Wildfire | 21.4781 | WDRM v4
53 | APPLE HILL 2102836878 | 39.4699 | 30.2953 | 9.1746 | Wildfire & EPSS | 43.8876 | WDRM v4
54 | COALINGA NO 2 11059260 | 39.3637 | 39.1603 | 0.20346 | Wildfire | 0 | WDRM v4
55 | LAYTONVILLE 1101518 | 38.8951 | 38.1141 | 0.78099 | Wildfire | 2.1587 | WDRM v4
56 | APPLE HILL 21028372 | 38.7665 | 34.2702 | 4.4963 | Wildfire | 59.0321 | WDRM v4
57 | LOS OSITOS 21037014 | 38.7165 | 38.6357 | 0.080815 | Wildfire | 0 | WDRM v4
58 | STILLWATER 11021466 | 38.3929 | 34.3774 | 4.0155 | Wildfire & PSPS | 23.2457 | WDRM v4
59 | PIT NO 3 21011482 | 37.308 | 37.1846 | 0.12347 | Wildfire | 12.2645 | WDRM v4
60 | GEYSERVILLE 1102904170 | 36.9939 | 34.3796 | 2.6142 | Wildfire | 21.4372 | WDRM v4
61 | FORESTHILL 11011802 | 36.4406 | 30.8293 | 5.6113 | Wildfire & PSPS | 25.4503 | WDRM v4
62 | FITCH MOUNTAIN 111324918 | 36.4262 | 35.8264 | 0.59982 | Wildfire | 24.6009 | WDRM v4
63 | MARIPOSA 2101439030 | 36.0716 | 35.9859 | 0.085693 | Wildfire | 21.0606 | WDRM v4
64 | CLAYTON 221296224 | 35.9806 | 35.4507 | 0.52991 | Wildfire | 10.2379 | WDRM v4
65 | PEORIA 170190090 | 35.8543 | 33.1277 | 2.7266 | Wildfire | 30.4357 | WDRM v4
66 | HOPLAND 11014626 | 35.6066 | 34.6606 | 0.94602 | Wildfire | 25.9035 | WDRM v4
67 | SILVERADO 2104632 | 35.5808 | 32.1845 | 3.3963 | Wildfire | 18.8126 | WDRM v4
68 | PLACERVILLE 2106935216 | 35.4512 | 34.222 | 1.2292 | Wildfire | 21.7834 | WDRM v4
69 | APPLE HILL 2102186912 | 34.9302 | 30.6161 | 4.3141 | Wildfire | 61.9458 | WDRM v4
70 | SHADY GLEN 1101941844 | 34.5974 | 29.2227 | 5.3747 | Wildfire & PSPS | 17.8895 | WDRM v4
71 | PINE GROVE 1102269286 | 34.1506 | 26.1142 | 8.0364 | Wildfire & PSPS | 31.6429 | WDRM v4
72 | ORO FINO 110239154 | 34.0841 | 28.7396 | 5.3445 | Wildfire & PSPS | 47.0539 | WDRM v4
73 | WEST POINT 110234416 | 33.9065 | 32.2029 | 1.7036 | Wildfire | 27.7318 | WDRM v4
74 | CEDAR CREEK 1101CB | 33.7551 | 29.4514 | 4.3038 | Wildfire & PSPS | 50.089 | WDRM v4
75 | SISQUOC 1102M52 | 33.4088 | 33.1637 | 0.24506 | Wildfire | 33.0745 | WDRM v4
76 | TEMPLETON 2113641367 | 33.3923 | 32.9903 | 0.40202 | Wildfire | 39.8704 | WDRM v4
77 | MARIPOSA 21019400 | 33.2984 | 31.1666 | 2.1319 | Wildfire | 64.2395 | WDRM v4
78 | FORESTHILL 1102359542 | 32.7979 | 30.1772 | 2.6207 | Wildfire | 19.4347 | WDRM v4
79 | CALAVERAS CEMENT 11011419 | 32.6283 | 32.0933 | 0.53505 | Wildfire | 15.4763 | WDRM v4
80 | BRUNSWICK 110651486 | 32.0751 | 30.4848 | 1.5903 | Wildfire | 60.9483 | WDRM v4
81 | SHINGLE SPRINGS 210913322 | 32.0191 | 31.847 | 0.17212 | Wildfire | 44.14 | WDRM v4
82 | PINE GROVE 11013170 | 32.0008 | 30.8997 | 1.101 | Wildfire | 41.7684 | WDRM v4
83 | WEST POINT 110236676 | 31.795 | 30.7184 | 1.0766 | Wildfire | 17.4163 | WDRM v4
84 | APPLE HILL 21021532 | 31.4372 | 26.2948 | 5.1423 | Wildfire | 40.3981 | WDRM v4
85 | CALAVERAS CEMENT 110147968 | 30.7825 | 30.4048 | 0.37764 | Wildfire | 17.3262 | WDRM v4
86 | WILDWOOD 1101384582 | 30.7606 | 30.7594 | 0.0012027 | Wildfire | 4.5387 | WDRM v4
87 | SANTA YNEZ 1102320270 | 30.7321 | 30.3443 | 0.38784 | Wildfire | 8.5371 | WDRM v4
88 | FRENCH GULCH 11022902 | 30.5736 | 30.5621 | 0.011534 | Wildfire | 7.0593 | WDRM v4
89 | STANISLAUS 17011812 | 30.5553 | 28.5064 | 2.0489 | Wildfire | 21.2819 | WDRM v4
90 | PERRY 110179696 | 30.4315 | 30.2638 | 0.16767 | Wildfire | 33.3788 | WDRM v4
(a) Adjusted in response to Critical Issue RN-PGE-26-02. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table 5-6
TABLE 5‑6:
RISK ASSESSMENT IMPROVEMENT PLAN
Key Risk Assessment Area | Proposed Improvement | Type of Improvement | Expected Value Add | Timeframe and Key Milestones
Conflagration Risk Modeling | Investigate development of improved representation of conflagration risk in consequence model | Technical | Improved quantification of risk related to urban conflagration | By end of 2027
Specificity of Vegetation Probabilistic Models | Investigate improved granularity of vegetation probabilistic models | Technical | Improved specificity of hazard tree identification for work plans | By end of 2027
Improved Asset Failure Probabilistic Models | Investigate opportunities to improve individual asset failure models | Technical | Improved effectiveness of mitigation workplans | By end of 2027

## Table 6-1
TABLE 6‑1:
PG&E PRIORITIZED AREAS BASED ON OVERALL UTILITY RISK
Priority | Circuit Segment and/or Span ID | Length (miles) | Overall Utility Risk | Wildfire Risk | Outage Program Risk | Percent of Overall Utility Risk | Associated Risk Driver
1 | CLAYTON 2212681608 | 33.2215 | 99.7013 | 92.6037 | 7.0976 | 0.4981% | Equipment failure Vegetation contact Contact from object
2 | BALCH NO 1 1101105414 | 7.4477 | 91.5229 | 91.5131 | 0.0098458 | 0.4573% | Equipment failure Vegetation contact Contact from object
3 | CLOVERDALE 1102672 | 22.4533 | 80.9024 | 78.7264 | 2.176 | 0.4042% | Vegetation contact Equipment failure Contact from object
4 | PLACERVILLE 21067522 | 73.5317 | 72.8321 | 67.696 | 5.1361 | 0.3639% | Vegetation contact Equipment failure Contact from object
5 | PLACERVILLE 210611132 | 44.4736 | 67.324 | 62.2574 | 5.0666 | 0.3364% | Vegetation contact Equipment failure Contact from object
6 | MIDDLETOWN 1101644756 | 15.2593 | 66.8951 | 65.0459 | 1.8492 | 0.3342% | Vegetation contact Equipment failure Contact from object
7 | STANISLAUS 1701CB | 38.5242 | 64.2834 | 62.1173 | 2.1661 | 0.3212% | Equipment failure Contact from object Vegetation contact
8 | EL DORADO PH 210119752 | 41.5804 | 61.3359 | 55.4086 | 5.9273 | 0.3064% | Vegetation contact Equipment failure Contact from object
9 | CALPINE 1144CB | 26.7587 | 60.6956 | 58.9532 | 1.7424 | 0.3032% | Contact from object Vegetation contact Equipment failure
10 | ALLEGHANY 1102CB | 18.792 | 60.0599 | 59.7834 | 0.27645 | 0.3001% | Vegetation contact Equipment failure Contact from object
11 | MARIPOSA 210237282 | 53.2532 | 59.3946 | 57.7906 | 1.604 | 0.2967% | Equipment failure Vegetation contact Contact from object
12 | BIG BEND 1101CB | 23.51 | 57.5444 | 51.6681 | 5.8763 | 0.2875% | Equipment failure Vegetation contact Contact from object
13 | WEST POINT 11024788 | 74.2727 | 57.4156 | 54.6136 | 2.8021 | 0.2869% | Equipment failure Vegetation contact Contact from object
14 | CALAVERAS CEMENT 1101544800 | 23.5406 | 57.3184 | 57.0604 | 0.25802 | 0.2864% | Equipment failure Vegetation contact Contact from object
15 | CALAVERAS CEMENT 1101502 | 37.9251 | 56.1338 | 54.458 | 1.6758 | 0.2805% | Equipment failure Vegetation contact Contact from object
16 | CORNING 110185152 | 25.5236 | 54.4345 | 48.2352 | 6.1993 | 0.272% | Equipment failure Vegetation contact Contact from object
17 | CURTIS 17048140 | 38.0418 | 54.0429 | 51.7497 | 2.2932 | 0.27% | Equipment failure Vegetation contact Contact from object
18 | COLUMBIA HILL 1101CB | 47.9377 | 53.4681 | 50.684 | 2.784 | 0.2671% | Vegetation contact Equipment failure Contact from object
19 | TEMPLETON 2113A12 | 41.3599 | 53.4192 | 53.0356 | 0.38359 | 0.2669% | Equipment failure Contact from object Vegetation contact
20 | FORT ROSS 112170288 | 25.013 | 52.9255 | 52.6791 | 0.24643 | 0.2644% | Vegetation contact Equipment failure Contact from object
21 | BIG BEND 1101641808 | 29.532 | 52.57 | 47.0195 | 5.5505 | 0.2626% | Equipment failure Vegetation contact Contact from object
22 | MARIPOSA 2101752630 | 19.2425 | 51.4021 | 51.3695 | 0.032589 | 0.2568% | Equipment failure Vegetation contact Contact from object
23 | SILVERADO 2104633600 | 25.0577 | 50.5596 | 44.9826 | 5.577 | 0.2526% | Equipment failure Vegetation contact Contact from object
24 | VACAVILLE 110838316 | 15.7285 | 49.3106 | 47.764 | 1.5466 | 0.2464% | Equipment failure Vegetation contact Contact from object
25 | APPLE HILL 110497086 | 28.4004 | 49.1966 | 46.843 | 2.3536 | 0.2458% | Vegetation contact Equipment failure Contact from object
26 | APPLE HILL 21029722 | 40.0897 | 48.5389 | 46.5058 | 2.0331 | 0.2425% | Vegetation contact Equipment failure Contact from object
27 | MIDDLETOWN 1101548 | 31.27 | 48.4984 | 41.3425 | 7.1559 | 0.2423% | Equipment failure Vegetation contact Contact from object
28 | PINE GROVE 11026080 | 34.8802 | 48.1154 | 46.5222 | 1.5931 | 0.2404% | Vegetation contact Equipment failure Contact from object
29 | HIGHLANDS 1102628 | 19.3754 | 46.8557 | 46.5809 | 0.27478 | 0.2341% | Equipment failure Contact from object Vegetation contact
30 | PLACERVILLE 21069712 | 26.1562 | 46.2948 | 43.8896 | 2.4052 | 0.2313% | Vegetation contact Equipment failure Contact from object
31 | HARTLEY 1101698 | 21.2775 | 46.1802 | 45.9563 | 0.22392 | 0.2307% | Equipment failure Vegetation contact Contact from object
32 | PUEBLO 2103678 | 36.7092 | 45.963 | 42.0971 | 3.8658 | 0.2296% | Vegetation contact Equipment failure Contact from object
33 | MARTELL 110191216 | 41.5937 | 45.6481 | 45.3977 | 0.25043 | 0.2281% | Vegetation contact Equipment failure Contact from object
34 | REDBUD 1101323962 | 16.9079 | 45.5277 | 36.441 | 9.0867 | 0.2275% | Equipment failure Vegetation contact Contact from object
35 | MOLINO 1102318 | 27.7967 | 45.412 | 44.6383 | 0.77372 | 0.2269% | Vegetation contact Equipment failure Contact from object
36 | HIGHLANDS 1103520 | 48.0022 | 44.295 | 41.366 | 2.929 | 0.2213% | Equipment failure Vegetation contact Contact from object
37 | COARSEGOLD 210410110 | 52.3108 | 43.9578 | 41.5037 | 2.4541 | 0.2196% | Equipment failure Vegetation contact Contact from object
38 | AUBERRY 1101R2578 | 47.5091 | 43.6409 | 40.7536 | 2.8873 | 0.218% | Equipment failure Vegetation contact Contact from object
39 | MARIPOSA 210237288 | 87.0249 | 43.5691 | 42.7023 | 0.86674 | 0.2177% | Vegetation contact Equipment failure Contact from object
40 | FROGTOWN 170113412 | 43.0363 | 43.5543 | 37.8631 | 5.6911 | 0.2176% | Equipment failure Vegetation contact Contact from object
41 | ELECTRA 1101CB | 23.973 | 43.215 | 41.7064 | 1.5086 | 0.2159% | Equipment failure Vegetation contact Contact from object
42 | CORNING 11021622 | 35.3851 | 42.7053 | 41.3156 | 1.3897 | 0.2134% | Equipment failure Contact from object Vegetation contact
43 | DIAMOND SPRINGS 110676088 | 34.243 | 42.3199 | 41.9075 | 0.4124 | 0.2114% | Vegetation contact Equipment failure Contact from object
44 | BONNIE NOOK 1102CB | 30.1758 | 41.8552 | 35.1003 | 6.7549 | 0.2091% | Vegetation contact Equipment failure Contact from object
45 | BRUNSWICK 11021010 | 47.0869 | 41.6777 | 40.6525 | 1.0252 | 0.2082% | Vegetation contact Equipment failure Contact from object
46 | CURTIS 170390320 | 32.1089 | 41.0182 | 39.6973 | 1.3209 | 0.2049% | Equipment failure Vegetation contact Contact from object
47 | MARIPOSA 210110070 | 26.2826 | 40.9066 | 40.8295 | 0.077089 | 0.2044% | Equipment failure Vegetation contact Contact from object
48 | GIRVAN 11011330 | 25.9983 | 40.5343 | 35.9333 | 4.601 | 0.2025% | Vegetation contact Equipment failure Contact from object
49 | APPLE HILL 110413512 | 31.275 | 40.3039 | 32.9483 | 7.3557 | 0.2014% | Vegetation contact Equipment failure Contact from object
50 | DIAMOND SPRINGS 11057722 | 62.1778 | 40.1837 | 39.017 | 1.1667 | 0.2008% | Vegetation contact Equipment failure Contact from object
51 | BALCH NO 1 1101406582 | 3.7849 | 40.1094 | 40.1094 | 0 | 0.2004% | Equipment failure Contact from object Vegetation contact
52 | MOUNTAIN QUARRIES 21011130 | 21.4781 | 39.6503 | 38.0279 | 1.6224 | 0.1981% | Vegetation contact Equipment failure Contact from object
53 | APPLE HILL 2102836878 | 43.8876 | 39.4699 | 30.2953 | 9.1746 | 0.1972% | Vegetation contact Equipment failure Contact from object
54 | COALINGA NO 2 11059260 | 0 | 39.3637 | 39.1603 | 0.20346 | 0.1967% | Equipment failure Contact from object Vegetation contact
55 | LAYTONVILLE 1101518 | 2.1587 | 38.8951 | 38.1141 | 0.78099 | 0.1943% | Vegetation contact Equipment failure Contact from object
56 | APPLE HILL 21028372 | 59.0321 | 38.7665 | 34.2702 | 4.4963 | 0.1937% | Vegetation contact Equipment failure Contact from object
57 | LOS OSITOS 21037014 | 0 | 38.7165 | 38.6357 | 0.080815 | 0.1934% | Equipment failure Contact from object Vegetation contact
58 | STILLWATER 11021466 | 23.2457 | 38.3929 | 34.3774 | 4.0155 | 0.1918% | Equipment failure Vegetation contact Contact from object
59 | PIT NO 3 21011482 | 12.2645 | 37.308 | 37.1846 | 0.12347 | 0.1864% | Vegetation contact Equipment failure Contact from object
60 | GEYSERVILLE 1102904170 | 21.4372 | 36.9939 | 34.3796 | 2.6142 | 0.1848% | Equipment failure Vegetation contact Contact from object
61 | FORESTHILL 11011802 | 25.4503 | 36.4406 | 30.8293 | 5.6113 | 0.1821% | Vegetation contact Equipment failure Contact from object
62 | FITCH MOUNTAIN 111324918 | 24.6009 | 36.4262 | 35.8264 | 0.59982 | 0.182% | Vegetation contact Equipment failure Contact from object
63 | MARIPOSA 2101439030 | 21.0606 | 36.0716 | 35.9859 | 0.085693 | 0.1802% | Vegetation contact Equipment failure Contact from object
64 | CLAYTON 221296224 | 10.2379 | 35.9806 | 35.4507 | 0.52991 | 0.1798% | Equipment failure Vegetation contact Contact from object
65 | PEORIA 170190090 | 30.4357 | 35.8543 | 33.1277 | 2.7266 | 0.1791% | Equipment failure Contact from object Vegetation contact
66 | HOPLAND 11014626 | 25.9035 | 35.6066 | 34.6606 | 0.94602 | 0.1779% | Equipment failure Vegetation contact Contact from object
67 | SILVERADO 2104632 | 18.8126 | 35.5808 | 32.1845 | 3.3963 | 0.1778% | Vegetation contact Equipment failure Contact from object
68 | PLACERVILLE 2106935216 | 21.7834 | 35.4512 | 34.222 | 1.2292 | 0.1771% | Vegetation contact Equipment failure Contact from object
69 | APPLE HILL 2102186912 | 61.9458 | 34.9302 | 30.6161 | 4.3141 | 0.1745% | Vegetation contact Equipment failure Contact from object
70 | SHADY GLEN 1101941844 | 17.8895 | 34.5974 | 29.2227 | 5.3747 | 0.1729% | Vegetation contact Equipment failure Contact from object
71 | PINE GROVE 1102269286 | 31.6429 | 34.1506 | 26.1142 | 8.0364 | 0.1706% | Vegetation contact Equipment failure Contact from object
72 | ORO FINO 110239154 | 47.0539 | 34.0841 | 28.7396 | 5.3445 | 0.1703% | Vegetation contact Equipment failure Contact from object
73 | WEST POINT 110234416 | 27.7318 | 33.9065 | 32.2029 | 1.7036 | 0.1694% | Vegetation contact Equipment failure Contact from object
74 | CEDAR CREEK 1101CB | 50.089 | 33.7551 | 29.4514 | 4.3038 | 0.1686% | Vegetation contact Equipment failure Contact from object
75 | SISQUOC 1102M52 | 33.0745 | 33.4088 | 33.1637 | 0.24506 | 0.1669% | Equipment failure Contact from object Vegetation contact
76 | TEMPLETON 2113641367 | 39.8704 | 33.3923 | 32.9903 | 0.40202 | 0.1668% | Equipment failure Vegetation contact Contact from object
77 | MARIPOSA 21019400 | 64.2395 | 33.2984 | 31.1666 | 2.1319 | 0.1664% | Equipment failure Vegetation contact Contact from object
78 | FORESTHILL 1102359542 | 19.4347 | 32.7979 | 30.1772 | 2.6207 | 0.1639% | Vegetation contact Equipment failure Contact from object
79 | CALAVERAS CEMENT 11011419 | 15.4763 | 32.6283 | 32.0933 | 0.53505 | 0.163% | Equipment failure Vegetation contact Contact from object
80 | BRUNSWICK 110651486 | 60.9483 | 32.0751 | 30.4848 | 1.5903 | 0.1603% | Vegetation contact Equipment failure Contact from object
81 | SHINGLE SPRINGS 210913322 | 44.14 | 32.0191 | 31.847 | 0.17212 | 0.16% | Vegetation contact Equipment failure Contact from object
82 | PINE GROVE 11013170 | 41.7684 | 32.0008 | 30.8997 | 1.101 | 0.1599% | Vegetation contact Equipment failure Contact from object
83 | WEST POINT 110236676 | 17.4163 | 31.795 | 30.7184 | 1.0766 | 0.1589% | Vegetation contact Equipment failure Contact from object
84 | APPLE HILL 21021532 | 40.3981 | 31.4372 | 26.2948 | 5.1423 | 0.1571% | Vegetation contact Equipment failure Contact from object
85 | CALAVERAS CEMENT 110147968 | 17.3262 | 30.7825 | 30.4048 | 0.37764 | 0.1538% | Equipment failure Vegetation contact Contact from object
86 | WILDWOOD 1101384582 | 4.5387 | 30.7606 | 30.7594 | 0.0012027 | 0.1537% | Vegetation contact Contact from object Equipment failure
87 | SANTA YNEZ 1102320270 | 8.5371 | 30.7321 | 30.3443 | 0.38784 | 0.1535% | Equipment failure Contact from object Vegetation contact
88 | FRENCH GULCH 11022902 | 7.0593 | 30.5736 | 30.5621 | 0.011534 | 0.1528% | Vegetation contact Equipment failure Contact from object
89 | STANISLAUS 17011812 | 21.2819 | 30.5553 | 28.5064 | 2.0489 | 0.1527% | Vegetation contact Equipment failure Contact from object
90 | PERRY 110179696 | 33.3788 | 30.4315 | 30.2638 | 0.16767 | 0.152% | Equipment failure Vegetation contact Contact from object

## Table PG&E-6.1.3-1
Internal Next Steps: Jake/Nelson to confirm with Greg that we do not need to update this table -- note added by Jake 7/19/25
TABLE PG&E‑6.1.3‑1:
MITIGATION EFFECTIVENESS ALONE AND IN COMBINATION
Line No. | System Hardening Mitigation(s) | Blended Average Effectiveness(a)
1 | Undergrounding All(b) | 99%
2 | Undergrounding Primary(c) Distribution Lines | 98%
3 | Line Removal with Remote Grid | 98%
4 | Covered Conductor + EPSS + PSPS(d) | 97%
5 | Covered Conductor + EPSS + DCD | 79%
6 | Covered Conductor | 67%
_______________
(a) This effectiveness evaluation is based on an assessment of each mitigation’s prevention of an ignition from active faults of known cause on overhead assets. Company initiated outages, including PSPS outages, outages of Unknown cause, as well as outages on existing underground assets are not applicable to this study and are excluded from calculation results as “N/A.”
(b) Includes distribution primary, secondary, and services line(s).
(c) Includes distribution secondary and services parallel to targeted primary line(s).
(d) The combined “Overhead with EPSS and PSPS” effectiveness differs from others in the table as it is the result of two independent studies. The first study yields PSPS effectiveness alone to be approximately 84% effective at mitigating wildfire risk. Subsequently, the combined effectiveness of approximately 79 percent for “Overhead with EPSS” is applied on top of the PSPS reduction, resulting in: Mitigation Effectiveness = 84% + (100%‑84%) * 79% = 97%.

## Table PG&E‑6.1.3.2‑1
TABLE PG&E‑6.1.3.2‑1:
DISTRIBUTION RISK AREAS
Mitigation | Geographic Area 1: | Geographic Area 2: | Geographic Area 3:
| Top Risk Areas based on Wildfire Risk Models (HFTD/HFRA) | Remaining Risk Areas based on Wildfire Risk Models (HFTD/HFRA) | Non‑HFTD/HFRA
Comprehensive Monitoring and Data Collection
Weather Stations | X | X | X
Wildfire Cameras | X | X
Asset Inspections | X | X | X
Vegetation Inspections | X | X | X
Operational Mitigation Activities
PSPS | X | X | X
EPSS | X | X
Equipment Maintenance and Repair, Includes Pole Replacement and Reinforcement | X | X | X
Pole Clearing | X | X | X
Substation Defensible Space | X | X
Resiliency Mitigation Activities
Undergrounding | X
Covered Conductor | X | X
Distribution Line Removal | X | X
HFTD/HFRA Open Tag Reduction ‑ Distribution (Backlog) | X | X

## Table PG&E‑6.1.3.2‑2
TABLE PG&E‑6.1.3.2‑2:
TRANSMISSION RISK AREAS
Mitigation | Geographic Area 1: | Geographic Area 2:
| (HFTD/HFRA) | (Non‑HFTD/HFRA)
Comprehensive Monitoring and Data Collection
Weather Stations | X | X
Wildfire Cameras | X
Asset Inspections | X | X
Vegetation Inspections | X | X
Operational Mitigation Activities
PSPS | X | X
EPSS | X
Equipment Maintenance and Repair, Includes Pole Replacement and Reinforcement | X | X
Utility Defensible Space (Pole/Structure Clearing) | X
Integrated Vegetation Management | X | X
Substation Defensible Space | X
Resiliency Mitigation Activities
Conductor Segment Replacement | X
Line Removal (Transmission) | X
Shunt Splice Installation | X

## Table 6-2
TABLE 6‑2:
STAKEHOLDER ROLES AND RESPONSIBILITIES IN DECISION MAKING PROCESS 24
Stakeholder | Stakeholder Point of Contact | Electrical Corporation Point of Contact | Stakeholder Role | Engagement Methods | Activities | Level of Engagement for Activity
Public | Various public entities and customers | Senior Director, Customer Engagement | Consults and informs regarding various wildfire mitigation planning and execution efforts including customer resilience, outreach and education and notifications. | Regional Working Groups | Wildfire Mitigation Strategy and Activities | See Tables 11‑5 and 11‑7 (Appendix F)
Joint IOU Statewide AFN Advisory Council
Joint IOU AFN Collaborative Planning Team
Joint IOU AFN Planning Team
PG&E’s People with Disabilities and Aging Advisory Council
Wildfire Safety Webinars
Various fire agencies | Various – See Table 11‑5 in Appendix F | PSS | Coordinates with local fire suppression agencies. | Phone conversations and in‑person engagement. | Wildfire Mitigation Strategy and Activities | See Tables 11‑5 and 11‑7 (Appendix F)
The PSS team engages external public safety partners on an on‑going basis to provide wildfire and PSPS emergency preparedness information and response support. Engagements encompass a variety of outreach channels such as: first responder workshops; wildfire safety town halls; California Governor’s Office of Emergency Services Mutual Aid Regional Advisory Council; general Regional Coordinator meetings; Quarterly Regional Working Group meetings; Community Wildfire Safety Program Advisory Committee meetings; professional group meetings; training/exercises/drills; and one‑on‑one delivery. Additionally, PSS team engagement follows California’s Standardized Emergency Management System, the Federal Emergency Management Agency and the National Incident Management Systems when communicating through our respective county Office of Emergency Services channels when in‑scope for a PSPS event or wildfire emergency posture.
Various Tribes | Various – See Table 11‑7 in Appendix F | Corporate Sustainability Principal: Tribal | See Section 11.3.3. | Quarterly meetings in 2024 and e‑mails, calls, newsletters, and in‑person meetings as warranted. | Wildfire Mitigation Strategy and Activities | See Tables 11‑5 and 11‑7 (Appendix F)
Electrical Corporation SMEs | Public Safety Specialist (PSS) | Senior Director Electric Program Management (Safety and Infrastructure Protection Team (SIPT) and PSS) | Provide insight into local environmental conditions to support wildfire mitigation planning. | WRGSC | Wildfire Mitigation Strategy and Activities | Internal
Investment Planning | Director Electric Investment Planning | Director Electric Investment Planning | Facilitates the incorporation of wildfire risk mitigation program funding into PG&E’s overall electric funding target allocation. | Enterprise Business Plan Deployment Process | Wildfire Mitigation Strategy and Activities | Internal
PG&E Executive Officer Team | Chief Risk Officer and Senior Vice President (SVP), Ethics and Compliance | Not Applicable | WRGSC‑Chair | WRGSC Meetings | Wildfire Mitigation Strategy and Activities | Internal
Drives decisions to prevent catastrophic wildfires, mitigation wildfire risk and reduce customer impact. Also drives decisions to support PG&E’s obtainment of its Safety Certificate. The scope of the WRGSC is in the charter included in Figure 6.1.3.4‑1 above.
Senior PG&E Leadership Team | SVP, Electric Operations | Not Applicable | WRGSC‑Voting Member | WRGSC Meetings | Wildfire Mitigation Strategy and Activities | Internal
Drives decisions to help prevent catastrophic wildfires, mitigate wildfire risk and reduce customer impact. Also drives decisions to support PG&E’s obtainment of its Safety Certificate. Provides feedback on constraints, operability, and ability to execute on potential mitigation plans.
Senior PG&E Leadership Team | SVP, Electric Engineering | Not Applicable | WRGSC‑Voting Member | WRGSC Meetings | Wildfire Mitigation Strategy and Activities | Internal
Drives decisions to help prevent catastrophic wildfires, mitigate wildfire risk and reduce customer impact. Also drives decisions to support PG&E’s obtainment of its Safety Certificate.
Provides feedback on the engineering and strategic objectives of potential mitigation plans, including the impacts to the investment planning portfolio.
Senior PG&E Leadership | SVP, Wildfire and Emergency Operations | Not Applicable | WRGSC‑Voting Member | WRGSC Meetings | Wildfire Mitigation Strategy and Activities | Internal
Drives decisions to help prevent catastrophic wildfires, mitigate wildfire risk, and leads emergency response and operations. Also drives decisions to support PG&E’s obtainment of its Safety Certificate.
Provides guidance and direction on the overall WMP development and submission.
_______________
Note: External stakeholder roles and responsibilities are not included in this table because the external stakeholders, the points of contact, roles, and engagement methods vary. We provide a list of external stakeholders in the narrative above.
Type of Activity – All Wildfire Mitigation Initiatives
Level of Engagement – Ensure internal alignment and support

## Table 5-5B
TABLE 5‑5B:
SUMMARY OF TOP RISK CIRCUIT SEGMENTS BY RISK-PER-MILE FOR CRITICAL ISSUE RN-PGE-26-02 (a)
Risk Ranking | Circuit, Segment, or Span ID | Overall Utility Risk Score | Wildfire Risk Score | Outage Program Risk Score | Top Risk Contributors | Total Miles | Version of Risk Model Used
1 | DUNBAR 11034882 | 176.1859 | 0.17747 | 176.0084 | PSPS | 0 | WDRM v4
2 | PUEBLO 1104968601 | 126.375 | 6.9226 | 119.4523 | PSPS | 0.0076055 | WDRM v4
3 | ARBUCKLE 110130376 | 97.2091 | 0.16375 | 97.0454 | PSPS | 0 | WDRM v4
4 | VACAVILLE 111112342 | 82.7625 | 1.4368 | 81.3257 | PSPS | 0.011497 | WDRM v4
5 | BALCH NO 1 1101CB | 72.557 | 72.5546 | 0.0023826 | Wildfire | 0.11656 | WDRM v4
6 | CALPINE 1144276-G | 47.9277 | 47.9277 | 0 | Wildfire | 0.026285 | WDRM v4
7 | CASTRO VALLEY 1110MR525 | 39.7273 | 0.46269 | 39.2646 | PSPS | 0.036734 | WDRM v4
8 | MARIPOSA REMOTE 0001CB | 33.6836 | 33.6836 | 0 | Wildfire | 0.16466 | WDRM v4
9 | SPAULDING 1101CB | 30.9247 | 30.9247 | 0 | Wildfire | 0.044275 | WDRM v4
10 | TIGER CREEK 0201CB | 29.4651 | 28.2478 | 1.2173 | Wildfire | 0.41859 | WDRM v4
11 | VACAVILLE 1111772224 | 29.4415 | 0.80181 | 28.6397 | PSPS | 0.042027 | WDRM v4
12 | CALPINE 1144962 | 25.8838 | 25.8838 | 0 | Wildfire | 0.039372 | WDRM v4
13 | CORDELIA 111013382 | 22.3582 | 0.22394 | 22.1342 | PSPS | 0 | WDRM v4
14 | KESWICK 1101CB | 20.5032 | 20.4311 | 0.072072 | Wildfire | 0.016571 | WDRM v4
15 | SPRING GAP 1702188426 | 16.1191 | 16.1191 | 0 | Wildfire | 0.0028409 | WDRM v4
16 | TASSAJARA 21123202 | 14.6247 | 13.2867 | 1.338 | Wildfire | 0.40658 | WDRM v4
17 | BALCH NO 1 1101105414 | 13.0815 | 13.0801 | 0.0014073 | Wildfire | 7.4477 | WDRM v4
18 | CLARKSVILLE 210551478 | 10.9083 | 0.43436 | 10.4739 | PSPS | 0.052525 | WDRM v4
19 | BALCH NO 1 1101406582 | 10.879 | 10.879 | 0 | Wildfire | 3.7849 | WDRM v4
20 | BUCKS CREEK 1102CB | 10.0915 | 10.0915 | 0 | Wildfire | 0.02961 | WDRM v4
21 | PEABODY 2106CB | 9.9466 | 0.68243 | 9.2642 | PSPS | 0.39332 | WDRM v4
22 | APPLE HILL 1104814656 | 9.8646 | 9.8478 | 0.016861 | Wildfire | 0.017476 | WDRM v4
23 | SCE TEJON TIE 1101CB | 9.7987 | 9.7511 | 0.047605 | Wildfire | 0.063593 | WDRM v4
24 | APPLE HILL 2102CB | 8.4552 | 7.8115 | 0.64372 | Wildfire | 0.16914 | WDRM v4
25 | MIWUK 170179118 | 8.2167 | 1.7863 | 6.4303 | Wildfire PSPS | 0.01936 | WDRM v4
26 | SALT SPRINGS 210110416 | 7.6719 | 7.5096 | 0.16232 | Wildfire | 1.0622 | WDRM v4
27 | DEL MAR 210938684 | 7.1655 | 0.24078 | 6.9247 | PSPS | 0 | WDRM v4
28 | OAKLAND J 1102CR102 | 6.9718 | 0.52599 | 6.4458 | PSPS | 0.31802 | WDRM v4
29 | WILDWOOD 1101384582 | 6.7774 | 6.7771 | 0.00026499 | Wildfire | 4.5387 | WDRM v4
30 | ALLEGHANY 1102WC 1101/2 | 6.5346 | 6.4582 | 0.076432 | Wildfire | 0.014692 | WDRM v4
31 | CALPINE 1146200-G | 5.804 | 5.804 | 0 | Wildfire | 0.0085228 | WDRM v4
32 | MARIPOSA 2101929360 | 5.6757 | 5.655 | 0.020699 | Wildfire | 0.067118 | WDRM v4
33 | CALPINE 1144304 | 5.6383 | 5.5865 | 0.051748 | Wildfire | 0.046358 | WDRM v4
34 | MONTICELLO 11011780 | 5.6225 | 1.247 | 4.3755 | Wildfire PSPS | 0.071663 | WDRM v4
35 | CEDAR CREEK 1101451856 | 5.5841 | 5.0782 | 0.50592 | Wildfire | 0.054774 | WDRM v4
36 | WYANDOTTE 11102590 | 5.4781 | 0.081003 | 5.397 | PSPS | 0 | WDRM v4
37 | VACAVILLE 1104CB | 5.4088 | 0.30631 | 5.1025 | PSPS | 0.43832 | WDRM v4
38 | RINCON 1102228730 | 5.3527 | 0.059847 | 5.2929 | PSPS | 0 | WDRM v4
39 | ELECTRA 1102CB | 5.3009 | 5.2504 | 0.050509 | Wildfire | 2.6041 | WDRM v4
40 | KESWICK 1101417066 | 5.2673 | 4.7976 | 0.46971 | Wildfire | 2.7584 | WDRM v4
41 | PIT NO 5 1101923612 | 5.1486 | 5.133 | 0.015596 | Wildfire | 0.85019 | WDRM v4
42 | NARROWS 2104CB | 5.0577 | 5.0577 | 0 | Wildfire | 0.0028409 | WDRM v4
43 | FRENCH GULCH 11011892 | 5.0522 | 5.0508 | 0.0014161 | Wildfire | 3.0199 | WDRM v4
44 | MARINA (F) 1101CB | 5.0335 | 5.0335 | 0 | Wildfire | 0 | WDRM v4
45 | CALISTOGA 110135588 | 4.9896 | 4.2731 | 0.71653 | Wildfire PSPS | 2.9426 | WDRM v4
46 | VACAVILLE 1104196294 | 4.9538 | 0.61011 | 4.3437 | Wildfire PSPS | 0.50768 | WDRM v4
47 | DOBBINS 1101CB | 4.8355 | 4.77 | 0.065504 | Wildfire | 0.74813 | WDRM v4
48 | CLAYTON 221296224 | 4.6805 | 4.6116 | 0.068933 | Wildfire | 10.2379 | WDRM v4
49 | WEST POINT 1101CB | 4.5246 | 4.5142 | 0.010392 | Wildfire | 4.8561 | WDRM v4
50 | TIGER CREEK 0201320746 | 4.5032 | 4.5016 | 0.0016526 | Wildfire | 3.5158 | WDRM v4
51 | TRIDAM POWERHOUSE 2101CB | 4.4824 | 4.4824 | 0 | Wildfire | 0.050742 | WDRM v4
52 | ELECTRA 110213414 | 4.4308 | 0.69535 | 3.7355 | Wildfire PSPS | 0 | WDRM v4
53 | CALPINE 1146394G | 4.3817 | 4.3817 | 0 | Wildfire | 0.011289 | WDRM v4
54 | FRENCH GULCH 11022902 | 4.3534 | 4.3518 | 0.0016423 | Wildfire | 7.0593 | WDRM v4
55 | MOUNTAIN QUARRIES 2101CB | 4.3308 | 4.2729 | 0.057947 | Wildfire | 0.052999 | WDRM v4
56 | VACA DIXON 110175740 | 4.0999 | 0.83569 | 3.2642 | Wildfire PSPS | 0.16543 | WDRM v4
57 | TASSAJARA 2112791386 | 4.0778 | 3.8409 | 0.23685 | Wildfire | 2.4789 | WDRM v4
58 | VACAVILLE 110847860 | 3.996 | 0.31624 | 3.6798 | PSPS | 0.31452 | WDRM v4
59 | DRUM 1101CB | 3.9822 | 3.9688 | 0.01341 | Wildfire | 2.1646 | WDRM v4
60 | PARADISE 1104457900 | 3.9774 | 1.1108 | 2.8666 | Wildfire PSPS | 3.6819 | WDRM v4
61 | DEL MAR 210975802 | 3.9728 | 0.14803 | 3.8247 | PSPS | 0.34916 | WDRM v4
62 | SILVERADO 2104209359 | 3.9382 | 2.4759 | 1.4623 | Wildfire PSPS EPSS | 0.013609 | WDRM v4
63 | BURNS 2101BL 2101 | 3.9313 | 3.9313 | 0 | Wildfire | 0.0032255 | WDRM v4
64 | MONROE 210392868 | 3.905 | 0.30315 | 3.6019 | PSPS | 0.1478 | WDRM v4
65 | POINT MORETTI 110135874 | 3.8671 | 3.8539 | 0.013151 | Wildfire | 0.21817 | WDRM v4
66 | ORO FINO 11022236 | 3.8531 | 3.833 | 0.020147 | Wildfire | 2.5753 | WDRM v4
67 | WISHON 1101CB | 3.8495 | 3.8495 | 0 | Wildfire | 0.034573 | WDRM v4
68 | CLAYTON 2212681608 | 3.7092 | 3.4452 | 0.26405 | Wildfire | 33.2215 | WDRM v4
69 | NEWARK 21KV 2111CB | 3.6765 | 3.6765 | 0 | Wildfire | 0 | WDRM v4
70 | PLACERVILLE 210658118 | 3.6745 | 2.8262 | 0.84834 | Wildfire EPSS | 0.10823 | WDRM v4
71 | MIDDLETOWN 1101644756 | 3.6635 | 3.5622 | 0.10127 | Wildfire | 15.2593 | WDRM v4
72 | ELECTRA 1101L1697 | 3.6542 | 3.5097 | 0.14443 | Wildfire | 7.014 | WDRM v4
73 | CLOVERDALE 1102672 | 3.6392 | 3.5413 | 0.097883 | Wildfire | 22.4533 | WDRM v4
74 | KESWICK 11011586 | 3.6344 | 3.6086 | 0.025805 | Wildfire | 4.8476 | WDRM v4
75 | CRESTA 1101103126 | 3.6138 | 2.3335 | 1.2803 | Wildfire PSPS | 0.90656 | WDRM v4
76 | FORT ROSS 1121CB | 3.6095 | 3.579 | 0.030478 | Wildfire | 0.016114 | WDRM v4
77 | VACAVILLE 1109799940 | 3.5599 | 0.57145 | 2.9885 | Wildfire PSPS | 0.51138 | WDRM v4
78 | CALPINE 1146CB | 3.5544 | 3.5544 | 0 | Wildfire | 3.7722 | WDRM v4
79 | GUSTINE 1102999258 | 3.5336 | 3.5326 | 0.0010053 | Wildfire | 0 | WDRM v4
80 | PARADISE 11042206 | 3.5153 | 0.19143 | 3.3238 | PSPS | 1.3978 | WDRM v4
81 | TASSAJARA 2112900058 | 3.5142 | 0.12947 | 3.3847 | PSPS | 0.070765 | WDRM v4
82 | PIKE CITY 11011720 | 3.5082 | 3.4639 | 0.044308 | Wildfire | 6.0244 | WDRM v4
83 | CALPINE 1144960 | 3.5061 | 3.5061 | 0 | Wildfire | 4.0614 | WDRM v4
84 | MADISON 1105995448 | 3.5017 | 3.4801 | 0.021553 | Wildfire | 0.29939 | WDRM v4
85 | CURTIS 1703258550 | 3.4759 | 3.4043 | 0.071563 | Wildfire | 8.4333 | WDRM v4
86 | VOLTA 110280982 | 3.4467 | 0.52876 | 2.918 | Wildfire PSPS | 0.50915 | WDRM v4
87 | ALLEGHANY 1102CB | 3.3977 | 3.3821 | 0.015639 | Wildfire | 18.792 | WDRM v4
88 | SILVERADO 2104646776 | 3.3656 | 2.7023 | 0.66333 | Wildfire PSPS | 5.6737 | WDRM v4
89 | ALTO 1124432 | 3.3596 | 3.2262 | 0.13339 | Wildfire | 11.917 | WDRM v4
90 | SILVERADO 2104940 | 3.3116 | 0.11626 | 3.1953 | PSPS | 0 | WDRM v4
91 | SCE REFUGIO 1701CB | 3.2543 | 3.2543 | 0 | Wildfire | 0.08053 | WDRM v4
92 | PINECREST 0401CB | 3.2279 | 3.207 | 0.020866 | Wildfire | 0.019597 | WDRM v4
93 | TEJON 11023760 | 3.1141 | 3.1141 | 0 | Wildfire | 6.4767 | WDRM v4
94 | CUYAMA 1103684566 | 3.1017 | 3.0854 | 0.016302 | Wildfire | 2.5774 | WDRM v4
95 | PIT NO 5 11011614 | 3.0876 | 3.0876 | 4.0719e-06 | Wildfire | 1.8419 | WDRM v4
96 | PIT NO 3 21011482 | 3.0725 | 3.0623 | 0.010169 | Wildfire | 12.2645 | WDRM v4
97 | PARADISE 11051212 | 3.0265 | 1.6898 | 1.3367 | Wildfire PSPS | 2.2457 | WDRM v4
98 | DIAMOND SPRINGS 1106176130 | 3.0145 | 0.72037 | 2.2942 | Wildfire PSPS | 0.019568 | WDRM v4
99 | BALCH NO 1 1101R372 | 3.0025 | 3.0025 | 3.095e-05 | Wildfire | 3.893 | WDRM v4
100 | PIT NO 5 110190846 | 2.999 | 2.999 | 4.0542e-05 | Wildfire | 0.088249 | WDRM v4
101 | TASSAJARA 2112D514R | 2.9167 | 0.5566 | 2.3601 | Wildfire PSPS | 0.58213 | WDRM v4
102 | WHITMORE 1101WTGLR | 2.9085 | 2.6958 | 0.21269 | Wildfire | 0.0029471 | WDRM v4
103 | TEJON 11022455 | 2.8946 | 2.6098 | 0.28485 | Wildfire | 7.8949 | WDRM v4
104 | BIG BASIN 1101124854 | 2.8928 | 2.8928 | 0 | Wildfire | 0.020075 | WDRM v4
105 | PIT NO 5 1101CB | 2.8712 | 2.8555 | 0.015738 | Wildfire | 0.13506 | WDRM v4
106 | ROSSMOOR 1102457174 | 2.8627 | 0.14356 | 2.7191 | PSPS | 0.4469 | WDRM v4
107 | RINCON 1101CB | 2.8527 | 0.12629 | 2.7264 | PSPS EPSS | 0.98207 | WDRM v4
108 | EL DORADO PH 2101757474 | 2.8386 | 2.8386 | 0 | Wildfire | 3.1096 | WDRM v4
109 | ALLEGHANY 1101SC 1101/2 | 2.836 | 2.7063 | 0.12965 | Wildfire | 0.017838 | WDRM v4
110 | MIWUK 170236888 | 2.8176 | 2.8055 | 0.012096 | Wildfire | 0.76273 | WDRM v4
111 | MIDDLETOWN 1101959140 | 2.7908 | 2.7143 | 0.076469 | Wildfire | 3.8629 | WDRM v4
112 | MARIPOSA 2101752630 | 2.7473 | 2.7456 | 0.0017418 | Wildfire | 19.2425 | WDRM v4
113 | MONTICELLO 1101130412 | 2.7439 | 2.3741 | 0.3698 | Wildfire PSPS | 3.7054 | WDRM v4
114 | INDIAN FLAT 1104CB | 2.7316 | 2.6933 | 0.038331 | Wildfire | 11.2205 | WDRM v4
115 | STELLING 11109265 | 2.7077 | 2.6672 | 0.040518 | Wildfire | 5.5009 | WDRM v4
116 | EL DORADO PH 2101CB | 2.7019 | 2.5558 | 0.14601 | Wildfire | 7.6912 | WDRM v4
117 | REDBUD 1101454 | 2.6979 | 2.6115 | 0.086456 | Wildfire | 5.8139 | WDRM v4
118 | PINE GROVE 110245292 | 2.6827 | 2.4192 | 0.26354 | Wildfire | 12.0223 | WDRM v4
119 | MONTE RIO 1113320 | 2.6771 | 2.6756 | 0.001519 | Wildfire | 4.8875 | WDRM v4
120 | CLOVERDALE 11024646 | 2.6452 | 0.50893 | 2.1362 | Wildfire PSPS | 0.14877 | WDRM v4
121 | SHINGLE SPRINGS 2108449638 | 2.6301 | 2.6238 | 0.0063384 | Wildfire | 0.024308 | WDRM v4
122 | CALISTOGA 1101894220 | 2.6178 | 2.5379 | 0.079965 | Wildfire | 11.234 | WDRM v4
123 | ALTO 11243745 | 2.557 | 2.4581 | 0.098911 | Wildfire | 5.6898 | WDRM v4
124 | HIGHLANDS 1102628 | 2.5569 | 2.5419 | 0.014994 | Wildfire | 19.3754 | WDRM v4
125 | JAMESON 110560052 | 2.5493 | 2.5151 | 0.034246 | Wildfire | 7.0227 | WDRM v4
126 | STANISLAUS 1702CB | 2.5402 | 2.4045 | 0.13569 | Wildfire | 8.9078 | WDRM v4
127 | OAKLAND K 1101CR178 | 2.5196 | 0.31939 | 2.2002 | Wildfire PSPS | 0.51299 | WDRM v4
128 | SHINGLE SPRINGS 210551738 | 2.502 | 0.093885 | 2.4081 | PSPS EPSS | 0.016579 | WDRM v4
129 | BIG BEND 1101CB | 2.4971 | 2.2421 | 0.25499 | Wildfire | 23.51 | WDRM v4
130 | PLACERVILLE 1109CB | 2.4948 | 0.55152 | 1.9432 | Wildfire PSPS | 0.0088181 | WDRM v4
131 | VACAVILLE 1103CB | 2.4945 | 0.1166 | 2.3779 | PSPS | 0 | WDRM v4
132 | CALAVERAS CEMENT 1101544800 | 2.4931 | 2.4819 | 0.011223 | Wildfire | 23.5406 | WDRM v4
133 | ALLEGHANY 1101DC 1101/2 | 2.4753 | 2.3353 | 0.13993 | Wildfire | 0.020333 | WDRM v4
134 | PARADISE 1105829194 | 2.4463 | 2.1427 | 0.30359 | Wildfire PSPS | 16.3296 | WDRM v4
135 | RINCON 110275816 | 2.4352 | 0.042197 | 2.393 | PSPS | 0 | WDRM v4
136 | WILLOW CREEK 1103181562 | 2.4196 | 1.9909 | 0.4287 | Wildfire EPSS | 0.0028409 | WDRM v4
137 | MARIPOSA 2102241564 | 2.4167 | 1.999 | 0.41774 | Wildfire EPSS | 1.0269 | WDRM v4
138 | BONNIE NOOK 1102542186 | 2.4059 | 2.3515 | 0.054357 | Wildfire | 8.1331 | WDRM v4
139 | TULE POWER HOUSE 1101CB | 2.4021 | 2.4021 | 0 | Wildfire | 4.2565 | WDRM v4
140 | PARADISE 1104954322 | 2.3916 | 1.6057 | 0.78591 | Wildfire PSPS | 3.3999 | WDRM v4
141 | SAN LUIS OBISPO 1104982992 | 2.38 | 2.3788 | 0.0012202 | Wildfire | 8.6324 | WDRM v4
142 | MIWUK 17021808 | 2.3751 | 2.0994 | 0.27566 | Wildfire PSPS | 3.3237 | WDRM v4
143 | CORNING 110185152 | 2.3597 | 2.091 | 0.26874 | Wildfire PSPS | 25.5236 | WDRM v4
144 | SANTA YNEZ 1101980192 | 2.3546 | 2.3064 | 0.048196 | Wildfire | 3.8797 | WDRM v4
145 | TASSAJARA 2112676362 | 2.3531 | 2.3284 | 0.024745 | Wildfire | 3.1497 | WDRM v4
146 | DEL MONTE 2104181640 | 2.3496 | 2.0582 | 0.29131 | Wildfire EPSS | 0.016177 | WDRM v4
147 | SILVERADO 210478268 | 2.3463 | 1.7995 | 0.54678 | Wildfire PSPS | 13.5964 | WDRM v4
148 | PUEBLO 110298730 | 2.3348 | 0.13851 | 2.1963 | PSPS | 0 | WDRM v4
149 | BUCKS CREEK 1103CB | 2.334 | 2.2954 | 0.038623 | Wildfire | 2.6656 | WDRM v4
150 | ALLEGHANY 1101VR816 | 2.3141 | 2.1641 | 0.14993 | Wildfire | 6.2444 | WDRM v4
151 | CALPINE 1144CB | 2.2869 | 2.2213 | 0.065653 | Wildfire | 26.7587 | WDRM v4
152 | PEORIA 1704877670 | 2.2751 | 2.2695 | 0.0055409 | Wildfire | 6.3809 | WDRM v4
153 | SILVERADO 2104324994 | 2.271 | 2.062 | 0.20898 | Wildfire | 0.78323 | WDRM v4
154 | CALPINE 1146400 | 2.2222 | 2.2222 | 0 | Wildfire | 1.8423 | WDRM v4
155 | ROUND MOUNTAIN 1101CB | 2.2108 | 2.2108 | 0 | Wildfire | 0.015504 | WDRM v4
156 | FORT ROSS 112170288 | 2.2077 | 2.1974 | 0.01028 | Wildfire | 25.013 | WDRM v4
157 | CASTRO VALLEY 1108MR233 | 2.2072 | 0.17893 | 2.0282 | PSPS | 0.13457 | WDRM v4
158 | PUEBLO 2103489964 | 2.2012 | 0.083603 | 2.1176 | PSPS | 0 | WDRM v4
159 | CALAVERAS CEMENT 11011419 | 2.1915 | 2.1556 | 0.035938 | Wildfire | 15.4763 | WDRM v4
160 | ELECTRA 11017104 | 2.1841 | 2.0976 | 0.086483 | Wildfire | 13.5819 | WDRM v4
161 | MARIPOSA 2102851902 | 2.1796 | 2.0876 | 0.092035 | Wildfire | 5.2046 | WDRM v4
162 | OAKLAND K 1102172340 | 2.1546 | 0.6036 | 1.551 | Wildfire PSPS | 1.4595 | WDRM v4
163 | SILVERADO 2105990552 | 2.1473 | 0.65698 | 1.4903 | Wildfire PSPS EPSS | 0.92532 | WDRM v4
164 | PLACERVILLE 2106CB | 2.1426 | 1.9849 | 0.15769 | Wildfire | 6.2833 | WDRM v4
165 | VACAVILLE 110838316 | 2.1419 | 2.0747 | 0.067178 | Wildfire | 15.7285 | WDRM v4
166 | RINCON 1103472 | 2.1394 | 0.084649 | 2.0547 | PSPS | 4.3043 | WDRM v4
167 | STELLING 1110568350 | 2.13 | 2.0896 | 0.040384 | Wildfire | 11.4785 | WDRM v4
168 | ALLEGHANY 1101806 | 2.1156 | 2.1064 | 0.0092331 | Wildfire | 11.9844 | WDRM v4
169 | PIT NO 3 2101CB | 2.1136 | 2.1065 | 0.0070841 | Wildfire | 5.5034 | WDRM v4
170 | FORESTHILL 110150486 | 2.1082 | 1.9145 | 0.19374 | Wildfire | 14.7593 | WDRM v4
171 | VACAVILLE 1108922767 | 2.1076 | 1.6708 | 0.43678 | Wildfire PSPS | 8.4118 | WDRM v4
172 | SILVERADO 2104CB | 2.1036 | 0.11035 | 1.9933 | PSPS | 0 | WDRM v4
173 | RINCON 1102CB | 2.0779 | 0.14554 | 1.9324 | PSPS | 1.9357 | WDRM v4
174 | PARADISE 1105878870 | 2.0718 | 1.1993 | 0.87249 | Wildfire PSPS EPSS | 13.6803 | WDRM v4
175 | SHADY GLEN 1101941844 | 2.0608 | 1.7407 | 0.32015 | Wildfire PSPS | 17.8895 | WDRM v4
176 | PUTAH CREEK 110267858 | 2.0575 | 1.9636 | 0.093899 | Wildfire | 11.1761 | WDRM v4
177 | PIKE CITY 1102CB | 2.0457 | 1.944 | 0.10165 | Wildfire | 9.8499 | WDRM v4
178 | FRENCH GULCH 1101CB | 2.0411 | 1.9245 | 0.11653 | Wildfire | 2.7103 | WDRM v4
179 | MIDDLETOWN 1101614 | 2.034 | 1.2235 | 0.81053 | Wildfire PSPS | 2.0676 | WDRM v4
180 | BONNIE NOOK 1101CB | 2.0242 | 1.863 | 0.16121 | Wildfire | 17.7515 | WDRM v4
181 | COALINGA NO 2 11059260 | 2.0201 | 2.0097 | 0.010442 | Wildfire | 0 | WDRM v4
182 | CLAYTON 2212614950 | 2.0166 | 1.9823 | 0.03429 | Wildfire | 0.67567 | WDRM v4
183 | PUEBLO 110247720 | 2.0082 | 0.11585 | 1.8923 | PSPS | 0 | WDRM v4
184 | NOTRE DAME 11042028 | 2.0074 | 1.9987 | 0.0087397 | Wildfire | 11.4061 | WDRM v4
185 | CLAYTON 2212334476 | 1.9969 | 0.8502 | 1.1467 | Wildfire PSPS | 0.031767 | WDRM v4
186 | SUNOL 1101298061 | 1.9949 | 1.927 | 0.067903 | Wildfire | 6.5459 | WDRM v4
187 | MOUNTAIN QUARRIES 21011130 | 1.9857 | 1.9044 | 0.081248 | Wildfire | 21.4781 | WDRM v4
188 | RINCON 1104786782 | 1.982 | 0.38292 | 1.5991 | Wildfire PSPS | 3.1473 | WDRM v4
189 | GARCIA 0401CB | 1.9759 | 1.9759 | 0 | Wildfire | 0.032213 | WDRM v4
190 | DUNBAR 1103799422 | 1.9636 | 1.837 | 0.12663 | Wildfire | 0.43286 | WDRM v4
191 | VACAVILLE 1104293462 | 1.9608 | 1.8851 | 0.075707 | Wildfire | 1.0785 | WDRM v4
192 | HARTLEY 1101698 | 1.9534 | 1.944 | 0.009472 | Wildfire | 21.2775 | WDRM v4
193 | PUTAH CREEK 1105665952 | 1.9494 | 1.8349 | 0.11454 | Wildfire | 0.060491 | WDRM v4
194 | SILVERADO 2104632 | 1.9481 | 1.7621 | 0.18595 | Wildfire | 18.8126 | WDRM v4
195 | SILVERADO 2105CB | 1.9357 | 0.12371 | 1.812 | PSPS EPSS | 0.016501 | WDRM v4
196 | TEJON 1102732836 | 1.9304 | 1.4115 | 0.51892 | Wildfire PSPS | 17.4481 | WDRM v4
197 | CAMP EVERS 2104189010 | 1.9274 | 0.53798 | 1.3894 | Wildfire EPSS | 0.027848 | WDRM v4
198 | APPLE HILL 110497086 | 1.9243 | 1.8322 | 0.092057 | Wildfire | 28.4004 | WDRM v4
199 | CALISTOGA 1101730666 | 1.9147 | 1.9002 | 0.014489 | Wildfire | 2.1883 | WDRM v4
200 | WEST POINT 110236676 | 1.9106 | 1.8459 | 0.064694 | Wildfire | 17.4163 | WDRM v4
201 | KONOCTI 1102714370 | 1.9064 | 1.8301 | 0.076255 | Wildfire | 2.9574 | WDRM v4
202 | SILVERADO 2104806500 | 1.9019 | 1.4858 | 0.41613 | Wildfire PSPS | 14.2716 | WDRM v4
203 | STILLWATER 11021466 | 1.8976 | 1.6991 | 0.19847 | Wildfire PSPS | 23.2457 | WDRM v4
204 | PIT NO 3 21011480 | 1.8936 | 1.8824 | 0.011181 | Wildfire | 2.21 | WDRM v4
205 | NARROWS PH 1151CB | 1.8835 | 1.8835 | 0 | Wildfire | 0.19775 | WDRM v4
206 | WILDWOOD 11011454 | 1.8774 | 1.8696 | 0.0077293 | Wildfire | 7.9395 | WDRM v4
207 | PINE GROVE 1101CB | 1.8764 | 1.7044 | 0.17198 | Wildfire | 5.0788 | WDRM v4
208 | REDBUD 1101323962 | 1.8751 | 1.5009 | 0.37424 | Wildfire PSPS | 16.9079 | WDRM v4
209 | PLACERVILLE 21069712 | 1.8738 | 1.7764 | 0.097352 | Wildfire | 26.1562 | WDRM v4
210 | CLARKSVILLE 2106CB | 1.8734 | 0.093649 | 1.7797 | PSPS | 0.014002 | WDRM v4
211 | WOODACRE 1102851 | 1.8733 | 1.4871 | 0.38619 | Wildfire PSPS | 2.233 | WDRM v4
212 | SARATOGA 1107667000 | 1.8663 | 1.8204 | 0.045886 | Wildfire | 8.4689 | WDRM v4
213 | ELECTRA 1101CB | 1.8561 | 1.7913 | 0.064798 | Wildfire | 23.973 | WDRM v4
214 | MARIPOSA 2101439030 | 1.8555 | 1.8511 | 0.0044079 | Wildfire | 21.0606 | WDRM v4
215 | ANTLER 11011376 | 1.8554 | 1.7778 | 0.077647 | Wildfire | 9.3242 | WDRM v4
216 | FRENCH GULCH 11011464 | 1.8521 | 1.849 | 0.0031039 | Wildfire | 0.90273 | WDRM v4
217 | ALTO 11221260 | 1.8493 | 1.8465 | 0.002775 | Wildfire | 5.7115 | WDRM v4
218 | RINCON 1104CB | 1.8468 | 0.069249 | 1.7775 | PSPS | 0 | WDRM v4
219 | TEJON 11023751 | 1.8452 | 1.6363 | 0.20891 | Wildfire PSPS | 8.6778 | WDRM v4
220 | RINCON 1102640 | 1.8446 | 0.061982 | 1.7826 | PSPS | 0 | WDRM v4
221 | CLARK ROAD 110247006 | 1.8411 | 1.5854 | 0.25577 | Wildfire PSPS | 4.6914 | WDRM v4
222 | VACAVILLE 11046542 | 1.8401 | 0.66542 | 1.1746 | Wildfire PSPS | 12.1806 | WDRM v4
223 | BIG BEND 1101641808 | 1.8395 | 1.6452 | 0.19422 | Wildfire PSPS | 29.532 | WDRM v4
224 | PIT NO 5 11011658 | 1.8335 | 1.8281 | 0.0054096 | Wildfire | 4.7641 | WDRM v4
225 | REDBUD 1101754544 | 1.8323 | 1.8027 | 0.029605 | Wildfire | 4.1597 | WDRM v4
226 | PIKE CITY 1101417084 | 1.8308 | 1.6172 | 0.21356 | Wildfire PSPS | 12.3056 | WDRM v4
227 | BEAR VALLEY 2105CB | 1.8205 | 1.7945 | 0.025939 | Wildfire | 3.7249 | WDRM v4
228 | CALAVERAS CEMENT 110147968 | 1.7987 | 1.7766 | 0.022066 | Wildfire | 17.3262 | WDRM v4
229 | EL DORADO PH 210219562 | 1.7867 | 1.4489 | 0.33779 | Wildfire PSPS | 3.3789 | WDRM v4
230 | DUNLAP 1103CB | 1.786 | 1.7686 | 0.017448 | Wildfire | 5.6209 | WDRM v4
231 | RINCON 1103649194 | 1.7847 | 0.050877 | 1.7338 | PSPS | 0 | WDRM v4
232 | SANTA YNEZ 1102320270 | 1.7837 | 1.7612 | 0.02251 | Wildfire | 8.5371 | WDRM v4
233 | EL DORADO PH 2102927014 | 1.7812 | 1.2516 | 0.52964 | Wildfire PSPS | 5.0935 | WDRM v4
234 | FORESTHILL 1102359542 | 1.7752 | 1.6333 | 0.14185 | Wildfire | 19.4347 | WDRM v4
235 | MIDDLETOWN 1101548 | 1.7691 | 1.5081 | 0.26104 | Wildfire PSPS | 31.27 | WDRM v4
236 | CLOVERDALE 110282888 | 1.7681 | 0.11191 | 1.6562 | PSPS | 0 | WDRM v4
237 | BIG BEND 1102884340 | 1.7598 | 0.65719 | 1.1026 | Wildfire PSPS | 1.112 | WDRM v4
238 | STANISLAUS 1701CB | 1.7589 | 1.6997 | 0.059268 | Wildfire | 38.5242 | WDRM v4
239 | COLUMBIA HILL 11012212 | 1.7554 | 1.643 | 0.11239 | Wildfire | 8.8989 | WDRM v4
240 | MOLINO 1102318 | 1.7496 | 1.7197 | 0.029808 | Wildfire | 27.7967 | WDRM v4
241 | LAURELES 111110141 | 1.7485 | 1.6919 | 0.056597 | Wildfire | 3.6622 | WDRM v4
242 | LAYTONVILLE 1101518 | 1.7333 | 1.6985 | 0.034803 | Wildfire | 2.1587 | WDRM v4
243 | SHADY GLEN 11012768 | 1.7317 | 1.5496 | 0.18208 | Wildfire PSPS | 7.3266 | WDRM v4
244 | LARKIN (Y) 1127CB | 1.7312 | 1.7312 | 0 | Wildfire | 0 | WDRM v4
245 | SHADY GLEN 1101898212 | 1.7303 | 0.92599 | 0.80432 | Wildfire PSPS | 0.42251 | WDRM v4
246 | EL DORADO PH 2102CB | 1.7262 | 1.4253 | 0.30092 | Wildfire PSPS | 6.6637 | WDRM v4
247 | WEST POINT 11021305 | 1.723 | 1.6868 | 0.036201 | Wildfire | 11.8861 | WDRM v4
248 | PLACERVILLE 2106935216 | 1.7218 | 1.6621 | 0.059701 | Wildfire | 21.7834 | WDRM v4
249 | PIT NO 7 1101CB | 1.7059 | 1.702 | 0.0039183 | Wildfire | 2.8406 | WDRM v4
250 | MIDDLETOWN 11011314 | 1.7043 | 1.2842 | 0.42008 | Wildfire PSPS | 0.97681 | WDRM v4
251 | ELK 1101CB | 1.7016 | 1.6809 | 0.020744 | Wildfire | 0.0077088 | WDRM v4
252 | DUNBAR 1103234 | 1.6914 | 1.3785 | 0.31297 | Wildfire PSPS | 7.7554 | WDRM v4
253 | ANTLER 1101484276 | 1.6897 | 1.6879 | 0.0017491 | Wildfire | 5.7155 | WDRM v4
254 | BEAR VALLEY 21059480 | 1.6857 | 1.668 | 0.017682 | Wildfire | 12.5214 | WDRM v4
255 | COVELO 1101516510 | 1.68 | 1.6792 | 0.00077511 | Wildfire | 3.8122 | WDRM v4
256 | COALINGA NO 2 1105897858 | 1.6752 | 1.5862 | 0.089009 | Wildfire | 0 | WDRM v4
257 | FROGTOWN 17011623 | 1.6714 | 1.6596 | 0.011808 | Wildfire | 15.9509 | WDRM v4
258 | SALT SPRINGS 21023118 | 1.6682 | 1.5943 | 0.07385 | Wildfire | 0.064923 | WDRM v4
259 | MARIPOSA 2101CB | 1.667 | 1.5929 | 0.074132 | Wildfire | 2.6803 | WDRM v4
260 | SAN RAFAEL 11011250 | 1.6644 | 1.663 | 0.0013894 | Wildfire | 3.682 | WDRM v4
261 | GEYSERVILLE 1102904170 | 1.6592 | 1.5419 | 0.11725 | Wildfire | 21.4372 | WDRM v4
262 | CLAYTON 2212204416 | 1.6552 | 1.589 | 0.066133 | Wildfire | 12.9188 | WDRM v4
263 | SO. CAL. EDISON #3 1101CB | 1.6514 | 1.6483 | 0.0031143 | Wildfire | 9.3455 | WDRM v4
264 | ORO FINO 1101CB | 1.6489 | 1.0541 | 0.59475 | Wildfire PSPS | 21.3667 | WDRM v4
265 | MOUNTAIN QUARRIES 2101979598 | 1.6466 | 1.5425 | 0.1041 | Wildfire | 3.8342 | WDRM v4
266 | DUNBAR 1103160 | 1.6425 | 0.095109 | 1.5474 | PSPS | 0.19181 | WDRM v4
267 | FORESTHILL 11011802 | 1.6425 | 1.3896 | 0.25292 | Wildfire PSPS | 25.4503 | WDRM v4
268 | STANISLAUS 17026028 | 1.6412 | 1.5054 | 0.13579 | Wildfire | 9.3472 | WDRM v4
269 | MONTE RIO 1113CB | 1.6407 | 1.5315 | 0.10924 | Wildfire | 0.047363 | WDRM v4
270 | CHALLENGE 1102CB | 1.6361 | 1.4471 | 0.18895 | Wildfire | 16.0477 | WDRM v4
271 | SILVERADO 2104633600 | 1.6331 | 1.4529 | 0.18014 | Wildfire PSPS | 25.0577 | WDRM v4
272 | CORDELIA 111240402 | 1.6299 | 0.049194 | 1.5807 | PSPS | 0 | WDRM v4
273 | WEST POINT 110112256 | 1.625 | 1.4569 | 0.16806 | Wildfire | 7.3619 | WDRM v4
274 | GIRVAN 11011330 | 1.599 | 1.4175 | 0.1815 | Wildfire PSPS | 25.9983 | WDRM v4
275 | EL DORADO PH 210119752 | 1.5985 | 1.444 | 0.15447 | Wildfire | 41.5804 | WDRM v4
(a) Adjusted in response to Critical Issue RN-PGE-26-02. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Figure 6-1
FIGURE 6-1:
PROJECTED OVERALL SERVICE TERRITORY RISK
(a) Updated based on adjustments made to the overall utility risk for programs in response to Critical Issues RN-PGE-26-04, RN-PGE-26-05 an RN-PGE-26-10. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table 6-3
TABLE 6‑3:
RISK IMPACT OF ACTIVITIES
Activity | Activity Section # | Activity - Effectiveness - Overall Risk | Activity - Effectiveness - Wildfire Risk | Activity - Effectiveness - Outage Program Risk | Cost-Benefit Score - Overall Risk(e) | Cost-Benefit Score - Wildfire Risk(e) | Cost-Benefit Score - Outage Program Risk(e) | % HFTD Covered | % HFTD/HFRA Covered | Expected % Risk Reduction | Model Used to Calculate Risk Impact
Covered conductor installation(a) | 8.2.1 | 62% | 67% | 23%(f) | 19.9 | 19.2 | 0.7 | 2.7% | 2.6% | 2.8% | WDRM v4
Undergrounding of electric lines and/or equipment(a) | 8.2.2 | 98% | 98% | 100%(g) | 8.4 | 8 | 0.4 | 4.3% | 4.2% | 6% | WDRM v4
PSPS(b) | 7 | 69.87% | 95% | -59% | 28.9092 | 48.579 | -19.6698 | 100% | 100% | NA | WDRM v4
EPSS(c) | 8.2.8 | 44.73% | 65% | -73% | 35.279 | 40.0192 | -4.7402 | 100% | 100% | NA | WDRM v4
HFTD/HFRA distribution backlog tags | 8.6.2 | NA | 14% | NA | NA | NA | NA | 75% | 75% | 1.9% | WDRM v4
Pole clearing - Compliance(d) | 9.4 | NA | 20% | NA | NA | NA | NA | 3.8% | 3.8% | 0.18% | WDRM v4
Pole clearing - Risk Reduction(d) | 9.4 | NA | 20% | NA | NA | NA | NA | 3.5% | 3.8% | 0.12% | WDRM v4
Distribution routine patrol(h) | 9.2.1 | NA | 5.5% | NA | NA | NA | NA | 100% | 100% | 2.4% | WDRM v4
Service drops / breakaway connectors | 8.2.10.6 | NA | 80% | NA | NA | NA | NA | 0.58% | 0.59% | 0.016% | WDRM v4
Transmission shunt splice installation | 8.4.9.2 | NA | 88% | NA | NA | NA | NA | NA | 0.742% | 0.21% | WTRM v2
Transmission conductor segment replacement | 8.2.5.1 | NA | 75% | NA | NA | NA | NA | NA | 0.4203% | 0.14% | WTRM v2
(a) In response to Critical Issue RN-PGE-26-04 and RN-PGE-05, Cost-Benefit Score - Overall, Cost-Benefit Score - Wildfire Risk, Cost-Benefit Score - Outage Program Risk, % HFTD Covered, %HFTD/HFRA Covered, and Expect % Risk Reduction data have been updated. See 2026-2028 WMP Revision Notice Response R0 for additional information.
(b) This figure represents catastrophic wildfire effectiveness
(c) This figure represents the effectiveness of EPSS at reducing ignitions under R3 and above FPI conditions
(d) In response to Criitical Issue RN-PGE-26-10, Pole Clearing is split between Pole Clearing - Compliance and Pole Clearing - Risk Mitigation. Percent of HFTD Covered, Percent of HFTD/HFRA Covered and Expected % Risk Reduction have been updated. See 2026-2028 WMP Revision Notice Response R0 for additional information.
(e) CBR values exclude foundational costs
(f) Covered Conductor is estimated to be approximately 52% effective in mitigating EPSS outages but has no impact on PSPS planned outages. The resulting blended average effectiveness for Outage Program (defined as PSPS and EPSS) risk is 23%.
(g) Undergrounding eliminates the need to implement outage programs (i.e. PSPS and EPSS) for the undergrounded lines because they do not pose the same risk as overhead assets during the extreme weather conditions that drive outage program events. However, as explained in Section 8.2.1 and 8.2.2, the degree to which an area with underground lines may still be subject to outage events depends on whether, and how much, the upstream line sections have been overhead hardened or undergrounded.
(h) Distribution routine patrol includes work on the legacy TRI. Revised Expected % Risk Reduction as result of Critical Issue RN-PGE-26-09 updated workplan. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table PG&E-6.2.1.2-1
TABLE PG&E-6.2.1.2-1
CONTINGENCY TABLE FOR EPSS EFFECTIVENESS CALCULATION
| Ignitions | Circuit-Mile Days | p | p1/p2 | Effectiveness
EPSS | 64 | 7949193 | 8.05×10^(-6) | 0.348 | 65%
Non-EPSS | 247 | 10672567 | 2.31×10^(-5)

## Table PG&E-6.2.1.2-2
TABLE PG&E-6.2.1.2-2
EXAMPLE CALCULATIONS FOR UNDERGROUNDING AND COVERED CONDUCTOR INSTALLATION
Step | Wildfire Risk Value | Comments
Wildfire Risk Reduction
Total WDRM Risk | 1204 | Total Risk Score (uncalibrated) to
measure workplan
Workplan WDRM Risk Exposure | 25 | Risk Score associated with the miles
workplan is addressing
% Effectiveness | 98% | Program Effectiveness applied against
targeted risk exposure
Workplan Wildfire Risk | 25 * 98% = 24.5 | Risk Reduction based on program
Reduction |  | effectiveness
WDRM to Enterprise MAVF | 17,704 / 1,204 = 14.70 | Calibrating WDRM to Enterprise MAVF
Calibration |  | Distribution Wildfire Score
Workplan Risk Reduction | 24.5 * 14.70 = 360 | Calibrating Risk Reduction to Enterprise
MAVF
PSPS Risk Reduction
Total PSPS Risk | 1953 | Total PSPS Risk Score
Total Distribution PSPS Risk | 1294 | Total PSPS Risk Score attributed to
Distribution scoping
Workplan PSPS Risk Exposure | 19 | Risk Score associated with the miles
workplan is addressing
% Effectiveness | 100% | Program Effectiveness applied against
targeted risk exposure
Risk Reduction | 19 * 100% = 19 | Risk Reduction based on program
effectiveness
EPSS Risk Reduction
Total EPSS Risk | 1049 | Total EPSS Risk Score
Workplan EPSS Risk Exposure | 7 | Risk Score associated with the miles
workplan is addressing
% Effectiveness | 100% | Program Effectiveness applied against
targeted risk exposure
Risk Reduction | 7 * 100% = 7 | Risk Reduction based on program
effectiveness
Overall Risk Reduction
Total Overall Risk Reduction | 360 + 19 + 7 = 386 | Total Overall Risk Reduction
Total Overall Utility Risk | 386 / 22,426 = 1.7% | Total Overall Utility Risk Reduction %
Reduction %

## Table PG&E-6.2.1.2-3
TABLE PG&E-6.2.1.2-3
EXAMPLE CALCULATIONS FOR BACKLOG TAGS
Step | Wildfire Risk Value | Comments
Total Overall Utility Risk | 22426
Total Distribution Wildfire | 17074
Risk
Total Unit Count | 66.8K | Number of open tags
Workplan Unit Count | 16.7K | Number of expected units worked
in 2026 workplan
% Exposure | 16.7K / 66.8K = 25% | Workplan / total count
Total Unit Risk Score | 13400 | Total risk score of open tags
Workplan Unit Risk Score | 3350 | Workplan risk score of open tags
% Risk Exposure | 25% | Percent tag risk being mitigated
WDRM Equipment Risk Exposure | 35% | Percent of distribution risk associated
with equipment
% Weighted Effectiveness | 90% | Discounted effectiveness value for
equipment
% Detectability | 15% | Percent of ignitions that are detectable
via inspection, creating a tag
Risk Reduction | 13,400*25%*35%*90%*15% = 158
% Risk Reduction | 158 / 22,426 = 0.7% | Risk Reduction / Total Utility Risk

## Table PG&E-6.2.1.2-4
TABLE PG&E-6.2.1.2-4
EXAMPLE CALCULATIONS FOR POLE CLEARING, DISTRIBUTION ROUTINE PATROLS, AND BREAKAWAY CONNECTOR INSTALLATION
Step | Wildfire Risk Value | Comments
Total Overall Utility Risk | 22426
Total Distribution Wildfire Risk | 17074
Total WDRM Risk | 1204 | Total Risk Score (uncalibrated) to
measure workplan
Workplan WDRM Risk Exposure | 7 | Risk Score associated with the miles
workplan is addressing
% Effectiveness | 20% | Program Effectiveness applied against
targeted risk exposure
Workplan Wildfire Risk | 7 * 20% = 1.5 | Risk Reduction based on program
Reduction |  | effectiveness
WDRM to Enterprise MAVF | 17,704 / 1,204 = 14.70 | Calibrating WDRM to Enterprise MAVF
Calibration |  | Distribution Wildfire Score
Workplan Risk Reduction | 1.5 * 14.70 = 22 | Calibrating Risk Reduction to Enterprise
MAVF
Total Overall Utility Risk | 22 / 22,426 = 0.1% | Total Overall Utility Risk Reduction %
Reduction %

## Table PG&E-6.2.1.2-5
TABLE PG&E-6.2.1.2-5
EXAMPLE CALCULATIONS FOR POLE CLEARING, DISTRIBUTION ROUTINE PATROLS, AND BREAKAWAY CONNECTOR INSTALLATION
Step | Wildfire Risk Value | Comments
Total Overall Utility Risk | 22426
Total Non-Vegetation Transmission Wildfire Risk | 644
Total WTRM Risk | 42162 | Total Risk Score (uncalibrated) to measure workplan
Workplan WTRM Risk Exposure | 1304 | Risk Score associated with the miles workplan is addressing
% Effectiveness | 75% | Program Effectiveness applied against targeted risk exposure
Workplan Wildfire Risk Reduction | 1304 * 75% = 978 | Risk Reduction based on program effectiveness
WTRM to Enterprise MAVF Calibration | 644 / 42,162= 0.015 | Calibrating WTRM to Enterprise MAVF Transmission Wildfire Score
Workplan Risk Reduction | 978 * 0.015 = 15 | Calibrating Risk Reduction to Enterprise MAVF
Total Overall Utility Risk Reduction % | 15 / 22,426 = 0.07% | Total Overall Utility Risk Reduction %

## Table-6-4A
TABLE 6‑4A:
SUMMARY OF RISK REDUCTION FOR TOP RISK CIRCUITS BY OVERALL UTILITY RISK (a)
Line No. | Circuit Segment Name | Initial Overall Utility Risk | 2026 Activities | 2026 Overall Utility Risk | 2027 Activities | 2027 Overall Utility Risk | 2028 Activities | 2028 Overall Utility Risk
1 | CLAYTON 2212681608 | 99.7013 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.8243 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.7099 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.541
2 | BALCH NO 1 1101105414 | 91.5229 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 24.1969 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 24.1659 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 24.1349
3 | CLOVERDALE 1102672 | 80.9024 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 29.0034 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.30705 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.30705
4 | PLACERVILLE 21067522 | 72.8321 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 27.9613 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 27.0796 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 26.1312
5 | PLACERVILLE 210611132 | 67.324 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.1319 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.8786 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.6252
6 | MIDDLETOWN 1101644756 | 66.8951 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 23.9515 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 23.3049 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 22.5888
7 | STANISLAUS 1701CB | 64.2834 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.2119 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.5401 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.3956
8 | EL DORADO PH 210119752 | 61.3359 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 24.8856 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.5075 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.0583
9 | CALPINE 1144CB | 60.6956 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 22.3536 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 22.3496 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 22.3455
10 | ALLEGHANY 1102CB | 60.0599 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.6639 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.37837 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.19363
11 | MARIPOSA 210237282 | 59.3946 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 21.0752 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.3548 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.5932
12 | BIG BEND 1101CB | 57.5444 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 23.6602 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 23.3734 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 23.0866
13 | WEST POINT 11024788 | 57.4156 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 21.2357 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.5914 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.9114
14 | CALAVERAS CEMENT 1101544800 | 57.3184 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.7222 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.6011 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9327
15 | CALAVERAS CEMENT 1101502 | 56.1338 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.6031 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.5767 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.5504
16 | CORNING 110185152 | 54.4345 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 22.8158 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 22.5151 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 22.1832
17 | CURTIS 17048140 | 54.0429 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.8137 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.188 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.5267
18 | COLUMBIA HILL 1101CB | 53.4681 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.8689 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.2072 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.4983
19 | TEMPLETON 2113A12 | 53.4192 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.3365 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.8286 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.2974
20 | FORT ROSS 112170288 | 52.9255 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.8294 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.15701 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.042308
21 | BIG BEND 1101641808 | 52.57 | Line removal Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.4967 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.1657 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.8346
22 | MARIPOSA 2101752630 | 51.4021 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.6102 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.467 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.1088
23 | SILVERADO 2104633600 | 50.5596 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 21.2821 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 21.2635 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.6125
24 | VACAVILLE 110838316 | 49.3106 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.9654 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.6349 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.2692
25 | APPLE HILL 110497086 | 49.1966 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.1522 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.322 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.5685
26 | APPLE HILL 21029722 | 48.5389 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.9738 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.7742 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.5745
27 | MIDDLETOWN 1101548 | 48.4984 | Line removal Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.5087 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.6845 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.5222
28 | PINE GROVE 11026080 | 48.1154 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.8353 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.8254 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.8154
29 | HIGHLANDS 1102628 | 46.8557 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.2102 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.3418 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.1399
30 | PLACERVILLE 21069712 | 46.2948 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.6466 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.5081 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.5142
31 | HARTLEY 1101698 | 46.1802 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.7784 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.3174 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.3605
32 | PUEBLO 2103678 | 45.963 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.1129 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4145 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0737
33 | MARTELL 110191216 | 45.6481 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.449 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.7902 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.0787
34 | REDBUD 1101323962 | 45.5277 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.9176 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.7205 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 20.5026
35 | MOLINO 1102318 | 45.412 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.6865 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.9679 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.1839
36 | HIGHLANDS 1103520 | 44.295 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.9166 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.4278 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.9088
37 | COARSEGOLD 210410110 | 43.9578 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.5769 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.05 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.4906
38 | AUBERRY 1101R2578 | 43.6409 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.7856 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.277 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.749
39 | MARIPOSA 210237288 | 43.5691 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.2153 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.6424 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.0357
40 | FROGTOWN 170113412 | 43.5543 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.5863 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.161 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.7135
41 | ELECTRA 1101CB | 43.215 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.7434 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.57 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.9213
42 | CORNING 11021622 | 42.7053 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.5866 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.4139 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.2234
43 | DIAMOND SPRINGS 110676088 | 42.3199 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.6543 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.2706 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.8456
44 | BONNIE NOOK 1102CB | 41.8552 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.435 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.7329 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.2123
45 | BRUNSWICK 11021010 | 41.6777 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.0741 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.915 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.7559
46 | CURTIS 170390320 | 41.0182 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.9274 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.6534 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.2183
47 | MARIPOSA 210110070 | 40.9066 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.8125 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.7392 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.5495
48 | GIRVAN 11011330 | 40.5343 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.7866 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.3457 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.6812
49 | APPLE HILL 110413512 | 40.3039 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.7233 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.3075 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.8599
50 | DIAMOND SPRINGS 11057722 | 40.1837 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.295 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.8138 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.3021
51 | BALCH NO 1 1101406582 | 40.1094 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.0923 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.078 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.0636
52 | MOUNTAIN QUARRIES 21011130 | 39.6503 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.9006 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.58 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.1991
53 | APPLE HILL 2102836878 | 39.4699 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.55 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 19.2001 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 18.8257
54 | COALINGA NO 2 11059260 | 39.3637 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.7874 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.0046 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.3819
55 | LAYTONVILLE 1101518 | 38.8951 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.6631 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.2124 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.0894
56 | APPLE HILL 21028372 | 38.7665 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.3276 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.0538 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.7509
57 | LOS OSITOS 21037014 | 38.7165 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.5142 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.5088 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.5034
58 | STILLWATER 11021466 | 38.3929 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.6993 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.283 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.8654
59 | PIT NO 3 21011482 | 37.308 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.949 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.97863 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.86318
60 | GEYSERVILLE 1102904170 | 36.9939 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.599 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.587 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.3318
61 | FORESTHILL 11011802 | 36.4406 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.1429 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.5455 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.2007
62 | FITCH MOUNTAIN 111324918 | 36.4262 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.5862 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.0256 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.4096
63 | MARIPOSA 2101439030 | 36.0716 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.3273 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.9916 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.6205
64 | CLAYTON 221296224 | 35.9806 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.2887 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.7168 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.4871
65 | PEORIA 170190090 | 35.8543 | Line removal Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.9719 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.7985 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.6251
66 | HOPLAND 11014626 | 35.6066 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.5754 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.142 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.6862
67 | SILVERADO 2104632 | 35.5808 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 8.8223 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 8.3619 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.8617
68 | PLACERVILLE 2106935216 | 35.4512 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1175 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7152 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2843
69 | APPLE HILL 2102186912 | 34.9302 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.8373 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.5775 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.2901
70 | SHADY GLEN 1101941844 | 34.5974 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.5652 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.4369 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.3205
71 | PINE GROVE 1102269286 | 34.1506 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 17.0888 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.7457 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 16.3777
72 | ORO FINO 110239154 | 34.0841 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 15.0892 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.6828 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.2455
73 | WEST POINT 110234416 | 33.9065 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.5894 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.1619 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.6995
74 | CEDAR CREEK 1101CB | 33.7551 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.3529 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.9912 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.6043
75 | SISQUOC 1102M52 | 33.4088 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.6176 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.4458 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.274
76 | TEMPLETON 2113641367 | 33.3923 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.6652 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.4586 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.2521
77 | MARIPOSA 21019400 | 33.2984 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.652 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.2635 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.85
78 | FORESTHILL 1102359542 | 32.7979 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.4512 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.3405 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.2297
79 | CALAVERAS CEMENT 11011419 | 32.6283 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.6857 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.3826 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9805
80 | BRUNSWICK 110651486 | 32.0751 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.8838 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.4582 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.9976
81 | SHINGLE SPRINGS 210913322 | 32.0191 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.8859 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.4886 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.0628
82 | PINE GROVE 11013170 | 32.0008 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.1718 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.1313 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 12.0907
83 | WEST POINT 110236676 | 31.795 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 11.4471 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.615 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8735
84 | APPLE HILL 21021532 | 31.4372 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.353 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 14.1429 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 13.911
85 | CALAVERAS CEMENT 110147968 | 30.7825 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.9325 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.9126 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0218
86 | WILDWOOD 1101384582 | 30.7606 | EPSS Vegetation routine patrol Vegetation hazard patrol | 10.7009 | EPSS Vegetation routine patrol Vegetation hazard patrol | 10.7009 | EPSS Vegetation routine patrol Vegetation hazard patrol | 10.7009
87 | SANTA YNEZ 1102320270 | 30.7321 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.6656 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.3882 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.8026
88 | FRENCH GULCH 11022902 | 30.5736 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.6183 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.0639 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.0386
89 | STANISLAUS 17011812 | 30.5553 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.2699 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 7.5884 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6513
90 | PERRY 110179696 | 30.4315 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.3186 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.9232 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.5083
(a) Adjusted in response to Critical Issue RN-PGE-26-02. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table PG&E-7-1
TABLE PG&E‑7‑1:
PSPS EVENT STATISTICS
Year | Number of Events Where De‑Energization Was Initiated(a) | Total Circuits De‑Energized(b) | Total Customers Impacted(c) | Total Customer Minutes of Interruption (CMI)(d)
2018 | 1 | 43 | 55864 | 87878279
2019 | 8 | 1842 | 2036019 | 5513240050
2020 | 6 | 817 | 649685 | 1336601298
2021 | 5 | 237 | 80391 | 147807660
2022(e) | – | – | – | –
2023 | 2 | 27 | 5098 | 5331165
2024 | 6 | 242 | 50519 | 97112035
_______________
(a) Number of Events Where De‑energization Was Initiated: Number of instances where utility operating protocol requires de‑energization of a circuit thereof to reduce ignition probability per year. This is only for events in which de‑energization ultimately occurred.
(b) Circuits De‑energized: The cumulative sum of circuits de‑energized by each PSPS event per year. If the same circuit was impacted by two different PSPS events, the circuit will be counted twice.
(c) Customers Impacted: The cumulative sum of customers impacted by each PSPS event per year. If multiple PSPS events impact the same customer, the customer is counted each time in the overall impact.
(d) CMI: The cumulative sum of customer minutes of de‑energization due to PSPS events per each year (if multiple PSPS events impact the same customer, the customer minutes of de‑energization is accounted for in each of the events for the given customer).
(e) We had no PSPS events in 2022.

## Table-6-4B
TABLE 6‑4B:
SUMMARY OF RISK REDUCTION FOR TOP RISK CIRCUITS BY RISK-PER-MILE FOR CRITICAL ISSUE RN-PGE-26-02 (a)
Line No. | Circuit Segment Name | Initial Overall Utility Risk | 2026 Activities | 2026 Overall Utility Risk | 2027 Activities | 2027 Overall Utility Risk | 2028 Activities | 2028 Overall Utility Risk
1 | DUNBAR 11034882 | 176.1859 | Vegetation routine patrol Vegetation hazard patrol | 176.1859 | Vegetation routine patrol Vegetation hazard patrol | 176.1859 | Vegetation routine patrol Vegetation hazard patrol | 176.1859
2 | PUEBLO 1104968601 | 126.375 | EPSS Vegetation routine patrol Vegetation hazard patrol | 122.219 | EPSS Vegetation routine patrol Vegetation hazard patrol | 122.219 | EPSS Vegetation routine patrol Vegetation hazard patrol | 122.219
3 | ARBUCKLE 110130376 | 97.2091 | Vegetation routine patrol Vegetation hazard patrol | 97.2091 | Vegetation routine patrol Vegetation hazard patrol | 97.2091 | Vegetation routine patrol Vegetation hazard patrol | 97.2091
4 | VACAVILLE 111112342 | 82.7625 | EPSS Vegetation routine patrol Vegetation hazard patrol | 81.8848 | EPSS Vegetation routine patrol Vegetation hazard patrol | 81.8848 | EPSS Vegetation routine patrol Vegetation hazard patrol | 81.8848
5 | BALCH NO 1 1101CB | 72.557 | EPSS Vegetation routine patrol Vegetation hazard patrol | 25.2429 | EPSS Vegetation routine patrol Vegetation hazard patrol | 25.2429 | EPSS Vegetation routine patrol Vegetation hazard patrol | 25.2429
6 | CALPINE 1144276-G | 47.9277 | EPSS Vegetation routine patrol Vegetation hazard patrol | 16.6731 | EPSS Vegetation routine patrol Vegetation hazard patrol | 16.6731 | EPSS Vegetation routine patrol Vegetation hazard patrol | 16.6731
7 | CASTRO VALLEY 1110MR525 | 39.7273 | EPSS Vegetation routine patrol Vegetation hazard patrol | 39.3781 | EPSS Vegetation routine patrol Vegetation hazard patrol | 39.3781 | EPSS Vegetation routine patrol Vegetation hazard patrol | 39.3781
8 | MARIPOSA REMOTE 0001CB | 33.6836 | EPSS Vegetation routine patrol Vegetation hazard patrol | 11.4778 | EPSS Vegetation routine patrol Vegetation hazard patrol | 11.2096 | EPSS Vegetation routine patrol Vegetation hazard patrol | 10.9134
9 | SPAULDING 1101CB | 30.9247 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.3899 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 10.0218 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.6536
10 | TIGER CREEK 0201CB | 29.4651 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.394 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.2139 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.0338
11 | VACAVILLE 1111772224 | 29.4415 | EPSS Vegetation routine patrol Vegetation hazard patrol | 28.9387 | EPSS Vegetation routine patrol Vegetation hazard patrol | 28.9387 | EPSS Vegetation routine patrol Vegetation hazard patrol | 28.9387
12 | CALPINE 1144962 | 25.8838 | EPSS Vegetation routine patrol Vegetation hazard patrol | 9.0044 | EPSS Vegetation routine patrol Vegetation hazard patrol | 9.0044 | EPSS Vegetation routine patrol Vegetation hazard patrol | 9.0044
13 | CORDELIA 111013382 | 22.3582 | Vegetation routine patrol Vegetation hazard patrol | 22.3582 | Vegetation routine patrol Vegetation hazard patrol | 22.3582 | Vegetation routine patrol Vegetation hazard patrol | 22.3582
14 | KESWICK 1101CB | 20.5032 | EPSS Vegetation routine patrol Vegetation hazard patrol | 7.1847 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 5.5128 | EPSS Vegetation routine patrol Vegetation hazard patrol | 5.5128
15 | SPRING GAP 1702188426 | 16.1191 | EPSS Vegetation routine patrol Vegetation hazard patrol | 5.6075 | EPSS Vegetation routine patrol Vegetation hazard patrol | 5.6075 | EPSS Vegetation routine patrol Vegetation hazard patrol | 5.6075
16 | TASSAJARA 21123202 | 14.6247 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.9111 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.8844 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.8577
17 | BALCH NO 1 1101105414 | 13.0815 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4585 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4541 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4496
18 | CLARKSVILLE 210551478 | 10.9083 | EPSS Vegetation routine patrol Vegetation hazard patrol | 10.6469 | EPSS Vegetation routine patrol Vegetation hazard patrol | 10.6469 | EPSS Vegetation routine patrol Vegetation hazard patrol | 10.6469
19 | BALCH NO 1 1101406582 | 10.879 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9237 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9198 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9159
20 | BUCKS CREEK 1102CB | 10.0915 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5987 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.52089 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0
21 | PEABODY 2106CB | 9.9466 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.5078 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.5073 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 9.5068
22 | APPLE HILL 1104814656 | 9.8646 | EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4434 | EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4434 | EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4434
23 | SCE TEJON TIE 1101CB | 9.7987 | EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4088 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 2.478 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.478
24 | APPLE HILL 2102CB | 8.4552 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.2107 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.93722 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.79994
25 | MIWUK 170179118 | 8.2167 | EPSS Vegetation routine patrol Vegetation hazard patrol | 7.1206 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 6.7009 | EPSS Vegetation routine patrol Vegetation hazard patrol | 6.7009
26 | SALT SPRINGS 210110416 | 7.6719 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7749 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7692 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7635
27 | DEL MAR 210938684 | 7.1655 | Vegetation routine patrol Vegetation hazard patrol | 7.1655 | Vegetation routine patrol Vegetation hazard patrol | 7.1655 | Vegetation routine patrol Vegetation hazard patrol | 7.1655
28 | OAKLAND J 1102CR102 | 6.9718 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.613 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.6081 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 6.6032
29 | WILDWOOD 1101384582 | 6.7774 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.3577 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.3577 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.3577
30 | ALLEGHANY 1102WC 1101/2 | 6.5346 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0973 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8659 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6345
31 | CALPINE 1146200-G | 5.804 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0191 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0191 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0191
32 | MARIPOSA 2101929360 | 5.6757 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9885 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9885 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9885
33 | CALPINE 1144304 | 5.6383 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9667 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.935 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9032
34 | MONTICELLO 11011780 | 5.6225 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.8308 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.8177 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 4.8045
35 | CEDAR CREEK 1101451856 | 5.5841 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.2996 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2331 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2331
36 | WYANDOTTE 11102590 | 5.4781 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.4776 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.4771 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.4766
37 | VACAVILLE 1104CB | 5.4088 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.2121 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.2106 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 5.209
38 | RINCON 1102228730 | 5.3527 | Vegetation routine patrol Vegetation hazard patrol | 5.3527 | Vegetation routine patrol Vegetation hazard patrol | 5.3527 | Vegetation routine patrol Vegetation hazard patrol | 5.3527
39 | ELECTRA 1102CB | 5.3009 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.89811 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.89598 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.89386
40 | KESWICK 1101417066 | 5.2673 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1116 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6947 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6929
41 | PIT NO 5 1101923612 | 5.1486 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.79251 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.77515 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.75779
42 | NARROWS 2104CB | 5.0577 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7595 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7595 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7595
43 | FRENCH GULCH 11011892 | 5.0522 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.755 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.55772 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.55431
44 | MARINA (F) 1101CB | 5.0335 | Vegetation routine patrol Vegetation hazard patrol | 5.0335 | Vegetation routine patrol Vegetation hazard patrol | 5.0335 | Vegetation routine patrol Vegetation hazard patrol | 5.0335
45 | CALISTOGA 110135588 | 4.9896 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1568 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.27736 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.23385
46 | VACAVILLE 1104196294 | 4.9538 | EPSS Vegetation routine patrol Vegetation hazard patrol | 4.5526 | EPSS Vegetation routine patrol Vegetation hazard patrol | 4.5526 | EPSS Vegetation routine patrol Vegetation hazard patrol | 4.5526
47 | DOBBINS 1101CB | 4.8355 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7118 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6964 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.681
48 | CLAYTON 221296224 | 4.6805 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2083 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.87375 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.84387
49 | WEST POINT 1101CB | 4.5246 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5301 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.30203 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.2432
50 | TIGER CREEK 0201320746 | 4.5032 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5284 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4849 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4372
51 | TRIDAM POWERHOUSE 2101CB | 4.4824 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5128 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4662 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4196
52 | ELECTRA 110213414 | 4.4308 | Vegetation routine patrol Vegetation hazard patrol | 4.4308 | Vegetation routine patrol Vegetation hazard patrol | 4.4308 | Vegetation routine patrol Vegetation hazard patrol | 4.4308
53 | CALPINE 1146394G | 4.3817 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5243 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5243 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5243
54 | FRENCH GULCH 11022902 | 4.3534 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5119 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72105 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71744
55 | MOUNTAIN QUARRIES 2101CB | 4.3308 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.506 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4636 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4211
56 | VACA DIXON 110175740 | 4.0999 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.5568 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.554 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.5512
57 | TASSAJARA 2112791386 | 4.0778 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5464 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5186 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4908
58 | VACAVILLE 110847860 | 3.996 | EPSS Vegetation routine patrol Vegetation hazard patrol | 3.8019 | EPSS Vegetation routine patrol Vegetation hazard patrol | 3.8019 | EPSS Vegetation routine patrol Vegetation hazard patrol | 3.8019
59 | DRUM 1101CB | 3.9822 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0154 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.53929 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.50792
60 | PARADISE 1104457900 | 3.9774 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.2797 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.2728 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.2652
61 | DEL MAR 210975802 | 3.9728 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.8764 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.876 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.8756
62 | SILVERADO 2104209359 | 3.9382 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.4063 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.4063 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 1.706
63 | BURNS 2101BL 2101 | 3.9313 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0464 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72519 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.40398
64 | MONROE 210392868 | 3.905 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.7212 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.7204 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.7196
65 | POINT MORETTI 110135874 | 3.8671 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2588 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.91556 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.81808
66 | ORO FINO 11022236 | 3.8531 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3085 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.2291 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.17768
67 | WISHON 1101CB | 3.8495 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.339 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3389 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3387
68 | CLAYTON 2212681608 | 3.7092 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.77474 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.73328 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68979
69 | NEWARK 21KV 2111CB | 3.6765 | Vegetation routine patrol Vegetation hazard patrol | 3.6765 | Vegetation routine patrol Vegetation hazard patrol | 3.6765 | Vegetation routine patrol Vegetation hazard patrol | 3.6765
70 | PLACERVILLE 210658118 | 3.6745 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.822 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.822 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.822
71 | MIDDLETOWN 1101644756 | 3.6635 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3117 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2763 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2371
72 | ELECTRA 1101L1697 | 3.6542 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3378 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3107 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2836
73 | CLOVERDALE 1102672 | 3.6392 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3047 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.013812 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.013812
74 | KESWICK 11011586 | 3.6344 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2496 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1427 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1089
75 | CRESTA 1101103126 | 3.6138 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1184 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1177 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1169
76 | FORT ROSS 1121CB | 3.6095 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.276 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1853 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1853
77 | VACAVILLE 1109799940 | 3.5599 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.1864 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.1854 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.1844
78 | CALPINE 1146CB | 3.5544 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2365 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2365 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2365
79 | GUSTINE 1102999258 | 3.5336 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2296 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2294 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2291
80 | PARADISE 11042206 | 3.5153 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.3973 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.3961 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.3948
81 | TASSAJARA 2112900058 | 3.5142 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4279 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4278 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.4277
82 | PIKE CITY 11011720 | 3.5082 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.092636 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.042876 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.033571
83 | CALPINE 1144960 | 3.5061 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2197 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2197 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2197
84 | MADISON 1105995448 | 3.5017 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2278 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.223 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2181
85 | CURTIS 1703258550 | 3.4759 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.90297 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.87841 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.85385
86 | VOLTA 110280982 | 3.4467 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.1195 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.1182 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 3.1169
87 | ALLEGHANY 1102CB | 3.3977 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0559 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.021405 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.010954
88 | SILVERADO 2104646776 | 3.3656 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5918 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.75433 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.7131
89 | ALTO 1124432 | 3.3596 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2147 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.44131 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.38931
90 | SILVERADO 2104940 | 3.3116 | Vegetation routine patrol Vegetation hazard patrol | 3.3116 | Vegetation routine patrol Vegetation hazard patrol | 3.3116 | Vegetation routine patrol Vegetation hazard patrol | 3.3116
91 | SCE REFUGIO 1701CB | 3.2543 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1321 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 0.038965 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.038965
92 | PINECREST 0401CB | 3.2279 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0534 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.32916 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.24302
93 | TEJON 11023760 | 3.1141 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0804 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78723 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78429
94 | CUYAMA 1103684566 | 3.1017 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0851 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0851 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0851
95 | PIT NO 5 11011614 | 3.0876 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0719 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.097273 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.095064
96 | PIT NO 3 21011482 | 3.0725 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0664 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.080595 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.071087
97 | PARADISE 11051212 | 3.0265 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9645 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9642 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.964
98 | DIAMOND SPRINGS 1106176130 | 3.0145 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.5483 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.5299 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.5114
99 | BALCH NO 1 1101R372 | 3.0025 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.044 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.49127 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.49077
100 | PIT NO 5 110190846 | 2.999 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0433 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.51023 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.51023
101 | TASSAJARA 2112D514R | 2.9167 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.5711 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.5707 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.5702
102 | WHITMORE 1101WTGLR | 2.9085 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1612 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1612 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1612
103 | TEJON 11022455 | 2.8946 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1413 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.106 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0701
104 | BIG BASIN 1101124854 | 2.8928 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.96837 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.93039 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.89242
105 | PIT NO 5 1101CB | 2.8712 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.20017 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.1946 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.18904
106 | ROSSMOOR 1102457174 | 2.8627 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7748 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7747 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7746
107 | RINCON 1101CB | 2.8527 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7737 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7731 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.7725
108 | EL DORADO PH 2101757474 | 2.8386 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.98751 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.98751 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.98751
109 | ALLEGHANY 1101SC 1101/2 | 2.836 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.99856 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.91891 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83927
110 | MIWUK 170236888 | 2.8176 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.76671 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.42491 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.41598
111 | MIDDLETOWN 1101959140 | 2.7908 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.5465 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.45898 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.44482
112 | MARIPOSA 2101752630 | 2.7473 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.94123 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.34565 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.3265
113 | MONTICELLO 1101130412 | 2.7439 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1776 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1561 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.4139
114 | INDIAN FLAT 1104CB | 2.7316 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.51902 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.5034 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.48777
115 | STELLING 11109265 | 2.7077 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.96809 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.93972 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.10784
116 | EL DORADO PH 2101CB | 2.7019 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.41698 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.41624 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.4155
117 | REDBUD 1101454 | 2.6979 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.98935 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.98205 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.97401
118 | PINE GROVE 110245292 | 2.6827 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0869 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.16623 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.08912
119 | MONTE RIO 1113320 | 2.6771 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.92338 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.072789 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.063752
120 | CLOVERDALE 11024646 | 2.6452 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.3322 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.3309 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.3296
121 | SHINGLE SPRINGS 2108449638 | 2.6301 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.88999 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.86153 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83307
122 | CALISTOGA 1101894220 | 2.6178 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72231 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71386 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.70542
123 | ALTO 11243745 | 2.557 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.92269 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.8625 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.024223
124 | HIGHLANDS 1102628 | 2.5569 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72087 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.56434 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.22591
125 | JAMESON 110560052 | 2.5493 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.90778 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.90008 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65582
126 | STANISLAUS 1702CB | 2.5402 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.93171 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.91697 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.90097
127 | OAKLAND K 1101CR178 | 2.5196 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.2962 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.2924 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.2885
128 | SHINGLE SPRINGS 210551738 | 2.502 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.442 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.4419 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.4419
129 | BIG BEND 1101CB | 2.4971 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0267 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0143 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0018
130 | PLACERVILLE 1109CB | 2.4948 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1489 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1453 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.1418
131 | VACAVILLE 1103CB | 2.4945 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.4199 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.4199 | EPSS Vegetation routine patrol Vegetation hazard patrol | 2.4199
132 | CALAVERAS CEMENT 1101544800 | 2.4931 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.85783 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.4611 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.084062
133 | ALLEGHANY 1101DC 1101/2 | 2.4753 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83997 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71954 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.5991
134 | PARADISE 1105829194 | 2.4463 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0425 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0198 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.99492
135 | RINCON 110275816 | 2.4352 | Vegetation routine patrol Vegetation hazard patrol | 2.4352 | Vegetation routine patrol Vegetation hazard patrol | 2.4352 | Vegetation routine patrol Vegetation hazard patrol | 2.4352
136 | WILLOW CREEK 1103181562 | 2.4196 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1745 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1745 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1745
137 | MARIPOSA 2102241564 | 2.4167 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1221 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1192 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1163
138 | BONNIE NOOK 1102542186 | 2.4059 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.87303 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.14131 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.088629
139 | TULE POWER HOUSE 1101CB | 2.4021 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83565 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.43051 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 0.3953
140 | PARADISE 1104954322 | 2.3916 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3624 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3538 | Overhead hardening Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 0.40982
141 | SAN LUIS OBISPO 1104982992 | 2.38 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.81347 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.69646 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.16572
142 | MIWUK 17021808 | 2.3751 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.97965 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.94395 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.90661
143 | CORNING 110185152 | 2.3597 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.98906 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.97603 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.96164
144 | SANTA YNEZ 1101980192 | 2.3546 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83805 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.2127 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.19607
145 | TASSAJARA 2112676362 | 2.3531 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.82186 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.7878 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.1219
146 | DEL MONTE 2104181640 | 2.3496 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0209 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.82946 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.82946
147 | SILVERADO 210478268 | 2.3463 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.79042 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.76689 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.74152
148 | PUEBLO 110298730 | 2.3348 | Vegetation routine patrol Vegetation hazard patrol | 2.3348 | Vegetation routine patrol Vegetation hazard patrol | 2.3348 | Vegetation routine patrol Vegetation hazard patrol | 2.3348
149 | BUCKS CREEK 1103CB | 2.334 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83469 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.82853 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72326
150 | ALLEGHANY 1101VR816 | 2.3141 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.26143 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.2455 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.22957
151 | CALPINE 1144CB | 2.2869 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.84226 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.8421 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.84195
152 | PEORIA 1704877670 | 2.2751 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78893 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.12704 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.11918
153 | SILVERADO 2104324994 | 2.271 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.91643 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.88131 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33963
154 | CALPINE 1146400 | 2.2222 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.77306 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.77306 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.77306
155 | ROUND MOUNTAIN 1101CB | 2.2108 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.7691 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6978 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6978
156 | FORT ROSS 112170288 | 2.2077 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.74372 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.0065492 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.0017648
157 | CASTRO VALLEY 1108MR233 | 2.2072 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0894 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0893 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0892
158 | PUEBLO 2103489964 | 2.2012 | Vegetation routine patrol Vegetation hazard patrol | 2.2012 | Vegetation routine patrol Vegetation hazard patrol | 2.2012 | Vegetation routine patrol Vegetation hazard patrol | 2.2012
159 | CALAVERAS CEMENT 11011419 | 2.1915 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78489 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.76454 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.13302
160 | ELECTRA 11017104 | 2.1841 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.79004 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.7591 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72602
161 | MARIPOSA 2102851902 | 2.1796 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.81296 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.80158 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.79019
162 | OAKLAND K 1102172340 | 2.1546 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7566 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7477 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7381
163 | SILVERADO 2105990552 | 2.1473 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7367 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7299 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7226
164 | PLACERVILLE 2106CB | 2.1426 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.8463 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83314 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.81858
165 | VACAVILLE 110838316 | 2.1419 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78036 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.766 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.75012
166 | RINCON 1103472 | 2.1394 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0868 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0858 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 2.0847
167 | STELLING 1110568350 | 2.13 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.74004 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.43231 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.23693
168 | ALLEGHANY 1101806 | 2.1156 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.73458 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63096 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.12798
169 | PIT NO 3 2101CB | 2.1136 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.73973 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.73862 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.73751
170 | FORESTHILL 110150486 | 2.1082 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.84443 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.81711 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.7876
171 | VACAVILLE 1108922767 | 2.1076 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0182 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.018 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.0177
172 | SILVERADO 2104CB | 2.1036 | Vegetation routine patrol Vegetation hazard patrol | 2.1036 | Vegetation routine patrol Vegetation hazard patrol | 2.1036 | Vegetation routine patrol Vegetation hazard patrol | 2.1036
173 | RINCON 1102CB | 2.0779 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9858 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9842 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.9825
174 | PARADISE 1105878870 | 2.0718 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.208 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1904 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1716
175 | SHADY GLEN 1101941844 | 2.0608 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.92716 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.91951 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.43605
176 | PUTAH CREEK 110267858 | 2.0575 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.76731 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.3881 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33645
177 | PIKE CITY 1102CB | 2.0457 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.75577 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.38045 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.32721
178 | FRENCH GULCH 1101CB | 2.0411 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78374 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78095 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.77816
179 | MIDDLETOWN 1101614 | 2.034 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.236 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.2185 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1996
180 | BONNIE NOOK 1101CB | 2.0242 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.61435 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.58881 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.56124
181 | COALINGA NO 2 11059260 | 2.0201 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.70756 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66739 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63543
182 | CLAYTON 2212614950 | 2.0166 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.70167 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.67919 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.61672
183 | PUEBLO 110247720 | 2.0082 | Vegetation routine patrol Vegetation hazard patrol | 2.0082 | Vegetation routine patrol Vegetation hazard patrol | 2.0082 | Vegetation routine patrol Vegetation hazard patrol | 2.0082
184 | NOTRE DAME 11042028 | 2.0074 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.38576 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.38506 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.38436
185 | CLAYTON 2212334476 | 1.9969 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3624 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3602 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3578
186 | SUNOL 1101298061 | 1.9949 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72859 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71704 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.70549
187 | MOUNTAIN QUARRIES 21011130 | 1.9857 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.74621 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.47976 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.31044
188 | RINCON 1104786782 | 1.982 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7418 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.737 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.7317
189 | GARCIA 0401CB | 1.9759 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68737 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68737 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68737
190 | DUNBAR 1103799422 | 1.9636 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.75033 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71551 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 0.12561
191 | VACAVILLE 1104293462 | 1.9608 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.73591 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.37192 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33663
192 | HARTLEY 1101698 | 1.9534 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66743 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.43642 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.31135
193 | PUTAH CREEK 1105665952 | 1.9494 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.73333 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72983 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71075
194 | SILVERADO 2104632 | 1.9481 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.48303 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.45782 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.43044
195 | SILVERADO 2105CB | 1.9357 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8597 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8591 | EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8585
196 | TEJON 1102732836 | 1.9304 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66497 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.31039 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.29134
197 | CAMP EVERS 2104189010 | 1.9274 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6363 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6343 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.6322
198 | APPLE HILL 110497086 | 1.9243 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.5993 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.10046
199 | CALISTOGA 1101730666 | 1.9147 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66847 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66111 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65375
200 | WEST POINT 110236676 | 1.9106 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68787 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.57778 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.11258
201 | KONOCTI 1102714370 | 1.9064 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.69467 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66299 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.22035
202 | SILVERADO 2104806500 | 1.9019 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60212 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60096 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.59981
203 | STILLWATER 11021466 | 1.8976 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.77594 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.75537 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.14162
204 | PIT NO 3 21011480 | 1.8936 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66481 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6626 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6604
205 | NARROWS PH 1151CB | 1.8835 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65524 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.3525 | Undergrounding EPSS Vegetation routine patrol Vegetation hazard patrol | 0.32845
206 | WILDWOOD 11011454 | 1.8774 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65753 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65709 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65664
207 | PINE GROVE 1101CB | 1.8764 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.76375 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.51064 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.3453
208 | REDBUD 1101323962 | 1.8751 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.86151 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.85339 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.84442
209 | PLACERVILLE 21069712 | 1.8738 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71425 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.70865 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.14224
210 | CLARKSVILLE 2106CB | 1.8734 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8153 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8152 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.8152
211 | WOODACRE 1102851 | 1.8733 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.89789 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.87946 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.19825
212 | SARATOGA 1107667000 | 1.8663 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.67002 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65914 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64825
213 | ELECTRA 1101CB | 1.8561 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.67619 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.41104 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.25433
214 | MARIPOSA 2101439030 | 1.8555 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6341 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.61683 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.59774
215 | ANTLER 11011376 | 1.8554 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68144 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.34922 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.29542
216 | FRENCH GULCH 11011464 | 1.8521 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64419 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.54938 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.54723
217 | ALTO 11221260 | 1.8493 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63584 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.61008 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.093189
218 | RINCON 1104CB | 1.8468 | Vegetation routine patrol Vegetation hazard patrol | 1.8468 | Vegetation routine patrol Vegetation hazard patrol | 1.8468 | Vegetation routine patrol Vegetation hazard patrol | 1.8468
219 | TEJON 11023751 | 1.8452 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.75806 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.67322 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6057
220 | RINCON 1102640 | 1.8446 | Vegetation routine patrol Vegetation hazard patrol | 1.8446 | Vegetation routine patrol Vegetation hazard patrol | 1.8446 | Vegetation routine patrol Vegetation hazard patrol | 1.8446
221 | CLARK ROAD 110247006 | 1.8411 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.81016 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.80378 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.79674
222 | VACAVILLE 11046542 | 1.8401 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4093 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.4027 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3957
223 | BIG BEND 1101641808 | 1.8395 | Line removal Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.7172 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.70561 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.69403
224 | PIT NO 5 11011658 | 1.8335 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6328 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62401 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.26583
225 | REDBUD 1101754544 | 1.8323 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65135 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64575 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63957
226 | PIKE CITY 1101417084 | 1.8308 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.44178 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.43653 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.32575
227 | BEAR VALLEY 2105CB | 1.8205 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33682 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33657 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33631
228 | CALAVERAS CEMENT 110147968 | 1.7987 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6388 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63764 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.11814
229 | EL DORADO PH 210219562 | 1.7867 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.84687 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.83415 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.82011
230 | DUNLAP 1103CB | 1.786 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62572 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.61934 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.61297
231 | RINCON 1103649194 | 1.7847 | Vegetation routine patrol Vegetation hazard patrol | 1.7847 | Vegetation routine patrol Vegetation hazard patrol | 1.7847 | Vegetation routine patrol Vegetation hazard patrol | 1.7847
232 | SANTA YNEZ 1102320270 | 1.7837 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.61904 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60294 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33679
233 | EL DORADO PH 2102927014 | 1.7812 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.98011 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.97838 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.97665
234 | FORESTHILL 1102359542 | 1.7752 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.24092 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.23493 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.22893
235 | MIDDLETOWN 1101548 | 1.7691 | Line removal Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.71165 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.57215 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.23792
236 | CLOVERDALE 110282888 | 1.7681 | Vegetation routine patrol Vegetation hazard patrol | 1.7681 | Vegetation routine patrol Vegetation hazard patrol | 1.7681 | Vegetation routine patrol Vegetation hazard patrol | 1.7681
237 | BIG BEND 1102884340 | 1.7598 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3456 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3378 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.3294
238 | STANISLAUS 1701CB | 1.7589 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.55304 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.53466 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.47598
239 | COLUMBIA HILL 11012212 | 1.7554 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66988 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64863 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33508
240 | MOLINO 1102318 | 1.7496 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60434 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.57666 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.54645
241 | LAURELES 111110141 | 1.7485 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62401 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.5976 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.56867
242 | LAYTONVILLE 1101518 | 1.7333 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60886 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.58878 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.27136
243 | SHADY GLEN 11012768 | 1.7317 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.56563 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.56004 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.54789
244 | LARKIN (Y) 1127CB | 1.7312 | Vegetation routine patrol Vegetation hazard patrol | 1.7312 | Vegetation routine patrol Vegetation hazard patrol | 1.7312 | Vegetation routine patrol Vegetation hazard patrol | 1.7312
245 | SHADY GLEN 1101898212 | 1.7303 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.144 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1437 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.1434
246 | EL DORADO PH 2102CB | 1.7262 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.79066 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.19012 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.15978
247 | WEST POINT 11021305 | 1.723 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60982 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.59337 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.10527
248 | PLACERVILLE 2106935216 | 1.7218 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.10284 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.083306 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.062376
249 | PIT NO 7 1101CB | 1.7059 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.59443 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.59271 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.59099
250 | MIDDLETOWN 11011314 | 1.7043 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.86909 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.23394 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.21947
251 | ELK 1101CB | 1.7016 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60693 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60693 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.57373
252 | DUNBAR 1103234 | 1.6914 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.78223 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.76486 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.74632
253 | ANTLER 1101484276 | 1.6897 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.58867 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.58805 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.28647
254 | BEAR VALLEY 21059480 | 1.6857 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.4083 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.40701 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.26535
255 | COVELO 1101516510 | 1.68 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.58448 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.58399 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.5835
256 | COALINGA NO 2 1105897858 | 1.6752 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63244 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.6317 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63095
257 | FROGTOWN 17011623 | 1.6714 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.57564 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.55599 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.53515
258 | SALT SPRINGS 21023118 | 1.6682 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.58489 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.55349 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.52209
259 | MARIPOSA 2101CB | 1.667 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62947 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62673 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62399
260 | SAN RAFAEL 11011250 | 1.6644 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.57206 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.56477 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.55749
261 | GEYSERVILLE 1102904170 | 1.6592 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65477 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65423 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.32883
262 | CLAYTON 2212204416 | 1.6552 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60881 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.59728 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.12109
263 | SO. CAL. EDISON #3 1101CB | 1.6514 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.57038 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.56335 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.24949
264 | ORO FINO 1101CB | 1.6489 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.96059 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.94649 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.93136
265 | MOUNTAIN QUARRIES 2101979598 | 1.6466 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64334 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64301 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.34762
266 | DUNBAR 1103160 | 1.6425 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.585 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.5845 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 1.584
267 | FORESTHILL 11011802 | 1.6425 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.72763 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.24996 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.23442
268 | STANISLAUS 17026028 | 1.6412 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64554 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62521 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60349
269 | MONTE RIO 1113CB | 1.6407 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.62556 | EPSS Vegetation routine patrol Vegetation hazard patrol | 0.60599 | Overhead hardening EPSS Vegetation routine patrol Vegetation hazard patrol | 0.44621
270 | CHALLENGE 1102CB | 1.6361 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68015 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.65916 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.22986
271 | SILVERADO 2104633600 | 1.6331 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68741 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.68681 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.34278
272 | CORDELIA 111240402 | 1.6299 | Vegetation routine patrol Vegetation hazard patrol | 1.6299 | Vegetation routine patrol Vegetation hazard patrol | 1.6299 | Vegetation routine patrol Vegetation hazard patrol | 1.6299
273 | WEST POINT 110112256 | 1.625 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.63968 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.35603 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.33547
274 | GIRVAN 11011330 | 1.599 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.66218 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64479 | Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.18466
275 | EL DORADO PH 210119752 | 1.5985 | Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.64856 | Overhead hardening Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.5084 | Overhead hardening Undergrounding Pole clearing EPSS Vegetation routine patrol Vegetation hazard patrol | 0.34032
(a) Adjusted in response to Critical Issue RN-PGE-26-02. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table 8-1
TABLE 8‑1:
GRID DESIGN, OPERATION, AND MAINTENANCE TARGETS BY YEAR
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | Target Unit | 2026 Target / Status | % Planned in HFTD for 2026 | % Planned in HFRA for 2026 | % Risk Reduction for 2026 | 2027 Target / Status | % Planned in HFTD for 2027 | % Planned in HFRA in 2027 | % Risk Reduction for 2027 | 2028 Target / Status | % Planned in HFTD for 2028 | % HFRA | % Risk Reduction for 2028 | Three‑ Year Total | Section; Page Number
planned in 2028
Grid Design, Operations, and Maintenance | Quantitative | Detailed Inspection ‑ Transmission (AI‑04) | AI‑04 | Transmission Structures | 22000 | 96.5% | 100% | 63.78% (Eyes on Risk) | 22000 | 96.5% | 100% | 63.78% (Eyes on Risk) | 22000 | 96.5% | 100% | 63.78% (Eyes on Risk) | 66000 | 8.3.1; p. 232
(Quarterly)
Grid Design, Operations, and Maintenance | Quantitative | Infrared Inspections ‑ Transmission (AI‑06) | AI‑06 | Circuit miles | 2500 | 94.6% | 100% | 72.95% (Eyes on Risk) | 2500 | 94.6% | 100% | 72.95% (Eyes on Risk) | 2500 | 94.6% | 100% | 72.95% (Eyes on Risk) | 7500 | 8.3.3; p. 235
(Quarterly)
Grid Design, Operations, and Maintenance | Quantitative | Aerial Scan Inspections ‑ Distribution (AI‑07A)(a) | n/a | Distribution Poles | 50000 | 98% | 100% | 24% | 20000 | 99% | 100% | 12% | 20000 | 98% | 100% | 9% | 90000 | 8.3.8 p. 240
| (Quarterly) | [6 empty] | (Eyes on Risk) |  |  |  | (Eyes on Risk) |  |  |  | (Eyes on Risk)
Grid Design, Operations, and Maintenance | Quantitative | Detailed Inspections ‑ Distribution (AI‑07D)(a) | AI‑07 | Distribution Poles | 300000 | 98% | 100% | 33% | 305000 | 94% | 100% | 47% | 215000 | 98% | 100% | 48% | 820000 | 8.3.8; p. 240
| (Quarterly) | [6 empty] | (Eyes on Risk) |  |  |  | (Eyes on Risk) |  |  |  | (Eyes on Risk)
Grid Design, Operations, and Maintenance | Quantitative | System Hardening ‑ Undergrounding (GH‑04)(b)(e) | GH‑04 | Circuit Miles | 360 (c) | 100% | 100% | 1.4% | 307 | 100% | 100% | 2.2% | 400 | 100% | 100% | 2.4% | 1067 | 8.2.2; p. 201
Grid Design, Operations, and Maintenance | Quantitative | System Hardening ‑ Transmission Shunt Splices (GH‑06) | GH‑06 | Shunt Splices | 250 | 100% | 100% | 0.07% | 250 | 100% | 100% | 0.07% | 250 | 100% | 100% | 0.07% | 750 | 8.2.5.1; p. 208
Grid Design, Operations, and Maintenance | Quantitative | System Hardening ‑ Transmission Conductor Segment Replacement (GH‑11) | GH‑11 | Conductor Segment | 4 | 100% | 100% | 0.05% | 5 | 100% | 100% | 0.05% | 6 | 100% | 100% | 0.05% | 15 | 8.2.5.1; p. 208
Grid Design, Operations, and Maintenance | Quantitative | Overhead Hardening ‑ Distribution (GH‑12)(e) | GH‑01 (d) | Circuit Miles | 294 | 100% | 100% | 1.2% | 190 | 98.7% | 100% | 1% | 190 | 99% | 100% | 0.6% | 674 | 8.2.1; p. 184
Grid Design, Operations, and Maintenance | Quantitative | Line Removal Enabled by Remote Grid ‑ Distribution (GH‑14)(e) | GH‑01 | Circuit Miles | 4 | 100% | 100% | 0.04% | 0 | n/a | n/a | n/a | 0 | n/a | n/a | n/a | 4 | 8.2.7.1; p. 211
Grid Design, Operations, and Maintenance | Qualitative | Proactive Animal Abatement Feasibility Study ‑ Transmission (GH‑13) | n/a | n/a | Started; March 2026 | n/a | n/a | n/a | In Progress; 2027 | n/a | n/a | n/a | Completed; December 31, 2028 | n/a | n/a | n/a | n/a | 8.2.13.1; p. 226
Grid Design, Operations, and Maintenance | Quantitative | Open Tag Reduction ‑ Distribution Backlog (GM‑03) | GM‑03 | Distribution EC Tags | Close 134% of the count of EC notifications created in HFTD/HFRA in 2025 | 100% | 99% | 0.6% | Close 153% of the count of EC notifications created in HFTD/HFRA from 2025 to 2026 | 100% | 99% | 0.6% | Close 160% of the count of EC notifications created in HFTD/HFRA from 2025 to 2027 | 100% | 99% | 0.6% | n/a | 8.6.2; p. 322
Grid Design, Operations, and Maintenance | Qualitative | Updates on EPSS Reliability Study (GM‑07) | GM‑07 | n/a | Completed; February 15, 2026 | n/a | n/a | n/a | Completed; February 15, 2027 | n/a | n/a | n/a | Completed; February 15, 2028 | n/a | n/a | n/a | n/a | 8.7.1.1; p. 333
Grid Design, Operations, and Maintenance | Quantitative | Service Breakaway Connectors (GM‑14) | n/a | Service Breakaway Connectors | 200 | 100% | 100% | 0.001% | 1400 | 100% | 100% | 0.007% | 1400 | 100% | 100% | 0.007% | 3000 | 8.2.10.6; p. 223
Grid Design, Operations, and Maintenance | Qualitative | Workforce Planning (GM‑15) | n/a | n/a | Completed; May 1, 2026 | n/a | n/a | n/a | Completed; May 1, 2027 | n/a | n/a | n/a | Completed; May 1, 2028 | n/a | n/a | n/a | n/a | 8.8.1; p. 351
_______________
(a) In response to Critical Issue RN PGE 26 06, the percent of risk reduction for detailed inspections and aerial inspections together account for 57 percent Eyes on Risk (EOR). PG&E aims to achieve a cumulative 57 percent EOR across aerial scan and detailed inspections. This EOR can be allocated in any way across the two inspections. See 2026 2028 WMP Revision Notice Response R0 for additional information.
(b) PG&E may include in these calculations the mileage and risk reduction from new system hardening technologies, such as Ground Level Distribution Systems (GLDS) discussed in ACI PG&E 25U 03, Section 2.3.
(c) In the 2023‑2025 WMP, PG&E provided a forecast of 440 undergrounding miles for 2026 (PG&E’s 2023‑2025 Base WMP R6, p. 408, Table 8.1.2‑2). The 2026 miles were provided as a forecast only to align to the total miles approved in PG&E’s 2023 GRC and were not a WMP target. Based on the undergrounding work completed in 2023 and 2024, and forecast for 2025, we are reducing the number of undergrounding miles needed to achieve the 18 percent risk reduction target for 2023‑2026 that is a requirement of PG&E’s 2023 GRC decision (Decision (D.) 23‑11‑069, Ordering Paragraph 22)
(d) In the 2023‑2025 WMP, the covered conductor initiative (GH‑01) included work associated with the system hardening program, including overhead covered conductor, system hardening undergrounding, and removal of overhead lines in HFTD, HFRA, or buffer zone areas. The covered conductor activity and target GH 12 have been updated for this revised 2026‑2028 Base WMP to remove undergrounding work, which is captured in GH‑04, and to remove line removal which is captured in GH 14 for line removal enabled by remote grid. See Critical Issue RN PGE 26 05 in 2026 2028 WMP Revision Notice Response R0 for additional information.
(e) In response to Critical Issue RN PGE 26 05, these targets and risk reduction estimates exclude system hardening for community rebuild purposes. See 2026 2028 WMP Revision Notice Response R0 for additional information.

## Table PG&E-8.2.1-1
TABLE PG&E‑8.2.1‑1:
MITIGATION EFFECTIVENESS ASSESSMENT – FAILURE MODE EXAMPLES 29
Line No. | Basic Cause of a Failure/Outage | Supplemental Cause of a Failure/Outage | Failed/ Involved Equipment | Equipment Condition | Outage Combination
1 | Third Party | Vehicle | Secondary | Broken, Wire on Ground | Third Party ¦ Vehicle ¦ Secondary ¦ Broken Wire on Ground
2 | Animal | Squirrel | Primary Overhead Conductor | Burned/ Flashed | Animal ¦ Squirrel ¦ Primary Overhead Conductor ¦ Burned/Flashed
3 | Company Initiated | Improper Construction | Primary Overhead Conductor | Deteriorated | Company Initiated ¦ Improper Construction ¦ Primary Overhead Conductor ¦ Deteriorated
4 | Environmental | Ice or Snow | Service Conductor | Broken, Wire on Ground | Environmental/External ¦ Ice or Snow ¦ Service Conductor ¦ Broken, Wire on Ground
/External
5 | Equipment Failure/Involved | Other | Primary Fuse | Broken | Equipment Failure/Other ¦ Primary Fuse ¦ Broken
6 | Unknown Cause | Patrol, Found Nothing | Primary Pole – Wood | Burned/ Flashed | Unknown Cause ¦ Patrol, Found Nothing ¦ Primary Pole – Wood ¦ Burned/Flashed
7 | Vegetation | Tree – Branch Fell on Line | Primary Anchor or Guy | Broken | Vegetation ¦ Tree – Branch Fell on Line ¦ Primary Anchor or Guy ¦ Broken
8 | Wildfire Mitigation | PSPS | Circuit Breaker | Normal | Wildfire Mitigation ¦ PSPS ¦ Circuit Breaker ¦ Normal

## Table PG&E‑8.2.1‑2
TABLE PG&E‑8.2.1‑2:
IGNITION MITIGATION EFFECTIVENESS RATINGS FOR THREE EXAMPLE MITIGATIONS
Line No. | Outage combination | UG All | UG Primary | Overhead CC + EPSS | CC with PSPS and EPSS
1 | Third Party I Vehicle I Secondary I Broken Wire on Ground | All | Medium | Medium | Very High
2 | Animal I Squirrel I Primary Overhead Conductor I Burned/Flashed | All | All | Very High | All
3 | Company Initiated I Improper Construction I Primary Overhead Conductor I Deteriorated(a) | N/A | N/A | N/A | N/A
4 | Environmental/External I Ice or Snow I Service Conductor I Broken, Wire on Ground(b) | All | None | None | All
5 | Equipment Failure/Other I Primary Fuse I Broken | All | All | Very High | All
6 | Unknown Cause I Patrol, Found Nothing I Primary Pole – Wood I Burned/Flashed | All | All | Very High | All
7 | Vegetation I Tree – Branch Fell on Primary Line I Anchor or Guy I Broken | All | All | Very High | All
8 | Wildfire Mitigation I PSPS I Circuit Breaker I Normal(a) | N/A | N/A | N/A | N/A
_______________
(a) Line numbers 3 and 8 are marked N/A because PG&E‑initiated outages were excluded from this mitigation effectiveness analysis because a PG&E‑initiated outage would not cause an ignition.
(b) The outage combination in line 4 relates to a conductor on a service line. None of these mitigations involves secondary or service lines, and so this outage scenario would not be prevented by any of these mitigations.

## Table PG&E‑8.2.1‑3
TABLE PG&E‑8.2.1‑3:
IGNITION MITIGATION EFFECTIVENESS REPRESENTATIVE BLENDED AVERAGE VALUES
System Hardening Scenarios | Blended Average Effectiveness(a)
Underground All (Underground Primary Lines, Secondary Lines and Services) | 99%
Underground Primary Distribution Lines | 98%
Line Removal w/ Remote Grid | 98%
Covered Conductor with EPSS and PSPS(b) | 97%
Covered Conductor with EPSS and DCD | 79%
Covered Conductor | 67%
_______________
Note: Assumptions – Analysis assumes no overhead degradation for life of the asset.
(a) This effectiveness evaluation is based on an assessment of each mitigation’s prevention of an ignition from active faults of known cause on overhead assets. Company‑initiated outages, including PSPS outages, outages of Unknown cause, as well as outages on existing underground assets are not applicable to this study and are excluded from calculation results as “N/A.”
(b) The combined “Overhead with EPSS and PSPS” effectiveness differs from others in the table as it is the result of two independent studies. The first study yields PSPS effectiveness alone to be approximately 84 percent effective at mitigating wildfire risk. Subsequently, the combined effectiveness of approximately 79 percent for “Overhead with EPSS” is applied on top of the PSPS reduction, resulting in: Mitigation Effectiveness = 84% + (100% 84%) * 79% = 97%.

## Table PG&E‑8.2.1‑4
TABLE PG&E‑8.2.1‑4:
COVERED CONDUCTOR AND UNDERGROUNDING IMPACTS ON THE LIKELIHOOD OF IGNITION(a) 32
Risk Driver | Description | Covered Conductor with Enhanced Powerline Safety Setting and Downed Conductor Detection | Underground Primary | Underground Primary and Secondary Lines and Services
(Underground All)
Equipment Failure | Events where failure of a PG&E asset, such as a conductor, arrester, insulator, breaker, transformer, etc., caused an ignition. This includes ignitions caused by wire-to-wire contact, commonly known as line slap. | Very High: The likelihood of ignition due to damage or failure of connection device, fuse, lightening arrestor, switch, and transformer | All: The likelihood of ignition due to damage or failure of anchor/guy, capacitor bank, connection device, crossarm, fuse, insulator and brushing, lightning arrestor, pole damage, recloser, sectionalizer, switch, transformer, and voltage regulator. | All: The likelihood of ignition due to damage or failure of anchor/guy, capacitor bank, connection device, crossarm, fuse, insulator and brushing, lightning arrestor, pole damage, recloser, sectionalizer, switch, transformer, voltage regulator, and conductor.
|  | High: The likelihood of ignition due to damage or failure of anchor/guy, crossarm, insulator and brushing, and pole damage. | Very High: The likelihood of ignition due to damage or failure of conductor damage or failure. | Medium High: The likelihood of ignition due to other equipment or facility failure.
|  | Medium High: The likelihood of ignition due to damage or failure of capacitor bank, recloser, and sectionalizer. | Medium High: The likelihood of ignition due to other equipment or facility failure. | All: The likelihood of ignition due to secondary damage or failure.
|  | Medium: The likelihood of ignition due to damage or failure of voltage regulator and secondary damage or failure. | Medium: The likelihood of ignition due to secondary damage or failure.
Vegetation Contact | Events where trees, tree limbs, and other vegetation come in contact with a PG&E asset, resulting in an ignition. | High: Reduces the likelihood of ignition risk due to branch not overhanging, branch overhanging, dead vegetation, vegetation falling into, vegetation growing into, and other vegetation contact. | Very High: The likelihood of ignition risk due to branch not overhanging, branch overhanging, dead vegetation, vegetation falling into, vegetation growing into, and other vegetation contact. | All: The likelihood of ignition risk due to branch not overhanging, branch overhanging, dead vegetation, vegetation falling into, vegetation growing into, and other vegetation contact.
Contact from Object | Events where objects come into contact with PG&E line equipment and create an ignition. This includes animal/bird contact, mylar balloons, and vehicles. | High: The likelihood of ignition due to animal contact, ballon contact, and vehicle contact. | All: The likelihood of ignition due to animal and ballon contact. | All: The likelihood of ignition due to animal contact, ballon contact, and vehicle contact.
|  | Medium: The likelihood of ignition due to contact from object. | Very High: The likelihood of an ignition due to vehicle contact. | High: The likelihood of ignition due to other contact from object.
High: The likelihood of ignition due to other contact from object.
Unable to Determine (Unknown) | Events associated with PG&E assets which led to an ignition, but where PG&E is unable to establish the main driver of the ignition. | High: The likelihood of ignition where PG&E is unable to determine the cause of an ignition. | Very High: The likelihood of an ignition where PG&E is unable to determine the cause of an ignition. | Very High: The likelihood of an ignition where PG&E is unable to determine the cause of an ignition.
Contamination | Events, including ignitions, caused by battery assets and contaminated insulators. | High: The likelihood of ignition due to contamination. | Very High: The likelihood of ignition due to contamination. | All: The likelihood of ignition due to contamination.
Other | Events without known causes. | Medium: The likelihood of ignition due to other causes. | Very High: The likelihood of ignition due to other causes. | Very High: The likelihood of ignition due to other causes.
Utility Work / Operation | Activities around utility processes. | None: The likelihood of ignition risk from utility work/operation. | None: The likelihood of ignition risk from utility work/operation. | None: The likelihood of ignition risk from utility work/operation.
Vandalism/ Theft | Vandalism from outside parties. | Medium High: The likelihood of ignition risk due to vandalism or theft. | Very High: The likelihood of ignition risk due to vandalism or theft. | All: The likelihood of ignition risk due to vandalism or theft.
(a) Updated based on Non-Substantive Errata filing on May 16, 2025 in accordance with Energy Safety issuance of Revision Notice at 21.

## Table PG&E‑8.2.1‑5
TABLE PG&E‑8.2.1‑5:
COVERED CONDUCTOR AND UNDERGROUNDING RISK REDUCTION TREND ANALYSIS
Activity | 2023 % Wildfire Risk Reduction | 2023 % EPSS Risk Reduction | 2023 % PSPS Risk Reduction | 2023 - 2024 Cumulative % Wildfire Risk Reduction | 2023 - 2024 Cumulative % EPSS Risk Reduction | 2023 - 2024 Cumulative % PSPS Risk Reduction
Covered conductor Installation | 0.25% | 0.23% | 0% | 0.36% | 0.35% | 0%
Undergrounding of electric lines and/or equipment | 0.66% | 0.69% | 0.83% | 1.54% | 1.21% | 2.05%

## Table PG&E‑8.2.7.2
TABLE PG&E‑8.2.7.2:
PSPS IMPACTS AVOIDED AFTER TEMPORARY MICROGRID DEPLOYMENT
DMG | Number of Impacts | Number of Customers(a)
Angwin | 17 | 48
Magalia | 13 | 37
Shingletown | 11 | 69
Pollock Pines | 8 | 44
Arnold | 7 | 87
Foresthill | 7 | 12
Georgetown | 7 | 98
Calistoga | 3 | 1622
Colfax | 2 | 366
Lucerne | 2 | 666
Groveland | 1 | 64
Middletown | 1 | 436
North Clearlake | 1 | 2410
_______________
(a) Indicates the number of customers energized by the microgrid each time it was operated.

## Table 8-2
TABLE 8‑2:
ASSET INSPECTION FREQUENCY, METHOD, CRITERIA, AND QUARTERLY TARGETS 6
Type | Inspection Activity (Program) | Frequency or Trigger (Note 1) | Method of Inspection (Note 2) | Governing Standards and Operating Procedures(b) | Cumulative Quarterly Target 2026, Q1(c) | Cumulative Quarterly Target 2026, Q2 | Cumulative Quarterly Target 2026, Q3 | Cumulative Quarterly Target 2026, Q4 | Cumulative Quarterly Target 2027, Q1 | Cumulative Quarterly Target 2027, Q2 | Cumulative Quarterly Target 2027, Q3 | Cumulative Quarterly Target 2027, Q4 | Cumulative Quarterly Target 2028, Q1 | Cumulative Quarterly Target 2028, Q2 | Cumulative Quarterly Target 2028, Q3 | Cumulative Quarterly Target 2028, Q4 | % of HFRA and HFTD Covered Annually by Inspection Type | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Transmission | Detailed (AI-04) | 3 years or WTRM | Drone, aerial lift, or ground visual | GO 165, TD 8123P 100, TD 1001M | - | 13200 | 22000 | 22000 | - | 13200 | 22000 | 22000 | - | 13200 | 22000 | 22000 | 40% | 0.2% | 19.2% | 14.7% (Asset)
Transmission | Infrared(a) (AI‑06) | 3 years or WTRM | Helicopter, drone, or a handheld sensor | GO 165, TD8123P100, TD 1001M, TD1001P14 | - | 500 | 1500 | 2500 | - | 500 | 1500 | 2500 | - | 500 | 1500 | 2500 | 40% | 0.02% | 0.15% | N/A (Circuit Mile)
Distribution | Aerial Scan(d) (AI‑07A) | 100% over 3-year cycle | Visual by aerial | GO 165, TD-2305M | - | 30000 | 50000 | 50000 | - | 12000 | 20000 | 20000 | - | 12000 | 20000 | 20000 | 5% | 0.12% | 0.66% | 0%
Distribution | Detailed(e)(f) (AI‑07D) | 100% over 3-year cycle | Visual by ground or aerial | TD-2305M-JA02, TD-2305P-03, TD-8123P-201 | - | 90000 | 190000 | 300000 | - | 90000 | 190000 | 305000 | - | 60000 | 160000 | 215000 | 42% | 0.15% | 15.96% | 0.95%
(a) Lines historically loaded below 40 percent may not be included for inspection due to low efficacy of method at low loading.
(b) Governing standards are available in Appendix E. Operating Procedures are available at: PG&E’s Community Wildfire Safety Program.
(c) Even though inspections typically commence in Q1, our main focus is on updates to inspection criteria based on learnings from the previous year, inspector training, and responding to the numerous winter storms that are typical across the service area. To enable a flexible response to changing conditions, we have not set an inspection target for Q1. Our overall target for each year remains unimpacted.
(d) In response to Critical Issue RN-PGE-26-06, Aerial Scan (AI-07A) target was created. The target units together with Detailed Inspections - Distribution (AI-07D) aim to achieve a cumulative 57% EOR. See 2026-2028 WMP Revision Notice Response R0 for additional information.
(e) Historical find rates are from detailed ground inspections only.
(f) In response to Critical Issue RN-PGE-26-06, Detailed inspections and aerial inspections targets together account for 57% Eyes-on-Risk (EOR). PG&E aims to achieve a cumulative 57% EOR across aerial scan and detailed inspections. This EOR can be allocated in any way across the two inspections. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table PG&E‑8.3.8.3‑1
TABLE PG&E‑8.3.8.3‑1:
2024 HFTD‑HFRA AERIAL INSPECTION FIND RATE BY NOTIFICATION PRIORITY 37
Electric Corrective Notification Priority | HFTD‑HFRA, Aerial Find Rate | HFTD‑HFRA, Ground Find Rate
| (Percentage of HFTD‑HFRA Aerial Inspections on Structures without an open Notification) | (Percentage of HFTD‑HFRA Ground Inspections on Structures without an open Notification)
A | 0.15% | 0.23%
X | 0.27% | 0.29%
B | 3.33% | 2.6%
E | 32.3% | 13.9%
F | 0.65% | 4.3%
_______________
Note 1: | Every year PG&E’s inspection workplan includes locations with an open notification and locations without an open notification. Therefore, the rates of EC Notification creation shown in Table 8.3.8.3‑1 cannot be applied to total outstanding inspection counts to predict future notifications. They must be applied to inspections on structures without an open EC notification. Roughly 6,000 structures without an open notification were inspected in HFTD/HFRA by ground and 140,000 by aerial in 2024.
Note 2: | As highlighted in the table above, Aerial inspections have a higher find rate of non‑emergency notifications compared to ground. This is expected because PG&E started aerial inspections at scale in 2024, and aerial inspections provide a unique vantage point for the top of pole conditions. We anticipate these find rates to decline when the same structures are re‑inspected with aerial in the next cycle.

## Table PG&E‑8.3.15.1‑1
TABLE PG&E‑8.3.15.1‑1:
SUBSTATION AND SWITCHYARD DRONE INSPECTION FIND RATE BY YEAR AND NOTIFICATION PRIORITY
Year | A (percentage) | B (percentage) | E (percentage)
2024 | 0.616% | 9.531% | 29.37%
2023 | 0.228% | 3.596% | 6.193%
2022 | 1.445% | 3.275% | 6.09%

## Table PG&E‑8.4‑1
TABLE PG&E‑8.4‑1:
EQUIPMENT MAINTENANCE AND REPAIR 39
Equipment Type(a) | Failure Rate in HFTD | CPUC Reportable Ignition Rate in HFTD
| (failures/1k assets/year) | (ignitions/failure)
| 2022‑2024 | 2014‑2024
8.4.1 – Capacitors | D: 0.324 | D: N/A
8.4.2 – Circuit Breakers | S(D): 0.182 | S(D): N/A
| S(T): 0.086 | S(T): N/A
8.4.3 – Connectors, Including Hotline Clamps | D: 0.901 | D: 0.060
| T: 0.435 | T: 0.105
8.4.4 – Conductor, Including Covered Conductor | D: 0.901 | D: 0.060
| T: 0.435 | T: 0.105
8.4.5 – Fuses, Including Expulsion Fuses | D: N/A | D: N/A
8.4.6 – Distribution Pole | D: 0.388 | D: 0.015
8.4.7 – Lightning Arrestors | D: 0.010 | D: 0.044
8.4.8 – Reclosers | D: 1.279 | D: 0.083
8.4.9 – Splices | D: 0.901 | D: 0.060
| T: 0.435 | T: 0.105
8.4.10 – Transmission Poles/Towers | T: 0.045 | T: 0.040
8.4.11 – Distribution Transformers | D: 3.297 | D: 0.008
8.4.12 – Non‑Exempt Equipment | N/A | N/A
8.4.13 – Pre‑GO 95 Legacy Equipment | D: N/A | D: N/A
8.4.14 – Other Equipment Not Listed | T (Switch): 2.217 | T (Switch): 0.111
| T (Insulator): 0.162 | T (Insulator): 0.075
| D (All Other): 0.865 | D (All Other): 0.017
_______________
(a) See specific Equipment Type sections for the nature of calculations.

## Table 8-3
TABLE 8‑3:
GRID DESIGN, ASSET INSPECTIONS, AND MAINTENANCE QA AND QC PROGRAM OBJECTIVES 12
Initiative/Activity Being Audited | Tracking IDs of Initiatives being Audited | Quality Program Type | Quality Management Initiative Tracking ID | Objective of the Quality Program
System Hardening – Undergrounding | GH‑04 | QC | GM‑11D | Ensure that new construction meets applicable standards.
System Hardening – Undergrounding | GH‑04 | QA | GM‑10D | Ensure that new construction meets applicable standards.
Open Tag Reduction – Distribution Backlog | GM‑03 | QC | GM‑13D | Ensure that corrective repair work meets applicable standards.
Open Tag Reduction – Distribution Backlog | GM‑03 | QA | GM‑12D | Ensure that corrective repair work meets applicable standards.
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution | AI‑07A, AI-07D | QC | GM‑09D(a) | Ensure inspections are following electrical corporation procedures for inspections.
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution | AI‑07A, AI-07D | QA | GM‑01D(a) | Ensure inspections are following electrical corporation procedures for inspections.
Detailed Inspection Transmission | AI‑04 | QC | GM‑09T | Ensure inspections are following electrical corporation procedures for inspections.
Detailed Inspection Transmission | AI‑04 | QA | GM‑01T | Ensure inspections are following electrical corporation procedures for inspections.
(a) GM-09D and GM-01D targets embed the Aerial Scan inspection program (AI-07A) with the Detailed Inspections - Distribution (AI-07D). The QA/QC will examine both AI-07A and AI-07D as a single population. The adjustments resulted from the Critical Issue RN-PGE-26-06. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table PG&E‑8.3‑1
TABLE PG&E‑8.3‑1:
ASSET INSPECTION FREQUENCY, METHOD, AND CRITERIA
Type | Inspection Activity (Program) | Frequency or Trigger | Method of Inspection | Governing Standards and Operating Procedures(f) | % of HFRA and HFTD Covered Annually by Inspection Type | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Transmission | Detailed Climbing | 3 years | Climbing | GO 165, | 25‑45% of 500 kV | 0% | 12.3% | 2.4%
|  |  |  | TD‑8123P‑100, TD‑1001M |  |  |  | (Asset)
Transmission | Intrusive Pole(a) | 10 years by line not to exceed 20 years by structure | Ground/ intrusive inspection | GO 165, | 5%‑25% of wood poles | 0.04% | 11.3% | 0.003%
|  |  |  | TD‑2325S |  |  |  | (Asset)
Transmission | Switch Function Tests(b) | 8 years | Detailed Aerial with some function tests as triggered | GO 165, | 12‑45% | 0.6% | 17% | 0.5%
|  |  |  | TD‑1006P‑02, TD‑1001M |  |  |  | (Asset)
Transmission | Patrol(c) | Every year not inspected by Detailed Inspection Program | Aerial or ground | GO 165, | 55‑75%(d) | 0.05% | 0.18% | 0.03%
|  |  |  | TD‑8123P‑100, TD‑1001M |  |  |  | (Asset)
Transmission | Conductor Measurement | TBD – Pilot | LineVue robotic device | NA – Pilot | NA – Pilot | NA ‑ Pilot | NA ‑ Pilot | NA – Pilot
Transmission | Proactive Sampling/Testing | TBD – Pilot | Laboratory or field analysis | NA ‑ Pilot | NA – Pilot | NA ‑ Pilot | NA ‑ Pilot | NA – Pilot
Distribution | Ground Patrol | WDRM V4 | Visual | TD‑8123S | ~67% | 0.035% | 0.07% | 0.003%
Distribution | IR Inspection | As needed to investigate emerging issues | Infrared | TD‑2022P‑01 | N/A | (per circuit‑mile inspected) | (per circuit‑mile inspected) | (per circuit‑mile inspected)
[6 empty] | 0 | 0.53 | 0
Distribution | Intrusive Pole Inspections | Approximately 10 or 20 year cycle(e) | Ground/ | TD‑2325S & TD‑2325P‑01 | N/A | 0.084% | 4% | 0.58%
hole‑boring
Distribution | LiDAR‑Based Pole Loading Assessments | First time analysis – does not have a recurring frequency | Helicopter and vehicle | N/A | N/A | N/A | N/A | N/A
Distribution | Overhead Equipment Inspections | Annually | Ground visual | TD‑2302P‑05 | 100% | N/A | N/A | N/A
Substation | Aerial (drone) Inspection | 3‑years or in‑year based on risk | Aerial | TD‑3322S | 100% over 3‑year cycle | See Table PG&E‑8.3‑15.1‑1 | See Table PG&E‑8.3‑15.1‑1 | See Table PG&E‑8.3‑15.1‑1
_______________
(a) Method only applicable to wood poles. Inspection scope is regionally‑optimized, leading to variable HFTD/HFRA coverage.
(b) Find Rate listed is for function tests. See Detailed Inspection for visual find rate.
(c) May change depending on yearly detailed inspection scope. Percent HFRA and HFTD covered by patrols in 100 percent with the inclusion of detailed inspections.
(d) Annual coverage of HFRA and HFTD is 100 percent, when combined with Transmission Detailed Inspections.
(e) PG&E plans to return to a 10‑year PT&T cycle beginning in 2027
(f) Governing standards are available in Appendix E. Operating Procedures are available at Community Wildfire Safety Program.

## Table 8-4
TABLE 8‑4:
GRID DESIGN, ASSET INSPECTIONS, AND MAINTENANCE QA AND QC ACTIVITY TARGETS
Initiative/Activity Being Audited | Quality Program Type | Type of Audit | Population / Sample Unit | 2026: Population Size | 2026: Sample Size | 2027: Population Size | 2027: Sample Size | 2028: Population Size | 2028: Sample Size | Percent of Sample in the HFTD/HFRA | Confidence Level/Margin of Error (MOE) | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
System Hardening - Undergrounding | QC | Field/Desktop | Circuit Miles | 360(a) | 302(a) | 307 | 264 | 400 | 329 | 100% | Minimum 99%/3% | 80% | 88% | 95%
System Hardening - Undergrounding | QA | Field/Desktop | Circuit Miles | 360(a) | 187(a) | 307 | 171 | 400 | 197 | 100% | 95%/5% | 88% | 92% | 95%
Open Tag Reduction – Distribution Backlog | QC | Field/Desktop | Distribution Overhead EC Tags | 70,000(b) | 25000 | 70,000(b) | 30000 | 70,000(b) | 35000 | 100% | Minimum 99%/1% | 80% | 88% | 95%
Open Tag Reduction – Distribution Backlog | QA | Field/Desktop | Distribution Overhead EC Tags | 70,000(b) | 383 | 70,000(b) | 383 | 70,000(b) | 383 | 100% | 95%/5% | 88% | 92% | 95%
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution | QC | Field/Desktop | Distribution Poles | 350,000(c) | 65000 | 325000(c) | 65000 | 235,000(c) | 65000 | 100% | Minimum 99%/1% | 95% | 95% | 95%
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution | QA | Field/Desktop | Distribution Poles | 350,000(c) | 384 | 325,000(c) | 384 | 235,000(c) | 384 | 100% | 95%/5% | 95% | 96% | 97%
Detailed Inspection Transmission | QC | Field/Desktop | Transmission Structures | 22000 | 9458 | 22000 | 9458 | 22000 | 9458 | 100% | Minimum 99%/1% | 95% | 95% | 95%
Detailed Inspection Transmission | QA | Field/Desktop | Transmission Structures | 22000 | 378 | 22000 | 378 | 22000 | 378 | 100% | 95%/5% | 95% | 96% | 97%
(a) In response to Critical Issue RN-PGE-26-05, population size has been adjusted to reflect the updated workplan for 2026. Sample size has been updated accordingly. See 2026-2028 WMP Revision Notice Response R0 for additional information.
(b) Subject to change in alignment with Initiative/Activity Being Audited Workplan.
(c) In response to Critical Issue RN-PGE-26-06, population size has been adjusted to reflect the updated workplan for 2026-2028. QA/QC will example both Aerial Scan Inspections - Distribution (AI-07A) and Detailed Inspections - Distribution (AI-07D) as a single population. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table PG&E‑8.5.2‑1
TABLE PG&E‑8.5.2‑1:
QA/QC GUIDANCE DOCUMENTS 42
Initiative/Activity Being Audited | Quality Program Type | Applicable Procedures(a) | Version(s) and effective date(s)
System Hardening – Undergrounding | QC | RISK‑6501P‑01 | 10/2024, Rev: 0
System Hardening – Undergrounding | QA | RISK‑6501P‑01 | 10/2024, Rev: 00
|  | RISK‑6501S | 10/2024, Rev: 00
Open Tag Reduction – Distribution Backlog | QC | RISK‑6501P‑05 | 04/2024, Rev: 4
Open Tag Reduction – Distribution Backlog | QA | RISK‑6501S | 10/2024, Rev: 00
|  | RISK‑6501P‑05 | 10/2024, Rev: 00
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution(b) | QC | RISK‑6501P‑04 | 04/2023, Rev: 0
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution(b) | QA | RISK‑6501S | 10/2024, Rev: 00
|  | RISK‑6501P‑08 | 10/2024, Rev: 00
Detailed Inspection Transmission | QC | RISK‑6501P‑04 | 04/2023, Rev: 0
Detailed Inspection Transmission | QA | RISK‑6501S | 10/2024, Rev: 00
|  | RISK‑6501P‑08 | 10/2024, Rev: 0
_______________
(a) The supporting documents are available at PG&E's Community Wildfire Safety Program.
(b) Updated to include Aerial Scan Inspections in response to Critical Issue RN-PGE-26-06. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table PG&E‑8.5.3‑1
TABLE PG&E‑8.5.3‑1:
QA/QC SAMPLING PLAN 43
Initiative/Activity Being Audited | Tracking IDs of Initiatives Being Audited | Quality Program Type | Quality Management Initiative Tracking ID | Sampling Plan
System Hardening – Undergrounding | GH‑04 | QC | GM‑11D | HFTD, HFRA, buffer areas, and fire rebuild areas
System Hardening – Undergrounding | GH‑04 | QA | GM‑10D | HFTD, HFRA, buffer areas, and fire rebuild areas
Open Tag Reduction – Distribution Backlog | GM‑03 | QC | GM‑13D | HFTD, HFRA, and buffer areas: priority informed by outage, ignition, Notice of Violation (NOV) trends
Open Tag Reduction – Distribution Backlog | GM‑03 | QA | GM‑12D | HFTD, HFRA, and buffer areas: priority informed by outage, ignition, NOV trends
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution | AI‑07A, AI-07D | QC | GM‑09D(a) | HFTD, HFRA, and buffer areas: priority informed by extreme, severe, high‑risk ranking. Not limited to any one inspection methodology and to include aerial scans.
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution | AI‑07A, AI-07D | QA | GM‑01D(a) | HFTD, HFRA, and buffer areas: priority informed by extreme, severe, high‑risk ranking. Not limited to any one inspection methodology and to include aerial scans.
Detailed Inspection Transmission | AI‑04 | QC | GM‑09T | HFTD, HFRA, and buffer areas: priority informed by extreme, severe, high‑risk ranking
Detailed Inspection Transmission | AI‑04 | QA | GM‑01T | HFTD, HFRA, and buffer areas: priority informed by extreme, severe, high‑risk ranking
(a) GM-09D and GM-01D targets embed the Aerial Scan inspection program (AI-07A) with the Detailed Inspections - Distribution (AI-07D). The QA/QC will examine both AI-07A and AI-07D as a single population. The adjustments resulted from the Critical Issue RN-PGE-26-06. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## TABLE PG&E 8.5.4‑1
TABLE PG&E-8.5.4‑1:
PASS RATE CALCULATION 44
Initiative/ Activity Being Audited | Quality Program Type | Sample Unit | Pass Criteria | Fail Criteria | Pass Rate Calculation
System Hardening – Undergrounding | QC | Circuit Miles | Attributes meeting QC audit acceptance criteria | Attributes not meeting QC audit acceptance criteria | Passed opportunities/total opportunities
System Hardening – Undergrounding | QA | Circuit Miles | Attributes meeting QA audit acceptance criteria | Attributes not meeting all QA audit acceptance criteria | Passed opportunities/total opportunities
Open Tag Reduction – Distribution Backlog | QC | Distribution Overhead EC Tags | Passed opportunities within audit checklist acceptance criteria based on location attributes | Failed opportunities within audit checklist acceptance criteria based on location attributes | Passed opportunities over total opportunities.
Open Tag Reduction – Distribution Backlog | QA | Distribution Overhead EC Tags | Passed opportunities within audit checklist acceptance criteria based on location attributes | Failed opportunities within audit checklist acceptance criteria based on location attributes | Passed opportunities over total opportunities.
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution(a) | QC | Unique inspection reviewed | Unique count of inspections reviewed where Audit Findings = 0 | Unique count of inspections reviewed where Audit Findings ≠ 0 | Total inspections passed/Total inspections reviewed
Aerial Scan Inspections - Distribution, Detailed Inspections – Distribution(a) | QA | Unique inspection reviewed | Unique count of inspections reviewed where Audit Findings = 0 | Unique count of inspections reviewed where Audit Findings ≠ 0 | Total inspections passed/Total inspections reviewed
Detailed Inspection Transmission | QC | Unique inspection reviewed | Unique count of inspections reviewed where Audit Findings = 0 | Unique count of inspections reviewed where Audit Findings ≠ 0 | Total inspections passed/Total inspections reviewed
Detailed Inspection Transmission | QA | Unique inspection reviewed | Unique count of inspections reviewed where Audit Findings = 0 | Unique count of inspections reviewed where Audit Findings ≠ 0 | Total inspections passed/Total inspections reviewed
(a) Updated to include Aerial Scan Inspections in response to Critical Issue RN-PGE-26-06. See 2026-2028 WMP Revision Notice Response R0 for additional information.

## Table 8‑5‑1
TABLE 8‑5‑1:
NUMBER OF PAST DUE ASSET WORK ORDERS CATEGORIZED BY AGE
(AS OF DECEMBER 31, 2024) 45
HTFD Area | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
HFTD‑Tier 2 | 33 | 88 | 149 | 934
HFTD‑Tier 3 | 86 | 220 | 86 | 101
Zone 1 | 2 | 1 | 6 | 20
Non‑HFTD HFRA | 18 | 10 | 19 | 63
Non‑HFTD Non‑HFRA | 191 | 1727 | 2709 | 8018

## Table 8‑6‑1
TABLE 8‑6‑1:
NUMBER OF PAST DUE ASSET WORK ORDERS CATEGORIZED BY PRIORITY LEVEL
(AS OF DECEMBER 31, 2024) 46
Priority Level | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
Priority 1 | – | – | – | –
Priority 2 | 296 | 1959 | 2795 | 8763
Priority 3 | 34 | 87 | 174 | 373

## Table PG&E‑8.6.2‑1
TABLE PG&E‑8.6.2‑1:
ANNUAL FORECASTED CREATIONS AND CLOSURE VOLUME
Year | Forecasted Annual Created | Forecasted Cumulative Creations Since 2025 | Forecasted Annual Closures | Forecasted Cumulative Closures Since 2026 | Percent of EC Tags Created Since 2025 Closed at EOY
2025 | 76000 | 76000 | N/A
2026 | 59000 | 135000 | 102000 | 102000 | >130%
2027 | 61000 | 196000 | 105000 | 207000 | >150%
2028 | N/A |  | 107000 | 314000 | 160%
_______________
Note: We are not held to these forecasted creation and closure volumes. Forecasted notification creations can change due to changes to inspection types and procedures among a variety of other variables.

## Table PG&E‑8.6.2‑2
TABLE PG&E‑8.6.2‑2:
ELECTRIC NOTIFICATIONS PRIORITY LEVELS 48
Line No. | GO 95 Rule 18 | PG&E Priority | Description | GO 95 Rule 18 Timeline for Corrective Action | PG&E Internal Timeline for Corrective Action (Electric Notifications)
1 | Level 1 | A (Electric) | An immediate risk of high potential impact to safety or reliability. | Take corrective action immediately, either by fully repairing or by temporarily repairing and reclassifying to a lower priority. | Consistent with GO 95, Rule 18
2 | Level 2 | X (Electric Dx) | High potential impact to safety or reliability but do not pose an immediate risk (introduced in spring 2024). | Time period for corrective action to be determined at the time of identification by a qualified Company representative, but not to exceed: | Corrective action within seven days from date condition identified for electric equipment
Six months for potential violations that create a fire risk located in Tier 3 of the HFTD.
12 months for potential violations that create a fire risk located in Tier 2 of the HFTD.
12 months for potential violations that compromise worker safety; and
36 months for all other Level 2 potential violations.
|  | B (Electric Dx) | Any other risk of at least moderate potential impact to safety or reliability: | Same as above | Corrective action within 6 months from date condition identified for electric equipment
Take corrective action within the specific time period (either by fully repairing or by temporarily repairing or reclassifying to Level 3 priority).
3 |  | E (Electric) | Any other risk of at least moderate potential impact to safety or reliability: | Same as above | Corrective action within:
|  |  | Take corrective action within the specific time period (either by fully repairing or by temporarily repairing or reclassifying to Level 3 priority). |  | Six months for conditions that create a fire risk located in HFTD Tier 3
12 months for conditions that create a fire risk located in HFTD Tier 2
Transmission: Corrective action timelines can be reduced below the maximum values listed above.
4 |  | H (Electric Dx) | These are PG&E Priority “E” Notifications that are planned to be addressed by a planned System Hardening Project. | Same as above. | Same as above.
5 | Level 3 | F (Electric) | Any risk of low potential impact to safety or reliability. | Take corrective action within 60 months subject to the specific exceptions. | Corrective actions to be addressed within five years from date condition is identified.
______________
Note: Exception – Potential violations specified in Appendix J or subsequently approved through Commission processes, including, but not limited to, a Tier 2 Advice Letter under GO 96B, that can be completed at a future time as opportunity‑based maintenance. Where an exception has been granted, repair of a potential violation must be completed the next time the Company’s crew is at the structure to perform tasks at the same or higher work level (i.e., public, communications, or electric level). The condition’s record in the auditable maintenance program must indicate the relevant exception and the date of the corrective action.

## Table 8‑5‑2
TABLE 8‑5‑2:
NUMBER OF PAST DUE ASSET WORK ORDERS CATEGORIZED BY AGE AND HFTD TIER
(AS OF DECEMBER 31, 2024) 49
HFTD Area | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
HFTD Tier 2 | 1 | 19 | 137 | 129785
HFTD Tier 3 | 1 | 7 | 59 | 45372

## Table 8‑6‑2
TABLE 8‑6‑2:
NUMBER OF PAST DUE ASSET WORK ORDERS CATEGORIZED BY PRIORITY LEVEL
(AS OF DECEMBER 31, 2024) 50
Priority Level | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
Level 2 | 2 | 26 | 196 | 167295
Level 3 | – | – | – | 7862

## Table 8‑5‑3
TABLE 8‑5‑3:
NUMBER OF PAST DUE ASSET WORK ORDERS CATEGORIZED BY AGE
(AS OF DECEMBER 31, 2024) 51
HTFD Area | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
Non‑HFTD | 32 | 13 | 34 | 6
HFTD‑Tier 2 | 1 | 1 | – | –
HFTD‑Tier 3 | – | – | – | –

## Table 8‑6‑3
TABLE 8‑6‑3:
NUMBER OF PAST DUE ASSET WORK ORDERS CATEGORIZED BY PRIORITY LEVEL
(AS OF DECEMBER 31, 2024) 52
Priority Level | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
Level 1 | – | – | – | –
Level 2 | 33 | 14 | 34 | 6
Level 3 | – | – | – | –

## Table 8‑7
TABLE 8‑7:
TOP TEN IMPACTED CIRCUITS FROM CHANGES TO EPSS IN THE PAST THREE YEARS (2022‑2024) 53
Circuit/Circuit Segment ID | Circuit/Circuit Segment Name | Circuit/Circuit Segment Length (Overhead Circuit Miles) | Number of Outages in Past Three Years | Cumulative Outage Duration | Cumulative Number of Customers Impacted by Outages
(in Minutes)
183052113 | Templeton 2113 | 321.7 | 59 | 13622 | 75974
83622106 | Camp Evers 2106 | 79.9 | 52 | 17961 | 60189
43432104 | Silverado 2104 | 142.2 | 52 | 23246 | 39419
253642101 | Poso Mountain 2101 | 59.1 | 51 | 27338 | 3117
63172101 | Madison 2101 | 168.1 | 51 | 16476 | 27571
182391103 | Oilfields 1103 | 144.5 | 50 | 68470 | 54977
153662102 | Apple Hill 2102 | 359.7 | 50 | 18794 | 79618
163351702 | Curtis 1702 | 117.4 | 49 | 20864 | 57264
153082106 | Placerville 2106 | 272.6 | 49 | 15871 | 77250
254061102 | Dunlap 1102 | 55.3 | 46 | 28294 | 4934

## Table PG&E 8.7.1.1‑1
TABLE PG&E 8.7.1.1‑1:
WILDFIRE RISK LEVELS 54
Risk Level | Definition
R1 | Very little or no fire danger.
R2 | Moderate fire danger.
R3 | Fire danger is so high that care must be taken using fire‑starting equipment. Local conditions may limit the use of machinery and equipment to certain hours of the day.
R4 | Fire danger is critical. Using equipment and open flames is limited to specific areas and times.
R5 | Fire danger is so critical that using some equipment and open flames is not allowed in certain areas.
R5‑Plus | The greatest level of fire danger where rapidly moving catastrophic wildfires are possible. This is typically when fire danger is R5 and there are additional high‑risk weather triggers (e.g., strong winds).

## Table PG&E‑8.7.1.1‑2
TABLE PG&E‑8.7.1.1‑2:
SUMMARY OF EPSS CAPABLE MILES 55
Mile Type | Miles | % Circuit Miles in HFRA
HFRA | 25026 | 100%
EPSS Buffer Zones | 9536 | 0%
Additional Miles (e.g., miles outside of HFRA or Buffer Areas electrically connected to an EPSS ‑capable device) | 9284 | 0%
Total | 44846 | 57%

## Table PG&E‑8‑9
TABLE PG&E‑8‑9:
WORKFORCE PLANNING, ASSET INSPECTIONS 56
QCR Worker Title | Minimum Qualifications for Target Role | Special Certification Requirements | Reference to Electrical Corporation Training/Qualification Programs
Compliance Inspector | QEW Consisting of Journeyman Lineman and New Inspector Training | Compliance Inspector Training Course | ELEC‑1000 (Initial)
TECH‑0020 (Refresher)
ELEC‑0340 (CONT)
ELEC‑0341 (CONT)
ELEC‑0342 (CONT)
Compliance Inspector – Underground | Journey Level Cable Splicer | Compliance Inspector Training Course | ELEC‑1000 (Initial)
TECH‑0020 (Refresher)
ELEC‑0340 (CONT)
ELEC‑0341 (CONT)
ELEC‑0342 (CONT)
_______________
(a) All PG&E employees and contractors meet the minimum qualifications for the assigned role.

## Table PG&E‑8‑10
TABLE PG&E‑8‑10:
WORKFORCE PLANNING, GRID HARDENING 57
Worker Title | Minimum Qualifications for Target Role | Special Certification Requirements/ Qualifications | Reference to Electrical Corporation Training/ Qualification Programs
General Foreman (Ext. only) | 18 years of age or older | QEW | Electrical Corporation: Required Trainings relevant to Wildfire Mitigation (see paragraphs above)
| High School Diploma, GED or equivalent experience | Journeyman Lineman Certificate (union sponsored) (i.e., NECA, IBEW Seal and Apprentice Certification) | Contractor: Contractor company is responsible for the qualifications of their employees. However, contracted employees are held to the same standards as PG&E employees.
| Journeyman Lineman having completed an accredited apprenticeship program |  | Multiple PG&E departments perform safety observations of contractors and perform quality audits of completed work. Contractors should have ISN badges that are confirmed by Environmental Health and Safety org. during site visits.
International Brotherhood of Electrical Workers (IBEW) Journeyman Lineman status in good standing
Class A California driver’s license
Foreman | 18 years of age or older | QEW | See above
(Elec. Corporation PG&E and External) | High School Diploma, GED or equivalent experience | Journeyman Lineman Certificate (union sponsored) (i.e., NECA, IBEW Seal and Apprentice Certification)
Journeyman Lineman having completed an accredited apprenticeship program
IBEW Journeyman Lineman status in good standing
Class A California driver’s license
Lineman | 18 years of age or older | QEW | See above
(Elec. Corporation PG&E and External) | High School Diploma, GED or equivalent experience | Journeyman Lineman Certificate (union sponsored) (i.e., NECA, IBEW Seal and Apprentice Certification)
Journeyman Lineman having completed an accredited apprenticeship program
IBEW Journeyman Lineman status in good standing
Class A California driver’s license
Apprentice Lineman | 18 years of age or older | N/A | See above
High School Diploma or GED
Successful passing of the ALP and the Three‑Day Climbing Couse
Valid California driver’s license
Valid Class A California driver’s permit and DMV medical card within 3 months of hire
Valid Class A California driver’s license and DMV medical card within 6 months of hire
Various physical requirements
Groundman (Ext. only) | 18 years of age or older | Occupational Safety and Health Administration (OSHA) 10 | See above
Class A California driver’s license with tanker endorsement
Utility Worker (Electrical Corp. only) | 18 years of age or older | N/A | See above
High School Diploma or GED
Valid CA Class C driver’s license (or higher)
Valid CA Class A license within three months of hire
Various physical requirements
Misc. Equipment Operator (Electrical Corp. only) | 18 years of age or older | N/A | See above
High school diploma or GED
Valid CA Class A driver’s license permit
Valid DMV Medical Card
Various physical requirements
Cable Splicers | 18 years of age or older | IBEW journeyman card for Cable Splicer or State JATC certification | See above
| High School Diploma or GED | 40‑hour Switchman Training Certification / Card
Valid CA Class C driver’s license (or higher)
2 years’ experience as Journey Cable Splicer
Apprentice Cable Splicer | Valid Class C California driver’s license | N/A | See above
Electric Crew Inspector (External) | Journeyman Lineman or certified by duly constituted Outside Line Construction Local Union of the IBEW with at least 3.5 years in the trade. | Journeyman Lineman Certificate | See above
Valid Class C California driver’s license.
Civil Crew Inspector | Valid Class C California driver’s license. | OSHA 10 | See above
_______________
(a) All PG&E and contract employees must meet the minimum qualifications for performing the assigned role.

## Table PG&E‑8‑11
TABLE PG&E‑8‑11:
WORKFORCE PLANNING, RISK EVENT INSPECTION 58
Worker Title | Minimum Qualifications for Target Role | Special Certification Requirements | Reference to Electrical Corporation Training/Qualification Programs
Troublemen | QEW. | N/A – Nothing beyond QEW | While these roles do not have certifications directly related to Wildfire and PSPS mitigation, these roles and their work is important to the ongoing, safe operation of PG&E equipment throughout our Service Area, including to mitigate wildfire risks.
In some instances, work can be performed by non ‑QEWs roles, but the work is always performed under the direction of a QEW.
Distribution Line Technicians | QEW. | N/A – Nothing beyond QEW | There is a specialized training program to inspect and maintain critical line control and voltage devices. While these roles do not have certifications directly related to Wildfire and PSPS mitigation, these roles and their work is important to the ongoing, safe operation of PG&E equipment throughout our Service Area, including to mitigate wildfire risks.
In some instances, work can be performed by non ‑QEWs roles, but the work is always performed under the direction of a QEW.
_______________
(a) All PG&E employees meet the minimum qualifications for performing the assigned role.
(b) PG&E does not use contractor resources for these roles. This work is completed by PG&E employees.

## Table 9-1
TABLE 9‑1:
VEGETATION MANAGEMENT TARGETS BY YEAR (Non‑inspection targets)
Initiative | Quantitative or Qualitative | Activity (Tracking ID) | Previous Tracking ID, if applicable | Target Unit | 2026 Target / Status | % Risk Reduction for 2026 | 2027 Target / Status | % Risk Reduction for 2027 | 2028 Target / Status | % Risk Reduction for 2028 | Three‑Year Total | Section;
Page Number
Vegetation Management and Inspections | Qualitative | Wood Management Benchmarking | n/a | n/a | Initiate benchmarking with peer utilities. | n/a | Gather benchmarking survey responses and facilitate discussions regarding potential alignment on best practices. | n/a | Complete implementation of any relevant updates to PG&E procedure, if applicable. | n/a | n/a | 9.5;
|  | (VM‑23)(a) | [9 empty] | p. 387
Vegetation Management and Inspections | Qualitative | ​​Workforce Planning ‑ Vegetation Management​ | n/a | n/a | Provide funding towards Community College towards recruitment of individuals looking to pursue a VM career path, provide funding for VM‑related certifications and memberships, complete annual audit of the completion of VM Training courses. | n/a | Provide funding towards Community College towards recruitment of individuals looking to pursue a VM career path, provide funding for VM‑related certifications and memberships, complete annual audit of the completion of VM Training courses. | n/a | Provide funding for VM‑related certifications and memberships, complete annual audit of the completion of VM Training courses. | n/a | n/a | 9.13;
|  | (VM‑24)(a) | [9 empty] | p. 426
Vegetation Management and Inspections | Qualitative | Integrated Vegetation Management Benchmarking | VM‑15 | n/a | Initiate benchmarking with peer utilities. | n/a | Gather benchmarking survey responses and facilitate discussions regarding potential alignment on best practices. | n/a | Complete implementation of any relevant updates to PG&E procedure, if applicable. | n/a | n/a | 9.7;
|  | (VM‑25)(a) | [9 empty] | p. 391
Vegetation Management and Inspections | Quantitative | Mitigation of Legacy Tree Removal Inventory (TRI) (VM‑26)(b) | VM‑04 | Trees | 40000 | 0.94% (Cumulative) | 85,000 (Cumulative) | 1.99% (Cumulative) | 135000 | 3.16% (Cumulative) | 135000 | 9.2.1; p. 366
[5 empty] | (Cumulative) |  |  |  | (Cumulative)
(a) | See Critical Issue RN-PGE-26-08 for additional information.
(b) | VM 26 is a cumulative target of 135,000 therefore the 85,000 trees shown in 2027 is inclusive of the 40,000 trees from 2026. The risk reduction shown is cumulative as well.

## Table 9-2
TABLE 9‑2:
Activity (Program) | Tracking ID | Previous Tracking ID, if applicable | Target Unit | Cumulative (Cml.) Quarterly Target 2026, Q1 | Cml. Quarterly Target 2026, Q2 | Cml. Quarterly Target 2026, Q3 | Cml. Quarterly Target 2026, Q4 | Cml. Quarterly Target 2027, Q1 | Cml. Quarterly Target 2027, Q2 | Cml. Quarterly Target 2027, Q3 | Cml. Quarterly Target 2027, Q4 | Cml. Quarterly Target 2028, Q1 | Cml. Quarterly Target 2028, Q2 | Cml. Quarterly Target 2028, Q3 | Cml. Quarterly Target 2028, Q4 | % HFTD | % Risk Reduction for 2026 | % Risk Reduction for 2027(a) | % Risk Reduction for 2028(a) | Three‑Year Total | Activity Timeline Target | Section; Page Number
Covered in 2026(d)
Pole Clearing Program ‑ Compliance(b) | VM‑02C | VM‑02 | Poles(c) | 13668 | 30958 | 45710 | 45710 | 13668 | 30958 | 45710 | 45710 | 13668 | 30958 | 45710 | 45710 | 4% | 0.06% | 0.06% | 0.06% | 137130 | 365 days | 9.4; p. 385
Pole Clearing Program ‑ Risk Reduction(b) | VM‑02R | VM‑02 | Poles(c) | 6820 | 16445 | 24290 | 24290 | 6820 | 16445 | 24290 | 24290 | 6820 | 16445 | 24290 | 24290 | 4% | 0.04% | 0.04% | 0.04% | 72870 | 365 days | 9.4; p. 385
Substation Inspections ‑ Distribution | VM‑05 | VM‑05 | Distribution Substations | 58 | 122 | 130 | 130 | 58 | 122 | 130 | 130 | 58 | 122 | 130 | 130 | 100% | 53% (Eyes on Risk) | 53% (Eyes on Risk) | 53% (Eyes on Risk) | 390 | 274 days | 9.6; p. 389
Substation Inspections – Transmission | VM‑06 | VM‑06 | Transmission Substations | ‑ | 53 | 55 | 55 | ‑ | 53 | 55 | 55 | ‑ | 53 | 55 | 55 | 100% | 23% (Eyes on Risk) | 23% (Eyes on Risk) | 23% (Eyes on Risk) | 165 | 274 days | 9.6; p. 389
Substation Inspections – Power Generation | VM‑07 | VM‑07 | Power Generation Switchyards and Powerhouses | ‑ | 52 | 58 | 58 | ‑ | 52 | 58 | 58 | ‑ | 52 | 58 | 58 | 100% | 24% (Eyes on Risk) | 24% (Eyes on Risk) | 24% (Eyes on Risk) | 174 | 274 days | 9.6; p. 389
Routine Transmission – Ground | VM‑13 | VM‑13 | Circuit Miles | 1989 | 10000 | 15000 | 17500 | 1925 | 10000 | 15000 | 17500 | 1925 | 10000 | 15000 | 17500 | 100% | 100% (Eyes on Risk) | 100% (Eyes on Risk) | 100% (Eyes on Risk) | 52500 | 365 days | 9.2.3; p. 375
Transmission Hazard Patrol (Second Patrol, Tree Mortality) | VM‑14 | VM‑14 | Circuit Miles | ‑ | ‑ | ‑ | 5625 | ‑ | ‑ | ‑ | 5625 | ‑ | ‑ | ‑ | 5625 | 100% | 100% (Eyes on Risk) | 100% (Eyes on Risk) | 100% (Eyes on Risk) | 16875 | 365 days | 9.2.4; p. 380
Distribution Routine Patrol | VM‑16 | VM‑16 | Circuit Miles | 11500 | 31500 | 50500 | 78200 | 11500 | 31000 | 50000 | 77800 | 11000 | 31000 | 50000 | 77500 | 100% | 100% (Eyes on Risk) | 100% (Eyes on Risk) | 100% (Eyes on Risk) | 233500 | 365 days | 9.2.1; p. 366
Distribution Hazard Patrol (Second Patrol, Tree Mortality) | VM‑17 | VM‑17 | Circuit Miles | 1500 | 4000 | 6500 | 10000 | 1500 | 4000 | 6500 | 10000 | 1500 | 4000 | 6500 | 10000 | 39% | 75.14% (Eyes on Risk) | 75.14% (Eyes on Risk) | 75.14% (Eyes on Risk) | 30000 | 365 days | 9.2.2; p. 371
(a) | Estimates for the 2027 & 2028 risk reduction are not available at the time of WMP submission. As such, 2026 risk reduction values will be used as a proxy.
(b) | Pole Clearing Program (VM 02) is separated into Pole Clearing Program-Compliance (VM 02C) and Pole Clearing Program - Risk Reduction (VM 02R) in response to Critical Issue RN-PGE-26-10. See 2026 2028 WMP Revision Notice Response R0 for additional information.
(c) | Poles are defined in this target as distribution and transmission poles and structures.
(d) | Values have been updated as a result of Substantive Errata filing on April 18, 2025, in accordance with Revision Notice at 21. Note that the values for Pole Clearing Program-Compliance and Pole Clearing Program-Risk Reduction have since been updated in response to Critical Issue RN-PGE-26-10.
(e) | In response to Critical Issue RN-PGE-26-09, PG&E created a target for Mitigation of Legacy Tree Removal Inventory (TRI) (VM-26). See Table 9-1 for more information on VM-26. Percent Risk Reduction for 2026 - 2028 has been updated to reflect the removal of the VM-26 from Distribution Routine Patrol. See 2026 2028 WMP Revision Notice Response R0 for more information.

## Table 9‑3
TABLE 9‑3:
VEGETATION MANAGEMENT INSPECTION FREQUENCY, METHOD, AND CRITERIA 61
Type | Inspection Activity | Area Inspected | Frequency | Section; Page Number
Distribution | Routine Patrol | Territory | Annual | 9.2.1; p. 366
Distribution | Hazard Patrol (previously referred to as “Second Patrol” or “Tree Mortality”) | HFTD/HFRA | Offset from annual inspections by approximately 6 months | 9.2.2; p.371
Transmission | Routine Patrol | Territory | Annual | 9.2.3; p. 375
Transmission | Hazard Patrol (previously referred to as “Second Patrol” or “Tree Mortality”) | HFTD/HFRA | Offset from annual inspections | 9.2.4; p. 380

## Table PG&E‑9.2.1.3‑1
TABLE PG&E‑9.2.1.3‑1:
RADIAL CLEARANCES, PER GO 95, APPENDIX E 62
Voltage of Line | Case 13 of | Case 14 of
| Table 1(a) | Table 1(b)
Radial clearances for any conductor of a line operating at 2,400 or more volts, but less than 72,000 volts | 4 feet | 12 feet
______________
(a) Case 13 of Table 1: Refers to GO 95, Rule 35, , Table 1. Case 13 is radial clearance of bare line conductors from tree branches or foliage in non‑HFTD.
(b) Case 14 of Table 1: Refers to GO 95, Rule 35, Table 1. Case 14 is radial clearance of bare line conductors from vegetation in the HFTD.
(c) GO 95 is available at the following link: https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M550/K438/550438485.pdf

## Table PG&E‑9.2.3.3‑1
TABLE PG&E‑9.2.3.3‑1:
PG&E MINIMUM CLEARANCE DISTANCES 63
| 60 or 70 kilovolts (kV) | 115 kV | 230 kV | 500 kV
PG&E Minimum Clearance Distance | 4 feet (ft.) | 10 ft. | 10 ft. | 15 ft.
_______________
Note: The PG&E defined minimum clearance distances are designed to meet or exceed all applicable regulatory requirements, including NERC Standard FAC‑003‑5, PRC 4293 and CPUC GO 95, Rule 35.

## Table PG&E‑9.2.3.3‑2
TABLE PG&E‑9.2.3.3‑2:
CPUC MINIMUM CLEARANCE DISTANCE REQUIREMENTS AND RECOMMENDATIONS 64
| 60 or 70 kV | 115 kV | 230 kV | 500 kV
CPUC Requirement in non‑HFTD (Case 13) | 1 ft. 6 in. | 1 ft.7 in. | 2 ft 6.5 in. | 9 ft.7 in.
CPUC Recommendation at Time of Trim | 4 ft. | 10 ft. | 10 ft. | 15 ft.
CPUC Requirement in HFTD (Case 14) | 4 ft. | 10 ft. | 10 ft. | 10 ft.
CPUC Recommendation at Time of Trim in HFTD | 12 ft. | 30 ft. | 30 ft. | 30 ft.
_______________
Note: The CPUC minimum clearance distances are in CPUC GO 95, Table 1 and Appendix E. Reasonable vegetation practices may make it advantageous for the purpose of public safety or service reliability to obtain greater clearances than those in this table to ensure compliance until the next scheduled maintenance.

## Table PG&E‑9.2.3.3‑3
TABLE PG&E‑9.2.3.3‑3:
NERC MINIMUM VEGETATION CLEARANCE DISTANCE (MVCD) IN FEET 65
Elevation (feet) | 60/70 kV | 115 kV | 230 kV | 500 kV
0‑500 | 1.1 ft. | 1.9 ft. | 4.0 ft. | 7.0 ft
501‑1,000 | 1.1 | 1.9 | 4.1 | 7.1
1,001‑2,000 | 1.1 | 1.9 | 4.2 | 7.2
2,001‑3,000 | 1.2 | 2 | 4.3 | 7.4
3,001‑4,000 | 1.2 | 2 | 4.3 | 7.5
4,001‑5,000 | 1.2 | 2.1 | 4.4 | 7.6
5,001‑6,000 | 1.2 | 2.1 | 4.5 | 7.8
6,001‑7,000 | 1.3 | 2.2 | 4.6 | 7.9
7,001‑8,000 | 1.3 | 2.2 | 4.7 | 8.1
8,001‑9,000 | 1.3 | 2.3 | 4.8 | 8.2
9,001‑10,000 | 1.4 | 2.3 | 4.9 | 8.3
10,001‑11,000 | 1.4 | 2.4 | 5 | 8.5
11,001‑12,000 | 1.4 | 2.5 | 5.1 | 8.6
12,001‑13,000 | 1.5 | 2.5 | 5.2 | 8.8
13,001‑14,000 | 1.6 | 2.6 | 5.3 | 8.9
14,001‑15,000 | 1.6 | 2.7 | 5.4 | 9.1

## Table 9‑4
TABLE 9‑4:
PARTNERSHIPS IN VEGETATION MANAGEMENT 66
Organization Name | Vegetation Management Activities Performed Pursuant to or Under the Partnership | Objective of the activities Performed Pursuant to or Under the Partnership | PG&E’s Role in the Partnership | Anticipated Accomplishments of Partnership Projects During the Three Years of the WMP Cycle
National Arbor Day | Coordinate energy savings tree giveaway within PG&E service territory. | Ensure right trees are planted with energy savings in mind. | Fund and oversee the scheduling of the tree giveaway. | 2025‑2028: successful communication and implementation of the tree giveaway.
CA Community Colleges | Fund scholarships to Community College Tree or PI Certification Courses. Ensure curriculum for both courses are current with Industry leading expectations and changes. | Encourage participation in Community College Certification Course by individuals who wish to consider Utility Arboriculture tree or inspection work as a career. | Scholarships: Fund a scholarship that is administered by the Community Colleges and Utility Arborist Association (UAA). | 2025: Set up PO to Fund Scholarships through 2028.
|  |  | Provide subject matter experts to review course materials and provide guidance as requested. | Between 2025 and 2028: Spend $1.7 million on scholarships. Note: Spend rate depends on attendance of classes and need for scholarships.
WCISA/ISA | Work to ensure Vegetation Management Inspectors (VMI) inspection staff has accessibility to take advanced Arboriculture certifications and recertification and access to Continuing education units. (CEU). | Proactively schedule advanced Certification and recertification courses with WCISA throughout the year for PG&E coworkers. Ensure current Arborists have easy access to CEU though their normal course of business. | Help drive the scheduling of the additional courses which would be offered to PG&E internal and external Coworkers. For CEU, work to proactively obtain CEU course codes in advance of trainings or meetings that qualify for CUE hours. | 2025: Set up four full Tree Risk Assessment Qualification (TRAQ) course set and refresher courses.
Through 2028: Facilitate CEU for benchmarks, roadshows, or meetings as they are scheduled. These actions will continue through 2028.
TABLE 9‑4:
Partnerships in Vegetation Management
(continued)
Organization Name | Vegetation Management Activities Performed Pursuant to or Under the Partnership | Objective of the activities Performed Pursuant to or Under the Partnership | PG&E’s Role in the Partnership | Anticipated Accomplishments of Partnership Projects During the Three Years of the WMP Cycle
CAL FIRE and Fire Safe Councils | Community level engagement through educational presentations, event booths, and tree planting events in partnership with both CAL FIRE & Fire Safe Councils. | Educate PG&E customers, CAL FIRE and Fire Safe Council local offices about safe planting practices near utilities. | Provide the local offices of the CAL FIRE and Fire Safe Council with tools to supply customers with information to make informed decisions when planting near utilities. | Continue to build relationships between central office(s) of the Fire Safe Councils, CAL FIRE, and PG&E’s Right Tree, Right Place Program. Provide planting recommendations for situations when assisting communities with plans for wildfire readiness.
Community Organizations (includes Clear Lake Environmental Research Center and Love Tuolumne County) | Support Lake County’s Hogback Fuel Crew to increase pay and retention of staff that support mutual aid fire response, projects for ingress‑egress improvement, and to protect local hospital and education institutions. | Wildfire capacity building investments in relatively high risk and low‑income regions. | Provide grant funding and tactical support as needed. | Increased and sustained fire and fuel capacity in relatively high risk and low income parts of PG&E service area.
| Support Love Tuolumne County to build and sustain its first roadside fuels crew, reducing risk to and from powerlines and improving ingress‑egress during wildfire events, at lower cost than previous grant‑funded County contract crews. |  |  | Identify learnings to inform whether to expand such partnership to other communities.
Support fuels treatment and linear roadside brushing in targeted high‑value locations. This is not compliance driven work.
National environmental and forestry non‑profits (includes American Forest Foundation, Blue Forest Conservation, and National Forest Foundation) | Support American Forest Foundation (AFF) to create on‑the‑ground risk reduction in Tuolumne County, while also conducting further development of pathways to scale work in Tuolumne and to other counties in PG&E service area on privately‑owned lands. | Create valuable on‑the‑ground risk reduction. | Provide grant funding, project down‑selection collaboration, and matching funds fundraising and/or tactical support as needed. | Landscape‑scale treatments.
| Support Blue Forest Conservation to provide flexible financing for landscape‑scale fuels treatments in Plumas and Eldorado National Forests, in combination with relevant water utilities and government grant funding. | Identify and/or co‑develop scalable pathways to cost‑effective wildfire risk reduction through partnership. |  | Development of multi‑faceted playbook for cost‑effective and large‑scale wildfire risk reduction through resilience partnerships. This is not compliance driven work.
National Forest Foundation has played a key role in resilience efforts with other peer utilities such as Liberty Utilities, Idaho Power, and Salt River Project. PG&E signed a memorandum of understanding with National Forest Foundation for future collaboration.
Local Fire and Forestry Districts and Departments (includes Northern Sonoma County Fire District, Garden Valley Fire District, Hogback Fuel Crew in Lake County) | Via grants to non‑profit partners, support and collaborate with fire and fuel crews to build capacity and achieve on‑the‑ground risk reduction. | Create valuable on‑the‑ground risk reduction. | Provide funding, project down‑selection collaboration, and matching funds fundraising and/or tactical support as needed. | Identify learnings to inform whether to expand such partnership to other communities.
Fuels treatment and linear roadside brushing in targeted high‑value locations. This is not compliance driven work.
Tribal governments and associations (incl. Tribal Ecosystem Restoration Alliance, California Heritage: Indigenous Research Project, and tribal fuel crews such as those for Mooretown and Southern Sierra Mi‑Wuk, Nation Tribes) | Support and collaborate with fire and fuel crews to build capacity and achieve on‑the‑ground risk reduction, such as roadside treatment projects improving ingress and egress on one‑way‑in and one‑way‑out roads while reducing risk to and from PG&E assets. | Wildfire capacity building investments, and on‑the‑ground risk reduction. | Provide grant funding to non‑profit partners and provide tactical support as needed. | Learnings to inform whether and how to expand such partnership to other communities.
Fuels treatment and linear roadside brushing in targeted high‑value locations. This is not compliance driven work.
Fire Safe Councils and Firewise organizations in targeted locations (incl. Butte, Napa, East Madera, and Mariposa) | Create on‑the‑ground wildfire risk reduction through fuels treatment. | Create valuable on‑the‑ground risk reduction. | Funding and tactical support as needed. | Identify learnings to inform whether to expand such partnership to other communities.
|  | Identify and/or co‑develop scalable pathways to cost‑effective wildfire risk reduction through partnership. | In the case of Butte County, match‑funding for a project in East Oroville which strengthened an application for a much larger CAL FIRE grant, which the Fire Safe Council was since awarded, reducing PG&E and community risk with larger‑scale treatment. | Fuels treatment and linear roadside brushing in targeted high‑value locations. This is not compliance driven work.
Resource Conservation Districts (incl. El Dorado and Nevada Counties) | Create on‑the‑ground wildfire risk reduction through fuels treatment. | Create valuable on‑the‑ground risk reduction. | Funding and tactical support as needed. | Learnings to inform whether and how to expand such partnership to other communities.
|  | Identify and/or co‑develop scalable pathways to cost‑effective wildfire risk reduction through partnership. |  | Fuels treatment Sand linear roadside brushing in targeted high‑value locations. This is not compliance driven work.
County (incl. Nevada and Lake Counties) | Provide grants to Counties through EPIC technology demonstration and deployment program to fund pilot community grapple truck and wood disposal programs with the Counties, enabling community wood to be picked up and pooled with operational PG&E wood for large‑scale nearby pyrolization into biochar via mobile carbonizers. | Create a new scalable tactic for reducing the cost, environmental impact, and safety of managing excess wood from vegetation projects through partnership. | Grant funding and large‑wood volumes and carbonizer utilization contract which reduced county wood disposal costs. | Long‑term carbon sequestration, improved wood disposal affordability, and reduced truck miles and associated motor‑vehicle risk, criteria pollutants, carbon emissions, road wear‑and‑tear.
Identify learnings to inform whether to expand such partnership to other communities.
This is not compliance driven work.

## Table 9-5
TABLE 9‑5:
VEGETATION MANAGEMENT QA AND QC PROGRAM OBJECTIVES
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
VM Operations Distribution | VM‑08D | QA | Complete the annual Quality Assurance Audit Plan to calculate and report the pass rate of VM Operations Program locations
VM Operations Transmission | VM‑08T | QA | Complete the annual Quality Assurance Audit Plan to calculate and report the pass rate of VM Operations Program locations.
VM Operations Distribution | VM22D | QC | Complete the annual Quality Control Audit Plan to determine the pass rate of VM Operations Program locations.
VM Operations Pole Clearing (a) | VM‑22P | QC | Complete the annual Quality Control Audit Plan to determine the pass rate of VM Operations Program locations.
VM Operations Transmission | VM‑22T | QC | Complete the annual Quality Control Audit Plan to determine the pass rate of VM Operations Program locations
Footnotes:
(a) We apply a consistent sampling ratio for both risk and compliance poles in our QC methodology. See 2026-2028 WMP Revision Notice Response R0, Critical Issue RN-PGE-26-10 for additional information.

## Table 9-6
TABLE 9‑6:
VEGETATION MANAGEMENT QA AND QC ACTIVITY
Initiative/ Activity Being Audited | Population /Sample Unit | 2026: Population Size (d) | 2026: Sample Size | 2026: % of Sample in HFTD/HFRA | 2027: Population Size (d) | 2027: Sample Size | 2027: % of Sample in HFTD/HFRA | 2028: Population Size (d) | 2028: Sample Size | 2028: % of Sample in HFTD/HFRA | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Vegetation Management Quality Assurance - Distribution Routine (VM-08D) | Miles (a) | 25,748(e) | 500 | 100% | 25,748(e) | 500 | 100% | 25,748(e) | 500 | 100% | 95/3.25% | 97% | 97% | 97%
Vegetation Management Quality Assurance - Transmission Routine (VM-08T) | Miles (a) | 5,624(e) | 200 | 100% | 5,624(e) | 200 | 100% | 5,624(e) | 200 | 100% | 95/3.25% | 97% | 97% | 97%
Vegetation Management Quality Control - Distribution Routine (VM-22D) | Spans (b) | 551,643(e) | 80,000 | 100% | 551,643(e) | 80,000 | 100% | 551,643(e) | 80,000 | 100% | 99/5% | 95% | 95% | 95%
Vegetation Management Quality Control - Pole Clearing (VM-22P) (c) | Poles (b) | 70,000 | 11,500 | 100% | 70,000 | 11,500 | 100% | 70,000 | 11,500 | 100% | 99/5% | 95% | 95% | 95%
Vegetation Management Quality Control - Transmission Routine (VM-22T) | Spans (b) | 50669 | 13,500 | 100% | 50669 | 13,500 | 100% | 50669 | 13,500 | 100% | 99/5% | 95% | 95% | 95%
Note:
(a) Overhead circuit miles in HFTD/HFRA
(b) VMQC Distribution/Transmission/Pole Population is comprised of the overhead span inspected or subject pole locations that have been cleared by VM Operations in HFTD/HFRA.
(c) The VC Pole Clearing Procedure considers both risk and compliance poles as subject; both subsets are incorporated into the sample population. Please Critical Issue RN-PGE-26-10 in 2026-2028 WMP Revision Notice Response R0 for additional information.
(d) Population Size subject to change for 2026-2028 due to construction activities and revisions to fire district/risk area boundaries.
(e) Updated based on Substantive Errata filed on April 18, 2025 in accordance with Energy Safety's issuance of Revision Notice at 21.
ORIGINAL -- DO NOT EDIT BELOW THIS LINE
TABLE 9‑6:
VEGETATION MANAGEMENT QA AND QC ACTIVITY
Initiative/ Activity Being Audited | Population /Sample Unit | 2026: Population Size | 2026: Sample Size | 2026: % of Sample in HFTD | 2027: Population Size | 2027: Sample Size | 2027: % of Sample in HFTD | 2028: Population Size | 2028: Sample Size | 2028: % of Sample in HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Vegetation Management Quality Assurance - Distribution Routine (VM-08D) | Inspections | 25,000 miles | 500 miles | 100% | 25,000 miles | 500 miles | 100% | 25,000 miles | 500 miles | 100% | 95/3.25% | 97% | 97% | 97%
Vegetation Management Quality Assurance - Transmission Routine (VM-08T) | Inspections | 5,380 miles | 200 miles | 100% | 5,380 miles | 200 miles | 100% | 5,380 miles | 200 miles | 100% | 95/3.25% | 97% | 97% | 97%
Vegetation Management Quality Control - Distribution Routine (VM-22D) | Inspections | 540,000 spans | 80,000 spans | 100% | 540,000 spans | 80,000 spans | 100% | 540,000 spans | 80,000 spans | 100% | 99/5% | 95% | 95% | 95%
Vegetation Management Quality Control - Pole Clearing (VM-22P) | Poles | 51,000 poles | 11,500 poles | 100% | 51,000 poles | 11,500 poles | 100% | 51,000 poles | 11,500 poles | 100% | 99/5% | 95% | 95% | 95%
Vegetation Management Quality Control - Transmission Routine (VM-22T) | Inspections | 5,380 miles | 13,500 spans | 100% | 5,380 miles | 13,500 spans | 100% | 5,380 miles | 13,500 spans | 100% | 99/5% | 95% | 95% | 95%
Population Size subject to change for 2026 -2028 due to construction activities

## Table-9‑7
TABLE 9‑7:
NUMBER OF PAST DUE VEGETATION MANAGEMENT WORK ORDERS
CATEGORIZED BY AGE AND HFTD TIER 69
HTFD Area | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
Non‑HFTD | 3 | – | – | –
HFTD Tier 2 | – | – | – | –
HFTD Tier 3 | – | – | – | –
_______________
Notes:
· Totals are based on number of days past due according to PG&E standards and procedures as of 12/31/2024.
· Constrained units are excluded.
· The work is complete for the three trees listed above.

## Table-9‑8
TABLE 9‑8:
NUMBER OF PAST DUE VEGETATION MANAGEMENT WORK ORDERS
CATEGORIZED BY AGE AND PRIORITY LEVELS 70
Priority Level | 0‑30 Days | 31‑90 Days | 91‑180 Days | 181+ Days
Priority 1 | – | – | – | –
Priority 2 | 3 | – | – | –
Priority 3 | – | – | – | –
_______________
Notes:
· Totals are based on number of days past due according to PG&E standards and procedures as of 12/31/2024.
· Constrained units are excluded.
· Priority 1 and Priority 2 categories include trees identified as P1 or P2 based on the Priority Tag Procedure and HN‑I or HN‑U based on the Transmission VM Imminent Threat and Hazard Notification Procedure.
· Priority 3 includes Distribution routine, non‑priority trees. The 365‑day standard timeline applies to Distribution routine, non‑priority work, as per procedure TD‑7102S.
· The work is complete for the three trees listed above.

## Table-9-9
TABLE 9‑9:
VEGETATION MANAGEMENT QUALIFICATIONS AND TRAINING(a) 71
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | # of Electrical Corporation Employees with Min Quals | # of Electrical Corporation Employees with Special Certifications | # of Contracted Employees with Min Quals | # of Contractor Employees with Applicable Certifications | Total # of Employees | Reference to Electrical Corporation Training/ Qualification Programs
VMI and Senior Vegetation Management Inspectors (SVMI) | For VMI: | • Certified Arborist | 300 | • Certified Arborist – 130 | 1007 | • Certified Arborist – 409 | 1291 | VMI Basics
| High School diploma or General Educational Development Test (GED), AND | • Registered Professional Forester |  | • Registered Professional Forester – 1 *Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. |  | • Registered Professional Forester – 2 *Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes.
Required to maintain a Class C driver’s license AND must meet one of the experience levels below:
Experience/education requirements (must meet one):
1year of related arboricultural experience, OR
ISA Certified Arborist, OR
2‑year or 4‑year college degree in a related field, AND
Approval by PG&E Representative
For SVMI:
High School diploma or GED, AND
Required to maintain a Class C driver’s license AND must meet one of the experience levels below:
5 years of experience as a tree crew climber/tree crew foreman with at least 2 years of line clearance certification, OR
5 years of experience as a Vegetation Management Inspector and Certified Arborist, OR
5 years of experience as a Registered Professional Forester, OR
5 years of experience as a Utility Inspector or higher classification with at least 1 year of vegetation management experience, OR
4 years of Military Service with honorable discharge and at least 1 year additional year of vegetation management inspection experience, AND
Approval by PG&E Representative.
Field Supervisor (FS) | Minimum of five (5) years’ experience in line clearance tree work and have been a qualified line clearance tree worker. -Equivalent experience may be acceptable at the discretion of the Vegetation Program Manager. The FS shall be familiar with the Contractor's work practices, PG&E's Specification, and all applicable legal and regulatory requirements relating to the Work required. | N/A | 0 | 0 | 195 | N/A | 195 | N/A – Tree Work Training is not provided by PG&E.
Foreman (FM) | A minimum of eighteen (18) months experience in line clearance tree work and is a qualified line clearance tree worker. Capable of climbing and possess a valid certification document issued by Contractor. Equivalent experience may be acceptable at the discretion of the Vegetation Program Manager. The FM shall be familiar with the Contractor's work practices, PG&E’s Specification, and all applicable legal and regulatory requirements relating to line clearance work and fire prevention related to the Work and use this knowledge to direct his/her crew(s). | N/A | 0 | 0 | 1353 | N/A | 1353 | N/A – Tree Work Training is not provided by PG&E.
Patrolman (PT) | A PT shall, by reason of his or her training and/or experience, and demonstrated through his or her performance, be familiar with the requirements of line clearance tree pruning and possess good customer contact skills. | N/A | 0 | 0 | 0 | N/A | 0 | N/A – Tree Work Training is not provided by PG&E.
Journeyman Tree Trimmer/Climber (CL) | A minimum of eighteen (18) months experience in line clearance tree work. Possess a valid certification document issued by Contractor. Met the state approved training requirements to work within ten (10) feet of energized conductors. Shall be familiar with the Contractor's work practices and requirements related to line clearance work. | N/A | 0 | 0 | 613 | N/A | 613 | N/A – Tree Work Training is not provided by PG&E.
Apprentice Trimmer/Climber (AC) | A minimum of three (3) months experience as a groundman. An AC shall be defined as a tree worker undergoing on- the-job training and shall have demonstrated the ability to perform his or her duties safely and in accordance with applicable state and federal regulations. | N/A | 0 | 0 | 818 | N/A | 818 | N/A – Tree Work Training is not provided by PG&E.
Groundman/Flagman (GM) | A GM shall be defined as a crew member other than a PT, CL or AC working under the direct supervision of the FM. | N/A | 0 | 0 | 525 | N/A | 525 | N/A – Tree Work Training is not provided by PG&E.
Vegetation Control Technician (VC Tech) | Vegetation control experience or other related work, including relevant pesticide and related licenses and certificates. Preferred - ISA Certified Arborist, ISA Certified Tree Worker, and/or TCIA Certified Tree Care Safety Professional. | N/A | 0 | 0 | 393 | N/A | 393 | VEGM-0302 and VEGM-0303
Brush Crew Foreman | Eighteen (18) months related experience. Electrical groundman or lineman experience preferred or any equivalent combination of experience and certified training that provides the required knowledge, skills, and abilities. High school graduate, or its equivalent required. | N/A | 0 | 0 | 53 | N/A | 53 | N/A – Tree Work Training is not provided by PG&E.
Specialized Tree Equipment Operator | Shall be capable of operating two-handed equipment (chain saw, circular saw, and have the physical ability to endure extreme climate variances. Willing and able to obtain specialized training and certifications as required, such as tree species identification. Must be able to perform physical labor such as lifting a minimum of 50 lbs. to shoulder height or more. | N/A | 0 | 0 | 145 | N/A | 145 | N/A – Tree Work Training is not provided by PG&E.
(VMQC) Quality Management Auditor (PG&E Internal) *The title for contractors are in the process to change | Bachelor’s degree in job‑related discipline or equivalent experience. | ISA Arborist. | 60 | 50 = ISA Arborist; 24 = ISA Utility Specialist; 49 = ISA TRAQ; * Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 82 | 66 = ISA Arborist; 17 = ISA Utility Specialist; 60 = ISA TRAQ; * Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 142 | Employees are profiled for training courses based on their roles.
| 3+ years of job‑related experience. | ISA Utility Specialist certification.
| Valid CA Class C Driver’s License or equivalent. | ISA TRAQ.
CPR/First Aid.
OSHA 30.
(VMQC) Quality Management Auditor, Senior (PG&E Internal) | Bachelor’s degree in job‑related discipline or equivalent experience. | ISA Utility Specialist certification. | 26 | 22 = ISA Arborist; 10 = ISA Utility Specialist; 19 = ISA TRAQ; * Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 0 | N/A | 26 | Employees are profiled for training courses based on their roles.
| 5+ years of job‑related experience. | ISA TRAQ.
| ISA Arborist certification or ability to obtain it within 12 months. | CPR/First Aid.
| Valid CA Class C Driver’s License or equivalent. | OSHA 30.
(VMQA) Program Manager (PG&E Internal) *The title for contractors are in the process to change | Bachelor’s degree or equivalent experience. | ISA Arborist. | 8 | 8 = ISA Arborist; 6 = ISA Utility Specialist; 8 = ISA TRAQ; 4 = ASQ;* Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 0 | N/A | 8 | Employees are profiled for training courses based on their roles.
| Job‑related experience, 3 years minimum. | ISA Utility Specialist certification.
ISA TRAQ.
(VMQA) Program Manager, Senior (PG&E Internal) | Bachelor’s degree in job‑related discipline or equivalent experience. | ISA Utility Specialist certification. | 2 | 2 = ISA Utility Specialist; 2 = ISA TRAQ;* Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 0 | N/A | 2 | Employees are profiled for training courses based on their roles.
| 5+ years of job‑related experience. | ASQ Certified Quality Auditor (CQA) certification.
| ISA Arborist certification or ability to obtain it within 12 months. | ISA TRAQ.
| Valid CA Class C Driver’s License or equivalent. | CPR/First Aid.
(VMQA) Compliance & Risk Consultant (PG&E Internal) *The title for contractors are in the process to change | Bachelor’s degree in job‑related discipline or equivalent experience. | ISA Utility Specialist certification. | 3 | 2 = ISA Arborist; 2 = ISA TRAQ; * Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 4 | 4 = ISA Arborist; 1 = ISA Utility Specialist; 2 = ISA TRAQ; * Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 7 | Employees are profiled for training courses based on their roles.
| 3+ years of job‑related experience. | ASQ CQA certification.
| ISA Arborist certification or ability to obtain it within 12 months. | ISA TRAQ.
| Valid CA Class C Driver’s License or equivalent. | CPR/First Aid.
(VMQA) Compliance & Risk Consultant, Senior (PG&E Internal) | Bachelor’s degree in job‑related discipline or equivalent experience. | ISA Utility Specialist certification. | 5 | 5 = ISA Utility Specialist; 3 = ISA TRAQ; * Note that due to the nature of the Credentials (Obtaining, expirations, renewals), the number is subject to changes. | 0 | N/A | 5 | Employees are profiled for training courses based on their roles.
| 5+ years of job‑related experience. | ASQ CQA certification.
| ISA Arborist certification | ISA TRAQ.
| Valid CA Class C Driver’s License or equivalent. | CPR/First Aid.
_______________
Note: Please note employee and contractor employee totals, as well as certifications may fluctuate.
(a) Updated in accordance with Energy Safety's issuance of Revision Notice at 21.

## Table PG&E‑9‑9
TABLE PG&E‑9‑9:
PG&E VMI BASIC WEB‑BASED COURSES 72
Course Number | Course Name | Description
VEGM0155WBT | Introduction To Vegetation Management | Safety Culture, Gov Regulations and Expectations.
VEGM0161WBT | Vegetation Management Patrol Safety | Procedure Access, Safety, How to prepare for the Work Day.
VEGM0165WBT | Overview Of PG&E Facilities | Introduction To Electrical Facilities
VEGM0170WBT | Evaluating Trees | Tree Growth, Tree Species Characteristics and Resources.
VEGM0175WBT | Identifying Tree Defects | Common Indicators of Tree Defects
VEGM0180WBT | VM Inspection Fundamentals | How To Inspect Vegetation Growing Near Facilities
VEGM0185WBT | Prescribing Tree Work | Priority Codes, Unified Work Codes, Proper Markings and Communication.
VEGM0190WBT | Abnormal Field Conditions | Abnormal Field Conditions: How To identify And Report Them
VEGM0195WBT | Major Woody Stems | How to Assess and Document Major Woody Stem
VEGM0198WBT | Positive Customer Relations | How To Demonstrate Positive Customer Relation Skills. Both on The Phone and in The Field.

## Table 10-1
TABLE 10‑1:
SITUATIONAL AWARENESS TARGETS BY YEAR
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID, if applicable | Target Unit | 2026 End of Year Total / Completion Date | % Risk Reduction for 2026 | 2027 Total / Status | % Risk Reduction for 2027* | 2028 Total / Status | % Risk Reduction for 2028* | Three- Year Total | Section; Page number
Situational Awareness and Forecasting | Quantitative | Line Sensor - Installations (SA-02) | SA-02 | Sensor Locations | 240 | 6.42% (Eyes on Risk) | 240 | 6.42% (Eyes on Risk) | 240 | 6.42% (Eyes on Risk) | 720 | 10.3.1; p. 448
Situational Awareness and Forecasting | Qualitative | Evaluate camera AI system performance and new functionalities (SA-08) | SA-08 | n/a | Completed; December 31, 2026 | n/a | n/a | n/a | n/a | n/a | n/a | 10.4.1; p. 456
Situational Awareness and Forecasting | Quantitative | Distribution Fault Anticipation (DFA) Installations (SA-10) | SA-10 | Sensor Locations | 15 | 9.92% (Eyes on Risk) | 15 | 9.92% (Eyes on Risk) | 15 | 9.92% (Eyes on Risk) | 45 | 10.3.1; p. 448
Situational Awareness and Forecasting | Quantitative | Early Fault Detection (EFD) Installations (SA-11) | SA-11 | Sensor Locations | 180 | 2.52% (Eyes on Risk) | 180 | 2.52% (Eyes on Risk) | 180 | 2.52% (Eyes on Risk) | 540 | 10.3.1; p. 448
Situational Awareness and Forecasting | Quantitative | Live Fuel Moisture Data Collection (SA-12) | n/a | Sample Locations | 25 | n/a | 25 | n/a | 25 | n/a | 75 | 10.2.1; p. 438 10.2.4; p. 447
Situational Awareness and Forecasting | Qualitative | Weather Station Network Evaluation (SA-13) | n/a | n/a | Completed; December 31, 2026 | n/a | Completed; December 31, 2027 | n/a | Completed; December 31, 2028 | n/a | n/a | 10.2.1; p. 438 10.2.4; p. 447
Situational Awareness and Forecasting | Qualitative | SmartMeters next generation capability evaluation (SA-14) | n/a | n/a | Started; March 2026 | n/a | In Progress; 2027 | n/a | Completed; December 31, 2028 | n/a | n/a | 10.3.3; p. 453
Situational Awareness and Forecasting | Quantitative | Weekly uptime of Wildfire Cameras (SA-15) | n/a | Average weekly uptime percentage | 90% | n/a | 90% | n/a | 90% | n/a | n/a | 10.4.1; p. 456
Situational Awareness and Forecasting | Quantitative | Weather Model Verification Tool (SA-16) | n/a | Weather Model Verifcation Tool | 1 | n/a | n/a | n/a | n/a | n/a | 1 | 10.5.3; p. 469
Situational Awareness and Forecasting | Qualitative | Weather Model Enhancements leveraging AI-ML (SA-17) | n/a | n/a | Started; March 2026 | n/a | In Progress; 2027 | n/a | Completed; December 31, 2028 | n/a | n/a | 10.5.3; p. 469
Situational Awareness and Forecasting | Quantitative | Weather Station Network Health (SA-18) | n/a | Percent of Weather Stations | 95% | n/a | 95% | n/a | 95% | n/a | n/a | 10.5.5; p. 470
Situational Awareness and Forecasting | Qualitative | Weather Station Network Optimization (SA-19) | n/a | n/a | Completed; December 31, 2026 | n/a | Completed; December 31, 2027 | n/a | Completed; December 31, 2028 | n/a | n/a | 10.5.5; p. 470
Note: Estimates for the 2027 & 2028 risk reduction are not available at the time of WMP submission. As such, 2026 risk reduction values will be used as a proxy.

## Table 10‑2
TABLE 10‑2:
ENVIRONMENTAL MONITORING SYSTEMS 74
System | Measurement/ | Frequency | Purpose and Integration
Observation
Weather stations | · Sustained wind speed | The standard frequency is six observations per hour. However, up to 120 observations per hour can be enabled on most stations. | · Improving situational awareness
| · Wind gust speed |  | · Assisting with Public Safety Power Shutoff (PSPS) event execution
| · Air temperature |  | · Improving weather forecasts through data assimilation by the Meteorological Assimilation Data Ingest System (MADIS)
| · Relative humidity |  | · Validating the performance of the weather models
Fuel moisture sampling and modeling | The percentage of moisture in collected samples of specific plant species from 30 select HFTD locations across the service territory. | Once a month | · Validating the fuel moisture models
· Improving situational awareness
· Building robust historical fuel moisture datasets

## Table 10‑3
TABLE 10‑3:
GRID OPERATION MONITORING SYSTEMS 75
System | Measurement/ Observation | Frequency | Purpose and Integration
Line sensors | Current/fault current | 15 minutes/triggered by fault magnitude threshold. | The detection and assistance in locating faults. In process of being integrated into analytics platform.
DFA | Current/voltage power flow anomalies | 256 samples per cycle continuous. Event capture triggered by condition‑based thresholds. | The detection and assistance in locating faults, abnormal power flow events, categorization of events. In process of being integrated into analytics platform.
EFD | Using sensors that monitor the Radio Frequency (RF) spectrum, the system detects the generation of Partial Discharge (PD) which is an indicator of equipment electrical degradation or arcing. Using measured accumulation of PD, the system can identify the location of these issues. | 1:25 duty cycle (Gen 3), continuous (Gen 4). Events matched based on timing and location on monitored circuit segments. | To detect failing equipment early and to detect vegetation encroachment. Plan to integrate into analytics platform.
Reclosers | Current/voltage/ | Continuously | This data is used to provide real‑time fault information as well as to assist in diagnosing system problems during and after events occur.
power/fault data

## Table 10‑4
TABLE 10‑4:
FIRE DETECTION SYSTEMS CURRENTLY DEPLOYED 76
Detection System | Capabilities | Companion Technologies | Contribution to Fire Detection and Confirmation
PG&E FDAS | Satellite detection and alerts from six satellites. Update cadence is every five minutes. | None | Provides valuable information to the utility and the public regarding the presence of new fires and the spread of existing fires in a timely fashion.
Wildfire Cameras w/AI detections | Over 600 cameras sponsored covering over 90 percent of the HFTD Tier 2 and 3 areas. | None | Video cameras allow fast and accurate detection or confirmation of wildfires, which can help operators assess the scope of resource response needed. Cameras have been equipped with AI smoke detection.

## Table PG&E‑10.5‑1
TABLE PG&E‑10.5‑1
PG&E OPERATIONAL MESOSCALE MODELING SYSTEM DEVELOPMENT 77
POMMS Version | Year Implemented | WRF Version | Key Features
1 | 2014 | 3.5.1 | Single 3 kilometer (km) grid using boundary conditions from a 12 km WRF run.
2 | 2018 | 4.0.2 | Nested 3 km grid, Mellor‑Yamada‑Nakanishi‑Niino (MYNN) surface layer scheme, Rapid Update Cycle (RUC) land surface model, 30‑year reanalysis.
3 | 2020 | 4.1.2 | Nested 2 km grid, Noah‑MP land surface model, stochastically perturbed ensemble, 30‑year reanalysis. See text and Table 2 for details.
4 | 2024 | 4.5.2 | Nested 2 km grid, irrigation triggered by crop‑growing season, Global Ensemble Forecasting System (GEFS)‑based ensemble, 30‑year reanalysis.

## Table PG&E‑10.5.1‑1
TABLE PG&E‑10.5.1‑1:
WEATHER VARIABLES
Variable | Description
Q2 | Water vapor mixing ratio
T2 | Temperature at 2 m
PSFC | Surface pressure
U10 | 10 m u wind component
V10 | 10 m v wind component
TSLB | Soil temperature
SMOIS | Soil moisture
ACSNOM | Accumulated melted snow
SNOWH | Physical snow depth
SWDOWN | Shortwave incoming radiation
ZNT | Time‑varying roughness length
UST | Friction velocity
PREC_ACC_C | Accumulated Cumulus precipitation
PREC_ACC_NC | Accumulated Grid scale (non‑convective) precipitation
SNOW_ACC_NC | Accumulated snow water equivalent

## Table 10-5
TABLE 10‑5:
FIRE POTENTIAL FEATURES
Feature Group/ Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
(Predictor)
TerrainRugged_Mean | surface | Measure of terrain ruggedness in each h3 hexagon | DEM | N/A | 10m | N/A
Slope_Degree_Mean | surface | Measure of slope in each h3 hexagon | DEM | N/A | 10m | N/A
Fuels: Grass | 300 m | Proportion of fuel category in h3 hexagon cell attributed to grass | Technosylva | Annual | 30m | N/A
Fuels: Grass Shrub | surface | Proportion of fuel category in h3 hexagon cell attributed to grass shrub | Technosylva | Annual | 30m | N/A
Fuels: Shrub | surface | Proportion of fuel category in h3 hexagon cell attributed to shrub | Technosylva | Annual | 30m | N/A
Fuels: Timber Litter | surface | Proportion of fuel category in h3 hexagon cell attributed to timber litter | Technosylva | Annual | 30m | N/A
Fuels: Timber Understory | surface | Proportion of fuel category in h3 hexagon cell attributed to timber understory | Technosylva | Annual | 30m | N/A
Fuels: Urban Roads Agg Low Burnable | surface | Proportion of fuel category in h3 hexagon cell attributed to dense urban, roads, or agriculture land | Technosylva | Annual | 30m | N/A
Fuels: Urban Roads Agg High Burnable | surface | Proportion of fuel category in h3 hexagon cell attributed to urban, roads, or agriculture land adjacent or surrounded by burnable fuels | Technosylva | Annual | 30m | N/A
fuel_bed_depth_ft | surface | The fuel bed depth from fuel model classes | Technosylva | Annual | 30m | N/A
ave_fuel_complexity | surface | The average fuel complexity derived from fuel model data | Technosylva | Annual | 30m | N/A
dfm_1000hr | surface | The moisture content in the 1,000 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
dfm_100hr | surface | The moisture content in the 100 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
dfm_10hr | surface | The moisture content in the 10 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
table 10‑5:
Fire Potential IndEX MODEL FEATURES
(CONTINUED)
Feature Group/ Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
(Predictor)
dfm_1hr | surface | The moisture content in the 1 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
lfm_chamise_new | surface | The moisture content in the LFM chamise new growth class | POMMS & Technosylva | daily | 2km | daily
ndvi | surface | The Normalized Vegetation Index per h3 hexagon | POMMS & Technosylva | Daily | 2km | daily
smois_0 | 5 cm | Moisture content in the soil at a depth of 5 cm | POMMS | 2x per day | 2km | hourly
vpd_mb_300m | 300m | Vapor pressure deficit at 300m | POMMS | 2x per day | 2km | hourly
vpd_mb_50m | 50m | Vapor pressure deficit at 50m | POMMS | 2x per day | 2km | hourly
vpd2m_mb | 2m | Vapor pressure deficit at 2m | POMMS | 2x per day | 2km | hourly
sfcdownshortwaveflux | surface | Shortwave flux at the surface – solar radiation | POMMS | 2x per day | 2km | hourly
temp_f_300m | 300m | Temperature at 300m above surface in Fahrenheit | POMMS | 2x per day | 2km | hourly
temp_f_50m | 50m | Temperature at 50m above surface in Fahrenheit | POMMS | 2x per day | 2km | hourly
temp2m_f | 2m | Temperature at 2m above surface in Fahrenheit | POMMS | 2x per day | 2km | hourly
tke_pbl_300m | 300m | Kinetic energy per unit mass observed in eddies characteristic of turbulent flow in Joules/kg at 300m | POMMS | 2x per day | 2km | hourly
tke_pbl_50m | 50m | Kinetic energy per unit mass observed in eddies characteristic of turbulent flow in Joules/kg at 50m | POMMS | 2x per day | 2km | hourly
ustar_frc_vel | 2m | Wind shear stress in velocity terms. | POMMS | 2x per day | 2km | hourly
ws_mph_300m | 300m | Wind speed at 300m above surface | POMMS | 2x per day | 2km | hourly
ws_mph_50m | 50m | Wind speed at 50m above surface | POMMS | 2x per day | 2km | hourly
ws_mph | 10m | Wind speed at 10m above surface | POMMS | 2x per day | 2km | hourly

## Table PG&E‑10.6.1‑1
TABLE PG&E‑10.6.1‑1:
FPI CLASS BREAKPOINTS 80
FPI Class | VIIRS Growth (Acres), Fire Radiative Power (Megawatts (MW)) | VIIRS Growth, Fire Radiative Power (MW)
| (<3 Hours Between VIIRS Detects) | (>=3 Hours Between VIIRS Detects)
Small | <70 acres | <70 acres
Large | <200 acres OR <200 MW | <200 acres OR <200 MW
Critical | <2,000 acres OR <2,000 MW | <7,000 acres OR <7,000 MW
Catastrophic | >=2,000 acres & >=2,000 MW | >=7,000 acres & >=7,000 MW

## Table PG&E‑10.6.1‑2
TABLE PG&E‑10.6.1‑2:
FIRE CONSEQUENCE DISTRIBUTION BY CLASS BREAKPOINTS 81
| % of Total Buildings Damaged |  |  |  | Buildings Damaged per 10,000 Acres
FPI Class Actual | Small | Large | Critical | Catastrophic | Small | Moderate | Critical | Catastrophic
Initial Detect | 0% | 0.8% | 4.6% | 30.8% | 2 | 6 | 78 | 683
Initial Burning Period | 0% | 1.2% | 3.7% | 31.1% | – | 19 | 36 | 392
(0+ to 24+ hours)
Second Burning Period (24+ to 72+ hours) | 0% | 0% | 3.4% | 8% | – | 1 | 26 | 69
Third Burning Period | 0% | 0.2% | 4.4% | 2.6% | – | 3 | 19 | 29
(3+ to 7+ days)
Extended Burning Period | 0% | 0% | 1% | 8.2% | – | – | 2 | 34
(More than 7+ days)

## Table PG&E‑10.6.1‑3
TABLE PG&E‑10.6.1‑3:
FPI MODEL SKILL SCORE COMPARISON 82
Fire Class | FPI 4.0 Model Receiver‑Operating Characteristic Curve (ROC) Area Under the Curve (AUC) | FPI 5.0 Model ROC AUC
Catastrophic | 0.88 | 0.95
Critical | Class Not Used | 0.88
Large | 0.55 | 0.62
Small | 0.68 | 0.73
Macro‑Average ROC AUC | 0.7 | 0.83

## Table PG&E‑10.6.1‑4
TABLE PG&E‑10.6.1‑4 :
FIRE POTENTIAL INDEX MODEL FEATURES 83
Feature Group/ Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
(Predictor)
TerrainRugged_Mean | surface | Measure of terrain ruggedness in each h3 hexagon | DEM | N/A | 10m | N/A
Slope_Degree_Mean | surface | Measure of slope in each h3 hexagon | DEM | N/A | 10m | N/A
Fuels: Grass | 300 m | Proportion of fuel category in h3 hexagon cell attributed to grass | Technosylva | Annual | 30m | N/A
Fuels: Grass Shrub | surface | Proportion of fuel category in h3 hexagon cell attributed to grass shrub | Technosylva | Annual | 30m | N/A
Fuels: Shrub | surface | Proportion of fuel category in h3 hexagon cell attributed to shrub | Technosylva | Annual | 30m | N/A
Fuels: Timber Litter | surface | Proportion of fuel category in h3 hexagon cell attributed to timber litter | Technosylva | Annual | 30m | N/A
Fuels: Timber Understory | surface | Proportion of fuel category in h3 hexagon cell attributed to timber understory | Technosylva | Annual | 30m | N/A
Fuels: Urban Roads Agg Low Burnable | surface | Proportion of fuel category in h3 hexagon cell attributed to dense urban, roads, or agriculture land | Technosylva | Annual | 30m | N/A
Fuels: Urban Roads Agg High Burnable | surface | Proportion of fuel category in h3 hexagon cell attributed to urban, roads, or agriculture land adjacent or surrounded by burnable fuels | Technosylva | Annual | 30m | N/A
fuel_bed_depth_ft | surface | The fuel bed depth from fuel model classes | Technosylva | Annual | 30m | N/A
ave_fuel_complexity | surface | The average fuel complexity derived from fuel model data | Technosylva | Annual | 30m | N/A
dfm_1000hr | surface | The moisture content in the 1,000 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
dfm_100hr | surface | The moisture content in the 100 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
dfm_10hr | surface | The moisture content in the 10 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
table‑10‑5:
Fire Potential IndEX MODEL FEATURES
(CONTINUED)
Feature Group/ Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
(Predictor)
dfm_1hr | surface | The moisture content in the 1 hr. dead fuel model class | POMMS & Technosylva | 2x per day | 2km | hourly
lfm_chamise_new | surface | The moisture content in the LFM chamise new growth class | POMMS & Technosylva | daily | 2km | daily
ndvi | surface | The Normalized Vegetation Index per h3 hexagon | POMMS & Technosylva | Daily | 2km | daily
smois_0 | 5 cm | Moisture content in the soil at a depth of 5 cm | POMMS | 2x per day | 2km | hourly
vpd_mb_300m | 300m | Vapor pressure deficit at 300m | POMMS | 2x per day | 2km | hourly
vpd_mb_50m | 50m | Vapor pressure deficit at 50m | POMMS | 2x per day | 2km | hourly
vpd2m_mb | 2m | Vapor pressure deficit at 2m | POMMS | 2x per day | 2km | hourly
sfcdownshortwaveflux | surface | Shortwave flux at the surface – solar radiation | POMMS | 2x per day | 2km | hourly
temp_f_300m | 300m | Temperature at 300m above surface in Fahrenheit | POMMS | 2x per day | 2km | hourly
temp_f_50m | 50m | Temperature at 50m above surface in Fahrenheit | POMMS | 2x per day | 2km | hourly
temp2m_f | 2m | Temperature at 2m above surface in Fahrenheit | POMMS | 2x per day | 2km | hourly
tke_pbl_300m | 300m | Kinetic energy per unit mass observed in eddies characteristic of turbulent flow in Joules/kg at 300m | POMMS | 2x per day | 2km | hourly
tke_pbl_50m | 50m | Kinetic energy per unit mass observed in eddies characteristic of turbulent flow in Joules/kg at 50m | POMMS | 2x per day | 2km | hourly
ustar_frc_vel | 2m | Wind shear stress in velocity terms. | POMMS | 2x per day | 2km | hourly
ws_mph_300m | 300m | Wind speed at 300m above surface | POMMS | 2x per day | 2km | hourly
ws_mph_50m | 50m | Wind speed at 50m above surface | POMMS | 2x per day | 2km | hourly
ws_mph | 10m | Wind speed at 10m above surface | POMMS | 2x per day | 2km | hourly

## Table 11-1
TABLE 11‑1:
EMERGENCY PREPAREDNESS AND COMMUNITY OUTREACH TARGETS BY YEAR 12
Initiative | Activity (Tracking ID #) | Previous Tracking ID, if applicable | 2026 End of Year Total / Completion Date | 2027 Status | 2028 Status | Section; Page number
Public Communication, Outreach, and Education Awareness | Community Engagement - Outreach to HFRA Infrastructure Customers (CO-04) | CO-04 | Completed; September 30, 2026 | Completed; September 30, 2027 | Completed; September 30, 2028 | 11.4; p. 514
Public Communication, Outreach, and Education Awareness | Community Engagement - Outage Preparedness Campaign (CO-05) | CO-05 | Completed; September 30, 2026 | Completed; September 30, 2027 | Completed; September 30, 2028 | 11.4; p. 514
Emergency Preparedness and Recovery Plan | Common Operating Picture Technology (EP-07) | EP-07 | Started; March 2026 | In Progress; 2027 | Completed; December 31, 2028 | 11.2; p. 487
External Collaboration and Coordination | Continue sharing PSPS lessons learned (PS-10) | PS-10 | Completed; December 31, 2026 | Completed; December 31, 2027 | Completed; December 31, 2028 | 11.3; p. 503
Customer Support in Wildfire and PSPS Emergencies | Access and Functional Needs (AFN) Customer Support During PSPS Emergencies (PS-12) | n/a | Started; April 2026 | In Progress; 2027 | Completed; December 31, 2028 | 11.5; p. 538

## Table‑11‑2
TABLE 11‑2:
KEY GAPS AND LIMITATIONS IN INTEGRATING WILDFIRE‑ AND PSPS‑SPECIFIC STRATEGIES INTO EMERGENCY PLAN 85
| Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Wildfire | After Action Review Trend Analysis | Use of an after‑action trend analysis capability across emergency centers, years and incident and event types will enable PG&E to identify repetitive problems impacting response operations. | Strategy: Beginning January 1, 2025, PG&E implemented a critique tool to input after action review hotwash items. This tool will enable trending across emergency centers, years and incident and event types.
Target Timeline:
Initiated: January 1, 2025
Updated: After EOC activations
Reviewed: Annually to identify trends.
PSPS | Errors in Automated Messaging deployment | During a PSPS event, at time of de‑energization, the process of deploying notifications to customers about current state of service to their location switches from a manual process with human actions to prep, stage and deploy notifications, to an automated system that is utilized for all outage communications. In certain cases, logic used for normal outage communications interfere with the automation of these messages, causing incorrect notifications, or no notification at all | Strategy: Work with Outage Management Tool (OMT) SME’s and program administrators to identify edge cases, like abnormal circuit configurations, mis‑mapped customers, and tools put in place to avoid duplicate messages to customers during blue sky outage communications.
Target Timeline: Communications around conflicts/issues with OMT Program team began when issue was known. Remedial actions put in place to correct (if possible) at that time. Mis mapped customers reviewed by Operations to correct data for proper transformer assignment at conclusion of each event.
PSPS | Notification Vendor performance | During several events, the vendor used for deploying PSPS notifications mishandled or disregarded files that needed to be processed/delivered, resulting in missed notifications to customers | Strategy: Ongoing dialog with Message Broadcast to identify root causes of missed notifications. Meeting on 12/6/24 with Message Broadcast leadership in San Ramon to discuss notification failures and re‑commitment from them to drive errors and miscommunication out of process. Payload testing and drills identified for Spring/Summer 2025 to practice and ensure readiness for PSPS events.
Target Timeline: By 7/1/25, conduct exercises and drills to PG&E’s satisfaction that file handling and notification deployment will be acceptable to meet PSPS compliance requirements on all notification requirements

## Table 11-3
TABLE 11‑3:
HIGH LEVEL COMMUNICATION PROTOCOLS, PROCEDURES, AND SYSTEMS WITH PUBLIC SAFETY PARTNERS 86
Public Safety Partner Group | Name of Entity | Key Protocols | Frequency of Pre‑Arranged Communication Review and Update
City | City of Amador | See 11.3.1 narrative for key protocols. | Annually
City | City of American Canyon | See 11.3.1 narrative for key protocols. | Annually
City | City of Anderson | See 11.3.1 narrative for key protocols. | Annually
City | City of Angels Camp | See 11.3.1 narrative for key protocols. | Annually
City | City of Arcata | See 11.3.1 narrative for key protocols. | Annually
City | City of Arvin | See 11.3.1 narrative for key protocols. | Annually
City | City of Atherton | See 11.3.1 narrative for key protocols. | Annually
City | City of Atwater | See 11.3.1 narrative for key protocols. | Annually
City | City of Auburn | See 11.3.1 narrative for key protocols. | Annually
City | City of Avenal | See 11.3.1 narrative for key protocols. | Annually
City | City of Bakersfield | See 11.3.1 narrative for key protocols. | Annually
City | City of Belmont | See 11.3.1 narrative for key protocols. | Annually
City | City of Belvedere | See 11.3.1 narrative for key protocols. | Annually
City | City of Benicia | See 11.3.1 narrative for key protocols. | Annually
City | City of Berkeley | See 11.3.1 narrative for key protocols. | Annually
City | City of Blue Lake | See 11.3.1 narrative for key protocols. | Annually
City | City of Brentwood | See 11.3.1 narrative for key protocols. | Annually
City | City of Brisbane | See 11.3.1 narrative for key protocols. | Annually
City | City of Burlingame | See 11.3.1 narrative for key protocols. | Annually
City | City of Calistoga | See 11.3.1 narrative for key protocols. | Annually
City | City of Capitola | See 11.3.1 narrative for key protocols. | Annually
City | City of Carmel‑by‑the | See 11.3.1 narrative for key protocols. | Annually
City | City of Chico | See 11.3.1 narrative for key protocols. | Annually
City | City of Chowchilla | See 11.3.1 narrative for key protocols. | Annually
City | City of Clayton | See 11.3.1 narrative for key protocols. | Annually
City | City of Clearlake | See 11.3.1 narrative for key protocols. | Annually
City | City of Cloverdale | See 11.3.1 narrative for key protocols. | Annually
City | City of Clovis | See 11.3.1 narrative for key protocols. | Annually
City | City of Coalinga | See 11.3.1 narrative for key protocols. | Annually
City | City of Colfax | See 11.3.1 narrative for key protocols. | Annually
City | City of Concord | See 11.3.1 narrative for key protocols. | Annually
City | City of Corcoran | See 11.3.1 narrative for key protocols. | Annually
City | City of Corning | See 11.3.1 narrative for key protocols. | Annually
City | City of Corte | See 11.3.1 narrative for key protocols. | Annually
City | City of Cotati | See 11.3.1 narrative for key protocols. | Annually
City | City of Cupertino | See 11.3.1 narrative for key protocols. | Annually
City | City of Daly City | See 11.3.1 narrative for key protocols. | Annually
City | City of Danville | See 11.3.1 narrative for key protocols. | Annually
City | City of Del Rey Oaks | See 11.3.1 narrative for key protocols. | Annually
City | City of Dinuba | See 11.3.1 narrative for key protocols. | Annually
City | City of Dos Palos | See 11.3.1 narrative for key protocols. | Annually
City | City of Dublin | See 11.3.1 narrative for key protocols. | Annually
City | City of East Palo Alto | See 11.3.1 narrative for key protocols. | Annually
City | City of El Cerrito | See 11.3.1 narrative for key protocols. | Annually
City | City of Emeryville | See 11.3.1 narrative for key protocols. | Annually
City | City of Fairfax | See 11.3.1 narrative for key protocols. | Annually
City | City of Fairfield | See 11.3.1 narrative for key protocols. | Annually
City | City of Ferndale | See 11.3.1 narrative for key protocols. | Annually
City | City of Firebaugh | See 11.3.1 narrative for key protocols. | Annually
City | City of Fort Bragg | See 11.3.1 narrative for key protocols. | Annually
City | City of Fortuna | See 11.3.1 narrative for key protocols. | Annually
City | City of Foster City | See 11.3.1 narrative for key protocols. | Annually
City | City of Fowler | See 11.3.1 narrative for key protocols. | Annually
City | City of Fremont | See 11.3.1 narrative for key protocols. | Annually
City | City of Fresno | See 11.3.1 narrative for key protocols. | Annually
City | City of Gilroy | See 11.3.1 narrative for key protocols. | Annually
City | City of Gonzales | See 11.3.1 narrative for key protocols. | Annually
City | City of Grass Valley | See 11.3.1 narrative for key protocols. | Annually
City | City of Greenfield | See 11.3.1 narrative for key protocols. | Annually
City | City of Gridley | See 11.3.1 narrative for key protocols. | Annually
City | City of Gustine | See 11.3.1 narrative for key protocols. | Annually
City | City of Half Moon Bay | See 11.3.1 narrative for key protocols. | Annually
City | City of Hanford | See 11.3.1 narrative for key protocols. | Annually
City | City of Hayward | See 11.3.1 narrative for key protocols. | Annually
City | City of Healdsburg | See 11.3.1 narrative for key protocols. | Annually
City | City of Hercules | See 11.3.1 narrative for key protocols. | Annually
City | City of Hillsborough | See 11.3.1 narrative for key protocols. | Annually
City | City of Hollister | See 11.3.1 narrative for key protocols. | Annually
City | City of Huron | See 11.3.1 narrative for key protocols. | Annually
City | City of Lone | See 11.3.1 narrative for key protocols. | Annually
City | City of Jackson | See 11.3.1 narrative for key protocols. | Annually
City | City of Kerman | See 11.3.1 narrative for key protocols. | Annually
City | City of King City | See 11.3.1 narrative for key protocols. | Annually
City | City of Lafayette | See 11.3.1 narrative for key protocols. | Annually
City | City of Lakeport | See 11.3.1 narrative for key protocols. | Annually
City | City of Larkspur | See 11.3.1 narrative for key protocols. | Annually
City | City of Lathrop | See 11.3.1 narrative for key protocols. | Annually
City | City of Lemoore | See 11.3.1 narrative for key protocols. | Annually
City | City of Lincoln | See 11.3.1 narrative for key protocols. | Annually
City | City of Livermore | See 11.3.1 narrative for key protocols. | Annually
City | City of Livingston | See 11.3.1 narrative for key protocols. | Annually
City | City of Loomis | See 11.3.1 narrative for key protocols. | Annually
City | City of Los Altos | See 11.3.1 narrative for key protocols. | Annually
City | City of Los Altos Hills | See 11.3.1 narrative for key protocols. | Annually
City | City of Los Banos | See 11.3.1 narrative for key protocols. | Annually
City | City of Los Gatos | See 11.3.1 narrative for key protocols. | Annually
City | City of Madera | See 11.3.1 narrative for key protocols. | Annually
City | City of Maricopa | See 11.3.1 narrative for key protocols. | Annually
City | City of Marina | See 11.3.1 narrative for key protocols. | Annually
City | City of Martinez | See 11.3.1 narrative for key protocols. | Annually
City | City of Marysville | See 11.3.1 narrative for key protocols. | Annually
City | City of McFarland | See 11.3.1 narrative for key protocols. | Annually
City | City of Mendota | See 11.3.1 narrative for key protocols. | Annually
City | City of Menlo Park | See 11.3.1 narrative for key protocols. | Annually
City | City of Merced | See 11.3.1 narrative for key protocols. | Annually
City | City of Mill Valley | See 11.3.1 narrative for key protocols. | Annually
City | City of Millbrae | See 11.3.1 narrative for key protocols. | Annually
City | City of Milpitas | See 11.3.1 narrative for key protocols. | Annually
City | City of Monte Sereno | See 11.3.1 narrative for key protocols. | Annually
City | City of Monterey | See 11.3.1 narrative for key protocols. | Annually
City | City of Moraga | See 11.3.1 narrative for key protocols. | Annually
City | City of Morgan Hill | See 11.3.1 narrative for key protocols. | Annually
City | City of Mountain View | See 11.3.1 narrative for key protocols. | Annually
City | City of Napa | See 11.3.1 narrative for key protocols. | Annually
City | City of Nevada City | See 11.3.1 narrative for key protocols. | Annually
City | City of Newark | See 11.3.1 narrative for key protocols. | Annually
City | City of Newman | See 11.3.1 narrative for key protocols. | Annually
City | City of Novato | See 11.3.1 narrative for key protocols. | Annually
City | City of Oakdale | See 11.3.1 narrative for key protocols. | Annually
City | City of Oakland | See 11.3.1 narrative for key protocols. | Annually
City | City of Oakley | See 11.3.1 narrative for key protocols. | Annually
City | City of Orange Cove | See 11.3.1 narrative for key protocols. | Annually
City | City of Orinda | See 11.3.1 narrative for key protocols. | Annually
City | City of Orland | See 11.3.1 narrative for key protocols. | Annually
City | City of Oroville | See 11.3.1 narrative for key protocols. | Annually
City | City of Pacific Grove | See 11.3.1 narrative for key protocols. | Annually
City | City of Pacifica | See 11.3.1 narrative for key protocols. | Annually
City | City of Paradise | See 11.3.1 narrative for key protocols. | Annually
City | City of Parlier | See 11.3.1 narrative for key protocols. | Annually
City | City of Petaluma | See 11.3.1 narrative for key protocols. | Annually
City | City of Piedmont | See 11.3.1 narrative for key protocols. | Annually
City | City of Pinole | See 11.3.1 narrative for key protocols. | Annually
City | City of Pittsburg | See 11.3.1 narrative for key protocols. | Annually
City | City of Placerville | See 11.3.1 narrative for key protocols. | Annually
City | City of Pleasant Hill | See 11.3.1 narrative for key protocols. | Annually
City | City of Pleasanton | See 11.3.1 narrative for key protocols. | Annually
City | City of Plymouth | See 11.3.1 narrative for key protocols. | Annually
City | City of Point Arena | See 11.3.1 narrative for key protocols. | Annually
City | City of Portola Valley | See 11.3.1 narrative for key protocols. | Annually
City | City of Red Bluff | See 11.3.1 narrative for key protocols. | Annually
City | City of Redwood | See 11.3.1 narrative for key protocols. | Annually
City | City of Reedley | See 11.3.1 narrative for key protocols. | Annually
City | City of Richmond | See 11.3.1 narrative for key protocols. | Annually
City | City of Rio Dell | See 11.3.1 narrative for key protocols. | Annually
City | City of Ripon | See 11.3.1 narrative for key protocols. | Annually
City | City of Riverbank | See 11.3.1 narrative for key protocols. | Annually
City | City of Rohnert Park | See 11.3.1 narrative for key protocols. | Annually
City | City of Ross | See 11.3.1 narrative for key protocols. | Annually
City | City of Saint Helena | See 11.3.1 narrative for key protocols. | Annually
City | City of Salinas | See 11.3.1 narrative for key protocols. | Annually
City | City of San Anselmo | See 11.3.1 narrative for key protocols. | Annually
City | City of San Bruno | See 11.3.1 narrative for key protocols. | Annually
City | City of San Carlos | See 11.3.1 narrative for key protocols. | Annually
City | City of San Francisco | See 11.3.1 narrative for key protocols. | Annually
City | City of San Joaquin | See 11.3.1 narrative for key protocols. | Annually
City | City of San Jose | See 11.3.1 narrative for key protocols. | Annually
City | City of San Juan Bautista | See 11.3.1 narrative for key protocols. | Annually
City | City of San Leandro | See 11.3.1 narrative for key protocols. | Annually
City | City of San Luis Obispo | See 11.3.1 narrative for key protocols. | Annually
City | City of San Mateo | See 11.3.1 narrative for key protocols. | Annually
City | City of San Pablo | See 11.3.1 narrative for key protocols. | Annually
City | City of San Rafael | See 11.3.1 narrative for key protocols. | Annually
City | City of San Ramon | See 11.3.1 narrative for key protocols. | Annually
City | City of Sand City | See 11.3.1 narrative for key protocols. | Annually
City | City of Sanger | See 11.3.1 narrative for key protocols. | Annually
City | City of Santa Cruz | See 11.3.1 narrative for key protocols. | Annually
City | City of Santa Maria | See 11.3.1 narrative for key protocols. | Annually
City | City of Santa Rosa | See 11.3.1 narrative for key protocols. | Annually
City | City of Saratoga | See 11.3.1 narrative for key protocols. | Annually
City | City of Sausalito | See 11.3.1 narrative for key protocols. | Annually
City | City of Scotts Valley | See 11.3.1 narrative for key protocols. | Annually
City | City of Seaside | See 11.3.1 narrative for key protocols. | Annually
City | City of Sebastopol | See 11.3.1 narrative for key protocols. | Annually
City | City of Selma | See 11.3.1 narrative for key protocols. | Annually
City | City of Shafter | See 11.3.1 narrative for key protocols. | Annually
City | City of Soledad | See 11.3.1 narrative for key protocols. | Annually
City | City of Sonoma | See 11.3.1 narrative for key protocols. | Annually
City | City of South San Francisco | See 11.3.1 narrative for key protocols. | Annually
City | City of Stockton | See 11.3.1 narrative for key protocols. | Annually
City | City of Suisun | See 11.3.1 narrative for key protocols. | Annually
City | City of Sunnyvale | See 11.3.1 narrative for key protocols. | Annually
City | City of Sutter Creek | See 11.3.1 narrative for key protocols. | Annually
City | City of Taft | See 11.3.1 narrative for key protocols. | Annually
City | City of Tehama | See 11.3.1 narrative for key protocols. | Annually
City | City of Tiburon | See 11.3.1 narrative for key protocols. | Annually
City | City of Tracy | See 11.3.1 narrative for key protocols. | Annually
City | City of Trinidad | See 11.3.1 narrative for key protocols. | Annually
City | City of Ukiah | See 11.3.1 narrative for key protocols. | Annually
City | City of Union City | See 11.3.1 narrative for key protocols. | Annually
City | City of Vacaville | See 11.3.1 narrative for key protocols. | Annually
City | City of Vallejo | See 11.3.1 narrative for key protocols. | Annually
City | City of Walnut Creek | See 11.3.1 narrative for key protocols. | Annually
City | City of Wasco | See 11.3.1 narrative for key protocols. | Annually
City | City of Watsonville | See 11.3.1 narrative for key protocols. | Annually
City | City of West Sacramento | See 11.3.1 narrative for key protocols. | Annually
City | City of Wheatland | See 11.3.1 narrative for key protocols. | Annually
City | City of Willits | See 11.3.1 narrative for key protocols. | Annually
City | City of Windsor | See 11.3.1 narrative for key protocols. | Annually
City | City of Winters | See 11.3.1 narrative for key protocols. | Annually
City | City of Woodland | See 11.3.1 narrative for key protocols. | Annually
City | City of Yountville | See 11.3.1 narrative for key protocols. | Annually
City | City of Yuba City | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | Bear Valley Fire Department | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | Burney Fire | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | City of Albany | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | Fire Area Coordinator | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | Fire Department | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | Office of Education | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | Orland Fire Department | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | Police Department | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | West Point Fire District | See 11.3.1 narrative for key protocols. | Annually
City Emergency Services | West Stanislaus Fire District | See 11.3.1 narrative for key protocols. | Annually
County | Alameda County | See 11.3.1 narrative for key protocols. | Annually
County | Alpine County | See 11.3.1 narrative for key protocols. | Annually
County | Amador County | See 11.3.1 narrative for key protocols. | Annually
County | Butte County | See 11.3.1 narrative for key protocols. | Annually
County | Calaveras County | See 11.3.1 narrative for key protocols. | Annually
County | El Dorado County | See 11.3.1 narrative for key protocols. | Annually
County | Fresno County | See 11.3.1 narrative for key protocols. | Annually
County | Glenn County | See 11.3.1 narrative for key protocols. | Annually
County | Kings County | See 11.3.1 narrative for key protocols. | Annually
County | Lake County | See 11.3.1 narrative for key protocols. | Annually
County | Lassen County | See 11.3.1 narrative for key protocols. | Annually
County | Madera County | See 11.3.1 narrative for key protocols. | Annually
County | Marin County | See 11.3.1 narrative for key protocols. | Annually
County | Mariposa County | See 11.3.1 narrative for key protocols. | Annually
County | Mendocino County | See 11.3.1 narrative for key protocols. | Annually
County | Merced County | See 11.3.1 narrative for key protocols. | Annually
County | Monterey County | See 11.3.1 narrative for key protocols. | Annually
County | Napa County | See 11.3.1 narrative for key protocols. | Annually
County | Placer County | See 11.3.1 narrative for key protocols. | Annually
County | Plumas County | See 11.3.1 narrative for key protocols. | Annually
County | San Benito County | See 11.3.1 narrative for key protocols. | Annually
County | San Joaquin County | See 11.3.1 narrative for key protocols. | Annually
County | San Luis Obispo County | See 11.3.1 narrative for key protocols. | Annually
County | Santa Barbara County | See 11.3.1 narrative for key protocols. | Annually
County | Santa Clara County | See 11.3.1 narrative for key protocols. | Annually
County | Santa Cruz County | See 11.3.1 narrative for key protocols. | Annually
County | Shasta County | See 11.3.1 narrative for key protocols. | Annually
County | Sierra County | See 11.3.1 narrative for key protocols. | Annually
County | Siskiyou County | See 11.3.1 narrative for key protocols. | Annually
County | Solano County | See 11.3.1 narrative for key protocols. | Annually
County | Sonoma County | See 11.3.1 narrative for key protocols. | Annually
County | Tehama County | See 11.3.1 narrative for key protocols. | Annually
County | Trinity County | See 11.3.1 narrative for key protocols. | Annually
County | Tulare County | See 11.3.1 narrative for key protocols. | Annually
County | Tuolumne County | See 11.3.1 narrative for key protocols. | Annually
County | Yuba County | See 11.3.1 narrative for key protocols. | Annually
County | Colusa County | See 11.3.1 narrative for key protocols. | Annually
County | Contra Costa County | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Alameda County Sheriffs Office of Emergency Services | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | El Dorado County Fire Protection District | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Emergency Medical Services (EMS) | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Fire Department | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Fire Protection District | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Mountain Valley EMS Agency | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Napa Co Fire Dept / Cal Fire | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Plumas Public Health | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Sheriff | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Sherriff’s Department | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Sherriff’s Office | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Alameda County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Calaveras County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Colusa County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Contra Costa County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | El Dorado County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Fresno County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Glen County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Humboldt County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Kern County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Kings County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Lassen County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Madera County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Marin County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Mariposa County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Mendocino County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Merced County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Monterey County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Napa County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Nevada County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Placer County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Plumas County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Sacramento County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | San Benito County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | San Francisco County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | San Joaquin County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | San Luis Obispo County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | San Mateo County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Santa Barbara County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Santa Clara County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Santa Cruz County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Shasta County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Sierra County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Siskiyou County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Solano County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Sonoma County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Stanislaus County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Sutter County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Tehama County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Trinity County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Tulare County OES | See 11.3.1 narrative for key protocols. | Annually
County Emergency Services | Yuba County OES | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Alameda County Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | California Pacific Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Enloe Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Glenn Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Marshall Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Natividad Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Queen of the Valley Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Santa Clara Valley Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Summit Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Bay Medical Foundation | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Solano Medical Center | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | American Hospital Management Corp | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | El Camino Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Hca Good Samaritan Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Heart Hospital of Bk Llc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | John C Fremont Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Kaiser Foundation Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Kern County Hospital Authority | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Marin General Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Mark Twain St Joseph’s Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Mayers Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Nme Hospitals Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Oroville Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Petaluma Valley Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Plumas District Hospital (State Agency) | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Redwood Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | San Benito Hospital District | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Santa Ynez Valley Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Seneca District Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sierra Nevada Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sierra Vista Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sonoma Valley Hospital District | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sonora Community Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Southern Monterey County Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St Helena Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St. Joseph Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St Luke’s Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Amador Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Bay Hospitals | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Lakeside Community Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Santa Ynez Valley Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Seneca District Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sierra Nevada Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sierra Vista Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sonoma Valley Hospital District | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sonora Community Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Southern Monterey County Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St Helena Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St. Joseph Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St Luke’s Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Amador Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Bay Hospitals | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Lakeside Community Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Santa Ynez Valley Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Seneca District Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sierra Nevada Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sierra Vista Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sonoma Valley Hospital District | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sonora Community Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Southern Monterey County Memorial Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St Helena Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St. Joseph Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | St Luke’s Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Amador Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Bay Hospitals | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Lakeside Community Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter Tracy Community Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Sutter West Bay Hospital | See 11.3.1 narrative for key protocols. | Annually
Emergency Hospitals | Twin Cities Community Hospital Inc | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Army Corps of Engineers | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Department of Health Service | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Department of IT | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Department of Public Safety | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Department of Veteran Affairs | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Dept of Transp, Federal Transit Admin | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | FBI | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Federal Communications Commission | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | FEMA | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | Housing and Urban Development | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Army | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Army 63rd Division | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Army Reserves | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Bureau of Reclamation | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Coast Guard Sector San Francisco | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Department of Health & Human Services | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Department of Homeland Security | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Department of the Interior | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Dept. of Housing & Urban Development | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Environmental Protection Agency | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. EPA | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Coast Guard | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Coast Guard Eleventh District | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Department of Agriculture | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Department of Defense | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Forest Service | See 11.3.1 narrative for key protocols. | Annually
Federal Agency | U.S. Forest Service Fire | See 11.3.1 narrative for key protocols. | Annually
Federal Emergency Services | Coast Guard | See 11.3.1 narrative for key protocols. | Annually
Federal Emergency Services | PHI Air Medical | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Community Clean Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | East Bay Community Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | MCE Clean Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Monterey Bay Community Power | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Peninsula Clean Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Pioneer Community Energy (PIO) | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Redwood Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | San Francisco Public Utilities | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | San Jose Clean Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Silicon Valley Clean Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Sonoma Clean Power | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Sonoma Water | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Valley Clean Energy | See 11.3.1 narrative for key protocols. | Annually
Publicly‑Owned Utilities | Western Area Power Administration | See 11.3.1 narrative for key protocols. | Annually
State Agency | Indian Health Service California Area | See 11.3.1 narrative for key protocols. | Annually
State Agency | State Government | See 11.3.1 narrative for key protocols. | Annually
State Emergency Services | CAL FIRE | See 11.3.1 narrative for key protocols. | Annually
State Emergency Services | CAL FIRE TCU | See 11.3.1 narrative for key protocols. | Annually
State Emergency Services | CAL FIRE/ECC | See 11.3.1 narrative for key protocols. | Annually
State Emergency Services | CAL FIRE/PCF | See 11.3.1 narrative for key protocols. | Annually
State Emergency Services | California Highway Patrol | See 11.3.1 narrative for key protocols. | Annually
State Emergency Services | California Office of Emergency Services | See 11.3.1 narrative for key protocols. | Annually
State Emergency Services | CHP Golden Gate Division Dispatch | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Altice/Suddenlink | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | American Tower | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | AT&T | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Broadwing Communications, LLC | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Calaveras Telephone Co | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Calneva | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Caltel | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Charter Communications | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Comcast | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Consolidated Communications | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Crown Castle | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Extenet | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Foresthill Telephone | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Frontier Communications | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Happy Valley Telephone Co | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Hornitos Telephone Co C/O Tds Telecom | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Mediacom California Llc | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Northland Cable Television Inc | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Northland Communications | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Ponderosa Telephone Co | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Qwest/Centurylink | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Sba Towers | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Sebastian Corp | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Sierra Tel Co Inc | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Sierra Telephone | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Sprint Corporation | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Spring Spectrum Lp | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Tds Telecom | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | T‑Mobile | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | US Cellular | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Verizon | See 11.3.1 narrative for key protocols. | Annually
Telecommunications Providers | Volcano Communications | See 11.3.1 narrative for key protocols. | Annually

## Table 11-4
TABLE 11‑4:
KEY GAPS AND LIMITATIONS IN COMMUNICATION COORDINATION WITH PUBLIC SAFETY PARTNERS 87
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
N/A | N/A | N/A

## Table 11-5
TABLE 11‑5:
COLLABORATION IN LOCAL AND REGIONAL WILDFIRE MITIGATION PLANNING 88
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., Non‑Governmental Organization, Fire Safe Council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Redwood City San Carlos Fire Department | Redwood San Carlos Fire AB 56 | 2023-01-03 | Met with Battalion Chief Lax.
San Mateo Consolidated Fire | San Mateo Consolidated AB 56 | 2023-01-04 | Met with Battalion Chief Tony Blackman at EOC.
San Mateo County Department of Emergency Management | San Mateo Consolidated AB 56 | 2023-01-04 | Met with Battalion Chief Tony Blackman at EOC.
Orland Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Capay Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Hamilton City Fire Department | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Willows City Fire Department | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Bayliss Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Elk Creek Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Kanawha Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Willows Rural Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Butte City Fire Department | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Glenn ‑ Codora Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
CAL FIRE ‑ Tehama‑Glenn | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Ord Bend Community Services District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Artois Fire Protection District | Glenn County Fire Chiefs Meeting | 2023-01-11 | Monthly meeting held at Glenn‑Codora Fire. Discussed AB 56 gas compliance and each agency chief received gas complaisance folder.
Coastside Fire Protection District | San Mateo County / Coast Side Fire AB 56 | 2023-01-11 | Met with Battalion Chief Ryan West & Battalion Chief Dave Hibdon.
CAL FIRE ‑ San Mateo‑Santa Cruz | San Mateo County / Coast Side Fire AB 56 | 2023-01-11 | Met with Battalion Chief Ryan West & Battalion Chief Dave Hibdon.
La Honda Fire Brigade | La Honda Fire Brigade AB 56 | 2023-01-15 | Met with Fire Chief Ari Delay representing La Honda Fire and San Bruno Fire.
San Bruno Fire Department | La Honda Fire Brigade AB 56 | 2023-01-15 | Met with Fire Chief Ari Delay representing La Honda Fire and San Bruno Fire.
Fall River Valley Fire Protection District | AB 56 Meeting with Fall River Valley FPD | 2023-01-19 | Met with Fire Chief Jeff Oldson.
Central County Fire Department | Central County Fire AB 56 | 2023-01-20 | Met with Chief Baker to discuss AB 56‑related information.
Colma Fire Protection District | Colma Fire District AB 56 | 2023-01-20 | Met with Captain Pardini and crew members to discuss AB 56‑related information.
Menlo Park Fire Protection District | Menlo Park Fire AB 56 | 2023-01-20 | Met with Chief Figone to discuss AB 56‑related information.
North County Fire Authority | North County Fire Authority AB 56 | 2023-01-20 | Met with Chief Fredrick and crew members to discuss AB 56‑related information.
South San Francisco Fire Department | South San Francisco Fire AB 56 | 2023-01-20 | Met with Chief Metch to discuss AB 56‑related information.
Woodside Fire Protection District | Woodside Fire District AB 56 | 2023-01-20 | Met with Chief Heard at Fire Station on SLAC campus to discuss AB 56‑related information.
CITY OF SAN JOSE | City of San Jose & PG&E Coordination Call #3 | 2023-01-20 | PG&E Mtg was an informal San Jose storm recap & hotwash attended by the RVP and other PG&E representatives.
Corning City Fire Department | Corning City Fire Department | 2023-01-24 | Met with Chief at his office and discussed gas compliance.
Red Bluff Fire Department | Red Bluff Fire Department | 2023-01-24 | Met with Fire Chief at his office and discussed gas compliance.
CAL FIRE ‑ San Benito‑Monterey | AB 56 Meeting | 2023-01-26 | Met with B/C Keith Tsudama.
Monterey Fire Department | AB 56 Meeting | 2023-01-26 | Met with D/C Cooper regarding training.
CAL FIRE ‑ Butte | CAL FIRE Butte AB 56 Meeting | 2023-01-26 | Met with Chief Garrett Sjolund to discuss Fire Department matters, training and AB 56. Chief Sjolund is the fire Chief for CAL FIRE Butte, Butte County Fire Department, Cities of Biggs, Gridley and Oroville Fire and the Town of Paradise Fire Department. Chief Sjolund provided with AB 56 Trifold, one for each department, as well as an electronic copy of the AB 56 information in a subsequent e‑mail so that he could distribute it to his staff.
Biggs Fire Department | CAL FIRE Butte AB 56 Meeting | 2023-01-26 | Met with Chief Garrett Sjolund to discuss Fire Department matters, training and AB 56. Chief Sjolund is the fire Chief for CAL FIRE Butte, Butte County Fire Department, Cities of Biggs, Gridley and Oroville Fire and the Town of Paradise Fire Department. Chief Sjolund provided with AB 56 Trifold, one for each department, as well as an electronic copy of the AB 56 information in a subsequent e‑mail so that he could distribute it to his staff.
Gridley Fire Department | CAL FIRE Butte AB 56 Meeting | 2023-01-26 | Met with Chief Garrett Sjolund to discuss Fire Department matters, training and AB 56. Chief Sjolund is the fire Chief for CAL FIRE Butte, Butte County Fire Department, Cities of Biggs, Gridley and Oroville Fire and the Town of Paradise Fire Department. Chief Sjolund provided with AB 56 Trifold, one for each department, as well as an electronic copy of the AB 56 information in a subsequent e‑mail so that he could distribute it to his staff.
Oroville Fire Department | CAL FIRE Butte AB 56 Meeting | 2023-01-26 | Met with Chief Garrett Sjolund to discuss Fire Department matters, training and AB 56. Chief Sjolund is the fire Chief for CAL FIRE Butte, Butte County Fire Department, Cities of Biggs, Gridley and Oroville Fire and the Town of Paradise Fire Department. Chief Sjolund provided with AB 56 Trifold, one for each department, as well as an electronic copy of the AB 56 information in a subsequent e‑mail so that he could distribute it to his staff.
Paradise Fire Department | CAL FIRE Butte AB 56 Meeting | 2023-01-26 | Met with Chief Garrett Sjolund to discuss Fire Department matters, training and AB 56. Chief Sjolund is the fire Chief for CAL FIRE Butte, Butte County Fire Department, Cities of Biggs, Gridley and Oroville Fire and the Town of Paradise Fire Department. Chief Sjolund provided with AB 56 Trifold, one for each department, as well as an electronic copy of the AB 56 information in a subsequent e‑mail so that he could distribute it to his staff.
San Bernardino County Fire Department | San Bernardino Co Fire Chiefs MTG | 2023-01-26 | During County Fire Chiefs meeting reviewed contingency plans, PG&E Gas Emergency Response Plan (GERP), AB 56 Gas Emergencies and discussed PSPS events. Mailed AB 56 Guide to Public Safety and discussed future First Responder Workshops (FRW) and exercises.
Apple Valley Fire Protection District | San Bernardino Co Fire Chiefs MTG | 2023-01-26 | During County Fire Chiefs meeting reviewed contingency plans, PG&E Gas GERP, AB 56 Gas Emergencies and discussed PSPS events. Mailed AB 56 Guide to Public Safety and discussed future FRWs and exercises.
CAL FIRE ‑ San Bernardino | San Bernardino Co Fire Chiefs MTG | 2023-01-26 | During County Fire Chiefs meeting reviewed contingency plans, PG&E Gas GERP, AB 56 Gas Emergencies and discussed PSPS events. Mailed AB 56 Guide to Public Safety and discussed future FRWs and exercises.
Victorville Fire Department | San Bernardino Co Fire Chiefs MTG | 2023-01-26 | During County Fire Chiefs meeting reviewed contingency plans, PG&E Gas GERP, AB 56 Gas Emergencies and discussed PSPS events. Mailed AB 56 Guide to Public Safety and discussed future FRWs and exercises.
Marine Corps Logistics Base Barstow Fire Department | San Bernardino Co Fire Chiefs MTG | 2023-01-26 | During County Fire Chiefs meeting reviewed contingency plans, PG&E Gas GERP, AB 56 Gas Emergencies and discussed PSPS events. Mailed AB 56 Guide to Public Safety and discussed future FRWs and exercises.
Marina Fire Department | AB 56 Meeting | 2023-01-27 | Met with Division Chief Carlos Vega at Round Table Pizza.
Santa Clara County Office of Emergency Management | Santa Clara County OA IWE#2, Meeting #2 | 2023-01-30 | Inclement weather event planning meeting for Santa Clara County.
Maxwell Fire Protection District | AB 56 Meeting | 2023-01-31 | Met with Maxwell Fire Department that included the AB 56 information in the First Responder Guide to Public Safety handout; e‑mailed the PDF document with same material
Arbuckle ‑ College City Fire Protection District | AB 56 Meeting | 2023-01-31 | Met with Arbuckle/College City Fire Department on AB 56 information in the First Responder Guide to Public Safety handout.
Williams Fire Protection Authority | AB 56 Meeting | 2023-01-31 | Met with Williams Fire Protection District pertaining to AB 56 information in the First Responder Guide to Public Safety Handout.
Little Lake Fire Protection District | Little Lake Fire Department AB 56 | 2023-01-31 | Project overview in person meeting for I‑751 pipeline inspection project in Willits planned for 2023. Discussed the First Responder Guide to Public Safety handout which I hand delivered to Fire Chief.
Santa Clara County Office of Emergency Management | Santa Clara County OA IWE#2, Meeting #3 | 2023-01-31 | Inclement weather event planning meeting for Santa Clara County.
Soledad Correctional Training Facility ‑ Fire Department | AB 56 Meeting | 2023-02-01 | Met with BLM, Camp Roberts, Soledad Correctional Center, Greenfield, Gonzales and King City Fire Departments.
Greenfield Fire Department | AB 56 Meeting | 2023-02-01 | Met with BLM, Camp Roberts, Soledad Correctional Center, Greenfield, Gonzales and King City Fire Departments.
King City Volunteer Fire Department | AB 56 Meeting | 2023-02-01 | Met with BLM, Camp Roberts, Soledad Correctional Center, Greenfield, Gonzales and King City Fire Departments.
Camp Roberts Fire Department | AB 56 Meeting | 2023-02-01 | Met in South County with BLM, Camp Roberts, Soledad Correctional Center, Greenfield, Gonzales and King City Fire Departments.
Bureau of Land Management ‑ Hollister | AB 56 Meeting | 2023-02-01 | Met in South County with BLM, Camp Roberts, Soledad Correctional Center, Greenfield, Gonzales and King City Fire Departments.
Gonzales Volunteer Fire Department | AB 56 Meeting | 2023-02-01 | Met in South County with BLM, Camp Roberts, Soledad Correctional Center, Greenfield, Gonzales and King City Fire Departments.
Yuba City Fire Department | AB 56 Meeting | 2023-02-01 | Met with Yuba City Fire Department Chief which included the AB 56 information in the First Responder Guide to Public Safety handout. Also e‑mailed the PDF document with same material.
San Francisco Fire Department | San Francisco Fire ‑ AB 56 | 2023-02-01 | Contingency Plan Meeting ‑ AB 56
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Clements Rural Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Stockton Fire Department | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Escalon Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Mokelumne Rural Fire District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Liberty Rural County Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Montezuma Fire Protection District | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Lodi Fire Department | San Joaquin County Fire Chief's Meeting | 2023-02-01 | Professional Group Meeting
Sutter Creek Fire Protection District | Amador County Fire Chiefs Meeting | 2023-02-02 | Professional Group Meeting
Ione Fire Department | Amador County Fire Chiefs Meeting | 2023-02-02 | Professional Group Meeting
CAL FIRE ‑ Amador‑El Dorado | Amador County Fire Chiefs Meeting | 2023-02-02 | Professional Group Meeting
Jackson Valley Fire Protection District | Amador County Fire Chiefs Meeting | 2023-02-02 | Professional Group Meeting
Hollister Fire Department | AB 56 Meeting | 2023-02-03 | Contingency Plan Meeting ‑ AB 56
San Juan Bautista Fire Department | AB 56 Meeting | 2023-02-03 | Contingency Plan Meeting ‑ AB 56
North County Fire Protection District of Monterey County | AB 56 Meeting | 2023-02-06 | Contingency Plan Meeting ‑ AB 56
Seaside Fire Department | AB 56 Meeting | 2023-02-06 | Contingency Plan Meeting – AB 56
Monterey County Regional Fire District | AB 56 Meeting | 2023-02-06 | Contingency Plan Meeting – AB 56
Presidio of Monterey‑Fire Department | AB 56 Meeting | 2023-02-06 | Contingency Plan Meeting – AB 56
Salinas Fire Department | AB 56 Meeting | 2023-02-06 | Contingency Plan Meeting – AB 56
Rough and Ready Fire Protection District | AB 56 Meeting | 2023-02-07 | Met with Nevada County Fire Chiefs which included the AB 56 information in the First Responder Guide to Public Safety handout.
CAL FIRE ‑ Nevada‑Yuba‑Placer | AB 56 Meeting | 2023-02-07 | Met with Nevada County Fire Chiefs which included the AB 56 information in the First Responder Guide to Public Safety handout.
Grass Valley Fire Department | AB 56 Meeting | 2023-02-07 | Met with Nevada County Fire Chiefs which included the AB 56 information in the First Responder Guide to Public Safety handout.
Rough and Ready Fire District | AB 56 Meeting | 2023-02-07 | Met with Nevada County Fire Chiefs which included the AB 56 information in the First Responder Guide to Public Safety handout.
Penn Valley Fire Protection District | AB 56 Meeting | 2023-02-07 | Met with Nevada County Fire Chiefs which included the AB 56 information in the First Responder Guide to Public Safety handout.
Clovis Fire Department | Clovis City Fire Dept Contingency Planning | 2023-02-07 | Reviewed Gas contingency plans with Chief. Future exercises and FRWs discussed. Mailed AB 56 First Responder Guide to Public Safety handout. E‑mailed Chief AB 56 Gas emergency contingency Planning. GERP, Gas emergency checklist and First responder guide to public safety attached.
Fig Garden Fire District | Fig Garden AB 56 Contingency Planning | 2023-02-07 | Reviewed Gas contingency plans with Chief. Future exercises and FRWs discussed. Mailed AB 56 First Responder Guide to Public Safety handout. E‑mailed Chief AB 56 Gas emergency contingency Planning. GERP, Gas emergency checklist and First responder guide to public safety attached.
Fresno Fire Department | Fresno City Fire AB 56 Contingency Planning | 2023-02-07 | Reviewed Gas contingency plans with Chief. Future exercises and FRWs discussed. Mailed AB 56 First Responder Guide to Public Safety handout. E‑mailed Chief AB 56 Gas emergency contingency Planning. GERP, Gas emergency checklist and First responder guide to public safety attached.
Sacramento River Fire Protection District | AB 56 Meeting | 2023-02-08 | Met with Sacramento River Fire Protection District focusing on AB 56 information in the First Responder Guide to Public Safety handout.
Princeton Fire Protection District | AB 56 Meeting | 2023-02-08 | Met with Princeton Fire Protection District focusing on AB 56 information in the First Responder Guide to Public Safety handout.
Colusa Fire Department | AB 56 Meeting | 2023-02-08 | Met with Colusa City Fire Department focusing on AB 56 information in the first responder guide to public safety handout.
CAL FIRE ‑ Tuolumne‑Calaveras | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Copperopolis Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Mokelumne Hill Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Central Calaveras Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Calaveras Consolidated Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
West Point Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Ebbetts Pass Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Murphys Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Altaville‑Melones Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Angels Camp Fire Department | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
San Andreas Fire Protection District | Calaveras County Chiefs Association Meeting | 2023-02-08 | Covered AB 56 requirements with Calaveras County Fire Chiefs and provided compliance materials at the meeting.
Marysville Fire Department | AB 56 Meeting | 2023-02-09 | Met with Marysville Fire Department (FD) to discuss AB 56 and go over the First Responder Guide to Public Safety handout.
Monterey Fire Department | AB 56 Meeting | 2023-02-09 | Met with Training Officers.
Twain Harte Community Services District Fire Department | Tuolumne County Fire Chiefs Association Meeting | 2023-02-09 | Met with Fire Chiefs on AB 56 requirements.
Sonora City Fire Department | Tuolumne County Fire Chiefs Association Meeting | 2023-02-09 | Met with Fire Chiefs on AB 56 requirements.
Mi‑Wuk Sugar Pine Fire Protection District | Tuolumne County Fire Chiefs Association Meeting | 2023-02-09 | Met with Fire Chiefs on AB 56 requirements.
Tuolumne Fire District | Tuolumne County Fire Chiefs Association Meeting | 2023-02-09 | Met with Fire Chiefs on AB 56 requirements.
CAL FIRE ‑ Tuolumne‑Calaveras | Tuolumne County Fire Chiefs Association Meeting | 2023-02-09 | Met with Fire Chiefs on AB 56 requirements.
Santa Clara County Emergency Managers Association | Santa Clara County Emergency Manager's Association Meeting | 2023-02-09 | Professional Group Meeting
Merced Fire Department | Merced Fire Department Chief's Meeting | 2023-02-14 | Met with City of Merced Fire Chief and Deputy Chief to present and discuss AB 56 information in the First Responder Guide to Public Safety handout, which was left with them. I also e‑mailed the digital (.pdf) version of the guide to them on 2/13/2023. Discussed PSPS Concurrent Emergencies.
Vacaville Fire Department | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Benicia Fire Department | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Suisun Fire Protection District | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Vallejo Fire Department | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Fairfield Fire Department | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Dixon Fire Department | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Fairfield Fire Department | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Suisun City Fire Department | Solano Co Fire Training Officers Meeting | 2023-02-15 | Contingency Plan Meeting – AB 56
Marin County Fire Department | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chief's and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
Central Marin Fire Authority | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chief's and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
Kentfield Fire Protection District | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chiefs and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
Marinwood Fire Department | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chiefs and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chief's were e‑mailed the PDF version of the trifold.
Novato Fire Protection District | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chief's and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
San Rafael Fire Department | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chief's and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
Mill Valley Fire Department | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chiefs and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
Ross Valley Fire Department | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chiefs and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
Southern Marin Fire Protection District | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chiefs and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
Tiburon Fire Protection District | AB 56 Meeting | 2023-02-16 | Met with Marin County Fire Chiefs and discussed AB 56 compliance in person using tri‑fold document for first responders. All Chiefs were e‑mailed the PDF version of the trifold.
American Medical Response | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting ‑ AB 56
Cottonwood Fire Protection District | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
Shasta CSD/Shasta Fire Protection District | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
Happy Valley Fire Protection District | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
Redding Fire Department | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
Anderson Fire Protection District | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
Shasta Lake Fire Protection District | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
Millville Fire Protection District | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
Shasta College Fire Department | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
American Red Cross | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Shasta‑Trinity | AB 56 Meeting with the Shasta County Fire Chiefs | 2023-02-16 | Contingency Plan Meeting – AB 56
South San Francisco Fire Department | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
North County Fire Authority | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
Menlo Park Fire Protection District | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
Woodside Fire Protection District | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
San Mateo Consolidated Fire | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
Redwood City San Carlos Fire Department | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
San Mateo County Fire | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
American Medical Response ‑ San Mateo County | San Mateo County Operations Chiefs Meeting | 2023-02-16 | Report out on PG&E Storms, AB 56 and planned joint training.
El Dorado Hills Fire Department | El Dorado Hills Training Center | 2023-02-16 | Met with El Dorado Hills FD Chief Dustin Hall and Mo Johnson at the new department training facility. EDHFD has requested a partnership and support from PG&E to provide utility related equipment at the training site to support additional firefighter safety and training.
Linda Fire Protection District | AB 56 Meeting | 2023-02-21 | Met with Station to discuss AB 56 First Responder Guide to Public Safety.
United States Bureau of Land Management ‑ Redding | United States Bureau of Land Management ‑ Redding | 2023-02-21 | Met with Jennifer and discussed AB 56 and provided compliance folder.
U.S. Forest Service ‑ Pacific Southwest Region, North Operations | United States Forest Service ‑ Pacific Southwest Region | 2023-02-21 | Met with Anthony Masovero Chief of the region 5 HQ. Discussed AB 56 and provided him the folder.
Santa Clara County Office of Emergency Management | Santa Clara County OP Inclement Weather Event Planning Call #4‑1 | 2023-02-21 | Key Points ‑ Expected Impacts. A dynamic system arrives Tuesday night into Wednesday morning, impacting the coast. Cold air behind the front will make for frigid temperatures Thursday through Saturday for the entire region. Northerly winds with stronger wind gusts will arrive Tuesday night, not diminishing until early Thursday morning. Cold temperatures will lower snow levels to between 1,000 and 1, 500 feet. Light rain will arrive on Wednesday, but a secondary pulse Thursday will make the rainfall more widespread Thursday night and into much of Friday.
Rodeo‑Hercules Fire Protection District | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
El Cerrito Fire Department | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
Chevron Refinery Fire Department | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
San Ramon Valley Fire Protection District | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
Moraga ‑ Orinda Fire Protection District | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
East Bay Regional Park District Fire Department | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
Crockett‑Carquinez Fire Protection District | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Santa Clara | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
Richmond Fire Department | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
Contra Costa County Fire Protection District | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
Pinole Fire Department | Contra Costa County Fire Chiefs AB 56 meeting | 2023-02-22 | Contingency Plan Meeting – AB 56
Butte County Sheriff's Department | Butte County Sheriff Office PG&E Event Information | 2023-02-22 | Met to discuss gas & electric safety and programs, PSS program, etc. Followed up with an e‑mail to Deputy Ennes providing AB 56 First Responder packet, PG&E Gas Safety Operations & Maintenance, and PG&E Concurrent Event information as support information for our discussion.
Oakland Fire Department | ALCO TO's Meeting ‑ February | 2023-02-22 | Professional Group Meeting
CAL FIRE ‑ State Headquarters | ALCO TO's Meeting ‑ February | 2023-02-22 | Professional Group Meeting
Berkeley Fire Department | ALCO TO's Meeting ‑ February | 2023-02-22 | Professional Group Meeting
Fremont Fire Department | ALCO TO's Meeting ‑ February | 2023-02-22 | Professional Group Meeting
City of Alameda Fire Department | ALCO TO's Meeting ‑ February | 2023-02-22 | Professional Group Meeting
CAL FIRE ‑ Santa Clara | ALCO TO's Meeting ‑ February | 2023-02-22 | Professional Group Meeting
East Bay Regional Park District Fire Department | ALCO TO's Meeting ‑ February | 2023-02-22 | Professional Group Meeting
Roseville Fire Department | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Sacramento Metropolitan Fire District | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
CAL FIRE ‑ Nevada‑Yuba‑Placer | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Auburn City Fire Department | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
South Placer Fire District | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Rocklin Fire Department | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Placer Hills Fire Protection District | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Newcastle Fire Protection District | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Placer County Fire Department | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Penryn Fire Protection District | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Lincoln Fire Department | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Paige Volunteer Fire Department | AB 56 Meeting | 2023-02-23 | Met with Paige Volunteer Fire Department to discuss the AB 56 information in the First Responder Guide to Public Safety handout which was presented in person.
Chico Fire Department | Chico Fire AB 56 | 2023-02-23 | Met to discuss AB 56, PG&Es Gas Safety, 811, PSS program, etc. Followed up with an e‑mail to Chief Zinko providing AB 56 First Responder packet, PG&E Gas Safety Operations & Maintenance, and PG&E Concurrent Event information.
Walnut Grove Fire Protection District | South Sacramento Fire Chiefs Meeting AB 56 | 2023-02-23 | AB 56 discussion to include winter storm recap, PSPS, EPSS, SIPT Program and update on gas transmission projects in Sac County
River Delta Fire Protection District | South Sacramento Fire Chiefs Meeting AB 56 | 2023-02-23 | AB 56 discussion to include winter storm recap, PSPS, EPSS, SIPT Program and update on gas transmission projects in Sac County
Cosumnes Community Services District | South Sacramento Fire Chiefs Meeting AB 56 | 2023-02-23 | AB 56 discussion to include winter storm recap, PSPS, EPSS, SIPT Program and update on gas transmission projects in Sac County
Sacramento Regional Fire/EMS Communications Center | South Sacramento Fire Chiefs Meeting AB 56 | 2023-02-23 | AB 56 discussion to include winter storm recap, PSPS, EPSS, SIPT Program and update on gas transmission projects in Sac County
Samoa Peninsula Fire Protection District | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Ferndale Volunteer Fire Department | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Loleta Fire Protection District | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Bridgeville Fire Protection District | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Blue Lake Fire Protection District | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Westhaven Volunteer Fire Department | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Fieldbrook Fire Department | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Willow Creek Volunteer Fire Department | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Orick Volunteer Fire Department | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Petrolia Volunteer Fire Department | AB 56 Meeting | 2023-03-01 | AB 56 discussion with the Humboldt County Fire Chiefs via Zoom due to the snow/storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Napa County Fire Department | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
Napa Fire Department | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
Calistoga Fire Department | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Sonoma‑Lake‑Napa | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
Angwin Volunteer Fire Department | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
Saint Helena Fire Department | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
Deer Park Volunteer Fire Department | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
Rutherford Volunteer Fire Department | Napa County Fire Agency AB 56 | 2023-03-02 | Contingency Plan Meeting – AB 56
Burbank‑Paradise Fire Protection District | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
CAL FIRE ‑ Tuolumne‑Calaveras | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Patterson Fire Department | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
West Stanislaus Fire Protection District | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Hughson Fire Department | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Oakdale Fire Department | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Modesto Fire Department | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Salida Fire Protection District | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Woodland Avenue Fire Protection District | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Ceres Fire Department | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Stanislaus Consolidated Fire Protection District | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Turlock Fire Department and Emergency Services | Stanislaus County Fire Chiefs Association Meeting | 2023-03-02 | Covered AB58 compliance requirements with Stanislaus County Fire Department Chiefs and provided compliance materials.
Cloverdale Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Eldridge Fire Department | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Graton Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Santa Rosa Fire Department | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Forestville Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Gold Ridge Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Healdsburg Fire Department | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
North Bay Fire | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Kenwood Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Northern Sonoma County Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Rohnert Park Department of Public Safety ‑ Police Department | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Sonoma Valley Fire District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Petaluma Fire Department | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Sonoma County Fire District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Rancho Adobe Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Schell‑Vista Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Sebastopol Fire Department | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Graton Fire Protection District | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Rohnert Park Department of Public Safety | Sonoma County Fire Chiefs Meeting | 2023-03-08 | Discussed AB 56 Material handed out included "Handling Gas and Electrical Emergencies" Reference guide for First Responders and e‑mailed "First Responder Guide to Public Safety" to the attendees. The discussion included PG&E abilities to respond, PG&E's Emergency Response Plan, first responder abilities, contingency plans, and resources such as the PG&E Responder Portal, the National Pipeline Mapping System. PDF versions of the handouts were sent to attendees and agencies not in attendance through the Fire Chiefs’ Association as additional reinforcement and compliance.
Ukiah Valley Fire Authority | Ukiah Valley Fire Authority AB 56 | 2023-03-08 | Met with Ukiah Valley Fire Authority in Willits, I hand delivered the First Responder Guide to Public Safety and we discussed Gas response best practices and available resources.
Mountain Gate Community Services Fire District | AB 56 Meeting with Mountain Gate Fire Protection District | 2023-03-09 | Met with Fire Chief Corey Stevens.
Jackson Valley Fire Protection District | Amador County Fire Chiefs Meeting | 2023-03-09 | Professional Group Meeting
Sutter Creek Fire Protection District | Amador County Fire Chiefs Meeting | 2023-03-09 | Professional Group Meeting
Ione Fire Department | Amador County Fire Chiefs Meeting | 2023-03-09 | Professional Group Meeting
Mule Creek State Prison Fire Department | Amador County Fire Chiefs Meeting | 2023-03-09 | Professional Group Meeting
California Highway Patrol ‑ Amador | Amador County Fire Chiefs Meeting | 2023-03-09 | Professional Group Meeting
Weaverville Fire Protection District | AB 56 Meeting | 2023-03-13 | AB 56 discussion with the Trinity County Fire Chiefs via Zoom due to the winter storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
Hayfork Volunteer Fire Department | AB 56 Meeting | 2023-03-13 | AB 56 discussion with the Trinity County Fire Chiefs via Zoom due to the winter storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
CAL FIRE ‑ Shasta‑Trinity | AB 56 Meeting | 2023-03-13 | AB 56 discussion with the Trinity County Fire Chiefs via Zoom due to the winter storm. The First Responder Guide to Public Safety handout was e‑mailed to the entire group prior to the meeting.
CAL FIRE ‑ San Luis Obispo | First Responder Guide discussion AB 56 | 2023-03-14 | Met with San Luis Obispo County Fire/CALFIRE which included the AB 56 information in the First Responder Guide to Public Safety handout that was given to them at the meeting.
Hopland Fire Protection District | AB 56 Hopland Fire District | 2023-03-21 | Discussed the First Responder Guide to Public Safety and best practices for Natural Gas response. Hand delivered the tri‑fold guide for 2023 and reviewed its contents.
Humboldt Bay Fire Protection District | AB 56 Meeting | 2023-03-22 | AB 56 discussion with the Humboldt County Fire Chiefs in person in Eureka. The First Responder Guide to Public Safety handout distributed and it also was e‑mailed to the entire group prior to the meeting.
Fortuna Fire Protection District | AB 56 Meeting | 2023-03-22 | AB 56 discussion with the Humboldt County Fire Chiefs in person in Eureka. The First Responder Guide to Public Safety handout distributed and it also was e‑mailed to the entire group prior to the meeting.
Arcata Fire Protection District | AB 56 Meeting | 2023-03-22 | AB 56 discussion with the Humboldt County Fire Chiefs in person in Eureka. The First Responder Guide to Public Safety handout distributed and it also was e‑mailed to the entire group prior to the meeting.
CAL FIRE ‑ Humboldt‑Del Norte | AB 56 Meeting | 2023-03-22 | AB 56 discussion with the Humboldt County Fire Chiefs in person in Eureka. The First Responder Guide to Public Safety handout distributed and it also was e‑mailed to the entire group prior to the meeting.
Rio Dell Fire Protection District | AB 56 Meeting | 2023-03-22 | AB 56 discussion with the Humboldt County Fire Chiefs in person in Eureka. The First Responder Guide to Public Safety handout distributed and it also was e‑mailed to the entire group prior to the meeting.
Blue Lake Rancheria Fire Department | AB 56 Meeting | 2023-03-23 | AB 56 discussion with Blue Lake Rancheria Fire Dept. The First Responder Guide to Public Safety handout distributed in person to the chief. He provided me a tour of their facility and equipment.
Redwood Valley‑Calpella Fire Protection District | AB 56 Redwood Valley‑Calpella Fire Department | 2023-03-24 | Discussed AB 56 and the First Responder Guide to Public Safety, along with best practices for Natural Gas response and available PG&E resources. I hand delivered the 2023 version of the trifold guide to the Fire Chief.
CAL FIRE ‑ Sonoma‑Lake‑Napa | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Clarksburg Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
West Plainfield Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Capay Valley Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Yocha Dehe Fire Department | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Davis Fire Department | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
University of California ‑ Davis Fire Department | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Dunnigan Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Knights Landing Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
West Sacramento Fire Department | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Elkhorn Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Esparto Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Madison Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Zamora Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Woodland Fire Department | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Yolo Fire Protection District | AB 56 | 2023-03-30 | E‑mailed AB 56 materials with a brief program description followed up with in person meetings where I again touched on main themes, FRW, Portals, Maps, SIPT Program, PSPS, EPSS, Gas Trans Upgrades and local hardening projects.
Sutter County Fire Department | AB 56 Meeting | 2023-03-30 | Met with Sutter County Fire Chief on AB 56 information in the First Responder Guide to Public Safety handout.
West Sacramento Fire Department | North Sac County AB 56 | 2023-03-30 | E‑mail to North Sac County Fire Chiefs with AB 56 materials and description of the program. Always discuss AB 56 materials when I have in person contact with Training Officers and Chief Officers.
Folsom Fire Department | North Sac County AB 56 | 2023-03-30 | E‑mail to North Sac County Fire Chiefs with AB 56 materials and description of the program. Always discuss AB 56 materials when I have in person contact with Training Officers and Chief Officers.
Sacramento Metropolitan Fire District | North Sac County AB 56 | 2023-03-30 | E‑mail to North Sac County Fire Chiefs with AB 56 materials and description of the program. Always discuss AB 56 materials when I have in person contact with Training Officers and Chief Officers.
California Department of Corrections and Rehabilitation‑ Folsom State Prison | North Sac County AB 56 | 2023-03-30 | E‑mail to North Sac County Fire Chiefs with AB 56 materials and description of the program. Always discuss AB 56 materials when I have in person contact with Training Officers and Chief Officers.
West Sacramento Fire Department | North Sac County AB 56 | 2023-03-30 | E‑mail to North Sac County Fire Chiefs with AB 56 materials and description of the program. Always discuss AB 56 materials when I have in person contact with Training Officers and Chief Officers.
Sacramento County Airport System Aircraft Rescue & Firefighting | North Sac County AB 56 | 2023-03-30 | E‑mail to North Sac County Fire Chiefs with AB 56 materials and description of the program. Always discuss AB 56 materials when I have in person contact with Training Officers and Chief Officer .
Benicia Fire Department | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Vacaville Fire Department | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Vallejo Fire Department | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Vacaville Fire Protection District | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Fairfield Fire Department | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
CAL FIRE ‑ Sonoma‑Lake‑Napa | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Suisun Fire Protection District | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Dixon Fire Department | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Suisun City Fire Department | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Cordelia Fire Protection District | Solano AB 56 | 2023-03-30 | AB 56 materials sent out in e‑mail followed up with zoom presentation
Manteca Fire Department | San Joaquin County Fire Chief's AB 56 Presentation/Mtg | 2023-04-05 | Presentenced AB 56 information at San Joaquin County Fire Chiefs Meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Collegeville Fire Protection District | San Joaquin County Fire Chief's AB 56 Presentation/Mtg | 2023-04-05 | Presentenced AB 56 information at San Joaquin County Fire Chiefs Meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Linden‑Peters Rural Fire Protection District | San Joaquin County Fire Chief's AB 56 Presentation/Mtg | 2023-04-05 | Presentenced AB 56 information at San Joaquin County Fire Chiefs Meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Stockton Fire Department | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Manteca Fire Department | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Collegeville Fire Protection District | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Lodi Fire Department | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Montezuma Fire Protection District | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Mokelumne Rural Fire District | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Linden‑Peters Rural Fire Protection District | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
San Joaquin County Sheriff's Department | San Joaquin County Fire Chief's April Mtg | 2023-04-05 | Professional Group Meeting
Calaveras County Sheriff's Department | CWSP Outreach with Law Enforcement | 2023-04-18 | CWSP – Outreach
California Highway Patrol ‑ Amador | CWSP Outreach with Law Enforcement | 2023-04-18 | CWSP – Outreach
Amador County Fire Protection District | AB 56 Presentation Mtg | 2023-04-18 | Contingency Plan Meeting – AB 56
City of Alameda Fire Department | ALCO Fire Chiefs Meeting | 2023-04-19 | Contingency Plan Meeting – AB 56
Hayward Fire Department | ALCO Fire Chiefs Meeting | 2023-04-19 | Contingency Plan Meeting – AB 56
Alameda County Fire Department | ALCO Fire Chiefs Meeting | 2023-04-19 | Contingency Plan Meeting – AB 56
Fremont Fire Department | ALCO Fire Chiefs Meeting | 2023-04-19 | Contingency Plan Meeting – AB 56
Berkeley Fire Department | ALCO Fire Chiefs Meeting | 2023-04-19 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Santa Clara | ALCO Fire Chiefs Meeting | 2023-04-19 | Contingency Plan Meeting – AB 56
Livermore‑Pleasanton Fire Department | ALCO Fire Chiefs Meeting | 2023-04-19 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Sonoma‑Lake‑Napa | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
California Department of Rehabilitation and Corrections ‑ Medical Facility | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Benicia Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Dixon Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Suisun City Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Fairfield Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Rio Vista Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Solano Community College ‑ Fire Academy | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Suisun City Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Vacaville Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Vallejo Fire Department | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
Vacaville Fire Protection District | Solano Co Training officers AB 56 | 2023-04-20 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Madera‑Mariposa‑Merced | Madera & Merced County AB 56 Meeting | 2023-04-24 | Met with Madera and Merced Counties Fire Chief's to review and discuss the AB 56 information in the First Responder Guide to Public Safety Handout, which was mailed to them the week prior. The digital version (pdf) was also e‑mailed out with the same material.
San Quentin State Prison Fire Department | AB 56 Meeting | 2023-04-26 | Met with the San Quentin Fire Department which included the AB 56 information in the First Responder Guide to Public Safety handout. I also e‑mailed the PDF version of the handout and delivered a hard copy in person.
Oakland Fire Department | ALCO TOs Meeting ‑ April | 2023-04-26 | This meeting was the Alameda County Fire Departments Training Officers monthly meeting.
Fremont Fire Department | ALCO TOs Meeting ‑ April | 2023-04-26 | This meeting was the Alameda County Fire Departments Training Officers monthly meeting.
Hayward Fire Department | ALCO TOs Meeting ‑ April | 2023-04-26 | This meeting was the Alameda County Fire Departments Training Officers monthly meeting.
Berkeley Fire Department | ALCO TOs Meeting ‑ April | 2023-04-26 | This meeting was the Alameda County Fire Departments Training Officers monthly meeting.
CHABOT COLLEGE | ALCO TOs Meeting ‑ April | 2023-04-26 | This meeting was the Alameda County Fire Departments Training Officers monthly meeting.
Amtrak | ALCO TOs Meeting ‑ April | 2023-04-26 | This meeting was the Alameda County Fire Departments Training Officers monthly meeting.
Waterloo – Morada Rural Fire Protection District | San Joaquin County OES Quarterly Stakeholders Meeting | 2023-04-26 | Professional Group Meeting
Stockton Fire Department | San Joaquin County OES Quarterly Stakeholders Meeting | 2023-04-26 | Professional Group Meeting
Lodi Fire Department | San Joaquin County OES Quarterly Stakeholders Meeting | 2023-04-26 | Professional Group Meeting
State of California Governor’s Office of Emergency Services (CAL OES) | San Joaquin County OES Quarterly Stakeholders Meeting | 2023-04-26 | Professional Group Meeting
San Joaquin County Office of Emergency Services | San Joaquin County OES Quarterly Stakeholders Meeting | 2023-04-26 | Professional Group Meeting
Kings County Fire Department | AB 56 compliant Contingency Planning meeting | 2023-04-27 | Contingency Planning with Kings County Fire Chief Dan Lynch. Mailed PDF of First responder Guide and discussed First responder workshops, Storage Facility at Gill Ranch, and concurrent events.
Barstow Fire Protection District ‑ City of Barstow Fire Department | San Bernardino Co Fire Chiefs Mtg | 2023-04-27 | During the meeting was able to review GERP and Concurrent PSPS event emergency plans with Fire Dept. Copy of GERP and other regulations was mailed to individual fire chiefs.
Apple Valley Fire Protection District | San Bernardino Co Fire Chiefs Mtg | 2023-04-27 | During the meeting was able to review GERP and Concurrent PSPS event emergency plans with Fire Dept. Copy of GERP and other regulations was mailed to individual fire chiefs.
Daggett Community Services District Fire Department | San Bernardino Co Fire Chiefs Mtg | 2023-04-27 | During the meeting was able to review GERP and Concurrent PSPS event emergency plans with Fire Dept. Copy of GERP and other regulations was mailed to individual fire chiefs.
San Bernardino County Fire Department | San Bernardino Co Fire Chiefs Mtg | 2023-04-27 | During the meeting was able to review GERP and Concurrent PSPS event emergency plans with Fire Dept. Copy of GERP and other regulations was mailed to individual fire chiefs.
Marine Corps Logistics Base Barstow Fire Department | San Bernardino Co Fire Chiefs Mtg | 2023-04-27 | During the meeting was able to review GERP and Concurrent PSPS event emergency plans with Fire Dept. Copy of GERP and other regulations was mailed to individual fire chiefs.
Firebaugh Fire Department | AB 56 Compliant Contingency Meeting | 2023-04-28 | Met with Chief Borboa, gave him the AB 56 ‑ 3 fold first responder guide, GERP, offered First Responder Workshop training. Will follow up to schedule FRWs for Firebaugh Fire Dept
Tuolumne County Office of Emergency Services | Tuolumne County Wildfire Preparedness Town Hall | 2023-04-29 | Staffed a table representing PG&E at the Tuolumne County Wildfire Preparedness Town Hall. Handed out CWSP related material to public and answered any questions they had related to Wildfire Safety and PG&E.
Tuolumne County Sheriff's Department | Tuolumne County Wildfire Preparedness Town Hall | 2023-04-29 | Staffed a table representing PG&E at the Tuolumne County Wildfire Preparedness Town Hall. Handed out CWSP related material to public and answered any questions they had related to Wildfire Safety and PG&E.
CAL FIRE ‑ Tuolumne‑Calaveras | Tuolumne County Wildfire Preparedness Town Hall | 2023-04-29 | Staffed a table representing PG&E at the Tuolumne County Wildfire Preparedness Town Hall. Handed out CWSP related material to public and answered any questions they had related to Wildfire Safety and PG&E.
U.S. Forest Service ‑ Stanislaus National Forest | Tuolumne County Wildfire Preparedness Town Hall | 2023-04-29 | Staffed a table representing PG&E at the Tuolumne County Wildfire Preparedness Town Hall. Handed out CWSP related material to public and answered any questions they had related to Wildfire Safety and PG&E.
Tuolumne Fire Safe Council | Tuolumne County Wildfire Preparedness Town Hall | 2023-04-29 | Staffed a table representing PG&E at the Tuolumne County Wildfire Preparedness Town Hall. Handed out CWSP related material to public and answered any questions they had related to Wildfire Safety and PG&E.
Thornton Rural Fire Protection District | AB 56 Presentation Meeting | 2023-05-03 | Provided AB 56 Presentation slide handout along with required guide at the station to personnel present. Also talked about concurrent emergencies and response.
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Liberty Rural County Fire Protection District | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Lodi Fire Department | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Montezuma Fire Protection District | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Stockton Fire Department | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Manteca Fire Department | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chiefs Meeting | 2023-05-03 | Advised group of upcoming trainings, seminars, and FRWs scheduled and offered additional trainings to all.
Albany Fire Department | AB 56 Meeting ‑ Albany Fire Department | 2023-05-05 | On Friday, May 5, 2023, I Met with Captain James Berry and Captain Tim Smysen regarding AB 56. Meeting occurred at the Albany Fire Station/HQ located at 1000 San Pablo Ave, Albany, CA. 94706.
Camp Parks Fire And Emergency Services | AB 56 Meeting ‑ Camp Parks Fire and Emergency Services | 2023-05-05 | On Friday, May 5, 2023, I met with Captain Blaise Turcotte at Camp Parks located at: 1001 12th, Street, Dublin, CA 94568. (925) 875 4902
Piedmont Fire Department | AB 56 Meeting ‑ Piedmont Fire Department | 2023-05-05 | Contingency Plan Meeting ‑ AB 56
CAL FIRE ‑ Lassen‑Modoc‑Plumas | AB 56 Meeting with CAL FIRE Lassen‑Modoc Unit Chief | 2023-05-05 | AB 56 Compliance meeting with Chief Scott Packwood while attending the 2023 SPI Cooperators Meeting in the Tehama‑Glenn Unit.
Suisun City Public Works | Suisun City PG&E Gov Forum | 2023-05-08 | CWSP ‑ Outreach
City of Suisun City Administrative Office | Suisun City PG&E Gov Forum | 2023-05-08 | CWSP ‑ Outreach
Suisun City Fire Department | Suisun City PG&E Gov Forum | 2023-05-08 | CWSP ‑ Outreach
Suisun City Police Department | Suisun City PG&E Gov Forum | 2023-05-08 | CWSP ‑ Outreach
American Red Cross | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Monterey County Regional Fire District | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
CAL FIRE ‑ San Benito‑Monterey | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
United States Forest Service‑ Los Padres | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Monterey County Health Department | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Marina Fire Department | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Monterey County 9‑1‑1 Emergency Communications | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Greenfield Fire Department | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Presidio of Monterey‑Fire Department | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Salinas Fire Department | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Seaside Fire Department | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Monterey Fire Department | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
North County Fire Protection District of Monterey County | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Pacific Gas & Electric Central Coast Division | Monterey County Fire Chiefs Meeting | 2023-05-08 | Chief Gutierrez coordinated discussion on gas related regulatory workshop, EPPS Posture and upcoming webinars.
Fowler Fire Department | AB 56 Compliance Contingency Planning Meeting | 2023-05-09 | Contingency Planning for gas emergencies with New Fire Chief for Fowler Fire Dept, Dustin Hail. Shared trifold first responder guide, GERP, and Gas emergency check list.
North Central Fire District | AB 56 Contingency Meeting | 2023-05-09 | Met with Chief Tim Henry, shared tri fold first responder guide, GERP, and Gas safety checklist. Plan to schedule FRWs or other training this year.
CAL FIRE ‑ Mendocino | Mendocino County Fire Chiefs Mtg: AB 56 | 2023-05-10 | Discussed AB 56 and response support available from PG&E. I hand delivered the trifold First Responders Guide to Public Safety to the remaining 2 Fire Chiefs. All other departments had been done previously. PDF versions were e‑mailed as well.
Anderson Valley Fire Protection District | Mendocino County Fire Chiefs Mtg: AB 56 | 2023-05-10 | Discussed AB 56 and response support available from PG&E. I hand delivered the trifold First Responders Guide to Public Safety to the remaining 2 Fire Chiefs. All other departments had been done previously. PDF versions were e‑mailed as well.
San Francisco Department of Emergency Management | SFDEM After Action Review (AAR) for Extended Power Outage | 2023-05-10 | Please join us on Wednesday, May 10, from 9:30am‑11am for an AAR regarding the extended power outages that occurred in April. Below is a link to a feedback survey for the Extended Power Outage April 2023 activation: https://www.surveymonkey.com/r/PowerOutageApril2023Feedback Please fill out the survey no later than noon on Tuesday. The purpose of this survey is to capture initial thoughts on the activation. Discussions on how the activation reflected FEMA core capabilities will be discussed in our AAR.
CAL FIRE ‑ Siskiyou | AB 56 Meeting ‑ Siskiyou | 2023-05-11 | Meeting with Cal Fire Siskiyou Battalion Chief and station staff regarding AB 56 and gas pipeline response. The 1st responder safety handout was sent by e‑mail.
Burney Fire Protection District | AB 56 Meeting with Burney Fire Protection District | 2023-05-11 | AB 56 Meeting held at the Burney Fire Protection District Station #1 with Chief Bob May and Fire Captain Courtney Hall
Bureau of Land Management ‑ Modoc | AB 56 Meeting with Modoc, Applegate District BLM Chief | 2023-05-11 | AB 56 Meeting with BLM Chief John Toomey of the BLM Applegate District Office.
Jackson Fire Department | AB 56 Presentation Meeting | 2023-05-11 | AB 56 Presentation Meeting with Jackson City Fire. Presented AB 56 handout with presentation.
Denair Fire Protection District | Denair Fire Protection District AB 56 Outreach | 2023-05-11 | In person meeting, AB 56 outreach. Handed out material and information during meeting.
Keyes Fire Protection District | Keyes Fire Protection District AB 56 Outreach | 2023-05-11 | In person meeting with Keyes FD. Covered AB 56 requirements, handed out materials.
Mountain View Fire Protection District | Mountain View Fire Protection District AB 56 Outreach | 2023-05-11 | In person AB 56 delivery of compliance material to provide information on gas related emergency response and coordination.
Newman Fire Protection District | Newman Fire Protection District AB 56 Outreach | 2023-05-11 | In person meeting, handed out material related to AB 56 compliance.
San Bernardino County Fire Department | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
Newberry Springs Community Services District Fire Department | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
Naval Air Weapons Base China Lake Federal Fire Department | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
Victorville Fire Department | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
California City Fire Department | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
Chino Valley Fire District | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
Big Bear Fire Department | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
Edwards Air Force Base Federal Fire Department | San Bernardino Co Training Officers | 2023-05-11 | Meeting in San Bernardino to discuss PG&E GERP and upcoming fire season. Material also mailed to Chiefs through US Postage
Turlock Rural Fire Protection District | Turlock Rural Fire Protection District AB 56 Outreach | 2023-05-11 | In person meeting discussing AB 56 compliance. Handed out material and information.
Westport Fire Protection District | Westport Fire Protection District AB 56 Outreach | 2023-05-11 | In person meeting discussing AB 56 compliance. Handed out material and information, discussed future FRW training.
Defense Logistics Agency Fire Department | Defense Logistics Agency Fire Department AB 56 E‑mail | 2023-05-12 | E‑mails to Defense Logistics Agency Fire Chief's (2) regarding AB 56 information in the First Responder Guide to Public Safety Handbook and certain Gas FRW slides. Two e‑mails sent to different Fire Chiefs (5/12/23 & 5/23/23).
Solano County Office of Emergency Services | Solano County Fire Safe | 2023-05-15 | CWSP ‑ Outreach
Vacaville Fire Protection District | Solano County Fire Safe | 2023-05-15 | CWSP ‑ Outreach
California Office of Emergency Services ‑ Yolo County | Solano County Fire Safe | 2023-05-15 | CWSP ‑ Outreach
CAL FIRE ‑ Sonoma‑Lake‑Napa | Solano County Fire Safe | 2023-05-15 | CWSP ‑ Outreach
Fairfield Fire Department | Solano County Fire Safe | 2023-05-15 | CWSP ‑ Outreach
Yocha Dehe Fire Department | Solano County Fire Safe | 2023-05-15 | CWSP ‑ Outreach
Coalinga Fire Department | AB 56 Contingency Meeting | 2023-05-17 | Discussed and shared First Responder tri‑fold guide, GERP, Gas safety check list and First Responder Workshops with Chief Greg Dupuis and BC Eric Beasley
Sanger Fire Department | AB 56_Sanger Contingency Planning | 2023-05-23 | Contingency planning with Chief Tarascou, Delivered First responder guide, GERP and gas safety checklist. First responder workshop training offered.
Olivehurst Public Utility District Fire Department | AB 56 Meeting | 2023-05-23 | Met with Olivehurst Fire Chief Randy York about the AB 56 information in the First Responder Guide to Public Safety Handout which I gave to the Chief in the meeting
Wheatland Fire Authority | AB 56 Meeting | 2023-05-23 | Met with Wheatland Fire Chief which included the AB 56 information in the First Responder Guide to Public Safety handout which i gave to the Fire Chief in out meeting.
Selma Fire Department | AB 56 Selma FD planning meeting | 2023-05-23 | Contingency planning with Chief Robert Peterson, Delivered First responder guide, GERP and gas safety checklist. First responder workshop training offered.
MOTCO Federal Fire Department ‑ Concord | MOTCO Federal Fire Department AB 56 meeting | 2023-05-25 | Met with Deputy Chief Burl Danley and provided information on AB 56 Regulatory commitment. Discussed our Emergency Response Plans, Portal access, GERP and Gas and Electric Training.
Beale Air Force Base Fire Emergency Services | AB 56 Meeting | 2023-05-30 | Met with Beal Air Force Base Fire department which included the information in the First Responder Guide to Public Safety handout.
Meridian Fire Protection District | AB 56 Meeting | 2023-06-01 | E‑mailed the AB 56 to Meridian Fire Department Chief Jason Cooper.
Carlotta Community Services District | AB 56 Meeting ‑ Carlotta VFD | 2023-06-05 | AB 56 and gas transmission line discussion with Chief Todd Calvo. I e‑mailed him the 2023 gas 1st responder handout and set up an FRW in July.
CAL FIRE ‑ Santa Clara | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Sunnyvale Department of Public Safety | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Morgan Hill Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
San Jose Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Palo Alto Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Gilroy Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Santa Clara County Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Milpitas Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Mountain View Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
South Santa Clara County Fire District | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Santa Clara Fire Department | AB 56 Santa Clara County Fire Chiefs | 2023-06-07 | Met with the Fire Chiefs of Santa Clara County, which included the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to each Fire Chief prior to the meeting.
Napa State Hospital Fire Department | Napa State Hospital Fire Department AB 56 | 2023-06-07 | Discussed Gas Emergencies and Gas Emergency Response.
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Stockton Fire Department | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Montezuma Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Escalon Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Liberty Rural County Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Thornton Rural Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Clements Rural Fire Protection District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Lodi Fire Department | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Mokelumne Rural Fire District | San Joaquin County Fire Chief's June Mtg | 2023-06-07 | Professional Group Meeting
Atascadero Fire Department | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
Templeton Community Services District Fire Department | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
Porterville Fire Department | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
CAL FIRE ‑ Fresno‑Kings | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
CAL FIRE ‑ San Benito‑Monterey | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
Fresno Fire Department | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
San Luis Obispo County Office of Emergency Services | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
Santa Margarita Fire Protection District | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
Pacific Gas & Electric Central Coast Division | ICS 300 for a PSPS Event | 2023-06-19 | PSPS Outreach
City of Rancho Cordova Administrative Office | Rancho Cordova Local Gov Forum | 2023-06-20 | Support LGA outreach as SME for CWSP issues
Dixon Fire Department | Solano Co Fire Chiefs PG&E VERC Tour | 2023-06-21 | Tour of PG&E VERC
Suisun City Fire Department | Solano Co Fire Chiefs PG&E VERC Tour | 2023-06-21 | Tour of PG&E VERC
Cordelia Fire Protection District | Green Valley HOA PG&E Underground Open House | 2023-06-22 | Community meeting where I supported UG team as a SME to discuss improvements with PG&E and wildfire ignitions.
West Sacramento Fire Department | Sac County OES Exercise Alignment Meeting | 2023-06-27 | Exercise planning meeting.
Sacramento County Sheriff's Department | Sac County OES Exercise Alignment Meeting | 2023-06-27 | Exercise planning meeting.
Sacramento Metropolitan Fire District | Sac County OES Exercise Alignment Meeting | 2023-06-27 | Exercise planning meeting.
Sacramento Fire Department | Sac County OES Exercise Alignment Meeting | 2023-06-27 | Exercise planning meeting.
Berkeley Fire Department | ALCO TOs Meeting ‑ June | 2023-06-28 | Professional Group Meeting
City of Alameda Fire Department | ALCO TOs Meeting ‑ June | 2023-06-28 | Professional Group Meeting
Hayward Fire Department | ALCO TOs Meeting ‑ June | 2023-06-28 | Professional Group Meeting
Oakland Fire Department | ALCO TOs Meeting ‑ June | 2023-06-28 | Professional Group Meeting
Livermore‑Pleasanton Fire Department | ALCO TOs Meeting ‑ June | 2023-06-28 | Professional Group Meeting
CAL FIRE ‑ Santa Clara | ALCO TOs Meeting ‑ June | 2023-06-28 | Professional Group Meeting
Herald Fire Protection District | AB 56 | 2023-06-30 | Contingency Plan Meeting – AB 56
Travis Air Force Base Fire Department | AB 56 | 2023-06-30 | Contingency Plan Meeting – AB 56
Wilton Fire Protection District | AB 56 | 2023-06-30 | Contingency Plan Meeting – AB 56
Isleton Fire Department | AB 56 | 2023-06-30 | Contingency Plan Meeting – AB 56
Willow Oak Fire Protection District | AB 56 | 2023-06-30 | Contingency Plan Meeting – AB 56
Winters Fire Department | AB 56 | 2023-06-30 | Contingency Plan Meeting – AB 56
Sacramento Fire Department | AB 56 Sacramento FD | 2023-06-30 | Professional Group Meeting
El Dorado Hills Fire Department | El Dorado Disaster Council | 2023-07-06 | Attended the quarterly county wide disaster council meeting. Provided a presentation on PSS Agency Representative (AREP) coordination during large incidents and provide an overview of our WMP and CWSP initiatives.
El Dorado County Sheriff's Department | El Dorado Disaster Council | 2023-07-06 | Attended the quarterly county wide disaster council meeting. Provided a presentation on PSS AREP coordination during large incidents and provide an overview of our WMP and CWSP initiatives.
El Dorado County Office of Emergency Services | El Dorado Disaster Council | 2023-07-06 | Attended the quarterly county wide disaster council meeting. Provided a presentation on PSS AREP coordination during large incidents and provide an overview of our WMP and CWSP initiatives.
American Red Cross ‑ Gold Country | El Dorado Disaster Council | 2023-07-06 | Attended the quarterly county wide disaster council meeting. Provided a presentation on PSS AREP coordination during large incidents and provide an overview of our WMP and CWSP initiatives.
CAL FIRE ‑ Amador‑El Dorado | El Dorado Disaster Council | 2023-07-06 | Attended the quarterly county wide disaster council meeting. Provided a presentation on PSS AREP coordination during large incidents and provide an overview of our WMP and CWSP initiatives.
City of Morgan Hill Administrative Office | Morgan Hill City Follow Up | 2023-07-11 | Mark Turner, Mayor; Christina Ramos, CM; Edith Ramirez, Asst. CM; Shane Palsgrove, Police Chief; Chris Ghione, Public Works Dir.
National Aeronautics and Space Administration (NASA) Ames Fire Department | AB 56 NASA/AMES Fire Department | 2023-07-14 | Discussed AB 56, provided handout via e‑mail to BC Greg Thornton.
San Joaquin County Office of Emergency Services | San Joaquin Co OP Area Stakeholder Quarterly Mtg | 2023-07-26 | Quarterly meeting to share information, trainings, and projects with others in OP area.
Central County Fire Department | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
San Mateo County Department of Emergency Management | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
East Palo Alto Police Department | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
Menlo Park Fire Protection District | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
Redwood City San Carlos Fire Department | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
San Mateo County Department of Public Health | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
San Francisco Airport | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
American Red Cross Peninsula | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
City of Woodside Administrative Office | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
City of Half Moon Bay Administrative Office | San Mateo County Emergency Managers | 2023-07-27 | Professional Group Meeting
CAL FIRE ‑ San Mateo‑Santa Cruz | Filoli Prescribed Burn | 2023-07-31 | Cal‑Fire organized Prescribed Burn at the Filoli Estate. 5 Acres. SIPT Crew on standby for asset protection.
San Mateo County Fire | Filoli Prescribed Burn | 2023-07-31 | Cal‑Fire organized Prescribed Burn at the Filoli Estate. 5 Acres. SIPT Crew on standby for asset protection.
Linden‑Peters Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
Liberty Rural County Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
San Joaquin County Office of Emergency Services | San Joaquin County Fire Chiefs Assoc Mtg | 2023-08-02 | Professional Group Meeting
San Mateo Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
South San Francisco Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Foster City Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Redwood City Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Mateo County Sheriff's Office | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Millbrae Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Brisbane Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Menlo Park Fire Protection District | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Menlo Park Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Mateo County Public Safety Communications | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Woodside Fire Protection District | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Redwood City San Carlos Fire Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Mateo County Fire | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Mateo Consolidated Fire | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
East Palo Alto Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Belmont Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Colma Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
South San Francisco Fire Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Atherton Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Mateo County Administrative Office | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Pacifica Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
PG&E | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Bruno Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
North County Fire Authority | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
California Highway Patrol ‑ Redwood City | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Bruno Fire Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Hillsborough Police Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
San Mateo County Department of Emergency Management | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Central County Fire Department | San Mateo County Police Chiefs & Fire Chiefs | 2023-08-02 | Covered the following topics: EPSS Live Action Drill Video Live Action Drill Sept 13th at St.17 911 Standby Dispatch Info PG&E General Updates.
Los Banos Fire Department | Los Banos FD AB 56 | 2023-08-03 | A digital copy of the AB 56 First Responder Packet was e‑mailed on May 9, 2023, and July 25,2023 to Chief Paul Tualla. A meeting with Captain Brian Thompson was held on August 3, 2023. Two hard copies of the AB 56 First Responder Packet were also left with Captain Thompson.
San Mateo County Department of Emergency Management | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
City of Half Moon Bay Administrative Office | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
South San Francisco Fire Department | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
East Palo Alto Police Department | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
Redwood City San Carlos Fire Department | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
American Red Cross Peninsula | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
Menlo Park Fire Protection District | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
City of Woodside Administrative Office | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
San Francisco Airport | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
San Mateo County Department of Public Health | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
Central County Fire Department | San Mateo County Emergency Managers | 2023-08-24 | Professional Group Meeting
Winters Fire Department | Winters Gas Ex Walk Thru | 2023-08-28 | Walk thru with Winters FD
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Lodi Fire Department | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Thornton Rural Fire Protection District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Mokelumne Rural Fire District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Liberty Rural County Fire Protection District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
California Highway Patrol ‑ Stockton | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Montezuma Fire Protection District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Stockton Fire Department | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
San Joaquin County Office of Emergency Services | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chief's Assoc. mtg | 2023-09-06 | Updated group on Active 911 with McDonald Island, Homeless issue, PSPS, and FRW training opportunities.
Mule Creek State Prison Fire Department | Amador County Fire Chief's Assoc. Mtg | 2023-09-07 | Talked about VMP Planning and PG&E Assets in plan with notifications. Offered FRWs and advised of Gas Grass Roots training in 2024. Cooperators also in attendance were Red Cross, Amador Water, Local Agency Formation Commission (LAFCO), East Bay Municipal Utility District (EBMUD), and American Legion Ambulance.
Ione Fire Department | Amador County Fire Chief's Assoc. Mtg | 2023-09-07 | Talked about VMP Planning and PG&E Assets in plan with notifications. Offered FRWs and advised of Gas Grass Roots training in 2024. Cooperators also in attendance were Red Cross, Amador Water, LAFCO, EBMUD, and American Legion Ambulance.
Amador County Fire Protection District | Amador County Fire Chief's Assoc. Mtg | 2023-09-07 | Talked about VMP Planning and PG&E Assets in plan with notifications. Offered FRWs and advised of Gas Grass Roots training in 2024. Cooperators also in attendance were Red Cross, Amador Water, LAFCO, EBMUD, and American Legion Ambulance.
Sutter Creek Fire Protection District | Amador County Fire Chief's Assoc. Mtg | 2023-09-07 | Talked about VMP Planning and PG&E Assets in plan with notifications. Offered FRWs and advised of Gas Grass Roots training in 2024. Cooperators also in attendance were Red Cross, Amador Water, LAFCO, EBMUD, and American Legion Ambulance.
CAL FIRE ‑ Amador‑El Dorado | Amador County Fire Chief's Assoc. Mtg | 2023-09-07 | Talked about VMP Planning and PG&E Assets in plan with notifications. Offered FRWs and advised of Gas Grass Roots training in 2024. Cooperators also in attendance were Red Cross, Amador Water, LAFCO, EBMUD, and American Legion Ambulance.
Jackson Valley Fire Protection District | Amador County Fire Chief's Assoc. Mtg | 2023-09-07 | Talked about VMP Planning and PG&E Assets in plan with notifications. Offered FRWs and advised of Gas Grass Roots training in 2024. Cooperators also in attendance were Red Cross, Amador Water, LAFCO, EBMUD, and American Legion Ambulance.
Lockwood Fire Protection District | Amador County Fire Chief's Assoc. Mtg | 2023-09-07 | Talked about VMP Planning and PG&E Assets in plan with notifications. Offered FRWs and advised of Gas Grass Roots training in 2024. Cooperators also in attendance were Red Cross, Amador Water, LAFCO, EBMUD, and American Legion Ambulance.
Suisun City Fire Department | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Vacaville Fire Department | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Dixon Fire Department | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Vallejo Fire Department | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Suisun Fire Protection District | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Rio Vista Fire Department | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Vacaville Fire Protection District | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Solano County Office of Emergency Services | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
Fairfield Fire Department | Solano Co Fire Chiefs meeting | 2023-09-07 | Discussed hardening, ungrounding, decrease in ignitions, PSPS recap, and gas ex in winters, Oct 11.
State of California Governor’s Office of Emergency Services (CAL OES) | MARAC OES Region II, Q3 Meeting | 2023-09-13 | Quarterly OES Region II MARAC Meeting
Barstow Fire Protection District ‑ City of Barstow Fire Department | High Desert Pipeline Professional Group Meeting | 2023-09-20 | Professional Group Meeting
San Bernardino County Fire Department | High Desert Pipeline Professional Group Meeting | 2023-09-20 | Professional Group Meeting
Barstow Police Department | High Desert Pipeline Professional Group Meeting | 2023-09-20 | Professional Group Meeting
Apple Valley Fire Protection District | High Desert Pipeline Professional Group Meeting | 2023-09-21 | Professional Group Meeting
CAL FIRE ‑ San Bernardino | High Desert Pipeline Professional Group Meeting | 2023-09-21 | Professional Group Meeting
San Bernardino County Fire Department | High Desert Pipeline Professional Group Meeting | 2023-09-21 | Professional Group Meeting
Livermore‑Pleasanton Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Piedmont Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Alameda County Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Oakland Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Piedmont Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Hayward Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Berkeley Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
City of Alameda Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Fremont Fire Department | ALCO TO's Meeting | 2023-09-27 | Alameda County Training Officers Meeting
Woodside Fire Protection District | Sheep Camp Area 5 SFPUC Prescribed Burn | 2023-09-28 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on San Francisco Public Utilities Commission (SFPUC) land. Reviewed Gas Transmission Line locations and access.
CAL FIRE ‑ San Mateo‑Santa Cruz | Sheep Camp Area 5 SFPUC Prescribed Burn | 2023-09-28 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas Transmission Line locations and access.
San Mateo Consolidated Fire | Sheep Camp Area 5 SFPUC Prescribed Burn | 2023-09-28 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas Transmission Line locations and access.
La Honda Fire Brigade | Sheep Camp Area 5 SFPUC Prescribed Burn | 2023-09-28 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas Transmission Line locations and access.
Menlo Park Fire Protection District | Sheep Camp Area 5 SFPUC Prescribed Burn | 2023-09-28 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas Transmission Line locations and access.
San Joaquin County Office of Emergency Services | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Woodbridge Rural Fire Protection District | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Clements Rural Fire Protection District | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Lodi Fire Department | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Thornton Rural Fire Protection District | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Stockton Fire Department | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Montezuma Fire Protection District | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Ripon Consolidated Fire Protection District | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
French Camp‑McKinley Rural Fire Protection District | San Joaquin Co Fire Chiefs Assoc Mtg | 2023-10-04 | Gave the group information regarding FRWs, the Gas Grass Roots training available in 2024, and the Hydro exercise at Lake Pardee.
Santa Clara County Office of Emergency Management | Santa Clara County OA Coordination Call, IWE 10‑1 | 2023-10-05 | Santa Clara County Operational Area Inclement Weather Event 10‑1, conference call for heat event.
San Joaquin County Office of Emergency Services | DWR San Joaquin Co Preseason Flood Mtg | 2023-10-11 | You are invited to join local flood emergency response partners to discuss flood preparedness in our region, hosted by San Joaquin County Office of Emergency Services in partnership with DWR State‑Federal Flood Operations Center. These in‑person meetings provide regional and local updates on annual flood preparedness activities. The San Joaquin County Meeting will be held Wednesday October 11, from 9am‑11:30am at Micke Grove Park Memorial Auditorium, 11793 N Micke Grove Road, Lodi. The parking permit is attached to show at the gate. Agenda Topics include: Winter Weather Outlook DWR Flood Operations Updates Regional Updates Multi‑Agency Coordination Flood Fighting Methods and Materials Reservoir Status & Outlook Statewide Grants Preseason meetings include scheduled presentations from these agencies: National Weather Service California Governor’s Office of Emergency Services (Cal OES) Department of Water Resources California Conservation Corps CAL FIRE U.S. Army Corps of Engineers
Santa Clara County Emergency Managers Association | Santa Clara County Emergency Manager's Association | 2023-10-12 | Regular monthly meeting. Focus: Winter preparations., Anderson Reservoir seismic retrofit.
CAL FIRE ‑ San Mateo‑Santa Cruz | Pomponio Ranch Prescribed Burn | 2023-10-12 | Cal‑Fire organized Prescribed Burn at the Filoli Estate. 5 Acres. CIPT Crew on standby for asset protection.
Santa Clara County Fire Safe Council | Santa Clara County FireSafe Council Monthly Board Meeting | 2023-10-17 | Monthly Board of Directors meeting.
San Bruno Fire Department | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
Redwood City San Carlos Fire Department | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
San Mateo County Public Safety Communications | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
CAL FIRE ‑ San Mateo‑Santa Cruz | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
San Mateo County Department of Emergency Management | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
Woodside Fire Protection District | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
Menlo Park Fire Protection District | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
State of California Governor’s Office of Emergency Services (CAL OES) | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
San Francisco Fire Department | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
Central County Fire Department | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
Colma Fire Protection District | San Mateo County Operations Chiefs Meeting | 2023-10-19 | Report out on PG&E Storms. AB 56. Planned Joint Training
Fort Mojave Tribal Police Department | High Desert Pipeline Professional Group Meeting | 2023-10-26 | Professional Group Meeting
Bullhead City Police Department | High Desert Pipeline Professional Group Meeting | 2023-10-26 | Professional Group Meeting
Bullhead City Fire Department | High Desert Pipeline Professional Group Meeting | 2023-10-26 | Professional Group Meeting
California Highway Patrol ‑ Mojave | High Desert Pipeline Professional Group Meeting | 2023-10-26 | Professional Group Meeting
CAL FIRE ‑ San Mateo‑Santa Cruz | Pomponio Ranch Prescribed Burn #2 | 2023-10-31 | Cal‑Fire organized Prescribed Burn at the Pomonio Ranch on approx. 100 Acres.
PG&E | Pomponio Ranch Prescribed Burn #2 | 2023-10-31 | Cal‑Fire organized Prescribed Burn at the Pomonio Ranch on approx. 100 Acres.
Santa Clara County Emergency Managers Association | Santa Clara County Emergency Managers Association Monthly Meeting | 2023-11-09 | Regular monthly professional association meeting. This month's discussion was on winter preparedness.
Santa Clara County Fire Safe Council | Santa Clara County Fire Safe Council Monthly Meeting | 2023-11-21 | Regular monthly meeting.
San Bruno Fire Department | San Bruno Fire | 2023-12-12 | Discussed AB 56, Micro Gid in La Honda, New Fire Station. Reviewed Drainage Pipe Fire incident in San Bruno. Bart Training Incident.
La Honda Fire Brigade | San Bruno Fire | 2023-12-12 | Discussed AB 56, Micro Gid in La Honda, New Fire Station. Reviewed Drainage Pipe Fire incident in San Bruno. Bart Training Incident.
California Highway Patrol ‑ Redwood City | CHP Redwood City | 2023-12-13 | Met with New California Highway Patrol (CHP) Commander for Redwood City: Brett Cochran. Discussed collaborative relationships and expectations.
PG&E | CHP Redwood City | 2023-12-13 | Met with New CHP Commander for Redwood City: Brett Cochran. Discussed collaborative relationships and expectations.
City of Calistoga Administrative Office | Calistoga Parks and Rec (CRC Location) | 2023-12-20 | Discussion and meeting regarding additional CRC locations in Calistoga in the event of a PSPS or prolonged power outage.
Menlo Park Fire Protection District | Menlo Park Fire | 2023-12-20 | Met with Chief Calvert. Discussed Health and Wellness training
PG&E | Menlo Park Fire | 2023-12-20 | Met with Chief Calvert. Discussed Health and Wellness training
PG&E | US&R CATF3 | 2023-12-21 | Met with Chief Wurdinger and CATF3 Staff. Discussed Rescue Site, Response & Training
Menlo Park Fire Protection District | US&R CATF3 | 2023-12-21 | Met with Chief Wurdinger and CATF3 Staff. Discussed Rescue Site, Response & Training
Sutter County Fire Department | Sutter County Building Permit Escalation | 2024-01-02 | Sutter County Fire Chief reached out to me to discuss concerns of new non permitted structures under construction on PG&E transmission sub‑station in Rio OSO. Coordinated with PG&E personnel and Sutter County Fire and Sutter County Building Department
Ripon Consolidated Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Thornton Rural Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Lodi Fire Department | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Montezuma Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
South San Joaquin County Fire Authority | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Lathrop‑Manteca Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
French Camp‑McKinley Rural Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Clements Rural Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Stockton Fire Department | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Escalon Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Waterloo ‑ Morada Rural Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Mokelumne Rural Fire District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Liberty Rural County Fire Protection District | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
San Joaquin County Office of Emergency Services | AB 56 Presentation for San Joaquin Fire Chiefs | 2024-01-03 | Presented AB 56 information at San Joaquin County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Central County Fire Department | Central County Fire AB 56 | 2024-01-03 | Met with Chief Murphy to discuss AB 56‑related information.
Redwood City San Carlos Fire Department | Redwood San Carlos Fire AB 56 | 2024-01-03 | Met with Chief Pucci.
San Bruno Fire Department | San Bruno Fire Department | 2024-01-03 | Met with Fire Chief Ari Delay representing La Honda Fire and San Bruno Fire.
La Honda Fire Brigade | San Bruno Fire Department | 2024-01-03 | Met with Fire Chief Ari Delay representing La Honda Fire and San Bruno Fire.
San Mateo Consolidated Fire | San Mateo Consolidated AB 56 | 2024-01-03 | Met with Fire Chief Kent Thrasher.
Tehama County Sheriff's Department | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
CAL FIRE ‑ Lassen‑Modoc‑Plumas | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Butte County Office of Emergency Services | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Glenn County Office of Emergency Services | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Sierra County Office of Emergency Services | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Siskiyou County Office of Emergency Services | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
State of California Governor’s Office of Emergency Services (CAL OES) | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Modoc County Sheriff's Department | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Sutter County Sheriff's Department | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Lassen County Office of Emergency Services | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Trinity County Office of Emergency Services | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Chico Fire Department | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Yuba County Office of Emergency Services | MARAC 111 Meeting | 2024-01-03 | Professional Group Meeting
Clements Rural Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Escalon Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Lodi Fire Department | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Liberty Rural County Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Thornton Rural Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
South San Joaquin County Fire Authority | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Mokelumne Rural Fire District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Montezuma Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Stockton Fire Department | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
San Joaquin County Office of Emergency Services | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Farmington Fire Protection District | San Joaquin County Fire Chief's Mtg | 2024-01-03 | Monthly Fire Chief's Meeting discussing upcoming Gas Grass Roots Training, FRW needs and training, and undergrounding electric. AB 56 presentation was also completed with Power Point handout and First Responder Guide to Public Safety brochure. AB 56 records done separately from Chiefs mtg.
Amador County Fire Protection District | AB 56 Presentation for Amador County Fire Chiefs | 2024-01-04 | Presented AB 56 information at Amador County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Sutter Creek Fire Protection District | AB 56 Presentation for Amador County Fire Chiefs | 2024-01-04 | Presented AB 56 information at Amador County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
CAL FIRE ‑ Amador‑El Dorado | AB 56 Presentation for Amador County Fire Chiefs | 2024-01-04 | Presented AB 56 information at Amador County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Ione Fire Department | AB 56 Presentation for Amador County Fire Chiefs | 2024-01-04 | Presented AB 56 information at Amador County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Jackson Valley Fire Protection District | AB 56 Presentation for Amador County Fire Chiefs | 2024-01-04 | Presented AB 56 information at Amador County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Colma Fire Protection District | Colma Fire District AB 56 | 2024-01-04 | Met with Acting Captain Paramedic Whitsitt to discuss AB 56‑related information and training.
Menlo Park Fire Protection District | Menlo Park Fire AB 56 | 2024-01-04 | Met with Battalion Chief Ken Babcock to discuss AB 56‑related information.
North County Fire Authority | North County Fire Authority AB 56 | 2024-01-04 | Met with Deputy Chief Abelson to discuss AB 56‑related information, 911 Standby and training.
CAL FIRE ‑ San Mateo‑Santa Cruz | San Mateo County / Coast Side Fire AB 56 | 2024-01-04 | Met with Battalion Chief Bob Simmons & PIO Cecile Juliette . They represent San Mateo County Fire, Coast side Fire and Cal‑Fire CZU. All contracted to Cal‑Fire for services.
Coastside Fire Protection District | San Mateo County / Coast Side Fire AB 56 | 2024-01-04 | Met with Battalion Chief Bob Simmons & PIO Cecile Juliette . They represent San Mateo County Fire, Coast side Fire and Cal‑Fire CZU. All contracted to Cal‑Fire for services.
San Mateo County Fire | San Mateo County / Coast Side Fire AB 56 | 2024-01-04 | Met with Battalion Chief Bob Simmons & PIO Cecile Juliette . They represent San Mateo County Fire, Coast side Fire and Cal‑Fire CZU. All contracted to Cal‑Fire for services.
South San Francisco Fire Department | South San Francisco Fire AB 56 | 2024-01-04 | Met with Chief Metch to discuss AB 56‑related information.
Woodside Fire Protection District | Woodside Fire District AB 56 | 2024-01-04 | Met with Fire Chief Tom Cuschier at the admin building to discuss AB 56‑related information. Also met with Fire Marshal to discuss emergency evacuation routes.
Jackson Valley Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ Billing Operations Support (BOS) Chambers. Additional FRW needs?
Sutter Creek Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ BOS Chambers. Additional FRW needs?
CAL FIRE ‑ Amador‑El Dorado | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ BOS Chambers. Additional FRW needs?
Amador County Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ BOS Chambers. Additional FRW needs?
Amador County Sheriff's Office | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ BOS Chambers. Additional FRW needs?
Ione Fire Department | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ BOS Chambers. Additional FRW needs?
California Highway Patrol ‑ Amador | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ BOS Chambers. Additional FRW needs?
Lockwood Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-01-04 | AB 56 Presentation to those fire agencies with gas. Discussed ‑ Gas Grass Roots Live Active Drill request from Amador agencies. Scheduled FRWs on Jan 17 & 18 @ BOS Chambers. Additional FRW needs?
Santa Clara County Office of Emergency Management | Santa Clara County OA IWE#1, Meeting #1 | 2024-01-08 | Inclement weather event planning meeting for Santa Clara County Operational Area.
Calaveras Consolidated Fire Protection District | Calaveras County Fire Chiefs Meeting/AB 56 Outreach | 2024-01-10 | AB 56 outreach, handed out materials in person and discussed gas related emergency response.
CAL FIRE ‑ Tuolumne‑Calaveras | Calaveras County Fire Chiefs Meeting/AB 56 Outreach | 2024-01-10 | AB 56 outreach, handed out materials in person and discussed gas related emergency response.
San Andreas Fire Protection District | Calaveras County Fire Chiefs Meeting/AB 56 Outreach | 2024-01-10 | AB 56 outreach, handed out materials in person and discussed gas related emergency response.
Orland Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Ord Bend Community Services District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Elk Creek Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Artois Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Capay Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Kanawha Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Hamilton City Fire Department | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Bayliss Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Butte City Fire Department | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Tehama‑Glenn | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Willows City Fire Department | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Willows Rural Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Glenn ‑ Codora Fire Protection District | Glenn County Fire Chiefs Meeting | 2024-01-10 | Contingency Plan Meeting – AB 56
Yuba City Fire Department | AB 56 Yuba City | 2024-01-11 | Meeting with Yuba City Fire Department which included the AB 56 information in the First Responder Guide to Public Safety handout which I delivered at the meeting.
Red Bluff Fire Department | Red Bluff Fire Department | 2024-01-11 | Met Matt at Red Bluff training facility. Discussed AB 56, gave him pamphlet and scheduled 3 FRWs
Santa Clara County Fire Safe Council | Santa Clara County Fire Safe Council Finance Committee | 2024-01-11 | Professional Group Meeting
U.S. Forest Service ‑ Mendocino National Forest | Tehama‑Glenn County Fire Safe Council Meeting | 2024-01-11 | Fire Safe Council meeting. Discussed PG&E Grants and they agreed to have a PG&E veg person assigned to the council in the future
Santa Clara County Office of Emergency Management | Santa Clara County OA IWE#1, Meeting #2 | 2024-01-11 | Inclement weather event planning meeting for Santa Clara County Operational Area.
Marysville Fire Department | AB 56 Marysville | 2024-01-12 | Meeting with Marysville Fire Department on the AB 56 information in the Public Safety Handbook which I gave to them in my presentation.
San Francisco Fire Department | San Francisco Fire Department ‑ AB 56 | 2024-01-12 | Contingency Plan Meeting – AB 56
Santa Clara County Fire Safe Council | Santa Clara County Fire Safe Council January 2024 Meeting | 2024-01-16 | Regular monthly board meeting.
East Bay Regional Park District Fire Department | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
Fremont Fire Department | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
CAL FIRE ‑ Santa Clara | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
Hayward Fire Department | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
Livermore‑Pleasanton Fire Department | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
Berkeley Fire Department | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
Alameda County Fire Department | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
PG&E | AB 56 ALCO TOs Meeting ‑ January | 2024-01-17 | Alameda County's Training Officers Monthly Meeting.
Anderson Fire Protection District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Burney Fire Protection District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
CAL FIRE ‑ Shasta‑Trinity | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Cottonwood Fire Protection District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Fall River Valley Fire Protection District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Millville Fire Protection District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Mountain Gate Community Services Fire District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Redding Fire Department | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Shasta Lake Fire Protection District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Shasta CSD/Shasta Fire Protection District | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Shasta College Fire Department | AB 56 Meeting with Shasta County Fire Chief's Association | 2024-01-18 | See attached attendance roster and agenda.
Crockett‑Carquinez Fire Protection District | Crockett Carquinez Fire Protection District AB 56 meeting | 2024-01-18 | Contingency Plan Meeting ‑ AB 56
Rodeo‑Hercules Fire Protection District | Rodeo Hercules Fire Protection District AB 56 meeting | 2024-01-18 | Contingency Plan Meeting ‑ AB 56
CAL FIRE ‑ Fresno‑Kings | CAL FIRE Fresno Kings Unit AB 56 meeting | 2024-01-19 | Contingency Planning meeting held with Chief Andy Cosentino and Chief Jose Medina. AB 56 covered as well as emergency response contingency planning. GERP was discussed and levels of activation and shared by e‑mail. 508_2024_First Responder Packet sent by e‑mail and United States Postal Service (USPS) to Chief Dustin Hail, Chief Cosentino and Chief Medina. FRWs will be presented in Spring.
Corning City Fire Department | Corning City Fire Department | 2024-01-19 | Met with Chief. Discussed all AB 56 compliance issues and provided him the tri‑fold
Firebaugh Fire Department | Firebaugh Contingency Planning meeting ‑ AB 56 | 2024-01-19 | Discussion with Chief Officer ‑ Contingency Planning meeting held with Battalion Chief Hector Marin. AB 56 covered as well as GERP and levels of response from PG&E. Shared via e‑mail with Chief Michael Molina and Chief Marin the GERP and the 508_2024_First Responder Packet. Chief Michael Molina mailed First responder packet USPS. FRW is planned for March.
Fowler Fire Department | Fowler FD AB 56 meeting | 2024-01-19 | Contingency Planning meeting held with Chief Andy Cosentino and Chief Jose Medina. AB 56 covered as well as emergency response contingency planning. GERP was discussed and levels of activation and shared by e‑mail. 508_2024_First Responder Packet sent by e‑mail and USPS to Chief Dustin Hail, Chief Cosentino and Chief Medina. FRWs will be presented in Spring.
Fresno County Fire Protection District | Fresno Fire Protection Contingency AB 56 meeting | 2024-01-19 | Contingency Planning meeting held with Chief Andy Cosentino and Chief Jose Medina. AB 56 covered as well as emergency response contingency planning. GERP was discussed and levels of activation and shared by e‑mail. 508_2024_First Responder Packet sent by e‑mail and USPS to Chief Dustin Hail, Chief Cosentino and Chief Medina. FRWs will be presented in Spring.
Red Bluff Fire Department | Red Bluff Fire Department | 2024-01-22 | Met at Training facility to schedule FRW classes and assistance with training grounds
Sanger Fire Department | Sanger Fire Dept Contingency Planning | 2024-01-23 | Discussion with Chief Officer ‑ Contingency Planning meeting held with Chief Training Officer Todd Wilson AB 56 covered with Chief Tarascou , Chief Daniel as well as GERP and levels of response from PG&E. Shared via e‑mail with Chief Officers the GERP and the 508_2024_First Responder Packet. Chief Tarascou was mailed First responder packet USPS. FRWs are planned for April.
El Dorado County Office of Emergency Services | El dorado County OES Hazard Mitigation Plan Meeting | 2024-01-23 | Meeting with El Dorado OES to review and update the county Hazard Mitigation Plan for utility
Victorville Fire Department | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Daggett Community Services District Fire Department | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Newberry Springs Community Services District Fire Department | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Apple Valley Fire Protection District | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Barstow Fire Protection District ‑ City of Barstow Fire Department | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
CAL FIRE ‑ San Bernardino | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
San Bernardino County Fire Department | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Edwards Air Force Base Federal Fire Department | San Bernardino County Fire Chiefs Mtg | 2024-01-24 | Presented AB 56 information at San Bernardino County Fire Chiefs Meeting for those Chiefs/Departments present at the meeting. AB 56 information in the First Responder Guide to Public Safety handout and select gas slides from the Gas FRW slide deck were handed out and discussed to those listed.
Garden Valley Fire Protection District | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
El Dorado County Office of Emergency Services | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
El Dorado Hills Fire Department | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
El Dorado County Fire Protection District | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
El Dorado County Fire District | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
Rescue Fire Department | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
Georgetown Fire Protection District | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
Mosquito Fire Protection District | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
CAL FIRE ‑ Amador‑El Dorado | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
Georgetown Fire Protection District | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
El Dorado County Fire Safe Council | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
Emergency Medical Services Authority ‑ El Dorado County | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
El Dorado National Forest ‑ Fire Department | El Dorado County Fire Chiefs Meeting | 2024-01-24 | Attended the El Dorado County Fire Chiefs Association bi‑monthly meeting and provided a report of PG&E PSS activities.
Boulder Creek Fire Protection District | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ San Mateo‑Santa Cruz | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
Santa Cruz Fire Department | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
Scotts Valley Fire Protection District | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
Zayante Fire Protection District | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
Felton Fire Protection District | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
Central Fire Protection District of Santa Cruz County | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
Watsonville Fire Department | AB 56 Meeting with Santa Cruz County Fire Chief's Association | 2024-01-25 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ Tehama‑Glenn | Red Bluff ‑ Cal Fire ‑ Fire Grounds | 2024-01-25 | Met to discuss planning for Tehama County Fire Grounds
Red Bluff Fire Department | Red Bluff ‑ Cal Fire ‑ Fire Grounds | 2024-01-25 | Met to discuss planning for Tehama County Fire Grounds
Town of Los Altos Hills Administrative Office | CWSP Los Altos Hill County Fire District Winter Safety Preparation | 2024-01-27 | CWSP – Outreach
Los Altos Hills County Fire District | CWSP Los Altos Hill County Fire District Winter Safety Preparation | 2024-01-27 | CWSP – Outreach
Jackson Fire Department | AB 56 Meeting | 2024-01-30 | Meeting with Jackson City Fire personnel which included AB 56 information in the First Responder Guide to Public Safety handout which I also e‑mailed to Chief Fishback the same day.
Vallejo Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Benicia Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Vacaville Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Suisun City Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Suisun Fire Protection District | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Dixon Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Travis Air Force Base Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Rio Vista Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Fairfield Fire Department | AB 56 Solano County Fire Chiefs Meeting | 2024-02-01 | Meeting to discuss the PG&E PSS and SIPT Program. Discussion on FRW, gas drills, supporting TTX and full‑scale exercises.
Happy Valley Fire Protection District | Happy Valley Fire Protection District | 2024-02-01 | Met with Garrett at his fire station. Discussed AB 56 compliance and provided him the AB 56 folder
CAL FIRE ‑ Sonoma‑Lake‑Napa | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
Napa County EMS Agency | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
Napa County Fire | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
Calistoga Fire Department | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
NAPA CITY OF | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
Saint Helena Fire Department | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
Napa County Fire Department | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
Napa State Hospital Fire Department | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
COUNTY OF NAPA | Napa County Fire Agencies AB 56 | 2024-02-01 | Contingency Plan Meeting – AB 56
Stanislaus Consolidated Fire Protection District | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
Modesto Fire Department | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
Hughson Fire Department | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
Oakdale Fire Department | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
Turlock Fire Department and Emergency Services | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
Patterson Fire Department | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
West Stanislaus Fire Protection District | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
Woodland Avenue Fire Protection District | Stanislaus County Fire Chiefs Meeting/AB 56 Outreach | 2024-02-01 | Completed in person AB 56 outreach. Handed out materials to Fire Chiefs.
U.S. Forest Service ‑ Pacific Southwest Region, North Operations | U.S. Forest Service ‑ Pacific Southwest Region, Northern Operations | 2024-02-01 | Weaver and I met with Anthony at his office. Discussed all AB 56 issues and provided him AB 56 folder
United States Bureau of Land Management ‑ Redding | United States Bureau of Land Management ‑ Redding | 2024-02-01 | Met with Garrett at BLM office. Discussed all AB 56 issues and provided him the AB 56 folder.
Napa County Fire | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
CAL FIRE ‑ Sonoma‑Lake‑Napa | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Napa Fire Department | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Calistoga Fire Department | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Saint Helena Fire Department | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
American Canyon Fire Department | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Napa State Hospital Fire Department | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Deer Park Volunteer Fire Department | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Angwin Volunteer Fire Department | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Dry Creek‑Lokoya Fire Dept | Napa County AB 56 | 2024-02-01 | In person meeting with the Napa County Fire Agency Chiefs to go over the AB 56 protocol
Fig Garden Fire District | Fig Garden AB 56 Contingency Plan | 2024-02-05 | Meeting with Emergency Preparedness Officer for Fresno City Fire – Chief Guynn Scheduling an additional meeting to discuss training dates with Chiefs Alcorn and Chief Chew. First Responder Guide mailed USPS and shared in an e‑mail with the GERP.
Fresno Fire Department | Fresno City Fire Contingency Planning Meeting | 2024-02-05 | Meeting with Emergency Preparedness Officer for Fresno City Fire – Chief Guynn Scheduling an additional meeting to discuss training dates with Chiefs Alcorn and Chief Chew. First Responder Guide mailed USPS and shared in an e‑mail with the GERP.
Kings County Fire Department | Kings County Fire Dept AB 56 | 2024-02-05 | Held AB 56 contingency meeting and discussed training available and levels of response. Shared in an e‑mail emergency dispatch # and GERP. Mailed USPS First Responder Guide
Collegeville Fire Protection District | AB 56 Meeting | 2024-02-06 | Informational/notification e‑mail with Collegeville Fire Department which included the AB 56 information power point presentation and the First Responder Guide to Public Safety handout which was attached.
Defense Logistics Agency Fire Department | AB 56 Meeting | 2024-02-06 | Informational/notification e‑mail with Defense Logistics Agency Fire Department which included the AB 56 information power point presentation and the First Responder Guide to Public Safety handout which was attached.
Sacramento Fire Department | AB 56 Sacramento City FD | 2024-02-06 | Discussion about PSS program, SIPT Program, FRWs. Discussed AREP role, Training role and our work to support our hardening/undergrounding in support of risk mitigation.
Defense Logistics Agency Fire Department | AB 56 Meeting | 2024-02-07 | Met with new Defense Logistics Agency Fire Department personnel at the San Joaquin County OES ICS‑300 course and presented material. Material included the PowerPoint presentation handout and the "First Responder Guide to Public Safety" handout. Assist Chief expressed additional training (FRW) at later date.
Linden‑Peters Rural Fire Protection District | AB 56 Mtg | 2024-02-07 | Conducted AB 56 presentation to agencies that were not present at last month’s Chief's mtg. Chiefs were given PowerPoint presentation handout as well as the "First Responder Guide to Public Safety" handout.
Woodbridge Rural Fire Protection District | AB 56 Mtg | 2024-02-07 | Conducted AB 56 presentation to agencies that were not present at last month’s Chief's mtg. Chiefs were given PowerPoint presentation handout as well as the "First Responder Guide to Public Safety" handout.
Sacramento Police Department | AB 56 Sacramento Police Department | 2024-02-07 | Discussed AB 56, PSS program and FRW with Captain Stigerts
Milpitas Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
CAL FIRE ‑ Santa Clara | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Santa Clara County Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Sunnyvale Department of Public Safety | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Palo Alto Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Morgan Hill Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
South Santa Clara County Fire District | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Santa Clara Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
State of California Governor’s Office of Emergency Services (CAL OES) | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Mountain View Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Gilroy Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
San Jose Fire Department | AB 56 Santa Clara County Fire Chiefs | 2024-02-07 | Meeting with the Santa Clara County Fire Chiefs, which included the AB 56 information in the First Responder Guide to Public Safety pamphlet, which I provided both a hard copy at the meeting, as well as e‑mailing a pdf version prior to the meeting.
Amador County Sheriff's Office | Amador County Community Preparedness Mtg | 2024-02-07 | Amador County Community Preparedness Meeting hosted by Amador County Public Health Department. Quarterly meeting discussing community preparedness and lessons learned by different agencies.
Amador County Fire Protection District | Amador County Community Preparedness Mtg | 2024-02-07 | Amador County Community Preparedness Meeting hosted by Amador County Public Health Department. Quarterly meeting discussing community preparedness and lessons learned by different agencies.
Amador County Public Health Dept. | Amador County Community Preparedness Mtg | 2024-02-07 | Amador County Community Preparedness Meeting hosted by Amador County Public Health Department. Quarterly meeting discussing community preparedness and lessons learned by different agencies.
Linden‑Peters Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Clements Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Escalon Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Liberty Rural County Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
San Joaquin County Office of Emergency Services | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Montezuma Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-02-07 | Professional Group Meeting
Clovis Fire Department | Clovis Fire AB 56 Contingency meeting | 2024-02-09 | E‑mail sent to Chief Ekk and Chief OConnor and Chief Don Banta First Responder Guide and Gerp. Met in person with Chief Banta (Training Battalion Chief) and will plan to schedule training in early summer. USPS mailed First Responder Guide to Chief EKK ‑ Unit Chief
Arbuckle ‑ College City Fire Protection District | AB 56 Meeting‑Arbuckle | 2024-02-13 | Meeting with Arbuckle Fire Department Chief Casey Cox. Discussion included information in the First Responder Guide to Public Safety handout which i gave to the Chief at the meeting
Maxwell Fire Protection District | AB 56 Meeting‑Maxwell | 2024-02-13 | Meeting with Maxwell Fire Department Chief Kenny Cohen. Discussion included information in the First Responder Guide to Public Safety handout which i gave to the Chief at the meeting
Sacramento River Fire Protection District | AB 56 Meeting‑Sac River FPD | 2024-02-13 | Meeting with Sacramento River Fire Protection District Chief Jeff Winters. Discussion included information in the First Responder Guide to Public Safety handout which i gave to the Chief at the meeting
El Dorado County Administrative Office | El Dorado Office of Wildfire Prevention Meeting | 2024-02-13 | Meeting with the El Dorado County Office of Wildfire Prevention and Resilience. Discussed information sharing and focused work areas in El Dorado County to support wildfire prevention efforts.
Linda Fire Protection District | AB 56‑Linda/Marysville | 2024-02-14 | Meeting with Linda Fire Department Chief. Discussion included information in the First Responder Guide to Public Safety handout which i gave to the Chief at the meeting.
Marysville Fire Department | AB 56‑Linda/Marysville | 2024-02-14 | Meeting with Linda Fire Department Chief. Discussion included information in the First Responder Guide to Public Safety handout which i gave to the Chief at the meeting.
Wheatland Fire Authority | AB 56 Wheatland | 2024-02-14 | Meeting with Wheatland Fire Department Chief. Discussion included information in the First Responder Guide to Public Safety handout which I gave to the Chief at the meeting.
CAL FIRE ‑ Butte | CAL FIRE Butte AB 56 2024 | 2024-02-14 | CAL FIRE Butte Chief Officer Meeting covering CAL FIRE Butte, Butte County Fire Department, City of Gridley Fire, City of Biggs Fire, City of Oroville Fire, and Town of Paradise Fire Department.
Gridley Fire Department | CAL FIRE Butte AB 56 2024 | 2024-02-14 | CAL FIRE Butte Chief Officer Meeting covering CAL FIRE Butte, Butte County Fire Department, City of Gridley Fire, City of Biggs Fire, City of Oroville Fire, and Town of Paradise Fire Department.
Biggs Fire Department | CAL FIRE Butte AB 56 2024 | 2024-02-14 | CAL FIRE Butte Chief Officer Meeting covering CAL FIRE Butte, Butte County Fire Department, City of Gridley Fire, City of Biggs Fire, City of Oroville Fire, and Town of Paradise Fire Department.
Paradise Fire Department | CAL FIRE Butte AB 56 2024 | 2024-02-14 | CAL FIRE Butte Chief Officer Meeting covering CAL FIRE Butte, Butte County Fire Department, City of Gridley Fire, City of Biggs Fire, City of Oroville Fire, and Town of Paradise Fire Department.
Oroville Fire Department | CAL FIRE Butte AB 56 2024 | 2024-02-14 | CAL FIRE Butte Chief Officer Meeting covering CAL FIRE Butte, Butte County Fire Department, City of Gridley Fire, City of Biggs Fire, City of Oroville Fire, and Town of Paradise Fire Department.
Butte County Fire Department | CAL FIRE Butte AB 56 2024 | 2024-02-14 | CAL FIRE Butte Chief Officer Meeting covering CAL FIRE Butte, Butte County Fire Department, City of Gridley Fire, City of Biggs Fire, City of Oroville Fire, and Town of Paradise Fire Department.
Central Marin Fire Authority | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Mill Valley Fire Department | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Kentfield Fire Protection District | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Marin County Fire Department | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
San Rafael Fire Department | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Marinwood Fire Department | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Southern Marin Fire Protection District | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Tiburon Fire Protection District | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Novato Fire Protection District | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Ross Valley Fire Department | AB 56 Meeting | 2024-02-15 | Met with Marin County Fire Chiefs to discuss the Annual AB 56 Compliance information from the First Responder Guide to Public Safety handout which I handed out. I also included a Power Point presentation. covering gas emergencies, PG&E response and resources.
Santa Clara County Office of Emergency Management | Santa Clara County OA IWE#8, Meeting #1 | 2024-02-15 | Inclement weather event planning meeting for Santa Clara County Operational Area.
San Jose Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #8 | 2024-02-15 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #8.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #9 | 2024-02-18 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #9.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #10 | 2024-02-19 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #10.
Rotary Club of Morgan Hill | CWSP Morgan Hill Rotary | 2024-02-21 | Community presentation on preparing for outages.
Sutter County Fire Department | AB 56 Sutter County Fire | 2024-02-21 | Meeting with Sutter County Fire Department which included the AB 56 information in the First Responder Guide to Public Safety handout which I gave to the Chief at the meeting.
Auburn City Fire Department | AB 56 Meeting | 2024-02-22 | Meeting with Auburn City Chief to discuss and deliver AB 56 flyer.
South Placer Fire District | AB 56 Meeting | 2024-02-22 | Meeting with Chief Duerr to discuss and go over the AB 56 flyer.
Roseville Fire Department | AB 56 Meeting | 2024-02-22 | Meeting with Assistant Chief Lockner to discuss and go over the AB 56 flyer.
Paige Volunteer Fire Department | AB 56 Meeting | 2024-02-22 | Meeting with Chief Estes to discuss and go over the AB 56 flyer.
Placer County Fire Department | AB 56 Meeting | 2024-02-22 | Meeting with Chief Estes to discuss and go over the AB 56 flyer.
Rocklin Fire Department | AB 56 Meeting | 2024-02-22 | Meeting with Chief Williams to discuss and go over the AB 56 flyer.
Penryn Fire Protection District | AB 56 Meeting | 2024-02-22 | Meeting with Chief Gow to discuss and go over the AB 56 flyer.
Newcastle Fire Protection District | AB 56 Meeting | 2024-02-22 | Meeting with Chief Gow to discuss and go over the AB 56 flyer.
Placer Hills Fire Protection District | AB 56 Meeting | 2024-02-22 | Meeting with Chief Gow to discuss and go over the AB 56 flyer.
Menlo Park Fire Protection District | Menlo Park Fire | 2024-02-22 | Professional Group Meeting
Woodside Fire Protection District | Menlo Park Fire | 2024-02-22 | Professional Group Meeting
Redwood City San Carlos Fire Department | Menlo Park Fire | 2024-02-22 | Professional Group Meeting
San Mateo County Public Safety Communications | Menlo Park Fire | 2024-02-22 | Professional Group Meeting
Palo Alto Fire Department | Menlo Park Fire | 2024-02-22 | Professional Group Meeting
El Dorado Hills Fire Department | AB 56 El Dorado Hills Fire | 2024-02-29 | AB 56 Outreach with El Dorado Hills Fire Department. Deputy Chief Dave Brady and I reviewed the outreach materials together and discussed emergency response issues.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #11 | 2024-02-29 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #11.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #12 | 2024-03-01 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #12.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA IWE #12 Follow Up Call | 2024-03-01 | Follow meeting with Santa Clara County Office of Emergency Management Director Dana Reed, RE: Op Area Coordinating Call, Inclement Weather Event #12.
Bakersfield Fire Department | Bakersfield Fire Dept AB 56 | 2024-03-04 | Remote meeting with Training 3 ‑ Chad Burton Bakersfield Fire Dept. E‑mailed GERP, First Responder Packet and quick guide regarding Gas response levels with emergency information. 6 FRWs are scheduled in July for Bakersfield FD.
CAL FIRE ‑ Nevada‑Yuba‑Placer | AB 56‑NEU | 2024-03-05 | Meeting with Nevada County fire Chiefs Meeting which included the AB 56 information in the First Responder Guide to Public Safety handout that was distributed to the Fire Chiefs.
CAL FIRE ‑ San Benito‑Monterey | CAL FIRE BEU | 2024-03-05 | Meeting with CAL FIRE BEU Chief to discuss GERP, concurring events, PSPS and future training event. Handout was provided.
Farmington Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Stockton Fire Department | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Collegeville Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
San Joaquin County Office of Emergency Services | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Montezuma Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Escalon Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Linden‑Peters Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Liberty Rural County Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
San Joaquin County Sheriff's Department | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc Mtg | 2024-03-06 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs.
Woodside Fire Protection District | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
North County Fire Authority | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
Menlo Park Fire Protection District | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
Central County Fire Department | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
North County Fire Authority | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
CAL FIRE ‑ San Mateo‑Santa Cruz | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
San Mateo County Department of Emergency Management | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
South San Francisco Fire Department | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
San Mateo County Fire | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
Redwood City San Carlos Fire Department | San Mateo County Fire Chiefs | 2024-03-06 | Reviewed AB 56 & Handed out First Responder Guide, PG&E updates, Storm AAR, Dispatch & Communications issues.
Burbank‑Paradise Fire Protection District | AB 56 Outreach Burbank‑Paradise Fire Protection District | 2024-03-07 | In person delivery of AB 56 outreach material and discussed information contained in handouts.
Denair Fire Protection District | AB 56 Outreach Denair Fire Protection District | 2024-03-07 | In person delivery of AB 56 outreach material and discussed information contained in handouts.
Keyes Fire Protection District | AB 56 Outreach Keyes Fire Protection District | 2024-03-07 | In person delivery of AB 56 outreach material and discussed information contained in handouts.
Turlock Rural Fire Protection District | AB 56 Outreach Turlock Rural Fire Protection District | 2024-03-07 | In person delivery of AB 56 outreach material and discussed information contained in handouts.
Coalinga Fire Department | Coalinga Fire Dept AB 56 | 2024-03-07 | Meeting with Chief Rider. Discussed contingency planning and training. Planning to schedule 6 FRWs and Substation tour in April/May 2024. Sent by USPS first responder guide to Chief Dupois and e‑mailed PDF versions of GERP and First Responder Guide
Ceres Fire Department | Stanislaus Co. Fire Chiefs / AB 56 Outreach Meeting | 2024-03-07 | Contingency Plan Meeting – AB 56
Newman Fire Protection District | Stanislaus Co. Fire Chiefs / AB 56 Outreach Meeting | 2024-03-07 | Contingency Plan Meeting – AB 56
Salida Fire Protection District | Stanislaus Co. Fire Chiefs / AB 56 Outreach Meeting | 2024-03-07 | Contingency Plan Meeting – AB 56
Westport Fire Protection District | Stanislaus Co. Fire Chiefs / AB 56 Outreach Meeting | 2024-03-07 | Contingency Plan Meeting – AB 56
Amador County Sheriff's Office | Amador County Fire Chiefs Assoc Mtg | 2024-03-07 | Gas Grass Roots Live Active Drill confirmation with Amador agencies for week of April 22. Additional FRW needs?
Sutter Creek Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-03-07 | Gas Grass Roots Live Active Drill confirmation with Amador agencies for week of April 22. Additional FRW needs?
Jackson Valley Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-03-07 | Gas Grass Roots Live Active Drill confirmation with Amador agencies for week of April 22. Additional FRW needs?
Amador County Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-03-07 | Gas Grass Roots Live Active Drill confirmation with Amador agencies for week of April 22. Additional FRW needs?
CAL FIRE ‑ Amador‑El Dorado | Amador County Fire Chiefs Assoc Mtg | 2024-03-07 | Gas Grass Roots Live Active Drill confirmation with Amador agencies for week of April 22. Additional FRW needs?
California Highway Patrol ‑ Amador | Amador County Fire Chiefs Assoc Mtg | 2024-03-07 | Gas Grass Roots Live Active Drill confirmation with Amador agencies for week of April 22. Additional FRW needs?
Butte County Administrative Office | CWSP Presentation Butte Co Admin & OES | 2024-03-08 | Community Wildfire Safety Program Presentation including PG&E layers to wildfire mitigation, identifying and reducing wildfire risk, Underground, Overhead System Hardening, Line Removal, Vegetation Management, EPSS, Public Safety Power Shutoffs, and the differences between EPSS and PSPS.
Butte County Office of Emergency Services | CWSP Presentation Butte Co Admin & OES | 2024-03-08 | Community Wildfire Safety Program Presentation including PG&E layers to wildfire mitigation, identifying and reducing wildfire risk, Underground, Overhead System Hardening, Line Removal, Vegetation Management, EPSS, Public Safety Power Shutoffs, and the differences between EPSS and PSPS.
San Bruno Fire Department | 1st Quarter Regional Working Group | 2024-03-08 | TD‑1464S Wildfire Prevention and Mitigation
Redwood City San Carlos Fire Department | 1st Quarter Regional Working Group | 2024-03-08 | TD‑1464S Wildfire Prevention and Mitigation
San Mateo County Department of Emergency Management | 1st Quarter Regional Working Group | 2024-03-08 | TD‑1464S Wildfire Prevention and Mitigation
Grass Valley Fire Department | AB 56 Meeting | 2024-03-11 | Meeting with Grass Valley Division Chief to discuss and go over the AB 56 flyer.
Nevada County Consolidated Fire Department | AB 56 Meeting | 2024-03-11 | Meeting with Chief Robitaille to discuss and go over the AB 56 flyer.
Rough and Ready Fire Protection District | AB 56 Meeting | 2024-03-11 | Meeting with Chief Robitaille to discuss and go over the AB 56 flyer.
Penn Valley Fire Protection District | AB 56 Meeting | 2024-03-11 | Meeting with Chief Robitaille to discuss and go over the AB 56 flyer.
Rough and Ready Fire District | AB 56 Meeting | 2024-03-11 | Meeting with Chief Robitaille to discuss and go over the AB 56 flyer.
San Mateo County Department of Emergency Management | San Mateo County Department of Emergency Management | 2024-03-12 | Discussed cooperative support. Communications methods and future events.
PG&E | San Mateo County Department of Emergency Management | 2024-03-12 | Discussed cooperative support. Communications methods and future events.
Hospital Council of Northern & Central California ‑ South Bay | Santa Clara County Hospitals Emergency Preparedness Partnership | 2024-03-12 | PG&E Presentation: Overview of PG&E Structure. Introduction of Customer Relations Managers (CRMs) and their area of responsibility Planned or Unplanned Events? How does the CRM work with the hospital, County OES, EMS, and other agencies during an outage or emergency? What services or resources should hospital be aware of during a long‑term outage? How is technology used to identify potential problem areas‑ (weather reports, AI, and other tools)? How can hospitals work with PG&E to identify other priority buildings on and off their campuses? The PG&E Hospital account management team will present on the emergency preparedness topics noted above. The Council is specifically interested in hearing more about how our PSS works with the County OES related to preparedness and during emergency events. It would be great to have you speak to the work you and your team do and connect with the emergency managers in attendance.
Manteca Fire Department | AB 56 Meeting | 2024-03-13 | E‑mail with Chief Marques with Manteca Fire Department which included AB 56 information in the First Responder Guide to Public Safety handout, AB 56 PowerPoint presentation handout, and a copy of PG&E's GERP as attachments. An in person meeting to discuss the material was also offered. Two previous attempts at the Chief's meetings to present were unsuccessful.
Mule Creek State Prison Fire Department | AB 56 Meeting | 2024-03-13 | E‑mail with Captain Tate with Mule Creek Fire Department which included AB 56 information in the First Responder Guide to Public Safety handout, AB 56 PowerPoint presentation handout, and a copy of PG&E's GERP as attachments. An in person meeting to discuss the material was also offered. Two previous attempts at the Chief's meetings to present were unsuccessful.
Kenwood Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Sonoma Valley Fire District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Schell‑Vista Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Petaluma Fire Department | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Sonoma County Fire & Emergency Services | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Graton Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Santa Rosa Fire Department | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Sebastopol Fire Department | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Rohnert Park Department of Public Safety | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Cloverdale Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Eldridge Fire Department | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Sonoma Valley Fire District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Forestville Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
North Bay Fire | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Geyserville Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Northern Sonoma County Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Gold Ridge Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Sonoma County Fire District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Healdsburg Fire Department | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Rancho Adobe Fire Protection District | Sonoma County Fire Chiefs Meeting | 2024-03-13 | AB 56 discussed First Responder Guide Book distributed to every agency. PowerPoint utilized to guide discussion and presentation.
Marina Fire Department | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
Monterey Fire Department | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
CAL FIRE ‑ San Benito‑Monterey | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
Seaside Fire Department | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
Salinas Fire Department | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
Hollister Fire Department | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
Greenfield Fire Department | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
Monterey County Regional Fire District | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
Presidio of Monterey‑Fire Department | Monterey County Fire Training Assoc | 2024-03-14 | Monterey Co Fire Training Officer Association meeting. Discussion and training on PG&E GERP, ERPT, PSPS, concurring events and other emergency incidents. Handouts provided.
El Dorado County Office of Emergency Services | El Dorado Hazard Mitigation Plan | 2024-03-18 | Attended the El Dorado County Hazard Mitigation Plan meeting.
El Dorado County Sheriff's Department | El Dorado Hazard Mitigation Plan | 2024-03-18 | Attended the El Dorado County Hazard Mitigation Plan meeting.
El Dorado Irrigation District | El Dorado Hazard Mitigation Plan | 2024-03-18 | Attended the El Dorado County Hazard Mitigation Plan meeting.
El Dorado Office of Education ‑ Emergency Preparedness | El Dorado Hazard Mitigation Plan | 2024-03-18 | Attended the El Dorado County Hazard Mitigation Plan meeting.
El Dorado County Administrative Office | El Dorado Hazard Mitigation Plan | 2024-03-18 | Attended the El Dorado County Hazard Mitigation Plan meeting.
Emergency Medical Services Authority ‑ El Dorado County | El Dorado Hazard Mitigation Plan | 2024-03-18 | Attended the El Dorado County Hazard Mitigation Plan meeting.
El Dorado Hills Fire Department | El Dorado Hazard Mitigation Plan | 2024-03-18 | Attended the El Dorado County Hazard Mitigation Plan meeting.
Camp Parks Fire And Emergency Services | AB 56 Meeting ‑ Camp Parks Fire & Emergency Service | 2024-03-20 | Discussed AB 56. Delivered materials verbally and via videos and handouts. Materials e‑mailed as well.
Tehama County Public Works Department | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
Tehama County Sheriff's Department | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
Corning City Fire Department | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
CAL FIRE ‑ Tehama‑Glenn | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
Red Bluff Fire Department | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
City of Red Bluff Public Works | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
TEHAMA COUNTY DEPARTMENT OF EDUCATION | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
State of California Governor’s Office of Emergency Services (CAL OES) | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
Tehama County Administrative Office | MCI Disaster Council Meeting | 2024-03-21 | Professional Group Meeting
Selma Fire Department | Selma Fire Dept Contingency Planning | 2024-03-22 | Contingency Planning meeting discussed with Chief Webster and Chief Gomez. AB 56 covered as well as emergency response contingency planning and levels of activation . GERP and 508_2024_First Responder Packet shared by e‑mail. 508_2024_First Responder Packet sent by USPS to Chief Jordan Webster. FRWs are under discussion for scheduling, 2024.
Hopland Fire Protection District | AB 56 Meeting ‑ Hopland | 2024-03-25 | Delivered the required materials in person and followed up with an e‑mail copy of the materials.
Chevron Refinery Fire Department | Chevron Refinery Fire Department | 2024-03-25 | Met with Chief Bosworth and Chevron Deputy Fire Chief and provided AB 56 handout. Discussed PG&E Contingency Plans, Emergency Response, and Portal. Reaffirmed myself as PG&E Liaison contact and provided business card.
North Central Fire District | North Central Fire District Contingency Planning | 2024-03-25 | Contingency Planning shared with Chief Tim Henry and Chief McAfee and training Captain Corey Cason . AB 56 covered as well as emergency response contingency planning. GERP was shared and levels of activation. 508_2024_First Responder Packet sent by e‑mail and USPS to Chief Tim Henry.
West Sacramento Fire Department | AB 56 Sac Co Fire Training Officers | 2024-03-26 | Training Meeting where I presented information on FRW, PSS, SIPT and various levels of collaboration we can participate in including field exercises etc.
Sacramento Metropolitan Fire District | AB 56 Sac Co Fire Training Officers | 2024-03-26 | Training Meeting where I presented information on FRW, PSS, SIPT and various levels of collaboration we can participate in including field exercises etc.
Sacramento County Airport System Aircraft Rescue & Firefighting | AB 56 Sac Co Fire Training Officers | 2024-03-26 | Training Meeting where I presented information on FRW, PSS, SIPT and various levels of collaboration we can participate in including field exercises etc.
CAL FIRE ‑ Amador‑El Dorado | AB 56 Sac Co Fire Training Officers | 2024-03-26 | Training Meeting where I presented information on FRW, PSS, SIPT and various levels of collaboration we can participate in including field exercises etc.
Shingle Springs Band of Miwok Fire Department | PG&E Wildfire Strategy/ El Dorado Fire Agency Meeting | 2024-03-27 | Meet and greet with the PG&E Wildfire Strategy Team, Garden Valley Fire and Shingle Springs Band of Miwok Fire Crew.
Garden Valley Fire Protection District | PG&E Wildfire Strategy/ El Dorado Fire Agency Meeting | 2024-03-27 | Meet and greet with the PG&E Wildfire Strategy Team, Garden Valley Fire and Shingle Springs Band of Miwok Fire Crew.
El Dorado County Administrative Office | PG&E Wildfire Strategy/ El dorado OWPR Meeting | 2024-03-27 | Meet and greet with El Dorado County CAO/ Office of Wildfire Preparedness and Resilience and our PG&E Wildfire Strategy Team.
Arcata Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Blue Lake Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Bridgeville Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
CAL FIRE ‑ Humboldt‑Del Norte | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Samoa Peninsula Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Humboldt Bay Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Loleta Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Fortuna Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Anderson Valley Fire Protection District | Humboldt County Fire Chiefs Meeting | 2024-03-27 | Meeting with the Humboldt County Fire Chiefs which included the AB 56 information in the first responder guide which has also been e‑mailed to them.
Merced Fire Department | Merced Fire Department AB 56 Meeting | 2024-03-27 | Met with a representative of the Merced Fire Department to discuss AB 56 and emergency response to natural gas incidents. Provided a hard copy of the First Responder Guide to Public Safety as well as e‑mailed a digital copy to them.
El Dorado Hills Fire Department | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, In‑Line Inspection (ILI) at El Dorado Hills and offered FRW.
CAL FIRE ‑ Amador‑El Dorado | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
El Dorado County Fire Protection District | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
El Dorado County Fire District | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
Pioneer Fire District | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
Garden Valley Fire Protection District | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
State of California Governor’s Office of Emergency Services (CAL OES) | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
U.S. Forest Service ‑ El Dorado National Forest | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
Emergency Medical Services Authority ‑ El Dorado County | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
El Dorado County Administrative Office | El Dorado County Fire Chiefs Assoc. | 2024-03-27 | Attended the bi monthly meeting of the El Dorado County Fire Chiefs. Provided a report on storm response, EPSS, ILI at El Dorado Hills and offered FRW.
CAL FIRE ‑ San Mateo‑Santa Cruz | Prescribed Burn 1st Walk through | 2024-03-28 | Walked planned area for future Prescribed Burn. Identified PG&E critical facilities. Discussed options and concerns.
PG&E | Prescribed Burn 1st Walk through | 2024-03-28 | Walked planned area for future Prescribed Burn. Identified PG&E critical facilities. Discussed options and concerns.
California City Fire Department | California City Fire Dept ‑ Contingency Planning | 2024-03-29 | Contingency Planning meeting held with Captain Guerrero AB 56 covered as well as emergency response contingency planning. GERP was discussed and levels of activation and shared by e‑mail. 508_2024_First Responder Packet sent by e‑mail and USPS to Chief Kosick (terminated 03/27/24) FRWs were discussed with Captain Guerrero and after the re‑organization of the Department we will schedule classes.
Kern County Fire Department | Kern County Fire AB 56 | 2024-04-02 | Contingency Planning meeting held with Chief Joe Appleton, AB 56 covered as well as emergency response contingency planning. GERP was discussed and levels of activation and shared by e‑mail. 508_2024_First Responder Packet sent by e‑mail and to Unit Chief Aaron Duncan, and Training Division Chief Derek Tisinger. 508_2024_First Responder Packet sent USPS (by Geoff Money) to Chief Duncan. FRWs are under discussion to schedule 2024 as well as a Gas Live Action Drill in Dec. 2024.
Yuba County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Plumas County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Tehama County Sheriff's Department | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Pacific Gas and Electric ‑ Emergency Management & Public Safety | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Glenn County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
State of California Governor’s Office of Emergency Services (CAL OES) | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Butte County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Modoc County Sheriff's Department | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Sutter County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Trinity County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Siskiyou County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Colusa County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Sierra County Office of Emergency Services | MARAC Region 3 | 2024-04-03 | Professional Group Meeting
Farmington Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Collegeville Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Stockton Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Clements Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Montezuma Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Escalon Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-04-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. TX Emergency Repair for Ripon, Escalon, Manteca, and Farmington areas PSPS TTX and FE Training EPSS Settings soon Amador Gas Drill (Observers?) FRWs available
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #13 | 2024-04-03 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #13.
Ukiah Valley Fire Authority | AB 56 Meeting | 2024-04-04 | Met with Chief Hutchison and reviewed AB 56 materials in the First Responder Guide which I mailed to the Chief the week Prior including the PDF document.
Redwood Valley‑Calpella Fire Protection District | AB 56 Meeting | 2024-04-04 | Meeting with Redwood Valley‑Capella Fire Department which included the AB 56 information in the First Responder Guide to Public Safety handout which I mailed to the Chief the week prior. Also e‑mailed the PDF document with the same material.
American Red Cross ‑ Gold Country | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
Tuolumne County Health Department | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
Tuolumne County Sheriff's Department | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
CAL FIRE ‑ Tuolumne‑Calaveras | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
U.S. Forest Service ‑ Stanislaus National Forest | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
Tuolumne County Animal Control | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
Tuolumne County Fire Department | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
Tuolumne County Office of Emergency Services | Tuolumne County Wildfire Preparedness Town Hall | 2024-04-06 | CWSP ‑ Outreach
CAL FIRE ‑ San Luis Obispo | AB 56 Meeting | 2024-04-09 | Contingency Plan Meeting ‑ AB 56
San Luis Obispo County Office of Emergency Services | AB 56 Meeting | 2024-04-09 | Contingency Plan Meeting ‑ AB 56
Camp Roberts Fire Department | AB 56 Meeting | 2024-04-09 | Contingency Plan Meeting ‑ AB 56
Mountain View Fire Protection District | AB 56 Outreach Mountain View FD | 2024-04-09 | Multiple attempts to contact and meet with Mtn. View FD Chief. Attempted to meet in person twice, sent hard copy AB 56 handout material. Followed up with e‑mail and attached PDF hand out material, text to cell phone, left message at FD phone, and left message on cell phone, all with no response.
Capay Valley Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
West Sacramento Fire Department | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Dunnigan Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Woodland Fire Department | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
CAL FIRE ‑ Sonoma‑Lake‑Napa | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Madison Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Yolo Emergency Communications Agency | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
West Plainfield Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Willow Oak Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Knights Landing Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Yocha Dehe Fire Department | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Winters Fire Department | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Zamora Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Yolo Fire Protection District | AB 56 Yolo Co Fire Chiefs Association | 2024-04-09 | Meeting included a dinner 18:00‑19:00, meeting 19:00‑21:00. This meeting was short as AB 56 was only new business.
Little Lake Fire Protection District | AB 56 Meeting | 2024-04-10 | Meeting with Little Lake/Willits fire chief which included the AB 56 information in the First Responder Guide to Public Safety handout which I mailed to the Chief two weeks prior and also on 4/11/2024. Also e‑mailed to the chief the PDF documentation with the same material.
Santa Clara County Emergency Managers Association | Santa Clara County Emergency Managers Association | 2024-04-11 | Professional Group Meeting
Marine Corps Logistics Base Barstow Fire Department | AB 56 MCLB Barstow | 2024-04-16 | Contact made with: Ryan Tworek Deputy Fire Chief, MCLB Barstow Fire & Emergency Services. AB 56 covered as well as emergency response contingency planning. GERP was discussed and levels of activation and shared by e‑mail. 508_2024_First Responder Packet sent by e‑mail and USPS to Chief Tworek. FRWs are being discussed to schedule.
Naval Air Weapons Base China Lake Federal Fire Department | China Lake Marine Naval Air Weapons Base AB 56 | 2024-04-16 | I e‑mailed Nathan Soria , and Chief of Operations 4 e‑mails. AB 56 covered in the e‑mails, as well as emergency response contingency planning. GERP was attached and a quick reference power point with emphasis on levels of activation, and training available. Also shared by e‑mail. 508_2024_First Responder Packet and sent by USPS to Chief Soria. Messages left ‑ 3X on office and cell voice mail (04/02, 4/12, 4/13). Assistant Chief James Bank called 3 X, and voice mail left on office and cell (4/02, 4/12, 4/13). E‑mail sent on 4/13 with delivery and read confirmation. See attached.
Bureau of Land Management ‑ Modoc | Modoc County Disaster Council | 2024-04-18 | Contingency Plan Meeting ‑ AB 56
CAL FIRE ‑ Lassen‑Modoc‑Plumas | Modoc County Disaster Council | 2024-04-18 | Contingency Plan Meeting ‑ AB 56
U.S. Forest Service ‑ Modoc National Forest | Modoc County Disaster Council | 2024-04-18 | Contingency Plan Meeting – AB 56
Modoc County Sheriff's Department | Modoc County Disaster Council | 2024-04-18 | Contingency Plan Meeting – AB 56
CAL FIRE ‑ San Mateo‑Santa Cruz | Cal‑Fire CZU | 2024-04-23 | Discussed Pipeline access, Pipeline Maps & Emergency Response
San Mateo County Department of Emergency Management | San Mateo County Department of Emergency Management | 2024-04-23 | Discussed Communications process, PSPS, CRCs and Back up generation.
Colusa County Office of Emergency Services | Colusa County LHMP Meeting | 2024-04-24 | Colusa County LHMP Meeting
Colusa County Sheriff's Department | Colusa County LHMP Meeting | 2024-04-24 | Colusa County LHMP Meeting
Rio Dell Fire Protection District | AB 56 Meeting | 2024-04-26 | Met with Rio Dell/Scotia Fire Chief and discussed AB 56 information and presented the trifold material. Rio Dell and Scotia Fire Departments have combined into one department.
Scotia Fire Protection District | AB 56 Meeting | 2024-04-26 | Meeting with Rio Dell/Scotia Fire Chief which included the AB 56 information in the First Responder Guide to Public Safety handout which I also e‑mailed to him on 5/6/2024 as a PDF document.
California Department of Corrections and Rehabilitation‑ Folsom State Prison | AB 56 Solano Co outreach | 2024-04-29 | AB 56 outreach via e‑mail/phone in support of making agencies aware of services and products from PG&E to first responders.
Vacaville Fire Protection District | AB 56 Solano Co outreach | 2024-04-29 | AB 56 outreach via e‑mail/phone in support of making agencies aware of services and products from PG&E to first responders.
Cordelia Fire Protection District | AB 56 Solano Co outreach | 2024-04-29 | AB 56 outreach via e‑mail/phone in support of making agencies aware of services and products from PG&E to first responders.
Davis Fire Department | AB 56 Yolo Co Extended Outreach | 2024-04-29 | Picking up missed agencies from previous chiefs meeting in Yolo County where we discussed PG&E first responder outreach
Elkhorn Fire Protection District | AB 56 Yolo Co Extended Outreach | 2024-04-29 | Picking up missed agencies from previous chiefs meeting in Yolo County where we discussed PG&E first responder outreach
Esparto Fire Protection District | AB 56 Yolo Co Extended Outreach | 2024-04-29 | Picking up missed agencies from previous chiefs meeting in Yolo County where we discussed PG&E first responder outreach
Blue Lake Rancheria Fire Department | AB 56 Meeting | 2024-04-30 | Meeting with Blue Lake Rancheria Fire Chief which included the AB 56 information in the First Responder Guide to Public Safety handout. I also e‑mailed the PDF document of the trifold.
Farmington Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
French Camp‑McKinley Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Stockton Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Montezuma Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Escalon Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Liberty Rural County Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-05-01 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Gas Drill Participation Thanks EPSS Settings soon FRWs available
Southern Trinity Volunteer Fire Department | AB 56 meeting | 2024-05-02 | Met with Southern Trinity VFD member (Seth Thorpe) regarding AB 56 tri‑fold information.
Amador County Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-05-02 | Gas Grass Roots Live Active Drill cancelled by Amador agencies. Moved to San Joaquin County Additional FRW offered
Lockwood Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-05-02 | Gas Grass Roots Live Active Drill cancelled by Amador agencies. Moved to San Joaquin County Additional FRW offered
CAL FIRE ‑ Amador‑El Dorado | Amador County Fire Chiefs Assoc Mtg | 2024-05-02 | Gas Grass Roots Live Active Drill cancelled by Amador agencies. Moved to San Joaquin County Additional FRW offered
Ione Fire Department | Amador County Fire Chiefs Assoc Mtg | 2024-05-02 | Gas Grass Roots Live Active Drill cancelled by Amador agencies. Moved to San Joaquin County Additional FRW offered
Sutter Creek Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-05-02 | Gas Grass Roots Live Active Drill cancelled by Amador agencies. Moved to San Joaquin County Additional FRW offered
California Highway Patrol ‑ Amador | Amador County Fire Chiefs Assoc Mtg | 2024-05-02 | Gas Grass Roots Live Active Drill cancelled by Amador agencies. Moved to San Joaquin County Additional FRW offered
Carlotta Community Services District | AB 56 meeting | 2024-05-03 | Met with Chief Todd Calvo regarding AB 56 information. Provided tri‑fold with current contact information.
California Department of Rehabilitation and Corrections ‑ Medical Facility | AB 56 Department of Corrections Vacaville | 2024-05-07 | Phone conversation followed up with e‑mail
CAL FIRE ‑ Siskiyou | Siskiyou County Cooperators Meeting | 2024-05-07 | Yearly wildland meeting with Fire cooperators. AB 56 covered with Unit Chief of Siskiyou. Folder provided
MOTCO Federal Fire Department ‑ Concord | MOTCO AB 56 meeting | 2024-05-10 | Met with Interim Fire Chief Burl Danley, discussed PG&E Emergency Response process, provided AB 56 handout material, confirmed PSS contact information and discussed PG&E First Responder Portal.
Meridian Fire Protection District | AB 56 Meridian | 2024-05-13 | Meeting with Meridian Fire Protection District which included the AB 56 information in the First Responder Guide to Public Safety handout which I gave to the Fire Chief.
Seaside Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Greenfield Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
CAL FIRE ‑ San Benito‑Monterey | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
King City Volunteer Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Gonzales Volunteer Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Marina Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Monterey Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Monterey County Regional Fire District | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
North County Fire Protection District of Monterey County | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Soledad Correctional Training Facility ‑ Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Salinas Fire Department | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
Bureau of Land Management ‑ Hollister | Monterey Co Fire Chiefs Mtg | 2024-05-13 | Meeting with fire chiefs from Monterey Co and San Benito Co. to discussion AB 56, hand out material, fire season, contingency planning, ICS and GERP.
U.S. Forest Service ‑ Region 5 Headquarters | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
Cosumnes Community Services District | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
Walnut Grove Fire Protection District | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
Isleton Fire Department | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
River Delta Fire Protection District | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
Herald Fire Protection District | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
Wilton Fire Protection District | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
Clarksburg Fire Protection District | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
Folsom Fire Department | AB 56 May Sac Yolo Co | 2024-05-15 | This report includes 9 agencies in both Sac, Yolo and Solano Co. Most were in person meetings with a couple that required e‑mail and phone calls.
TURLOCK IRRIGATION DISTRICT | City of Turlock EOC Coordination Meeting | 2024-05-15 | City of Turlock is upgrading equipment and technology in local EOC, and looking to host quarterly coordination meetings and update contact lists with agency reps.
Cal Trans District 10 | City of Turlock EOC Coordination Meeting | 2024-05-15 | City of Turlock is upgrading equipment and technology in local EOC, and looking to host quarterly coordination meetings and update contact lists with agency reps.
City of Turlock Administrative Office | City of Turlock EOC Coordination Meeting | 2024-05-15 | City of Turlock is upgrading equipment and technology in local EOC, and looking to host quarterly coordination meetings and update contact lists with agency reps.
Turlock Police Department | City of Turlock EOC Coordination Meeting | 2024-05-15 | City of Turlock is upgrading equipment and technology in local EOC, and looking to host quarterly coordination meetings and update contact lists with agency reps.
Turlock Fire Department and Emergency Services | City of Turlock EOC Coordination Meeting | 2024-05-15 | City of Turlock is upgrading equipment and technology in local EOC, and looking to host quarterly coordination meetings and update contact lists with agency reps.
San Francisco Department of Emergency Management | SF Department of Emergency Mgt. | 2024-05-15 | Introduction of new Bay Region VP to SF DEM Command staff.
Olivehurst Public Utility District Fire Department | AB 56 Olivehurst | 2024-05-16 | Meeting with Olivehurst Fire Department on the AB 56 information in the First Responder Guide to Public Safety handout which i gave to the Department Representative.
San Quentin State Prison Fire Department | AB 56 Meeting | 2024-05-17 | Meeting with San Quentin Fire Department to discuss the AB 56 compliance for first responders. Delivered the pamphlet and discussed the items contained within.
El Dorado Hills Fire Department | El Dorado Hills ILI I‑800 Site Tour | 2024-05-23 | Liaison Meeting (non‑scheduled)
Beale Air Force Base Fire Emergency Services | AB 56 Beal AFB | 2024-05-28 | Meeting with Beal AFB which included the AB 56 information in the first responder guide to public safety handout which i gave to the fire chief.
Albany Fire Department | AB 56 Meeting ‑ Albany Fire Department 053024 | 2024-05-30 | On Thursday, May 30, 2024, I met with Training Lieutenant Eric Ortenblad regarding AB 56. Meeting occurred at the Albany Fire Station/HQ located at 1000 San Pablo Ave, Albany, CA.
CAL FIRE ‑ Mendocino | AB 56 Meeting | 2024-06-04 | Meeting with MEU Deputy Unity Chief which included the AB 56 information in the First Responder Guide to Public Safety handout. Also left 11 additional guides.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #14 | 2024-06-04 | Planning Meeting
U.S. Forest Service ‑ El Dorado National Forest | USFS ENF Fire Kick Off Meeting | 2024-06-05 | Pre‑season all hand meeting presentation for the USFS El Dorado National Forest. Focus on PSS and SIPT Programs. 156 employees in attendance.
National Aeronautics and Space Administration (NASA) Ames Fire Department | AB 56 NASA Ames Fire Department | 2024-06-05 | Meeting with NASA Ames Moffett Field FD regarding the AB 56 information in the First Responder Guide to Public Safety handout which I e‑mailed to Steve Bristow for dissemination to the respective Chief Officers.
Madera County Sheriff's Department | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
CHP ‑ Oakhurst | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
Madera County Office of Emergency Services | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
American Red Cross ‑ Central California | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
CAL FIRE ‑ Madera‑Mariposa‑Merced | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
NORTH FORK RANCHERIA INDIAN HOUSING AUTHORITY | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
Madera County Fire Department | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
Mariposa County Fire Department | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
Merced County Fire Department | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
Madera Fire Department | North Fork Rancheria Emergency Preparedness Meeting | 2024-06-05 | Provided an invitation to teach FRWs to the Oakhurst CHP Commander, CAL FIRE ‑ MMU Chief, Madera Sheriff's Office Commander, Madera OES, American Red Cross and North Fork Rancheria Emergency Response Team. Provided an overview of PSS Roles & Responsibilities and how PG&E fit into other agencies emergency responses.
City of Alameda Fire Department | AB 56 ‑ City of Alameda Fire Department 060624 | 2024-06-06 | Conducted an AB 56 presentation with Training Captain Alex Barbour. Meeting conducted over TEAMS.
Garden Valley Fire Protection District | Hometown Wildfire Safety Collaborative | 2024-06-06 | Facilitate the Wildfire Risk and Strategy team to meet with the Garden Valley Fire Department. Working to develop an agreement on funding for a fire fuels reduction crew and equipment.
Davis Fire Department | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Yolo County Office of Emergency Services | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
CAL FIRE ‑ Sonoma‑Lake‑Napa | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Yolo Fire Protection District | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Winters Fire Department | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
American Medical Response ‑ West Sacramento | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
West Sacramento Fire Department | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Yolo Emergency Communications Agency | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Yolo County Sheriff's Department | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
California Highway Patrol ‑ Woodland | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Woodland Fire Department | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Esparto Fire Protection District | Yolo County Fire Chiefs Meeting | 2024-06-11 | Quarterly meeting, discussed desire to perform more FRWs with law enforcement community. Looking to be invited to monthly or quarterly meetings with LE.
Santa Clara County Emergency Managers Association | Santa Clara County Emergency Manager's Association | 2024-06-13 | Monthly membership meeting.
Calaveras County Water District | Calaveras County Utility Emergency Response Coordination Meeting | 2024-06-17 | Contingency Plan Meeting
Calaveras County Department of Public Works | Calaveras County Utility Emergency Response Coordination Meeting | 2024-06-17 | Contingency Plan Meeting
Calaveras County Office of Emergency Services | Calaveras County Utility Emergency Response Coordination Meeting | 2024-06-17 | Contingency Plan Meeting
Santa Clara County Fire Safe Council | Santa Clara County Fire Safe Council Monthly Board Meeting | 2024-06-18 | Professional Group Meeting
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #15 | 2024-07-01 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #15.
Ripon Consolidated Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Stockton Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Clements Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Montezuma Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Linden‑Peters Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-07-03 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. EOC activated for PSPS/Heat event Fire Response notifications, Unprotected Zone FRWs available
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #16 | 2024-07-03 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #16.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #17 | 2024-07-05 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #17.
Bakersfield Fire Department | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
kern county public health | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Bakersfield Police Department | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
California State University Bakersfield | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
State of California Governor’s Office of Emergency Services (CAL OES) | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Stallion Springs CSO | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
California City Fire Department | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Aging Adult Services‑Kern County | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
American Red Cross Bakersfield | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Delano Police Department | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern County Office of Emergency Services | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern county public works | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Southern California Edison | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
CAL Water Bakersfield | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Edwards Air Force Base Federal Fire Department | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern Communications | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern County DHS | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern County Sheriff's Department | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
kern county superintendent of schools | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern Community College District | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern County Fire Department | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern County EMS | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Kern County Transit | Kern Co. Op Area Meeting | 2024-07-08 | Attendance at quarterly scheduled Kern Co OES Op Area Meeting. Met the Director and Deputy Director for Kern Co OES in person to introduce myself and provide them with my background and contact information.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #18 | 2024-07-08 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #18.
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #19 | 2024-07-10 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #19
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #20 | 2024-07-12 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #20
San Mateo County Department of Emergency Management | Emergency Evacuation Planning for San Mateo County | 2024-07-15 | Planning meeting for Emergency Evacuation Routes in San Mateo County. Discussed CRC sites and PSPS for PG&E.
San Mateo Police Department | Emergency Evacuation Planning for San Mateo County | 2024-07-15 | Planning meeting for Emergency Evacuation Routes in San Mateo County. Discussed CRC sites and PSPS for PG&E.
San Mateo County Sheriff's Office | Emergency Evacuation Planning for San Mateo County | 2024-07-15 | Planning meeting for Emergency Evacuation Routes in San Mateo County. Discussed CRC sites and PSPS for PG&E.
North County Fire Authority | Emergency Evacuation Planning for San Mateo County | 2024-07-15 | Planning meeting for Emergency Evacuation Routes in San Mateo County. Discussed CRC sites and PSPS for PG&E.
San Bruno Fire Department | Emergency Evacuation Planning for San Mateo County | 2024-07-15 | Planning meeting for Emergency Evacuation Routes in San Mateo County. Discussed CRC sites and PSPS for PG&E.
Glenn County Sheriff's Department | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Tehama County Sheriff's Department | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Butte County Office of Emergency Services | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Sutter County Office of Emergency Services | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Glenn County Office of Emergency Services | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Trinity County Office of Emergency Services | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Shasta County Office of Emergency Services | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Pacific Gas and Electric Emergency Preparedness ‑ North Valley | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
California Office of Emergency Services Region 3 ‑ Shasta | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Sierra Pacific Industries | MARAC Region 3 | 2024-07-17 | Liaison Meeting (non‑scheduled)
Woodside Fire Protection District | Badge Pinning & Station Tour | 2024-07-18 | Professional Group Meeting
Menlo Park Fire Protection District | Badge Pinning & Station Tour | 2024-07-18 | Professional Group Meeting
San Mateo County Public Safety Communications | Badge Pinning & Station Tour | 2024-07-18 | Professional Group Meeting
San Mateo County Fire | Badge Pinning & Station Tour | 2024-07-18 | Professional Group Meeting
Redwood City San Carlos Fire Department | Badge Pinning & Station Tour | 2024-07-18 | Professional Group Meeting
Central County Fire Department | Badge Pinning & Station Tour | 2024-07-18 | Professional Group Meeting
San Mateo County Department of Emergency Management | Badge Pinning & Station Tour | 2024-07-18 | Professional Group Meeting
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #21 | 2024-07-19 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #21
San Joaquin County Office of Emergency Services | San Joaquin Co OP Area Stakeholder Quarterly Mtg | 2024-07-24 | Quarterly meeting to share information, trainings, and projects with others in OP area.
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin Co OP Area Stakeholder Quarterly Mtg | 2024-07-24 | Quarterly meeting to share information, trainings, and projects with others in OP area.
Lodi Fire Department | San Joaquin Co OP Area Stakeholder Quarterly Mtg | 2024-07-24 | Quarterly meeting to share information, trainings, and projects with others in OP area.
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Clements Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Montezuma Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Escalon Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-08-07 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Woodside Fire Protection District | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
San Bruno Fire Department | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
Stanford Office of Emergency Management | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
La Honda Fire Brigade | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
North County Fire Authority | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
San Mateo County Public Safety Communications | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
San Mateo Consolidated Fire | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
San Mateo County Department of Emergency Management | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
CAL FIRE ‑ San Mateo‑Santa Cruz | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
Fire Safe San Mateo County | Fire Safe Council | 2024-08-14 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Watch Duty. Discussed how to use it and future expansion.
East Bay Regional Park District Fire Department | Alameda County Training Officers Meeting 8‑28‑2024 0900 | 2024-08-28 | Alameda County Training Officers Meeting.
Oakland Fire Department | Alameda County Training Officers Meeting 8‑28‑2024 0900 | 2024-08-28 | Alameda County Training Officers Meeting.
Fremont Fire Department | Alameda County Training Officers Meeting 8‑28‑2024 0900 | 2024-08-28 | Alameda County Training Officers Meeting.
Hayward Fire Department | Alameda County Training Officers Meeting 8‑28‑2024 0900 | 2024-08-28 | Alameda County Training Officers Meeting.
Chabot‑Las Positas Community College District | Alameda County Training Officers Meeting 8‑28‑2024 0900 | 2024-08-28 | Alameda County Training Officers Meeting.
Internal PG&E Account | Mission Monthly Operating Review | 2024-08-28 | Mission Monthly Operating Review
Garden Valley Fire Protection District | Hometown Wildfire Safety Collaborative | 2024-09-04 | Hometown Wildfire Safety Collaborative kick off meeting with Garden Valley Fire Department and Wildfire Risk and Strategy, Kevin Johnson. Funding of $600,000 was granted to and received by the Garden Valley Fire Department to fund a wildfire fire fuels reduction crew and equipment. Meeting to discuss execution of the agreement, coordination and communications.
El Dorado Hills Fire Department | El Dorado County Fire Safe Council Meeting | 2024-09-18 | Attended the monthly general meeting of the El Dorado County Fire Safe Council. PG&E has a standing report out on the agenda. In that report I covered our CWSP "Layers of Protection" safety efforts in the county. I provided an update to the Hometown Wildfire Safety Collaboration effort with Garden Valley Fire Department. I introduced Sashi Sabaratnam as our new Wildfire Resilience Chief.
Garden Valley Fire Protection District | El Dorado County Fire Safe Council Meeting | 2024-09-18 | Attended the monthly general meeting of the El Dorado County Fire Safe Council. PG&E has a standing report out on the agenda. In that report I covered our CWSP "Layers of Protection" safety efforts in the county. I provided an update to the Hometown Wildfire Safety Collaboration effort with Garden Valley Fire Department. I introduced Sashi Sabaratnam as our new Wildfire Resilience Chief.
El Dorado County Fire Safe Council | El Dorado County Fire Safe Council Meeting | 2024-09-18 | Attended the monthly general meeting of the El Dorado County Fire Safe Council. PG&E has a standing report out on the agenda. In that report I covered our CWSP "Layers of Protection" safety efforts in the county. I provided an update to the Hometown Wildfire Safety Collaboration effort with Garden Valley Fire Department. I introduced Sashi Sabaratnam as our new Wildfire Resilience Chief.
El Dorado County Administrative Office | El Dorado County Fire Safe Council Meeting | 2024-09-18 | Attended the monthly general meeting of the El Dorado County Fire Safe Council. PG&E has a standing report out on the agenda. In that report I covered our CWSP "Layers of Protection" safety efforts in the county. I provided an update to the Hometown Wildfire Safety Collaboration effort with Garden Valley Fire Department. I introduced Sashi Sabaratnam as our new Wildfire Resilience Chief.
El Dorado National Forest ‑ Fire Department | El Dorado County Fire Safe Council Meeting | 2024-09-18 | Attended the monthly general meeting of the El Dorado County Fire Safe Council. PG&E has a standing report out on the agenda. In that report I covered our CWSP "Layers of Protection" safety efforts in the county. I provided an update to the Hometown Wildfire Safety Collaboration effort with Garden Valley Fire Department. I introduced Sashi Sabaratnam as our new Wildfire Resilience Chief.
CAL FIRE ‑ Amador‑El Dorado | El Dorado County Fire Safe Council Meeting | 2024-09-18 | Attended the monthly general meeting of the El Dorado County Fire Safe Council. PG&E has a standing report out on the agenda. In that report I covered our CWSP "Layers of Protection" safety efforts in the county. I provided an update to the Hometown Wildfire Safety Collaboration effort with Garden Valley Fire Department. I introduced Sashi Sabaratnam as our new Wildfire Resilience Chief.
San Mateo County Department of Emergency Management | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
San Mateo Consolidated Fire | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
Pacifica Police Department | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
South San Francisco Police Department | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
South San Francisco Fire Department | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
Menlo Park Fire Protection District | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
Central County Fire Department | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
Woodside Fire Protection District | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
PG&E | San Mateo County Emergency Managers | 2024-09-26 | Emergency Managers. Discussed future FRW for CERT and Drone Inspections in San Mateo County
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #22 | 2024-10-01 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #22
South San Joaquin County Fire Authority | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Stockton Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Thornton Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Escalon Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Lathrop‑Manteca Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Woodbridge Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Clements Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Lodi Fire Department | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Waterloo ‑ Morada Rural Fire Protection District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Mokelumne Rural Fire District | San Joaquin County Fire Chiefs Assoc. Mtg. | 2024-10-02 | Monthly San Joaquin County Fire Chiefs Association meeting sharing past and future incidents, events, trainings, and other information of importance to the Chiefs. FRWs are also offered every month to all attending Chiefs. Tracy PSPS details/follow up FRWs available
Santa Clara County Office of Emergency Management | Santa Clara County Office of Emergency Management OA Inclement Weather Event #23 | 2024-10-02 | Santa Clara County Office of Emergency Management, Op Area Coordinating Call, Inclement Weather Event #23
CAL FIRE ‑ San Mateo‑Santa Cruz | Sheep Camp Area 5 SFPUC Prescribed Burn | 2024-10-11 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas & Electric Transmission Line locations, access and safety working around them. .
Kings Mountain Fire Brigade | Sheep Camp Area 5 SFPUC Prescribed Burn | 2024-10-11 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas & Electric Transmission Line locations, access and safety working around them. .
Woodside Fire Protection District | Sheep Camp Area 5 SFPUC Prescribed Burn | 2024-10-11 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas & Electric Transmission Line locations, access and safety working around them. .
San Francisco Water Department | Sheep Camp Area 5 SFPUC Prescribed Burn | 2024-10-11 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas & Electric Transmission Line locations, access and safety working around them. .
PG&E | Sheep Camp Area 5 SFPUC Prescribed Burn | 2024-10-11 | Cal‑Fire organized Prescribed Burn at the Sheep Camp Vista Point on SFPUC land. Reviewed Gas & Electric Transmission Line locations, access and safety working around them. .
CAL FIRE ‑ San Mateo‑Santa Cruz | Fire Safe Council | 2024-10-16 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Fire Evac . Discussed how to use it and future expansion.
Woodside Fire Protection District | Fire Safe Council | 2024-10-16 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Fire Evac . Discussed how to use it and future expansion.
PG&E | Fire Safe Council | 2024-10-16 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Fire Evac . Discussed how to use it and future expansion.
Redwood City San Carlos Fire Department | Fire Safe Council | 2024-10-16 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Fire Evac . Discussed how to use it and future expansion.
Central County Fire Department | Fire Safe Council | 2024-10-16 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Fire Evac . Discussed how to use it and future expansion.
North County Fire Authority | Fire Safe Council | 2024-10-16 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Fire Evac . Discussed how to use it and future expansion.
San Francisco Water Department | Fire Safe Council | 2024-10-16 | San Mateo County Fire Safe Council monthly meeting. Guest speaker was from Fire Evac . Discussed how to use it and future expansion.
City of East Palo Alto Administrative Office | DEM Listening Session | 2024-10-17 | Review Annual Plan. Performed two group exercises.
American Red Cross Peninsula | DEM Listening Session | 2024-10-17 | Review Annual Plan. Performed two group exercises.
Central County Fire Department | DEM Listening Session | 2024-10-17 | Review Annual Plan. Performed two group exercises.
East Palo Alto Police Department | DEM Listening Session | 2024-10-17 | Review Annual Plan. Performed two group exercises.
San Mateo County Department of Emergency Management | DEM Listening Session | 2024-10-17 | Review Annual Plan. Performed two group exercises.
Central County Fire Department | DEM Listening Session | 2024-10-17 | Review Annual Plan. Performed two group exercises.
PG&E | DEM Listening Session | 2024-10-17 | Review Annual Plan. Performed two group exercises.
CITY OF LOS ANGELES D W P | Ca. Utilities Round Table | 2024-10-22 | Professional group meeting with utility agencies in California discussing utility issues and solutions.
Southern California Edison | Ca. Utilities Round Table | 2024-10-22 | Professional group meeting with utility agencies in California discussing utility issues and solutions.
Sacramento Municipal Utility District (SMUD) | Ca. Utilities Round Table | 2024-10-22 | Professional group meeting with utility agencies in California discussing utility issues and solutions.
City of Roseville | Ca. Utilities Round Table | 2024-10-22 | Professional group meeting with utility agencies in California discussing utility issues and solutions.
CAL FIRE ‑ Santa Clara | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
Berkeley Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
Hayward Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
Piedmont Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
East Bay Regional Park District Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
Fremont Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
Oakland Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
Livermore‑Pleasanton Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
Alameda County Fire Department | Alameda County Training Officers Meeting 10‑23‑2024 0900 | 2024-10-23 | Alameda County Training Officers Meeting.
CAL FIRE ‑ San Mateo‑Santa Cruz | Pomponio Ranch Prescribed Burn | 2024-10-23 | Cal‑Fire organized Prescribed Burn at the Tom Kat Ranch
CAL FIRE ‑ San Mateo‑Santa Cruz | TomKat Ranch Prescribed Burn | 2024-10-25 | Cal‑Fire organized Prescribed Burn at the TomKat Ranch in Pescadero. Supported Remote
Calaveras County Department of Public Works | Calaveras County Winter Utility Contingency Meeting | 2024-10-30 | Contingency Plan Meeting
Calaveras County Office of Emergency Services | Calaveras County Winter Utility Contingency Meeting | 2024-10-30 | Contingency Plan Meeting
Calaveras County Water District | Calaveras County Winter Utility Contingency Meeting | 2024-10-30 | Contingency Plan Meeting
Internal PG&E Account | Calaveras County Winter Utility Contingency Meeting | 2024-10-30 | Contingency Plan Meeting
AT&T | Calaveras County Winter Utility Contingency Meeting | 2024-10-30 | Contingency Plan Meeting
Amador County Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-11-07 | Bi‑monthly Fire Chief's Association meeting. Group advised of PG&E events, incidents, and training opportunities since last meeting. FRWs offered to all attending agencies.
CAL FIRE ‑ Amador‑El Dorado | Amador County Fire Chiefs Assoc Mtg | 2024-11-07 | Bi‑monthly Fire Chief's Association meeting. Group advised of PG&E events, incidents, and training opportunities since last meeting. FRWs offered to all attending agencies.
Ione Fire Department | Amador County Fire Chiefs Assoc Mtg | 2024-11-07 | Bi‑monthly Fire Chief's Association meeting. Group advised of PG&E events, incidents, and training opportunities since last meeting. FRWs offered to all attending agencies.
Sutter Creek Fire Protection District | Amador County Fire Chiefs Assoc Mtg | 2024-11-07 | Bi‑monthly Fire Chief's Association meeting. Group advised of PG&E events, incidents, and training opportunities since last meeting. FRWs offered to all attending agencies.
Jackson Fire Department | Amador County Fire Chiefs Assoc Mtg | 2024-11-07 | Bi‑monthly Fire Chief's Association meeting. Group advised of PG&E events, incidents, and training opportunities since last meeting. FRWs offered to all attending agencies.
Member of the Public ‑ Colusa | Elk Creek 1101 Community Meeting | 2024-11-14 | Community meeting to discuss PSPS, EPSS, Wildfires
El Dorado County Fire Protection District | Pay Fire Discussion | 2024-11-26 | Met with Fire Chief Tim Cordero regarding some questions and concerns post Pay Fire. Conversation revolved around PG&E community wildfire safety program and work focused in and around the City of Placerville. I will provide additional information to share with council members.
Hayward Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
Berkeley Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
Oakland Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
East Bay Regional Park District Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
City of Alameda Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
CAL FIRE ‑ Santa Clara | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
Alameda County Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
Fremont Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.
Livermore‑Pleasanton Fire Department | Alameda County Training Officers Meeting 11‑27‑2024 0900 | 2024-11-27 | Alameda County Training Officers Meeting.

## Table 11-6
TABLE 11‑6:
KEY GAPS AND LIMITATIONS IN COLLABORATING ON LOCAL AND REGIONAL WILDFIRE MITIGATION PLANNING 89
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
PG&E roles and responsibilities | PG&E is not the lead authority for wildfires, nor can we require local jurisdictions to create wildfire plans. | Strategy: PG&E remains committed to helping our partners. PG&E will continue to review and provide feedback on local wildfire plans, as it relates to electric and gas impacts during a wildfire, if requested by the local jurisdiction.
Target Timeline: Ongoing.
Collaboration with local wildfire mitigation planning | Our wildfire & climate resiliency work is not connected to the work of communities & agencies | Strategy: Wildfire & Climate Resiliency Chief is currently developing a Wildfire Resilience Corridors pilot with a community within our Areas of Concern (AOC). The pilot’s goal is to co‑develop wildfire mitigation programs and projects with pilot communities that will mutually benefit both community assets and utility infrastructure. Planned projects may be jointly funded with the pilot community.
Target Timeline: 2025‑2028.

## Table 11-7
TABLE 11‑7:
COLLABORATION WITH TRIBAL AGENCIES 90
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
WASHOE TRIBE | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
JACKSON RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
IONE BAND OF MIWOK INDIANS | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
BUENA VISTA RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
BERRY CREEK RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
ENTERPRISE RANCHERIA OF MAIDU INDIANS | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
MOORETOWN RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
MECHOOPDA INDIAN TRIBE | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
COLUSA RANCHERIA (CAHIL DEHE WINTUN) | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
CORTINA RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
SHINGLE SPRINGS RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
BIG SANDY RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
COLD SPRINGS RANCHERIA OF MONO INDIANS | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
TABLE MOUNTAIN RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
GRINDSTONE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
BEAR RIVER BAND OF ROHNERVILLE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
BLUE LAKE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
KARUK TRIBE | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
WIYOT TRIBE (Table Bluff) | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
CHER‑AE HEIGHTS INDIAN COMMUNITY OF THE TRINIDAD RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
YUROK TRIBE | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
HOOPA VALLEY TRIBE | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
BIG LAGOON RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
TEJON INDIAN TRIBE | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
SANTA ROSA RANCHERIA, Tachi‑Yokut | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
SCOTTS VALLEY BAND OF POMO INDIANS | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
ROBINSON RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
ELEM INDIAN COLONY | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
LOWER LAKE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
MIDDLETOWN RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
HABEMATOLEL POMO OF UPPER LAKE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
BIG VALLEY RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
SUSANVILLE INDIAN RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
NORTH FORK RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
PICAYUNE (CHUKCHANSI) RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
HOPLAND RESERVATION | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
MANCHESTER‑PT ARENA RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
COYOTE VALLEY BAND OF POMO INDIANS | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
PINOLEVILLE RESERVATION | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
LAYTONVILLE (CAHTO TRIBE) RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
POTTER VALLEY RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
SHERWOOD VALLEY RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
ROUND VALLEY RESERVATION | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
REDWOOD VALLEY RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
GUIDIVILLE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
UNITED AUBURN INDIAN COMMUNITY | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
GREENVILLE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
WILTON RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
CALIFORNIA VALLEY MIWOK TRIBE (Sheep Valley) | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
SANTA YNEZ BAND OF CHUMASH INDIANS | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
PIT RIVER TRIBES | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
REDDING RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
FEDERATED INDIANS OF GRATON RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
STEWARTS POINT RANCHERIA (KASHAYA POMO) | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
CLOVERDALE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
LYTTON RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
DRY CREEK RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
PASKENTA RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
TULE RIVER INDIAN TRIBE | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
CHICKEN RANCH RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
TUOLUMNE RANCHERIA | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments
YOCHA DEHE WINTUN NATION | See Section 11.3.3: Collaboration with Tribal Governments | 2024 quarterly meetings, e‑mails, calls, newsletter, in person meeting if requested | Communications sent to tribal governments

## Table 11-8
TABLE 11‑8:
KEY GAPS AND LIMITATIONS IN COLLABORATING WITH TRIBAL AGENCIES 91
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
Staffing | The tribal team is limited to two Full‑Time Equivalents to cover the entire service area. Additional team members are needed to cover the 112 tribal governments in the service area. | The team is working on hiring of additional support for a regional tribal outreach and engagement model. Working to bring individuals on to assist in 2025.

## Table 11-9
TABLE 11‑9:
PROTOCOLS FOR EMERGENCY COMMUNICATION TO STAKEHOLDER GROUPS 92
Stakeholder Group/Target Community | Event Type | Method(s) for Communicating | Means to Verify Message Receipt | Interests or Concerns Before, During, and After Wildfire and PSPS Events
Tribal Government | Wildfire‑related outage | E‑mail to tribally‑identified/approved contacts, PG&E website | Request message receipts | PG&E will provide information on fire‑related outages as needed. We are not the primary source of communications for those types of outages. We do provide information on outages through our website for all tribal customers, this will include reason and Estimated Time of Restoral (ETOR) when possible.
Tribal Government | PSPS‑related outage | E‑mail and calls to tribally‑identified/approved contacts, text messages, PG&E website | Confirmation via contact with phone call | PG&E has regulatory requirements for PSPS‑related outages. We follow those requirements closely for tribal governments within the PG&E service area.
Tribal Government | Restoration of service | E‑mail and calls to tribally‑identified/approved contacts, PG&E website, text messages | E‑mail or call as needed | PG&E reaches out to tribal governments during outages to give them ETOR during planned outages. If there is an unplanned outage on tribal lands, we will provide ETOR through our website, through customer notifications or directly to tribal governments when requested.
First Responders | Wildfire | None | None | Electric service outage information
First Responders | Wildfire‑related outage | Phone Call/Text/E‑mail regarding status of electric service | None | Electric service outage information
First Responders | PSPS‑related outage | Phone/Text/E‑mail notifications | Automated notification tracking | PSPS Outage Start time, Portal updates, estimated time of restoration, AFN support resources, CRC locations,
First Responders | Restoration of service | Phone/Text/E‑mail notification | Automated notification tracking | Estimated time of restoration
MBL Program and SIV Customers | Wildfire | None | None | Electric service outage information, Community Based Support resources, safety information
MBL Program and SIV Customers | Wildfire‑related outage | Phone Call/Text/E‑mail regarding status of electric service | None | Electric service outage information, Community Based Support resources, safety information
MBL Program and SIV Customers | PSPS‑related outage | Phone/Text/E‑mail notifications, with re‑attempts | Request and track customer acknowledgements, doorbell rings deployed for non‑acknowledged prior to de‑energization | PSPS Outage Start time, estimated time of restoration, AFN support resources, CRC locations, PG&E support programs and rebates
MBL Program and SIV Customers | Restoration of service | Phone/Text/E‑mail notification | None | In event of relocation, understanding ability to safely return home.
Limited English Proficiency | Wildfire | None | None | Electric service outage information
Limited English Proficiency | Wildfire‑related outage | Phone | None | Electric service outage information, including estimated time of restoration is available in Spanish through blue sky outage notifications via phone.
Limited English Proficiency | PSPS‑related outage | Phone/Text/E‑mail | None | PSPS customer notifications are delivered in‑language if a customer’s language preference is on file. If there is no language preference on file, the notification is delivered in English. Customers with limited English proficiency have access to translation phone numbers, highlighting that translation services are available in over 240 languages.
Limited English Proficiency | Restoration of service | Phone | None | Confirmation that power is restored is available in Spanish through blue sky outage notifications via phone.
CBO in‑event support and resources | Wildfire | E‑mail from PG&E Emergency Operations Situation Room | Request acknowledgement of activation | Area of impact, including County/Zip code information.
CBO in‑event support and resources | Wildfire‑related outage | E‑mail from PG&E Emergency Operations Situation Room | Request acknowledgment of activation | Area of impact, including County/Zip code information. Estimated times of restoration.
CBO in‑event support and resources | PSPS‑related outage | E‑mail from PG&E Emergency Operations Situation Room | Request acknowledgement of activation | Area of impact, including County/Zip code information. Weather/De‑energization start times. Estimated times of restoration.
CBO in‑event support and resources | Restoration of service | E‑mail from PG&E Emergency Operations Situation Room | None | Zip Code/County level restoration information for demobilization activities.
CFI | Wildfire | Phone Call/Text/E‑mail regarding status of electric service | none | electric service outage information
CFI | Wildfire‑related outage | Phone Call/Text/E‑mail regarding status of electric service | none | Electric service outage information
CFI | PSPS‑related outage | Phone/Text/E‑mail notifications, with re‑attempts | Request and track customer acknowledgements | PSPS Outage Start time, estimated time of restoration
CFI | Restoration of service | Phone/Text/E‑mail notifications | none | confirming power is restored
Telecommunications and Water Providers | Wildfire | Phone Call/Text/E‑mail regarding status of electric service | None | Electric service outage information
Telecommunications and Water Providers | Wildfire‑related outage | Phone Call/Text/E‑mail regarding status of electric service | None | Electric service outage information
Telecommunications and Water Providers | PSPS‑related outage | Phone/Text/E‑mail notifications, with re‑attempts | Request and track customer acknowledgements | PSPS Outage Start time, estimated time of restoration
Telecommunications and Water Providers | Restoration of service | Phone Call/Text/E‑mail regarding status of electric service | None | Confirming power is restored
Transmission‑Level Entities | Wildfire | Phone Call/Text/E‑mail regarding status of electric service | NONE | Electric service outage information
Transmission‑Level Entities | Wildfire‑related outage | Phone Call/Text/E‑mail regarding status of electric service | NONE | Electric service outage information
Transmission‑Level Entities | PSPS‑related outage | Phone/Text/E‑mail notifications, with re‑attempts and direct engagement from Grid Control Center | Request and track customer acknowledgements | PSPS Outage Start time, estimated time of restoration, and phone number to Grid Control Center
Transmission‑Level Entities | Restoration of service | Grid Control Center contacts customer directly | None | If power has not been restored Grid Control Center phone number is provided
Third‑Party Commodity Suppliers | Wildfire | Phone Call/Text/E‑mail regarding status of electric service | none | Electric service outage information
Third‑Party Commodity Suppliers | Wildfire‑related outage | Phone Call/Text/E‑mail regarding status of electric service | none | Electric service outage information
Third‑Party Commodity Suppliers | PSPS‑related outage | Phone/Text/E‑mail notifications, with re‑attempts | Request and track customer acknowledgements | PSPS Outage Start time, estimated time of restoration
Third‑Party Commodity Suppliers | Restoration of service | Phone Call/Text/E‑mail regarding status of electric service | none | Confirming power is restored
Media | Wildfire | N/A | N/A | PG&E is not the lead entity providing information to the media regarding wildfires alone. That is the purview of the agency leading the response (typically CAL FIRE).
Media | Wildfire‑related outage | Various | Various | PG&E does not typically issue proactive notifications to media on wildfire‑related outages alone; if there are outages that media inquire about, PG&E will respond‑‑typically by e‑mail or phone‑‑explaining the nature of the outage.
Media | PSPS‑related outage | E‑mail | N/A | PG&E has documented procedures for sending alerts to the media when PG&E has alerted the public to the possibility of a PSPS event. These occur after customer notifications have been sent. PG&E will also respond to inbound media inquiries by phone and will grant interviews as appropriate.
News release
Media | Restoration of service | E‑mail | N/A | PG&E will often provide proactive updates to the media on service restoration—typically for larger events—by e‑mail or news release. PG&E will also respond to inbound media inquiries by phone and will grant interviews as appropriate.
News release
General Public | Wildfire | None | None | Electric service outage information
General Public | Wildfire‑related outage | Phone/Text/E‑mail | None | Electric service outage information, including estimated time of restoration
General Public | PSPS‑related outage | Phone/Text/E‑mail | None | PSPS forecasted time of de‑energization, estimated time of restoration, CRC and other customer support information, maps of impacted areas, preparedness and support resources
General Public | Restoration of service | Phone/Text/E‑mail | None | Confirmation that power is restored in case of relocation during outage.

## Table 11-10
TABLE 11‑10:
LIST OF TARGET COMMUNITIES 93
Target Community | Interests or Concerns Before, During, and After Wildfire and PSPS Events
MBL Allowance Program Participants (including individuals reliant on Life Support) | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications and the importance of notification acknowledgement to confirm receipt. Continuous power, including portable battery options and backup generation rebates for qualified customers, and overall resilience support available.
SIV or reliant on electricity for durable medical equipment or assistive technology | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications and the importance of notification acknowledgement to confirm receipt. Continuous power, including portable battery options and backup generation rebates for qualified customers, and overall resilience support available.
Income‑Qualified | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications. Available backup generation rebates for qualified customers, food replacement options, MBL Allowance Program and overall resilience support available.
Limited English Proficiency | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information and indicate language preference to receive notifications in preferred language. Available backup generation rebates for qualified customers and overall resilience support available. Education materials available in preferred language
Blind or Low Vision | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications. Available backup generation rebates for qualified customers and overall resilience support available. Education materials available in large print or Braille.
Deaf or Hard of Hearing | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications. Available backup generation rebates for qualified customers and overall resilience support available. Education materials are available in American Sign Language (ASL).
Disabled (Physical, Cognitive or Developmental) or Age 65+ | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications. Available backup generation rebates for qualified customers, food replacement options, MBL Allowance Program and overall resilience support available.
Residential and SMB Unassigned Customers of Record | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications. Available backup generation rebates for qualified customers.
Property Owners and Property Managers | How to educate tenants to drive awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to sign up for Address Level Alerts to receive direct notification of possible PSPS for non‑account holders and promotion of the MBL Program. Available backup generation rebates for qualified customers.
Critical Facilities | Awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information to receive notifications. Available backup generation resources and coordination of resilience plan with the utility.
CBO | How to educate consumers to drive awareness of and preparation for potential PSPS, wildfire or unplanned outages where EPSS is enabled, including how to update contact information (account holders) or sign up for Address Level Alerts to receive direct notification of possible PSPS (non‑account holders) and promotion of applicable programs such as the MBL Program, continuous power options, including portable battery options and backup generation rebates, and overall resilience support available.
Vegetation Management | For the systemwide Annual Maintenance and Second Patrol programs, PG&E sends notifications to customers via e‑mail ~3‑7 days in advance of both inspection and tree work.
For the Vegetation Control program (clearing around the base of poles), PG&E sends notifications to customers via e‑mail ~3‑7 days in advance of performing work. For this program, inspection and tree work are typically performed on the same day.
For the Integrated Vegetation Management program (transmission), PG&E sends direct mail to landowners notifying them of vegetation work along our transmission corridor. In 2025, PG&E will also begin sending email notifications to customers ahead of this work.
For select vegetation projects in sensitive areas (e.g., previous wildfire, old growth trees), PG&E may send a tailored notification to customers via direct mail or e‑mail. Additionally, PG&E may host a community open house to describe our work and answer questions in person.

## Table 11-11
TABLE‑11 11:
KEY GAPS AND LIMITATIONS IN PUBLIC EMERGENCY COMMUNICATION STRATEGY 96
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Errors in Automated Messaging deployment | During a PSPS event, at time of de‑energization, the process of deploying notifications to customers about current state of service to their location switches from a manual process with human actions to prep, stage and deploy notifications, to an automated system that is utilized for all outage communications. In certain cases, logic used for normal outage communications interfere with the automation of these messages, causing incorrect notifications, or no notification at all | Strategy: Work with OMT SME’s and program administrators to identify edge cases, like abnormal circuit configurations, mis‑mapped customers, and tools put in place to avoid duplicate messages to customers during blue sky outage communications.
Target Timeline: Communications around conflicts/issues with OMT Program team began when issue was known. Remedial actions put in place to correct (if possible) at that time. New processes and auditing tools put in place in December 2024 to review playbooks prior to sending notifications to attempt corrections, and validate service activity and notification preferences. Mis‑mapped customers reviewed by Operations to correct data for proper transformer assignment at conclusion of each event.
Notification Vendor performance | During several events, the vendor used for deploying PSPS notifications mishandled or disregarded files that needed to be processed/delivered, resulting in missed notifications to customers | Strategy: Ongoing dialog with Message Broadcast to identify root causes of missed notifications. Meeting on 12/6/24 with Message Broadcast leadership in San Ramon to discuss notification failures and re‑commitment from them to drive errors and miscommunication out of process. Payload testing and drills identified for Spring/Summer 2025 to practice and ensure readiness for PSPS events.
Target Timeline: By 7/1/25, conduct exercises and drills to determine that that file handling and notification deployment will be acceptable to meet PSPS compliance requirements on all notification requirements.

## Table PG&E‑11.4.3‑1
TABLE PG&E‑11.4.3‑1:
PG&E’S PUBLIC COMMUNICATION, OUTREACH, AND EDUCATION AWARENESS PROGRAMS 94
Core Activity | Event Type | Period of Application (Before, During, After Incident) | Name of Outreach or Education Program | Description of Program | Target Audience | Reference/ Link
Awareness and Preparedness Education | PSPS, Wildfire Safety, EPSS | Before, During, After Incident | CWSP | Virtual education about PSPS, wildfire safety, EPSS, etc. To educate all customers to be prepared. | Customers | www.pge.com/firesafetywebinars
Awareness and Preparedness Education | PSPS, Wildfire Safety, EPSS | Before, During, After Incident | CWSP | Virtual or in person education about PSPS, wildfire safety, EPSS, etc. To educate all customers to be prepared. | Customers | N/A
Awareness and Preparedness Education | PSPS, Wildfire Safety, EPSS | Before | CWSP | Virtual education about PSPS, wildfire safety, EPSS, etc. To educate partner agencies and organizations for message amplification. | In‑Home Support Services, Regional Centers, California Foundation for Independent Living Centers (CFILC), and other CBO Informational Partners | www.pge.com/firesafetywebinars
Awareness and Preparedness Education | PSPS, Wildfire Safety, EPSS | Before | CWSP | Virtual education about PSPS, wildfire safety, EPSS, etc. To educate partner agencies and organizations for message amplification. | Multi‑cultural media partners | N/A
Awareness and Preparedness Education | PSPS, EPSS, MBL | Before, during | CWSP | Radio, online and social media education about PSPS, EPSS, MBL, and other preparedness and resource information. | Customers, AFN, Master Meter, MBL, visitors, multi‑cultural | N/A
Awareness and Preparedness Education | PSPS, Wildfire Safety, EPSS | Before | CWSP | E‑mail outreach with awareness, preparedness and resources information about PSPS, wildfire safety, EPSS, contact information, etc. | Customers, AFN, Master Meter, MBL, CBOs | N/A
Awareness and Preparedness Education | PSPS, Wildfire Safety, EPSS | Before | CWSP | Direct mail outreach with awareness, preparedness and resources information about PSPS, wildfire safety, EPSS, contact information, etc. | Customers, AFN, MBL | N/A
TABLE PG&E‑11.4.3‑1:
PG&E’s Public Communication, Outreach, and Education Awareness Programs
(continued)
Core Activity | Event Type |  | Period of Application (Before, During, After Incident) | Name of Outreach or Education Program | Description of Program | Target Audience |  | Reference/ Link
Awareness and Preparedness Education | PSPS, Wildfire Safety, EPSS | Before |  | CWSP | Bill inserts with awareness, preparedness and resources information about PSPS, wildfire safety, EPSS, contact information, etc. | MBL |  | N/A
MBL Acquisition | MBL |  | Before | MBL | Acquisition outreach via paid media, social media, e‑mail and direct mail for the MBL Program. |  | AFN/MBL | N/A
EPSS Multiple Outage Follow‑Up | Wildfire Safety |  | After | CWSP | Acknowledgement of recent outages and actions PG&E is taking to improve reliability in the community. |  | Customers | N/A
EPSS Multiple Outage Follow‑Up | Wildfire Safety |  | After | CWSP | Acknowledgement of recent outages and actions PG&E is taking to improve reliability in the community. |  | Elected Officials | N/A
EPSS Multiple Outage Follow‑Up | Wildfire Safety |  | After | CWSP | Acknowledgement of recent outages and actions PG&E is taking to improve reliability in the community. |  | Customers | www.pge.com/firesafetywebinars
EPSS Multiple Outage Follow‑Up | Wildfire Safety |  | After | CWSP | Acknowledgement of recent outages and actions PG&E is taking to improve reliability in the community. |  | Customers, Elected Officials | N/A

## Table PG&E‑11.4.4‑1
TABLE PG&E‑11.4.4‑1:
IDENTIFYING AFN CUSTOMERS 95
Customer Group | Number of Customers
Customers enrolled in the MBL Program; | 248811
Residential customers on tiered rate plans;(a) | Redundant with MBL
Energy Savings Assistance (ESA) Program participants;(b) | 46203
Customers enrolled in California Alternate Rates for Energy (CARE) Program or Family Electric Rate Assistance (FERA); | 1419796
Customers that self‑identify as having a person with a disability in the household (e.g., disabled); | 41432
Customers who self‑select to receive utility communications in non‑standard format (e.g., in braille or large print); and | 1199
Customers who indicate a non‑English language preference. | 1542152
Customers that self‑identify as having a person in the household that uses durable medical equipment; | 52067
Customers that self‑identify as having a person in the household that uses Assistive Technology; | 8329
Customers that self‑identify as having a person in the household that has a hearing disability (e.g., deaf, or hard‑of‑hearing); | 26636
Customers that self‑identify as having a person in the household that has a vision disability (e.g., Low Vision); | 15859
Customers that self‑identify as having a person in the household that is blind; and | 1319
Customers that self‑identify as having a person in the household that is 65+ years old. | 79046
_______________
(a) Customers enrolled in MBL program may receive an additional allotment of electricity and/or gas per month (approximately 500 kilowatt‑hours of electricity or 12 percent discount if they are on an eligible electric rate, and/or 25 therms of gas per month).
(b) To qualify for the ESA Program, a residential customer’s household income must be at or below 200 percent of Federal Poverty Guidelines, as per D.05‑10‑044. See Appendix E.

## Table 12-1
TABLE 12‑1:
ENTERPRISE SYSTEMS TARGETS24
Initiative | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | 2026 End of Year Total / Completion Date | 2027 Total / Status | 2028 Total / Status | Section; Page Number
Enterprise System - Vegetation Management | VM Critical Datasets Data Quality Remediation (ES-01) | n/a | Started; January 2026 (a) | In Progress; 2027 (a) | Completed; December 31, 2028 (a) | 12.1.1; p. 546
Enterprise System - Asset Management and Inspection | Evaluate and create new methods(s) to improve the Accuracy of Asset Inventory Data (ES-02) | n/a | Started; March 2026 | In Progress; 2027 | Completed; December 31, 2028 | 12.1.1; p. 546
Enterprise System - Grid Monitoring | Grid Monitoring Sensor Systems Efficacy Assessment (ES-03) | n/a | Started; March 2026 | In Progress; 2027 | Completed; December 31, 2028 | 12.1.1; p. 546
Enterprise System - Weather Forecasting | Participate in Company Disaster Recovery Exercise (ES-04) | n/a | Completed; December 31, 2026 | n/a | n/a | 12.1.1; p. 546
Enterprise System - Risk Assessment | Integration of continuous grid monitoring technologies (ES-05) | n/a | Started; March 2026 | In Progress; 2027 | Completed; December 31, 2028 | 12.1.1; p. 546
Note:
(a) See 2026-2028 WMP Revision Notice Response R0, Critical Issue response RN-PGE-26-08 for additional information.

## Table 13-1
TABLE 13‑1:
LESSONS LEARNED 98
Year of Lesson Learned | Subject | Category and Source of Lessons Learned | Description of Lesson Learned | Proposed WMP Improvement | Timeline for Implementation | Reference
2023 | Undergrounding and System Hardening process efficiency | Cost and process efficiency opportunities | Program cost savings can be achieved through multiple mechanisms, such as lump sum contracts with vendors, and updating standards, such as spoils management and trench depth. | Negotiate and structure contract terms with undergrounding and system hardening vendors to support more cost‑effective services; Updated standard for the handling and testing of spoils to maximize efficiencies; updated standard for trench depth that provide exceptions for 24” depth in approved cases with hard rock excavation. | 2024 and 2025 | N/A
Source: internal continuous improvement effort
2023‑ | Undergrounding project management improvement | Enhancing the customer experience | We can improve the customer experience and optimize project schedules by engaging with customers earlier and regularly throughout an underground project. | Increased and enhanced customer communication channels and cadence based on key project milestones. | 2024 and 2025 | N/A
2024 |  | Source: customer feedback
2023‑ | Continuous focus on safety | Safety Standards | Contractor safety requirements can help prevent third‑party dig ins to utilities | Establish requirements for all contractors to develop and implement a Dig In Prevention procedure that aligns with PG&E’s Damage Prevention procedure. | 2025 | N/A
2024 |  | Source: internal continuous improvement effort
2023 | Improve inspection and remediation process | ACI – Addressing Risk from Hazard Trees Benchmarking | Considerations for remote sensing technologies may enable improved monitoring and identification of risk | Evaluate remote sensing technologies to inform inspection and remediation processes | 2025‑2026 | ACI PG&E‑23B‑15
2024 | Real‑time monitoring | Sensing intelligence to inform patrol and restoration and causal evaluations | Installation of Gridscope technology has provided enhanced intelligence on outage locations and in at least 10 instances has identified hazards prior to an outage and associated ignition. | Continue scaling the use of Gridscope as part of a real‑time monitoring strategy that provides multi‑sensor intelligence prior to ignition risk and supports monitoring of asset degradation. | 2025‑2028 | N/A
Source: internal continuous improvement effort
2024 | Feedback from Energy Safety, CPUC, or other authoritative bodies | ACI – Reduce customer impact from EPSS | The EPSS program has seen initial data results that demonstrate there is an improved reliability pick up where vegetation and animal mitigation work is performed. Additionally, the program has identified a customer group that has experienced more than five EPSS outages, year‑over‑year, since the expansion of the program in 2022. | The EPSS Program will maintain a focused effort on vegetation and animal mitigation work on circuit zones with a high frequency of vegetation or animal cause. The program will also enhance its efforts to target additional outage mitigation or direct customer support for those customers that have been most impacted. | 2025‑2028 | ACI PG&E 25U‑06
2024 | Internal monitoring and fault detection | ACI – Operations | The leading fault type for all outages that result in ignitions during EPSS protection continues to be from high impedance fault conditions. Since 2022, PG&E has deployed Downed Conductor Detection (DCD) capability to capture high impedance fault conditions within HFRA. DCD has been installed across 87 percent of the HFRA. These installations have reduced high impedance fault type ignitions but there remains a gap on extreme low amperage fault conditions that DCD cannot detect. | Enhance the sensitive ground fault pick‑ups to allow for detection of high impedance fault conditions not detectable by the existing DCD algorithm. Also, continue the reprogramming of SGF trip floor settings criteria to increase detection of faults to 5‑amp fault conditions within five seconds. | 2024‑2028 | ACI PG&E‑23‑14
2022 | Wildfire and resiliency work | Source: collaboration with local wildfire mitigation planning | Our wildfire and climate resiliency work is not connected to the work of communities and agencies | Wildfire & Climate Resiliency Chief is currently developing a Wildfire Resilience Corridors pilot with a community within our AOC. The pilot’s goal is to co‑develop wildfire mitigation programs and projects with pilot communities that will mutually benefit both community assets and utility infrastructure. | 2025 to 2028 | N/A

## Table PG&E‑13.2‑1
TABLE PG&E‑13.2‑1:
WORKING GROUPS AND LESSONS LEARNED 99
Energy Safety‑Required Meetings by Area for Continuous Improvement | Interactions Attended or Planned | Lessons Learned
ACI PG&E 25U‑02: Cross‑Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety | PacificCorp, PG&E, SCE, and SDG&E participate in monthly meetings in addition to the engagements referenced in Appendix D for ACI PG&E 25U‑02. | The utilities improved our understanding of the maturity of remote sensing technologies and learned how to utilize such technologies to supplement current practices. We also learned from each other’s demonstrations and use cases for remote sensing technologies such as satellite and LiDAR‑based identification.
The above referenced meetings are scheduled to continue through 2025.
ACI PG&E‑25U‑03: Continuation of Grid Hardening Joint Studies | PacificCorp, PG&E, SCE, and SDG&E participate in quarterly meetings to provide a platform to benchmark and share undergrounding best practices. | See Appendix D for ACI PG&E‑25U‑03, for applicable lessons learned.
PG&E, SCE, and SDG&E participate in bi‑monthly meetings to discuss mitigation effectiveness studies.
Liberty, PacificCorp, PG&E, Nevada Energy, SCE, and SDG&E participate in monthly meetings to discuss System Protection and Device Settings. These sessions also include discussions on Covered Conductors.
These meetings are scheduled through 2025.
ACI PG&E23B‑22: Continuation of Effectiveness of Enhanced Clearance Joint Study | PG&E, SCE, and SDG&E participate in bi‑monthly meetings to conduct ongoing discussions regarding enhanced VM mitigation efforts. | See Appendix D for ACI PG&E23B‑22 for applicable lessons learned.
The above referenced meeting is scheduled to continue through 2025.

## Table 13-2
Table 13-2
LESSONS LEARNED FROM DISCONTINUED ACTIVITIES
Discontinued Activity (Tracking ID) | Rationale for Discontinuation | Lessons Learned | Replacement Activities (Include Page # Where Discussed)
Transmission – Ground Detailed Inspection Program (AI‑02) and Transmission – Aerial Detail Inspection (AI‑04) | Programs are being combined based on visual aspects of both programs. The program is now known as Transmission – Detailed Inspection Program | Combing Ground and Aerial programs into one target allows for flexibility to address wildfire risk by method choice to best suit location and structure type. | Transmission – Detailed Inspection Program Section 8.3.1; p. 232
Transmission Climbing Detailed Inspection Program (AI‑05) | Program to still continue, but not under WMP commitment. | Climbing program focuses on 500 kV steel structure integrity which is not common source of ignition. | Transmission – Detailed Climbing Inspection Program Section 8.3.2; p. 234
Substation Supplemental Inspections (removal of ground and infrared inspections and continuing aerial drone inspections as a part of routine inspections) (Formerly AI‑08, AI‑09, and AI‑10) | The WMP substation supplemental inspection program was originally developed to focus on ignition risks independent from existing routine substation inspections. A comparative analysis of supplemental and routine inspections was completed in 2023 and 2024. This analysis confirmed redundancy and equal effectiveness of two of the three methods—ground and infrared inspection. Furthermore, substation routine ground inspections are performed more frequently, monthly or bi‑monthly, in comparison to the annual supplemental inspection. PG&E proposes to streamline substation inspections by removing duplicative ground and infrared inspections, while retaining drone‑based aerial inspections as a part of the routine inspections process. The drone‑based aerial inspection provides unique risk detection perspectives not captured from the ground and infrared methods. The routine substation inspection program will continue to provide ground and infrared inspections to substations pursuant to GO 174. Power Generation Switchyards are regulated either by GO 167, or Federal Energy Regulatory Commission (FERC) in situations where operations are under a FERC license. These regulatory commitments focus on maintenance and operations requirements, and do not identify an inspection requirement. Power Generation performs routine inspections of switchyards in alignment with substation routine inspection program. | PG&E originally planned supplemental inspection targets by requiring three separate methods for each single supplemental inspection: ground, infrared, and aerial. The 2026‑2028 WMP will continue with drone‑based aerial inspections as a part of the ongoing routine inspection process but will remove the duplicative ground and infrared supplemental inspection methods. This proposed change is expected to yield equivalent ignition risk detectability while streamlining the inspections programs to be more efficient. | Substation Drone Inspection Program Section 8.3.15; p. 258
Filling Asset Inventory Data Gaps (AI-11) | AI-11 has been replaced by ES-02. | This activity will continue under ES-02, which is described in Section 12.1.1. | Evaluate and create new method(s) to improve the accuracy of asset inventory data (ES 02) Section 12.1.1; p. 546
Community Engagement - Meetings (CO-01) | This activity is being reported on externally in other forums. | PG&E will incorporate this activity into Section 11.4.3 | Section 11.4.3; p. 522
Community Engagement - Surveys (CO-02) | This activity is being reported on externally in other forums. | PG&E will incorporate this activity into Section 11.4.3 | Section 11.4.3; p. 522
Complete PSPS and Wildfire Tabletop and Functional Exercises (EP-01) | This activity is being reported on externally in other forums. | This Emergency Preparedness program addresses hazards beyond wildfires and we have worked to ensure wildfire related activities are included within these processes. | n/a
Maintain all hazards planning and preparedness program in 2023-2025 (EP-02) | This activity is being reported on externally in other forums. | This Emergency Preparedness program addresses hazards beyond wildfires and we have worked to ensure wildfire related activities are included within these processes. | n/a
Expand all hazards planning to include additional threats and scenarios in 2023-2025 (EP-04) | This activity is being reported on externally in other forums. | This Emergency Preparedness program addresses hazards beyond wildfires and we have worked to ensure wildfire related activities are included within these processes. | n/a
Annually review of CERP and the two wildfire related annexes (EP-06) | This activity is being reported on externally in other forums. | This Emergency Preparedness program addresses hazards beyond wildfires and we have worked to ensure wildfire related activities are included within these processes. | n/a
Threats and Hazards Identification and Risk Assessment (THIRA) updates executive briefings (EP-08) | This activity is being reported on externally in other forums. | The THIRA is an all hazard identification beyond just wildfires and we have worked to ensure wildfire related activities are included in these processes. | n/a
System Hardening – Distribution (GH-01) (a) | Revised Overhead Hardening Distribution Target (GH-12) and new Line Removal Enabled by Remote Grid Target (GH-14). | These activities have been incorporated into GH-12, described in Section 8.2.1, and GH-14, described in Section 8.2.7.1. | Covered Conductor Installation Section 8.2.1; p. 184 Remote Grids Section 8.2.7.1, p. 211
Reduce PSPS impacts to customer events (PS-07) | Significant progress made during the 2023-2025 WMP cycle to reduce PSPS impacts to customers. | Significant progress made during the 2023-2025 WMP cycle to reduce PSPS impacts to customers | n/a
Artificial Intelligence in Wildfire Cameras (SA-01) | SA-01 is continued under SA-08. | PG&E will incorporate this activity under SA-08 described in Section 10.4.1. | Existing Ignition Detection Sensors and Systems Section 10.4.1; p. 456
LiDAR Data Collection – Transmission (VM-01) | We will continue to improve remote sensing with LiDAR and Satellite technologies. | - LiDAR tree analytics capture risk in the system - Inspectors use LiDAR analytics for all spans in Transmission - Satellite or Spaceborne data pilots for Transmission is in progress | Satellite technology evaluation in progress Section 9.2; p. 364
Focused Tree Inspections (FTI) (VM‑03) | Component(s) of the initiative will be incorporated into the Distribution Routine Patrol program. | PG&E is still in the process of evaluating which component(s) of the FTI scope may be incorporated into the Distribution Routine Patrol program. This analysis will be based on findings from efficacy studies planned to be performed in 2025. | Distribution Routine Patrol Section 9.2.1; p. 366
Tree Removal Inventory (TRI) (VM‑04) (b) | Revised to Mitigation of Legacy Tree Removal Inventory (TRI) (VM-26). | In the proposed consolidated program structure, the process of what was the legacy TRI program will occur during the distribution routine programs. See VM-26. | Distribution Routine Patrol Section 9.2.1; p. 366
Evaluate emerging technologies (VM-12) | This work will continue under new VM Enterprise Systems qualitative target. | VM is evaluating emerging technologies as it pertains to individual programs. For example, VM distribution inspections is reviewing remote sensing technology for potential incorporation into this program’s process. | Distribution Routine Patrol Section 9.2.1; p. 366
Vegetation Management for Operational Mitigations (VMOM) (VM‑18) | Component(s) of the initiative will be incorporated into Activities Based on Weather Conditions | PG&E will incorporate VMOM into activities described in Section 9.9.1. | Activities Based on Weather Conditions Section 9.9.1; p. 411
Smart Tape (N/A) | PG&E funded a lab‑only proof of concept in 2022‑2023 using the EPSS Emergent Technology expense budget to evaluate the feasibility of using “smart tape” technology for rapid fault location on EPSS‑enabled lines. The proof of concept was structured in three phases. PG&E decided to conclude the project at the end of Phase II, due to the following findings: 1) The vendor had not demonstrated sufficiently rapid product development progress in line with PG&E’s needs. 2) The proposed equipment design had moved away from initial “smart tape” concept to a larger, bulkier design that no longer held unique value proposition compared to other market‑available sensors 3) The proposed design was not compatible with PG&E’s desire for cost‑effectiveness at scale. | This effort validated the use of a phased approach with clear exit clauses when evaluating solutions with low technology readiness levels. This type of phased approach allows PG&E to engage with technology vendors iterating on early prototypes while managing the inherent risks of early‑stage technology. PG&E’s contract structure and overall approach with the “smart tape” vendor has provided a model for other engagements involving low technology readiness levels. | Real time monitoring for wildfire risk reduction, including, but not limited to Gridscope. For more information on Gridscope, see Section 8.7.1.3.2; p. 345
(a) See 2026-2028 WMP Revision Notice Response R0, Critical Issue RN‑PGE‑26‑04 for additional information.
(b) See 2026-2028 WMP Revision Notice Response R0, Critical Issue RN‑PGE‑26‑09 for additional information.

## TABLE PG&E-RN-PGE-26-04-01
TABLE PG&E-RN-PGE-26-04-01
UPDATED GH-12 AND GH-14 TARGETS
WMP Initiative | 2026 | 2027 | 2028 | 2026-2028 Total
Revised GH-12 – Overhead Hardening - Distribution | 294 | 190 | 190 | 674
(New) GH-14 – Line Removal Enabled by Remote Grid – Distribution | 4 | 0 | 0 | 4

## TABLE PG&E-RN-PGE-26-04-02
TABLE PG&E-RN-PGE-26-04-02:
ADJUSTMENTS TO GH-12 TARGETS
| 2026 | 2027 | 2028 | 2026-2028 Total
Original WMP Targets: GH-12 | 318 | 200 | 200 | 718
Adjustment: remove remote grid LR | -24 | -10 | -10 | -44
Revised WMP Targets: GH-12 | 294 | 190 | 190 | 674

## TABLE PG&E-RN-PGE-26-05-01
TABLE PG&E-RN-PGE-26-05-01:
ORIGINAL AND REVISED GH-04 TARGETS
| 2026 | 2027 | 2028 | 2026-2028 Total
Original WMP Targets: GH-04 | 370 | 307 | 400 | 1077
Adjustment: remove community rebuild UG ​ | -10​ | 0​ | 0​ | -10​
Revised WMP Targets: GH-04​ | 360​ | 307​ | 400 ​ | 1067

## TABLE PG&E-RN-PGE-26-05-02
TABLE PG&E-RN-PGE-26-05-02:
GH-04 TARGET BREAKDOWN
| 2026 | 2027 | 2028 | 2026-2028 Total
Revised WMP Targets: GH-04 | 360 ​ | 307​ | 400 ​ | 1067
Known Fire Rebuild UG | 2 | 7 | 0​ | 9
Planned UG (non-rebuild) | 358 | 300 | 400 | 1058

## TABLE PG&E-RN-PGE-26-05-03
TABLE PG&E-RN-PGE-26-05-03:
GH-12 TARGET BREAKDOWN
| 2026 | 2027 | 2028 | 2026-2028 Total
Revised WMP Targets: GH-12 | 294 | 190 | 190 | 674
Known Fire Rebuild OH | 0 | 1 | 0 | 1
Planned OH (non-rebuild) | 294 | 189 | 190 | 673

## TABLE PG&E-RN-PGE-26-07-01
TABLE PG&E-RN-PGE-26-07-01:
TEST INSPECTION TARGETS
| 2021 - 2025 | 2026-2028
Non-HFTD | 561 | 348
HFTD Tier 3, Tier 2, Zone 1, and HFRA | 393 | 0

## TABLE PG&E-RN-PGE-26-07-02
TABLE PG&E-RN-PGE-26-07-02:
INSPECTION PROGRAM FIND RATES
Inspection Activity (Program) | Frequency or Trigger | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Switch Function Tests | 8 years | 0.6% | 17% | 0.5%
Detailed (AI-04) and Infrared (AI-06) | 3 years or WTRM | 0.6% | 29.7% | 1.5%

## Table PG&E-RN-PGE-26-08-01
Table PG&E-RN-PGE-26-08-01:
Wood Management Benchmarking Target (VM-23) Timeline and Milestones
Activity # | Phase | Activity | Start Date | End Date
1 | Develop and Implement | Identify peer utility points of contact for Wood Management benchmarking. | 1/1/2026 | 2026-06-30
2 | Develop and Implement | Facilitate kickoff call, share points of interest, and align with each peer utility on benchmark direction. | 2026-07-01 | 2026-09-30
3 | Develop and Implement | Draft and finalize questions for benchmark survey and distribute to participants. | 2026-10-01 | 2026-12-31
4 | Develop and Implement | Collect peer utility Benchmark surveys. | 2027-01-01 | 2027-03-31
5 | Review Results | Process responses and identify common themes and potential best practices; share results with other utilities. | 2027-04-01 | 2027-06-30
6 | Review Results | Complete discussions with other utilities regarding potential agreement on best practices that may be collectively implemented, if any. | 2027-07-01 | 2027-09-30
7 | Practice Adoption | Complete implementation of any relevant updates to PG&E procedure, if applicable. | 2027-10-01 | 2028-09-30

## Table PG&E-RN-PGE-26-08-02
Table PG&E-RN-PGE-26-08-02
Workforce Planning – Vegetation Management Target (VM-24) Timeline and Milestones
Activity # | Target Category | Target | Start Date | End Date
1 | Recruitment | Provide $1,500,000 of funding towards Community College scholarships towards recruitment of individuals who are looking to pursue a VM career path through the Community College VM programs. | 2026-01-01 | 2027-12-31
2 | Retention | Provide $10,000 funding annually to support retention by paying for the following VM-related certifications and memberships such as: | Annual Cycles:
|  | · Arborist Certification | 01/01/2026 – 12/31/2026
|  | · TRAQ (Tree Risk Assessment Qualified) Certification | 01/01/2027 – 12/31/2027
|  | · CTSP (Certified Tree Safety Professional) Certification | 01/01/2028 – 12/31/2028
· ISA (International Society of Arboriculture) Membership
· UAA (Utility Arborist Association) Membership
3 | Training | Complete annual audit of completion of One VM Training and Basic Curriculum courses for VMI Personnel | Annual Cycles:
01/01/2026 – 12/31/2026
01/01/2027 – 12/31/2027
01/01/2028 – 12/31/2028

## Table PG&E-RN-PGE-26-08-03
Table PG&E-RN-PGE-26-08-03
Integrated Vegetation Management Benchmarking Target (VM-25) Timeline and Milestones
Activity # | Phase | Activity | Start | Due Date
1 | Develop and Implement | Identify peer utility points of contact for Integrated Vegetation Management benchmarking. | 1/1/2026 | 2026-06-30
2 | Develop and Implement | Facilitate kickoff call, share points of interest, and align with each peer utility on benchmark direction. | 2026-07-01 | 2026-09-30
3 | Develop and Implement | Draft and finalize questions for benchmark survey and distribute to participants. | 2026-10-01 | 2026-12-31
4 | Develop and Implement | Collect peer utility Benchmark surveys. | 2027-01-01 | 2027-03-31
5 | Review Results | Process responses and identify common themes and potential best practices; share results with other utilities. | 2027-04-01 | 2027-06-30
6 | Review Results | Complete discussions with other utilities regarding potential agreement on best practices that may be collectively implemented, if any. | 2027-07-01 | 2027-09-30
7 | Practice Adoption | Complete implementation of any relevant updates to PG&E procedure, if applicable. | 2028-01-05 | 2028-12-31

## Table PG&E-RN-PGE-26-08-04
Table PG&E-RN-PGE-26-08-04
VM Critical Data Sets Data Quality Remediation (Vegetation Management) Target (ES-01) Timeline and Milestones
Focus Area | Target | Start | Due Date
Manage critical datasets | Achieve active management of the 4 highest-prioritized critical datasets. | 2026-01-01 | 2026-12-31
Maintain critical datasets | Enable monitoring of 4 managed critical datasets. | 2026-01-01 | 2026-12-31
Mitigate data quality issues | Develop annual report of identified DQ issue remediations. | 2026-01-01 | 2026-12-31
Manage critical datasets | Achieve active management of additional 6 highest prioritized critical datasets (10 cumulative total). | 2027-01-01 | 2027-12-31
Maintain critical datasets | Enable monitoring of 10 managed critical datasets. | 2027-01-01 | 2027-12-31
Mitigate data quality issues | Develop annual report of identified DQ issue remediations. | 2027-01-01 | 2027-12-31
Manage critical datasets | Achieve active management of additional 8 highest prioritized critical datasets (18 cumulative total). | 2028-01-01 | 2028-12-31
Maintain critical datasets | Enable monitoring of 18 managed critical datasets. | 2028-01-01 | 2028-12-31
Mitigate data quality issues | Develop annual report of identified DQ issue remediations. | 2028-01-01 | 2028-12-31

## Table PG&E-RN-PGE-26-09-01
Table PG&E-RN-PGE-26-09-01
Program Consolidation Timeline and Milestones
Activity # | Phase | Activity | Start | Due Date
1 | Data Gathering and Analysis | Data assessment | 2025-08-01 | 2025-08-30
2 | Data Gathering and Analysis | Perform remote sensing technology evaluation | 2025-08-01 | 2025-10-15
3 | Scope Definition | Define Distribution Routine Patrol program scope | 2025-08-01 | 2025-10-30
4 | Technology Development and Change Management | Develop 2026 workplan | 2025-10-15 | 2025-11-15
5 | Technology Development and Change Management | Implement One VM technology enhancement(s) | 2025-08-01 | 2025-12-15
6 | Technology Development and Change Management | Update Distribution Routine Patrol procedure(s), as required | 2025-11-01 | 2025-12-15
7 | Technology Development and Change Management | Conduct training(s) on updated procedures and/or One VM changes | 2025-11-15 | 2025-12-31
8 | Technology Development and Change Management | Update One VM technical documentation | 2025-08-01 | 2025-12-31
9 | Continuous Improvement | Iteratively update Distribution Routine Patrol program scope, if applicable | 1/1 annually, if applicable | 12/31 annually, if applicable

## Table PG&E-13.3-1
Table PG&E-13.3-1
COMPLETED WMP ACTIVITIES
Activity | 2023‑2025 WMP Section Number | 2023‑2025 WMP Activity Tracking ID | Completion Year
Installation of System Automation Equipment – Distribution Protective Devices | 8.1.2.8.1 | GH‑07 | 2023
Installation of System Automation Equipment – Installation of Devices to Eliminate High Impedance Back feed Conditions | 8.1.2.10.2 | n/a | 2024
Line Removal (in the HFTD) – Transmission | 8.1.2.9.1 | n/a | 2024
Motor Switch Operator Switch Replacement | 8.1.2.10.3 | GH‑09 | 2024
Non-Exempt Surge Arrester Replacement | 8.1.2.10.4 | GH‑08 | 2024
Replace Non‑Exempt Expulsion Fuses | 8.1.2.10.5 | GH‑10 | 2025
Other Grid Topology Improvements to Mitigate or Reduce PSPS Events – Transmission | 8.1.2.11.1 | n/a | 2023
Other Grid Topology Improvements to Mitigate or Reduce PSPS Events – Distribution | 8.1.2.11.2 | n/a | 2023
Other Grid Topology Improvements to Mitigate or Reduce PSPS Events – Substation | 8.1.2.11.3 | n/a | 2022
The Calistoga Temporary Microgrid (There are currently no plans to deactivate the remaining 12 active temporary microgrids) | 8.1.2.7.2 | n/a | 2025
Retainment of Inspectors and Internal Workforce Development | 8.1.9.1 | AI-01 | 2025
Develop Distribution Aerial Inspections Program | 8.1.3.2.7 | AI-03 | 2023
Evaluate Covered Conductor Effectiveness | 8.1.2.1 | GH-02 | 2025
Evaluate and Implement Covered Conductor Effectiveness Impact on Inspections and Maintenance Standard | 8.1.2.1 | GH-03 | 2023
System Hardening - Transmission | 8.1.2.5.1 | GH-05 | 2024
HFTD/HFRA Open Tag Reduction – Transmission | 8.1.7.1 | GM-02 | 2024
EPSS – Down Conductor Detection | 8.1.2.10.1 | GM-06 | 2024
Eliminate HTFD/HFRA Distribution Backlog | 8.1.7.2 | GM-08 | 2023
Evaluate enhancements for the PSPS Transmission guidance | 9.2.1 | PS-01 | 2025
Evaluate incorporation of approved IPW enhancements into the PSPS Distribution guidance | 9.2.1 | PS-02 | 2025
Pilot using drones for PSPS restoration | 9.1.2 | PS-11 | 2024
Evaluate the transition of the Portable Battery Program to permanent battery solutions | 8.5.3 | PS-05 | 2025
Provide portable batteries to PG&E customers | 8.5.3 | PS-06 | 2025
Evaluate emerging technologies to reduce PSPS customer impact | 9.1.2 | PS-08 | 2025
Reduce PSPS impacts via Undergrounding | 9.1.2 | PS-09 | 2025
EFD and DFA Reporting | 8.3.3.1 | SA-03 | 2025
FPI and IPW Modeling - Revision Evaluation | 8.3.6.3 | SA-04 | 2025
Evaluate FPI and IPW Modeling enhancements in 2023 - 2025 | 8.3.6.3 | SA-05 | 2025
Monitor and evaluate the Cameras AI system’s performance | 8.3.2.3 | SA-07 | 2025
EFD and DFA Reporting | 8.3.3.1 | SA-09 | 2025
Evaluate FPI and IPW Modeling enhancements in 2026 - 2032 | 8.3.6.3 | SA-06 | 2025
Constraint Resolution Procedural Guideline | 8.2.6 | VM-09 | 2025
One VM Application Record Keeping Enhancement (Routine, Second Patrol) | 8.2.4 | VM-19 | 2024
Record Keeping Enhancement (VMOM, TRI) | 8.2.4 | VM-20 | 2024
Focused Tree Inspection (FTI) Program Record Keeping Enhancement | 8.2.2.2.5 | VM-21 | 2024
Inspection in HFTD and HFRA supporting key vegetation management initiatives | 8.2.2 | VM-10 | 2024
Enhance and refine Focus Tree Inspection – Areas of Concern (AOC) | 8.2.2.2.5 | VM-11 | 2024

## Table ACI PG&E-25U-01-1
TABLE ACI‑PG&E‑25U‑01‑1:
CORRELATION BETWEEN SUB MODELS AND OUTAGE MODELS

## Table ACI‑PG&E‑25U‑04‑1
TABLE ACI‑PG&E‑25U‑04‑1:
INSPECTION SCENARIO SUMMARY
Scenarios | Scenario Description | Detailed Inspections | Scan Inspections | Eyes‑on‑Risk | Total Cost | CBR (x10^‑8)
WMP Proposed | All structures receive detailed inspections every three years with Extreme/Severe/High structures also receiving scans in between years, such as the overall frequencies are extreme and severe inspected every year (either by detailed or scan), high inspected every two years (either by detailed or scan), low and medium inspected every three years (by detailed). | 218395 | 37042 | 57% | $32.8 million | 1.737
1 | Extreme and severe consequence plat maps inspected annually, high inspected every two years, low and medium inspected every three years. | 238310 | – | 49.7% | $33.4 million | 1.489
2 | Extreme, severe, and high consequence plat maps inspected annually, medium and low inspected every three years. | 278848 | – | 66% | $39.0 million | 1.691
3 | Extreme, severe, and high consequence plat maps inspected annually, medium inspected every two years, and low inspected every three years. | 326053 | – | 72.2% | $45.6 million | 1.582
4 | Extreme and severe consequence plat maps inspected annually, high and medium inspected every two years, low inspected every three years. | 285516 | – | 55.9% | $40.0 million | 1.398
5 | Changing the severe consequence percent rank from less than or equal to 99 percent and greater than 98 percent to less than or equal to 99 percent and greater than 95 percent and inspecting extreme and severe consequence plat maps annually, high every two years, medium and low every three years. | 251556 | – | 57.1% | $35.2 million | 1.622

## Table ACI‑PG&E‑25U‑04‑2
TABLE ACI‑PG&E‑25U‑04‑2:
COMPARISON OF RISK MODELS PERCENTILE GROUPINGS USED IN DISTRIBUTION INSPECTION PLANNING
| Risk Model | Factor | Extreme | Severe | High | Medium | Low
2023‑2025 WMP | WDRM v3 | Consequence | 0‑1% | 1‑2% | 1‑10% | 10‑20% | 20‑100%
2026‑2028 WMP Proposal | WDRM v4 | Risk OR | 0‑1% | 1‑2% | 1‑10% | 10‑20% | 20‑100%
|  | Consequence | 0‑1% | 1‑2% | 1‑10% | 10‑40% | 40‑100%

## Table ACI‑PG&E‑25U‑05‑1
TABLE ACI‑PG&E‑25U‑05‑1:
IONA PROGRAM 2024 RESULTS SUMMARY
Category | Investigation Count |  |  | Transformer Count | Comments
| Non‑HFTD | HFTD2/3 | Total
Successful Intervention – Replaced Transformer | 29 | 9 | 38 | 44 | Incipient transformer failures – remediation initiated through IONA(a)
Successful Prediction – Replaced Transformer | 14 | 4 | 18 | 18 | Transformer Failures – remediation initiated independent of IONA
Sub‑total – Transformer Remediation | 43 | 13 | 56 | 62
Successful Intervention – Non‑TX Remediation | 81 | 23 | 104 | – | Non‑transformer risks – remediation initiated through IONA
Successful Prediction – Non‑TX Remediation | 11 | 4 | 15 | – | Non‑transformer risks – remediation initiated independent of IONA
Sub‑total – Non Transformer Remediation | 92 | 27 | 119 | –
Non‑Risk Issue | 80 | 21 | 101 | – | Outages, SmartMeter data issues etc.
False Positive Prediction | 5 | 1 | 6 | – | False positive prediction by model
Total | 220 | 62 | 282 | –
_______________
(a) Transformer count higher than investigation count since some locations involved transformer banks
Notes:
· Successful Intervention: IONA predicted issue, remediated through IONA workflow.
· Successful Prediction: IONA predicted issue, remediation was initiated independent of IONA workflow.

## Table ACI‑PG&E‑25U‑05‑2
TABLE ACI‑PG&E‑25U‑05‑2:
RISK REDUCTION CALCULATION PER WDRM v4
Risk Reduction Category | Risk Reduction Calculated Using WDRM v4
Transformer Unit Replacements (44 Transformers) | 1.1924
Additional Equipment Replaced (Pole, crossarm) | 0.00038005
Total Risk Reduction | 1.1928