## README
In the event of a discrepancy between the tables in these sheets and respective tables in the content of SCE's 2026-2028 Wildfire Mitigation Plan, the latest version of SCE's 2026-2028 Wildfire Mitigation Plan in PDF format should be interpreted as containing the latest and correct information.

## Table B-01
Table B-01: SCE Model Inventory
Model Name | Model Description | Inputs | Outputs
Overhead Conductor Equipment/Facility Failure (EFF) | Model predicts outages with potential to cause sparks where the leading factor is equipment failure | GIS Conductor Data, Conductor Physical Characteristics, Vegetation Inspection/Proximity, Aggregated Climatology, Short Circuit Duty, Current Flux Density | Probability of Failure
Overhead Conductor Contact with Foreign Object (CFO) | Model predicts outages with potential to cause sparks where the leading factor is contact with a foreign object | GIS Conductor Data, Conductor Physical Characteristics, Vegetation Inspection/Proximity, Aggregated Climatology, Fatality Analysis Reporting System | 6 Way Multi Label (Vegetation, Animal, Vehicle Hit, Balloon, Other, Unknown) Probability of Failure
Transformer Failure Sub-Model | Model predicts transformer failures as indicated by deterioration, damage, and failure SAP replacement codes | Transformer Inventory Data, Aggregated Climatology, Short Circuit Duty, Meter Usage | Probability of Failure
Switch Failure Sub-Model | Model predicts switch failures as indicated by deterioration, damage, and failure SAP replacement codes and inspection notifications | Switch Inventory Data, Switching Operations, Aggregated Climatology, Short Circuit Duty | Probability of Failure
Capacitor Notification Sub-Model | Model predicts capacitor failures as indicated by deterioration, damage, and failure inspection notifications | Capacitor Inventory Data, Aggregated Climatology, Capacitor Health Data (automated devices), Historical Circuit Reliability | Probability of Failure

## Table SCE B-01
Table SCE B-01 - De-energization Thresholds [1]
Unhardened Thresholds | FPI > 12 AND Wind (Sustained) > 31 mph OR Wind (Gust) > 46 mph
Hardened Thresholds | FPI > 13 in all Fire Climate Zones (FCZs) except Zone 1 “Coastal” where FPI > 12 is used AND Wind (Sustained) > 40 mph OR Wind (Gust) > 58 mph.
[1] Thresholds may be adjusted in an actual PSPS event based on the risks and complexities associated with the event and the specific risk factors associated with each circuit. Information on specific threshold adjustments can be found in the PSPS-post event reports for each event.

## SCE-25U-05
SCE-25U-05 Transmission Conductor Splice Assessment 2023-2024 Findings
| a) FLOC | b) Detail (phase and sub-conductor) | c) X-ray Inspection Date | d) Date of Aerial Inspection Prior to X-ray | e) Date of Most Recent Ground Inspection Prior to X-ray | f) Date of Most Recent Infrared Inspection Prior to X-ray | g) Circuit Name | Circuit ET | h) Findings (P1, P2, P3, None) | i) Failure Mode
1 | OH-7018670 | T17-3 to T17-4 Left Phase Left Sub | 2023-01-23 | 2022-06-29 | 2022-06-02 | 2021-09-30 | PARDEE-VINCENT NO. 1 | ET-01925 | P3 | Lack of grease and improper crimps
2 | OH-7018670 | T17-3 to T17-4 Left Phase Right Sub | 2023-01-23 | 2022-06-29 | 2022-06-02 | 2021-09-30 | PARDEE-VINCENT NO. 1 | ET-01925 | P3 | Lack of grease and improper crimps
3 | OH-7018670 | T17-3 to T17-4 Middle Phase Left Sub | 2023-01-23 | 2022-06-29 | 2022-06-02 | 2021-09-30 | PARDEE-VINCENT NO. 1 | ET-01925 | P3 | Lack of grease
4 | OH-7018670 | T17-3 to T17-4 Middle Phase Right Sub | 2023-01-23 | 2022-06-29 | 2022-06-02 | 2021-09-30 | PARDEE-VINCENT NO. 1 | ET-01925 | P3 | Lack of grease and improper crimps
5 | OH-7018670 | T17-3 to T17-4 Right Phase Left Sub | 2023-01-23 | 2022-06-29 | 2022-06-02 | 2021-09-30 | PARDEE-VINCENT NO. 1 | ET-01925 | P3 | Lack of grease
6 | OH-7018670 | T17-3 to T17-4 Right Phase Right Sub | 2023-01-23 | 2022-06-29 | 2022-06-02 | 2021-09-30 | PARDEE-VINCENT NO. 1 | ET-01925 | P3 | Lack of grease and improper crimps
7 | OH-4388661E | Top Phase | 2023-01-26 | 2022-03-03 | 2022-05-20 | 2022-04-27 | MOORPARK-CRATER-MALIBU | ET-01408-M | P2 | Steel core gap
8 | OH-4388661E | Middle Phase | 2023-01-26 | 2022-03-03 | 2022-05-20 | 2022-04-27 | MOORPARK-CRATER-MALIBU | ET-01408-M | P2 | Splice is curved
9 | OH-4388661E | Bottom Phase | 2023-01-26 | 2022-03-03 | 2022-05-20 | 2022-04-27 | MOORPARK-CRATER-MALIBU | ET-01408-M | P2 | Steel core gap, splice is curved
10 | OH-7027499 | T19-2 to T19-3 Left Phase Left Sub | 2023-05-10 | 2021-05-21 | 2022-04-25 | 2023-04-21 | DEVERS-VALLEY NO 2 | ET-00072 | None | N/A
11 | OH-7027499 | T19-2 to T19-3 Left Phase Right Sub | 2023-05-10 | 2021-05-21 | 2022-04-25 | 2023-04-21 | DEVERS-VALLEY NO 2 | ET-00072 | None | N/A
12 | OH-7027499 | T19-2 to T19-3 Middle Phase Left Sub | 2023-05-10 | 2021-05-21 | 2022-04-25 | 2023-04-21 | DEVERS-VALLEY NO 2 | ET-00072 | None | N/A
13 | OH-7027499 | T19-2 to T19-3 Middle Phase Right Sub | 2023-05-10 | 2021-05-21 | 2022-04-25 | 2023-04-21 | DEVERS-VALLEY NO 2 | ET-00072 | None | N/A
14 | OH-7027499 | T19-2 to T19-3 Right Phase Left Sub | 2023-05-10 | 2021-05-21 | 2022-04-25 | 2023-04-21 | DEVERS-VALLEY NO 2 | ET-00072 | None | N/A
15 | OH-7027499 | T19-2 to T19-3 Right Phase Right Sub | 2023-05-10 | 2021-05-21 | 2022-04-25 | 2023-04-21 | DEVERS-VALLEY NO 2 | ET-00072 | None | N/A
16 | OH-A1320800E | A1320800E to A1320801E East Span, Bottom Phase | 2023-05-10 | 2022-03-15 | 2023-03-16 | 2021-10-21 | DEVERS-BANNING-WINDPARK | ET-01911 | P1 | Steel core gap
17 | OH-A1320777E | A1320777E to A1320776E West Span, Bottom Phase | 2023-05-10 | 2022-03-24 | 2023-03-24 | 2021-10-21 | DEVERS-BANNING-WINDPARK | ET-01911 | None | N/A
18 | OH-A1320777E | A1320777E to 1320778E East Span, Bottom Phase | 2023-05-10 | 2022-03-24 | 2023-03-24 | 2021-10-21 | DEVERS-BANNING-WINDPARK | ET-01911 | None | N/A
19 | OH-A1320777E | A1320777E to 1320778E East Span, Top Phase | 2023-05-10 | 2022-03-24 | 2023-03-24 | 2021-10-21 | DEVERS-BANNING-WINDPARK | ET-01911 | None | N/A
20 | OH-4601201E | East Span Bottom Phase | 2023-05-11 | 2023-02-28 | 2023-02-06 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | P2 | Steel core gap
21 | OH-4601201E | East Span Middle Phase | 2023-05-11 | 2023-02-28 | 2023-02-06 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
22 | OH-4601201E | East Span Top Phase | 2023-05-11 | 2023-02-28 | 2023-02-06 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
23 | OH-4601201E | West Span Bottom Phase | 2023-05-11 | 2023-02-28 | 2023-02-06 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | P3 | Partial discharge
24 | OH-4601201E | West Span Middle Phase | 2023-05-11 | 2023-02-28 | 2023-02-06 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
25 | OH-4601201E | West Span Top Phase | 2023-05-11 | 2023-02-28 | 2023-02-06 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
26 | OH-1989008E | 1989008E to 1989009E Left Phase 1st Splice | 2023-05-11 | 2023-02-16 | 2023-02-09 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
27 | OH-1989008E | 1989008E to 1989009E Left Phase 2nd Splice | 2023-05-11 | 2023-02-16 | 2023-02-09 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
28 | OH-1989008E | 1989008E to 1989009E Left Phase 3rd Splice | 2023-05-11 | 2023-02-16 | 2023-02-09 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | TBD
29 | OH-1989008E | 1989008E to 1989009E Middle Phase | 2023-05-11 | 2023-02-16 | 2023-02-09 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
30 | OH-1989008E | 1989008E to 1989009E Right Phase | 2023-05-11 | 2023-02-16 | 2023-02-09 | 2022-05-04 | El Casco-Banning-Bottle | ET-00061 | None | N/A
31 | OH-1573751E | 1573751E to 1573750E Top Phase | 2023-05-16 | 2021-03-19 | 2021-07-08 | 2019-10-24 | La Fresa-Crest | ET-01237 | P3 | Steel core gap
32 | OH-1573751E | 1573751E to 1573750E Middle Phase | 2023-05-16 | 2021-03-19 | 2021-07-08 | 2019-10-24 | La Fresa-Crest | ET-01237 | P3 | Steel core gap
33 | OH-1573751E | 1573751E to 1573750E Bottom Phase | 2023-05-16 | 2021-03-19 | 2021-07-08 | 2019-10-24 | La Fresa-Crest | ET-01237 | P2 | Steel core gap
34 | OH-1915814E | 1915814E to 1915815E Middle Phase | 2023-05-17 | 2021-03-29 | 2021-06-11 | 2019-10-24 | Marymount-Rolling Hills | ET-00758 | None | N/A
35 | OH-1819537E | 1819537E to 1819538E Top Phase | 2023-05-22 | 2020-08-18 | 2020-04-04 | 2019-10-16 | Layfair-San Dimas | ET-00830 | None | N/A
36 | OH-1819537E | 1819537E to 1819538E Middle Phase | 2023-05-22 | 2020-08-18 | 2020-04-04 | 2019-10-16 | Layfair-San Dimas | ET-00830 | None | N/A
37 | OH-1819537E | 1819537E to 1819538E Bottom Phase | 2023-05-22 | 2020-08-18 | 2020-04-04 | 2019-10-16 | Layfair-San Dimas | ET-00830 | None | N/A
38 | OH-4547312E | 4547312E to 4547313E Top Phase | 2023-05-24 | 2022-04-15 | 2020-03-26 | 2019-10-16 | Padua-Layfair | ET-00860 | None | N/A
39 | OH-7016329 | M4T3 to M4T4 North Phase Right Splice | 2023-09-15 | 2023-03-07 | 2023-05-18 | 2019-11-02 | CHATSWORTH-NATURAL | ET-00149 | None | N/A
40 | OH-7016329 | M4T3 to M4T4 North Phase Left Splice | 2023-09-15 | 2023-03-07 | 2023-05-18 | 2019-11-02 | CHATSWORTH-NATURAL | ET-00149 | None | N/A
41 | OH-7016329 | M4T3 to M4T4 South Phase Right Splice | 2023-09-15 | 2023-03-07 | 2023-05-18 | 2019-11-02 | CHATSWORTH-NATURAL | ET-00149 | None | N/A
42 | OH-7016329 | M4T3 to M4T4 South Phase Left Splice | 2023-09-15 | 2023-03-07 | 2023-05-18 | 2019-11-02 | CHATSWORTH-NATURAL | ET-00149 | None | N/A
43 | OH-7016329 | M4T3 to M4T4 Middle Phase Right Splice | 2023-09-15 | 2023-03-07 | 2023-05-18 | 2019-11-02 | CHATSWORTH-NATURAL | ET-00149 | None | N/A
44 | OH-7016329 | M4T3 to M4T4 Middle Phase Left Splice | 2023-09-15 | 2023-03-07 | 2023-05-18 | 2019-11-02 | CHATSWORTH-NATURAL | ET-00149 | None | N/A
45 | OH-1830725E | OH1830725E/1830726E to OH1830727E/1830728E Left Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P3 | Aluminum strands not fully compressed
46 | OH-1830725E | OH1830725E/1830726E to OH1830727E/1830728E Middle Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P3 | Aluminum strands not fully compressed
47 | OH-1830725E | OH1830725E/1830726E to OH1830727E/1830728E Right Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P2 | Steel sleeve off centered, steel core gap, aluminum strands not fully compressed
48 | OH-1830727E | OH1830727E/1830728E to OH1830729E/1830730E Left Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P1 | Steel sleeve off centered, steel core gap, aluminum strands not fully compressed
49 | OH-1830727E | OH1830727E/1830728E to OH1830729E/1830730E Middle Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P2 | Steel sleeve off centered, steel core gap, aluminum strands not fully compressed
50 | OH-1830727E | OH1830727E/1830728E to OH1830729E/1830730E Right Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P1 | Steel sleeve off centered, steel core gap, aluminum strands not fully compressed
51 | OH-1830729E | OH1830729E/1830730E to OH1830731E/1830732E Left Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P2 | Steel core gap, improper crimps, lack of grease
52 | OH-1830729E | OH1830729E/1830730E to OH1830731E/1830732E Middle Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P3 | Aluminum strands not fully compressed
53 | OH-1830729E | OH1830729E/1830730E to OH1830731E/1830732E Right Phase | 2023-10-20 | 2023-07-26 | 2023-07-26 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | P3 | Repair rods around splice
54 | OH-1830735E | OH1830735E/1830736E to OH1830737E/1830738E Middle Phase | 2023-10-20 | 2023-07-26 | 2023-07-28 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | None | N/A
55 | OH-1830735E | OH1830735E/1830736E to OH1830737E/1830738E Right Phase | 2023-10-20 | 2023-07-26 | 2023-07-28 | 2019-04-11 | LEE VINING-RUSH CREEK | ET-02047 | None | N/A
56 | OH-7009537 | Top Phase Left Sub | 2024-03-18 | 2023-09-26 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
57 | OH-7009537 | Top Phase Right Sub | 2024-03-18 | 2023-09-26 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
58 | OH-7009537 | Middle Phase Right Sub | 2024-03-18 | 2023-09-26 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
59 | OH-7009537 | Middle Phase Left Sub | 2024-03-18 | 2023-09-26 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
60 | OH-7009537 | Bottom Phase Left Sub | 2024-03-18 | 2023-09-26 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
61 | OH-7009537 | Bottom Phase Right Sub | 2024-03-18 | 2023-09-26 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
62 | OH-7009541 | Top Phase Left Sub | 2024-03-19 | 2023-10-05 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
63 | OH-7009541 | Top Phase Right Sub | 2024-03-19 | 2023-10-05 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
64 | OH-7009541 | Middle Phase Right Sub | 2024-03-19 | 2023-10-05 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
65 | OH-7009541 | Middle Phase Left Sub | 2024-03-19 | 2023-10-05 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
66 | OH-7009541 | Bottom Phase Left Sub | 2024-03-19 | 2023-10-05 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | P3 | Steel core gap
67 | OH-7009541 | Bottom Phase Right Sub | 2024-03-19 | 2023-10-05 | 2024-01-27 | 2019-02-17 | Etiwanda-San Bernardino | ET-00397 | None | N/A
68 | OH-7029287 | Top Phase Left Sub | 2024-03-21 | 2024-01-31 | 2024-02-03 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
69 | OH-7029287 | Top Phase Right Sub | 2024-03-21 | 2024-01-31 | 2024-02-03 | 2022-05-09 | Devers-San Bernardino | ET-00526 | P3 | Steel core gap
70 | OH-7029287 | Middle Phase Right Sub | 2024-03-21 | 2024-01-31 | 2024-02-03 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
71 | OH-7029287 | Middle Phase Left Sub | 2024-03-21 | 2024-01-31 | 2024-02-03 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
72 | OH-7029287 | Bottom Phase Left Sub | 2024-03-21 | 2024-01-31 | 2024-02-03 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
73 | OH-7029287 | Bottom Phase Right Sub | 2024-03-21 | 2024-01-31 | 2024-02-03 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
74 | OH-7029269 | Top Phase Left Sub | 2024-03-21 | 2024-01-30 | 2024-02-10 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
75 | OH-7029269 | Top Phase Right Sub | 2024-03-21 | 2024-01-30 | 2024-02-10 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
76 | OH-7029269 | Middle Phase Right Sub | 2024-03-21 | 2024-01-30 | 2024-02-10 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
77 | OH-7029269 | Middle Phase Left Sub | 2024-03-21 | 2024-01-30 | 2024-02-10 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
78 | OH-7029269 | Bottom Phase Left Sub | 2024-03-21 | 2024-01-30 | 2024-02-10 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
79 | OH-7029269 | Bottom Phase Right Sub | 2024-03-21 | 2024-01-30 | 2024-02-10 | 2022-05-09 | Devers-San Bernardino | ET-00526 | None | N/A
80 | OH-7017236 | Top Phase | 2024-03-26 | 2023-04-12 | 2023-09-08 | 2019-03-26 | Moorpark-Santa Clara No. 1 | ET-00775 | P3 | Steel sleeve off centered, steel core gap
81 | OH-7017236 | Middle Phase | 2024-03-26 | 2023-04-12 | 2023-09-08 | 2019-03-26 | Moorpark-Santa Clara No. 1 | ET-00775 | None | N/A
82 | OH-7017236 | Bottom Phase | 2024-03-26 | 2023-04-12 | 2023-09-08 | 2019-03-26 | Moorpark-Santa Clara No. 1 | ET-00775 | None | N/A
83 | OH-7017239 | Top Phase | 2024-03-26 | 2023-12-26 | 2022-03-12 | 2019-03-26 | Moorpark-Santa Clara No. 1 | ET-00775 | P3 | Steel sleeve off centered, steel core gap
84 | OH-7017239 | Middle Phase | 2024-03-26 | 2023-12-26 | 2022-03-12 | 2019-03-26 | Moorpark-Santa Clara No. 1 | ET-00775 | None | N/A
85 | OH-7017239 | Bottom Phase | 2024-03-26 | 2023-12-26 | 2022-03-12 | 2019-03-26 | Moorpark-Santa Clara No. 1 | ET-00775 | None | N/A
86 | OH-7018357 | Top Phase | 2024-03-28 | 2023-10-31 | 2023-05-16 | 2021-09-28 | Pardee-Santa Clara | ET-00776 | P3 | Lack of grease
87 | OH-7018357 | Middle Phase | 2024-03-28 | 2023-10-31 | 2023-05-16 | 2021-09-28 | Pardee-Santa Clara | ET-00776 | P3 | Lack of grease
88 | OH-7018357 | Bottom Phase | 2024-03-28 | 2023-10-31 | 2023-05-16 | 2021-09-28 | Pardee-Santa Clara | ET-00776 | P2 | Steel sleeve off centered, steel core gap
89 | OH-7018394 | Top Phase | 2024-03-28 | 2024-01-30 | 2023-08-01 | 2021-09-28 | Pardee-Santa Clara | ET-00776 | None | N/A
90 | OH-7018394 | Middle Phase | 2024-03-28 | 2024-01-30 | 2023-08-01 | 2021-09-28 | Pardee-Santa Clara | ET-00776 | None | N/A
91 | OH-7018394 | Bottom Phase | 2024-03-28 | 2024-01-30 | 2023-08-01 | 2021-09-28 | Pardee-Santa Clara | ET-00776 | None | N/A
92 | OH-4435003E | Top Phase | 2024-04-12 | 2023-03-01 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | None | N/A
93 | OH-4435003E | Middle Phase | 2024-04-12 | 2023-03-01 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | None | N/A
94 | OH-4435003E | Bottom Phase | 2024-04-12 | 2023-03-01 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | None | N/A
95 | OH-1840480E | 1840480E to 1840478E Top Phase | 2024-04-12 | 2023-02-24 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | P3 | Steel core gap
96 | OH-1840480E | 1840480E to 1840478E Middle Phase | 2024-04-12 | 2023-02-24 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | None | N/A
97 | OH-1840480E | 1840480E to 1840478E Bottom Phase | 2024-04-12 | 2023-02-24 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | P2 | Steel core gap
98 | OH-1840480E | 1840480E to 1840481E Top Phase | 2024-04-12 | 2023-02-24 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | None | N/A
99 | OH-1840480E | 1840480E to 1840481E Middle Phase | 2024-04-12 | 2023-02-24 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | None | N/A
100 | OH-1840480E | 1840480E to 1840481E Bottom Phase | 2024-04-12 | 2023-02-24 | 2023-06-05 | 2023-03-16 | Moorpark-Valdez | ET-01971 | None | N/A
101 | OH-2072694E | Bottom Left Phase | 2024-04-22 | 2023-10-12 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P3 | Steel core gap
102 | OH-2072694E | Bottom Right Phase | 2024-04-22 | 2023-10-12 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P2 | Steel core gap
103 | OH-2072694E | Top Phase AOL | 2024-04-22 | 2023-10-12 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P2 | Steel core gap
104 | OH-2072694E | Top Phase BOL | 2024-04-22 | 2023-10-12 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P2 | Steel core gap
105 | OH-4533535E | 4533535E to 125096S Top Phase | 2024-04-22 | 2023-08-30 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | None | N/A
106 | OH-4533535E | 4533535E to 125096S Bottom Phase | 2024-04-22 | 2023-08-30 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P2 | Steel core gap
107 | OH-4533535E | 4533535E to 4533536E Top Phase | 2024-04-22 | 2023-08-30 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P2 | Steel core gap
108 | OH-4533535E | 4533535E to 4533536E Bottom Phase | 2024-04-22 | 2023-08-30 | 2024-03-30 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P3 | Steel core gap
109 | OH-2072743E | Top Phase | 2024-04-22 | 2024-02-06 | 2024-03-24 | 2021-10-18 | Moreno-Moval-Vista | ET-00505 | P2 | Steel core gap
110 | OH-1843601E | Middle Phase | 2024-05-02 | 2023-10-07 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | None | N/A
111 | OH-2116203E | Left Phase | 2024-05-02 | 2023-10-03 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | None | N/A
112 | OH-2116203E | Middle Phase | 2024-05-02 | 2023-10-03 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | None | N/A
113 | OH-2116203E | Right Phase | 2024-05-02 | 2023-10-03 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | None | N/A
114 | OH-2116202E | Left Phase (AOL) | 2024-05-02 | 2023-10-03 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | None | N/A
115 | OH-2116202E | Left Phase (BOL) | 2024-05-02 | 2023-10-03 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | None | N/A
116 | OH-2116202E | Middle Phase | 2024-05-02 | 2023-10-03 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | P3 | Steel core gap
117 | OH-2116202E | Right Phase | 2024-05-02 | 2023-10-03 | 2024-02-12 | 2022-04-19 | Saugus-Elizabeth Lake-MWD Foothill | ET-01570 | P3 | Steel core gap
118 | OH-120025 | 120025 to 120024 Top Phase | 2024-10-14 | 2023-07-06 | 2023-07-12 | 2024-09-28 | Control-Haiwee-Inyokern | ET-77245 | P2 | Steel core gap
119 | OH-120025 | 120025 to 120026 Top Phase | 2024-10-14 | 2023-07-06 | 2023-07-12 | 2024-09-28 | Control-Haiwee-Inyokern | ET-77245 | None | N/A
120 | OH-120027 | 120027 to 120026 Bottom Phase | 2024-10-14 | 2023-07-06 | 2023-07-12 | 2024-09-28 | Control-Haiwee-Inyokern | ET-77245 | None | N/A
121 | OH-120027 | 120027 to 120028 Bottom Phase | 2024-10-14 | 2023-07-06 | 2023-07-12 | 2024-09-28 | Control-Haiwee-Inyokern | ET-77245 | P2 | Steel core gap
122 | OH-120155 | 120155 to 120154 Bottom Phase | 2024-10-14 | 2024-07-24 | 2024-05-30 | 2024-09-28 | Control-Haiwee-Inyokern | ET-77245 | P3 | Steel core gap
123 | OH-120155 | 120155 to 120156 Bottom Phase | 2024-10-14 | 2024-07-24 | 2024-05-30 | 2024-09-28 | Control-Haiwee-Inyokern | ET-77245 | P2 | Steel core gap
124 | OH-120162 | 120162 to 2124494E Top Phase | 2024-10-15 | 2024-07-24 | 2024-05-30 | 2024-09-28 | Control-Coso-Haiwee-Inyokern | ET-77246 | P1 | Steel core off centered, lack of grease, signs of corrosion
125 | OH-120162 | 120162 to 1829608E Top Phase | 2024-10-15 | 2024-07-24 | 2024-05-30 | 2024-09-28 | Control-Coso-Haiwee-Inyokern | ET-77246 | P1 | Steel core off centered, lack of grease, signs of corrosion

## Table SCE D-01
Table SCE D-01: % SCE FLOCS and Simulated Acres Burned
Percent Burn | % FLOCs >300 Acres Burned 8h Burn | % FLOCs >300 Acres Burned 24h Burn | % FLOCs >10K Acres Burned 8h Burn | % FLOCs >10K Acres Burned 24h Burn
20 | 38.6% | 65.7% | 0% | 4%
40 | 48.5% | 70.3% | 0.1% | 12.5%
50 | 51.6% | 71.8% | 0.3% | 16%
60 | 54.1% | 73.2% | 0.5% | 19.4%
80 | 60.4% | 76.6% | 1% | 28.1%
90 | 64.3% | 79% | 1.5% | 36%
95 | 67.1% | 80.3% | 2.7% | 42%
98 | 69.7% | 81.6% | 4.3% | 47.4%
100 | 72.8% | 83.1% | 9.3% | 54.9%

## Table SCE D-02
Table SCE D-02: 2022-2024 Transmission HFRI Inspections [1]
Category | 2022 | 2023 | 2024
Annual WMP Target | 16000 | 28000 | 28000
Total Asset Inspections | 18035 | 29707 | 32397
Ground & Aerial Inspection | 16270 | 27672 | 30040
Ground Only Inspection | 902 | 1186 | 1668
Aerial Only Inspection | 863 | 849 | 689
Access/Environ Constraint | 232 | 126 | 33
[1] Scope and target for 2023 and 2024 increased due to change in risk methodology. A small subset of assets may be inspected more than once a year based on risk criteria.

## Table SCE D-03
Table SCE D-02: Plan for Implementation of Recommendations from Third-Party Study and White Paper.
ID | Recommendation | Milestones | Timeline
TP01 | Standardizing vegetation management data (e.g., inspection and trim records) would provide additional information about the clearances that are achieved more broadly for primary overhead circuits and would allow for more robust analyses of clearance effectiveness. | Update existing VM-related outage investigation data collection form to require key data elements to improve data analysis. | June 2025
|  | Rebuild vegetation outage analysis dashboard using recently implemented VM data warehouse (Snowflake) | December 2025
|  | Integrate outage investigation data into VM work management system (Arbora). | December 2026
TP02 | Outage investigation reports did not include an estimate of radial clearance at the time of the outage for two of the three IOUs. Adding this estimate to the outage investigation report for all IOUs would provide valuable information to future analyses of clearance effectiveness. | Update existing outage investigation data collection form to require key data elements to improve data analysis. | June 2025
|  | Communication/Training to outage investigators | October 2025
TP03 | Implement a time-series, grid-type analysis. This analysis will leverage weather and landcover data, dividing utility service territories into grid cells for detailed evaluation over time. | SCE already has fire science and meteorology data that is incorporated into risk analysis, such as with its Areas of Concern (AOC) identification to aid decision making. For identifying AOC, among other items, near term weather such as drought conditions, and vegetation growth based on recent rains in specific locations is taken into consideration. | N/A
WP01 | It is recommended that each IOU make efforts to implement within their data records the ability to associate outage and ignition investigation information as part of their work activity history. | Update existing VM-related outage investigation data collection form to require key data elements to improve data analysis. | June 2025
|  | Integrate outage investigation data into VM work management system (Arbora). | December 2026
WP02 | Utilities may also additionally benefit from the monitoring of vegetation conditions and clearance by leveraging remote sensing technologies, especially those with larger service territories. By collecting higher frequency data over time utilities may identify patterns in vegetation growth and tree health and measure the minimal clearance based on outage and ignition rates associated with specific circuits or segments to enhance situational awareness. This will allow utilities to modify their clearance practices accordingly. Without data collection, opportunities for learning and improvement are reduced. | Publish remote sensing crown polygons into work management system for inspection activities | December 2025
|  | Expand baseline network digital twin model | June 2026
|  | Reduce ground-based inspections. (ongoing - subject to adjustment based on technological constraints and operational needs). | 2026-2028
WP03 | This study recommends identifying locations with historically higher wind gusts and drier fuel conditions to inform of the risk and prioritization of inspection and clearance activities. The strategy should consider location-specific treatments or enhanced clearance practices. Additional mitigation methods should be considered particularly in forest and shrubland areas. Additionally, the establishment of radial clearance at time of pruning should consider multiple factors such as species, growth rate, hazard abatement, industry standards, and tree health. | SCE already has a Severe Risk Area layer which encompasses PSPS high wind areas, egress/ingress, acreage impacted, and communities of elevated fire concern. This layer helps determine remediation prioritization for routine line clearing, and inspection cadences based on tree risk index for hazard tree mitigations. In addition, as part of AOC seasonal patrols, SCE factors historical wind gusts and areas with drier fuel conditions as part of the considerations for identifying AOCs. | N/A