## OEIS Table 3-1
Priority | Risk | Risk Driver | x% of ignitions in HFTD | x% of overhead faults in HFTD *** | Topographical and Climatological Risk Factors
1 | Equipment /facility failure or damage | Pole | 2.326% | 7.139% | n/a
2 | Contact from object | Animal contact | 27.91% | 12.37% | Humidity, wind gust, elevation, FPI
3 | Equipment /facility failure or damage | Fuse | 2.326% | 1.417% | Aspect
4 | Unknown | Unknown | 0% | 28.5% | Temperature, humidity, slope, consequence and wind gust pertaining to the location, elevation
5 | Contact from object | Land vehicle contact | 11.63% | 9.973% | Wind gust, elevation, slope, temperature, humidity
6 | Equipment /facility failure or damage | Conductor | 2.326% | 4.905% | FPI, slope
7 | Lightning | Lightning | 0% | 5.613% | FPI
8 | Equipment /facility failure or damage | Cross arm | 0% | 4.033% | Slope, aspect, FPI
9 | Equipment /facility failure or damage | Lightning arrestor | 9.302% | 1.907% | n/a
10 | Equipment /facility failure or damage | Transformer | 0% | 4.087% | Wind gust
11 | Equipment /facility failure or damage | Connector device * | 9.302% | 5.395% | Consequence pertaining to the location, slope
11 | Equipment /facility failure or damage | Splice * | n/a | n/a | n/a
12 | Equipment /facility failure or damage | Other | 4.651% | 0.3815% | Temperature, elevation, humidity, wind gust
13 | Vegetation contact | Fall-in (branch failure) | 4.651% | 2.452% | Wind gust, elevation, FPI, humidity
13 | Vegetation contact | Fall-in (trunk failure)** | n/a | n/a | Wind gust, elevation, FPI, humidity
13 | Vegetation contact | Fall-in (root failure)** | n/a | n/a | Wind gust, elevation, FPI, humidity
14 | Contact from object | Other contact from object | 2.326% | 2.561% | n/a
15 | Equipment /facility failure or damage | Switch | 2.326% | 0.218% | Consequence pertaining to the location, humidity
16 | Contact from object | Balloon contact | 9.302% | 2.561% | Consequence pertaining to the location, wind gust, elevation, humidity
17 | Equipment /facility failure or damage | Insulator and bushing | 2.326% | 0.8174% | n/a
18 | Equipment /facility failure or damage | Cutout | 0% | 1.362% | Consequence pertaining to the location, elevation, humidity
19 | Contact from object | 3rd party contact | 2.326% | 1.308% | FPI
21 | Wire-to-wire contact | Wire-to-wire contact | 2.326% | 0.7629% | Aspect, temperature, slope
22 | Equipment /facility failure or damage | Anchor/guy | 2.326% | 0.7084% | Consequence, wind gust, elevation, aspect, humidity
23 | Contamination | Contamination | 2.326% | 0.1635% | n/a
24 | Vandalism/theft | Vandalism/ theft | 0% | 0.109% | n/a
25 | Equipment /facility failure or damage | Capacitor bank | 0% | 0.436% | n/a
26 | Equipment /facility failure or damage | Recloser | 0% | 0.2725% | FPI
27 | Contact from object | Aircraft vehicle | 0% | 0.218% | Elevation
28 | Vegetation contact | Blow-in | 0% | 0.0545% | Wind gust
29 | Equipment /facility failure or damage | Voltage regulator/booster | 0% | 0.109% | Humidity
30 | Vegetation contact | Grow-in | 0% | 0.109% | Slope
31 | Equipment /facility failure or damage | Unknown | 0% | 0.0545% | n/a
n/a | Contact from object | Unknown | 0% | 0% | n/a
n/a | Equipment /facility failure or damage | Relay | n/a | n/a | n/a
n/a | Equipment /facility failure or damage | Sectionalizer | n/a | n/a | n/a
n/a | Equipment /facility failure or damage | Tap | n/a | n/a | n/a
n/a | Equipment /facility failure or damage | Tie wire | n/a | n/a | n/a
n/a | Protective device operation | Protective device operation | n/a | n/a | n/a
n/a | Dig-in | Dig-in | n/a | n/a | n/a
* Connector and Splice related ignitions are tracked as one driver, Splice is grouped into the risk driver Connection Device as a combined priority ranking.
**Vegetation Fall-in (trunk failure) and Fall-in (root failure) are grouped into one risk driver Fall-in (branch failure) as a combined priority ranking.
*** This column was added by SDG&E.

## OEIS Table 3-2
Performance Metric* | Assumption that underlies the use of the metric | Section associated with the Performance Metric (state “WMP” if the metric applies to entire plan) | 2026 Projected | 2027 Projected | 2028 Projected
Vegetation caused ignitions in the HFTD during FPI ratings of Elevated or higher | To evaluate the performance of risk reduction from vegetation mitigations during fire prone weather conditions | Section 9 | 1 | 1 | 1
Vegetation caused ignitions in the HFTD during an RFW | To evaluate the performance of risk reduction from vegetation mitigations during fire prone weather conditions | Section 9 | 1 | 1 | 1
Equipment caused ignitions in the HFTD during FPI ratings of Elevated or higher | To evaluate the performance of risk reduction from asset inspection and grid hardening during fire-prone conditions | Section 8 | 5 | 5 | 5
Equipment caused ignitions in the HFTD during an RFW | To evaluate the performance of risk reduction from asset inspection and grid hardening during fire-prone conditions | Section 8 | 1 | 1 | 1
Equipment caused ignition rate in the HFTD during a High FPI rating | To evaluate the performance of risk reduction from asset inspection and grid hardening during fire-prone conditions | Section 8 | 0.03 | 0.03 | 0.03
Vegetation caused outages in the HFTD during an Elevated FPI | To evaluate the performance of risk reduction from vegetation mitigations during fire prone weather conditions | Section 9 | 4 | 4 | 4
Vegetation caused outages in the HFTD during an RFW | To evaluate the performance of risk reduction from vegetation mitigations during fire prone weather conditions | Section 9 | 1 | 1 | 1
Overhead faults on circuits in the HFTD during an Elevated FPI | To evaluate the performance of risk reduction from overall mitigations during fire-prone conditions | Section 8 | 135 | 135 | 135
Overhead faults on circuits in the HFTD during an RFW | To evaluate the performance of risk reduction from overall mitigations during fire-prone conditions | Section 8 | 11 | 11 | 11
Energized wire down events in the HFTD during an FPI of Elevated or higher | To evaluate the performance of risk reduction from grid hardening related mitigations during fire-prone conditions | Section 8 | 9 | 9 | 9
Energized wire down events in the HFTD during an RFW | To evaluate the performance of risk reduction from grid hardening related mitigations during fire-prone conditions | Section 8 | 1 | 1 | 1
Overhead fault rate in the HFTD during a High FPI | To evaluate the performance of risk reduction from overall mitigations during fire-prone conditions | Section 8 | 0.9 | 0.9 | 0.9
*Based on 2020-2024 averages

## OEIS Table 3-3
Year of WMP Cycle | 308762
2026 | Projected =$325,739
2027 | Projected =$308,762
2028 | Projected =$388,255
*Projected spend includes capital and O&M, direct costs only

## OEIS Table 4-1
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | Total
Area served (sq. mi.) | 1396 | 1426 | 1574 | 4396
Number of customers served (meters) | 173368 | 32228 | 1332248 | 1537844
Overhead transmission lines (circuit miles) | 724 | 268 | 821 | 1813
Overhead distribution lines (circuit miles) | 1781 | 1592 | 2940 | 6313
Underground transmission lines (circuit miles) | 42 | 9 | 141 | 192
Underground distribution lines (circuit miles) | 2352 | 601 | 8407 | 11360

## OEIS Table 4-2
Ignition Date | Fire Name | Official Cause | Fire Size (acres) | No. of Fatalities | No. of Structures Destroyed and Damaged | Financial Loss (US$) | Lesson(s) Learned
2007-10-21 | Witch Creek – Guejito Fire (fires merged) | CAL FIRE Reports determined that the causes of the ignition were, among other factors, power lines | 197990 | 2 | 1736 | $2.4 billion* | SDG&E learned the importance of situational awareness and has since developed a weather station and camera network, operational standards for work or stoppage of work under elevated and extreme conditions, risk assessment and strategy for grid hardening prioritized by risk, and improved its alliance with communication infrastructure providers to address maintenance issues.
2007-10-22 | Rice Fire | CAL FIRE Reports determined that the causes of the ignition were, among other factors, power lines | 9472 | 0 | 248 | $2.4 billion* | SDG&E had similar lessons learned as from the Witch Creek-Guejito fire, and also learned the importance of vegetation management improvements and achieving better clearances in a timely manner.
*$2.4 billion represents the consolidated settlement of claims and associated costs related to the Witch Creek and Rice fires.

## OEIS Table 4-3
Entry # | Circuit ID | Name of Circuit | Dates of Outages | Number of Customers Hours of PSPS per Outage | Measures Taken, or Planned to Be Taken, to Reduce the Need for and Impact of Future PSPS of Circuit | Estimated Annual Decline in PSPS Events and PSPS Impact on Customers
1 | 1030 | 1030 | Oct 10-11, 2019 Oct 24-25, 2019 Oct 30-31, 2019 Sept 9, 2020 Dec 2–4, 2020 Dec 7–9, 2020 Dec 23–24, 2020 Dec 9-11, 2024 | 556 3,830 34,959 102 45,367 35,031 561 38,040 | Strategic Undergrounding: 44.61 miles completed to date; 8.77 miles planned for 2025; 59.5 miles planned for 2027-2028 that will be extended to 2031-2032 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 7 SCADA reclosers available for sectionalizing Situational Awareness: 6 weather stations on circuit Customer Resiliency Programs: 175 customers have participated to date; customers will be invited to participate in 2025 | 36,363 fewer customer hours of PSPS per year
2 | 1166 | 1166 | Oct 24-25, 2019 Oct 30-31, 2019 Dec 2-4, 2020 Dec 7-8, 2020 Dec 23-24, 2020 Nov 25-26, 2021 Dec 9-11, 2024 | 8,411 3,639 12,881 873 4,578 3,360 5,804 | PSPS Sectionalizing: 3 SCADA reclosers available for sectionalizing Situational Awareness: 2 weather stations on circuit Customer Resiliency Programs: 60 customers have participated to date; customers will be invited to participate in 2025 | 5,957 fewer customer hours of PSPS per year
3 | 1215 | 1215 | Oct 24-26, 2019 Oct 30-31, 2019 Oct 27, 2020 Dec 2-4, 2020 Dec 7-8, 2020 Nov 6-7, 2024 Dec 9-11, 2024 | 6,431 5,180 922 6,066 2,591 4,362 6,986 | Strategic Undergrounding: 1.4 miles to be completed in 2025; 0.5 miles planned for 2025, 14.9 miles planned for 2026, and 8.1 miles planned for 2027 will be extended to 2029-30 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 4 SCADA reclosers available for sectionalizing Situational Awareness: 1 weather station on circuit Customer Resiliency Programs: 30 customers have participated to date; customers will be invited to participate in 2025 | 2,758 fewer customer hours of PSPS per year
4 | 157 | 157 | Oct 24-26, 2019 Oct 30-31, 2019 Dec 2-4, 2020 Dec 7-9, 2020 Dec 23-24, 2020 Nov 25-26, 2021 Nov 6-8, 2024 Dec 9-11, 2024 | 33,147 23,413 39,926 23,721 11,998 21,572 6,659 48,208 | Strategic Undergrounding: 6.9 miles planned for 2027 will be extended to 2029-30 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 7 SCADA reclosers available for sectionalizing Situational Awareness: 6 weather stations on circuit Customer Resiliency Programs: 114 customers have participated to date; customers will be invited to participate in 2025 | 8,042 fewer customer hours of PSPS per year
5 | 214/CTL1 | 214/CTL1 | Oct 24-26, 2019* Oct 30-31, 2019 Dec 2-4, 2020* Dec 7-9, 2020* Dec 24, 2020* Nov 25, 2021 Dec 9-11, 2024* | 29,003 11,723 38,947 27,007 10,345 4,701 36,284 | Strategic Undergrounding: 9.4 miles planned for 2026, 35.27 miles planned for 2027, and 10.21 miles planned for 2028 will be extended to 2030-32 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 7 SCADA reclosers available for sectionalizing Situational Awareness: 5 weather stations on circuit Customer Resiliency Programs: 47 customers have participated to date; customers will be invited to participate in 2025 | 3,433 fewer customer hours of PSPS per year
6 | 215 | 215 | Oct 25-26, 2019 Oct 30-31, 2019 Dec 3-4, 2020 Dec 7-8, 2020 Dec 24, 2020 Dec 9-11, 2024 | 15,687 14,491 18,208 7,733 3,989 22,504 | PSPS Sectionalizing: 4 SCADA reclosers available for sectionalizing Situational Awareness: 4 weather stations on circuit Customer Resiliency Programs: 82 customers have participated to date; customers will be invited to participate in 2025 | 5,009 fewer customer hours of PSPS per year
7 | 220 | 220 | Oct 24-26, 2019* Oct 30-31, 2019 Dec 2-4, 2020* Dec 7-9, 2020* Dec 24, 2020* Dec 9-11, 2024* | 12,158 12,384 16,252 13,905 4,187 15,166 | Strategic Undergrounding: 11.45 miles completed in 2024; 6 miles to be completed in 2025; 10.4 miles planned for 2025, 35.44 miles planned for 2026, 8.41 miles planned for 2027, and 8 miles planned for 2028 will be extended to 2029-32 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 3 SCADA reclosers available for sectionalizing Situational Awareness: 4 weather stations on circuit Customer Resiliency Programs: 16 customers have participated to date; customers will be invited to participate in 2025 | 8,781 fewer customer hours of PSPS per year
8 | 222 | 222 | Oct 24-26, 2019 Oct 30-31, 2019 Dec 2-4, 2020 Dec 7-10, 2020 Dec 23-24, 2020 Dec 9-11, 2024 | 59,335 50,094 61,822 54,124 4,703 66,226 | Strategic Undergrounding: 62 miles completed to date; 6 miles to be completed in 2025; 13.7 miles planned for 2025, 13.52 miles planned for 2026, 44.52 miles planned for 2027, and 14.65 miles planned for 2028 will be extended to 2029-32 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 7 SCADA reclosers available for sectionalizing Situational Awareness: 7 weather stations on circuit Customer Resiliency Programs: 618 customers have participated to date; customers will be invited to participate in 2025 | 95,367 fewer customer hours of PSPS per year
9 | 358 | 358 | Oct 24-25, 2019 Oct 30-31, 2019 Dec 2-4, 2020 Dec 7-8, 2020 Dec 23-24, 2020 Nov 25-26, 2021 Nov 6-7, 2024 Dec 9-11, 2024 | 9,287 11,316 15,190 3,819 3,300 7,822 2,777 8,266 | Strategic Undergrounding: 5.56 miles completed to date; 5.24 miles to be completed in 2025; 4.6 miles planned for 2026 and 3.5 miles planned for 2027 will be extended to 2030-31 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 1 SCADA recloser available for sectionalizing; 1 device planned for 2026 Situational Awareness: 3 weather stations on circuit Customer Resiliency Programs: 41 customers have participated to date; customers will be invited to participate in 2025 | 13,017 fewer customer hours of PSPS per year
10 | 441 | 441 | Oct 24-26, 2019 Oct 30-31, 2019 Oct 27, 2020 Dec 2-3, 2020 Dec 7-8, 2020 Nov 6-7, 2024 Dec 9-11, 2024 | 5,329 4,026 760 2,596 2,418 2,966 5,006 | Strategic Undergrounding: 0.2 miles completed to date; 6.32 miles to be completed in 2025; 4 miles planned for 2026 and 4.75 miles planned for 2027 will be extended to 2030-31 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 4 SCADA reclosers available for sectionalizing Situational Awareness: 2 weather stations on circuit Customer Resiliency Programs: 19 customers have participated to date; customers will be invited to participate in 2025 | 2,961 fewer customer hours of PSPS per year
11 | 445 | 445 | Oct 10-11, 2019 Oct 24-26, 2019 Oct 30-31, 2019 Oct 27, 2020 Dec 2–4, 2020 Dec 7–8, 2020 Nov 24-26, 2021 Nov 6-7, 2024 Dec 9-11, 2024 | 6,967 16,837 13,495 5,111 40,936 19,877 40,013 13,026 43,975 | Strategic Undergrounding: 27.43 miles completed to date; 1.89 miles to be completed in 2025; 39.62 miles planned for 2026 and 2027 will be extended to 2032-33 due to 2024-27 GRC Decision funding prioritization PSPS Sectionalizing: 7 SCADA reclosers available for sectionalizing Situational Awareness: 4 weather stations on circuit Customer Resiliency Programs: 89 customers have participated to date; customers will be invited to participate in 2025 | 16,245 fewer customer hours of PSPS per year
12 | 75 | 75 | Oct 24-25, 2019 Oct 30-31, 2019 Dec 2-4, 2020 Dec 7-9, 2020 Dec 23-24, 2020 | 345 493 13,863 689 238 | Strategic Undergrounding: 12.55 miles completed to date; 0.1 miles in scope to be completed by 2025 (3 miles of underbuilt overhead to be removed from service) PSPS Sectionalizing: 2 SCADA reclosers available for sectionalizing Situational Awareness: 2 weather stations on circuit Customer Resiliency Programs: 87 customers have participated to date; customers will be invited to participate in 2025 | 4,012 fewer customer hours of PSPS per year
13 | 78 | 78 | Oct 24-25, 2019 Oct 30-31, 2019 Dec 2-4, 2020 Dec 7-8, 2020 Dec 24, 2020 Nov 25, 2021 Dec 9-11, 2024 | 6,249 7,877 8,980 2,259 2,196 1,328 5,465 | Strategic Undergrounding: 1.21 miles completed in 2024; 1 mile planned for 2026 will be extended to 2029 due to 2024-27 GRC decision prioritization PSPS Sectionalizing: 3 SCADA reclosers available for sectionalizing Situational Awareness: 2 weather stations on circuit Customer Resiliency Programs: 30 customers have participated to date; customers will be invited to participate in 2025 | 4,989 fewer customer hours of PSPS per year
14 | 79 | 79 | Oct 10-11, 2019 Oct 24-26, 2019 Oct 29-31, 20219 Nov 17-18, 2019 Sept 8-9, 2020 Dec 2-4, 2020 Dec 7-9, 2020 Dec 23-24, 2020 Nov 24-26, 2021 Nov 6-7, 2024 Dec 9-11, 2024 | 451 29,262 27,981 182 256 37,476 33,615 298 4,369 370 40,953 | Strategic Undergrounding: 3.38 miles completed to date; 25 miles planned for 2026-27 will be extended to 2030-31 due to 2024-27 GRC decision prioritization PSPS Sectionalizing: 10 SCADA reclosers available for sectionalizing Situational Awareness: 9 weather stations on circuit Customer Resiliency Programs: 113 customers have participated to date; customers will be invited to participate in 2025 | 8,998 fewer customer hours of PSPS per year
15 | 909 | 909 | Oct 30-31, 2019 Dec 2-4, 2020 Dec 7-8, 2020 Dec 23-24, 2020 Dec 10-11, 2024 | 15,458 17,826 7,812 5,483 14,776 | Strategic Undergrounding: 2.69 miles completed to date; 31.85 miles planned for 2026 and 2028 will be extended to 2031-32 due to 2024-27 GRC decision prioritization PSPS Sectionalizing: 2 SCADA reclosers available for sectionalizing Situational Awareness: 2 weather stations on circuit Customer Resiliency Programs: 8 customers have participated to date; customers will be invited to participate in 2025 | 1,986 fewer customer hours of PSPS per year
*Customers on 4 kV circuit CTL1 were impacted as a result of de-energizing circuit 214. No independent operations for PSPS purposes occurred on 4 kV circuit CTL1.

## OEIS Table 5-1
Assumption | Justification | Limitation | Applicable Models
Average duration of PSPS de-energization for every SCADA Sectionalizing Device | Historical average PSPS de-energization in the service territory, along with subject matter expertise, is used to determine this value. | Estimating the potential duration of a PSPS de-energization at each SCADA Sectionalizing Device is a complex task as multiple variables are in play (e.g., weather forecast, firefighting resources, existing wildfires, crew availability). | - WiNGS-Ops - WiNGS-Planning - PSPS Risk
Customer impact scaling factor (Wildfire, PSPS, PEDS Vulnerability) | Subject matter expertise is used to determine a scaling factor to more accurately represent PSPS impacts to the critical and vulnerable population. | There is a lack of reliable data on how to quantify PSPS impacts on customers, specifically to subsets of customers such as critical and vulnerable. | - WiNGS-Ops - WiNGS-Planning - PSPS Risk
Serious injuries and fatalities (SIFs) per customer minute de-energized | Historical data and subject matter expertise is used to determine an estimation of the potential number of fatalities and serious injuries due to a PSPS. | There is a lack of historical data on serious injuries or fatalities due to PSPS de-energizations in California. | - WiNGS-Ops - WiNGS-Planning - PSPS Risk
Financial impact during a PSPS de-energization | Subject matter expertise is used to estimate this value based on proxies derived from the federal per diem rate for lodging, meals, and incidentals in San Diego County. | There is a lack of historical data on financial impacts to SDG&E customers due to PSPS de-energizations. | - WiNGS-Ops - WiNGS-Planning - PSPS Risk
Number of SIFs per structure destroyed in case of a wildfire | Subject matter expertise is used to estimate this value based on worst-case estimations of acres burned calculated by Technosylva. | Estimating fatalities per structure destroyed in the service territory is challenging due to several factors. This metric is highly dependent on the availability and effectiveness of firefighting resources, the timeliness and clarity of evacuation notices, the specific location of the event, and the prevailing weather conditions at the time. | - WiNGS-Ops - WiNGS-Planning - Wildfire Risk
Outage duration in case of a wildfire | Subject matter expertise is used to estimate this value based on estimates of outage duration and assumed restoration duration. | Estimating restoration time following a catastrophic wildfire is inherently challenging due to the numerous variables involved. The severity of the event plays a crucial role, as more severe wildfires can cause extensive damage to infrastructure, making restoration efforts more complex and time-consuming. Additionally, factors such as the availability of resources, accessibility of affected areas, weather conditions, and the extent of damage to critical infrastructure all contribute to the difficulty in providing accurate restoration time estimates. | - WiNGS-Ops - WiNGS-Planning - Wildfire Risk
Financial impacts in case of a wildfire | Subject matter expertise is used to estimate this value based on simulation outputs of buildings destroyed and acres impacted output. | Property value estimates are based on general assumptions and do not take into account the size, condition, location, or market value of the property | - WiNGS-Ops - WiNGS-Planning - Wildfire Risk
Annual risk event rates | Historic data is used to normalize wildfire, PSPS, and PEDS risks and quantify expected value averages. | Aannual frequency rates are calibrated based on historical observations, ensuring they accurately reflect past trends. However, these rates do not account for potential future conditions or changes. This means that while the model provides a reliable estimate based on historical data, it may not fully capture the impact of evolving factors such as climate change, new infrastructure developments, or changes in vegetation and land use. | - WiNGS-Ops - WiNGS-Planning - PSPS Risk
Burn probability | Subject matter expertise is used to select a representation of the worst fire weather days in the service territory. The burn probability is assumed to be 100% for these days. | Subject matter experts select these days to balance a representative sample of days with fire weather conditions present in theHFTD. This approach aims to accurately estimate the potential impacts of catastrophic wildfires while considering current weather conditions, community insights, and local knowledge (e.g., terrain, fuels, vegetation). Additionally, it takes into account computational resources, given the time and cost involved in conducting this analysis. | - WiNGS-Ops - WiNGS-Planning - Wildfire Risk
Wildfire hazard intensity | Data from the 125 worst fire weather days is identified by subject matter experts at SDG&E and is used by Technosylva to calculate this value. Technosylva simulated outputs include flame length, rate of spread, acres burned, buildings threatened, buildings destroyed, and population impacted. | Technosylva unsuppressed simulations have a duration of 24 hours. Wildfire consequence values are calculated based on acres burned and structures destroyed. | - WiNGS-Ops - WiNGS-Planning - Wildfire Risk
PEDS annual frequency | This value is determined using historical data on PEDS outage durations in HFTD portions of the service territory. | This annual frequency may not accurately represent future outage frequencies, as the number of future device installations and outages are unknown and difficult to estimate. SDG&E activates settings only during extreme or elevated fire weather conditions. | WiNGS-Planning
PEDS event consequence values | This value is determined using historical data on PEDS outage durations recorded in the SAIDIDAT database. | Historical duration and CMI estimates may not accurately reflect future PEDS consequence impact estimates. | WiNGS-Planning
Annual PSPS de-energization during high fire risk days | This value is determined using meteorology subject matter expertise and historical event records. | The current methodology is calibrated using past PSPS de-energizations and may not adequately account for the increasing frequency and severity of fire weather conditions. | WiNGS-Planning
Overhead-to-underground mile conversion rate | This contingency value is applied to non-roadway miles to account for additional miles to underground. | Roadway miles based on buffer of roadway with intersecting spans | WiNGS-Planning
Grid-hardening lifecycle years | Subject matter expertise is used to determine this value. | Expected lifespan in years | WiNGS-Planning
Mitigation installation cost-per-mile | Historical grid-hardening data and subject matter expertise are used to determine this value. | Does not take into account site and grid specific attributes | WiNGS-Planning
Mitigation efficacy rates | Data on efficacy studies for each mitigation option is used to determine this value. | Limited to internal risk event data available | WiNGS-Planning
Hardening-State Station Alert Speed Thresholds | Operational wind gust thresholds determined during the latest PSPS are used to determine this value. | These thresholds are defined for each event and take into account numerous factors, such as the magnitude and severity of forecasted weather conditions, fuel moisture content, available firefighting resources, and other relevant variables. This comprehensive approach ensures that the PSPS alert thresholds are tailored to the specific circumstances of each event, enhancing the effectiveness of the response and minimizing risks to public safety. | WiNGS-Planning

## OEIS Table 5-2
Scenario ID | Design Scenario | Purpose
WL1 | Wind Load Condition 1 – Baseline | This baseline scenario is modeled using 2 years of historical weather and fuel data analysis.
WL2 | Wind Load Condition 2 – Very High | This very high scenario is modeled using 2 years of historical weather and fuel data analysis, as it incorporates the 95th percentile wind gust conditions recorded in the service territory within the selected years for the analysis.
WL3 | Wind Load Condition 3 – Extreme | This extreme scenario is modeled using 2 years of historical weather and fuel data analysis, as it incorporates the 99th percentile wind gust conditions recorded in the service territory within the selected years for the analysis.
WL4 | Wind Load Condition 4 – Credible Worst Case | This credible worst case scenario is modeled using 2 years of historical weather and fuel data analysis, as it incorporates the maximum wind gust conditions recorded in the service territory within the selected years for the analysis.
VG1 | Vegetation Condition 1 – Existing Fuel Load (based on extreme weather conditions) and existing Vegetation Tree inventory assets | The existing fuel load conditions and current tree inventory datasets within the service territory are incorporated into the probability of failure models and the conditional probability of ignition model. The model assumes the surface fuel layer as of the end of 2023. SDG&E is currently collaborating with Technosylva to update this layer.
VG2 | Vegetation Condition 2 – Short-Term Forecasted Fuel Load conditions | Short-term potential changes in fuel conditions throughout the service territory are not currently included in wildfire simulations. However, future model updates or sensitivity analysis studies may incorporate simulations of these changes in fuel conditions, if deemed informative.
VG3 | Vegetation Condition 3 – Long-Term Extreme Forecasted Fuel Load conditions | Long-term potential changes in fuel conditions throughout the service territory are not currently included in wildfire simulations. However, future model updates or sensitivity analysis studies may incorporate simulations of these changes in fuel conditions, if deemed informative.
WV1 | Weather Conditions (WL1 + WL2 +WL3+ WL4) and Vegetation Conditions (VG1) during historical worst fire weather days in SDG&E's service territory | Millions of simulated year events are used to capture all potential permutations of weather, vegetation, and fire weather conditions within the service area. This comprehensive simulation approach allows for a thorough analysis and understanding of various scenarios, enhancing the accuracy of safety, reliability, and financial estimates. Additionally, it helps identify the most appropriate and cost-effective solutions for grid hardening at each feeder segment in HFTD.

## OEIS Table 5-3
Scenario ID | Extreme-Event Scenario | Purpose
n/a | Extreme Event Scenarios | Not applicable for WiNGS-Planning as this model is designed to incorporate historical weather conditions experienced within the service territory.

## OEIS Table 5-4
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
1 (WiNGS-Ops WiNGS-Planning) | Safety Impacts | Refer to Section 5.2.2.2, Consequence of Risk Event, for a detailed description of the methodology and assumptions. | - Expected number of customers affected by wildfire or PSPS de-energization event - Scaling factors for AFN customer impacts - PSPS de-energization duration - Equivalent Safety Serious Injuries and Fatalities (SIF) calculated based on Technosylva estimates of structures destroyed - Cost-benefit conversion factors | Wildfire, PSPS, and/or PEDS models | The expected number of serious injuries and fatalities for a wildfire or PSPS de-energization event | Estimates (in dollars) based on cost-benefit framework
2 (WiNGS-Ops WiNGS-Planning) | Reliability Impacts | Refer to Section 5.2.2.2, Consequence of Risk Event, for a detailed description of the methodology and assumptions. | - Expected number of customers affected by wildfire or PSPS de-energization - PSPS de-energization duration - Subject matter expert conservative assumption to estimate Customer Minutes Interrupted (CMI) values based on estimates of outage duration and assumed restoration duration - Cost-benefit conversion factors | Wildfire, PSPS, and/or PEDS models | The expected reliability impact | Estimates (in dollars) based on cost-benefit framework
3 (WiNGS-Ops WiNGS-Planning) | Financial Impacts | Refer to Section 5.2.2.2, Consequence of Risk Event, for a detailed description of the methodology and assumptions. | - Expected number of customers affected by wildfire or PSPS de-energization event - PSPS de-energization duration - Subject matter expert conservative assumption to translate buildings destroyed and acres impacted estimated by Technosylva simulations to financial dollars. - Cost-benefit conversion factors | Wildfire, PSPS, and/or PEDS models | The expected financial impact | Estimates (in dollars) based on cost-benefit framework
4 (WiNGS-Ops WiNGS-Planning) | Burn Probability | Assumed 100% for selected days to represent the worst fire weather days in the service area. | Subject matter experts select a representative sample of days with fire weather conditions present in HFTD portions of the service territory. This approach aims to accurately estimate the potential impacts of catastrophic wildfires while considering current weather conditions, community insights, and local knowledge (e.g., terrain, fuels, vegetation). It also takes into account computational resources, given the time and cost to conduct the analysis. | Meteorology, Fire Science, Engineering, and Risk Analytics identify historical weather conditions representing the worst fire weather days in the service territory | Representative weather conditions where ignitions could lead to wildfires that could result in fatalities, widespread property destruction, and multi-billion-dollar liabilities. These conditions could also necessitate proactive power shutoffs, which impact customers, communities, and local economies. | unitless
5 (WiNGS-Ops WiNGS-Planning) | Wildfire Hazard Intensity | Calculated by Technosylva for the 125 worst fire weather days identified by subject matter experts. Simulated outputs include flame length, rate of spread, acres burned, buildings threatened, buildings destroyed, and population impacted. | - Technosylva unsuppressed simulations that have a duration of 24 hours - Wildfire consequence values, which are calculated based on acres burned and structures destroyed | Meteorology, Fire Science, Engineering, and Risk Analytics identify historical weather conditions representing the worst fire weather days in the service territory | Estimates of acres burned and structures destroyed at asset locations for different weather conditions. | - Acres -Number of structures destroyed
6 (WiNGS-Ops WiNGS-Planning) | Wildfire Likelihood | Weather conditions (WL1 + WL2 +WL3+ WL4) and vegetation conditions (VG1) during the historical worst fire weather days in the service territory. | - Historical weather station data - Historical electrical outages (SAIDIDAT) - CPUC reportable ignitions - SDG&E evidence of heat records - GIS attributes - Surface fuel layer | See Appendix B | Wildfire LoRE | Outage and ignition rates per mile
7 (WiNGS-Ops WiNGS-Planning) | Wildfire Consequence | Maximum buildings destroyed combined with maximum acres affected per segment. | Probability distribution of potential ignition consequences based on the 125 worst fire weather days in the service territory at ignition points along overhead electrical assets. | Technosylva's simulation inputs: 125 worst fire weather days, fuel surface layer, and 24-hour unsuppressed simulation. | Safety, reliability, and financial consequence estimates. | Estimates (in dollars) based on cost-benefit framework
8 (WiNGS-Planning ) | PSPS Likelihood | The probability of a SCADA sectionalizing device experiencing de-energization is calculated based on historical events. | - Historical weather station data - Historical PSPS de-energization events - GIS asset attributes - Distribution grid connectivity | -Weather station data - GIS asset data | PSPS LoRE | Number of events per year
9 (WiNGS-Planning) | PSPS Consequence | Weather conditions (WL1 + WL2 +WL3+ WL4) and vegetation conditions (VG1) during the historical worst fire weather days in the service territory. | - Number and type of customers de-energized - Expected duration of PSPS | - Customer information - PSPS duration assumptions | PSPS CoRE | Estimates (in dollars) based on cost-benefit framework
10 (WiNGS-Ops) | PSPS Likelihood | Likelihood = 1 | Assumption based on weather and fuel conditions during extreme fire weather conditions that meet the criteria for initiating a PSPS. | Subject matter expert assumptions | PSPS LoRE | Unitless
11 (WiNGS-Ops) | PSPS Consequence | - Event specific assumptions - 24 hour de-energization event | - Number and type of customers de-energized - Expected duration of PSPS | - Customer information - PSPS duration assumptions - Grid connectivity | PSPS CoRE | Unitless
12 (WiNGS-Planning) | PEDS Likelihood | The probability of a SCADA sectionalizing device experiencing an outage due to device settings or protective equipment. Calculated based on historical events. | Historical outage events when settings are enabled | Historical SAIDIDAT outage information | PEDS LoRE | Number of events per year
13 (WiNGS-Planning) | PEDS Consequence | Estimated PEDS consequence values at each SCADA sectionalizing device where protective equipment and device settings are enabled. | - Number of customers minutes interrupted - Expected duration of PEDS event | - Customer information - PEDS duration assumptions | PEDS CoRE | Estimates (in dollars) based on cost-benefit framework
14 (WiNGS-Ops) | PEDS Likelihood PEDS Consequence | n/a | n/a | n/a | n/a | n/a
15 (WiNGS-Planning WiNGS-Ops) | Customer impact scaling factor | Scaling factors of the Safety attribute determined by subject matter expertise to artificially elevate the safety risk estimates for PSPS Critical Facilities, Urgent, Essential, Sensitive, Life Support, MBL, and AFN customers | Customer counts for PSPS Critical Facilities, Urgent, Essential, Sensitive, Life Support, MBL, and AFN customers that are associated to each SCADA sectionalizing device. | GIS production via AWS | Customer counts per category | Integers
16 (Wildfire Likelihood) | Conductor PoF | Weather conditions (WL1 + WL2 +WL3+ WL4) and vegetation conditions (VG1) during the historical worst fire weather days in the service territory. | - Historical Weather conditions - Historical conductor failures - Asset location and attributes | See Appendix B | Number of asset failures per hour and per mile | Failures/(mile-hour) that are aggregated to failures/year
17 (Wildfire Likelihood) | Vegetation PoF | Weather conditions (WL1 + WL2 +WL3+ WL4) and vegetation conditions (VG1) during the historical worst fire weather days in the service territory. | - Historical Weather conditions - Historical vegetation failures - Asset location and attributes | See Appendix B | Number of asset failures per hour and per mile | Failures/(mile-hour) that are aggregated to failures/year
18 (Wildfire Likelihood) | Vehicle Contact PoF | Weather conditions (WL1 + WL2 +WL3+ WL4) and vegetation conditions (VG1) during the historical worst fire weather days in the service territory. | - Historical weather conditions - Historical vehicle to asset contacts - Asset location and attributes of nearby roads | See Appendix B | Number of asset failures per hour and per mile | Failures/(mile-hour) that are aggregated to failures/year
19 (Wildfire Likelihood) | Other Equipment & Foreign Object PoF | Weather conditions (WL1 + WL2 +WL3+ WL4) and vegetation conditions (VG1) during the historical worst fire weather days in the service territory. | - Historical Weather conditions - Historical conductor failures due to non-wind-related events or external objects (e.g., animals, balloons, transformers, etc.) - Asset location and attributes | See Appendix B | Number of asset failures per hour and per mile | Failures/(mile-hour) that are aggregated to failures/year
20 (Wildfire Likelihood) | Pole/Span Conditional PoI | Weather conditions (WL1 + WL2 +WL3+ WL4) and vegetation conditions (VG1) during the historical worst fire weather days in the service territory. | Weather conditions and asset level probability of failure models (PoF) and conditional ignition probability model (PoI) | See Appendix B | Ignitions per hour and per mile | Ignitions/(mile-hour) that are aggregated to ignitions/year

## OEIS Table 5-5
Risk Ranking (by Overall Utility Risk Per Mile) | Circuit, Segment, or Span ID | Overall Utility Risk Score | Wildfire Risk Score | Outage Program Risk Score | Top Risk Contributors | Total Miles | Version of Risk Model Used | Overall Utility Risk Per Mile*
1 | 222-1986R | 79194348.7939 | 78602169.7569 | 592179.037 | Wildfire | 21.2556 | Version 4 | 3725802.2593
2 | 237-1765R | 28249252.4704 | 28064039.1156 | 185213.3548 | Wildfire | 8.3421 | Version 4 | 3386367.5403
3 | 222-1990R | 45106640.152 | 44939414.3997 | 167225.7524 | Wildfire | 14.2375 | Version 4 | 3168165.4334
4 | 358-682F | 37602118.365 | 37073060.587 | 529057.778 | Wildfire | 12.5079 | Version 4 | 3006264.7727
5 | 909-451 | 55252374.6886 | 54850768.6606 | 401606.028 | Wildfire | 20.5957 | Version 4 | 2682717.8449
6 | 909-805R | 32313161.0224 | 32075252.6475 | 237908.3748 | Wildfire | 13.4184 | Version 4 | 2408131.4078
7 | 1458-601R | 37077301.9797 | 36838604.201 | 238697.7787 | Wildfire | 15.4477 | Version 4 | 2400175.1463
8 | 908-2038R | 41258574.2326 | 40800963.6338 | 457610.5988 | Wildfire | 17.9266 | Version 4 | 2301533.1908
9 | 1021-1748F | 35156122.4002 | 34811510.8905 | 344611.5097 | Wildfire | 17.727 | Version 4 | 1983191.3045
10 | 237-30R | 65515491.9922 | 64815658.7441 | 699833.2481 | Wildfire | 33.4712 | Version 4 | 1957370.1445
11 | 237-17R | 27080737.569 | 26780685.6631 | 300051.9059 | Wildfire | 14.6369 | Version 4 | 1850170.6508
12 | 237-2R | 30894123.4063 | 30619728.0088 | 274395.3975 | Wildfire | 16.7242 | Version 4 | 1847267.6138
13 | 1030-42R | 28398789.4867 | 27971255.8292 | 427533.6574 | Wildfire | 16.7214 | Version 4 | 1698351.3729
14 | 971-2050R | 28484583.8082 | 28174790.2275 | 309793.5808 | Wildfire | 20.7013 | Version 4 | 1375979.9329
15 | 524-69R | 40375330.9497 | 39985024.927 | 390306.0227 | Wildfire | 34.1718 | Version 4 | 1181538.8033
* The column "Overall Utility Risk Score per Mile" was added by SDG&E.

## OEIS Table 5-6
Key Risk Assessment Area | Proposed Improvement | Type of Improvement | Expected Value Add | Timeframe and Key Milestones | Model
RA-1, risk assessment methodology | RA-1-A. Incorporate Social Vulnerability Index (SVI) | Model Enhancements | Incorporating the SVI into wildfire CoRE and PSPS CoRE risk assessments would incorporate insights from social vulnerability metrics and improve equity in the evaluation of potential impacts on communities during both wildfires and PSPS de-energizations. | 2026: Integrate SVI factor into wildfire and PSPS consequence models | WiNGS-Ops WiNGS-Planning
RA-1, risk assessment methodology | RA-1-B. Retrain models and explore new methodologies | Model Enhancements | Integrating Moody’s RMS into the wildfire CoRE model may lead to insights into long-duration fires that incorporate fire suppression activities. | 2026-2028: Expand existing collaboration with Moody's RMS to assess their stochastic approach to fire consequence modeling. Ongoing efforts for model improvement | WiNGS-Ops WiNGS-Planning
RA-1, risk assessment methodology | RA-1-C. Estimate PSPS de-energization duration | Model Enhancements | Estimating PSPS de-energization duration and customer minutes impacted for each segment provides additional insights and context for PSPS de-energization decision-making. Estimates include all customers and the medical baseline, AFN, and socially vulnerable subsets. | 2026-2028: Integrate PSPS de-energization duration into wildfire and PSPS CoRE models | WiNGS-Ops WiNGS-Planning
RA-1, risk assessment methodology | RA-1-D. Develop templates for standardizing the creation, validation, and deployment of models in cloud environments | Data Governance and Data Architecture | Templates will enhance efficiency, promote consistency, and facilitate easier management of models. | 2026-2028: Develop and integrate templates into process, collect feedback, and refine and finalize templates | WiNGS-Ops WiNGS-Planning
RA-1, risk assessment methodology | RA-1-E. Retrain PoF and PoI models and explore new methodologies | Model Enhancements | Enhancing the modularity and flexibility of the existing PoF and PoI models (e.g. vegetation and conductor) will allow predictions beyond the boundaries of the HFTD and enhance the accuracy and predictability of the models. | 2026-2028: Modify the current model code to ensure compatibility with AWS. Incorporate new features and observations | WiNGS-Ops WiNGS-Planning
RA-1, risk assessment methodology | RA-1-F. Retrain the condition PoI model and explore new methodologies | Model Enhancements | Retraining the condition PoI model will enhance the accuracy and predictability of the model. | 2026-2028: Collaborate with Technosylva to investigate the integration of LFM daily values into the existing condition PoI model | WiNGS-Ops WiNGS-Planning
RA-2, design basis | RA-2-A. Continued evaluation of probabilities and uncertainties around expected event impacts | Model Enhancements | Incorporating climate change factors will enhance the accuracy, predictability, and data quality of the model as well as improve decision making around evaluation of projected scenarios. | 2026-2028: Explore incorporating climate change factors into risk event probabilities | WiNGS-Planning
RA-3, risk presentation | RA-3-A. Improve, expand, and enhance the WiNGS-Ops and WiNGS-Planning visualization platform. | Visualization Platform | Enhancing the visualization platform would facilitate quick and easy access to reliable data, faster initial loads, and overall stability of the platform. Identify potential enhancements for existing plots, tables, and graphs to elevate user experience and facilitate efficient risk information transfer. | 2026-2028: Ongoing efforts for improvement of the visualization platform | WiNGS-Ops WiNGS-Planning
RA-3, risk presentation | RA-3-B. Institute subject matter expert visualization review | Visualization Platform | Regular review of the platform would ensure the precision of displayed data, enhance existing visualizations, and pinpoint areas for improvement. | 2026-2028: Institute regular meetings with subject matter experts, visualization developers, and platform users. Establish a process for collecting and evaluating feedback. | WiNGS-Ops WiNGS-Planning
RA-4, risk event tracking | RA-4-A. Develop a more comprehensive procedure and maintain third-party reviews for all models | Model Validation and User Acceptance | More comprehensive procedures will ensure quality of the models. | 2026-2028: Implement a more comprehensive independent third-party review process to conduct audits on data, models, and pipelines | WiNGS-Ops WiNGS-Planning
RA-6, data engineering optimization | RA-6-A. Optimize model architecture and pipelines to allow for sensitivity analysis | Data Governance and Data Architecture | Optimization will facilitate in-depth sensitivity analysis and comprehensive assessment of uncertainties. This encompasses refining the model architecture for a detailed examination of its responses to diverse inputs and conditions, which will establish a robust framework to evaluate uncertainties in model predictions. | 2026-2028: Initiate enhancements to model architecture, review methodologies, and optimize feature engineering. Refine the model architecture for a detailed examination of its responses to diverse inputs and conditions. | WiNGS-Ops WiNGS-Planning
RA-6, data engineering optimization | RA-6-B. Track model error | Model Validation and User Acceptance | A tracking system will promote diligent monitoring of remediation efforts. | 2026-2028: Establish an internal tracking system for model issues and independent audit findings | WiNGS-Ops WiNGS-Planning

## OEIS Table 6-1
Priority | Circuit Segment and/or Span ID | Length (miles) | Overall Utility Risk | Wildfire Risk | Outage Program Risk | Percent of Overall Utility Risk | Associated Risk Drivers
1 | 222-1986R | 21.2556 | 79194349 | 78602170 | 592179 | 2.612% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
2 | 237-30R | 33.4712 | 65515492 | 64815659 | 699833 | 2.16% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
3 | 909-451 | 20.5957 | 55252375 | 54850769 | 401606 | 1.822% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
4 | 222-1990R | 14.2375 | 45106640 | 44939414 | 167226 | 1.487% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
5 | 908-2038R | 17.9266 | 41258574 | 40800964 | 457611 | 1.361% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
6 | 524-69R | 34.1718 | 40375331 | 39985025 | 390306 | 1.331% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
7 | 358-682F | 12.5079 | 37602118 | 37073061 | 529058 | 1.24% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
8 | 1458-601R | 15.4477 | 37077302 | 36838604 | 238698 | 1.223% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
9 | 1021-1748F | 17.727 | 35156122 | 34811511 | 344612 | 1.159% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
10 | 909-805R | 13.4184 | 32313161 | 32075253 | 237908 | 1.066% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
11 | 237-2R | 16.7242 | 30894123 | 30619728 | 274395 | 1.019% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
12 | 971-2050R | 20.7013 | 28484584 | 28174790 | 309794 | 0.9393% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
13 | 1030-42R | 16.7214 | 28398789 | 27971256 | 427534 | 0.9365% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
14 | 237-1765R | 8.3421 | 28249252 | 28064039 | 185213 | 0.9316% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
15 | 237-17R | 14.6369 | 27080738 | 26780686 | 300052 | 0.893% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
16 | 907-1716R | 12.7815 | 27066455 | 26848173 | 218282 | 0.8925% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
17 | 1030-989R | 19.582 | 26696216 | 26471622 | 224594 | 0.8803% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
18 | 214-1122R | 19.9074 | 26281150 | 25993614 | 287536 | 0.8667% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
19 | 599-19R | 27.9316 | 25743456 | 25588005 | 155451 | 0.8489% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
20 | 1030-20R | 15.7168 | 25318462 | 25101311 | 217151 | 0.8349% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
21 | 235-899R | 14.5858 | 23678661 | 23291810 | 386852 | 0.7808% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
22 | 351-819R | 12.622 | 23517428 | 23341044 | 176383 | 0.7755% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
23 | 972-1590F | 20.6608 | 23409154 | 23032888 | 376266 | 0.772% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
24 | 972-32R | 15.6835 | 22914328 | 22336491 | 577837 | 0.7556% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
25 | 908-2055F | 11.56 | 22564078 | 22357449 | 206630 | 0.7441% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
26 | 214-647R | 11.3022 | 22354309 | 22185078 | 169231 | 0.7372% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
27 | 236-1569R | 16.0076 | 21222913 | 20875681 | 347232 | 0.6999% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
28 | 354-1706R | 18.9327 | 20510259 | 20339348 | 170911 | 0.6764% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
29 | 79-808R | 10.6674 | 19978326 | 19824672 | 153653 | 0.6588% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
30 | 215-1534R | 7.8127 | 19489706 | 19294169 | 195538 | 0.6427% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
31 | 1021-25R | 6.9741 | 18825690 | 18768979 | 56711 | 0.6208% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
32 | 79-785 | 13.604 | 18780929 | 18244488 | 536440 | 0.6193% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
33 | 597-595 | 17.4555 | 18774394 | 17938779 | 835615 | 0.6191% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
34 | 157-81R | 27.7907 | 18749596 | 18188039 | 561557 | 0.6183% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
35 | 352-27R | 13.0331 | 18614182 | 18495149 | 119034 | 0.6138% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
36 | 79-679R | 7.3706 | 18448583 | 18245132 | 203451 | 0.6084% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
37 | 357-45R | 11.815 | 17696753 | 17249773 | 446979 | 0.5836% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
38 | 357-2049F | 7.806 | 16869708 | 16664985 | 204723 | 0.5563% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
39 | 222-2085 | 31.2755 | 16772308 | 16218059 | 554249 | 0.6% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
40 | 470-47R | 24.3072 | 16740391 | 16634977 | 105414 | 0.6% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
41 | 356-19R | 24.1038 | 16012786 | 15654558 | 358229 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
42 | 1458-1131R | 6.1667 | 15987427 | 15842278 | 145148 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
43 | 1039-13 | 16.5898 | 15957171 | 15550885 | 406286 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
44 | 908-1172R | 10.1766 | 15766519 | 15502578 | 263941 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
45 | 73-1163 | 11.2661 | 15337185 | 15116479 | 220706 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
46 | 971-1973R | 10.9521 | 15148796 | 15005297 | 143499 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
47 | 971-383R | 9.7066 | 14770596 | 14538989 | 231607 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
48 | CB 351 | 6.7335 | 14599735 | 14550362 | 49373 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
49 | 78-26R | 6.3703 | 14526727 | 14317113 | 209613 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
50 | 216-1859F | 8.4771 | 14041288 | 13926879 | 114409 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
51 | 350-2192R | 31.8811 | 13871622 | 13613238 | 258385 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
52 | 524-46R | 12.3091 | 13710953 | 13572074 | 138879 | 0.5% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
53 | 353-904R | 7.0653 | 13534407 | 13457602 | 76804 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
54 | 350-2201R | 14.5687 | 13521745 | 13424968 | 96777 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
55 | 176-197F | 13.767 | 13172958 | 12751842 | 421116 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
56 | 970-1341R | 4.3966 | 12961613 | 12917272 | 44341 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
57 | CB 236 | 9.3687 | 12711188 | 12408602 | 302586 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
58 | 215-1531R | 8.4597 | 12702412 | 12475573 | 226839 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
59 | 79-658R | 9.5078 | 12321076 | 12230391 | 90685 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
60 | 521-32R | 9.9971 | 12241713 | 12165680 | 76033 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
61 | 182-2240F | 13.8138 | 11917199 | 11236832 | 680367 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
62 | 1030-1777 | 5.7761 | 11817577 | 11650338 | 167240 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
63 | 908-1236 | 5.4265 | 11763931 | 11622998 | 140933 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
64 | 357-750R | 8.4165 | 11757625 | 11499648 | 257977 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
65 | 1250-677R | 9.4852 | 11748909 | 11662207 | 86701 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
66 | 442-728R | 22.2475 | 11572221 | 10238671 | 1333550 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
67 | 176-161R | 10.6068 | 11523305 | 11381449 | 141856 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
68 | CB 971 | 5.1074 | 11456698 | 11400371 | 56327 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
69 | 521-14R | 12.6964 | 11350287 | 10974725 | 375563 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
70 | 524-27R | 14.5985 | 11317694 | 11291558 | 26136 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
71 | CB 355 | 8.9743 | 11288353 | 11157039 | 131314 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
72 | 971-388R | 17.9011 | 11267961 | 11152745 | 115216 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
73 | 350-41R | 16.422 | 11201389 | 11075404 | 125985 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
74 | 217-835R | 18.3176 | 10686933 | 10546230 | 140703 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
75 | 445-18R | 24.8581 | 10619797 | 10161862 | 457935 | 0.4% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
76 | 73-678R | 14.1729 | 10591377 | 10412424 | 178953 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
77 | CB RA1 | 9.6284 | 10517062 | 10338977 | 178085 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
78 | 357-50R | 10.8632 | 10432489 | 10123495 | 308994 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
79 | 1166-342R | 11.5801 | 10322642 | 10227749 | 94892 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
80 | 789-4R | 12.3028 | 10274006 | 10265349 | 8657 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
81 | 217-983R | 6.8811 | 10116963 | 10020804 | 96159 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
82 | 1166-18R | 7.5917 | 10108490 | 10085269 | 23221 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
83 | 176-1834R | 13.5415 | 10068517 | 9779527 | 288990 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
84 | 1022-17F | 4.5633 | 9800679 | 9763527 | 37152 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
85 | 236-1535R | 7.8693 | 9719042 | 9595871 | 123171 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
86 | 79-676R | 4.5924 | 9714146 | 9547622 | 166524 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
87 | 445-1311R | 13.2995 | 9632591 | 9146839 | 485752 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
88 | 222-1433R | 6.2775 | 9617971 | 9578744 | 39227 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
89 | 1023-46AE | 19.1678 | 9469915 | 9089007 | 380908 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
90 | RA1-402R | 3.8122 | 9339338 | 9276379 | 62959 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
91 | 356-30AE | 20.8132 | 9294675 | 8868206 | 426469 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
92 | 73-683R | 10.907 | 9288033 | 9142043 | 145990 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
93 | 353-1429R | 5.9518 | 9221802 | 8990136 | 231667 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
94 | 972-942R | 7.8388 | 9149684 | 9068839 | 80845 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
95 | 351-871R | 4.4941 | 9144312 | 9119654 | 24659 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
96 | 788-34R | 16.0985 | 9132237 | 8614678 | 517559 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
97 | 448-744R | 29.2157 | 9104562 | 8347200 | 757362 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
98 | 907-1702R | 5.3095 | 9100558 | 9075654 | 24904 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
99 | 521-700R | 13.3513 | 9012545 | 8927134 | 85411 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
100 | 524-50R | 10.5116 | 8801877 | 8643495 | 158382 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
101 | 521-18R | 12.5093 | 8713017 | 8657406 | 55612 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
102 | 1215-32R | 12.1911 | 8696504 | 8389974 | 306530 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
103 | 973-1245R | 3.3435 | 8620111 | 8579828 | 40283 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
104 | 859-42R | 17.8147 | 8606972 | 8594826 | 12146 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
105 | CB 788 | 21.0708 | 8569068 | 8146827 | 422241 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
106 | 521-1856R | 12.1965 | 8477862 | 8290638 | 187224 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
107 | 209-1769F | 31.9017 | 8462802 | 8440861 | 21941 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
108 | 907-1562AE | 4.1122 | 8439769 | 8238564 | 201206 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
109 | 450-1851F | 7.0884 | 8274122 | 8210482 | 63640 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
110 | 1458-565R | 5.7011 | 8159979 | 8098401 | 61578 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
111 | 972-1582R | 11.1523 | 8019179 | 7901674 | 117505 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
112 | 971-29R | 3.8006 | 8015407 | 7972516 | 42890 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
113 | 908-1372R | 3.7273 | 7960290 | 7828738 | 131552 | 0.3% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
114 | 355-41R | 6.2962 | 7500586 | 7388137 | 112449 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
115 | 222-2013R | 13.7044 | 7426976 | 7133534 | 293441 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
116 | 222-1523R | 12.4352 | 7406689 | 7156613 | 250076 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
117 | CB 476 | 18.0017 | 7260322 | 5346745 | 1913577 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
118 | 445-1325F | 11.7129 | 7250723 | 6968326 | 282396 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
119 | 78-782R | 1.7152 | 7202316 | 7167197 | 35119 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
120 | 974-715R | 8.7188 | 7107170 | 7075030 | 32140 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
121 | 1021-1760R | 2.9682 | 7055716 | 6926993 | 128723 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
122 | 236-1573R | 7.1517 | 6927856 | 6778520 | 149336 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
123 | CB 470 | 12.4373 | 6922049 | 6609552 | 312497 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
124 | RB1-427R | 12.6949 | 6920124 | 6752264 | 167859 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
125 | CB OK1 | 7.3438 | 6915682 | 6846549 | 69133 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
126 | 1250-671R | 2.001 | 6815428 | 6443061 | 372367 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
127 | 520-1527R | 10.7038 | 6763001 | 6541016 | 221985 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
128 | 449-13R | 16.5478 | 6729965 | 6090026 | 639939 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
129 | 214-1135R | 11.6815 | 6666922 | 6627374 | 39547 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
130 | CB 1235 | 20.7706 | 6645572 | 6585224 | 60348 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
131 | 1030-18R | 3.5275 | 6620910 | 6532115 | 88794 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
132 | 973-626R | 10.906 | 6521724 | 6393286 | 128438 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
133 | 474-22AE | 9.6011 | 6435983 | 6428610 | 7374 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
134 | 1250-27R | 4.6189 | 6418508 | 5971509 | 446999 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
135 | 975-22R | 1.6544 | 6417038 | 5152705 | 1264334 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
136 | 230-133AE | 11.3506 | 6388694 | 6277696 | 110998 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
137 | 411-30R | 24.6051 | 6370041 | 6272318 | 97724 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
138 | 907-2820R | 2.4583 | 6348476 | 6346946 | 1530 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
139 | CB 1234 | 17.3068 | 6311492 | 5319837 | 991655 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
140 | 239-2215R | 12.0589 | 6268657 | 6158320 | 110337 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
141 | 73-1130R | 12.0339 | 6201607 | 6033466 | 168141 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
142 | 1215-12R | 8.3178 | 6147284 | 6017064 | 130220 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
143 | CB 357 | 5.0178 | 6110855 | 5866849 | 244006 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
144 | RB1-433R | 6.3644 | 5946508 | 5905825 | 40683 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
145 | 1090-73F | 10.606 | 5899045 | 5876651 | 22395 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
146 | 175-90R | 11.9254 | 5741495 | 5561271 | 180223 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
147 | 73-23R | 8.2208 | 5733791 | 5642495 | 91295 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
148 | 909-453R | 2.3515 | 5703040 | 5701153 | 1887 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
149 | 78-35R | 1.532 | 5696336 | 5695327 | 1009 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
150 | 448-9R | 17.7839 | 5644811 | 5273685 | 371126 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
151 | 522-38R | 17.4926 | 5639841 | 5439140 | 200702 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
152 | 521-27R | 10.1674 | 5618623 | 5550020 | 68603 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
153 | 908-1368R | 18.6854 | 5570793 | 5361811 | 208982 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
154 | 350-2196R | 34.4453 | 5570686 | 5402875 | 167811 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
155 | 79-714R | 5.9877 | 5536621 | 5332551 | 204070 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
156 | 157-189R | 27.7167 | 5507024 | 5091861 | 415162 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
157 | 524-1782F | 8.5739 | 5468134 | 5455868 | 12266 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
158 | 356-16R | 5.9928 | 5437438 | 5336373 | 101064 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
159 | 215-38R | 6.4307 | 5434815 | 5375941 | 58875 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
160 | 441-30R | 5.7333 | 5348877 | 5272517 | 76360 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
161 | 236-1567R | 5.8553 | 5332004 | 5229334 | 102670 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
162 | 66-1213R | 16.7053 | 5312268 | 5193772 | 118496 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
163 | 283-55R | 7.2309 | 5299634 | 5223022 | 76612 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
164 | 470-40AE | 6.1881 | 5264969 | 5176968 | 88001 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
165 | 449-693R | 8.4553 | 5260706 | 5196145 | 64561 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
166 | CB RA2 | 3.5953 | 5229902 | 5131211 | 98691 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
167 | 973-1226R | 8.4832 | 5177870 | 5039262 | 138608 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
168 | 231-1635R | 29.745 | 5142095 | 5074262 | 67833 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
169 | 1030-1728R | 2.6777 | 5124159 | 5035021 | 89138 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
170 | CB MOR1 | 3.55 | 5119714 | 5045788 | 73926 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
171 | 357-1299R | 2.7532 | 5098733 | 5082457 | 16276 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
172 | 1022-322R | 3.6661 | 5072199 | 5029594 | 42605 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
173 | 1021-855 | 2.9135 | 5034375 | 5009473 | 24902 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
174 | 520-35R | 14.3572 | 4997794 | 4822591 | 175203 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
175 | 1090-74F | 9.8927 | 4990920 | 4972119 | 18801 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
176 | 234-48R | 11.5796 | 4939379 | 4912539 | 26840 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
177 | 176-194R | 9.0746 | 4934160 | 4820768 | 113392 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
178 | 212-725R | 11.8649 | 4887827 | 4846330 | 41497 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
179 | 222-2063 | 4.9145 | 4859776 | 4852517 | 7259 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
180 | 307-234R | 4.6394 | 4762848 | 4550699 | 212149 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
181 | 441-27R | 7.3796 | 4750127 | 4655244 | 94883 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
182 | 1138-6R | 19.4272 | 4663878 | 4249839 | 414039 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
183 | 991-1206R | 9.2129 | 4576791 | 4566682 | 10109 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
184 | 353-901F | 2.3892 | 4555619 | 4296049 | 259570 | 0.2% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
185 | 221-788 | 3.6174 | 4481914 | 4457135 | 24779 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
186 | 240-2004R | 19.7983 | 4437659 | 4344912 | 92747 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
187 | 445-894R | 26.8775 | 4421002 | 3895845 | 525157 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
188 | 175-64R | 10.35 | 4385400 | 4276794 | 108606 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
189 | 235-897R | 6.6053 | 4375038 | 3877449 | 497589 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
190 | 1458-1061 | 2.3455 | 4370099 | 4312123 | 57976 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
191 | 971-371R | 2.4735 | 4351506 | 4330446 | 21060 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
192 | CB 599 | 11.4604 | 4323244 | 4315017 | 8228 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
193 | 1233-591R | 6.4721 | 4300184 | 4242542 | 57642 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
194 | 471-36F | 3.9252 | 4253667 | 4039168 | 214499 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
195 | 305-32R | 7.0648 | 4233867 | 4103697 | 130169 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
196 | 182-2252R | 3.4226 | 4229945 | 4196758 | 33186 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
197 | 1105-1479 | 3.4339 | 4228044 | 4224871 | 3173 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
198 | 1001-1820F | 6.479 | 4222247 | 3859583 | 362664 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
199 | 176-164R | 6.2526 | 4184747 | 4105075 | 79671 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
200 | 67-34R | 20.3065 | 4180137 | 3921084 | 259053 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
201 | CB 233 | 18.8385 | 4127696 | 4075589 | 52106 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
202 | CB 1250 | 2.5689 | 4075236 | 4072564 | 2672 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
203 | 175-2024R | 7.3674 | 4029008 | 3992844 | 36165 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
204 | 1166-15R | 5.0748 | 3965222 | 3896389 | 68833 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
205 | 221-37AE | 7.7195 | 3934773 | 3817749 | 117024 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
206 | 221-6R | 6.0572 | 3904259 | 3899503 | 4756 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
207 | 157-204R | 13.2184 | 3876133 | 3836814 | 39319 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
208 | CB 471 | 9.5888 | 3808733 | 3802289 | 6444 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
209 | TM1-10R | 3.3899 | 3782857 | 3763197 | 19659 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
210 | 1023-48R | 16.5267 | 3773847 | 3675354 | 98494 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
211 | 249-24R | 15.5693 | 3753230 | 3597511 | 155719 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
212 | 240-2006R | 12.1512 | 3742572 | 3707607 | 34965 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
213 | CB RC1 | 3.232 | 3739875 | 3707620 | 32254 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
214 | DV1-3R | 7.3926 | 3719400 | 3539616 | 179784 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
215 | 221-1230F | 3.8686 | 3690962 | 3687573 | 3389 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
216 | 1250-8R | 4.2055 | 3684980 | 3616965 | 68015 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
217 | 445-39R | 8.4532 | 3678581 | 3220261 | 458320 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
218 | 240-2032R | 13.8096 | 3665735 | 3549054 | 116681 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
219 | 217-837R | 12.6807 | 3657183 | 3461858 | 195325 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
220 | 354-24AE | 3.6864 | 3653654 | 3234792 | 418862 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
221 | 908-2040 | 5.3209 | 3646805 | 3351774 | 295031 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
222 | 237-1761R | 7.4915 | 3634146 | 3612196 | 21950 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
223 | 222-1988R | 0.94526 | 3619436 | 3592934 | 26502 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
224 | 350-2188R | 22.0576 | 3602012 | 3439370 | 162642 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
225 | 220-298R | 33.1318 | 3585631 | 3204472 | 381159 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
226 | 1233-585R | 6.2353 | 3561959 | 3505653 | 56306 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
227 | 441-23R | 5.1261 | 3518020 | 3428405 | 89616 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
228 | 974-23R | 16.0805 | 3492863 | 3272567 | 220295 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
229 | 230-2060R | 9.1409 | 3473455 | 3392757 | 80698 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
230 | 454-48F | 3.4244 | 3441166 | 3430800 | 10367 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
231 | 520-1509R | 15.3043 | 3413912 | 3165391 | 248521 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
232 | 444-43R | 20.6063 | 3413814 | 3334275 | 79539 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
233 | 920-1342R | 6.3664 | 3406646 | 3384147 | 22499 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
234 | 176-1845R | 7.3522 | 3401023 | 3324151 | 76872 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
235 | 246-34R | 12.821 | 3387006 | 3202237 | 184769 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
236 | CB SL1 | 6.6007 | 3361570 | 3150270 | 211301 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
237 | 791-419F | 5.507 | 3349759 | 3101216 | 248543 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
238 | CB 1023 | 3.9246 | 3332739 | 3326465 | 6274 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
239 | CB 234 | 11.0316 | 3294853 | 3257847 | 37006 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
240 | 221-23R | 7.9883 | 3270238 | 3013933 | 256305 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
241 | 157-232R | 10.9006 | 3160508 | 3010962 | 149546 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
242 | 396-699R | 20.4475 | 3136952 | 2766177 | 370775 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
243 | 75-2259F | 4.3521 | 3135458 | 3128270 | 7187 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
244 | 157-1928R | 3.1864 | 3052674 | 3024213 | 28462 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
245 | 233-123R | 15.066 | 3035805 | 3000562 | 35242 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
246 | 79-799R | 6.7626 | 3034823 | 2947433 | 87391 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
247 | CB PE1 | 6.7553 | 3027548 | 2867898 | 159650 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
248 | 1233-587R | 7.6085 | 2983729 | 2921128 | 62601 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
249 | 520-1045R | 8.7312 | 2978814 | 2899718 | 79096 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
250 | 206-1817 | 11.7296 | 2976573 | 2969127 | 7447 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
251 | 177-955 | 4.7979 | 2963406 | 2318247 | 645159 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
252 | 1023-200R | 3.7841 | 2889973 | 2868051 | 21922 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
253 | 452-38AE | 2.7653 | 2823751 | 2821884 | 1867 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
254 | 236-1561R | 5.1765 | 2823578 | 2746271 | 77307 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
255 | CB 305 | 5.6647 | 2786774 | 2706155 | 80619 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
256 | 212-773R | 11.8401 | 2758567 | 2642067 | 116499 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
257 | 1001-1130R | 3.7048 | 2758283 | 2661345 | 96938 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
258 | CB 907 | 1.375 | 2742284 | 2737736 | 4548 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
259 | 221-344R | 11.5724 | 2735928 | 2629449 | 106479 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
260 | 231-1136R | 13.2557 | 2730918 | 2684542 | 46376 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
261 | 217-48AE | 15.1559 | 2727585 | 2396178 | 331407 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
262 | 175-24R | 4.8509 | 2651435 | 1873251 | 778185 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
263 | 520-1489R | 17.8309 | 2637934 | 2552368 | 85566 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
264 | 448-47R | 8.8214 | 2612271 | 2400903 | 211368 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
265 | 67-24R | 13.6103 | 2610800 | 2443585 | 167215 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
266 | 79-685R | 3.9579 | 2564752 | 2548703 | 16049 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
267 | 237-28F | 1.5879 | 2530225 | 2500530 | 29696 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
268 | 353-593F | 2.0774 | 2519059 | 2498440 | 20619 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
269 | 1094-35F | 5.1365 | 2514283 | 2510139 | 4144 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
270 | CB 231 | 8.6068 | 2499974 | 2482127 | 17847 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
271 | 73-1164 | 1.3216 | 2448829 | 2415513 | 33316 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
272 | 307-1538F | 2.2173 | 2407233 | 2192285 | 214948 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
273 | 305-35R | 5.5248 | 2371786 | 2317508 | 54278 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
274 | 1458-1058F | 1.4693 | 2365690 | 2023559 | 342131 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
275 | 233-86F | 17.4522 | 2341674 | 2011557 | 330118 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
276 | 221-824 | 3.4163 | 2324221 | 2251307 | 72915 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
277 | 449-6R | 5.3305 | 2320016 | 2216710 | 103306 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
278 | 236-1563R | 3.7138 | 2260662 | 2229176 | 31487 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
279 | 387-11 | 13.7926 | 2227281 | 1988428 | 238853 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
280 | 353-594F | 1.221 | 2215650 | 2214151 | 1498 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
281 | 1215-28R | 3.06 | 2215156 | 2097533 | 117623 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
282 | 75-996R | 10.9093 | 2211138 | 2194050 | 17088 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
283 | 188-11F | 5.0004 | 2209344 | 2206187 | 3157 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
284 | 214-583R | 6.1356 | 2208313 | 2188307 | 20007 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
285 | 220-288R | 7.2415 | 2198680 | 2118137 | 80543 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
286 | 212-886R | 8.9137 | 2163525 | 2135826 | 27699 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
287 | 1030-1823F | 0.91593 | 2150974 | 2139065 | 11909 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
288 | 1100-1172R | 2.2354 | 2144979 | 2138024 | 6955 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
289 | 448-714R | 11.8164 | 2119752 | 1180662 | 939090 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
290 | 307-1684R | 3.7428 | 2117857 | 2065520 | 52338 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
291 | CB 237 | 0.84619 | 2111575 | 2101904 | 9670 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
292 | 79-660R | 7.564 | 2087039 | 2034167 | 52871 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
293 | 520-1904 | 7.6936 | 2084536 | 2011217 | 73319 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
294 | 230-1586R | 8.614 | 2072884 | 1887664 | 185219 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
295 | CTL1-3R | 6.8671 | 2064033 | 1628525 | 435508 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
296 | 157-257R | 23.0074 | 2061188 | 1680704 | 380484 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
297 | 221-675R | 7.0073 | 2055424 | 2045346 | 10078 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
298 | 520-45 | 9.4684 | 2044646 | 1994999 | 49647 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
299 | 217-41AE | 13.7784 | 2013597 | 1796629 | 216968 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
300 | 283-71F | 5.1553 | 2013590 | 1767951 | 245639 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
301 | 230-127AE | 10.5112 | 2000465 | 1900121 | 100345 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
302 | 921-800F | 5.8841 | 1991711 | 1525775 | 465936 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
303 | 353-900F | 0.99152 | 1991358 | 1766220 | 225138 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
304 | 206-974 | 8.7475 | 1943672 | 1937614 | 6058 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
305 | 182-2250 | 1.2528 | 1939213 | 1934190 | 5023 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
306 | 75-41 | 2.6099 | 1937585 | 1934834 | 2751 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
307 | 220-294R | 13.4125 | 1925888 | 1623347 | 302541 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
308 | 211-771R | 14.1159 | 1890633 | 1721677 | 168956 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
309 | 1243-45R | 4.2257 | 1878383 | 1860483 | 17899 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
310 | 157-273R | 8.4758 | 1867403 | 1774229 | 93174 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
311 | 411-1873R | 9.9068 | 1857539 | 1817298 | 40241 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
312 | 442-16R | 10.8114 | 1834938 | 1763136 | 71801 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
313 | 221-1251R | 16.3418 | 1814850 | 1589148 | 225703 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
314 | 211-312R | 18.1587 | 1809515 | 1524787 | 284727 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
315 | 445-19R | 11.1993 | 1766704 | 1496872 | 269831 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
316 | 212-1177R | 12.4913 | 1738925 | 1659398 | 79527 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
317 | 185-51F | 8.9873 | 1723971 | 1584784 | 139186 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
318 | 214-613R | 5.4881 | 1721769 | 1475342 | 246427 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
319 | 288-18 | 5.4562 | 1717867 | 1651247 | 66620 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
320 | 75-32R | 2.4181 | 1708385 | 1701119 | 7266 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
321 | 355-6R | 1.7237 | 1698710 | 1357932 | 340778 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
322 | CB 928 | 3.6036 | 1655011 | 1319990 | 335021 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
323 | CB 1106 | 1.2773 | 1646984 | 568815 | 1078169 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
324 | CB 232 | 6.8056 | 1642597 | 1599467 | 43130 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
325 | 176-200F | 1.165 | 1635841 | 1459888 | 175953 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
326 | 520-1525R | 7.8576 | 1632803 | 1604824 | 27979 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
327 | 67-45R | 10.2425 | 1627951 | 1510503 | 117447 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
328 | 79-668R | 9.2899 | 1606907 | 1139717 | 467190 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
329 | 445-17R | 3.4282 | 1603556 | 1422688 | 180868 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
330 | 206-953R | 8.4224 | 1585852 | 1580692 | 5160 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
331 | 239-2211R | 2.7707 | 1585172 | 1564094 | 21078 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
332 | 212-1204R | 10.0072 | 1570376 | 1491430 | 78946 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
333 | 1233-259R | 4.8975 | 1558539 | 1536152 | 22386 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
334 | 920-735AE | 7.5286 | 1554328 | 1072820 | 481508 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
335 | CB JU1 | 2.6673 | 1531749 | 1498742 | 33006 | 0.1% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
336 | 474-29 | 1.8853 | 1510730 | 1509132 | 1598 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
337 | 449-16R | 2.4038 | 1495506 | 1450226 | 45280 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
338 | 212-758R | 9.6756 | 1482462 | 1442028 | 40434 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
339 | 520-10R | 5.0582 | 1478745 | 1448788 | 29957 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
340 | 212-888R | 6.9867 | 1471062 | 1438972 | 32090 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
341 | 908-1370R | 5.8533 | 1466276 | 1346129 | 120147 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
342 | CB 327 | 0.87727 | 1456709 | 1453689 | 3020 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
343 | 387-15 | 6.7754 | 1455053 | 1295209 | 159844 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
344 | 217-972R | 9.5829 | 1438659 | 1307400 | 131259 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
345 | CB 246 | 11.0435 | 1438442 | 1294643 | 143798 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
346 | CB 1243 | 5.0473 | 1438363 | 1434754 | 3609 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
347 | 504-1563 | 9.2025 | 1424191 | 1418597 | 5594 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
348 | CB 1090 | 4.8975 | 1414511 | 1409149 | 5362 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
349 | 215-1544R | 2.7396 | 1412430 | 1385495 | 26935 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
350 | 1021-883R | 0.68239 | 1386630 | 1380795 | 5835 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
351 | 1233-589R | 3.2034 | 1386491 | 1371477 | 15013 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
352 | 463-1229 | 11.4998 | 1378318 | 1364772 | 13546 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
353 | 247-46 | 6.4578 | 1360333 | 1258488 | 101845 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
354 | 222-1503R | 2.6021 | 1359395 | 1293519 | 65877 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
355 | 445-897R | 1.0659 | 1351775 | 1314502 | 37273 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
356 | 411-47R | 14.6036 | 1350406 | 1296039 | 54367 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
357 | 358-33 | 0.45755 | 1344644 | 1340076 | 4567 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
358 | CB 200 | 13.8235 | 1342656 | 401401 | 941254 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
359 | 473-36R | 14.9443 | 1339207 | 10897 | 1328309 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
360 | 410-50R | 11.9653 | 1314333 | 1306249 | 8084 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
361 | CB 412 | 17.7277 | 1311992 | 1159435 | 152557 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
362 | CB 975 | 0.46496 | 1304374 | 1298020 | 6354 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
363 | 91-7F | 7.7339 | 1295991 | 1243884 | 52107 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
364 | 63-797R | 3.9205 | 1294921 | 1241111 | 53810 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
365 | 241-570 | 18.8601 | 1283068 | 448908 | 834160 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
366 | 206-1105 | 4.2677 | 1279044 | 1276283 | 2761 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
367 | 212-734R | 17.8821 | 1265960 | 1239608 | 26352 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
368 | CB 240 | 6.5815 | 1263032 | 1233691 | 29340 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
369 | 357-1147R | 0.95666 | 1251176 | 1239446 | 11730 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
370 | CB 175 | 2.8512 | 1236507 | 1040413 | 196095 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
371 | 448-1234R | 3.0297 | 1211619 | 1179995 | 31625 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
372 | CB 590 | 1.5992 | 1201404 | 758282 | 443122 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
373 | 211-279R | 15.3767 | 1199632 | 1073512 | 126121 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
374 | 240-1028R | 5.5421 | 1181536 | 1162446 | 19090 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
375 | 1243-319R | 3.321 | 1178043 | 1170365 | 7678 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
376 | 576-201F | 0 | 1160460 | $- | 1160460 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
377 | 859-13F | 10.7166 | 1153856 | 1146360 | 7496 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
378 | CB 1101 | 3.0366 | 1133279 | 1130105 | 3174 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
379 | CB 441 | 6.0637 | 1133081 | 1065956 | 67124 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
380 | 450-1854 | 2.1386 | 1132289 | 1078517 | 53772 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
381 | 239-2213R | 5.4023 | 1116470 | 1076921 | 39549 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
382 | CB BN2 | 10.1083 | 1098831 | 1091744 | 7087 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
383 | CB 522 | 6.96 | 1074326 | 961464 | 112862 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
384 | CB 591 | 9.3315 | 1060547 | 957018 | 103529 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
385 | CB 204 | 14.6288 | 1059531 | 856339 | 203192 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
386 | 212-799R | 5.2246 | 1038800 | 1008878 | 29922 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
387 | 210-392R | 10.6016 | 1037896 | 889812 | 148084 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
388 | CB FB2 | 5.2678 | 1029584 | 971192 | 58393 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
389 | 239-2217R | 4.9148 | 1029567 | 713201 | 316366 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
390 | 1001-1140R | 1.3333 | 1005685 | 946203 | 59482 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
391 | 212-739R | 9.5874 | 998791 | 965055 | 33736 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
392 | 198-37R | 7.3848 | 973100 | 929637 | 43463 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
393 | CB 791 | 2.9851 | 969889 | 967787 | 2101 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
394 | CB 248 | 4.4809 | 962153 | 957351 | 4802 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
395 | 242-1426F | 3.42 | 960345 | 633435 | 326909 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
396 | CB 542 | 2.267 | 949478 | 906320 | 43157 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
397 | 393-14R | 2.6388 | 924804 | 173746 | 751058 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
398 | 1090-636R | 8.1866 | 919373 | 863579 | 55794 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
399 | CB 66 | 7.6461 | 917867 | 857861 | 60006 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
400 | CB RA3 | 5.0727 | 916197 | 636737 | 279461 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
401 | 450-88R | 3.7312 | 894374 | 384234 | 510141 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
402 | 357-2047F | 0.49562 | 878930 | 839250 | 39680 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
403 | 532-763 | 6.6682 | 872935 | 192670 | 680265 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
404 | CB 790 | 1.346 | 864253 | 541657 | 322596 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
405 | 591-39AE | 8.7941 | 863682 | 263803 | 599879 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
406 | CB 358 | 0.31499 | 861433 | 162618 | 698816 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
407 | 242-1411F | 0.27213 | 861031 | 2839 | 858192 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
408 | 239-2207R | 6.8952 | 860323 | 843815 | 16508 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
409 | 442-509R | 4.9693 | 852926 | 724344 | 128582 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
410 | 908-30 | 1.5403 | 847524 | 818047 | 29477 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
411 | 175-94R | 2.0289 | 836246 | 666976 | 169269 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
412 | 540-241R | 1.2638 | 833631 | 564790 | 268841 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
413 | CB 249 | 3.6983 | 826921 | 802439 | 24482 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
414 | 521-1819R | 5.3936 | 811000 | 724333 | 86667 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
415 | 500-1531 | 0.97704 | 800550 | 172930 | 627621 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
416 | 504-40R | 7.4225 | 796376 | 791219 | 5157 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
417 | CB 474 | 4.6676 | 794880 | 791734 | 3145 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
418 | 1021-92 | 0.46834 | 794363 | 791178 | 3185 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
419 | 450-1853F | 1.1027 | 792202 | 734912 | 57290 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
420 | 240-1044 | 2.7573 | 791336 | 781085 | 10250 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
421 | 230-181 | 2.4656 | 788722 | 774443 | 14279 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
422 | 1118-1718F | 0.77126 | 788376 | 783678 | 4698 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
423 | CB 1138 | 7.6676 | 765496 | 574088 | 191408 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
424 | 789-15 | 1.1117 | 761981 | 761323 | 657 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
425 | 300-484F | 10.4561 | 754132 | 696898 | 57234 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
426 | 520-1902R | 10.4533 | 748333 | 578741 | 169592 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
427 | 307-1492R | 1.5443 | 744313 | 688944 | 55369 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
428 | CB 306 | 1.2839 | 737500 | 716009 | 21491 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
429 | 504-2501R | 5.5121 | 733683 | 730076 | 3607 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
430 | CB 395 | 0.85682 | 731695 | 5615 | 726080 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
431 | 1090-1734 | 2.1343 | 730548 | 725008 | 5540 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
432 | 157-207R | 2.0208 | 719086 | 718279 | 808 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
433 | 233-41R | 10.1081 | 718991 | 701522 | 17469 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
434 | 221-35 | 0.64962 | 710327 | 706480 | 3847 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
435 | 186-940R | 2.8176 | 708016 | 192783 | 515234 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
436 | 442-729 | 2.7701 | 704609 | 680766 | 23843 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
437 | 1022-26R | 0.38903 | 694720 | 689285 | 5436 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
438 | CB 396 | 3.6322 | 669815 | 96069 | 573745 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
439 | CB 1140 | 0.29399 | 668098 | 195 | 667903 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
440 | 237-26F | 2.4644 | 663215 | 470121 | 193094 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
441 | 182-2254R | 0.87803 | 655801 | 650139 | 5662 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
442 | 975-7 | 0 | 645751 | $- | 645751 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
443 | CB 178 | 3.4303 | 644514 | 642158 | 2356 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
444 | CB NVS1 | 10.0271 | 638079 | 631801 | 6277 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
445 | CB 392 | 4.5493 | 632789 | 37713 | 595076 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
446 | 448-735R | 8.2068 | 630763 | 499073 | 131689 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
447 | CB 455 | 7.4072 | 628651 | 623227 | 5424 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
448 | 991-1 | 1.2636 | 626862 | 412906 | 213956 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
449 | 452-1404F | 0.80794 | 625542 | 624941 | 601 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
450 | 449-683 | 1.6021 | 625313 | 604656 | 20657 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
451 | 67-37R | 8.2782 | 622304 | 542523 | 79781 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
452 | 221-782R | 3.289 | 618017 | 609875 | 8143 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
453 | CB 241 | 3.3744 | 614484 | 32157 | 582327 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
454 | 212-638R | 4.2816 | 609780 | 604091 | 5689 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
455 | CB 307 | 1.1522 | 601867 | 540077 | 61790 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
456 | 358-1175F | 0.47553 | 599583 | 582832 | 16752 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
457 | 505-635R | 22.8048 | 591818 | 576198 | 15620 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
458 | 916-381 | 1.3913 | 590912 | 419985 | 170927 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
459 | 970-18AE | 0 | 588322 | $- | 588322 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
460 | 326-35R | 13.9548 | 586183 | 109665 | 476517 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
461 | 1023-89R | 4.3252 | 585509 | 513363 | 72146 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
462 | 456-5 | 7.8148 | 584439 | 579147 | 5292 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
463 | 441-279R | 2.1594 | 582163 | 531722 | 50442 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
464 | 444-9R | 14.7171 | 571237 | 403911 | 167326 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
465 | 177-941AE | 7.2284 | 569509 | 565012 | 4497 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
466 | CB 390 | 1.4761 | 555196 | 22866 | 532330 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
467 | 96-47R | 7.8716 | 553695 | 488905 | 64791 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
468 | 288-2380F | 1.7432 | 550610 | 511420 | 39190 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
469 | CB 391 | 0.66137 | 550204 | 2886 | 547318 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
470 | 442-758F | 1.1019 | 549983 | 544074 | 5909 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
471 | CB 473 | 8.3298 | 543890 | 104236 | 439654 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
472 | 450-50R | 0.51918 | 537070 | 174706 | 362364 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
473 | 230-1606R | 2.6869 | 536384 | 423572 | 112812 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
474 | 334-46F | 0 | 529891 | $- | 529891 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
475 | 442-525 | 4.5645 | 526126 | 304904 | 221222 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
476 | CB 387 | 6.7638 | 522650 | 366600 | 156050 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
477 | 448-724R | 8.7678 | 520639 | 396646 | 123993 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
478 | 591-1594R | 3.0667 | 519957 | 500848 | 19109 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
479 | 586-3 | 4.2473 | 516808 | 454434 | 62374 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
480 | 214-536R | 2.6683 | 513329 | 506733 | 6596 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
481 | 1090-639R | 4.354 | 509502 | 468582 | 40920 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
482 | 553-27R | 16.2339 | 504265 | 493342 | 10923 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
483 | 504-287R | 7.8402 | 501828 | 496494 | 5334 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
484 | 210-172R | 6.4924 | 498150 | 448825 | 49324 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
485 | 244-29 | 20.8303 | 494908 | 187284 | 307624 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
486 | 454-45AE | 4.39 | 491786 | 204646 | 287140 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
487 | 204-32R | 17.63 | 490461 | 472621 | 17840 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
488 | 214-17AE | 6.825 | 484036 | 471453 | 12583 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
489 | CB 524 | 3.4998 | 481331 | 453656 | 27675 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
490 | 288-149R | 4.8645 | 481284 | 453892 | 27392 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
491 | 442-764R | 2.5085 | 474738 | 433481 | 41256 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
492 | 1139-4F | 4.1474 | 472177 | 1225 | 470952 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
493 | 183-440 | 3.165 | 471201 | 350430 | 120772 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
494 | 392-23F | 2.6426 | 466525 | 4306 | 462219 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
495 | 353-902F | 0.57917 | 465101 | 292268 | 172833 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
496 | 300-483F | 5.4324 | 458782 | 456399 | 2383 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
497 | 920-823 | 3.3104 | 458219 | 313175 | 145044 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
498 | 1242-1084 | 1.5712 | 456193 | 455151 | 1042 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
499 | 233-81F | 4.0824 | 447779 | 425199 | 22580 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
500 | CB 235 | 0.15928 | 443543 | 443368 | 175 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
501 | 928-19 | 2.1411 | 434883 | 432579 | 2304 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
502 | 1458-1056 | 0.50061 | 427448 | 386682 | 40766 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
503 | 182-2242F | 0 | 422927 | $- | 422927 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
504 | CB 556 | 1.5472 | 422664 | 421588 | 1076 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
505 | 157-165R | 4.8606 | 418568 | 367109 | 51459 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
506 | CB 576 | 0.64527 | 417702 | 327341 | 90362 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
507 | 1105-1483 | 0.32386 | 417001 | 394048 | 22953 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
508 | 486-61R | 8.0996 | 415568 | 410127 | 5442 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
509 | CB 313 | 1.4046 | 413098 | 130441 | 282657 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
510 | 858-14 | 3.2698 | 411696 | 409681 | 2016 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
511 | 1242-1079R | 1.6259 | 411541 | 410114 | 1427 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
512 | 1001-1814AE | 0.43788 | 409062 | 405584 | 3478 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
513 | 781-44 | 15.9541 | 408039 | 39351 | 368688 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
514 | CB 242 | 3.397 | 406818 | 261841 | 144977 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
515 | 176-1836R | 1.5242 | 404482 | 273584 | 130898 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
516 | 243-14R | 13.05 | 404259 | 119250 | 285008 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
517 | 1007-9F | 0 | 402779 | $- | 402779 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
518 | 214-4R | 3.7494 | 400189 | 391625 | 8565 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
519 | CB 394 | 0.54963 | 400010 | 10424 | 389585 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
520 | 395-33R | 0.79815 | 396976 | 552 | 396423 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
521 | CB 185 | 3.8089 | 396851 | 317222 | 79628 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
522 | 792-47R | 7.7364 | 393985 | 6610 | 387375 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
523 | 340-378F | 8.3752 | 393785 | 388139 | 5646 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
524 | 243-20R | 10.387 | 388804 | 281395 | 107409 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
525 | 973-530AE | 0.03428 | 388006 | 25128 | 362878 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
526 | CB 980 | 1.8653 | 387849 | 386670 | 1179 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
527 | CB 562 | 1.5066 | 385060 | 384067 | 993 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
528 | CB 247 | 3.5733 | 379742 | 266881 | 112861 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
529 | CB 188 | 10.3012 | 378367 | 371687 | 6680 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
530 | 334-21 | 7.2951 | 378214 | 336942 | 41272 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
531 | 240-1148 | 3.4333 | 376720 | 364957 | 11763 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
532 | 239-89R | 2.8193 | 376425 | 371745 | 4680 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
533 | 341-1155F | 4.5127 | 374361 | 371520 | 2841 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
534 | 205-369R | 15.9271 | 370183 | 359719 | 10463 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
535 | 242-1413F | 1.8794 | 367354 | 30385 | 336969 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
536 | 280-24AE | 2.1642 | 365789 | 11503 | 354285 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
537 | CB 195 | 2.8899 | 363250 | 215997 | 147252 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
538 | CB 303 | 12.3992 | 349915 | 65449 | 284466 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
539 | CB FB1 | 7.7129 | 346587 | 127990 | 218597 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
540 | 732-15R | 5.2317 | 342637 | 338981 | 3656 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
541 | 576-205F | 0 | 339549 | $- | 339549 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
542 | CB 91 | 2.7814 | 337735 | 315531 | 22204 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
543 | 1139-5 | 0.75514 | 335857 | 1245 | 334612 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
544 | CB 974 | 0.11723 | 334304 | 334087 | 217 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
545 | CB 546 | 7.344 | 334161 | 19682 | 314478 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
546 | 444-15R | 8.351 | 333846 | 322554 | 11293 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
547 | 970-4AE | 0 | 331307 | $- | 331307 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
548 | 840-308F | 1.0854 | 330349 | 328335 | 2014 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
549 | 221-1249R | 25.1976 | 329372 | 200694 | 128678 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
550 | 68-42 | 1.3063 | 327449 | 265995 | 61454 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
551 | 79-1215F | 0.2301 | 324126 | 322778 | 1348 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
552 | 401-39R | 0.64865 | 323232 | 10321 | 312911 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
553 | 390-18 | 3.9404 | 318845 | 52868 | 265977 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
554 | 221-38AE | 0.70208 | 318097 | 106237 | 211860 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
555 | 210-9R | 2.7176 | 317772 | 161505 | 156267 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
556 | 183-439 | 1.1486 | 316478 | 209604 | 106873 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
557 | 394-422F | 1.6971 | 314151 | 1037 | 313114 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
558 | CB 280 | 4.0675 | 310797 | 50007 | 260790 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
559 | CB 973 | 0.12822 | 310401 | 310189 | 213 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
560 | 206-963F | 4.5674 | 308008 | 304622 | 3386 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
561 | CB 523 | 6.3104 | 305569 | 113664 | 191905 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
562 | 523-31AE | 4.4118 | 305199 | 35698 | 269502 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
563 | 350-2182R | 0.41228 | 302428 | 300219 | 2209 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
564 | 93-10R | 9.5466 | 302332 | 274241 | 28091 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
565 | 1101-593F | 0 | 299798 | $- | 299798 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
566 | 450-1850 | 0.60374 | 296714 | 288153 | 8561 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
567 | CB 244 | 5.2595 | 295551 | 110842 | 184709 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
568 | 972-1641 | 0 | 295084 | $- | 295084 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
569 | 181-53F | 1.2419 | 294623 | 49953 | 244670 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
570 | 245-486 | 4.3474 | 294231 | 105012 | 189219 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
571 | 454-49F | 1.5199 | 292974 | 222826 | 70149 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
572 | 590-6 | 0 | 292116 | $- | 292116 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
573 | 542-45F | 0 | 292050 | $- | 292050 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
574 | 276-228 | 17.7437 | 290991 | 33915 | 257077 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
575 | 241-746 | 0.38732 | 290982 | 28895 | 262087 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
576 | 222-1992R | 0.78597 | 288771 | 249949 | 38821 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
577 | 1085-109F | 0 | 288289 | $- | 288289 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
578 | 241-820AE | 3.04 | 286770 | 42737 | 244033 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
579 | 558-301R | 2.4663 | 286655 | 284794 | 1861 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
580 | 278-22R | 15.5778 | 285167 | 15714 | 269453 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
581 | 310-1192F | 9.1648 | 284942 | 5320 | 279622 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
582 | CB 243 | 3.2755 | 284281 | 261821 | 22460 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
583 | 1039-14AE | 0 | 282520 | $- | 282520 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
584 | 311-14R | 0.75338 | 278652 | 45364 | 233288 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
585 | CB CG1 | 8.3125 | 278521 | 262149 | 16372 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
586 | 278-630 | 10.8269 | 273714 | 15642 | 258072 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
587 | CB 596 | 1.4705 | 273330 | 272281 | 1049 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
588 | 454-53F | 0.73506 | 272540 | 1990 | 270550 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
589 | 492-343R | 3.0856 | 272427 | 101317 | 171110 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
590 | CB 855 | 3.5599 | 270562 | 268851 | 1711 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
591 | 189-782F | 2.3879 | 270400 | 176794 | 93606 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
592 | CB 386 | 7.9203 | 266448 | 156901 | 109548 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
593 | CB 116 | 7.0256 | 265470 | 125282 | 140188 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
594 | CB SC2 | 7.0339 | 261452 | 5773 | 255678 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
595 | 212-743R | 3.6616 | 261428 | 253730 | 7698 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
596 | 452-39AE | 1.292 | 261242 | 260228 | 1015 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
597 | CB 331 | 2.8949 | 261210 | 259592 | 1618 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
598 | 390-15 | 1.561 | 260996 | 1650 | 259347 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
599 | CB 1525 | 6.2326 | 259690 | 92171 | 167520 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
600 | 520-22R | 3.0796 | 258296 | 193007 | 65289 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
601 | 907-1602 | 0.10398 | 257242 | 253809 | 3433 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
602 | 928-37F | 0 | 256938 | $- | 256938 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
603 | 63-35AE | 1.9439 | 256468 | 195479 | 60989 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
604 | CB 314 | 1.0947 | 255580 | 135298 | 120281 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
605 | 797-32F | 0 | 255490 | $- | 255490 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
606 | CB 920 | 0.96496 | 251904 | 251342 | 562 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
607 | CB 103 | 10.3631 | 251308 | 10163 | 241145 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
608 | CB 970 | 0.092045 | 251007 | 250922 | 85 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
609 | CB 245 | 7.1536 | 248325 | 75145 | 173180 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
610 | 1162-363 | 1.6328 | 247999 | 242411 | 5588 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
611 | CB 57 | 7.9972 | 246572 | 33082 | 213491 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
612 | CB SC1 | 7.9705 | 245131 | 4372 | 240758 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
613 | 510-49R | 2.222 | 240587 | 66688 | 173900 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
614 | 1162-324R | 3.3255 | 240290 | 211906 | 28384 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
615 | 595-500 | 2.1604 | 238236 | 71013 | 167224 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
616 | CB 1081 | 9.8183 | 237950 | 71179 | 166771 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
617 | 274-23R | 14.1254 | 237928 | 11199 | 226730 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
618 | CB CG2 | 8.5261 | 237574 | 219947 | 17626 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
619 | 221-1235F | 0.0489 | 236177 | $- | 236177 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
620 | 394-419 | 0 | 235784 | $- | 235784 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
621 | 330-810R | 2.7411 | 235356 | 11155 | 224201 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
622 | 840-374 | 1.3115 | 232556 | 224795 | 7761 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
623 | 277-48 | 10.0475 | 230022 | 13477 | 216545 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
624 | 795-816R | 6.4011 | 228765 | 10881 | 217885 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
625 | 546-14R | 3.7622 | 227213 | 3294 | 223919 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
626 | 578-227AE | 7.3342 | 226195 | 7249 | 218946 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
627 | 901-1124 | 2.1134 | 225481 | 223883 | 1599 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
628 | CB 414 | 16.8574 | 223669 | 89730 | 133939 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
629 | CB 597 | 1.0557 | 218049 | 217312 | 736 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
630 | 331-40AE | 0 | 217394 | $- | 217394 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
631 | 330-8R | 9.8311 | 217251 | 25140 | 192110 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
632 | 492-14R | 10.8722 | 216578 | 7046 | 209532 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
633 | CB 329 | 2.4417 | 215285 | 208457 | 6828 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
634 | 542-43F | 0 | 213616 | $- | 213616 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
635 | CB 732 | 16.7686 | 213157 | 202440 | 10718 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
636 | 1081-38AE | 1.1752 | 213068 | 166263 | 46805 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
637 | CB 230 | 0.62576 | 212827 | 212430 | 397 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
638 | 182-2243F | 0 | 211321 | $- | 211321 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
639 | 315-485AE | 1.6445 | 209856 | 208811 | 1045 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
640 | CB 286 | 12.3718 | 207241 | 136058 | 71183 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
641 | CB 275 | 3.0089 | 206623 | 94737 | 111887 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
642 | 1162-329R | 3.4321 | 206588 | 199607 | 6981 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
643 | 501-786 | 1.0739 | 204084 | 203332 | 751 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
644 | 92-619F | 3.3373 | 202869 | 95112 | 107757 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
645 | 312-14F | 0.8655 | 202124 | 306 | 201818 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
646 | 703-279R | 8.8328 | 201974 | 67109 | 134865 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
647 | 279-11AE | 13.9777 | 201506 | 6211 | 195295 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
648 | 972-1644 | 0 | 200447 | $- | 200447 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
649 | CB 63 | 2.7163 | 198805 | 71918 | 126887 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
650 | 277-459F | 9.8924 | 196345 | 15554 | 180791 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
651 | CB 203 | 6.2051 | 195752 | 18760 | 176992 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
652 | 230-371AE | 1.4237 | 195725 | 159935 | 35791 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
653 | 93-559R | 6.9136 | 194930 | 174931 | 19998 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
654 | CB 704 | 1.7828 | 194569 | 66328 | 128240 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
655 | 1072-6 | 0.23504 | 193612 | 715 | 192897 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
656 | CB 911 | 0.9375 | 193603 | 193113 | 490 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
657 | CB 701 | 17.7385 | 193602 | 88709 | 104893 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
658 | 971-381R | 0.075568 | 191895 | 191775 | 121 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
659 | 94-41 | 13.5683 | 189671 | 183389 | 6283 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
660 | CB 65 | 6.2999 | 189266 | 117454 | 71811 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
661 | 855-46AE | 0.25303 | 188553 | 188332 | 221 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
662 | 276-158R | 15.2584 | 188059 | 8834 | 179225 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
663 | CB MA1 | 11.2421 | 187689 | 5888 | 181800 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
664 | 308-464 | 3.726 | 187215 | 9916 | 177298 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
665 | 86-552F | 20.0174 | 186636 | 173008 | 13628 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
666 | CB GM2 | 12.8498 | 185867 | 177938 | 7928 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
667 | 972-1642 | 0.038636 | 185301 | $- | 185301 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
668 | CB 61 | 8.4142 | 184260 | 32427 | 151833 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
669 | 197-1150F | 1.3604 | 183538 | 182319 | 1219 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
670 | CB 1007 | 0.54489 | 183252 | 182883 | 369 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
671 | 452-1405 | 0.38935 | 181217 | 180926 | 292 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
672 | CB 514 | 20.4863 | 180275 | 165899 | 14376 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
673 | 242-1419F | 0 | 179230 | $- | 179230 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
674 | 794-1002 | 1.1659 | 176664 | 10327 | 166337 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
675 | CB 799 | 1.1328 | 176617 | 175677 | 940 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
676 | 1081-11 | 7.6814 | 174685 | 32406 | 142280 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
677 | 172-569R | 17.4465 | 174581 | 122594 | 51987 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
678 | 362-47F | 14.5108 | 174273 | 63604 | 110668 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
679 | CB BN1 | 10.2073 | 173803 | 167495 | 6308 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
680 | 230-1008R | 0.76383 | 171588 | 170503 | 1086 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
681 | 364-36 | 7.918 | 171187 | 3466 | 167721 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
682 | 303-189AE | 8.0475 | 171003 | 5809 | 165194 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
683 | 210-394R | 3.6236 | 170593 | 120221 | 50372 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
684 | 1081-666F | 5.8293 | 169875 | 136342 | 33532 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
685 | 60-603F | 6.0002 | 169513 | 15339 | 154175 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
686 | 417-21R | 10.3053 | 169298 | 63109 | 106189 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
687 | 1458-456F | 0.14415 | 167569 | 49948 | 117621 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
688 | 279-10AE | 13.1186 | 166571 | 9847 | 156725 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
689 | CB 1073 | 6.1307 | 166060 | 10151 | 155910 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
690 | 203-21R | 2.1493 | 165994 | 7751 | 158242 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
691 | 933-472F | 2.0138 | 165868 | 164254 | 1614 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
692 | CB 927 | 0.68868 | 165399 | 164835 | 564 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
693 | 308-486AE | 3.6318 | 164678 | 3925 | 160753 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
694 | CB 511 | 2.4116 | 163941 | 157304 | 6637 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
695 | 341-920 | 12.9709 | 161886 | 154106 | 7780 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
696 | 311-43 | 4.1521 | 159858 | 3739 | 156119 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
697 | 1243-38R | 0.34621 | 158251 | 157423 | 828 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
698 | 308-485AE | 1.6722 | 157977 | 4384 | 153594 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
699 | 1215-10R | 0.56254 | 157888 | 123933 | 33955 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
700 | 275-45 | 1.1627 | 157581 | 672 | 156909 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
701 | 1458-1057F | 0 | 155999 | $- | 155999 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
702 | CB 781 | 3.2938 | 155425 | 39056 | 116369 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
703 | CB 365 | 10.8739 | 153829 | 25899 | 127930 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
704 | 583-318F | 2.2297 | 153561 | 152694 | 867 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
705 | 973-533AE | 0 | 153489 | $- | 153489 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
706 | 908-2062F | 0.11194 | 153311 | 151129 | 2182 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
707 | CB 282 | 1.0646 | 152507 | 7242 | 145265 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
708 | 1140-13F | 0 | 150625 | $- | 150625 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
709 | CB MV1 | 5.3483 | 150338 | 147015 | 3323 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
710 | 545-874R | 3.5507 | 149861 | 8965 | 140896 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
711 | 62-22AE | 8.7206 | 149851 | 18549 | 131301 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
712 | CB AD1 | 9.4 | 147894 | 14484 | 133410 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
713 | CB 492 | 2.6833 | 147697 | 74150 | 73548 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
714 | CB 750 | 1.0979 | 147170 | 146696 | 474 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
715 | 973-534AE | 0 | 146186 | $- | 146186 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
716 | CB 143 | 3.3491 | 145604 | 79518 | 66086 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
717 | 171-708R | 12.6172 | 144381 | 92868 | 51513 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
718 | 331-42AE | 0 | 143891 | $- | 143891 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
719 | 386-25R | 2.3127 | 143657 | 50797 | 92860 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
720 | 542-44F | 0 | 143031 | $- | 143031 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
721 | 579-350F | 0.61875 | 142767 | 3184 | 139583 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
722 | 172-567R | 10.6971 | 141922 | 88263 | 53659 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
723 | 116-31F | 2.0027 | 141477 | 525 | 140953 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
724 | 442-780 | 1.4734 | 141385 | 72107 | 69277 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
725 | 1090-70F | 0.64526 | 140837 | 123964 | 16873 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
726 | CB 578 | 4.9491 | 140492 | 16927 | 123565 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
727 | 835-11F | 1.0576 | 139955 | 139435 | 520 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
728 | 286-989AE | 10.8825 | 139872 | 5630 | 134241 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
729 | 415-33 | 9.518 | 139779 | 28191 | 111587 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
730 | CB 288 | 9.475 | 139689 | 70804 | 68885 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
731 | 1458-1117F | 0 | 139463 | $- | 139463 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
732 | 364-49R | 10.7492 | 138167 | 19819 | 118347 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
733 | 390-346AE | 1.9503 | 137769 | 42121 | 95649 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
734 | CB PB1 | 6.9699 | 137604 | 4517 | 133087 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
735 | 452-1403 | 0.20947 | 137227 | 137083 | 144 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
736 | 545-50F | 3.0186 | 135826 | 1446 | 134380 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
737 | CB 857 | 2.4864 | 134821 | 132842 | 1978 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
738 | 170-3R | 7.9656 | 134608 | 96026 | 38581 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
739 | CB 196 | 0.59317 | 134470 | 4225 | 130245 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
740 | CB 202 | 11.6007 | 133986 | 127451 | 6535 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
741 | 292-317F | 0 | 133936 | $- | 133936 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
742 | CB 215 | 0.14848 | 133913 | 133772 | 141 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
743 | CB 350 | 0.13314 | 133574 | 133469 | 104 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
744 | 415-1237R | 9.2329 | 133096 | 16823 | 116273 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
745 | CB 981 | 0.87121 | 132757 | 132287 | 470 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
746 | 780-468R | 1.3398 | 132176 | 2845 | 129331 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
747 | 368-24 | 6.8786 | 131820 | 7181 | 124639 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
748 | 306-2246 | 0 | 131581 | $- | 131581 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
749 | CB 281 | 6.8986 | 131323 | 1504 | 129819 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
750 | 274-40 | 7.8386 | 130226 | 3450 | 126777 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
751 | 1140-11F | 0 | 129277 | $- | 129277 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
752 | CB 783 | 1.3273 | 129217 | 53785 | 75432 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
753 | CB 183 | 2.7093 | 128802 | 29182 | 99620 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
754 | CB SHC1 | 0 | 128745 | $- | 128745 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
755 | 535-10F | 0 | 128195 | $- | 128195 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
756 | 799-504R | 1.3381 | 127406 | 126494 | 912 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
757 | 702-27R | 12.2498 | 127298 | 18550 | 108749 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
758 | CB 284 | 2.2045 | 126881 | 60798 | 66083 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
759 | CB 415 | 5.4938 | 126421 | 34896 | 91525 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
760 | 505-1676F | 5.4025 | 126311 | 122916 | 3394 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
761 | CB 68 | 1.521 | 125603 | 122631 | 2972 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
762 | 545-43AE | 0 | 125182 | $- | 125182 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
763 | 595-1454F | 1.3606 | 124925 | 104030 | 20895 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
764 | 310-719F | 3.2121 | 124515 | 2818 | 121697 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
765 | CB 330 | 3.7435 | 124250 | 41442 | 82808 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
766 | 205-1550 | 2.7852 | 124006 | 122174 | 1833 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
767 | 390-16F | 0 | 123139 | $- | 123139 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
768 | CB HW1 | 1.0525 | 122438 | 121648 | 790 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
769 | 783-1451F | 0 | 122428 | $- | 122428 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
770 | CB 789 | 2.8581 | 122362 | 120731 | 1631 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
771 | CB 56 | 3.7124 | 122212 | 11814 | 110398 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
772 | 275-48F | 3.4754 | 122148 | 7054 | 115094 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
773 | 306-2258F | 0 | 122044 | $- | 122044 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
774 | CB 1085 | 0.4608 | 121815 | 35728 | 86087 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
775 | 308-484AE | 4.8747 | 121719 | 10534 | 111185 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
776 | 230-2067 | 0.1678 | 121607 | 113066 | 8541 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
777 | CB FM3 | 9.8417 | 121112 | 82076 | 39036 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
778 | CB EO3 | 14.1508 | 120883 | 111840 | 9043 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
779 | 492-1091F | 5.9958 | 120640 | 3519 | 117121 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
780 | 928-6F | 0 | 120509 | $- | 120509 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
781 | 797-30F | 0 | 119863 | $- | 119863 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
782 | CB 77 | 15.8875 | 119749 | 107941 | 11809 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
783 | CB BRM1 | 7.8361 | 119568 | 5473 | 114095 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
784 | 142-33 | 9.6922 | 118712 | 24353 | 94360 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
785 | 209-661 | 1.3877 | 118711 | 117657 | 1054 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
786 | 277-456F | 0 | 118447 | $- | 118447 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
787 | 280-382AE | 4.587 | 117950 | 11406 | 106544 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
788 | CB 93 | 6.2065 | 117852 | 58642 | 59210 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
789 | CB 444 | 0.43141 | 117443 | 114721 | 2722 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
790 | 1079-9 | 8.0419 | 117302 | 111427 | 5876 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
791 | 1001-1231F | 0.094697 | 117157 | 116026 | 1131 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
792 | 522-36 | 2.2803 | 116958 | 26355 | 90603 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
793 | 57-736 | 1.4816 | 116892 | 572 | 116320 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
794 | 314-43F | 0 | 116601 | $- | 116601 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
795 | CB 417 | 4.8645 | 116540 | 48438 | 68102 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
796 | CB 144 | 4.3479 | 116349 | 82257 | 34092 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
797 | CB 497 | 3.432 | 116265 | 114208 | 2058 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
798 | CB 589 | 1.6411 | 115513 | 114581 | 932 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
799 | CB 287 | 2.9707 | 114668 | 82479 | 32188 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
800 | 1006-829F | 0.47178 | 114530 | 114256 | 274 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
801 | CB 171 | 2.7693 | 113919 | 38509 | 75411 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
802 | 61-21F | 1.9962 | 113445 | 7576 | 105869 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
803 | 522-34 | 1.8014 | 112712 | 48494 | 64218 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
804 | 64-14F | 8.9328 | 111705 | 5085 | 106620 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
805 | 58-754F | 2.4574 | 111561 | 12109 | 99452 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
806 | CB 535 | 0.31174 | 111498 | 5113 | 106386 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
807 | 701-48AE | 3.0439 | 111353 | 1684 | 109669 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
808 | 545-47F | 2.6369 | 110979 | 1509 | 109470 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
809 | 391-437 | 0 | 110969 | $- | 110969 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
810 | CB 368 | 3.9384 | 110284 | 14619 | 95665 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
811 | CB 192 | 4.2902 | 109582 | 106716 | 2866 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
812 | CB 142 | 10.8841 | 108633 | 61940 | 46693 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
813 | CB 1245 | 0.4697 | 108100 | 107830 | 270 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
814 | 56-669F | 0.57918 | 107608 | 107 | 107500 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
815 | 69-45F | 0.32272 | 106781 | 2878 | 103903 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
816 | 314-44F | 0 | 106470 | $- | 106470 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
817 | 303-487AE | 1.8256 | 106350 | 5298 | 101052 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
818 | 936-188 | 1.8436 | 105840 | 104307 | 1533 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
819 | 702-25 | 0.91362 | 105790 | 17944 | 87846 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
820 | CB 64 | 3.6049 | 105416 | 33786 | 71630 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
821 | 247-48 | 0.44811 | 105203 | 103291 | 1912 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
822 | CB LR1 | 12.453 | 104991 | 96719 | 8272 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
823 | 212-880R | 1.6392 | 104944 | 102617 | 2327 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
824 | CB 274 | 0.089394 | 104809 | 293 | 104516 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
825 | 792-46 | 5.8164 | 104788 | 29197 | 75591 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
826 | 548-17F | 2.5892 | 104212 | 102231 | 1981 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
827 | 511-1337 | 0 | 103151 | $- | 103151 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
828 | 365-34R | 4.1672 | 103074 | 4918 | 98156 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
829 | 731-49F | 16.5002 | 102830 | 92258 | 10572 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
830 | CB 851 | 0.77311 | 102552 | 101982 | 570 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
831 | 1007-10F | 0 | 102018 | $- | 102018 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
832 | CB 461 | 2.4203 | 101871 | 100499 | 1372 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
833 | 1117-1121F | 0.2763 | 101566 | 18451 | 83115 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
834 | 90-44AE | 3.5829 | 101370 | 11902 | 89469 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
835 | 578-242F | 2.7303 | 101249 | 1132 | 100118 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
836 | 165-621F | 12.0826 | 101147 | 92717 | 8430 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
837 | 702-30 | 8.6788 | 100370 | 67726 | 32645 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
838 | CB 463 | 1.5028 | 99973 | 99155 | 818 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
839 | CB 364 | 4.5699 | 99513 | 18330 | 81183 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
840 | 1073-480 | 0.27083 | 99119 | 2764 | 96355 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
841 | 991-384AE | 0 | 98033 | $- | 98033 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
842 | 795-725AE | 0 | 97546 | $- | 97546 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
843 | 1140-8F | 1.0602 | 97447 | 538 | 96909 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
844 | 1297-34F | 2.0714 | 97117 | 3563 | 93554 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
845 | 783-848F | 0 | 97082 | $- | 97082 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
846 | 443-218R | 2.5293 | 96981 | 93015 | 3966 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
847 | 196-38F | 0 | 96900 | $- | 96900 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
848 | 417-791AE | 1.9314 | 96252 | 1747 | 94505 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
849 | 308-563AE | 0.99238 | 95526 | 18508 | 77019 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
850 | 1094-7 | 1.7031 | 95330 | 94153 | 1177 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
851 | CB 292 | 0.81042 | 94669 | 62928 | 31740 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
852 | 192-657AE | 1.8044 | 94561 | 93546 | 1015 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
853 | 1103-13AE | 0.27027 | 94466 | 94245 | 221 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
854 | 65-38AE | 0 | 94199 | $- | 94199 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
855 | CB SSC1 | 5.0489 | 94186 | 1887 | 92299 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
856 | 1085-8F | 0 | 93882 | $- | 93882 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
857 | 196-43F | 0.2589 | 93765 | 4819 | 88946 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
858 | 58-110F | 6.2108 | 93515 | 10853 | 82662 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
859 | CB 363 | 3.2214 | 93314 | 5438 | 87876 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
860 | CB DM2 | 4.8831 | 93216 | 52686 | 40529 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
861 | 513-42F | 0.8341 | 92914 | 5115 | 87799 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
862 | CB 366 | 3.4801 | 92421 | 13650 | 78771 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
863 | CB 186 | 4.111 | 92389 | 89279 | 3110 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
864 | 299-814AE | 2.8968 | 92055 | 90046 | 2010 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
865 | 511-1338AE | 0 | 92003 | $- | 92003 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
866 | 361-686F | 4.0396 | 90674 | 3251 | 87423 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
867 | 452-37AE | 0.40967 | 90621 | 90314 | 307 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
868 | CB 362 | 4.5676 | 90594 | 18985 | 71610 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
869 | CB GN1 | 4.8692 | 90346 | 3992 | 86354 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
870 | 65-1086 | 0 | 90216 | $- | 90216 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
871 | CB 279 | 4.4104 | 90028 | 17657 | 72371 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
872 | 282-565F | 0.85098 | 89978 | 374 | 89604 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
873 | 1160-1 | 0 | 89915 | $- | 89915 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
874 | 242-1420F | 1.2443 | 89560 | 11212 | 78348 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
875 | CB 1039 | 0.84625 | 89254 | 59286 | 29968 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
876 | 314-814F | 0 | 89230 | $- | 89230 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
877 | 242-776F | 0.6741 | 89087 | 10166 | 78921 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
878 | 510-798 | 0 | 89061 | $- | 89061 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
879 | CB 902 | 7.7576 | 88958 | 83737 | 5221 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
880 | 114-48 | 6.0661 | 88861 | 3625 | 85235 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
881 | CB 62 | 1.8229 | 88591 | 15820 | 72771 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
882 | 144-442F | 3.5848 | 88451 | 1480 | 86971 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
883 | 442-46R | 0.055682 | 88141 | 1538 | 86603 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
884 | 463-1136F | 0.58561 | 88015 | 85684 | 2331 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
885 | CB 352 | 0.125 | 87874 | 87191 | 683 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
886 | 116-32F | 0 | 87669 | $- | 87669 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
887 | 794-15 | 4.1462 | 86375 | 6073 | 80302 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
888 | CB 199 | 5.8392 | 86249 | 82182 | 4067 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
889 | 168-702F | 4.9932 | 86050 | 82715 | 3334 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
890 | 990-713 | 0.065909 | 85922 | 389 | 85534 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
891 | CB VDN1 | 6.0672 | 85523 | 3716 | 81806 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
892 | 366-48 | 2.5229 | 85178 | 1535 | 83643 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
893 | 1458-454F | 0 | 84091 | $- | 84091 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
894 | CB AD3 | 5.5978 | 83374 | 8632 | 74742 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
895 | 68-1356AE | 0 | 83350 | $- | 83350 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
896 | 512-300F | 0 | 82639 | $- | 82639 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
897 | 171-34 | 4.3813 | 81203 | 36273 | 44930 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
898 | 783-854F | 0 | 81195 | $- | 81195 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
899 | 1458-519 | 0.057008 | 81004 | 80966 | 38 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
900 | 368-1054F | 0.47745 | 80991 | 159 | 80832 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
901 | 57-463AE | 5.4167 | 80983 | 2569 | 78414 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
902 | 171-704R | 4.9861 | 80614 | 49461 | 31154 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
903 | CB 780 | 4.5818 | 78995 | 20638 | 58358 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
904 | 197-969F | 0 | 78761 | $- | 78761 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
905 | 445-1323 | 0.19716 | 78544 | 77964 | 580 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
906 | CB 308 | 2.3447 | 77795 | 14284 | 63510 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
907 | 59-465 | 7.5326 | 77379 | 49898 | 27481 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
908 | 1458-1062F | 0 | 76809 | $- | 76809 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
909 | 535-11F | 0 | 76628 | $- | 76628 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
910 | 140-481R | 5.1055 | 76552 | 17010 | 59542 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
911 | 286-1053R | 9.9807 | 76516 | 14919 | 61597 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
912 | 90-32 | 3.1322 | 76419 | 4659 | 71760 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
913 | 223-526R | 2.4396 | 76101 | 74312 | 1789 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
914 | 140-496 | 2.3094 | 76076 | 7769 | 68307 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
915 | CB 1162 | 1.5907 | 75201 | 72679 | 2522 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
916 | 361-45R | 2.965 | 74923 | 3550 | 71372 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
917 | CB 140 | 3.3106 | 74831 | 12781 | 62050 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
918 | 314-13F | 0.47273 | 74541 | 56748 | 17793 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
919 | 146-566 | 0 | 73831 | $- | 73831 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
920 | 1202-9 | 3.468 | 73442 | 71121 | 2321 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
921 | CB 512 | 0.53466 | 72992 | 7274 | 65718 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
922 | CB 120 | 0.83351 | 72890 | 34144 | 38746 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
923 | 58-737F | 0 | 72400 | $- | 72400 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
924 | 991-383 | 0 | 72257 | $- | 72257 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
925 | CB 525 | 0.53731 | 72157 | 12714 | 59443 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
926 | CB 361 | 1.65 | 72053 | 2633 | 69420 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
927 | 791-424F | 0 | 71897 | $- | 71897 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
928 | 512-50AE | 2.2912 | 71824 | 544 | 71281 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
929 | CB 270 | 2.0546 | 71459 | 11377 | 60082 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
930 | 216-220R | 0.052462 | 71282 | 71210 | 71 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
931 | CB 545 | 1.9879 | 70980 | 14178 | 56802 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
932 | CB EOS1 | 17.8417 | 70924 | 58759 | 12165 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
933 | CB EN1 | 9.5242 | 70862 | 11651 | 59211 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
934 | CB 1166 | 0.085985 | 70820 | 70676 | 144 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
935 | 171-567 | 4.0096 | 70655 | 40359 | 30297 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
936 | 1201-282F | 1.7013 | 70653 | 69709 | 944 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
937 | 434-301 | 0.75759 | 70650 | 70320 | 329 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
938 | CB 334 | 5.1123 | 70516 | 67049 | 3467 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
939 | 834-887AE | 1.3721 | 70347 | 69393 | 954 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
940 | CB 94 | 3.3957 | 70260 | 67745 | 2515 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
941 | CB 40 | 7.115 | 69517 | 64814 | 4703 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
942 | 417-44AE | 0.70607 | 68544 | 75 | 68469 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
943 | 783-847F | 0 | 68084 | $- | 68084 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
944 | 284-660R | 0.21894 | 67711 | 25335 | 42376 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
945 | CB 475 | 2.5995 | 67585 | 65692 | 1893 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
946 | 1073-888F | 0 | 67344 | $- | 67344 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
947 | 768-20AE | 0.6589 | 67305 | 66911 | 394 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
948 | CB 540 | 0.93788 | 67245 | 66736 | 509 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
949 | CB 443 | 1.7657 | 67147 | 65999 | 1148 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
950 | 61-13F | 1.5653 | 66914 | 736 | 66177 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
951 | 287-27AE | 0 | 66801 | $- | 66801 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
952 | 114-18AE | 4.008 | 66683 | 3125 | 63559 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
953 | 1458-1115F | 0 | 66507 | $- | 66507 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
954 | 172-630R | 4.8346 | 66311 | 4323 | 61988 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
955 | CB 472 | 6.9083 | 66092 | 61406 | 4686 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
956 | CB PB5 | 5.8622 | 65931 | 3849 | 62081 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
957 | CB TR1 | 0.82749 | 65581 | 65009 | 572 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
958 | CB 380 | 6.7373 | 65141 | 60862 | 4279 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
959 | 172-615R | 6.2257 | 65021 | 20405 | 44616 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
960 | CB 797 | 0.92273 | 65019 | 64271 | 748 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
961 | 329-215F | 1.3032 | 64925 | 1159 | 63766 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
962 | 181-49 | 0.13883 | 64766 | 5260 | 59507 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
963 | CB 289 | 4.3732 | 64739 | 25424 | 39315 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
964 | 708-47 | 0 | 64504 | $- | 64504 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
965 | 68-27 | 1.0051 | 64464 | 61937 | 2527 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
966 | CB 715 | 2.2625 | 64215 | 62669 | 1546 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
967 | CB 702 | 1.5752 | 63754 | 63026 | 728 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
968 | 520-1936 | 0.1358 | 63711 | 63566 | 145 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
969 | 170-46 | 14.4293 | 63311 | 25126 | 38185 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
970 | 197-1157F | 0.44794 | 63166 | 824 | 62341 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
971 | 313-550AE | 1.3333 | 63029 | 22186 | 40843 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
972 | 909-812 | 0.023485 | 62984 | 62909 | 75 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
973 | 968-476F | 2.5405 | 62492 | 60559 | 1933 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
974 | 68-775 | 0 | 61202 | $- | 61202 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
975 | 289-906AE | 3.7338 | 60632 | 3654 | 56978 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
976 | CB 558 | 1.6337 | 60272 | 59574 | 698 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
977 | 95-29R | 9.681 | 60126 | 15047 | 45080 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
978 | 793-27AE | 0.72117 | 59591 | 5424 | 54166 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
979 | 358-681F | 0 | 59327 | $- | 59327 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
980 | CB 214 | 0.040909 | 59200 | 59129 | 70 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
981 | CB 460 | 0.95644 | 58917 | 58392 | 525 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
982 | CB 88 | 10.0387 | 58867 | 52619 | 6248 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
983 | 1458-1075F | 0.03428 | 58234 | 58197 | 37 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
984 | CB 564 | 0.65684 | 57572 | 57173 | 399 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
985 | 448-1203F | 0 | 57383 | $- | 57383 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
986 | CB 163 | 19.7841 | 56872 | 50429 | 6443 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
987 | 781-1359 | 1.9734 | 56466 | 361 | 56105 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
988 | CB 147 | 0.60265 | 56226 | 7470 | 48755 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
989 | 35-2 | 0.48065 | 55557 | 3369 | 52188 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
990 | 730-835 | 4.7612 | 55260 | 52123 | 3137 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
991 | CB 776 | 2.6153 | 55068 | 51026 | 4042 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
992 | 299-1011 | 4.203 | 54999 | 51754 | 3245 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
993 | 1100-1168F | 0.18447 | 54719 | 54035 | 684 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
994 | 116-12R | 3.2824 | 54555 | 3025 | 51530 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
995 | CB 59 | 0.80076 | 54425 | 53924 | 502 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
996 | SEA1-384F | 6.4007 | 54325 | 10781 | 43544 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
997 | CB AG1 | 2.6702 | 54269 | 1229 | 53040 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
998 | 57-1296F | 4.3852 | 54256 | 44708 | 9548 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
999 | CB 456 | 6.0005 | 54234 | 49710 | 4524 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1000 | CB 536 | 1.5002 | 54110 | 41228 | 12882 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1001 | 244-33F | 0.17124 | 53967 | 86 | 53881 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1002 | 546-525R | 3.3962 | 53674 | 3999 | 49675 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1003 | 714-549F | 1.7489 | 53275 | 52245 | 1030 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1004 | 92-618F | 0 | 53106 | $- | 53106 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1005 | 255-43AE | 17.4344 | 53100 | 41289 | 11811 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1006 | CB FM2 | 0.69792 | 52722 | 6903 | 45819 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1007 | CB 184 | 0.49848 | 52487 | 380 | 52107 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1008 | 59-816F | 0 | 52163 | $- | 52163 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1009 | 297-828AE | 1.7713 | 51978 | 50793 | 1184 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1010 | 244-32F | 0.80758 | 51191 | 4231 | 46960 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1011 | 74-35R | 1.7629 | 50930 | 49730 | 1199 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1012 | 368-21AE | 3.2028 | 50816 | 4021 | 46795 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1013 | CB 69 | 1.1767 | 50796 | 46834 | 3962 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1014 | CB 190 | 1.1379 | 50750 | 49708 | 1041 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1015 | CB 153 | 14.7847 | 50616 | 40693 | 9923 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1016 | 1297-35F | 1.8046 | 50401 | 1821 | 48580 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1017 | 146-275R | 0.74015 | 50176 | 15771 | 34406 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1018 | CB 145 | 1.2373 | 50158 | 32328 | 17830 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1019 | 286-990AE | 4.5934 | 50012 | 2668 | 47345 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1020 | CB 579 | 1.4538 | 49662 | 10758 | 38904 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1021 | 795-817AE | 0 | 49517 | $- | 49517 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1022 | 252-129 | 4.6668 | 49485 | 42886 | 6599 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1023 | 594-1379F | 0.51875 | 49429 | 49138 | 291 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1024 | CB 85 | 6.3067 | 49322 | 45427 | 3896 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1025 | 56-670F | 1.1852 | 49225 | 292 | 48933 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1026 | CB 553 | 3.1561 | 49064 | 46441 | 2623 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1027 | 394-418F | 0 | 48475 | $- | 48475 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1028 | 795-821F | 2.1524 | 48074 | 8925 | 39149 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1029 | CB 381 | 0.78239 | 47716 | 46951 | 765 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1030 | CB 531 | 6.3466 | 47684 | 43029 | 4655 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1031 | 178-968AE | 6.2909 | 47611 | 43426 | 4184 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1032 | 222-2108 | 0 | 46877 | $- | 46877 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1033 | CB 410 | 6.5019 | 46542 | 41826 | 4715 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1034 | 94-24F | 7.7121 | 46367 | 42509 | 3858 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1035 | CB 92 | 2.9091 | 46332 | 40566 | 5767 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1036 | 311-1163F | 0.65624 | 46195 | 39124 | 7071 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1037 | 534-1080F | 0 | 45877 | $- | 45877 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1038 | 511-831 | 0.15682 | 45774 | 5129 | 40645 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1039 | 533-7AE | 2.0012 | 45746 | 5187 | 40560 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1040 | CB 949 | 14.4241 | 45641 | 35997 | 9644 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1041 | 781-1356R | 1.2461 | 45624 | 3648 | 41976 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1042 | 287-20 | 0.66515 | 45559 | 2796 | 42763 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1043 | CB OT2 | 3.4801 | 45421 | 1465 | 43956 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure
1044 | CB EN2 | 5.9322 | 45216 | 24242 | 20974 | <0.10% | Conductor failure, Vegetation failure, Other Equipment & Foreign Object failure, Vehicle Contact failure

## OEIS Table 6-2
Stakeholder | Stakeholder Point of Contact | Electrical Corporation Point of Contact | Stakeholder Role | Engagement Methods | Activity | Level of Engagement for Activity
SDG&E Wildfire Council | Executive Leadership | SDG&E VP - Wildfire & Climate Science | Provide executive-level review of and direction regarding wildfire mitigation activities. | Monthly meeting | Report wildfire mitigation progress, evaluate risk mitigations, and discuss wildfire safety culture and strategies to enhance risk reduction | SDG&E executive and employees
SDG&E Board Safety Committee | SDG&E Board Safety Committee Chair | Executive Leadership | Provide oversight regarding safety matters affecting the Company. | Quarterly meeting | Review safety matters impacting SDG&E, lessons learned, and review company safety trends | SDG&E management and employees
Wildfire Safety Community Advisory Council | Executive Leadership | SDG&E Chief Operating Officer | Gather input and feedback from community stakeholders regarding wildfire and PSPS safety matters at the SDG&E executive leadership and Board level. | Quarterly meeting | Discuss wildfire community risks and community needs | Local community leaders, SDG&E Board Safety Committee leadership, SDG&E executive management and employees.
Fire Directors Steering Team | Director members at SDG&E | Director of Wildfire Mitigation | Provide input and review wildfire mitigation and PSPS mitigation initiatives | Monthly meeting | Report wildfire mitigation progress, evaluate risk mitigations, and discuss wildfire safety culture and strategies to reduce risk | Operational directors
Regional Emergency Manager Working Group | Working Group Lead | Emergency Operations Services Manager | The working group provides information on local jurisdictional planning efforts. The electrical corporation provides information on wildfire mitigations within local jurisdictions | Bi-monthly meetings | Provide update on planning, preparedness, and response to all hazards facing the Utility. | Federal, State, Local
County Fire Chiefs | Committee members and leadership | Fire Science and Coordination Program and OFER | Provide an open line of communication between teams. | Monthly meeting | Provide updates on utility hazards training and coordination. | Federal, State, Local
Local, State, and Federal Fire Agencies | Specific to Agencies, typically chief level and above. Can include other ranks within departments depending on the need and complexity of a request. | Fire Science and Coordination and OFER | Internal annual review of standard practice and external review of fire prevention plans, coordinated with the agencies having jurisdiction. All agencies have the ability to call and discuss incidents, plans, and mitigations at any time and input is incorporated as necessary. | 24/7 On Call and various professional relationships | Coordinate, train, and respond with first responders. Coordinate projects and support objectives. | Federal, State, Local
San Diego County Evacuation Planning Committee | Committee members and leadership (members include fire agencies, law enforcement, and emergency operations) | Fire Science and Coordination Program Manager and OFER | Serve as a cooperator during evacuations and repopulation operations and provide utility related expertise. Other agencies provide information based on their area of expertise. | Monthly and Quarterly Meetings | Participate in meetings, provide feedback and execute utility portions of evacuations orders and warnings | Federal, State, Local
San Diego County Training Chiefs | Training Chiefs | Fire Science and Coordination and OFER | Coordinate with and trains local first responders on utility safety and emerging technologies. Sponsor and participate in the planning and execution of an annual county-wide wildland drill, providing subject matter expertise and participants. | Monthly meetings and at training events | Attend meetings and organize, develop, schedule, and execute trainings. | Federal, State, Local
Unified Disaster Council | Director of San Diego County Office of Emergency Services | Director of Emergency Management | County provides information on regional emergency/ disaster mitigation programs. SDG&E provides information on wildfire mitigations within the county. | Bi-monthly meetings | Provide update on planning, preparedness, and response to all hazards facing the Utility. | Federal, State, Local
Southern CA Tribal Emergency Managers Group | Director of San Diego County Office of Emergency Services | Sr. Tribal Affairs Manager | The working group coordinates and shares planning efforts. SDG&E provides information on wildfire mitigation. | Quarterly meetings | Share knowledge on emergency preparedness. | Share resources and on occasion host meetings
Tribal Working Group | Climate Science Alliance | Sr. Tribal Affairs Manager | The working group coordinates and shares planning efforts. SDG&E provides support and information on wildfire mitigation. | Bi-monthly meetings | Share traditional and climate science knowledge. | Share resources and on occasion provide presentations

## OEIS Table 6-3
Initiative Activity | Initiative Activity Section # | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness- Outage Program Riska | Cost-Benefit Score - Overall Risk | Cost-Benefit Score - Wildfire Risk | Cost-Benefit Score – Outage Program Riskb | % HFTD Covered | % HFTD/HFRA Coveredc | Expected % Risk Reduction | Model(s) Used to Calculate Risk Impact
Combined Covered Conductor (WMP.0455) | 8.2.1 | 61.71% | 61.71% | n/ad | 1.8 | 1.8 | n/a | 3.85% | n/a | 0.8% | WiNGS-Planning v4.0
PSPS Sectionalizing Enhancements (WMP.461)e | 8.2.11.1 | n/a | n/a | n/a | n/a | n/a | n/a | 100% | n/a | n/a | WiNGS-Planning v4.0
Microgrids (WMP.462) | 8.2.7 | 100%f | 0% | 100%f | 0 | 0g | 0 | 0.18% | n/a | 100% | WiNGS-Planning v4.0
Advanced Protection (WMP.463) | 8.2.8.1 | 8% | 8% | n/a | 6.71 | 6.71 | n/a | 5.95% | n/a | 0.17% | WiNGS-Planning v4.0
Strategic Undergrounding (WMP.473) | 8.2.2 | 98% | 98% | 98% | 16.49 | 16.49 | n/a | 0.01% | n/a | 4.05% | WiNGS-Planning v4.0
Distribution Overhead System Hardening (WMP.475) | 8.2.5.1 | 39% | 39% | n/a | 2.18 | 2.18 | n/a | 0.36% | n/a | 0.03% | WiNGS-Planning v4.0
Distribution Overhead Detailed Inspections (WMP.478) | 8.3.1 | 29% | 29% | n/a | 52.53 | 52.53 | n/a | 100% | n/a | 10.8% | WiNGS-Planning v4.0
Transmission Overhead Detailed Inspections (WMP.479) | 8.3.2 | 28% | 28% | n/a | n/ai | n/ai | n/ai | 100% | n/a | n/ai | WiNGS-Planning v4.0
Detailed Inspections (WMP.494) | 9.2.1 | 4.95% | 4.95% | n/a | 15.13 | 15.13 | n/a | 100% | n/a | 14.16% | WiNGS-Planning v4.0
Fuels Management (WMP.497) | 9.7 | 4.95% | 4.95% | n/a | 0.6 | 0.6 | n/a | 0.69% | n/a | 0.33% | WiNGS-Planning v4.0
Off-Cycle Patrol (WMP.508) | 9.2.2 | 4.95% | 4.95% | n/a | 48.81 | 48.81 | n/a | 100% | n/a | 13.75% | WiNGS-Planning v4.0
Pole Clearing (Brushing) (WMP.512) | 9.4 | 4.95% | 4.95% | n/a | 15.44 | 15.44 | n/a | 100% | n/a | 13.77% | WiNGS-Planning v4.0
Strategic Pole Remediation (WMP.1189) | 8.2.3.2 | 39% | 39% | n/a | 4.4 | 4.4 | n/a | 0.83% | n/a | 0.13% | WiNGS-Planning v4.0
Early Fault Detection (WMP.1195) | 10.3.1 | 16% | 16% | n/a | 76.35 | 76.35 | n/a | 32.99% | n/a | 1.01% | WiNGS-Planning v4.0
Distribution Overhead Patrol Inspections (WMP.488) | 8.3.7 | 10% | 10% | n/a | 190.89 | 190.89 | n/a | 100% | n/a | 20.74% | WiNGS-Planning v4.0
Distribution Wood Pole Intrusive Inspections (WMP.483) | 8.3.4 | 10% | 10% | n/a | 20.55 | 20.55 | n/a | 23.58% | n/a | 1.93% | WiNGS-Planning v4.0
Risk-Informed Drone Inspections (WMP.552) | 8.3.6 | 29% | 29% | n/a | 54.9 | 54.95 | n/a | 26.97% | n/a | 5.76% | WiNGS-Planning v4.0
[a]SDG&E does not currently calculate mitigation effectiveness for outage program risk except for WMP.462 and WMP.473.
[b]SDG&E's current methodology is designed to calculate the wildfire CBR and is not currently equipped to generate distinct CBR calculations for wildfire and outage program risks.
[c]SDG&E does not use HFRA boundaries.
[d]SDG&E does not directly calculate the effectiveness of PSPS and PEDS outage mitigations. However, the WiNGS-Planning model estimates risk reduction by simulating an increase in the alert wind gust thresholds.
[e]SDG&E does not calculate the CBR and risk reduction for this mitigation. See section 8.2.11.1.4 for details.
[f]Activity Effectiveness is when Microgrid is in operation.
[g]The Microgrid activity is not designed to mitigate wildfire risk directly. Therefore, CBR and effectiveness specific to wildfire risk are zero.
[h]Activity effectiveness percentage is based on subject matter expert assumption.
[i]Transmission programs are funded through FERC allocations and, as such, are not included in the calculation of CBR or risk reduction metrics within the WMP.

## OEIS Table 8-1
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | Target Unit | 2026 Target / Status | % Planned in HFTD for 2026 | % Planned in HFRA for 2026 | % risk reduction for 2026 * | 2027 Target/Status | % Planned in HFTD for 2027 | % Planned in HFRA for 2027 | % risk reduction for 2027 * | 2028 Target/Status | % Planned in HFTD for 2028 | % Planned in HFRA for 2028 | % risk reduction for 2028 * | 3-year total | Section; Page number
Work Orders | Qualitative | Corrective Maintenance Program (CMP) (WMP.1433) - Repair wildfire-related conditions within established timeframes | n/a | n/a | By 12/31/2026, complete repairs within required timeframes | n/a | n/a | n/a | By 12/31/2027, complete repairs within required timeframes | n/a | n/a | n/a | By 12/31/2028, complete repairs within required timeframes | n/a | n/a | n/a | n/a | 8.6; p. 225
Equipment Maintenance and Repair | Qualitative | Transmission Asset Health (WMP.1458) - Analyze asset health for transmission shield wire, insulators, and hardware; explore proactive replacement strategies | n/a | n/a | By 12/31/2026, begin data analysis of asset health, current condition, and outage history of transmission equipment | n/a | n/a | n/a | By 12/31/2027, continue analysis of transmission equipment, and review and adjust replacement strategies | n/a | n/a | n/a | By 12/31/2028, continue analysis of transmission equipment, and review and adjust replacement strategies | n/a | n/a | n/a | n/a | 8.4; p. 205
Grid Ops and Procedures | Qualitative | Personnel Training (WMP.1452)- Examine electric line crew training and incorporate updates annually. | n/a | n/a | By 12/31/2026, update electric line crew training. | n/a | n/a | n/a | By 12/31/2027, update electric line crew training. | n/a | n/a | n/a | By 12/31/2028, update electric line crew training. | n/a | n/a | n/a | n/a | 8.7; p. 231
Workforce Planning | Qualitative | Workforce Planning (Asset Mgmt) - Consult with subject matter experts to update the Storm and PSPS curriculum.(WMP.1453) | n/a | n/a | By 12/31/2026, update Storm and PSPS training with lessons learned. | n/a | n/a | n/a | By 12/31/2027, update Storm and PSPS training with lessons learned. | n/a | n/a | n/a | By 12/31/2028, update Storm and PSPS training with lessons learned. | n/a | n/a | n/a | n/a | 8.8; p. 238
Other grid topology improvements to mitigate or reduce PSPS events | Qualitative | Standby Power Program: (WMP.468) Assess and enable resiliency and backup power solutions for eligible non-residential customers in the high fire threat district. | n/a | n/a | By 12/31/2026, enable backup power solutions of priority sites. | n/a | n/a | n/a | By 12/31/2027, enable backup power solutions of priority sites. | n/a | n/a | n/a | By 12/31/2028, enable backup power solutions of priority sites. | n/a | n/a | n/a | n/a | 8.2.11; p. 173
Other grid topology improvements to mitigate or reduce PSPS events | Qualitative | Customized Resiliency Assessments: (WMP.1432) Assess and enable resiliency and backup power solutions for eligible residential customers in the high fire threat district. | n/a | n/a | By 12/31/2026, offer resiliency support for eligible customers. | n/a | n/a | n/a | By 12/31/2027, offer resiliency support for eligible customers. | n/a | n/a | n/a | By 12/31/2028, offer resiliency support for eligible customers. | n/a | n/a | n/a | n/a | 8.2.11; p. 173
Other grid topology improvements to mitigate or reduce PSPS events | Qualitative | Generator Assistance Program: (WMP.467) Provide rebates on backup power solutions for eligible customers in the high fire threat district. | n/a | n/a | By 12/31/2026, enable rebates for backup power solutions for eligible customers. | n/a | n/a | n/a | By 12/31/2027, enable rebates for backup power solutions for eligible customers. | n/a | n/a | n/a | By 12/31/2028, enable rebates for backup power solutions for eligible customers. | n/a | n/a | n/a | n/a | 8.2.11; p. 173
Grid Design and System Hardening | Quantitative | Combined Covered Conductor (WMP.455) | n/a | Miles | 50 | 100% | n/a | 0.13% | 50 | 100% | n/a | 0.4% | 30 | 100% | n/a | 0.27% | 130 | 8.2.1; p. 160
Grid Design and System Hardening | Quantitative | PSPS Sectionalizing Enhancements (WMP.461) | n/a | Switches | 7 | 100% | n/a | n/a | 6 | 100% | n/a | n/a | 5 | 100% | n/a | n/a | 18 | 8.2.11; p. 173
Grid Design and System Hardening | Quantitative | Microgrids (WMP.462) | n/a | Microgrids | 0 | n/a | n/a | n/a | 0 | n/a | n/a | n/a | 1 | 100% | n/a | 100% | 1 | 8.2.7; p. 169
Grid Design and System Hardening | Quantitative | Advanced Protection (WMP.463) | n/a | Nodes | 30 | 100% | n/a | 0.0421% | 30 | 100% | n/a | 0.0574% | 30 | 100% | n/a | 0.0725% | 90 | 8.2.8.1; p. 170
Grid Design and System Hardening | Quantitative | Strategic Undergrounding (WMP.473) | n/a | Miles | 0 | n/a | n/a | n/a | 0 | n/a | n/a | n/a | 50 | 100% | n/a | 4.05% | 50 | 8.2.2; p. 161
Grid Design and System Hardening | Quantitative | Distribution Overhead System Hardening (WMP.475) | n/a | Miles | 6.53 | 100% | n/a | 0.03% | 0 | n/a | n/a | n/a | 0 | n/a | n/a | n/a | 6.53 | 8.2.5.1; p. 166
Grid Design and System Hardening | Quantitative | Transmission Overhead Hardening (WMP.543) | n/a | Miles | 6.02 | 100% | n/a | n/a | 11.94 | 100% | n/a | n/a | 3 | 100% | n/a | n/a | 20.96 | 8.2.5.2; p. 167
Grid Design and System Hardening | Quantitative | Transmission Overhead Hardening (Distribution Underbuilt) (WMP.545) | n/a | Miles | 1.2 | 100% | n/a | 0.0005% | 7.1 | 100% | n/a | 0.0091% | 3 | 100% | n/a | 0.0027% | 11.3 | 8.2.5.2; p. 167
Grid Design and System Hardening | Quantitative | Strategic Pole Remediation (WMP.1189) | n/a | Poles | 200 | 93% | n/a | 0.04% | 200 | 86% | n/a | 0.05% | 200 | 70% | n/a | 0.04% | 600 | 8.2.10; p. 173
Asset Inspections | Quantitative | Distribution Overhead Detailed Inspections (WMP.478) | n/a | Inspections | 21924 | 100% | n/a | 6.52% | 17779 | 100% | n/a | 2.58% | 11537 | 100% | n/a | 1.7% | 51240 | 8.3.1; p. 182
Asset Inspections | Quantitative | Transmission Overhead Detailed Inspections (WMP.479) | n/a | Inspections | 2447 | 83% | n/a | n/a | 2524 | 81% | n/a | n/a | 2545 | 87% | n/a | n/a | 7516 | 8.3.2; p. 184
Asset Inspections | Quantitative | Transmission Infrared Inspections (WMP.482) | n/a | Inspections | 7294 | 84% | n/a | n/a | 7294 | 84% | n/a | n/a | 7294 | 84% | n/a | n/a | 21882 | 8.3.3; p. 186
Asset Inspections | Quantitative | Distribution Wood Pole Intrusive Inspections (WMP.483) | n/a | Inspections | 1214 | 100% | n/a | 0.05% | 5477 | 100% | n/a | 0.35% | 11923 | 100% | n/a | 1.53% | 18614 | 8.3.4; p. 188
Asset Inspections | Quantitative | Transmission Wood Pole Intrusive Inspections (WMP.1190) | n/a | Inspections | 68 | 100% | n/a | n/a | 196 | 100% | n/a | n/a | 24 | 100% | n/a | n/a | 288 | 8.3.5; p. 190
Asset Inspections | Quantitative | Risk-Informed Drone Inspections (WMP.552) | n/a | Inspections | 9000 | 85% | n/a | 1.49% | 9000 | 96% | n/a | 1.88% | 9000 | 98% | n/a | 2.39% | 27000 | 8.3.6; p. 191
Asset Inspections | Quantitative | Distribution Overhead Patrol Inspections (WMP.488) | n/a | Inspections | 84678 | 100% | n/a | 6.91% | 84678 | 100% | n/a | 6.91% | 84678 | 100% | n/a | 6.91% | 254034 | 8.3.7; p. 195
Asset Inspections | Quantitative | Transmission Overhead Patrol Inspections (WMP.489) | n/a | Inspections | 7454 | 84% | n/a | n/a | 7454 | 84% | n/a | n/a | 7454 | 84% | n/a | n/a | 22362 | 8.3.8; p. 197
Asset Inspections | Quantitative | Substation Patrol Inspections (WMP.492) | n/a | Inspections | 381 | 100% | n/a | n/a | 381 | 100% | n/a | n/a | 381 | 100% | n/a | n/a | 1143 | 8.3.9; p. 199
Asset Inspections | Quantitative | Transmission Switch Inspections (WMP.1509) | n/a | Inspections | 3 | 100% | n/a | n/a | 4 | 100% | n/a | n/a | 4 | 100% | n/a | n/a | 11 | 8.3.10; p. 201
* The expected risk reduction for an activity is dependent on specific projects scoped and is subject to change. (See Section 6.1.3.2.6)

## OEIS Table 8-2
Type | Inspection Activity (Program) | Frequency or Trigger (Note 1) | Method of Inspection (Note 2) | Governing Standards & Operating Procedures | Cumulative Quarterly Target 2026, Q1 | Cumulative Quarterly Target 2026, Q2 | Cumulative Quarterly Target 2026, Q3 | Cumulative Quarterly Target 2026, Q4 | Cumulative Quarterly Target 2027, Q1 | Cumulative Quarterly Target 2027, Q2 | Cumulative Quarterly Target 2027, Q3 | Cumulative Quarterly Target 2027, Q4 | Cumulative Quarterly Target 2028, Q1 | Cumulative Quarterly Target 2028, Q2 | Cumulative Quarterly Target 2028, Q3 | Cumulative Quarterly Target 2028, Q4 | % of HFRA and HFTD Covered Annually by Inspection Type | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Distribution | Distribution Overhead Detailed Inspections (WMP.478) | 5 years | Ground | GO 165, 95 | 5481 | 10962 | 16443 | 21924 | 4444 | 8888 | 13332 | 17779 | 2884 | 5768 | 8652 | 11537 | 20% | 0.1188% | 2.392% | n/a
Transmission | Transmission Overhead Detailed Inspections (WMP.479) | 3 years | Ground | GO 165, 95 FAC-501-WECC | 433 | 917 | 1685 | 2447 | 913 | 1437 | 2127 | 2524 | 654 | 1325 | 1980 | 2545 | 33% | 0.2546% | 7.525% | 0.6648%
Transmission | Transmission Infrared Inspections (WMP.482) | Annual | Aerial (helicopter) Ground | GO 165, 95 | 0 | 0 | 7294 | 7294 | 0 | 0 | 7294 | 7294 | 0 | 0 | 7294 | 7294 | 1 | 0 | 0% | 0%
Distribution | Distribution Wood Pole Intrusive Inspections (WMP.483) | 10 years | Ground | GO 165, 95 | 303 | 606 | 909 | 1214 | 1369 | 2738 | 4107 | 5477 | 3000 | 6000 | 9000 | 11923 | 0 - 10%* | 0.04694% | 0.9153% | n/a
Transmission | Transmission Wood Pole Intrusive Inspections (WMP.1190) | 8 years | Ground | GO 165, 95 | 17 | 34 | 51 | 68 | 49 | 98 | 147 | 196 | 6 | 12 | 18 | 24 | 0 - 10%* | 0% | 0.7874% | 0%
Distribution | Risk-Informed Drone Inspections (WMP.552) | Risk-based in HFTD and WUI | Aerial - drone Ground | n/a | 2250 | 4500 | 6750 | 9000 | 2250 | 4500 | 6750 | 9000 | 2250 | 4500 | 6750 | 9000 | 11% | 0.4375% | 21.68% | n/a
Distribution | Distribution Overhead Patrol Inspections (WMP.488) | Annual | Ground | GO 165, 95 | 21170 | 42340 | 63510 | 84678 | 21170 | 42340 | 63510 | 84678 | 21170 | 42340 | 63510 | 84678 | 100% | 0.005762% | 0.2374% | n/a
Transmission | Transmission Overhead Patrol Inspections (WMP.489) | Annual | Aerial - helicopter | GO 165, 95 FAC-501-WECC | 7121 | 7121 | 7121 | 7454 | 7121 | 7121 | 7121 | 7454 | 7121 | 7121 | 7121 | 7454 | 100% | 0% | 0.04498% | 0%
Substation | Substation Patrol Inspections (WMP.492) | Monthly or Bi-monthly | Ground | GO 174 | 90 | 192 | 282 | 381 | 90 | 192 | 282 | 381 | 90 | 192 | 282 | 381 | 100% | n/a** | n/a** | n/a**
Transmission | Transmission Switch Inspections (WMP.1509) | 3 years | Ground | n/a | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 4 | 33% | n/a** | n/a** | n/a**
*HFTD inspections vary by year and are determined by a regional master schedule.
**Inspection findings are not subject to GO 95, Rule 18 Levels.

## OEIS Table 8-3
QA/QC Activity Name | QA/QC Activity Tracking ID | Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Quality assurance/quality control of Distribution Overhead Detailed Inspections | WMP.491 | Distribution Overhead Detailed Inspections | WMP.478 | QA/QC | Ensure SDG&E inspection procedures are being adhered to
Quality assurance/quality control of Transmission Inspections | WMP.1191 | Transmission Overhead Detailed Inspections | WMP.479 | QA / QC | Ensure inspections are following SDG&E’s procedures for inspections
Quality assurance/quality control of Risk-Informed Drone Inspections | WMP.1192 | Risk-Informed Drone Inspections | WMP.552 | QA/QC | Ensure SDG&E inspection procedures are being adhered to
Quality assurance/quality control of Wood Pole Intrusive (Transmission & Distribution) | WMP.1193 | Wood Pole Intrusive (Transmission & Distribution) | WMP.1190, WMP.483 | QA/QC | Ensure SDG&E inspection procedures are being adhered to
Quality assurance/quality control of Corrective Maintenance Program | WMP.1434 | Corrective Maintenance Program | WMP.1433 | QA/QC | Ensure SDG&E repair procedures are being adhered to
Quality assurance/quality control of Substation Inspections | WMP.1194 | Substation Patrol Inspections | WMP.492 | QA/QC | Ensure SDG&E substation inspection procedures and checklists are being adhered to
QA/QC of Transmission Switch Inspections | WMP.1510 | Transmission Switch Inspections | WMP.1509 | QA/QC | Ensure inspections are following SDG&E’s procedures for inspections
Quality assurance/quality control of PSPS Sectionalizing Enhancement Program | WMP.1435 | PSPS Sectionalizing Enhancement Program | WMP.461 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable
Quality assurance/quality control of Advanced Protection Program | WMP.1496 | Advanced Protection Program | WMP.463 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable
Quality assurance/quality control of Strategic Undergrounding Program | WMP.1497 | Strategic Undergrounding Program | WMP.473 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable
Quality assurance/quality control of Distribution Overhead System Hardening Program | WMP.1498 | Distribution Overhead System Hardening Program | WMP.475 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable
Quality assurance/quality control of Transmission Overhead Hardening | WMP.1499 | Transmission Overhead Hardening | WMP.543 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable
Quality assurance/quality control of Transmission Overhead Hardening (Distribution Underbuild) | WMP.1500 | Transmission Overhead Hardening (Distribution Underbuild) | WMP.545 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable
Quality assurance/quality control of Strategic Pole Remediation Program | WMP.1501 | Strategic Pole Remediation Program | WMP.1189 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable
Quality assurance/ quality control of Combined Covered Conductor | WMP.1508 | Combined Covered Conductor | WMP.455 | QA/QC | Validate work is performed in accordance with project documents, standards, specifications, and codes, as applicable

## OEIS Table 8-4
QA/QC Activity Name | Initiative/Activity Being Audited | Type of Audit | Population / Sample Unit | 2026: Population Size | 2026: Sample Size | 2027: Population Size | 2027: Sample Size | 2028: Population Size | 2028: Sample Size | Percent of Sample in the HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Quality assurance/quality control of Distribution Detailed Inspections (WMP.491) | Distribution Overhead Detailed Inspections (WMP.478) | Field and Desktop | Findings | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 50% of findings found during inspection | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 50% of findings found during inspection | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 50% of findings found during inspection | 100% | n/a* | 95% | 95% | 95%
Quality assurance/quality control of Transmission Inspections (WMP.1191) | Transmission Overhead Detailed Inspections (WMP.479) | Field and Desktop | Findings | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 100% of conditions identified during inspection | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 100% of conditions identified during inspection | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 100% of conditions identified during inspection | 100% | n/a* | n/a see Section 8.5.4 Pass Rate Calculation | n/a see Section 8.5.4 Pass Rate Calculation | n/a see Section 8.5.4 Pass Rate Calculation
Quality assurance/quality control of Wood Pole Intrusive (Transmission & Distribution) (WMP.1193) | Transmission Wood Pole Intrusive Inspections (WMP.1190) & Distribution Wood Pole Intrusive Inspections (Distribution) (WMP.483) | Field | Intrusive Inspections | 1282 | 5% | 5673 | 5% | 11947 | 5% | 100% | n/a* | 95% | 95% | 95%
Quality assurance/quality control of Risk-Informed Drone Inspections (WMP.1192) | Risk-Informed Drone Inspections (WMP.552) | Desktop | Drone Inspections | 9000 | 15% | 9000 | 15% | 9000 | 15% | 90% | n/a* | 98% | 98% | 98%
Quality assurance/quality control of Substation Inspections (WMP.1194) | Substation Patrol Inspections (WMP.492) | Field | Findings | 45 | 18 | 45 | 18 | 45 | 18 | 100% | n/a* | 90% | 90% | 90%
Quality assurance/quality control of Transmission Switch Inspections (WMP.1510) | Transmission Switch Inspections (WMP.1509) | Field and Desktop | Switch Function Inspections | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 100% of conditions identified during inspection | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 100% of conditions identified during inspection | Population size, determined based on findings from inspections, is unknown at this time. See Section 8.5.3 Sampling Plan. | 100% of conditions identified during inspection | 100% | n/a* | n/a see Section 8.5.4 Pass Rate Calculation | n/a see Section 8.5.4 Pass Rate Calculation | n/a see Section 8.5.4 Pass Rate Calculation
Quality assurance/quality control of Corrective Maintenance Program (WMP.1434) | Corrective Maintenance Program (WMP.1433) | Field and Desktop | OH Fire or Safety Related Corrective Actions | Population size determined based on number of Corrective Action Repairs needed. | 1% | Population size determined based on number of Corrective Action Repairs needed. | 1% | Population size determined based on number of Corrective Action Repairs needed. | 1% | 100% | n/a* | 90% | 90% | 90%
Quality assurance/quality control of Grid Hardening PSPS Sectionalizing Enhancement Program (WMP.1435) | PSPS Sectionalizing Enhancement Program (WMP.461) | Field and Desktop | Switches | Population size determined based on completed PSPS Sectionalizing work. | 95% of Population Size | Population size determined based on completed PSPS Sectionalizing work. | 95% of Population Size | Population size determined based on completed PSPS Sectionalizing work. | 95% of Population Size | 100% | 95% / 2% | 95% | 95% | 95%
Quality assurance/quality control of Advanced Protection Program (WMP.1496) | Advanced Protection Program (WMP.463) | Field and Desktop | Nodes | Population size determined based on completed Advanced Protection work. | 95% of Population Size | Population size determined based on completed Advanced Protection work. | 95% of Population Size | Population size determined based on completed Advanced Protection work. | 95% of Population Size | 100% | 95% / 2% | 95% | 95% | 95%
Quality assurance/quality control of Strategic Undergrounding Program (WMP.1497) | Strategic Undergrounding Program (WMP.473) | Field and Desktop | Miles | Population size determined based on completed Strategic Undergrounding work. | 95% of Population Size | Population size determined based on completed Strategic Undergrounding work. | 95% of Population Size | Population size determined based on completed Strategic Undergrounding work. | 95% of Population Size | 100% | 95% / 2% | 95% | 95% | 95%
Quality assurance/quality control of Distribution Overhead System Hardening Program (WMP.1498) | Distribution Overhead System Hardening Program (WMP.475) | Field and Desktop | Miles | Population size determined based on completed Distribution Overhead System Hardening work. | 95% of Population Size | Population size determined based on completed Distribution Overhead System Hardening work. | 95% of Population Size | Population size determined based on completed Distribution Overhead System Hardening work. | 95% of Population Size | 100% | 95% / 2% | 95% | 95% | 95%
Quality assurance/quality control of Transmission Overhead Hardening (WMP.1499) | Transmission Overhead Hardening (WMP.543) | Field and Desktop | Miles | Population size determined based on completed Transmission Overhead Hardening work. | 95% of Population Size | Population size determined based on completed Transmission Overhead Hardening work. | 95% of Population Size | Population size determined based on completed Transmission Overhead Hardening work. | 95% of Population Size | 100% | 95% / 2% | 95% | 95% | 95%
Quality assurance/quality control of Transmission Overhead Hardening (Distribution Underbuild) (WMP.1500) | Transmission Overhead Hardening (Distribution Underbuild) (WMP.545) | Field and Desktop | Miles | Population size determined based on completed Transmission Overhead Hardening work. | 95% of Population Size | Population size determined based on completed Transmission Overhead Hardening work. | 95% of Population Size | Population size determined based on completed Transmission Overhead Hardening work. | 95% of Population Size | 100% | 95% / 2% | 95% | 95% | 95%
Quality assurance/ quality control of Combined Covered Conductor (WMP.1508) | Combined Covered Conductor (WMP.455) | Field and Desktop | Miles | Population size determined based on completed Combined Covered Conductor work. | 95% of Population Size | Population size determined based on completed Combined Covered Conductor work. | 95% of Population Size | Population size determined based on completed Combined Covered Conductor work. | 95% of Population Size | 100% | 95% / 2% | 95% | 95% | 95%
*SDG&E does not calculate Confidence Level/MOE for Transmission, Distribution, or Substation programs.

## OEIS Table 8-5
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Transmission HFTD Tier 2 | 0 | 0 | 0 | 0
Transmission HFTD Tier 3 | 0 | 0 | 0 | 0
Distribution HFTD Tier 2 | 0 | 9 | 10 | 7
Distribution HFTD Tier 3 | 21 | 18 | 26 | 3

## OEIS Table 8-6
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 21 | 27 | 36 | 10
Priority 3 | 0 | 0 | 0 | 0

## OEIS Table 8-7
Circuit/Circuit Segment ID | Circuit/Circuit Segment Name | Circuit Length Overhead Circuit Miles | Number of Outages in Past 3 Years | Cumulative Outage Duration | Cumulative Number of Customers Impacted by Outages | Cumulative Customer Minutes**
237* | C237 | 75.3862 | 3 | 1706 | 3410 | 861520
520 | C520 | 96.7784 | 1 | 1008 | 541 | 543517
1233 | C1233 | 28.4282 | 3 | 1609 | 878 | 465162
442 | C442 | 37.3076 | 2 | 797 | 1374 | 363757
288 | C288 | 1.8466 | 1 | 853 | 895 | 263556
222* | C222 | 97.2227 | 1 | 775 | 1025 | 243195
230 | C230 | 42.4434 | 1 | 352 | 961 | 240520
448 | C448 | 79.0705 | 1 | 445 | 1026 | 191595
235 | C235 | 14.429 | 1 | 248 | 731 | 181288
599 | C599 | 39.2608 | 1 | 63 | 2458 | 143473
212 | C212 | 114.2949 | 1 | 263 | 518 | 124838
859 | C859 | 7.0809 | 1 | 211 | 751 | 120517
73 | C73 | 57.8506 | 1 | 224 | 495 | 105478
444 | C444 | 42.5816 | 1 | 360 | 294 | 101670
356 | C356 | 37.86 | 1 | 230 | 1 | 230
* Circuit/circuit segments are all in the Top 20% Overall Utility Risk shown in OEIS Table 6-4
** This column was added by SDG&E and is not in the 2026-2028 Wildfire Mitigation Plan Technical Guidelines

## OEIS Table 8-8
Circuit/Circuit Segment ID Recloser | Number of Outages in Past 3 Years | Cumulative Outage Duration | Cumulative Number of Customers Impacted by Outages | Cumulative Customer Minutes**
364 | 9 | 1184 | 60876 | 4606674
237 * | 10 | 3517 | 15173 | 2190224
322 | 2 | 438 | 16818 | 2181048
415 | 5 | 3104 | 13164 | 2002316
325 | 4 | 1789 | 16689 | 1783980
214 | 17 | 7410 | 6603 | 1460141
RA2 | 3 | 1062 | 2918 | 1385607
520 | 12 | 3653 | 11088 | 1258592
781 | 5 | 1238 | 25936 | 1212009
286 | 4 | 1216 | 20283 | 1211621
* Circuit/Circuit Segment is in Top 20% Overall Utility Risk shown in OEIS Table 6-4
** This column was added by SDG&E and is not in the 2026-2028 Wildfire Mitigation Plan Technical Guidelines

## OEIS Table 9-1
Initiative | Quantitative or Qualitative | Activity (Tracking ID) | Previous Tracking ID, if applicable | Target Unit | 2026 Target/Status | % Risk Reduction for 2026 | 2027 Target/Status | % Risk Reduction for 2027 | 2028 Target/Status | % Risk Reduction 2028 | 3-year Total | Section; Page Number
Wood & Slash Management | Qualitative | Sustainability (WMP.1460) - As part of the company sustainability goal, SDG&E will explore additional options of diverting green waste from landfills to recycling facilities. | n/a | n/a | By year end, engage Supply Management Department to research prospective recycling vendors. | n/a | By year end, enter service agreement with new recycling vendor(s) to divert green waste. | n/a | By year end, continue engaging additional vendor opportunities to reach company goal. | n/a | n/a | 9.5; p. 252
Workforce Planning (Vegetation Management) | Qualitative | Workforce Planning (Vegetation Management) (WMP.506) - Manage vegetation management workforce through qualification and certification requirements. | n/a | n/a | By year end, manage Vegetation Management workforce through the validation of required, annual contractor training including fire preparedness, hazard tree assessment, environmental, and customer service. Track training completion of internal staff for the Company’s Environmental & Safety Compliance Management Program (ESCMP) addressing compliance requirements, all applicable environmental, health and safety laws, rules, and regulations, and company standards. Validate internal and company workforce are compliant with required ISA-certification requirements of applicable job positions. | n/a | By year end, manage Vegetation Management workforce through the validation of required, annual contractor training including fire preparedness, hazard tree assessment, environmental, and customer service. Track training completion of internal staff for the Company’s ESCMP addressing compliance requirements, all applicable environmental, health and safety laws, rules, and regulations, and company standards. Validate internal and company workforce are compliant with required ISA-certification requirements of applicable job positions. | n/a | By year end, manage Vegetation Management workforce through the validation of required, annual contractor training including fire preparedness, hazard tree assessment, environmental, and customer service. Track training completion of internal staff for the Company’s ESCMP addressing compliance requirements, all applicable environmental, health and safety laws, rules, and regulations, and company standards. Validate internal and company workforce are compliant with required ISA-certification requirements of applicable job positions. | n/a | n/a | 9.13; p. 269
Integrated Vegetation Management | Quantitative | Fuels Management (WMP.497) | n/a | Pole | 500 | 0.03% | 500 | 0.03% | 500 | 0.03% | 1500 | 9.7; p. 253
Defensible Space | Qualitative | See Substation Patrol Inspections (WMP.492) Activity- There are no planned improvements. | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 9.6; p. 253

## OEIS Table 9-2
Activity (Program) | Tracking ID | Previous Tracking ID, if applicable | Target Unit* | Cumulative (Cml.) Quarterly Target 2026, Q1 | Cml. Quarterly Target 2026, Q2 | Cml. Quarterly Target 2026, Q3 | Cml. Quarterly Target 2026, Q4 | Cml. Quarterly Target 2027, Q1 | Cml. Quarterly Target 2027, Q2 | Cml. Quarterly Target 2027, Q3 | Cml. Quarterly Target 2027, Q4 | Cml. Quarterly Target 2028, Q1 | Cml. Quarterly Target 2028, Q2 | Cml. Quarterly Target 2028, Q3 | Cml. Quarterly Target 2028, Q4 | % HFTD Covered in 2026 | % Risk Reduction for 2026 | % Risk Reduction for 2027 | % Risk Reduction for 2028 | 3- year Total | Activity Timeline Target | Section; Page Number
Detailed Inspection | WMP.1502 | n/a | Circuit Miles | 2625 | 5250 | 7857 | 10500 | 2625 | 5250 | 7857 | 10500 | 2625 | 5250 | 7857 | 10500 | 100% | 4.72% | 4.72% | 4.72% | 31500 | 2028-12-31 | 9.2; p. 247
Detailed Inspection | WMP.494 | n/a | Inspections | 121375 | 242750 | 364125 | 485500 | 121375 | 242750 | 364125 | 485500 | 121375 | 242750 | 364125 | 485500 | 100% | 4.72% | 4.72% | 4.72% | 1456500 | 2028-12-31 | 9.4; p. 251
Off-Cycle Patrol | WMP.1503 | n/a | Circuit Miles | 1212 | 2424 | 3636 | 4850 | 1212 | 2424 | 3636 | 4850 | 1212 | 2424 | 3636 | 4850 | 100% | 4.58% | 4.58% | 4.58% | 14550 | 2028-12-31 | 9.2; p. 247
Off-Cycle Patrol | WMP.508 | n/a | VMA | 26 | 52 | 78 | 106 | 26 | 52 | 78 | 106 | 26 | 52 | 78 | 106 | 100% | 4.58% | 4.58% | 4.58% | 318 | 2028-12-31 | 9.4; p. 251
Pole Clearing | WMP.1504 | n/a | Circuit Miles | 375 | 750 | 1125 | 1500 | 375 | 750 | 1125 | 1500 | 375 | 750 | 1125 | 1500 | 100% | 4.59% | 4.59% | 4.59% | 4500 | 2028-12-31 | 9.2; p. 247
Pole Clearing | WMP.512 | n/a | Poles Cleared | 5500 | 11000 | 16500 | 22000 | 5500 | 11000 | 16500 | 22000 | 5500 | 11000 | 16500 | 22000 | 100% | 4.59% | 4.59% | 4.59% | 66000 | 2028-12-31 | 9.4; p. 251
*To help assess risk more accurately, SDG&E included inspections, VMAs, and pole brush units, in addition to circuit-miles in order to preserve more granular metrics. Tracking IDs associated with the unit metrics are only provided in this table for future metric reporting purposes.

## OEIS Table 9-3
Type | Inspection Activity (Program) | Area Inspected | Frequency
Transmission and Distribution | Detailed Inspections (WMP.494, WMP.1502) | Service Territory | Annual
Transmission and Distribution | Off-Cycle Patrols (WMP.508, WMP.1503) | HFTD | Annual

## OEIS Table 9-4
Partnerships Agency/Organization | Activities | Objectives | Electrical Corporation Role | Anticipated Accomplishments
Fire Safe Council of San Diego County | Residential chipping program, home survivability assessments, roadside brushing (vegetation removal), and fuel break construction | 1 - Community protection (defensible space), 2 - Electric infrastructure protection/resilience, 3 - Evacuation route improvement | Collaboration in the planning phase and funding of the implementation. | 2026-2028: Planned annual treatments: 190 acres, 400 homes, and 400 electric poles.
Viejas Band of Kumeyaay Indians | Residential defensible space and roadside brushing | 1 - Community protection (defensible space), 2 - Electric infrastructure protection/resilience | Collaboration in the planning phase and funding of the implementation. | 2026-2028: Planned annual treatments: 97 acres, 94 homes, & 94 electric poles.
Campo Band of Diegueno Mission Indians | Fuel break maintenance | 1 - Community protection (defensible space), 2 - Electric infrastructure protection/resilience | Collaboration in the planning phase and funding of the implementation. | 2026-2028: Annual maintenance: 2 miles of fuel break totaling 43 acres, 7 transmission towers
San Diego Regional Fire & Emergency Services Foundation | Support Fire Safe Councils across the County in activities such as vegetation management/ removal, green waste chipping events, defensible space assistance, community education, and home hardening | 1 - Community protection (defensible space) | Funding the implementation. | 2025: Support at least 10 Fire Safe Councils across 18 zip codes primarily in the HFTD. Provide education and training to all FSC at the EOC and Resilience Center.
Inter-Tribal Long Term Recovery Foundation | Provide wildfire preparedness supplies and workshops including cultural burning for resilience. | 1 - Community education, 2 - Community protection (defensible space) | Funding of the implementation | Partnership with the Climate Science Alliance's Collaboration of Native Nations for Climate Transformation and identify and train Tribal cultural burn technicians and practitioners.

## OEIS Table 9-5
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Detailed Inspections | WMP.494, WMP.1502 | QA/QC | Ensure contractors are following SDG&E contractual requirements, procedures, and standards for safety, compliance, and reliability.
Pruning and Removal | WMP.1492 | QA/QC | Ensure contractors are following SDG&E contractual requirements, procedures, and standards for safety, compliance, and reliability.
Pole Clearing | WMP.512, WMP.1504 | QA/QC | Ensure contractors are following SDG&E contractual requirements, procedures, and standards for safety, compliance, and reliability.

## OEIS Table 9-6
QA/QC Activity Name* | Initiative/ Activity Being Audited | Population / Sample Unit** | 2026: Population Size | 2026: Sample Size | 2026: % of Sample in HFTD | 2027: Population Size | 2027: Sample Size | 2027: % of Sample in HFTD | 2028: Population Size | 2028: Sample Size | 2028: % of Sample in HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Quality assurance/quality control of Vegetation Management (WMP.1493) | Detailed Inspections (WMP.1502) | Circuit Miles | 10500 | 2800 | 50% | 10500 | 2800 | 50% | 10500 | 2800 | 50% | 99%/3.0% | 90% | 90% | 90%
Quality assurance/quality control of Vegetation Management (WMP.1505) | Detailed Inspections (WMP.494) | Inspections | 485500 | 72825 | 50% | 485500 | 72825 | 50% | 485500 | 72825 | 50% | 99%/3.0% | 90% | 90% | 90%
Quality assurance/quality controlof Prune and Removal (WMP.1494) | Prune and Removal (WMP.1511) | Circuit Miles | Population size determined based on completed Prune and Removal work | 15% | 50% | Population size determined based on completed Prune and Removal work | 15% | 50% | Population size determined based on completed Prune and Removal work | 15% | 50% | 99%/3.0% | 90% | 90% | 90%
Quality assurance/quality control of Prune and Removal (WMP.1506) | Prune and Removal (WMP.1492) | Trees trimmed/removed | Population size determined based on completed Prune and Removal work | 15% | 50% | Population size determined based on completed Prune and Removal work | 15% | 50% | Population size determined based on completed Inspection work | 15% | 50% | 99%/3.0% | 90% | 90% | 90%
Quality assurance/quality control of Pole Clearing (WMP.1495) | Pole Clearing (WMP.1504) | Circuit Miles | 1500 | 350 | 90% | 1500 | 350 | 90% | 1500 | 350 | 90% | 99%/3.0% | 90% | 90% | 90%
Quality assurance/quality control if Pole Clearing (WMP.1507) | Pole Clearing (WMP.512) | Poles Cleared | 22000 | 3300 | 90% | 22000 | 3300 | 90% | 22000 | 3300 | 90% | 99%/3.0% | 90% | 90% | 90%
*This column was added by SDG&E and is not in the OEIS WMP Guidelines
**To help assess risk more accurately, SDG&E included inspections, VMAs, and pole brush units, in addition to circuit-miles in order to preserve more granular metrics. Tracking IDs associated with the unit metrics are only provided in this table for future metric reporting purposes.

## OEIS Table 9-7
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 42 | 71 | 22 | 1
HFTD Tier 2 | 75 | 225 | 5 | 1
HFTD Tier 3 | 300 | 29 | 1 | 0

## OEIS Table 9-8
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
High Priority (Priority 1) | 40 | 12 | 2 | 0
Low Priority (Priority 2) | 335 | 242 | 4 | 1

## OEIS Table 9-9
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | # of Electrical Corporation Employees with Min Quals | # of Electrical Corporation Employees with Special Certifications | # of Contracted Employees with Min Quals | # of Contractor Employees with Applicable Certifications | Total # of Employees | Reference to Electrical Corporation Training/Qualification Programs
Vegetation Management Compliance Manager | Bachelor’s Degree in Forestry, Biology, or Horticulture and/or equivalent training/experience. 7 years’ experience in Utility Vegetation Management. | International Society of Arboriculture (ISA) Certified Arborist ISA Utility Specialist | 1 | 1 | n/a | n/a | 1 | International Society of Arboriculture Certified Arborist Program
Vegetation Management WMP Manager | Bachelor’s Degree in Forestry, Biology, or Horticulture and/or equivalent training/experience. | International Society of Arboriculture (ISA) Certified Arborist ISA Utility Specialist | 1 | 1 | n/a | n/a | 1 | International Society of Arboriculture Certified Arborist Program
Vegetation Management Operational Manager | Bachelor’s Degree in Forestry, Biology, or Horticulture and/or equivalent training/experience 7 years’ experience in Utility Vegetation Management, including 3 years in contractor management | International Society of Arboriculture (ISA) Certified Arborist ISA Utility Specialist | 1 | 1 | n/a | n/a | 1 | International Society of Arboriculture Certified Arborist Program
Vegetation Management Business Advisor | Bachelor’s degree in Finance, Accounting, Data Analytics, Business Administration, or related | No special certification required | 1 | n/a | n/a | n/a | 1 | n/a
Vegetation Management Senior Data Analyst | Bachelor’s degree in Engineering, Economics, Finance, Data Analytics, or related | No special certification required | 2 | n/a | n/a | n/a | 2 | n/a
Area Forester/ Contract Administrator | 3 years’ utility vegetation management experience. Bachelor’s degree in Forestry, Biology, Horticulture, or related field (preferred). | International Society of Arboriculture (ISA) Certified Arborist | 8 | 8 | n/a | n/a | 8 | International Society of Arboriculture Certified Arborist Program
Vegetation Management Lead Forester | Bachelor’s degree in Forestry, Biology, Horticulture, or related field (preferred). 3-5 years’ experience administering vegetation management programs. Supervisory experience working with external contractors. | International Society of Arboriculture (ISA) Certified Arborist | 1 | 1 | n/a | n/a | 1 | International Society of Arboriculture Certified Arborist Program
Forester Patrol Person | 3 years’ utility vegetation management experience. Bachelor’s degree in Forestry, Biology, Environmental Science, Horticulture, or related field (preferred). | International Society of Arboriculture (ISA) Certified Arborist | 4 | 4 | n/a | n/a | 4 | International Society of Arboriculture Certified Arborist Program
Resource Coordinator (Customer Help Desk) | High school diploma, college courses (preferred). 3 years’ customer service experience. Microsoft Office proficiency. Strong technical writing skills (preferred). Working knowledge of Mainframe, GIS, SAP and Distribution Planning Scheduling applications (preferred). | No special certification required | 3 | n/a | n/a | n/a | 3 | n/a
Auditor | Bachelor’s degree in Forestry, Biology, Environmental Science, Horticulture, or related field (preferred); Current Class C Driver’s License with clean driver safety record | International Society of Arboriculture (ISA) Certified Arborist | n/a | n/a | 29 | 16 | 29 | International Society of Arboriculture Certified Arborist Program
Pre-Inspector | Bachelor’s degree in Forestry, Biology, Environmental Science, Horticulture, or related field (preferred). Current Class C driver’s license with clean driver safety record. | International Society of Arboriculture (ISA) Certified Arborist | n/a | n/a | 62 | 53 | 62 | International Society of Arboriculture Certified Arborist Program
Tree Trim General Foreperson/ Supervisor | 5 years’ line clearance tree pruning experience as a Foreman. Current California driver's license (Class B endorsement). General computer knowledge. Strong leadership qualities. | International Society of Arboriculture (ISA) Certified Arborist | n/a | n/a | 12 | 7 | 12 | International Society of Arboriculture Certified Arborist Program
Tree Trimmer | Current California driver's license (Class B endorsement). General computer skills. | Line-Clearance Qualified Arborist (or Trainee) | n/a | n/a | 148 | 148 | 148 | United States Department of Labor Standard OSHA 1910.269; ANSI Z133 Safety Standards
Pole Brush General Foreman / Supervisor | 5 years’ line clearance tree pruning experience as a Foreman. Current California driver's license (Class C endorsement). General computer knowledge. | Qualified Applicator Certification | n/a | n/a | 5 | 3 | 5 | California Department of Pesticide Regulation Licensing Program
Pole Brusher | Current California driver's license (Class C endorsement). General computer skills. | No special certification required | 27 | n/a | n/a | n/a | 27 | n/a

## OEIS Table 10-1
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID, if applicable | Target Unit | 2026 End of Year Total/Completion Date | % Risk Reduction for 2026 | 2027 Total/Status | % Risk Reduction for 2027 | 2028 Total/Status | % Risk Reduction for 2028 | 3- year Total | Section; Page number
Environmental Monitoring Systems (Section 10.2) | Quantitative | Air Quality Station Maintenance (WMP. 1431) | n/a | Sensor Maintenance | 192 | n/a | 192 | n/a | 192 | n/a | 576 | 10.2; p. 277
Environmental Monitoring Systems | Qualitative | Weather Station Data -Update 95th, 99th and max wind gust annually utilizing prior years weather station data. (WMP.1461) | n/a | n/a | By 12/31/2026, complete annual adjustments to max wind gust thresholds | n/a | By 12/31/2027, complete annual adjustments to max wind gust thresholds | n/a | By 12/31/2028, complete annual adjustments to max wind gust thresholds | n/a | n/a | 10.2; p. 277
Grid Monitoring Systems | Qualitative | Grid Monitoring Systems Data Integration-Integrate power quality, fault data, and smoke detection to enhance situational awareness and support grid reliability. (WMP.1444) | n/a | n/a | By 12/31/2026, begin integration of power quality, fault data and smoke detection into a central monitoring system to enhance real-time monitoring, response, and prevention | n/a | By 12/31/2027, begin integration of power quality, fault data and smoke detection into a central monitoring system to enhance real-time monitoring, response, and prevention | n/a | By 12/31/2028, begin integration of power quality, fault data and smoke detection into a central monitoring system to enhance real-time monitoring, response, and prevention | n/a | n/a | 10.3; p. 279
Grid Monitoring Systems | Quantitative | Early Fault Detection (WMP.1195) | n/a | nodes | 60 | 0.31% | 60 | 0.24% | 60 | 0.46% | n/a | 10.3; p. 279
Ignition Detection Systems | Qualitative | Ignition Detection Systems -Cameras - Ongoing review to identify camera communication network single points of failure to avoid interruption of camera imagery. (WMP.1343) | n/a | n/a | By 12/31/2026, complete annual monitoring of network | n/a | By 12/31/2027, complete annual monitoring of network | n/a | By 12/31/2028, complete annual monitoring of network | n/a | n/a | 10.4; p. 283
Ignition Detection Systems | Quantitative | Quarterly validation of weekly uptime for Ignition Detection Cameras (WMP.1467) ** | n/a | Quarterly validations | 4 | n/a | 4 | n/a | 4 | n/a | 4 | 10.4; p. 283
Weather Forecasting | Qualitative | See Fire Potential Index (WMP.450) in OEIS Table 10-1 | n/a | n/a | See Fire Potential Index (WMP.450) in OEIS Table 10-1 | n/a | See Fire Potential Index (WMP.450) in OEIS Table 10-1 | n/a | See Fire Potential Index (WMP.450) in OEIS Table 10-1 | n/a | See Fire Potential Index (WMP.450) in OEIS Table 10-1 | 10.5; p. 287
Weather Forecasting | Quantitative | Post-processing success rate - WRF simulations (WMP.1465) | n/a | Success Rate | 97% | n/a | 97% | n/a | 97% | n/a | 97% | 10.5; p. 287
Weather Station Maintenance and Calibration | Qualitative | Communication success rate of weather stations (WMP.1466) | n/a | n/a | By 12/31/2026, complete monitoring of communication success rate of weather stations | n/a | By 12/31/2027, complete monitoring of communication success rate of weather stations | n/a | By 12/31/2028, complete monitoring of communication success rate of weather stations | n/a | n/a | 10.5.5 ; p. 292
Weather Station Maintenance and Calibration | Quantitative | Weather Station Maintenance and Calibration* (WMP. 1430) | n/a | Station maintenance | 217 | n/a | 217 | n/a | 217 | n/a | 651 | 10.5.5; p. 292
Fire Potential Index (FPI) | Qualitative | Fire Potential Index - Ongoing analysis of FPI predictions versus observations to potentially improve FPI. (WMP.450) | n/a | n/a | By 12/31/2026, complete annual analysis | n/a | By 12/31/2027, complete annual analysis | n/a | By 12/31/2028, complete annual analysis | n/a | n/a | 10.6; p. 292
*The weather station network consists of 223 weather stations throughout the service territory. Six of these stations are owned by SDG&E but are maintained by AEM (https://aem.eco/) . SDG&E is responsible for maintenance and calibration of the other 217 weather stations.
** The Alert California Cameras are built on the High-Performance Wireless Research and Education Network (HPWREN) in partnership with UC San Diego and local fire departments. SDG&E does not have control of the uptime, but will report any downtime to the vendor.

## OEIS Table 10-2
System | Measurement/ Observation | Frequency | Purpose and Integration
Weather Stations | Wind speed, wind direction, wind gusts, temperature, and humidity | 6 measurements per hour | Increases situational awareness and obtains foundational data for operational and mission critical activities.
Air Quality Sensors | Concentration of PM2.5 | 6 measurements per hour | Converts concentrations to an index (AQI) and quickly notifies employees when air quality is unhealthy.
Fuel Moisture & NDVI Cameras | Fuel moisture values | Daily values of 10-hour fuels and grass health respectively | Provide accurate reflection of the state of fuels, which is important for understanding fire potential.

## OEIS Table 10-3
System | Measurement/Observation | Frequency | Purpose and Integration
Advanced Radio Frequency Sensors | Radio Frequency signals | Real-time | Used to correlate trends and determine failing equipment and the location of the failing equipment.
Power Quality Meters | Event based voltage and current waveforms (greater than 128 samples per cycle) | Event based | Waveform data is consumed by a platform that uses AI and machine learning algorithms to determine failing equipment and the location of the failing equipment.
SCADA | Telemetered points in RTUs provide status and analog data based on sensor type. Field devices are on both 12 kV and 4 kV circuits. | Varies by sensor type | Used by DSOs to monitor and control field equipment. Monitors telemetered points and alarms and operates field RTUs giving DSOs real-time situational awareness.
Data Historian | Collects and tracks data such as electricity usage, energy consumption, and other data points such as megawatts, mega volt amps, and reactive power breaker status. | Real time (60 seconds or less), varies by sensor type | Captures, stores, and provides access to real-time and historical data from sensors, devices, and systems. Used to monitor and optimize energy consumption, identify problems and inefficiencies, and perform data analysis and reporting.
OMS | Locations and duration of outages (SCADA is source of data). | Continuous (24 hours a day, 7 days a week, 365 days) | Hub for distribution operations regarding outage and distribution planning management. Integrated with a variety of systems to identify and restore outages.
LPCN OTV | Monitors field devices, such as WFIs and federal aviation (FAA) lights, that are connected through the Low Power Communications Network (LPCN). | 1 measurement per hour for each WFI (2,900 total WFIs) and 3 measurements per hour for each FAA light. | See Measurement/Observation
Synchrophasors/ Phasor Measurement Units (PMU) | Displays measured electrical quantities such as phase voltage magnitude, phase current magnitude, phase angle, and frequency of electrical signals in the grid (e.g., MW, MVAR, Phase Angle, Frequency, Phase Magnitude). | Real time; 30 samples per second per PMU sensor location | Used to display and measure electrical characteristics of the electric power system. Data is transmitted to a central monitoring system where it can be used for data analysis, reporting, and control purposes.
Smart Meter | Collects meter data such as measured intervals and register consumption data for billing customers as well as other meter information such as voltage, events, and alarms. Openway is used for pinging / load-side voltage checks for groups of meters to verify outage conditions. | Voltage Data is collected once per day. Alarm data is transmitted real-time. All other data is retrieved once per day. | Smart Meter Openway is integrated to OMS, for pinging / load-side voltage checks. OSIPi is subscribed to receive voltage information from a subset of pre-designated meters.

## OEIS Table 10-4
Detection System | Capabilities | Companion Technologies | Contribution to Fire Detection and Confirmation
Satellite Based Remote Sensing | Ignition detection from geostationary satellite | Used with camera imagery to verify fire detection | Provide confirmation of wildfires and help operators assess the scope of resource response needed.
Cameras | Smoke detection | Used with satellite ignition detection to verify fire | Corroborate the initial hot spot detections from space.

## OEIS Table 10-5
Feature Group | Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
Weather | Temperature | Surface | Temperature at the surface in Fahrenheit | Weather model | 6 per day | 1 km | Hourly
Fuel Moisture | Dead Fuel Moisture | Surface | Fuel moisture content | Weather model and third-party dataset | Daily | 2 km | Daily
Fuel Moisture | Dead Fuel | Ground | 10-hour fuels are 0.25 inch to 1 inch in diameter | Remote Automatic Weather Stations (RAWS) | Hourly | 1.5 km grid | Hourly
Fuel Moisture | Live Fuel | Ground | Moisture content within living vegetation | U.S. Forest Service | Bi-Monthly | National Forests | Bi-Monthly
Fuel Moisture | Grass | Space | Normalized Difference Vegetation Index (NDVI) | Planet Labs | Weekly | 3.7 m | Daily

## OEIS Table 11-1
Initiative | Activity (Tracking ID #) | Previous Tracking ID, if applicable | 2026 End of Year Total/Completion Date | 2027 Status | 2028 Status | Section; Page number
Emergency Preparedness and Recovery Plan (Section 11.2) | Augment the CEADPP by incorporating detailed plans, concepts of operations, and annexes tailored to specific identified risks. (WMP.1008) | n/a | By 12/31/2026 the CEADPP will be updated to incorporate applicable lessons learned from 2025 and include additional requirements as they are identified | By 12/31/2027 the CEADPP will be updated to incorporate applicable lessons learned from 2026 and include additional requirements as they are identified | By 12/31/2028 the CEADPP will be updated to incorporate applicable lessons learned from 2027 and include additional requirements as they are identified | Section 11.2; p. 298
External Collaboration and Coordination (Section 11.3) | Enhance current collaborations and establish new ones with CBOs, public safety agencies, and government entities that deliver emergency preparedness education, response, and support services. (WMP.1454) | n/a | By 12/13/2026, expand the CBO network to approximately 55 CBOs. Additional CBOs will target circuit segments in the HFTD that have a high number of individuals with AFN. | By 12/31/2027, expand the CBO network to approximately 60 CBOs. Additional CBOs will target circuit segments in the HFTD that have a high number of individuals with AFN. | By 12/31/2028, expand the CBO network to approximately 65 CBOs. Additional CBOs will target circuit segments in the HFTD that have a high number of individuals with AFN. | Section 11.3; p. 305
Public Communication, Outreach, and Education Awareness (Section. 11.4) | Focus on creating more meaningful and interactive engagements including proactive preparedness through community collaboration, Tribal feedback sessions, and a combination of Outreach and AFN engagement. Organize a series of Wildfire Safety Fairs and mini-Wildfire Safety Fairs aimed at educating, engaging, and preparing customers in rural communities for wildfires. Implement Wildfire/PSPS Public Education campaign leading up to the Santa Ana wind season. Solicit customer feedback on communications and messaging and use results to improve communications and notifications for the following year. (WMP.527) | n/a | By 12/31/2026 the Wildfire, PSPS and AFN Public Education campaigns will have concluded. Customer feedback will be gathered and used to improve communications for 2027. Host Tribal Nation learning sessions post PSPS activations to acquire level of satisfaction with communication and resiliency. Incorporate feedback where applicable. Continue partnerships with CBOs and AFN collaborative council for amplification of preparedness information by end of year. Host Wildfire Safety Fairs and mini-Wildfire Safety Fairs in key communities of concern. | By 12/31/2027 the Wildfire, PSPS and AFN Public Education campaigns will have concluded. Customer feedback will be gathered and used to improve communications for 2028. Host Tribal Nation learning sessions post PSPS activations to acquire level of satisfaction with communication and resiliency. Incorporate feedback where applicable. Continue partnerships with CBO's and AFN collaborative council for amplification of preparedness information by end of year. Host Wildfire Safety Fairs and mini-Wildfire Safety Fairs in key communities of concern. | By 12/31/2028 the Wildfire, PSPS and AFN Public Education campaigns will have concluded. Customer feedback will be gathered and used to improve communications for 2029. Host Tribal Nation learning sessions post PSPS activations to acquire level of satisfaction with communication and resiliency. Incorporate feedback where applicable. Continue partnerships with CBO's and AFN collaborative council for amplification of preparedness information by end of year. Host Wildfire Safety Fairs and mini-Wildfire Safety Fairs in key communities of concern. | Section 11.4; p. 312
Customer Support in Wildfire and PSPS Emergencies (Section 11.5) | Enhance support and resources provided to impacted customers at CRCs. (WMP.1455) | n/a | By 12/31/2026 incorporate applicable lessons learned and feedback received for CRCs. | By 12/31/2027 incorporate applicable lessons learned and feedback received for CRCs. | By 12/31/2028 incorporate applicable lessons learned and feedback received for CRCs. | Section 11.5; p. 320

## OEIS Table 11-2
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Changing regulatory requirements | Constant changes in regulatory requirements make integrating wildfire- and PSPS-specific strategies into the CEADPP difficult. New regulations require additional planning and stakeholder engagement, which takes time and effort. | Assign regulatory oversight to personnel in order to maintain continuous awareness of changing regulations and ensure incorporation into the CEADPP.

## OEIS Table 11-3
Public Safety Partner Group | Name of Entity | Key Protocols | Frequency of Prearranged Communication Review and Update
Emergency Response | 2-1-1 Orange County | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | 2-1-1 San Diego | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Alvarado Hospital | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | American Red Cross of Orange County | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | American Red Cross San Diego Region | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Communication Service Providers | AT&T | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Barona Band of Mission Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
CAL FIRE | Cal Fire | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
CalOES | Cal OES | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
CalOES | Cal OES Office of Tribal Affairs | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | California Highway Patrol | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Caltrans | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Campo Band of Kumeyaay Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Carlsbad Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Carlsbad Water | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Communication Service Providers | Charter | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Aliso Viejo | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Carlsbad | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Chula Vista | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Coronado | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Dana Point | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Del Mar | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of El Cajon | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Encinitas | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Escondido | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Imperial Beach | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of La Mesa | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Laguna Beach | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Laguna Hills | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Laguna Niguel | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Lemon Grove | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Mission Viejo | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of National City | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Oceanside | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Poway | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Rancho Santa Margarita | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of San Clemente | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of San Diego | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of San Diego Office of Emergency Services | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of San Diego Water Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of San Juan Capistrano | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of San Marcos | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Santee | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Solana Beach | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | City of Vista | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Community Choice Aggregators | Clean Energy Alliance | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Coronado Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Coronado Police Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | County of Orange | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | County of San Diego | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | County of San Diego Office of Emergency Services | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Communication Service Providers | Cox Communications | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
The Commission | CPUC | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
CalOES | CUEA | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Deer Springs Fire Protection District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Descanso Community Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | El Cajon Police Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Waste Water Service Providers | Encina Waste Water Authority | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Encinitas Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Engineering and Capital Projects Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Escondido Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Escondido Police and Fire Communications | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Ewiiaapaayp Band of Kumeyaay Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | FACT (Facilitating Access to Coordinated Transportation) | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Affected Publicly Owned Utilities | Fallbrook Public Utility District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Family Health Centers San Diego | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Harrison Park Mutual Water | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Heartland Communications | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Heartland Fire | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Helix Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Iipay Nation of Santa Ysabel | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Imperial Beach Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Inaja-Cosmit Band of Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Indian Health Council | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Jacumba Community Service District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Jamul Indian Village A Kumeyaay Nation | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Julian Community Service District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Kaiser Permanente | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | La Jolla Band of Luiseno Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | La Posta Band of Mission Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Laguna Niguel Police Services | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Lakeside Fire Protection District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Lakeside Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Waste Water Service Providers | Leucadia Wastewater Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Los Coyotes Band of Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Los Tules Mutual Water Company | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Manzanita Band of the Kumeyaay Nation | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Mesa Grande Band of Mission Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Metropolitan Water District of Southern California | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Mission Hospital Laguna Beach | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Mission Hospital Mission Viejo | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Monte Vista Fire Dispatch Center | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Moulton Niguel Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Municipal Water District of Orange County | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Naval Base Coronado | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Navy Region Southwest | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | North County Dispatch Center | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | North County Fire Protection District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Oceanside Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Oceanside Police Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Office of Representative Darrell Issa | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Office of Representative Juan Vargas | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Office of Representative Mike Levin | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Office of Representative Sara Jacobs | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Office of Representative Scott Peters | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Office of Senator Catherine Blakespear | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Olivenhain Municipal Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Orange County Board of Supervisors | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Orange County Fire Authority | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Orange County OES | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Orange County Sheriff's Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Orange County United Way, 2-1-1 Orange County | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Otay Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Padre Dam Municipal Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Pala Band of Mission Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Palomar Health | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Palomar Health San Marcos Medical Office | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Palomar Medical Center Escondido | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Palomar Medical Center Poway | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Palomar Mountain Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Paradise Valley Hospital | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Pauma Band of Luiseno Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Pechanga Band of Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Pine Valley Mutual Water Company | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Port of San Diego | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Port of San Diego Harbor Police Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Rady Children's Hospital | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Rady Children's Hospital San Diego | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Rainbow Municipal Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Ramona Municipal Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Rancho Pauma Mutual Water Company | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Rancho Santa Fe Assn. | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Rancho Santa Teresa Water | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Rincon Band of Luiseno Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Rincon Del Diablo Municipal Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Saddleback College | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Community Choice Aggregators | San Diego Community Power | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Diego County Regional Airport Authority | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Diego County Sheriff's Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | San Diego County Water Authority | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Diego Fire Rescue | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Diego Law Enforcement Coordination Center | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Diego Police Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Diego Zoo Wildlife Alliance - Safari Park | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Affected Publicly Owned Utilities | San Elijo Joint Powers Authority | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Marcos Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | San Pasqual Band of Mission Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Santa Fe Irrigation District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Santa Margarita Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Scripps Health | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | SDG&E | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Sharp Healthcare | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | South Coast Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | South Orange County Water Authority | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Southern Indian Health Council | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | State of California | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | State of California Department of Water Resources | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Sweetwater Water Authority | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Sycuan Band of the Kumeyaay Nation | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Communication Service Providers | T-Mobile/Sprint | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Tri-City Medical Center | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | VA Medical Ctr | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Vallecitos Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Valley Center Municipal Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Communication Service Providers | Verizon Wireless | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Viejas Band of Kumeyaay Indians | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Emergency Response | Vista Fire Department | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Vista Irrigation District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | West Cuca Mutual Water Company | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly
Water Service Providers | Yuima Municipal Water District | Partner Portal; Email; Voice; Meetings, Trainings, Exercises (hosted by SDG&E and by partner); GIS data services | Quarterly

## OEIS Table 11-4
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Engagement overload | Partners not providing as much engagement or feedback due to increased requests. | Strategy: Leverage the partner focus group to determine strategies to increase engagement and feedback Target Timeline: By 12/31/2026, gather feedback from partners By 12/31/2027, design and implement strategy By 12/31/2028, re-assess and adjust as necessary
Quarterly Update of Public Safety Partner Contact Information | Current updates require SDG&E staff to proactively reach out to update Public Safety Partner contact information at a regularly scheduled interval. This does not capture dynamic changes outside of that schedule. | Strategy: Add contact information self-service functionality in the Public Safety Partner Portal so that partners can update their information in real time. Target Timeline: By 12/31/2026, add resource card in Partner Portal with a contact information survey and create business process to leverage survey responses for regular updates. Design self-serve functionality for Partner Portal By 12/31/2027, implement and release self-service functionality to Public Safety Partner contacts By 12/31/2028, re-asses and adjust as necessary

## OEIS Table 11-5
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
2-1-1 San Diego | CEADPP | 2024 version (April 2024) | Wildfire/PSPS protocols feedback and review
2-1-1 Orange County | CEADPP | 2024 version (April 2024) | Wildfire/PSPS protocols feedback and review
CAL FIRE | CEADPP | 2024 version (April 2024) | Wildfire/PSPS protocols feedback and review
County OES | CEADPP | 2024 version (April 2024) | Wildfire/PSPS protocols feedback and review
Cal OES | CEADPP | 2024 version (April 2024) | Wildfire/PSPS protocols feedback and review
San Diego County | CEADPP | 2024 version (April 2024) | Wildfire/PSPS protocols feedback and review
American Red Cross | CEADPP | 2024 version (April 2024) | Wildfire/PSPS protocols feedback and review
211 San Diego | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
Cal OES Office of Tribal Coordination | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
CAL FIRE | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
California Governor's Office of Emergency Services | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
California Public Utilities Commission | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
City of San Diego | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
County of San Diego OES | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
County of San Diego | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
CPUC | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
Metropolitan Water District of Southern California | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
Port of San Diego Harbor Police | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
Rainbow Municipal Water District | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
San Diego Community Power | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
San Diego County Fire Prot. District | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
San Diego County OES | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
San Diego Sheriff's Department | Wildfire Preparedness | 2024 version (June 2024) | Wildfire Preparedness and Resiliency Workshop
All local government, tribal, and public safety partners invited | Wildfire Preparedness and Resiliency | 2024-06-24 | PSPS Preparedness & Wildfire Safety Workshop
Representatives from local government, tribal, and public safety partners | Wildfire Preparedness | As scheduled | EOC Tours

## OEIS Table 11-6
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
No current gaps or limitations noted in collaboration efforts with local and regional partners on local wildfire planning efforts. | n/a | n/a

## OEIS Table 11-7
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Mesa Grande | Wildfire Preparedness and Resiliency | Tribal Events – 3/2024; 7/2024; 11/2024 | Held listening sessions on Tribal priorities, provided overview of undergrounding project on Circuit 222, received feedback on CAVA, held low-income workshops, and held a Customer Resiliency Solutions townhall.
Iipay Nation of Santa Ysabel - | Wildfire Preparedness and Resiliency | Tribal Events - 01/2024; 2/2024;4/2024; 6/2024;9/2024; 11/2024 | Held listening sessions on Tribal priorities, provided overview of undergrounding project on Circuit 220, received feedback on CAVA, discussed undergrounding colocation with Caltrans, discussed Department of Energy resiliency grant, and participated in Earth Day Fair, co-sponsored Safety Fair.
Jamul Indian Village | Emergency Preparedness | Tribal Events – 03/2024; 5/2024 | Held listening session on Tribal priorities, reviewed Tribal Emergency Response, provided customer resiliency collateral, and participated in Earth Day Fair.
La Posta | Wildfire Preparedness and Resiliency | Tribal Events – 02/2024; 3/2024;5/2024; 10/2024 | Held listening session on Tribal priorities, participated in Earth Day Fair, provided update of undergrounding project on Circuit 1215, and reviewed feedback on PSPS activation.
Pala | Wildfire Resiliency | Tribal Events – 04/2024; 7/2024; 8/2024; 11/2024 | Held meet and greet listening session on Tribal priorities and received feedback on CAVA.
Rincon | Community Outreach | Tribal Events – 01/2024; 2/2024; 3/2024; 4/2024; 5/2024; 6/2024; 7/2024; 8/2024; 10/2024; 11/2024; 12/2024 | Provided overview of undergrounding project on Circuit 990, discussed interconnection projects, delivered microgrid incentive program information, reviewed feedback on PSPS activation, and participated in career fair.
San Pasqual | Wildfire Resiliency | Tribal Events – 05/2024; 6/2024; 8/2024; 10/2024 | Provided overview of undergrounding project on Circuit 1030, discussed undergrounding colocation with ATT, and addressed cultural resources and access protocols issues.
Campo | Wildfire Preparedness and Resiliency | Tribal Events – 01/2024; 2/2024; 3/2024; 4/2024; 5/2024; 6/2024; 7/2024; 8/2024; 9/2024; 10/2024; 11/2024 | Participated in Campo Earth Day, delivered microgrid incentive program information, discussed undergrounding colocation, provided overview of undergrounding project circuit 1215, and participated in Healthy Families and Community Fair.
Ewiiaaiipyaap | Wildfire Resiliency | Tribal Events - 01/2024 | Provided overview of undergrounding project on Circuit 358.
Pauma | Wildfire Preparedness and Resiliency | Tribal Events - 01/2024; 4/2024; 7/2024; 8/2024 | Participated in Community Police Night Out Event, addressed cultural and access protocols, provided a grant to the fire department, and delivered customer resiliency informational items.
La Jolla | Wildfire Preparedness and Resiliency | Tribal Events - 01/2024; 5/2024; 7/2024 | Delivered microgrid incentive program information, held a listening session, participated in community event, and participated in Earth Day Fair.
Los Coyotes | Wildfire Preparedness and Resiliency | Tribal Events - 3/2024; 5/2024; 11/2024 | Held education session on vegetation management access protocols, sponsored tree planting event, and provided overview of undergrounding project on Circuit 210.
Barona | Wildfire Resiliency | Tribal Events - 3/2024; 7/2024 | Participated in Healthy Families event and other listening sessions.
Viejas | Wildfire Preparedness and Resiliency | Tribal Events - 5/2024 | Participated in Earth Day Fair and provided update of undergrounding project on Circuit 358.
Manzanita | Wildfire Preparedness and Resiliency | Tribal Events - 01/2024; 2/2024; 3/2024; 8/2024; 12/2024 | Provided update of undergrounding project on Circuit 215 update, addressed cultural and access protocols, participated in Healthy Family Events, and participated in Earth Day Fair.
Southern California Tribes | Wildfire Preparedness | Tribal Events – 3/2024; 5/2024; 6/2024; 7/2024; 9/2024; 11/2024; 12/2024 | Participated quarterly in Southern California Tribal Emergency Managers Meeting and participated and facilitated focus group sessions with Inter-Tribal Long Term Recovery foundation Resiliency Breakfast and SDG&E Workshop.

## OEIS Table 11-8
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
Trust of outside entities | There is little to no trust for SDG&E | Strategy: Provide cultural competency training and stress reciprocity to internal business. Target timeline: Execute first training by Q3 of 2026.
Limited participation from Tribes on wildfire and PSPS plans and support services | Low Tribal participation in annual workshops and tours | Strategy: Continue to offer in person and virtual workshops and continue to conduct annual survey. Participate in planned Tribal events, and offer mini grants. Target timeline: Annual survey was implemented in 2025. Begin participation in Tribal events in 2026.
Limited funding for Tribal projects | Because Tribes are often dependent on grant funding, Tribes with fewer resources struggle to provide basic needs to their members. | Strategy: Fund partial time for an SDG&E liaison position within Tribal governments of under resourced Tribes. Target timeline: Next GRC cycle.

## OEIS Table 11-9
Stakeholder Group/ Target Community | Event Type | Method(s) for Communicating | Means to Verify Message Receipt | Interests or Concerns Before, During, and After Wildfire and PSPS events
General public | Wildfire | CNS system (text, voice message, and email), website updates, PSPS app, SDG&E Today | CNS message confirmation tracking, web traffic tracking, and app downloads/performance. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
General public | Wildfire-related outage | CNS system (text, voice message, and email), website updates, PSPS app, SDG&E Today | CNS message confirmation tracking, web traffic tracking, and app downloads/performance. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
General public | PSPS-related de-energization | CNS system (text, voice message, and email), website updates, PSPS app, SDG&E Today | CNS message confirmation tracking, web traffic tracking, and app downloads/performance. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
General public | Restoration of service | CNS system (text, voice message, and email), website updates, PSPS app, SDG&E Today | CNS message confirmation tracking, web traffic tracking, and app downloads/performance. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
Priority essential services | Wildfire | Emails, plus access to website updates, PSPS app, PSP app, and SDG&E NewsCenter | Email delivery confirmations, updating for any that come back unsent. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
Priority essential services | Wildfire-related outage | Emails, plus access to website updates, PSPS app, PSP app, and SDG&E NewsCenter | Email delivery confirmations, updating for any that come back unsent. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
Priority essential services | PSPS-related de-energization | Emails, plus access to website updates, PSPS app, PSP app, and SDG&E NewsCenter | Email delivery confirmations, updating for any that come back unsent. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
Priority essential services | Restoration of service | Emails, plus access to website updates, PSPS app, PSP app, and SDG&E NewsCenter | Email delivery confirmations, updating for any that come back unsent. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
AFN populations | Wildfire, wildfire-related outage, PSPS-related de-energization, restoration of service | CNS system (text, voice message, and email), website updates, PSPS app, SDG&E Today | CNS message confirmation tracking, web traffic tracking, and app downloads/performance. If no reply is given, house visits could be performed. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
Non-English speakers | Wildfire, wildfire-related outage, PSPS-related de-energization, restoration of service | CNS system (text, voice message, and email), website updates, PSPS app, SDG&E Today | CNS message confirmation tracking, web traffic tracking, and app downloads/performance. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.
Tribes | Wildfire, wildfire-related outage, PSPS-related de-energization, restoration of service | CNS system (text, voice message, and email), website updates, PSPS app, SDG&E Today | CNS message confirmation tracking, web traffic tracking, and app downloads/performance. | Awareness of a current wildfire, scope of impacted communities, current status and areas threatened, available resources, and ongoing updates until wildfire is contained.

## OEIS Table 11-10
Target Community | Interests or Concerns Before, During, and After Wildfire and PSPS events
Non-English speakers | Limited access to understand electrical corporation wildfire hazards and risks, specific actions that can be taken to reduce risk, and awareness of emergency services and resources.
People in remote or isolated areas | Limited access to resources such as transportation and/or the ability to receive emergency notifications, specific actions that can be taken to reduce risk, and awareness of emergency services and resources.
Elderly (Seniors 62+) | Impaired physical mobility, diminished sensory awareness, chronic health conditions, and/or social and economic limitations that interfere with the ability to prepare for, react to, and recover from a wildfire or a PSPS activation.
People with limited technology | Limited and/or no access to emergency notifications and limited understanding of electrical corporation wildfire hazards and risks, specific actions that can be taken to reduce risk, and awareness of emergency services and resources.
Customers enrolled in utility program: CARE, FERA, MBL, including Life Support (Critical Care) | Accuracy of self-certification status renewal to support accurate and timely emergency notifications are received.
Customer with disabilities | Providing education on resources available to further support customers who have mobility, hearing, learning, or seeing disabilities these customers during an emergency.
Customers who receive their bill in an alternate format (e.g., Braille, large print) | Limited ability to digest educational material, collateral, and emergency notifications if not presented in an alternate format.
Customers who self-identify as AFN or an individual with AFN in the household | Limited ability to understand the requirements and limited knowledge of the self-identification process.
Tribal members | Difficult to reach due to diversity – some live on reservations, some off, some are a part of federally recognized tribes and others are not. Increased risk due to their location in remote and/or HFTD areas with limited access to broadband, limited technology, health disparities, and impacted by socioeconomic factors.
Website information | Maintaining current information on the website to serve as a repository for wildfire safety resources for customers. It also provides information on PSPS activations, wildfire safety projects, emergency preparedness, Community Resource Centers (CRCs) and more.
PSPS Mobile App | Providing real -time alerts and updates in English and Spanish on a PSPS activation for up to five addresses. Information includes customized notifications, CRC information with GPS directions, and other real-time updates and safety information related to PSPS activities.
Public Safety Partner Mobile App | Updating regional public safety partners via the Public Safety Partner mobile app to allow them to access the Public Safety Portal from the field on their mobile devices. Features include real-time map information linked to a secure GIS portal, the ability for partners to follow the PSPS activation status of one or more jurisdictions of their choice, customized push notifications, sectionalizing devices listed by community, and a resource page that includes a social media tool kit, point of contact information, and community flyers.
SDG&E Alexa Skill | Providing real-time updates and information via Alexa skill on weather forecasts, RFWs, the FPI, air quality, the potential for a PSPS activation, and where to find resources about a PSPS activation, as well as flex alerts.
Media Engagement | Establishing partnerships with local broadcast and print media continue to inform customers of proactive safety and preparedness outreach prior to, during, and after a PSPS activation or wildfire. Local broadcast and print media, including designated emergency broadcast radio, amplify messaging during a wildfire or PSPS activation. Press updates are also posted to SDGENews.com and on social media channels.
PSPS Paid Campaign | Informing customers via the PSPS Paid Campaign of the latest technology advancements to further refine the decision-making required when activating a PSPS protocols. Providing tips and available resources during a PSPS activation on what to expect during a PSPS activation, and where to go to receive support services is available. Sharing communication tools including social media, local community social media pages, print, digital and outdoor advertising, wildfire Safety Fairs, in-Community events, in-Community newsletters, newspapers; community bulletins/ posters, community stores, supermarkets, laundromats, barber shops, airport, train and bus depot video monitor messaging, athletic event/stadium ads, local broadcast media and journalist education, message amplification by CBOs, and power outage and preparedness videos.

## OEIS Table 11-11
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Customer/Public Wildfire/PSPS Notifications/Communications Comprehension | Improving our customers retention and comprehension of communications and messaging during a PSPS activation or related emergency event. | Strategy: Continue to conduct annual surveys as required and use feedback to improve communications and messaging for the following year. This includes Public Education efforts, customer notification content and customer/public messaging during PSPS activations. Target timeline: Annually
Customer understanding of support services during PSPS de-energizations vs. planned outages | Customers sometimes contact PSPS AFN support partners looking for assistance during a planned outage, especially if it occurs near a PSPS activation. | Strategy: Continue to provide education on what support services are offered for PSPS de-energizations and notify the customer contact center when a customer is inaccurately referred to an AFN Support Partner. Target timeline: Ongoing
Updating current customer contact information | This is a constant effort to retain updated contact information for customers. | Strategy: SDG&E will continue to utilize the call to action of updating contact information, signing up for PSPS notifications and downloading the Alerts by SDG&E app to receive notifications and updates about PSPS de-energizations. Additionally, the company will explore additional opportunities to solicit and retain updated customer contact information. Target timeline: Ongoing

## OEIS Table 12-1
Initiative | Qualitative or Quantitative Target | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | 2026 End of Year Total/Completion Date | 2027 Total/Status | 2028 Total/Status | Section; Page Number
Asset Management and Inspection Enterprise System | Qualitative | Asset Management and Inspection Enterprise System-Utilize advanced technology and analytics - including integrating Asset 360 and IIP data - to develop, enhance, expand risk-informed strategies, and enhance transparency for asset management (WMP.1457) | n/a | By 12/31/2026, integrate advanced technology and analytics, including Asset 360 and IIP data, to develop risk-informed strategies for asset management. | By 12/31/2027, continue enhancing and expanding these risk-informed strategies to improve transparency and efficiency in asset management. | By 12/31/2028, continue enhancing and expanding these risk-informed strategies to improve transparency and efficiency in asset management. | Section 8.3; p. 152
Vegetation Management Enterprise System | Qualitative | Vegetation Management Enterprise System-Enhance asset tracking, data analytics, and scheduling capabilities to more effectively manage and support Vegetation Management activities. (WMP.511) | n/a | By mid-2026: Integrate historical meteorology data (e.g., wind gust) into PowerWorkz field application ("Epoch") as a GIS visualization tool for improved field situational awareness and decision-making. By 12/31/26: Complete update of new version of Powerworkz desktop work management application ("Cityworks") to enhance work order management and vegetation management activity scheduling. | By mid-2027: Complete migration of all vegetation management data into AWS and the Cloud. By 12/31/27: Replace all current SSRS reporting with AWS-reporting capabilities and dashboarding to track, manage, and report on all vegetation management activity status. | By mid-2028: Move from a Mobile Data Platform hardware tool used for data collection to a newer and more functional tool such as I-Pad to improve efficiency, functionality, and worker safety. By 12/31/28: Integrate data modeling and predictive analytics to improve vegetation mangement activity scheduling, risk management, project scoping, etc. | Section 9; p. 208
Vegetation Management Enterprise System-Advanced Analytics | Qualitative | Vegetation Management Enterprise System-Advanced Analytics-Advanced analytics for proactive vegetation inspection (WMP.1464) | n/a | By mid-2026: Complete and test v.2.0 of the Probability of Vegetation Contact model. Focus on model tuning and testing – including field-validation surveys with vegetation management subject matter experts. By 12/31/2026: Test v.1.0 of the Probability of Hazard model. Focus on model tuning and testing – including field-validation surveys with vegetation management subject matter experts. By 12/31/2026: Complete phase I of Vegetation Management data migration from PowerWorkz-Oracle to AWS. | By early 2027: Begin AWS data-product developments (phase II) to streamline operational analytics, reporting, and future model developments. By mid-2027: Begin design and exploratory data analysis for a Vegetation Growth model. By 12/31/2027: Conduct proof-of-concept study(ies) with applicable vendor(s) to better understand the efficacy of remote sensing technologies for identifying non-compliant vegetation. | By early 2028: Complete v.1.0 of data-product developments and integrate with existing models and reporting systems where applicable. By 12/31/2028: Where applicable, continue investigating and/or begin implementing remote sensing technologies identified during proof of concept study(ies) in 2027. By 12/31/2028: Test/utilize risk models to develop indices for prioritizing and conducting targeted Off-Cycle Patrols. | Section 9; p. 208
Enterprise Data Foundation | Qualitative | Enterprise Data Foundation-Migrate data from on-premise to the AWS Cloud (WMP.519) | n/a | By 12/31/2026: Establish data migration patterns, successfully migrate data sets including grid hardening, assets, and PSPS/risk events, and implement data validation, integrity, and governance processes to ensure quality and integrity throughout the migration journey. | By 12/31/2027: Execute data integration from the upgraded SAP S/4 HANA platform for ERP, transitioning from the legacy SAP ECC system. Additionally, implement data ingestion processes for the new Transmission SAP S/4 HANA system while maintaining enterprise data quality standards. | By 12/31/2028: Integrate and ingest critical data from all newly implemented systems across the organization. This initiative will include establishing data pipelines, security protocols, and ETL processes. The integration will prioritize data quality and system compatibility while maintaining compliance standards. | Section 12; p. 325
Risk Methodology and Assessment | Qualitative | Risk Assessment Systems - Enhance WiNGS Visualization Platform (WMP.442) | n/a | By 12/31/2026: Continue enhancing the visualization platform to facilitate quick and easy access to reliable data to inform de-energization and mitigation investment planning decisions, faster initial loads and overall stability of the platform. Identify potential enhancements for existing features to elevate user experience and facilitate efficient risk information transfer. | By 12/31/2027: Continue to integrate and deploy additional enhancements, bug fixes and features. Explore and expand additional use cases for risk modeling and visualization platform. | By 12/31/2028: Continue regular meetings with internal subject matter experts, visualization developers, and platform users to ensure the precision of displayed data and effective visualizations as well as pinpoint areas for improvement. Explore and expand additional use cases for risk modeling and visualization platform. | Section 5.7; p. 78
Weather Forecasting | Qualitative | See FPI (WMP.450) | n/a | See OEIS Table 10-1 | See OEIS Table 10-1 | See OEIS Table 10-1 | Section 10.5; p. 237
Grid Monitoring | Qualitative | Data Integration (WMP.1444) | n/a | See OEIS Table 10-1 | See OEIS Table 10-1 | See OEIS Table 10-1 | Section 10.1; p. 237
Ignition Detection | Qualitative | Ignition Detection Systems - Cameras(WMP.1343) | n/a | See OEIS Table 10-1 | See OEIS Table 10-1 | See OEIS Table 10-1 | Section 10.1; p. 237

## OEIS Table 13-1
ID # | Year of Lesson Learned | Subject | Category and Source of Lesson Learned | Description of Lesson Learned | Proposed WMP Improvement | Timeline for Implementation | Reference
1 | 2024 | Double Down Initiative PSPS | Outcome From Previous WMP Cycles PSPS | Proactive, risk-informed corrective maintenance can potentially reduce scope of PSPS activations. | Risk-informed prioritization of CMP corrective work prior to San Diego's Santa Ana wind season. Implement prioritization for pole loading calculation related findings (utilization & clearance infractions) with Electric Distribution Engineering | 2025-2028 | n/a
2 | 2024 | Double Down Initiative | Outcome From Previous WMP Cycles | Notify field users and corporate security of potential hazards and customer warnings before approaching private property. | Enable GeoCall to allow field users to enter data on customer and property restrictions, and identify on GIS/maps in real time. | 2025-2028 | n/a
3 | 2024 | Double Down Initiative | Outcome From Previous WMP Cycles | Establish a process to identify, review, and maintain distribution access roads that need maintenance​. | Prioritize access roads to devices on circuits that are frequently de-energized for PSPS to help reduce the time it takes to patrol​, and develop dashboard for districts to submit and review status of projects. | 2025-2028 | n/a
4 | 2024 | PSPS | Nov 6-8, 2024 PSPS Activation | Data refresh rates between GIS and the Customer Notification System resulted in inconsistent customer data | A focus team has been created to resolve the issue. | 2025-2027 | PSPS Post-Event Report - Nov 6-8, 2024
5 | 2024 | PSPS | PSPS After Action Report (AAR) | Identified areas of improvement for the Customer Notification System, which includes ability to create customer lists based on switching plans and other real-time changes to support re-energization. | Identify requirements for improvements and execute projects based on priority, difficulty, and budget. | 2025-2027 | n/a
6 | 2024 | Risk Methodology and Assessment | Dec 2024/Jan 2025 PSPS Activations Areas for Continuous Improvement | As more end users gain access and are using the WiNGS visualization tools, there is an opportunity to improve user experience as well as the timeliness and consistency of the data refresh. | Provide easy and quick access to reliable data and provide an optimized user interface to inform decision making. | Ongoing | OEIS Table 5-6 ACI SDGE-25U-03
7 | 2022-2024 | Wildfire Mitigation Strategy | Areas for Continuous Improvement | Continue journey of more risk-informed and data-driven decision making. | Incorporate lifecycle cost analysis to explore combined mitigation effectiveness to inform mitigation selection and prioritization. | 2024-2028 | WMP 2026-2028, Section 6 ACI SDGE-23-06
8 | 2022 | Vegetation management and inspections | Collaboration with other IOUs Areas for Continuous Improvement | Continue analysis of enhanced clearance research to inform updated forecasts and program scope. | Refine scope of enhanced clearances. | 2023-2028 | Section 9.2 ACI SDGE-25U-09
9 | 2024 | Land Rights and Permits | Feedback from Government Agencies | Agency approval is needed before advancing to design phase for agency projects. | Process was updated to hold projects at 60 percent design, instead of advancing to 100 percent of the design through the QA and approval process. By holding the project at the 60 percent design milestone, a higher level of engagement can be achieved during any design revisions. | Ongoing | n/a
10 | 2024 | Land Rights and Permits | Feedback from Government Agencies | Certain agencies have complex or restrictive design criteria. Incorporating agency approval criteria into internal design guidelines will streamline the approval process. | Agency approval criteria should be identified and included in the Design Preference Guideline (DPG). | Ongoing | n/a
11 | 2024 | Land Rights and Permits | Feedback from Government Agencies | Stronger relationships with agency representatives may help mitigate some rejections and re-submittals. | Develop relationships with agency staff. Increasing time and effort up front to create these relationships allows for a greater depth of communication. Instead of rejecting a submittal, which would lead to revisions and re-submittal, agency staff can call or send messages with questions that can be answered in a timely manner. | Ongoing | n/a
12 | 2024 | Undergrounding | Grid Hardening Working Group | Cultural, Tribal Nation and Environmental Considerations: Early on, the program didn’t realize the challenge and demand required to understand Tribal Nation sensitivities, regulatory requirements, and the need for thorough engagement, which often requires multiple meetings and extended timelines. Without understanding Tribal Nation sensitivities, regulatory requirements, and need for thorough engagement, it’s difficult to complete a 30% design review. | SDG&E collaborates with multiple government agencies such as the County of San Diego, Department of the Interior, Bureau of Indian Affairs, Caltrans, and the U.S. Forest Service, to ensure proper land rights and permits are obtained. | Ongoing | n/a
13 | 2024 | Undergrounding | Grid Hardening Working Group | Data-Management and Technology Integration: Emphasis on systemizing data collection and processing at all levels, including subs and liaisons, to prevent process inefficiencies. Early data collection enables better project management and problem resolution. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
14 | 2024 | Undergrounding | Grid Hardening Working Group | Feedback and Continuous Improvement: Silos within the program hinder collaboration, as not all teams are aware of each other’s work. A shared platform for visibility into all ongoing work would enhance communication and coordination. Programs with funding obligations often require detailed reporting, which could be formalized into a monthly program report for better program wide visibility and documentation. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
15 | 2024 | Undergrounding | Grid Hardening Working Group | Financial Management and Budgeting: A budget funding calculator was introduced to help price projects and assist requestors in understanding costs. The Last Planner System, including planning and scheduling, was used to track survey progress and efficiency. Monthly reports were sent to the team for feedback and improvements. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
16 | 2024 | Undergrounding | Grid Hardening Working Group | Process Improvement and Efficiency: Initially the program was managed as a collection of individual projects, leading to inefficiencies. Each group reviewed and developed deliverables at every stage gate, creating bottlenecks and a lack of collective project tracking. The program transitioned to a streamlined approach by consolidating all disciplines’ deliverables into a single file, improving efficiency. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
17 | 2024 | Undergrounding | Grid Hardening Working Group | Program Governance and Leadership: In person governance workshops brought SDG&E executives and AECOM together, highlighting different ideas and understanding of AECOM global program management and energy utility approaches. These workshops emphasized the importance of governance, planning and alignment. SDGE leadership, demonstrated strong commitment from day one, signaling their intent to do things differently by bringing in AECOM. Their sponsorship and alignment with functional leads were key to program success. Leadership events, such as roundtables, were valuable for fostering alignment and inclusion early in the program. Expanding these roundtables beyond leadership to the entire program team could enhance inclusivity and engagement. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
18 | 2024 | Undergrounding | Grid Hardening Working Group | Risk Management and Planning - Granular Analysis and Root Cause Identification: Analyzing delays at a granular level helps identify patterns (e.g., common owners or encroachments) and predict future risks. Root cause analysis identifies driving factors of risks/delays and informs mitigation plans. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
19 | 2024 | Undergrounding | Grid Hardening Working Group | Safety and Field Operations: The safety team built strong personal relationships with field team members and the construction safety services team by actively engaging in the field. They provided hands-on coaching to promote safer practices and reinforce safe behaviors, fostering a shared understanding of safety expectations. By placing Field Safety Officers on-site, they established a culture of trust, making it clear that the goal was not to catch mistakes but to support contractors in working safely. Additionally, the safety team exceeded SDG&E’s written reporting protocols by following up with team members after reports by phone call, further strengthening relationships and reinforcing their commitment to safety. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
20 | 2024 | Undergrounding | Grid Hardening Working Group | Stakeholder Engagement and Management - Focus Group Meetings: To address challenges with private property owners hesitant to sign easements, focus group meetings were implemented. These meetings included regular participation from program and project management, legal counsel, lands, and land service representatives, and communications to align on and resolve issues that historically caused delays. By bringing the right decision-makers together every two weeks, the team could address new challenges, make decisions in real-time, and avoid delays caused by email bottlenecks. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a
21 | 2024 | Undergrounding | Grid Hardening Working Group | Team Collaboration and Communication: Establishing a partnership with SDG&E involved working alongside them rather than merely beside them, fostering sponsorship and collaborative relationships. Contractor partnerships, such as with NV5, were critical. Building trust and including contractors in conversations led to significant cost savings and strengthened relationships. | Continue to collaborate with Grid Hardening Working Group and our own impact departments to create and implement solutions. | Ongoing | n/a

## OEIS Table 13-2
Discontinued Initiative Activity (Tracking ID) | Rationale for Discontinuation | Lessons Learned | Replacement Activities (include page # where discussed)
Wireless Fault Indicators (WMP.449) | The current wireless fault indicators were discontinued by the manufacturer. These units communicate into On-Ramp, but do not communicate with SCADA, which makes it obsolete as a wireless indicator. Therefore, they are used manually by field personnel as a fault indicator. | SDG&E is exploring alternative technologies and will continue to utilize existing fault indicators to achieve risk reduction. | n/a
Generator Grant Program (WMP.466) | Changes in the product technology and market availability of viable options has changed since the launch of this program, and the same type of customers will be served with resiliency assessments and resources based on evolving technology and availability. | Customers across the high fire threat district have varying degrees of resiliency for potential power outages, and an offering that assesses customer awareness and resource preparedness can better align the appropriate support. | Customized Resiliency Assessments (WMP.1432); Section 8.2.11.3; p. 175
Distribution infrared inspections (WMP.481) | Distribution Infrared Inspections have consistently yielded an extremely low find rate since the program's inception in 2020. See ACI SDGE-25U-08 (Appendix D) for more information. | As discussed in ACI SDGE-25U-08 (Appendix D), alternative technologies and traditional inspection methods can be used to identify the findings that were historically identified through this program. | Distribution Inspections (WMP.478, WMP.488, WMP.552); Section 8.3.1; p. 182; Section 8.3.7; p. 195; Section 8.3.6; p. 191 EFD (WMP.1195); Section 10.3.1; p. 279
Transmission 69 kV Tier 3 Visual Inspections (WMP.555) | The inspection program yielded an extremely low find rate. See Section 8.3.10.2 for more information. | The supplemental program is ineffective and issues can be identified through other inspection programs. | Transmission Inspections (WMP.479, WMP.482, WMP.489); Section 8.3.2; p. 157; Section 8.3.3; p. 159; Section 8.3.8; p. 169 SDG&E continues to perform inspections in advance of PSPS de-energizations and restoration.
Distribution Communications Reliability Improvements (WMP.549) | Due to budget reductions in the GRC, SDG&E has focused its budget on projects that have the greatest impact on risk reduction in the HFTD. The DCRI project, while providing communication for these projects, has a lower impact on risk reduction than other programs. | Through the process of providing Private LTE services, a standard has been developed for Transmission/Distribution sites as well as stand-alone Telecom sites which will allow SDG&E to effectively address these type of telecommunication installations in the future. | Communication needs for the projects funded by WMP will be addressed as those projects are built out, instead of proactively. There is currently no identified replacement for this program to serve these projects.
Community Tree Rebate Program (WMP.1326) | To promote customer affordability and reflect SDG&E’s authorized revenue requirements, the Community Tree Rebate Program has been discontinued. SDG&E also believes it has substantively met the overall goal of the program to engage those customers eligible to participate in the program. The cessation of the program does not negatively impact the company’s risk mitigation measures as the program is not primarily aimed at risk reduction. | This program offered rebate tiering by tree size to encourage the planting of larger tree sizes that would be more likely to thrive. Improvements were made to eligibility criteria to eliminate customer confusion by providing clear qualifications by zip code and a list of pre-selected tree species. A user-friendly application process included clear instructions and the ability to upload photos, which reduced the administrative burden and increased participation. | The Community Tree Rebate Program will not be replaced. See Section 9.3 for additional information on Right Tree, Right Place.