## Table of Contents
Table Number | Table Name
PAC 2-1 | Responsible Persons
3-1 | List of Risks and Risk Drivers to Prioritize
3-2 | Self-Identified Performance Metrics
3-3 | Summary of Projected WMP Expenditures
PAC 3-1 | Table PAC 3-1: PacifiCorp Tracking IDs for the 2026-2028 WMP
4-1 | High-Level Service Territory Components
4-2 | Catastrophic Electrical Corporation Wildfires
4-3 | Frequently Deenergized Circuits
5-1 | Risk Model Assumptions and Limitations
5-2 | Summary of Design Scenarios
5-3 | Extreme-Event Scenarios
5-4 | Summary of Risk Models
5-5 | Summary of Top-Risk Circuits, Segments, or Spans
5-6 | Utility Risk Assessment Improvement Plan
PAC 5-1 | Risk Model Components
PAC 5-2 | FireSight Attributes
PAC 5-3 | Comparison of General Characteristics of Wind-Driven and Fuel/Terrain-Driven Wildfires
PAC 5-4 | Comparison for FireSight Risk Metrics In the HFTD and HFRA at the 95th Percentile
6-1 | List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk
6-2 | Stakeholder Roles and Responsibilities in the Decision-Making Process
6-3 | Risk Impact of Activities
6-4 | Summary of Risk Reduction for Top-Risk Circuits
PAC 6-1 | Summary of Risk Reduction for Circuits With Maximum Fuel/Terrain Wildfire Risk Scores
8-1 | Grid Design, Operation, and Maintenance Targets by Year
8-2 | Asset Inspection Frequency, Method, and Criteria
8-3 | Grid Design, Asset Inspections, and Maintenance QA and QC Program Objectives
8-4 | Grid Design, Asset Inspections, and Maintenance QA and QC Activity Targets
8-5 | Number of Past Due Asset Work Orders Categorized by Age
8-6 | Number of Past Due Asset Work Orders Categorized by Age for Priority Levels
8-7 | Top Ten Impacted Circuits from Changes to PEDS in the Past Three Years
PAC 8-1 | Current ESS Mode Configurations
PAC 8-2 | 2024 Reliability Impacts for Circuits Activated in ESS settings
PAC 8-3 | Suppression Equipment
PAC 8-4 | T&D Operations Based on Fire Risk Potential
PAC 8-5 | Workforce Planning, Grid Hardening
9-1 | Vegetation Management Targets by Year (Non-inspection Targets)
9-2 | Vegetation Inspections and Pole Clearing Targets by Year
9-3 | Vegetation Management Inspection Frequency, Method, and Criteria
9-4 | Partnerships in Vegetation Management
9-5 | Vegetation Management QA and QC Program Objectives
9-6 | Vegetation Management QA and QC Activity Targets
9-7 | Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier
9-8 | Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels
9-9 | Vegetation Management Qualifications and Training
PAC 9-1 | Distribution Minimum Post-Work Vegetation Clearance Distances
PAC 9-2 | Transmission Clearance Requirements
10-1 | Situational Awareness Targets by Year
10-2 | Environmental Monitoring Systems
10-3 | Grid Operation Monitoring Systems
10-4 | Fire Detection Systems Currently Deployed
10-5 | Fire Potential Index Features
PAC 10-1 | Planned Grid Monitoring System Improvements
PAC 10-2 | FireRisk and FireSim Weather Inputs
11-1 | Emergency Preparedness and Community Outreach Targets by Year
11-2 | Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan
11-3 | High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners
11-4 | Example of Key Gaps and Limitations in Communication Coordination with Public Safety Partners
11-5 | Collaboration in Local and Regional Wildfire Mitigation Planning
11-6 | Key Gaps and Limitations in Collaborating on Local and Regional Wildfire Mitigation Planning
11-7 | Collaboration with Tribal Agencies
11-8 | Key Gaps and Limitations in Collaborating with Tribal Agencies
11-9 | Protocols for Emergency Communication to Stakeholder Groups
11-10 | List of Target Communities
11-11 | Key Gaps and Limitations in Public Emergency Communication Strategy
12-1 | Enterprise Systems Targets
13-1 | Lessons Learned
13-2 | Lessons Learned from Discontinued Activities
PAC 13-1 | DFA Use Cases and Results
B-1 | Model Inventory
PAC B-1 | FireSight and WFA-E Model Inputs
PAC B-2 | FireSight Outputs
PAC B-3 | Fire Potential Index Inputs
PAC B-4 | Asset Fire Susceptibility Layers
PAC B-5 | Locational Risk Factors Layers
PAC D-1 | Mapping of 2026-2028 WMP Initaitves and Activities to 2025 Maturity Survey Categories, Capabilities and Subcapabilities
PAC E-1 | Referenced Regulations, Codes, and Standards
PAC F-1 | PacifiCorp Referenced Policies and Standards in the 2026-2028 WMP
PAC G-1 | Other Supporting Documents Referenced in the 2026-2028 WMP

## PAC 2-1
Table PAC 2-2: Responsible Persons
Name | Title | Contact Information | Component(s)
Joshua Jones | Vice President, Asset Management and Wildfire | Email: Joshua.jones@pacificorp.com | Executive Level Owner with Overall Responsibility
Phone: 801-220-4212
Melissa Swenson | Director, Wildfire Mitigation Program Delivery | Email: Melissa.swenson@pacificorp.com | Sections 1, 2, 3-3.3, 3.5, 3.6, 4-4.2, 6, 6.2, 6.2.2, 8.1-8.1.2, 13-13.3, Appendix C, Appendix D, Appendix F, Appendix G, PC-25U-11
Phone: 503 320-8941
Aaron Hickey | Director, Field Ops/Distribution | Email: Aaron.hickey@pacificorp.com | Sections 8.7.3, 8.7.4
Phone: 971-242-6209
Alex Vaz | Director, Asset Investment Strategy and Policy | Email: Alex.vaz@pacificorp.com | Sections 6.1-6.1.2
Phone: 801-220-2112
Amanada Lindsey | Director, Business Operations | Email: Amanada.lindsey@pacificorp.com | Sections 12-12.2, ACI PC-25U-08
Phone: 503-813-5346
Carrie Laird | Managing Director, Power Delivery Support | Email: Carrie.laird@pacificorp.com | Sections 10-10.2.4, 10.5-10.6.3
Phone: 503-813-5409
Eddie Summit | Director, Asset Maintenance and Compliance | Email: Eddie.summit@pacificorp.com | Sections 8.3.4
Phone: 801-220-4010
Hallie Frazee | Wildfire Mitigation Communications Program | Email: Hallie.frazee@pacificorp.com | Sections 11.4-11.4.3, 11.4.5, 11.4.6, 11.5
Phone: 503-813-5590
Jon Connelly | Director, Real Time Grid Engineering | Email: Jonathan.connelly@pacificorp.com | Sections 8.4, 8.7, 8.7.1,8.7.2,10.3,10.3.1, Table 8-7, ACIs PC-25U-09, PC-23B-20
Phone: 503-813-6152
Jon Moulton | Managing Director, Asset Management | Email: Jonathan.moulton@pacificorp.com | Sections 8.3-8.3.3, 8.3.5-8.3.7, 8.5-8.5.7, 8.6, ACIs PC-25U-06, PC-25U-07,
Phone: 801-220-2360
Josh Hooley | Director, Vegetation | Email: Josh.Hooley@pacificorp.com | Sections 9-9.5.4, 9.7-9.13.2, ACI PC-23B-16
Phone: 541-955-7941
Kevin Benson | Managing Director, Asset Risk and Performance | Email: Kevin.benson@pacificorp.com | Sections 3.4, 4.3, 5-5.7, 6.2.1, Appendix B, ACIs PC-25-01,
|  | Phone: (541) 213-1990 | PC-23B-02, PC-25U-02, PC-25U-03, PC-25U-04, PC-25U-05, PC-25U-03
Kevin Schiedler | Wildfire Mitigation Delivery Director | Email: Kevin.Schiedler@pacificorp.com | Sections 6.2.1.3, 8.28.2.13
Phone:503-813-5595
Megan Buckner | Director, Wildfire Mitigation Program Delivery | Email: megan.buckner@pacificorp.com | Sections 6.1.3, 10.4-10.4.4
Phone: 503-813-5209
Elenore Yotsov | Director of Emergency Management | Email: Elenore.yotsov@pacificorp.com | Sections 7, 11-11.3.3, 11.4.4
Phone: (503) 319-6819
Pooja Kishore | State Regulatory Affairs Manager | Email: Pooja.kishore@pacificorp.com | Appendix E
Phone: 503-813-7314
Rohit Nair | Managing Director, T & D Innovation and Strategy | Email: Rohit.nair@pacificorp.com | Sections 10.3.2-10.3.4
Phone: 801-220-4352
Stephanie Beall | Director, Meteorology | Email: Stephanie.beall@pacificorp.com | Section 3.7
Phone: 385-515-1232
Tim Barry | Director, Field Ops/Substation | Email: Timothy.barry@pacificorp.com | Sections 9.6-9.6.4
Phone: 541-776-5481
Tom Eide | Vice President, Operations | Email: Thomas.eide@pacificorp.com | ACI PC-25U-10
Phone: 541-776-5467
Return to Table of Contents

## 3-1
Table 3-1: List of Risks and Risk Drivers to Prioritize
Priority | Risk | Risk Driver | x% of ignitions in HFTD | Topographical and Climatological Risk Factors
1 | Unknown | Unknown | 23.81% | Unknown
2 | Vegetation Contact | Outside Clearance Zone | 14.29% | Wind-Driven Risk Fuel/Terrain Driven Risk
3 | Fire | Fire | 14.29% | Wind-Driven Risk Fuel/Terrain Driven Risk
4 | Contact from object | Unknown | 0% | Not Tracked
5 | Equipment / facility failure or damage | Degradation-Line Element | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
6 | Equipment / facility failure or damage | Degradation-Protective/Control Device | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
7 | Equipment / facility failure or damage | Equipment Error-Line Element | 9.52% | Wind-Driven Risk Fuel/Terrain Driven Risk
8 | Other | Other | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
9 | Equipment / facility failure or damage | Transformer | 0% | Not Tracked
10 | Contact from object | Foreign Contact-Land vehicle contact | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
11 | Equipment / facility failure or damage | Cutout | 0% | Not Tracked
12 | Equipment / facility failure or damage | Connector device | 0% | Not Tracked
13 | Contact from object | Other contact from object | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
14 | Contamination | Contamination | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
15 | Equipment / facility failure or damage | Equipment Error-Other | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
16 | Equipment / facility failure or damage | Other - Unknown | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
17 | Equipment / facility failure or damage | Equipment Error-Protective/Control Device | 4.76% | Wind-Driven Risk Fuel/Terrain Driven Risk
18 | Contact from Object | Bird | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
19 | Equipment / facility failure or damage | Fuse | 0% | Not Tracked
20 | Lightning | Lightning | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
21 | Equipment / facility failure or damage | Degradation-Other | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
22 | Equipment / facility failure or damage | Conductor | 0% | Not Tracked
23 | Equipment / facility failure or damage | Other-Other | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
24 | Wire-to-wire contact | Wire-to-wire contact | 0% | Not Tracked
25 | Contact from Object | Animal Contact | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
26 | Equipment / facility failure or damage | Insulator and bushing | 0% | Not Tracked
27 | Other | Utility Error/Other | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
28 | Vegetation Contact | Within Clearance Zone (right-of-way) | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
29 | Equipment / facility failure or damage | Cross arm | 0% | Not Tracked
30 | Vandalism/ theft | Vandalism/ theft | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
31 | Equipment / facility failure or damage | Degradation-Structural Elements | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
32 | Protective device operation | Protective device operation | 0% | Not Tracked
33 | Equipment / facility failure or damage | Voltage regulator /booster | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
34 | Contact from Object | Third-party contact | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
35 | Equipment / facility failure or damage | Lightning arrestor | 0% | Not Tracked
36 | Equipment / facility failure or damage | Degradation-Voltage Control | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
37 | Dig-in | Dig-in | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
38 | Equipment / facility failure or damage | Splice | 0% | Not Tracked
39 | Equipment / facility failure or damage | Pole | 0% | Not Tracked
40 | Equipment / facility failure or damage | Equipment Error-Unknown | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Other-Structural Elements | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Equipment Error-Structural Elements | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Environmental-Protective/Control Device | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Environmental-Structural Elements | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Other-Line Element | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Environmental-Line Element | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Degradation-Unknown | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Environmental-Other | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Emergency Repairs | Emergency Repairs | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Contact from Object | Aircraft Vehicle contact | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Contact from Object | Balloon contact | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Customer Request | Customer Request | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Environmental-Unknown | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Other-Protective/Control Device | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Anchor/guy | 0% | Not Tracked
40 | Equipment / facility failure or damage | Capacitor bank | 0% | Not Tracked
40 | Vegetation Contact | Other | 0% | Wind-Driven Risk Fuel/Terrain Driven Risk
40 | Equipment / facility failure or damage | Sectionalizer | 0% | Not Tracked
40 | Equipment / facility failure or damage | Switch | 0% | Not Tracked
40 | Equipment / facility failure or damage | Relay | 0% | Not Tracked
40 | Equipment / facility failure or damage | Recloser | 0% | Not Tracked
40 | Equipment / facility failure or damage | Tie wire | 0% | Not Tracked
40 | Equipment / facility failure or damage | Tap | 0% | Not Tracked
40 | Vegetation contact | Blow-in | 0% | Not Tracked
40 | Equipment / facility failure or damage | Unknown | 0% | Not Tracked
40 | Vegetation contact | Fall in (branch failure) | 0% | Not Tracked
40 | Vegetation contact | Fall in (root failure) | 0% | Not Tracked
40 | Vegetation contact | Fall in (trunk failure) | 0% | Not Tracked
40 | Vegetation contact | Grow-in | 0% | Not Tracked
Return to Table of Contents

## 3-2
Table 3-2: Self-Identified Performance Metrics
Performance Metric | Assumption that underlies the use of the metric | Section associated with the Performance Metric (state “WMP” if the metric applies to entire plan)
PSPS Customer Minutes Interrupted | This metric helps the Company understand the Customer exposure to PSPS as mitigations are implemented . This metric will be annualized. | WMP
PSPS Events | This metric helps the Company understand if there are changes in PSPS as mitigations designed to reduce the frequency of them are implemented . This metric will be annualized. | WMP
Enhanced Safety Settings (ESS) (PEDS) Customer Minutes Interrupted | This metric helps the Company understand the Customer exposure to ESS as mitigations are implemented. This metric will be annualized. | WMP
Risk Events | Total number of risk events that is presented in Table 3 of the Quarterly Data Reporting (QDR). | WMP
Ignition Events | Total number of risk events that is presented in Table 3 of the Quarterly Data Reporting (QDR) and the data source is outage reporting system in which outage refers to fire in comment or outage cause . Assumption is that with mitigation activities described in the WMP, the number of ignition events will decrease. This metric will be annualized | WMP
Equipment Inspection Findings | With regular equipment inspections, over time PacifiCorp expects to see a decrease in findings of conditions that could cause and energy release risk. This will be annualized. | 8.3
Return to Table of Contents

## 3-3
Table 3-3: Summary of WMP Projected Expenditures
Year | Spend (thousand $USD)
2026 | 187648
2027 | 183115
2027 | 183905
Return to Table of Contents

## PAC 3-1
Table PAC 3-1: PacifiCorp Tracking IDs for the 2026-2028 WMP
Initiative Tracking ID | Initiative/ Program
AI-01 | Transmission Patrol Inspections
AI-02 | Distribution Patrol Inspections
AI-03 | Transmission Detail Inspections
AI-04 | Distribution Detail Inspections
AI-05 | Transmission Intrusive Pole Inspections
AI-06 | Distribution Intrusive Pole Inspections
AI-07 | Enhanced IR Inspections on Transmission Lines
AI-08 | Enhanced IR Inspections on Distribution Lines
AI-09 | Transmission Drone Inspections
AI-10 | Distribution Drone Inspections
AI-11 | Substation Inspections
AI-12 | Quality Assurance / Quality Control (Asset Inspections)
AI-13 | Work Orders (Asset Management)
AI-14 | Transmission Patrol Inspections QA/QC
AI-15 | Distribution Patrol Inspections QA/QC
AI-16 | Transmission Detailed Inspections QA/QC
AI-17 | Distribution Detailed Inspections QA/QC
AI-18 | Transmission Intrusive Inspections QA/QC
AI-19 | Distribution Intrusive Inspections QA/QC
CO-01 | Public Outreach and Education Awareness Program
CO-02 | Engagement with Access and Functional Needs Populations
CO-03 | Collaboration on Local Wildfire Mitigation Planning Develop and update wildfire de-energization materials for customers to communicate PacifiCorp Emergency De-Energization for Wildfire.
CO-04 | Best Practice Sharing with Other Utilities
CO-05 | Conduct pre-season and post-season customer surveys to assess understanding of messaging and information shared by PacifiCorp and inform adjustments in messaging
CO-06 | Create a way for non-account holders to register for outage/emergency alerts
CO-07 | Continue to identify customers who are Electricity Dependent
CO-08 | Coordinate and integrate resources with state, community and utility to minimize duplication of AFN programs
CO-09 | Identify enhancements to programs and resources needed to mitigate the impacts of PSPS on AFN customers
CO-10 | Increase awareness of PacifiCorp's programs and services available for AFN customers before, during and after a PSPS
EP-01 | Emergency Preparedness Plan
EP-02 | External Collaboration and Coordination
EP-03 | Public Emergency Communication Strategy
EP-05 | Customer Support in Wildfire and PSPS Emergencies
ES-01 | Enterprise Systems Development
ES-02 | Business Transformation Wave 4: Maximo
ES-03 | Data Integration (Foundry)
ES-04 | Distributed Sensor Operation Insights and Analytics
ES-05 | Implement new vegetation management work management software
ES-06 | Quality Assurance/Quality Control: Create QA/QC process and procedure for reviewing data in the Vegetation Management database (Quality Reviews)
ES-07 | Vegetation Management and Inspections: Develop work prioritization to incorporate within [Mobile Data Management System (MDMS)]
GH-01 | Line Rebuild - Covered Conductor Installation
GH-02 | Distribution Pole Replacements and Reinforcements
GH-03 | Transmission Pole/Tower Replacements and Reinforcements
GH-04 | Installation of System Automation Equipment
GH-05 | Expulsion Fuse Replacement
GH-12 | Microgrids
GH-13 | Line Removals (in HFTD)
GH-14 | Workforce Planning (Grid Hardening)
GH-15 | Pole Wraps
GH-16 | Undergrounding of electric lines and/or equipment
GO-01 | Equipment Settings to Reduce Wildfire Risk (Grid Ops): ESS and Fault Indicators
GO-02 | Grid Response Procedures and Notifications (Grid Ops): Patrols
MA-01 | Maintenance: Weather Station
PS-01 | Protocols on PSPS
RA-01 | Risk and Risk Component Calculation
RA-02 | Top Risk Areas within the HFRA
RA-03 | Other Key Metrics
RA-04 | Enterprise System for Risk Assessment
SA-01 | Environmental Monitoring Systems
SA-02 | Grid Monitoring Systems
SA-03 | Smoke and Air Quality Sensors
SA-04 | Wildfire Detection Cameras
SA-05 | Weather Forecasting
SA-06 | Fire Potential Index
SA-07 | Installation of cFCI
SA-08 | Installation of SCAN
SA-09 | Distribution Protective Settings Review
SA-10 | Installation of Advanced AMI Meters
SA-11 | Situational Awareness Tools and Models
SA-12 | Implement WRF Ensemble Forecasting
SA-13 | Climate Vulnerability Assessment
SA-14 | Machine Learning techniques of Normalized Differential Vegetation Index (NDVI) and Self Organizing Maps (SOMs)
VM-01 | Vegetation Inspections: Detailed Inspection – Distribution
VM-02 | Vegetation Inspections: Detailed Inspection - Transmission
VM-03 | Vegetation Inspections: Patrol Inspection - Distribution
VM-04 | Vegetation Inspections: Patrol Inspection - Transmission
VM-05 | Pole Clearing
VM-06 | Clearance - Distribution
VM-07 | Clearance - Transmission
VM-11 | Quality Assurance / Quality Control (Vegetation)
VM-12 | Wood and Slash Management
VM-13 | Substation Defensible Space
VM-14 | Integrated Vegetation Management
VM-15 | Workforce Planning (Vegetation Management)
VM-16 | Routine (Detailed) Inspection – Local Transmission (TNT)
VM-17 | Routine (Detailed) Inspection – Main Grid (MGI)
VM-18 | Pole Clearing PRC 4292 (DPL)
VM-19 | Pole Clearing (LRA)
VM-20 | Routine Distribution (Detailed)
VM-21 | Routine Transmission (Detailed)
VM-22 | Off-cycle Distribution (Patrol)
VM-23 | Non-Routine Transmission (Patrol)
VM-24 | Pole Clearing
VM-25 | Substation Defensible Space
VM-26 | Defensible Space: Develop hazard tree process for tracking inspection of trees outside of Substation property.
VM-27 | Integrated Vegetation Management: develop a process for conducting outreach to known nurseries participating in the tree replacement program.
VM-28 | Integrated Vegetation Management: Review and identify opportunities to expand use of tree growth regulator.
WP-01 | Wildfire Mitigation Strategy Development
WP-02 | Identifying and Evaluating Mitigation Initiatives

## 4-1
Table 4-1: High-Level Service Territory Components
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | Total
Area Served (sq. mi.) | 7014.9706 | 128.603 | 4148.8366 | 11292.4102
Number of Customers Served | 18718 | 1189 | 27489 | 47396
Overhead Transmission Lines (circuit miles) | 319.4902 | 23.2652 | 386 | 728.7553
Overhead Distribution Lines (circuit miles) | 769.9872 | 40.3306 | 1705.9539 | 2516.2716
Underground Transmission Lines (circuit miles) | 0 | 0 | 0 | 0
Underground Distribution Lines (circuit miles) | 348.4464 | 54.6879 | 236.4878 | 639.6222
Return to Table of Contents

## 4-2
Table 4-2: Catastrophic Electrical Corporation Wildfires
Ignition Date | Fire Name | Official Cause | Fire Size (acres) | No of Fatalities | No of Structures Destroyed and Damaged | Financial Loss (US$) | Lesson(s) Learned
2020-09-08 | Slater | Under Investigation | 157270 | 2 | 377 | TBD | Under Investigation
2022-07-29 | McKinney | Under Investigation | 60138 | 4 | 196 | TBD | Under Investigation
Return to Table of Contents

## 4-3
Table 4-3: Frequently Deenergized Circuits
Entry # | Circuit ID | Name of Circuit | Date of Outages | Number of Customers Hours of PSPS per Outage | Measures Taken, or Planned to Be Taken, to Reduce the Need for and Impact of Future PSPS of Circuit | Estimated Annual Decline in PSPS Events and PSPS Impact on Customers
1 | N/A | N/A | N/A | N/A | N/A | N/A
2 | N/A | N/A | N/A | N/A | N/A | N/A
3 | N/A | N/A | N/A | N/A | N/A | N/A
4 | N/A | N/A | N/A | N/A | N/A | N/A
5 | N/A | N/A | N/A | N/A | N/A | N/A
Return to Table of Contents

## 5-1
Table 5-1: Risk Model Assumptions and Limitations
Assumption | Justification | Constraints/Limitations | Applicable Model(s)
POF score calculated at the circuit level is relatively evenly distributed amongst each circuit’s segments | The Hierarchical Bayes modeling approach generalizes the conditions per segment at the circuit level | May underestimate or overestimate the POF for specific segments within each circuit. | Expected Wildfire Risk, Terrain Risk, Wind Risk, Composite Risk
POF score captures intrinsic nuances of outage profiles | In the absence of detailed faulted equipment data, the Hierarchical Bayes modeling approach intrinsically shows nuanced differentiation of equipment conditions that lead to outages | Outage conditions of equipment and environmental factors are not explicitly modeled` | Expected Wildfire Risk, Terrain Risk, Wind Risk, Composite Risk
Weather day selection appropriately captures the full asset risk spectrum | Technosylva bases weather day selection on a full risk spectrum rather than using the worst fire weather days | Risk profile covers all weather conditions, not just the important high fire weather days | Expected Wildfire Risk, Terrain Risk, Wind Risk, Composite Risk
PSPS Likelihood can be based on standardized Meteorological conditions | Without a dataset of historical PSPS events in California, PacifiCorp is planning to use a set of conditions to base PSPS risk per segment on. | Conditions are relative to each segment and not based on wind speed thresholds | PSPS Risk, PSPS LoRE
Circuit Segments are not predefined in PacifiCorp’s Distribution network topology. | PacifiCorp does not have the amount of SCADA sectionalizing needed to define grid hardening, PSPS, and PEDS risk units | Risk is quantified at the Technosylva (100 m) segment units and must be rolled up to a project level to understand RSE value and risk reduction over time. This issue will need to be rectified to optimize a grid hardening portfolio of risk reduction with associated cost. | Overall Risk, Wildfire Risk, PSPS Risk, PEDS Risk, Wildfire Lore, Wildfire CoRE, PSPS LoRE, PSPS CoRE, PEDS LoRE, Peds CoRE
Return to Table of Contents

## 5-3
Table 5-3: Extreme-Event Scenarios
Scenario ID | Extreme Event Scenario | Purpose
ES1 | Climate Change 1 | Impact of climate change on long-term weather and vegetation conditions that impact fire behavior.
Weather Condition 2
Vegetation Condition 3
Return to Table of Contents

## 5-4
Table 5-4: Summary of Risk Models
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
R1 | Overall Utility Risk | WC1, WC2, VC1, VC2, VC3, WLC5 | Ignition Risk | See Appendix B, FireSight Model | Composite Risk Score Wildfire Risk Associated with ignitions from Utility Assets | Composite risk score is a 1 to 5 rating based on normalization of combined outputs.
Locational risk calculated from all surrounding assets, environmental characteristics, and demographics
R2 | Wildfire Risk | WC1, WC2, VC1, VC2, VC3, WLC5 | Wildfire Likelihood (F: Probability of Wildfire Event) Wildfire Consequence (F: Conditional Impact) | See Appendix B, FireSight Model | Possible Acres burned Number of buildings threatened | Acres/Fire simulation Buildings/Fire simulation
[5 empty] | Estimated number of buildings destroyed Population in area Population at risk | Buildings Destroyed /Fire simulation Population Impacted/Fire simulation
Population at Risk/Fire simulation
WL1 | Wildfire Likelihood (F: Probability of Wildfire Event) | WC1, WC2, VC1, VC2, VC3, WLC5 | Burn Probability (F: Fire Spread Potential) Ignition Likelihood (F: Probability of Fault) | See Appendix B, FireSight Model | Probability of a wildfire | Wildfires/ Year
WL3 | Burn Probability (F: Fire Spread Potential) | WC1, WC2, VC1, VC2, VC3, WLC5 | Historic Weather Conditions | PacifiCorp’s 30 Year Weather Research & Forecast (WRF) input to FireSight Model. See Appendix B. Technosylva provides land characteristics and fuels moisture information, see Appendix B | Probability of a wildfire burning a specific location (POI from FireSight model) | Value between 0 and 1.0 representing the percent probability.
Terrain Surface Fuels
WUI and Non-Forest Fuels Land Use
Canopy Fuels Hydrography Croplands Fuel Moisture
WL2 | Ignition Likelihood (F: Probability of Fault) | WC1, WC2, VC1, VC2, VC3, WLC5 | Probability of Fault Historic wind conditions Likelihood of vegetation contact | See Appendix B, FireSight Model | Probability of ignition occurring (POF from FireSight Model) | Ignitions/ Year
Likelihood of an object contact
WL4 | Equipment Likelihood of Ignition | WC1, WC2, WLC5 | Asset location and attributes | GREATER, provided by PacifiCorp | Probability of equipment in extreme weather conditions | See PoF discussion in Section 5.2.1
|  |  | Historic weather conditions | PacifiCorp’s 30 Year Weather Research & Forecast (WRF) Inputs provided to Wildfire Risk
Reduction Module-See Appendix B
WL5 | Contact from Vegetation Likelihood | WC1, WC2, VC1, VC2, VC3, WLC5 | Fire incidents near The Electric Corporation assets | PacifiCorp Fire Incident Database | Likelihood of a vegetation contacts | Contacts/ Year
|  |  | Asset location and attributes | PacifiCorp: GREATER
PacifiCorp inputs provided to Technosylva for FireSight- See Appendix B
|  |  | Surface Fuels | Technosylva provides terrain and fuels information, see Appendix B
WUI and Non-Forest Fuels Land Use
Canopy Fuels
WL6 | Contact from Object Ignition Likelihood | WC1, WC2, WLC5 | Fire incidents near PacifiCorp assets | PacifiCorp: Fire Incident Database | Likelihood of an object contact | Contacts/ Year
PacifiCorp: GREATER
PacifiCorp inputs provided to Technosylva for FireSight- See Appendix B
WC1 | Wildfire Consequence (F: Conditional Impact) | WC1, WC2, WLC5 | Wildfire Exposure Potential | See Appendix B, FireSight Model | Number of buildings threatened Estimated number of buildings destroyed Population at risk | Plexels / 8-hour
|  |  | Wildfire Vulnerability Fire Hazard Intensity |  | Community Resilience
WC2 | Wildfire Exposure Potential | N/A | Buildings Damage Inspection Dataset (DINS) Building loss factor Critical Facilities Population | Supplied/managed by Technosylva, see Appendix B | Buildings at risk Population a risk | Polygon footprints/ 8- hour
90 meters/ 8-hour
WC3 | Wildfire Vulnerability | N/A | Suppression Difficulty Population Density Roads | Supplied/managed by Technosylva, see Appendix B | Socially vulnerable populations at risk Egress difficulty Suppression difficulty | Plexels/ 8-hour
Socially Vulnerable Population
Fire Stations
WC4 | Fire Hazard Intensity | WC1, WC2, WLC5 | Fire Growth Flame Length Crown Fire Acres Burn Frequency | Supplied/managed by Technosylva, see Appendix B | Fire Behavior Area Impacted | Acres/8-hour
Return to Table of Contents

## 5-5
Table 5-5: Summary of Top-Risk Circuits, Segments, or Spans
Risk Ranking | Circuit, Segment, or Span ID | Overall Utility Risk Score | Wildfire Risk Score | Outage Program Risk Score | Top Risk Contributors | Total Miles | Version of Risk Model Used
1 | 5G31 | TBD | 192.7143 | TBD | Max Wind Score: 0.93, Max Terrain Score: 0.73 | 15.995 | 0.1.0
2 | 5G33 | TBD | 76.0426 | TBD | Max Wind Score: 0.90, Max Terrain Score: 0.79 | 6.4002 | 0.1.0
3 | 5G21 | TBD | 74.5515 | TBD | Max Wind Score: 0.79, Max Terrain Score: 0.82 | 6.6803 | 0.1.0
4 | 5G83 | TBD | 53.1595 | TBD | Max Wind Score: 0.81, Max Terrain Score: 0.66 | 4.7731 | 0.1.0
5 | 4G1 | TBD | 48.5248 | TBD | Max Wind Score: 0.78, Max Terrain Score: 0.74 | 4.5977 | 0.1.0
6 | 5G149 | TBD | 45.9221 | TBD | Max Wind Score: 0.82, Max Terrain Score: 0.64 | 4.1906 | 0.1.0
7 | 5G5 | TBD | 32.236 | TBD | Max Wind Score: 0.88, Max Terrain Score: 0.71 | 2.7772 | 0.1.0
8 | 5L87 | TBD | 20.0705 | TBD | Max Wind Score: 0.81, Max Terrain Score: 0.55 | 1.9231 | 0.1.0
9 | 5L83 | TBD | 19.3541 | TBD | Max Wind Score: 0.92, Max Terrain Score: 0.57 | 1.6543 | 0.1.0
10 | 5G45 | TBD | 11.3355 | TBD | Max Wind Score: 1.00, Max Terrain Score: 0.88 | 0.68595 | 0.1.0
11 | 5G151 | TBD | 10.7736 | TBD | Max Wind Score: 0.89, Max Terrain Score: 0.76 | 0.84054 | 0.1.0
12 | 5G23 | TBD | 9.8309 | TBD | Max Wind Score: 0.78, Max Terrain Score: 0.51 | 0.93049 | 0.1.0
13 | 5L97 | TBD | 7.8135 | TBD | Max Wind Score: 0.72, Max Terrain Score: 0.72 | 0.66528 | 0.1.0
14 | 7G81 | TBD | 4.8352 | TBD | Max Wind Score: 0.78, Max Terrain Score: 0.60 | 0.4174 | 0.1.0
15 | 7G73 | TBD | 1.3044 | TBD | Max Wind Score: 0.64, Max Terrain Score: 0.64 | 0.12427 | 0.1.0
16 | 7G75 | TBD | 1.2716 | TBD | Max Wind Score: 0.50, Max Terrain Score: 0.73 | 0.12427 | 0.1.0
Return to Table of Contents

## 5-2
Table 5-2: Summary of Design Scenarios
Scenario ID | Design Scenario | Purpose
WLC1 | Wind Load | Baseline wind load used in design, construction, and maintenance
WLC2 | Wind Load | 95th percentile wind gusts based on maximum daily values over the 30-year history
WLC3 | Wind Load | Wind gusts with a probability of exceedance of five percent over the three-year WMP cycle (i.e. 60-year return interval)
WLC4 | Wind Load | Wind gusts with a probability of exceedance of 1 percent over the three-year WMP cycle (i.e. 300-year return interval)
WLC5 | Wind Load | FireSight models wind speeds to identify at what point a specific transmission or distribution circuit may fail in windy conditions. The results are based on three-hour aggregated probabilities based on the maximum wind gust during that three-hour period
WC1 | Weather Condition | Anticipated weather conditions over the next three years. This is based on historical weather days that best represent the days when weather and fuel conditions can lead to increased risk of ignition.
WC2 | Weather Condition | Long term conditions. PacifiCorp has provided 30 years of the 30-Year Weather Research and Forecast (WRF) Model to Technosylva to calculate the 600 historical weather days that best represents the days when weather and fuel conditions can lead to increased risk of ignition. PacifiCorp is now providing the WRF annually to capture new days that should be incorporated into the historical weather days to account for changing conditions in locations
VC1 | Vegetation Condition | Modeling of current vegetation conditions to identify where current vegetation fuels risk
VC2 | Vegetation Condition | Modeling of projected 2025 vegetation conditions to identify potential mid-range vegetation fuels risk
VC3 | Vegetation Condition | Modeling of projected 2025 vegetation conditions to identify potential mid-range vegetation fuels risk
Return to Table of Contents

## 5-6
Table 5-6: Utility Risk Assessment Improvement Plan
Key Risk Assessment Area | Proposed Improvement | Type of Improvement | Expected Value Add | Timeframe and Key Milestones
Risk Presentation | PC-25U-02: PSPS and Wildfire Risk Trade-Off Transparency | Technical | Quantification and understanding PSPS risk along its system in comparison to wildfire risk | EOY 2025
Risk Assessment Methodology | Monetization of Risk Events for Application in Mitigation Alternatives Analysis | Programmatic | More accurate assessment of risk spend efficiency and benefit cost ratios in evaluating mitigations. | EOY 2025
Design Basis | Creation of PEDS Risk Model | Programmatic | Ability to understand PSPS risk buydown over the wildfire mitigation portfolio | EOY 2025
Model Architecture | Model Architecture Improvements | Technical | Ability to create reproducible models, archive release versions, and scale logic. | EOY 2025
Model Architecture | Model Taxonomy and Versioning | Technical | Ability to track model versions. Ability to run new model with historic data as well as run an old model with new data | EOY 2025
Design Basis | Dynamic Grid Hardening Efficacy Rates | Programmatic | Update the constants used for grid hardening program efficacy with ranges based on localized conditions | EOY 2025
Risk Assessment Methodology | Portfolio Optimization and Grid Hardening Recommendations | Programmatic | Automation of maximizing risk reduction considering targets, constraints (budgets), construction limitations, and project timeline | EOY 2026
Model Validation | Model Validation and Verification | Technical | Quality assurance | EOY 2026
Climate change | Implement a climate change planning model component | Programmatic | Anticipation of climate change impacts on risk scores | EOY 2026
Risk Assessment Methodology | PC-25U-03 Independent Review Transparency | Technical | Validation of methodology and best practices by third-party | EOY 2027
Risk Presentation | PC-25U-01: Establish formal process of recognition of high-risk areas beyond the CPUC-established HFTD | Technical | A systematic approach for adding high-risk areas to the HFTD | EOY 2027
Risk Presentation | PC-23B-02: Calculating Risk Scores Using 95th Percentile Values | Programmatic | Alignment with fundamental mathematical standards and optimization of mitigation prioritization decisions | EOY 2027
Return to Table of Contents

## PAC 5-1
Table PAC 5-1: Risk Model Components
Model | Risk Component | Design Scenarios | Key Inputs | Source of Inputs | Key Outputs | Units
Planning Model | Wind Risk | Rate of Spread | Rate of Spread | Technosylva FireSight RAIL and RAVE models, December 2023 – Expected Risk | Wind Risk score | Natural units per segment
|  | 95th percentile, Population Impacted | 95th percentile, Population Impacted
|  | 95th percentile, Buildings Destroyed | 95th percentile, Buildings Destroyed
|  | 95th percentile, | 95th percentile, Terrain Difficulty Index, Disabled Population, Poverty Population
Planning Model | Terrain Risk | Fire Behavior Index | Fire Behavior Index | Technosylva FireSight RAIL and RAVE models, December 2023 – Expected Risk | Terrain Risk score | Natural units per segment
|  | 95th percentile, Fire Size Potential | 95th percentile, Fire Size Potential
|  | 95th percentile, Flame Length | 95th percentile, Flame Length
|  | 95th percentile | 95th percentile, Terrain Difficulty Index, Fire Station Density,
Planning Model | Composite Risk | Rate of Spread | Wind Risk score, Terrain Risk score | Technosylva FireSight RAIL and RAVE models, December 2023 – Expected Risk | Composite Risk score | Natural units per segment
95th percentile, Population Impacted
95th percentile, Buildings Destroyed
95th percentile, Fire Behavior Index
95th percentile, Fire Size Potential
95th percentile, Flame Length
95th percentile
Planning Model | PSPS Risk: In development
Planning Model | PEDS Risk: In development
Return to Table of Contents

## PAC 5-2
Table PAC 5-2: FireSight Attributes
RAIL | RAVE | Attribute | Description: | Percentiles | Used in the Composite (Wildfire) Risk Score
(Circuit Level) | (Plexel)
Yes | Yes | Acres Burned | Number of Acres Burned | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | No
| Yes | Building Density | Building Density per Plexel | N/A | No
Yes | Yes | Buildings Destroyed | Number of Buildings Destroyed | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | No
| Yes | Building Loss Factor | Estimated Building Loss Factor Within the Plexel. | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | Yes
| Yes | Building Loss Factor (Average-Mean) | Average Estimated Building Loss Factor Within the Plexel. | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | No
| Yes | Building Loss Factor (Median) | Average Estimated Building Loss Factor Within the Plexel. | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | No
Yes | Yes | Buildings Threatened | Number of Buildings Threatened | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | No
| Yes | Burn Frequency | Burn Frequency is the number of times a plexel is touched from all assets ignited simulations run for the selected weather days. It is similar to traditional burn probability although this only represents a frequency, not a probability. | N/A | No
| Yes | Disability Population | Disability Population Ratio | N/A | Yes
Yes | Yes | Fire Behavior Index | Fire Behavior Index | N/A | Yes
| Yes | Fire Station Density | Density of Fire Stations in a location | N/A | Yes
Yes | Yes | Flame Length | Feet | N/A | Yes
| Yes | Fuel Model Majority | Majority Fuel in Each Plexel | N/A | Yes
| Yes | Number of Buildings | Number of Building per Plexel | N/A | No
| Yes | Population Count | Population Count per Plexel | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | No
| Yes | Population Density | Population Density per Plexel | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | No
Yes | Yes | Population Impacted | Population Count | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | Yes
| Yes | Poverty Population | Poverty Population Ratio | N/A | Yes
Yes | Yes | Rate of Spread | 66 Feet/Hour | 0, 20, 40, 60, 80, 90, 95, 98, and 100 | Yes
| Yes | Road Availability-With Social Vulnerability Population | Availability of Roads in a Location with Consideration of Social Vulnerability Population | N/A | No
| Yes | Road Availability-With No Population | Availability of Roads in a Location with No Consideration of Social Vulnerability Population | N/A | No
| Yes | Road Miles | Total Miles (Major + Minor) | N/A | No
| Yes | Senior Population | Senior Population Ratio | N/A | No
| Yes | Terrain Difficulty Index | Terrain Difficulty per Plexel | N/A | Yes
| Yes | Years Since Last Fire | Years Since Last Fire per Plexel | N/A | No
Return to Table of Contents

## PAC 5-3
Table PAC 5-3: Comparison of General Characteristics of Wind-Driven and Fuel/Terrain-Driven Wildfires
Category | Wind-Driven Wildfires | Fuel/Terrain-Driven Wildfires
Locational Risk | More likely in areas subject to PSPS (Public Safety Power Shutoff) | Confined to areas of complex fuels and terrain with difficult access
Frequency | Some years have none; others several | Annually during peak fire season
Event Duration | One-three days per event | Can persist several weeks or months
Outage Risk | Wind-driven and somewhat predictable | Difficult to predict
Consequence | Immediately catastrophic | May be catastrophic over time
Return to Table of Contents

## PAC 5-4
Table PAC 5‑4: Comparison for FireSight Risk Metrics In the HFTD and HFRA at the 95th Percentile
Network | Fire Boundary | Quantity | Mean of Acres Impacted (P95) | Mean of Structures Impacted (P95) | Mean of Structures Destroyed (P95) | Mean of Population Impacted (P95) | Mean of Fire Behavior Index (P95) | Mean of Flame Length (P95) | Mean of Rate of Spread (P95)
Distribution | HFRA | 11142 | 863.85 | 27.37 | 9.36 | 19.35 | 2.61 | 5.07 | 26.94
Distribution | HFTD | 18085 | 596.19 | 14.29 | 5.35 | 13.04 | 2.36 | 6 | 18.38
Transmission | HFRA | 1974 | 1292.03 | 20.71 | 6.95 | 15.08 | 2.83 | 5.75 | 28.99
Transmission | HFTD | 5654 | 565.61 | 6.98 | 2.6 | 6.87 | 2.39 | 6.53 | 16.73
HFRA Divided by HFTD |  | 0.55 | 1.86 | 2.26 | 2.05 | 1.73 | 1.15 | 0.86 | 1.59
Return to Table of Contents

## 6-1
Table 6-1: Prioritized Areas in PacifiCorp’s Service Territory Based on Overall Utility Risk
Priority | Circuit Segment and/or Span ID | Length (miles) | Overall Utility Risk | Wildfire Risk | Outage Program Risk | Percent of Overall Utility Risk | Associated Risk Drivers
1 | 5G31 | 15.995 | TBD | 192.7143 | TBD | 1.58% | Max Wind Score: 0.93, Max Terrain Score: 0.73
2 | 5G33 | 6.4002 | TBD | 76.0426 | TBD | 0.62% | Max Wind Score: 0.90, Max Terrain Score: 0.79
3 | 5G21 | 6.6803 | TBD | 74.5515 | TBD | 0.61% | Max Terrain Score: 0.82, Max Wind Score: 0.79, Max Terrain Score: 0.82
4 | 5G83 | 4.7731 | TBD | 53.1595 | TBD | 0.44% | Max Wind Score: 0.81, Max Terrain Score: 0.66
5 | 4G1 | 4.5977 | TBD | 48.5248 | TBD | 0.4% | Max Wind Score: 0.78, Max Terrain Score: 0.74
6 | 5G149 | 4.1906 | TBD | 45.9221 | TBD | 0.38% | Max Wind Score: 0.82, Max Terrain Score: 0.64
7 | 5G5 | 2.7772 | TBD | 32.236 | TBD | 0.26% | Max Wind Score: 0.88, Max Terrain Score: 0.71
8 | 5L87 | 1.9231 | TBD | 20.0705 | TBD | 0.16% | Max Wind Score: 0.81, Max Terrain Score: 0.55
9 | 5L83 | 1.6543 | TBD | 19.3541 | TBD | 0.16% | Max Wind Score: 0.92, Max Terrain Score: 0.57
10 | 5G45 | 0.68595 | TBD | 11.3355 | TBD | 0.09% | Max Wind Score: 1.00, Max Terrain Score: 0.88
11 | 5G151 | 0.84054 | TBD | 10.7736 | TBD | 0.09% | Max Wind Score: 0.89, Max Terrain Score: 0.76
12 | 5G23 | 0.93049 | TBD | 9.8309 | TBD | 0.08% | Max Wind Score: 0.78, Max Terrain Score: 0.51
13 | 5L97 | 0.66528 | TBD | 7.8135 | TBD | 0.06% | Max Wind Score: 0.72, Max Terrain Score: 0.72
14 | 7G81 | 0.4174 | TBD | 4.8352 | TBD | 0.04% | Max Wind Score: 0.78, Max Terrain Score: 0.60
15 | 7G73 | 0.12427 | TBD | 1.3044 | TBD | 0.01% | Max Wind Score: 0.64, Max Terrain Score: 0.64
16 | 7G75 | 0.12427 | TBD | 1.2716 | TBD | 0.01% | Max Terrain Score: 0.73, Max Wind Score: 0.50, Max Terrain Score: 0.73
Return to Table of Contents

## 6-2
Table 6-2: Stakeholder Roles and Responsibilities in the Decision-Making Process
Stakeholder | Stakeholder Point of Contact | PacifiCorp Point of Contact | Stakeholder Role | Engagement Methods | Activity | Level of Engagement for Activity
Power Delivery | SVP, Power Delivery | SVP, Power Delivery | Executive sponsor | Meeting | All | Executive sponsor of Wildfire Risk Governance Committee and Wildfire Scoping Governance Committee
Asset Risk | Managing Director, Asset Risk | Managing Director, Asset Risk | Define companies’ wildfire risk areas and the composite risk scores. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Facilitator of Wildfire Risk Governance Committee
Advisor in Wildfire Scoping Governance Committee
Asset Management | Managing Director, Asset Management | Managing Director, Asset Management | Propose new initiatives, plan initiatives, track initiative progress. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening. | Advisor in Wildfire Scoping Governance Committee
Operations | VP, System Operations | VP, System Operations | Provide input into system hardening scopes and proposed initiatives for Electrical Corporation states. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Operations | VP, T&D Operations, Electrical Corporation | VP, T&D Operations, Electrical Corporation | Provide input into system hardening scopes and proposed initiatives for Electrical Corporation states. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Operations | VP, T&D Operations, Rocky Mountain Power | VP, T&D Operations, Rocky Mountain Power | Provide input into system hardening scopes and proposed initiatives for Rocky Mountain Power states. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Project Management | VP, Project Management | VP, Project Management | Provide input into system hardening initiatives. | Meeting, Phone, Email | System Hardening | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Engineering | VP, Engineering & T&D Standards | VP, Engineering & T&D Standards | Provide input into system hardening and new initiatives. | Meeting, Phone, Email | System Hardening | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Wildfire Program Delivery | VP, Asset Management & Wildfire | VP, Asset Management & Wildfire | Provide input into initiatives with alignment to the wildfire mitigation plan. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Asset Investment Strategy & Policy | Director, Asset Investment Strategy and Policy | Director, Asset Investment Strategy and Policy | Provide input into the alignment of initiative to asset strategy and policy. | Meeting, Phone, Email | Inspections, System Hardening | Advisor in Wildfire Risk Governance Committee
Facilitator of Wildfire Scoping Governance Committee
Legal | Assistant General Counsel | Assistant General Counsel | Provides legal consult | Meeting, Email | All | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Field Engineering | Director, Field Engineering | Director, Field Engineering | Provide input into system hardening scopes. | Meeting, Phone, Email | System Hardening | Advisor in Wildfire Risk Governance Committee
Advisor in Wildfire Scoping Governance Committee
Delivery Assurance | Managing Director, Delivery Assurance | Managing Director, Delivery Assurance | Provide input into the alignment of initiative cost with the company budget. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Voting member in Wildfire Risk Governance Committee
Voting member in Wildfire Scoping Governance Committee
Technical Services & Training | Managing Director, Technical Services and Training | Managing Director, Technical Services and Training | Provide input into the alignment of initiative to services and training support. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Advisor in Wildfire Risk Governance Committee
Advisor in Wildfire Scoping Governance Committee
Project Management Office | Director, Wildfire PMO | Director, Wildfire PMO | Provide input into the alignment of initiative cost with the company budget. | Meeting, Phone, Email | System Hardening | Advisor in Wildfire Risk Governance Committee
Advisor in Wildfire Scoping Governance Committee
Wildfire Mitigation Program Delivery | Director, Wildfire Program Delivery | Director, Wildfire Program Delivery | Provide input into initiatives with alignment to the wildfire mitigation plan. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Advisor in Wildfire Risk Governance Committee
Advisor in Wildfire Scoping Governance Committee
Asset Risk | Director, Asset Risk | Director, Asset Risk | Provide input into the alignment of initiative to asset risk. | Meeting, Phone, Email | Inspections, System Hardening | Advisor in Wildfire Risk Governance Committee
Advisor in Wildfire Scoping Governance Committee
Wildfire Mitigation Planning | Director, Wildfire Plan | Director, Wildfire Plan | Provide input into initiatives with alignment to the wildfire mitigation plan. | Meeting, Phone, Email | Inspections, Situational Awareness, System Hardening | Advisor in Wildfire Risk Governance Committee
Advisor in Wildfire Scoping Governance Committee
Return to Table of Contents

## 6-3
Table 6-3 Risk Impact of Activities
Activity | Activity Section | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness – Outage Program Risk | Cost-Benefit Score - Overall Risk | Cost-Benefit Score – Wildfire Risk | Cost-Benefit Score – Outage Program Risk | % HFTD Covered | % HFTD/HFRA Covered | Expected % Risk Reduction | Model(s) Used to Calculate Risk Impact
Covered Conductor Installation | 8.2.1 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | FireSight, TBD
Undergrounding of Electric Lines and/or Equipment | 8.2.2 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | FireSight, TBD
Distribution Pole Replacements and Reinforcements | 8.2.3 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Installation of System Automation Equipment | 8.2.8 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Line Removal in the HFTD | 8.2.9 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Other Technologies and Systems | 8.2.12 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Asset Inspections | 8.3.1, 8.3.2 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Intrusive Pole Inspections | 8.3.3 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Substation Inspections | 8.3.4 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Infrared Inspections of Distribution Electric Lines and Equipment | 8.3.5 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Infrared Inspections of Transmission Electric Lines and Equipment | 8.3.6 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Equipment Settings to Reduce Wildfire Risk | 8.7.1 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Vegetation Pruning and Removal | 9.3 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Pole Clearing | 9.4 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Wood and Slash Management | 9.5 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Defensible Space | 9.6 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Grid Monitoring Systems | 10.3 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Ignition Detection Systems | 10.4 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Return to Table of Contents

## 6-4
Table 6-4 Summary of Risk Reduction for Top-Risk Circuits
Circuit, Segment, or Span ID | Initial Overall Utility Risk | 2026 Activities | 2026 Overall Utility Risk | 2027 Activities | 2027 Overall Utility Risk | 2028 Activities | 2028 Overall Utility Risk
4G1 | TBD | No 2026 Activities GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | GH-01 Line Rebuild – Covered Conductor Installation | TBD | No 2028 Activities | TBD
5G149 | TBD | No 2026 Activities GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Planned for 2025 | TBD | GH-01 Line Rebuild – Covered Conductor Installation | TBD | No 2028 Activities | TBD
5G151 | TBD | No 2026 Activities GH-04 System Automation Completed in 2024 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G21 | TBD | No 2026 Activities GH-04 System Automation Completed in 2023 GH-05 Expulsion Fuse Replacement Completed in 2023 | TBD | No 2027 Activities | TBD | GH-01 Line Rebuild – Covered Conductor Installation | TBD
5G23 | TBD | No 2026 Activities GH-04 System Automation Completed in 2023 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | GH-01 Line Rebuild – Covered Conductor Installation | TBD | No 2028 Activities | TBD
5G31 | TBD | No 2026 Activities GH-04 System Automation Completed in 2023 GH-05 Expulsion Fuse Replacement Planned for 2025 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G33 | TBD | GH-01 Line Rebuild – Covered Conductor Installation GH-05 Expulsion Fuse Replacement GH-04 System Automation Completed in 2023 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G45 | TBD | GH-01 Line Rebuild – Covered Conductor Installation Planned for 2025 GH-05 Expulsion Fuse Replacement Planned for 2025 GH-04 System Automation Completed in 2019 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G5 | TBD | No 2026 Activities GH-04 System Automation Completed in 2023 GH-05 Expulsion Fuse Replacement Planned for 2025 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G83 | TBD | GH-01 Line Rebuild – Covered Conductor Installation Planned for 2025 GH-04 System Automation Planned for 2025 GH-05 Expulsion Fuse Replacement Completed in 2019 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5L83 | TBD | No 2026 Activities GH-04 System Automation Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5L87 | TBD | GH-04 System Automation GH-05 Expulsion Fuse Replacement Planned for 2025 | TBD | No 2027 Activities | TBD | GH-01 Line Rebuild – Covered Conductor Installation | TBD
5L97 | TBD | No 2026 Activities GH-04 System Automation Completed in 2022 GH-05 Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
7G73 | TBD | No 2026 Activities GH-01 Line Rebuild – Covered Conductor Installation Completed 2022 GH-04 System Automation Completed in 2021 GH-05 Completed in 2022 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
7G75 | TBD | No 2026 Activities GH-01 Line Rebuild – Covered Conductor Installation Completed 2022 GH-04 System Automation Completed in 2020 GH-05 Completed in 2022 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
7G81 | TBD | No 2026 Activities GH-01 Line Rebuild – Covered Conductor Installation Planned for 2025 GH-04 System Automation Completed in 2022 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
Return to Table of Contents

## PAC 6-1
Table PAC 6-1 Summary of Risk Reduction for Circuits With Maximum Fuel/Terrain Wildfire Risk Scores
Circuit, Segment, or Span ID | Max Terrain Score | Max Wind Score | 2026 Activities | 2026 Overall Maximum Fuel/Terrain Risk | 2027 Activities | 2027 Overall Maximum Fuel/Terrain Risk | 2028 Activities | 2028 Overall Maximum Fuel/Terrain Risk
5G39 | 0.97 | 0.64 | GH-01 Line Rebuild - Covered Conductor Installation GH-16 Undergrounding of electric lines and/or equipment GH044 System Automation Completed in 2023 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5R165 | 0.96 | 0.61 | GH-01 Line Rebuild - Covered Conductor Installation GH-04 System Automation Planned to Complete in 2025 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
8G95 | 0.94 | 0.46 | GH-01 Line Rebuild - Covered Conductor Installation Planned to Complete in 2025 GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Completed in 2023 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5R171 | 0.9 | 0.68 | GH-01 Line Rebuild - Covered Conductor Installation GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5R170 | 0.89 | 0.49 | GH-01 Line Rebuild - Covered Conductor Installation GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G97 | 0.89 | 0.36 | GH-01 Line Rebuild - Covered Conductor Installation Planned to Complete in 2025 GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5R96 | 0.88 | 0.48 | GH-01 Line Rebuild - Covered Conductor Installation Planned to Complete in 2025 GH-16 Undergrounding of electric lines and/or equipment GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
7G75 | 0.84 | 0.78 | GH-01 Line - Covered Conductor Installation Rebuild Completed in 2022 GH-04 System Automation Completed in 2020 GH-05 Expulsion Fuse Replacement Completed in 2022 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G16 | 0.83 | 0.42 | GH-01 Line - Covered Conductor Installation GH-05 Expulsion Fuse Replacement Completed in 2021 GH-05 Expulsion Fuse Replacement Completed in 2022 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
7G73 | 0.8 | 0.62 | GH-01 Line - Covered Conductor Installation Completed in 2022 GH-04 System Automation Completed in 2021 GH-05 Expulsion Fuse Replacement Completed in 2022 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G83 | 0.79 | 0.99 | GH-01 Line Rebuild - Covered Conductor Installation Planned to Complete in 2025 GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Planned to Complete in 2025 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G41 | 0.78 | 0.8 | GH-01 Line - Covered Conductor Installation Rebuild GH-05 Expulsion Fuse Replacement Completed in 2022 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G79 | 0.77 | 0.41 | GH-01 Line Rebuild - Covered Conductor Installation Planned to Complete in 2025 GH-04 System Automation Completed in 2022 GH-05 Expulsion Fuse Replacement Completed in 2023 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
5G23 | 0.77 | 0.96 | GH-01 Line Rebuild - Covered Conductor Installation Planned for 20301 GH-04 System Automation Completed in 2023 GH-05 Expulsion Fuse Replacement Completed in 2024 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
7G71 | 0.76 | 0.37 | GH-01 Line Rebuild - Covered Conductor Installation Completed in 2022 GH-04 System Automation Completed in 2021 GH-05 Expulsion Fuse Replacement Completed in 2022 | TBD | No 2027 Activities | TBD | No 2028 Activities | TBD
1 GH-01 schedule in conjunction with planned substation replacement.
Return to Table of Contents

## 8-2
Table 8-2: Asset Inspection Frequency, Method, and Criteria
Type | Inspection Activity (Program) | Frequency or Trigger (Note 1) | Method of Inspection (Note 2) | Governing Standards & Operating Procedures | Cumulative Quarterly Target Year 1 Q1 | Cumulative Quarterly Target Year 1 Q2 | Cumulative Quarterly Target Year 1 Q3 | Cumulative Quarterly Target Year 1 Q4 | Cumulative Quarterly Target Year 2 Q1 | Cumulative Quarterly Target Year 2Q2 | Cumulative Quarterly Target Year 2Q3 | Cumulative Quarterly Target Year 2 Q4 | Cumulative Quarterly Target Year 3 Q1 | Cumulative Quarterly Target Year 3 Q2 | Cumulative Quarterly Target Year 3 Q3 | Cumulative Quarterly Target Year 3 Q4 | % of HFRA and HFTD Covered Annually by Inspection Type | Condition Find Rate Level 1 Condition Find Rate | Condition Find Rate Level 2 Condition Find Rate | Condition Find Rate Level 3 Condition Find Rate
Transmission | Patrol | 1 year | Ground/Air | GO 165 | 616.2 | 5972.0823 | 9783.2329 | 12324 | 616.2 | 5972.0823 | 9783.2329 | 12324 | 616.2 | 5972.0823 | 9783.2329 | 12324 | 100% | 0.001448% | 0.02172% | 0.02172%
Distribution | Patrol | 1 year | Ground | GO 165 | 2674.9 | 13535.0963 | 37512.8385 | 53498 | 2712.45 | 13725.1007 | 38039.4403 | 54249 | 2706.7 | 13696.0055 | 37958.8022 | 54134 | 100% | 0.0003964% | 0.08523% | 0.08523%
Transmission | Detailed | 5 year | Ground | GO 165 | 67.23 | 73.7402 | 1374.0961 | 2241 | 49.8 | 54.6223 | 1017.8489 | 1660 | 76.89 | 84.3356 | 1571.5342 | 2563 | 20% | 0.01646% | 1.539% | 1.539%
Distribution | Detailed | 5 year | Ground | GO 165 | 1436.2136 | 2187.5073 | 4472.6029 | 5996 | 1544.4806 | 2352.4095 | 4809.7638 | 6448 | 1346.3904 | 2050.6969 | 4192.8788 | 5621 | 20% | 0.004344% | 42.28% | 42.28%
Transmission | Intrusive | 10 year | Ground | GO 165 | 0 | 0 | 810.6 | 1351 | 0 | 0 | 551.4 | 919 | 0 | 0 | 1645.8 | 2743 | 10% | 0.03834% | 20.51% | 20.51%
Distribution | Intrusive | 10 year | Ground | GO 165 | 0 | 0 | 3661.2 | 6102 | 0 | 0 | 3210.6 | 5351 | 0 | 0 | 3279.6 | 5466 | 10% | 0.01444% | 41.64% | 41.64%
Transmission | Substation | 8-12 times a year | Ground | GO 174 | 36 | 54 | 90 | 108 | 36 | 54 | 90 | 108 | 36 | 54 | 90 | 108 | 100% | 0.03% | 0% | 0.37%
Distribution | Substation | 8-12 times a year | Ground | GO 174 | 129 | 172 | 301 | 344 | 129 | 172 | 301 | 344 | 129 | 172 | 301 | 344 | 100% | 0% | 0% | 0%
Distribution Transmission | Infrared | N/A 5 year | Ground Air | N/A | TBD 0 | TBD 1,000 | TBD 4,000 | TBD 7,345 | TBD 0 | TBD 1,000 | TBD 4,000 | TBD 5,168 | TBD 0 | TBD 1,000 | TBD 4,000 | TBD 7,339 | TBD 20% | N/A | N/A | N/A
Transmission Distribution | Infrared | 1 year | Air | N/A | 1400 | 1400 | 12324 | 12324 | 1400 | 1400 | 12324 | 12324 | 1400 | 1400 | 12324 | 12324 | 100% | 0% | 0.04% | 0%
Return to Table of Contents

## 8-3
Table 8-3: Grid Design, Asset Inspections, and Maintenance QA and QC Program Objectives
Initiative/Activity Being Audited | Activity (Tracking ID #) | Quality Program Type | Objective of the Quality Program
Distribution Detailed Inspections | AI-12 AI-17 | QA/QC | Ensure that inspection was performed correctly and meet appliable policies
Distribution Intrusive Inspections | AI-12 AI-19 | QA/QC | Ensure that inspection was performed correctly and meet appliable policies
Distribution Patrol Inspections | AI-12 AI-15 | QA/QC | Ensure that inspection was performed correctly and meet appliable policies
Transmission Detailed Inspections | AI-12 AI-16 | QA/QC | Ensure that inspection was performed correctly and meet appliable policies
Transmission Intrusive Inspections | AI-12 AI-18 | QA/QC | Ensure that inspection was performed correctly and meet appliable policies
Transmission Patrol Inspections | AI-12 AI-14 | QA/QC | Ensure that inspection was performed correctly and meet appliable policies
Line Rebuild - Covered Conductor Installation | GH-01 | QA | Ensure that new construction meets applicable standards
Undergrounding of Electric Lines and/or Equipment | GH-16 | QA | Ensure that new construction meets applicable standards
Distribution Pole Replacement and Reinforcements | GH-02 | QA | Ensure that new construction meets applicable standards
Transmission Pole Replacement and Reinforcements | GH-03 | QA | Ensure that new construction meets applicable standards
Installation of System Automation Equipment | GH-04 | QA | Ensure that new construction meets applicable standards
Expulsion Fuse Replacement | GH-05 | QA | Ensure that new construction meets applicable standards
ESS Circuit Hardening | GO-01 | QA | Ensure that installation meets applicable standards
Return to Table of Contents

## 8-4
Table 8-4: Grid Design, Asset Inspections, and Maintenance QA and QC Activity Targets
Initiative/Activity Being Audited | Type of Audit | Population/Sample Unit | 2026: Population Size | 2026: Sample Size | 2027: Population Size | 2027: Sample Size | 2028: Population Size | 2028: Sample Size | Percent of Sample in the HFTD | Confidence level/MOE | 2026 Pass Rate target | 2027 Pass Rate target | 2028 Pass Rate target
AI-12 | QA | Facility Points | 15690 | 785 | 14378 | 719 | 16393 | 820 | 59.32% | 95% / 2% | 95% | 95% | 95%
AI-14 | QA/QC of AI-01 - Transmission Patrol | Facility Points | 12324 | 124 | 12324 | 124 | 12324 | 124 | 77.4% | 0.02 | 95% | 95% | 95%
AI-15 | QA/QC of AI-02 - Distribution Patrol | Facility Points | 53498 | 536 | 54249 | 544 | 54134 | 542 | 25.1% | 0.02 | 95% | 95% | 95%
AI-16 | QA/QC of AI-03 - Transmission Detailed | Facility Points | 2241 | 113 | 1660 | 84 | 2563 | 129 | 81.6% | 0.02 | 95% | 95% | 95%
AI-17 | QA/QC of AI-04 - Distribution Detailed | Facility Points | 5996 | 300 | 6448 | 323 | 5621 | 282 | 23.3% | 0.02 | 95% | 95% | 95%
AI-18 | QA/QC of AI-05 - Transmission Intrusive | Facility Points | 1351 | 69 | 919 | 46 | 2743 | 138 | 66.6% | 0.02 | 95% | 95% | 95%
AI-19 | QA/QC of AI-06 - Distribution Intrusive | Facility Points | 6102 | 306 | 5351 | 269 | 5466 | 274 | 22.3% | 0.02 | 95% | 95% | 95%
GH-01 | QA | Miles | 120 116 | 120 116 | 120 118 | 120 118 | 120 116 | 120 116 | 100% | 95% / 2% | 95% | 95% | 95%
GH-16 | QA | Miles | 4 | 4 | 2 | 2 | 4 | 4 | 100% | 95% / 2% | 95% | 95% | 95%
GH-02 | QA | Distribution Poles | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 100% | 95% / 2% | 95% | 95% | 95%
GH-03 | QA | Transmission Poles | 240 | 240 | 240 | 240 | 240 | 204 | 100% | 95% / 2% | 95% | 95% | 95%
GH-04 | QA | Devices | 4 | 4 | TBD | TBD | TBD | TBD | 100% | 95% / 2% | 95% | 95% | 95%
GH-05 | QA | Fuse Locations | 1500 | 1500 | TBD | TBD | TBD | TBD | 100% | 95% / 2% | 95% | 95% | 95%
GO-01 | QA | Circuits | 3 | 3 | 3 | 3 | 3 | 3 | TBD | 95% / 2% | 95% | 95% | 95%
Return to Table of Contents

## 8-5
Table 8-5: Number of Past Due Asset Work Orders Categorized by Age*
HFTD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 85 | 65 | 54 | 148
HFTD Tier 2 | 0 | 2 | 5 | 78
HFTD Tier 3 | 0 | 3 | 0 | 1
As of 3/25/2025
Return to Table of Contents

## 8-6
Table 8-6: Number of Past Due Asset Work Orders Categorized by Age for Priority Levels
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 85 | 70 | 59 | 227
Priority 3 | 0 | 0 | 0 | 0
As of 3/25/2025
Return to Table of Contents

## 8-7
Table 8-7: Top Ten Impacted Circuits from Changes to PEDS in the Past Three Years
Circuit/Circuit Segment ID | Circuit/Circuit Segment Name | Circuit/Circuit Segment Length (overhead circuit miles) | Number of Outages in Past Three Years | Cumulative Outage Duration (Hours) | Cumulative number of Customers Impacted by Outages
4G1 | 4G1 | 26 | 38 | 141.6 | 10089
6G25 | 6G25 | 52.4 | 35 | 196.8 | 2766
5L82 | 5L82 | 94.7 | 31 | 99.4 | 6565
5G79 | 5G79 | 33.9 | 30 | 112.3 | 21496
5L87 | 5L87 | 66.3 | 28 | 87.5 | 10867
5G23 | 5G23 | 78.1 | 23 | 62.9 | 5126
5G21 | 5G21 | 97.1 | 23 | 59.2 | 7713
5G83 | 5G83 | 78.9 | 23 | 78.7 | 7582
5G41 | 5G41 | 88.2 | 19 | 83.3 | 3951
5G7 | 5G7 | 49.9 | 17 | 112.7 | 7300
Return to Table of Contents

## PAC 8-1
Table PAC 8-1: Current ESS Mode Configurations
Relay | ESS Mode | Expected Fault Operation | Reclosing Action | Coordinates With Reclosers | Action to Restore | Notes
SEL-351 | EFR | Trip, Reclose, Trip, Lockout | Yes | Yes | EFR On, Reclose Off | ESS Mode is Tagged/Reclose Off if EFR not available.
SEL-751 | EFR | Trip, Reclose, Trip, Lockout | Yes | Yes | EFR On, Reclose Off | ESS Mode is Tagged/Reclose Off if EFR not available.
SEL-751A | Tagged/Reclose Off | Trip, Lockout | No | No | Reclose Off | ESS Mode depends on reclosing switch type: 43RT - Tagged 43R - Reclose Off
SEL-651R2 | EFR | Trip, Reclose, Lockout | Yes | Yes | EFR On, Reclose Off | ESS Mode is Tagged if EFR not available.
SEL-651RA | EFR | Trip, Reclose, Lockout | Yes | Yes | EFR On, Reclose Off | ESS Mode is Tagged if EFR not available.
Form 3 | Reclose Off | Trip, Lockout | No | No | Reclose Off
Form 4 | Reclose Off | Trip, Lockout | No | No | Reclose Off
Form 5 | Tagged | Trip, Lockout | No | No | Reclose Off
Form 6 | EFR | Trip, Reclose, Trip, Lockout | Yes | Yes | Reclose Off | ESS Mode is Tagged if EFR not available.
Fusesaver | Tagged (Lever down) | Trip, Lockout | No | No | Lever down
DPU | Tagged/Reclose Off | Trip, Lockout | No | No | Reclose Off | ESS Mode depends on reclosing switch type: 43RT - Tagged 43R - Reclose Off
DPU2000 | Tagged/Reclose Off | Trip, Lockout | No | No | Reclose Off | ESS Mode depends on reclosing switch type: 43RT - Tagged 43R - Reclose Off
DPU2000R | Tagged/Reclose Off | Trip, Lockout | No | No | Reclose Off | ESS Mode depends on reclosing switch type: 43RT - Tagged 43R - Reclose Off
Electromechanical | Tagged/Reclose Off | Trip, Lockout | No | No | Reclose Off | ESS Mode depends on reclosing switch type: 43RT - Tagged 43R - Reclose Off
Return to Table of Contents

## PAC 8-2
Table PAC 8-2: 2024 Reliability Impacts for Circuits Activated in ESS settings
Metric | Number
Number of outages | 354
Average Duration of Outages (minutes) | 219.62
Frequency of Outages per Circuit | 6.81
Number of Customers Impacted | 115224
Average Response Time for Outages (minutes) | 81.61
Return to Table of Contents

## PAC 8-3
Table PAC 8-3: Suppression Equipment
Equipment | Location
Fire Toolbox Containing: | Carried in Vehicle
One backpack pump-type fire extinguisher filled with water,
Two axes
Two McLeod fire tools,
A sufficient number of shovels: A round point shovel with an overall length of not less than forty-six (46) inches so that each employee at the operation can be equipped to fight fire.
2- 250-Gallon Water Trailers | Crescent City, CA
2- 250-Gallon Water Trailers | Yreka, CA
Return to Table of Contents

## PAC 8-4
Table PAC 8-4: T&D Operations Based on Fire Risk Potential
Fire Risk Potential
Practice | Yellow | Orange | Red
PPE Equipment and Tools | X | X | X
Daily How Work Evaluation | X | X | X
Additional Work Evaluation |  | X | X
Cancel Hot Work |  |  | X
Return to Table of Contents

## PAC 8-5
Table PAC 8-5: Asset Inspections, Grid Hardening Qualifications
Worker Title | Minimum Qualifications for Target Role | Special Certification Requirements | Reference to PacifiCorp Training/Qualification Programs
Journeyman Lineman | Qualified Electrical Worker | Journeyman Lineman card | Company provided annual wildfire training
Highline Patrolman | Qualified Electrical Worker | Journeyman Lineman card with patrolman qualifications met | Company provided annual wildfire training
Relay Technician | Qualified Electrical Worker | Journeyman meter and relay card | Company provided annual wildfire training
Highline Patrolman | Journeyman Lineman card with patrolman qualifications met | Journeyman Lineman card and Wire Strike training | Company provided annual wildfire training
Journeyman Wireman | Qualified Electrical Worker | Journeyman Lineman card | Company provided annual wildfire training
Return to Table of Contents

## 9-1
Table 9-1: Vegetation Management Targets by Year (Non-Inspection targets)
Initiative | Quantitative or Qualitative | Activity (Tracking ID) | Previous Tracking ID, if applicable | Target Unit | 2026 Target/Status | % Risk Reduction for 2026 | 2027 Target/Status | % Risk Reduction for 2027 | 2028 Target/Status | % Risk Reduction for 2028 | Three-Year Total | Section; Page Number
Wood and Slash Management/Debris Disposal: benchmark debris management data collection with other California utilities to learn how other utilities conduct and track debris management. | Qualitative | VM-12 | N/A | N/A | Start Initiate benchmarking activities: April 2026 | TBD | Continue benchmarking Consolidate benchmarking data and continue discussion with utilities as needed | TBD | Complete Benchmarking Implement changes/improvements to procedures or data management if applicable: September 2028 | TBD | N/A | 9.5.4 p.284
Defensible Space: Develop hazard tree process for tracking inspection of trees outside of Substation property. | Qualitative | VM-13 VM-26 | N/A | N/A | Process Development Review work management software and identify potential improvements to track inspection of substation perimeters: October 2026 | TBD | Implement Develop and implement work management software improvements, if applicable: December 2027 | TBD | N/A | TBD | N/A | 9.6.4 p. 295
Integrated Vegetation Management: Review and identify opportunities to expand use of tree growth regulator. | Qualitative | VM-14 VM-28 | N/A | N/A | Start Identify additional locations (districts) for use of tree growth regulator if applicable and begin implementation: March 2026 | TBD | In progress Identify additional locations (districts) as applicable and continued implementation of tree growth regulator in locations (districts) identified in 2026, where applicable: December 2027 | TBD | Complete Continued implementation of tree growth regulator in locations (districts) identified in 2026 and 2027, where applicable: 2028 | TBD | N/A | 9.7.4 p. 297-298
Integrated Vegetation Management: develop a process for conducting outreach to known nurseries participating in the tree replacement program. | Qualitative | VM-14 VM-27 | N/A | N/A | Start Develop outreach process and expectations for nursery participation in the tree replacement program: December 2026 | TBD | Implement outreach and coordination with participating nurseries: October 2027 | TBD | Ongoing Implementation N/A | TBD | N/A | 9.7.4 p. 298
Vegetation Management and Inspections: Develop and implement formal inspection contractor benchmarking processes. | Qualitative | VM-15 | N/A | N/A | Start Develop inspection contractor benchmarking (meeting with training/review) expectations and pertinent material: December 2026 | TBD | Implement process with inspection contractors: March 2027 | TBD | Ongoing Implementation Continue annual implementation of inspection contractor benchmarking: December 2028 | TBD | N/A | 9.13.2 p. 321
Return to Table of Contents

## 9-2
Table 9-2: Vegetation Inspections and Pole Clearing Targets by Year
Activity (Program) | Tracking ID | Previous Tracking ID, if applicable | Target Unit | Cumulative (Cml.) Quarterly Target 2026 Q1 | Cumulative (Cml.) Quarterly Target 2026 Q2 | Cumulative (Cml.) Quarterly Target 2026 Q3 | Cumulative (Cml.) Quarterly Target 2026 Q4 | Cumulative (Cml.) Quarterly Target 2027 Q1 | Cumulative (Cml.) Quarterly Target 2027 Q2 | Cumulative (Cml.) Quarterly Target 2027 Q3 | Cumulative (Cml.) Quarterly Target 2027 Q4 | Cumulative (Cml.) Quarterly Target 2028 Q1 | Cumulative (Cml.) Quarterly Target 2028 Q2 | Cumulative (Cml.) Quarterly Target 2028 Q3 | Cumulative (Cml.) Quarterly Target 2028} Q4 | % HFTD Covered in 2026 | % Risk Reduction for 2026 | % Risk Reduction for 2027 | % Risk Reduction for 2028 | Three-Year Total | Activity Timeline Target | Section; Page Number
Routine (Detailed) Inspection – Distribution (DNT) | VM-01 | N/A | Circuit Miles | 378 | 464 | 731 | 824 | 301.08 | 503.39 | 854.81 | 874.82 | 373.97 | 407.86 | 825.81 | 833.77 | 42% | TBD | TBD | TBD | 2532.59 | 365 Days | 9.2.1 p. 268-273
Routine (Detailed) Inspection – Local Transmission (TNT) | VM-02 VM-16 | VM-02 | Circuit Miles | 19 | 114 | 134 | 134 | 160.79 | 461.32 | 478.54 | 478.54 | 83.14 | 134.12 | 141.62 | 141.62 | 43% | TBD | TBD | TBD | 754.16 | 365 Days | 9.2.4 p. 281-283
Routine (Detailed) Inspection – Main Grid (MGI) | VM-02 VM-17 | VM-02 | Circuit Miles | 83 | 130 | 130 | 130 | 44.99 | 130.44 | 130.44 | 130.44 | 83.28 | 134.26 | 141.76 | 141.76 | 71% | TBD | TBD | TBD | 402.2 | 365 Days | 9.2.3 p. 277-281
Off-Cycle (Patrol) Inspection – Distribution (FIN) | VM-03 | N/A | Circuit Miles | 681 | 1109 | 1109 | 1109 | 481.27 | 996.21 | 1035.83 | 1035.83 | 761.12 | 1124.26 | 1183.16 | 1183.16 | 86% | TBD | TBD | TBD | 3327.99 | 365 Days | 9.2.2 p. 273-276
Off-Cycle (Patrol) Inspection – Transmission (FIT) | VM-04 | N/A | Circuit Miles | 104 | 329 | 329 | 329 | 67.68 | 115.58 | 115.58 | 115.58 | 83.14 | 134.12 | 142 417 | 142 417 | 91% | TBD | TBD | TBD | #VALUE! | 365 Days | 9.2.5 p. 284-287
Pole Clearing PRC 4292 (DPL) | VM-05 VM-18 | N/A | Distribution Poles | 3999 | 7998 | 11999 | 11999 | 3999 | 7998 | 11999 | 11999 | 3999 | 7998 | 11999 | 11999 | ~33% | TBD | TBD | TBD | 35997 | 270 Days | 9.4 p. 290-292
Pole Clearing (LRA) | VM-05 VM-19 | N/A | Distribution Poles | 1064 | 2128 | 3192 | 3192 | 1064 | 2128 | 3192 | 3192 | 1064 | 2128 | 3192 | 3192 | ~35% | TBD | TBD | TBD | 9576 | 270 Days | 9.4 p. 290-292
Substation Defensible Space | VM-13 VM-25 | N/A | Substations | 14 | 28 | 42 | 55 | 14 | 28 | 42 | 55 | 14 | 28 | 42 | 55 | 100% | TBD | TBD | TBD | 165 | 365 Days | 9.6 p. 294-295
Return to Table of Contents

## 9-3
Table 9-3: Vegetation Management Inspection Frequency, Method, and Criteria
Type | Inspection Activity (Program) | Area impacted | Frequency
Distribution | Routine | Territory wide | Every three years
Distribution | Off-cycle | Lines within or that intersect HFTD Tier 2 or Tier 3, HFRA | Annual
Transmission | Routine Main Grid | Territory wide | Annual
Transmission | Routine Local | Territory wide | Minimum every three years
Transmission | Non-Routine | Lines within or that intersect HFTD Tier 2 or Tier 3, HFRA | Annual
Return to Table of Contents

## 9-3 Vegetation Management I (2) (hidden)
Table 9-3: Vegetation Management Inspection Frequency, Method, and Criteria
Type | Inspection Activity (Program) | Area impacted | Frequency
Return to Table of Contents

## 9-4
Table 9-4: Partnerships in Vegetation Management
Partnering Agency/ Organization | Activities | Objectives | Electrical Corporation Role | Anticipated Accomplishments
N/A | N/A | N/A | N/A | N//A
Return to Table of Contents

## 9-5
Table 9-5: Vegetation Management QA and QC Program Objectives
Initiative/Activity Being Audited | Activity (Tracking ID #) | Quality Program Type | Objective of the Quality Program
Routine Distribution (Detailed) | VM-11 VM-20 | QC | To ensure contractor pre-inspectors are following electrical corporation procedures, to identify trees that were missed, and to identify work that was not conducted in accordance with requirements.
Off-cycle Distribution (Patrol) Routine Transmission (Detailed) | VM-11 VM-21 | QC | To ensure contractors follow company pre-inspectors are following electrical corporation procedures, to identify trees that were missed, and to identify work that was not conducted in accordance with requirements.
Off-cycle Distribution (Patrol) | VM-22 | QC | To ensure contractors follow company procedures, to identify trees that were missed, and to identify work that was not conducted in accordance with requirements.
Non-Routine Transmission (Patrol) | VM-11 VM-23 | QC | To ensure contractors follow company pre-inspectors are following electrical corporation procedures, to identify trees that were missed, and to identify work that was not conducted in accordance with requirements.
Pole Clearing | VM-11 VM-24 | QC | To ensure work is conducted in accordance with requirements.
Substation Defensible Space | VM-13 | QC | To ensure contractors achieve defensible space around assigned structures according to procedure.
Return to Table of Contents

## 9-6
Table 9-6: Vegetation Management QA and QC Activity Targets
Initiative/Activity Being Audited | Population/Sample Unit | 2026: Population Size | 2026: Sample Size | 2026 Percent of Sample in the HFTD | 2027: Population Size | 2027: Sample Size | 2027 Percent of Sample in the HFTD | 2028: Population Size | 2028: Sample Size | 2028 Percent of Sample in the HFTD | Confidence level/MOE | 2026 Pass Rate target | 2027 Pass Rate target | 2028 Pass Rate target
Routine Distribution (Detailed) | Circuit Miles | 825 | 825* | 42% of Sample miles in HFRA/HFTD | 875 | 875 | 56% of Sample miles in HFRA/HFTD | 834 | 834 | 55% of Sample miles in HFRA/HFTD | N/A | 95% | 95% | 95%
Routine Transmission (Detailed)Tree Maintenance Work | Circuit Miles | 264 | 157 | 50% of Sample miles in HFRA/HFTD | 609 | 214 | 50% of Sample miles in HFRA/HFTD | 284 | 164 | 50% of Sample miles in HFRA/HFTD | 95%/5% | 95% | 95% | 95%
Off-cycle Distribution (Patrol) | Circuit Miles | 1109 | 1109 | 86% of Sample miles in HFRA/HFTD | 1036 | 1036 | 78% of Sample miles in HFRA/HFTD | 1183 | 1183 | 71% of Sample miles in HFRA/HFTD | N/A | 95% | 95% | 95%
Off-cycle Transmission (Patrol) | Circuit Miles | 329 | 329 | 91% of Sample miles in HFRA/HFTD | 116 | 116 | 56% of Sample miles in HFRA/HFTD | 417 | 417 | 73% of Sample miles in HFRA/HFTD | N/A | 95% | 95% | 95%
Pole Clearing (DPL and LRA) | Distribution Poles | 15191 | 1519 | TBD – Target is majority of Sample Poles in HFRA/HFTD | 15191 | 1519 | TBD – Target is majority of Sample Poles in HFRA/HFTD | 15191 | 15,191 1,519 | TBD – target is majority of Sample Poles in HFRA/HFTD | 99% | 95% | 95% | 95%
Defensible Space | Substations | 55 | 28 | TBD | 55 | 28 | TBD | 55 | 28 | TBD | N/A | 95%** | 95% | 95%
*A portion of the corrective maintenance associated Routine Distribution (Detailed) inspections are generally completed late in the calendar year, which results in completion of post audit activities to be completed during the beginning of the following calendar year. Other external factors may also impact completion of post-audits within the same calendar year the maintenance action was completed.
Return to Table of Contents

## 9-7
Table 9-7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier
HFTD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | TBD | TBD | TBD | TBD
HFTD Tier 2 | TBD | TBD | TBD | TBD
HFTD Tier 3 | TBD | TBD | TBD | TBD
Return to Table of Contents

## 9-8
Table 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | TBD | TBD | TBD | TBD
Priority 2 | TBD | TBD | TBD | TBD
Priority 3 | TBD | TBD | TBD | TBD
Return to Table of Contents

## 9-9
Table 9-9: Vegetation Management Qualifications and Training
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | # of PacifiCorp Employees with Min Quals | # of PacifiCorp Employees with Special Certifications | # of Contracted Employees with Min Quals | # of Contractor Employees with Applicable Certifications | Total # of Employees | Reference to PacifiCorp Training /Qualification Programs
Utility Forestry Arborist I (PacifiCorp Forester) | Degree in vegetation management, forestry or related field or the equivalent combination of education and experience | ISA Arborist ISA Utility Specialist | 6 | 5 | N/A | N/A | 6 | Vegetation SOP
Utility Forestry Arborist II (PacifiCorp Forester) | Degree in vegetation management, forestry or related field or the equivalent combination of education and experience (minimum three years related experience) | ISA Arborist ISA Utility Specialist | 0 | N/A | N/A | N/A | 0 | Vegetation SOP
Utility Forestry Arborist III (PacifiCorp Forester) | Degree in vegetation management, forestry or related field or the equivalent combination of education and experience (minimum three-five years related experience) | ISA Arborist ISA Utility Specialist | 2 | 2 | N/A | N/A | 2 | Vegetation SOP
Sr, Utility Forestry Arborist (PacifiCorp Forester) | Degree in vegetation management, forestry or related field or the equivalent combination of education and experience (minimum ten years related experience) | ISA Arborist ISA Utility Specialist | 5 | 4 | N/A | N/A | 5 | Vegetation SOP
Vegetation Manager (PacifiCorp Forester) | Degree in vegetation management, forestry or related field or the equivalent combination of education and experience (minimum seven years related experience and three years of supervisory role) | ISA Arborist ISA Utility Specialist | 2 | 2 | N/A | N/A | 2 | Vegetation SOP
Forest Technician I | Required to obtain ISA Arborist certification within six months | N/A | N/A | N/A | N/A | TBD | TBD | Vegetation SOP
Forest Technician II | Minimum two years arboricultural-related experience or combination of education and practical experience | ISA Arborist | N/A | N/A | N/A | TBD | TBD | Vegetation SOP
Forest Technician III | Minimum three years arboricultural-related experience or combination of education and practical experience | ISA Arborist ISA Utility Specialist | N/A | N/A | N/A | TBD | TBD | Vegetation SOP
Forest Technician IV | Minimum three years arboricultural-related experience or combination of education and practical experience | ISA Arborist ISA Utility Specialist ISA Tree Risk Assessment Qualification Herbicide applicator license or similar | N/A | N/A | TBD | TBD | TBD | Vegetation SOP
Supervisors (e.g., General Foreperson) | Determined by Contractor | ISA Arborist ISA Utility Specialist Herbicide applicator license or similar | N/A | N/A | TBD | TBD | TBD | Vegetation SOP
Crew Leaders and Tree Trimmers | Determined by Contractor/Union | Qualified Line Clearance or Qualified Line Clearance Trainee | N/A | N/A | TBD | TBD | TBD | Vegetation SOP
Return to Table of Contents

## PAC 9-1
Table PAC 9-1: Distribution Minimum Post-Work Vegetation Clearance Distances
Clearance | Slow Growing (<1 ft/yr.) | Moderate Growing (1-3 ft/yr.) | Fast Growing (> 3 ft./yr.)
Side Clearance | 12 ft. | 12 ft. | 14 ft.
Under Clearance | 12 ft. | 14 ft. | 16 ft.
Overhang Clearance | 12 ft. | 14 ft. | 14 ft.
Return to Table of Contents

## PAC 9-2
Table PAC 9-2: Transmission Clearance Requirements
Line Voltage
| 500 kV | 345 kV | 230 kV | 161 kV | 138 kV | 115 kV | 69 kV | >69 kV
MVCD | 8.5 ft | 5.3 ft | 5.0 ft | 3.4 ft | 2.9 ft | 2.4 ft | 1.4 ft | N/A
Action Thresholds | 18.5 ft | 15.5 ft | 15 ft | 13.5 ft | 13 ft | 12.5 ft | 10.5 ft | 10 ft
Minimum Clearances Following Work | 50 ft | 40 ft | 30 ft | 30 ft | 30 ft | 30 ft | 25 ft | 20 ft
Return to Table of Contents

## 10-1
Table 10-1: Situational Awareness Targets by Year
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID, if applicable | Target Unit | 2026 End of Year Total/Completion Date | % Risk Reduction for 2026 | 2027 Total/Status | % Risk Reduction for 2027 | 2028 Total/Status | % Risk Reduction for 2028 | Three-year Total | Section; Page number
Situational Awareness Tools and Models | Qualitative | SA-05 SA-11 | SA-05 | N/A | -Extension of WRF Reanalysis -Annual updates to fuels models -Annual review of wildfire criteria | TBD | -Extension of WRF Reanalysis -Annual updates to fuels models -Annual review of wildfire criteria | TBD | -Extension of WRF Reanalysis -Annual updates to fuels models -Annual review of wildfire criteria | TBD | N/A | 10.5.3 p. 367
Implement WRF Ensemble Forecasting | Qualitative | SA-05 SA-12 | SA-05 | N/A | Implemented, March 2026 | TBD | N/A | TBD | N/A | TBD | N/A | 10.5.3 p. 367
Climate Vulnerability Assessment | Qualitative | SA-05 SA-13 | N/A | N/A | Study Underway Delivery of modeled climate change impacts to seasonal weather averages and extreme weather events in September 2026 | TBD | Study Delivered Preliminary review of asset climate vulnerability for potential use in design standards and wildfire risk modeling | TBD | N/A | TBD | N/A | 10.5.3 p. 368
Machine Learning techniques of Normalized Differential Vegetation Index (NDVI) and Self Organizing Maps (SOMs) | Qualitative | SA-05 SA-14 | N/A | N/A | NDVI Complete & SOMs in-progress, July 2026 | TBD | NDVI reviewed and updated & SOMs Complete, July 2027 | TBD | N/A NDVI reviewed and updated, July 2028 | TBD | N/A | 10.5.3 p. 368
Fire Potential Index (FPI) Improvements | Qualitative | SA-06 | SA-06 | N/A | Annual evaluation of FPI performance and updates as needed | TBD | Annual evaluation of FPI performance and updates as needed | TBD | Annual evaluation of FPI performance and updates as needed | TBD | N/A | 10.6.3 p. 377
Weather Station Maintenance and Calibration | Quantitative | MA-01 | MA-01 | Weather Station Fleet | 100% | TBD | 100% | TBD | 100% | TBD | 100% | 10.5.5 p. 370-371
Expansion of Weather Station Network | Quantitative | SA-01 | SA-01 | Weather Stations | 5 | TBD | 4 | TBD | 0 | TBD | 9 | 10.2.3 p. 329-331
Installation of cFCI | Quantitative | SA-02 SA-07 | N/A | Devices | 30 | TBD | 30 | TBD | 30 | TBD | 90 | 10.3.3 p. 342
Installation of SCAN | Quantitative | SA-02 SA-08 | N/A | Locations | 20 | TBD | 20 | TBD | 0 | TBD | 40 | 10.3.3 p. 342
Distribution Protective Settings Review | Quantitative | SA-02 SA-09 | N/A | N/A | TBD | TBD | TBD | TBD | TBD | TBD | N/A | 10.3.3 p. 343
Installation of Advanced AMI Meters | Quantitative | SA-02 SA-10 | N/A | Meters | 5000 | TBD | 0 | TBD | 0 | TBD | 5000 | 10.3.3 p. 343
Return to Table of Contents

## 10-2
Table 10-2: Environmental Monitoring Systems
System | Measurement/ Observation | Frequency | Purpose and Integration
Microstation | Temperature, Humidity, Wind Speed & Gust, Wind Direction, Rainfall | 10 min | Improve weather modeling and forecasts, improve real time weather data and inform operational decisions.
RAWS Weather Station | Temperature, Humidity, Wind Speed & Gust, Wind Direction, Rainfall, and 10-hour Dead Fuel Moisture | 10 min | Improve understanding of fuel moisture near infrastructure, weather forecasts and real time situational awareness in remote locations
Portable Stations | Temperature, Humidity, Wind Speed & Gust, Wind Direction, Rainfall | 5 min | Deployed as needed in areas where additional weather data is necessary to temporarily increase weather data granularity for situational awareness.
Return to Table of Contents

## 10-3
Table 10-3: Grid Operation Monitoring Systems
System | Measurement/ Observation | Frequency | Purpose and Integration
Line Sensors: cFCI Distribution (≤35kV) | Current, eField, Conductor Temperature / Fault current magnitude, Oscillography | Fault current magnitudes captured and oscillography by condition based thresholds. 5-min to hourly interval logging current, efield and conductor temperature parameters. | Fault locating/restoration and precursors: supports zone based patrol and predictive location modeling with short circuit analysis. Interval data: supports loadflow engineering studies. Integrations: EMS/SCADA, Pi Historians, Web dashboard
Line Sensor: Early Fault Detection | Partial discharge, time-synchronized high frequency RF emissions (nano-joules), coupled to transmission lines / RF source location/distance from measurement point and intensity | Once per-second | Detection of localized defects in overhead insulators and conductors, baselining line characteristics and change detection. Integrations: Web dashboard and email alerts.
Line Sensor: Gridware | Vibration, eField, acoustics, optical camera / Structure failure, tree impact, voltage presence, visual field conditions | Event occurrence: impact to line, structure failure, loss of voltage | Integrations: Web dashboard, email alerts, phone-calls to control center.
Circuit Breaker/Recloser Monitoring: SCAN | Current, Voltage / Relay fault current magnitudes, breaker operation, event based COMTRADE files, and sequence of event records | Fault current magnitudes and event reported upon occurrence. Continuous retrieval of sequence of event records. | Fault locating/restoration and precursors: predictive location modeling with short circuit analysis. Analysis of protective device coordination and event pre-cursers Integrations: EMS/SCADA, Pi Historians Web dashboard
Circuit Breaker/Recloser Monitoring: DFA | Current, Voltage / Oscillography, fault current magnitudes, breaker operation, series/shunt arcing events | Fault current magnitudes and event reported upon occurrence | Fault locating/restoration and precursors: predictive location modeling with short circuit analysis. Analysis of protective device coordination and event pre-cursers Integrations: Web dashboard and email alerts.
Return to Table of Contents

## 10-4
Table 10-4: Fire Detection Systems Currently Deployed
Detection System | Capabilities | Companion Technologies | Contribution to Fire Detection and Confirmation
High-Definition Cameras | AI software 24/7 to support early detection of ignitions | Satellite Imagery Weather Station Data Fire Modeling Software | Supports wildfire-reactive responses to ignition
Fire Modeling Software | 1-126 hour forecast of the wildfire potential and consequence if there is a wildfire | Weather Research and Forecasting (WRF) | Provides identification of areas that may require additional monitoring due to conditions
Return to Table of Contents

## 10-5
Table 10-5: Fire Potential Index Features
Feature Group | Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
Weather | Wind, sustained and gusts | 10m | Wind speed and gust measured | Internal PacifiCorp WRF | Twice daily | 2km | Hourly
Fuel Complexity | Fuel type, fuel load and fuel age | Surface | Quantifies the fuel type, fuel load and fuel age | Technosylva | Annually | 30m | N/A
Weather | Relative humidity, vapor pressure deficit | Surface | Moisture variable from the atmosphere | Internal PacifiCorp WRF | Twice daily | 2km | Hourly
Terrain | Terrain Difficulty Index | N/A | Quantifies the terrain and its potential impacts on suppression activity including accessibility, fuel penetrability, and ease of opening fire line. | Technosylva | Annually | 30m | N/A
Fuel Moisture | 1 and 10 hour dead fuel moisture | 10m | Moisture of dead fuels | Internal PacifiCorp WRF | Twice daily | 2km | Hourly
Fuel Moisture | Woody and Herbaceous Live Fuel moisture | 10m | Moisture of live fuels | Remote Sensing data | Daily |  | Hourly
Return to Table of Contents

## PAC 10-1
Table PAC 10-1: Planned Grid Monitoring System Improvements
System | Description | Impact | % Risk Impact Implementation Schedule | Implementation Schedule
Line Sensors: cFCI Distribution (≤35kV) | Installation of line sensors capable of detecting and reporting overcurrent events and faults in HFTD. | Early detection and localization of overcurrent events enables proactive corrective actions to be taken; if a fault occurs localization improve response time | TBD | Install an average of nine to 15 line sensors on HFTD circuits.
Circuit Breaker/Recloser Monitoring/Control: SCAN | Installation of communications network infrastructure and operational technology enabling retrieval of relay event files and control of operation state | Control of operational state enables activation of fast-acting overcurrent protection and high-impedance fault detection algorithms. Event files enable root cause analysis, evaluation of protection system effectiveness, and identifying opportunities for improvement. | TBD | Installation to communications infrastructure at up to 30 field recloser locations in 2026 and 2027
AMI: Advanced Bellwether Meters | Installation of advanced AMI meters at bellwether location to facilitate detection of broken energized downed conductors and localization of high-impedance faults | Early detection and localization of voltage abnormalities on distribution networks. Algorithmic processing of alarms with physics-based models enables event detection; correlations with high-impedance alarms from protective relays enhances localization. | TBD | Installation of up to 5,000 bellweather meters in 2026
Distribution Protective Settings Review | Update protection devices where implementation of settings did not occur at the time of installation | Reduction in sustained outage frequency when using EFR versus Tagged. The initiative reviewed the settings previously issued for the devices that are in scope and after the settings are reviewed, ensured they are re-issued and installed to the current standard. | TBD | Updates completed by end of 2026
Distributed Sensor Operation Insights and Analytics | Development of a platform integrating event records from protective relays, distribution cFCI sensors, and other grid-edge devices.; | Enables improved situational awareness, detection and localization of energized downed conductors, impending faults, high-impedance fault precursors and quantitative assessment protection settings performance. | TBD | 2026: Anticipated Production Release 2027: Ongoing Implementation 2028: Maintenance
Return to Table of Contents

## PAC 10-2
Table PAC 10-2: FireRisk and FireSim Weather Inputs
Feature Group | Description | Spatial Granularity (meters) | Temporal Granularity | Data Vintage | Source
Landscape | Terrain | 10 | Yearly |  | United States Geological Survey (USGS)
Landscape | Surface Fuels | 30/10 | Pre Fire Season, Monthly Update In Fire Season, End Of Fire Season | 2020 | Technosylva
Landscape | WUI and Non Forest Fuels Land Use | 30/10 | Twice A Year | 2020 | Technosylva
Landscape | Canopy Fuels (Cbd,Ch,Cc,Cbh) | 30/10 | Pre Fire Season, Monthly Update In Fire Season, End Of Fire Season | 2020 | Technosylva
Landscape | Roads Network | 30 | Yearly |  | USGS
Landscape | Hydrography | 30 | Yearly |  | USGS
Landscape | Croplands | 30 | Yearly | 1997 | United States Department of Agriculture
Weather and Atmosphere | Wind Speed | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Wind Direction | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Wind Gust | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Air Temperature | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Surface Pressure | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Relative Humidity | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Precipitation | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Radiation | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Water Vapor Mixing Ratio 2m | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Weather and Atmosphere | Snow Accumulated - Observed | 1000 | Daily |  | NOAA
Weather and Atmosphere | Precipitation Accumulated - Observed | 4000 | Daily |  | NOAA
Weather and Atmosphere | Burn Scars | 10 | 5 Days | 2000 | NASA/ESA
Weather and Atmosphere | Weather Observations Data | Points | 10 Min |  | Synoptic
Fuels | Herbaceous Live Fuel Moisture | 250 | Daily / 5-Day Forecast | 2000 | Technosylva
Fuels | Woody Live Fuel Moisture | 250 | Daily / 5-Day Forecast | 2000 | Technosylva
Fuels | 1 Hr. Dead Fuel Moisture | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Fuels | 10 Hr. Dead Fuel Moisture | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Fuels | 100 Hr. Dead Fuel Moisture | 2000 | Hourly / 126 Hour Forecast |  | Technosylva
Fuels | 1000 Hr. Dead Fuel Moisture | 2001 | Hourly / 126 Hour Forecast |  | Technosylva
Return to Table of Contents

## 11-1
Table 11-1: Emergency Preparedness and Community Outreach Targets by Year
Initiative | Activity (Tracking ID #) | Previous Tracking ID, if applicable | 2026 End of Year Total/Completion Date | 2027 Status | 2028 Status | Section; Page number
Conduct pre-season and post-season customer surveys to assess understanding of messaging and information shared by PacifiCorp and inform adjustments in messaging. | CO-01 CO-05 | CO-01 | -Conduct pre-season survey -Conduct post-season survey | -Conduct pre-season survey -Conduct post-season survey | -Conduct pre-season survey -Conduct post-season survey | 11.4.6 p.428 429
Create a way for non-account holders to register for outage/emergency alerts | CO-01 CO-06 | N/A | Create alerts system for non-account holders and socialize new alerts system to customers. | N/A | N/A | 11.4.6 p.428 429
Continue to identify customers who are Electricity Dependent | CO-02 CO-07 | CO-02 | - Enhance existing marketing and outreach campaigns based on data and feedback received through surveys and interviews - Continue to work with CBOs, regional centers and healthcare organizations to ensure their clients are informed about available PSPS resources - Partner with Wildfire Advisory Board members and other AFN service providers to better understand the needs of AFN customers and gaps in PacifiCorp’s current offerings | - Enhance existing marketing and outreach campaigns based on data and feedback received through surveys and interviews - Continue to work with CBOs, regional centers and healthcare organizations to ensure their clients are informed about available PSPS resources - Partner with Wildfire Advisory Board members and other AFN service providers to better understand the needs of AFN customers and gaps in PacifiCorp’s current offerings | - Enhance existing marketing and outreach campaigns based on data and feedback received through surveys and interviews - Continue to work with CBOs, regional centers and healthcare organizations to ensure their clients are informed about available PSPS resources - Partner with Wildfire Advisory Board members and other AFN service providers to better understand the needs of AFN customers and gaps in PacifiCorp’s current offerings | 11.4.6 p. 245-427, 429
Coordinate and integrate resources with state, community and utility to minimize duplication of AFN programs | CO-02 CO-08 | N/A | - Identify opportunities and efficiencies to ease Medical Baseline (MBL) program enrollment in accordance with CPUC and legislative framework | - Identify opportunities and efficiencies to ease Medical Baseline (MBL) program enrollment in accordance with CPUC and legislative framework | - Identify opportunities and efficiencies to ease Medical Baseline (MBL) program enrollment in accordance with CPUC and legislative framework | 11.4.6 p. 245-427, 429
Identify enhancements to programs and resources needed to mitigate the impacts of PSPS on AFN customers | CO-02 CO-09 | CO-02 | - Continue to review customer feedback from PSPS survey results, including CRC survey results, to benchmark and evaluate if programmatic changes are needed to enhance existing resources and support | - Continue to review customer feedback from PSPS survey results, including CRC survey results, to benchmark and evaluate if programmatic changes are needed to enhance existing resources and support | - Continue to review customer feedback from PSPS survey results, including CRC survey results, to benchmark and evaluate if programmatic changes are needed to enhance existing resources and support | 11.4.6 p. 245-427, 429
Increase awareness of PacifiCorp's programs and services available for AFN customers before, during and after a PSPS | CO-02 CO-10 | CO-02 | - Increase awareness among PacifiCorp’s Wildfire Advisory Board (Board) members via presentations/materials - Engage with the Board, CBOs, health care coalitions and other local AFN service providers to identify opportunities to amplify AFN program messaging - Explore making appropriate updates to PSPS materials to reflect the needs of individuals with AFN | - Increase awareness among PacifiCorp’s Wildfire Advisory Board (Board) members via presentations/materials - Engage with the Board, CBOs, health care coalitions and other local AFN service providers to identify opportunities to amplify AFN program messaging - Explore making appropriate updates to PSPS materials to reflect the needs of individuals with AFN | - Increase awareness among PacifiCorp’s Wildfire Advisory Board (Board) members via presentations/materials - Engage with the Board, CBOs, health care coalitions and other local AFN service providers to identify opportunities to amplify AFN program messaging - Explore making appropriate updates to PSPS materials to reflect the needs of individuals with AFN | 11.4.6 p. 429
Develop and update wildfire de-energization materials for customers to communicate PacifiCorp Emergency De-Energization for Wildfire. | CO-03 | N/A | -Update emergency de-energization materials for 2026 wildfire season and paid advertising campaigns. -Present on emergency de-energization in California WMP Webinar. Include emergency de-energization information in pre-season customer emails. | -Update emergency de-energization materials for 2026 wildfire season and paid advertising campaigns. -Present on emergency de-energization in California WMP Webinar. Include emergency de-energization information in pre-season customer emails. | -Update emergency de-energization materials for 2026 wildfire season and paid advertising campaigns. -Present on emergency de-energization in California WMP Webinar. Include emergency de-energization information in pre-season customer emails. | 11.4.6 p. 428-429
Western Wildfire Communications Workshop | CO-04 | N/A | Complete two workshops | Complete two workshops | Complete two workshops | 13.2 p. 447
Review and update outage procedures in ERP plan-Restoration Annex | EP-01 | N/A | Plan reviewed and updated as identified. | Plan reviewed and updated as identified. | Plan reviewed and updated as identified. | 11.2 p. 381
Continue the use of tabletop exercises to prepare for emergencies and PSPS events. | EP-02 | EP-02 | 1 Functional Exercise (FE), 1 Tabletop Exercise (TTX), 1 Workshop Dates for 2026 TBD | 1 (FE), 1 (TTX), 1 workshop Date for 2027 TBD | 1 (FE), 1 (TTX), 1 workshop Dates for 2028 TBD | 11.3.2 p. 405-407
Implement improvement to Public Safety Partner Portal (PSP Portal) | EP-03 | EP-03 | N/A | Security Improvements | Reporting Improvements | 11.3.1 p. 401-402
Return to Table of Contents

## 11-2
Table 11-2: Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Limited feedback from partners on PSPS playbook during workshop review. | Limited feedback from partners on PSPS playbook during workshop review. | Continue outreach, training, and exercise with partners to ensure alignment of plans, roles and expectations during system events. Target Timeline: Annually by June 30
Return to Table of Contents

## 11-3
Table 11-3: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners
Public Safety Partner Group | Name of Entity | Key Protocols | Frequency of Prearranged Communication Review and Update
Emergency Management | California State OES | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Del Norte County OES | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Modoc County OES | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Shasta County OES | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Siskiyou OES | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Hoopa Tribe | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Karuk Tribe | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Quartz Valley Indian Reservation | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Tolowa Dee-ni’ Tribe | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Emergency Management | Yurok Tribe | Public Safety Partner Portal, Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Quarterly
Telecommunications | Siskiyou Telephone | Public Safety Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Biannual PSPS exercises: TTX and FE
Telecommunications | AT&T | Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Biannual PSPS exercises: TTX and FE
Telecommunications | Frontier Communications | Email, Phone, Voice, Meetings, Exercises ERP Annex 01 External Emergency Coordination and Communications. | Biannual PSPS exercises: TTX and FE
Return to Table of Contents

## 11-4
Table 11-4: Example of Key Gaps and Limitations in Communication Coordination with Public Safety Partners
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Feedback on PSPS Playbook | No feedback on the 2025 PSPS Playbook updates during the CA Wildfire Advisory board meeting on 03/21/2025 | Walk through the PSPS playbook in greater detail during the pre-wildfire season meeting with the California Wildfire Advisory Board (WAB) in March to further engage the Board in preparation for the TTX and FE in April and May. Target Timeline: March 2025 WAB Meeting and 2025 TTX and FE
Return to Table of Contents

## 11-5
Table 11-5: Collaboration in Local and Regional Wildfire Mitigation Planning
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
California State OES | Wildfire Mitigation Plan, PSPS, ECC Activations | Spring 2025 | Quarterly
Del Norte County OES | Wildfire Mitigation Plan, PSPS, and Community Wildfire Protection | Spring 2025 | Quarterly
Modoc County OES | Wildfire Mitigation Plan, PSPS, and Community Wildfire Protection | Spring 2025 | Quarterly
Shasta County OES | Mitigation Plan, PSPS, and Community Wildfire Protection | Spring 2025 | Quarterly
Siskiyou County OES | Wildfire Mitigation Plan, PSPS, and Community Wildfire Protection | Spring 2025 | Quarterly
Hoopa Tribe | Wildfire Mitigation Plan, PSPS | Spring 2025 | Quarterly
Karuk Tribe | Wildfire Mitigation Plan, PSPS | Spring 2025 | Quarterly
Emergency Management | Quartz Valley Indian Reservation | Summer 2025 | Quarterly
Tolowa Dee-ni’ Tribe | Wildfire Mitigation Plan, PSPS | Spring 2025 | Quarterly
Yurok Tribe | Wildfire Mitigation Plan, PSPS | Spring 2025 | Quarterly
Siskiyou Telephone | Wildfire Mitigation Plan, PSPS | Spring 2025 | Biannual PSPS exercises: TTX and FE
AT&T | Wildfire Mitigation Plan, PSPS | Spring 2025 | Biannual PSPS exercises: TTX and FE
Frontier Communications | Wildfire Mitigation Plan, PSPS | Spring 2025 | Biannual PSPS exercises: TTX and FE
Return to Table of Contents

## 11-6
Table 11-6: Key Gaps and Limitations in Collaborating on Local and Regional Wildfire Mitigation Planning
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Minimal feedback received from exercise participants. | During the 2024 exercise series limited engagement occurred and little to no feedback was provided by attendees | Encourage participation during exercise and feedback following exercise by way of survey. Encourage conversation and questions during Wildfire Safety Advisory Board (WSAB) meetings. WSAB meetings are held bi-annually and are scheduled pre- and post-wildfire season (usually March and November). Meetings include a workshop to review the PSPS playbook along with discussion regarding program and process improvement. Tabletop and functional exercises are held pre-season and include participation from public safety partners, representation from Tribal Nations, and shareholders.
Return to Table of Contents

## 11-7
Table 11-7: Collaboration with Tribal Agencies
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Karuk Tribe | Wildfire Mitigation Plan, PSPS, Cultural Monitoring Plan | Spring 2025 | Quarterly
Yurok Tribe | Wildfire Mitigation Plan, PSPS | Spring 2025 | Quarterly
Quartz Valley Indian Reservation | Wildfire Mitigation Plan, PSPS | Summer 2025 | Quarterly
Tolowa Dee-ni’ Nation | Wildfire Mitigation Plan, PSPS | Spring 2025 | Quarterly
Shasta Tribe | Wildfire Mitigation Plan, PSPS | Spring 2025 | Quarterly
Shasta Tribe | Wildfire Mitigation Plan, PSPS, Cultural Monitoring Plan | Spring 2025 | Quarterly
Return to Table of Contents

## 11-8
Table 11-8: Key Gaps and Limitations in Collaborating with Tribal Agencies
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
Communication/Outreach | Assembling correct contact info for individual Tribes | Centralized location for contact workbook/spreadsheet and staff assigned to keep it current.
Cultural competency | Having an understanding of Tribal governments and their assets, what is of cultural and historical importance, etc. | Internal trainings through the Tribal Liaison Representative
Relationship-building | Cultivating partnerships with Tribes | Identify issues of mutual interest and commonalities; ways to support, etc.
Creating a formal MOU or official document about mutual support during emergencies - | Have a reciprocal agreement with Tribes for emergency needs such as a lease agreement for emergency use of Tribal lands; access to facilities, vehicles, etc. | Support from leadership in PacifiCorp and Tribal leadership.
Return to Table of Contents

## 11-9
Table 11-9: Protocols for Emergency Communication to Stakeholder Groups
Stakeholder Group/Target Community | Event Type | Method(s) for Communicating | Means to Verify Message Receipt | Interests or Concerns Before, During, and After Wildfire and PSPS events
General Public | Wildfire | Media release, interviews, social media, website, standard customer notification via all available channels. | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | How long will the event last, where to learn more information, steps to take to be prepared during an outage
General Public | Wildfire-related outage | Media release, interviews, social media, website, direct customer calls, standard customer notification via all available channels | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | How long will the event last, where to learn more information, steps to take to be prepared during an outage
General Public | PSPS-related outage | Media release, interviews, social media, website, standard PSPS customer notifications via all available channels | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | How long the event will last, where to learn more information, steps to take to be prepared during an outage, resources available at CRCs
General Public | Restoration of service | Media release, interviews, social media, website, standard customer notification via all available channels | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | How long the event will last, where to learn more information, how to contact PacifiCorp for restoration issues
Priority Essential Services | Wildfire | Emergency Management personnel, Public Safety Partners, ESF12, RBMs | Customer notifications (call, email, phone) verified/tracked through customer notification too and direct outreach from Emergency Management or RBM | How long will the outage last, will generator support be provided for facilities if they do not have generators.
Priority essential services | Wildfire-related outage | Emergency Management personnel, Public Safety Partners, ESF12, Regional Business Managers (RBMs) | Customer notifications (call, email, phone) verified/tracked through customer notification too and direct outreach from Emergency Management or RBM | How long will the outage last, will generator support be provided for facilities if they do not have generators.
Priority essential services | PSPS-related outage | Emergency Management personnel, Public Safety Partners, ESF12, RBMs, Public Safety Partner Portal | Customer notifications (call, email, phone) verified/tracked through customer notification too and direct outreach from Emergency Management or RBM | How long will the outage last, will generator support be provided for facilities if they do not have generators.
Priority essential services | Restoration of service | Emergency Management personnel, Public Safety Partners, ESF12, RBMs , | Customer notifications (call, email, phone) verified/tracked through customer notification too and direct outreach from Emergency Management or RBM | How long will the outage last, will generator support be provided for facilities if they do not have generators.
AFN populations | Wildfire | Media release, interviews, social media, website, standard customer notification via available channels | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | How long will outage last, programs to support medical/AFN customers, update contact information, steps to take to be prepared for an outage
AFN populations | Wildfire-related outage | Media release, interviews, social media, website, standard customer notification via available channels | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | How long will outage last, programs to support medical/AFN customers, update contact information, steps to take to be prepared for an outage .
AFN populations | PSPS-related outage | Standard PSPS notification via all available channels; plus additional PSPS notifications via personal phone calls; and possible in person welfare check if unable to reach via phone | Confirm via personal phone call or welfare check | How long will outage last, programs to support medical/AFN customers, how PacifiCorp communicate with customers with medical certificate and others who have self-identified as having an AFN, resources available at CRCs
AFN populations | Restoration of service | Standard customer notification via all available channels | Confirm via personal phone call or welfare check | Limited awareness of PacifiCorp’s de-energization process, including restoration and how the Company communicates with customers that have self-identified as having an AFN (including customers in the medical certificate and medical baseline programs) during each phase. How to contact PacifiCorp for restoration issues
Populations with limited English proficiency | Wildfire, wildfire related outage, PSPS-related de-energization, restoration of service | Media release, interviews, social media, website translated content in key languages: English, Spanish, standard customer notification via all available channels | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | Limited awareness of PacifiCorp’s de-energization process, including restoration and how the Company communicates with Customers and communities during each phase. Resources available to support customers such as CRCs during a PSPS. How to contact PacifiCorp for restoration issues
Tribes | Wildfire, wildfire related outage, PSPS-related de-energization, restoration of service | Emergency Management personnel, Public Safety Partners, ESF12, RBMs, Media release, interviews, social media, website; standard customer notification via all available channels | Customer notifications (call, email, phone) verified/tracked through customer notification too and direct outreach from Emergency Management or RBM | Limited awareness of PacifiCorp’s de-energization process, including restoration and how the Company communicates with Customers and communities during each phase. Resources available to support customers such as CRCs during a PSPS. How to contact PacifiCorp for restoration issues
People in remote areas | Wildfire, wildfire related outage, PSPS-related de-energization, restoration of service | Media release, interviews, social media, website, standard customer notification via all available channels | Social media/media releases verified on Pacific Power website and social media channels; Customer notifications (call, email, phone) verified/tracked through customer notification tool | Limited access to information and resources based upon geographical location and available essential services. Resources available to support customers such as CRCs during a PSPS. How to contact PacifiCorp for restoration issues. High fire risk areas in need of information on defensible space.
Return to Table of Contents

## 11-10
Table 11-10: List of Target Communities
Target Community | Interests or Concerns Before, During, and After Wildfire and PSPS events
AFN populations including Medical Baseline customers | Limited access to information and resources to prepare for wildfire. Limited awareness of Pacific Power’s PSPS process, including restoration and how we communicate with customers that have self-identified as having an AFN (including customers in the medical certificate and medical baseline programs) during each phase.
Community Based Organizations | These organizations are established in the communities as entities that provide essential and consistent services to the residents and are a place that residents rely on for information. In working with these organizations, PacifiCorp can provide wildfire and PSSP information before, during and after an event which provides an additional reach to customers that may not seek out information on PacifiCorp’s website, App and customer service.
Rural Residential Customers | Limited access to information and resources based upon geographical location and available essential services. Information on defensible space, understanding the steps we take to initiate a PSPS event and how the restoration process is conducted and how we communicate with customers during each phase
Commercial Customers that have a high impact of essential services to a small community with limited resources | Working with essential service businesses and those that provide considerable employment or resources to a community. To provide timely information when PacifiCorp is preparing for a PSPS event to mitigate adverse effects to available services and resources within the community by the businesses having time to implement continuity plans.
Return to Table of Contents

## 11-11
Table 11-11: Key Gaps and Limitations in Public Emergency Communication Strategy
Gap or Limitation Subject | Brief Description of Gap or Limitation | Remedial Action Plan
PSPS Awareness | Customer recall of PSPS fluctuates based on most recent PSPS occurrence; Customer recall of PSPS fluctuates pre-season (lower) to post-season (higher) | Strategy: Focus communications on preparedness for outage, whether due to PSPS or other factors. Promote PacifiCorp website as a resource for information (e.g., via bill insert, social media) Target Timeline: Year round
Generator Rebate Program | Customer awareness of generator rebate program remains low (8%) | Strategy: Add/ emphasize information about the generator rebate program to preparedness communications Target Timeline: Year-round in alignment with outage awareness communications
Wildfire Safety Communications Awareness | Wildfire safety awareness among customers fluctuates pre-season (lower) vs. Post-season (higher) | Strategy: Reevaluate off season messaging and cadence in pre-fire season survey. Target Timeline: Year Round, following customer survey findings
Master meter PSPS tenant notifications | Tenants do not receive PSPS notifications. Only the master meter/account holder (i.e. landlord, property manager) will receive these notifications. | Add master meter/account holder tenant reminder in all PSPS notifications: Create a master meter toolkit to notify tenants about PSPS via email/mail Target Timeline: 2026
AFN Customer Program Awareness | Customers lack awareness of programs to support AFN preparedness and resilience, resulting in low AFN self identification and program participation | Develop AFN self identification webform Enhance Accessibility Program Toolkit for Partners Target Timeline: 2026
Emergency de-energizations | Customers are unaware of PacifiCorp’s process for emergency de-energizations and why they occur. | Communicate emergency de-energization in annual WMP webinar. Target Timeline: Annually by end of Q2
Communications and Outreach to Smaller Agencies | Smaller agencies such as rural/volunteer fire departments or community centers need information on PacifiCorp’s wildfire and PSPS processes and communications during an incident but can feel overwhelmed by information coming from multiple Company sources. | Working internally on streamlining processes to have the right communications at the right time and the right channels. Target Timeline: 2027
Engagement With Tribal Nations on PSPS and wildfire processes and communications. | Need for pre-wildfire season outreach and education for Tribal Nations of PacifiCorp’s PSPS and wildfire response processes. Share PacifiCorp’s new EM & Fire Response resources/contact information. | Meet with Tribal Nations to discuss PacifiCorp’s processes for Wildfire, PSPS and other emergencies. Maintain current database of who their point of contact is at PacifiCorp, Target Timeline: 2026
Return to Table of Contents

## 12-1
Table 12-1: Enterprise Systems Targets
Initiative | Activity (Tracking ID #) | Previous Tracking ID, if applicable | 2026 End of Year Total/Completion Date | 2027 Status | 2028 Status | Section; Page number
Business Transformation Wave 4: Maximo* | ES-01 ES-02 | N/A | Design complete by EOY. Development in flight. | Anticipated production release 2027 | Maintenance | 12.2 p. 439
Data Integration (Foundry) | ES-01 ES-03 | RA-04 | Implement Annual review of data and implementation of updates | N/A Annual review of data and implementation of updates | N/A Annual review of data and implementation of updates | 10.5.3 p. 368
Distributed Sensor Operation Insights and Analytics | ES-01 ES-04 | N/A | Anticipated Production Release Establishment of API integrations with headend systems collecting distribution cFCI and protective relay event records and AMI Datalake; December 2026 | Ongoing Implementation Use case implementation of analytics supporting the reconciliation of event records against known outages; December 2026 | Maintenance Use case implementation of analytics supporting the characterization of protection and sensor effectiveness against known outages; December 2027 | 10.3.3 p. 343
Implement new vegetation management work management software | ES-01 ES-05 | N/A | Implement Complete rollout of updated MDMS: March 2026* | N/A | N/A | 12.2 p. 440
Quality Assurance/Quality Control: Create QA/QC process and procedure for reviewing data in the Vegetation Management database (Quality Reviews) | ES-01 ES-06 | N/A | N/A | Define sScope of data review process based on experience using updated MDMS: October 2027 | Implement identified scope of data review: March 2028 | 12.2 p. 440
Vegetation Management and Inspections: Develop work prioritization to incorporate within MDMS | ES-01 ES-07 | N/A | Start Finalize and implement priority levels to be applied to applicable work units: March 2026 | Implement N/A | Ongoing Implementation N/A | 9.2.1.6 p. 273
Model Validation and Verification | RA-01 | N/A | Implement, March 2026 | Ongoing Maintenance N/A | Ongoing Maintenance N/A | 5.7 p. 111, 116-117
Ignition Detection Systems: Total Wildfire Cameras in Coverage of HFTD/HFRA13 | SA-04 | N/A | 50% 10 | 65% 10 | 80% 10 | 10.4.1 p. 345-347
*Subject to other work and transformation activities
13 As of 2025, there are eight wildfire cameras installed in the HFTD/HFRA. Location of the two planned installations in 2026 is dependent on alignment with program objectives and goals.
Return to Table of Contents

## 13-1
Table 13-1: Lessons Learned
ID # | Year of Lesson Learned | Subject | Category and Source of Lesson Learned | Description of Lesson Learned | Proposed WMP Improvement | Timeline for Implementation | Reference
1 | 2024 | Emergency Preparedness: Wildfire Response | 2024 Wildfire Season Experience | Utilizing existing roles/functions for situational awareness for wildfires was a challenge. Often this activity occurred during the work day/weekends and late hours and personnel had to balance their existing roles with their situational awareness responsibilities. | Establish a Wildfire Intelligence Center to eventually provide 24/7 monitoring of all hazards that threaten Company equipment with a focus on wildfire. | 2025 | Section 11.2.1 Improvements made since the last WMP submission. Discussions with PG&E and Southern California Edison
2 | 2024 | Emergency Preparedness: External Collaboration and Communication | 2024 Wildfire Season Experience | While emergency management has many relationships, PacifiCorp serves over 90 counties in its six-states through a variety of networks between local, regional and state fire agencies and coordination centers. These relationships need to be bolstered to improve real time ability to coordinate. | Establish a Wildfire and Emergency Response Team who are strategically located in the Company's operational areas to support local response to active wildfire and liaison with fire agency jurisdictions. | 2025 | Section 11.2.1 Improvements made since the last WMP submission.
3 | 2024 | PSPS Decision Making | Internal Exercise | During PSPS, uniform conditions must be assumed on circuits with only one weather station downstream of the WUI border or protective devices meaning all upstream customers are de-energized if conditions are unknown. | Increase the number of weather stations near the WUI border and near upstream protective devices allowing PSPS decision making to be more surgical in reducing the number of affected customers and the time spent patrolling. | 2026-2028 | Table 10-1
4 | 2024 | Public Communications and Outreach | Community forums and feedback from Public Safety Partners. | When there are outages on due to ESS (Section 8.7.1) or Emergency De-energization from wildfire (Figure 11-4) they want information on why the outage is happening. | Updated the outage map to show if an outage is due to a Emergency De-energization or on a circuit with ESS. | 2025 | Figure PAC 11-3
5 | 2024 | WSS Re-Energization Decision Making | Internal Discussion | More weather information is necessary near substations and WUI border for System Operations to confirm whether or not conditions are favorable to testing the line for reenergization without patrol. | Increase the number of weather stations between weather stations and substations deep in wildland. | 2026-2028 | Table 10-1
6 | 2025 | Public Communications and Outreach | Customer WMP Webinars | Non-account holders (ex: customers on master meter, landlords with rentals) do not receive notifications of PSPS, ESS or Emergency De-energization Outages, which go to the customer of record | Create a way for non-account holders to register for outage/emergency alerts | 2026 | 2025 California Wildfire Webinar
7 | 2025 | Public Communications and Outreach | AFN Planning | PacifiCorp files an annual AFN Plan with the CPUC, but previously there has not been clear links between the AFN plan and WMP initiatives. | AFN Initiatives in the 2026-2028 WMP align with the objectives of the 2025 AFN Plan | 2026-2028 | Table 11-1 PacifiCorp's AFN Plan included in Appendix F
Return to Table of Contents

## 13-2
Table 13-2: Lessons Learned from Discontinued Activities
Discontinued Activity (Tracking ID) | Rationale for Discontinuation | Lessons Learned | Replacement Activities (include page # where discussed)
SA-02 | Pacific Power installed Distribution Fault Anticipators (DFA) devices as a pilot to evaluate new technological capabilities on the system. | -Provides a structured database that categorizes events and identifies reoccurring events with similar waveforms and characteristics. This feature is extremely valuable and should be implemented as part of an automated outage analysis system. -Capable of performing waveform analytics that identify a variety of fault types -DFA does not provide location information for the types of events that are of interest for preventing wildfires. It needs to be combined with other technologies to be useful. However, many of the new technologies can provide actionable information without DFA. -Installation of dedicated DFA sensors in the substation adds significant costs and time delays for deployment. | Table PAC 10 1: Planned Grid Monitoring System Improvements: -Line Sensors: cFCI Distribution (≤35kV) -AMI: Advanced Bellwether Meters
Return to Table of Contents

## PAC 13-1
Table PAC 13-1: DFA Use Cases and Results
Use Case | Proposed | Confirmed | Comments
Series arcing and detection of degraded switches and connectors | ü | Ó | Correlation between some of the series arcing events and AMI meter alarms has been established. Robust data analytics platform required to detect, localize and develop narrow patrol zones.
Cap bank problems, transformer problems | ü | P | Cap bank issues have been identified and fixed.
Fault Location | Ó | Ó | DFA has demonstrated it can provide useful fault information; however, it duplicates results from other tools (relay data, CFCI’s, etc.).
Fault Induced Conductor Slap, recurring faults, troubleshooting “unknown cause” outages, etc. | ü | Ó | The system is capable of doing analytics that can help identify issues Pacific Power does not otherwise know about, but so far there haven’t been any documented successes.
Other – vegetation contacts, transformers failing etc. | ü | Ó | Insufficient data was available from alerts to confirm the issue or localize the source.
Return to Table of Contents

## B-1
Table PAC B-1: Model Inventory
Model Name | Model Description
FireSight | Used for modeling of long-term wildfire risk for planning as described in Section 5.2
WFA-E: FireCast/FireSim | Used for Situational Awareness as described in Section 10.5.1
Fire Potential Index | Used for Situational Awareness as described in Section 10.6
Return to Table of Contents

## PAC B-1
Table PAC B-1: FireSight and WFA-E Model Inputs
Dataset | Spatial Resolution | Start of Dataset | Dataset Update Frequency | Source
(Meters)
Landscape Characteristics
Terrain | 10 |  | Yearly | United States Geological Survey (USGS)
Surface Fuels | 30/10 | 2020 | Pre-Fire Season, Monthly Update in Fire Season, End of Fire Season | Technosylva
Wildland Urban Interface (WUI) and Non-Forest Fuels Land Use | 30/10 | 2020 | Twice A Year | Technosylva
Canopy Fuels (CBD, CH, CC, CBH) | 30/10 | 2020 | Pre-Fire Season, Monthly Update in Fire Season, End of Fire Season | Technosylva
Roads Network | 30 |  | Yearly | USGS
Hydrography | 30 |  | Yearly | USGS
Croplands | 30 | 1997 | Yearly | USDA
Weather And Atmospheric Data
Wind Speed | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva)
Wind Direction | 2000 | 1990 | Hourly /96 Hour Forecast | Technosylva
Wind Gust | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva
Air Temperature | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva
Surface Pressure | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva
Relative Humidity | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva
Precipitation | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva
Radiation | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva
Water Vapor Mixing Ratio 2 meter | 2000 | 1990 | Hourly / 96 Hour Forecast | Technosylva
Snow Accumulated – Observed | 1000 | 2008 | Daily | National Oceanic and Atmospheric Administration (NOAA)
Precipitation Accumulated - Observed | 4000 | 2008 | Daily | NOAA
Burn Scars | 10 | 2000 | 5 Days | National Aeronautics and Space Administration (NASA)/ European Space Agency (ESA)
Weather Observations Data | Points | 1990 | 10 Min | Synoptic
Fuel Moisture
Herbaceous Live Fuel Moisture | 250 | 2000 | Daily / 5-Day Forecast | Technosylva
Woody Live Fuel Moisture | 250 | 2000 | Daily / 5-Day Forecast | Technosylva
1-Hour Dead Fuel Moisture | 2000 | 1990 | Hourly / 124 Hour Forecast | Technosylva
10-Hour Dead Fuel Moisture | 2000 | 1990 | Hourly / 124 Hour Forecast | Technosylva
100-Hour Dead Fuel Moisture | 2000 | 1990 | Hourly / 124 Hour Forecast | Technosylva
Values at Risk
Buildings | Polygon Footprints | 2020-21 | Yearly | Microsoft/Technosylva
Damage Inspection (DINS) | Points | 2014-21 | Yearly | Cal Fire
Population | 90 | 2019 | Yearly | LANDSCAN, Oak Ridge National Laboratory (ONRL)
Roads | Vector Lines | 2021 | Yearly | Caltrans
Social Vulnerability | Plexels | 2021 | Yearly | ESRI Geoenrichment Service
Fire Stations | Points | 2021 | Yearly | ESRI, USGS
Building Loss Factor | Building Footprints | 2022 | Yearly | Technosylva
Critical Facilities | Points | 2021 | Yearly | Fire Resource Assessment Program (FRAP), Cal Fire
Potential Ignition Locations
Distribution & Transmission Lines | Linear Segments | 2022 | Updated Quarterly | PacifiCorp
Poles & Equipment | Points | 2022 | Updated Quarterly | PacifiCorp
Outage History | Points | 1989 | Annual | PacifiCorp
Ignition History | Points | 2020 | Annual | PacifiCorp
Fire Activity
Hotspots MODIS | 1000 | 2000 | Twice A Day | NASA
Hotspots VIIRS | 375 | 2014 | Twice A Day | NASA
Hotspots GOES 16/17 | 3000 | 2019 | 10 Minute | NASA
Fireguard | Polygons | 2020 | 15 Minute | National Guard
Fire Season Perimeters | Polygons | 2021 | Daily | National Incident Feature Service (NIFS)
Historic Fire Perimeters | Polygons | 1900 | Yearly | Cal Fire
Alert Wildfire Cameras | Live Feeds | Real Time | 1 Minute | Alert Wildfire Consortium
Lighting Strikes | 1000 | Real Time | 1 Minute | Earth Networks / Others
Return to Table of Contents

## PAC B-2
Table PAC B-2: FireSight Outputs
Attribute | Description: | Percentiles
Acres Burned | Number of Acres Burned | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Building Density | Building Density per Plexel | N/A
Buildings Destroyed | Number of Buildings Destroyed | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Building Loss Factor | Estimated Building Loss Factor Within the Plexel. | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Building Loss Factor (Average-Mean) | Average Estimated Building Loss Factor Within the Plexel. | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Building Loss Factor (Median) | Average Estimated Building Loss Factor Within the Plexel. | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Buildings Threatened | Number of Buildings Threatened | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Burn Frequency | Burn Frequency is the number of times a plexel is touched from all assets ignited simulations run for the selected weather days. It is similar to traditional burn probability although this only represents a frequency, not a probability. | N/A
Disability Population | Disability Population Ratio | N/A
Fire Behavior Index | Fire Behavior Index | N/A
Fire Station Density | Density of Fire Stations in a location | N/A
Flame Length | Feet | N/A
Fuel Model Majority | Majority Fuel in Each Plexel | N/A
Number of Buildings | Number of Building per Plexel | N/A
Population Count | Population Count per Plexel | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Population Density | Population Density per Plexel | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Population Impacted | Population Count | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Poverty Population | Poverty Population Ratio | N/A
Rate of Spread | 66 Feet/Hour | 0, 20, 40, 60, 80, 90, 95, 98, and 100
Road Availability-With Social Vulnerability Population | Availability of Roads in a Location with Consideration of Social Vulnerability Population | N/A
Road Availability-With No Population | Availability of Roads in a Location with No Consideration of Social Vulnerability Population | N/A
Road Miles | Total Miles (Major + Minor) | N/A
Senior Population | Senior Population Ratio | N/A
Terrain Difficulty Index | Terrain Difficulty per Plexel | N/A
Years Since Last Fire | Years Since Last Fire per Plexel | N/A
Return to Table of Contents

## PAC B-3
Table PAC B-3: Fire Potential Index Inputs
Feature Group | Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
Weather | Wind, sustained and gusts | 10m | Wind speed and gust measured | Internal PacifiCorp WRF | Twice daily | 2km | Hourly
Fuel Complexity | Fuel type, fuel load and fuel age | Surface | Quantifies the fuel type, fuel load and fuel age | Technosylva | Annually | 30m | N/A
Weather | Relative humidity, vapor pressure deficit | Surface | Moisture variable from the atmosphere | Internal PacifiCorp WRF | Twice daily | 2km | Hourly
Terrain | Terrain Difficulty Index | N/A | Quantifies the terrain and its potential impacts on suppression activity including accessibility, fuel penetrability, and ease of opening fire line. | Technosylva | Annually | 30m | N/A
Fuel Moisture | 1 and 10 hour dead fuel moisture | 10m | Moisture of dead fuels | Internal PacifiCorp WRF | Twice daily | 2km | Hourly
Fuel Moisture | Woody and Herbaceous Live Fuel moisture | 10m | Moisture of live fuels | Remote Sensing data | Daily |  | Hourly
Return to Table of Contents

## PAC B-4
Table PAC B- 4: Asset Fire Susceptibility Layers
Layer | Description | Units
Burn Frequency | Burn Frequency is the number of times a plexels is touched from all asset ignited simulations run for the selected weather days. It is similar to traditional burn probability although this only represents a frequency, not a probability. | Number of times impacted by a fire simulation
Fire Behavior Index | The Fire Behavior Index layer group includes FBI results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8-hour simulation runs. | Fire Behavior Index within the plexel
Acres | The Acres layer group includes acres results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8- hour simulation runs. | Acres burned within the plexel
Buildings Threatened | The Buildings Threatened layer group includes buildings impacted results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8-hour simulation runs. | Number of buildings impacted within the plexel
Buildings Destroyed | The Buildings Destroyed layer group includes buildings destroyed results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8-hour simulation runs. | Estimated number of buildings destroyed within the plexel
Building Loss Factor | The Building Loss Factor layer group includes building loss factor results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8-hour simulation runs. | Estimated building loss factor within the plexel
Population | The Population layer group includes population impacted results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8-hour simulation runs. | Number of population (people) impacted within the plexel
Flame Length | The Flame Length layer group includes flame length results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8-hour simulation runs. | Flame Length in feet within the plexel
Rate of Spread | The Rate of Spread layer group includes rate of spread results for percentiles 100, 98, 95, 90, 80, 60, 40, 20, and 0 for 8-hour simulation runs | Rate of Spread in chains / hour within the plexel
Return to Table of Contents

## PAC B-5
Table PAC B- 5: Locational Risk Factors Layers
Layer | Description | Units
Total Miles—Major Roads | Total miles of major roads by plexel | Miles
Total Miles—Minor Roads | Total miles of minor roads by plexel | Miles
Fuel Model Majority | Majority fuel model within each plexel | Fuel model number of fuels that have the most acres within the plexel
Building Density | Building Density by plexel | Buildings per acre
Number of Buildings | Number of Buildings by plexel | Number of buildings
Building Loss Factor (Median) | Median building loss factor by plexel | Percent
Building Loss Factor (Mean) | Average building loss factor by plexel | Percent
Population Count | Population Count by plexel | Number of People
Population Density | Population Density by plexel | Population Per Acre
Fire Stations Density | Density of Fire Stations by plexel. Represents a mean value of a density surface created from station points using a Kernel interpolation method. | Stations per sq. mile using a 20-mile search distance.
Terrain Difficulty Index | Technosylva’s Terrain Difficulty Index (2022) by plexel | Values from Very Low to Extreme
Disability Population Ratio | Disability population ratio by plexel | Percent of population identified as disabled within the plexel
Poverty Population Ratio | Poverty population ratio by plexel | Percent of population identified as under the poverty level within the plexel
Senior Population Ratio | Senior population ratio by plexel | Percent of population identified as senior (GE 65 years of age) within the plexel
Road Availability (without social vulnerability) | Road Availability without factoring social vulnerability (disability, poverty, and senior) population ratios by plexel | Poor to Good Egress
Road Availability (with social vulnerability) | Road Availability using social vulnerability (disability, poverty, and senior) population ratios by plexel | Poor to Good Egress
Years Since Last Fire | Years since last fire by plexel (calculated for 2022) | Years
Return to Table of Contents

## PAC D-1
Table PAC D-1: Mapping of 2026-2028 WMP Initiatives and Activities to 2025 Maturity Survey Categories, Capabilities and Sub-Capabilities
Category A: Risk Assessment and Mitigation Strategy
Capability | I. | II. | III. | IV. | V. | VI.
| 1. Statistical weather, climate, and wildfire modeling | 2. Calculation of wildfire and PSPS hazard and exposure to societal values | 3. Calculation of community vulnerability to wildfire and PSPS | 4. Calculation of risk and risk components | 5. Risk event tracking and integration of lessons learned | 6. Risk-informed wildfire mitigation strategy
Sub capability | Initiative or Activity
Automation |  | PC-25U-02: PSPS model will be onboarded by EOY 2025
Climate change | Table 5-6: Implement a climate change planning model component |  | PC-25U-02: PSPS model will be onboarded by EOY 2025
Comprehensiveness |  | PC-25U-02: PSPS model will be onboarded by EOY 2025 |  |  |  | Table 5-6: Monetization of risk events for use in RSE calculations
Frequency & risk buy-down | [5 empty] | Table 5-6: Monetization of risk events for use in RSE calculations
IT infrastructure and database management |  |  | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions
Modularization |  |  |  | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions
Quality assurance and quality control (QA/QC) and subject matter expert (SME) verification |  |  | PC-25U-02: PSPS model will be onboarded by EOY 2025
Stability of assumptions | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions |  |  | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions |  | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions
Transparency |  |  |  | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions
Validation |  | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions |  |  |  | Table 5-6: -Create reproducible model development environment using Python, Azure Dev Ops (ADO), and Azure Cloud resources. -Implement a standardized model taxonomy to track release versions
Category B: Situational Awareness and Forecasting
Capability | I. | II. | III. | IV. | V. | VI.
| 7. Ignition likelihood estimation | 8. Weather forecasting ability | 9. Wildfire spread forecasting | 10. Data collection for near-real-time conditions | 11. Wildfire detection and alarm systems | 12. Centralized monitoring of real-time conditions
Sub capability | Initiative or Activity
Level of sophistication |  | Table 10-2: Implement WRF Ensemble Forecasting
Category C: Grid Design, Inspections, and Maintenance
Capability | I. | II. | III. | IV. | V. | VI.
| 13. Asset inventory and condition database | 14. Asset inspections | 15. Asset maintenance and repair | 16. Grid design and resiliency | 17. Asset and grid personnel training and quality | N/A
Sub capability | Initiative or Activity
Learning and improvement |  |  | Table 5-2: -Creation of PEDS Risk Model -Monetization of Risk Events for Application in Mitigation Alternatives Analysis -Dynamic Grid Hardening Efficacy Rates -Portfolio Optimization and Grid Hardening Recommendations
Risk buy-down |  |  |  | Table 5-2: -Creation of PEDS Risk Model -Monetization of Risk Events for Application in Mitigation Alternatives Analysis -Dynamic Grid Hardening Efficacy Rates -Portfolio Optimization and Grid Hardening Recommendations
Category D: Vegetation Management and Inspections
Capability | I. | II. | III. | IV. | V. | VI.
| 18. Vegetation inventory and condition database | 19. Vegetation inspections | 20. Vegetation treatment | 21. Vegetation personnel training and quality | 22. Best Management Practices for Transmission Rights-of-Ways (ROWs) | N/A
Sub capability | Initiative or Activity
Quality assurance and quality control (QA/QC) and subject matter expert (SME) verification | Table 9-1: Quality Assurance/Quality Control: Create QA/QC process and procedure for reviewing data in the Vegetation Management database (Quality Reviews) |  |  | Table 9-1: Quality Assurance/Quality Control: Create QA/QC process and procedure for reviewing data in the Vegetation Management database (Quality Reviews)
Spatial granularity |  | Table 9-1: Implement new vegetation management work management software
Category G: Community Outreach and Engagement
Capability | I. | II. | III. | IV. | V. | VI.
| 34. Public outreach and education awareness | 35. Public engagement in electrical corporation wildfire mitigation planning process | 36. Engagement with AFN and socially vulnerable populations | 37. Collaboration on local wildfire mitigation planning | 38. Cooperation and best practice sharing with other electrical corporations | N/A
Sub capability | Initiative or Activity
Effectiveness |  |  | Table 11-1: Conduct pre-season and post-season customer surveys to assess understanding of messaging and information shared by PacifiCorp and inform adjustments in messaging.
Spatial granularity |  |  | 2025: AFN Toolkit Implementation
Return to Table of Contents

## PAC E-1
Table PAC E-1: Referenced Regulations, Codes, and Standards
Name of Regulation, Code, or Standard | Brief Description
CA CCR Title 14 Sections 1250-1258 | Title 14 (Board of Forestry and Fire Protection Regulations). (14 CCR 1250). The purpose is to provide specific exemptions from: electric pole and tower firebreak clearance standards, electric conductor clearance standards and to specify when and where the standards apply.
CA CPUC 768.6(a). | The commission shall establish standards for disaster and emergency preparedness plans within an existing proceeding, including, but not limited to, use of weather reports to preposition manpower and equipment before anticipated severe weather, methods of improving communications between governmental agencies and the public, and methods of working to control and mitigate an emergency or disaster and its aftereffects.
CA CPUC 8386(a) | Each electrical corporation shall construct, maintain, and operate its electrical lines and equipment in a manner that will minimize the risk of catastrophic wildfire posed by those electrical lines and equipment.
CA CPUC 4427 | During any time of the year when burning permits are required in an area pursuant to this article, no person shall use or operate any motor, engine, boiler, stationary equipment, welding equipment, cutting torches, tarpots, or grinding devices from which a spark, fire, or flame may originate, which is located on or near any forest-covered land, brush-covered land, or grass-covered land, without doing both of the following: (a)First clearing away all flammable material, including snags, from the area around such operation for a distance of 10 feet. (b)Maintain one serviceable round point shovel with an overall length of not less than forty-six (46) inches and one backpack pump water-type fire extinguisher fully equipped and ready for use at the immediate area during the operation. This section does not apply to portable powersaws and other portable tools powered by a gasoline-fueled internal combustion engine.
CA CPUC 4428 | No person, except any member of an emergency crew or except the driver or owner of any service vehicle owned or operated by or for, or operated under contract with, a publicly or privately owned utility, which is used in the construction, operation, removal, or repair of the property or facilities of such utility when engaged in emergency operations, shall use or operate any vehicle, machine, tool or equipment powered by an internal combustion engine operated on hydrocarbon fuels, in any industrial operation located on or near any forest, brush, or grass-covered land between April 1 and December 1 of any year, or at any other time when ground litter and vegetation will sustain combustion permitting the spread of fire, without providing and maintaining, for firefighting purposes only, suitable and serviceable tools in the amounts, manner and location prescribed in this section. (a)On any such operation a sealed box of tools shall be located, within the operating area, at a point accessible in the event of fire. This fire toolbox shall contain: one backpack pump-type fire extinguisher filled with water, two axes, two McLeod fire tools, and a sufficient number of shovels so that each employee at the operation can be equipped to fight fire. (b)One or more serviceable chainsaws of three and one-half or more horsepower with a cutting bar 20 inches in length or longer shall be immediately available within the operating area, or, in the alternative, a full set of timber-felling tools shall be located in the fire toolbox, including one crosscut falling saw six feet in length, one double-bit ax with a 36-inch handle, one sledge hammer or maul with a head weight of six, or more, pounds and handle length of 32 inches, or more, and not less than two falling wedges. (c)Each rail speeder and passenger vehicle, used on such operation shall be equipped with one shovel and one ax, and any other vehicle used on the operation shall be equipped with one shovel. Each tractor used in such operation shall be equipped with one shovel. (d)As used in this section: (1)“Vehicle” means a device by which any person or property may be propelled, moved, or drawn over any land surface, excepting a device moved by human power or used exclusively upon stationary rails or tracks. (2)“Passenger vehicle” means a vehicle which is self-propelled and which is designed for carrying not more than 10 persons including the driver, and which is used or maintained for the transportation of persons, but does not include any motortruck or truck tractor
CA CPUC 8386(c)(7), (11), (16), (19), (20). | Each electrical corporation shall construct, maintain, and operate its electrical lines and equipment in a manner that will minimize the risk of catastrophic wildfire posed by those electrical lines and equipment. Each electrical corporation shall annually prepare and submit a wildfire mitigation plan to the Wildfire Safety Division for review and approval. A description of the electrical corporation's appropriate and feasible procedures for notifying a customer who may be impacted by the deenergizing of electrical lines. A description of the electrical corporation's protocols for the deenergization of the electrical corporation's transmission infrastructure, for instances when the deenergization may impact customers showing that the electrical corporation has an adequately sized and trained workforce to promptly restore service after a major event. A description of how the plan is consistent with the electrical corporation's disaster and emergency preparedness plan. A statement of how the electrical corporation will restore service after a wildfire.
CA CPUC D. 21-05-019 | Electric utilities must develop disaster and emergency preparedness plans and seek local government input so as to improve communication with the public and mitigate the effects of catastrophic events.
CA CPUC R. 15-06-009 | Requires, among other things, that water and electric utilities develop disaster and emergency preparedness plans and seek local government input so as to improve communication with the public and mitigate the effects of catastrophic events.
CA GO 165 | This General Order applies to all electric distribution and transmission facilities (excluding those facilities contained in a substation) that come within the jurisdiction of this Commission, located outside of buildings, including electric distribution and transmission facilities that belong to non-electric utilities. The requirements of this order are in addition to the requirements imposed upon utilities under General Orders 95 and 128 to maintain a safe and reliable electric system.
CA GO 166 | The purpose of these standards is to ensure that jurisdictional electric utilities are prepared for emergencies and disasters to minimize damage and inconvenience to the public which may occur because of electric system failures, major outages, or hazards posed by damage to electric facilities. The standards will facilitate the Commission’s investigations into the reasonableness of the utility’s response to emergencies and major outages. Such investigations will be conducted following every major outage, pursuant to and consistent with Public Utilities Code Section 364(c) and Commission policy.
CA GO 174 | “Rules for Electric Utility Substations”: The purpose of these rules is to formulate, for the State of California, uniform requirements for substation inspection programs, the application of which will promote the safety of workers and the public and enable adequacy of service. Substations shall be designed, constructed and maintained for their intended use, regard being given to the conditions under which they are to be operated, to promote the safety of workers and the public and enable adequacy of service
CA GO 95 Rule 35 | “Clearance Requirements for Overhead Wires”. Where overhead conductors traverse trees and vegetation, safety and reliability of service demand that certain vegetation management activities be performed in order to establish necessary and reasonable clearances. These requirements apply to all overhead electrical supply and communication facilities that are covered by this General Order, including facilities on lands owned and maintained by California state and local agencies.
CA PRC 4291 | A person who owns, leases, controls, operates, or maintains a building or structure in the state responsibility area shall at all times maintain defensible space of 100 feet from each side and from the front and rear of a structure, but not beyond the property line and shall maintained and space fuels in a condition so that a wildfire would be unlikely to ignite the structure.
CA PRC 4292 | Any person that owns, controls, operates, or maintains any electrical transmission or distribution line upon any mountainous land, or forest-covered land, brush-covered land, or grass-covered land shall, during such times and in such areas as are determined to be necessary by the director or the agency which has primary responsibility for fire protection of such areas, maintain around and adjacent to any pole or tower which supports a switch, fuse, transformer, lightning arrester, line junction, or dead end or corner pole, a firebreak which consists of a clearing of not less than 10 feet in each direction from the outer circumference of such pole or tower. This section does not, however, apply to any line which is used exclusively as telephone, telegraph, telephone or telegraph messenger call, fire or alarm line, or other line which is classed as a communication circuit by the Public Utilities Commission. The director or the agency which has primary fire protection responsibility for the protection of such areas may permit exceptions to the requirements of this section which are based upon the specific circumstances involved.
CA PRC 4293 | Except as otherwise provided in Section 4294 to 4296, inclusive, any person that owns, controls, operates, or maintains any electrical transmission or distribution line upon any mountainous land, or in forest-covered land, brush-covered land, or grass-covered land shall, during such times and in such areas as are determined to be necessary by the director or the agency which has primary responsibility for the fire protection of such areas, maintain a clearance of the respective distances which are specified in this section in all directions between all vegetation and all conductors which are carrying electric current: (a)For any line which is operating at 2,400 or more volts, but less than 72,000 volts, four feet. (b) For any line which is operating at 72,000 or more volts, but less than 110,000 volts, six feet. (c)For any line which is operating at 110,000 or more volts, 10 feet. In every case, such distance shall be sufficiently great to furnish the required clearance at any position of the wire, or conductor when the adjacent air temperature is 120 degrees Fahrenheit, or less. Dead trees, old decadent or rotten trees, trees weakened by decay or disease and trees or portions thereof that are leaning toward the line which may contact the line from the side or may fall on the line shall be felled, cut, or trimmed to remove such hazard. The director or the agency which has primary responsibility for the fire protection of such areas may permit exceptions to the requirements of this section which are based upon the specific circumstances involved.
National Incident Management System | The National Incident Management System (NIMS) guides all levels of government, nongovernmental organizations and the private sector to work together to prevent, protect against, mitigate, respond to and recover from incidents. NIMS provides stakeholders across the whole community with the shared vocabulary, systems and processes to successfully deliver the capabilities described in the National Preparedness System. NIMS defines operational systems that guide how personnel work together during incidents.
NERC FAC-003 | “Transmission Vegetation Management". Established to ensure that Transmission Owners have a vegetation management program to prevent transmission line contact with vegetation, and to ensure that certain vegetation-related outages are reported to the appropriate Regional Reliability Organization.
United States Forest Service (USFS) Industrial Fire Precaution Levels | Industrial Fire Precaution Levels are stages that apply to work activities, including personal use firewood cutting, on Forest Service or BLM lands in order to reduce the risk of a wildfire starting from the operation.
Return to Table of Contents

## PAC F-1
Table PAC F 1: PacifiCorp Referenced Policies and Standards in the 2026-2028 WMP
Standard or Policy | Section Referenced
Transmission and Distribution System Condition Priorities and Correction Timelines Asset Management Policy No 292 | Section 8.5.2
Detailed Inspections for T&D Lines Asset Management Policy 009 | Section 8.5
Clearance Table for Distribution and Transmission Line Inspectors NESC and GO 95 Grandfathering Matrix Facility Point Inspection NESC and GO 95 Frequently Asked Questions Condition Code Dropdowns Asset Management Procedure 069 | Section 8.3
Visual Assurance Inspections —Safety Patrol of G Transmission and Distribution Lines Asset Management Policy No 011 | Section 8.3
Helicopter Standard Operating Procedure for Line Inspections Facility Inspection Procedure No 203 | Section 8.3
Wood Pole Test & Treatment Transmission and Distribution Lines Asset Management Policy 013 | Section 8.3.3
Substation inspection Asset Management Policy No 034 | Section 8.3.4
Policy 001 Maintenance Intervals for Apparatus, Relays, Meters, Line Patrol/Inspections, Wires Equipment and Communications Equipment | Section 8.4
Exhibit M.07 Performance Based Requirements for Pacific Power Detailed Inspections and Detailed Test and Treat Activity | Section 8.5
Operating Transmission and Distribution Assets During periods of Elevated Wildfire Risk Power Delivery Policy PAC-1000 | Section 8.7
Operating Bulk Electric System (BES) Transmission Assets During Identified Wildfire Risk System Operations Procedure SOP-200 | Section 8.7
Operating Sub-Transmission Assets During Identified Wildfire Risk System Operations Procedure SOP-201 | Section 8.7
Operating Distribution Assets During Identified Wildfire Risk System Operations Procedure, SOP-202 | Section 8.7
Example of a Daily Work Evaluation Summary Record | Section 8.7.3
PacifiCorp’s Transmission & Distribution Vegetation Management Program Standard Operating Procedures (SOP), Revision 8, dated 8/29/2024 | Section 9
Substation Manager Audits Procedures | Section 9.6
Transmission Grid Operations Operating Procedure PCC-215 Guidelines for Communication of Vegetation Conditions that Present an Imminent Threat of Transmission Line Outage | Section 9.2
Wildfire Encroachment System Operations Procedure SOP-203 | Section 11
PSPS Execution Playbook | Section 11
Annex 01: 2025 Public Safety Power Shutoff Community Resource Center Playbook | Section 11
Emergency Response Plan (ERP), Sixth edition, dated April 23, 2025 | Section 11
R1812005 PacifiCorp Annual AFN Plan 2025 1-31-25 | Section 11
Return to Table of Contents

## PAC G-1
Table PAC G-1: Other Supporting Documents Referenced in the 2026-2028 WMP
Document | Section Reference
Wildfire Mapping Refresh & Benchmark | Section 5.6
ANSI A300 Tree Care Standards - Tree Care Industry Association, LLC. | Section 9
International Society of Arboriculture | Section 9.3
Marking Guidelines for Fire-Injured Trees in California | Section 9.10
PC-25U-07 PacifiCorp Imminent Threat Condition Review | Appendix D: Grid Design, Operations, and Maintenance
Return to Table of Contents

## PAC 11-1 High-Level Communi (2) (hidden)
Table PAC 11-1: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners
Timing | Communication
48-72 hours prior | De-energization warning to Public Safety Partners and priority customers
24-48 hours prior | De-energization warning
Phone call to customer with MBL/AFN
1 – 4 hours prior | De-energization imminent
Phone call to customers with MBL/AFN
Additional outreach to uncontacted customers with MBL/AFN
Beginning of Event | Beginning of Event
Wellness check call for customers with MBL/AFN during extended events
Re-energization begins | Re-energization begins
Re-energization completed | Re-energization completed
Wellness check call for re-energized customers with MBL/AFN
Cancellation of event | De-energization event canceled
Return to Table of Contents