## LU Table 3-1
LU Table 3‑1: Liberty WMP Initiative Tracking IDs
WMP Initiative Category | WMP Initiative Activity | WMP Initiative ID
Grid Design, Operations, and Maintenance | Covered conductor installation | WMP-GDOM-GH-01
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | WMP-GDOM-GH-02
Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements | WMP-GDOM-GH-03
Grid Design, Operations, and Maintenance | Transmission pole/tower replacements and reinforcements | WMP-GDOM-GH-04
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP-GDOM-GH-05
Grid Design, Operations, and Maintenance | Emerging grid hardening technology installations and pilot progress | WMP-GDOM-GH-06
Grid Design, Operations, and Maintenance | Microgrids | WMP-GDOM-GH-07
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP-GDOM-GH-08
Grid Design, Operations, and Maintenance | Line removal (in HFTD) | WMP-GDOM-GH-09
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP-GDOM-GH-10
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP-GDOM-GH-11
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above: | WMP-GDOM-GH-12
Grid Design, Operations, and Maintenance | Tree attachment removals | WMP-GDOM-GH-12a
Grid Design, Operations, and Maintenance | Expulsion fuse replacement | WMP-GDOM-GH-12b
Grid Design, Operations, and Maintenance | Animal guards | WMP-GDOM-GH-12c
Grid Design, Operations, and Maintenance | CalFIRE exempt hardware | WMP-GDOM-GH-12d
Grid Design, Operations, and Maintenance | Open wire/grey wire | WMP-GDOM-GH-12e
Grid Design, Operations, and Maintenance | Detailed inspections of distribution electric lines and equipment | WMP-GDOM-AI-01
Grid Design, Operations, and Maintenance | Intrusive pole inspections | WMP-GDOM-AI-02
Grid Design, Operations, and Maintenance | Patrol inspections of distribution electric lines and equipment | WMP-GDOM-AI-03
Grid Design, Operations, and Maintenance | Other discretionary inspections of distribution electric lines and equipment: Drone inspections | WMP-GDOM-AI-04
Grid Design, Operations, and Maintenance | Quality assurance / quality control of inspections | WMP-GDOM-AI-05
Grid Design, Operations, and Maintenance | Substation inspections | WMP-GDOM-AI-06
Grid Design, Operations, and Maintenance | Equipment maintenance and repair | WMP-GDOM-MR-01
Grid Design, Operations, and Maintenance | Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01
Grid Design, Operations, and Maintenance | Grid response procedures and notifications | WMP-GDOM-GO-02
Grid Design, Operations, and Maintenance | Personnel work procedures and training in conditions of elevated fire risk | WMP-GDOM-GO-03
Grid Design, Operations, and Maintenance | Automatic recloser operations | WMP-GDOM-GO-04
Grid Design, Operations, and Maintenance | Asset Management and Inspection Enterprise System | WMP-GDOM-GO-05
Vegetation Management & Inspections | Vegetation Management Inspection Program - Detailed | WMP-VM-INSP-01
Vegetation Management & Inspections | Vegetation Management Inspection Program - Patrol | WMP-VM-INSP-02
Vegetation Management & Inspections | Vegetation Management Inspection Program - LiDAR | WMP-VM-INSP-03
Vegetation Management & Inspections | Pole Clearing | WMP-VM-VFM-01
Vegetation Management & Inspections | Wood and Slash Management | WMP-VM-VFM-02
Vegetation Management & Inspections | Substation Defensible Space | WMP-VM-VFM-03
Vegetation Management & Inspections | Fire-Resilient Right-of-Ways | WMP-VM-VFM-04
Vegetation Management & Inspections | Clearance | WMP-VM-VFM-05
Vegetation Management & Inspections | Fall-In Mitigation | WMP-VM-VFM-06
Vegetation Management & Inspections | High-Risk Species | WMP-VM-VFM-07
Vegetation Management & Inspections | Emergency Response Vegetation Management | WMP-VM-VFM-08
Vegetation Management & Inspections | Vegetation Management Enterprise System | WMP-VM-ESG-01
Vegetation Management & Inspections | Quality Assurance and Quality Control | WMP-VM-QAQC-01
Situational Awareness & Forecasting | Environmental monitoring systems | WMP-SA-01
Situational Awareness & Forecasting | Grid monitoring systems | WMP-SA-02
Situational Awareness & Forecasting | Fire detection and alarm systems | WMP-SA-03
Situational Awareness & Forecasting | Weather forecasting | WMP-SA-04
Situational Awareness & Forecasting | Fire Potential Index | WMP-SA-05
Situational Awareness & Forecasting | Ignition likelihood calculation | WMP-SA-06
Situational Awareness & Forecasting | Ignition consequence calculation | WMP-SA-07
Emergency Preparedness | Wildfire and PSPS emergency preparedness plan | WMP-EP-01
Emergency Preparedness | Collaboration and coordination with public safety partners | WMP-EP-02
Emergency Preparedness | Public notification and communication strategy | WMP-EP-03
Emergency Preparedness | Preparedness and planning for service restoration | WMP-EP-04
Emergency Preparedness | Customer support in wildfire and PSPS emergencies | WMP-EP-05
Emergency Preparedness | Learning after wildfire and PSPS events | WMP-EP-06
Community Outreach and Engagement | Public outreach and education awareness for wildfires, PSPS, outages from protective equipment and device settings, and vegetation management | WMP-CO-01
Community Outreach and Engagement | Public engagement in WMP decision-making process | WMP-CO-02
Community Outreach and Engagement | Engagement with AFN populations, local governments, and tribal communities | WMP-CO-03
Community Outreach and Engagement | Collaboration on local wildfire mitigation and planning | WMP-CO-04
Community Outreach and Engagement | Best practice sharing with other electrical corporations | WMP-CO-05

## Table 3-1
Table 3‑1: List of Risks and Risk Drivers to Prioritize
Priority | Risk | Risk Driver | % of ignitions in HFTD | Topographical and Climatological Risk Factors
1 | Equipment / facility failure or damage | Connector device | 17.65% | Extreme weather, heat, wind
1 | Vegetation contact | Fall-in (branch failure) | 11.76% | Elevation, slope, wind, extreme weather
1 | Vegetation contact | Fall-in (trunk failure) | 11.76% | Elevation, slope, wind, extreme weather
1 | Equipment / facility failure or damage | Conductor | 11.76% | Extreme weather, heat, wind
1 | Wire-to-wire contact | Wire-to-wire contact | 5.88% | Extreme weather, heat, wind
1 | Vegetation contact | Fall-in (root failure) | 0 | Elevation, slope, wind, extreme weather
1 | Vegetation contact | Blow-in | 0 | Elevation, slope, wind, extreme weather
1 | Vegetation contact | Grow-in | 0 | Elevation, slope, wind, extreme weather
2 | Contact from object | Animal contact | 11.76% | N/A
2 | Equipment / facility failure or damage | Other | 5.88% | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Anchor/guy | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Capacitor bank | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Cross arm | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Fuse | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Cutout | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Insulator and bushing | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Lightning arrestor | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Pole | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Recloser | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Relay | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Sectionalizer | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Splice | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Switch | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Tap | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Tie wire | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Transformer | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Voltage regulator / booster | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Unknown | 0 | Extreme weather, heat, wind
3 | Unknown | Unknown | 11.76% | N/A
3 | Contact from object | Unknown | 5.88% | Extreme weather, heat, wind
3 | Vandalism/ theft | Vandalism / theft | 5.88% | N/A
3 | Contact from object | Ballon contact | 0 | Wind
3 | Contact from object | Land vehicle contact | 0 | N/A
3 | Contact from object | Aircraft vehicle contact | 0 | N/A
3 | Contact from object | Third-party contact | 0 | N/A
3 | Contact from object | Other contact from object | 0 | N/A
3 | Contamination | Contamination | 0 | Extreme weather, heat, wind
3 | Protective device operation | Protective device operation | 0 | N/A
3 | Lightning | Lightning | 0 | Extreme weather
3 | Dig-in | Dig-in | 0 | N/A

## Table 3-2
Table 3‑2: Self-Identified Performance Metrics (N/A) [1]
[1] Liberty does not use performance metrics beyond those required by Energy Safety and thus does not provide a Table 3-2.

## Table 3-3
Table 3‑3: Summary of Liberty Projected WMP Expenditures, 2026-2028
Year of WMP Cycle | Projected Spend (thousands $USD)
2026 | 36473
2027 | 36194
2028 | 37086

## Table 4-1
Table 4 1. Liberty Service Territory High-Level Statistics
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | Total
Area served (square miles) | 922.78 | 13.17 | 547.92 | 1483.87
Number of customers served | 41713 | 3019 | 3500 | 48232
Overhead transmission lines (circuit miles) | 28.41 | 2.36 | 2.12 | 32.89
Overhead distribution lines (circuit miles) | 1259.86 | 124.73 | 92.31 | 1476.9
Underground transmission lines (circuit miles) | 1.3 | 0 | 0 | 1.3
Underground distribution lines (circuit miles) | 536.67 | 10.22 | 38.38 | 585.29
Hardened overhead transmission lines (circuit miles) | 0 | 0 | 0 | 0
Hardened overhead distribution lines (circuit miles) | 43.57 | 0 | 0 | 43.57
Substations (#) | 11 | 1 | 2 | 14
Power generation facilities (#) | 0 | 0 | 0 | 0
Distribution transformers (#) | 7,015 | 365 | 581 | 7,961
Reclosers (#) | 39 | 0 | 3 | 42
Poles (#) | 21,366 | 1,737 | 1,815 | 24,918
Microgrids (#) | 1 | 0 | 0 | 1

## Table 4-2
Table 4‑2: Liberty Catastrophic Wildfire History
Ignition Date | Fire Name | Official Cause | Fire Size | No. of Fatalities | No. of Structures Destroyed and Damaged | Financial Loss (US$) | Lessons Learned
(acres)
2020-11-17 | Mountain View Fire | Unknown | 20385 | 1 | 80 destroyed | $184M | Developed new PSPS criteria to account for late season weather conditions that occurred on the day of the fire.

## Table 4-3
Table 4‑3: Frequently Deenergized Circuits
Circuit ID | Name of Circuit | Dates of Outages | Number of Customer Hours of PSPS per Outage | Measures Taken, or Planned to Be Taken to Reduce the Need for and Impact of Future PSPS of Circuit | Estimated Annual Decline in PSPS Events and PSPS Impact on Customers
Muller 1296 | Muller 1296 | 11/11/2024, 11/20/2024, and 11/22/2024 | 10,516.33, 12,350.78, and 9,550.23 | Distribution pole replacements and reinforcements, traditional overhead hardening, situational awareness, sectionalizing devices, and Sensitive Relay Profile | 33%-50% decline in PSPS events

## LU Table 5-1
LU Table 5‑1: PSPS Thresholds For Circuits with SRP
Circuit Type | Wind Gust (MPH) | FFWI
Without SRP | 40 | 50
With SRP | 50 | 50

## Table 5-1
Table 5‑1: Primary Risk Modeling Assumptions and Limitations
Assumption | Justification | Limitation | Applicable Models
The physical framework development is based on an idealized situation in steady state spread, which may not fit some extreme behavior of fires. | The model is semi-empirical and as a result does not capture all possible wildfire scenarios. | The model may not represent unique weather cases. | Wildfire Spread Model
Fuels are assumed to be continuous and uniform for the scale of the input (typically between 10-to-30-meter (m) resolution) | This is the highest resolution data available across the service territory, and the standard for fuels mapping for fire agencies and IOUs in the US. | Real fuels are more granular and thus not captured by the fire spread modeling. | Wildfire Spread Model
Fire characteristics at a point considers only the conditions at that point (point-functional model). This means that there are certain non-local phenomena like: | Point functional models are much faster to solve than non-local ones. | Several non-local effects like radiation concentration from different parts of the front are not considered. | Wildfire Spread Model
· Increase of ROS due to a concave front.
· Fire interaction between different parts of the same fire or a different one.
Fire spread is assumed to be elliptical although there are several variations such as double ellipse, oval, egg-shape, etc. | Fire perimeters obtained in constant wind and slope conditions are known to have a pseudo elliptical shape. The difference between existing fire shape models is small and it is not clear which one is the correct one. | This approach only captures a macroscopic shape of the perimeter. | Wildfire Spread Model
Weather is given hourly and is assumed to remain constant during that time. There is no interpolation in time to compute evolution of weather between hours. | Computing sub hourly wind speeds is expensive and not the standard among fire agencies or IOUs. Sub hourly data is not readily available. | Winds change more rapidly than at the hour level and thus are not captured by the fire spread model. | Wildfire Spread Model
Reliability of weather inputs in the mid-range forecast (2 to 5 days) | Weather forecasts become less accurate the further out in time you model, however WRF models are proven to be very accurate in reflecting past weather scenarios and predicting future short-term weather scenarios. | Fire spread models are impacted due to imperfect weather. | Wildfire Spread Model
Fire is not coupled with the atmosphere in any way. This may seem like a major limitation in the model as wind is a main contribution to fire spread and at present many models (especially physical ones) try to couple wind and fire. | It is not technically feasible to run millions of simulations considering the coupling effect given current science and technology. Empirical and semiempirical models have been developed using an average wind speed as an input, so it is not clear that considering more granular wind at the front is advisable or performs less. | Fire atmosphere interactions are not captured. | Wildfire Spread Model
Fire is assumed to be fully developed. Fire acceleration, flashover, or decay is not considered. | Fire acceleration only affects the initial time of the fire expansion and its effect on an 8-hour simulation may not be too significant. | Models are not valid for short duration fires. | Wildfire Spread Model
Atmospheric instability, which may have a deep impact on ROS (beer 1991), is not considered in the model. | Capturing atmospheric instability is challenging with the present forecast available. | There is a significant range of fire behavior that may not be considered in the model. | Wildfire Spread Model
Gusts are not considered in the model. | Gust duration is highly unpredictable and that could affect the fire very differently. | Fire behavior at a lower scale is not expected to follow a simple symmetrical behavior with respect to wind and slope. | Wildfire Spread Model
No interaction between slope and wind other than creating an effective or equivalent wind. This means that fire is assumed to have an elliptical shape no matter the alignment of wind and slope. | The slope-wind effect is known to be significantly symmetrical in fires under control conditions. There are not many nonphysical models that describe the wind-slope effect in a non-symmetrical way. | Fire behavior at a lower scale is not expected to follow a simple symmetrical behavior with respect to wind and slope. | Wildfire Spread Model
Fuel array description of the vegetation may not perfectly describe fuel characteristics. | There are no perfect fuel datasets available at the territory scale. However, additional custom fuel models have been developed and used to reflect more accurate spread in WUI, agricultural and timber areas. | Fuel characteristics are not captured perfectly by the fire spread model. | Wildfire Spread Model
Spotting is only considered in surface fires. | Calculating crown spotting would require having an accurate tree inventory (height, species, width, etc.). | Wildfire spread for crown fires is impacted. | Wildfire Spread Model
Asset Risk Condition Modifier weights are projected based on manufacturer, historical, and scientific data. | To project the condition of an asset in the future, the condition must be modified to account for work performed on the system to calculate risk. | Condition modifiers may not accurately portray the projected risk. | Probability of Failure (APF)
Condition Modifiers influence POI or POF
Weibull for Asset Failure
POI should be scaled on the same scale as the other models. | To make the risk interpretable, the POI is scaled from 1 to 9. | There’s no logical threshold between 1, 2 and 3. | Consequence of Failure (ACF)
Probability of Fire (POF)
Conductor risk factors are equivalent. | There is not sufficient knowledge to accurately weight the conductor risk factors. | It is considered that the material is equivalent in risk to length of span, even if it’s not. | Probability of Failure (APF)
Conductor does not have a degradation factor. | Lack of information on the present number of splices on the network, age of conductor, and failure model. | The conductor will not degrade over time in the model. | Probability of Failure (APF)
Projected Vegetation work orders are based on past work orders. | Using historical work order information has been effective in estimating accurate work volume . | The model will mimic what was done in the past, which may not be accurate. | Probability of Failure (APF)
Degradation of vegetation uses data outside of Liberty’s available data. | The model simulates growth of vegetation. | Vegetation Degradation is based on scientific research and not historical data. | Probability of Failure (APF)
The decision trees may suggest interventions that would not be typically done in the field. | Over time, Liberty will fine tune the decision trees based on usage of the tool. | Until the model is validated the decision tree output are subject to SME review. | Probability of Failure (APF)
Deterministic methods can pinpoint the exact time of asset failure. | Direxyon uses Monte Carlo Simulation Methodology. | Asset failures are inherently unpredictable in real-world situations. | Asset Failure Risk (AFR)
Deterministic methods can estimate cost. | Direxyon uses Monte Carlo Simulation Methodology. | Costs are inherently unpredictable in real-world situations. | Asset Failure Risk (AFR)
Restoration time is a factor of PSPS Consequence | Repair times can vary, and future work will analyze a method for solving this component | Post PSPS/SRP event restoration time is not accounted for. | PSPS Consequence (PC)
Entire circuits are de-energized during PSPS/SRP Outage Events | It may be possible to isolate or shutdown parts of a circuit | This simplification may overestimate the impact of these events. | PSPS Risk (PR)
Environmental factors remain constant over time | DRAT does not consider environmental or climatic changes | Potential long-term shifts in wind behavior or FFWI due to climate change are not considered. | PSPS Risk (PR)
A uniform random distribution is assumed for the secondary conductor asset type | DRAT recognizes a uniform distribution of Tree Attachments between 5 and 50 | Actuality of Tree Attachments in the Liberty’s system maybe statistically incorrect. | Asset Failure Risk (AFR)

## Table 5-2
Table 5‑2: Liberty Summary of Design Basis Scenarios
Scenario ID | Design Scenario | Purpose
WLC1 | Wind Load | Baseline wind load used in design, construction, and maintenance.
WLC2 | Wind Load | 95th percentile wind gusts based on maximum daily values over a 30-year history.
WLC3 | Wind Load | Wind gusts with a probability of exceedance of five percent over the three-year WMP cycle (i.e. 60-year return interval)
WLC4 | Wind Load | Wind gusts with a probability of exceedance of one percent over the three-year WMP cycle (i.e. 300-year return interval).
WLC5 | Wind Load | WFA models wind speeds to identify at what point a specific transmission or distribution circuit may fail in windy conditions. The results are based on three-hour aggregated probabilities based on the maximum wind gust during that three-hour period.
WC1 | Weather Condition | Anticipated weather conditions over the next three years. This is based on historical weather days that best represents the days when weather and fuel conditions can lead to increased risk of ignition.
WC2 | Weather Condition | Long-term conditions. Technosylva has calculated the historical weather days that best represent the days when weather and fuel conditions can lead to increased risk of ignition based on their Weather Research and Forecast (WRF) Model. WRF is calculated annually to capture new days that should be incorporated into the historical weather days to account for changing conditions in locations.
VC1 | Vegetation Condition | Modeling of current vegetation conditions to identify where current vegetation fuels risk.
VC2 | Vegetation Condition | Modeling of projected 2025 vegetation conditions to identify potential mid-range vegetation fuels risk.
VC3 | Vegetation Condition | Modeling of projected 2030 vegetation conditions to identify potential long-range vegetation fuels risk.

## Table 5-3
Table 5‑3: Liberty Summary of Extreme-Event Scenarios
Scenario ID | Extreme-Event Scenario | Purpose
ES1 | Climate Change 1 | Impact of climate change on long-term weather and vegetation conditions that impact fire behavior.
Weather Condition 2
Vegetation Condition 3

## Table 5-6
Table 5‑6: Liberty Utility Risk Assessment Improvement Plan
Key Risk Assessment Area | Proposed Improvement | Type of Improvement | Expected Value Add | Timeframe and Key Milestones
RA-1, Data Quality and Data Input | Establish a process to continually test data quality and data input to improve the results of the tool | Programmatic and technical | This is a programmatic and technical improvement to continually test and improve the data | Data will be tested annually, or more frequently, and the first test will be performed in 2026
RA-2, Risk Assessment Methodology | Establish a process to continually test the risk modeling methodology and benchmark with peer utilities. Include wildfire and PSPS risk assessment documentation, including both quantitative and qualitative approaches | Programmatic and technical | This is a programmatic and technical improvement to continually improve the risk calculations and model | The methodology will be tested annually, or more frequently, and the first test will be performed in 2026
RA-3, Evaluate and Improve Results | Establish a feedback loop with subject matter experts to continually test and improve the results of the risk tool. This should include presentation of risk, including dashboards and assessments | Programmatic and technical | This is a programmatic and technical improvement to continually improve the results of the risk assessment tool | The results, including the top-risk circuits list, will be tested annually, or more frequently, and the first test will be in 2026
RA-4, Risk Event Tracking and Testing | Establish a process to track and reconstruct risk events for the purpose of integrating lessons learned and improvement | Programmatic and technical | This is a programmatic and technical improvement to continually improve the results of the risk assessment tool | Liberty will track and reconstruct a minimum of three events to integrate lessons learned. The first three events will be reconstructed and tested in 2026
RA-5, Use the Results to Inform Decision Making and Design Basis | Establish a cadence to present and deliver the results with business planners and operators to be incorporated into the decision-making and design process. This should include justification for design basis scenarios | Programmatic | This is a programmatic improvement to advance risk-based decision making | The risk assessment results will be produced annually, or more frequently, so Liberty can better inform the WMP Updates, including the 2027 Update, and subsequent Updates and Base Plan submittals
RA-6, Establish Clear Roles and Responsibility to Drive Improvement | Assign a dedicated resource the responsibility of improving and delivering risk-based results for better decision making. Place an emphasis on data quality, methodology, and subject matter expert and industry tested results | Programmatic | Dedicating an employee to focus on and execute continual improvement actions will lead to a better tool and subsequent results | Liberty will onboard the dedicate resource by Q2 2026 with an established role and responsibilities. Further, to ensure continued improvement, Liberty will finalize a documented procedure that compliments the continuous improvement portion of this Risk Assessment Improvement Plan by Q3 2026
RA-7, Evaluate and Improve the Outage Risk Results | Evaluate and improve the calculation and scaling of outage risk including, but not limited to, the items included in RN-LU-26-01 | Technical | Improved outage and PSPS results will improve the quality of the overall utility risk results. Improved results will allow for more informed business, design, and operational decision making. When the results are trusted by the subject matter experts, the program and tool will build acceptance and advance the associated risk mitigation | These improvements will be complete so the updated results can be included in the 2027 WMP Update

## Table 5-4
Table 5‑4: Summary of Fire Risk Model and PSPS Risk Model
FIRE RISK MODEL
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
UR | Utility Risk | Previous modeling scenarios | Wildfire Risk | Previous modeling steps | Utility Risk | Risk score between 0-1
PSPS Risk
Asset Failure Risk
WR | Wildfire Risk | WC1, WC2, VC1, VC2, VC3, WLC5 | Wildfire Likelihood | Previous modeling steps | Fire Risk Score 0-81 | Risk score between 0-1
Wildfire Consequence
WC | Wildfire Consequence | WC1, WC2, WLC5 | Population Impact | WFA Conditional Fire Risk | Fire Size Potential, Buildings Threatened/Destroyed, Population Impacts | Risk score between 0-1
|  |  | Impacted structures | WFA Expected Fire Risk
Acres burned
Spatial/Temporal ignition patterns
WL | Wildfire Likelihood | WC1, WC2, VC1, VC2, VC3, WLC5 | Probability of Outage (“POU”) | Previous modeling steps | Probability of wildfire caused by electrical equipment | 0-1 probability
Probability of Ignition (“POI”)
Probability of Failure (“POF”)
AFR | Asset Failure Risk | VC1, VC2 | Probability of Failure | Previous modeling steps | Asset Failure Risk | Risk score between 0-1
Consequence of Failure
APF | Probability of Failure | VC1, VC2 | Utility Asset Data | GIS System | Asset Probability of Failure Score | 0-1 probability
|  |  | Outage Data | OMS
Condition Modifiers
ACF | Consequence of Failure | No design scenario | Fire Consequence Metrics | Technosylva WFA | Asset Consequence of Failure Score | Risk score between 0-1
Community Resilience
Probability of Ignition
PSPS RISK MODEL
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
PR | PSPS Risk | WC1 | PSPS Consequence | Previous modeling steps | PSPS Risk | Risk score between 0-1
PSPS Likelihood
PC | PSPS Consequence | WC1 | Outage duration | Customer records | PSPS Consequence Risk | Risk score between 0-1
Customer count by circuit
PL | PSPS Likelihood | WC1, WLC3 | PSPS thresholds relative to weather conditions | Gridded hourly weather data | PSPS Likelihood Risk | 0-1 probability
SRP Availability
OPR | Outage Program Risk | No design scenario | PSPS Risk | Previous modeling steps | Outage Program Risk | Risk score between 0-1
SRP Outage Risk
SOR | SRP Outage Risk | No design scenario | SRP Outage Likelihood | Previous modeling steps | SRP Outage Risk | Risk score between 0-1
SRP Outage Consequence
SOL | SRP Outage Likelihood | WC1, WLC3 | Technosylva WFA | Asset Failure Risk | SRP Outage Likelihood | 0-1 probability
|  |  | Asset Failure Risk | Technosylva
SOC | SRP Outage Consequence | No design scenario | Outage duration | Customer records | SRP Outage Consequence | Risk score between 0-1
Customer count driven by circuit

## Table 5-5
Table 5‑5: Liberty Top-Risk Circuits
Utility Risk Rank | Circuit ID | Wildfire Risk | Primary Overhead Miles | Top Risk Contributors | Version of Risk Model used
1 | MEY3400 | 0.41634 | 54.1102 | Age of Assets Tree Attachments Expulsion Fuses Vegetation | DRAT Phase 3.1
2 | MEY3300 | 0.22674 | 52.5764 | Age of Assets Expulsion Fuses | DRAT Phase 3.1
3 | MEY3500 | 0.11497 | 27.2045 | Age of Assets Tree Attachments Expulsion Fuses Vegetation | DRAT Phase 3.1
4 | STL3101 | 0.09903 | 15.5184 | Age of Assets Vegetation | DRAT Phase 3.1
5 | GLS7400 | 0.091791 | 32.6838 | Age of Assets Expulsion Fuses | DRAT Phase 3.1
6 | POR3200 | 0.085682 | 20.7806 | Age of Assets Tree Attachments Expulsion Fuses | DRAT Phase 3.1
7 | TAH7300 | 0.083782 | 56.6554 | Age of Assets Tree Attachments Expulsion Fuses | DRAT Phase 3.1
8 | SRB51 | 0.073794 | 6.8057 | Age of Assets | DRAT Phase 3.1
9 | TPZ1202 | 0.0707 | 54.6285 | Expulsion Fuses | DRAT Phase 3.1
10 | MEY3200 | 0.067784 | 21.5137 | Age of Assets Tree Attachments Expulsion Fuses Vegetation | DRAT Phase 3.1
11 | MEY3100 | 0.049425 | 17.523 | Age of Assets Tree Attachments Expulsion Fuses Vegetation | DRAT Phase 3.1
12 | CAL2501 | 0.041789 | 4.6404 | Age of Assets Vegetation | DRAT Phase 3.1
13 | MULLER1296 | 0.036705 | 43.5564 | Expulsion Fuses | DRAT Phase 3.1
14 | STL3501 | 0.029134 | 13.7961 | Age of Assets Tree Attachments Expulsion Fuses | DRAT Phase 3.1
15 | SQV8200 | 0.028243 | 5.0127 | Expulsion Fuses Vegetation | DRAT Phase 3.1
16 | POR3100 | 0.028149 | 13.2601 | Age of Assets | DRAT Phase 3.1
17 | T608 | 0.026781 | 17.278 | Vegetation | DRAT Phase 3.1
18 | KBH5200 | 0.021719 | 23.2809 | Age of Assets Tree Attachments Expulsion Fuses Vegetation | DRAT Phase 3.1
19 | TAH5201 | 0.017803 | 21.082 | Age of Assets Expulsion Fuses | DRAT Phase 3.1

## Table 6-1
Table 6‑1: Circuit Prioritization List Based on Overall Utility Risk
Priority | Circuit | Length (miles) | Wildfire Risk | Percent of Overall Fire Risk | Associated Risk Drivers
1 | MEY3400 | 54.1102 | 0.41634 | 23.4% | Age of Assets Tree Attachments Expulsion Fuses Vegetation
2 | MEY3300 | 52.5764 | 0.22674 | 12.74% | Age of Assets Expulsion Fuses
3 | MEY3500 | 27.2045 | 0.11497 | 6.462% | Age of Assets Tree Attachments Expulsion Fuses Vegetation
4 | STL3101 | 15.5184 | 0.09903 | 5.566% | Age of Assets Vegetation
5 | GLS7400 | 32.6838 | 0.091791 | 5.159% | Age of Assets Expulsion Fuses
6 | POR3200 | 20.7806 | 0.085682 | 4.816% | Age of Assets Tree Attachments Expulsion Fuses
7 | TAH7300 | 56.6554 | 0.083782 | 4.709% | Age of Assets Tree Attachments Expulsion Fuses
8 | SRB51 | 6.8057 | 0.073794 | 4.148% | Age of Assets
9 | TPZ1202 | 54.6285 | 0.0707 | 3.974% | Expulsion Fuses
10 | MEY3200 | 21.5137 | 0.067784 | 3.81% | Age of Assets Tree Attachments Expulsion Fuses Vegetation
11 | MEY3100 | 17.523 | 0.049425 | 2.778% | Age of Assets Tree Attachments Expulsion Fuses Vegetation
12 | CAL2501 | 4.6404 | 0.041789 | 2.349% | Age of Assets Vegetation
13 | MULLER1296 | 43.5564 | 0.036705 | 2.063% | Expulsion Fuses
14 | STL3501 | 13.7961 | 0.029134 | 1.638% | Age of Assets Tree Attachments Expulsion Fuses
15 | SQV8200 | 5.0127 | 0.028243 | 1.587% | Expulsion Fuses Vegetation
16 | POR3100 | 13.2601 | 0.028149 | 1.582% | Age of Assets
17 | T608 | 17.278 | 0.026781 | 1.505% | Vegetation
18 | KBH5200 | 23.2809 | 0.021719 | 1.221% | Age of Assets Tree Attachments Expulsion Fuses Vegetation
19 | TAH5201 | 21.082 | 0.017803 | 1.001% | Age of Assets Expulsion Fuses

## LU Table 6-1
LU Table 6-1: Initiative Activities for Risk Drivers of Prioritized Circuits
Activity | Risk Reduction | Estimated Cost | Impacts | Implementation Schedule
Pole Replacement | 14% | 15000000 | Refer to Section 8 | Refer to Section 8
Tree Attachment Removal | 2% | 3490000 | Refer to Section 8 | Refer to Section 8
Fuse Replacements | 8% | 6000000 | Refer to Section 8 | Refer to Section 8
Vegetation Work | 2% | 36000000 | Refer to Section 9 | Refer to Section 9

## Table 6-2
Table 6‑2: Liberty Stakeholder Roles and Responsibilities in the Decision-Making Process
Stakeholder | Stakeholder Point of Contact | Electrical Corporation Point of Contact | Stakeholder Role | Engagement Methods | Activity | Level of Engagement Activity
Liberty Executive Leadership | Chief Executive Officer; Chief Transformation Officer | Liberty President | Informed; Consulted; Decision-maker | Quarterly Meetings; Emails; Phone Calls | All WMP activities | Local; State; Federal; Tribal
County | County Supervisor | Senior Manager, Customer Solutions; Emergency Manager | Informed | Meetings, exercises, workshops | System hardening; vegetation management; emergency preparedness | Local
Tahoe Regional Planning Agency | Special Projects Manager; Associate Environmental Specialist; Forester | Manager, Vegetation Management; Environmental Specialist | Decision-maker; consulted | Planning and prioritizing all WF mitigations | System hardening; vegetation management | Local
Sheriff's Department | Sherriff; Office of Emergency Services | Manager, Emergency Management | informed; decision-maker | Meetings, exercises, workshops | Emergency preparedness | Local
Cal Fire | Battalion Chief; Assistant Chief | Fire Protection Specialist; System Forester; Manager, Emergency Management | Informed; Consulted; Decision-maker | Meetings, Emails, Phone Calls, Exercises | Vegetation management, emergency preparedness; community outreach | Local, State
California Tahoe Conservancy | Public Land Management Specialist, Associate Environmental Planner | Manager, Vegetation Management; Environmental Specialist | Decision-maker; consulted | Meetings, Emails, Phone Calls | System hardening; vegetation management | Local, State
California State Parks | Senior Environmental Scientist, California State Parks - Sierra District | Manager, Vegetation Management; Environmental Specialist | Decision-maker; consulted | Meetings, Emails, Phone Calls | System hardening; vegetation management | Local, State
City | City Manager | Senior Manager, Customer Solutions; Emergency Manager | Informed; Consulted; Decision-maker | Meetings, Emails, Phone Calls | System hardening, vegetation management, emergency preparedness, community outreach | Local
US Forest Service | Recreation Management Specialist, Lands and Special Uses | Manager, Vegetation Management; Environmental Specialist | Decision-maker; consulted | Meetings, Emails, Phone Calls, Operating Plans | System hardening; vegetation management | Local, Federal
Cal Trans | District Permit Engineer | Manager, Vegetation Management; Manager, Lands | Decision-maker; consulted | Meetings, Emails | System hardening; vegetation management | Local, State
Fire Department | Fire Chief | Fire Protection Specialist; Manager, Emergency Management; System Forester | Decision-maker; informed; consulted | Meetings; Emails, Exercises | Vegetation management, emergency preparedness; community outreach | Local
Public; customers | Varies; Manager, Communications | Varies | Informed | Workshops, outreach events, bill inserts, social media | System hardening, vegetation management, emergency preparedness | Local
Washoe Tribe | Emergency Manager, California Tribal Historic Preservation Officer | Key Account Manager, Emergency Manager, Environmental Specialist | Decision-maker, Consulted, Informed | Meetings, Email, Phone Call | Emergency preparedness, community outreach, cultural consultation and monitoring | Tribal
Key Accounts; Critical Facilities | Varies | Key Account Manager; Sr. Manager Customer Solutions | Informed; Consulted | Meetings, Emails, Phone Call | System hardening, vegetation management, emergency preparedness, community outreach | Local
Bureau of Land Management | Sierra Front Office - Assistant Field Manager | Environmental Specialist | Decision-maker; consulted | Meetings, Emails, Phone Calls | System hardening, vegetation management | Federal
NV Energy | Emergency Manager; Principal Meteorologist | Manager, Emergency Management; Sr. Manager, Wildfire Prevention | Decision-maker; consulted; informed |  | Emergency preparedness | Local
Community Based Organizations | Varies | Key Account Manager; Sr. Manager Customer Solutions | Informed; Consulted | workshops, outreach events, meetings, emails, phone calls | Emergency preparedness, community outreach | Local

## Table 6-3
Table 6‑3: Risk Impact Activities
Activity | Activity ID # | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness – Outage Program Risk | Cost-Benefit Score Overall Risk | Cost-Benefit Score Wildfire Risk | Cost-Benefit Score Outage Program Risk | % HFTD Covered | % HFTD/HFRA Covered | Expected % Risk Reduction | Model used to Calculate Risk Impact
Grid monitoring systems | WMP-SA-02 | Not Calculated | Not Calculated | Not Calculated | Not Calculated | Not Calculated | Not Calculated | 100% | 100% | Not Calculated | DRAT 3.1
Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01 | Not Calculated | 50% | Not Calculated | Not Calculated | 125000 | Not Calculated | 100% | 100% | 4.671% | DRAT 3.1
Expulsion fuse replacement | WMP-GDOM-GH-12b | Not Calculated | 39.67% | Not Calculated | Not Calculated | 10083.5917 | Not Calculated | 47.62% | 44.35% | 8.111% | DRAT 3.1
Distribution pole replacements and reinforcements | WMP-GDOM-GH-03 | Not Calculated | 95% | Not Calculated | Not Calculated | 13157.8947 | Not Calculated | 6.388% | 5.957% | 14.11% | DRAT 3.1
Open wire/grey wire | WMP-GDOM-GH-12e | Not Calculated | 78.72% | Not Calculated | Not Calculated | 732879.925 | Not Calculated | 100% | 100% | 0.8882% | DRAT 3.1
Vegetation Management Inspection Program - Detailed | WMP-VM-INSP-01 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | DRAT 3.1
Undergrounding of electric lines and/or equipment | WMP-GDOM-GH-02 | Not Calculated | 99% | Not Calculated | Not Calculated | Not Calculated | Not Calculated | 0% | 0% | 0% | DRAT 3.1
Wood and Slash Management | WMP-VM-VFM-02 | Not Calculated | 50% | Not Calculated | 48607.6432 | 48607.6432 | Not Calculated | 35.38% | 32.94% | 2.82% | DRAT 3.1
Quality Assurance and Quality Control | WMP-VM-QAQC-01 | Not Calculated | 30.59% | Not Calculated | Not Calculated | 6902.6165 | Not Calculated | 36% | 36% | Non-significant | DRAT 3.1
Covered conductor installation | WMP-GDOM-GH-01 | Not Calculated | 50% | Not Calculated | Not Calculated | 4139456.8293 | Not Calculated | 1.7% | 1.583% | 1.998% | DRAT 3.1
Clearance | WMP-VM-VFM-05 | Not Calculated | 50% | Not Calculated | Not Calculated | 14.9178 | Not Calculated | 100% | 100% | 1.913% | DRAT 3.1
Fall-In Mitigation | WMP-VM-VFM-06 | Not Calculated | 50% | Not Calculated | Not Calculated | 3505.3514 | Not Calculated | 100% | 100% | 2.626% | DRAT 3.1
Detailed inspections of distribution electric lines and equipment | WMP-GDOM-AI-01 | 0% | 0% | 0% | 0% | 0% | 0% | 63.68% | 60.54% | 0% | DRAT 3.1
Tree attachment removals | WMP-GDOM-GH-12a | Not Calculated | 78.72% | Not Calculated | Not Calculated | 24303.8247 | Not Calculated | 9.934% | 9.444% | 1.996% | DRAT 3.1
Vegetation Inspection - LiDAR and Patrol |  | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | DRAT 3.1
Pole Clearing | WMP-VM-VFM-01 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | DRAT 3.1
Patrol inspections of distribution electric lines and equipment | WMP-GDOM-AI-03 | Not Calculated | 40.5% | Not Calculated | Not Calculated | 239.2322 | Not Calculated | 100% | 100% | Non-significant | DRAT 3.1
Fire-Resilient Right-of-Ways | WMP-VM-VFM-04 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 0% | DRAT 3.1
Intrusive pole inspections | WMP-GDOM-AI-02 | 0% | 0% | 0% | 0% | 0% | 0% | 37.52% | 37.14% | 0% | DRAT 3.1
Other discretionary inspections of distribution electric lines and equipment: Drone inspections | WMP-GDOM-AI-04 | 0% | 0% | 0% | 0% | 0% | 0% | 7.369% | 6.924% | 0% | DRAT 3.1

## Table 6-4
Table 6‑4: Summary of Risk Reduction for Top Circuits
Circuit | Initial Wildfire Risk | 2026 Activities | 2026 Wildfire Risk | 2027 Activities | 2027 Wildfire Risk | 2028 Activities | 2028 Wildfire Risk
MEY3400 | 0.41634 | Grid hardening, including covered conductor, VM, patrol inspections, drone inspections | 0.27642 | Grid hardening, including covered conductor, VM, detailed inspections, drone inspections | 0.24214 | Grid hardening, VM, patrol inspections, drone inspections | 0.26426
MEY3300 | 0.22674 | Grid hardening, VM, detailed inspections, drone inspections | 0.22161 | Grid hardening, VM, patrol inspections, drone inspections | 0.22855 | Grid hardening, VM, patrol inspections, drone inspections | 0.22686
MEY3500 | 0.11497 | Grid hardening, VM, patrol inspections, drone inspections | 0.10704 | Grid hardening, VM, detailed inspections, drone inspections | 0.093108 | Grid hardening, VM, patrol inspections, drone inspections | 0.099085
STL3101 | 0.09903 | Grid hardening, VM, patrol inspections | 0.063062 | Grid hardening, VM, detailed inspections | 0.068991 | Grid hardening, VM, patrol inspections | 0.051645
GLS7400 | 0.091791 | Grid hardening, VM, patrol inspections | 0.085975 | Grid hardening, VM, patrol inspections | 0.09207 | Grid hardening, VM, detailed inspections | 0.1025
POR3200 | 0.085682 | Grid hardening, VM, patrol inspections | 0.058914 | Grid hardening, VM, patrol inspections | 0.060096 | Grid hardening, VM, patrol inspections | 0.063755
TAH7300 | 0.083782 | Grid hardening, VM, patrol inspections | 0.067613 | Grid hardening, VM, patrol inspections | 0.059359 | Grid hardening, VM, patrol inspections | 0.064145
SRB51 | 0.073794 | Grid hardening, VM, patrol inspections | 0.092946 | Grid hardening, VM, patrol inspections | 0.09682 | Grid hardening, VM, detailed inspections | 0.088052
TPZ1202 | 0.0707 | Grid hardening, VM, Detailed Inspections | 0.080044 | Grid hardening, VM, patrol inspections | 0.060783 | Grid hardening, VM, patrol inspections | 0.063262
MEY3200 | 0.067784 | Grid hardening, VM, patrol inspections, drone inspections | 0.045047 | Grid hardening, VM, patrol inspections, drone inspections | 0.063873 | Grid hardening, VM, patrol inspections, drone inspections | 0.064989
MEY3100 | 0.049425 | Grid hardening, VM, patrol inspections | 0.046784 | Grid hardening, VM, detailed inspections | 0.042189 | Grid hardening, VM, patrol inspections | 0.047203
CAL2501 | 0.041789 | Grid hardening, VM, patrol inspections | 0.024844 | Grid hardening, VM, patrol inspections | 0.031354 | Grid hardening, VM, detailed inspections | 0.03031
MULLER1296 | 0.036705 | Grid hardening, including covered conductor, VM, detailed inspections | 0.026088 | Grid hardening, including covered conductor, VM, patrol inspections | 0.027208 | Grid hardening, including covered conductor, VM, patrol inspections | 0.025093
STL3501 | 0.029134 | Grid hardening, VM, patrol inspections | 0.029884 | Grid hardening, VM, detailed inspections | 0.035679 | Grid hardening, VM, patrol inspections | 0.021659
SQV8200 | 0.028243 | Grid hardening, VM, patrol inspections | 0.023451 | Grid hardening, VM, patrol inspections | 0.024808 | Grid hardening, VM, detailed inspections | 0.017321
POR3100 | 0.028149 | Grid hardening, VM, patrol inspections | 0.030841 | Grid hardening, VM, patrol inspections | 0.025383 | Grid hardening, VM, detailed inspections | 0.020278
T608 | 0.026781 | Grid hardening, VM, patrol inspections | 0.030525 | Grid hardening, VM, patrol inspections | 0.02203 | Grid hardening, VM, detailed inspections | 0.036365
KBH5200 | 0.021719 | Grid hardening, VM, patrol inspections | 0.013496 | Grid hardening, VM, patrol inspections | 0.018948 | Grid hardening, VM, patrol inspections | 0.016107
TAH5201 | 0.017803 | Grid hardening, VM, patrol inspections | 0.02084 | Grid hardening, VM, patrol inspections | 0.02267 | Grid hardening, VM, patrol inspections | 0.020698

## LU Table 7-1
LU Table 7‑1: Lessons Learned from Liberty PSPS Events
Observation | Corrective Action | Status of Corrective Action
Medical Baseline (MBL) customer tags on meters needed to be updated. | Perform field audit of all MBL meters on the system to confirm proper tags are in place. | To be completed as of 12/31/2025
Improved communication is needed between regulatory liaisons and other members of the IMT to record event information more efficiently, such as customer impact counts and communications with Public Safety Partners (“PSPs”). | Improvements to the incident tracking spreadsheet. | Completed
Improved logistics are needed to support the Washoe CRC location, which is relatively remote. More affordable options for lunch items at the CRC and more timely transport and distribution of repair supplies to the Walker and Coleville areas are needed. | Put contracts in place with vendors for CRC lunches. Stage repair materials in Liberty’s CONEX boxes for use in the Walker and Coleville areas. | Completed
During 2024 PSPS events, Liberty’s Community Outreach team took responsibility for notifying PSPs, community officials, and key accounts instead of the PSP liaison, who has multiple duties. | Officially assign PSP notification responsibility to the community outreach team. | Completed

## Table 8-1
Table 8‑1: Liberty Grid Design, Operation and Maintenance Targets by Year, 2026-2028 [4]
WMP Initiative Category | Quantitative or Qualitative Target | WMP Initiative Activity | WMP Initiative Tracking ID | Target Unit | 2026 Target / Status | % Planned in HFTD for 2026 | % Planned in HFRA for 2026 | % Risk Reduction for 2026 | 2027 Target / Status | % Planned in HFTD for 2027 | % Planned in HFRA in 2027 | % Risk Reduction for 2027 | 2028 Target / Status | % Planned in HFTD for 2028 | % HFRA planned in 2028 | % Risk Reduction for 2028 | Three- Year Total | Section; Page Number
Grid Design, Operations, and Maintenance | Quantitative | Covered conductor installation | WMP-GDOM-GH-01 | Circuit miles | 3.9 | 100% | 100% | 2.51% | 3.5 | 100% | 100% | 3.47% | 3.7 | 100% | 100% | 2% | 11.1 | 8.2.1; pp.117-119
Grid Design, Operations, and Maintenance | Quantitative | Undergrounding of electric lines and/or equipment | WMP-GDOM-GH-02 | Circuit miles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2.2; pp. 119-120
Grid Design, Operations, and Maintenance | Quantitative | Distribution pole replacements and reinforcements[1] | WMP-GDOM-GH-03 | Poles | 400 | 100% | 100% | 13.29% | 400 | 100% | 100% | 16.21% | 400 | 100% | 100% | 12.77% | 1200 | 8.2.3; pp. 120-122
Grid Design, Operations, and Maintenance | Quantitative | Traditional overhead hardening | WMP-GDOM-GH-05 | Circuit miles | 1.1 | 100% | 100% | Not calculated | 1.1 | 100% | 100% | Not calculated | 1.1 | 100% | 100% | Not calculated | 3.3 | 8.2.5; pp. 122-124
Grid Design, Operations, and Maintenance | Quantitative | Emerging grid hardening technology installations and pilot progress | WMP-GDOM-GH-06 | No target unit identified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2.6; p. 124
Grid Design, Operations, and Maintenance | Quantitative | Microgrids | WMP-GDOM-GH-07 | Microgrids | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2.7; pp. 124-125
Grid Design, Operations, and Maintenance | Quantitative | Installation of system automation equipment | WMP-GDOM-GH-08 | Automatic Reclosers | 0; initiative is complete | 0 | 0 | 0 | 0; initiative is complete | 0 | 0 | 0 | 0; initiative is complete | 0 | 0 | 0 | 0 | 8.2.8; p. 125
Grid Design, Operations, and Maintenance | Quantitative | Line removal (in HFTD) | WMP-GDOM-GH-09 | Circuit miles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2.9; p. 126
Grid Design, Operations, and Maintenance | Quantitative | Other technologies and systems not listed above: | WMP-GDOM-GH-12 [5] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8.2.12; pp. 126-130
Grid Design, Operations, and Maintenance | Quantitative | Tree attachment removals | WMP-GDOM-GH-12a | Tree attachments | 60 | 100% | 100% | 1.46% | 60 | 100% | 100% | 3.11% | 60 | 100% | 100% | 0.89% | 180 | 8.2.12.1; pp. 126-128
Grid Design, Operations, and Maintenance | Quantitative | Expulsion fuse replacement | WMP-GDOM-GH-12b | Expulsion fuses | 500 | 100% | 100% | 6.17% | 500 | 100% | 100% | 6.59% | 500 | 100% | 100% | 11.39% | 1500 | 8.2.12.2; pp. 128-129
Grid Design, Operations, and Maintenance | Quantitative | Animal guards | WMP-GDOM-GH-12c | Animal guards | 0; initiative is complete | 0 | 0 | 0 | 0; initiative is complete | 0 | 0 | 0 | 0; initiative is complete | 0 | 0 | 0 | 0 | 8.2.12.3; p. 129
Grid Design, Operations, and Maintenance | Quantitative | Open wire/grey wire | WMP-GDOM-GH-12e | Circuit miles | 5.2 | 100% | 100% | 0.08% | 5.2 | 100% | 100% | 3.11% | 5.2 | 100% | 100% | 0.89% | 15.6 | 8.2.12.5; pp. 129-130
Grid Design, Operations, and Maintenance | Quantitative | Detailed inspections of distribution electric lines and equipment[2] | WMP-GDOM-AI-01 | Circuit miles | 207 | 97% | 100% | 0% | 198.5 | 99% | 100% | 0% | 219.5 | 85% | 100% | 0% | 625 | 8.3.1; pp. 134-135
Grid Design, Operations, and Maintenance | Quantitative | Intrusive pole inspections | WMP-GDOM-AI-02 | Poles | 2031 | 98% | 100% | 0% | 2389 | 97% | 100% | 0% | 2860 | 88% | 100% | 0% | 7280 | 8.3.2; pp. 135-136
Grid Design, Operations, and Maintenance | Quantitative | Patrol inspections of distribution electric lines and equipment[3] | WMP-GDOM-AI-03 | Circuit miles | 553.4 | 93% | 100% | 0% | 568.8 | 93% | 100% | 0% | 542.8 | 96% | 100% | 0% | 1665 | 8.3.3; p. 136
Grid Design, Operations, and Maintenance | Quantitative | Other discretionary inspections of distribution electric lines and equipment: Drone inspections | WMP-GDOM-AI-04 | Circuit miles (primary and secondary) | 127 | TBD | 100% | 0 | 127 | TBD | 100% | 0 | 127 | TBD | 100% | 0 | 381 | 8.3.4; p. 137-138
Grid Design, Operations, and Maintenance | Quantitative | Quality assurance / quality control of inspections | WMP-GDOM-AI-05 | % of detailed inspections | 12% | TBD – based on QA/QC sample | 100% | 0% | 12% | TBD – based on QA/QC sample | 100% | 0% | 12% | TBD – based on QA/QC sample | 100% | 0% | 12% | 8.5; pp. 148-154
Grid Design, Operations, and Maintenance | Quantitative | Substation inspections | WMP-GDOM-AI-06 | Substations | 44 | 100% | 100% | 0 | 44 | 100% | 100% | 0 | 44 | 100% | 100% | 0 | 132 | 8.3.5; p.138
Grid Design, Operations, and Maintenance | Qualitative | Equipment Maintenance and Repair | WMP-GDOM-MR-01 | Utilization of Asset Tracking Application | All Asset Inspections and Repairs recorded in Asset Tracking | N/A | N/A | Not calculated | All Asset Inspections and Repairs recorded in Asset Tracking | N/A | N/A | Not calculated | All Asset Inspections and Repairs recorded in Asset Tracking | N/A | N/A | Not calculated | All Asset Inspections and Repairs recorded in Asset Tracking | 8.4; p.139-147
Grid Design, Operations, and Maintenance | Quantitative | Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01 | # of circuits with SRP | Complete - SRP implemented on 100% of Liberty circuits | 100% | 100% | 5.03% | Complete - SRP implemented on 100% of Liberty circuits | 100% | 100% | 3.18% | Complete - SRP implemented on 100% of Liberty circuits | 100% | 100% | 5.75% | Complete – SRP implemented on 100% of Liberty circuits | 8.7.1; pp. 158-160
Grid Design, Operations, and Maintenance – Grid Operations and Procedures | Qualitative | Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01 | SRP circuit settings | Review settings of 1/3 of SRP circuits | 83% | 100% | Not calculated | Review settings of 1/3 of SRP circuits | 83% | 100% | Not calculated | Review settings of 1/3 of SRP circuits | 83% | 100% | Not calculated | Review of all SRP circuits | 8.7.1; pp. 158-160
Grid Design, Operations, and Maintenance | Qualitative | Work Orders | WMP-GDOM-AI | Complete all work orders within specified timeframe according to priority level | No new past due work orders from inspections | N/A | N/A | Not calculated | No new past due work orders from inspections | N/A | N/A | Not calculated | No past due work orders | N/A | N/A | Not calculated | No past due work orders | 8.6; pp. 155-157
Grid Design, Operations, and Maintenance | Qualitative | Workforce Planning | WMP-GDOM-AI | Inspector Training Program – Standards for Development | Approval and adoption of Standards for Inspector Development | N/A | N/A | Not calculated | Implement Inspector Training Program | N/A | N/A | Not calculated | All new inspectors complete Inspector Training Program | N/A | N/A | Not calculated | All new inspectors complete Inspector Training Program | 8.7.4; pp.163-166
[1] Liberty does not have a separate WMP initiative for transmission pole and tower replacements. Liberty captures pole replacements on its transmission system within WMP-GDOM-03.
[2] Liberty does not have a separate program for transmission inspections. Liberty has approximately 75 miles of 60kV lines and 19 miles of 120kV lines that are included in the distribution inspection program.
[3] Liberty does not have a separate program for transmission inspections. Liberty has approximately 75 miles of 60kV lines and 19 miles of 120kV lines that are included in the distribution inspection program.
[4] WMP initiatives with qualitative targets have N/A values for % Planned in HFTD/HFRA columns because those targets are not directed to specific locations.
[5] Refer to WMP initiatives WMP-GDOM-GH-12a, WMP-GDOM-GH-12b, WMP-GDOM-GH-12c, WMP-GDOM-GH-12e for relevant information related to these initiatives. WMP initiative WMP-GDOM-12 does not have a specified target as it is a combination of the aforementioned initiatives and therefore values in this row are N/A.

## Table 8-2
Table 8‑2: Liberty Asset Inspection Frequency, Method and Criteria
Type [1] | Inspection Activity (Program) | Frequency or Trigger (Note 1) | Method of Inspection (Note 2) | Governing Standards & Operating Procedures | Cumulative Quarterly Target 2026, Q1 | Cumulative Quarterly Target 2026, Q2 | Cumulative Quarterly Target 2026, Q3 | Cumulative Quarterly Target 2026, Q4 | Cumulative Quarterly Target 2027, Q1 | Cumulative Quarterly Target 2027, Q2 | Cumulative Quarterly Target 2027, Q3 | Cumulative Quarterly Target 2027, Q4 | Cumulative Quarterly Target 2028, Q1 | Cumulative Quarterly Target 2028, Q2 | Cumulative Quarterly Target 2028, Q3 | Cumulative Quarterly Target 2028, Q4 | % of HFRA and HFTD Covered Annually by Inspection Type | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Distribution | Detailed Inspections | 5-year cycle for OH; | Ground | G.O. 165 | 20 circuit miles | 50 circuit miles | 150 circuit miles | 207 circuit miles | 20 circuit miles | 50 circuit miles | 150 circuit miles | 198.5 circuit miles | 20 circuit miles | 50 circuit miles | 150 circuit miles | 219.5 circuit miles | 20% | 0.03% | 7.75% | 30.1% (Assets)
|  | 3-year cycle for UG | [15 empty] | (Assets) | (Assets)
Distribution | Intrusive Pole Inspections | 10-year cycle | Ground | G.O. 165 | 0 poles | 0 poles | 2,031 poles | 2,031 poles | 0 poles | 0 poles | 2,389 poles | 2,389 poles | 0 poles | 0 poles | 2,860 poles | 2,860 poles | 10% | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection
Distribution | Patrol Inspections | Annually | Ground and Aerial | G.O. 165 | 200 circuit miles | 553.4 circuit miles | 553.4 circuit miles | 553.4 circuit miles | 200 circuit miles | 568.8 circuit miles | 568.8 circuit miles | 568.8 circuit miles | 200 circuit miles | 542.8 circuit miles | 542.8 circuit miles | 542.8 circuit miles | 80% | 0.02% | 0.12% | 0.04% (Assets)
[18 empty] | (Assets) | (Assets)
Distribution | Other Discretionary Inspections: Drone inspections | No specified frequency | Drone | G.O. 165 | 0 circuit miles | 0 circuit miles | 127 circuit miles | 127 circuit miles | 0 circuit miles | 127 circuit miles | 127 circuit miles | 127 circuit miles | 0 circuit miles | 127 circuit miles | 127 circuit miles | 127 circuit miles | 7% | TBD | TBD | TBD
Substation | Substation Inspections | Quarterly | Ground | G.O. 174 | 10 substations | 22 substations | 34 substations | 44 substations | 10 substations | 22 substations | 34 substations | 44 substations | 10 substations | 22 substations | 34 substations | 44 substations | 100% | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection
[1] Liberty does not have a separate program for transmission inspections. Liberty has approximately 75 miles of 60kV lines and 19 miles of 120kV lines that are included in the distribution inspection program.

## Table 8-3
Table 8‑3: Grid Hardening and Asset Inspection QA and QC Program Objectives
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
New construction in Grid Hardening WMP initiatives (i.e., Covered Conductor Installation) | (i.e., WMP-GDOM-GH-01) | Post-construction inspections | Confirm new construction meets applicable standards. New construction follows Liberty’s construction standards and best practices in construction.
Detailed Asset Inspections | WMP-GDOM-AI-01 | QC | Confirm that the inspection and corrective action process for existing electric distribution and transmission assets are conducted. and documented in an accurate and effective manner. Inspections are performed on all assets at the time of construction, while conducting G.O. 165 and G.O. 174 mandated patrols and detailed inspections and in compliance with Liberty’s OQ/QC 3rd party validation process to ensure accuracy is being met and constructions process are following the standards.
Equipment Settings to Reduce Wildfire Risk | WMP-GDOM-GO-01 | QA/QC | Relay settings are peer reviewed before being issued to the field. In-service settings are reviewed on a three-year cycle.

## Table 8-4
Table 8‑4: Grid Hardening and Asset Inspection QA and QC Activity Targets
Initiative/ Activity Being Audited | Type of Audit | Population/ Sample Unit | 2026: Population Size | 2026: Sample Size | 2027: Population Size | 2027: Sample Size | 2028: Population Size | 2028: Sample Size | Percent of Sample in the HFTD | Confidence level / MOE | 2026: Pass Rate Target | 2027: Pass Rate Target | 2028: Pass Rate Target
Detailed Asset Inspections | Field | Detailed asset inspections | All detailed inspections completed in 2026 | 12% | All detailed inspections completed in 2027 | 12% | All detailed inspections completed in 2027 | 12% | 100% | 95/10 | 90% | 90% | 90%
New construction in Grid Hardening WMP initiatives (i.e., Covered Conductor Installation) | Field | Completed new construction | All new construction completed in 2026 | 100% of new construction completed by contractors and 10% of new construction completed by Liberty | All new construction completed in 2027 | 100% of new construction completed by contractors and 10% of new construction completed by Liberty | All new construction completed in 2028 | 100% of new construction completed by contractors and 10% of new construction completed by Liberty | 100% | Unknown – population and sample sizes vary year to year | 95% | 95% | 95%

## LU Table 8-1
LU Table 8‑1: QA/QC Procedures
Document Name and ID | Version | Effective Date
Asset Inspection QA-QC 2023 Final | 1.1 | 2024-05-23
Underground Electric Standards | 2 | 2027-11-01
Overhead Electric Standards | 1 | 2019-09-01

## LU Table 8-2
LU Table 8‑2: Liberty Asset Inspection QA/QC Program Sample Size and Units
Inspection Type | Cycle | Total Circuit Miles | Total Units | Annual Circuit Miles | Annual Units | Statistical Sampling
[6 empty] | CL/MoE | % | Annual Sample Units
OH Poles, Devices, and Conductors | 5-year | 707 | Units N/A | 142 | Units N/A | 95/10 | 12% | 17 miles
Intrusive Pole | 10-year | N/A | 24700 | N/A | 2470 | 99/7 | 1% | 34 poles
Substations | Quarterly | N/A | 12 | N/A | 42 | Does not apply | 5% | 2 substations

## Table 8-5
Table 8‑5: Number of Past Due Asset Work Orders Categorized by Age
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 14 | 5 | 0 | 23
HFTD Tier 2 | 32 | 29 | 9 | 333
HFTD Tier 3 | 0 | 9 | 8 | 20

## Table 8-6
Table 8‑6: Number of Past Due Asset Work Orders Categorized by Age for Priority Levels
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 46 | 43 | 17 | 376
Priority 3 | 0 | 0 | 0 | 0

## Table 8-7
Table 8‑7: Top Impacted Circuits from SRP Program in 2024
Circuit/Circuit Segment ID | Circuit/Circuit Segment Name | Circuit/Circuit Segment Length (overhead circuit miles) | Number of Outages in Past Three Years | Cumulative Outage Duration | Cumulative Number of Customers Impacted by Outages
MEY3300 | Meyers 3300 | 52.6 | 1 | 128.58 | 19

## LU Table 8-3
LU Table 8‑3: Liberty Workforce Planning, Asset Inspections, Grid Hardening and Risk Event Inspection
Worker Title | Minimum Qualifications | Training Practices
Inspector Foreman | • Journeyman lineman | • Fulcrum application and database training
| • Minimum two years journeyman lineman experience | · On the job training of company standards and G.O. 95
• Class A Driver’s License
· Expert knowledge of G.O. 95 and company’s construction standards.
Inspector | • Journeyman lineman | • Fulcrum application and database training
| • Minimum one year journeyman lineman experience | • On the job training of company standards and G.O. 95
• Class A Driver’s License
• General knowledge of G.O. 95 and company’s construction standards
Qualified Electrical Worker (“QEW”) | • Journeyman lineman | • Fulcrum application and database training
| • Minimum one-year journeyman lineman experience | • On the job training of company standards and G.O. 95
• Class A Driver’s License
• General knowledge of G.O. 95 and Liberty’s construction standards
Lineman | • Journeyman lineman | • On the job training of company standards and G.O. 95
| • Class A Driver’s license | • On the job training of covered conductor
Lineman Working Foreman | • Journeyman lineman | • On the job training of company standards and G.O. 95
| • Minimum two years’ experience as Journeyman | • Hendrix training of covered conductor installation (ACS and Tree Wire)
• Lineman
• Class A Driver’s license
Engineer IV | • Must possess a Bachelor of Science in Electrical Engineering or an equivalent engineering degree from an accredited four-year college or university | • SEL, GIS, CAD, OCalc, Quadra, OSI PI, Aspen Oneliner
• Must hold PE certification
Capital Administrator | • Associates or Bachelor’s degree in Construction Administration, Accounting or a related field or a minimum of three years of technical experience with a utility or other related field | • Great Plains Job Cost Training, FERC Code Training, SOX Policy Training, Capital Expenditure Policy Training, Excel Training
• Working knowledge of accounting, project management and construction management practices
Project Manager | • Associates or Bachelor’s degree in Project Management, Construction Administration, Engineering in a related field or a PMP certification and a minimum of five years of technical experience with a utility or other related field. Must have a demonstrated working knowledge of project management and construction management practices. | • PM Basics, Capital Expenditure Policy Training, Great Plains training, MS Project, Excel Training, Electrical Distribution 101, OH & UG Const Training
Substation Electrician | • Must have successfully completed the Electrician Apprentice training program or equivalent | • On the job training of substation equipment maintenance and replacement
| • Must be qualified to perform switching | • On the job training of PZM application
Substation Electrician Foreman | • Journeyman Electrician | • On the job training of substation equipment maintenance and replacement
| • Minimum two years’ experience as journeyman electrician | • On the job training of PZM application
• Must be qualified to perform switching.
Job Facilitator | • Journeyman lineman | • On the job training of company standards and G.O. 95
| • Minimum two years’ experience as journeyman lineman | • On the job training of covered conductor installation (ACS and Tree Wire)
| • Class A Driver’s License | • On the job training of internal QA/QC process
• Fulcrum application and database training

## Table 9-1
Table 9‑1: Liberty Vegetation Management Targets by Year (Non-inspection Targets)
Initiative | Quantitative or Qualitative | Activity (Tracking ID) | Target Unit | 2026 Target/Status | x% Risk Impact | 2027 Target/Status | x% Risk Impact | 2028 Target/Status | x% Risk Impact | Three-Year Total | Section; Page Number
[5 empty] | 2026 |  | 2027 |  | 2028
Integrated Vegetation Management | Qualitative | Maintain Tree Line USA (WMP-VM-VFM-04) | N/A | Complete by December 31, 2026 | N/A | Complete by December 31, 2027 | N/A | Complete by December 31, 2028 | N/A | N/A | 9.7; pp. 186-188
Workforce Planning | Qualitative | Liberty will continue to report annually on its recruitment, retention, and training of vegetation management and inspection personnel. | N/A | Complete by December 31, 2026 | N/A | Complete by December 31, 2027 | N/A | Complete by December 31, 2028 | N/A | N/A | 9.13; pp. 208-211
Wood and Slash Management | Quantitative | WMP-VM-VFM-02 | Acres | 280 | 4.04% | 280 | 0.7% | 280 | 0.7% | 840 | 9.5; pp. 182-184
Substation Defensible Space | Quantitative | WMP-VM-VFM-03 | Substation inspections | 12 | 0% | 12 | 0% | 12 | 0% | 36 | 9.6; pp. 184-186
Clearance | Quantitative | WMP-VM-VFM-05 | Circuit miles | 700 | 2.96% | 700 | 3.34% | 700 | 1.91% | 2100 | 9.3; pp.179-181
Fall-In Mitigation | Quantitative | WMP-VM-VFM-06 | Circuit miles | 220 | 4.36% | 220 | 2.06% | 220 | 1.38% | 660 | 9.3; pp.179-181

## Table 9-2
Table 9‑2: Liberty Vegetation Management Inspections and Pole Clearing Targets by Year
Activity (Program) | Tracking ID | Target Unit | Cumulative (Cml.) Quarterly Target 2026, Q1 | Cml. Quarterly Target 2026, Q2 | Cml. Quarterly Target 2026, Q3 | Cml. Quarterly Target 2026, Q4 | Cml. Quarterly Target 2027, Q1 | Cml. Quarterly Target 2027, Q2 | Cml. Quarterly Target 2027, Q3 | Cml. Quarterly Target 2027, Q4 | Cml. Quarterly Target 2028, Q1 | Cml. Quarterly Target 2028, Q2 | Cml. Quarterly Target 2028, Q3 | Cml. Quarterly Target 2028, Q4 | % HFTD Covered in 2026 | % Risk Reduction 2026 | % Risk Reduction 2027 | % Risk Reduction 2028 | Three-Year Total | Activity Timeline Target | Section; Page Number
Vegetation Management Inspection Program - Detailed | WMP-VM-INSP-01 | Circuit miles | 55 | 110 | 165 | 220 | 55 | 110 | 165 | 220 | 55 | 110 | 165 | 220 | 33% | 0% | 0% | 0% | 660 | 365 days | 9.2.1; pp. 171-176
Vegetation Management Program - LiDAR | WMP-VM-INSP-03 | Circuit miles | 0 | 0 | 700 | 700 | 0 | 0 | 700 | 700 | 0 | 0 | 700 | 700 | 100% | 0% | 0% | 0% | 2100 | Approx. 90 days for acquisition to data delivery | 9.2.3; pp.177-179
Pole Clearing – PRC 4292 Required | WMP-VM-VFM-01 | Poles | 0 | 1633 | 3266 | 4900 | 0 | 1633 | 3266 | 4900 | 0 | 1633 | 3266 | 4900 | 100% | 0% | 0% | 0% | 14700 | Approx. 150 days | 9.4; pp.181-182
Pole Clearing – Discretionary | WMP-VM-VFM-01-D | Poles | 0 | 133 | 266 | 400 | 0 | 133 | 266 | 400 | 0 | 133 | 266 | 400 | 100% | 0% | 0% | 0% | 1200 | Approx. 150 days | 9.4; pp.181-182

## Table 9-3
Table 9‑3: Vegetation Management Inspection Frequency, Method, and Criteria
Inspection Type | Inspection Activity (Program) | Area Inspected | Frequency
Transmission and Distribution | Vegetation Management Program - LiDAR | Territory | Annual
Transmission and Distribution | Vegetation Management Program – Detailed | Territory | Three-year cycle
Transmission and Distribution | Vegetation Management Program – Patrol | Territory | As needed

## LU Table 9-1
LU Table 9‑1: Vegetation Management Detailed Inspection Procedures
Document Name and ID | Version | Effective Date
Vegetation Management Plan (VM-02) | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | 1 | 2021-04-08
Post Work Verification Procedure (VM-04) | 2 | 2025-02-28
Vegetation Threat Procedure (VM-05) | 2 | 2022-06-03
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | 1 | 2024-01-01
Vegetation Management Inspection Manual (VM-07) | 1 | 2023-08-25

## LU Table 9-2
LU Table 9-2: Radial Clearance Requirements PRC 4293; GO 95, HFTD (Case 14)
Voltage | Regulation Clearance Distance | Maintenance Action Threshold | Maintenance Clearance Distance
| (“RCD”) | (“MAT”) | (“MCD”)
12kV - 25kV | 4’ | 6’ | 12’-15’
60kV | 4’ | 6’ | 12’-15’
120kV | 10’ | 15’ | 30-35'

## LU Table 9-3
LU Table 9-3: Radial Clearance Requirements; GO 95, Rule 35, Non-HFTD (Case 13)
Voltage | Regulation Clearance Distance | Maintenance Action Threshold | Maintenance Clearance Distance
| (“RCD”) | (“MAT”) | (“MCD”)
12kV - 25kV | 1.5’ | 6’ | 12’-15’
60kV | 1.5’ | 6’ | 12’-15’
120kV | 1.7’ | 15’ | 30-35'

## LU Table 9-4
LU Table 9-4: Hazard Tree Attributes
Hazard Tree Attributes
Basal wound
Bleeding or resinous
Bulges and/or swellings
Cankers, including bleeding & gall rust
Cavities
Codominant or multiple stems from base or higher on trunk
Conks indicating heart rot, root rot, sap rot or canker rot
Cracks including shear
Dead branches and/or top
Dieback of twigs and/or branches
Embedded wires or cables
Excessive lean toward electrical facilities or excessive bow
Fire damage
Foliage – off color, flagging or loss
Hazard beam
History of limb failure(s) on tree
Included bark
Insect activity such as frass from termites, bark beetles or carpenter ants
Lightning damage
Live crown ration below 30%
Mistletoe – dwarf or broad-leaf
Nesting holes – birds, mammals, insects
Past poor pruning practices
Roots injured, exposed, undermined, or uplifted
Seam
Species failure patterns
Unnatural or structurally unsound canopy weight distribution
Weak, unsound branch attachments

## LU Table 9-5
LU Table 9-5: Vegetation Management Site Attributes
Site Attributes
Areas known to be affected by introduced tree pathogens
Areas of recent clearing/new edge
Change in drainage
Change in grade
Construction – including trenching, paving or road construction
Cultural disturbance to landscape – natural or unnatural
Diseased center – dead tree in middle and dying trees around it
High stand density with single species composition
High winds (fire watch)
History of failure(s) at site
History of repeated outages on circuit
Fire damage
Recent thinning or logging
Slope (by grade or percentage)
Soils prone to slides
Specific conditions like high winds
Storm damage

## LU Table 9-6
LU Table 9-6: Vegetation Management LiDAR Inspection Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-7
LU Table 9-7: Vegetation Grow-In Zones, LiDAR Grow-In Analysis
Category | 12kV - 25kV | 60kV | 120kV
Grow-In Zone 1 | 0 - 1.5 feet | 0 - 1.5 feet | 0 - 4 feet
Grow-In Zone 2 | 1.5 – 4 feet | 1.5 – 4 feet | 4 - 10 feet
Grow-In Zone 3 | 4 – 6 feet | 4 – 6 feet | 10 - 15 feet
Grow-In Zone 4 | 6 – 12 feet | 6 – 12 feet | 15 - 30 feet

## LU Table 9-8
LU Table 9‑8: Vegetation Fall-In Zone Categories, LiDAR Fall-In Analysis
Zone Category | Criteria
Fall-In Zone 1 | Overstrike over 6 feet
Fall-In Zone 2 | Strike/overstrike less than 6 feet
Fall-In Zone 3 | Fall within 6 feet of wire

## LU Table 9-9
LU Table 9-9: Vegetation Management Pruning and Removal Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-08
Post Work Verification Procedure (VM-04) | Process | 2 | 2025-02-28
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | Process | 1 | 2024-01-01

## LU Table 9-10
LU Table 9-10: Vegetation Management Pole Clearing Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Post Work Verification Procedure (VM-04) | Process | 2 | 2025-02-28
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | Process | 1 | 2024-01-01
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-11
LU Table 9-11: Vegetation Management Wood and Slash Management Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Post Work Verification Procedure (VM-04) | Process | 2 | 2025-02-28

## LU Table 9-12
LU Table 9‑12: Vegetation Management Defensible Space Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-13
LU Table 9-13: Vegetation Management IVM Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-08
Post Work Verification Procedure (VM-04) | Process | 2 | 2025-02-28
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | Process | 1 | 2024-01-01
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## Table 9-4
Table 9‑4: Liberty Partnerships in Vegetation Management
Partnering Agency/Org. | Activities | Objectives | Liberty Role | Anticipated Accomplishments
National Forest Foundation and Lake Tahoe Basin Management Unit | Implementation of the Forest Resilience Corridor Project on National Forest Land adjacent to Liberty electrical infrastructure. | Forest Resiliency Corridors, Fire Resilient ROWs | Liberty provides funding and in-kind contributions for project work. Liberty is a key stakeholder and involved in the planning and implementation process. | 1,138 acres along 28 miles of overhead powerlines on National Forest Land treated.
Arbor Day Foundation | Coordinate Tree Replacement Program in Liberty’s service territory | Tree Replacement Program | Client | 5,000 compatible plants distributed since the project began in 2022. Maintain Tree Line USA recognition.
Truckee Meadows Fire Protection District | Mastication, chipping, fuels removal, pole grubbing, fire standby, community outreach | Fuel Management, Asset Protection | Client | Implement fuel reduction projects and provide fire standby services to exempt PAL or other restricted operations during fire season.
Truckee Fire Protection District | Fuel management, forest thinning, community outreach. | Fuel reduction and wildfire mitigation work in Truckee Fire Protection jurisdiction and Liberty service area overlap. | Liberty develops specifications and implements fuels and thinning work around powerlines within Truckee Fire Protection District project footprints. Liberty has participated in joint utility and fire agency collaboration and ordinance review as a result of this partnership. | Continue collaboration on additional joint projects in the Truckee area.
Local Fire, Forestry, Resource Conservation, and Special Interest Groups | Coordination of fuels reduction and wildfire mitigation efforts; knowledge sharing | Wildfire risk reduction. | Participates in weekly meetings with representatives from agencies and organizations invested in wildfire mitigation efforts in the Tahoe Basin. Liberty may implement work based on feedback or to meet mutual objectives of stakeholders. | Leverage opportunities to implement joint projects aimed at mitigating wildfire risk.

## LU Table 9-14
LU Table 9-14: Vegetation Management Procedures for Activities Based on Weather Conditions
Document Name and ID | Version | Effective Date
Hazard Tree Management Plan (VM-03) | 1 | 2021-04-08
Vegetation Threat Procedure (VM-05) | 2 | 2022-06-03
Fire Prevention Plan | 1 | 2020-10-09

## LU Table 9-15
LU Table 9-15: Procedures for Post-Fire Restoration
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-08
Post Work Verification Procedure (VM-04) | Process | 2 | 2025-02-28
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## Table 9-5
Table 9‑5: Vegetation Management QA and QC Program Objectives
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Completed Tree Work | WMP-VM-VFM-05 | QC | To provide reasonable assurance that Tree Work is being completed as prescribed and in compliance with applicable regulations
Detailed Inspections | WMP-VM-INSP-01 | QC | To provide reasonable assurance that Detailed Inspections are being performed as scheduled
Hazard Tree Work | WMP-VM-VFM-06 | QC | To provide reasonable assurance that Hazard Tree Work is being completed as prescribed and in compliance with applicable regulations
Pole Clearing | WMP-VM-VFM-01 | QC | To provide reasonable assurance that Pole Clearing Work is being completed as prescribed and in compliance with applicable regulations
Compliance with minimum clearance requirements | WMP-VM-VFM-01 | Compliance Audit | To provide reasonable assurance that minimum clearance requirements are being maintained

## Table 9-6
Table 9-6: Vegetation Management QA and QC Activity Targets
Initiative/ Activity Being Audited | Population /Sample Unit | 2026 Population Size | 2026 Sample Size | 2026 % of Sample in HFTD | 2027 Population Size | 2027 Sample Size | 2027 % of Sample in HFTD | 2028: Population Size | 2028 Sample Size | 2028 % of Sample in HFTD | Confidence level / MOE | 2026 Pass Rate Target | 2027 Pass Rate Target | 2028 Pass Rate Target
Completed Tree Work | Annual Circuit Miles | 700 Miles | 228 Miles | 100% | 700 Miles | 228 Miles | 100% | 700 Miles | 228 Miles | 100% | 99/7 | 95% | 95% | 95%
Detailed Inspections | Annual Circuit Miles | 233 Miles | 76 Miles | 100% | 233 Miles | 76 Miles | 100% | 233 Miles | 76 Miles | 100% | 99/7 [1] | 95% | 95% | 95%
Hazard Tree Work | Annual Hazard Trees | 6,000 Trees | 597 Trees | 100% | 6,000 Trees | 597 Trees | 100% | 6,000 Trees | 597 Trees | 100% | 99/5 | 95% | 95% | 95%
Pole Clearing | Annual Poles | 4,900 Poles | 584 Poles | 100% | 4,900 Poles | 584 Poles | 100% | 4,900 Poles | 584 Poles | 100% | 99/5 | 92% | 92% | 92%
Compliance Audit | Circuit Miles | 700 Miles | 40 Miles | 100% | 700 Miles | 40 Miles | 100% | 700 Miles | 40 Miles | 100% | 95/3 | 99% | 99% | 99%
[1] Due to the small number of units in this category, the sample size was based on the 3-year plan. 700 miles over the 3-year period (233 miles per year) at a CL of 99 and MoE of 7 results in 228 miles during that 3-year period or 76 miles annually

## LU Table 9-16
LU Table 9-16: Vegetation Management QA/QC Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-08
Post Work Verification Procedure (VM-04) | Process | 2 | 2025-02-28
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-17
LU Table 9-17: Vegetation Management QA/QC Sample Size
Work Type | Category | Annual Circuit Miles | Annual Hazard Trees | Annual Poles | Statistical Sampling
[5 empty] | CL/MoE | % | Units
Completed Tree Work | Transmission and Distribution | 700 | - | - | 99/7 | 33 | 228 Miles
Detailed Inspections | Transmission and Distribution | 233 | - | - | 99/7 [1] | 33 | 76 Miles
Hazard Tree Work | Transmission and Distribution | - | 6000 | - | 99/5 | 10 | 597 Trees
Pole Clearing | Transmission and Distribution | - | - | 4900 | 99/5 | 12 | 584 Poles
Compliance Audit | Transmission and Distribution | 700 | - | - | 95/3 [2] | 6 | 40 miles
[1] Due to the small number of units, in this category, the sample size was based on the 3-year plan. 700 miles over the 3-year period (233 miles per year) at a CL of 99 and MoE of 7 results in 228 miles during that 3-year period or 76 miles annually.
[2] The sample size selection methodology for the Compliance Audit varies from the sample size selection methodology for QC inspections. A 95% CL, 3% MoE, and 99% Std Dev (historical rate of compliance) was used for the Compliance Audit.

## LU Table 9-18
LU Table 9-18: Pass Rate Sample Units
Work Type | Category | Sample Unit
Completed Tree Work | Transmission and Distribution | Single Tree
Detailed Inspections | Transmission and Distribution | Single Tree
Hazard Tree Work | Transmission and Distribution | Single Tree
Pole Clearing | Transmission and Distribution | Single Pole

## LU Table 9-19
LU Table 9-19: Completed Tree Work Criteria
Conditions Evaluated | Category
Work Performed as Prescribed | Pass / Fail
Maintenance Clearance Distance Achieved | Pass / Fail
Will Hold Until Next Inspection | Pass / Fail
Potential Hazard Remains | Pass / Fail
Site Clean | Pass / Fail
ANSI Pruning Applied | Pass / Fail
Other Trees Affected | Pass / Fail
Site Condition Stable | Pass / Fail

## LU Table 9-20
LU Table 9-20: VM Detailed Inspections Criteria
Conditions Evaluated | Category
Location Information Correct | Pass / Fail
Species Correct | Pass / Fail
Quantity Correct | Pass / Fail
Work Type Noted | Pass / Fail
Tree Health Noted | Pass / Fail
Priority Noted | Pass / Fail
Project Type Noted | Pass / Fail
Clean Up Method Noted | Pass / Fail
Quantity of Non-Listed Trees | Pass / Fail

## LU Table 9-21
LU Table 9-21: Hazard Tree Work Criteria
Conditions Evaluated | Category
Work Performed as Prescribed | Pass / Fail
Potential Hazard Remains | Pass / Fail
Site Clean | Pass / Fail
Other Trees Affected | Pass / Fail
Site Condition Stable | Pass / Fail

## LU Table 9-22
LU Table 9-22: Pole Clearing Criteria
Conditions Evaluated | Category
Location Information Correct | Pass / Fail
Subject Pole | Pass / Fail
Pole Clearing Tag | Pass / Fail
PRC 4292 Radial Clearance | Pass / Fail
PRC 4292 Vertical Clearance 0-8ft | Pass / Fail
PRC 4292 Vertical Clearance >8ft | Pass / Fail
ANSI Pruning Applied | Pass / Fail
Site Clean | Pass / Fail

## Table 9-7
Table 9‑7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 0 | 0 | 0 | 0
HFTD Tier 2 | 0 | 0 | 0 | 0
HFTD Tier 3 | 0 | 0 | 0 | 0

## Table 9-8
Table 9‑8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 0 | 0 | 0 | 0
Priority 3 | 0 | 0 | 0 | 0

## Table 9-9
Table 9‑9: Vegetation Management Qualifications and Training
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | # of Electrical Corporation | # of Electrical Corporation | # of Contracted Employees with Min Quals | # of Contracted Employees with Applicable Certifications | Total # of Employees | Reference to Electrical Corporation Training/Qualification Programs
|  |  | Employees with Min Quals | Employees with
Applicable Certifications
Supervisor, Vegetation Management | Five years’ experience in utility arboriculture; Bachelor's degree or equivalent | ISA Certified Arborist or Registered Professional Forester, ISA Utility Specialist | 1 | 1 | 0 | 0 | 1 | No formal training program required for this position.
System Arborist/Forester | Three years’ experience in utility arboriculture; Bachelor’s degree or equivalent | ISA Certified Arborist or Registered Professional Forester, ISA Utility Specialist | 4 | 4 | 0 | 0 | 4 | No formal training program required for this position.
Supervisor, Utility Forester | Three years’ experience in utility arboriculture | ISA Certified Arborist or Registered Professional Forester | 0 | 0 | 1 | 1 | 1 | No formal training program required for this position.
Utility Forester I | Less than one year experience in utility arboriculture | None | 0 | 0 | 0 | 0 | 0 | No formal training program required for this position.
Utility Forester II | One year experience in utility arboriculture | None | 0 | 0 | 0 | 0 | 0 | No formal training program required for this position.
Utility Forester III | Two years' experience in utility arboricultural | ISA Certified Arborist or Registered Professional Forester | 0 | 0 | 1 | 0 | 1 | No formal training program required for this position.
Utility Forester IV | Three years’ experience in utility arboriculture | ISA Certified Arborist or Registered Professional Forester | 0 | 0 | 0 | 0 | 0 | No formal training program required for this position.
Utility Forester V | Five years’ experience in utility arboriculture | ISA Certified Arborist, ISA Certified Utility Specialist or Registered Professional Forester | 0 | 0 | 5 | 5 | 5 | No formal training program required for this position.
Vegetation Coordinator | One year experience in utility arboriculture | None | 0 | 0 | 1 | 0 | 1 | No formal training program required for this position.
Tree Crew Supervisor | 18 months experience as Line Clearance Certified Tree Worker | ISA Certified Arborist, EHAP, CPR + First Aid, OSHA 10, OSHA 30, CTSP | 0 | 0 | 5 | 2 ISA Certified Arborist, 5 EHAP, CPR + First Aid; 1 OSHA 10, OSHA 30, CTSP | 5 | No formal training program required for this position.
Line Clearance Certified Tree Worker | 18 months experience as Apprentice Line Clearance Certified Tree Worker | EHAP, CPR + First Aid, OSHA 10, OSHA 30, OSHA 40 | 0 | 0 | 12 | 12 EHAP, CPR + First Aid; 2 OSHA 10; 1 OSHA 30, OSHA 40 | 12 | No formal training program required for this position.
Apprentice Line Clearance Certified Tree Worker | Two years’ experience as a Groundperson | EHAP, CPR + First Aid, OSHA 10, CTSP | 0 | 0 | 11 | 11 EHAP, CPR + First Aid; 1 OSHA 10; 1 CTSP | 11 | No formal training program required for this position.
Equipment Operator | Commercial Driver’s License | EHAP, CPR + First Aid | 0 | 0 | 2 | 2 | 2 | No formal training program required for this position.
Groundperson/Flagger | Related training and on the job experience | EHAP, CPR + First Aid | 0 | 0 | 15 | 15 | 15 | No formal training program required for this position.

## LU Table 9-23
LU Table 9-23: Liberty VM Credentials or Certifications
Credential or Certification Type | Liberty Internal VM Full-Time Employees with Credentials
| Number | Percentage
ISA Certified Arborist | 6 | 86%
ISA Tree Risk Assessment Qualification | 5 | 71%
ISA Certified Utility Specialist | 6 | 86%
ISA Board Certified Master Arborist | 1 | 14%
ISA Prescription Pruning Qualification | 1 | 14%
Certified Tree Safety Professional | 1 | 14%
Utility Vegetation Management Professional Certificate | 1 | 14%
PMI Project Management Professional | 1 | 14%

## Table 10-1
Table 10‑1: Situational Awareness WMP Initiative Targets
WMP Initiative Category | Initiative | Activity (Tracking ID #) | Quantitative or Qualitative Target | Target Unit | 2026 End of Year Total / Completion Date | % Risk Reduction for 2026 | 2027 Total / Status | % Risk Reduction for 2027 | 2028 Total / Status | % Risk Reduction for 2028 | Three- Year Total | Section; Page Number
Situational Awareness and Forecasting | Environmental monitoring systems | Fuel Moisture Sampling (WMP-SA-01) | Quantitative | Fuel sampling locations monitored | 5 | Not calculated | 5 | Not calculated | 5 | Not calculated | 15 | 10.2.1; pp.216-220
Situational Awareness and Forecasting | Environmental monitoring systems | Fuel Moisture Sampling (WMP-SA-01) | Qualitative | Use field collected fuel moisture samples to supplement automated ERC percentiles | Complete December 31, 2026 | Not calculated | Complete December 31, 2027 | Not calculated | Complete December 31, 2028 | Not calculated | Complete | 10.2.1; pp.216-220
Situational Awareness and Forecasting | Grid monitoring systems | WMP-SA-02 | Quantitative | Fault Indicators Installed | Complete December 31, 2025 | Not calculated | Complete | Not calculated | Complete | Not calculated | Complete | 10.3.1; pp. 223-225
Situational Awareness and Forecasting | Grid monitoring systems | WMP-SA-02 | Qualitative | Sensitive Earth Fault (SEF) protection module study | Complete December 31, 2026 | Not calculated | Complete | Not calculated | Complete | Not calculated | Complete | ACI: LU-25U-08
Situational Awareness and Forecasting | Ignition Detection Systems | WMP-SA-03 | Quantitative | Wildfire Cameras Sponsored | 8 | Not calculated | 8 | Not calculated | 8 | Not calculated | 24 | 10.4.1; pp. 227-229
Situational Awareness and Forecasting | Ignition Detection Systems | WMP-SA-03 | Qualitative | Finalize Agreement with UNR for wildfire camera sponsorship | Complete December 31, 2025 | Not calculated | Complete | Not calculated | Complete | Not calculated | Complete | 10.4.1; pp. 227-229
Situational Awareness and Forecasting | Weather forecasting | WMP-SA-04 | Quantitative | Percent of weather stations in service | 80% | Not calculated | 80% | Not calculated | 80% | Not calculated | 80% | 10.2.1; pp.216-220
10.5.5; pp. 233-234
Situational Awareness and Forecasting | Weather forecasting | WMP-SA-04 | Quantitative | Percent of weather stations in service | Complete December 31, 2026 | Not calculated | Complete December 31, 2027 | Not calculated | Complete December 31, 2028 | Not calculated | Complete | 10.5.1; pp. 230-232
Situational Awareness and Forecasting | Weather Station Maintenance and Calibration | Weather Station Inspections (WMP-SA-01) | Quantitative | Weather Stations Inspected | 39 | Not calculated | 39 | Not calculated | 39 | Not calculated | 117 | 10.5.5; pp. 233-234
Situational Awareness and Forecasting | Weather Station Maintenance and Calibration | Weather Station Health (WMP-SA-01) | Qualitative | Conduct necessary repairs and updates to maintain weather station network health | Complete December 31, 2026 | Not calculated | Complete December 31, 2027 | Not calculated | Complete December 31, 2028 | Not calculated | Complete | 10.5.5; pp. 233-234

## Table 10-2
Table 10‑2: Liberty Environmental Monitoring Systems
System | Measurement/ Observation | Frequency | Purpose and Integration
Weather stations | • Temperature (°F) | 6 observations per hour | • Improve weather forecasts with observed weather station data
| • Dew Point (%) |  | • Configure alerts
| • Wind Speed (mph) |  | • Generate reports
• Wind Direction
• Wind Gust (mph)
• Wind Gust Direction
• Latest Rain (inches)
• Fuel Moisture (%)
• Soil Moisture (%)
• Soil Temperature (°F)
Remote sensing fuel moisture | • Fuel Moisture (%) | 6 observations per hour | • Calculate fuel moisture content
Remote sensing soil moisture | • Soil Moisture (%) | 6 observations per hour | • Calculate soil moisture content
Fuel moisture field sampling | • Live woody (%) | 1 per week | • Calculate Energy Release Component
| • 1,000 hour (%) |  | • Fire behavior calculations
• Live fuel moisture by predominant species

## Table 10-3
Table 10‑3: Liberty Grid Monitoring Systems
System | Measurement/ Observation | Frequency | Purpose and Integration
Fault indicators | Line tripped or Line not tripped | Varies based on trip events | Expedite response and location of tripped lines
Recloser Controllers | Real-time SCADA data, fault event data, SER data | Continuous | Provide real-time visibility into recloser operations, fault detection, and event logging. Majority integrated with SCADA for system-wide situational awareness and control.
Substation Protective Relays | SCADA data, fault event records, Sequence of Events (“SER”) logs | Continuous | Enable monitoring and diagnostics of substation events. Relay-triggered events automatically notify engineers via ArcSELerator TEAM. Supports root cause analysis and corrective action planning.

## Table 10-4
Table 10‑4: Fire Detection Systems Currently Deployed
Detection System | Capabilities | Companion Technologies | Contribution to Fire Detection and Confirmation
Video Cameras (ALERTWest) | AI wildfire detection | None | Confirmed detections will generate alerts to assist in quicker response and suppression times.
Fire growth potential software (PyreCast) | Forecasts for active fires, risk, and fire weather | Satellite-based heat detection, weather models, weather station data | By combining satellite-based detection, predictive modeling, and weather forecast integration, PyreCast offers a comprehensive tool for fire detection and confirmation, enhancing wildfire situational awareness and response strategies.
Fire growth potential software (Technosylva Wildfire Analyst) | Wildfire spread predictions | FireRisk, FireSight | The ability to simulate fire spread under forecast weather conditions helps identify areas at greatest risk, supporting proactive planning and mitigation efforts.

## Table 10-5
Table 10 5: Fire Potential Features
Feature Group | Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
Weather | Wind force | Surface | Wind gust force at surface | High Resolution Rapid Refresh (HRRR) Model | 4 times per day | 3 km | Hourly
Weather | Wind force | Surface | Wind gust force at surface | North American Mesoscale Model (NAM) Weather Model | 4 times per day | 3 km | Hourly
Weather | Wind force | Surface | Wind gust force at surface | Global Forecast System (GFS) Weather Model | 4 times per day | 13 km | 3 hours
Weather | Wind force | Surface | Wind gust force at surface | European Center for Medium Range Weather Forecasts (ECMWF) Weather Model | 4 times per day | 14 km | 12 hours
Weather | Wind speed | Surface | 3 second wind gust speed at surface | High Resolution Rapid Refresh (HRRR) Weather Model | 4 times per day | 3 km | Hourly
Weather | Wind speed | Surface | 3 second wind gust speed at surface | North American Mesoscale Model (NAM) Weather Model | 4 times per day | 3 km | Hourly
Weather | Wind speed | Surface | 3 second wind gust speed at surface | Global Forecast System (GFS) Weather Model | 4 times per day | 13 km | 3 Hours
Weather | Wind speed | Surface | 3 second wind gust speed at surface | European Center for Medium Range Weather Forecasts (ECMWF) Weather Model | 4 times per day | 14 km | 12 Hours
Fuel | Head fire flame length | Surface | Operational fire spread model used to calculate length | Eularian Level set Model of Fire Spread (ELMFIRE) | 4 times per day | 30 m | 6 Hours

## Table 11-1
Table 11‑1: Emergency Preparedness and Community Outreach Targets by Year
WMP Initiative Category | WMP Initiative | Activity (Tracking ID#) | 2026 End of Year Total / Completion Date | 2027 Status | 2028 Status | Section; Page Number
Emergency Preparedness | Collaboration and coordination with public safety partners (“PSPs”) | WMP-EP-02 | Conduct emergency drills; continue engagement with local stakeholders and PSPs to prepare for and respond to fire-related event; meet with Community Advisory Boards. | Conduct emergency drills; continue engagement with local stakeholders and PSPs to prepare for and respond to fire-related event; meet with Community Advisory Boards | Conduct emergency drills; continue engagement with local stakeholders and PSPs to prepare for and respond to fire-related event; meet with Community Advisory Boards | 11.3.1; pp. 254-257
Emergency Preparedness | Customer support in wildfire and PSPS emergencies | WMP-EP-05 | Conduct Incident Command Training for all identified IC members and hold a PSPS Tabletop exercise; continue implementation of Liberty’s AFN Plan; continue maintenance of emergency response plans; enhance documentation and use of lessons learned to update plans. | Conduct Incident Command Training for all identified IC members and hold a PSPS Tabletop exercise; continue implementation of Liberty’s AFN Plan; continue maintenance of emergency response plans; enhance documentation and use of lessons learned to update plans. | Conduct Incident Command Training for all identified IC members and hold a PSPS Tabletop exercise; continue implementation of Liberty’s AFN Plan; continue maintenance of emergency response plans; enhance documentation and use of lessons learned to update plans. | 11.5; pp. 282-284
Emergency Preparedness | Learning after wildfire and PSPS events | WMP-EP-06 | After action reports for each event | After action reports for each event | After action reports for each event | 7; p.105-108
Community Outreach and Engagement | Public outreach and education awareness for wildfires, PSPS, outages from protective equipment and device settings, and vegetation management | WMP-CO-01 | Two wildfire and PSPS outreach surveys | Two wildfire and PSPS outreach surveys | Two wildfire and PSPS outreach surveys | 11.4.3; pp. 272-276
Community Outreach and Engagement | Engagement with AFN populations, local governments, and tribal communities | WMP-CO-03 | 9 Events | 9 Events | 9 Events | 11.4.4; pp.277-279
Community Outreach and Engagement | Engagement with AFN populations, local governments, and tribal communities | WMP-CO-03 | Enhance accessibility based on community feedback and evolve best practices where possible | Enhance accessibility based on community feedback and evolve best practices where possible | Enhance accessibility based on community feedback and evolve best practices where possible | 11.4.4; pp.277-279
Community Outreach and Engagement | Best practice sharing with other electrical corporations | WMP-CO-05 | Participation in working groups (i.e., Risk Modeling Working Group) and Joint IOU Councils (i.e., AFN Collaborative Council) | Participation in working groups (i.e., Risk Modeling Working Group) and Joint IOU Councils (i.e., AFN Collaborative Council) | Participation in working groups (i.e., Risk Modeling Working Group) and Joint IOU Councils (i.e., AFN Collaborative Council) | 5; p. 34 11.3.2; pp. 258-259 11.4.4; pp. 278-279 13.1; pp. 294-295

## Table 11-2
Table 11‑2: Liberty Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan
Gap or Limitation Subject | Remedial Brief Description | Remedial Action Plan
Liberty’s 2024 CEMP lacked detailed descriptions of Incident Management Team Liaison functions. | Manager, Emergency management should work with IMT to update CEMP. | Liberty’s CEMP was updated on 05/06/2025 to include these descriptions.
Liberty’s 2024 CEMP included a description of how its Incident Command System (“ICS”) was organized, but not the Incident Action Planning Process. | Manager, Emergency management should work with IMT to update CEMP. | Liberty’s CEMP was updated on 05/06/2025 to list the steps in the Incident Action Planning Process.

## LU Table 11-1
LU Table 11‑1: Emergency Management Personnel Training
Training Topic | Purpose and Scope | Training Method | Training Frequency | Position or Title of Personnel Required to Take Training | Form of Verification or Reference
Community Resource Center (“CRC”) Response | • Train internal employees in Community Resource Center Lead positions. Training for the process of setting up and supporting Community Resource Center locations in the event of PSPS | Virtual or in-person | Annual | Community Resource Center Lead, CRC Contractor | Training logs
Introduction to the electrical corporation’s emergency preparedness plan | • The contents of emergency response plans, in particular those for wildfire- and PSPS specific incidents | Online course, workshop, or in-person training | Annual | All-staff | Training materials and training logs
• The electrical corporation’s overall safety practices and those specific to wildfire and PSPS incidents
• The organizational structure of how the electrical corporation responds to, manages, and recovers from incidents
• The electrical corporation’s and public safety partners’ roles and responsibilities before, during, and after a wildfire or PSPS incident
• The electrical corporation’s notification and activation protocols for wildfires and PSPS incidents
Emergency response procedures during a wildfire | • Incident Management Team Assignments during a wildfire scenario | Workshop or in-person training | Annually, prior to fire season | Incident Management Team | Training logs
• Wildfire response procedures during Incident
• Immediate Response, 0-2 hours
• Intermediate Response, 2-12 hours
• Extended Response, Greater than 12 hours
• Demobilization/System Recovery
Practices, policies, and procedures for emergency response and service restoration for PSPS events | • Incident Management Team actions for PSPS Stages 1, 2a, 2b, 2c, 3, 4, and 5 as outlined in the PSPS Playbook | TTX and FSX | Annual | Incident Management Team | Training logs
Introduction to the electrical corporation’s mutual aid agreement with aid partner (contractor training) | • Familiarize aid partners with the concepts and actions in the mutual aid operations plan prior to implementation | Online course, workshop, or in-person training | Annual | All potential mutual aid resources | Training materials and training logs
• Allow responding resources the opportunity to practice their procedures and responsibilities
• Scope items include:
o Contents of mutual aid operations plan, in particular those on wildfire- and PSPS-specific incidents
o The electrical corporation’s overall safety practices and those specific to wildfire and PSPS incidents
o The organizational structure and interoperability of how the mutual aid partners and resources collaborate and coordinate
o The electrical corporation’s and public safety partners’ roles and responsibilities before, during, and after a wildfire or PSPS incident
o The electrical corporation’s notification and activation protocols for wildfires and PSPS events

## Table 11-3
Table 11 3: Liberty Communication Protocols, Procedures, and Systems with Public Safety Partners
Public Safety Partner Group | Key Protocols | Frequency of Prearranged Communication Review and Update
City and county officials, fire, law enforcement, and critical infrastructure | Text, email, and/or voice message via OnSolve system; PSP partner portal; exercises; state executive briefings | Annually (April)
CPUC | Email notifications; state executive briefings; PSP portal | Annually (April)
CalOES | OES notification forms; state executive briefings; email communications; PSP portal | Annually (April)

## Table 11-4
Table 11‑4: Gaps and Limitations in Communication Coordination with PSPs
Gap or Limitation Subject | Remedial Brief Description | Remedial Action Plan
During an event, a complete list of Public Safety Partners (“PSPs”) that have been contacted is needed by the Regulatory Liaison in a timely manner to facilitate reporting to regulatory agencies. | A record of PSP contact should be added to Liberty’s in-event tracking spreadsheet for more efficient reporting by the Regulatory Liaison. | Strategy: IMT members will update the in -event tracking spreadsheet to create a section for PSP contact.
Target timeline: Completed
For 2024 events, Liberty’s Customer Solutions team took over responsibility of notification to PSPs, community officials, and key accounts from the PSP Liaison position, which worked well. The PSP Liaison already has multiple duties. | Assign PSP notification officially to Liberty’s Customer Solutions team. | Strategy: Re-assignment of duties.
Target timeline: Completed

## Table 11-5
Table 11‑5: Liberty Collaboration in Local Wildfire Mitigation Planning
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Sierra County Fire Safe and Watershed Council | Home/FireSafe Sierra County (firesafesierracounty.org) | Wildland Urban Interface Project to reduce hazardous fuels upon 65 acres adjacent to Sierraville, CA. | Liberty is a Council stakeholder. Attended meetings: 02/27/2025
Nevada County Quarterly Wildfire Stakeholder Meeting | Fire adapted communities and community archetypes |  | Meets quarterly; Attended meetings: 03/07/2025
Liberty and NV Energy Fire Mitigation/PSPS Collaboration | None | Coordination on PSPS exercises and wildfire mitigation. | Meets monthly; Attended meetings: 05/19/2024
Washoe Tribe | Tribal Government Wildfire Safety | Briefed on the Community Resource Center (CRC) MOU between Liberty Utilities and the Washoe Tribe | Attended meetings: 05/02/2024

## Table 11-6
Table 11‑6: Gaps and Limitations in Collaborating on Local Wildfire Mitigation Planning
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
More timely transport and distribution of repair supplies to the Walker / Coleville area is needed as well. | Repair materials for Walker / Coleville should be pre-staged. | Strategy: Store repair materials in CONEX boxes for more timely repairs.
Target timeline: Completed

## Table 11-7
Table 11‑7: Collaboration with Tribal Agencies
Name of Tribal Agency | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Washoe Tribe | Memorandum of Understanding (“MOU”) | 2024-10-17 | Agreement reached for sue of tribal facility as CRC location.

## Table 11-8
Table 11‑8: Gaps and Limitations in Collaborating with Tribal Agencies
Subject of Gap or Limitation | Description of Gap or Limitation | Strategy for Improvement
The Washoe CRC location is somewhat remote. More affordable options are needed by the logistics team for lunch items at this CRC. | Vendor contracts are needed for acquisition of CRC lunches. | Strategy: Execute new contracts with vendors for food options.
Target timeline: Complete

## Table 11-9
Table 11‑9: Protocols for Emergency Communication to Stakeholder Groups
Stakeholder Group | Event Type | Method(s) for Communicating | Means to Verify Message Receipt
General public | Wildfire | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. This applies to all Liberty constituents to include the General Public, Priority Services, AFN populations, populations with limited English-speaking ability, and tribal populations. | Community Outreach; Public Workshops; Yearly surveys
General public | Wildfire-related outage | Liberty will employ standard communication channels to communicate wildfire-related outages including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. These signs will be critically important to educate tourists in Liberty’s service territory. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt
General public | PSPS-related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. These signs will be critically important to educate tourists in Liberty’s service territory. Liberty has a PSPS Playbook with pre-scripted messages to deliver during all five stages of a PSPS. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt
General public | Restoration of service | Following the event, Liberty focuses on transparency in educating customers and the public on the impact of the event and soliciting customer feedback to improve communication efforts for any future event. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt, After Action Briefings and Reports
Priority essential services | Wildfire | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. These efforts focus on immediate actions that customers and priority essential services can take to remain safe, resilient, and informed during an emergency. | Community Outreach; Public Workshops; Yearly surveys
Priority essential services | Wildfire related outage | During a major outage or emergency that affects a significant number of customers, an email is sent to personnel, agencies, and media to provide information, detail, and status of the outage. As the outage or emergency continues, status update emails and/or phone calls will be made to keep the agencies and media informed. Liberty will also disseminate detailed information on the wildfire including a list and maps of impacted communities, critical facilities, and estimated number of impacted customers and share it with local public safety partners and elected officials via our Public Safety Partner Portal. Public Safety Partners are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
Priority essential services | PSPS-related outage | Liberty will disseminate detailed information on the PSPS event, including a list and maps of impacted communities, critical facilities, and estimated number of impacted customers and share it with local public safety partners and elected officials via our Public Safety Partner Portal. Public Safety Partners are notified via the OnSolve Communication system. | Notification receipt via OnSolve, feedback from public workshops.
Priority essential services | Restoration of service | Once the outage has concluded and the system is back to normal, a final email will be sent to close out the communication of the incident, and Public Safety Partners are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
AFN populations | Wildfire Related outage | Medical Baseline or Green Cross customers who will be affected by the outage will receive a direct phone call from Liberty CalPeco staff notifying them of outage details, including but not limited to time, duration, and reason. Liberty’s goal, whenever possible, is to notify the medical baseline customer group 72 hours in advance of a planned outage. | Notification receipt via OnSolve.
AFN populations | PSPS related outage | Medical Baseline or Green Cross customers who will be affected by the outage will receive a direct phone call from Liberty CalPeco staff notifying them of outage details, including but not limited to time, duration, and reason. Liberty’s goal, whenever possible, is to notify the medical baseline customer group 72 hours in advance of a planned outage. If the customer can’t be contacted via OnSolve a Liberty staff member will knock on the customer’s door and leave a door hanger. | Notification receipt via OnSolve. In person door knock if no OnSolve receipt notification; Door hanger if door not answered.
AFN populations | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Liberty Customers are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
Spanish population with limited English proficiency | Wildfire related outage | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. English and Spanish have been identified as the most prevalent languages used in the Liberty service territory. Customers are notified via the OnSolve Communication system which has the ability to notify in English and Spanish. Liberty Customer Service has staff members and a Community Outreach Coordinator available who are fluent in Spanish. | Customer Service in person communication; Notification receipt via OnSolve.
Spanish population with limited English proficiency | PSPS related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. Customers are notified via the OnSolve Communication system. | Customer Service in person communication; Notification receipt via OnSolve.
Spanish population with limited English proficiency | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Customers are notified via the OnSolve Communication system. | Customer Service in person communication; Notification receipt via OnSolve.
Washoe Tribe | Wildfire related outage | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. Liberty has conducted in person briefings on emergency management at Tribal meetings. | Community Outreach; Public Workshops; Yearly surveys
Washoe Tribe | PSPS related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. Liberty has a PSPS Playbook with pre-scripted messages to deliver during all five stages of a PSPS. Liberty Customers are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
Washoe Tribe | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt; After Action Briefings and Reports
People in remote areas | Wildfire related outage | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. Liberty has made extensive efforts to present on emergency management briefings in the towns of Portola and Loyalton in the north part of the service territory and in Alpine and Mono Counties in the southern portion of the service territory. | Community Outreach; Public Workshops; Yearly surveys
People in remote areas | PSPS related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. Liberty has a PSPS Playbook with pre-scripted messages to deliver during all five stages of a PSPS. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt
People in remote areas | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt; After Action Briefings and Reports

## Table 11-10
Table 11‑10: List of Target Communities for Outreach and Awareness Efforts
Target Community | Interests or Concerns Before, During, and After Wildfire and PSPS events
Identified Access and Functional Needs individuals | Liberty understands customers with access and functional needs may require earlier communication to plan for needs before, during, and after PSPS events and require communication regarding available resources. Liberty values targeted outreach to Access and Functional Needs populations with a focus on PSPS preparedness measures, education around Liberty’s notification system, and importance of updated contact information.
Individuals enrolled in Medical Baseline Allowance Program | Liberty understands customers with medical needs may require earlier communication to plan for medical needs before, during, and after PSPS events and require communication regarding available resources.
Community Based Organizations (“CBOs”) | Liberty understands CBOs require communication regarding PSPS events in order to effectively communicate with and support their communities before, during, and after PSPS events.

## LU Table 11-2
LU Table 11‑2: List of Community Partners
Community Partners | County | City
Sierra Community House | Placer | Kings Beach, CA
Tahoe Truckee Community Foundation | Nevada | Truckee, CA
Placer County Health & Human Services | Placer | Carnelian Bay, CA
Sierra Senior Services | Nevada | Truckee, CA
North Tahoe Truckee Homeless Services | Nevada | Truckee, CA
FREED Independent Living Center | Nevada, Placer, Sierra | Grass Valley, CA
Placer Independent Resource Services (“PIRS”) | Placer, El Dorado, Alpine | Auburn, CA
211 Connecting Point | Nevada, Placer | Grass Valley, CA
Nevada County Health & Human Services | Nevada | Truckee, CA
Portola Family Resource Center | Plumas | Portola, CA
Plumas County Mental Health | Plumas | Portola, CA
Eastern Plumas Healthcare | Plumas | Portola, CA
Partnership HealthPlan of CA | Plumas | Fairfield, CA
Loyalton Senior Citizens of Sierra Co. | Sierra | Loyalton, CA
Sierra County Health and Human Services | Sierra | Loyalton, CA
Sierra County Public Health | Sierra | Loyalton, CA
Loyalton Family Resource Center | Sierra | Loyalton, CA
Boys and Girls Club of Lake Tahoe | El Dorado | South Lake Tahoe, CA
Live Violence Free | El Dorado | South Lake Tahoe, CA
Tahoe Coalition for the Homeless | El Dorado | South Lake Tahoe, CA
El Dorado Health and Human Services | El Dorado | Placerville, CA
First 5 / Community Hub El Dorado | El Dorado | Placerville, CA
South Lake Tahoe Family Resource Center | El Dorado | South Lake Tahoe, CA
Tahoe Youth and Family Services | El Dorado | South Lake Tahoe, CA
Tahoe Magic | El Dorado | South Lake Tahoe, CA
Bread and Broth | El Dorado | South Lake Tahoe, CA
Catalyst Community | El Dorado | South Lake Tahoe, CA
Rolling Start, Inc. Independent Living Center | Mono | San Bernardino, CA
Mono County Health and Human Services | Mono | Coleville, CA
Mono County Public Health | Mono | Mammoth Lakes, CA
Alpine County Health and Human Services | Alpine | Markleeville, CA
Washoe Tribe | Alpine | Markleeville, CA

## LU Table 11-3
LU Table 11‑3: Community Outreach and Education Programs
Core Activity | Event Type | Period of Application (Before, During, After Incident) | Name of Outreach or Education Program | Description of Program | Target Audience
Wildfire Advisory Council Meeting | Virtual | Biennial | Wildfire Advisory Council Meeting | Perform general PSPS and Wildfire Mitigation outreach ahead of fire season. | All customers
Digital, print, and radio advertising | Campaign | All | PSPS and Wildfire Mitigation Awareness Advertising | Campaign occurs from April-October of each year, covering PSPS and Wildfire Mitigation awareness topics. | All customers, medical baseline customers
Advertising in HOA publications and customer emails | Email, social media | Before | None | Perform general PSPS and Wildfire Mitigation outreach ahead of fire season. | All Customers
Manage outreach /awareness webpage | Virtual | All | Liberty PSPS and Wildfire Mitigation awareness webpage | Social media posts, bill inserts, and customer emails help drive traffic to webpage that covers PSPS and wildfire mitigation awareness topics. | All Customers
General Community Outreach Events | In-Person | Before | None | Liberty attendance at community outreach events to spread PSPS awareness and preparedness education, update contact information, and provide education on available customer programs and Liberty notification system. | All customers
Community Based Organization (“CBO”) Meetings | In-Person, Virtual | Before | None | Liberty staff meetings with local CBOs to share PSPS awareness and available materials, preparedness education, customer program updates, and to maintain up to date contract information for CBO facing communities. | CBOs, AFN Customers
Collaborative Community Outreach with CBOs | In-Person | Before | None | Liberty involvement in collaborative outreach events to spread PSPS awareness and preparedness education, update contact information, and provide education on available customer programs and Liberty notification system. This form of outreach leverages CBO relationships within the community to access local communities and supports targeted outreach efforts to reach AFN populations. | All customers, AFN customers, CBOs
Provision of Shelf-Stable Meal Boxes to Senior Nutrition Programs | In-Person | Before | Shelf Stable Meal Box Delivery | Provide preparedness information, customer assistance program information and shelf stable food items to vulnerable seniors. | All customers

## Table 11-11_
Table 11‑11: Gaps and Limitations in Public Emergency Communication Strategy
Gap or Limitation Subject | Remedial Brief Description | Remedial Action Plan
During 2024 PSPS events, some customers were notified as being in scope for events but were not de-energized and did not receive notices of cancellation. | Liberty should update its protocols an in-event tracking spreadsheet to make sure customers that are notified, but not, de-energized receive cancellation notices. | Strategy: Liberty will update its in-event tracker to specifically capture cancellation notifications.
Target Timeline: Completed
2024 PSPS events highlighted the need to update Liberty’s MBL customer contact list, as some members of the list had recently passed away. | Liberty should do an internal review of its MBL customer list. | Target Timeline: Completed

## Table 12-1
Table 12‑1: Enterprise System Targets
WMP Initiative | Activity (Tracking ID#) | 2026 End-of-Year Total / Completion Date | 2027 Total / Status | 2028 Total / Status | Section; Page Number
Enterprise System – Vegetation Management | Vegetation Data Quality Management (WMP-VM-ESG-01) | Started: March 2026 | In Progress | Completed: December 31, 2028 | 12.1.1; pp.285-286
Enterprise System – Asset Management and Inspection | Asset Management Inspection Application Reduction (N/A) | Started: March 2026 | In Progress | Completed: December 31, 2028 | 12.1.1; pp.285-286

## Table 13-1
Table 13‑1: WMP Lessons Learned
ID # | Year of Lesson Learned | Subject | Category and Source of Lesson Learned | Description of Lesson Learned | Proposed WMP Improvement | Timeline for Implementation | Reference
1 | 2023-2024 | Grid Hardening | Feedback from government agencies | Permitting projects with multiple agencies can cause project delays. Delays can be due to lack of resources by permitting agencies to respond to requests within expected timelines and other projects within the same area may create need for additional collaboration. | Work with contractors familiar with permitting agency process & requirements. | Ongoing | 8.2; pp. 115-131
2 | 2024-2025 | Vegetation Management | QA/QC | In the 2023-2025 WMP Liberty determined pass rate targets for all conditions being evaluated in each QC program component. Liberty determined it is more beneficial to assess an overall pass rate for each of its QC program components to evaluate program effectiveness. Liberty still reviews QC failures for each condition being evaluated in each QC program component, however, measures overall work quality by looking at the overall pass rate, an average of all conditions evaluated. | Liberty is updating QC targets as detailed in its 2026-2028 WMP, Section 9.11, Table 9-19 Vegetation Management QA and QC Activity Targets | 2025 | 9.11; pp. 196-205
3 | 2025 | Vegetation Management | Fuel Management | Leverage joint IOU partnerships for potential of shared biomass utilization projects. | Liberty will continue to collaborate with neighboring utilities to explore opportunities for alternative biomass utilization, as well as other industry specific benchmarking. | Ongoing | 9.3-9.7; pp.179-188
4 | 2025 | Vegetation Management | Key Performance Indicators | Liberty identified the need to regularly track and report contractor key performance indicators (KPI) to monitor contractor production metrics. | Liberty developed KPI reporting to set targets to measure production against for its VM contractors. | Completed 2025 | 12; pp. 285-291
5 | 2025 | Vegetation Management | Contractor Safety | Liberty identified opportunities to continue enhancing safety oversite of contractor work. | Liberty has implemented routine safety observations of VM contractors and worked with its primary tree contractor to implement an updated job tailboard form to include a more detailed roping and rigging plan for tree work. | Ongoing | 9; 167-212
6 | 2024 | Grid Design, Operations, and Maintenance | Collaboration efforts with other electrical corporations | NV Energy's new wildfire encroachment policy, if implemented on the 619 line, would lead to loss of power supply to all customers in Portola and Loyalton. | Plumas-Sierra Rural Electrical Cooperative could provide an alternate power supply to Portola and Loyalton. | Completed 2024 | 8; 109-166
7 | 2024 | PSPS | 2024 PSPS Events | Refer to Table 7‑1. | Refer to Table 7‑1. | Ongoing | 7; pp. 107-108
8 | 2020-2024 | Risk Modeling | Risk Modeling Working Group | Liberty has gained a greater understanding of best practices across the CA IOUs regarding the following topics: | Liberty will continue to participate in the Joint IOU Wildfire Risk Modeling Working Group to understand best practices across the California IOUs (i.e., further integration of community vulnerability, improvements to wildfire consequence modeling). | Ongoing | 5; pp. 34-83
• Modeling baselines
• Fire consequence
• Asset risk events and ignitions
• Vegetation risk events and ignitions
• PSPS likelihood
• PSPS consequence and reliability analysis and impacts
• Modeling algorithms, components, and interdependencies
• Smoke and suppression impacts
• Climate change impacts
9 | 2022 | Data tracking | Feedback from stakeholders; outcomes from previous WMP cycles | Liberty was lacking data quality for tracking and reporting WMP initiatives. | Refer to Section 12. | Completed 2024 | 12; pp. 285-291
10 | 2024 | Emergency Preparedness, Collaboration, and Public Awareness | Feedback from government agencies and stakeholders; outcomes from previous WMP cycles. | Liberty was lacking MBL specific door hangers for communication of critical information during PSPS events. | MBL specific letter to be used as part of the PSPS notification process to leave at customers' houses after exhausting other attempts to notify via text, phone, or other means. | Completed 2024 | 11; 240-284
11 | 2024 | Emergency Preparedness, Collaboration, and Public Awareness | Feedback from government agencies and stakeholders | Some customers do not understand why PSPS may occur | Provide additional educational materials to Public Safety Partners for them to share through their community outreach channels. | Completed 2024 | 11; 240-284

## Table 13-2
Table 13‑2: Lessons Learned from Discontinued Activities
Discontinued Activity (Tracking ID) | Rationale for Discontinuation | Lessons Learned | Replacement Activities
Substation Equipment Replacement (WMP-GDOM-GH-12f) | The activity, as previously described, encompassed general substation equipment replacements and upgrades—many of which were not directly tied to wildfire ignition risk. Furthermore, feedback from both internal reviews and Energy Safety emphasized that the initiative lacked clearly defined objectives and measurable outcomes specific to wildfire prevention | 1) Clarity and Risk Relevance Are Essential: Initiative activities must be clearly defined and directly tied to measurable wildfire risk reduction to be meaningful and auditable. 2) Program Discipline: Ongoing feedback loops with Energy Safety and operational teams are critical to ensuring that WMP initiatives remain aligned with their intended purpose and are responsive to actual risk | The underlying work, such as substation inspections and emergency equipment replacements, continues as part of routine utility operations and capital upgrade programs. While the discontinued initiative will no longer be tracked under a separate WMP initiative, risk mitigation previously attributed to this initiative is now supported through the following ongoing activities and WMP initiatives: Substation Inspections (WMP-GDOM-AI-06) and Substation Defensible Space (WMP-VM-VFM-03)