## Tab 1 - Overview tab
IE AIR Attachments
Independent Evaluator: | NV5/Guidehouse
Electrical Corporation: | PacifiCorp
Legends
Tab 1 | Overview Tab - Instructions and overview
Tab 2 | Catalog of Initiatives - Initiative review and funding compliance of all initiatives
Tab 3 | Data Requests - Comprehensive list of documents reviewed
Tab 4 | SME Interviews - Summary of interviews conducted

## Tab 2 - Catalog of Initiatives
Catalog of Initiatives
Independent Evaluator: | NV5/Guidehouse
Electrical Corporation: | PacifiCorp
WMP Category | Initiative Tracking ID | WMP Section Number | Initiative Name | Initiative Type | WMP - Initiative Description | WMP - Initiative Target | EC-Claimed Progress (Q4 QDR) | EC-Claimed Progress (EC AIR) | EC-Claimed Progress | EC-Claimed Initiative Status | Target Not Met - Rationale | Sample Size (#) | Sample Validation Rate (%) | Verification Method | Initiative Validation Rate (%) | IE Finding on Initiative | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%) | Funding discrepancy - finding | Funding discrepancy - detail | Satisfied Risk Reduction Goal - finding | Satisfied Risk Reduction Goal - detail
Grid Design Operations and Maintenance | AI-01 | 8.1.3.1 | Transmission Patrol inspections | Non-focus & non-field verifiable | Transmission Patrol Inspections | 12030 | 12032 | 12032 | 12032 | Target met | N/A | 18 | 100% | Desktop and Financial | 100% | Initiative validated | 87 | 55 | 37% | Underspend | PacifiCorp’s 2025 actual expenditure for AI-01 (Transmission Patrol Inspections) was lower than the planned budget because the cost to complete the inspections in 2025 was less than originally forecast in the 2023–2025 Base WMP. When Transmission Detail Inspections (AI-03) were completed before the scheduled Transmission Patrol Inspections (AI-01) for the same assets, the Patrol Inspections (AI-01) were not performed, avoiding duplicative work and therefore lowering the overall spend on AI-01.
Grid Design Operations and Maintenance | AI-02 | 8.1.3.1 | Distribution Patrol Inspections | Non-focus & non-field verifiable | Distribution Patrol Inspections | 50485 | 58741 | 58741 | 58741 | Target met | N/A | 18 | 100% | Desktop and Financial | 116% | Initiative validated | 268 | 443 | 65% | Overspend | PacifiCorp’s 2025 actual expenditure for AI‑02 (Distribution Patrol Inspections) exceeded the planned budget because the number of required patrol inspections in 2025 was significantly higher than assumed in the 2023–2025 Base WMP. Following a change in the safety assurance frequency to an annual inspection requirement, the total number of overhead distribution safety patrols increased by approximately 8,000 units compared to the original WMP target. This higher inspection volume resulted in actual expenditures above the planned level.
Grid Design Operations and Maintenance | AI-03 | 8.1.3.2 | Transmission Detail Inspections | Focus & non-field verifiable | Transmission Detail Inspections | 540 | 509 | 509 | 509 | Target met | PacifiCorp completed 509 transmission detail inspections in 2025. The remaining locations were identified as retired facility points or misidentified assets that did not meet the criteria for transmission detail inspection. | 64 | 100% | Desktop and Financial | 94% | Initiative not validated | 20 | 48 | 140% | Overspend | PacifiCorp’s 2025 actual expenditure for AI‑03 (Transmission Detail Inspections) exceeded the planned budget because the cost per detailed inspection was higher than assumed in the 2025 WMP Update. Although the number of structures requiring detailed inspection in 2025 was slightly lower than forecast, the unit cost to perform the inspections was greater than anticipated, resulting in total expenditures above the planned level.
Grid Design Operations and Maintenance | AI-04 | 8.1.3.2 | Distribution Detail Inspections | Focus & non-field verifiable | Distribution Detail Inspections | 10135 | 18556 | 18556 | 18556 | Target met | N/A | 73 | 100% | Desktop and Financial | 183% | Initiative validated | 221 | 578 | 162% | Overspend | PacifiCorp’s 2025 actual expenditure for AI‑04 (Distribution Detail Inspections) exceeded the planned budget because the number of required inspections in 2025 was significantly higher than assumed in the 2023–2025 Base WMP. Due to the Tier 2/3 pilot program transitioning from a five-year cycle to a two-year cycle for detail inspections, starting in 2025, the total number of inspections increased by approximately 8,000 above the planned target. This higher inspection volume resulted in actual expenditures above the planned level.
Grid Design Operations and Maintenance | AI-05 | 8.1.3.3 | Transmission Intrusive Pole Inspections | Focus & non-field verifiable | Transmission Intrusive Pole Inspections - Transmission and Distribution | 1257 | 1246 | 1246 | 1246 | Target met | The remaining 11 inspection locations were determined to be either retired facility points or incorrectly labeled in the system and did not meet the criteria for inspection as part of this initiative (e.g., one location was incorrectly noted as overhead when it was underground). PacifiCorp considers this initiative complete for 2025 and does not have any corrective actions for the slight variance. | 69 | 100% | Desktop and Financial | 99% | Initiative validated | 64 | 131 | 105% | Overspend | PacifiCorp’s 2025 actual expenditure for AI‑05 (Transmission Intrusive Pole Inspections) exceeded the planned budget because more transmission poles required intrusive inspection in 2025 than assumed in the 2025 WMP Update. Intrusive inspection volumes vary annually based on the pole inspection cycle and the number of structures scheduled for testing in a given year. The higher inspection volume in 2025 resulted in actual expenditures above the planned level.
Grid Design Operations and Maintenance | AI-06 | 8.1.3.3 | Distribution Intrusive Pole Inspections | Focus & non-field verifiable | Distribution Intrusive Pole Inspections - Transmission and Distribution | 3173 | 3162 | 3162 | 3162 | Target met | The remaining 11 inspection locations were determined to be either retired facility points or incorrectly labeled in the system and did not meet the criteria for inspection as part of this initiative (e.g., one location was incorrectly noted as overhead when it was underground). PacifiCorp considers this initiative complete for 2025 and does not have any corrective actions for the slight variance. | 71 | 100% | Desktop and Financial | 99% | Initiative validated | 175 | 135 | 23% | Underspend | PacifiCorp’s 2025 actual expenditure for AI‑06 (Distribution Intrusive Pole Inspections) was lower than the planned budget because fewer distribution poles required intrusive inspection in 2025 than assumed in the 2025 WMP Update. Intrusive inspection volumes vary annually based on the inspection cycle and the number of poles scheduled for testing in a given year. The lower inspection volume resulted in actual expenditures below the planned level.
Grid Design Operations and Maintenance | AI-07 | 8.1.3.6 | Enhanced (Infrared) Inspections in Transmission Lines | Non-focus & non-field verifiable | Enhanced (Infrared) Inspections in Transmission Lines | 700 | 1567 | 15656 Inspectioms 692 Line-Miles | 1567 | Target met | PacifiCorp completed 15,656 enhanced (infrared) inspections on transmission lines, equating to approximately 692 line miles. Three transmission lines totaling approximately eight line miles were decommissioned in 2024 and could not be inspected as part of the 2025 program. The company used the FPI database to confirm completions and reviewed results against completed work orders. PacifiCorp considers this initiative complete for 2025 and does not have any corrective actions for the slight variance. | 18 | 100% | Desktop and Financial | 224% | Initiative validated | 90 | 87 | 3% | Underspend | N/A
Grid Design Operations and Maintenance | AI-08 | 8.1.3.5 | Enhanced (Infrared) Inspections in Distribution Lines | Non-focus & non-field verifiable | Enhanced (Infrared) Inspections in Distribution Lines | N/A | 1300 | 32286 Inspections 1300 Line-Miles | 1300 | Target met | N/A | 18 | 100% | Desktop and Financial | 100% | Initiative validated | 0 | 218 | N/A | Overspend | PacifiCorp’s 2025 actual expenditure for AI‑08 (Enhanced (Infrared) Inspections in Distribution Lines) exceeded the planned budget because no funding was originally included for 2025 at the time the 2023–2025 Base WMP was filed. The pilot program for enhanced infrared inspections was scoped only for 2023 and 2024, and, as noted in Table 8‑4 of the WMP, any 2025 activity was contingent on the results of the pilot. Following the 2024 inspection season, the pilot was approved to continue into 2025, including expansion into the HFTD. As a result, inspection work proceeded in 2025 even though no dollars had been budgeted for this initiative, leading to actual expenditures above the planned level.
Grid Design Operations and Maintenance | AI-11 | 8.1.3.4 | Substation Inspections | Non-focus & non-field verifiable | Substation Inspections | 451 | 450 | 451 | 450 | Target met | N/A | 18 | 100% | Desktop and Financial | 99.8% | Initiative validated | 180 | 175 | 3% | Underspend | N/A
Grid Design Operations and Maintenance | AI-12 | 8.1.6 | Quality Assurance and Quality Control | Non-focus & non-field verifiable | QA/QC of Asset Inspections | 756 | 1567 | 1887 | 1567 | Target met | N/A | 18 | 100% | Desktop and Financial | 207% | Initiative validated | 36 | 66 | 83% | Overspend | PacifiCorp’s 2025 actual expenditure for AI‑12 (Quality Assurance and Quality Control) exceeded the planned budget because the total number of inspections subject to QA/QC review in 2025 was higher than anticipated in the 2023–2025 Base WMP. QA/QC activity levels are directly driven by the volume of transmission and distribution inspections completed each year, and increased inspection counts resulted in higher QA/QC workload and associated costs, leading to actual expenditures above the planned level.
Community Outreach and Engagement | CO-01 | 8.5.2 | Public Outreach and Education Awareness Program | Non-focus & non-field verifiable | Public Outreach and Education Awareness Program | 60% or more of the sample survey areaware of wildfire safety communications PacifiCorp remains the most mentioned source of communication about wildfire preparedness 1 additional language for the medical certificate | Complete | 1 additional language for the medical certificate 60% or more of the sample survey are aware of wildfire safety communica-tions | 60% or more of the sample survey areaware of wildfire safety communications PacifiCorp remains the most mentioned source of communication about wildfire preparedness 1 additional language for the medical certificate | Target met | N/A | N/A | N/A | Desktop and Financial | N/A | Initiative validated | 110 | 107 | 3% | Underspend | N/A
Community Outreach and Engagement | CO-02 | 8.5.3 | Engagement with access and functional needs populations | Non-focus & non-field verifiable | N/A | Increase outreach to AFN populations | Complete | N/A | Increase outreach to AFN populations | Target met | N/A | N/A | N/A | Desktop and Financial | N/A | Initiative validated | N/A | N/A | N/A |  | N/A
Community Outreach and Engagement | CO-03 | 8.5.4 | Collaboration on local wildfire mitigation planning | Non-focus & non-field verifiable | N/A | Continue partnering with public safety partners in communities throughout California regarding wildfire safety and preparedness and PSPS | Complete | N/A | Continue partnering with public safety partners in communities throughout California regarding wildfire safety and preparedness and PSPS | Target met | N/A | N/A | N/A | Desktop and Financial | N/A | Initiative validated | N/A | N/A | N/A |  | N/A
Emergency Preparedness | EP-01 | 8.4.2 | Emergency preparedness plan | Non-focus & non-field verifiable | N/A | Complete Internal staff Emergency Coordination Center (ECC) and Department Operations Center (DOC) three-year training program | Complete | N/A | Complete Internal staff Emergency Coordination Center (ECC) and Department Operations Center (DOC) three-year training program | Target met | N/A | N/A | N/A | Desktop and Financial | N/A | Initiative validated | 320 | 472 | 48% | Overspend | PacifiCorp’s 2025 actual expenditure for EP‑01 (Emergency Preparedness Plan) exceeded the planned budget due to the expansion of emergency-related work groups supporting wildfire and PSPS preparedness activities. In 2025, PacifiCorp increased staffing and resources across the Wildfire Intelligence Center, Meteorology, Emergency Management, and Emergency Response functions to meet operational and regulatory needs. These organizational changes increased the labor and program costs attributed to this initiative beyond what was assumed in the 2025 WMP Update.
Emergency Preparedness | EP-02 | 8.4.2.3 | External Collaboration and Coordination | Non-focus & non-field verifiable | To enhance awareness of PSPS plan and understanding of roles and responsibilities. | 1 Functional Exercise (FE) 1 Tabletop Exercise (TTX) 1 workshop | Complete | 1 Functional Exercise (FE) 1 Tabletop Exercise (TTX) 1 workshop | 1 Functional Exercise (FE) 1 Tabletop Exercise (TTX) 1 workshop | Target met | N/A | N/A | N/A | Desktop and Financial | N/A | Initiative validated | 10 | 1.3 | 87% | Underspend | PacifiCorp’s 2025 actual expenditure for EP‑02 (External Collaboration and Coordination) was lower than the planned budget because funding requirements for this initiative continued to decline in 2025. As coordination processes and stakeholder engagement activities became more streamlined, fewer resources were needed than assumed in the 2025 WMP Update, resulting in actual expenditures below the planned level.
Emergency Preparedness | EP-03 | 8.4.4.1 | Public emergency communication strategy | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | N/A | N/A | N/A |  | N/A
Emergency Preparedness | EP-05 | 8.4.6 | Customer support in wildfire and PSPS emergencies | Non-focus & non-field verifiable | N/A | Evaluate expansion of the free portable battery and backup electric power rebate programs | Complete | N/A | Evaluate expansion of the free portable battery and backup electric power rebate programs | Target met | N/A | N/A | N/A | Desktop and Financial | N/A | Initiative validated | N/A | N/A | N/A |  | N/A
Grid Design Operations and Maintenance | GH-01 | 8.1.2.1 | Line Rebuild - Covered conductor installation | Focus & field verifiable | Line Rebuild program - Covered Conductor installation. Includes undergrounding | 120 | 123 | 123 | 123 | Target met | N/A | 65 | Desktop - 97% Field - 95.5% | Field, Desktop and Financial | 98.7% | Initiative validated | 120000 | 182258 | 52% | Overspend | PacifiCorp’s 2025 expenditure for GH-01 (Line Rebuild – Covered Conductor Installation) exceeded the budget estimated in the 2025 WMP Update primarily because the cost per mile of installing covered conductor was higher than anticipated due to upgraded agreements with design and construction contractors. Some incremental contract changes included field engineering support, post-construction inspections, and extended warranty. Additionally, PacifiCorp completed additional design scoping in 2025 to have designs and permits in place for 2026 work.
Grid Design Operations and Maintenance | GH-02 | 8.1.2.3 | Distribution Pole Replacement | Focus & field verifiable | Distribution Pole Replacement | 2400 | 2544 | 2544 | 2544 | Target met | N/A | 71 | Desktop - 99% Field - 93% | Field and Desktop | 102% | Initiative validated | N/A | N/A | N/A |  | N/A
Grid Design Operations and Maintenance | GH-03 | 8.1.2.4 | Transmission Pole Replacement | Focus & field verifiable | Transmission Pole Replacement | 240 | 250 | 250 | 250 | Target met | N/A | 57 | 100% | Field and Desktop | 104% | Initiative validated | N/A | N/A | N/A |  | N/A
Grid Design Operations and Maintenance | GH-04 | 8.1.2.8 | Installation of system automation equipment | Focus & field verifiable | Relay/Recloser/Circuit Breaker Replacements / Upgrade | 10 | 23 | 23 | 23 | Target met | N/A | 21 | Desktop - 91% Field - 100% | Field, Desktop and Financial | 220% | Initiative validated | 2500 | 7158 | 186% | Overspend | PacifiCorp’s 2025 expenditure for GH-04 (Installation of System Automation Equipment) exceeded the budget estimated in the 2023–2025 Base WMP for several reasons. The estimated budget was based on the installation of 10 units; however, in accordance with Energy Safety guidance, PacifiCorp completed 23 units, including 13 units not completed in prior years. This resulted in an increase in the overall amount of work completed and associated costs for this initiative. Furthermore, the cost per unit was higher than anticipated due to the engagement of a construction project management company to oversee system hardening projects, as well as higher-than-expected costs associated with extending communications to field devices.
Grid Design Operations and Maintenance | GH-05 | 8.1.2.12 | Expulsion fuse replacement | Focus & field verifiable | Replacement of expulsion fuses | 500 Replace all expulsion fuses within the HFTD and HFRA | 932 | 932 | 932 | Target met | N/A | 68 | Desktop - 90% Field - 90% | Field, Desktop and Financial | 168% | Initiative validated | 1000 | 1455 | 46% | Overspend | PacifiCorp’s 2025 expenditure for GH-05 (Expulsion Fuse Replacement) exceeded the budget estimated in the 2025 WMP Update primarily because the budget was based on 500 fuse replacements, and 932 were completed. GH-05 includes both targeted fuse replacements and fuse replacements performed concurrently with line rebuild work under GH-01. In 2025, the company completed 181 targeted fuse replacements and an additional 751 replacements concurrently with line rebuild work. As outlined in PacifiCorp’s 2025 WMP Update, the company prioritizes the replacement of expulsion fuses in coordination with line rebuild projects whenever practical. Performing fuse replacements during line rebuild activities is an intentional strategy to maximize operational efficiency and minimize overall system costs for customers.
Grid Design Operations and Maintenance | GH-12 | 8.1.2.7 | Microgrids | Non-focus & non-field verifiable | Feasibility Study | Feasibility Study | Complete | N/A | Complete | Target met | N/A | N/A | N/A | Desktop | N/A | Initiative validated | N/A | N/A | N/A |  | N/A
Grid Design Operations and Maintenance | GO-01 | 8.1.8.1 | Equipment Settings to Reduce Wildfire Risk (Grid Ops): EFR and Fault Indicators | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | N/A | N/A | N/A |  | N/A
Grid Design Operations and Maintenance | GO-02 | 8.1.8.3 | Grid Response Procedures and Notifications (Grid Ops): Patrols | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 600 | 152 | 75% | Underspend | PacifiCorp’s 2025 expenditure for GO-02 (Grid Response Procedures and Notifications (Grid Ops): Patrols) was less than the planned 2025 budget due to a change to PacifiCorp’s Wildfire Encroachment System Operations Procedure SOP-203, which resulted in fewer post outage patrols in 2025. This resulted in lower operations and maintenance and less expenditure than planned.
Grid Design Operations and Maintenance | MA-01 | 8.1.4 | Weather Station Maintenance and Repair | Non-focus & non-field verifiable | Weather Station Maintenance and Repair | Continue planned transmission and distribution wires maintenance Continue planned substation apparatus maintenance programs | Complete | N/A | Continue planned transmission and distribution wires maintenance Continue planned substation apparatus maintenance programs | Target met | N/A | N/A | N/A | Desktop and Financial | N/A | Initiative validated | 410 | 399 | 3% | Underspend | N/A
| PS-01 | 9.1.6 | Protocols on PSPS | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 750 | 0 | 100% | Underspend | PacifiCorp’s 2025 actual expenditure for PS‑01 (Protocols on PSPS) was lower than the planned budget because no PSPS events occurred in 2025. In the absence of PSPS events, no related operational activities or associated costs were incurred, resulting in actual expenditures below the planned level.
| RA-01 | 6.2.2 | Risk and Risk Component Calculation | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 155 | 345 | 123% | Overspend | PacifiCorp’s 2025 expenditure for RA‑01 (Risk and Risk Components Calculation) exceeded the planned budget because the Asset Risk Data Science team added four additional full‑time employees to support increasingly complex risk‑modeling requirements. This staffing expansion increased the operations and maintenance hours and associated costs allocated to this initiative, resulting in actual expenditures above the planned level.
| RA-02 | 6.4.1 | Top Risk Areas within the HFRA | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | N/A | N/A | N/A |  | N/A
| RA-03 | 6.4.3 | Other Key Metrics | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 0 | 0 | 0% | No discrepancy | N/A
| RA-04 | 6.5 | Enterprise System for Risk Assessment | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 73 | 701 | 860% | Overspend | PacifiCorp’s 2025 expenditure for RA‑04 (Enterprise System for Risk Assessment) exceeded the planned budget because the original estimate assumed that software costs would be expensed over multiple years rather than capitalized. When the costs were instead capitalized in 2025, a larger portion of the total cost was recognized within the year, resulting in actual expenditures above the planned level.
Situational Awareness and Forecasting | SA-01 | 8.3.2 | Environmental monitoring systems | Non-focus & non-field verifiable | Installation of weather stations | 6 | 8 | 8 | 8 | Target met | N/A | 8 | 100% | Desktop and Financial | 133% | Initiative validated | 120 | 141 | 18% | Overspend | PacifiCorp’s 2025 actual expenditure for SA‑01 (Environmental Monitoring Systems) exceeded the planned budget because the company installed more environmental monitoring stations than originally projected in the 2023–2025 Base WMP. As reflected in the WMP, PacifiCorp adjusts annual installation quantities based on operational needs and situational awareness requirements, and in 2025, additional stations were installed to support wildfire risk monitoring beyond the initial forecast. These added installations resulted in higher costs than the planned budget assumed.
Situational Awareness and Forecasting | SA-02 | 8.3.3.1 | Grid Monitoring Systems | Non-focus & non-field verifiable | Evluate Distribution Fault Anticipation | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 0 | 34 | N/A | Overspend | PacifiCorp’s 2025 actual expenditure for SA‑02 (Grid Monitoring Systems) exceeded the planned budget because the initiative continued to incur communication costs associated with existing distribution fault anticipation (DFA) devices through 2025. Although support‑service costs were no longer included in this initiative beginning in the 2023–2025 Base WMP, cellular communication charges remained necessary to operate the devices until their service contracts expired. These ongoing communication costs resulted in actual expenditures above the planned budget, which assumed no spending for 2025.
Situational Awareness and Forecasting | SA-03 | 8.3.4.1 | Smoke and Air Quality Sensors | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 0 | 0 | 0% | No discrepancy | N/A
Situational Awareness and Forecasting | SA-04 | 8.3.4.1 | High Definition Cameras | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 80 | 80 | 0% | No discrepancy | N/A
Situational Awareness and Forecasting | SA-05 | 8.3.5 | Weather Forecasting | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 670 | 165 | 71% | Underspend | PacifiCorp’s 2025 actual expenditure for SA-05 (Weather Forecasting) was lower than the planned budget due to unanticipated Department of Energy (DOE) grant reimbursements and changes in PacifiCorp’s contract with Technosylva. DOE reimbursements applied to more activities than initially expected, reducing net expenditure for the initiative. In addition, Technosylva’s updated contract structure resulted in certain forecasting and modeling costs being invoiced differently than reflected in the planning forecast, contributing to lower actual spending within SA-05.
Situational Awareness and Forecasting | SA-06 | 8.3.6.1 | Fire Potential Index | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 96 | 996 | 938% | Overspend | PacifiCorp’s 2025 actual expenditure for SA-06 (Fire Potential Index) exceeded the planned budget due to changes in PacifiCorp’s contract with Technosylva and because the weather modeling and forecasting enhancements completed in 2025 were greater in scope than assumed in the Base 2023–2025 WMP. The updated Technosylva contract structure resulted in higher costs than originally anticipated. In addition, PacifiCorp expanded its high-performance computing clusters from two to five units to support both an extension of the Weather Research and Forecasting (WRF) deterministic model from 3.5 to 5 days and implementation of the WRF ensemble system. Building the ensemble model required additional computing capacity to generate nine high-resolution forecasts, which improve the detection of low-probability, high-impact events such as PSPS conditions. These enhancements provide greater advanced situational awareness capabilities than anticipated based on the original 2025 planned spend.
Vegetation Management and Inspections | VM-01 | 8.2.2.1 | Detailed Inspection – Distribution | Non-focus & non-field verifiable | Detailed inspections for vegetation clearances around distribution electric lines. | 826 | 826 | 826 | 826 | Target met | N/A | 18 | 100% | Desktop and Financial | 100% | Initiative validated | 310 | 731 | 136% | Overspend | PacifiCorp’s 2025 actual expenditure for VM‑01 (Detailed Inspection – Distribution) exceeded the planned budget primarily due to an increase in required inspection volume following the establishment of the HFRA. As documented in the 2025 WMP Update, PacifiCorp implemented the FireSight risk model and identified 728 miles of new HFRA territory, which must be inspected to the same standards as CPUC Tier 2 and Tier 3 HFTD areas. This operational change resulted in higher inspection volumes than assumed in the 2023–2025 Base WMP. As a result, the actual 2025 expenditures exceeded the planned budget.
Vegetation Management and Inspections | VM-02 | 8.2.2.2 | Detailed Inspection - Transmission | Non-focus & non-field verifiable | Detailed inspections for vegetation clearances around transmission electric lines. | 270 | 270 | 270 | 270 | Target met | N/A | 17 | 100% | Desktop and Financial | 100% | Initiative validated | 87 | 112 | 29% | Overspend | PacifiCorp’s 2025 actual expenditure for VM‑02 (Detailed Inspection – Transmission) exceeded the planned budget due to expanded inspection requirements resulting from the establishment of the HFRA. As documented in the 2025 WMP Update, PacifiCorp’s implementation of the FireSight risk model identified new HFRA mileage that must be inspected to the same standards as CPUC Tier 2 and Tier 3 HFTD areas, increasing the total inspection scope beyond what was assumed in the 2023–2025 Base WMP.
Vegetation Management and Inspections | VM-03 | 8.2.3.3 | Patrol Inspection - Distribution | Non-focus & non-field verifiable | Patrol (ground) inspections for vegetation clearances around distribution electric lines. | 1182 | 1182 | 1182 | 1182 | Target met | N/A | 18 | 100% | Desktop and Financial | 100% | Initiative validated | 285 | 469 | 65% | Overspend | PacifiCorp’s 2025 actual expenditure for VM‑03 (Patrol Inspection – Distribution) exceeded the planned budget due to an increase in required inspection mileage following the establishment of the HFRA. The implementation of the FireSight risk model identified new HFRA mileage that must be patrolled to the same standards as CPUC Tier 2 and Tier 3 HFTD areas, increasing required patrol coverage beyond the assumptions in the 2023–2025 Base WMP. Additionally, inspection mileage exceeded the forecast, increasing from 922 planned miles to 1,183 miles, driving higher unit costs, further contributing to the variance. As a result, actual 2025 expenditures were higher than planned.
Vegetation Management and Inspections | VM-04 | 8.2.2.4 | Patrol Inspection - Transmission | Non-focus & non-field verifiable | Patrol (ground) inspections for vegetation clearances around transmission electric lines. | 417 | 417 | 417 | 417 | Target met | N/A | 18 | 100% | Desktop and Financial | 100% | Initiative validated | 102 | 84 | 18% | Underspend | “PacifiCorp’s 2025 actual expenditure for VM‑04 (Patrol Inspection – Transmission) differed from the planned budget due to changes in inspection mileage requirements following the establishment of the HFRA. As reflected in the 2025 WMP Update, the implementation of the FireSight risk model identified additional HFRA transmission mileage that must be patrolled annually using the same standards as CPUC Tier 2 and Tier 3 HFTD areas, expanding the scope of required work beyond the assumptions in the 2023–2025 Base WMP. In practice, inspection volume increased from an expected 329-line miles to 417-line miles, reflecting an increase in required coverage. While the cost per mile decreased due to efficiencies in execution, the total inspection requirement exceeded the originally planned volumes, contributing to the variance from budget assumptions.
Vegetation Management and Inspections | VM-05 | 8.2.3.1.2 | Fuels management – Pole clearing beyond PRC 4292 | Focus & field verifiable | Pole clearing beyond PRC 4292 | 3126 | 3126 | 3126 | 3126 | Target met | N/A | 184 | Desktop - 100% Field - 85% | Field, Desktop and Financial | 89.9% | Initiative not validated | 530 | 731 | 38% | Overspend | PacifiCorp’s 2025 actual expenditure for VM‑05 (Pole Clearing) exceeded the planned budget due to increased clearing requirements following the establishment of the HFRA. As described in the 2025 WMP Update, the FireSight risk model identified substantial new HFRA acreage that must be managed to the same standards as CPUC Tier 2 and Tier 3 HFTD areas, expanding the total number of poles requiring clearing relative to the assumptions used in the 2023–2025 Base WMP. This expansion required pole clearing across a greater number of miles than originally forecast. Actual 2025 workload increased from an expected 3,014 miles to 3,192 miles, and the cost-pe-mile also increased, contributing to higher-than-planned expenditures.
Vegetation Management and Inspections | VM-06 | 8.2.2.2 | Clearance - Distribution | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 12770 | 13467 | 5% | Overspend | N/A
Vegetation Management and Inspections | VM-07 | 8.2.2.2 | Clearance - Transmission | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 2520 | 2724 | 8% | Overspend | N/A
Vegetation Management and Inspections | VM-08 | 8.2.3.3 | Fall-in Mitigation | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 40 | 0 | 100% | Underspend | PacifiCorp’s 2025 actual expenditure for VM‑08 (Fall‑in Mitigation) was lower than planned because the underlying fieldwork associated with the Enhanced Overhang Reduction pilot was discontinued prior to the start of the 2025 implementation period. Although funding was carried forward into 2025 in case additional fieldwork verification was required, no field activities were needed and the remaining evaluation consisted only of desktop review and internal discussions. As a result, no fieldwork occurred and no expenditures were incurred under this initiative in 2025.
Vegetation Management and Inspections | VM-11 | 8.2.5 | QA/QC - Post-Audits Distribution (Patrol) | Focus & non-field verifiable | Patrol post-audits on distribution electric lines | 1182 | 1182 | 1182 | 1182 | Target met | N/A | 124 | 100% | Desktop and Financial | 100% | Initiative validated | 165 | 223 | 35% | Overspend | PacifiCorp’s 2025 actual expenditure for VM‑11 (Quality Assurance/ Quality Control) exceeded the planned budget due to an increase in required QA/QC activities associated with expanded inspection scope in the HFRA. Following implementation of the FireSight risk model, the 2025 WMP Update established new HFRA territory that must be inspected and audited to the same standards as CPUC Tier 2 and Tier 3 HFTD areas, which increased the volume of vegetation inspections subject to QA/QC review. As a result, higher audit volumes and more extensive verification requirements led to increased costs beyond what was originally forecast for 2025.
Vegetation Management and Inspections | VM-11 | 8.2.5 | QA/QC - Post-Audits Transmission (Patrol) | Focus & non-field verifiable | Patrol post-audits on transmission electric lines | 417 | 417 | 417 | 417 | Target met | N/A | 62 | 100% | Desktop and Financial | 100% | Initiative validated | 165 | 223 | 135% | Overspend | PacifiCorp’s 2025 actual expenditure for VM‑11 (Quality Assurance/ Quality Control) exceeded the planned budget due to an increase in required QA/QC activities associated with expanded inspection scope in the HFRA. Following implementation of the FireSight risk model, the 2025 WMP Update established new HFRA territory that must be inspected and audited to the same standards as CPUC Tier 2 and Tier 3 HFTD areas, which increased the volume of vegetation inspections subject to QA/QC review. As a result, higher audit volumes and more extensive verification requirements led to increased costs beyond what was originally forecast for 2025.
| WP-01 | 7.1.2 | Wildfire Mitigation Strategy Development | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 845 | 980 | 16% | Overspend | PacifiCorp’s 2025 actual expenditure for WP‑01 (Wildfire Mitigation Strategy Development) exceeded the planned budget due to organizational changes in wildfire mitigation planning. During 2025, PacifiCorp reorganized staff supporting wildfire mitigation strategy development and adjusted how planning-related costs were allocated across the company’s service territories. These changes resulted in a greater share of wildfire mitigation planning costs attributed to this initiative than was assumed in the 2025 WMP Update used to establish the planned budget.
| WP-02 | 7.1.4.1 | Identifying and Evaluating Mitigation Initiatives | Non-focus & non-field verifiable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Desktop and Financial | N/A | N/A | 280 | 18 | 94% | Underspend | PacifiCorp’s 2025 actual expenditure for WP‑02 (Identifying and Evaluating Mitigation Initiatives) was lower than the planned budget because spending on the drone pilot program in 2025 was less than anticipated in the 2025 WMP Update. As a result, actual costs attributed to this initiative were below the planned level.
Note on K11: Number of "actuals" from which samples are selected

## Tab 3 - Data Requests
Data Requests
Independent Evaluator: | NV5/Guidehouse
Electrical Corporation: | PacifiCorp
Date Sent | Date Response Received | Section / Initiative | Data Request Number | List of Documents Received
2026-02-09 | 2026-02-12 | N/A | DR1 | PC_2025_Q1_R0.xlsx, PC_2025_Q2_R0.xlsx, PC_2025_Q3_R0.xlsx, PC_2025_Q4_R0.xlsx
2026-02-09 | 2026-02-12 | N/A | DR1 | PC_2025_Q1_SpatialDataStatusReport.xlsx, PC_2025_Q2_SpatialDataStatusReport.xlsx, PC_2025_Q3_SpatialDataStatusReport.xlsx, PC_2025_Q4_SpatialDataStatusReport.xlsx, PC_2025_Q1.gdb.zip, PC_2025_Q1_R1.gdb.zip, PC_2025_Q2.gdb.zip, PC_2025_Q3.gdb.zip, PC_2025_Q3_R1.gdb.zip, PC_2025_Q4.gdb.zip
2026-02-09 | 2026-02-12 | N/A | DR1 | PC_2025_EOY_R0.xlsx
2026-02-09 | 2026-02-12 | N/A | DR1 | NON_ESD_PC_AKM_20250911_0924 Response.docx NON_ESD_PC_AKM_20250911_0924.pdf NON_ESD_PC_AKM_20250911_1055 Response.docx NON_ESD_PC_AKM_20250911_1055.pdf NON_ESD_PC_AKM_20250911_1105 Response.docx NON_ESD_PC_AKM_20250911_1105.pdf NON_ESD_PC_MAZ_20250910_0900 response.docx INTERNET NOV_ESD_PC_MAZ_20250910_0900 Closure.msg NON_ESD_PC_MAZ_20250910_0900.pdf NON_ESD_PC_MAZ_20250910_0906 Response.docx INTERNET NOV_ESD_PC_MAZ_20250910_0906 Closure.msg NON_ESD_PC_MAZ_20250910_0906.pdf NOV_ESD_PC_CAC23_20250116_1055 Response Draft.docx _INTERNET_ RE_ NOV_ESD_PC_CAC23_20250116_1055 - Closed Notification.msg NON_ESD_PC_AKM_20250911_1055.pdf NOV_ESD_PC_CAC23_20241219_1132 - PacifiCorp Response.docx _INTERNET_ NOV_ESD_PC_CAC23_20241219_1132 - Closed Notification.msg NOV_ESD_PC_CAC23_20241219_1132.pdf
2026-02-09 | 2026-02-12 | Vegetation Management | DR1 | SOP_08292024.pdf
2026-02-09 | 2026-02-12 | Asset Management | DR1 | Inspection Plan for California in 2025.xlsx
2026-02-09 | 2026-02-12 | Asset Management | DR1 | 009-Detailed Inspections for T&D Lines R14 [01_22_2025].pdf 011-Safety Patrol Inspections [02_25_2025].pdf 013-Intrusive Testing (Pole Test And Treat) [01_22_2025}.pdf 001-Maintenance_Intervals_R44 [12_11_2025].xlsx 069-Condition Codes [12_29_2025].xlsx
2026-02-09 | 2026-02-12 | Asset Management | DR1 | SOP_08292024.pdf PacifiCorp_QAQC_Program_Guidelines_v2.pdf
2026-02-27 | 2026-03-04 | AI-08, CO-02, CO-03, EP-01, EP-05, GH-12, MA01 | DR2 | No Document Requested
2026-03-12 | 2026-03-17 | AI-01, AI-02, AI-03, AI-04, AI-05, AI-06, AI-07, AI-08 | DR3 | CA 2025 Inspections Performed.xlsx
2026-03-12 | 2026-03-17 | AI-11 | DR3 | AI-11_CA 2025 Substation Inspections.xlsx
2026-03-12 | 2026-03-17 | AI-12 | DR3 | CA 2025 Inspections Performed.xlsx
2026-03-12 | 2026-03-17 | GH-01 | DR3 | Q1-4 2025 line rebuild 1.xlsx
2026-03-12 | 2026-03-17 | GH-02 | DR3 | dist poles.xlsx
2026-03-12 | 2026-03-17 | GH-03 | DR3 | transmission poles.xlsx
2026-03-12 | 2026-03-17 | GH-04 | DR3 | system automation.xlsx
2026-03-12 | 2026-03-17 | GH-05 | DR3 | fuses.xlsx
2026-03-12 | 2026-03-17 | SA-01 | DR3 | Item 16-Weather Stations
2026-03-12 | 2026-03-17 | VM-01, VM-02, VM-03, VM-04 | DR3 | CA_Miles_Unit_2025.xlsx
2026-03-12 | 2026-03-17 | VM-05 | DR3 | PpNotificationPoleClearing_2025_LRA.xlsx PpPoleTreatmentDetail_2025_LRA.xlsx
2026-03-12 | 2026-03-17 | VM-11 | DR3 | CA_Master_Post Audit Tracker_2025.xlsm
2026-03-20 | 2026-03-25 | AI-01 | DR4 | Refer to folder AI-01. UNDERSTANDING THE FP22 INSPECTION SCREEN.PDF Supplemental Info.docx
2026-03-20 | 2026-03-25 | AI-02 | DR4 | Refer to folder AI-02.
2026-03-20 | 2026-03-25 | AI-03 | DR4 | Refer to folder AI-03.
2026-03-20 | 2026-03-25 | AI-04 | DR4 | Refer to folder AI-04.
2026-03-20 | 2026-03-25 | AI-05 | DR4 | Refer to folder AI-05.
2026-03-20 | 2026-03-25 | AI-06 | DR4 | Refer to folder AI-06.
2026-03-20 | 2026-03-25 | AI-07 | DR4 | Refer to folder AI-07.
2026-03-20 | 2026-03-25 | AI-08 | DR4 | Refer to folder AI-08.
2026-03-20 | 2026-03-25 | AI-11 | DR4 | Item 9_ CA Substation Inspection Results
2026-03-20 | 2026-03-25 | AI-12 | DR4 | Refer to folder AI-12.
2026-03-20 | 2026-03-25 | SA-01 | DR4 | SA-01 8 weather station 2025 CA documents
2026-03-20 | 2026-03-25 | VM-01, VM-02, VM-03, VM-04 | DR4 | Work release pdf's 2025 Weekly Unit Tracker
2026-03-20 | 2026-03-25 | VM-11 | DR4 | Forester Audit Forms pdf's POST AUDIT 2025_MASTER Tracker_CA
2026-03-23 | 2026-03-26 | CO-01 | DR5 | Fall 2025 California Wildfire Survey Results.pptx
2026-03-23 | 2026-03-26 | CO-02 | DR5 | Wildfire_2025_Customer-Comms_AFN-Master-Meter-Email.docx Wildfire_2025_Customer-Comms_AFN-Preseason.docx Wildfire_2025_Customer-Comms_Backup-Power-End-of-Year-Email.docx PP_Tenant-PSPS-Flyer_English.pdf PP_Tenant-PSPS-Flyer_Spanish.pdf PP_Wildfire-Customer-Programs-Handout_English.pdf PP_Wildfire-Customer-Programs-Handout_Hmong.pdf PP_Wildfire-Customer-Programs-Handout_Spanish.pdf Wildfire_2025_Collateral_AFN-Partner-Toolkit_Pacific-Power.pdf Wildfire_2025_Customer-Comms_FA25-CA-Survey-Follow-Up-Letter.pdf Wildfire_2025_Customer-Comms_SP25-CA-Survey-Follow-Up-Letter.pdf AFN_Collateral-Links_2025.xlsx
2026-03-23 | 2026-03-26 | CO-03 | DR5 | See supporting documentation provided for EP-02 Pacific Power CA Wildfire Advisory Board March 2025_fv.pdf WAB Board Slides and Feeback 3.21.25.pdf 2025 CA PSPS TTX Del Norte Co Situation Manual – CONFIDENTIAL.pdf 2025 CA PSPS TTX Del Norte CO Slide Deck – CONFIDENTIAL.pdf CA TTX 5.27.25 Meeting Invitation with Materials Attached.pdf In Person Sign In Sheet 5.27.2025.pdf 2025 CA PSPS TTX Del Norte Co Attendance Virtual Roster.xlsx 2025 CA PSPS TTX Del Norte Co Invite List v051425.xlsx 2025 CA PSPS FE Siskiyou CO. EXPLAN – CONFIDENTIAL.pdf CA Functional Exercise 6.5.2025.pdf Exercise 2025 PacifiCorp Cal OES PSPS Notification Form PDF 06052025-EXERCISE.pdf Pacific-Power Public-Safety-Portal External Orgs_060525.pdf 2025 CA PSPS FE Siskiyou Co. Exercise Slides – CONFIDENTIAL.pptx 2025 CA PSPS FE Siskiyou Co. Attendance report 6-05-25.xlsx
2026-03-23 | 2026-03-26 | EP-01 | DR5 | 2025 Emergency Response Plan FOR INTERNAL USE ONLY.pdf 2025 Annex 01 External Emergency Coordination and Communication FOR INTERNAL USE ONLY.pdf 2025 Exec. Policy Group Training.pdf PAC-Executive Policy Group Onboarding_2025 CONFIDENTIAL.pdf Situation Manual PP ECC PSPS TTX 2025 CONFIDENTIAL.pdf PP ECC PSPS TTX 2025 CONFIDENTIALpptx
2026-03-23 | 2026-03-26 | EP-02 | DR5 | Pacific Power CA Wildfire Advisory Board March 2025_fv.pdf WAB Board Slides and Feeback 3.21.25.pdf 2025 CA PSPS TTX Del Norte Co Situation Manual – CONFIDENTIAL.pdf 2025 CA PSPS TTX Del Norte CO Slide Deck – CONFIDENTIAL.pdf CA TTX 5.27.25 Meeting Invitation with Materials Attached.pdf In Person Sign In Sheet 5.27.2025.pdf 2025 CA PSPS TTX Del Norte Co Attendance Virtual Roster.xlsx 2025 CA PSPS TTX Del Norte Co Invite List v051425.xlsx 2025 CA PSPS FE Siskiyou CO. EXPLAN – CONFIDENTIAL.pdf CA Functional Exercise 6.5.2025.pdf Exercise 2025 PacifiCorp Cal OES PSPS Notification Form PDF 06052025-EXERCISE.pdf Pacific-Power Public-Safety-Portal External Orgs_060525.pdf 2025 CA PSPS FE Siskiyou Co. Exercise Slides – CONFIDENTIAL.pptx 2025 CA PSPS FE Siskiyou Co. Attendance report 6-05-25.xlsx
2026-03-23 | 2026-03-26 | EP-05 | DR5 | Wildfire_2025_Customer-Comms_AFN-Master-Meter-Email.docx Wildfire_2025_Customer-Comms_AFN-Preseason.docx Wildfire_2025_Customer-Comms_Backup-Power-End-of-Year-Email.docx PP_Tenant-PSPS-Flyer_English.pdf PP_Tenant-PSPS-Flyer_Spanish.pdf PP_Wildfire-Customer-Programs-Handout_English.pdf PP_Wildfire-Customer-Programs-Handout_Hmong.pdf PP_Wildfire-Customer-Programs-Handout_Spanish.pdf Wildfire_2025_Collateral_AFN-Partner-Toolkit_Pacific-Power.pdf Wildfire_2025_Customer-Comms_FA25-CA-Survey-Follow-Up-Letter.pdf Wildfire_2025_Customer-Comms_SP25-CA-Survey-Follow-Up-Letter.pdf AFN_Collateral-Links_2025.xlsx https://www.pacificpower.net/content/dam/pcorp/documents/en/pacificpower/outages-safety/wildfire-safety/california-reports/PacifiCorp_Annual_AFN_Plan_2026_AppendixC2.pdf
2026-03-23 | 2026-03-26 | GH-12 | DR5 | Confidentiality Decl to OEIS re Boxpower Studies Revised_SignedRDA.pdf
2026-03-23 | 2026-03-26 | MA-01 | DR5 | CA_2025 APP_Substation Maintenance.xlsx
2026-03-23 | 2026-03-26 | MA-01 | DR5 | CA_2025 Wires Maintenance.xlsx
2026-03-30 | 2026-04-02 | Vegetation Management | DR6 | Foundry-QDR-VegetationProjectPoint-2025_3.xlxs PpNotificationPoleClearing_2025.xlsx
2026-04-03 | 2026-04-08 | VM-01 | DR7 | 1) Refer to folder VM-01 2) 2025 Unit Tracker_weekly progress.xlsx
2026-04-03 | 2026-04-08 | VM-02 | DR7 | 1) Refer to folder VM-02 2) 2025 Unit Tracker_weekly progress.xlsx
2026-04-03 | 2026-04-08 | VM-03 | DR7 | 1) Refer to folder VM-03 2) 2025 Unit Tracker_weekly progress.xlsx
2026-04-03 | 2026-04-08 | VM-04 | DR7 | 1) Refer to folder VM-04 2) 2025 Unit Tracker_weekly progress.xlsx
2026-04-03 | 2026-04-08 | AI-12 | DR7 | Independent Evaluator Data Request 7 - Asset Inspections.docx
2026-04-03 | 2026-04-08 | AI-04 | DR7 | Independent Evaluator Data Request 7 - Asset Inspections.docx
2026-04-16 | 2026-04-21 | GH-01 | DR8 | Refer to folder - Attachments - DR 8 Grid Hardening GH-01
2026-04-16 | 2026-04-21 | GH-02 | DR8 | Refer to folder - Attachments - DR 8 Grid Hardening GH-02
2026-04-16 | 2026-04-21 | GH-03 | DR8 | Refer to folder - Attachments - DR 8 Grid Hardening GH-03
2026-04-16 | 2026-04-21 | GH-04 | DR8 | Refer to folder - Attachments - DR 8 Grid Hardening GH-04
2026-04-16 | 2026-04-21 | GH-05 | DR8 | Refer to folder - Attachments - DR 8 Grid Hardening GH-05
2026-04-16 | 2026-04-21 | VM-05 | DR8 | Refer to folder - Attachments - DR 8 / Work complete work releases, PDF
2026-04-24 | 2026-04-29 | VM-01 | DR9 | Distribution Detailed Inspection Mileages.docx
2026-04-24 | 2026-04-29 | VM-01 | DR9 | 5G7 DNT MGE closed WR 2025 - Copy.pdf
2026-04-24 | 2026-04-29 | VM-01 | DR9 | 5L78 DNT TREES COMPLETED WORK RELEASE 2025.pdf
2026-04-24 | 2026-04-29 | VM-03 | DR9 | 5G97 FIN MGE closed WR 2025.pdf
2026-04-24 | 2026-04-29 | VM-04 | DR9 | Attestation.pdf
2026-04-24 | 2026-04-29 | CO-02 | DR9 | 2025 AFN Plan: https://www.pacificpower.net/content/dam/pcorp/documents/en/pacificpower/outages-safety/wildfire-safety/california-reports/PacifiCorp_Annual_AFN_Plan_2025.pdf PacifiCorp_Annual_AFN_Plan_2025.pdf 2024 AFN Plan: https://www.pacificpower.net/content/dam/pcorp/documents/en/pacificpower/outages-safety/wildfire-safety/california-reports/PacifiCorp_2024_Access_and_Functional_Needs_Report.pdf
2026-04-24 | 2026-04-29 | GH-02 | DR9 | WO 07368950 - 5G1 Fort Jones WO 7-Redline PST Package-00.pdf
2026-04-24 | 2026-04-29 | GH-02 | DR9 | Report for system hardening unit not found in supporting documentation pole 222200.docx
2026-04-24 | 2026-04-29 | MA-01 | DR9 | 001.xlsx
2026-04-24 | 2026-04-29 | MA-01 | DR9 | CALIFORNIA_WEATHER_STATION_2025_MAINTENANCE.xlsx
2026-04-24 | 2026-04-29 | AI-05 | DR9 | CALIFORNIA_DATA_REQUEST_DR09_15_16.docx
2026-04-30 | 2026-05-05 | VM-02 | DR10 | CRE668087_Item_2_Response.docx Work_ID_Dates_CRE668087.xlsx
2026-04-30 | 2026-05-05 | GH-04 | DR10 | Refer to Grid Hardening folder, Item 3.
2026-04-30 | 2026-05-05 | GH-04 | DR10 | Refer to Grid Hardening folder, Item 4.
2026-04-30 | 2026-05-05 | GH-04 | DR10 | GH-04_Attestation.pdf
2026-05-14 | 2026-05-20 | GH-04 | DR11 | Please refer to Grid Hardening Folder, Item 1.
2026-05-14 | 2026-05-20 | GH-04 | DR11 | TULELAKE(CA)_5L83_25865_20230929.pdf
2026-05-14 | 2026-05-20 | GH-04 | DR11 | Morrison Creek SEQ1_CA - WO 10076877.pdf
2026-05-15 | 2026-05-20 | Asset Management | DR12 | Inspection Plan for California in 2025.xlsx 001-Maintenance_Intervals_R44 [12_11_2025].xlsx 069-Condition Codes [12_29_2025].xlsx 009-Detailed Inspections for T&D Lines R14 [01_22_2025].pdf 011-Safety Patrol Inspections [02_25_2025].pdf 013-Intrusive Testing (Pole Test And Treat) [01_22_2025}.pdf
2026-05-15 | 2026-05-20 | Asset Management | DR12 | 2025 Asset Inspection Audit Calcs Table 8-7.xlsx
2026-05-15 | 2026-05-20 | Asset Management | DR12 | Yreka Desktop Audit (03-26 to 04-24).xlsx Yreka Desktop Audit (03-26 to 04-24).msg Yreka Field Audit_03252025.msg Yreka Field Audit_03252025.pdf
2026-05-15 | 2026-05-20 | QA/QC | DR12 | Asset Inspections: Overhead Detailed Inspection Program Audit Process (Dec 2024).pdf Exhibit M.07 - PP Performance Requirements for Inspect Test.pdf
2026-05-22 | 2026-05-27 | VM-02 | DR13 | IE DR 13 - Item 1 Response.docx WE0103_2025_MASTER Mile Tracker_CA_CRE668087.xlsm
2026-05-22 | 2026-05-27 | AI-12 | DR13 | Refer to tab "AI Pass Rate"

## Tab 4 - SME Interviews
SME Interviews
Independent Evaluator: | NV5/Guidehouse
Electrical Corporation: | PacifiCorp
Interview date | Section / Initiative | SME interview number | Positions interviewed | Summary of interview
2026-04-22 | VM-01, VM-03, VM-04 | 001 | Vegetation Management Team: Kowalek, David (PacifiCorp) <david.kowalek@pacificorp.com> Garrett, John (PacifiCorp) <john.garrett@pacificorp.com> McKinney, William (PacifiCorp) <william.mckinney@pacificorp.com> Nair, Lakshmi (PacifiCorp) <lakshmi.nair@pacificorp.com> King, Brian (PacifiCorp) <brian.king@pacificorp.com> Hooley, Josh (PacifiCorp) <josh.hooley@pacificorp.com> | Meeting to discuss IE questions related to VM-01, VM-03, and VM-04
2026-04-30 | GH-04 | 002 | Grid Hardening Team: Schiedler, Kevin (PacifiCorp) <Kevin.Schiedler@pacificorp.com> david.schober@pacificorp.com; wendy.sukowatey@pacificorp.com Garrett, John (PacifiCorp) <John.Garrett@pacificorp.com> Nair, Lakshmi (PacifiCorp) <Lakshmi.Nair@pacificorp.com> McKinney, William (PacifiCorp) <William.McKinney@pacificorp.com> David Kowalek (David.Kowalek@pacificorp.com) <david.kowalek@pacificorp.com> Chissom, Russ (PacifiCorp) <Russ.Chissom@pacificorp.com> | Meeting to discuss IE questions related to GH-04
2026-05-13 | GH-04 | 003 | Grid Hardening Team: Schiedler, Kevin (PacifiCorp) <Kevin.Schiedler@pacificorp.com> david.schober@pacificorp.com; wendy.sukowatey@pacificorp.com Garrett, John (PacifiCorp) <John.Garrett@pacificorp.com> Nair, Lakshmi (PacifiCorp) <Lakshmi.Nair@pacificorp.com> McKinney, William (PacifiCorp) <William.McKinney@pacificorp.com> David Kowalek (David.Kowalek@pacificorp.com) <david.kowalek@pacificorp.com> Chissom, Russ (PacifiCorp) <Russ.Chissom@pacificorp.com> | Follow-up meeting to 4/30/26 Discuss new IE questions related to GH-04