## Tab 1 - Overview tab
IE AIR Attachments
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Bear Valley Electric Service
Legends
Tab 1 | Overview Tab - Instructions and overview
Tab 2 | Catalog of Initiatives - Initiative review and funding compliance of all initiatives
Tab 3 | Data Requests - Comprehensive list of documents reviewed
Tab 4 | SME Interviews - Summary of interviews conducted

## Tab 2 - Catalog of Initiatives
Catalog of Initiatives
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Bear Valley Electric Service
WMP Category | Initiative Tracking ID | WMP Section Number | Initiative Name | Initiative Type | WMP - Initiative Description | WMP - Initiative Target | EC-Claimed Progress (Q4 QDR) | EC-Claimed Progress (EC AIR) | EC-Claimed Progress (DR) | IE Declared Actual | EC-Claimed Initiative Status | Target Not Met - Rationale | Sample Size (#) | Sample Validation Rate (%) | Verification Method | IE Declared Initiative Completion Percent (%) | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%) | Funding discrepancy - finding | Funding discrepancy - detail | Satisfied Risk Reduction Goal - finding | Satisfied Risk Reduction Goal - detail
Grid Design Operations and Maintenance | GD_1 | 8.1.2.1 | Covered Conductor Replacement Project | Focus & field verifiable | Replace Covered Conductors on 5.10 Circuit Miles | 5.1 | 7.73 | 7.73 | 7.72 | 7.72 | Target met | N/A | 3.1 | 100% | Field Inspections Pole Locations (Frontload Data, DR015) Sample As-builts (DR015.b, DR015.c) | 152% | 1840600 | 5572700 | 202.8% | Overspend | Board-authorized scope acceleration, not uncontrolled cost growth. Reconciliation item: reconcile the residual actual-spend and mileage difference between the AIR figure and the DR004 unit-cost basis. | Yes | N/A
Grid Design Operations and Maintenance | GD_2 | 8.1.2.1 | Radford Line Replacement Project | Focus & non-field verifiable | Replace 0 Circuit Miles | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 117100 | 100% | Overspend | $117.1K of prior-year (November 2024) work invoiced in 2025 (reported +100%). | N/A | N/A
Grid Design Operations and Maintenance | GD_3 | 8.1.2.2 | Minor Undergrounding Upgrades Projects | Non-focus & non-field verifiable | Initiate UG Projects as Needed (100% of Budget) | Initiate UG Projects as Needed (100% of Budget) | In Progress | In Progress | 8 Project Locations | 8 Project Locations | Target met | N/A | 8 | 100% | Field Inspections Service Locations (Frontload Data) | 100% | 301200 | 172600 | -42.7% | Underspend | Consistent with the demand-driven nature of the initiative and does not indicate a funding-adequacy or implementation concern. | Yes | N/A
Grid Design Operations and Maintenance | GD_4 | 8.1.2.3 | Distribution Pole Replacements & Reinforcements | Focus & field verifiable | Replace/Reinforce 100 Poles | 100 | 123 | 123 | 125 | 125 | Target met | N/A | 62 | 98.8% | Field Inspections Pole Locations (Frontload Data) | 122% | 788800 | 2388300 | 202.8% | Overspend | Completed 123 poles against the 100-pole target under the April 2025 UWC authorization. | Yes | N/A
Grid Design Operations and Maintenance | GD_5 | 8.1.2.3 | Radford Line Replacement Project | Non-focus & non-field verifiable | Replace 0 Poles | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 0 | 50200 | 100% | Overspend | This $0-budget initiative reflects $50.2K of prior-year (2024) work invoiced in 2025 (reported +100%). | N/A | N/A
Grid Design Operations and Maintenance | GD_6 | 8.1.2.3 | Evacuation Route Hardening Project | Focus & field verifiable | Perform Hardening Activities on 500 Poles | 500 | 851 | 851 | 851 | 851 | Target met | N/A | 119 | 98.7% | Field Inspections Pole Locations (Frontload Data, DR020, DR049.b) | 168% | 794100 | 540400 | -31.9% | Underspend | 2025 scope target was exceeded (851 poles against 500), with new-install wrap cost booked to the related hardening initiatives. | Yes | N/A
Grid Design Operations and Maintenance | GD_8 | 8.1.2.5 | Traditional Overhead Hardening | Non-focus & non-field verifiable | Perform Overhead Hardening | As Needed Maintenance Budget (% of Budget) | In Progress | N/A | 16 Maintenance Items | 16 Maintenance Items | Target met | N/A | 11 | 100% | Maintenance Repair Log (Frontload Data) 16 Maintenance Records (DR050) | 100% | 803300 | 1011500 | 25.9% | Overspend | Additional in-scope hardening work was performed within the program, which BVES_DR004 Item 6 attributes to planned replacement of non-exempt surge arresters under ACI Issue BVES-23-14, with associated splice replacement on the same pole. | Yes | N/A
Grid Design Operations and Maintenance | GD_10 | 8.1.2.7 | Bear Valley Solar Energy Project, Microgrids | Focus & non-field verifiable | Implement Bear Valley Solar Energy Project | 100% Project Completion | Pursuing Conditional Use Permit | Delayed | Decision Approving Settlement Agreement | Decision Approving Settlement Agreement | Target not met | Project was deferred pending CPUC approval and is carried into the 2026–2028 WMP. | N/A | N/A | CPUC Approval Decision (Frontload Data) | 0% | 13578400 | 702200 | -94.8% | Underspend | Regulatory-timing deferral – CPUC approval did not occur until December 18, 2025. Project was deferred pending CPUC approval and is carried into the 2026–2028 WMP. | N/A | N/A
Grid Design Operations and Maintenance | GD_11 | 8.1.2.7 | Energy Storage Project, Microgrids | Focus & non-field verifiable | Implement Bear Valley Storage Project | 100% Project Completion | This project is being carried over to the 2026-2028 Base WMP. | Delayed | Decision Approving Settlement Agreement | Decision Approving Settlement Agreement | Target not met | Project was deferred pending CPUC approval and is carried into the 2026–2028 WMP. | N/A | N/A | CPUC Approval Decision (Frontload Data) | 0% | 10342000 | 32500 | -99.7% | Underspend | Regulatory-timing deferral – CPUC approval did not occur until December 18, 2025. Project was deferred pending CPUC approval and is carried into the 2026–2028 WMP. | N/A | N/A
Grid Design Operations and Maintenance | GD_12 | 8.1.2.8 | Substation Automation | Non-focus & non-field verifiable | Complete Automation of 3 Substations | 3 | 3 | 3 | 3 | 3 | Target met | N/A | 3 | 100% | Field Inspections Substation Locations (Frontload Data) | 100% | 640200 | 364400 | -43.1% | Underspend | The automation target was met with cost recorded under the related rebuild budgets. | Yes
Grid Design Operations and Maintenance | GD_13 | 8.1.2.8 | Switch & Field Device Automation | Focus & non-field verifiable | Install 11 Switches | 11 | 11 | 11 | 12 | 11 | Target met | N/A | 11 | 100% | Field Inspections Switch Locations (Frontload Data) | 100% | 640200 | 1370600 | 114.1% | Overspend | The automation target was met at a higher equipment-and-labor cost than estimated. | Yes | N/A
Grid Design Operations and Maintenance | GD_14 | 8.1.2.8 | Capacitor Bank Upgrade Project | Focus & field verifiable | Replace 6 Capacitor Banks | 6 | 6 | 8 | 6 | 6 | Target met | N/A | 6 | 100% | Field Inspections Capacitor Bank Locations (Frontload Data) Installation Location Clarification (DR021) | 100% | 311500 | 594100 | 90.7% | Overspend | The target was met at a higher equipment-and-labor cost than estimated. | Yes | N/A
Grid Design Operations and Maintenance | GD_15 | 8.1.2.8 | Fust TripSaver Automation | Focus & field verifiable | Install 50 Fust TripSavers | 50 | 50 | 73 | 49 | 49 | Target met | N/A | 46 | 100% | Field Inspections Fuse Tripsaver Locations (Frontload Data) Installation Location Clarification (DR049) | 98% | 133600 | 400400 | 199.7% | Overspend | Installed 73 units against the 50-unit target at a labor-weighted cost above estimate. | Yes | N/A
Grid Design Operations and Maintenance | GD_16 | 8.1.2.8 | Server Room | Non-focus & non-field verifiable | Project Milestones for Server Installation | 100% Project Completion | Completed | Completed | Project Completion Documentation | Project Completion Documentation | Target met | N/A | N/A | N/A | Field Inspections Server Room Location (Frontload Data) | 100% | 0 | 42600 | 100% | Overspend | $0-budget initiative reflects $42.6K of prior-year (2023–2024) work invoiced in 2025 (reported +100%); the 2023–2025 lifecycle total is within approximately 1% of the WMP forecast. | N/A | N/A
Grid Design Operations and Maintenance | GD_17 | 8.1.2.8 | Distribution Management Center | Non-focus & non-field verifiable | Project Milestones for Distribution Management Center | 100% Project Completion | Completed | Completed | Completed in 2024 | Completed in 2024 | Target met | N/A | N/A | N/A | N/A | N/A | 0 | 11900 | 100% | Overspend | This $0-budget initiative reflects $11.9K of prior-year (2024) work invoiced in 2025 (reported +100%); the IE carries a lifecycle-cost observation to the synthesis. | N/A | N/A
Grid Design Operations and Maintenance | GD_19 | 8.1.2.10 | Tree Attachment Removal Project | Focus & non-field verifiable | Remove 100 Tree Attachments | 100 | 110 | 110 | 110 | 110 | Target met | N/A | 62 | 98.6% | Field Inspections Project Completion Documentation (Frontload Data) | 108% | 592700 | 861900 | 45.4% | Overspend | Material and labor escalation and 6–9 month ordering lead times, with new-install fire wrap booked to this initiative. | Yes | N/A
Grid Design Operations and Maintenance | GD_21 | 8.1.2.12 | BVPP Phase 4 Upgrade Project | Focus & non-field verifiable | Project Milestones for Upgrade Project | 100% Project Completion | Completed | N/A | BVPP Phase 4 upgrades were completed in 2024. | BVPP Phase 4 upgrades were completed in 2024. | Target met | N/A | N/A | N/A | BVES Written Response (Frontload Data) | 100% | 0 | 79500 | 100% | Overspend | This $0-budget initiative reflects $79.5K of prior-year (2024) work invoiced in 2025 (reported +100%); the IE carries a lifecycle-cost observation to the synthesis. | N/A | N/A
Grid Design Operations and Maintenance | GD_22 | 8.1.2.12 | Partial Safety and Technical Upgrades to Maltby Substation | Non-focus & non-field verifiable | Project Milestones for Maltby Substation | 100% Project Completion | Completed | Completed | The electrical equipment was installed October 31, 2025, and the substation was reenergized November 14, 2025. | The electrical equipment was installed October 31, 2025, and the substation was reenergized November 14, 2025. | Target met | N/A | N/A | N/A | Maltby Substation Timeline BVES Written Response Substation Photos (Frontload Data) | 100% | 1777500 | 1896600 | 6.7% | Overspend | N/A | N/A | N/A
Grid Design Operations and Maintenance | GD_23 | 8.1.2.12 | Safety and Technical Upgrades to Lake Substation | Focus & non-field verifiable | Project Milestones for Lake Substation | No Action | In Progress | N/A | In Progress | In Progress | N/A | N/A | N/A | N/A | Lake Substation Timeline (Frontload Data) | N/A | 0 | 1374520 | 100% | Overspend | AIR Attachment D omits this Focus initiative despite $1,374.5k of 2025 spend reported in BVES_DR001 and confirmed in BVES_DR004 Item 10 and BVES_DR004.b as a clerical reporting error. The IE carries the 2025 EC AIR errata adding GD_23 with its planned amount, 2025 actual, and variance driver as a reportable item to the Executive Summary. | N/A | N/A
Grid Design Operations and Maintenance | GD_24 | 8.1.2.12 | Partial Safety and Technical Upgrades to Village Substation | Non-focus & non-field verifiable | Project Milestones for Village Substation | No Action | Delay | N/A | Village Substation Statement | Village Substation Statement | N/A | N/A | N/A | N/A | BVES Written Response (Frontload Data) | N/A | 0 | 0 | 0% |  | N/A | N/A | N/A
Grid Design Operations and Maintenance | GD_25 | 8.1.3.1 | Detailed Inspection Program | Non-focus & non-field verifiable | Complete 53 Circuit Miles of Detailed Inspections | 53 | 53 | 53 | 49 | 49 | Target not met | Although all the sampling data was validated, due to the four circuit mileage shortfall, the initiative validation rate is 92% which is outside of the 95% Energy Safety Threshold. | 34 Asset Points | 100% | Inspection Log 34 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 92% | 14300 | 31300 | 118.9% | Overspend | Labor hours exceeded the small forecast while the 53-circuit-mile target was achieved. | No | Did not meet target goal thus not achieving risk reduction goal.
Grid Design Operations and Maintenance | GD_26 | 8.1.3.2 | Patrol Inspection Program | Non-focus & non-field verifiable | Complete 205 Circuit Miles of Patrol Inspections | 205 | 205 | 205 | 197 | 197 | Target met | N/A | 14 Asset Points | 100% | Patrol Inspection List (Frontload Data) 14 Inspection Records (DR031) Circuit Mileage by Circuit (DR002) | 96% | 33400 | 73000 | 118.6% | Overspend | Patrol labor hours exceeded the small forecast while the target was achieved. | Yes | N/A
Grid Design Operations and Maintenance | GD_27 | 8.1.3.3 | UAV Thermography | Non-focus & non-field verifiable | Inspect 205 Circuit Miles | 205 | 205 | 205 | 205 | 205 | Target met | N/A | 34 Asset Points | 100% | UAV and Thermal Inspection List 34 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 100% | 74100 | 61300 | -17.3% | Underspend | Work was contracted below forecast with the inspection target achieved. | Yes | N/A
Grid Design Operations and Maintenance | GD_28 | 8.1.3.4 | UAV HD Photography/Videography | Non-focus & non-field verifiable | Inspect 205 Circuit Miles | 205 | 205 | 205 | 205 | 205 | Target met | N/A | 34 Asset Points | 100% | UAV and Thermal Inspection List 34 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 100% | 74100 | 59500 | -19.7% | Underspend | Work was contracted below forecast with the target achieved under the engagement shared with VM_3. | Yes | N/A
Grid Design Operations and Maintenance | GD_29 | 8.1.3.1 | LiDAR Inspections | Non-focus & non-field verifiable | Inspect 205 Circuit Miles | 205 | 205 | 205 | 187 | 187 | Target not met | Although all sampling data was validated, the total number of circuit miles based on the circuits listed in the frontload data spreadsheet led to a shortfall of 18 circuit miles from the target. | 30 Asset Points | 100% | LiDAR Inspection List 30 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 91% | 85400 | 76200 | -10.8% | Underspend | Standalone cost report supports a corrected actual of $85,366, which brings the variance to under 1%. | No | Did not meet target goal thus not achieving risk reduction goal.
Grid Design Operations and Maintenance | GD_30 | 8.1.3.6 | 3rd Party Ground Patrol | Non-focus & non-field verifiable | Inspect 205 Circuit Miles | 205 | 205 | 205 | 205 | 205 | Target met | N/A | 34 Asset Points | 100% | 3rd Party Inspection List 34 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 100% | 61500 | 16400 | -73.3% | Underspend | Patrol scope was completed at a lower contracted cost under the shared VM_5 engagement. | Yes | N/A
Grid Design Operations and Maintenance | GD_31 | 8.1.3.7 | Intrusive Pole Inspections | Non-focus & non-field verifiable | Inspect 850 Poles | 850 | 850 | 850 | 915 | 915 | Target met | N/A | 33 | 100% | Intrusive Inspection List 33 Inspection Records (Frontload Data) | 108% | 19700 | 38400 | 94.9% | Overspend | Higher contracted rate on completed scope with the target achieved. | Yes | N/A
Grid Design Operations and Maintenance | GD_32 | 8.1.3.8 | Substation Inspections | Non-focus & non-field verifiable | Complete 144 Substation Inspections | 144 | 156 | 156 | 143 | 143 | Target met | N/A | 28 | 96% | Substation Inspection List (Frontload Data) 27 Inspection Records (DR037) | 95% | 291700 | 335200 | 14.9% | Overspend | More labor hours and a higher contracted testing cost while the annual target was exceeded (156 of 144). | Yes | N/A
Grid Design Operations and Maintenance | GD_33 | 8.1.4.3 | Equipoment Maintenance & Repair | Non-focus & non-field verifiable | Replace 100% of Connectors As Needed | As Needed Maintenance (100% of Budget) | In Progress | N/A | Maintenance Repair Log 15 Work Orders | Maintenance Repair Log 15 Work Orders | Target met | N/A | N/A | N/A | Maintenance Repair Log (Frontload Data) 11 Maintenance Items | 100% | 1105400 | 1352200 | 22.3% | Overspend | Higher labor hours from inspection-finding resolution and storm response (an approximate 61% routine / 39% storm-related split). | Yes | N/A
Grid Design Operations and Maintenance | GD_34 | 8.1.5 | Asset Management and Inspection Enterprise System(s) | Non-focus & non-field verifiable | 100% Maintenance of Asset Management System | 100% | In Progress | In Progress | Three iRestore Fully Executed Contracts | Three iRestore Fully Executed Contracts | Target met | N/A | N/A | N/A | 3 Fully Executed iRestore Contracts (Frontload Data) | 100% | 59400 | 46000 | -22.6% | Underspend | Lower-than-estimated labor cost to update and maintain the system. | Yes | N/A
Grid Design Operations and Maintenance | GD_35 | 8.1.6 | Asset Quality Assurance/Quality Control | Non-focus & non-field verifiable | Complete 20 Asset QCs on WMP Work | 20 | 20 | 20 | 20 | 20 | Target met | N/A | N/A | N/A | QC Assessment Log (Frontload Data) 13 Asset QC Records (DR041) | 100% | 20900 | 27600 | 32.1% | Overspend | More QA/QC labor than estimated with the 20-QC target achieved. | Yes | N/A
Grid Design Operations and Maintenance | GD_36 | 8.1.7 | Open Work Orders | Non-focus & non-field verifiable | Complete All WOs Within GO95 Timeframe | Complete All WOs Within GO95 Timeframe | In Progress | N/A | GO165 Procedure Document | No documentation proving that all open WO have been resolved. | Target not met | Although BVES provided ample documentation that outlines the open work order procedure in alignment with GO165, BVES did not provide adequate documentation that demonstrates all open work orders were resolved within the GO95 timeframe. | N/A | N/A | GO165 Procedure (Frontload Data) | 0% | 18300 | 24200 | 32.2% | Overspend | Additional hours needed to resolve open work orders. | No | No evidence to support target was achieved, thus no way to validate risk reduction goal.
Grid Design Operations and Maintenance | GD_37 | 8.1.8.1 | Equipment Setting to Reduce Wildfire Risk | Non-focus & non-field verifiable | Review & Evaluate System Settings | Review & Evaluate System Settings | In Progress | N/A | System Settings Have Been Reviewed & Evaluated | System Settings Have Been Reviewed & Evaluated | Target met | N/A | N/A | N/A | BVES ERDP Rev. 2 BVES PSPS Procedures Rev. 3 EPSS Implementation List (Frontload Data) | 100% | 5200 | 6900 | 32.7% | Overspend | Additional annual review and update hours. | Yes | N/A
Grid Design Operations and Maintenance | GD_38 | 8.1.8.2 | Grid Response Procedures & Notifications | Non-focus & non-field verifiable | Review & Update Procedure Annually | Review & Update Procedure Annually | In Progress | N/A | Procedures Have Been Reviewed and Updated | Procedures Have Been Reviewed and Updated | Target met | N/A | N/A | N/A | BVES ERDP Rev. 2 Firefighting Coordination Protocols (Frontload Data) | 100% | 9200 | 12100 | 31.5% | Overspend | Additional annual review and update hours. | Yes | N/A
Grid Design Operations and Maintenance | GD_39 | 8.1.8.3 | Personnel Work Procedures & Training in Conditions of Elevated Fire Risk | Non-focus & non-field verifiable | Finalize Review On Policies and Procedures | Finalize Review | In Progress | N/A | Procedures Have Been Reviewed and Updated | Procedures Have Been Reviewed and Updated | Target met | N/A | N/A | N/A | BVES PSPS Procedures Rev. 3 PSPS Exercise Spreadsheet BVES PSPS Post-Season Report (Frontload Data) | 100% | 3900 | 5200 | 33.3% | Overspend | Additional annual procedure and training update hours. | Yes | N/A
Grid Design Operations and Maintenance | GD_40 | 8.1.9 | Workforce Planning | Non-focus & non-field verifiable | Verify Staffing Level | Staffing Level Verified | In Progress | N/A | 2025 Staffing Levels Verified | 2025 Staffing Levels Verified | Target met | N/A | N/A | N/A | Fully Executed & Amended Contracts (Frontload Data) | 100% | 6500 | 8600 | 32.3% | Overspend | Additional workforce-planning review hours. | Yes | N/A
Grid Design Operations and Maintenance | ST_1 | 5.4.5 | Environmental Compliance & Permitting | Non-focus & non-field verifiable | Review Annually and Update | Annual Review and Update | In Progress | N/A | Snow Summit Permit | Snow Summit Permit | Target met | N/A | N/A | N/A | Snow Summit Permit (Frontload Data) | 100% | 26200 | 34500 | 31.7% | Overspend | NONE PROVIDED | N/A | N/A
Vegetation Management and Inspections | VM_1 | 8.2.2.1 | Detailed Inspections | Focus & non-field verifiable | Complete 53 Circuit Miles of Detailed Inspections | 53 | 53 | 53 | 1636 Points/ 128 Detailed Point Inspections = 49 Circuit Miles | 1636 Points/ 128 Detailed Point Inspections = 49 Circuit Miles | Target not met | The IE was able to cross-reference the point data to the “Circuit Mileage by Circuit” spreadsheet for the circuits shown; however, the circuit mileage totaled 49 circuit miles, not the 53 circuit miles claimed. | 128 Asset Points | 100% | Detailed Inspections List 128 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 92% | 14300 | 31300 | 118.9% | Overspend | inspection labor hours exceeded the small forecast while the 53-circuit mile target was achieved. | No | Did not meet target goal thus not achieving risk reduction goal.
Vegetation Management and Inspections | VM_2 | 8.2.2.1 | Patrol Inspections | Focus & non-field verifiable | Complete 205 Circuit Miles of Patrol Inspections | 205 | 205 | 205 | 205 | 205 | Target met | N/A | 19 Asset Points | 100% | Patrol Inspections List (Frontload Data) 22 Circuit Inspection Records (DR071) Circuit Mileage by Circuit (DR002) | 100% | 33400 | 73000 | 118.6% | Overspend | Patrol labor hours exceeded the small forecast while the 205-circuit mile target was achieved. | Yes | N/A
Vegetation Management and Inspections | VM_3 | 8.2.2.1 | UAV HD Photography/Videography | Non-focus & non-field verifiable | Complete 205 Circuit Miles of Inspections | 205 | 205 | 205 | 6,613 Points = 205 Circuit Miles/ ResourceKeeper | 6,613 Points = 205 Circuit Miles/ ResourceKeeper | Target met | N/A | 34 Asset Points | 100% | UAV and Thermal Inspection List 34 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 100% | 74100 | 59500 | -19.7% | Underspend | Work was contracted below forecast with the 205-circuit mile target achieved under the engagement shared with GD_28. | Yes | N/A
Vegetation Management and Inspections | VM_4 | 8.2.2.1 | LiDAR Inspections | Non-focus & non-field verifiable | Complete 205 Circuit Miles of LiDAR Inspections | 205 | 205 | 205 | 197 Points = 186.86 Circuit Miles 30 Points | 197 Points = 186.86 Circuit Miles 30 Points | Target not met | Although all sampling data was validated, the total number of circuit miles based on the circuits listed in the frontload data spreadsheet led to a shortfall of ~18 circuit miles from the target, resulting in an initiative validation rate of 91%. | 30 Asset Points | 100% | LiDAR Inspection List 30 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 91% | 76200 | 85400 | 12.1% | Overspend | Higher contracted rate/labor on the shared LiDAR engagement with the target achieved; the amount is supported by vendor backup. | No | Did not meet target goal thus not achieving risk reduction goal.
Vegetation Management and Inspections | VM_5 | 8.2.2.1 | 3rd Party Ground Patrol | Non-focus & non-field verifiable | Complete 205 Circuit Miles of Ground Patrol inspections | 205 | 205 | 205 | 205 | 205 | Target met | N/A | 34 Asset Points | 100% | 3rd Party Ground Patrol List 34 Inspection Records (Frontload Data) Circuit Mileage by Circuit (DR002) | 100% | 61500 | 16400 | -73.3% | Underspend | Patrol scope was completed at a lower contracted cost under the shared GD_30 engagement. | Yes | N/A
Vegetation Management and Inspections | VM_6 | 8.2.2.1 | Substation Inspections | Non-focus & non-field verifiable | Complete Inspections of 144 Substations | 144 | 156 | 156 | 12 Substations – Monthly Completion Dates (143 Total)/30 PDF Inspection Reports | 12 Substations – Monthly Completion Dates (143 Total)/30 PDF Inspection Reports | Target met | N/A | 28 | 100% | Substation Inspection List (Frontload Data) 30 Substation Inspection Records (DR075) | 99% | 4500 | 5100 | 13.3% | Overspend | Additional inspection labor on a small base with the target exceeded (156 of 144). | Yes | N/A
Vegetation Management and Inspections | VM_7 | 8.2.3.1 | Pole Clearing | Non-focus & non-field verifiable | Review & Update Procedure | Review & Update Procedure | N/A | N/A | Procedure Reviewed & Updated | Procedure Reviewed & Updated | Target met | N/A | N/A | N/A | BVES Vegetation Management Programs (DR076) | 100% | 0 | 0 | 0% |  | N/A | N/A | N/A
Vegetation Management and Inspections | VM_8 | 8.2.3.2 | Wood and Slash Management | Non-focus & non-field verifiable | Meet Waste Removal Requirements | Meet Waste Removal Requirements | Achieved | Completed | Waste Removal Requirements Met | Waste Removal Requirements Met | Target met | N/A | N/A | N/A | Vegetation Management Contract (Frontload Data) | 100% | 507200 | 519400 | 2.4% | Overspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM_9 | 8.2.3.3 | Clearance | Non-focus & non-field verifiable | Clear 72 Circuit Miles | 72 | 91 | 91 | 91 | 91 | Target met | N/A | 25 | 100% | Clearance Completed Inventory Completed Clearance Log VegClear .gdb (Frontload Data) | 126% | 2157600 | 2205300 | 2.2% | Overspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM_10 | 8.2.3.4 | Fall-In Mitigation | Non-focus & non-field verifiable | Mitigate 88 Trees | 88 | 164 | 164 | 164 | 164 | Target met | N/A | 29 | 100% | Field Inspections Tree Removal Locations (Frontload Data, DR061) | 186% | 342200 | 350800 | 2.5% | Overspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM_11 | 8.2.3.5 | Substation Defensible Space | Non-focus & non-field verifiable | Inspect and Clear 13 Substations | 13 | 13 | 13 | 11 | 11 | Target not met | Although BVES claimed all 13 Substations were inspected and cleared, the provided documentation demonstrates that only 11 met this target. The reasoning provided for the Maltby Substation is adequate and provides detail and context as to why no inspection or abatement was performed on this substation during 2025. However, no further information was provided for the Village Substation leading to invalidation. | 13 | 92% | Defensible Space Inspection List (Frontload Data) 11 Substation Inspection Records (DR062) | 92% | 15900 | 9700 | -39% | Underspend | The 13-substation scope was completed at a lower contracted cost. | No | Did not meet target goal thus not achieving risk reduction goal.
Vegetation Management and Inspections | VM_12 | 8.2.3.6 | High Risk Species | Non-focus & non-field verifiable | WMP Plan Review & Vegetation Discussion with Experts | WMP Plan Review & Vegetation Discussion with Experts | N/A | N/A | 338 High-Risk Locations 778 Trees Remediated | 338 High-Risk Locations 778 Trees Remediated | Target met | N/A | N/A | N/A | High-Risk Species Mitigation Inventory (Frontload Data) | 100% | 342200 | 350800 | 2.5% | Overspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM_13 | 8.2.3.7 | Fire-Resilient Rights-of-Way | Non-focus & non-field verifiable | Fire-Resilient Rights-of-Way Clearance | N/A | In Progress | Completed and Ongoing for 2026-2028 WMP cycle | Inspection Report (9/9/24) | Inspection Report (9/9/24) | N/A | N/A | N/A | N/A | Rights-of-Way Inspection Record (Frontload Data) | N/A | 14900 | 17900 | 20.1% | Overspend | Additional program development labor on a small base with the objective accomplished. | N/A | N/A
Vegetation Management and Inspections | VM_14 | 8.2.3.8 | Emergency Response Vegetation Management | Non-focus & non-field verifiable | Verify Readiness and Review of Plan | Verification of Readiness and Review of Plan | In Progress | N/A | Reviewed and Updated Procedure | Reviewed and Updated Procedure | Target met | N/A | N/A | N/A | BVES PSPS Procedures Rev. 3 PSPS Exercise Spreadsheet PSPS Post-Season Report 2025 (Frontload Data) | 100% | 29700 | 37700 | 26.9% | Overspend | Higher than normal emergency response volume rather than scope expansion. | Yes | N/A
Vegetation Management and Inspections | VM_15 | 8.2.4 | Vegetation Management Enterprise System | Non-focus & non-field verifiable | Review and Update Procedures | Ongoing Monitoring and Maintenance | In Progress | N/A | Ongoing Monitoring and Maintenance | Ongoing Monitoring and Maintenance | Target met | N/A | N/A | N/A | VM Contract VM Enterprise System ScrnSht (Frontload Data) Three VM Contract Extensions (DR066) | 100% | 22300 | 19700 | -11.7% | Underspend | System objective was completed below the small forecast. | Yes | N/A
Vegetation Management and Inspections | VM_16 | 8.2.5 | Quality Assurance/Quality Control | Non-focus & non-field verifiable | Complete 72 Vegetation Management QA/QC Reviews | 72 | 187 | 187 | 187 | 187 | Target met | N/A | 29 | 100% | Vegetation Management QC Log (Frontload Data) 29 Vegetation QC Records (DR067) | 260% | 52500 | 68800 | 31% | Overspend | QA/QC volume substantially exceeded the target. | Yes | N/A
Vegetation Management and Inspections | VM_17 | 8.2.6 | Open Work Orders | Non-focus & non-field verifiable | Resolve all WOs Within GO95 Timeframe | All Work Orders Resolved Within GO95 Timeframe | In Progress | N/A | 3,280 Completed Work Orders | 3,280 Completed Work Orders | Target met | N/A | N/A | N/A | 2025 Vegetation Management Work Log (Frontload Data) | 100% | 36800 | 46000 | 25% | Overspend | Additional resolution labor with the work reported in progress. | Yes | N/A
Vegetation Management and Inspections | VM_18 | 8.2.7 | Workforce Planning | Non-focus & non-field verifiable | Verify Staffing Level | Staffing Level Verified | In Progress | N/A | Daily Staffing Sample, Executed Contract | Daily Staffing Sample, Executed Contract | Target met | N/A | N/A | N/A | Staffing Example (Week) Vegetation Management Contract Contractor Fully Executed Contract (Frontload Data) | 100% | 6500 | 8600 | 32.3% | Overspend | Additional workforce planning review labor on a small base with the objective met. | Yes | N/A
Vegetation Management and Inspections | VM_19 | 8.2.2.7 | AiDash | Non-focus & non-field verifiable | AIDash Software | N/A | In Progress | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 40000 | 8600 | -78.5% | Underspend | Variance reflects how the fixed annual cost was allocated to the WMP rather than reduced scope. | N/A | N/A
Situational Awareness and Forecasting | SAF_1 | 8.3.2 | Advanced Weather Monitoring and Weather Stations | Focus & non-field verifiable | 100% Ongoing Monitoring and Maintenance | 100% Ongoing Monitoring and Maintenance | In Progress | BVES evaluated that the current 20 weather stations provide satisfactory coverage (with overlap) of the BVES service area. | 20 Weather Stations/ Maintenance Log | 20 Weather Stations/ Maintenance Log | Target met | N/A | N/A | N/A | Weather Station List (Frontload Data) | 100% | 7500 | 57400 | 665.3% | Overspend | Annual maintenance was performed on 20 weather stations with two replacements in 2025, at a labor-and-parts cost well above the small budget. | Yes | N/A
Situational Awareness and Forecasting | SAF_2 | 8.3.3 | Install Fault Indicators | Focus & non-field verifiable | Install Fault Indicators | 0 | N/A | Project Completed in 2023 | 15 Fault Indicators Installed 2025 | 15 Fault Indicators Installed 2025 | Target met | N/A | 15 | 100% | Fault Indicator Installation Log (Frontload Data) 15 Activation Records (DR053) | 100% | 0 | 279000 | 100% | Overspend | This $0-budget initiative reflects $279.0K of prior-year (2023–2024) project work invoiced in 2025 (reported +100%); BVES_DR004 Item 3 confirms the cost was not accrued in 2023 or 2024. As a prior-year carryover against a $0 budget, it is excluded from the >10% count, and the IE carries a lifecycle-cost observation to the synthesis. | N/A | N/A
Situational Awareness and Forecasting | SAF_3 | 8.3.3 | Online Diagnostic System | Non-focus & non-field verifiable | Install Grid Monitoring System on 1 Circuit | 1 | 1 | 1 | 1 | 1 | Target met | N/A | 1 | 100% | EGM Sensor Locations Erwin (Frontload Data) | 100% | 75900 | 72700 | -4.2% | Underspend | N/A | Yes | N/A
Situational Awareness and Forecasting | SAF_4 | 8.3.4.1 | HD ALERTWildfire Cameras | Non-focus & non-field verifiable | Evaluate Need for Additional HD ALERT Cameras | N/A | N/A | BVES evaluated the HD ALERTCalifornia Cameras as providing satisfactory coverage of the BVES service area. | BVES Does Not Install or Perform Maintenance on HD Cameras | BVES Does Not Install or Perform Maintenance on HD Cameras | N/A | N/A | N/A | N/A | BVES Written Response (Frontload Data) | N/A | 0 | 0 | 0% |  | N/A | N/A | N/A
Situational Awareness and Forecasting | SAF_5 | N/A | Weather Forecasting | Non-focus & non-field verifiable | Weather Forecasting | 100% Ongoing Monitoring and Maintenance | In Progress | N/A | Ongoing Monitoring and Maintenance | Ongoing Monitoring and Maintenance | Target met | N/A | N/A | N/A | BVES Written Response (Frontload Data) | 100% | 67500 | 79400 | 17.6% | Overspend | Contracted forecasting costs were higher than initially planned. | Yes | N/A
Situational Awareness and Forecasting | SAF_6 | N/A | Fire Potential Index | Non-focus & non-field verifiable | Fire Potential Index | 100% Ongoing Monitoring and Maintenance | In Progress | N/A | Ongoing Monitoring and Maintenance | Ongoing Monitoring and Maintenance | Target met | N/A | N/A | N/A | BVES Written Response (Frontload Data) | 100% | 50900 | 64800 | 27.3% | Overspend | Contracted costs were higher than initially planned. | Yes | N/A
Situational Awareness and Forecasting | SAF_7 | 8.3.3.1 | GreenGridiSIU | Non-focus & non-field verifiable | GreenGridiSIU | N/A | Qualitative | N/A | 15 Cameras Installed CPUCGG Spreadsheet | 15 Cameras Installed CPUCGG Spreadsheet | Target met | N/A | N/A | N/A | CPUCGG GreenGrid iSIU List (Frontload Data) | 100% | 0 | 0 | 0% |  | N/A | N/A | N/A
Situational Awareness and Forecasting | RMA_1 | 8.3.5.1 | Technosylva Contractor Program | Focus & non-field verifiable | Technosylva Contractor Program | N/A | In Progress | N/A | Contract Executed May 9, 2022/ Option to Extend to 4/26/27 | Contract Executed May 9, 2022/ Option to Extend to 4/26/27 | Target met | N/A | N/A | N/A | Technosylva Fully Executed Contract & Amendment (Frontload Data) | 100% | 84800 | 378400 | 346.2% | Overspend | Additional contracted expense reflects work with the contractor to further develop the Utility Risk Model under the referenced statement of work. | N/A | N/A
Situational Awareness and Forecasting | WMSD_1 | 8.3.3.4 | Evaluating Mitigation Initiatives | Non-focus & non-field verifiable | Evaluating Mitigation Initiatives | N/A | N/A | N/A | 2025 Outage Log/Statement | 2025 Outage Log/Statement | N/A | N/A | N/A | NA | 2025 Outage Log BVES Written Response (Frontload Data) | N/A | 31400 | 41400 | 31.8% | Overspend | Costs were higher than estimated due to more labor hours dedicated to this effort. | N/A | N/A
Emergency Preparedness | EP_1 | 8.4.2.1 | Emergency Preparedness Plan | Non-focus & non-field verifiable | Yearly Review of Emergency Preparedness Plan | Yearly Review by FEMA Six-Step Process Completed by Apr. 2025 | In Progress | Objective Completed | 2025 PSPS Training Exercises and 13 Stakeholder Engagements | 2025 PSPS Training Exercises and 13 Stakeholder Engagements | Target met | N/A | N/A | N/A | BVES ERDP Rev. 2 BVES ERDP Review Written Response PSPS Exercise Spreadsheet (Frontload Data) | 100% | 5000 | 6600 | 32% | Overspend | Plan updates required more hours than estimated on a small ($5K) budget, with all 2025 activities achieved. | Yes | N/A
Emergency Preparedness | EP_2 | 8.4.3.1 | External Collaboration and Coordination | Non-focus & non-field verifiable | Increase Coordination With Community Stakeholders | Meetings with Community Partners and Mutual Aid Groups | In Progress | Objective Completed | 4 Engagement Meetings Completed | 4 Engagement Meetings Completed | Target met | N/A | N/A | N/A | Community Partner Mutual Aid Log (Frontload Data) | 100% | 22700 | 30800 | 35.7% | Overspend | Higher than estimated costs to attend additional Joint IOU workshops and wildfire mitigation conferences. | Yes | N/A
Emergency Preparedness | EP_3 | 8.4.4 | Public Emergency Communication Strategy | Non-focus & non-field verifiable | Develop Communications With Stakeholders and Customers | Review and Evaluate Communication Strategy Two Times per Year | In Progress | Quarterly Revisions | Reviewed and Evaluated Communication Strategy | Reviewed and Evaluated Communication Strategy | Target met | N/A | N/A | N/A | PSPS Exercise Spreadsheet (Frontload Data) | 100% | 4400 | 5900 | 34.1% | Overspend | More labor hours than estimated on a small ($4.4K) budget, with additional hours arising from the unplanned SCE PSPS event (BVES_DR004 Item 11) and all 2025 activities achieved. | Yes | N/A
Emergency Preparedness | EP_4 | 8.4.5.1 | Preparedness & Planning for Service Restoration | Non-focus & non-field verifiable | Update Service Restoration Plan with Operations | Update Service Restoration Plan with Operations Group by June 2025 | In Progress | Update on March 5, 2025 | 2025 PSPS Stakeholder Engagements | 2025 PSPS Stakeholder Engagements | Target not met | In the 2025 EC AIR, BVES states that lessons learned from these two training exercises were incorporated into the March 5, 2025, update of the Service Restoration Plan; however, these events did not take place until June 2025, thus presenting a discrepancy. No other event or exercise listed in the frontload data provided was conducted prior to June 2025. BVES did not provide a copy of the updated Service Restoration Plan. | N/A | N/A | PSPS Exercise Spreadsheet (Frontload Data) | 0% | 6000 | 7900 | 31.7% | Overspend | More annual review and lessons-learned update hours than estimated, with increased BVES labor cost, on a small ($6K) budget. | No | Did not meet target goal thus not achieving risk reduction goal.
Emergency Preparedness | EP_5 | 8.4.6 | Customer Support in Wildfire & PSPS Emergencies | Non-focus & non-field verifiable | Customer Support in Wildfire & PSPS Emergencies | Yearly Review and Evaluate PSPS Program Completed by April 2025 | In Progress | Objective Completed | 2025 PSPS Pre-Season Report | 2025 PSPS Pre-Season Report | Target not met | The documentation provided by BVES indicates that the PSPS Pre-Season Report was submitted to the CPUC on July 1, 2025, approximately three months after the required completion date. | N/A | N/A | Pre-Season Report Correspondence Pre-Season Tables Pre-Season Report (Frontload Data) | 0% | 3700 | 4800 | 29.7% | Overspend | More procedure review and update hours than estimated, with increased BVES labor cost, on a small ($3.7K) budget. | No | Did not submit pre-season report to CPUC untal after the required completion date.
Community Outreach and Engagement | COE_1 | 8.5.2 | Public Outreach & Education Awareness Program | Non-focus & non-field verifiable | Complete 360 Public Outreach & Education Events | 360 | 1184 | 1184 | 1184 | 1184 | Target met | N/A | 34 | 100% | WMP PSPS Outreach Tracking Log (Frontload Data) 34 Outreach Records (DR006) | 329% | 95500 | 131100 | 37.3% | Overspend | Higher advertising and contracted public relations costs and to additional outreach hours during the unplanned SCE PSPS event, with the program completed. | Yes | N/A
Community Outreach and Engagement | COE_2 | 8.5.1.2 | Engagement with Access and Functional Needs Populations | Non-focus & non-field verifiable | Verify and Evaluate 12 AFN Customer Needs | 12 | 26 | 26 | 24 | 24 | Target met | N/A | 15 | 100% | AFN Email Correspondence WMP PSPS Outreach Tracking Log (Frontload Data) | 200% | 31800 | 41600 | 30.8% | Overspend | higher advertising and contracted public-relations costs and to additional AFN engagement hours during the unplanned SCE PSPS event, with the activities completed. | Yes | N/A
Community Outreach and Engagement | COE_3 | 8.5.4 | Collaboration on Local Wildfire Mitigation Planning | Non-focus & non-field verifiable | Collaborate with Communication on Local Wildfire Mitigation Planning | Review and Maintain Program | Objective Completed | Objective Completed | 6 Engagements Throughout 2025 with Local Stakeholders | 6 Engagements Throughout 2025 with Local Stakeholders | Target met | N/A | N/A | N/A | Local Fire Mitigation Collaboration Log (Frontload Data) | 100% | 24000 | 30500 | 27.1% | Overspend | Additional collaboration conferences and meetings on a small ($24K) budget, with the 2025 activities achieved. | Yes | N/A
Community Outreach and Engagement | COE_4 | 8.5.5 | Best Practive Sharing with Other Utilities | Non-focus & non-field verifiable | Conduct 15 Work Groups and Conferences | 15 | 125 | 125 | 121 | 121 | Target met | N/A | 27 | 93% | Nonlocal Fire Mitigation Collaboration Log (Frontload Data) 25 Event Records (DR009) | 750% | 15700 | 20700 | 31.8% | Overspend | Additional best-practice conferences and meetings on a small ($15.7K) budget, with the 2025 activities achieved. | Yes | N/A
Note on K11: Number of "actuals" from which samples are selected

## Tab 3 - Data Requests
Data Requests
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Bear Valley Electric Service
Date Sent | Date Response Received | Section / Initiative | Data Request Number | List of Documents Received
2026-02-19 | 2026-03-13 | All | Frontload Request | Initial Verification Documentation for All Initiatives (.docx; .xlsx; .pdf; .gdb)
2026-02-19 | 2026-02-25 | EOY Financials | DR001 | DR001_WMP 2025 Initiative Costs 2025-1.xlsx
2026-03-24 | 2026-03-27 | Circuit Mileage & HFTD GD_25; 26; 27; 28; 29; 30; VM_1; 2; 3; 4; 5 GD_31; 32; 35; VM_6; 11; 16 | DR002 | Circuit Mileage by Circuit.xlsx HFTD Confirmation.docx Portal Access Confirmation.docx
2026-03-30 | 2026-04-02 | GD_25; 26; 27; 28; 29; VM_1; 2; 3; 4; 5 | DR003 | BVES_DR003 HFTD Breakdown 03.30.26.xlsx
2026-04-02 | 2026-04-17 | COE_1 | DR006 | Audit WMP PSPS Ads.xlsx
2026-04-02 | 2026-04-17 | COE_2 | DR007 | AFN Sampling Confirmation 2025.xlsx
2026-04-02 | 2026-04-17 | COE_4 | DR009 | Data for 25 Meetings (i.e., agendas, presentation information, etc.) Wildfire Collab Agendas 2025.xlsx
2026-04-02 | No Addt'l Data | GD_25 | DR030
2026-04-02 | 2026-04-17 | GD_26 | DR031 | Substation Inspections 2025.xlsx BASE: Circuit Inspection Records (14 Circuits) ALTERNATE: Circuit Inspection Records (4 Circuits)
2026-04-02 | Resource Keeper | GD_27 | DR032
2026-04-02 | Resource Keeper | GD_28 | DR033
2026-04-02 | No Addt'l Data | GD_29 | DR034
2026-04-02 | No Addt'l Data | GD_30 | DR035
2026-04-02 | No Addt'l Data | GD_31 | DR036
2026-04-02 | 2026-04-17 | GD_32 | DR037 | BASE: BVES Substation Inspection Sheets (27) ALTERNATE: BVES Substation Inspection Sheets (7)
2026-04-02 | 2026-04-17 | GD_35 | DR041 | QC Assessment.xlsx BASE: BVES Overhead Distribution and Transmission Plans (13 Locations) ALTERNATE: BVES Overhead Distribution and Transmission Plans (4 Locations)
2026-04-02 | No Addt'l Data | VM_1 | DR060
2026-04-02 | 2026-04-17 | VM_11 | DR062 | Devensible Space 2.xlsx Weed Abatement Reports (11)
2026-04-02 | 2026-04-17 | VM_16 | DR067 | BASE: Tree Trimming QC Reports (29) ALTERNATE: Tree Trimming QC Reports (8)
2026-04-02 | 2026-04-17 | VM_2 | DR071 | BVES Circuit Inspection Records (22)
2026-04-02 | Resource Keeper | VM_3 | DR072
2026-04-02 | No Addt'l Data | VM_4 | DR073
2026-04-02 | No Addt'l Data | VM_5 | DR074
2026-04-02 | 2026-04-17 | VM_6 | DR075 | BASE: BVES Substation Inspection Sheets (30) ALTERNATE: BVES Substation Inspection Sheets (7)
2026-04-02 | 2026-04-10 | VM_9 | DR078 | 2025 VM_9 Work.xlsx VM_9 Completed Clearance Spreadsheet.xlsx
2026-04-13 | QDR Provided | VM_9 | DR078.b | BVES_DR078.b_VM9.xlsx VM-VFM-09 Sampling Attachment.xlsx
2026-04-13 | 2016-04-15 | GD_14 | DR020 | Fire Wrap Clarification.docx
2026-04-13 | 2016-04-15 | GD_15 | DR021 | Cap Bank Discrepancy Clarification.docx
2026-04-13 | 2016-04-15 | GD_6 | DR049 | Trip Saver 2025_v2.xlsx Trip Saver Clarification.docx
2026-04-13 | 2016-04-15 | VM_10 | DR061 | 2025 Removal List copy.xlsx
2026-04-14 | 2026-04-17 | GD_22 | DR027 | BVES Storage Building-Floorplan Rev.2 12-10-25 estimate BVES megal enclosure.pdf IMG_0749.JPG IMG_0750.JPG Maltby Switchgear Enclosure.docx
2026-04-14 | 2026-04-17 | RMA_1 | DR051 | C#3234-0021 Amendment 2 REDLINED-FULLY EXECUTED
2026-04-14 | 2026-04-17 | SAF_1 | DR052 | WeatherStationMaintLog (002).xlsx
2026-04-14 | 2026-04-17 | VM_18 | DR069 | C#3569-000 Agreement-FULLY EXECUTED
2026-04-17 | 2026-04-29 | GD_1 | DR015 | DR015.xlsx
2026-04-17 | 2026-04-22 | GD_6 | DR049.b | DR049.b_Fire Wrap 2025_v2.xlsx Fire Wrap Discrepancy.docx
2026-04-22 | 2026-05-01 | Financials | DR004 | 2xweatherunits2025 2024-07-22_BVES_2025_WMP_R2 BVES_DR004_Financial Response.xlsx CAPEX UWC April 2025 C#3315-AiDash-SAAS Veg Mgmt: (1) Invoice, (1) Contract C#3412-Davey Resource Group-LiDAR: (2) Invoices, (1) Contract C#3416 Alamon-Ground Patrol: (3) Invoices, (1) Contract Direxyon: Bear Valley-Phase 2 Statement of Work_2024-11-06 Hampton Tedder 3rd Party QC Invoices: (2) Invoices
2026-04-22 | Void | QAQC Program | DR005
2026-04-24 | 2026-04-24 | QAQC Program | DR005.b | BVES_DR005_QAQC Questionnaire.docx Specific QAQC Procedural Documents (68)
2026-04-24 | 2026-04-29 | GD_1 | DR015.b | AS-BUILT-DESIGN SAMPLES Covered Conductor No Designs.docx
2026-05-05 | 2026-05-08 | GD_25 Financials | DR004.b | GD_23 Not on AIR.docx
2026-05-05 | 2026-05-08 | GD_8 | DR050 | Plan/Material Sheets for Covered Wire Program Pole Changes (16)
2026-05-13 | 2026-05-19 | SAF_2 | DR053 | 12024BV.JPG 12367BV.JPG 15137BV.JPG 16074BV.JPG
2026-05-13 | 2026-05-19 | VM_7 | DR076 | BVES INC VM and QC Programs Policy and Procedures Rev2
2026-05-13 | 2026-05-19 | VM_15 | DR066 | C#3315-000 FINAL REVISED INC ALL ADDENDUMS AND TERMS-FULLY EXECUTED C#3315-001 Amend 1 - FULLY EXECUTED c#3315-002 Amend 2 Rev 2-For Signature_FULLY EXECUTED
2026-05-15 | 2026-05-19 | GD_1 | DR015.c | Boulder Baldwin CC Install.docx

## Tab 4 - SME Interviews
SME Interviews
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Bear Valley Electric Service
Interview date | Section / Initiative | SME interview number | Positions interviewed | Summary of interview