## Tab 1 - Overview tab
IE AIR Attachments
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Southern California Edison
Legends
Tab 1 | Overview Tab - Instructions and overview
Tab 2 | Catalog of Initiatives - Initiative review and funding compliance of all initiatives
Tab 3 | Data Requests - Comprehensive list of documents reviewed
Tab 4 | SME Interviews - Summary of interviews conducted

## Tab 2 - Catalog of Initiatives
Catalog of Initiatives
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Southern California Edison
WMP Category | Initiative Tracking ID | WMP Section Number | Initiative Name | Initiative Type | WMP - Initiative Description | WMP - Initiative Target | EC-Claimed Progress (Q4 QDR) | EC-Claimed Progress (EC AIR) | EC-Claimed Progress (DR) | IE Declared Actual | EC-Claimed Initiative Status | Target Not Met - Rationale | Sample Size (#) | Sample Validation Rate (%) | Verification Method | IE Declared Initiative Completion Percent (%) | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%) | Funding discrepancy - finding | Funding discrepancy - detail | Satisfied Risk Reduction Goal - finding | Satisfied Risk Reduction Goal - detail
Grid Design Operations and Maintenance | IN-1.1 | 8.1.3.1 | Distribution High Fire Risk - Informed (HFRI) Inspections & Remediations (Ground & Aerial) | Focus & non-field verifiable | Inspect 187,000 Structures | 187000 | 280783 | 460222 | 228083 | 228083 | Target met | N/A | 138 | 50% | Distribution Ground & Aerial Inspection List (Frontload Data) SCE Written Response 138 Inspection Records (DR010) | 61% | 35256000 | 41818000 | 18.6% | Overspend | 2025 forecasted budget, and following the GRC filing, SCE revised the Operations and Maintenance (O&M) budget associated with the initiative. | No | Did not meet target goal and was unable to confirm if risk reduction goal was met.
Grid Design Operations and Maintenance | IN-1.2 | 8.1.3.2 | Transmission High Fire Risk - Informed (HFRI) Inspections & Remediations (Ground & Aerial) | Focus & non-field verifiable | Inspect 24,500 Structures | 24500 | 33886 | 67457 | 31365 | 31365 | Target not met | The sampling data provided by SCE can be verified for evidence of completed work; however, no inspection report criteria, methodology, or defined inspection parameters were provided for IE review. As a result, the IE was unable to confirm whether the submitted inspection documentation was consistent with SCE’s established inspection documentation standards or whether the inspections were performed in accordance with defined program requirements. | 138 | 50% | Transmission Ground & Aerial Inspection List (Frontload Data) SCE Written Response 138 Inspection Records (DR011) | 64% | 16246000 | 12858000 | -20.9% | Underspend | Approximately 81% of the underspend was attributable to operational efficiency gains, while the remaining 19% was associated with increased usage of T360 inspections, neither of which negatively affected the intended wildfire risk reduction outcomes. | No | Did not meet target goal and was unable to confirm if risk reduction goal was met.
Grid Design Operations and Maintenance | IN-3 | 8.1.3.5 | Infrared Inspection of Energized Overhead Distribution Facilities & Equipment | Non-focus & non-field verifiable | Inspect 5,300 Circuit Miles | 5300 | 5636 | 5636.34 | 5363 | 5363 | Target met | N/A | 34 | 100% | Distribution Infrared Inspection List (Frontload Data) 34 Circuit Miles of Inspection Records Map Package (.mpk) (DR012) | 106% | 476000 | 606000 | 27.3% | Overspend | Conservative budgeting assumptions related to uncertainty surrounding the timing and availability of the Major Sporting Events (MSE) memorandum account when the revised budget was developed. | Yes | N/A
Grid Design Operations and Maintenance | IN-4 | 8.1.3.6 | Infrared Inspection, Corona Scanning, and High-Definition Imagery of Energized Overhead Transmission Facilities & Equipment | Non-focus & non-field verifiable | Inspect 1,000 Circuit Miles | 1000 | 1052 | 1051.7 | 1051.7 | 1051.7 | Target met | N/A | 34 | 100% | Infrared Corona HD Inspection List (Frontload Data) 34 Circuit Miles of Inspection Records (DR013) | 105% | 105000 | 211000 | 101% | Overspend | Increased aircraft operation costs, additional transmission circuits flown to ensure full HFRA coverage, and unanticipated engineering review contract expenses. | Yes | N/A
Grid Design Operations and Maintenance | IN-5 | 8.1.3.7 | Generation High Fire Risk - Informed Inspections & Remediation | Non-focus & non-field verifiable | Perform 170 Generation Related Inspections | 170 | 238 | 238 | 238 | 238 | Target met | N/A | 30 | 70% | Generation Inspections List (Frontload Data) 30 Inspection Records (DR014) | 98% | 280000 | 69000 | -75.4% | Underspend | Although inspections identified a higher number of remediation notifications, most findings were lower priority and addressed through an established multi-year remediation cadence, resulting in lower overall costs. | Yes | N/A
Grid Design Operations and Maintenance | IN-8 | 8.1.5 | Inspection & Maintenance Tools | Focus & non-field verifiable | Monitor Utilization of Inspection Work Management Tool | Monitor Utilization of Inspection Work Management Tool, and Make Enhancements as Necessary | Activity year-end target will not be met due to extended work on system execution plan, system engineering specifications, and additional quality verifications. | Target Not Met | N/A | N/A | Target not met | Utilization was not monitored in 2025 therefore there is no substantiating data for utilization in 2025. | N/A | N/A | Inspection & Maintenance Tools Response | 0% | 3130000 | 13181000 | 321.1% | Overspend | Expanded InspectForce scope, including integration of Distribution Ground, survey redesigns based on field feedback, and continued operational support for both InspectApp and InspectForce during the transition to Salesforce Field Service Mobile. | N/A | N/A
Grid Design Operations and Maintenance | IN-9a | 8.1.3.8 | Transmission Conductor & Splice Assessment: Spans with LineVue | Non-focus & non-field verifiable | Transmission Conductor & Splice Assessment: Spans with LineVue | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2023-2025 WMP 2025 WMP Update | N/A | 1793000 | 9000 | -99.5% | Underspend | SCE stated that it is discontinuing its Transmission Conductor Span Assessment initiative (IN-9a) due to its zero percent find rate in 2023 and 2024 as well as the cost and complexity of performing these inspections. SCE obtained approval from Energy Safety to discontinue IN-9 through the 2025 WMP update. | N/A | N/A
Grid Design Operations and Maintenance | IN-9b | 8.1.3.8 | Transmission Conductor & Splice Assessment: Splices with X-Ray | Non-focus & non-field verifiable | Transmission Conductor & Splice Assessment: Splices with X-Ray | TBD Based on Engineering Analysis performed in 2023/2024 | Completed | SCE's engineering analysis and lessons learned showed that x-rays were leading to a high rate of shunting remediation. Accordingly, SCE started foregoing x-ray inspections and proactively shunting Transmission splices in 2025 | 117 Shunt Installations | 117 Shunt Installations | Target not met | The data provided by SCE and the statement in the 2025 EC AIR can be verified for evidence of completed shunt installations and documented results of the completed engineering analysis. However, no documentation was provided demonstrating implementation of X-Ray Inspections, an initiative parameter explicitly required by Section 8.1.3.8 of the WMP. | N/A | N/A | Transmission Conductor & Splice Assessment List (Frontload Data) | 0% | 543000 | 0 | -100% | Underspend | SCE stated that it is discontinuing its Transmission Conductor Span Assessment initiative (IN-9) due to its zero percent find rate in 2023 and 2024 as well as the cost and complexity of performing these inspections. SCE obtained approval from Energy Safety to discontinue IN-9 through the 2025 WMP update. | N/A | N/A
Grid Design Operations and Maintenance | SH-1 | 8.1.2.1.1 | Covered Conductor | Focus & field verifiable | Complete 500 Circuit Miles of Covered Conductor | 500 | 710.42 | 706 | 706 | 706 | Target met | N/A | 116 Asset Points | 100% | Field Evaluation As-Builts (DR025/.b) | 141% | 490874000 | 598285000 | 21.9% | Overspend | Completion of 63 additional circuit miles due to favorable weather conditions, resulting in approximately $44 million in additional costs. SCE also reported approximately $43 million in increased cost per mile associated with higher helicopter usage, exception-time activities, contractor spending, and related overhead costs required to perform work in rugged terrain and support aerial operations and pole replacements. An additional approximately $21 million was attributed to rollover and trailing costs from prior-year work. | Yes | N/A
Grid Design Operations and Maintenance | SH-2 | 8.1.2.2.1 | Undergrounding Overhead Conductor | Focus & field verifiable | Complete 30 Circuit Miles | 30 | 45.37 | 45 | 45 | 45 | Target met | N/A | 125 Asset Points | 100% | Field Evaluation As-Builts (DR031/.b) | 150% | 317078000 | 127297000 | -59.9% | Underspend | Implementation of a cost-efficiency plan that refined targeted undergrounding construction standards, resulting in savings related to design, materials, and system-hardening efficiencies. The underrun was also impacted by the CPUC ultimately authorizing fewer planned miles than originally forecasted in SCE’s GRC filing. | Yes | N/A
Grid Design Operations and Maintenance | SH-5 | 8.1.2.8.1 | Remote Controlled Automatic Reclosers Settings Update | Non-focus & non-field verifiable | Install 5 RAR/RCS Sectionalizing Devices | 5 | 13 | 13 | 13 | 13 | Target met | N/A | 13 | 100% | RAR/RCS Sectionalizing Devices Install List (Frontload Data) 13 RAR/RCS Install Records (DR032) | 260% | 7201000 | 2732000 | -62.1% | Underspend | Actual RAR installation volumes in 2025 were lower than forecasted due to fewer PSPS-impacted circuits than originally assumed when the budget was developed using historical installation averages. | Yes | N/A
Grid Design Operations and Maintenance | SH-8 | 8.3.3.1.2.1 | Transmission Open Phase Detection | Non-focus & non-field verifiable | Transmission Open Phase Detection | TBD | TOPD logic installed at 7 locations. | TOPD logic installed at 7 locations. | 17 Records (7 Circuits)/ Screenshots for 7 Circuits | 17 Records (7 Circuits)/ Screenshots for 7 Circuits | Target met | N/A | 7 | 100% | Transmission Open Phase Detection Install List (Frontload Data) SCE Written Response TOPD Broken Conductor Data (DR033) | 100% | 0 | 334000 | 100% | Overspend | SCE originally expected the Transmission Open Phase Detection (TOPD) program to conclude by the end of 2024 and therefore did not budget for 2025 activities. Following further evaluation, SCE implemented enhanced higher-sensitivity software logic upgrades across TOPD locations in HFRA to improve detection performance and reduce false operations. | N/A | N/A
Grid Design Operations and Maintenance | SH-10 | 8.1.2.3.1 | Tree Attachments Remediation | Focus & non-field verifiable | Tree Attachments Remediation | 141 | Delayed | 34 | 34 | 34 | Target not met | SCE completed the 34 tree remediations claimed in the 2025 EC AIR - shortfall of 107 remediations and therefore missing the 141 remediation target. | 27 | 100% | Tree Attachment Remediation List (Frontload Data) 27 Tree Attachment Records (DR026) | 24% | 10570000 | 1843000 | -82.6% | Underspend | Tree Attachment projects were delayed by weather, permitting, and execution constraints, including pending approvals from the National Park Service, Caltrans, and the U.S. Forest Service, seasonal access restrictions in Sequoia National Park, potential delays related to planned park housing development, and limited Caltrans staffing for application processing. | No | Did not meet target goal and was unable to confirm if risk reduction goal was met.
Grid Design Operations and Maintenance | SH-14 | 8.1.2.5.2 | Long Span Initiative (LSI) | Focus & field verifiable | Remediate 1,000 Individual Spans | 1000 | 1102 | 1102 | 1102 | 1102 | Target met | N/A | 123 | 100% | Field Evaluation Geodatabase File (DR001) | 110% | 8499000 | 2409000 | -71.7% | Underspend | actual line spacer installation costs were lower than the revised budget due to efficiency gains from bundling work activities, which reduced repeat crew dispatches. | Yes | N/A
Grid Design Operations and Maintenance | SH-16 | 8.1.2.1.2 | Vibration Damper Retrofit | Non-focus & non-field verifiable | Complete 600 Structures | 600 | 731 | 725 | 725 | 725 | Target met | N/A | 33 | 100% | Field Evaluation Geodatabase File (DR001) | 121% | 244000 | 534000 | -318.9% | Underspend | Accounting issue in which approximately $0.818 million in Vibration Damper costs were recorded under Distribution capital preventative maintenance (IN-1.1) rather than this activity. | Yes | N/A
Grid Design Operations and Maintenance | SH-17 | 8.1.2.6.1 | Rapid Earth Current Limiters (REFCL)(Ground Fault Neutralizer [GFN]) | Non-focus & non-field verifiable | Compoete GFN Construction at 2 Substations | 2 | 4 | 4 | 4 | 4 | Target met | N/A | 4 | 100% | Field Evaluation Construction Photos (Frontload Data / DR029) | 200% | 40340000 | 44323000 | 9.9% | Overspend | N/A | Yes | N/A
Grid Design Operations and Maintenance | SH-18 | 8.1.2.6.2 | Rapid Earth Current Limiters (REFCL) - Grounding Conversion | Non-focus & non-field verifiable | Complete 4 Grounding Conversions | 4 | 3 | 3 | 3 | 3 | Target not met | The data supports SCE’s reported completion of the three (3) claimed grounding conversions under the SH-18 initiative, however, falling one short of the 2025 completion goal of four. | 3 | 100% | Field Evaluation Construction Photos (Frontload Data / DR030/.b) | 75% | 5956000 | 1283000 | -78.5% | Underspend | Several grounding conversion projects were delayed by easement access issues, rights checks, environmental clearances, and pending government approvals. O&M costs were also below budget because few equipment events required investigation and minimal maintenance was needed for the newly installed equipment. | N/A | N/A
Vegetation Management and Inspections | VM-1 | 8.2.3.4.1 | Hazard Tree Mitigation Program (HTMP) | Focus & field verifiable | Inspect and Mitigate 440 Grids/Circuits | 440 | 526 | 526 | 526 | 526 | Target met | N/A | 110 | 100% | Field Evaluation Geodatabase File (DR001) | 120% | 44037000 | 11919000 | -72.9% | Underspend | Fewer hazard tree conditions identified on inspected HFRA circuits than forecasted, resulting in lower mitigation volumes, as well as lower than anticipated participation in the HTMP Property Owner Incentives program. | Yes | N/A
Vegetation Management and Inspections | VM-2 | 8.2.3.1.1 | Structure Brushing | Focus & non-field verifiable | Inspect and Clear 63,700 Structures | 63700 | 157691 | 157665 | 157665 | 157665 | Target met | NA | 138 | 87% | Structure Brushing List (Frontload Data) 138 Brushing Records (DR036) | 215% | 26197000 | 24437000 | -6.7% | Underspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM-3 | 8.2.3.3.2 | Expanded Clearances for Generation Legacy Facilities | Non-focus & non-field verifiable | Inspect and Clear 48 Sites | 48 | 63 | 63 | 63 | 63 | Target met | N/A | 23 | 100% | Expanded Clearance for Legacy Facilities List (Frontload Data) 23 Site Records (DR037) | 131% | 450000 | 414000 | -8% | Underspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM-4 | 8.2.3.4.2 | Dead & Dying Tree Removal | Focus & field verifiable | Inspect and Mitigate 536 Grids/Circuits | 536 | 600 | 600 | 600 | 600 | Target met | N/A | 113 | 100% | Field Evaluation Geodatabase File (DR001) | 112% | 28686000 | 7433000 | -74.1% | Underspend | Lower-than-expected tree removal volumes, as approximately 4,000 trees were remediated compared to the forecasted 8,600 trees, resulting in lower overall costs. | Yes | N/A
Vegetation Management and Inspections | VM-6 | N/A | Vegetation Management Work Management Tools (Arbora) | Non-focus & non-field verifiable | Monitor stabilization of Arbora and continue execution of plan to enable additional VM maintenance programs. | Monitor stabilization of Arbora and continue execution of plan to enable additional VM maintenance programs. | Complete | Complete | VM-6 YE Evidence | Complete | Target met | N/A | N/A | N/A | Arbora Work Management Tool (SAD & SES) (Frontload Data) | 100% | 6637000 | 4507000 | -32.1% | Underspend | Removal of iPad-related O&M costs from the Arbora project after those costs were disallowed under the 2022 WM/VM decision. | N/A | N/A
Vegetation Management and Inspections | VM-7 | 8.2.3.3.1 | Detailed Inspections for the Prescription, Where Necessary and Feasible, of Expanded Vegetation Clearances from Distribution Lines in HFRA | Focus & non-field verifiable | Inspect 770 Distribution Grids/Circuits | 770 | 789 | 789 | 785 | 785 | Target met | N/A | 118 | 100% | Vegetation Detailed Inspections List (Frontload Data) SCE Written Response 118 Inspection Records (DR040) | 93% | 224988000 | 204737000 | -9% | Underspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM-8 | 8.2.3.3.1 | Detailed Inspections for the Prescription, Where Necessary and Feasible, of Expanded Vegetation Clearances from Transmission Lines in HFRA | Focus & non-field verifiable | Inspect 416 Transmission Grids/Circuits | 416 | 448 | 448 | 443 | 443 | Target met | N/A | 106 | 100% | Vegetation Detailed Inspections List (Frontload Data) SCE Written Response 106 Inspection Records (DR041) | 108% | 20956000 | 13120000 | -37.4% | Underspend | Increased execution efficiency, which reduced Time & Equipment (T&E) costs, including contractor travel, lodging, per diem, and other reimbursable expenses associated with line clearing activities, while remaining aligned with the authorized GRC revenue requirement. | Yes | N/A
Vegetation Management and Inspections | VM-9 | 8.2.2.4 | LiDAR Distribution Vegetation Inspections | Non-focus & non-field verifiable | Conduct 1,020 Circuit Miles of Inspections | 1020 | 4032 | 4031.75 | 4031.75 | 4031.75 | Target met | N/A | 34 | 50% | LiDAR Vegetation Inspections List Distribution (Frontload Data) 34 Circuit Miles of Inspection Records (DR042) | 198% | 44467000 | 17615000 | -60.4% | Underspend | Reduced scope of work due to limited vendor availability during Q1-Q2 2025 while SCE finalized a new RFP process, along with lower contractor rates implemented under new vendor contracts in mid-2025. | N/A | N/A
Vegetation Management and Inspections | VM-10 | 8.2.2.4 | LiDAR Transmission Vegetation Inspections | Non-focus & non-field verifiable | Conduct 1,750 Circuit Miles of Inspections | 1750 | 2182 | 2179.17 | 2179.17 | 2179.17 | Target not met | SCE did not provide the requested documentation: inspection reports, associated photos, and work/repair orders. SCE should submit inspection reports detailing findings, conditions, and remediations, not simply completion records. | 34 | 50% | LiDAR Vegetation Inspections List Transmission (Frontload Data) 34 Circuit Miles of Inspection Records (DR043) | 62% | 11132000 | 9918000 | -10.9% | Underspend | Reduced scope of work due to limited vendor availability during Q1-Q2 2025 while SCE finalized a new RFP process, along with lower contractor rates implemented under new vendor contracts in mid-2025. | N/A | N/A
Situational Awareness and Forecasting | SA-1 | 8.3.2.1.1 | Weather Stations | Focus & non-field verifiable | Install 15 Weather Stations | 15 | 202 | 202 | 202 | 202 | Target met | N/A | 82 | 100% | Weather Station Installations List (Frontload Data) SCE Written Response 82 Weather Station Records (DR020) | 1347% | 6398000 | 9670000 | 51.1% | Overspend | Higher recurring costs associated with SCE’s expanded weather station network following the January 2025 Southern California wildfires and increased contractor-related expenses for calibration, maintenance, and ongoing support exceeded original forecasts without negatively affecting intended wildfire risk reduction outcomes. | Yes | N/A
Situational Awareness and Forecasting | SA-3 | 8.3.5 | Weather & Fuels Modeling | Non-focus & non-field verifiable | Implement Machine Learning at Remaining Weather Stations Locations | Implement machine learning at remaining weather station locations that meet eligible criteria. | SCE met target to operationalize machine learning at selected locations by sending the forecast output daily with other weather model outputs. | SCE met target to implement machine learning at remaining weather station locations by sending the forecast output daily with other weather model outputs. | Machine Learning Implemented at 171 Weather Station Locations | 171 | Target met | N/A | N/A | N/A | Weather & Fuels Modeling List (Frontload Data) | 100% | 8027000 | 13877000 | 72.9% | Overspend | Higher-than-planned capital and O&M costs associated with development and support of the cloud-based High-Powered Computer Clusters (HPCC) platform. Expanded forecasting capabilities from 3 to 7 days required additional computational power, increased cloud solution development costs, and higher licensing and support expenses for the Technosylva modeling platform. | Yes | N/A
Situational Awareness and Forecasting | SA-8 | 8.3.2.1.2 | Fire Spread Modeling | Non-focus & non-field verifiable | Recommend How Consequence Metrics Can Be Used for PSPS Decisions Making | Provide recommendation for how consequence metrics can be used for PSPS decision making. | SCE met target. SCE benchmarked consequence metrics against real-time events. SCE will continue to use model for the In-Event Risk Calculator and be used as an additional data point. | SCE met target. SCE benchmarked consequence metrics against real-time events. SCE will continue to use model for the In-Event Risk Calculator and be used as an additional data point. | Recommendation Provided | Recommendation Provided | Target met | N/A | N/A | N/A | Fire Science Enhancements Recommendation | 100% | 3287000 | 2491000 | -34.9% | Underspend | Deferral of climate change modeling and the SOMS project from 2025 to 2026, along with lower-than-expected Fuel Sampling Program costs due to fewer sampling locations and reduced labor hours. | Yes | N/A
Situational Awareness and Forecasting | SA-10 | 8.3.4.1.1 | High Definition (HD) Cameras | Non-focus & non-field verifiable | Install HD Cameras | None Planned - installs will be based on reassessment in 2024. | 2 | 2 Cameras Relocated | 2 | 2 | Target met | N/A | 2 | 100% | HD Cameras Reassessment HD Cameras Relocations (Frontload Data) Operational ScrnShts (DR026) | 100% | 4665000 | 3618000 | -22.4% | Underspend | Administrative delays by UCSD postponing installation of 10 planned HD camera sites from 2025 to 2026. | N/A | N/A
Situational Awareness and Forecasting | SA-11 | 8.3.3.1.1 | Early Fault Detection (EFD) | Focus & non-field verifiable | Install 200 EFDs | 200 | 204 | 200 | 200 | 200 | Target met | N/A | 83 | 100% | Early Fault Detection Install List (Frontload Data) 83 Inspection Records (JIS & GIS) (DR027) | 100% | 12644000 | 8619000 | -31.8% | Underspend | Capital budget was based on a higher installation target of 300 units, while the compliance WMP target was 200 installs, which SCE achieved. Additionally, O&M costs were lower than forecasted because few sensor events required investigation or dispatch of field crews. | Yes | N/A
Emergency Preparedness | DEP-2 | 8.4.2.2.1 | SCE Emergency Response Training | Non-focus & non-field verifiable | Ensure that PSPS Response Teams are Fully Qualified/Re-Qualified by July 1 Annually | PSPS response teams are fully qualified/requalified by 07/01 annually to maintain readiness. | PSPS training and exercise requalification series is complete. | SCE met target. 2025 PSPS Training and Requalification Series is complete. | SCE Emergency Response Training (159 Employees) | SCE Emergency Response Training (159 Employees) | Target met | N/A | N/A | N/A | Emergency Response Training List (Frontload Data) | 114% | 1193000 | 68000 | -94.3% | Underspend | SCE met its annual qualification target for emergency response training at the revised number of 139 employees trained, which contributed to a 94% underrun for the initiative. | N/A | N/A
Emergency Preparedness | DEP-5 | 8.4.3.3.1 | Aerial Suppression | Non-focus & non-field verifiable | Reassess Availability and Funding for Aerial Suppression Resources in Service Area | SCE will continue to reassess availability and funding for aerial suppression resources in SCE's service area annually to determine QRF strategy. | Contracts were issued at the end of 2024, and final payment was provided to the agencies in January 2025. | Contracts were issued at the end of 2024, and final payment was provided to the agencies in January 2025. | Ventura County, Orange County, Los Angeles County | Complete | Target met | N/A | N/A | N/A | Aerial Suppression Agreements (LA, OC, Ventura) Payments (Frontload Data) | 100% | 35000000 | 36902000 | 5.4% | Overspend | N/A | Yes | N/A
Emergency Preparedness | PSPS-2 | 8.4.6.2 | Customer Care Program (Critical Care Backup Battery)(CCBB) Program) | Non-focus & non-field verifiable | Complete 85% Battery Deliveries Within 30 Days | 85% Battery Deliveries Completed Within 30 Days | 100% of the eligible customers who enrolled in the CCBB program received their batteries within 30 days. | 100% of the eligible customers who enrolled in the CCBB program received their batteries within 30 days. | 7,640 Deliveries (92% Within 30 Days) | 7,640 Deliveries (92% Within 30 Days) | Target met | N/A | 34 | 100% | Critical Care Backup Battery List (Frontload Data) SCE Written Response 34 Battery Records (DR024) | 100% | 8670000 | 7572000 | -12.7% | Underspend | Cost savings achieved from transitioning to smaller battery sizes in 2025. | Yes | N/A
Emergency Preparedness | PSPS-3 | 8.4.6.3 | Customer Care Program (Portable Power Station and Generation or Rebates) | Non-focus & non-field verifiable | Process 85% Rebate Claims Within 30 Days | 85% Rebate Claims Processed Within 30 Days | 100% success rate was achieved in paying all claims within the target of 30 days. | 100% success rate was achieved in paying all claims within the target of 30 days. | 6,263 Rebates (100% Within 30 Days) | 6,263 Rebates (100% Within 30 Days) | Target met | N/A | 34 | 100% | Portable Power Station & Generator Rebates List (Frontload Data) 34 Rebate Records (DR025) | 100% | 1391000 | 2279000 | 63.8% | Overspend | Demand for both PSPS-3 rebate programs surged following the January 2025 windstorms, resulting in the typical annual rebate volume being fully claimed within the first two months of the year. | Yes | N/A
Community Outreach and Engagement | DEP-1 | 8.5.2.1 | Wildfire Safety Community Meetings | Non-focus & non-field verifiable | Wildfire Safety Community Meetings | Continue or revise - determined based on outcome of 2023-2024. | 14 | 14 | 14 | 14 | Target met | N/A | 14 | 100% | Wildfire Safety Community Meetings 14 Meeting Records (incl. materials, agendas, etc.) (Frontload Data) | 100% | 132000 | 68000 | -48.5% | Underspend | Strategic cost-saving measures and efficient resource allocation practices. | N/A | N/A
Community Outreach and Engagement | DEP-4 | 8.4.2.3 | Customer Research & Education | Non-focus & non-field verifiable | Conduct at Leat 3 PSPS-Related Customer Studies | 3 | 3 | 3 | Pre- and Post-Season Survey Results, PSPS Survey Results | 3 | Target met | N/A | 3 | 100% | Customer Research and Education Study Reports (Frontload Data) | 100% | 4337000 | 2018000 | -53.5% | Underspend | Deferral of certain research activities and planned PSPS content enhancements into 2026. | N/A | N/A
Note on K11: Number of "actuals" from which samples are selected

## Tab 3 - Data Requests
Data Requests
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Southern California Edison
Date Sent | Date Response Received | Section / Initiative | Data Request Number | List of Documents Received
2026-03-18 | 2026-03-23 | Geodatabase Files: SH-1; SH-2; SH-14; SH-16; SH-17; SH-18; VM-1; VM-4 | DR001
2026-04-09 | 2026-04-30 | IN-1.1 | DR010 | IE02-SCE-2025 Q.01.IN-1.1 Answer SCE-_DR010_IN-1.1 Base Sampling Request_Response SCE-DR010_IN-1.1 Alternate Sample Request
2026-04-09 | 2026-04-30 | IN-1.2 | DR011 | IE02-SCE-2025 Q.02.IN-1.2 Anwer IN-1.2-Alternate Sampling Response
2026-04-09 | 2026-04-24 | IN-3 | DR012 | 03.IN-3_IE02-SCE-2025 Q.03.IN-3 Answer 03.IN-3_IN-3_2025 Alternate Sample)Complete.mpk 03.IN-3_IN-3_2025 Alternate Sample_Complete_cGIS Images 03.IN-3_IN-3_Alternate Samples_Complete 03.IN-3_IN-3_2025 Base Sample.mpk 03.IN-3_IN-3_2025 Base Sample_Complete_cGIS Images 03.IN-3_IN-3_2025 Base Samples_Complete
2026-04-09 | 2026-04-24 | IN-4 | DR013 | 04.IN-4_IE02-SCE-2025 Q.04.IN-4 Answer 04.IN-4_IN-4_Response_Alternate Sample 04.IN-4_IN-4_Response_Base Sample
2026-04-09 | 2026-04-24 | IN-5 | DR014 | 05.IN-5_IE02-SCE-2025 Q.05.IN-5 Answer 05.IN-5_IN-5 Inspection Survey Information 2025 Alternate Sample_Complete.xls 05.IN-5_IN-5 Inspection Survey Information 2025 Base Sample_Complete.xls
2026-04-09 | 2026-04-24 | PSPS-2 | DR018 | 06.PSPS-2_IE02-SCE-2025 Q.06.PSPS-2 Answer 06.PSPS-2_PSPS-2_2025 Alternate Sample_Complete.xlsx 06.PSPS-2_PSPS-2_2025 Base Sample_Complete.xlsx
2026-04-09 | 2026-04-24 | PSPS-3 | DR019 | 07.PSPS-3_IE02-SCE-2025 Q.07.PSPS-3 Answer 07.PSPS-3_PSPS-3_2025 Alternate Sample_Complete.xlsx 07.PSPS-3_PSPS-3_2025 Base Sample_Complete.xlsx
2026-04-09 | 2026-04-24 | SA-1 | DR020 | 08.SA-1_IE02-SCE-2025 Q.08.SA-1 Answer 08.SA-1_SA-1_2025 Alternate Sample_Complete.xlsx 08.SA-1_SA-1_2025 Base Sample_Complete.xlsx
2026-04-09 | 2026-04-30 | SA-10 | DR021 | IE02-SCE-2025 Q.09.SA-10 Answer
2026-04-09 | 2026-04-30 | SA-11 | DR022 | IE02-SCE-2025 Q.10.SA-11 Answer SA-11_Alternate Sample)Complete SA-11 Base Sample_Complete SA11_EFD_900number_Alternate Sample_Evidence SA11_EFD_900number_Base Sample_Evidence
2026-04-09 | 2026-04-30 | SH-10 | DR026 | IE02-SCE-2025 Q.13.SH-10 Answer
2026-04-09 | 2026-04-30 | SH-5 | DR032 | IE02-SCE-2025 Q.11.SH-5 Answer
2026-04-09 | 2026-04-30 | SH-8 | DR033 | IE02-SCE-2025 Q.12.SH-8 Answer SH-8 Transmission Open Phase Detection Compliance Evidence 2025
2026-04-09 | 2026-04-30 | VM-10 | DR035 | IE02-SCE-2025 Q.19.VM-10 Answer VM-10_2025 Alternate Sample_Complete VM-10_2025 Base Sample_Complete
2026-04-09 | 2026-04-30 | VM-2 | DR036 | IE02-SCE-2025 Q.14.VM-2 Answer VM-2 2025 Base Redacted Structure Brushing Reports (138) VM-2 2025 Alternate Redacted Structure Brushing Reports (35)
2026-04-09 | 2026-04-30 | VM-3 | DR037 | IE02-SCE-2025 A.15.VM-3 Answer VM-3 Associated Records 2025 Alternate Sample.xlsx VM-3 Associated Records 2025 Base Sample.xlsx
2026-04-09 | 2026-04-30 | VM-7 | DR040 | IE02-SCE-2025 Q.16.VM-7 Answer BASE: 2025 Grid Cover Sheets/Inspections (23) ALTERNATE: 2025 Grid Cover Sheets/Inspections (5)
2026-04-09 | 2026-04-30 | VM-8 | DR041 | IE02-SCE-2025 Q.17.VM-8 Answer BASE: 2025 Grid Cover Sheets/Inspections (16) ALTERNATE: 2025 Grid Cover Sheets/Inspections (5)
2026-04-09 | 2026-04-30 | VM-9 | DR042 | IE02-SCE-2025 Q.18.VM-9 Answer VM-9_2025 Alternate Sample_Complete VM-9_2025 Base Sample_Complete
2026-04-13 | 2026-04-16 | SH-1 | DR025 | IE03-SCE-2025 A.01.SH-1 Answer IE03-SCE-2025 Q.02.SH-1 Answer
2026-04-13 | 2026-04-16 | SH-17 | DR029 | IE03-SCE-2025 A.01.SH-17 Answer
2026-04-13 | 2026-04-16 | SH-18 | DR030 | IE03-SCE-2025 Q.01.SH-18 Answer
2026-04-13 | 2026-04-16 | SH-2 | DR031 | IE03-SCE-2025 Q.01.SH-2 Answer IE03-SCE-2025 Q.02.SH-2 Answer
2026-04-22 | Void | QAQC Program | DR002
2026-04-24 | 2026-04-29 | QAQC Program | DR002.b | GP-003 Training Management GP-004 Findings Management GP-013 Data Trending Process GP-014 Technical Review Board IE04-SCE-2025 Q.01 T&D C&Q Answer IE04-SCE-2025 Q.02 Veg. Mgmt Answer SCE DR002.b Vegetation Management QAQC Questionnaire SCE_DR002.b_QAQC Questionnaire_OEIS 2025 WMP Data Request_TD QAQC_Final
2026-04-27 | 2026-04-30 | SH-18 | DR030.b | IE05-SCE-2025 Q.01.SH-18 Answer
2026-04-28 | 2026-05-08 | SH-1 | DR025.b | IE06-SCE-2025 Q.01 SH-1 Answer OEIS Confidentiality Application_IE06-SCE-2025 IE06-SCE-2025 01-SH-1 Response_Confidential (62 As-Builts) IE06-SCE-2025 01-SH-1 Response_Confidential-2 (79 As-Builts)
2026-04-28 | 2026-05-08 | SH-2 | DR031.b | IE06-SCE-2025 Q.02 SH-2 Answer OEIS Confidentiality Applicatoin_IE06-SCE-2025 IE06-SCE-2025 02-SH-2 Response-CONFIDENTIAL (93 As-Builts)
2026-05-06 | 2026-05-18 | Financials | DR003 | IE07-SCE-2025-Financials Q.01-20 Answer IE07-SCE-2025-Financials Q.02 Supplemental Answer
2026-05-19 | 2026-05-22 | VM-7 & VM-8 | DR040.b | IE08-SCE-2025 Q.01 Answer IE08-SCE-2025 Q.02 Answer
2026-05-21 | 2026-05-26 | DEP-2 | DR007 | IE09-SCE-2025 Q.01 Answer

## Tab 4 - SME Interviews
SME Interviews
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Southern California Edison
Interview date | Section / Initiative | SME interview number | Positions interviewed | Summary of interview