## Tab 1 - Overview tab
IE AIR Attachments
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Pacific Gas & Electric
Legends
Tab 1 | Overview Tab - Instructions and overview
Tab 2 | Catalog of Initiatives - Initiative review and funding compliance of all initiatives
Tab 3 | Data Requests - Comprehensive list of documents reviewed
Tab 4 | SME Interviews - Summary of interviews conducted

## Tab 2 - Catalog of Initiatives
Catalog of Initiatives
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Pacific Gas & Electric
WMP Category | Initiative Tracking ID | WMP Section Number | Initiative Name | Initiative Type | WMP - Initiative Description | WMP - Initiative Target | EC-Claimed Progress (Q4 QDR) | EC-Claimed Progress (EC AIR) | EC-Claimed Progress (DR) | IE Declared Actual | EC-Claimed Initiative Status | Target Not Met - Rationale | Sample Size (#) | Sample Validation Rate (%) | Verification Method | IE Declared Initiative Completion Percent | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%) | Funding discrepancy - finding | Funding discrepancy - detail | Satisfied Risk Reduction Goal - finding | Satisfied Risk Reduction Goal - detail
Grid Design Operations and Maintenance | AI-01 | 8.1.9.1 | Retainment of Inspectors and Internal Workforce Development | Non-focus & non-field verifiable | Develop a strategy to improve long-term retention of trained and qualified inspectors and develop a strategy to grow and maintain an experienced internal inspection workforce while mentoring and training new employees. |  | Completed | Increased permanent compliance inspector headcount in organization by 74 inspectors and increased employee tenure. | Increase in staffing levels. |  | Target met | N/A | N/A | N/A | PG&E Headcount 2023-2025 (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% |  | N/A | No Goal Provided | N/A
Grid Design Operations and Maintenance | AI-02 | 8.1.3.1.1 | Detailed Inspection Transmission - Ground | Non-focus & non-field verifiable | Complete 22,000 Ground Inspections on Transmission | 22000 | 24033 | N/A | 24033 | 24033 | Target met | N/A | 35 | 100% | Transmission Ground Inspection List (Frontload Data) 35 Inspection Records (DR007) | 109% | 8500000 | 5801000 | -31.8% | Underspend | Early training and favorable weather enabled PG&E to mobilize inspection resources sooner, improving work sequencing and operational efficiency, | TBD | N/A
Grid Design Operations and Maintenance | AI-04 | 8.1.3.1.2 | Detailed Inspection Transmission - Aerial | Non-focus & non-field verifiable | Complete 19,000 Aerial Inspections on Transmission | 19000 | 23519 | N/A | 23519 | 23519 | Target met | N/A | 35 | 100% | Transmission Aerial Inspection List (Frontload Data) 35 Inspection Records (DR008) | 124% | 22591000 | 16584000 | -26.6% | Underspend | Lower unit costs and efficiencies achieved through the transition to unitized cost structures during execution. | TBD | N/A
Grid Design Operations and Maintenance | AI-05 | 8.1.3.1.3 | Detailed Inspection Transmission - Climbing | Non-focus & non-field verifiable | Complete 1,200 Climbing Inspections on Transmission | 1200 | 1873 | N/A | 1696 | 1696 | Target met | N/A | 34 | 100% | Transmission Climbing Inspection List (Frontload Data) 34 Inspection Records (DR009) | 141% | 1751000 | 3033000 | 73.2% | Overspend | Expanded scope of work resulting from COA findings, along with increased unit costs associated with reinspection activities and accelerated completion timelines. | TBD | N/A
Grid Design Operations and Maintenance | AI-06 | 8.1.3.1.4 | Transmission Infrared Inspections | Non-focus & non-field verifiable | Complete 3,500 Circuit Miles of Infrared Inspections on Transmission | 3500 | 4222 | N/A | 4222 | 4222 | Target met | N/A | 34 | 100% | Transmission Infrared Inspection List (Frontload Data) 34 Circuit Miles of Inspection Records (DR010) | 121% | 1549000 | 1399000 | -9.7% | Underspend | N/A | TBD | N/A
Grid Design Operations and Maintenance | AI-07 | 8.1.3.2.1 | Detailed Ground Inspections - Distribution | Focus & non-field verifiable | Complete 244,000 Ground & Aerial Pole Inspections | 244000 | 279939 | N/A | 279939 | 279939 | Target met | N/A | 138 | 100% | Distribution Ground Inspection List (Frontload Data) 138 Inspection Records (DR011) | 115% | 40228000 | 36279000 | -9.8% | Underspend | N/A | No | 2025 EC AIR reports a corresponding Risk Impact of 33.54% Eyes-on-Risk achieved, falling short of the target provided in the WMP. PG&E states that this shortage is due to the work plan for the three-year WMP cycle was front loaded with higher risk assets in 2023 and 2024. PG&E claims that they successfully met the overall intent of the commitment by averaging 48% Eyes-on-Risk across the 2023-2025 cycle, exceeding the 44% three-year average established in the 2023-2025 WMP.
Grid Design Operations and Maintenance | AI-08 | 8.1.3.3.1 | Supplemental Inspections - Substation Distribution | Non-focus & non-field verifiable | Complete 78 Substation Distribution Inspections | 78 | 78 | N/A | 78 | 78 | Target met | N/A | 24 | 99% | Distribution Substation Inspection List (Frontload Data) 24 Inspection Records (DR012) | 99% | 2702000 | 1854000 | -31.4% | Underspend | Inspection tool updates that increased inspection efficiency. | TBD | N/A
Grid Design Operations and Maintenance | AI-09 | 8.1.3.3.1 | Supplemental Inspections - Substation Transmission | Non-focus & non-field verifiable | Complete 41 Substation Transmission Inspections | 41 | 41 | N/A | 41 | 41 | Target met | N/A | 19 | 98% | Transmission Substation Inspection List (Frontload Data) 19 Inspection Records (DR013) | 98% | 1701000 | 2660000 | 56.4% | Overspend | An error during the budget-setting process in which the activity was underfunded yet implementation of work continued. | TBD | N/A
Grid Design Operations and Maintenance | AI-10 | 8.1.3.3.1 | Supplemental Inspections - Hydroelectric Substations & Powerhouses | Non-focus & non-field verifiable | Complete 40 Hydroelectric Substation & Powerhouse Inspections | 40 | 41 | N/A | 42 | 42 | Target met | N/A | 19 | 98% | Hydroelectric & Powerhouse Inspection List (Frontload Data) 19 Inspection Records (DR014) | 101% | 2150000 | 1037000 | -51.8% | Underspend | Inspection tool updates that increased inspection efficiency. | TBD | N/A
Grid Design Operations and Maintenance | AI-11 | 8.1.5 | Filling Asset Inventory Gaps | Non-focus & non-field verifiable | Listing targeted distribution and transmission equipment and populating missing age data in the Asset Registry. | List of targeted distribution and transmission equipment types. Baseline and actual rate of completeness for the "Installation Date" data element for each targeted distribution and transmission equipment type (90% weighted average completeness across risk prioritized equipment). | N/A | Population of missing age data in the Asset Inventory and Condition Database was completed to more than 90 percent weighted average across risk prioritized distribution and transmission equipment types. | 94.70 Fill Rate | 94.70% Fill Rate | Target met | N/A | N/A | N/A | Baseline and Endline Assets Fill Rate (DR003 Remaining Frontload Data) | 100% | 2500000 | 686000 | -72.6% | Underspend | The successful use of an estimated age model that enabled PG&E to exceed its asset age data completeness target more efficiently than anticipated, reducing reliance on more resource-intensive manual methods. | No Goal Provided | N/A
Grid Design Operations and Maintenance | GH-01 | 8.1.2.1 | System Hardening - Distribution | Focus & field verifiable | Complete 520 Circuit Miles of Distribution Hardening | 520 | 539.01 | 539.04 | 539.04 | 539.04 | Target met | N/A | 110 | 100% | Field Evaluation System Hardening - Distribution GIS Documentation (DR002) As-Builts (DR022) | 104% | 248940000 | 283952000 | 14.1% | Overspend | Hardening a greater number of circuit miles than budgeted. | Yes | PG&E completed 539.01 circuit miles of system hardening work, exceeding operational targets, thus achieving the stated 4.70% risk reduction goal.
Grid Design Operations and Maintenance | GH-02 | 8.1.2.1 | Evaluate Covered Conductor Effectiveness | Non-focus & non-field verifiable | Update the covered conductor recorded effectiveness calculation using 2024 outage data. | Update the covered conductor recorded effectiveness calculation using 2024 outage data. | Completed | Covered Conductor Effectiveness calculation updated using 2024 outage data. | Whitepaper summarizing covered conductor effectiveness calculation updated using 2024 outage data. | Whitepaper summarizing covered conductor effectiveness calculation updated using 2024 outage data. | Target met | N/A | N/A | N/A | 2025 Covered Conductor Estimated Effectiveness (Frontload Data) | 100% | 0 | 0 | 0% |  |  | No Goal Provided | N/A
Grid Design Operations and Maintenance | GH-04 | 8.1.2.2 | 10K Undergrounding | Focus & field verifiable | Complete 330 Circuit Miles of Undergrounding | 330 | 333.82 | 333.82 | 333.82 | 333.82 | Target met | N/A | 98 | 100% | Field Evaluation 10K Undergrounding GIS Documentation (DR002) As-Builts (DR024) | 101% | 1212822000 | 1210527000 | 0.2% | No discrepancy | N/A | Yes
Grid Design Operations and Maintenance | GH-05 | 8.1.2.5.1 | System Hardening - Transmission | Focus & field verifiable | Complete 5 Circuit Miles of Transmission Hardening | 5 | 19.4 | 19.8 | 19.8 | 19.8 | Target met | N/A | 17 | 100% | Field Evaluation System Hardening - Transmission GIS Documentation (DR002) As-Builts (DR025) | 396% | 21517000 | 9331000 | -56.6% | Underspend | The elimination of approximately $10 million in temporary generation costs at Foresthill Substation after PG&E coordinated an alternative switching configuration and protection scheme with Operations and System Protection. | Yes
Grid Design Operations and Maintenance | GH-06 | 8.1.2.5.1 | System Hardening - Transmission Shunt Splices | Non-focus & non-field verifiable | Install Shunt Splices on 25 Transmission Lines | 25 | 25 | 25 | 14 of 15 planned lines validated; 62 shunt splice locations verified. | 14 of 15 planned lines validated; 62 shunt splice locations verified. |  |  | 15 | 93% | CalFire 2022 Powerline Equipoment Identification Pocket Guide v2 Field Evaluation System Hardening - Transmission GIS Documentation (DR002) | 93% | 4374000 | 3573000 | -18.3% | Underspend | PG&E’s transition from external contractors to internal crews as part of a cost savings initiative piloted in 2025 - internal crews already possessed the necessary capabilities and credentials, resulting in cost savings without any reduction in work quality. | TBD | N/A
Grid Design Operations and Maintenance | GH-08 | 8.1.2.10.4 | Surge Arrestor - Removals |  | Remove Non-Exempt Surge Arrestors Where Known Grounding Issues Exist | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 500000 | 1868000 | 134% | Overspend | Associated with QA, documentation remediation, and closeout activities for previously installed surge arresters, including validation and correction of records for more than 69,000 locations to ensure accurate documentation and project closeout. | Yes | N/A
Grid Design Operations and Maintenance | GH-10 | 8.1.2.10.5 | Non-Exempt Expulsion Fuse - Removal | Focus & field verifiable | Remove Non-Exempt Expulsion Fuses From 1,400 Locations | 1400 | 1451 | 1451 | 1451 | 1451 | Target met | N/A | 126 | 100% | CalFire 2022 Powerline Equipment Identification Pocket Guide v2 Field Evaluation Non-Exempt Expulsion Fuse – Removal GIS Documentation (DR002) | 104% | 5485000 | 8200000 | 49.5% | Overspend | The addition of approximately 700 equipment fuses to the 2025 workplan after budget development in order to meet the WMP target of 1,400 fuse removals, as the original budget only accounted for the remaining non-exempt line fuses within the initial program scope. | Yes | N/A
Grid Design Operations and Maintenance | GH-11 | 8.1.2.5.1 | System Hardening – Transmission Conductor Segment Replacement | Non-focus & non-field verifiable | Replace Conductor Segments on 2 Transmission Lines | 2 | 2 | 2 | 2 | 2 | Target met | N/A | 2 | 100% | Field Evaluation System Hardening – Transmission Conductor Segment Replacement GIS Documentation (DR002) | 100% | 1112000 | 1031000 | -7.3% | Underspend | N/A | Yes | N/A
Grid Design Operations and Maintenance | GM-01 | 8.1.6.1 | Asset Inspections - Quality Assurance | Focus & non-field verifiable | Perform system inspection QA audits on QC completed locations and achieve the associated quality pass rates for each asset inspection program as specified below: Transmission Inspections – HFTD/HFRA: 500 audit locations*, 95% pass rate. Distribution Inspections – HFTD/HFRA: 1,500 Audit locations*, 95% pass rate. | Transmission Inspections – HFTD/HFRA: 500 audit locations*, 95% pass rate. Distribution Inspections – HFTD/HFRA: 1,500 Audit locations*, 95% pass rate. | Transmission Inspections - 1,783 Inspected, 1,783 Passed = 100% Pass Rate Distribution Inspections - 1,871 Inspected, 1778 Passed = 99.83% Pass Rate | Transmission Inspections - 1,783 Inspected, 1,783 Passed = 100% Pass Rate Distribution Inspections - 1,871 Inspected, 1778 Passed = 99.83% Pass Rate | Transmission Inspections - 1,783 Inspected, 1,783 Passed = 100% Pass Rate Distribution Inspections - 1,871 Inspected, 1778 Passed = 99.83% Pass Rate | Transmission Inspections - 1,783 Inspected, 1,783 Passed = 100% Pass Rate Distribution Inspections - 1,871 Inspected, 1778 Passed = 99.83% Pass Rate | Target met | N/A | 67 Distribution 66 Transmission | 100% | QA Distribution Audit List QA Transmission Audit List (Frontload Data) 67 Distribution Audit Records 66 Transmission Audit Records (DR029) | 178% | 5068000 | 4527000 | -10.7% | Underspend | Resource optimization efforts, including earlier work planning and scheduling, better alignment of internal resources with WMP commitments, and the addition of internal personnel, which reduced reliance on contractors and lowered overtime and double-time costs. | Yes | N/A
Grid Design Operations and Maintenance | GM-03 | 8.1.7.2 | HFTD/HFRA Open Tag Reduction – Distribution Backlog | Non-focus & non-field verifiable | Reduce HFTD/HFRA and Additional EC Open Tag Backlog by 50,000 | Close at least 25,000 additional EC notifications on top of closing an equivalent number of EC notification created in HFRA/HFTD locations in 2025. | 127,291 Closed Tags | N/A | 127,291 Closed Tags | 127,291 Closed Tags | Target met | N/A | 35 Tags | 100% | Closed Tags List (Frontload Data) Order Cancellation Forms, Contractor Face Sheets, O-Calc GO95 Forms, and EH Overhead Tag Forms (DR030) | 509% | 600000 | 532000 | -11.3% | Underspend | Attributable to lower unit costs for completed work. | Yes | N/A
Grid Design Operations and Maintenance | GM-06 | 8.1.2.10.1 | EPSS - Down Conductor Detection (DCD) | Non-focus & non-field verifiable | Install 250 DCD Protective Devices | 250 | 518 | 494 | 517 | 517 | Target met | N/A | 32 | 100% | CalFire 2022 Powerline Equipment Identification Pocket Guide v2 Field Evaluation EPSS - Down Conductor Detection (DCD) GIS Documentation (DR002) | 198% | 31259000 | 33977000 | 8.7% | Overspend | N/A | Yes | N/A
Grid Design Operations and Maintenance | GM-07 | 8.1.8.1.1 | Update on EPSS Reliability Study | Non-focus & non-field verifiable | Provide Updated EPSS Reliability Study | Provide annually an updated Enhanced Powerline Safety Settings (EPSS) reliability impact study per Areas for Continued Improvement (ACI) | Completed | Reliability study submitted to Energy Safety on February 28, 2025. | Reliability study submitted to Energy Safety on February 28, 2025. | Reliability study submitted to Energy Safety on February 28, 2025. | Target met | N/A | N/A | N/A | EPSS Reliability Study – Evaluation and Reporting Narrative (Frontload Data) Energy Safety E-Filing Website | 100% | 0 | 0 | 0% |  | N/A | Yes | N/A
Grid Design Operations and Maintenance | GM-09 | 8.1.6.2 | Asset Inspection – Quality Control | Focus & non-field verifiable | Transmission – 17,450 audit locations; 95 percent pass rate Distribution – 170,000 audit locations; 95 percent pass rate | Transmission – 17,450 audit locations; 95 percent pass rate Distribution – 170,000 audit locations; 95 percent pass rate | Transmission Inspections – 19,842 Inspected, 99.99% Pass Rate Distribution Inspections – 177,742 Inspected, 99.92% Pass Rate | Transmission Inspections – 19,842 Inspected, 99.99% Pass Rate Distribution Inspections – 177,742 Inspected, 99.92% Pass Rate | Transmission Inspections – 19,842 Inspected, 99.99% Pass Rate Distribution Inspections – 177,742 Inspected, 99.92% Pass Rate | Transmission Inspections – 19,842 Inspected, 99.99% Pass Rate Distribution Inspections – 177,742 Inspected, 99.92% Pass Rate | Target met | N/A | 68 Distribution 70 Transmission | 100% | QC Distribution Audit List QC Transmission Audit List (Frontload Data) 68 Distribution Audit Records 70 Transmission Audit Records (DR033) | 105% | 21250000 | 17373000 | -18.2% | Underspend | Increased operational efficiency achieved through earlier work planning and scheduling, improved alignment of internal resources with WMP commitments, and onboarding additional internal personnel, which reduced contractor reliance and lowered overtime and double-time labor costs. | N/A | N/A
Vegetation Management and Inspections | VM-01 | 8.2.2.1.1 | LiDAR Data Collection – Transmission | Non-focus & non-field verifiable | Complete 17,500 Circuit Miles of LiDAR Inspections | 17500 | 17954 | N/A | 17954 | 17954 | Target met | N/A | 35 | 100% | LiDAR Inspection List (Frontload Data) 35 Circuit Miles of Attestations (DR045) | 103% | 6409000 | 11044000 | 72.3% | Overspend | Higher-than-forecasted annual contract pricing increases associated with LiDAR data processing and analytical support activities. | N/A | N/A
Vegetation Management and Inspections | VM-02 | 8.2.3.1 | Pole Clearing Program | Focus & non-field verifiable | Pole Clearing 77,376 Distribution Poles | 2025 pole count to be adjusted by the ending pole population in the previous year (2024) poles per Vegetation Control Standard TD-7112S will be inspected, cleared, and maintained where clearing is necessary. (77,376 Poles based on refreshed asset registry prior to work beginning) | 81129 | 80301 | 80301 | 80301 | Target met | N/A | 138 | 100% | Pole Clearing Work Log (Frontload Data) 138 Pole Clearing Records (DR046) | 104% | 27363000 | 32851000 | 20.1% | Overspend | Increased work scope and inspection volumes - additional SMU-20 scope units increased total completed units, while expanded focus on 1254C pole-clearing tree work increased locations from approximately 5,000 to 16,000, contributing an estimated $4.4 million cost increase. | Yes | N/A
Vegetation Management and Inspections | VM-03 | 8.2.2.2.5 | Focused Tree Inspection (FTI) Program | Non-focus & non-field verifiable | Complete 1,500 Circuit Miles of Focused Tree Inspections | 1500 | 1531.32 | N/A | 1531 | 1531 | Target met | N/A | 35 | 97% | Focused Tree Inspection List (Frontload Data) 35 FTI Records (DR047) | 102% | 183964000 | 101900000 | -44.6% | Underspend | Lower unit costs resulting from differences between the December End Target (DET) and the operational workplan unit cost - Focused Tree Inspection (FTI) funding was reduced through PDC change control, with a portion of the funding reallocated to support Distribution Routine and Second Patrol programs. | Yes | N/A
Vegetation Management and Inspections | VM-04 | 8.2.2.2.4 | Tree Removal Inventory | Focus & non-field verifiable | Remove 25,000 Trees | 25000 | 31702 | 31311 | 31702 | 31702 | Target met | N/A | 138 | 100% | Tree Removal Inventory List (Frontload Data) 138 Tree Records (DR048) | 127% | 70386000 | 29429000 | -58.2% | Underspend | Reduction in the Tree Removal Inventory (TRI) budget from $68.407 million to $34.796 million - reduced funding was reallocated to support Distribution Routine, Distribution Second Patrol, VMOM, and Distribution VC programs. | Yes | N/A
Vegetation Management and Inspections | VM-05 | 8.2.2.3.1 | Defensible Space Inspections – Distribution Substation | Focus & non-field verifiable | Inspect 131 Distribution Substations | 131 | 130 | 130 | 130 | 130 | Target met | N/A | 67 | 100% | Distribution Substation Inspection List (Frontload Data) 67 Substation Records (DR049) | 99% | 2200000 | 2113000 | -4% | Underspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM-06 | 8.2.2.3.1 | Defensible Space Inspections – Transmission Substation | Non-focus & non-field verifiable | Inspect 55 Transmission Substations | 55 | 55 | N/A | 55 | 55 | Target met | N/A | 21 | 100% | Transmission Substation Inspection List (Frontload Data) 21 Substation Records (DR050) | 100% | 1211000 | 1271000 | 5% | Overspend | N/A | Yes | N/A
Vegetation Management and Inspections | VM-07 | 8.2.2.3.1 | Defensible Space Inspections – Hydroelectric Substations and Powerhouses | Non-focus & non-field verifiable | Inspect 61 Hydroelectric Substations and Powerhouses | 61 | 58 | 58 | 58 | 58 | Target met | N/A | 22 | 100% | Hydroelectric Substation & Powerhouses List (Frontload Data) 22 Substation Records (DR051) | 95% | 1550000 | 1503000 | -3% | Underspend | N/A | No | PG&E states that the expected risk reduction was not achieved due to two powerhouses being removed from scope and two additional powerhouses being shutdown and disconnected from the grid.
Vegetation Management and Inspections | VM-08 | 8.2.5 | Vegetation Management – Quality Assurance | Focus & non-field verifiable | Distribution: 2,862 audit locations; 95% pass rate Transmission: 1,374 audit locations; 95% pass rate Vegetation Control Pole Clearing: 2,061 audit locations; 95% pass rate | Distribution: 2,862 audit locations; 95% pass rate Transmission: 1,374 audit locations; 95% pass rate Vegetation Control Pole Clearing: 2,061 audit locations; 95% pass rate | Distribution Routine VM – HFTD: 4,101 audit locations; 99.92% pass rate. Transmission VM – HFTD: 2,042 audit locations; 99.99% pass rate. Vegetation Control Pole Clearing – HFTD: 2,647 audit locations; 100% pass rate. | Distribution Routine VM – HFTD: 4,101 audit locations; 99.92% pass rate. Transmission VM – HFTD: 2,042 audit locations; 99.99% pass rate. Vegetation Control Pole Clearing – HFTD: 2,647 audit locations; 100% pass rate. | Distribution Routine VM – HFTD: 4,101 audit locations; 99.92% pass rate. Transmission VM – HFTD: 2,042 audit locations; 99.99% pass rate. Vegetation Control Pole Clearing – HFTD: 2,647 audit locations; 100% pass rate. | Distribution Routine VM – HFTD: 4,101 audit locations; 99.92% pass rate. Transmission VM – HFTD: 2,042 audit locations; 99.99% pass rate. Vegetation Control Pole Clearing – HFTD: 2,647 audit locations; 100% pass rate. | Target met | N/A | 47 Distribution 46 Transmission 45 Pole Clearing | 100% | QA Distribution Audit List QA Transmission Audit List QA Pole Clearing Audit List (Frontload Data) 138 Inspection Audit Records (DR052) | 139% | 10283000 | 9495000 | -7.7% | Underspend | N/A | N/A | N/A
Vegetation Management and Inspections | VM-09 | 8.2.6 | Constraint Resolution Procedural Guideline | Non-focus & non-field verifiable | Process of Centralizing Constraints Resolution | Process of Centralizing Constraints Resolution | Complete | Complete | Constraint Resolution Procedural Guidelines Completion Report | Constraint Resolution Procedural Guidelines Completion Report | Target met | N/A | N/A | N/A | Constraint Resolution Procedural Guidelines Completion Report (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% |  | N/A | No Goal Provided | N/A
Vegetation Management and Inspections | VM-13 | 8.2.2.1.1 | Routine Ground – Transmission | Non-focus & non-field verifiable | Complete 17,740 Circuit Miles of Ground Inspections | 17740 | 17953 | 17953 | 17953 | 17953 | Target met | N/A | 35 | 100% | Transmission Routine Ground Inspection List (Frontload Data) 35 Circuit Miles of Inspection Records (DR054) | 101% | 24797000 | 27553000 | 11.1% | Overspend | Increased VM oversight presence driven by organizational and programmatic changes implemented to support operational improvements related to wildfire mitigation, quality, and safety commitments | Yes | N/A
Vegetation Management and Inspections | VM-14 | 8.2.2.1.2 | Transmissoin Second Patrol | Non-focus & non-field verifiable | Complete 5,625 Circuit Miles of Second Patrol Inspections | 5625 | 6058 | 6058 | 6058 | 6058 | Target met | N/A | 34 | 100% | Transmission Second Patrol Inspection List (Frontload Data) 34 Circuit Miles of Inspection Records (DR056) | 108% | 1152000 | 1872000 | 62.5% | Overspend | LiDAR cost allocations associated with VM-14 - $3.90 million in total LiDAR costs related to VM-14, $1.44 million was recorded under VM-14, while the remaining costs were captured under VM-01. | Yes | N/A
Vegetation Management and Inspections | VM-15 | 8.2.2.1.3 | Integrated Vegetation Management – Transmission | Non-focus & non-field verifiable | Complete 6,504 Acres of Vegetation Management Inspections | 6504 | 6659 | 6659.31 | 6659.31 | 6659.31 | Target met | N/A | 34 | 100% | VM-15 Execution Summary (Frontload Data) 8 Attestations (34 Acres) (DR056) | 102% | 15524000 | 13682000 | -11.9% | Underspend | Unit efficiencies resulting from reduced vegetation volume across portions of the completed acreage - prior right-of-way projects had already cleared and expanded these areas, reducing the amount of vegetation requiring removal. | TBD
Vegetation Management and Inspections | VM-16 | 8.2.2.2.1 | Distribution Routine Patrol | Focus & non-field verifiable | Complete 78,200 Circuit Miles of Routine Patrol Inspections | 78200 | 78476 | 78438 | 78438 | 78438 | Target met | N/A | 138 | 100% | Distribution Routine Patrol Inspection List (Frontload Data) 138 Circuit Miles of Inspection Records (DR057) | 100% | 745303000 | 885992000 | 18.9% | Overspend | Increased Distribution Routine work volumes, expanded pre-inspection activities, and Reliability Blitz work. | Yes | N/A
Vegetation Management and Inspections | VM-17 | 8.2.2.2.2 | Distribution Second Patrol | Non-focus & non-field verifiable | Complete 25,685 Circuit Miles of Second Patrol Inspections | 25685 | 25714 | 25704 | 25704 | 25704 | Target met | N/A | 35 | 100% | Distribution Second Patrol Inspection List (Frontload Data) 35 Circuit Miles of Inspection Records (DR058) | 100% | 124040000 | 143387000 | 15.6% | Overspend | Increase in the Distribution Routine budget from $745.303 million to $849.843 million - increased spending was offset through reductions in FTI, Distribution Wood Management, VM Tech, Vegetation Management Quality, and TRI initiatives. | Yes | N/A
Vegetation Management and Inspections | VM-18 | 8.2.2.2.3 | VM for Operational Mitigations (VMOM) | Non-focus & non-field verifiable | Mitigate 6,500 Trees | 6500 | 8326 | 8165 | 8165 | 8165 | Target met | N/A | 34 | 100% | One VM Tree Mitigations Log (Frontload Data) 34 Tree Records (DR059) | 126% | 9681000 | 11328000 | 17% | Overspend | Higher-than-expected unit costs resulting from an overestimation of planned operational efficiencies during forecasting, as well as increased tree work costs in the Sierra and Central Valley regions due to larger and more complex trees, difficult terrain, additional crew requirements, and permitting needs. | TBD | N/A
Vegetation Management and Inspections | VM-19 | 8.2.4 | One VM Application Record Keeping Enhancement |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | 27000000 | 16075000 | -40.5% | Underspend | All work related to this initiative was completed in 2024. | N/A | N/A
Vegetation Management and Inspections | VM-22 | 8.2.5.2 | Vegetation Management - Quality Control | Focus & non-field verifiable | Distribution Routine VM – HFTD: 85,000 audit locations; 95% pass rate. Transmission VM – HFTD: 14,500 audit locations; 95% pass rate. Vegetation Control Pole Clearing – HFTD: 12,500 audit locations; 95% pass rate. | Distribution Routine VM – HFTD: 85,000 audit locations; 95% pass rate. Transmission VM – HFTD: 14,500 audit locations; 95% pass rate. Vegetation Control Pole Clearing – HFTD: 12,500 audit locations; 95% pass rate. | Distribution Routine VM – HFTD: 90,164 audit locations; 99.24% pass rate. Transmission VM – HFTD: 15,675 audit locations; 99.76% pass rate. Vegetation Control Pole Clearing – HFTD: 13,312 audit locations; 99.45% pass rate. | Distribution Routine VM – HFTD: 90,164 audit locations; 99.24% pass rate. Transmission VM – HFTD: 15,675 audit locations; 99.76% pass rate. Vegetation Control Pole Clearing – HFTD: 13,312 audit locations; 99.45% pass rate. | Distribution Routine VM – HFTD: 90,164 audit locations; 99.24% pass rate. Transmission VM – HFTD: 15,675 audit locations; 99.76% pass rate. Vegetation Control Pole Clearing – HFTD: 13,312 audit locations; 99.45% pass rate. | Distribution Routine VM – HFTD: 90,164 audit locations; 99.24% pass rate. Transmission VM – HFTD: 15,675 audit locations; 99.76% pass rate. Vegetation Control Pole Clearing – HFTD: 13,312 audit locations; 99.45% pass rate. | Target met | N/A | 45 Distribution 47 Transmission 45 Pole Clearing | 100% | QC Distribution Audit List QC Transmission Audit List QC Pole Clearing Audit List (Frontload Data) 138 Inspection Audit Records (DR060) | 106% | 26602000 | 24483000 | -8% | Underspend | N/A | N/A | N/A
Situational Awareness and Forecasting | SA-02 | 8.3.3.1 | Line Sensor - Installations | Non-focus & non-field verifiable | Install Line Sensors on 40 Circuits | 40 | 45 | N/A | 45 | 45 | Target met | N/A | 20 | 100% | Line Sensor Installation Log (Frontload Data) 20 Line Sensor Records (DR039) | 113% | 2349000 | 1834000 | -21.9% | Underspend | Fewer installations than originally forecasted. |  | N/A
Situational Awareness and Forecasting | SA-05 | 8.3.6.3 | Evaluate FPI and IPW Modeling Enhancements | Non-focus & non-field verifiable | Evaluate Enhancements to the FPI Model and the IPW Model | Evaluate Enhancements to the FPI Model and the IPW Model | Completed in Q2 of 2025. | August 2024 – Version 5 models were deployed. | WRGSC Meeting/ PSPS Document (8/24) | WRGSC Meeting/ PSPS Document (8/24) | Target met | N/A | N/A | N/A | Wildfire Risk Governance Committee July 18, 2024 PSPS Models & Guidance for Decision Making Rev. 1.1 (DR003 Remaining Frontload Data) | 100% | 4861000 | 3631000 | -25.3% | Underspend | In-year accounting changes that reclassified certain SAPP/Numerical Weather Prediction system development, testing, and validation costs from Capital to Expense following review by Capital Accounting. Pre-ordering weather station materials is treated as an incremental current-year program cost rather than being incorporated into future-year forecasts. | TBD | N/A
Situational Awareness and Forecasting | SA-07 | 8.3.2.3 | Monitor and Evaluate the Cameras AI System’s Performance | Non-focus & non-field verifiable | Monitor and evaluate the AI system’s performance. | In partnership with Digital Path, monitor and evaluate the AI system’s performance and explore additional features/inputs to further enhance the system. | Completed | Monitored and evaluated the AI system’s performance – all vendor reports expected were received by 11/26/25. | Monitored and evaluated the AI system’s performance. | Monitored and evaluated the AI system’s performance. | Target met | N/A | N/A | N/A | ALERTWest Hit Tracker Digital Path Road Map Update HD Camera AI Automated Fire Detection (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Situational Awareness and Forecasting | SA-09 | 8.3.3.1 | EFD and DFA Reporting | Non-focus & non-field verifiable | Perform a feasibility study on the use of EFD/DFA technologies to successfully identify incipient failures as a supplement to field inspections. | Perform a feasibility study on the use of EFD/DFA technologies to successfully identify incipient failures as a supplement to field inspections. If feasible, complete a data driven proposal for integrating sensor findings into the inspection program. | N/A | A feasibility study on the use of EFD/DFA technologies to successfully identify incipient failures as a supplement to field inspections. | A Feasibility Study was Conducted | A Feasibility Study was Conducted | Target met | N/A | N/A | N/A | SA-09 EFD and DFA Reporting Analysis (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Situational Awareness and Forecasting | SA-10 | 8.3.3.1 | Distribution Fault Anticipation (DFA) – Installations | Focus & non-field verifiable | Install DFAs on 15 Circuits | 15 | 17 | N/A | 17 | 17 | Target met | N/A | 15 | 100% | DFA Installation Log (Frontload Data) DFA Serial Number and First Comm. Table Circuit Screenshots from the DFA Portal (DR043) | 113% | 2861000 | 3154000 | 10.2% | Overspend | Requiring additional units to achieve its eyes-on-risk target. | Yes | N/A
Situational Awareness and Forecasting | SA-11 | 8.3.3.1 | Early Fault Detection (EFD) – Installations | Non-focus & non-field verifiable | Install EFDs on 4 Circuits | 4 | [6 empty] | 4 | 100% | EFD Sap Completion Log EFD Unique Data Log EFD Circuits & Associated Mileage (Frontload Data) SAP Record of Completion (DR044) | 100% | 6677000 | 7347000 | 10% | Overspend | Error during the budget-setting process in which the activity was underfunded yet implementation of work continued. | Yes | N/A
Emergency Preparedness | EP-01 | 8.4.2.3.1 | Complete PSPS and Wildfire Tabletop and Functional Exercises | Non-focus & non-field verifiable | Complete PSPS and Wildfire Tabletop and Functional Exercise | Complete PSPS and Wildfire Tabletop and Functional Exercise | 4 PSPS & Wildfire Tabletop & Functional Exercises | 4 PSPS & Wildfire Tabletop & Functional Exercises | 4 PSPS & Wildfire Tabletop & Functional Exercises | 4 PSPS & Wildfire Tabletop & Functional Exercises | Target met | N/A | 4 | 100% | PG&E EOC Incident Action Plan (DR003 Remaining Frontload Data) | 200% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Emergency Preparedness | EP-02 | 8.4.3.1 | Maintain All Hazards Planning & Preparedness Programs | Non-focus & non-field verifiable | Maintain the All Hazards Planning and Preparedness Program to provide emergency response and safely and expeditiously restore service. | Maintain the All Hazards Planning and Preparedness Program to provide emergency response and safely and expeditiously restore service. | Completed | Maintained the All-Hazards Planning and Preparedness Program through compliance reporting within the GO 166 filing on April 30, 2025. | All-Hazards Planning Filed on April 30, 2025 | All-Hazards Planning Filed on April 30, 2025 | Target met | N/A | N/A | N/A | PG&E GO 166 Annual Filing on April 30, 2025 (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Emergency Preparedness | EP-04 | 8.4.3.1 | Expand All Hazards Planning to Include Additional Threats and Scenarios | Non-focus & non-field verifiable | Expand the All Hazards planning program to include additional threats and scenarios. | Expand the All Hazards planning program to include additional threats and scenarios. | Completed | Expanded all hazard planning by adding two new Hazard Annexes to the CERP. These include one to support Capacity Shortage events and one to support Volcano events. | Volcano & Capacity Shortage Annex 2025 (2 Annexes) | Volcano & Capacity Shortage Annex 2025 (2 Annexes) | Target met | N/A | N/A | N/A | Capacity Shortage Annex Volcano Annex (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Emergency Preparedness | EP-06 | 8.4.3.1 | Review & Revise CERP and the Two Wildfire-Related Annexes | Non-focus & non-field verifiable | Update 3 documents (1 CERP and 2 wildfire-related annexes) | Update 3 documents (1 CERP and 2 wildfire-related annexes) | 3 Documents (1 CERP and 2 wildfire-related annexes) | N/A | 3 Documents (1 CERP and 2 wildfire-related annexes) | 3 Documents (1 CERP and 2 wildfire-related annexes) | Target met | N/A | 3 | 100% | CERP PSPS Annex Wildfire Annex (Frontload Data Response) | 100% | 0 | 0 | 0% | N/A | N/A | N/A | N/A
Emergency Preparedness | PS-01 | 9.2.1 | Evaluate Enhancements for the PSPS Transmission Guidance | Non-focus & non-field verifiable | Evaluate enhancements for the PSPS Transmission guidance to enhance focus of PSPS events. | Evaluate enhancements for the PSPS Transmission guidance to enhance focus of PSPS events. | Completed | Changes to the PSPS input models occurred since last season, sensitivity analysis was performed, and new guidance was presented to the Wildfire Risk. | Enhancements Evaluated for PSPS 5.5 Guidance | Enhancements Evaluated for PSPS 5.5 Guidance | Target met | N/A | N/A | N/A | PG&E Transmission PSPS Models & Guidance Change Detail (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Emergency Preparedness | PS-02 | 9.2.1 | Evaluate Incorporation of Approved IPW Enhancements into the PSPS Distribution Guidance | Non-focus & non-field verifiable | Evaluate incorporation of approved IPW enhancements into the PSPS Distribution guidance to enhance focus of PSPS events. | Evaluate incorporation of approved IPW enhancements into the PSPS Distribution guidance to enhance focus of PSPS events. | Completed | Changes to the PSPS input models occurred since last season, sensitivity analysis was performed, and new guidance was presented to the WRGSC. | PSPS Distribution Guidance Enhancements – July 10, 2025 | PSPS Distribution Guidance Enhancements – July 10, 2025 | Target met | N/A | N/A | N/A | Distribution PSPS 5.5 Models (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Emergency Preparedness | PS-06 | 8.5.3 | Provide Portable Batteries to PG&E Customers | Non-focus & non-field verifiable | Provide 3,300 Portable Batteries | 3300 | 3798 | 3798 | 3798 | 3798 | Target met | N/A | 34 | 100% | Three Battery Delivery Lists (Frontload Data Response) 44 Battery Records (DR036) | 115% | 12795000 | 5043000 | -60.6% | Underspend | Reduced battery distribution needs outside of PSPS events, the use of existing battery inventory procured in 2024, discontinuation of a previously purchased battery model, and a transition to lower-cost smaller batteries that meet UL 2743 requirements. | N/A | N/A
Emergency Preparedness | PS-07 | 9.1.5 | Reduce PSPS Impacts | Focus & non-field verifiable | Mitigate 13,000 Customer Events | 13000 | 9219 | 13327 | 13327 | 13327 | Target met | N/A | 137 | 100% | Customers Mitigated per Device or UG (Frontload Data Response) | 103% | 0 | 0 | 0% | N/A | N/A | N/A | N/A
Emergency Preparedness | PS-10 | 9.1.3 | Continue Sharing PSPS Lessons Learned | Non-focus & non-field verifiable | Continue sharing PSPS lessons learned and best practices with CA IOUs through monthly meetings focused on PSPS (12 meetings). | Continue sharing PSPS lessons learned and best practices with CA IOUs through monthly meetings focused on PSPS (12 Meetings). | Monthly (12) Meetings | Monthly (12) Meetings | Monthly (12) Meetings | Monthly (12) Meetings | Target met | N/A | 12 | 100% | 12 Joint Utility Working Group Filings (DR003 Remaining Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Community Outreach and Engagement | CO-01 | 8.5.2 | Community Engagement – Meetings | Non-focus & non-field verifiable | Conduct 22 Community Engagement Meetings | 22 | N/A | 22 | 22 | 22 | Target met | N/A | 14 | 100% | Community Engagement Meetings List Community Engagement Post-Event Write-Ups (DR016) | 100% | 0 | 0 | 0% | N/A | N/A | No Goal Provided | N/A
Community Outreach and Engagement | CO-02 | 8.5.2 | Community Engagement – Surveys | Non-focus & non-field verifiable | Deploy 2 PSPS Education and Outreach Surveys | 2 | 2 | N/A | 2 | 2 | Target met | N/A | 2 | 100% | Pre- and Post-Wildfire Season Surveys (Frontload Data) | 100% | 0 | 0 | 0% | N/A | N/A | N/A | N/A
Note on K11: Number of "actuals" from which samples are selected

## Tab 3 - Data Requests
Data Requests
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Pacific Gas & Electric
Date Sent | Date Response Received | Section / Initiative | Data Request Number | List of Documents Received
2026-02-24 | 2026-02-27 | EOY Financials | DR001 | PGE_DR001_20260409_ATCH001.xlsx (04.09 Update) PGE_2025-WMP_IE_DR001_20260227_Q01_ATCH01.xlsx (04.21 Update) PGE_2025-WMP-IE_DR001_20260227_RESPONSE
2026-03-18 | 2026-03-23 | Geodatabase Files: GH-01; GH-04; GH-05; GH-06; GH-10; GH-11; GM-06 | DR002 | PG&E DR_002.gdb (74 Files) PGE_2025_DR-002_20260323_RESPONSE_D001 PGE_DR-002_20260323_RESPONSE_CONF DECLAR
2026-03-19 | 2026-04-03 | Remaining Frontload Data | DR003 | PGE_DR-003_20260327_AI-01 RESPONSE_Q001_ATCH001.xlsx PGE_DR-003_20260327_AI-11 RESPONSE_Q001_ATCH002.xlsx PGE_DR-003_20260327_EP-02 RESPONSE_Q001_ATCH003 PGE_DR-003_20260327_EP-04 RESPONSE_Q001_ATCH004 (2) PGE_DR-003_20260327_EP-04 RESPONSE_Q001_ATCH005 (2) PGE_DR-003_20260327_GH-02 RESPONSE_Q001_ATCH006 (2) PGE_DR-003_20260327_PS-02 RESPONSE_Q001_ATCH007 (2) PGE_DR-003_20260327_RESPONSE_CONF DECLARATION PGE_DR-003_20260327_RESPONSE_D001 PGE_DR-003_20260327_SA-05 RESPONSE_Q001_ATCH008 (2) PGE_DR-003_20260327_SA-05 RESPONSE_Q001_ATCH009 (2) PGE_DR-003_20260327_SA-09 RESPONSE_Q001_ATCH010 (2) PGE_DR-003_20260403_CONF DECLARATION PGE_DR-003_20260403_EP-01 RESPONSE_Q001_ATCH001 (2) PGE_DR-003_20260403_EP-01 RESPONSE_Q001_ATCH002 (2) PGE_DR-003_20260403_GM-07 RESPONSE_Q001_ATCH003 PGE_DR-003_20260403_PS-01 RESPONSE_Q001_ATCH004 PGE_DR-003_20260403_PS-10 RESPONSE_Q001_ATCH005-ATCH016 (12) PGE_DR-003_20260403_EP-01 RESPONSE_D002 PGE_DR-003_20260403_SA-07 RESPONSE_Q001_ATCH017-ATCH19 (6) PGE_DR-003_20260403_VM-09 RESPONSE_Q001_ATCH020
2026-04-06 | 2026-05-01 | AI-02 | DR007 | PGE_2025_DR-007_20260501_RESPONSE PGE_2025_DR-007_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-007_20260501_RESPONSE_Q001_ATCH001-ATCH035 (70) ALTERNATE: PGE_DR-007_20260501_RESPONSE_Q001_ATCH001-ATCH009 (18)
2026-04-06 | 2026-05-01 | AI-04 | DR008 | PGE_2025_DR-008_20260501_RESPONSE PGE_2025_DR-007_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-008_20260501_RESPONSE_Q001_ATCH001-ATCH035 (70) ALTERNATE: PGE_DR-008_20260501_RESPONSE_Q001_ATCH001-ATCH009 (18)
2026-04-06 | 2026-05-01 | AI-05 | DR009 | PGE_2025_DR-009_20260501_RESPONSE PGE_2025_DR-009_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-009_20260501_RESPONSE_Q001_ATCH001-ATCH034 (68) ALTERNATE: PGE_DR-009_20260501_RESPONSE_Q001_ATCH001-ATCH009 (18)
2026-04-06 | 2026-05-01 | AI-06 | DR010 | PGE_2025_DR-010_20260501_RESPONSE PGE_2025_DR-010_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-010_20260501_RESPONSE_Q001_ATCH001-ATCH011 (22) ALTERNATE: PGE_DR-010_20260501_RESPONSE_Q001_ATCH001 (2)
2026-04-06 | 2026-05-08 | AI-07 | DR011 | PGE_2025_DR-011_20260508_RESPONSE PGE_2025_DR-011_20260508_RESPONSE_CONF DECLARATION BASE: PGE_DR-011_20260508_RESPONSE_Q001_ATCH001-ATCH138 (276) ALTERNATE: PGE_DR-011_20260508_RESPONSE_Q001_ATCH001-ATCH035 (70)
2026-04-06 | 2026-05-01 | AI-08 | DR012 | PGE_2025_DR-012_20260501_RESPONSE PGE_2025_DR-012_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-012_20260501_RESPONSE_Q001_ATCH062_REDACTED PGE_DR-012_20260501_RESPONSE_Q001_ATCH001-ATCH072 (144) ALTERNATE: PGE_DR-012_20260501_RESPONSE_Q001_ATCH001-ATCH018 (36)
2026-04-06 | 2026-05-01 | AI-09 | DR013 | PGE_2025_DR-013_20260501_RESPONSE PGE_2025_DR-013_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-013_20260501_RESPONSE_Q001_ATCH001-ATCH057 (114) ALTERNATE: PGE_DR-013_20260501_RESPONSE_Q001_ATCH001-ATCH015 (30)
2026-04-06 | 2026-05-01 | AI-10 | DR014 | PGE_2025_DR-014_20260501_RESPONSE PGE_2025_DR-014_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-014_20260501_RESPONSE_Q001_ATCH001-ATCH057 (114) ALTERNATE: PGE_DR-014_20260501_RESPONSE_Q001_ATCH001-ATCH015 (30)
2026-04-06 | 2026-05-08 | GM-01 | DR029 | PGE_2025_DR-029_20260508_RESPONSE PGE_2025_DR-029_20260508_RESPONSE_CONF DECLARATION BASE: PGE_DR-029_20260508_RESPONSE_Q001_ATCH001-ATCH133 (266) ALTERNATE: PGE_DR-029_20260508_RESPONSE_Q002_ATCH001-ATCH034 (68)
2026-04-06 | 2026-05-01 | GM-03 | DR030 | PGE_2025_DR-030_20260501_RESPONSE PGE_2025_DR-030_20260501_RESPONSE_CONF DECLARATION BASE: PGE_DR-030_20260501_RESPONSE_Q001_ATCH001-ATCH034 (68) ALTERNATE: PGE_DR-030_20260501_RESPONSE_Q002_ATCH001-ATCH009 (18)
2026-04-06 | 2026-05-08 | GM-09 | DR033 | PGE_2025_DR-033_20260508_RESPONSE PGE_DR-033_20260508_RESPONSE_CONF DECLARATION BASE: PGE_DR-033_20260508_RESPONSE_Q001_ATCH001-ATCH145 (290) ALTERNATE: PGE_DR-033_20260508_RESPONSE_Q002_ATCH001-ATCH036 (72)
2026-04-06 | 2026-05-08 | PS-06 | DR036 | PGE_2025_DR-036_20260508_RESPONSE PGE_DR-036_20260508_RESPONSE_CONF DECLARATION BASE: PGE_DR-036_20260508_RESPONSE_Q001_ATCH001-ATCH051 (102) ALTERNATE: PGE_DR-036_20260508_RESPONSE_Q002_ATCH001-ATCH018 (36)
2026-04-06 | 2026-04-24 | SA-02 | DR039 | PGE_2025_DR-039_20260424_RESPONSE PGE_DR-039_20260424_RESPONSE_CONF DECLARATION BASE: PGE_DR-039_20260424_RESPONSE_Q001_ATCH001-ATCH027 (54) ALTERNATE: PGE_DR-039_20260424_RESPONSE_Q002_ATCH001-ATCH007 (14)
2026-04-06 | 2026-04-24 | SA-10 | DR043 | PGE_2025_DR-043_20260424_RESPONSE PGE_DR-043_20260424_RESPONSE_CONF DECLARATION PGE_DR-043_20260424_RESPONSE_Q001_ATCH001 PGE_DR-043_20260424_RESPONSE_Q001_ATCH002 (2)
2026-04-06 | 2026-04-24 | SA-11 | DR044 | PGE_2025_DR-044_20260424_RESPONSE PGE_DR-044_20260424_RESPONSE_Q001_ATCH001 PGE_DR-044_20260424_RESPONSE_Q001_ATCH002-ATCH003 (4) PGE_DR-044_20260424_RESPONSE_CONF DECLARATION PGE_DR-44_20260424_RESPONSE_Q001_ATCH001.xlsx
2026-04-06 | 2026-04-24 | VM-01 | DR045 | PGE_2025_DR-045_20260424_RESPONSE PGE_DR-045_20260424_RESPONSE_CONF DECLARATION PGE_DR-045_20260424_RESPONSE_Q001_ATCH001 (2)
2026-04-06 | 2026-05-01 | VM-02 | DR046 | PGE_2025_DR-046_20260501_RESPONSE BASE: PGE_DR-046_20260501_RESPONSE_Q001_ATCH001.xlsx ALTERNATE: PGE_DR-046_20260501_RESPONSE_Q002_ATCH001.xlsx
2026-04-06 | 2026-04-24 | VM-03 | DR047 | PGE_2025_DR-047_20260424_RESPONSE BASE: PGE_DR-047_20260424_RESPONSE_Q001_ATCH001.xlsx PGE_DR-047_20260424_RESPONSE_Q001_ATCH002-ATCH004 (3) ALTERNATE: PGE_DR-047_20260424_RESPONSE_Q002_ATCH001-ATCH002 (2)
2026-04-06 | 2026-05-08 | VM-04 | DR048 | PGE_2025_DR-048_RESPONSE_20260508 PGE_DR-048_20260508_RESPONSE_Q001_ATCH001.xlsx PGE_DR-048_20260508_RESPONSE_Q002_ATCH001.xlsx
2026-04-06 | 2026-04-24 | VM-05 | DR049 | PGE_2025_DR-049_20260424_RESPONSE PGE_DR-049_20260424_RESPONSE_CONF DECLARATION BASE: PGE_DR-049_20260424_RESPONSE_Q001_ATCH001-ATCH134 (268) ALTERNATE: PGE_DR-049_20260424_RESPONSE_Q002_ATCH001-ATCH034 (68)
2026-04-06 | 2026-04-24 | VM-06 | DR050 | PGE_2025_DR-050_20260424_RESPONSE PGE_DR-050_20260424_RESPONSE_CONF DECLARATION BASE: PGE_DR-050_20260424_RESPONSE_Q001_ATCH001-ATCH029 (58) ALTERNATE: PGE_DR-050_20260424_RESPONSE_Q002_ATCH001-ATCH010 (20)
2026-04-06 | 2026-04-24 | VM-07 | DR051 | PGE_2025_DR-051_20260424_RESPONSE PGE_DR-051_20260424_RESPONSE_CONF DECLARATION BASE: PGE_DR-051_20260424_RESPONSE_Q001_ATCH001-ATCH021 (42) ALTERNATE: PGE_DR-051_20260424_RESPONSE_Q002_ATCH001-ATCH006 (12)
2026-04-06 | 2026-05-08 | VM-08 | DR052 | PGE_2025_DR-052_20260508_RESPONSE BASE: PGE_DR-052_20260508_RESPONSE_Q001_ATCH001-ATCH003.xlsx (3) ALTERNATE: PGE_DR-055_20260508_RESPONSE_Q002_ATCH001-ATCH003.xlsx (3)
2026-04-06 | 2026-04-17 | VM-13 | DR054 | PGE_2025_DR-054_20260417_RESPONSE PGE_DR-054_20260417_RESPONSE_Q001_ATCH001.xlsx PGE_DR-054_20260417_RESPONSE_Q002_ATCH001.xlsx
2026-04-06 | 2026-04-17 | VM-14 | DR055 | PGE_2025_DR-055_20260417_RESPONSE PGE_DR-055_20260417_RESPONSE_Q001_ATCH001.xlsx PGE_DR-055_20260417_RESPONSE_Q002_ATCH001.xlsx
2026-04-06 | 2026-05-01 | VM-15 | DR056 | PG&E_DR056_VM-15 R1.xlsx PG&E_DR056_VM-15 R2.xlsx PG&E_DR056_VM-15.xlsx VM-15 SAMPLING ATTACHMENT R1.xlsx VM-15 SAMPLING ATTACHMENT R2.xlsx VM-15 SAMPLING ATTACHMENT.xlsx
2026-04-06 | 2026-05-01 | VM-16 | DR057 | PGE_2025_DR-057_20260501_RESPONSE BASE: PGE_DR-057_20260501_RESPONSE_Q001_ATCH001.xlsx PGE_DR-057_20260501_RESPONSE_Q001_ATCH002_REDACTED ALTERNATE: PGE_DR-057_20260501_RESPONSE_Q002_ATCH001.xlsx
2026-04-06 | 2026-05-01 | VM-17 | DR058 | PGE_2025_DR-058_20260501_RESPONSE BASE: PGE_DR-058_20260501_RESPONSE_Q001_ATCH001.xlsx PGE_DR-058_20260501_RESPONSE_Q001_ATCH002_REDACTED ALTERNATE: PGE_DR-058_20260501_RESPONSE_Q002_ATCH001.xlsx
2026-04-06 | 2026-04-24 | VM-18 | DR059 | PGE_2025_DR-058_20260501_RESPONSE BASE: PGE_DR-058_20260501_RESPONSE_Q001_ATCH001.xlsx PGE_DR-058_20260501_RESPONSE_Q001_ATCH002_REDACTED ALTERNATE: PGE_DR-058_20260501_RESPONSE_Q002_ATCH001.xlsx
2026-04-06 | 2026-05-08 | VM-22 | DR060 | PGE_2025_DR-060_20260508_RESPONSE PGE_DR-060_20260508_RESPONSE_CONF DECLARATION BASE: PGE_DR-060_20260508_RESPONSE_Q001_ATCH001.xlsx PGE_DR-060_20260508_RESPONSE_Q001_ATCH002_CONF.xlsx PGE_DR-060_20260508_RESPONSE_Q001_ATCH002_REDACTED.xlsx PGE_DR-060_20260508_RESPONSE_Q001_ATCH003.xlsx ALTERNATE: PGE_DR-060_20260508_RESPONSE_Q002_ATCH001-ATCH003.xlsx (4)
2026-04-13 | 2026-04-16 | GH-05 | DR025 | PGE_2026_DR-025_20260416_RESPONSE PGE_DR-025_20260416_RESPONSE_CONF DECLARATION PGE_DR-025_20260416_RESPONSE_Q001_ATCH001 (2)
2026-04-17 | 2026-04-22 | CO-01 | DR016 | PGE_2025_DR-016_20260422_RESPONSE PGE_DR-016_20260422_RESPONSE_CONF DECLARATION PGE_DR-016_20260422_RESPONSE_Q001_ATCH001 CONF: 001_Q1 REGIONAL TOWNHALL_20250311_CONF 002_Q1 REGIONAL TOWNHALL_20250312_CONF 003_Q1 REGIONAL TOWNHALL_20250318_CONF 004_Q1 REGIONAL TOWNHALL_20250320_CONF 005_Q1 REGIONAL TOWNHALL_20250327_CONF 006_WILDFIRE SAFETY WEBINAR #1_20250327_CONF 007_WILDFIRE SAFETY WEBINAR #2_20250514_CONF 008_IN-PERSON OPEN HOUSE_20250515_CONF 009_WILDFIRE SAFETY WEBINAR #3_20250522_CONF 010_WILDFIRE SAFETY WEBINAR #4_20250528_CONF 011_WILDFIRE SAFETY WEBINAR #5_20250604_CONF 012_WILDFIRE SAFETY WEBINAR #6_20250605_CONF 013_WILDFIRE SAFETY WEBINAR #7_20250610_CONF 014_WILDFIRE SAFETY WEBINAR #8_20250624_CONF 015_WILDFIRE SAFETY WEBINAR #9_20250625_CONF 016_IN-PERSON OPEN HOUSE_20250701_CONF 017_Q2 REGIONAL TOWNHALL_20250820_CONF 018_Q2 REGIONAL TOWNHALL_20250826_CONF 019_Q2 REGIONAL TOWNHALL_20250903_CONF 020_Q2 REGIONAL TOWNHALL_20250904_CONF 021_Q2 REGIONAL TOWNHALL_20250909_CONF 022_Q2 REGIONAL TOWNHALL_20250910_CONF REDACTED: PGE_2025_DR016-20260422_RESPONSE PGE_DR-016_20260422_RESPONSE_CONF DECLARATION PGE)DR-016_20260422_RESPONSE_Q001_ATCH001.xlsx
2026-04-22 | Void | QAQC Program | DR004
2026-04-24 | 2026-05-08 | QAQC Program | DR004.b | PGE_DR-004.b_20260508_QUESTIONNAIRE PGE_DR-004.b_20260508_RESPONSE PGE_DR-004.b_20260508_RESPONSE_Q010_ATCH001-ATCH011 (11)
2026-05-08 | 2026-05-15 | GH-01 | DR022 | PGE_2025_DR-022_20260518_RESPONSE PGE_DR-022_20260518_RESPONSE_Q001_ATCH001.xlsx PGE_DR-022_20260518_RESPONSE_Q001_ATCH002-ATCH006 (5) PGE_DR-022_20260518_SUPP_RESPONSE_CONF DECLARATION
2026-05-08 | 2026-05-15 | GH-04 | DR024 | PGE_2025_DR-024_20260518_RESPONSE_D002 PGE_DR-024_20260518_RESPONSE_Q001_ATCH001.xlsx PGE_DR-024_20260518_RESPONSE_ATCH002-ATCH006 (5) PGE_DR-024_20260518_SUPP_RESPONSE_CONF DECLARATION
2026-05-08 | 2026-05-13 | GH-11 | DR028 | PGE_2025_DR-028_20260513_RESPONSE PGE_DR-028_20260513_RESPONSE_CONF DECLARATION PGE_DR-028_20260513_RESPONSE_Q001_ATCH001-ATCH002 (4)
2026-05-14 | 2026-05-22 | Financials | DR005 | PGE_2025_DR-005_20260520_RESPONSE_D-001 PGE_2025_DR-005_20260520_RESPONSE_D-002

## Tab 4 - SME Interviews
SME Interviews
Independent Evaluator: | Bureau Veritas North America
Electrical Corporation: | Pacific Gas & Electric
Interview date | Section / Initiative | SME interview number | Positions interviewed | Summary of interview