## Index
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
Dataset Index
Background
This supplemental excel file supports this Workpaper EPSS Toy Problem (Attach. B, WP016A) by providing example data that traces how raw WDRM model outputs flow through six datasets to calculate final circuit segment EPSS outage risk. This file includes examples for three circuit segments representing high, medium, and low risk levels.
Worksheet | Word Doc Reference | Data Set Name
1-high_risk_wdrm_pof | Dataset 1 | Raw WDRM PoF
2-high_risk_epss_enablement | Dataset 2 | EPSS Enablement
3-high_risk_sustain_outage_frac | Dataset 3 | Sustained Outage Fraction
4-high_risk_cs_epss_pof | Dataset 4 | EPSS PoF
5-high_risk_cs-consequence | Dataset 5 | Consequence
6-high_risk_cs_epss_outage_risk | Dataset 6 | Final EPSS Outage Risk
1-med_risk_wdrm_pof | Dataset 1 | Raw WDRM PoF
2-med_risk_epss_enablement | Dataset 2 | EPSS Enablement
3-med_risk_sustain_outage_frac | Dataset 3 | Sustained Outage Fraction
4-med_risk_cs_epss_pof | Dataset 4 | EPSS PoF
5-med_risk_cs-consequence | Dataset 5 | Consequence
6-med_risk_cs_epss_outage_risk | Dataset 6 | Final EPSS Outage Risk
1-low_risk_wdrm_pof | Dataset 1 | Raw WDRM PoF
2-low_risk_epss_enablement | Dataset 2 | EPSS Enablement
3-low_risk_sustain_outage_frac | Dataset 3 | Sustained Outage Fraction
4-low_risk_cs_epss_pof | Dataset 4 | EPSS PoF
5-low_risk_cs-consequence | Dataset 5 | Consequence
6-low_risk_cs_epss_outage_risk | Dataset 6 | Final EPSS Outage Risk

## 1-high_risk_wdrm_pof
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
High Risk WDRM PoF
cs_name | circuit_name | primary_conductor_line_slap_cause | primary_conductor_wire_down_cause | primary_conductor_other_cause | third_party_balloon | third_party_other | vegetation_branch | vegetation_trunk | vegetation_other | other_equipment_type | secondary_conductor | capacitor_bank_equipment_cause | dpd_equipment_cause | fuse_equipment_cause | support_structure_equipment_cause | support_structure_electrical_cause | switch_equipment_cause | transformer_equipment_cause | transformer_equipment_leaking | voltage_regulator_equipment_cause | animal_bird | animal_squirrel | animal_other | third_party_vehicle
TEMPLETON 2113CB | TEMPLETON 2113 | 0.035219 | 0.2634 | 0.1366 | 0.028116 | 0.069254 | 0.20616 | 0.092856 | 0.040475 | 3.1961 | 0.073366 | 0.014085 | 0.0085901 | 0.059586 | 0.17232 | 0.11268 | 0.011105 | 0.61007 | 0.028465 | null | 0.60932 | 0.11776 | 0.056717 | 0.19684
Note: The rates above reflect the expected outage count during wildfire season for that specific failure mode

## 2-high_risk_epss_enablement
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
High Risk EPSS Enablement
circuit_id | circuit_name | total_days_epss_enabled | total_days_wf_season | epss_enablement
183052113 | TEMPLETON 2113 | 1227 | 1281 | 0.95785

## 3-high_risk_sustain_outage_frac
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
High Risk Sustained Outage Fraction
subset_name | outage_count | sustained_outage_count | sustained_outage_fraction
vegetation_trunk | 5090 | 5001 | 0.98251
other_equipment_type | 33470 | 22310 | 0.66657
third_party_other | 1356 | 1307 | 0.96386
third_party_balloon | 643 | 575 | 0.89425
primary_conductor_other_cause | 1317 | 1239 | 0.94077
transformer_equipment_leaking | 0 | 0 | 0
vegetation_other | 3434 | 3292 | 0.95865
primary_conductor_line_slap_cause | 457 | 435 | 0.95186
voltage_regulator_equipment_cause | 157 | 111 | 0.70701
primary_conductor_wire_down_cause | 2836 | 2697 | 0.95099
third_party_vehicle | 3788 | 3494 | 0.92239
animal_other | 401 | 382 | 0.95262
capacitor_bank_equipment_cause | 82 | 53 | 0.64634
support_structure_equipment_cause | 1069 | 1036 | 0.96913
support_structure_electrical_cause | 1749 | 1684 | 0.96284
animal_bird | 4498 | 4318 | 0.95998
switch_equipment_cause | 0 | 0 | 0
vegetation_branch | 5693 | 5585 | 0.98103
animal_squirrel | 4336 | 4176 | 0.9631
dpd_equipment_cause | 331 | 225 | 0.67976
secondary_conductor | 1591 | 1578 | 0.99183
fuse_equipment_cause | 3409 | 3332 | 0.97741
transformer_equipment_cause | 0 | 0 | 0

## 4-high_risk_cs_epss_pof
Workpaper 016B | [9 empty] | Workpaper 016B | [9 empty] | Workpaper 016B | [9 empty] | Workpaper 016B | [8 empty] | Workpaper 016B
Pacific Gas and Electric Company | [9 empty] | Pacific Gas and Electric Company | [9 empty] | Pacific Gas and Electric Company | [9 empty] | Pacific Gas and Electric Company | [8 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [9 empty] | Electrical Undergrounding Program | [9 empty] | Electrical Undergrounding Program | [9 empty] | Electrical Undergrounding Program | [8 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [9 empty] | EPSS Toy Problem Calculations | [9 empty] | EPSS Toy Problem Calculations | [9 empty] | EPSS Toy Problem Calculations | [8 empty] | EPSS Toy Problem Calculations
High Risk EPSS PoF | [9 empty] | High Risk EPSS PoF | [9 empty] | High Risk EPSS PoF | [9 empty] | High Risk EPSS PoF | [8 empty] | High Risk EPSS PoF
[10 empty] | (Continued) | [9 empty] | (Continued) | [9 empty] | (Continued) | [8 empty] | (Continued)
cs_name | circuit_name | prob_epss_failure_primary_conductor_line_slap_cause | prob_epss_failure_primary_conductor_wire_down_cause | prob_epss_failure_primary_conductor_other_cause | prob_epss_failure_third_party_balloon | prob_epss_failure_third_party_other | prob_epss_failure_vegetation_branch | prob_epss_failure_vegetation_trunk | prob_epss_failure_vegetation_other | prob_epss_failure_other_equipment_type | prob_epss_failure_secondary_conductor | prob_epss_failure_capacitor_bank_equipment_cause | prob_epss_failure_dpd_equipment_cause | prob_epss_failure_fuse_equipment_cause | prob_epss_failure_support_structure_equipment_cause | prob_epss_failure_support_structure_electrical_cause | prob_epss_failure_switch_equipment_cause | prob_epss_failure_transformer_equipment_cause | prob_epss_failure_transformer_equipment_leaking | prob_epss_failure_voltage_regulator_equipment_cause | prob_epss_failure_animal_bird | prob_epss_failure_animal_squirrel | prob_epss_failure_animal_other | prob_epss_failure_third_party_vehicle | prob_non_epss_failure_primary_conductor_line_slap_cause | prob_non_epss_failure_primary_conductor_wire_down_cause | prob_non_epss_failure_primary_conductor_other_cause | prob_non_epss_failure_third_party_balloon | prob_non_epss_failure_third_party_other | prob_non_epss_failure_vegetation_branch | prob_non_epss_failure_vegetation_trunk | prob_non_epss_failure_vegetation_other | prob_non_epss_failure_other_equipment_type | prob_non_epss_failure_secondary_conductor | prob_non_epss_failure_capacitor_bank_equipment_cause | prob_non_epss_failure_dpd_equipment_cause | prob_non_epss_failure_fuse_equipment_cause | prob_non_epss_failure_support_structure_equipment_cause | prob_non_epss_failure_support_structure_electrical_cause | prob_non_epss_failure_switch_equipment_cause | prob_non_epss_failure_transformer_equipment_cause | prob_non_epss_failure_transformer_equipment_leaking | prob_non_epss_failure_voltage_regulator_equipment_cause | prob_non_epss_failure_animal_bird | prob_non_epss_failure_animal_squirrel | prob_non_epss_failure_animal_other | prob_non_epss_failure_third_party_vehicle
TEMPLETON 2113CB | TEMPLETON 2113 | 0.033735 | 0.25229 | 0.13084 | 0.02693 | 0.066334 | 0.19747 | 0.088942 | 0.038769 | 3.0614 | 0.070274 | 0.013491 | 0.008228 | 0.057074 | 0.16505 | 0.10793 | 0 | 0 | 0 | 0 | 0.58363 | 0.11279 | 0.054326 | 0.18855 | 0.032111 | 0.23993 | 0.12309 | 0.024082 | 0.063937 | 0.19373 | 0.087387 | 0.037166 | 2.0406 | 0.069699 | 0.0087198 | 0.005593 | 0.055785 | 0.15996 | 0.10391 | 0 | 0 | 0 | 0 | 0.56028 | 0.10863 | 0.051752 | 0.17391

## 5-high_risk_cs-consequence
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
High Risk Consequence
cs_name | circuit_name | conductor_outage_expected_duration | conductor_outage_avg_customer_value_of_service | conductor_outage_mean_customers_impacted_by_EPSS | conductor_outage_mean_customers_impacted_by_non_EPSS | structure_outage_expected_duration | structure_outage_avg_customer_value_of_service | structure_outage_mean_customers_impacted_by_EPSS | structure_outage_mean_customers_impacted_by_non_EPSS | dollarized_consequence_with_epss_enabled_on_support_structures | dollarized_consequence_with_epss_disabled_on_support_structures | dollarized_consequence_with_epss_enabled_on_conductors | dollarized_consequence_with_epss_disabled_on_conductors | cmi_consequence_with_epss_enabled_on_support_structures | cmi_consequence_with_epss_disabled_on_support_structures | cmi_consequence_with_epss_enabled_on_conductors | cmi_consequence_with_epss_disabled_on_conductors
TEMPLETON 2113CB | TEMPLETON 2113 | 238.7726 | 3.9261 | 4946 | 1839.2887 | 248.9813 | 3.3868 | 3750.3093 | 1325.9629 | 3162401.3042 | 1118101.6116 | 4636596.4642 | 1724229.5891 | 933756.6961 | 330139.9052 | 1180969.3514 | 439171.7751

## 6-high_risk_cs_epss_outage_risk
Workpaper 016B | [10 empty] | Workpaper 016B | [9 empty] | Workpaper 016B
Pacific Gas and Electric Company | [10 empty] | Pacific Gas and Electric Company | [9 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [10 empty] | Electrical Undergrounding Program | [9 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [10 empty] | EPSS Toy Problem Calculations | [9 empty] | EPSS Toy Problem Calculations
High Risk EPSS Outage Risk | [10 empty] | High Risk EPSS Outage Risk | [9 empty] | High Risk EPSS Outage Risk
[11 empty] | (Continued) | [9 empty] | (Continued)
cs_name | circuit_name | epss_outage_risk_dollarized | epss_outage_annual_cmi | epss_outage_likelihood | epss_outage_consequence_dollarized | epss_outage_expected_outage_count_per_wf_season | epss_outage_risk_dollarized_primary_conductor_line_slap_cause | epss_outage_risk_dollarized_primary_conductor_wire_down_cause | epss_outage_risk_dollarized_primary_conductor_other_cause | epss_outage_risk_dollarized_third_party_balloon | epss_outage_risk_dollarized_third_party_other | epss_outage_risk_dollarized_vegetation_branch | epss_outage_risk_dollarized_vegetation_trunk | epss_outage_risk_dollarized_vegetation_other | epss_outage_risk_dollarized_other_equipment_type | epss_outage_risk_dollarized_secondary_conductor | epss_outage_risk_dollarized_capacitor_bank_equipment_cause | epss_outage_risk_dollarized_dpd_equipment_cause | epss_outage_risk_dollarized_fuse_equipment_cause | epss_outage_risk_dollarized_support_structure_equipment_cause | epss_outage_risk_dollarized_support_structure_electrical_cause | epss_outage_risk_dollarized_switch_equipment_cause | epss_outage_risk_dollarized_transformer_equipment_cause | epss_outage_risk_dollarized_transformer_equipment_leaking | epss_outage_risk_dollarized_voltage_regulator_equipment_cause | epss_outage_risk_dollarized_animal_bird | epss_outage_risk_dollarized_animal_squirrel | epss_outage_risk_dollarized_animal_other | epss_outage_risk_dollarized_third_party_vehicle
TEMPLETON 2113CB | TEMPLETON 2113 | 16082076.3092 | 4206095.6806 | 1268.6631 | 12676.3959 | 1.1178 | 101048.2672 | 756088.235 | 394409.9459 | 83341.6446 | 197323.3609 | 581568.9608 | 261713.2829 | 115673.5751 | 10676009.3134 | 205652.4519 | 32914.3157 | 19766.5303 | 118117.5731 | 343115.5863 | 225116.8309 | 0 | 0 | 0 | 0 | 1219235.3299 | 235238.1151 | 113937.0928 | 401805.8974

## 1-med_risk_wdrm_pof
Workpaper 016B | [7 empty] | Workpaper 016B | [7 empty] | Workpaper 016B
Pacific Gas and Electric Company | [7 empty] | Pacific Gas and Electric Company | [7 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [7 empty] | Electrical Undergrounding Program | [7 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [7 empty] | EPSS Toy Problem Calculations | [7 empty] | EPSS Toy Problem Calculations
Medium Risk WDRM PoF | [7 empty] | Medium Risk WDRM PoF | [7 empty] | Medium Risk WDRM PoF
[8 empty] | (Continued) | [7 empty] | (Continued)
cs_name | circuit_name | primary_conductor_line_slap_cause | primary_conductor_wire_down_cause | primary_conductor_other_cause | third_party_balloon | third_party_other | vegetation_branch | vegetation_trunk | vegetation_other | other_equipment_type | secondary_conductor | capacitor_bank_equipment_cause | dpd_equipment_cause | fuse_equipment_cause | support_structure_equipment_cause | support_structure_electrical_cause | switch_equipment_cause | transformer_equipment_cause | transformer_equipment_leaking | voltage_regulator_equipment_cause | animal_bird | animal_squirrel | animal_other | third_party_vehicle
SAN BENITO 210488772 | SAN BENITO 2104 | 0.070924 | 0.73814 | 0.36058 | 0.071865 | 0.18762 | 0.75553 | 0.45945 | 0.17333 | 5.0952 | 0.15297 | 0.0031803 | null | 0.26257 | 0.38686 | 0.22923 | 0.010506 | 1.4148 | 0.056206 | null | 0.91958 | 0.20637 | 0.028623 | 0.64129
**The rates above reflect the expected outage count during wildfire season for that specific failure mode

## 2-med_risk_epss_enablement
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
Medium Risk EPSS Enablement
circuit_id | circuit_name | total_days_epss_enabled | total_days_wf_season | epss_enablement
182742104 | SAN BENITO 2104 | 625 | 1281 | 0.4879

## 3-med_risk_sustain_outage_frac
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
Medium Risk Sustained Outage Fraction
subset_name | outage_count | sustained_outage_count | sustained_outage_fraction
vegetation_trunk | 5090 | 5001 | 0.98251
other_equipment_type | 33470 | 22310 | 0.66657
third_party_other | 1356 | 1307 | 0.96386
third_party_balloon | 643 | 575 | 0.89425
primary_conductor_other_cause | 1317 | 1239 | 0.94077
transformer_equipment_leaking | 0 | 0 | 0
vegetation_other | 3434 | 3292 | 0.95865
primary_conductor_line_slap_cause | 457 | 435 | 0.95186
voltage_regulator_equipment_cause | 157 | 111 | 0.70701
primary_conductor_wire_down_cause | 2836 | 2697 | 0.95099
third_party_vehicle | 3788 | 3494 | 0.92239
animal_other | 401 | 382 | 0.95262
capacitor_bank_equipment_cause | 82 | 53 | 0.64634
support_structure_equipment_cause | 1069 | 1036 | 0.96913
support_structure_electrical_cause | 1749 | 1684 | 0.96284
animal_bird | 4498 | 4318 | 0.95998
switch_equipment_cause | 0 | 0 | 0
vegetation_branch | 5693 | 5585 | 0.98103
animal_squirrel | 4336 | 4176 | 0.9631
dpd_equipment_cause | 331 | 225 | 0.67976
secondary_conductor | 1591 | 1578 | 0.99183
fuse_equipment_cause | 3409 | 3332 | 0.97741
transformer_equipment_cause | 0 | 0 | 0

## 4-med_risk_cs_epss_pof
Workpaper 016B | [16 empty] | Workpaper 016B | [15 empty] | Workpaper 016B
Pacific Gas and Electric Company | [16 empty] | Pacific Gas and Electric Company | [15 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [16 empty] | Electrical Undergrounding Program | [15 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [16 empty] | EPSS Toy Problem Calculations | [15 empty] | EPSS Toy Problem Calculations
Medium Risk EPSS PoF | [16 empty] | Medium Risk EPSS PoF | [15 empty] | Medium Risk EPSS PoF
[17 empty] | (Continued) | [15 empty] | (Continued)
cs_name | circuit_name | prob_epss_failure_primary_conductor_line_slap_cause | prob_epss_failure_primary_conductor_wire_down_cause | prob_epss_failure_primary_conductor_other_cause | prob_epss_failure_third_party_balloon | prob_epss_failure_third_party_other | prob_epss_failure_vegetation_branch | prob_epss_failure_vegetation_trunk | prob_epss_failure_vegetation_other | prob_epss_failure_other_equipment_type | prob_epss_failure_secondary_conductor | prob_epss_failure_capacitor_bank_equipment_cause | prob_epss_failure_dpd_equipment_cause | prob_epss_failure_fuse_equipment_cause | prob_epss_failure_support_structure_equipment_cause | prob_epss_failure_support_structure_electrical_cause | prob_epss_failure_switch_equipment_cause | prob_epss_failure_transformer_equipment_cause | prob_epss_failure_transformer_equipment_leaking | prob_epss_failure_voltage_regulator_equipment_cause | prob_epss_failure_animal_bird | prob_epss_failure_animal_squirrel | prob_epss_failure_animal_other | prob_epss_failure_third_party_vehicle | prob_non_epss_failure_primary_conductor_line_slap_cause | prob_non_epss_failure_primary_conductor_wire_down_cause | prob_non_epss_failure_primary_conductor_other_cause | prob_non_epss_failure_third_party_balloon | prob_non_epss_failure_third_party_other | prob_non_epss_failure_vegetation_branch | prob_non_epss_failure_vegetation_trunk | prob_non_epss_failure_vegetation_other | prob_non_epss_failure_other_equipment_type | prob_non_epss_failure_secondary_conductor | prob_non_epss_failure_capacitor_bank_equipment_cause | prob_non_epss_failure_dpd_equipment_cause | prob_non_epss_failure_fuse_equipment_cause | prob_non_epss_failure_support_structure_equipment_cause | prob_non_epss_failure_support_structure_electrical_cause | prob_non_epss_failure_switch_equipment_cause | prob_non_epss_failure_transformer_equipment_cause | prob_non_epss_failure_transformer_equipment_leaking | prob_non_epss_failure_voltage_regulator_equipment_cause | prob_non_epss_failure_animal_bird | prob_non_epss_failure_animal_squirrel | prob_non_epss_failure_animal_other | prob_non_epss_failure_third_party_vehicle
SAN BENITO 210488772 | SAN BENITO 2104 | 0.034604 | 0.36014 | 0.17593 | 0.035063 | 0.091539 | 0.36862 | 0.22417 | 0.084569 | 2.486 | 0.074633 | 0.0015517 | 0 | 0.12811 | 0.18875 | 0.11184 | 0 | 0 | 0 | 0 | 0.44866 | 0.10069 | 0.013965 | 0.31289 | 0.032938 | 0.34249 | 0.16551 | 0.031355 | 0.088231 | 0.36163 | 0.22025 | 0.081072 | 1.6571 | 0.074023 | 0.0010029 | 0 | 0.12522 | 0.18292 | 0.10769 | 0 | 0 | 0 | 0 | 0.43071 | 0.096974 | 0.013303 | 0.2886

## 5-med_risk_cs-consequence
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
Medium Risk Consequence
cs_name | circuit_name | conductor_outage_expected_duration | conductor_outage_avg_customer_value_of_service | conductor_outage_mean_customers_impacted_by_EPSS | conductor_outage_mean_customers_impacted_by_non_EPSS | structure_outage_expected_duration | structure_outage_avg_customer_value_of_service | structure_outage_mean_customers_impacted_by_EPSS | structure_outage_mean_customers_impacted_by_non_EPSS | dollarized_consequence_with_epss_enabled_on_support_structures | dollarized_consequence_with_epss_disabled_on_support_structures | dollarized_consequence_with_epss_enabled_on_conductors | dollarized_consequence_with_epss_disabled_on_conductors | cmi_consequence_with_epss_enabled_on_support_structures | cmi_consequence_with_epss_disabled_on_support_structures | cmi_consequence_with_epss_enabled_on_conductors | cmi_consequence_with_epss_disabled_on_conductors
SAN BENITO 210488772 | SAN BENITO 2104 | 255.8051 | 2.6263 | 1221 | 184.051 | 262.7938 | 2.6308 | 1222.024 | 199.8962 | 844846.4 | 138198.2784 | 820297.8567 | 123649.9981 | 321140.3242 | 52531.4897 | 312338.0151 | 47081.1848

## 6-med_risk_cs_epss_outage_risk
Workpaper 016B | [9 empty] | Workpaper 016B | [10 empty] | Workpaper 016B
Pacific Gas and Electric Company | [9 empty] | Pacific Gas and Electric Company | [10 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [9 empty] | Electrical Undergrounding Program | [10 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [9 empty] | EPSS Toy Problem Calculations | [10 empty] | EPSS Toy Problem Calculations
Medium Risk EPSS Outage Risk | [9 empty] | Medium Risk EPSS Outage Risk | [10 empty] | Medium Risk EPSS Outage Risk
[10 empty] | (Continued) | [10 empty] | (Continued)
cs_name | circuit_name | epss_outage_risk_dollarized | epss_outage_annual_cmi | epss_outage_likelihood | epss_outage_consequence_dollarized | epss_outage_expected_outage_count_per_wf_season | epss_outage_risk_dollarized_primary_conductor_line_slap_cause | epss_outage_risk_dollarized_primary_conductor_wire_down_cause | epss_outage_risk_dollarized_primary_conductor_other_cause | epss_outage_risk_dollarized_third_party_balloon | epss_outage_risk_dollarized_third_party_other | epss_outage_risk_dollarized_vegetation_branch | epss_outage_risk_dollarized_vegetation_trunk | epss_outage_risk_dollarized_vegetation_other | epss_outage_risk_dollarized_other_equipment_type | epss_outage_risk_dollarized_secondary_conductor | epss_outage_risk_dollarized_capacitor_bank_equipment_cause | epss_outage_risk_dollarized_dpd_equipment_cause | epss_outage_risk_dollarized_fuse_equipment_cause | epss_outage_risk_dollarized_support_structure_equipment_cause | epss_outage_risk_dollarized_support_structure_electrical_cause | epss_outage_risk_dollarized_switch_equipment_cause | epss_outage_risk_dollarized_transformer_equipment_cause | epss_outage_risk_dollarized_transformer_equipment_leaking | epss_outage_risk_dollarized_voltage_regulator_equipment_cause | epss_outage_risk_dollarized_animal_bird | epss_outage_risk_dollarized_animal_squirrel | epss_outage_risk_dollarized_animal_other | epss_outage_risk_dollarized_third_party_vehicle
SAN BENITO 210488772 | SAN BENITO 2104 | 3781857.1751 | 1439385.6867 | 1349.9769 | 2801.4237 | 0.94071 | 24312.7214 | 253072.4381 | 123847.8994 | 24884.86 | 64179.3992 | 257664.1937 | 156650.5959 | 59347.0352 | 1834327.4161 | 52068.0284 | 1172.3293 | 0 | 90928.7188 | 134183.7538 | 79608.3872 | 0 | 0 | 0 | 0 | 319526.9842 | 71665.56 | 9959.8466 | 224457.0078

## 1-low_risk_wdrm_pof
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
Low Risk WDRM PoF
cs_name | circuit_name | primary_conductor_line_slap_cause | primary_conductor_wire_down_cause | primary_conductor_other_cause | third_party_balloon | third_party_other | vegetation_branch | vegetation_trunk | vegetation_other | other_equipment_type | secondary_conductor | capacitor_bank_equipment_cause | dpd_equipment_cause | fuse_equipment_cause | support_structure_equipment_cause | support_structure_electrical_cause | switch_equipment_cause | transformer_equipment_cause | transformer_equipment_leaking | voltage_regulator_equipment_cause | animal_bird | animal_squirrel | animal_other | third_party_vehicle
OAKLAND K 1103CR188 | OAKLAND K 1103 | 0.012073 | 0.12698 | 0.045042 | 0.006691 | 0.028048 | 0.25045 | 0.17325 | 0.10555 | 0.40509 | 0.020374 | 0.002777 | null | 0.024006 | 0.060423 | 0.027779 | 0.0038586 | 0.2068 | 0.016832 | null | 0.028524 | 0.10608 | 0.0053182 | 0.062522
**The rates above reflect the expected outage count during wildfire season for that specific failure mode

## 2-low_risk_epss_enablement
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
Low Risk EPSS Enablement
circuit_id | circuit_name | total_days_epss_enabled | total_days_wf_season | epss_enablement
12101103 | OAKLAND K 1103 | 139 | 1281 | 0.10851

## 3-low_risk_sustain_outage_frac
Workpaper 016B
Pacific Gas and Electric Company
Electrical Undergrounding Program
EPSS Toy Problem Calculations
Low Risk Sustained Outage Fraction
subset_name | outage_count | sustained_outage_count | sustained_outage_fraction
vegetation_trunk | 5090 | 5001 | 0.98251
other_equipment_type | 33470 | 22310 | 0.66657
third_party_other | 1356 | 1307 | 0.96386
third_party_balloon | 643 | 575 | 0.89425
primary_conductor_other_cause | 1317 | 1239 | 0.94077
transformer_equipment_leaking | 0 | 0 | 0
vegetation_other | 3434 | 3292 | 0.95865
primary_conductor_line_slap_cause | 457 | 435 | 0.95186
voltage_regulator_equipment_cause | 157 | 111 | 0.70701
primary_conductor_wire_down_cause | 2836 | 2697 | 0.95099
third_party_vehicle | 3788 | 3494 | 0.92239
animal_other | 401 | 382 | 0.95262
capacitor_bank_equipment_cause | 82 | 53 | 0.64634
support_structure_equipment_cause | 1069 | 1036 | 0.96913
support_structure_electrical_cause | 1749 | 1684 | 0.96284
animal_bird | 4498 | 4318 | 0.95998
switch_equipment_cause | 0 | 0 | 0
vegetation_branch | 5693 | 5585 | 0.98103
animal_squirrel | 4336 | 4176 | 0.9631
dpd_equipment_cause | 331 | 225 | 0.67976
secondary_conductor | 1591 | 1578 | 0.99183
fuse_equipment_cause | 3409 | 3332 | 0.97741
transformer_equipment_cause | 0 | 0 | 0

## 4-low_risk_cs_epss_pof
Workpaper 016B | [11 empty] | Workpaper 016B | [11 empty] | Workpaper 016B | [11 empty] | Workpaper 016B
Pacific Gas and Electric Company | [11 empty] | Pacific Gas and Electric Company | [11 empty] | Pacific Gas and Electric Company | [11 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [11 empty] | Electrical Undergrounding Program | [11 empty] | Electrical Undergrounding Program | [11 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [11 empty] | EPSS Toy Problem Calculations | [11 empty] | EPSS Toy Problem Calculations | [11 empty] | EPSS Toy Problem Calculations
Low Risk EPSS PoF | [11 empty] | Low Risk EPSS PoF | [11 empty] | Low Risk EPSS PoF | [11 empty] | Low Risk EPSS PoF
[12 empty] | (Continued) | [11 empty] | (Continued) | [11 empty] | (Continued)
cs_name | circuit_name | prob_epss_failure_primary_conductor_line_slap_cause | prob_epss_failure_primary_conductor_wire_down_cause | prob_epss_failure_primary_conductor_other_cause | prob_epss_failure_third_party_balloon | prob_epss_failure_third_party_other | prob_epss_failure_vegetation_branch | prob_epss_failure_vegetation_trunk | prob_epss_failure_vegetation_other | prob_epss_failure_other_equipment_type | prob_epss_failure_secondary_conductor | prob_epss_failure_capacitor_bank_equipment_cause | prob_epss_failure_dpd_equipment_cause | prob_epss_failure_fuse_equipment_cause | prob_epss_failure_support_structure_equipment_cause | prob_epss_failure_support_structure_electrical_cause | prob_epss_failure_switch_equipment_cause | prob_epss_failure_transformer_equipment_cause | prob_epss_failure_transformer_equipment_leaking | prob_epss_failure_voltage_regulator_equipment_cause | prob_epss_failure_animal_bird | prob_epss_failure_animal_squirrel | prob_epss_failure_animal_other | prob_epss_failure_third_party_vehicle | prob_non_epss_failure_primary_conductor_line_slap_cause | prob_non_epss_failure_primary_conductor_wire_down_cause | prob_non_epss_failure_primary_conductor_other_cause | prob_non_epss_failure_third_party_balloon | prob_non_epss_failure_third_party_other | prob_non_epss_failure_vegetation_branch | prob_non_epss_failure_vegetation_trunk | prob_non_epss_failure_vegetation_other | prob_non_epss_failure_other_equipment_type | prob_non_epss_failure_secondary_conductor | prob_non_epss_failure_capacitor_bank_equipment_cause | prob_non_epss_failure_dpd_equipment_cause | prob_non_epss_failure_fuse_equipment_cause | prob_non_epss_failure_support_structure_equipment_cause | prob_non_epss_failure_support_structure_electrical_cause | prob_non_epss_failure_switch_equipment_cause | prob_non_epss_failure_transformer_equipment_cause | prob_non_epss_failure_transformer_equipment_leaking | prob_non_epss_failure_voltage_regulator_equipment_cause | prob_non_epss_failure_animal_bird | prob_non_epss_failure_animal_squirrel | prob_non_epss_failure_animal_other | prob_non_epss_failure_third_party_vehicle
OAKLAND K 1103CR188 | OAKLAND K 1103 | 0.0013101 | 0.013778 | 0.0048874 | 0.00072604 | 0.0030434 | 0.027176 | 0.018799 | 0.011453 | 0.043955 | 0.0022108 | 0.00030132 | 0 | 0.0026049 | 0.0065564 | 0.0030143 | 0 | 0 | 0 | 0 | 0.0030951 | 0.01151 | 0.00057707 | 0.0067842 | 0.001247 | 0.013103 | 0.004598 | 0.00064926 | 0.0029334 | 0.026661 | 0.01847 | 0.01098 | 0.029299 | 0.0021927 | 0.00019476 | 0 | 0.002546 | 0.006354 | 0.0029023 | 0 | 0 | 0 | 0 | 0.0029713 | 0.011086 | 0.00054973 | 0.0062577

## 5-low_risk_cs-consequence
Workpaper 016B | [5 empty] | Workpaper 016B | [5 empty] | Workpaper 016B
Pacific Gas and Electric Company | [5 empty] | Pacific Gas and Electric Company | [5 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [5 empty] | Electrical Undergrounding Program | [5 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [5 empty] | EPSS Toy Problem Calculations | [5 empty] | EPSS Toy Problem Calculations
Low Risk Consequence | [5 empty] | Low Risk Consequence | [5 empty] | Low Risk Consequence
[6 empty] | (Continued) | [5 empty] | (Continued)
cs_name | circuit_name | conductor_outage_expected_duration | conductor_outage_avg_customer_value_of_service | conductor_outage_mean_customers_impacted_by_EPSS | conductor_outage_mean_customers_impacted_by_non_EPSS | structure_outage_expected_duration | structure_outage_avg_customer_value_of_service | structure_outage_mean_customers_impacted_by_EPSS | structure_outage_mean_customers_impacted_by_non_EPSS | dollarized_consequence_with_epss_enabled_on_support_structures | dollarized_consequence_with_epss_disabled_on_support_structures | dollarized_consequence_with_epss_enabled_on_conductors | dollarized_consequence_with_epss_disabled_on_conductors | cmi_consequence_with_epss_enabled_on_support_structures | cmi_consequence_with_epss_disabled_on_support_structures | cmi_consequence_with_epss_enabled_on_conductors | cmi_consequence_with_epss_disabled_on_conductors
OAKLAND K 1103CR188 | OAKLAND K 1103 | 250.5506 | 1.2177 | 668 | 241.9615 | 259.7216 | 1.2151 | 683.1538 | 193.1327 | 215592.4459 | 60949.5968 | 203805.3853 | 73821.9529 | 177429.806 | 50160.7331 | 167367.8096 | 60623.6118

## 6-low_risk_cs_epss_outage_risk
Workpaper 016B | [8 empty] | Workpaper 016B | [9 empty] | Workpaper 016B
Pacific Gas and Electric Company | [8 empty] | Pacific Gas and Electric Company | [9 empty] | Pacific Gas and Electric Company
Electrical Undergrounding Program | [8 empty] | Electrical Undergrounding Program | [9 empty] | Electrical Undergrounding Program
EPSS Toy Problem Calculations | [8 empty] | EPSS Toy Problem Calculations | [9 empty] | EPSS Toy Problem Calculations
Low Risk EPSS Outage Risk | [8 empty] | Low Risk EPSS Outage Risk | [9 empty] | Low Risk EPSS Outage Risk
[9 empty] | (Continued) | [9 empty] | (Continued)
cs_name | circuit_name | epss_outage_risk_dollarized | epss_outage_annual_cmi | epss_outage_likelihood | epss_outage_consequence_dollarized | epss_outage_expected_outage_count_per_wf_season | epss_outage_risk_dollarized_primary_conductor_line_slap_cause | epss_outage_risk_dollarized_primary_conductor_wire_down_cause | epss_outage_risk_dollarized_primary_conductor_other_cause | epss_outage_risk_dollarized_third_party_balloon | epss_outage_risk_dollarized_third_party_other | epss_outage_risk_dollarized_vegetation_branch | epss_outage_risk_dollarized_vegetation_trunk | epss_outage_risk_dollarized_vegetation_other | epss_outage_risk_dollarized_other_equipment_type | epss_outage_risk_dollarized_secondary_conductor | epss_outage_risk_dollarized_capacitor_bank_equipment_cause | epss_outage_risk_dollarized_dpd_equipment_cause | epss_outage_risk_dollarized_fuse_equipment_cause | epss_outage_risk_dollarized_support_structure_equipment_cause | epss_outage_risk_dollarized_support_structure_electrical_cause | epss_outage_risk_dollarized_switch_equipment_cause | epss_outage_risk_dollarized_transformer_equipment_cause | epss_outage_risk_dollarized_transformer_equipment_leaking | epss_outage_risk_dollarized_voltage_regulator_equipment_cause | epss_outage_risk_dollarized_animal_bird | epss_outage_risk_dollarized_animal_squirrel | epss_outage_risk_dollarized_animal_other | epss_outage_risk_dollarized_third_party_vehicle
OAKLAND K 1103CR188 | OAKLAND K 1103 | 23245.2056 | 19098.9015 | 40.8508 | 569.0265 | 0.018789 | 174.9433 | 1840.7793 | 656.6541 | 100.0412 | 403.7133 | 3570.5259 | 2467.8257 | 1523.6859 | 6795.4222 | 288.6955 | 53.0928 | 0 | 406.4116 | 1026.2407 | 472.9664 | 0 | 0 | 0 | 0 | 486.1884 | 1805.8862 | 90.9069 | 1081.2263