## Sheet1
Count | Party Name | Data Set | Data Request | Question No. | Question ID | Supp / Rev | Question Text | Responses | Requestor | Date Received | Final Due Date | Date Sent | # of Atchs | Confidential (Y/N) | Links | 2026 EUP Section No. | 2026 EUP Section Name | Category | Subcategory
1 | OEIS | 001 | OEIS_001 | 001 | OEIS_001_Q001 | No | Q01. KDMM Calculations a. Climate Escalation a. Provide Baseline Wildfire Risk, Baseline EPSS Risk, and Baseline PSPS Risk without climate factors for each Circuit Segment from 2025 to 2092. b. Provide the Wildfire Risk, PSPS Risk and EPSS Risk climate factors for each Circuit Segment from 2025 to 2092. c. Provide the baseline KDMMs with climate factors applied for each Circuit Segment from 2025 to 2092. d. Are there different values for each HFTD tier/county/Circuit Segment? e. Does climate impact to Fire Weather Index (FWI) affect both EPSS and PSPS or just PSPS? Core Capability 4 states just PSPS, however WP006 states PSPS and EPSS. f. Provide a sample calculation to demonstrate how Climate Factors are calculated with Fire Weather Index (FWI) and Heat Day multipliers. g. Which KDMMs is climate escalation applied to (Likelihood/Consequence/Risk)? b. Inflation Escalation a. Which KDMMs is inflation escalation applied to (Likelihood/Consequence/Risk)? c. Plan Tracking Objectives a. Do the risk reduction targets represent instantaneous risk reduction for all projects completed in the given year including inflation and climate escalation up to that year? If not, what do they represent? b. Are values in the Plan Tracking Objectives presented in nominal values for the given year or in year 2028 present value? d. Target/Timeline Table a. Footnote (d) indicates that risk values represent unmitigated and residual risk for all projects completed in a given year, however the risk columns are labeled as Change In Instant/Cumulative Risk. Are the Change in Risk columns reporting pre/post mitigation risk or risk reduction for all projects in a given year? b. Do the change in Instantaneous Wildfire and Outage Program Risk columns represent risk reduction for all projects completed in a given year, including climate and inflation escalation up to year 10? If not, what do they represent? c. Are the change in Wildfire and Outage Program Risk columns presented in nominal values or in year 2028 present value? e. Risk Model Impact Factor a. Do KDMM calculations in Tables 5, 8, 11, 12, 13 or 15 and the Model Risk Landscape JSON incorporate the Risk Model Impact Factor? b. How is the Risk Model Impact Factor applied? i. Is it applied to baseline KDMMs prior to calculations or to final values? ii. Provide an explanation and examples to demonstrate at what stage the Risk Model Impact Factor adjustment is applied to the following calculations if applicable: PMO, Plan Tracking Objectives, Target Timeline Table, etc. | Climate Escalation a. Please see the “Baseline Risks – Q001a.a” tab in the provided attachment “EUP-PhI_DR_OEIS_Q001Atch01.xlsx”. b. Please see the “Climate Escalations - Q001.a.b” tab in the provided attachment “EUP-PhI_DR_OEIS_Q001Atch01.xlsx” for the Wildfire Risk, PSPS Risk and EPSS Risk climate factors from 2025 through 2092. c. Please see the “KDMMs – Q001.a.c” tab in the provided attachment “EUPPhI_DR_OEIS_Q001Atch01.xlsx” for the Overall Utility Risk, Ignition Risk, Ignition Consequence, Ignition Likelihood, Outage Program Risk, Outage Program Consequence, and Outage Program Likelihood values from 2025 through 2092. d. Yes. Climate escalation factors are circuit-segment specific and are not assigned uniformly by HFTD tier or county. Consequently, different circuit segments may have different climate escalation factors. e. Climate impact to Fire Weather Index (FWI) affects Wildfire, and both EPSS and PSPS as stated in WP006. The text regarding Core Capability 4 at Chapter 7, Section G.4.c, will be updated as part of errata to indicate that FWI affects Wildfire, PSPS, and EPSS. f. As discussed via email with Energy Safety, PG&E will submit the response to Question 1af on October 23, 2026. g. Climate escalation is applied to Wildfire Risk, Wildfire Consequence, Outage Program Risk, and Outage Program Likelihood. Inflation escalation is applied to EUP-PhI_DR_OEIS_001-Q001 Page 3 Wildfire Risk, Wildfire Consequence, Outage Program Risk and Outage Program Consequence. Please see a detailed breakdown below of how climate escalation and inflation escalation is applied to each Key Decision-Making Metric (KDMM). Wildfire Risk: Wildfire Risk is adjusted for both climate escalation and inflation escalation. Climate escalation is applied to account for the increased severity of wildfire impacts over time due to changing climate conditions. Inflation escalation is applied to account for the increasing monetary value of wildfire impacts over time. Wildfire Likelihood: Wildfire Likelihood is not adjusted for climate escalation or inflation. PG&E does not assume climate change increases the frequency of ignitions. Instead, climate change is reflected through the severity of wildfire outcomes if an ignition occurs (i.e., consequence). Inflation escalation is not applied because Wildfire Likelihood is not a monetized metric. Wildfire Consequence: Wildfire Consequence is impacted by both climate escalation and inflation. Climate increases the potential severity of wildfire impacts, while inflation increases the dollar value of those impacts over time. Wildfire Consequence is calculated as Wildfire Risk divided by Wildfire Likelihood. Because Wildfire Risk is adjusted for both climate escalation and inflation, while Wildfire Likelihood remains unchanged, the resulting Wildfire Consequence values inherently reflect both climate and inflation adjustments as a derived metric. Outage Program Risk: Outage Program Risk is adjusted for both climate escalation and inflation. Climate escalation is applied to account for the expected impact of changing climate conditions on outage occurrence over time, while inflation is applied to account for increases in the monetary value of outage impacts over time Outage Program Likelihood: Outage Program Likelihood is adjusted for climate escalation but is not adjusted for inflation escalation. Climate escalation is applied to reflect the expected impact of changing climate conditions on the frequency of outage events over time. Inflation escalation is not applied because Outage Program Likelihood is not a monetized metric. Outage Program Consequence: Outage Program Consequence is adjusted for inflation but is not adjusted for climate escalation. Outage Program Consequence is calculated as Outage Program Risk divided by Outage Program Likelihood. Because both Outage Program Risk and Outage Program Likelihood are adjusted for climate escalation, the climate adjustment is captured in both the numerator and denominator and therefore does not adjust the resulting consequence value. However, inflation is applied to Outage Program Risk but not to Outage Program Likelihood. As a result, the inflation adjustment flows through to the derived Outage Program Consequence values, while the climate adjustment does not. Overall Utility Risk: Overall Utility Risk is adjusted for both climate escalation and inflation because it is derived from the sum of Wildfire Risk and Outage Program Risk. Since both Wildfire Risk and Outage Program Risk are climate- EUP-PhI_DR_OEIS_001-Q001 Page 4 and inflation-adjusted, Overall Utility Risk also reflects the impacts of both climate escalation and inflation. b. Inflation Escalation a. Please refer to the response to question 1.a.g. c. Plan Tracking Objectives a. Yes. The risk reduction targets in the Plan Tracking Objectives represent instantaneous risk reduction, meaning the reduction in Overall Utility Risk (OUR) measured at a single point in time, specifically the year in which the project is estimated to be completed. For Projects completed in a future year, the associated OUR values are escalated from the 2028 base year using the applicable climate escalation and inflation assumptions through the project's completion year. As a result, the reported risk reduction reflects the nominal value of risk avoided in the year the project is completed, rather than in 2028 values. b. The values in the Plan Tracking Objectives are presented in nominal values for the applicable year, not in 2028 present values. Accordingly, the associated Overall Utility Risk (OUR) values reflect the applicable inflation and climate escalation assumptions through the year in which the risk reduction is realized for each project. d. Target/Timeline Table a. The Change in Instantaneous Risk at year 10 and Change in Cumulative Risk over 55-year columns represents the change in risk at year 10 (2037) attributable to all projects completed in the specified Workplan Year. These values are calculated as pre-mitigation risk less residual (post-mitigation) risk and therefore quantify the avoided risk achieved by the mitigation, rather than reporting pre-mitigation or residual risk levels themselves. For an illustrative example of how the following risk metrics are calculated: Change Instantaneous Wildfire Risk at Year 10, Change in Cumulative Wildfire Risk Over 55 Years, Change Instantaneous Outage Program Risk at Year 10, and Change in Cumulative Outage Program Risk Over 55 Years, please refer to the "Q001e.b.ii" tab in “EUP-PhI_DR_OEIS_Q001Atch01.xlsx”. b. Yes, the Change in Instantaneous Wildfire Risk at Year 10 and Change in Instantaneous Outage Program Risk at Year 10 columns represent the risk reductions for the respective years, including inflation and climate escalation. For example, the Change in Instantaneous Wildfire Risk at Year 10 and Change in Instantaneous Outage Program Risk at Year 10 columns for Year 2 in the Target Timeline Table (or 2029) represent the change in risk attributed to the projects which have been slated for 2029. Please note that the projects that have been selected and used to develop the Target Timeline Table are forecasted and will change as projects have been scoped. For an illustrative example of how the following risk metrics are calculated: Change Instantaneous Wildfire Risk at Year 10, Change in Cumulative Wildfire Risk Over 55 Years, Change Instantaneous Outage Program Risk at Year 10, and Change in Cumulative Outage Program Risk Over 55 Years, please refer to the "Q001e.b.ii" tab in “EUP-PhI_DR_OEIS_Q001Atch01.xlsx”. EUP-PhI_DR_OEIS_001-Q001 Page 5 c. The values presented in the Wildfire and Outage Program Risk columns are nominal values. e. Risk Model Impact Factor a. No, KDMM calculations in Tables 5, 8, 11, 12, 13 or 15 and the Model Risk Landscape JSON do not incorporate the Risk Model Impact Factor. b. As described in Chapter 2 at Section D.1.a.1, PG&E applies the Risk Model Impact Factor as a 20 percent reduction to the projected Ignition and Outage Program Risk reductions calculated using the risk models available at the time of filing. The Risk Model Impact Factor is applied to the Plan Mitigation Objective (PMO) and associated planning and tracking metrics, including the Plan Tracking Objectives (PTOs) and Target/Timeline Table (TTT) risk values. i. The Risk Model Impact Factor is applied to final risk values; specifically, final risk reduction values for Wildfire Risk and Outage Program Risk. ii. The Risk Model Impact Factor is applied to the instantaneous Wildfire Risk and Outage Program Risk reduction values after inflation, climate escalation, and mitigation effectiveness have been applied. Accordingly, the adjustment is applied to the project's nominal-year risk reduction values (e.g., a project completed in 2034 would use the corresponding 2034 risk reduction values rather than 2028 values). The adjusted Wildfire Risk and Outage Program Risk reduction values are then summed to derive the final Overall Utility Risk (OUR) reduction used in the calculation of the Plan Mitigation Objective (PMO), Plan Tracking Objectives (PTOs), and Target Timeline Table (TTT). This methodology is applied consistently across all PMO, PTO, and TTT calculations. The Risk Model Impact Factor is not applied to any other risk metrics presented in the EUP filing. Please refer to the illustrative example in the “Q001e.b.ii” tab of “EUPPhI_DR_OEIS_Q001Atch01.xlsx”, which demonstrates the process used to calculate the wildfire and outage risk reduction values, apply the Risk Model Impact Factor adjustment, and derive the final OUR reduction incorporated into the PMO, PTO, and TTT calculations for a representative circuit segment | Dmitriy Lysak, Richard Cao, Adam Berlinerman | 2026-10-07 | 2026-10-12 | 2026-10-12 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-001.zip | 2.7 | Risk Modeling | KDMM Calculations | Climate Escalation; Inflation Escalation
2 | OEIS | 001 | OEIS_001 | 002 | OEIS_001_Q002 | No | Q02. Benefit-Cost Ratios (BCRs) and CPUC Data Template a. WP006 states that PG&E is using a real discount rate of 4.61% (nominal ATWACC adjusted for inflation) for decision making. PG&E also provides discounted values under the Hybrid and Societal discount rates, consistent with the Risk-Based Decision- Making Framework (RDF). a. What are the “real discount rates” that were used under the Hybrid and Societal discount rate scenarios? b. Given that long-term expected inflation (2.28%) is greater than the Societal discount rate (2%), the “real” Societal discount rate would be a negative value. However, the 2% rate is the social rate of time preference (SRTP) estimated by the Office of Management and Budget (OMB) that is already a real rate that is adjusted for inflation.1 Confirm whether an additional inflation adjustment is being applied to the current 2% SRTP. c. Per the RDF Phase 3 decision, the Hybrid discount rate incorporates the “10- year effective average inflation rate as measured by the California statewide consumer price index.”2 Confirm whether an additional inflation adjustment is applied to the Hybrid rate to derive a “real” rate when calculating BCRs. b. Are the BCRs calculated only over the project’s useful life? For all Confirmed Projects in CPUC Table 1, the useful_life for ALT1 is 48 years. However, in CPUC Table 7, ALT1 accrues costs over 55 years and not 48 years. Why is this the case? c. PG&E has provided different “total cost” numbers in separate parts the tabular data submission. Looking only at Proj0001 Undergrounding as Scoped as an example, in Energy Safety’s Screen 4 Table (Table C.13), total_costs = 17.2725. In CPUC Table 1, present_value_project_costs = 15.45557. a. As outlined in WP006, the denominator of the BCR is the NPV Lifetime Costs which equals the present value of installation capital costs and incremental lifetime O&M costs. Do either of the provided total cost numbers represent the NPV Lifetime Costs as defined in WP006? b. If the answer above is no, then describe which cost components are missing and describe how to derive the NPV Lifetime Costs from the given total_costs and present_value_project_costs values. d. In CPUC Table 7, where costs_type = “Total CapEx” or “O&M Costs (NBB),” the reported annual_costs_in_year_1 appear to include pre-year 1 costs that were incurred. a. Confirm whether annual_costs_in_year_1 only includes year 1 costs or if it also includes pre-year 1 costs. b. If pre-year 1 costs are included with year 1 costs, provide the pre-year 1 costs broken out by year along with a revised year 1 cost for these cost_types. e. In CPUC Table 4, the fields wildfire_rebuild_miles, associated_asset_miles, associated_assets_present_value_capital_costs, and 1 https://www.whitehouse.gov/wp-content/uploads/2023/11/CircularA-4DiscountHistory.pdf 2 https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M533/K099/533099839.PDF, pg. 103 associated_assets_total_mitigation_benefit are listed as 0 for every Confirmed Projectin the initial portfolio. Are these values correct? If so, explain the zeroes. If not, provide correct values. f. Provide detailed inputs and steps on how the unscaled and scaled BCRs were calculated for one example rru_id from PG&E’s portfolio. At a minimum, the response should include: a. all detailed benefit and cost lines for the complete BCR time horizon, b. the discounted cost and benefits for the complete BCR time horizon, c. the total present value of the numerator and denominator, d. an explanation of at which point the risk scaling function is applied and a comparison between scaled and unscaled inputs. g. PG&E uses the BCR for 100% Undergrounding (100% UG) at the end of Screen 2 and start of Screen 3 where Circuit Segments are filtered. PG&E uses the 100% UG BCR again for the Screen 3 Benefit-Cost Comparison. a. Are these two 100% UG BCRs values identical? Prior to the Screen 3 Benefit- Cost Comparison, PG&E inputs scope mileage and unit cost assumptions into their Foundry WPC Feedback Loop Tool. Updated mileage and unit cost assumptions are input again following the Desktop Scoping Meeting. Does this result in revised 100% UG BCRs? b. If the 100% UG BCR does change, provide the revised 100% UG BCR that is utilized for the Screen 3 Benefit-Cost Comparison for all Confirmed Projects that have passed through Screen 3. c. As stated in WP004, each feedback loop record is assigned a status: Draft, Pre- DSM, or Final. For all Alternative Mitigations, are the BCRs reported in the Screen 4 Table the “final” BCRs following the Desktop Scoping Meeting or are they the BCRs evaluated prior to the initial Screen 3 Benefit-Cost Comparison? | a. a. For the Hybrid discount rate scenario, a real discount rate of 3.73% was used for safety and reliability terms and the WACC real discount rate of 4.61% was used for financial terms. A real discount rate of -0.27% was used under the Societal discount rate scenario (see discussion of WACC Hybrid, and Societal discount rate methodologies in PG&E’s Electrical Undergrounding Plan, Rev. 0 (September 30,2026), OEIS Docket #PGE-EUP, Vol. 1, p. 316). b. Yes. In the EUP as filed, we inadvertently applied an additional inflation adjustment to the 2% Societal discount rate, resulting in the -0.27% real rate identified above. Because the 2% Societal discount rate is already expressed as a real rate, that additional adjustment should not have been applied. We are correcting this error through the October 12, 2026, errata by applying the 2% Societal discount rate directly, without an additional adjustment for inflation. c. An additional inflation adjustment is appropriately applied to the nominal Hybrid discount rate to derive a real discount rate when calculating BCRs. Per the RDF Phase 3 Decision (D. 24-05-064), the Hybrid discount rate formulation incorporates the "10-year effective average inflation rate as measured by the California statewide consumer price index", the “10-year effective average percapita real growth rate of wages”, and the “most recent near-term SRTP” 3 of 2%.4 The product of the terms of the Hybrid discount rate formulation thus produces a nominal discount rate from which the real discount rate can be derived. b. The inclusion of incremental_om_costs and incremental_om_savings values beyond year 48 for Alt1 RRUs resulted from the use of an incorrect 55-year expected useful life for Overhead Hardening. We corrected these values in the SPD-37 Table 7 errata filed on October 12, 2026. c. a. Yes. The total_costs value of 17.2725 for Proj0001 in Energy Safety’s Screen 4 Table (Table C.13) represents the NPV Lifetime Costs as defined in WP006. Accordingly, no additional cost components are required to derive the NPV Lifetime Costs for purposes of the BCR calculation. Note, that the reference to incremental lifetime O&M costs in section 4.1, figure 9: Benefit Cost Ratio Calculation of WP006 is intended to reflect the difference between the lifetime O&M costs associated with the mitigation alternative and the lifetime O&M costs of the baseline scenario. b. N/A d. 3 D.24-05-064, Decision Addressing Phase 3 Issues, R.20-07-013, pp. 103–104 (June 6, 2024); https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M533/K099/533099839.PDF. 4 See WP011, Core Capability 4.1 EUP-PhI_DR_OEIS_001-Q002 Page 4 a. The annual_costs_in_year_l also includes pre-year 1 costs, in order to accurately reflect the accrued total costs for the RRUs in Portfolio P00, for which costs begin accruing in 2026. b. Please see the “Q002.d.b” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”. e. These values are all correct for the reasons provided below for each case: wildfire_rebuild_miles: this is currently 0 for all RRUs in P00 because none of the RRUs are associated with a Wildfire Rebuild Project, and because PG&E does not identify a pre-mitigation wildfire_rebuild_miles value for circuit segments which are in a wildfire rebuild area. The designation of a circuit segment as being within a wildfire rebuild area is determined by the presence of recorded damage to PG&E assets and/or facilities as a result of a wildfire incident. associated_asset_miles: this is currently 0 because the only associated assets PG&E is able to provide in SPD37 T4 is the secondary and/or service circuit segment length for each RRU, and that data is incomplete in PG&E’s system of record. PG&E may be able to provide secondary and/or service circuit segment miles for some RRUs in the future. associated_assets_present_value_capital_costs: this will always be 0 because PG&E does not assign any present value capital cost to secondary or service conductor miles. associated_assets_total_mitigation_benefit: this will always be 0 because PG&E does not assign any risk mitigation benefit to secondary or service conductor miles. f. a. For the detailed benefit and cost lines for the complete BCR time horizon, please see the “Q002.f” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”. b. For the discounted cost and benefits for the complete BCR time horizon, please see the “Q002.f” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”. c. For the total present value of the numerator and denominator, d. please see the “Q002.f” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”.Risk scaling occurs prior to all subsequent calculations performed within the Wildfire Benefit Cost Analysis (WBCA) to derive the risk reduction benefits that go into the numerator of Benefit Cost Ratio (BCR). Scaled or unscaled risk exposure values are provided by the applicable Enterprise Risk Bow Tie and incorporated into the WBCA as an input. The WBCA then uses these risk exposure values in all downstream calculations and data transformations. For additional information on how risk exposure is incorporated into the WBCA, please refer to Section 2.3, Risk Exposure Inputs, of the WBCA Whitepaper (WP006). For the numerator of unscaled BCR Calculation we use total risk reduction benefits by adding: - Unscaled Wildfire Risk Reduction Benefits EUP-PhI_DR_OEIS_001-Q002 Page 5 - Unscaled EPSS Risk Reduction Benefits - Unscaled PSPS Risk Reduction Benefits - Unscaled Baseline Outage Reliability Risk Reduction Benefits - Unscaled Public Safety Risks Reduction Benefits from PCEEE For the numerator of scaled BCR Calculation we use a total risk reduction benefit by adding: - Scaled Wildfire Risk Reduction Benefits - Unscaled EPSS Risk Reduction Benefits - Scaled PSPS Risk Reduction Benefits - Unscaled Baseline Outage Reliability Risk Reduction Benefits - Unscaled Public Safety Risks Reduction from PCEEEg. a. No, the Screen 2 100% UG BCR used to start Screen 3 is different from the final Screen 3 100% UG BCR. The final Screen 3 100% UG BCR value following scoping is the result of the updated understanding of the site conditions and required route modifications to build the 100% UG solution. b. The 100% UG BCR does change. The revised Screen 3 BCR used for decisionmaking is in PG&E’s underlying dataset housed in Foundry. Please note this BCR is not a required value in EUP Data Table C.12 (Screen 3). These BCRs are shared in Table 13 when the 100% UG solution is selected as the project as scoped. However, what is in table 13 does not provide the 100% UG BCR value in all cases – rather BCR from just the undergrounding portion of the project. To see a comparable 100% UG in screen 2 to beyond, please see the “Q002.g.b” tab of the attachment “ EUP-PhI_DR_OEIS_001-Q002Atch01.xlsx” that shows BCRs for 100% UG from Screen 2 and Screen3/4. c. Yes, the BCRs included in EUP Data Table C.13 Screen 4 are the final BCR values calculated after scoping is completed. No Screen 2 BCR values are used to finalize the mitigation decision in Screen 3, they are all updated to account for the findings in our scoping meetings | Dmitriy Lysak, Richard Cao, Adam Berlinerman | 2026-10-07 | 2026-10-12 | 2026-10-12 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-001.zip | 2.7 | Risk Modeling | Benefit-Cost Ratios (BCRs) and CPUC Data Template | Discount Rates; Cost Inputs
3 | OEIS | 001 | OEIS_001 | 003 | OEIS_001_Q003 | No | Q03. Circuit Segment Length a. Define the denominator in the overall utility risk density per mile used to evaluate the High-Risk Threshold in the EUP as 'program_length'. Describe PG&E's process for computing this length as well as the OUR density. This description should include how 7 State of California – A Natural Resources Agency OFFICE OF ENERGY INFRASTRUCTURE SAFETY 715 P Street, 15th Floor ¦ Sacramento, CA 95814 916 902-6000 ¦ www.energysafety.ca.gov Gavin Newsom, Governor Forest Kaser, Director PG&E accounts for previously undergrounded lines, lines with covered conductor installed on them, the treatment of HFTD miles, the treatment of HFRA miles and the treatment of rebuild areas both in and out of the HFTD/HFRA. b. Provide a table with the following information for each segment submitted in Table 6 of the EUP. The goal of the table is to understand how the 'program length' (i.e. the denominator of the OUR density calculation) is computed. If more columns are necessary to compute 'program length', append them to the end of the table and define them in your response to the above question. Column Name Field Description Data Type Notes circuit_segment_id A unique value identifying the Circuit Segment ID. NVARCHAR(255) Must match the IDs submitted in Table 6 of the EUP circuit_id A unique value identifying the circuit. NVARCHAR(255) Must match the IDs submitted in Table 6 of the EUP circuit_segment_lengt h The length of the entire Circuit Segment, in miles. This should match the values already submitted in Table 6. REAL Primary Only hftd_length The length of the Circuit Segment in HFTD Tier 2/3 REAL Primary Only hfra_only_length The length of the Circuit Segment in HFRA not included in the HFTD REAL Primary Only rebuild_length The length of the circuit Segment in designated Rebuild Areas REAL Primary Only program_length Length used to evaluate risk per mile for High-Risk eligibility REAL Primary Only eligible_construction_l ength Overhead length eligible for consideration in the EUP REAL Primary Only overall_utiltiy_risk Overall Utility Risk on the segment REAL Not attitude adjusted our_density Measurement of OUR Risk per mile used to evaluate High-Risk eligibility REAL Not attitude adjusted additional_column(1) To be provided if necessary additional_column(2) To be provided if necessary etc. To be provided if necessary | a. For non-Fire Rebuild Projects, the denominator of the Overall Utility Risk (OUR) density metric is the total HFTD/HFRA union primary overhead conductor mileage associated with the project. This mileage is calculated as the sum of [hftd_only_circuit_segment_length] and [hfra_only_circuit_segment_length] reported in EUP Table C.6. HFTD and HFRA miles are treated equally and are both included in the HFTD/HFRA union primary overhead conductor mileage. The HFTD and HFRA mileage components are mutually exclusive, with HFRA mileage representing HFRA areas outside the HFTD, and therefore may be summed without double counting. No weighting or preferential treatment is applied to HFTD or HFRA miles. The OUR density per mile is calculated by dividing the applicable OUR value by this mileage. For purposes of Screen 1, no distinction is made between overhead conductor that may have been previously hardened through undergrounding or covered conductor installation. During detailed project scoping (Screen 3), previously hardened miles are removed from the candidate project scope. However, because OUR is allocated proportionally across a circuit segment, the removal of previously hardened miles does not materially affect the calculated OUR density. For Fire Rebuild Projects, the denominator is the project's total primary overhead conductor mileage, including primary overhead conductor miles both inside and EUP-PhI_DR_OEIS_001-Q003 Page 3 outside of HFTD and HFRA areas. This mileage is represented by [circuit_segment_length] in EUP Table C.6. Because Fire Rebuild Projects are sometimes located outside HFTD and HFRA areas, the HFTD/HFRA-specific mileage fields are not used. The OUR density per mile is calculated by dividing the applicable OUR value by [circuit_segment_length]. This treatment captures the full project mileage because Fire Rebuild Projects may include primary overhead conductor located outside the HFTD/HFRA union. Note, there are not circuit segment with Fire Rebuild Projects included. b. Please refer to attachment “EUP-PhI_DR_OEIS_001-Q003Atch01.xlsx” for the requested table. The attachment is based on data available at Screen 2, before detailed project scoping. The attachment calculates program_length as the sum of hftd_length and hfra_only_length. Data field program_length and eligible_construction_length are equivalent values. No additional columns were added because the provided fields are sufficient to reproduce the program-length calculation. For purposes of the attachment: • hftd_length represents primary overhead conductor mileage within the HFTD; • hfra_only_length represents primary overhead conductor mileage within the HFRA but outside the HFTD; • program_length represents the denominator used to calculate OUR density; • eligible_construction_length is equivalent to program_length; and • our_density equals overall_utility_risk divided by program_length | Dmitriy Lysak, Richard Cao, Adam Berlinerman | 2026-10-07 | 2026-10-12 | 2026-10-12 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-001.zip | 2.7 | Risk Modeling | Circuit Segment Length | Risk Density; Eligibility Metrics
4 | MGRA | 001 | MGRA_001 | 001 | MGRA_001_Q001 | No | Please provide a redline version of the updates made compared to Revision 0. | Please see “EUP-PhI_DR_MGRA_001-Q001Atch01.pdf” for a redline of the Wildfire Consequence Model v4 Documentation Rev 2 against the baseline of Rev 0. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | WDRM v4 Consequence Model | Documentation Updates; Revision Tracking
5 | MGRA | 001 | MGRA_001 | 002 | MGRA_001_Q002 | No | Figure 11 of this document is identical to Figure 10 of the previous version, purportedly showing “TDI Predicted Wildfire Outcomes”. PG&E acknowledged the data used in this figure was erroneous in a data request response to MGRA. (WMP-Discovery2026-2028_DR_MGRA_006-Q005Supp01), well in advance of the release of the updated documentation. Why was the correction not included in the update? | In WMP-Discovery2026-2028_DR_MGRA_006-Q005Supp01, our response states: The calculations in the section of documentation that includes Figures 9 and 10 were included as examples from a development version of the model, notably before weights were added to emphasize model fit against fires with more buildings in their footprints compared to those with fewer buildings, and fit using an earlier version of the fires data set. The primary purpose of the revised Wildfire Consequence Version 4 document was to provide an easier to follow explanation of the modeling process. To support this objective, additional explanatory text and visualizations were added to improve the clarity of the methodology and enhance understanding of each step. Updating or revising specific examples was outside the scope of this document update. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | Marsh Third Party Impact Analysis | Data Validation
6 | MGRA | 001 | MGRA_001 | 003 | MGRA_001_Q003 | No | PG&E states that it “currently faces an estimated average annual loss of $512 million due to damage to our distribution infrastructure caused by wildfires” and cites to the Marsh Impact Analysis paper (WP005). Provide the calculations underlying and supporting this estimate, a. From Marsh, if the calculations are available, and/or b. From PG&E’s own data. | In WMP-Discovery2026-2028_DR_MGRA_006-Q005Supp01, our response states: The calculations in the section of documentation that includes Figures 9 and 10 were included as examples from a development version of the model, notably before weights were added to emphasize model fit against fires with more buildings in their footprints compared to those with fewer buildings, and fit using an earlier version of the fires data set. The primary purpose of the revised Wildfire Consequence Version 4 document was to provide an easier to follow explanation of the modeling process. To support this objective, additional explanatory text and visualizations were added to improve the clarity of the methodology and enhance understanding of each step. Updating or revising specific examples was outside the scope of this document update. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.5 | Cost and Benefits | Marsh Third Party Impact Analysis | Infrastructure Losses; Cost Valuation
7 | MGRA | 001 | MGRA_001 | 004 | MGRA_001_Q004 | No | PG&E also states that: “All else being equal, it is estimated that during the 10-year EUP period, the wildfire risk reduction achieved from undergrounding could facilitate a reduction in homeowner insurance premiums for commercially available insurance plans in our service territory of 18 percent,” also based on a citation from the Marsh Analysis (WP005, p. 12) Provide the assumptions and calculations on which this assertion is based. a. From Marsh, if the calculations are available, and/or b. From PG&E’s own understanding of the Marsh Analysis. | a. Marsh’s approach, including data sources, modeling, assumptions, and calculations, is described in the Methodology Overview sections of WP005. That approach includes Marsh’s proprietary modeling and calculations. Further detail on Marsh’s calculations underlying the estimated reduction in homeowner insurance premiums for commercially available insurance is confidential and/or proprietary, and can only be provided upon the execution of a non-disclosure agreement (NDA). Please send an email to EUPinfo@pge.com to obtain an NDA that may be used for this proceeding. Once the NDA is fully executed, PG&E will provide the requested information. b. The WP005, Methodology Overview sections describe Marsh’s analysis of the potential effect of PG&E’s EUP on homeowner insurance premiums for commercially available insurance plans. This document and the EUP speak for themselves, and PG&E does not have a separate or different understanding of Marsh’s assumptions and calculations. As stated above, further detail on Marsh’s calculations underlying the estimated reduction in homeowner insurance premiums for commercially available insurance is confidential and/or proprietary, and can only be provided upon the execution of an NDA. Please send an email to EUPinfo@pge.com to obtain an NDA that may be used for this proceeding. Once the NDA is fully executed, PG&E will provide the requested information. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.5 | Cost and Benefits | Marsh Third Party Impact Analysis | Insurance Premiums; Customer Benefits
8 | MGRA | 001 | MGRA_001 | 005 | MGRA_001_Q005 | No | G&E states that it “assumes that undergrounding eliminates PSPS and EPSS events on the underground portions of a Circuit Segment, resulting in 100 percent effectiveness for those risk categories.” (p. 67) a. Explain how PG&E’s model and assumption take upstream above ground circuit segments that may be subject to PSPS into account. b. What fraction of circuit segments in the proposed portfolio have above-ground circuit segments upstream that have been subject to PSPS and EPSS at the beginning of the project? c. Does PG&E’s EUP project sequencing prioritize circuit segments that have downstream circuit segments that have been undergrounded? If so, where and how was this incorporated into PG&E’s planning process? | a. PG&E’s PSPS risk methodology accounts for risks associated with upstream overhead lines and equipment through its PSPS risk calculation. Under this methodology, customer-experienced PSPS risk is allocated to upstream circuit segments located within the historical PSPS event polygon based on the relative mileage exposure of those circuit segments within the polygon. As a result, PSPS risk experienced by downstream customers is apportioned among the upstream circuit segments that contribute to the PSPS exposure. Please refer to EUP-PhI_DR_MGRA_001-Q005Atch01.pdf for an illustration of how PSPS risk is allocated among upstream circuit segments within a PSPS event polygon. To calculate PSPS risk reduction benefits, mitigation effectiveness is applied after PSPS risk has been allocated. For undergrounding projects, PG&E assumes that undergrounded facilities are 100% effective against PSPS, while overhead facilities are assumed to be 0% effective against PSPS. For hybrid projects, the reduction in circuit-observed PSPS risk is proportional to the percentage of the circuit segment that is undergrounded. Because the PSPS risk calculation already allocates risk among upstream circuit segments based on mileage exposure within the PSPS event polygon, the PSPS risk attributed to a given downstream circuit segment has already been reduced through the allocation process to account for upstream impacts. For example, if an entire circuit segment is undergrounded, the project receives the benefit associated only with the portion of circuit-observed PSPS risk allocated to that circuit segment; the remaining risk is allocated to upstream circuit segments. Applying an effectiveness value of less than 100 percent to the risk allocated to the undergrounded facilities would therefore account for the upstream impacts a second time. Accordingly, PG&E applies 100 percent effectiveness to the undergrounded portion of a circuit segment after the PSPS risk has been calculated and allocated. In other words, residual PSPS risk associated with upstream overhead facilities is represented through the risk allocation methodology itself, rather than through a reduction in the effectiveness assigned to undergrounded facilities. b. PG&E interprets “proposed portfolio” as the estimated EUP Plan (i.e., the underlying projects that constitute the Plan Mitigation Objective). Of the 360 circuit segments included in the estimated EUP Plan, 332 have experienced an upstream Enhanced Powerline Safety Settings (EPSS) activation, and 206 have experienced an upstream Public Safety Power Shutoff (PSPS) activation in the seven-year lookback period used for the PSPS Outage Program Risk Model, which combines PSPS Lookback Study (2018–2022) with SCADA-captured PSPS events from 2023–2024. c. No. PG&E does not incorporate the existence of previously undergrounded downstream circuit segments as an explicit input, weighting factor, or ranking criterion in EUP project sequencing. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | PSPS and EPSS | Upstream Risk Allocation; Mitigation Effectiveness
9 | MGRA | 001 | MGRA_001 | 006 | MGRA_001_Q006 | No | Regarding Spatial Data Submissions (p. 254), a. provide non-confidential versions of Project-Level Data, b. provide a detailed explanation for the confidentiality of data files that cannot be provided in a non-confidential version. | a. PG&E reviewed the requested project-level GIS data provided to Energy Safety to determine whether a non-confidential version could be produced. However, the confidential information is inherent to the datasets and cannot be reasonably segregated from the non-confidential information. Because the data contains detailed geographic and infrastructure-specific information regarding the electric system, including locations of switches, transformers, fuses, capacitors, and poles, redaction or aggregation of the GIS file sent to Energy Safety would either fail to adequately protect confidential information or materially diminish the usefulness and responsiveness of the data. Accordingly, PG&E is unable to provide non-confidential versions of these files and has produced them on a confidential basis pursuant to Public Utilities Code Section 15475(c); Government Code Sections 6254(k), (ab) and 6255(a); 6 U.S.C. Section 131; and 6 Code of Federal Regulations Section 29.2. Please send an email to EUPinfo@pge.com to obtain an NDA that may be used for this proceeding. Once the NDA is fully executed, PG&E can provide the requested information. b. Please see the response to subpart (a). The confidential GIS file sent to Energy Safety is inherent to the datasets and cannot be reasonably segregated from the responsive data. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.8 | Reporting Metrics | Geodatabase Files | GIS Data; Confidentiality
10 | MGRA | 001 | MGRA_001 | 007 | MGRA_001_Q007 | No | Please provide Excel files for PG&E tables in the EUP containing numerical data, specifically including: a. Table 3-4 (p. 104) b. Table 3-11 (p. 145) c. WP010 CORE CAPABILITY 3: SUPPORTING FORM d. Tables on pp. 581-584. e. WP012 CORE CAPABILITY 5: SUPPORTING FORMULAS f. WP013 CORE CAPABILITY 6: SUPPORTING FORMULAS g. WP014 CORE CAPABILITY 7: SUPPORTING FORMULAS h. The supplemental Excel file, EPSS Toy Problem Calculations (Attach. B, WP016B) i. The supplemental excel file, PSPS Toy Problem Calculations (Attach. B, WP017B) | Please see “EUP-PhI_DR_MGRA_001-Q007Atch01.zip” for the requested files. Please note, the tables requested in subpart (d) are part of Workpaper 011, which has been added to the attachment folder. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | Excel Files | Supporting Data
11 | MGRA | 001 | MGRA_001 | 008 | MGRA_001_Q008 | No | Regarding the flowchart in Figure 3-1 PROJECT ACCEPTANCE FRAMEWORK – SCREEN 1: All decision paths appear to lead to Eligible CPZs. It would appear the horizontal arrow joining the “Ignition Tail Risk Threshold Ineligible” and the Eligible CPZ box is in error. Confirm, or provide explanation of why this is a valid decision path. | The horizontal arrow is not an error. Screen 1 assigns an eligibility determination (e.g., High Risk Threshold Eligible, High Frequency Outage Threshold Eligible, Ignition Tail Risk Threshold Eligible, or EUP Ineligible) to each circuit segment but does not end the workflow at the point where designation is assigned. All segments continue beyond the designation boxes shown in Figure 3-1, with the resulting eligibility determination retained for use in subsequent steps of the Project Acceptance Framework. The rectangular "Mark as" boxes record the outcome of a threshold evaluation, while the diamond-shaped nodes represent workflow decision points. The horizontal arrow ensures that all circuit segments receive and retain a recorded Screen 1 designation before the workflow proceeds. It does not indicate that a circuit segment designated as ineligible becomes eligible or advances to Screen 2. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.4 | Project Acceptance Framework | Project Acceptance Framework | Eligibility Determination
13 | MGRA | 002 | MGRA_002 | 002 | MGRA_002_Q002 | No | Please provide an Excel spreadsheet containing an entry for every circuit segment included in Plan EUP-01 (i.e. those listed in PGE_Initial_2026_09_30_T6_R0.csv). For each circuit segment provide: a. Circuit segment ID b. Nearest weather station distance < 3.0 miles? (Y/N) c. If nearest weather station distance < 3.0 miles, provide Weather Station ID. | Please see PG&E’s response to MGRA-2-1 for publicly available information responsive to subpart b and subpart c of this request. PG&E will supplement this response with the requested spreadsheet by October 30, 2026, consistent with its October 13, 2026 extension request. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.4 | Project Acceptance Framework | Wind | Circuit Segments; Weather Station Proximity
14 | MGRA | 002 | MGRA_002 | 003 | MGRA_002_Q003 | No | In PG&E’s Project Variable Modifier (PVM) analysis (p. 350), SME’s assessed the effectiveness of mitigation alternatives against 2,700 failure modes that occurred in the HFTD. a. Does this failure mode analysis include damage caused during PSPS events that were detected during post-PSPS patrols? b. If “no”, how otherwise does PG&E incorporate damage that is induced by high winds? | a. No, the mitigation effectiveness analysis that informs the Project Variable Modifiers (PVMs) is based on sustained outage events from 2015 through 2024 and the documented causes associated with those events. Company-initiated outages, including Public Safety Power Shutoff (PSPS) events, are not incorporated into the PVM mitigation effectiveness values. b. Damage associated with high winds is incorporated into the mitigation effectiveness analysis when it results in a documented failure event captured in the historical outage dataset and attributed to a recorded cause or supplemental cause. As such, many wind-related failures are reflected in the effectiveness calculations through outage events that occurred under normal operating conditions. However, damage identified during post-PSPS patrols that did not result in a sustained outage event is not separately included in the PVM mitigation effectiveness analysis. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | Wind | Post-PSPS Patrols; Project Variable Modifiers
15 | MGRA | 002 | MGRA_002 | 004 | MGRA_002_Q004 | No | PG&E’s Tail Risk Project-Level Standard states that in order for a project to demonstrate substantial Wildfire Risk reduction of at least 90%. a. What is the origin of the 90% threshold? b. Is this 90% threshold in comparison to completely unmitigated, or with respect to existing mitigations in place (i.e. EPSS and PSPS)? | a. The EUP Guidelines, Section 2.7.9.2, Project-Level Standards, Subsection (c), Tail Risk Project-Level Standard, states that the “Tail Risk Project-Level Standard is the minimum decrease in wildfire likelihood that any Undergrounding Project considered under the Ignition Tail Risk Threshold must achieve to meet the required substantial reduction of the risk of wildfire.” As described in PG&E’s EUP, Chapter 6: Model Report, Section M, Project-Level Thresholds and Standards, 2(c), Tail Risk Project-Level Standard: “PG&E selected 90 percent as a conservative Standard to distinguish substantial mitigation from incremental improvement. Under this Standard, a Project must reduce at least 90 percent of pre-mitigation Ignition Likelihood or Outage Program Likelihood, leaving no more than 10 percent of the original likelihood remaining. PG&E considers this requires the Project to materially reduce the underlying ignition likelihood, rather than merely produce a marginal or measurable change”. b. The Ignition Tail Risk Project-Level Standard uses a Wildfire Likelihood baseline that is already mitigated by Enhanced Powerline Safety Settings (EPSS) and Public Safety Power Shutoff (PSPS) as the basis for determining whether the standard is satisfied. Specifically, satisfaction of the 90% Ignition Tail Risk Project-Level Standard requires a 90% reduction relative to this already operationally mitigated Wildfire Likelihood baseline. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | Mitigation Effectiveness Analysis | Tail Risk Standard; Threshold Basis
16 | MGRA | 002 | MGRA_002 | 005 | MGRA_002_Q005 | No | Repeat the 2024 analysis performed for Data Request RAMP- 2024_DR_TURN_006-Q004, in particular Table 1, showing the amount of covered conductor deployed and facility ignitions, updating this data to the end of September 2024. Likewise repeat the effectiveness calculation for covered conductor performed in DR_TURN_006-Q004 showing details. | PG&E interprets this request to ask for updated data as of September 2026. Please see the table below for the requested updated analysis: Metric 2018 2019 2020 2021 2022 2023 2024 Deployed Covered Conductor miles* 15.8 2025 2026 YTD Total 145 334.5 146.8 334.6 144.8 108.1 206.9 265 1,701. 05 Deployed Covered Conductor cumulative miles* 15.8 160.7 495.2 642.0 976.7 1,121. 5 1,229 .6 1,436. 5 All facility Ignitions associated with Distribution lines in HFTD / HFRA** 247 176 194 200 123 1,701. 5 1,701. 5 108 145 85 84 879 Page 1 EUP-PhI_DR_MGRA_002-Q005 EUP-PhI_DR_MGRA_002-Q005 Page 2 All CPUC RFIs associated with Distribution lines in HFTD / HFRA** 146 114 138 130 85 58 94 55 59 1362 Facility Ignitions associated with Overhead Covered Conductor Distribution lines in HFTD / HFRA ** 0 0 0 1 1 2 1 0 0 5 CPUC RFI associated with Overhead Covered Conductor Distribution lines in HFTD / HFRA ** 0 0 0 1 1 0 0 0 0 2 *minor variations in previously reported values from the original RAMP 2024_DR_TURN_006 Q004 Table 1 are due to final validations during project closure and rounding during calculations ** The results presented above were generated using data as of 10/15/2026. Some differences may exist between these results and previously reported figures. These variances may be attributable to historical updates to the underlying data, differences in reporting methodology, or changes to HFTD/HFRA boundaries over time. Based on the above data, PG&E has estimated a covered conductor mitigation effectiveness of 87.9 percent. This is done by comparing ignitions observed on bare vs. covered conductor during the 2018 to 2026 YTD period as set forth below.1 Effectiveness = 1 - (𝑝𝑝̂Covered)/( 𝑝𝑝̂Bare) = 1 - 0.077%/0.629%= 87.8%1 The details of the effectiveness calculation are provided in Appendix A. PG&E reiterates that it is inappropriate to use the above calculation for the reasons stated in response to subparts (a) and (b) of the referenced RAMP response, provided for reference here as “EUP-PhI_DR_MGRA_002-Q005Atch01.pdf.” In addition to the reasons stated in “EUP-PhI_DR_MGRA_002-Q005Atch01.pdf,” a simple count of observed ignitions on covered conductor circuits is not an appropriate way to estimate covered conductor effectiveness because it does not account for PG&E's other wildfire mitigations that operate on the same facilities, particularly Public 1 PG&E participates in the Joint CC Effectiveness Study to better understand the advantages, operative failures modes, and current state of knowledge regarding covered conductors. Based on the latest update, using data through 2022, the estimated effectiveness is 64 percent. This is consistent with the previous results that were completed using data through 2020. See Joint IOU Covered Conductor Working Group Report. A copy of the report is provided as Attachment 2023-03-27 to PG&E’s 2023 WMP. (Attachment 2023-03 27_PGE_2023_WMP_R0_Appendix D ACI PG&E-22-11_Atch01.) Safety Power Shutoff (PSPS) and Enhanced Powerline Safety Settings (EPSS). On the highest-risk days that meet PSPS criteria, PG&E de-energizes facilities in the affected areas, including covered conductor. Accordingly, ignitions involving those facilities that might have occurred under the most severe conditions are not reflected in the observed ignition counts. Similarly, EPSS quickly de-energizes a line when a fault is detected, which reduces the likelihood that a fault results in an ignition. Because these mitigations work together, their individual effects cannot be separated in a simplified count of observed ignitions like the one requested, and this significantly impacts the results of this calculation. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-16 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Mitigation Effectiveness Analysis | Covered Conductor; Ignition Data
17 | MGRA | 002 | MGRA_002 | 007 | MGRA_002_Q007 | No | On p. 526, PG&E states that: “Marsh analyzed this data set to determine what fire characteristics (acres burned, estimated financial losses, reported fatalities, seasonality, weather conditions) were most predictive of a given ignition type. This analysis concluded that estimated losses were by far the strongest predictor of ignition source, including utility-asset related causes.” a. The meaning of this statement is unclear. Please explain. | a. Marsh compared the listed ignition characteristics to determine which factor provided the greatest predictive power for the ignition's source. The analysis found that estimated financial losses provided the strongest predictive power for utility asset-related causes of the ignition source and were thus selected as a frequency proxy for the Probabilistic Attribution calculation. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Marsh Third Party Impact Analysis | Probabilistic Attribution; Ignition Source
18 | MGRA | 002 | MGRA_002 | 008 | MGRA_002_Q008 | No | Regarding the estimate of homeowner premium savings due to undergrounding (p.534): a. Does the Marsh insurance model assume the historical impact of utility wildfire in the PG&E service area (80% of losses due to utility-related wildfire)? b. Does the Marsh insurance model take climate change into account, in which risk from wildfire due to all sources will increase during the analysis period? c. Does the Marsh insurance model assume that risk mitigation efforts undertaken by utilities will be immediately reflected in homeowner insurance rates? | a. The Marsh homeowners’ insurance model accounted for the impact that historical fires have had on premium pricing. Until July 2025, insurance carriers could only use historical losses when setting premium rates. This meant that known loss areas and areas designated high fire risk were likely to experience higher premiums on average than lower risk areas. Marsh’s analysis of historical pricing trends confirmed this relationship. Historical fires are critical data points within Marsh’s wildfire models, which produced the modeled average annual losses used to model anticipated premium impact. b. The Marsh insurance model already accounts for risks from all wildfire, regardless of source. This is because while Marsh studied the impact of undergrounding PG&E attributable risk, the insurance impact was derived from what changes Marsh expected in the total wildfire risk in PG&E service area. Climate change was modeled but as part of a separate, longer-term analysis of undergrounding impact under extreme climate risk pathways. EUP-PhI_DR_MGRA_002-Q008 Page 2 c. Marsh’s analysis indicated that modeled average annual losses were correlated with premiums. Real calendar years are difficult to compare directly with modeled years but, to the extent that underlying wildfire data reflects risk improvement, with that data then resulting in lower modeled average annual losses, then Marsh expects premiums to account for these lower average annual losses. With the rule change allowing modeling to be used by carriers to set pricing strategy, Marsh anticipates that this relationship between mitigation effectiveness and better premiums will be stronger. Marsh expressly characterizes its results as directional, area-based estimates, and not a prediction or guarantee of future premiums outcomes. One notable limitation to Marsh’s analysis, acknowledged within the report, is that premium pricing is also contingent on several other factors, including other natural catastrophe perils, outside the scope of Marsh’s analysis. Marsh’s findings include the caveat that its results are contingent on all other perils remaining unchanged. Since wildfire is only one covered peril, any severe non-wildfire losses could offset any premium savings achieved by lower wildfire risk. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Marsh Third Party Impact Analysis | Insurance Premiums; Climate Assumptions
19 | MGRA | 002 | MGRA_002 | 009 | MGRA_002_Q009 | No | In Workpaper 016B, EPSS Toy Problem Calculations, p. 710, the largest contribution by far to the outage count is classified as “other_equipment_type” (33,470 versus the next largest vegetation_branch at 5,693). a. What subcategories of event constitute other_equipment_type, and what are their respective contributions to outages? b. Are all outages listed arising while EPSS triggering conditions are set? c. What fraction of outages listed in the categories listed in Workpaper 016B result in ignition? | a. The other_equipment_type category are outages that are used to train the Other Equipment WDRM v4 event probability model. Other equipment is a catch-all for outages with a cause that does not belong with any other causal model or has no recorded cause. Please see Section 3.5.1.10, Other Equipment Model, in EUP attachment B-WP015, Distribution Event Probability Models Version 4, for more information on the Other Equipment Model. b. Transformer and switch-related failure modes are considered independent of EPSS operation. This is why Workpaper 016B, EPSS Toy Problem Calculations, shows zero outages for those subsets. The other failure types can result in an EPSS outage if they occur on a circuit downstream of an EPSS enabled protective device. c. The outage counts for the toy problem in Workpaper 016B were created for illustrative purposes. Please see Table 30 – Outage and Ignition Event Counts Summary in Section 3.6.1.3, Model Data, of EUP attachment B-WP015, Distribution Event Probability Models Version 4, for outage and ignition counts associated with each event type in WDRM v4. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | EUPS and PSPS | EPSS Outages; Event Probability Models
20 | MGRA | 002 | MGRA_002 | 010 | MGRA_002_Q010 | No | For WP020 EUP PSPS V1 RISK MODEL DOCUMENTATION a. Provide a description/red-line of the changes made on 3/3/2026. b. How does PG&E take upstream sections into account when calculating PSPS and EUP risk, and how does this show up int the priortization of circuits to be undergrounded? c. For hybrid projects, what does PG&E assume for the change in reliability risk? | a. Please see “EUP-PhI_DR_MGRA_002-Q010Atch01.pdf” for a redline of the changes made on 3/3/2026. b. Please see PG&E’s response to EUP-PhI_DR_MGRA_001-Q005a for a description of how PG&E accounts for the impact of PSPS events on upstream circuit segments. c. PG&E treats reliability risks (PSPS and EPSS outage risks) in hybrid projects by allocating the pre-mitigation reliability risk across the circuit segment in proportion to the mileage treated by each mitigation type, then applying the appropriate mitigation effectiveness to each portion For additional information, please see Chapter 2, Section D.1.g, “How Undergrounding Projects With Multiple Subprojects Will Be Reported and How the Risk Reduction Will Be Allocated Between Subprojects” and Chapter 7, Core Capability 5, “Accounting for Undergrounding Projects with Multiple Mitigations and Subprojects”. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.4; 2.7 | Project Acceptance Framework; Risk Modeling | EUPS and PSPS | Upstream Risk Allocation; Hybrid Projects