## Sheet1
Count | Party Name | Data Set | Data Request | Question No. | Question ID | Supp / Rev | Question Text | Responses | Requestor | Date Received | Final Due Date | Date Sent | # of Atchs | Confidential (Y/N) | Links | 2026 EUP Section No. | 2026 EUP Section Name | Category | Subcategory
1 | OEIS | 001 | OEIS_001 | 001 | OEIS_001_Q001 | No | Q01. KDMM Calculations a. Climate Escalation a. Provide Baseline Wildfire Risk, Baseline EPSS Risk, and Baseline PSPS Risk without climate factors for each Circuit Segment from 2025 to 2092. b. Provide the Wildfire Risk, PSPS Risk and EPSS Risk climate factors for each Circuit Segment from 2025 to 2092. c. Provide the baseline KDMMs with climate factors applied for each Circuit Segment from 2025 to 2092. d. Are there different values for each HFTD tier/county/Circuit Segment? e. Does climate impact to Fire Weather Index (FWI) affect both EPSS and PSPS or just PSPS? Core Capability 4 states just PSPS, however WP006 states PSPS and EPSS. f. Provide a sample calculation to demonstrate how Climate Factors are calculated with Fire Weather Index (FWI) and Heat Day multipliers. g. Which KDMMs is climate escalation applied to (Likelihood/Consequence/Risk)? b. Inflation Escalation a. Which KDMMs is inflation escalation applied to (Likelihood/Consequence/Risk)? c. Plan Tracking Objectives a. Do the risk reduction targets represent instantaneous risk reduction for all projects completed in the given year including inflation and climate escalation up to that year? If not, what do they represent? b. Are values in the Plan Tracking Objectives presented in nominal values for the given year or in year 2028 present value? d. Target/Timeline Table a. Footnote (d) indicates that risk values represent unmitigated and residual risk for all projects completed in a given year, however the risk columns are labeled as Change In Instant/Cumulative Risk. Are the Change in Risk columns reporting pre/post mitigation risk or risk reduction for all projects in a given year? b. Do the change in Instantaneous Wildfire and Outage Program Risk columns represent risk reduction for all projects completed in a given year, including climate and inflation escalation up to year 10? If not, what do they represent? c. Are the change in Wildfire and Outage Program Risk columns presented in nominal values or in year 2028 present value? e. Risk Model Impact Factor a. Do KDMM calculations in Tables 5, 8, 11, 12, 13 or 15 and the Model Risk Landscape JSON incorporate the Risk Model Impact Factor? b. How is the Risk Model Impact Factor applied? i. Is it applied to baseline KDMMs prior to calculations or to final values? ii. Provide an explanation and examples to demonstrate at what stage the Risk Model Impact Factor adjustment is applied to the following calculations if applicable: PMO, Plan Tracking Objectives, Target Timeline Table, etc. | Climate Escalation a. Please see the “Baseline Risks – Q001a.a” tab in the provided attachment “EUP-PhI_DR_OEIS_Q001Atch01.xlsx”. b. Please see the “Climate Escalations - Q001.a.b” tab in the provided attachment “EUP-PhI_DR_OEIS_Q001Atch01.xlsx” for the Wildfire Risk, PSPS Risk and EPSS Risk climate factors from 2025 through 2092. c. Please see the “KDMMs – Q001.a.c” tab in the provided attachment “EUPPhI_DR_OEIS_Q001Atch01.xlsx” for the Overall Utility Risk, Ignition Risk, Ignition Consequence, Ignition Likelihood, Outage Program Risk, Outage Program Consequence, and Outage Program Likelihood values from 2025 through 2092. d. Yes. Climate escalation factors are circuit-segment specific and are not assigned uniformly by HFTD tier or county. Consequently, different circuit segments may have different climate escalation factors. e. Climate impact to Fire Weather Index (FWI) affects Wildfire, and both EPSS and PSPS as stated in WP006. The text regarding Core Capability 4 at Chapter 7, Section G.4.c, will be updated as part of errata to indicate that FWI affects Wildfire, PSPS, and EPSS. f. As discussed via email with Energy Safety, PG&E will submit the response to Question 1af on October 23, 2026. g. Climate escalation is applied to Wildfire Risk, Wildfire Consequence, Outage Program Risk, and Outage Program Likelihood. Inflation escalation is applied to EUP-PhI_DR_OEIS_001-Q001 Page 3 Wildfire Risk, Wildfire Consequence, Outage Program Risk and Outage Program Consequence. Please see a detailed breakdown below of how climate escalation and inflation escalation is applied to each Key Decision-Making Metric (KDMM). Wildfire Risk: Wildfire Risk is adjusted for both climate escalation and inflation escalation. Climate escalation is applied to account for the increased severity of wildfire impacts over time due to changing climate conditions. Inflation escalation is applied to account for the increasing monetary value of wildfire impacts over time. Wildfire Likelihood: Wildfire Likelihood is not adjusted for climate escalation or inflation. PG&E does not assume climate change increases the frequency of ignitions. Instead, climate change is reflected through the severity of wildfire outcomes if an ignition occurs (i.e., consequence). Inflation escalation is not applied because Wildfire Likelihood is not a monetized metric. Wildfire Consequence: Wildfire Consequence is impacted by both climate escalation and inflation. Climate increases the potential severity of wildfire impacts, while inflation increases the dollar value of those impacts over time. Wildfire Consequence is calculated as Wildfire Risk divided by Wildfire Likelihood. Because Wildfire Risk is adjusted for both climate escalation and inflation, while Wildfire Likelihood remains unchanged, the resulting Wildfire Consequence values inherently reflect both climate and inflation adjustments as a derived metric. Outage Program Risk: Outage Program Risk is adjusted for both climate escalation and inflation. Climate escalation is applied to account for the expected impact of changing climate conditions on outage occurrence over time, while inflation is applied to account for increases in the monetary value of outage impacts over time Outage Program Likelihood: Outage Program Likelihood is adjusted for climate escalation but is not adjusted for inflation escalation. Climate escalation is applied to reflect the expected impact of changing climate conditions on the frequency of outage events over time. Inflation escalation is not applied because Outage Program Likelihood is not a monetized metric. Outage Program Consequence: Outage Program Consequence is adjusted for inflation but is not adjusted for climate escalation. Outage Program Consequence is calculated as Outage Program Risk divided by Outage Program Likelihood. Because both Outage Program Risk and Outage Program Likelihood are adjusted for climate escalation, the climate adjustment is captured in both the numerator and denominator and therefore does not adjust the resulting consequence value. However, inflation is applied to Outage Program Risk but not to Outage Program Likelihood. As a result, the inflation adjustment flows through to the derived Outage Program Consequence values, while the climate adjustment does not. Overall Utility Risk: Overall Utility Risk is adjusted for both climate escalation and inflation because it is derived from the sum of Wildfire Risk and Outage Program Risk. Since both Wildfire Risk and Outage Program Risk are climate- EUP-PhI_DR_OEIS_001-Q001 Page 4 and inflation-adjusted, Overall Utility Risk also reflects the impacts of both climate escalation and inflation. b. Inflation Escalation a. Please refer to the response to question 1.a.g. c. Plan Tracking Objectives a. Yes. The risk reduction targets in the Plan Tracking Objectives represent instantaneous risk reduction, meaning the reduction in Overall Utility Risk (OUR) measured at a single point in time, specifically the year in which the project is estimated to be completed. For Projects completed in a future year, the associated OUR values are escalated from the 2028 base year using the applicable climate escalation and inflation assumptions through the project's completion year. As a result, the reported risk reduction reflects the nominal value of risk avoided in the year the project is completed, rather than in 2028 values. b. The values in the Plan Tracking Objectives are presented in nominal values for the applicable year, not in 2028 present values. Accordingly, the associated Overall Utility Risk (OUR) values reflect the applicable inflation and climate escalation assumptions through the year in which the risk reduction is realized for each project. d. Target/Timeline Table a. The Change in Instantaneous Risk at year 10 and Change in Cumulative Risk over 55-year columns represents the change in risk at year 10 (2037) attributable to all projects completed in the specified Workplan Year. These values are calculated as pre-mitigation risk less residual (post-mitigation) risk and therefore quantify the avoided risk achieved by the mitigation, rather than reporting pre-mitigation or residual risk levels themselves. For an illustrative example of how the following risk metrics are calculated: Change Instantaneous Wildfire Risk at Year 10, Change in Cumulative Wildfire Risk Over 55 Years, Change Instantaneous Outage Program Risk at Year 10, and Change in Cumulative Outage Program Risk Over 55 Years, please refer to the "Q001e.b.ii" tab in “EUP-PhI_DR_OEIS_Q001Atch01.xlsx”. b. Yes, the Change in Instantaneous Wildfire Risk at Year 10 and Change in Instantaneous Outage Program Risk at Year 10 columns represent the risk reductions for the respective years, including inflation and climate escalation. For example, the Change in Instantaneous Wildfire Risk at Year 10 and Change in Instantaneous Outage Program Risk at Year 10 columns for Year 2 in the Target Timeline Table (or 2029) represent the change in risk attributed to the projects which have been slated for 2029. Please note that the projects that have been selected and used to develop the Target Timeline Table are forecasted and will change as projects have been scoped. For an illustrative example of how the following risk metrics are calculated: Change Instantaneous Wildfire Risk at Year 10, Change in Cumulative Wildfire Risk Over 55 Years, Change Instantaneous Outage Program Risk at Year 10, and Change in Cumulative Outage Program Risk Over 55 Years, please refer to the "Q001e.b.ii" tab in “EUP-PhI_DR_OEIS_Q001Atch01.xlsx”. EUP-PhI_DR_OEIS_001-Q001 Page 5 c. The values presented in the Wildfire and Outage Program Risk columns are nominal values. e. Risk Model Impact Factor a. No, KDMM calculations in Tables 5, 8, 11, 12, 13 or 15 and the Model Risk Landscape JSON do not incorporate the Risk Model Impact Factor. b. As described in Chapter 2 at Section D.1.a.1, PG&E applies the Risk Model Impact Factor as a 20 percent reduction to the projected Ignition and Outage Program Risk reductions calculated using the risk models available at the time of filing. The Risk Model Impact Factor is applied to the Plan Mitigation Objective (PMO) and associated planning and tracking metrics, including the Plan Tracking Objectives (PTOs) and Target/Timeline Table (TTT) risk values. i. The Risk Model Impact Factor is applied to final risk values; specifically, final risk reduction values for Wildfire Risk and Outage Program Risk. ii. The Risk Model Impact Factor is applied to the instantaneous Wildfire Risk and Outage Program Risk reduction values after inflation, climate escalation, and mitigation effectiveness have been applied. Accordingly, the adjustment is applied to the project's nominal-year risk reduction values (e.g., a project completed in 2034 would use the corresponding 2034 risk reduction values rather than 2028 values). The adjusted Wildfire Risk and Outage Program Risk reduction values are then summed to derive the final Overall Utility Risk (OUR) reduction used in the calculation of the Plan Mitigation Objective (PMO), Plan Tracking Objectives (PTOs), and Target Timeline Table (TTT). This methodology is applied consistently across all PMO, PTO, and TTT calculations. The Risk Model Impact Factor is not applied to any other risk metrics presented in the EUP filing. Please refer to the illustrative example in the “Q001e.b.ii” tab of “EUPPhI_DR_OEIS_Q001Atch01.xlsx”, which demonstrates the process used to calculate the wildfire and outage risk reduction values, apply the Risk Model Impact Factor adjustment, and derive the final OUR reduction incorporated into the PMO, PTO, and TTT calculations for a representative circuit segment | Dmitriy Lysak, Richard Cao, Adam Berlinerman | 2026-10-07 | 2026-10-12 | 2026-10-12 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-001.zip | 2.7 | Risk Modeling | KDMM Calculations | Climate Escalation; Inflation Escalation
2 | OEIS | 001 | OEIS_001 | 002 | OEIS_001_Q002 | No | Q02. Benefit-Cost Ratios (BCRs) and CPUC Data Template a. WP006 states that PG&E is using a real discount rate of 4.61% (nominal ATWACC adjusted for inflation) for decision making. PG&E also provides discounted values under the Hybrid and Societal discount rates, consistent with the Risk-Based Decision- Making Framework (RDF). a. What are the “real discount rates” that were used under the Hybrid and Societal discount rate scenarios? b. Given that long-term expected inflation (2.28%) is greater than the Societal discount rate (2%), the “real” Societal discount rate would be a negative value. However, the 2% rate is the social rate of time preference (SRTP) estimated by the Office of Management and Budget (OMB) that is already a real rate that is adjusted for inflation.1 Confirm whether an additional inflation adjustment is being applied to the current 2% SRTP. c. Per the RDF Phase 3 decision, the Hybrid discount rate incorporates the “10- year effective average inflation rate as measured by the California statewide consumer price index.”2 Confirm whether an additional inflation adjustment is applied to the Hybrid rate to derive a “real” rate when calculating BCRs. b. Are the BCRs calculated only over the project’s useful life? For all Confirmed Projects in CPUC Table 1, the useful_life for ALT1 is 48 years. However, in CPUC Table 7, ALT1 accrues costs over 55 years and not 48 years. Why is this the case? c. PG&E has provided different “total cost” numbers in separate parts the tabular data submission. Looking only at Proj0001 Undergrounding as Scoped as an example, in Energy Safety’s Screen 4 Table (Table C.13), total_costs = 17.2725. In CPUC Table 1, present_value_project_costs = 15.45557. a. As outlined in WP006, the denominator of the BCR is the NPV Lifetime Costs which equals the present value of installation capital costs and incremental lifetime O&M costs. Do either of the provided total cost numbers represent the NPV Lifetime Costs as defined in WP006? b. If the answer above is no, then describe which cost components are missing and describe how to derive the NPV Lifetime Costs from the given total_costs and present_value_project_costs values. d. In CPUC Table 7, where costs_type = “Total CapEx” or “O&M Costs (NBB),” the reported annual_costs_in_year_1 appear to include pre-year 1 costs that were incurred. a. Confirm whether annual_costs_in_year_1 only includes year 1 costs or if it also includes pre-year 1 costs. b. If pre-year 1 costs are included with year 1 costs, provide the pre-year 1 costs broken out by year along with a revised year 1 cost for these cost_types. e. In CPUC Table 4, the fields wildfire_rebuild_miles, associated_asset_miles, associated_assets_present_value_capital_costs, and 1 https://www.whitehouse.gov/wp-content/uploads/2023/11/CircularA-4DiscountHistory.pdf 2 https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M533/K099/533099839.PDF, pg. 103 associated_assets_total_mitigation_benefit are listed as 0 for every Confirmed Projectin the initial portfolio. Are these values correct? If so, explain the zeroes. If not, provide correct values. f. Provide detailed inputs and steps on how the unscaled and scaled BCRs were calculated for one example rru_id from PG&E’s portfolio. At a minimum, the response should include: a. all detailed benefit and cost lines for the complete BCR time horizon, b. the discounted cost and benefits for the complete BCR time horizon, c. the total present value of the numerator and denominator, d. an explanation of at which point the risk scaling function is applied and a comparison between scaled and unscaled inputs. g. PG&E uses the BCR for 100% Undergrounding (100% UG) at the end of Screen 2 and start of Screen 3 where Circuit Segments are filtered. PG&E uses the 100% UG BCR again for the Screen 3 Benefit-Cost Comparison. a. Are these two 100% UG BCRs values identical? Prior to the Screen 3 Benefit- Cost Comparison, PG&E inputs scope mileage and unit cost assumptions into their Foundry WPC Feedback Loop Tool. Updated mileage and unit cost assumptions are input again following the Desktop Scoping Meeting. Does this result in revised 100% UG BCRs? b. If the 100% UG BCR does change, provide the revised 100% UG BCR that is utilized for the Screen 3 Benefit-Cost Comparison for all Confirmed Projects that have passed through Screen 3. c. As stated in WP004, each feedback loop record is assigned a status: Draft, Pre- DSM, or Final. For all Alternative Mitigations, are the BCRs reported in the Screen 4 Table the “final” BCRs following the Desktop Scoping Meeting or are they the BCRs evaluated prior to the initial Screen 3 Benefit-Cost Comparison? | a. a. For the Hybrid discount rate scenario, a real discount rate of 3.73% was used for safety and reliability terms and the WACC real discount rate of 4.61% was used for financial terms. A real discount rate of -0.27% was used under the Societal discount rate scenario (see discussion of WACC Hybrid, and Societal discount rate methodologies in PG&E’s Electrical Undergrounding Plan, Rev. 0 (September 30,2026), OEIS Docket #PGE-EUP, Vol. 1, p. 316). b. Yes. In the EUP as filed, we inadvertently applied an additional inflation adjustment to the 2% Societal discount rate, resulting in the -0.27% real rate identified above. Because the 2% Societal discount rate is already expressed as a real rate, that additional adjustment should not have been applied. We are correcting this error through the October 12, 2026, errata by applying the 2% Societal discount rate directly, without an additional adjustment for inflation. c. An additional inflation adjustment is appropriately applied to the nominal Hybrid discount rate to derive a real discount rate when calculating BCRs. Per the RDF Phase 3 Decision (D. 24-05-064), the Hybrid discount rate formulation incorporates the "10-year effective average inflation rate as measured by the California statewide consumer price index", the “10-year effective average percapita real growth rate of wages”, and the “most recent near-term SRTP” 3 of 2%.4 The product of the terms of the Hybrid discount rate formulation thus produces a nominal discount rate from which the real discount rate can be derived. b. The inclusion of incremental_om_costs and incremental_om_savings values beyond year 48 for Alt1 RRUs resulted from the use of an incorrect 55-year expected useful life for Overhead Hardening. We corrected these values in the SPD-37 Table 7 errata filed on October 12, 2026. c. a. Yes. The total_costs value of 17.2725 for Proj0001 in Energy Safety’s Screen 4 Table (Table C.13) represents the NPV Lifetime Costs as defined in WP006. Accordingly, no additional cost components are required to derive the NPV Lifetime Costs for purposes of the BCR calculation. Note, that the reference to incremental lifetime O&M costs in section 4.1, figure 9: Benefit Cost Ratio Calculation of WP006 is intended to reflect the difference between the lifetime O&M costs associated with the mitigation alternative and the lifetime O&M costs of the baseline scenario. b. N/A d. 3 D.24-05-064, Decision Addressing Phase 3 Issues, R.20-07-013, pp. 103–104 (June 6, 2024); https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M533/K099/533099839.PDF. 4 See WP011, Core Capability 4.1 EUP-PhI_DR_OEIS_001-Q002 Page 4 a. The annual_costs_in_year_l also includes pre-year 1 costs, in order to accurately reflect the accrued total costs for the RRUs in Portfolio P00, for which costs begin accruing in 2026. b. Please see the “Q002.d.b” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”. e. These values are all correct for the reasons provided below for each case: wildfire_rebuild_miles: this is currently 0 for all RRUs in P00 because none of the RRUs are associated with a Wildfire Rebuild Project, and because PG&E does not identify a pre-mitigation wildfire_rebuild_miles value for circuit segments which are in a wildfire rebuild area. The designation of a circuit segment as being within a wildfire rebuild area is determined by the presence of recorded damage to PG&E assets and/or facilities as a result of a wildfire incident. associated_asset_miles: this is currently 0 because the only associated assets PG&E is able to provide in SPD37 T4 is the secondary and/or service circuit segment length for each RRU, and that data is incomplete in PG&E’s system of record. PG&E may be able to provide secondary and/or service circuit segment miles for some RRUs in the future. associated_assets_present_value_capital_costs: this will always be 0 because PG&E does not assign any present value capital cost to secondary or service conductor miles. associated_assets_total_mitigation_benefit: this will always be 0 because PG&E does not assign any risk mitigation benefit to secondary or service conductor miles. f. a. For the detailed benefit and cost lines for the complete BCR time horizon, please see the “Q002.f” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”. b. For the discounted cost and benefits for the complete BCR time horizon, please see the “Q002.f” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”. c. For the total present value of the numerator and denominator, d. please see the “Q002.f” tab of the attachment “EUP-PhI_DR_OEIS_001- Q002Atch01.xlsx”.Risk scaling occurs prior to all subsequent calculations performed within the Wildfire Benefit Cost Analysis (WBCA) to derive the risk reduction benefits that go into the numerator of Benefit Cost Ratio (BCR). Scaled or unscaled risk exposure values are provided by the applicable Enterprise Risk Bow Tie and incorporated into the WBCA as an input. The WBCA then uses these risk exposure values in all downstream calculations and data transformations. For additional information on how risk exposure is incorporated into the WBCA, please refer to Section 2.3, Risk Exposure Inputs, of the WBCA Whitepaper (WP006). For the numerator of unscaled BCR Calculation we use total risk reduction benefits by adding: - Unscaled Wildfire Risk Reduction Benefits EUP-PhI_DR_OEIS_001-Q002 Page 5 - Unscaled EPSS Risk Reduction Benefits - Unscaled PSPS Risk Reduction Benefits - Unscaled Baseline Outage Reliability Risk Reduction Benefits - Unscaled Public Safety Risks Reduction Benefits from PCEEE For the numerator of scaled BCR Calculation we use a total risk reduction benefit by adding: - Scaled Wildfire Risk Reduction Benefits - Unscaled EPSS Risk Reduction Benefits - Scaled PSPS Risk Reduction Benefits - Unscaled Baseline Outage Reliability Risk Reduction Benefits - Unscaled Public Safety Risks Reduction from PCEEEg. a. No, the Screen 2 100% UG BCR used to start Screen 3 is different from the final Screen 3 100% UG BCR. The final Screen 3 100% UG BCR value following scoping is the result of the updated understanding of the site conditions and required route modifications to build the 100% UG solution. b. The 100% UG BCR does change. The revised Screen 3 BCR used for decisionmaking is in PG&E’s underlying dataset housed in Foundry. Please note this BCR is not a required value in EUP Data Table C.12 (Screen 3). These BCRs are shared in Table 13 when the 100% UG solution is selected as the project as scoped. However, what is in table 13 does not provide the 100% UG BCR value in all cases – rather BCR from just the undergrounding portion of the project. To see a comparable 100% UG in screen 2 to beyond, please see the “Q002.g.b” tab of the attachment “ EUP-PhI_DR_OEIS_001-Q002Atch01.xlsx” that shows BCRs for 100% UG from Screen 2 and Screen3/4. c. Yes, the BCRs included in EUP Data Table C.13 Screen 4 are the final BCR values calculated after scoping is completed. No Screen 2 BCR values are used to finalize the mitigation decision in Screen 3, they are all updated to account for the findings in our scoping meetings | Dmitriy Lysak, Richard Cao, Adam Berlinerman | 2026-10-07 | 2026-10-12 | 2026-10-12 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-001.zip | 2.7 | Risk Modeling | Benefit-Cost Ratios (BCRs) and CPUC Data Template | Discount Rates; Cost Inputs
3 | OEIS | 001 | OEIS_001 | 003 | OEIS_001_Q003 | No | Q03. Circuit Segment Length a. Define the denominator in the overall utility risk density per mile used to evaluate the High-Risk Threshold in the EUP as 'program_length'. Describe PG&E's process for computing this length as well as the OUR density. This description should include how 7 State of California – A Natural Resources Agency OFFICE OF ENERGY INFRASTRUCTURE SAFETY 715 P Street, 15th Floor ¦ Sacramento, CA 95814 916 902-6000 ¦ www.energysafety.ca.gov Gavin Newsom, Governor Forest Kaser, Director PG&E accounts for previously undergrounded lines, lines with covered conductor installed on them, the treatment of HFTD miles, the treatment of HFRA miles and the treatment of rebuild areas both in and out of the HFTD/HFRA. b. Provide a table with the following information for each segment submitted in Table 6 of the EUP. The goal of the table is to understand how the 'program length' (i.e. the denominator of the OUR density calculation) is computed. If more columns are necessary to compute 'program length', append them to the end of the table and define them in your response to the above question. Column Name Field Description Data Type Notes circuit_segment_id A unique value identifying the Circuit Segment ID. NVARCHAR(255) Must match the IDs submitted in Table 6 of the EUP circuit_id A unique value identifying the circuit. NVARCHAR(255) Must match the IDs submitted in Table 6 of the EUP circuit_segment_lengt h The length of the entire Circuit Segment, in miles. This should match the values already submitted in Table 6. REAL Primary Only hftd_length The length of the Circuit Segment in HFTD Tier 2/3 REAL Primary Only hfra_only_length The length of the Circuit Segment in HFRA not included in the HFTD REAL Primary Only rebuild_length The length of the circuit Segment in designated Rebuild Areas REAL Primary Only program_length Length used to evaluate risk per mile for High-Risk eligibility REAL Primary Only eligible_construction_l ength Overhead length eligible for consideration in the EUP REAL Primary Only overall_utiltiy_risk Overall Utility Risk on the segment REAL Not attitude adjusted our_density Measurement of OUR Risk per mile used to evaluate High-Risk eligibility REAL Not attitude adjusted additional_column(1) To be provided if necessary additional_column(2) To be provided if necessary etc. To be provided if necessary | a. For non-Fire Rebuild Projects, the denominator of the Overall Utility Risk (OUR) density metric is the total HFTD/HFRA union primary overhead conductor mileage associated with the project. This mileage is calculated as the sum of [hftd_only_circuit_segment_length] and [hfra_only_circuit_segment_length] reported in EUP Table C.6. HFTD and HFRA miles are treated equally and are both included in the HFTD/HFRA union primary overhead conductor mileage. The HFTD and HFRA mileage components are mutually exclusive, with HFRA mileage representing HFRA areas outside the HFTD, and therefore may be summed without double counting. No weighting or preferential treatment is applied to HFTD or HFRA miles. The OUR density per mile is calculated by dividing the applicable OUR value by this mileage. For purposes of Screen 1, no distinction is made between overhead conductor that may have been previously hardened through undergrounding or covered conductor installation. During detailed project scoping (Screen 3), previously hardened miles are removed from the candidate project scope. However, because OUR is allocated proportionally across a circuit segment, the removal of previously hardened miles does not materially affect the calculated OUR density. For Fire Rebuild Projects, the denominator is the project's total primary overhead conductor mileage, including primary overhead conductor miles both inside and EUP-PhI_DR_OEIS_001-Q003 Page 3 outside of HFTD and HFRA areas. This mileage is represented by [circuit_segment_length] in EUP Table C.6. Because Fire Rebuild Projects are sometimes located outside HFTD and HFRA areas, the HFTD/HFRA-specific mileage fields are not used. The OUR density per mile is calculated by dividing the applicable OUR value by [circuit_segment_length]. This treatment captures the full project mileage because Fire Rebuild Projects may include primary overhead conductor located outside the HFTD/HFRA union. Note, there are not circuit segment with Fire Rebuild Projects included. b. Please refer to attachment “EUP-PhI_DR_OEIS_001-Q003Atch01.xlsx” for the requested table. The attachment is based on data available at Screen 2, before detailed project scoping. The attachment calculates program_length as the sum of hftd_length and hfra_only_length. Data field program_length and eligible_construction_length are equivalent values. No additional columns were added because the provided fields are sufficient to reproduce the program-length calculation. For purposes of the attachment: • hftd_length represents primary overhead conductor mileage within the HFTD; • hfra_only_length represents primary overhead conductor mileage within the HFRA but outside the HFTD; • program_length represents the denominator used to calculate OUR density; • eligible_construction_length is equivalent to program_length; and • our_density equals overall_utility_risk divided by program_length | Dmitriy Lysak, Richard Cao, Adam Berlinerman | 2026-10-07 | 2026-10-12 | 2026-10-12 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-001.zip | 2.7 | Risk Modeling | Circuit Segment Length | Risk Density; Eligibility Metrics
4 | MGRA | 001 | MGRA_001 | 001 | MGRA_001_Q001 | No | Please provide a redline version of the updates made compared to Revision 0. | Please see “EUP-PhI_DR_MGRA_001-Q001Atch01.pdf” for a redline of the Wildfire Consequence Model v4 Documentation Rev 2 against the baseline of Rev 0. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | WDRM v4 Consequence Model | Documentation Updates; Revision Tracking
5 | MGRA | 001 | MGRA_001 | 002 | MGRA_001_Q002 | No | Figure 11 of this document is identical to Figure 10 of the previous version, purportedly showing “TDI Predicted Wildfire Outcomes”. PG&E acknowledged the data used in this figure was erroneous in a data request response to MGRA. (WMP-Discovery2026-2028_DR_MGRA_006-Q005Supp01), well in advance of the release of the updated documentation. Why was the correction not included in the update? | In WMP-Discovery2026-2028_DR_MGRA_006-Q005Supp01, our response states: The calculations in the section of documentation that includes Figures 9 and 10 were included as examples from a development version of the model, notably before weights were added to emphasize model fit against fires with more buildings in their footprints compared to those with fewer buildings, and fit using an earlier version of the fires data set. The primary purpose of the revised Wildfire Consequence Version 4 document was to provide an easier to follow explanation of the modeling process. To support this objective, additional explanatory text and visualizations were added to improve the clarity of the methodology and enhance understanding of each step. Updating or revising specific examples was outside the scope of this document update. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | Marsh Third Party Impact Analysis | Data Validation
6 | MGRA | 001 | MGRA_001 | 003 | MGRA_001_Q003 | No | PG&E states that it “currently faces an estimated average annual loss of $512 million due to damage to our distribution infrastructure caused by wildfires” and cites to the Marsh Impact Analysis paper (WP005). Provide the calculations underlying and supporting this estimate, a. From Marsh, if the calculations are available, and/or b. From PG&E’s own data. | In WMP-Discovery2026-2028_DR_MGRA_006-Q005Supp01, our response states: The calculations in the section of documentation that includes Figures 9 and 10 were included as examples from a development version of the model, notably before weights were added to emphasize model fit against fires with more buildings in their footprints compared to those with fewer buildings, and fit using an earlier version of the fires data set. The primary purpose of the revised Wildfire Consequence Version 4 document was to provide an easier to follow explanation of the modeling process. To support this objective, additional explanatory text and visualizations were added to improve the clarity of the methodology and enhance understanding of each step. Updating or revising specific examples was outside the scope of this document update. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.5 | Cost and Benefits | Marsh Third Party Impact Analysis | Infrastructure Losses; Cost Valuation
7 | MGRA | 001 | MGRA_001 | 004 | MGRA_001_Q004 | No | PG&E also states that: “All else being equal, it is estimated that during the 10-year EUP period, the wildfire risk reduction achieved from undergrounding could facilitate a reduction in homeowner insurance premiums for commercially available insurance plans in our service territory of 18 percent,” also based on a citation from the Marsh Analysis (WP005, p. 12) Provide the assumptions and calculations on which this assertion is based. a. From Marsh, if the calculations are available, and/or b. From PG&E’s own understanding of the Marsh Analysis. | a. Marsh’s approach, including data sources, modeling, assumptions, and calculations, is described in the Methodology Overview sections of WP005. That approach includes Marsh’s proprietary modeling and calculations. Further detail on Marsh’s calculations underlying the estimated reduction in homeowner insurance premiums for commercially available insurance is confidential and/or proprietary, and can only be provided upon the execution of a non-disclosure agreement (NDA). Please send an email to EUPinfo@pge.com to obtain an NDA that may be used for this proceeding. Once the NDA is fully executed, PG&E will provide the requested information. b. The WP005, Methodology Overview sections describe Marsh’s analysis of the potential effect of PG&E’s EUP on homeowner insurance premiums for commercially available insurance plans. This document and the EUP speak for themselves, and PG&E does not have a separate or different understanding of Marsh’s assumptions and calculations. As stated above, further detail on Marsh’s calculations underlying the estimated reduction in homeowner insurance premiums for commercially available insurance is confidential and/or proprietary, and can only be provided upon the execution of an NDA. Please send an email to EUPinfo@pge.com to obtain an NDA that may be used for this proceeding. Once the NDA is fully executed, PG&E will provide the requested information. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.5 | Cost and Benefits | Marsh Third Party Impact Analysis | Insurance Premiums; Customer Benefits
8 | MGRA | 001 | MGRA_001 | 005 | MGRA_001_Q005 | No | G&E states that it “assumes that undergrounding eliminates PSPS and EPSS events on the underground portions of a Circuit Segment, resulting in 100 percent effectiveness for those risk categories.” (p. 67) a. Explain how PG&E’s model and assumption take upstream above ground circuit segments that may be subject to PSPS into account. b. What fraction of circuit segments in the proposed portfolio have above-ground circuit segments upstream that have been subject to PSPS and EPSS at the beginning of the project? c. Does PG&E’s EUP project sequencing prioritize circuit segments that have downstream circuit segments that have been undergrounded? If so, where and how was this incorporated into PG&E’s planning process? | a. PG&E’s PSPS risk methodology accounts for risks associated with upstream overhead lines and equipment through its PSPS risk calculation. Under this methodology, customer-experienced PSPS risk is allocated to upstream circuit segments located within the historical PSPS event polygon based on the relative mileage exposure of those circuit segments within the polygon. As a result, PSPS risk experienced by downstream customers is apportioned among the upstream circuit segments that contribute to the PSPS exposure. Please refer to EUP-PhI_DR_MGRA_001-Q005Atch01.pdf for an illustration of how PSPS risk is allocated among upstream circuit segments within a PSPS event polygon. To calculate PSPS risk reduction benefits, mitigation effectiveness is applied after PSPS risk has been allocated. For undergrounding projects, PG&E assumes that undergrounded facilities are 100% effective against PSPS, while overhead facilities are assumed to be 0% effective against PSPS. For hybrid projects, the reduction in circuit-observed PSPS risk is proportional to the percentage of the circuit segment that is undergrounded. Because the PSPS risk calculation already allocates risk among upstream circuit segments based on mileage exposure within the PSPS event polygon, the PSPS risk attributed to a given downstream circuit segment has already been reduced through the allocation process to account for upstream impacts. For example, if an entire circuit segment is undergrounded, the project receives the benefit associated only with the portion of circuit-observed PSPS risk allocated to that circuit segment; the remaining risk is allocated to upstream circuit segments. Applying an effectiveness value of less than 100 percent to the risk allocated to the undergrounded facilities would therefore account for the upstream impacts a second time. Accordingly, PG&E applies 100 percent effectiveness to the undergrounded portion of a circuit segment after the PSPS risk has been calculated and allocated. In other words, residual PSPS risk associated with upstream overhead facilities is represented through the risk allocation methodology itself, rather than through a reduction in the effectiveness assigned to undergrounded facilities. b. PG&E interprets “proposed portfolio” as the estimated EUP Plan (i.e., the underlying projects that constitute the Plan Mitigation Objective). Of the 360 circuit segments included in the estimated EUP Plan, 332 have experienced an upstream Enhanced Powerline Safety Settings (EPSS) activation, and 206 have experienced an upstream Public Safety Power Shutoff (PSPS) activation in the seven-year lookback period used for the PSPS Outage Program Risk Model, which combines PSPS Lookback Study (2018–2022) with SCADA-captured PSPS events from 2023–2024. c. No. PG&E does not incorporate the existence of previously undergrounded downstream circuit segments as an explicit input, weighting factor, or ranking criterion in EUP project sequencing. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | PSPS and EPSS | Upstream Risk Allocation; Mitigation Effectiveness
9 | MGRA | 001 | MGRA_001 | 006 | MGRA_001_Q006 | No | Regarding Spatial Data Submissions (p. 254), a. provide non-confidential versions of Project-Level Data, b. provide a detailed explanation for the confidentiality of data files that cannot be provided in a non-confidential version. | a. PG&E reviewed the requested project-level GIS data provided to Energy Safety to determine whether a non-confidential version could be produced. However, the confidential information is inherent to the datasets and cannot be reasonably segregated from the non-confidential information. Because the data contains detailed geographic and infrastructure-specific information regarding the electric system, including locations of switches, transformers, fuses, capacitors, and poles, redaction or aggregation of the GIS file sent to Energy Safety would either fail to adequately protect confidential information or materially diminish the usefulness and responsiveness of the data. Accordingly, PG&E is unable to provide non-confidential versions of these files and has produced them on a confidential basis pursuant to Public Utilities Code Section 15475(c); Government Code Sections 6254(k), (ab) and 6255(a); 6 U.S.C. Section 131; and 6 Code of Federal Regulations Section 29.2. Please send an email to EUPinfo@pge.com to obtain an NDA that may be used for this proceeding. Once the NDA is fully executed, PG&E can provide the requested information. b. Please see the response to subpart (a). The confidential GIS file sent to Energy Safety is inherent to the datasets and cannot be reasonably segregated from the responsive data. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.8 | Reporting Metrics | Geodatabase Files | GIS Data; Confidentiality
10 | MGRA | 001 | MGRA_001 | 007 | MGRA_001_Q007 | No | Please provide Excel files for PG&E tables in the EUP containing numerical data, specifically including: a. Table 3-4 (p. 104) b. Table 3-11 (p. 145) c. WP010 CORE CAPABILITY 3: SUPPORTING FORM d. Tables on pp. 581-584. e. WP012 CORE CAPABILITY 5: SUPPORTING FORMULAS f. WP013 CORE CAPABILITY 6: SUPPORTING FORMULAS g. WP014 CORE CAPABILITY 7: SUPPORTING FORMULAS h. The supplemental Excel file, EPSS Toy Problem Calculations (Attach. B, WP016B) i. The supplemental excel file, PSPS Toy Problem Calculations (Attach. B, WP017B) | Please see “EUP-PhI_DR_MGRA_001-Q007Atch01.zip” for the requested files. Please note, the tables requested in subpart (d) are part of Workpaper 011, which has been added to the attachment folder. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.7 | Risk Modeling | Excel Files | Supporting Data
11 | MGRA | 001 | MGRA_001 | 008 | MGRA_001_Q008 | No | Regarding the flowchart in Figure 3-1 PROJECT ACCEPTANCE FRAMEWORK – SCREEN 1: All decision paths appear to lead to Eligible CPZs. It would appear the horizontal arrow joining the “Ignition Tail Risk Threshold Ineligible” and the Eligible CPZ box is in error. Confirm, or provide explanation of why this is a valid decision path. | The horizontal arrow is not an error. Screen 1 assigns an eligibility determination (e.g., High Risk Threshold Eligible, High Frequency Outage Threshold Eligible, Ignition Tail Risk Threshold Eligible, or EUP Ineligible) to each circuit segment but does not end the workflow at the point where designation is assigned. All segments continue beyond the designation boxes shown in Figure 3-1, with the resulting eligibility determination retained for use in subsequent steps of the Project Acceptance Framework. The rectangular "Mark as" boxes record the outcome of a threshold evaluation, while the diamond-shaped nodes represent workflow decision points. The horizontal arrow ensures that all circuit segments receive and retain a recorded Screen 1 designation before the workflow proceeds. It does not indicate that a circuit segment designated as ineligible becomes eligible or advances to Screen 2. | Joseph Mitchell | 2026-10-09 | 2026-10-14 | 2026-10-14 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-001.zip | 2.4 | Project Acceptance Framework | Project Acceptance Framework | Eligibility Determination
13 | MGRA | 002 | MGRA_002 | 002 | MGRA_002_Q002 | No | Please provide an Excel spreadsheet containing an entry for every circuit segment included in Plan EUP-01 (i.e. those listed in PGE_Initial_2026_09_30_T6_R0.csv). For each circuit segment provide: a. Circuit segment ID b. Nearest weather station distance < 3.0 miles? (Y/N) c. If nearest weather station distance < 3.0 miles, provide Weather Station ID. | Please see PG&E’s response to MGRA-2-1 for publicly available information responsive to subpart b and subpart c of this request. PG&E will supplement this response with the requested spreadsheet by October 30, 2026, consistent with its October 13, 2026 extension request. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.4 | Project Acceptance Framework | Wind | Circuit Segments; Weather Station Proximity
14 | MGRA | 002 | MGRA_002 | 003 | MGRA_002_Q003 | No | In PG&E’s Project Variable Modifier (PVM) analysis (p. 350), SME’s assessed the effectiveness of mitigation alternatives against 2,700 failure modes that occurred in the HFTD. a. Does this failure mode analysis include damage caused during PSPS events that were detected during post-PSPS patrols? b. If “no”, how otherwise does PG&E incorporate damage that is induced by high winds? | a. No, the mitigation effectiveness analysis that informs the Project Variable Modifiers (PVMs) is based on sustained outage events from 2015 through 2024 and the documented causes associated with those events. Company-initiated outages, including Public Safety Power Shutoff (PSPS) events, are not incorporated into the PVM mitigation effectiveness values. b. Damage associated with high winds is incorporated into the mitigation effectiveness analysis when it results in a documented failure event captured in the historical outage dataset and attributed to a recorded cause or supplemental cause. As such, many wind-related failures are reflected in the effectiveness calculations through outage events that occurred under normal operating conditions. However, damage identified during post-PSPS patrols that did not result in a sustained outage event is not separately included in the PVM mitigation effectiveness analysis. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | Wind | Post-PSPS Patrols; Project Variable Modifiers
15 | MGRA | 002 | MGRA_002 | 004 | MGRA_002_Q004 | No | PG&E’s Tail Risk Project-Level Standard states that in order for a project to demonstrate substantial Wildfire Risk reduction of at least 90%. a. What is the origin of the 90% threshold? b. Is this 90% threshold in comparison to completely unmitigated, or with respect to existing mitigations in place (i.e. EPSS and PSPS)? | a. The EUP Guidelines, Section 2.7.9.2, Project-Level Standards, Subsection (c), Tail Risk Project-Level Standard, states that the “Tail Risk Project-Level Standard is the minimum decrease in wildfire likelihood that any Undergrounding Project considered under the Ignition Tail Risk Threshold must achieve to meet the required substantial reduction of the risk of wildfire.” As described in PG&E’s EUP, Chapter 6: Model Report, Section M, Project-Level Thresholds and Standards, 2(c), Tail Risk Project-Level Standard: “PG&E selected 90 percent as a conservative Standard to distinguish substantial mitigation from incremental improvement. Under this Standard, a Project must reduce at least 90 percent of pre-mitigation Ignition Likelihood or Outage Program Likelihood, leaving no more than 10 percent of the original likelihood remaining. PG&E considers this requires the Project to materially reduce the underlying ignition likelihood, rather than merely produce a marginal or measurable change”. b. The Ignition Tail Risk Project-Level Standard uses a Wildfire Likelihood baseline that is already mitigated by Enhanced Powerline Safety Settings (EPSS) and Public Safety Power Shutoff (PSPS) as the basis for determining whether the standard is satisfied. Specifically, satisfaction of the 90% Ignition Tail Risk Project-Level Standard requires a 90% reduction relative to this already operationally mitigated Wildfire Likelihood baseline. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | Mitigation Effectiveness Analysis | Tail Risk Standard; Threshold Basis
17 | MGRA | 002 | MGRA_002 | 007 | MGRA_002_Q007 | No | On p. 526, PG&E states that: “Marsh analyzed this data set to determine what fire characteristics (acres burned, estimated financial losses, reported fatalities, seasonality, weather conditions) were most predictive of a given ignition type. This analysis concluded that estimated losses were by far the strongest predictor of ignition source, including utility-asset related causes.” a. The meaning of this statement is unclear. Please explain. | a. Marsh compared the listed ignition characteristics to determine which factor provided the greatest predictive power for the ignition's source. The analysis found that estimated financial losses provided the strongest predictive power for utility asset-related causes of the ignition source and were thus selected as a frequency proxy for the Probabilistic Attribution calculation. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Marsh Third Party Impact Analysis | Probabilistic Attribution; Ignition Source
18 | MGRA | 002 | MGRA_002 | 008 | MGRA_002_Q008 | No | Regarding the estimate of homeowner premium savings due to undergrounding (p.534): a. Does the Marsh insurance model assume the historical impact of utility wildfire in the PG&E service area (80% of losses due to utility-related wildfire)? b. Does the Marsh insurance model take climate change into account, in which risk from wildfire due to all sources will increase during the analysis period? c. Does the Marsh insurance model assume that risk mitigation efforts undertaken by utilities will be immediately reflected in homeowner insurance rates? | a. The Marsh homeowners’ insurance model accounted for the impact that historical fires have had on premium pricing. Until July 2025, insurance carriers could only use historical losses when setting premium rates. This meant that known loss areas and areas designated high fire risk were likely to experience higher premiums on average than lower risk areas. Marsh’s analysis of historical pricing trends confirmed this relationship. Historical fires are critical data points within Marsh’s wildfire models, which produced the modeled average annual losses used to model anticipated premium impact. b. The Marsh insurance model already accounts for risks from all wildfire, regardless of source. This is because while Marsh studied the impact of undergrounding PG&E attributable risk, the insurance impact was derived from what changes Marsh expected in the total wildfire risk in PG&E service area. Climate change was modeled but as part of a separate, longer-term analysis of undergrounding impact under extreme climate risk pathways. EUP-PhI_DR_MGRA_002-Q008 Page 2 c. Marsh’s analysis indicated that modeled average annual losses were correlated with premiums. Real calendar years are difficult to compare directly with modeled years but, to the extent that underlying wildfire data reflects risk improvement, with that data then resulting in lower modeled average annual losses, then Marsh expects premiums to account for these lower average annual losses. With the rule change allowing modeling to be used by carriers to set pricing strategy, Marsh anticipates that this relationship between mitigation effectiveness and better premiums will be stronger. Marsh expressly characterizes its results as directional, area-based estimates, and not a prediction or guarantee of future premiums outcomes. One notable limitation to Marsh’s analysis, acknowledged within the report, is that premium pricing is also contingent on several other factors, including other natural catastrophe perils, outside the scope of Marsh’s analysis. Marsh’s findings include the caveat that its results are contingent on all other perils remaining unchanged. Since wildfire is only one covered peril, any severe non-wildfire losses could offset any premium savings achieved by lower wildfire risk. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Marsh Third Party Impact Analysis | Insurance Premiums; Climate Assumptions
19 | MGRA | 002 | MGRA_002 | 009 | MGRA_002_Q009 | No | In Workpaper 016B, EPSS Toy Problem Calculations, p. 710, the largest contribution by far to the outage count is classified as “other_equipment_type” (33,470 versus the next largest vegetation_branch at 5,693). a. What subcategories of event constitute other_equipment_type, and what are their respective contributions to outages? b. Are all outages listed arising while EPSS triggering conditions are set? c. What fraction of outages listed in the categories listed in Workpaper 016B result in ignition? | a. The other_equipment_type category are outages that are used to train the Other Equipment WDRM v4 event probability model. Other equipment is a catch-all for outages with a cause that does not belong with any other causal model or has no recorded cause. Please see Section 3.5.1.10, Other Equipment Model, in EUP attachment B-WP015, Distribution Event Probability Models Version 4, for more information on the Other Equipment Model. b. Transformer and switch-related failure modes are considered independent of EPSS operation. This is why Workpaper 016B, EPSS Toy Problem Calculations, shows zero outages for those subsets. The other failure types can result in an EPSS outage if they occur on a circuit downstream of an EPSS enabled protective device. c. The outage counts for the toy problem in Workpaper 016B were created for illustrative purposes. Please see Table 30 – Outage and Ignition Event Counts Summary in Section 3.6.1.3, Model Data, of EUP attachment B-WP015, Distribution Event Probability Models Version 4, for outage and ignition counts associated with each event type in WDRM v4. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | EUPS and PSPS | EPSS Outages; Event Probability Models
20 | MGRA | 002 | MGRA_002 | 010 | MGRA_002_Q010 | No | For WP020 EUP PSPS V1 RISK MODEL DOCUMENTATION a. Provide a description/red-line of the changes made on 3/3/2026. b. How does PG&E take upstream sections into account when calculating PSPS and EUP risk, and how does this show up int the priortization of circuits to be undergrounded? c. For hybrid projects, what does PG&E assume for the change in reliability risk? | a. Please see “EUP-PhI_DR_MGRA_002-Q010Atch01.pdf” for a redline of the changes made on 3/3/2026. b. Please see PG&E’s response to EUP-PhI_DR_MGRA_001-Q005a for a description of how PG&E accounts for the impact of PSPS events on upstream circuit segments. c. PG&E treats reliability risks (PSPS and EPSS outage risks) in hybrid projects by allocating the pre-mitigation reliability risk across the circuit segment in proportion to the mileage treated by each mitigation type, then applying the appropriate mitigation effectiveness to each portion For additional information, please see Chapter 2, Section D.1.g, “How Undergrounding Projects With Multiple Subprojects Will Be Reported and How the Risk Reduction Will Be Allocated Between Subprojects” and Chapter 7, Core Capability 5, “Accounting for Undergrounding Projects with Multiple Mitigations and Subprojects”. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.4; 2.7 | Project Acceptance Framework; Risk Modeling | EUPS and PSPS | Upstream Risk Allocation; Hybrid Projects
16 | MGRA | 002 | MGRA_002 | 005 | MGRA_002_Q005 | No | Repeat the 2024 analysis performed for Data Request RAMP- 2024_DR_TURN_006-Q004, in particular Table 1, showing the amount of covered conductor deployed and facility ignitions, updating this data to the end of September 2024. Likewise repeat the effectiveness calculation for covered conductor performed in DR_TURN_006-Q004 showing details. | PG&E interprets this request to ask for updated data as of September 2026. Please see the table below for the requested updated analysis: Metric 2018 2019 2020 2021 2022 2023 2024 Deployed Covered Conductor miles* 15.8 2025 2026 YTD Total 145 334.5 146.8 334.6 144.8 108.1 206.9 265 1,701. 05 Deployed Covered Conductor cumulative miles* 15.8 160.7 495.2 642.0 976.7 1,121. 5 1,229 .6 1,436. 5 All facility Ignitions associated with Distribution lines in HFTD / HFRA** 247 176 194 200 123 1,701. 5 1,701. 5 108 145 85 84 879 Page 1 EUP-PhI_DR_MGRA_002-Q005 EUP-PhI_DR_MGRA_002-Q005 Page 2 All CPUC RFIs associated with Distribution lines in HFTD / HFRA** 146 114 138 130 85 58 94 55 59 1362 Facility Ignitions associated with Overhead Covered Conductor Distribution lines in HFTD / HFRA ** 0 0 0 1 1 2 1 0 0 5 CPUC RFI associated with Overhead Covered Conductor Distribution lines in HFTD / HFRA ** 0 0 0 1 1 0 0 0 0 2 *minor variations in previously reported values from the original RAMP 2024_DR_TURN_006 Q004 Table 1 are due to final validations during project closure and rounding during calculations ** The results presented above were generated using data as of 10/15/2026. Some differences may exist between these results and previously reported figures. These variances may be attributable to historical updates to the underlying data, differences in reporting methodology, or changes to HFTD/HFRA boundaries over time. Based on the above data, PG&E has estimated a covered conductor mitigation effectiveness of 87.9 percent. This is done by comparing ignitions observed on bare vs. covered conductor during the 2018 to 2026 YTD period as set forth below.1 Effectiveness = 1 - (𝑝𝑝̂Covered)/( 𝑝𝑝̂Bare) = 1 - 0.077%/0.629%= 87.8%1 The details of the effectiveness calculation are provided in Appendix A. PG&E reiterates that it is inappropriate to use the above calculation for the reasons stated in response to subparts (a) and (b) of the referenced RAMP response, provided for reference here as “EUP-PhI_DR_MGRA_002-Q005Atch01.pdf.” In addition to the reasons stated in “EUP-PhI_DR_MGRA_002-Q005Atch01.pdf,” a simple count of observed ignitions on covered conductor circuits is not an appropriate way to estimate covered conductor effectiveness because it does not account for PG&E's other wildfire mitigations that operate on the same facilities, particularly Public 1 PG&E participates in the Joint CC Effectiveness Study to better understand the advantages, operative failures modes, and current state of knowledge regarding covered conductors. Based on the latest update, using data through 2022, the estimated effectiveness is 64 percent. This is consistent with the previous results that were completed using data through 2020. See Joint IOU Covered Conductor Working Group Report. A copy of the report is provided as Attachment 2023-03-27 to PG&E’s 2023 WMP. (Attachment 2023-03 27_PGE_2023_WMP_R0_Appendix D ACI PG&E-22-11_Atch01.) Safety Power Shutoff (PSPS) and Enhanced Powerline Safety Settings (EPSS). On the highest-risk days that meet PSPS criteria, PG&E de-energizes facilities in the affected areas, including covered conductor. Accordingly, ignitions involving those facilities that might have occurred under the most severe conditions are not reflected in the observed ignition counts. Similarly, EPSS quickly de-energizes a line when a fault is detected, which reduces the likelihood that a fault results in an ignition. Because these mitigations work together, their individual effects cannot be separated in a simplified count of observed ignitions like the one requested, and this significantly impacts the results of this calculation. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-16 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Mitigation Effectiveness Analysis | Covered Conductor; Ignition Data
21 | TURN | 001 | TURN_001 | 001 | TURN_001_Q001 | No | 1. Please provide PG&E’s WDRMv4 model in Excel with all circuit segments and the following information, including all calculations and data in Excel: a. Segment name/ID; b. Total Risk; c. PSPS risk; d. EPSS risk; e. Wildfire risk; f. Any other risks that are quantified (please specify). g. BCR of undergrounding with scaling; h. BCR of undergrounding without scaling; i. BCR of undergrounding without avoided O&M (scaled); j. BCR of undergrounding with avoided O&M (unscaled). | Please see Sheet Q1 Attachment “EUP-PhI_DR_TURN_001-Q001Atch01.xlsx” for all requested information and calculations. For purposes of responding to Question 1i, PG&E interprets “BCR of undergrounding without avoided O&M (scaled)” as excluding Baseline Lifetime Operations and Maintenance (O&M) Costs from the denominator. Accordingly, the denominator is calculated as the sum of UG Primary Lifetime Capital Costs and UG Primary Lifetime O&M Costs, with scaled risk benefits used in the numerator. For purposes of responding to Question 1j, PG&E interprets “BCR of undergrounding with avoided O&M (unscaled)” as including the net avoided O&M costs associated with undergrounding in the denominator. Accordingly, the denominator is calculated as UG Primary Lifetime Capital Costs less the difference between Baseline Lifetime O&M Costs and UG Primary Lifetime O&M Costs, with unscaled risk benefits used in the numerator. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.7 | Risk Modeling | WDRMv4 Model | Circuit Segment Risk; Scaled and Unscaled BCR
22 | TURN | 001 | TURN_001 | 002 | TURN_001_Q002 | No | 2. Regarding PGE_Initial_2026_09_30_T11_R0, in Excel with supporting data and working formulas please provide all inputs and outputs to the benefit-cost ratio for the 28 projects, including alternatives (proj0001 to proj00028 identified in column B). This should include, but is not limited to, values of all benefits including assumptions. For these 28 projects please also provide: a. The amount of reliability vs. wildfire risk reduced in absolute units and as a percentage of total risk. Please provide in Excel with all assumptions. b. A list of all alternative mitigations modeled and their associated mitigation effectiveness for wildfire risk and reliability risk, separately. Please provide the source of mitigation effectiveness values. i. What mitigations did PG&E model to reduce reliability risk, specifically? ii. Did PG&E model battery or backup diesel generator rebates as an alternative? Why or why not? c. The unit cost assumed for each alternative mitigation and the source of these values. d. The BCR of each project and alternative modeled but remove the avoided O&M component. Please provide in Excel with all supporting assumptions. e. The unscaled BCR of each project and alternative. Please provide in Excel with all supporting assumptions. f. Please provide the unscaled BCR of each project removing the net O&M component of the calculation. Please provide in Excel with all supporting assumptions. g. Please explain why there are negative BCRs for each instance of a negative BCR (if different). Please interpret the meaning of a negative benefit-cost ratio. h. Please add columns to this spreadsheet that indicates the number of overhead miles for each circuit segment and which of these circuit segments are part of the 4,000 overhead miles of the proposed portfolio. i. If not previously provided, for all projects with a negative BCR of the 28 projects, please provide the annual cost and avoided O&M assumptions in Excel for all years and all values. | a. Please see Columns AX and BA in the “TURN_001_Q002a-h” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx” for the reliability and wildfire risk reduced in absolute units and as a percentage of total risk on the circuit segment. b. Please see Columns BB and BF in the “TURN_001_Q002a-h” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx”. i. PG&E models the following mitigation comparison types during Screen 2 of the Portfolio Screening Process: No Build Baseline, 100% Underground (UG), Alternative Mitigation 1 (Alt 1 or Covered Conductor), Alternative Mitigation 2 (Alt 2 or Remote Grid), and Additional Comparison 1 (AC1 or 50% UG and 50% CC). The discussion of PG&E’s portfolio screening methodology and evaluation of mitigation comparison types is provided in Volume 1, Chapter 4, Portfolio Framework, including the discussion of Screen 2 mitigation alternatives. Additional information regarding each mitigation comparison type is provided in Table 3-9 in PG&E’s EUP Filing, Volume 1. Information regarding the mitigation effectiveness values used to calculate reliability risk reduction for the given mitigation comparisons, including the methodology and supporting assumptions can be found in PG&E’s EUP Filing, Volume 2, Workpaper B-WP001, “Mitigation Effectiveness Analysis.” ii. No. PG&E did not model customer battery or generator rebate programs as Alternative Mitigations in the EUP. The EUP evaluates Circuit Segment-level mitigations that reduce Ignition Risk and/or reduce the need for outage programs such as Public Safety Power Shutoff (PSPS) and Enhanced Powerline Safety Settings (EPSS). Customer battery and generator programs are resiliency measures intended to help participating customers manage the impacts of outages; however, they do not reduce Circuit Segment Ignition Risk and do not reduce the need to initiate PSPS or EPSS under wildfire conditions. Additionally, customer battery systems generally provide backup power only to selected critical loads rather than restoring normal electric service to the entire premise. While backup generators may provide broader customer-side backup capability, their operation and effectiveness depend on customer installation, maintenance, and fuel availability. Regardless of whether a customer has a battery or generator, a PSPS or EPSS event would still be recorded as an outage for the customer because electric service from the distribution system has been interrupted. Accordingly, customer battery and generator programs were not evaluated as alternatives to the Circuit Segment-level infrastructure mitigations considered in the EUP. c. Please see Column BG in the “TURN_001_Q002a-h” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx” for the unit cost assumed for each alternative mitigation. The circuit segment level unit cost per mile for a mitigation scenario is derived by dividing the total initial capital spend by the total HFTD-HFRA union miles in the circuit segment. Please see Section D, Subsection J of Chapter 2 in PG&E’s EUP Filing Volume 1 for additional information on how the unit costs were derived. Please note the Unit Cost per Mile of Proposed Mitigation includes the Present Value Revenue Requirement (PVRR) of 1.39. d. Please see Column BO in the “TURN_001_Q002a-h” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx” for the BCR of each project and alternative modeled without the avoided O&M component. PG&E interprets avoided O&M cost as the O&M cost of the baseline scenario that is no longer incurred as a cost under the given Comparison Name. e. Please see Column BP in the “TURN_001_Q002a-h” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx.” for the unscaled BCR of each project and alternative. f. Please see Column BQ in the “TURN_001_Q002a-h” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx.” for the unscaled BCR of each project without the net O&M component. PG&E interprets net O&M cost being the net of O&M cost of mitigation and the baseline scenario. g. A negative benefit-cost ratio ("BCR") can occur under the following circumstances: For projects that include Undergrounding as a mitigation: A negative BCR can occur when the net lifetime cost savings, from Underground O&M cost reductions relative to the No Build Baseline, exceed the capital installation costs of undergrounding (and capital installation costs of other mitigations, if applicable). As a result, the denominator of the BCR calculation is negative, producing a negative BCR. A negative benefit cost ratio has no direct interpretation for selecting investments, other than they effectively have no cost. If PG&E has multiple negative BCRs when evaluating alternatives, it will select the project with the greatest benefits, as the best investment candidate. h. Please see Column BR in the “TURN_001_Q002a-h” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx.” The miles reported in this column represent the scoped mileage from Screen 3, which corresponds to the existing overhead line miles that are proposed to be removed and replaced with underground facilities. These circuit segments are part of the proposed 5,000-mile undergrounding portfolio. i. Please see Column E to DJ in the “TURN_001_Q002i” tab in the provided attachment “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx”. PG&E is interpreting the annual cost and avoided O&M cost assumptions to mean the costs and savings as it pertains to O&M. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.7 | Risk Modeling | Benefit-Cost Ratio (BCR) | Project BCR Inputs; Alternative Mitigations
23 | TURN | 001 | TURN_001 | 003 | TURN_001_Q003 | No | 3. Regarding PGE_Initial_2026_09_30_T11_R0 please provide the following in Excel with all supporting calculations and assumptions: a. The unscaled benefit-cost ratio for each circuit segment and alternative mitigation modeled for all rows. b. The unscaled benefit-cost ratio for each circuit segment that removes the net avoided O&M savings component of the calculation. | a. Please see Columns R in the “TURN_001_Q003” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx” for the unscaled benefit-cost ratio for each circuit segment and alternative mitigation modeled. b. Please see Columns S in the “TURN_001_Q003” tab of “EUP-PhI_DR_TURN_001-Q002Atch01.xlsx” for the unscaled benefit-cost ratio for each circuit segment without the net avoided O&M savings component. PG&E interprets net O&M cost being the net of O&M cost of mitigation and the baseline scenario. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.7 | Risk Modeling | Benefit-Cost Ratio (BCR) | Unscaled BCR; Net O&M Savings
24 | TURN | 001 | TURN_001 | 004 | TURN_001_Q004 | No | 4. Regarding PGE_Initial_2026_09_30_T11_R0 what units are each of the benefits in? How can they be converted to dollars? Please provide an illustrative example. a. For each type of risk, please provide the total units of risk and the derivation of this in Excel with supporting data. | All the units are monetized and $ Million. The units are already in dollars. a. Please see EUP-PhI_DR_TURN_001-Q004Atch01.xlsx for the requested supporting data. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.7 | Risk Modeling | Risk Quantification | Risk Units; Monetization
25 | TURN | 001 | TURN_001 | 005 | TURN_001_Q005 | No | 5. Please provide PG&E’s data, assumptions and calculations for all “avoided O&M savings,” separately for each category of savings. Please provide for each year of the 50-year asset life of the proposal. | Please refer to the attachment “EUP_TURN_001_Q005.xlsx” for PG&E’s data and assumptions regarding annual O&M savings for each O&M category resulting in savings. For capital and expense components of O&M categories, PG&E evaluates the cost of the O&M category for the Baseline and modeled mitigations of Undergrounding, Overhead Hardening, and Remote Grid with Line Removal for each circuit segment. The variance in O&M category cost between the Baseline and modeled mitigation scenario is categorized as Savings if the Baseline cost exceeds that of the modeled mitigation, and as a Cost if the modeled mitigation cost exceeds that of the Baseline. Note that data provided in the attachment are presented as annual values of 2028 dollars per unit of measurement (e.g., 2028 dollars per mile) by O&M category and modeled mitigation. The 2028-dollar valuation does not change by year, though nominal and present values can vary by year due to inflation adjustments and discounting. Additionally, data is provided only for the Undergrounding and Remote Grid with Line Removal mitigations as the savings associated with the Overhead Hardening mitigation are estimated to be zero. Finally, Baseline Vegetation Management costs vary by circuit segment, but these costs are entirely characterized as Savings for the Undergrounding and Remote Grid with Line Removal mitigations. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Avoided O&M Savings | O&M Savings; Annual Cost Data
26 | TURN | 001 | TURN_001 | 006 | TURN_001_Q006 | No | 6. Regarding distribution vegetation management programs, please provide the following: a. PG&E’s total expenditures for all distribution vegetation management programs, separately by program, from 2018-2025 on an annual basis. b. Please provide the unit cost for all distribution vegetation management programs, separately by program, from 2018-2025 on an annual basis. | a. Please see the Excel file titled "EUP-PhI_DR_TURN_001-Q006Atch01.xlsx” for PG&E's recorded distribution vegetation management (VM) expenditures, units, and unit cost by program, on an annual basis from 2018 through 2025. All costs are in nominal year dollars (Thousands). Unit costs are shown in nominal year dollars per unit. The tables are broken down as follows: • Table 1: Total Recorded Costs by Major Program: Total recorded expenditures for each major VM program by year. • Table 2: Unitized Program / Activity Costs: Recorded costs for the programs and activities for which PG&E tracks units. • Table 3: Non-Unitized Programs / Activity Costs: Total supporting and other non-unitized costs • Total Cost Reconciliation: Shows that the unitized costs (Table 2) plus the non-unitized costs (Table 3) equal the Total Distribution VM costs (Table 1) • Units: Shows the recorded units for each program and activity. • Unit Costs: Shows the calculated unit costs for each program and activity. The attachment includes the following VM programs for the years each was in place: • Routine Distribution: 2018–2025 • Tree Mortality: 2018–2020 • Hazard Patrol/Second Patrol: 2021–2025 • Enhanced Vegetation Management (EVM): 2018–2022 • Vegetation Control: 2020–2025 • Targeted Inspections (also referred to as Focused Tree Inspection or FTI): 2023–2025 • Tree Removal Inventory: 2023–2025 • Vegetation Management for Operational Mitigations (VMOM): 2023–2025 Please note the following caveats: 1. Unit costs are calculated averages. PG&E does not record unit costs in its accounting system. Unit costs are calculated by dividing recorded unitized costs (Table 2) by recorded units, which may not include supporting and non-unitized costs (Table 3). Trims and removals have different costs, so these figures are average costs per tree, not recorded unit costs. 2. Over this period, PG&E’s VM programs and activities have changed in name, scope, and structure, since 2020 GRC. Values for one program may not be directly comparable from one year to the next. 3. Tree Mortality costs were recorded in the Catastrophic Event Memorandum Account (CEMA), outside the VM Balancing Account (VMBA), before 2020. PG&E began recovering Tree Mortality costs in the VMBA on February 16,2020. 4. EVM’s predecessor, Accelerated Wildfire Risk Reduction (AWRR), began in 2018. Its costs were recorded in the Fire Hazard Prevention Memorandum Account, outside the VMBA. 5. Routine Distribution includes EVM overhang maintenance beginning in 2023. 6. Unit costs are provided only where PG&E has tracked and reported units for that program year. Where units were not reported, the unit cost is not provided. b. Please see the Excel file titled " EUP-PhI_DR_TURN_001-Q006Atch01.xlsx” and the caveats included in PG&E’s response to subpart a. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Distribution Vegetation Management Programs | Vegetation Management Costs; Unit Costs
27 | TURN | 001 | TURN_001 | 007 | TURN_001_Q007 | No | 7. Please provide the total number of overhead and underground miles, separately, as part of system hardening, fire rebuild, or any other wildfire-related program over the same time period (2018-2025) on an annual basis. This should include all miles regardless of project status or cost recovery. | Please see the table below for completed overhead hardening (OH) and undergrounding (UG) miles from 2018 through 2025 as of October 19, 2026. The reported miles in the table below include overhead and undergrounding miles from all of our system hardening, fire rebuild, and other wildfire-related programs, regardless of cost-recovery.1 It does not include line removal miles, which were not included in this request. PG&E notes that, historically, a single project may include miles from more than one hardening method (i.e., overhead hardening, undergrounding, line removal), and its miles may be completed in different years. Miles are reported in the year they were completed | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Historical Wildfire Mitigation Program Mileage | Overhead Hardening Miles; Undergrounding Miles
28 | TURN | 001 | TURN_001 | 008 | TURN_001_Q008 | No | 8. PG&E’s EUP Vol. 1, p. 7 states, “PG&E identified approximately 8,800 overhead miles that are eligible for undergrounding under the EUP Guidelines, representing approximately 11,000 underground miles after applying standard engineering conversion factors. From this eligible population, PG&E developed a proposed portfolio of approximately 5,000 underground miles that reflects the scale of undergrounding necessary to deliver substantial system-level wildfire and reliability risk reduction while maintaining a practical and executable program over the ten-year planning horizon.” a. Please provide an explanation and underlying analysis in Excel that demonstrates why the 8,800 miles are eligible. Please include all supporting data, calculations, and assumptions. i. This should include in Excel a list of all circuit segments in WDRMv4 with associated mileage and all total risk amounts for each risk separately (wildfire risk, reliability risk, etc.), and a column indicating which are the 8,800 overhead miles. b. In the spreadsheet provided for part (a), please indicate which were selected for the 4,000 overhead / 5,000 underground miles and explain why they were selected. Please include all relevant data for why they were selected. c. Please provide the level of risk reduction, for each risk addressed, achieved by the 5,000 miles. Please provide all supporting workpapers, data, analysis, and assumptions in Excel. i. Please provide as much granularity as possible, including which circuit segments are included in the 4,000 OH miles. d. For each risk listed, please provide the current estimate of the total risk in PG&E’s service territory on an annual basis. Please include all data, assumptions, and calculations in Excel. i. Please provide on a scaled and unscaled basis. | Please note that all Wildfire Risk values, whether scaled or unscaled, referenced in this response and Attachment “EUP-PhI_DR_TURN_001-Q008Atch01” are presented on a mitigated basis and reflect Wildfire Risk after accounting for the risk-reduction effects of existing PSPS and EPSS operational mitigations. a. Please see the underlying analysis supporting the derivation of the approximately 8,800 overhead (OH) mile workplan in Attachment “EUP-PhI_DR_TURN_001-Q008Atch01.xlsx.” Please note that the initial workplan was developed primarily using high-level planning assumptions and Screen 2 Benefit-Cost Ratio (BCR) data. The following provides a step-by-step description of the process used to develop the estimated workplan. All column references below are to Sheet “Q8.a” of Attachment “EUP-PhI_DR_TURN_001-Q008Atch01.xlsx”:  Identify Circuit Segments that meet an EUP risk threshold. This determination is reflected in the column “Eligible Circuit via an EUP Threshold.”  Identify whether each Circuit Segment is included in Progress Report 0. This is reflected in the column “Circuit Segment in Progress Report 0.  Estimate the mileage available for mitigation on each WDRM v4 Circuit Segment. The resulting mileage is reflected in the columns “Available HFTD/HFRA Union Length OH Primary Miles” and “Available HFTD/HFRA Union Length UG Primary Miles.” These values incorporate the “Progress Report 0 Scoped UG Miles” and “Percentage of Circuit Segment Mileage Available” fields. PG&E also developed a high-level estimate of the mileage remaining available for mitigation on individual Circuit Segments, as reflected in the column “Percentage of Circuit Segment Mileage Available to be Mitigated.” This estimate accounts for previously completed and planned mitigation work to the extent reasonably identifiable from available data. The estimate is subject to uncertainty due to factors including changes in risk model versions and differences in geographic definitions and naming conventions between models and source datasets.  Evaluate the Undergrounding Primary BCR relative to the Overhead Hardening BCR. For purposes of this comparison, the Overhead Hardening BCR is subject to the applicable BCR Uncertainty Factor. The resulting workplan inclusion determination is reflected in the column “For inclusion in estimate EUP Workplan,” which consolidates the applicable high-level workplan inclusion criteria and returns a “Yes” or “No” for each Circuit Segment.  Calculate the estimated eligible OH mileage. Summing the values in “Available HFTD/HFRA Union Length OH Primary Miles” for Circuit Segments where “For inclusion in estimate EUP Workplan” equals “Yes” results in approximately 8,805 OH miles.  Calculate the corresponding estimated UG mileage. Summing the values in “Available HFTD/HFRA Union Length UG Primary Miles” for Circuit Segments where “For inclusion in estimate EUP Workplan” equals “Yes” results in approximately 11,008 UG miles. b. As described in PG&E’s EUP, Vol. 1, Chapter 1, Section B.1 (Achieving Substantial Risk Reduction), p. 7, the proposed 5,000 underground-mile portfolio reflects the scale of undergrounding necessary to deliver substantial system-level wildfire and reliability risk reduction while maintaining a practical and executable program over the ten-year planning horizon. The following provides a step-by-step description of the process used to develop the estimated 5,000 underground-mile workplan. All column references below are to Sheet “Q8.a” of Attachment “EUP-PhI_DR_TURN_001-Q008Atch01.xlsx”:  Identify Circuit Segments included in Portfolio 0. Circuit Segments included in Portfolio 0 are identified in the column “Circuit Segment in Progress Report 0,” and the associated scoped underground mileage is reflected in the column “Progress Report 0 Scoped UG Miles.” Circuit Segments included in Portfolio 0 are included in the estimated 5,000 underground-mile workplan. These projects represent approximately 162 underground miles.  Identify the remaining underground mileage required to develop the estimated 5,000-mile workplan. After accounting for the approximately 162 underground miles associated with Portfolio 0, approximately 4,838 additional underground miles are required to develop the estimated 5,000 underground-mile workplan.  Prioritize the remaining eligible Circuit Segments based on Wildfire Risk Rank. Circuit Segments included within the broader approximately 8,805 OH-mile eligible population described in response to Question 8(a) are sorted based on Wildfire Risk Rank.  Calculate cumulative available underground mileage. Following the Wildfire Risk Rank sorting described above, PG&E calculates the cumulative sum of the mileage reflected in the column “Available HFTD/HFRA Union Length UG Primary Miles.”  Identify the Circuit Segments included in the estimated 5,000 underground-mile workplan. Circuit Segments are included based on the prioritization described above until the cumulative underground mileage, inclusive of Portfolio 0, reaches approximately 5,000 underground miles. Please note that development of the estimated EUP workplan is performed within PG&E’s data repository system, Foundry, using Python scripts. This allows PG&E to implement the workplan logic, including the allocation of Circuit Segment mileage across plan years and, where necessary, the allocation of a portion of the final Circuit Segment required to reach the approximately 5,000 underground-mile workplan. As a result, due to limitations in replicating this allocation logic in Excel, the mileage presented in the attachment may not sum to exactly 5,000 underground miles or the corresponding approximately 4,000 overhead miles. These differences reflect the allocation of partial Circuit Segment mileage within the Foundry-based workplan logic and do not represent a difference in the estimated EUP workplan mileage. Additionally, the estimated EUP workplan is subject to change as projects progress through the Project Acceptance Framework, including Screen 3 project scoping, and as additional project-specific information becomes available. Accordingly, the specific Circuit Segments, mileage, and associated risk reflected in the estimated workplan may change over time. c. Please refer to Sheet “Q8.c” of Attachment “EUP-PhI_DR_TURN_001-Q008Atch01.xlsx” for a summary of the estimated risk addressed by the 5,000 underground-mile EUP workplan. The values presented are estimates based primarily on high-level Circuit Segment eligibility criteria and Screen 2 Benefit-Cost Ratio (BCR) information. The specific projects included in the estimated workplan, and therefore the associated risk addressed, may change as projects undergo further evaluation and scoping in Screen 3 of the Project Acceptance Framework. i. Please see Attachment EUP-PhI_DR_TURN_001-Q008Atch01.xlsx, Sheet "Q8.a." Filtering Column K to "Yes" shows the circuit segments included in the 4,000 overhead miles. Additional columns in that sheet provide segment-level detail. d. Please refer to Sheet “Q8.d.i” of Attachment “EUP-PhI_DR_TURN_001-Q008Atch01.xlsx” for a summary of PG&E’s estimated systemwide scaled and unscaled risks, expressed in 2028 dollars ($M). The following risk values are provided: i. Unscaled Overall Utility Risk (2028 $M) ii. Unscaled Wildfire Risk mitigated by PSPS and EPSS (2028 $M) iii. Unscaled PSPS Risk (2028 $M) iv. Unscaled EPSS Risk (2028 $M) v. Scaled Overall Utility Risk (2028 $M) vi. Scaled Wildfire Risk mitigated by PSPS and EPSS (2028 $M) vii. Scaled PSPS Risk (2028 $M) | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.4 | Project Acceptance Framework | Undergrounding Eligibility and Portfolio Selection | Eligible Miles; Portfolio Sizing
29 | TURN | 001 | TURN_001 | 009 | TURN_001_Q009 | No | 9. PG&E’s EUP Vol 1 at pp. 355-356 states PG&E evaluated industry benchmarks to determine acceptable risk. We reviewed data from the Federal Energy Regulatory Commission, the Department of Defense, the Nuclear Regulatory Commission, and the United Kingdom’s Health and Safety Executive. We chose an individual risk acceptance of 0.5 x 10-6 fatalities per year defined as an acceptable risk for an average individual in the vicinity of a nuclear power plant. The individual risk acceptance criterion was converted to an acceptance loss exceedance curve, which was then used to identify the minimum number of Circuit Segments that are required for mitigation at the system level, if they were prioritized by wildfire risk per mile, to reach an acceptable level of risk in the HFTD/HFRA (in aggregate). PG&E then draws a risk buy-down curve plotting each Circuit Segment, with overall utility risk per mile on the y-axis and wildfire risk per mile rank on the x-axis. The High-Risk Threshold is then set to the lowest Overall Utility Risk value per mile within the number of Circuit Segments that are required for mitigation. a. Please provide this analysis in Excel with all supporting data, workpapers, and assumptions. b. In Excel, if not provided, please provide a list of all circuit segments in WDRMv4 with ID and calculate the risk threshold metric. Please include all data and calculations and indicate which circuit segments are eligible per this screen. c. Please explain why the individual risk acceptance for a nuclear power plant is the relevant threshold for undergrounding projects in the EUP. | a. This analysis in Excel with all supporting data, workpapers, and assumptions are provided in the attachment “EUP-PhI_DR_TURN_001-Q009Atch01.xlsx”. b. A list of all circuit segments in WDRMv4 indicating which circuit segments are eligible per this screen are provided in the attachment “EUP-PhI_DR_TURN_001-Q009Atch.xlsx”, tab “3. All_CS”. c. The primary objective of undergrounding under PG&E's Electric Undergrounding Plan (EUP) is to protect public safety by reducing the risk of catastrophic utility-caused wildfires. California has not adopted a wildfire-specific risk tolerance criterion. PG&E therefore based its criterion on an established federal benchmark for catastrophic safety risk: the U.S. Nuclear Regulatory Commission (NRC) Safety Goal Policy Statement (51 Fed. Reg. 28044, August 4, 1986). Under that goal, the risk to an average individual in the vicinity of a nuclear power plant of prompt fatalities that might result from reactor accidents should not exceed 0.1 percent of the sum of fatality risks resulting from other accidents to which the members of the U.S. population are generally exposed. This corresponds to about 0.5×10⁻6 fatalities per person per year, and PG&E uses that value as its individual risk acceptance criterion. PG&E does not suggest that wildfire hazards are physically comparable to nuclear accidents. The NRC criterion is relevant to consider for wildfire risk for the following reasons. 1. It also addresses the public safety risk imposed on members of the public who live near infrastructure operated by a regulated utility. The NRC developed its safety goals to answer how safe such facilities must be for the surrounding public. That is the same question the High Risk Threshold must answer for utility-caused wildfire. 2. It uses the same measure of consequences. The NRC goal addresses fatalities from accidents, which are similar to wildfire fatalities. 3. The NRC goal is defined for the average individual in the vicinity of the facility. PG&E applied in the EUP this criterion to the average individual exposed to wildfire in the High Fire Threat District and High Fire Risk Area (HFTD/HFRA). 4. It is well-established, well-researched and stable. The NRC safety goal was adopted through a regulatory process and has been successfully used in U.S. regulatory decision-making for nearly four decades. In the absence of other wildfire-specific risk thresholds, PG&E believes that this is the best benchmark that is available now that can be used in the EUP. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.7 | Risk Modeling | High-Risk Threshold | Risk Acceptance Criterion; Loss Exceedance
30 | TURN | 001 | TURN_001 | 010 | TURN_001_Q010 | No | 10. Regarding Table 2-5 on page 63. a. Please provide all analysis in Excel supporting the values in this table. b. In Excel, please provide all circuit segments in WDRMv4 including ID and overhead mileage. Please calculate each metric for each circuit segment shown in the table, unless not applicable. i. Please include all data and assumptions to calculate the metric. ii. For each value other than lines 5 and 6 please provide the average value of the metric in PG&E’s HFTD. Please provide in Excel with all supporting calculations and assumptions including at the circuit segment level. iii. Please indicate which circuit segments meet the threshold criteria set by PG&E. iv. For lines 5 and 6, please provide the list of mitigations that can meet this standard. 1. Please indicate which of these mitigations were modeled in the EUP. | a. Please see the requested information provided in “EUP-PhI_DR_TURN_001-Q010Atch01.xlsx.” b. Please see the requested information provided in “EUP-PhI_DR_TURN_001-Q010Atch01.xlsx.” i. Please see the table below Line No Standard or Threshold Value Cell Reference in EUP-PhI_DR_TURN_001-Q010Atch01 1 High Risk Threshold $0.029M OUR/OH Mile High Risk!C:3 2 Ignition Tail Risk Threshold $52.437M per ignition Tail Risk!D:6 3 High Frequency Outage Program Threshold 5,559 outage minutes/year Outage Risk!D:6 4 High Risk Project-Level Standard Varies High Risk!I:I 5 High Frequency Outage Program Project-Level Standard 90% See Below 6 Tail Risk Project-Level Standard 90% See Below 7 Ignition Portfolio-Level Standard – Portfolio Level $0.045M /OH Mile Portfolio Level Standards!E:4 8 Outage Portfolio-Level Standard – Portfolio Level $0.100M /OH Mile Portfolio Level Standards!E:5 9 Ignition Portfolio-Level Standard – System Level $0.0023M /OH Mile Portfolio Level Standards!E:6 10 Outage Portfolio-Level Standard – System Level $0.0049M /OH Mile Portfolio Level Standards!E:7 High Frequency Outage Program Project-Level Standard The EUP Guidelines, Section 2.7.9.2, Project-Level Standards, Subsection (b), High Frequency Outage Program Project-Level Standard, states that the “High Frequency Outage Program Project-Level Standard is the minimum decrease in Outage Program Likelihood as measured through formal calculations of the KDMMs that any Undergrounding Project considered under the High Frequency Outage Program must achieve to meet the required substantial increase in electrical reliability achieved by reducing the use of public safety power shutoffs, enhanced powerline safety settings, deenergization events, and any other outage programs.” As described in Chapter 7: Risk Modeling Methodology, Section M, Project-Level Thresholds and Standards, 2(b), High Frequency Outage Program Project-Level Standard, a Project must reduce the likelihood of Enhanced Powerline Safety Settings (EPSS) and Public Safety Power Shutoff (PSPS) on a Circuit Segment by at least 90 percent. PG&E selected 90 percent as a conservative Standard to distinguish substantial mitigation from incremental improvement. Under this Standard, a Project must reduce at least 90 percent of pre-mitigation Outage Program Likelihood, leaving no more than 10 percent of the original likelihood remaining. PG&E considers this level of reduction a readily verifiable demonstration of substantial improvement because it requires the Project to materially reduce the underlying hazard rather than merely produce a marginal or measurable change. Tail Risk Project-Level Standard The EUP Guidelines, Section 2.7.9.2, Project-Level Standards, Subsection (c), Tail Risk Project-Level Standard, states that the “Tail Risk Project-Level Standard is the minimum decrease in wildfire likelihood that any Undergrounding Project considered under the Ignition Tail Risk Threshold must achieve to meet the required substantial reduction of the risk of wildfire.” As described in PG&E’s EUP, Chapter 6: Model Report, Section M, Project-Level Thresholds and Standards, 2(c), Tail Risk Project-Level Standard: “PG&E selected 90 percent as a conservative Standard to distinguish substantial mitigation from incremental improvement. Under this Standard, a Project must reduce at least 90 percent of pre-mitigation Ignition Likelihood or Outage Program Likelihood, leaving no more than 10 percent of the original likelihood remaining. PG&E considers this requires the Project to materially reduce the underlying ignition likelihood, rather than merely produce a marginal or measurable change”. ii. Please see the table below Line No Standard or Threshold Value Cell Reference in EUP-PhI_DR_TURN_001-Q010Atch01 1 High Risk Metric Average $0.402M OUR/OH Mile High Risk!C:4 2 Ignition Tail Risk Metric Average $1.463M /OH Mile Tail Risk!D:7 3 High Frequency Outage Program Average 103 outage minutes/year Outage Risk!D:7 4 High Risk Project-Level Standard Average $0.397M OUR/OH Mile High Risk!C:5 5 High Frequency Outage Program Project-Level Standard 90% Not Applicable 6 Tail Risk Project-Level Standard 90% Not Applicable 7 Ignition Portfolio-Level Standard – Portfolio Level $0.045M /OH Mile Portfolio Level Standards!E:4 8 Outage Portfolio-Level Standard – Portfolio Level $0.100M /OH Mile Portfolio Level Standards!E:5 9 Ignition Portfolio-Level Standard – System Level $0.0023M /OH Mile Portfolio Level Standards!E:6 10 Outage Portfolio-Level Standard – System Level $0.0049M /OH Mile Portfolio Level Standards!E:7 iii. See Table Below Line No Standard or Threshold Cell Reference in EUP-PhI_DR_TURN_001-Q010Atch01 1 High Risk Threshold High Risk!E:E 2 Ignition Tail Risk Threshold High Risk!R:R 3 High Frequency Outage Program Threshold High Risk!Q:Q iv. Undergrounding and Remote Grid with Line Removal are the alternatives modeled in the EUP that can achieve the 90 percent standard. Undergrounding is modeled as eliminating EPSS and PSPS likelihood on the mitigated portion of the Circuit Segment. Overhead Hardening is also modeled, but it provides no reduction in PSPS likelihood and only partial reduction in EPSS likelihood. As a result, Overhead Hardening alone would not satisfy the 90 percent High Frequency Outage Program Project-Level Standard. For hybrid projects, compliance depends on the combined mitigation effectiveness across the Circuit Segment. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.3 | Demonstration of Substantial Risk Reduction | Project-Level Standards | Thresholds and Standards; Circuit Segment Metrics
31 | TURN | 001 | TURN_001 | 011 | TURN_001_Q011 | No | 11. Please provide the wildfire, PSPS, and EPSS mitigation effectiveness values for all mitigations modeled by PG&E in its EUP. | The mitigation values used in PG&E’s EUP are listed in Volume 1, Table PCS-6, pp. 401-405. | A Mireille Fall | 2026-10-19 | 2026-10-22 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-001.zip | 2.7 | Risk Modeling | Mitigation Effectiveness | Mitigation Effectiveness Values; Table PCS-6
32 | MGRA | 003 | MGRA_003 | 001 | MGRA_003_Q001 | No | Table 1-2, p. 15, shows calculations for Unscaled and Mitigated Risk Reduction and Scaled and Unmitigated Risk Reduction. a. Provide an additional column for Scaled and Mitigated Risk Reduction. | a. Please see the table below for the requested information: Line No. Risk Type Unscaled and Mitigated Risk Reduction Scaled and Unmitigated Risk Reduction Scaled and Mitigated Risk Reduction 1 Total Wildfire and Outage Program Risk $15.1 $117.4 $30.3 2 Wildfire $4.5 $104.9 $17.8 3 EPSS $6.3 $6.3 $6.3 4 PSPS $4.3 $6.2 $6. | Joseph Mitchell | 2026-10-19 | 2026-10-22 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-003.zip | 2.7 | Risk Modeling | Wind | Scaled and Mitigated Risk Reduction; Table 1-2
33 | MGRA | 003 | MGRA_003 | 002 | MGRA_003_Q002 | No | With regard to PG&E’s response to MGRA Data Request 2, Question 3, does PG&E incorporate damage or hazards identified in post-PSPS patrols in any of its risk calculations? If so how? | Yes. PG&E uses damage and hazard information identified during post-PSPS restoration patrols to inform PSPS avoided ignition analyses in its WDRM v4 and WLDFR (Wildfire Risk Bow Tie) models. In WDRM v4, PSPS damages and hazards are included as a type of failure in the failure probability models and use an assumed ignition rate in the ignition probability model. Wildfire Risk Bow Tie model also uses PSPS damages and hazards data in estimating ignitions avoided through PSPS events. It calculates avoided ignitions by multiplying the number of hazards and damages identified during post-PSPS patrols by an outage-to-ignition rate derived from historical ignition and outage data associated with vegetation- and equipment-caused events during Red Flag Warning (RFW) conditions in High Fire Threat Districts (HFTDs). These avoided ignitions are then annualized along with the historical ignition data for baseline risk calculation for applicable drivers and RFW outcomes. | Joseph Mitchell | 2026-10-19 | 2026-10-22 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-003.zip | 2.7 | Risk Modeling | Wind | Post-PSPS Patrols; Avoided Ignitions
34 | MGRA | 003 | MGRA_003 | 003 | MGRA_003_Q003 | No | Table PCS-6 shows the risk reduction of overhead hardening as 67% for balloons and 57% for covered conductor line slap. PG&E’s previous WMP filing (pp. 191- 194) shows that these risk reduction values were much higher. a. What accounts for the much lower efficiency estimated by PG&E for balloons and line slap than was reported in PG&E’s WMP? b. Southern California Edison reported 99% effectiveness of covered conductor for both balloons and line slap in its GRC filing.1 Why is PG&E’s estimate of covered conductor efficiency so low for these drivers? c. In its response to RAMP-2024_DR_TURN_006-Q004, PG&E calculated that the observed efficiency of covered conductor inclusive of EPSS was 79.3%. Does this value have any relationship to the 79% efficiency PG&E claims for system wide effectiveness of overhead hardening and EPSS in its EUP? d. For both balloons and line slap, provide the data analysis, statistics, and analysis that led PG&E to derive the numbers presented in PCS-6. | a. The values cited from PG&E’s prior WMP are not directly comparable to the values presented in Table PCS-6 because the analyses reflect different mitigation scenarios and methodologies. PG&E assumes MGRA is referring to the Joint IOU Grid Hardening Working Group Report, which cites results of various outage drivers. In the EUP, Table PCS-6 presents the incremental effectiveness of Overhead Hardening with respect to the baseline wildfire risk condition that already includes EPSS and PSPS mitigations, whereas the WMP effectiveness values are derived with respect to a baseline condition without EPSS and PSPS mitigations. The covered conductor effectiveness values in WMP TABLE PG&E-8.2.1-3, are labelled to indicate which, if any, additional operational mitigations they include. Accordingly, the differences in the balloon and line-slap values do not indicate that PG&E concluded covered conductor became less effective. Rather, we reflect differences in the mitigation scenario and analytical methodology being evaluated. Please refer to PG&E’s Mitigation Effectiveness Workpaper in the EUP (WP 001, Section 2.3.1, Vol 2, pp. 501-503) where we explain the incremental approach to mitigation effectiveness by mitigation type and the operational controls in place. b. Covered-conductor effectiveness estimates are utility-specific and reflect differences in mitigation design, underlying data, failure-mode definitions, engineering assumptions, and analytical methodology. This distinction is supported by the Joint IOU covered-conductor work. The most recent Joint IOU Grid Hardening Working Group report is particularly relevant. Using PG&E’s methodology and historical outages classified according to WDRM v4 drivers, it reported PG&E Overhead Hardening effectiveness of 88% for Third Party (Balloon) and 85% for Primary Conductor-Line Slap. As detailed in that report, PG&E’s overall effectiveness value is 67%, which increases to 79% when combined with EPSS and DCD, while SCE estimates a 60% effectiveness for its Wildfire Covered Conductor Program (WCCP) and SDG&E estimates a 44% effectiveness for CC at reducing wildfire risk. Thus, comparing individual driver values or overall effectiveness values across utilities without accounting for methodological differences can produce misleading conclusions. The 99% SCE estimate reflects SCE’s methodology and assumptions and is not directly interchangeable with PG&E’s reported values. c. No, these values are distinct because they were derived through different analyses. The 79% value in the EUP and our 2027 GRC is based on our mitigation effectiveness analysis and reflects Overhead System Hardening combined with EPSS and DCD. That analysis uses engineering assessments of each mitigation's ability to prevent ignition across more than 2,700 combinations of outage failure modes and more than 100,000 historical outage failure events. The 79.3% value in RAMP-2024_DR_TURN_006-Q004 was a simple comparison of observed facility ignition rates on covered and bare conductor in HFTD/HFRA from 2018 through 2024 year-to-date. We provided the value in response to TURN's request which required the specific methodology. As we explained in our response, the limited number of ignitions observed on covered conductor is not sufficient to support a meaningful effectiveness calculation, and thus is not the method PG&E uses to establish mitigation effectiveness values. For PG&E’s updated analysis and a more detailed explanation of the limitations of this methodology, please refer to PG&E’s response to EUP-Ph1_DR_MGRA_002-Q005 and Attachment EUP-Ph1_DR_MGRA_002-Q005Atch01. d. Please see the following attachment, “EUP-PhI_DR_MGRA_003-Q003Atch01.xlsx,” which provides the data, calculations, and results supporting the mitigation effectiveness values for Third Party – Balloon and Primary Conductor – Line Slap reported in Table PCS-6. Please see EUP Volume 2, Workpaper WP001 (Mitigation Effectiveness Analysis) that describes the approaches used to derive the mitigation effectiveness values. | Joseph Mitchell | 2026-10-19 | 2026-10-22 | 2026-10-22 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-003.zip | 2.7 | Risk Modeling | Hardening | Covered Conductor; Balloon and Line Slap Effectiveness
35 | MGRA | 003 | MGRA_003 | 004 | MGRA_003_Q004 | No | PG&E’s Risk Model Change Factor Calculation (pp. 55-57) shows that there is 20% more calculated risk per mile with WDRM v3 than there is with WDRM v4. However, overall risk is increased by 30% through inclusion of PG&E’s suppression and ingress/egress submodules. a. How does PG&E reconcile these two values? | The two percentages are not directly comparable. PG&E's Risk Model Change Factor measures the change in risk density for the proposed EUP portfolio. MGRA's approximately 30% figure compares aggregate modeled risk between WDRM v3 and v4. Because WDRM produces relative, rather than absolute, risk values, comparisons between versions are meaningful only when calibrated to Bow Tie risk. Any increase or decrease in total system risk is therefore determined by the Bow Tie system risk evaluation, not aggregate WDRM risk. Additionally, WDRM v4 introduced multiple substantive enhancements, including improved historical fire data, 24-hour simulations, Terrain Difficulty Index, and public egress and wildfire suppression adjustments. Collectively, these enhancements altered the relative geographic distribution of modeled risk and produced a flatter risk profile. As a result, the proposed EUP portfolio can have lower relative risk per mile under WDRM v4 than under WDRM v3 | Joseph Mitchell | 2026-10-19 | 2026-10-22 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-003.zip | 2.3 | Demonstration of Substantial Risk Reduction | Risk Model | Risk Model Change Factor; WDRM v3 and v4
36 | TURN | 002 | TURN_002 | 001 | TURN_002_Q001 | No | Refer to Table 1-2 in PG&E EUP Vol 1 on p. 15. Please provide the following total Bow Tie wildfire risk and reliability risk totals in Excel with supporting workpapers, data, and calculations: a. Total with PSPS and EPSS (mitigated). b. Total without PSPS and EPSS (unmitigated). c. Total, scaled. d. Total, unscaled. | Please see “EUP-PhI_DR_TURN_002-Q001Atch01.xlsx” for the requested total Bow Tie wildfire and reliability risk values. Supporting workpapers, data, and calculations are provided in Risk Model EO – WLDFR, EO – WEPSS, and EO – WPSPS workpapers that were submitted in PG&E’s 2027 GRC filing (A.25-05-009), Exhibit (PG&E-2), Chapter 1, Errata 2, filed April 10, 2026. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.7 | Risk Modeling | Bow Tie Risk Totals | Bow Tie Risk; Mitigated and Unmitigated Totals
37 | TURN | 002 | TURN_002 | 002 | TURN_002_Q002 | No | Please provide total wildfire damages ($’s), structures burned, and fatalities, separately, in PG&E’s service territory from all causes of wildfire from 2015-2025 on an annual basis. Please provide in Excel with supporting data. a. Please indicate, for each year, the percentage of damages, structures burned, and fatalities were started by a fire cause by utility equipment. | Total wildfire dollar damages from all causes within the CAL FIRE State Responsibility Area (SRA), reported separately for the northern and southern regions, are available in Table 17, “CAL FIRE SRA Dollar Damage by Cause, by Unit,” of the CAL FIRE Redbooks . Dollar damages associated with wildfires outside the CAL FIRE SRA are not available to PG&E. Annual totals for structures destroyed, structures damaged, and fatalities associated with wildfires greater than 300 acres in PG&E’s service territory from 2015-2025 are provided in “Annual_Summary” tab of “EUP-PhI_DR_TURN_002-Q002Atch01.xlsx”. a. For each year, the estimated percentages of structures destroyed, structures damaged, and fatalities attributable to wildfires caused by utility equipment, based on wildfires greater than 300 acres , are provided in the “Annual_Summary” tab of “EUP-PhI_DR_TURN_002-Q002Atch01.xlsx”. PG&E is unable to provide the percentages of dollar damages attributable to wildfires caused by utility equipment because fire-level dollar damage data are not available from CAL FIRE. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.7 | Risk Modeling | Wildfire Damages, Structures Burned, and Fatalities | Historical Wildfire Impacts; Utility-Caused Share
38 | TURN | 002 | TURN_002 | 003 | TURN_002_Q003 | No | Please provide the Risk Attitude function formula, parameters, inputs, and outputs. Please clearly describe, or show in a simple spreadsheet calculation, how the Risk Attitude function is used in the Wildfire Risk Bow Tie model (PG&E's EUP Vol 1 at pp 299). a. Please provide supporting documentation and explanations, including any spreadsheets with all formulas intact, for the derivation of this function. | PG&E’s Risk Attitude function is a piecewise linear function with three regions. The formula, specified for each of the three regions, is as follows: 𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑛𝑛1:𝑆𝑆1(𝑉𝑉)=𝑆𝑆𝑆𝑆𝑆 𝑆𝑆𝑒 1𝑉𝑉 𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑛𝑛2:𝑆𝑆2(𝑉𝑉)=𝑌𝑌𝐴𝐴,1+𝑆𝑆𝑆𝑆𝑆 𝑆𝑆𝑒 2􀵫𝑉𝑉−𝑋𝑋𝐴𝐴,1􀵯 𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑅𝑛𝑛3:𝑆𝑆3(𝑉𝑉)=𝑌𝑌𝐴𝐴,2+𝑆𝑆𝑆𝑆𝑆 𝑆𝑆𝑒 3􀵫𝑉𝑉−𝑋𝑋𝐴𝐴,2􀵯 Where parameters are: Slopei is the slope for the Scaling Function in Region i. The slopes are {1, 2, 7.5} in Regions {1, 2, 3} XA,i is the upper bound of the monetized value for Attribute A in Region i YA,i is the y-intercept for Attribute A in Region i The input is the monetized value (V) for a particular Attribute representing risk event consequence. The monetized value is the product of the impact in Natural Units and the Attribute-specific monetization factor. The output of the function is the risk-adjusted monetized value for a given V. Please see “EUP-Phl-DR_TURN_002-Q003Atch01.xlsm” for an implementation of PG&E’s Risk Attitude function. In Row 28 of said workbook, a user can input any desired Safety, Electric Reliability, or Financial consequence value (in Natural Units) per event and see what the corresponding risk adjusted monetized consequence value per event is. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.7 | Risk Modeling | Risk Attitude Function | Risk Attitude Function; Risk Scaling
39 | TURN | 002 | TURN_002 | 004 | TURN_002_Q004 | No | Please provide the “risk-neutral” dollar total from the Bow Tie model (PG&E's EUP Vol 1 p. 271-272). Please provide in Excel with supporting data and calculations. | Please see “EUP-PhI_DR_TURN_002-Q001Atch01.xlsx”, table section “d. Unscaled 2025 Risk Score” (Columns G–J), for the requested “risk-neutral” dollar total from the Bow Tie model (PG&E's EUP Vol 1 p. 271-272). Supporting workpapers, data, and calculations are provided in Risk Model EO – WLDFR, EO – WEPSS, and EO – WPSPS workpapers that were submitted in PG&E’s 2027 GRC filing (A.25-05-009), Exhibit (PG&E-2), Chapter 1, Errata 2, filed April 10, 2026. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.7 | Risk Modeling | Risk-Neutral Risk | Bow Tie Model; Unscaled Risk
40 | TURN | 002 | TURN_002 | 005 | TURN_002_Q005 | No | Please explain, and provide supporting calculations in Excel format with all native formulas intact, the non-linear risk adjustment from the Multi-Attribute Value Function (MAVf) that adjusts the consequence of more extreme events (PG&E’s EUP Vol 2 at p. 982). a. Please provide an example calculation with explanation showing the impact of the risk adjustment formula. | The Multi-Attribute Value Function (MAVf) in the Wildfire Consequence (WFC) model version 4 described in PG&E’s EUP Vol 2 at p.982 uses the same non-linear function described in EUP-PhI_DR_TURN_002-Q003. The only difference is that WFC version 4 uses values of $15 million for the Value of Statistical Life, and $3.16/CMI (customer minutes interrupted), both in 2023 dollars. a. The example calculations associated with the explanation for Q003 are included as EUP-Phl-DR_TURN_002-Q003Atch01.xlsm. The value in cell C3 would be updated to $15 million for the Value of Statistical Life and the value in cell C4 would be updated to $3.16/CMI (customer minutes interrupted) to represent the MAVf in the WFC model version 4. Clarifying Note: Page 982 of the EUP Vol 2 lists the value of VSL used as $12.5M which was referring to an older version that was updated to $15M before the wildfire consequence version 4 was finalized. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.7 | Risk Modeling | Multi-Attribute Value Function (MAVf) | MAVF; Non-Linear Risk Adjustment
41 | TURN | 002 | TURN_002 | 006 | TURN_002_Q006 | No | Refer to Table 1-2 in PG&E EUP Vol 1 on p. 15. Please explain and provide supporting calculations in Excel format with all native formulas intact for the scaling of wildfire risk from $4.5 to $104.9 B. a. Please explain and provide supporting calculations in Excel format with all native formulas intact for the ~1.44 scaling factor of PSPS from $4.3 to $6.2 B. b. Explain why EPSS risk remains $6.3 B in the two scenarios presented. | Please see the “TURN_002_Q006” tab in “EUP-PhI_DR_TURN_002-Q006_Atch01.xlsx” for the supporting calculations underlying the $4.5 billion and $104.9 billion wildfire risk reduction values. As described in Section 1.3 of PG&E EUP Volume 1, the $4.5 billion value reflects wildfire risk reduction without risk-averse scaling and includes wildfire, EPSS, and PSPS risk within the baseline. In contrast, the $104.9 billion value reflects wildfire risk reduction with risk-averse scaling applied and excludes EPSS and PSPS risk from the baseline. Accordingly, the $104.9 billion value cannot be derived by simply applying the wildfire risk-aversion scalar to the $4.5 billion value. The two values are based on different underlying risk baselines. The $4.5 billion value includes EPSS and PSPS mitigations in the baseline, while the $104.9 billion value is based solely on wildfire risk and does not include EPSS or PSPS mitigations in the baseline. As a result, the difference between the two values reflects both the application of risk-averse scaling and the use of different baseline risk compositions. a. Please see “TURN_002_Q006a” tab of “EUP-PhI_DR_TURN_002-Q006_Atch01.xlsx” for the supporting calculations to demonstrate the application of the PSPS risk-averse scaling factor. b. Please see “TURN_002_Q006b” tab for EPSS. EPSS risk remains $6.3 billion in both scenarios because EPSS event consequence does not typically exceed the threshold for the severe consequence (Region 2) as defined in the PG&E’s risk-averse scaling function. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.7 | Risk Modeling | Risk Scaling | Risk-Averse Scaling; Table 1-2
42 | TURN | 002 | TURN_002 | 007 | TURN_002_Q007 | No | Referring to WP006 (Vol. 2, pp. 545–546 and 556–562) and Table 1-2 (Vol. 1, p. 15): a. For each benefit category (Wildfire, EPSS, PSPS), please state whether the inflation factor “(1 + Inflation Rate)” is applied (i) once, to convert values to 2028 dollars, or (ii) year by year over the benefit period to produce nominal values. b. Please state which discount rate (7.0% nominal or 4.61% real) was used to calculate each present value in Table 1-2. Please provide the table in Excel with all supporting data and calculations. c. If benefits were escalated year by year and discounted at the real rate, please explain why this does not overstate present-value benefits. Please restate Table 1-2 using a consistent method. d. Please provide the annual benefit streams behind Table 1-2, in both nominal and 2028 real dollars, in native Excel format. | a. Annual risk values are first converted from 2025 dollars to 2028 dollars by applying a (1+2.28%) annual inflation factor over the three-year period, along with the applicable climate factor. Once all risks are expressed in 2028 dollars, PG&E calculates the lifetime present value of risk (and therefore benefits) using the real discount rate over the effective life of the asset. Climate factors continue to be applied on a year-by-year basis beyond 2028; however, inflation is not. The 2.28% inflation factor is used only once to establish a common 2028-dollar baseline across all benefit categories, including Wildfire, EPSS, and PSPS. Thereafter, annual climate factors are applied to project future risk levels, while all values remain in constant 2028 dollars and present value calculations are performed using the real discount rate. A 2.28% inflation throughout the years can be used to come up with nominal yearly values. However, the present value calculations use real values and a real discount rate. b. PG&E utilized the real discount rate of 4.61% to calculate the present values presented in Table 1-2. Please see the tabs “TURN_002-Q007b_(WF_PV)’, “TURN_002-Q007b_(EPSS_PV)”, “TURN_002-Q007b_(PSPS_PV)” in “EUP-PhI_DR_TURN_002-Q007Atch01.xlsx” for the supporting data, formulas, and calculation steps used to derive the present values used to generate Table 1-2. Total present value of risk is the sum of the three tabs related to Wildfire(WF), EPSS, and PSPS. c. PG&E did not escalate benefits year by year and then discount them using the real discount rate. Rather, as explained in the response to part (a) above, PG&E first escalated the modeled risk values from 2025 to 2028 to express all benefits in a common 2028-dollar basis. Once the benefits were converted to 2028 dollars, PG&E applied the real discount rate to calculate present values. Because the inflation adjustment was applied only once to establish a consistent 2028 baseline, and not repeatedly over the analysis period, the methodology does not overstate present-value benefits. d. Please see “EUP-PhI_DR_TURN_002-Q007Atch01.xlsx” for the nominal and real dollars breakout of the values in Table 1-2. Note that tabs that show Wildfire Related yearly nominal values and real values are TURN_002-TURN_002-Q007d_(WF_Nominal) and TURN_002-Q007d_(WF_Real) respectively. Similar tab naming conventions for EPSS and PSPS are used. Tab “TURN_002-Q007d_Summary” provides a summary of all present values, nominal values, and real values related to wildfire, PSPS, EPSS and the total risk. The tab also provides an illustrative example that shows how the use of nominal discount rate on nominal values and real discount on real values yields the same annual present value. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.5 | Project Timelines, Workforce Development Plan, Costs and Benefits, and Non-Ratepayer Funding Sources | Inflation and Discount Rates | Present Value Methodology; Table 1-2
43 | TURN | 002 | TURN_002 | 008 | TURN_002_Q008 | No | Explain why PG&E applied a single system-level PSPS/EPSS risk reduction when allocating Bow Tie wildfire risk to circuit segments, rather than circuit- or segment-specific reductions. Identify any alternatives PG&E considered and why they were rejected. | PG&E’s Enterprise Wildfire Bow Tie produces an absolute, monetized wildfire-risk value at the system level. It does not produce a location-specific Bow Tie wildfire-risk value for each circuit segment. By contrast, WDRM V4 produces relative wildfire-risk scores at the circuit-segment level. The WBCA therefore bridges those two models by taking the system-level post-PSPS/post-EPSS Bow Tie risk and allocating it to circuit segments in proportion to their WDRM risk scores. PG&E did not identify any other alternatives than the approach that was taken. | A Mireille Fall | 2026-10-20 | 2026-10-23 | 2026-10-23 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-turn-data-request-002.zip | 2.7 | Risk Modeling | PSPS and EPSS Risk Allocation | Bow Tie Risk Allocation; Circuit Segments
44 | MGRA | 004 | MGRA_004 | 001 | MGRA_004_Q001 | No | PG&E in various places and for various purposes uses both scaled and unscaled wildfire risk calculation. In Table 9-3, p. 397, PG&E indicates that Scaled Wildfire Risk post-PSPS is a precursor to the BCR metric: a. In the rest of the document and supplemental files, please identify all instances for which “BCR” or “Benefit-Cost Ratio” implies the use of scaled wildfire risk in the benefit calculation, and for which “BCR” or “Benefit-Cost Ratio” implies the use of unscaled wildfire risk, unless the title of the variable or section already specifies whether the BCR uses scaled or unscaled benefit values. b. If there are tables in which a BCR is presented that depends on scaled wildfire risk, please present an alternative table where columns are added presenting unscaled wildfire risk. | a. The BCRs calculated in the EUP and supporting workpapers use Scaled Wildfire Risk post-PSPS and post-EPSS, consistent with Table 9-3 (Model Risk Landscape Variables). The SPD-37 Appendix 1 Data Submission (Attachment D) separately reports scaled and unscaled BCR values in fields identified as benefit_cost_ratio_scaled and benefit_cost_ratio_unscaled. b. Unscaled BCRs are provided in PG&E’s SPD-37 Appendix 1 Data Submission (Attachment D, SPD-37 Data Table 1), alongside the scaled BCRs, for each project and comparison type. These can be matched to the applicable project-level information in Tables C.11, C.13, and C.15 using the Project ID. | Joseph Mitchell | 2026-10-20 | 2026-10-23 | 2026-10-23 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-004.zip | 2.8 | Reporting Metrics | Benefit-Cost Ratio (BCR) | Scaled and Unscaled BCR; Table 9-3
45 | MGRA | 004 | MGRA_004 | 002 | MGRA_004_Q002 | No | Specify which of the following variables used in the PG&E data tables use scaled wildfire risk and which use unscaled wildfire risk. a. Ignition_consequence b. 100_percent_ug_total_risk_reduction c. 100_percent_ug_cost_benefit_ratio d. project_as_scoped_total_risk_reduction e. project_as_scoped_cost_benefit_ratio f. screen_2_alt_1_total_risk_reduction g. screen_2_alt_1_cost_benefit_ratio h. screen_2_alt_2_total_risk_reduction i. screen_2_alt_2_cost_benefit_ratio j. screen_3_alt_total_risk_reduction k. screen_3_alt_cost_benefit_ratio l. baseline_cumulative_risk m. project_as_scoped_cumulative_risk n. screen_3_alt_cumulative_risk | Please see the requested information below: Variable Unscaled/Scaled Status a. Ignition_consequence Unscaled b. 100_percent_ug_total_risk_reduction Scaled c. 100_percent_ug_cost_benefit_ratio Scaled d. project_as_scoped_total_risk_reduction Scaled e. project_as_scoped_cost_benefit_ratio Scaled f. screen_2_alt_1_total_risk_reduction Scaled g. screen_2_alt_1_cost_benefit_ratio Scaled h. screen_2_alt_2_total_risk_reduction Scaled i. screen_2_alt_2_cost_benefit_ratio Scaled j. screen_3_alt_total_risk_reduction Scaled k. screen_3_alt_cost_benefit_ratio Scaled l. baseline_cumulative_risk Unscaled m. project_as_scoped_cumulative_risk Unscaled n. screen_3_alt_cumulative_risk Unscaled | Joseph Mitchell | 2026-10-20 | 2026-10-23 | 2026-10-23 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-004.zip | 2.8 | Reporting Metrics | Benefit-Cost Ratio (BCR) | Data Table Variables; Scaled and Unscaled Risk
46 | OEIS | 002 | OEIS_002 | 001 | OEIS_002_Q001 | No | Q01. Fire Rebuild Areas a.PG&E defines a “Fire Rebuild Area” as “four or more spans of electric distribution infrastructure damaged by a fire” (PG&E EUP, p. 98). Table 24 from PG&E’s Tabular Data submission, however, identifies “Wildfire Rebuild Areas” by fire event which can consist of multiple impacted circuit segments. i.State whether a “Fire Rebuild Area is (i) a single circuit segment, (ii) a fire event that may include multiple circuit segments, or (iii) something else. ii.Provide PG&E’s definition of a “Fire Rebuild Area” and cite any documentation that establishes it. b.Regarding the types of fires that qualify: i.Explain why PG&E uses “Fire” rather than “Wildfire” when referring to rebuild areas and projects. ii.State whether “Fire Rebuild Areas” and “Fire Rebuild Projects” include line damage caused by fires other than wildfires (e.g., structure or vehicle fires) (Yes/No). i.If yes, identify each Table 24 entry caused by a non-wildfire fire and the fire type. ii.If yes, explain the basis for including non-wildfire fires as eligible rebuild areas under the EUP. c.Regarding Table 24 of PG&E’s Tabular Data submission: i.State whether the fire events provided in Column A of this table, are PG&E’s “Fire Rebuild Areas” (Yes/No). If no, identify the field that identifies “Fire Rebuild Areas.” ii.For the data in Table 24, provide: (i) each system of record used; (ii) the validation steps performed; and (iii) how often data is updated. iii.Identify each government agency to which PG&E reports the fire-event or "Fire Rebuild Area” information in Table 24. For each agency, provide the agency/program receiving the information and the reporting mechanism (dataset, filing, incident report, or other). If none, state so. iv.For the data in Table 24, please identify fire events that occurred outside State Responsibility Areas where CalFire is the primary emergency response agency. For these entries, please identify which emergency response agency was the primary emergency response agency for the fire event. v.Several Table 24 entries do not provide an ignition date or fire location. For each such entry, provide: (i) ignition date; (ii) location; (iii) fire cause; (iv) whether the fire was a wildfire (Yes/No); (v) HFTD/HFRA status; and (vi) supporting documentation (e.g. CAL FIRE or local fire agency incident report). If this information is not available, provide a justification on why. vi.For fire events where “Fire Location” is provided as latitude and longitude, do the coordinates represent the point of ignition, a random spot within the fire perimeter, or something else? vii.Please explain how PG&E determines which latitude and longitude coordinates to use to identify the location of Fire Events. | Fire Rebuild Areas a. i. The Fire Rebuild area definition applies to a single circuit segment. ii. As noted in the question, PG&E defines “Fire Rebuild Area” as “An area with four or more spans of electric distribution infrastructure damaged by fire that requires the electrical distribution facilities to be reconstructed or repaired.” (EUP, Vol. 2, p. 1178.) This definition is consistent with Energy Safety’s definition of “Wildfire Rebuild Area” on page A-7 of the Guidelines and PG&E’s approved 2026-2028 Wildfire Mitigation Plan which states that “System hardening is deployed where significant rebuild is required (e.g. four or more spans and/or segments with intermittent damage) and other repairs will not suffice.” (PG&E 2026-2028 WMP, p. 190.) b. i. PG&E does not distinguish between wildfire events and other fire events in the context of rebuilding infrastructure damaged by fire. PG&E uses Fire Rebuild Areas rather than Wildfire Rebuild Areas for consistency with its 2026-2028 Wildfire Mitigation Plan. ii. PG&E does not distinguish between wildfire events and other fire events in the context of rebuilding infrastructure damaged by fire, because both result in the same outcome: repairs to the damaged distribution infrastructure. Accordingly, PG&E’s undergrounding tracking and GIS system do not distinguish between causes of fire events in its service territory for purpose of this rebuild work or for providing a wildfire/non-wildfire distinction. in Table 24. PG&E describes the process for defining a Circuit Segment as a Fire Rebuild Project in Chapter 3, Section D.1.a. c. i. No. The Fire Event Name in Table 24 Column A describes a fire incident which is associated with electric distribution infrastructure damage. The Fire Rebuild Areas for each Fire Event Name are listed in the Affected Circuit Segments field, and in the rebuild_area column in Table 6. ii. The process used to define Fire Rebuild Areas is described in Chapter 3, Section D.1.a. The systems of record used to identify Affected Circuit Segments and Facilities Impacted are one or more of the following: a. A Fire Rebuild Project scoped on the Circuit Segment using the damage assessment process described in Chapter 3, Section D.1.a (pp. 98-100). b. The presence of Electric Corrective (EC) 22 tags from fires spanning 2015 to 2025 on the Circuit Segment. Fire Event Names are derived from the Fire Rebuild Project description in the System Hardening Workplan, or by matching a Fire Event Name referenced in the EC Tag historical dataset to a historical CAL FIRE incident using information published by CAL FIRE at https://www.fire.ca.gov/incidents. Fires resulting in the creation of a Fire Rebuild Project or an EC Tag may occur at any time. New Fire Events will be added to Table 24 any time the data is refreshed, specifically prior to the creation of an EUP Progress Report. iii. PG&E does not report the data in Table 24 to any agency other than the Office of Energy and Infrastructure Safety. Table 24 was created solely to comply with the requirements in the Section 2.4.3.1 of the EUP Guidelines. iv. PG&E does not specifically record whether fire events take place within or without State Responsibility Areas within the systems of record used to produce Table 24, and cannot provide this information for the Circuit Segment or Fire Event Name. v. PG&E derives the Ignition Date and Fire Location data from historical CAL FIRE data published at https://www.fire.ca.gov/incidents. PG&E may not be able to associate historical fire damage on its electric distribution infrastructure with a CAL FIRE event, resulting in the ‘Unknown’ data shown in these fields in Table 24. PG&E only records fire damage on its infrastructure and therefore cannot independently provide the requested data for all Fire Events. vi. The coordinates in the Fire Location field are derived from historical CAL FIRE data published at https://www.fire.ca.gov/incidents. PG&E has not confirmed what the coordinates provided by Cal FIRE represent for each fire. vii. See answer to b.vi. | David Rey | 2026-10-21 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-002.zip | 2.4 | Project Acceptance Framework | Fire Rebuild Areas | Fire Rebuild Area Definition; Table 24
47 | OEIS | 002 | OEIS_002 | 002 | OEIS_002_Q002 | No | Q02. Fire Rebuild Projects a.Provide PG&E's definition of a “Fire Rebuild Project” and cite any documentation that establishes it. b.On p. 253 of PG&E’s EUP, PG&E states that the: “status of rebuild work for wildfire areas that do not have associated system hardening work and/or is not in Fire Rebuild Areas is designated as ‘N/A’.” a.Explain how a Fire Rebuild Project could not be in a Fire Rebuild Area. b.Provide a specific example from a Fire Rebuild Project in PG&E’s EUP | a. PG&E’s EUP defines “Fire Rebuild Projects” as “Reconstruction or repair of a Circuit Segment located in a Fire Rebuild Area.” (EUP, Vol. 2, p. 1178.) PG&E defines “Fire Rebuild Area” as “An area with four or more spans of electric distribution infrastructure damaged by fire that requires the electrical distribution facilities to be reconstructed or repaired.” (EUP, Vol. 2, p. 1178.) This definition is consistent with Energy Safety’s definition of “Wildfire Rebuild Area” on page A-7 of the Guidelines and PG&E’s approved 2026-2028 Wildfire Mitigation Plan which states that “System hardening is deployed where significant rebuild is required (e.g. four or more spans and/or segments with intermittent damage) and other repairs will not suffice.” (PG&E 2026-2028 WMP, p. 190.) b. A Fire Rebuild Project that qualifies for PG&E’s EUP is a Confirmed Project that has passed through the damage assessment process described in EUP Chapter 3, Section D.1.a, and in Figure 3-2. a. A Fire Rebuild Project will always be in a Fire Rebuild Area. The Rebuild Status field in Table 24 will only show ‘N/A’ if there is not currently a planned or completed Fire Rebuild Project associated with the Fire Event. b. There are no planned or completed Fire Rebuild Projects included in Progress Report 0 of the EUP. Therefore, there is no Fire Rebuild Project example available within the current EUP dataset. As a result, all applicable entries reflect that no associated Fire R | David Rey | 2026-10-21 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-002.zip | 2.4 | Project Acceptance Framework | Fire Rebuild Projects | Fire Rebuild Project Definition; Rebuild Status
48 | OEIS | 002 | OEIS_002 | 003 | OEIS_002_Q003 | No | Q03. Emergency Damage and Customer Service Assessment a.Provide PG&E's definitions of a “span” and a “segment” as used in the Emergency Damage and Customer Service Assessment (PG&E EUP Figure 3-2). b.Provide PG&E's definition of “intermittent damage” as used in the Emergency Damage and Customer Service Assessment (PG&E EUP Figure 3-2). c.Regarding intermittent damage: i. Describe the process by which intermittent damage is identified, documented, and reviewed. ii.Provide PG&E’s procedure for determining whether damage is classified as intermittent. iii.Provide PG&E’s procedure for calculating whether the intermittent damage exceeds 50%. d.On p. 99 of PG&E’s EUP, PG&E states that a: “Circuit Segment is only prioritized as a Fire Rebuild Project if it is reviewed according to the [Emergency Damage and Customer Service Assessment] damage assessment process described in this paragraph and in Figure 3-2 below.” i. At what point in the assessment does circuit segment get designated a Fire Rebuild project: (i) whenever a circuit segment is reviewed, regardless of the assessment’s outcome, (ii) if the circuit segment has 4 or more damaged spans or 50% intermittent damage, or (iii) something else. | A "span" in this context refers to the overhead primary conductor extending between two poles. A "segment" refers to a section of distribution line identified for assessment and potential mitigation evaluation following a wildfire event. EUP-PhI_DR_OEIS_002-Q003 Page 2 b. PG&E does not maintain a separate glossary definition for "intermittent damage" within the EUP. For purposes of the Emergency Damage and Customer Service Assessment, intermittent damage refers to wildfire damage that is distributed throughout an assessed segment rather than concentrated within a single contiguous portion of the segment. Figure 3-2 evaluates whether the proportion of damaged facilities within the assessed segment exceeds the applicable threshold used to determine whether additional mitigation evaluation is warranted. c. i. During a wildfire event, PG&E identifies the fire boundary and assesses all poles located within that boundary. Damage information is documented during the assessment process and affected facilities are organized into segments for evaluation. Segments are assigned unique identifiers and structured to support evaluation of hardening opportunities, construction planning, resource deployment, and documentation of work. Following assessment, PG&E reviews the documented damage within the identified segments to determine the extent and distribution of damage and evaluates the segment in accordance with the Emergency Damage and Customer Service Assessment process shown in Figure 3-2. ii. PG&E determines whether damage is intermittent by evaluating the distribution of damaged structures throughout the assessed segment. Damage that is distributed throughout the segment rather than concentrated within a localized portion of the segment is evaluated under the intermittent-damage pathway identified in Figure 3-2. iii. PG&E calculates the intermittent damage percentage by dividing the number of damaged structures within the assessed segment by the total number of structures within that segment. The resulting percentage is then compared to the threshold identified in Figure 3-2 to determine whether the segment proceeds to mitigation evaluation. d. A circuit segment is not designated as a Fire Rebuild Project merely because it has been reviewed through the Emergency Damage and Customer Service Assessment process, nor is designation automatic upon meeting the damage thresholds identified in Figure 3-2. A segment is identified as a Fire Rebuild Project only after: 1. The segment has been evaluated under the Emergency Damage and Customer Service Assessment process; 2. The applicable damage criteria in Figure 3-2 have been met; 3. Restoration and mitigation alternatives have been evaluated; and 4. Undergrounding is selected as the preferred mitigation strategy for the affected segment. Accordingly, the correct characterization is (iii) something else. If repair, overhead hardening, remote grid, or another mitigation alternative is selected, the segment would not be identified as a Fire Rebuild Project for EUP reporting purposes | David Rey | 2026-10-21 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-002.zip | 2.4 | Project Acceptance Framework | Emergency Damage and Customer Service Assessment | Damage Assessment; Intermittent Damage
49 | OEIS | 002 | OEIS_002 | 004 | OEIS_002_Q004 | No | Q04. Scope of Hardening Following Rebuild Project Determination a.Provide PG&E's methodology for determining the portion of a Circuit Segment that is included within the scope of a Rebuild Project once a Circuit Segment has been determined to qualify as a Rebuild Project. b.After a project is designated as a Rebuild Project and 100% Undergrounded is determined as the grid hardening mitigation, which of the following scenarios would occur: i.undergrounding of only the damaged spans or segments; ii.undergrounding of the entire Circuit Segment; iii.undergrounding of the portions of the Circuit Segment within HFTD or HFRA zones; iv.undergrounding of adjacent portions of unaffected Circuit Segments. | a. Identification of a Fire Rebuild Area does not automatically result in a Fire Rebuild Project, nor does it automatically place an entire Circuit Segment into the Fire Rebuild Project evaluation process. Following a wildfire event, PG&E assesses the damaged facilities within the Fire Rebuild Area and evaluates the affected portion of the Circuit Segment in accordance with the Emergency Damage and Customer Service Assessment process described in Figure 3-2. Only the fire-affected portion of the Circuit Segment is advanced through the Fire Rebuild Project evaluation process. If undergrounding is ultimately selected as the preferred mitigation strategy and approved for execution, the final project scope is established through project development and engineering design. b. Undergrounding is generally evaluated only for the fire-affected portion of the Circuit Segment as described by scenario (i): undergrounding of the damaged spans or segments. The final undergrounding scope is developed through our scoping and engineering design process and may be adjusted based on project-specific engineering, constructability, operational, permitting, environmental, or other considerations. | David Rey | 2026-10-21 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-002.zip | 2.4 | Project Acceptance Framework | Scope of Hardening Following Rebuild Project Determination | Rebuild Project Scope; Undergrounding Scope
50 | OEIS | 002 | OEIS_002 | 005 | OEIS_002_Q005 | No | Q05. Fire Rebuild Project Risk Baselines a.On p. 53, PG&E states: “Circuit Segments entirely outside HFTD/HFRA are excluded from the Plan Mitigation Objective.” i.State whether PG&E would underground eligible, Non-HFTD Rebuild Projects through the EUP Program (Yes/No) i.If yes, state if the risk reduction achieved by undergrounding eligible, Non-HFTD Rebuild Projects would count toward the Plan Mitigation Objective (Yes/No). ii.If yes, state whether the miles achieved by undergrounding eligible, Non-HFTD Rebuild Projects would count toward PG&E’s 4,000 undergrounding mile target (Yes/No). b.On p.355 of PG&E’s EUP, PG&E states that the “Pre-Wildfire distribution infrastructure for Fire Rebuild Projects where the fire occurred before January 1, 2023, would not beavailable for baseline comparisons. See discussion of previously-scoped projects in Chapter 3, Section D.5.” i.Explain why PG&E is unable to provide this information. ii.State whether PG&E is proposing to incorporate Fire Rebuild Projects associated with wildfire events prior to 2023 into the EUP portfolio, even if those Fire Rebuild Projects do not meet all EUP requirements (Yes/No). i.If yes, explain the basis for including these projects despite not meeting the EUP all requirements. | a. No. Under Figure 3-2, a non-HFTD project would not qualify for consideration as a Fire Rebuild Project using undergrounding as the selected mitigation strategy. a.i. Not applicable a.ii. Not applicable b.i. PG&E is unable to provide pre-wildfire baseline comparisons for Fire Rebuild Projects associated with wildfire events occurring before January 1, 2023 because the EUP risk baseline is derived from the WDRM V4 circuit geometries and associated risk framework established as of January 1, 2023. Comparable pre-wildfire baseline information consistent with the EUP methodology is therefore unavailable for wildfire events that occurred before that date. Reconstructing equivalent baseline risk values would require recreating historical circuit geometries and risk model inputs that predate establishment of the EUP baseline framework. b.ii. No. PG&E is not proposing to include Fire Rebuild Projects associated with wildfire events occurring prior to January 1, 2023 in the EUP portfolio. The discussion regarding projects associated with wildfire events occurring before January 1, 2023 addresses the availability of pre-wildfire baseline comparisons and does not establish inclusion of those projects in the EUP portfolio. | David Rey | 2026-10-21 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-002.zip | 2.4 | Project Acceptance Framework | Fire Rebuild Project Risk Baselines | Non-HFTD Rebuild Projects; Pre-2023 Baselines
51 | OEIS | 003 | OEIS_003 | 001 | OEIS_003_Q001 | No | Selection of Alternative Mitigation Strategies for Screens 2 and 3 1. Provide the analyses and decision criteria supporting PG&E’s selection of the Alternative Mitigation strategies used in Screens 2 and 3: a. Identify the mitigation types and combinations of mitigation types PG&E evaluated for inclusion in its Alternative Mitigation framework, including any which were excluded. b. Describe the screening criteria applied to each candidate mitigation, including technical feasibility, risk reduction, reliability, costs, scalability, readiness, and applicability to the EUP Circuit Segment population. c. Explain why PG&E selected overhead hardening and 100% Remote Grid as the Screen 2 alternatives and how PG&E determines that these alternatives constitute useful comparisons to undergrounding. | PG&E's Project Acceptance Framework evaluates permanent wildfire mitigation strategies at different levels of project maturity in Screens 2 and 3. Screen 2 uses standardized design variations to provide a consistent and transparent comparison of mitigation alternatives across Eligible Circuit Segments based on the information available at that stage. Screen 3 incorporates more detailed project-specific information developed through scoping, including feasibility, constructability, local conditions, project configuration, and updated scope and cost information. Accordingly, the Screen 2 comparisons do not establish that each modeled alternative is technically feasible or preferred for implementation across the entirety of every Eligible Circuit Segment. Rather, they provide a standardized basis for comparing undergrounding with other permanent mitigation strategies. Screen 3 then provides a more refined, project-specific comparison based on the available project scope and feasibility information. The EUP specifically explains that PG&E uses homogeneous mitigation design variations at Screen 2 to provide a logical, consistent, and transparent basis for comparison, while Screen 3 incorporates more detailed project-scope and feasibility information (EUP Vol. 1, Ch. 3, Section D.2, pp. 110-111; Table 3-9, p. 115). a. PG&E evaluates the following permanent-infrastructure design variations through the Project Acceptance Framework (EUP Vol. 1, Ch. 3, Section D.2, pp. 110-111; See Table 3-9, p. 115 for detailed descriptions): Screen Comparison Mitigation(s) Screen 2 100% Underground (100% UG) 100% UG includes relocating existing high-risk overhead primary distribution lines underground. PG&E currently also undergrounds secondary and service lines that run parallel to the UG primary lines Screen 2 Alternative Mitigation 1 (Alt 1) 100% overhead hardening (covered conductor and associated framing) Screen 2 Alternative Mitigation 2 (Alt 2) 100% Remote Grid with line removal, where feasible Screen 2 Additional Comparison 1 (AC 1) Hybrid – 50% underground / 50% overhead hardening Screen 3 100% UG Undergrounding; may include small overhead-hardened portions only where required for feasibility (e.g., Transmission-line under-build) Screen 3 Screen 3 Alternative Mitigation (S3 AM) Best-BCR non-undergrounding option: covered conductor, remote grid, or a combination, where feasible Screen 3 Additional Comparison 2 (AC 2) Scoped hybrid of undergrounding, overhead hardening and/or remote grid Screen 3 Additional Comparison 3 (AC 3) Best-BCR alternative (100% UG, S3 AM, or AC 2 plus Remote Grid / LEIP where feasible) These design variations reflect the distinction between the standardized comparisons conducted at Screen 2 and the project-specific configurations evaluated at Screen 3. The 50% Undergrounding and 50% Overhead-Hardening Hybrid is treated as an Additional Comparison rather than an Alternative Mitigation because it includes undergrounding. The EUP Guidelines define “Alternative Mitigation” as a mitigation strategy, other than Undergrounding, used to reduce the consequence or likelihood of wildfires and Outage Program Events on a particular Circuit Segment (EUP Guidelines, Appendix A). The Guidelines separately require comparison of 100% Undergrounding against two Alternative Mitigations (EUP Guidelines Section 2.7.10(a), (e)-(f), pp. 44-45). Operational mitigations, including Enhanced Powerline Safety Settings (EPSS), Downed Conductor Detection (DCD), and Public Safety Power Shutoff (PSPS), are reflected in the Baseline rather than evaluated as separate permanent-infrastructure alternatives (Vol. 1, Ch. 3, p. 111; Table 3-9, note (a); Ch. 3, Section D.3.a.11, p. 143). Removal of idle lines and redundant circuit ties is evaluated during the Screen 3 Alternative Mitigation Review (Ch. 3, Section D.3.a.5, p. 131). PG&E included in the Project Acceptance Framework all permanent wildfire mitigation technologies approved for wide-scale use by PG&E that could be evaluated as alternatives under the EUP Guidelines. Technologies intended to improve the cost or implementation efficiency of an existing mitigation, including Fluid Free Steerable Boring, Native Slurry Backfill, and GLDS/MCDS, are not separate mitigation alternatives (Ch. 3, p. 116). Other technologies, including Continuous Grid Monitoring sensors, Early Fault Detection, are being implemented and evaluated through the 2026-2028 WMP and were not included as separate Alternative Mitigations in the EUP Project Acceptance Framework (EUP Vol. 1, Ch. 3, Section D.2.d, p. 118). REFCL likewise was not included as an Alternative Mitigation because it is not approved for wide-scale deployment by PG&E. b. In the EUP Screens 2 and 3 processes and analyses, PG&E considered: (1) whether a mitigation was approved for wide-scale use and suitable for deployment in PG&E’s service territory (EUP Vol. 1, Ch. 3, Section D.2.b, p. 116); (2) whether it satisfied the comparative-metric requirements in the EUP Guidelines Section 2.7.10 (Ch. 3, Section D.2.a, p. 116; Ch. 7, Section N, pp. 361–362); and (3) whether its wildfire risk reduction, reliability effects, lifecycle costs, and other benefits could be quantified consistently through the WBCA to support comparison across alternatives (Ch. 5, Section C.3.a, pp. 197–199; Attach. B, WP006). These considerations address technical feasibility, wildfire risk reduction, reliability, cost, scalability, and applicability across the EUP Circuit Segment population. For alternatives evaluated through the Project Acceptance Framework, wildfire risk reduction is quantified using mitigation effectiveness values and Project Variable Modifiers (Attach. B, WP001; Vol. 1, Table PCS-6), and lifecycle costs and benefits are evaluated through the WBCA. The BCR analysis reflects lifetime capital installation costs and operation and maintenance costs, net of applicable avoided costs or savings. The level of feasibility information available differs between Screens 2 and 3. At Screen 2, PG&E applies standardized assumptions to support consistent planning-level comparisons across Eligible Circuit Segments. Screen 2 therefore does not represent a determination that each modeled mitigation could be implemented across the entirety of every Circuit Segment. At Screen 3, PG&E incorporates more detailed project-specific information developed through scoping and evaluates the alternatives using the project configuration and feasibility information available at the time. For example, the Screen 3 hybrid comparison can be updated from the standardized Screen 2 configuration to reflect the actual proportions of undergrounding, overhead hardening, and/or Remote Grid that are feasible for the project. For Remote Grid in particular, feasibility considerations include customer willingness, site availability, land rights, environmental and permitting requirements, and engineering feasibility (Table 3-9, note (b), p. 115). Screen 3 therefore provides the appropriate stage for determining how a mitigation or combination of mitigations may be configured for a particular project. c. The EUP Guidelines prescribe aboveground hardening using covered conductor, together with associated protective equipment and settings, as Screen 2 Alternative Mitigation 1. PG&E selected 100% overhead hardening for this comparison because overhead hardening is an established PG&E GRC/WMP system-hardening mitigation program that can be evaluated broadly across the Eligible Circuit Segment population and provides a meaningful comparison to undergrounding with respect to wildfire risk reduction, reliability effects, and lifecycle costs (EUP Vol. 1, Ch. 4, Section D.2, pp. 168–172). PG&E’s EUP defines this alternative as the replacement of bare overhead primary conductor and associated framing with covered conductor, together with the applicable system-hardening measures. The EUP Guidelines further require Alternative Mitigation 2 to meet or exceed the risk reduction of Alternative Mitigation 1 and identify line removal with Remote Grid as an example of an eligible mitigation (EUP Guidelines Section 2.7.10(e)-(f); EUP Vol. 1, Ch. 7, Section N, pp. 361-362). PG&E selected 100% Remote Grid with line removal as Screen 2 Alternative Mitigation 2 because Remote Grid represents a distinct permanent mitigation approach that, where feasible, allows removal of overhead facilities while maintaining electric service through standalone, decentralized utility infrastructure. PG&E did not select a hybrid configuration that included undergrounding as Alternative Mitigation 2 because the EUP Guidelines define an “Alternative Mitigation” as a mitigation strategy other than Undergrounding (EUP Guidelines Appendix A). The Guidelines separately require comparison of 100% Undergrounding against two Alternative Mitigations (EUP Guidelines Section 2.7.10(a), (e)-(f), pp. 44-45). PG&E's prior experience implementing Remote Grid solutions and removing associated overhead facilities provided relevant operational experience with Remote Grid as a permanent mitigation in appropriate circumstances. PG&E also selected the 100% Remote Grid configuration for Screen 2 to maintain a homogeneous comparison at this preliminary stage. Using homogeneous mitigation design variations provides a logical, consistent, and transparent basis for comparing materially different permanent mitigation strategies across Eligible Circuit Segments (EUP Vol. 1, Table 3-9, p. 115). The Screen 2 Remote Grid comparison does not represent a determination that converting the entirety of each Eligible Circuit Segment to Remote Grid is technically feasible or would be selected for implementation. Rather, it provides a standardized analytical comparison. More granular project configurations, including combinations of undergrounding, overhead hardening, and/or Remote Grid where feasible, can be evaluated in Screen 3 using project-specific scoping information (EUP Vol. 1, Table 3-9, p. 115). Screen 2 BCRs are preliminary Circuit Segment-level comparisons that are refined through Screen 3 as more detailed project-specific scope and feasibility information becomes available (EUP Vol. 1, Ch. 3, p. 110-111). | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | Selection of Alternative Mitigation Strategies for Screens 2 and 3 | Screen 2 and 3 Alternatives; Screening Criteria
52 | OEIS | 003 | OEIS_003 | 002 | OEIS_003_Q002 | No | Q02. Consideration of Alternative Screen 2 Alt 2 Configurations 1. Identify whether PG&E considered alternative configurations for Screen 2 Alternative Mitigation 2 (Alt 2) other than 100% Remote Grid, including but not limited to combinations of overhead hardening with Rapid Earth Fault Current Limiters (REFCL) or other advanced protection, advanced grid monitoring, line removal, system reconfiguration, or partial Remote Grid: a. For each configuration evaluated, identify the components, feasibility and risk-reduction criteria, and the results or basis for eliminating it from further consideration. b. For mitigation combinations not evaluated, explain the reasons they were not considered and whether PG&E anticipates assessing their use during EUP implementation. 2. Explain whether PG&E considered using different Screen 2 Alternative Mitigation 2 configurations for Eligible Circuit Segments based on technical applicability, rather than a single 100% Remote Grid design variation, and provide any existing supporting analysis. Include whether PG&E performed any automated circuit segment screening or technical suitability assessments, such as simple checks based on customer count, segment length, and position on the circuit. | 1. PG&E did not evaluate alternative configurations of Screen 2 Alternative Mitigation 2 (Alt 2), other than 100% Remote Grid with associated line removal, as separate Screen 2 design variations. PG&E used 100% Remote Grid as a standardized configuration to provide a consistent planning-level basis for comparing mitigation alternatives across the Eligible Circuit Segment population (EUP Vol. 1, Table 3-9, p. 115). Screen 2 does not represent a determination that 100% Remote Grid is technically feasible across the entirety of every Circuit Segment. Rather, Screen 2 BCRs are high-level Circuit Segment-level values, and project-specific configurations and feasibility are evaluated in Screen 3 as more detailed scoping and technical information becomes available (EUP Vol. 1, Ch. 3, p. 110-111; Table 3-9, note (b), p. 115). The EUP provides for evaluation of project-specific combinations of undergrounding, overhead hardening, and Remote Grid at Screen 3 when more detailed scoping and feasibility information is available (Table 3-9 and note (b), p. 115; Figure 3-8, p. 140). Opportunities to remove idle lines and redundant circuit ties are evaluated through the Screen 3 Alternative Mitigation Review (Ch. 3, Section D.3.a.5, p. 131; Figure 3-6, p. 130). Configurations that include undergrounding are evaluated as Additional Comparisons rather than as separate Screen 2 Alt 2 design variations. a. PG&E did not evaluate configurations other than 100% Remote Grid with associated line removal as separate Screen 2 Alt 2 design variations. Accordingly, PG&E does not have configuration-specific Screen 2 analyses identifying the components, feasibility, and risk reduction criteria, or results or bases for eliminating the other combinations identified in the question from further consideration. b. PG&E did not evaluate the combinations identified in the question as separate Screen 2 Alt 2 design variations for two reasons. First, configurations involving line removal, system reconfiguration, partial Remote Grid, or combinations of Remote Grid with overhead hardening require project-specific topology, scoping, and feasibility information that is not available at Screen 2. These configurations may be evaluated at Screen 3 based on the portions of undergrounding, overhead hardening, and/or Remote Grid that are feasible for the particular project. Remote Grid feasibility considerations include customer willingness, site availability, land rights, environmental and permitting requirements, and engineering feasibility. Opportunities to remove idle lines and redundant circuit ties are also evaluated during the Screen 3 Alternative Mitigation Review (EUP Vol. 1, Table 3-9 and note (b), p. 115; Ch. 3, Section D.3.a.5, p. 131; Figure 3-6, p. 130; Figure 3-8, p. 140). Second, PG&E included in the Project Acceptance Framework all permanent wildfire mitigation technologies approved for wide-scale use by PG&E that could be evaluated as alternatives under the EUP Guidelines. REFCL was not evaluated as a separate Screen 2 Alt 2 configuration because it is not currently an approved PG&E standard mitigation practice, and PG&E does not have an approved standard for REFCL installation. As described in PG&E’s 2026-2028 WMP, Section 8.7.1.3.1, REFCL continues to undergo testing and evaluation, including evaluation of its reliability and safety impacts. Similarly, Continuous Grid Monitoring sensors and Early Fault Detection are being implemented and evaluated through PG&E’s 2026-2028 WMP but are not approved standard mitigation practices for inclusion as separate Alternative Mitigations in the EUP Project Acceptance Framework (EUP Vol. 1, Ch. 3, Section D.2.d, p. 118). Enhanced Powerline Safety Settings (EPSS) and Downed Conductor Detection (DCD) are reflected in the Baseline rather than evaluated as separate permanent-infrastructure alternatives (EUP Vol. 1., Ch. 3, pp. 110-111; Table 3-9, note (a); Ch. 3, Section D.3.a.11, p. 143). During EUP implementation, PG&E will continue to evaluate new and innovative practices involving line sensing, protection, and other wildfire mitigations. If a technology becomes an approved standard mitigation practice, PG&E would determine how it should be evaluated within the Project Acceptance Framework, including whether its applicability can be evaluated through a standardized Screen 2 comparison or requires project-specific evaluation at Screen 3. PG&E will continue to evaluate applicable project-specific combinations of approved mitigations through the Screen 3 Alternative Mitigation Review and Additional Comparisons. 2. PG&E did not evaluate different Screen 2 Alternative Mitigation 2 configurations for individual Eligible Circuit Segments based on technical applicability. As described above, PG&E used 100% Remote Grid with associated line removal as a standardized Screen 2 configuration to provide a consistent planning-level basis for comparing mitigation alternatives across the Eligible Circuit Segment population. Screen 2 does not represent a determination that 100% Remote Grid is technically feasible across the entirety of each Circuit Segment. Rather, project-specific configurations and feasibility are evaluated at Screen 3 as more detailed scoping and technical information becomes available (EUP Vol. 1, Ch. 3, pp. 110-111; Table 3-9 and note (b), p. 115). PG&E did not perform automated Circuit Segment screening or technical suitability assessments at Screen 2 to identify different Alt 2 configurations based on factors such as customer count, segment length, or position on the circuit. At Screen 3, as part of the project-specific Remote Grid feasibility review, PG&E identifies potential Remote Grid locations, including portions of a Circuit Segment that are end of line, relatively long, and serve relatively few customers, and evaluates site-specific feasibility considerations. These considerations include customer willingness, site availability, land rights, environmental and permitting requirements, and engineering feasibility (EUP Vol. 1, Table 3-9 and note (b), p. 115; Figure 3-8, p. 140). Accordingly, PG&E does not have a separate Screen 2 analysis identifying different Alt 2 configurations for individual Eligible Circuit Segments based on technical suitability. The supporting analysis for the Screen 2 approach and the subsequent consideration of project-specific configurations is reflected in the EUP Project Acceptance Framework and Screen 3 Alternative Mitigation Review described above. | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | Consideration of Alternative Screen 2 Alt 2 Configurations | Alt 2 Configurations; Remote Grid
53 | OEIS | 003 | OEIS_003 | 003 | OEIS_003_Q003 | No | Q03. Feasibility and Decision Value of 100% Remote Grid as Screen 2 Alternative Mitigation 2 1. Explain the role of 100% Remote Grid with line removal (100% RG) as Screen 2 Alternative Mitigation 2 (Alt 2): a. Identify whether Screen 2 identified any Eligible Circuit Segments for which 100% Remote Grid has a higher modeled benefit-cost ratio (BCR) than both 100% undergrounding and Screen 2 Alternative Mitigation 1, and which appear, based on currently available information, to be reasonable candidates for further Remote Grid scoping. i. In making this preliminary assessment, consider factors such as circuit topology and configuration, customer count, circuit segment location, service continuity needs, and other relevant technical or operational constraints. ii. For each such segment, provide its Circuit Segment ID, the BCRs for the three Screen 2 design variations, and a brief explanation of the factors supporting its potential suitability for further evaluation, including any significant known constraints. b. Describe what segment-level feasibility screening is performed between Screen 2 and Screen 3 for potential 100% Remote Grid projects including customer count, load, system configuration, land constraints, reliability requirements, and any other material limitations. c. Explain how results from the 100% Remote Grid comparison inform Screen 2 screening or project progression and later Screen 3 mitigation selection, given that partial Remote Grid opportunities may be identified through separate project-level reviews. | The 100% Remote Grid design variation provides a standardized, planning-level comparison of a distinct permanent mitigation strategy using common assumptions across Eligible Circuit Segments (Table 3-9). As with the other Screen 2 design variations, the 100% Remote Grid comparison is a preliminary comparison and does not establish that Remote Grid is technically feasible or preferred for implementation across the entirety of a Circuit Segment. Project-specific Remote Grid configuration and feasibility are evaluated at Screen 3 as more detailed scoping and technical information become available. a. Screen 2 identified 36 Eligible Circuit Segments for which the modeled benefit-cost ratio (BCR) for 100% Remote Grid was higher than the modeled BCRs for both 100% undergrounding and Screen 2 Alternative Mitigation 1 (Overhead Hardening). These 36 Eligible Circuit Segments and their respective Screen 2 BCRs for 100% Undergrounding, Alternative Mitigation 1, and Alternative Mitigation 2 (100% Remote Grid) are provided in Attachment “EUP-PhI_DR_OEIS-003-Q003Atch01.xlsx.” The underlying Screen 2 BCRs for the three design variations (100% UG, Alt 1 and Alt 2) are also provided by Eligible Circuit Segment in Table C.11 (Attachment A-2) to the EUP. However, PG&E has not determined that these 36 Eligible Circuit Segments are reasonable candidates for further Remote Grid scoping. Screen 2 applies standardized assumptions and does not include the project-specific information necessary to make that determination. A higher modeled BCR for 100% Remote Grid is an analytical result from the Screen 2 comparison, not a determination of Remote Grid feasibility or suitability. i. The factors identified in the question, including circuit topology and configuration, customer count, Circuit Segment location, service continuity needs, and other technical or operational constraints, are evaluated through project-specific scoping and feasibility review at Screen 3 rather than as part of the standardized Screen 2 analysis. Accordingly, PG&E did not use those factors at Screen 2 to determine which of the 36 Circuit Segments are reasonable candidates for further Remote Grid scoping. ii. The 36 Eligible Circuit Segments meeting the BCR comparison described above, together with the requested BCRs for 100% Undergrounding, Alternative Mitigation 1, and Alternative Mitigation 2 (100% Remote Grid), are provided in Attachment “EUP-PhI_DR_OEIS_003-Q003Atch01.xlsx.” These BCRs are also provided by Eligible Circuit Segment in Table C.11 of Attachment A-2 of the EUP. PG&E does not have, from the Screen 2 analysis, the requested segment-specific explanations of potential suitability or significant known constraints because the project-specific information necessary to assess those considerations is developed and evaluated at Screen 3. These 36 Eligible Circuit Segments have not yet undergone the Screen 3 project-specific review described above; that review will occur as the applicable projects enter Screen 3 of the Project Acceptance Framework. b. Remote Grid feasibility is evaluated at Screen 3 rather than through a separate feasibility-screening step between Screens 2 and 3. As part of the Screen 3 Alternative Mitigation review, PG&E identifies potential Remote Grid locations and evaluates portions of a Circuit Segment that are end of line, relatively long, and EUP-PhI_DR_OEIS_003-Q003 Page 3 serve relatively few customers. PG&E then performs a desktop review of site-specific features that may make Remote Grid infeasible and develops an expected cost (pp. 140–141). Remote Grid feasibility considerations include customer willingness, site availability, land rights, environmental and permitting requirements, and engineering feasibility (Table 3-9, note (b)). The EUP does not establish numeric thresholds for these considerations; they are evaluated through the project-specific desktop review and scoping. c. The Screen 2 100% Remote Grid comparison provides a standardized, planning-level analytical result. It does not determine whether a Circuit Segment progresses, whether Remote Grid is feasible, or which mitigation ultimately will be selected. Consistent with the Screen 2 framework described in PG&E’s responses to Questions 001 and 002, project-specific mitigation configurations and feasibility are evaluated at Screen 3 when more detailed topology, scoping, engineering, cost, and site information is available. At Screen 3, PG&E may evaluate Remote Grid as part of the Screen 3 Alternative Mitigation, Additional Comparison 2, or Additional Comparison 3, where feasible. These Screen 3 reviews may identify partial Remote Grid opportunities, including Remote Grid applied to a smaller portion of a project together with undergrounding, overhead hardening, or other feasible project-specific configurations. Thus, a favorable Screen 2 100% Remote Grid BCR provides comparative planning-level information, but project-specific Remote Grid feasibility, configuration, and mitigation selection are evaluated at Screen 3. | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | Feasibility and Decision Value of 100% Remote Grid | 100% Remote Grid; Screen 2 BCRs
54 | OEIS | 003 | OEIS_003 | 004 | OEIS_003_Q004 | No | Q04. Remote Grid Screening in Screen 3 and Additional Comparison 3 1. Does the Remote Grid feasibility review used for Screen 3 Alternative Mitigation (S3 AM) follow the same criteria/process as Additional Comparison 3 (AC3)? If not, describe each process and provide the Remote Grid feasibility result for each Portfolio 0 project. a. Describe the screening sequence, technical feasibility criteria, and decision points for Remote Grid under each process. State whether the same criteria are used; if not, explain the differences. b. Explain how a Remote Grid option could be included in S3 AM rather than being considered only within AC2 or AC3.c. For all Confirmed Projects for which Remote Grid was considered for S3 AM, please provide the BCR for the model design variation that was compared to the chosen S3 AM. 2. Choose one of the confirmed projects for which OH + Remote Grid was considered for use as S3 AM. Use this project as an example and explain how and where the Remote Grid location was identified, how the total BCR was calculated, and the likely reasons the BCR was less then 100% OH for that project. | The EUP describes the Remote Grid and LEIP feasibility criteria in the context of AC 3 (pp. 140–141): PG&E identifies portions of a Circuit Segment that are end of line, relatively long, and serve few customers, then completes a desktop screen for site-specific features that would make Remote Grid infeasible. Feasibility also depends on customer willingness, site availability, land rights, environmental, permitting and engineering factors (Table 3-9, note (b)). The EUP does not set separate feasibility criteria for S3 AM. S3 AM and AC 3 differ in when Remote Grid is considered and why, not in the feasibility criteria. a. Sequence and decision points: • S3 AM: During the Screen 3 Alternative Mitigation Review, PG&E determines the non-undergrounding alternative with the best BCR. Where a feasible Remote Grid opportunity is identified, it is included in S3 AM if it improves upon or exceeds the BCR of covered conductor (Table 3-9, note (b)). The S3 AM BCR is then compared to the 100% UG and AC 2 BCRs using the 70 percent rule (pp. 131–139). • AC 2: If the AC 2 scope equals 100% UG or S3 AM, the most viable Remote Grid location is added (Figure 3-6). • AC 3: After the preferred alternative is selected, every Screen 3 segment is reviewed for Remote Grid and LEIP candidates and screened for infeasibility, and an expected cost is developed. AC 3 becomes the Project as Scoped only if its BCR exceeds the Project as Scoped BCR. If Remote Grid is found infeasible, the selected scope is kept (Figure 3-8; pp. 140–141). b. Where feasible, S3 AM may consist entirely of covered conductor, entirely of Remote Grid, or a combination of the two (Table 3-9). A Remote Grid option may be included in S3 AM when it is identified during the Screen 3 Alternative Mitigation Review and scoping process, costed through the Feedback Loop (p. 133), and determined to have a BCR that improves upon or exceeds the covered conductor BCR. Otherwise, Remote Grid is considered through AC 2 or AC 3. c. Below is a table of confirmed projects where OH + RG was considered for S3 AM. project_id CPZ OH + RG1 BCR OH + RG2 BCR OH BCR RG site Reason why OH + RG < OH BCR Proj00001 PUEBLO 21031970 2.1327 N/A 3.1209 RG site considered at end of line (EOL), initiallyto reduce UG scope by0.38 miles. This mitigation type failed. Then re-evaluated RG site for S3 AM. Only addresses 0.23 mile of OH bare conductor. Capital cost for the RG site is $1.65M. EUP-PhI_DR_OEIS_003-Q004 Page 3 Proj00003 FORESTHILL 1101CB 2.5604 2.8375 3.9227 Two RG sites are considered in this zone, both at EOL. RG1 site considered at EOL, initiallyto reduce UG scope by 0.36 miles. This mitigation type failed. RG2 site considered at EOL, initiallyto reduce UG scope by 0.37 miles. This mitigation type failed. Both RG sites re-evaluated RG site for S3 AM. RG1 addresses 0.14 mile of OH bare conductor. Capital cost for RG1 site is $1.77M. RG2 addresses 0.43 mile of OH bare conductor. Capital cost for RG2 site is $1.85M. Proj00004 DUNBAR 1103799422 0.3651 N/A 4.5058 RG site considered at EOL as part of S3 AM. Only addresses 0.05 mile of OH bare conductor. Capital cost for the RG site is $2.21M. Proj00005 FORESTHILL 11011820 0.3947 N/A 0.5417 RG site considered at EOL, initiallyto reduce UG scope by 0.22 miles. This mitigation type failed. Then re-evaluated RG site for S3 AM. Only addresses 0.13 mile of OH bare conductor. Capital cost for the RG site is $1.71M. Proj00008 GEYSERVILLE 1102904170 2.2303 N/A 2.5764 RG site considered at EOL, initiallyto reduce UG scope by 1.627 miles. This mitigation type failed. Then re-evaluated RG site for S3 AM. Only addresses 0.71 mile of OH bare conductor. Capital cost for the RG site is $3.25M. Proj00011 EL DORADO PH 2101668674 3.5476 N/A 5.6122 RG site considered at EOL, initiallyto reduce UG scope by 0.11 miles. This mitigation type failed. Then re-evaluated RG site for S3 AM. Only addresses 0.11 mile of OH bare conductor. Capital cost for the RG site is $1.98M. Proj00020 CAMP EVERS 210510294 0.736 N/A 1.1098 RG site considered at EOL, initiallyto reduce UG scope by 0.18 miles. This mitigation type failed. Then re-evaluated RG site for S3 AM. Only addresses 0.05 mile of OH bare conductor. Capital cost for the RG site is $1.04M. Proj00026 CAMP EVERS 2105534190 0.5659 N/A 0.7902 RG site considered at EOL, initiallyto reduce UG scope by 0.11 miles. This mitigation type failed. Only addresses 0.11 mile of OH bare conductor. Capital Then re-evaluated RG site for S3 AM. cost for the RG site is $1.05M | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | Remote Grid Screening in Screen 3 and Additional Comparison 3 | Screen 3 Alternative Mitigation; Additional Comparison 3
55 | OEIS | 003 | OEIS_003 | 005 | OEIS_003_Q005 | No | Q05. Basis and Application of the 70% BCR Threshold 1. Provide the basis for applying the 70% BCR comparison threshold described in EUP Chapter 3: a. Provide the quantitative analysis, empirical evidence, or other documentation supporting the use of a uniform 30% estimate-uncertainty allowance across projects and mitigation types. Distinguish uncertainty in project costs from uncertainty in modeled benefits and BCRs. b. Explain how the 30% allowance is translated into the 70% comparative BCR rule, including whether it represents a statistical confidence interval, estimating range, or policy-based screening tolerance. c. Identify each Confirmed Project where the BCR of 100% undergrounding or AC2 was between 70% and 100% of the S3 AM BCR. For each, provide the comparison BCRs, mitigation selected, and rationale for selection. d. Explain whether PG&E performed sensitivity analyses using different uncertainty thresholds or project-specific uncertainty ranges. Provide any existing results and describe how the project-selection outcome would differ without the 70% rule. | a. As described in PG&E's EUP (Volume 1, Chapter 3, pp. 136–137), the 30 percent estimate uncertainty range is based on: • Industry-standard estimating practice (AACE cost estimate classifications), which recognizes that cost estimates developed during project scoping are not yet fully mature; • Energy Safety's recommendation in its Decision on PG&E's 2026–2028 Base WMP (February 5, 2026, pp. 19–20) to reduce PG&E's prior 50 percent estimate uncertainty range to 30 percent, reflecting improvements in data quality and modeling while still accounting for residual uncertainty in the decision-making process; and • Inherent uncertainty in modeled risk point estimates, driven by compounding assumptions, variability in inputs, and structural limitations of quantitative risk models. The first basis relates to uncertainty in project cost estimates, which affects the denominator of the BCR. Modeled risk reduction benefits, which affect the numerator, are also subject to uncertainty. PG&E did not develop a separate quantitative analysis for the EUP filing to derive the 30 percent value or quantify separate uncertainty allowances for cost and modeled benefits. Consistent with Energy Safety's WMP Decision, PG&E uses the 30 percent estimate uncertainty range in applying the comparative BCR rule described in Chapter 3. However, PG&E did provide a quantitative estimate of the uncertainty factor relevant to risk reduction benefits, in the Joint Reply Comments for Application A.26-02-005, filed July 7, 2026, filed jointly with SDG&E and Southern California Edison. That analysis, which begins on page 44 of the document, illustrates how the aggregation of several uncertainty components in modeling and effectiveness values results in a downside uncertainty between 26.9%-39.4% for mitigations that include covered conductor. This analysis supports 30 percent as a reasonable approximation of uncertainty in modeled mitigation benefits. b. The 70 percent figure is 100 percent minus the 30 percent estimate uncertainty range and is not a separate or additional threshold (Chapter 3, p. 136). It is not a statistical confidence interval or a policy-based screening tolerance and does not mean that every cost estimate, risk estimate, or resulting BCR carries a uniform 30 percent statistical uncertainty. c. Confirmed projects 8, 10, 13, 15, 16, 17, and 19 all were selected with the use of the 70% comparative BCR rule. Each were selected following the decision tree outlined in Figures 3-7 and 3-8. See “EUP-PhI_DR_OEIS_003-Q005Atch01.xlsx” for details. d. PG&E did not perform sensitivity analyses using alternative uncertainty thresholds or project-specific uncertainty ranges for the EUP filing. Without the 70 percent rule, the alternative with the highest modeled BCR would have been selected for each project identified in response to part (c), subject to the Additional Comparison 3 review described in Chapter 3, pp. 140–141 | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | Basis and Application of the 70% BCR Threshold | 70% Comparative BCR Rule; Estimate Uncertainty
56 | OEIS | 003 | OEIS_003 | 006 | OEIS_003_Q006 | No | Q06. Project-Level Standards for Confirmed Projects 1. In Table 12, 12 of the 28 Confirmed Projects do not meet the Project-Level Standard for Project as Scoped. For each Confirmed Project that does not meet its applicable Project-Level Standard: a. Identify the Project ID, applicable eligibility threshold and Project-Level Standard, the modeled post-mitigation values, and the extent to which the standard is not met. b. Provide the specific project-level justification for including the project as a Confirmed Project.c. Identify the location in the narrative or other submitted material where this justification is provided or indicate that it has not been documented on a project-specific basis. | Under the EUP Guidelines, not every Undergrounding Project in the Portfolio needs to meet the Project-Level Standards. Any Confirmed Project that does not must be further justified in the narrative submission in Table C.12 (EUP Guidelines § 2.7.9.2; EUP Vol. 1, Ch. 7, p. 358). PG&E provides that justification in the "additional justification" field of Table C.12. In developing Portfolio 0, PG&E selected projects consistent with the applicable Portfolio 0 requirements established in Section 2.4.5.2 of the EUP Guidelines and, where applicable, the EUP Project Acceptance Framework. The EUP Guidelines include specific Portfolio 0 requirements that may result in the inclusion of projects that do not otherwise advance through the Project Acceptance Framework. PG&E also considered the applicable Portfolio 0 requirements, Screen 2 analytical results, available project-specific information, project development maturity and readiness, and the expected ability of projects to continue advancing through the Project Acceptance Framework. a. Please refer to the attachment “EUP-PhI_DR_OEIS_003-Q006Atch01.xlsx” sheet "OEIS003-Q006a". Column A shows the Project IDs and Column I identifies the applicable eligibility threshold. The Project-Level Standards are provided in Columns AF, AL, and AR. Columns AH, AN, and AT indicate whether High Risk, Ignition Tail Risk, and High Frequency Outage Program Project-Level Standards, respectively, are met based on the corresponding project level post-mitigation risk, ignition, and frequency reductions. The extent to which an applicable standard is not met can be determined by comparing the applicable Project-Level Standard with the corresponding post-mitigation reduction. For example, column AF provides the High-Risk Project-Level Standard, and Column AG provides the modeled risk reduction per mile. Column G shows whether the project meets any applicable Project-Level Standard. b. The inclusion of each of the 12 Confirmed Projects identified in part (a) is supported by its selection consistent with the applicable Portfolio 0 requirements and, where applicable, the EUP Project Acceptance Framework. The applicable selection considerations included the Portfolio 0 requirements, Screen 2 analytical results, available project-specific information, project development maturity and readiness, and the expected ability of projects to continue advancing through the Project Acceptance Framework. For each of the 12 Confirmed Projects, Table C.12 provides a specific justification in the "Additional Justification" field. Table C.12 identifies Benefit Cost Ratio constraints as the reason the applicable Project-Level Standard was not met. Additional project-specific information is provided in Attachment “EUP-PhI_DR_OEIS_003-Q006Atch01.xlsx,” including the extent of undergrounding and, where applicable, Portfolio 0 requirements or other project-specific considerations. For the 12 projects that are eligible but do not meet the applicable Project-Level Standard, Column H provides the fraction of overhead miles removed through undergrounding, based on the miles undergrounded in Column BE relative to the eligible miles for undergrounding in Column J. Across these projects, the fraction of eligible miles undergrounded is less than 100 percent. Projects with less than 100 percent of eligible miles undergrounded achieve correspondingly lower risk-reduction benefits, which may limit their ability to meet the applicable Project-Level Standard. Additionally: • Proj00013 does not meet the applicable Project-Level Standard because it does not include PSPS benefits after scoping. • Proj00008 and Proj00021 are included to satisfy the Portfolio 0 requirements in the EUP Guidelines, section 2.4.5.2, to include two projects based on Ignition Tail Risk Threshold eligibility. • Proj00028 and Proj00027 are included to satisfy the Portfolio 0 requirement to include two projects based on High Frequency Outage Program Threshold eligibility. c. For each of the 12 Confirmed Projects identified in part (a), the project-specific justification is provided in the “Additional Justification” field of Table C.12. Additional project-specific information supporting the justifications is provided in PG&E’s response to part (b) above and in Attachment “EUP-PhI_DR_OEIS_003-Q006Atch01.xlsx,” sheet “OEIS003-Q006a.” | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | Project-Level Standards for Confirmed Projects | Project-Level Standards; Portfolio 0 Justification
57 | OEIS | 003 | OEIS_003 | 007 | OEIS_003_Q007 | No | Q07. Selection of Confirmed Projects and the 28 Portfolio 0 Projects 1. Describe and document how PG&E selected the initial 28 Confirmed Projects from the broader list of Eligible Circuit Segments: a. Identify the candidate population at each decision point, including the screening, ranking, feasibility, scheduling, and other criteria used to select the 28 projects. b. For each Confirmed Project, identify whether it was in an existing GRC/WMP undergrounding workplan, had completed any scoping, or otherwise entered project development before application of the proposed EUP Project Acceptance Framework. Provide the relevant dates or stage of development. c. Identify any higher-ranked eligible Circuit Segments or Undergrounding Projects, under the ranking measures used by PG&E, that were not included in Portfolio 0 and describe the principal reasons for exclusion or deferral. d. Explain how Portfolio 0 demonstrates the proposed Project Acceptance Framework, distinguishing the selection of previously scoped projects from projects selected entirely through the proposed EUP process. 2. Describe the process PG&E will use to advance Eligible Circuit Segments through the Project Acceptance Framework to become Confirmed projects during the remainder of the EUP. Include the KDMMs and other criteria that will be used to prioritize which Circuit Segments advance first. | 1. PG&E began with the population of Circuit Segments that satisfied Screen 1 eligibility requirements. PG&E then reviewed that population to identify candidate projects capable of collectively satisfying the Portfolio 0 requirements established in the EUP Guidelines. PG&E also considered Screen 2 analytical results and available project-specific information as part of developing Portfolio 0. Screen 2 provides a standardized, planning-level comparison and does not itself determine which Eligible Circuit Segments advance or the project-specific mitigation ultimately selected. The objective was to develop an initial portfolio that both satisfied the required representation of project types and risk thresholds and consisted of projects reasonably expected to progress through the Project Acceptance Framework. a. The candidate population was progressively narrowed through the Project Acceptance Framework. Screen 1 - Eligibility Screening Candidate Population: 2,946, All evaluated Circuit Segments. Criteria Applied: Eligibility requirements described in the EUP; identification of Circuit Segments that satisfied the applicable wildfire risk and program eligibility criteria. Output: Eligible Circuit Segments. Screen 2 - Mitigation Comparison and Economic Evaluation Candidate Population: 1,054. An additional analysis was performed to support the EUP Phase 1 Plan to identify projects that would satisfy the 25-project requirement and whose undergrounding results were expected to support continued advancement through the Project Acceptance Framework under the range of benefit-cost methodologies under consideration in A.26-02-005 at the time of filing. Eligible Circuit Segments from Screen 1. Criteria Applied: Comparison of undergrounding to alternative mitigation options; benefit-cost analysis; evaluation of project-level performance metrics and risk reduction potential. Output: Standardized planning-level analytical results comparing undergrounding and the Screen 2 alternative mitigation design variations, including their modeled BCRs. Screen 3 - Feasibility and Project Development Candidate Population: 36. Eligible Circuit Segments entering project-specific scoping and feasibility review. Criteria Applied: Engineering feasibility; constructability considerations; permitting requirements; environmental and land rights considerations; scope development activities; project scheduling and execution readiness. Output: Projects that could reasonably advance toward confirmation. Portfolio 0 Selection Candidate Population: 28. Screen 3 projects and projects already progressing through planning or scoping activities during the transition period. Criteria Applied: Satisfaction of EUP Guidelines Portfolio 0 requirements; representation of required project types and thresholds; Screen 2 analytical results; project development maturity and readiness; expected ability to continue advancing through the Project Acceptance Framework. Output: The initial 28 Confirmed Projects comprising Portfolio 0. b. Of the initial 28 Confirmed Projects, ten (10) projects were included in PG&E's forecasted undergrounding workplans supporting the 2026-2028 WMP and 2027-2030 GRC. While these projects had been identified for planning purposes, they had not been previously scoped or evaluated using the WMP, nor GRC project Acceptance Frameworks. All ten projects, along with 17 Confirmed Projects, were subsequently evaluated and scoped under the EUP Project Acceptance Framework and advanced through the EUP screening process before being designated as Confirmed Projects. Please see the Q7.1.b tab on the "EUP-PhI_DR_OEIS_003-Q007Atch01.xlsx" and reference Column E "In GRC/WMP UG Workplan?". Please see Exhibit (PG&E-16), Chapter 7, Attachment B: PG&E's 2023-2027 System Hardening Workplan for the workplan PG&E submitted as part of the 2027 GRC. c. PG&E considered the applicable Portfolio 0 requirements, Screen 2 analytical results, available project-specific information, project development maturity and readiness, and the expected ability of projects to continue advancing through the Project Acceptance Framework where undergrounding remained the preferred mitigation alternative. In developing Portfolio 0, PG&E selected projects with sufficiently favorable undergrounding BCR results to provide greater confidence that they could continue to advance under the benefit-cost methodologies under consideration in A.26-02-005 at the time of filing. Accordingly, some eligible Circuit Segments may not have been included in Portfolio 0 despite having a higher risk rank because the available information, project development status, or other Project Acceptance Framework considerations did not support advancement at that time. This approach helps limit potential project scoping rework and supports efficient progression through the Project Acceptance Framework. Please see "EUP-PhI_DR_OEIS_003-Q007Atch01.xlsx," which includes the Circuit Segments that were not included in Portfolio 0 despite having a higher risk rank than segments that were included. In the attachment, Column B provides the risk rank and Column K indicates whether the segment was included in Portfolio 0. d. Portfolio 0 reflects application of the EUP analytical framework during a transition period and includes both projects that had already entered planning, scoping, or development under existing undergrounding programs and projects evaluated through the EUP process. Portfolio 0 includes projects that entered the framework through two primary pathways: Previously Scoped or Planned Projects: Some projects had already entered planning, scoping, or development activities under existing undergrounding programs before implementation of the proposed EUP framework. For these projects, the EUP analyses were applied to evaluate eligibility, mitigation comparisons, project-level performance metrics, and consistency with Portfolio 0 requirements. Projects Evaluated Through the EUP Process: Other projects were evaluated using the framework beginning with the eligible Circuit Segment population and advancing through the applicable screening and evaluation steps. These projects demonstrate how the framework can be applied prospectively to identify and prioritize candidate undergrounding projects. As a result, Portfolio 0 demonstrates application of the EUP analytical framework and portfolio development process during the transition period while reflecting a mix of project maturity levels that existed when the framework was introduced. 2. During the remainder of the EUP, PG&E will advance Eligible Circuit Segments through the Project Acceptance Framework using the sequential screening, evaluation, and prioritization process described in Chapter 3. The process consists of: Step 1 - Screen 1 Eligibility Evaluation: Circuit Segments will be evaluated against the Screen 1 eligibility requirements to determine whether further consideration under the EUP is warranted. Step 2 - Screen 2 Mitigation Comparison and Project Evaluation: Eligible Circuit Segments will undergo the standardized comparison of undergrounding and alternative mitigation design variations, including calculation of modeled BCRs. These results provide planning-level comparative information and do not themselves determine the project-level specific mitigation ultimately selected. PG&E will compare undergrounding against alternative wildfire mitigation strategies to provide a standardized, planning-level comparison of modeled value and risk reduction. Step 3 - Screen 3 Feasibility and Project Development: Eligible Circuit Segments entering project-specific scoping and feasibility review will undergo additional project development activities, including engineering assessment, scope development, feasibility evaluation, constructability review, permitting review, environmental review, and land rights assessment. Step 4 - Screen 4 Prioritization: Projects that successfully complete project development activities will be prioritized for advancement based on the framework's project and portfolio evaluation criteria. These include: Overall Utility Risk reduction, which is an aggregation of project-level KDMMs, as described in PG&E's EUP Chapter 7, Section E, as the top-level metrics used to evaluate the efficacy of an Undergrounding Project; project feasibility and constructability; schedule readiness and ability to advance; Fire Rebuild Program considerations, where applicable; bundling opportunities and portfolio optimization considerations; and other portfolio-level considerations identified in the EUP. Projects that successfully advance through these evaluations and satisfy applicable portfolio requirements will be designated as Confirmed Projects and incorporated into the EUP. | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | Selection of Confirmed Projects and Portfolio 0 | Portfolio 0; Project Acceptance Framework
58 | OEIS | 003 | OEIS_003 | 008 | OEIS_003_Q008 | No | Q08. New Mitigation Technologies 1. In Chapter 3, page 116 of PG&E’s EUP, PG&E states that it considers Minimum Cover Distribution Systems (MCDS) and Ground Level Distribution Systems (GLDS) to be improvements to existing undergrounding methods rather than separate mitigation alternatives. a. Explain the basis for this classification, particularly given the differences in installation methods and potential differences in risk characteristics and cost compared to conventional undergrounding. b. Describe how PG&E envisions incorporating MCDS and GLDS into the EUP if these technologies become suitable for deployment at a greater scale.i. Would they be used in place of conventional undergrounding on certain projects and evaluated as undergrounding in Screens 2 and 3? ii. How would PG&E assess and account for any differences in the technologies, including in wildfire risk reduction, reliability, and costs? c. Provide a brief technical description of MCDS and GLDS, including their intended applications, current testing and pilot status, and what additional testing or validation is needed before deployment at a greater scale. | a. PG&E interprets “new mitigation technologies” to mean new mitigation alternatives considered in Screens 2 and 3. The EUP identifies MCDS and GLDS, along with Fluid-Free Steerable Boring and Native Slurry Backfill, as technologies aimed at increasing the cost efficiency of existing mitigations rather than as new mitigation alternatives. MCDS and GLDS are alternative construction methods being assessed as potentially faster and less costly approaches to placing electric distribution facilities deeper underground in specific locations. These technologies remain in development and pilot testing and are not currently relied upon as standalone mitigation alternatives for long-term EUP planning. Rather, they are being evaluated as potential improvements to how undergrounding is constructed and deployed. Accordingly, PG&E classified these technologies as improvements to existing mitigations rather than separate mitigation alternatives. b. i. If validated and determined suitable for broader deployment, MCDS or GLDS could be used in place of conventional underground construction on projects or portions of projects where technically and economically appropriate. Consistent with the EUP’s treatment of MCDS and GLDS as technologies aimed at increasing the cost efficiency of undergrounding, the applicable construction method, scope, and costs would be reflected in the project evaluation. ii. PG&E would evaluate MCDS and GLDS based on available engineering, safety, reliability, wildfire risk, cost, permitting, and operational information and incorporate appropriate technology-specific assumptions into project design and applicable EUP analyses. Broader deployment may also require further engagement with other regulators, including the CPUC, before deploying these technologies at scale c. MCDS and GLDS are alternative construction methods that PG&E is assessing as potentially faster and less costly approaches to undergrounding electric lines in specific locations, including difficult terrain and environmentally/culturally sensitive areas. MCDS installs the system below grade using minimum cover, while GLDS installs the system at ground level. PG&E has piloted MCDS & GLDS, including an installation on the Antler 1101 circuit that was energized in May 2026 and the other on the Woodside 1101 circuit energized in December 2023. Both are serving customer load. PG&E continues to assess these construction methods for broader applicability, including necessary engineering, safety, reliability, cost, permitting, and operational considerations | David Rey | 2026-10-23 | 2026-10-28 | 2026-10-28 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-003.zip | 2.4 | Project Acceptance Framework | New Mitigation Technologies | MCDS and GLDS; Construction Methods
59 | MGRA | 002 | MGRA_002 | 001 | MGRA_002_Q001 | No | Please provide an Excel spreadsheet containing an entry for every active PG&E weather station. For each weather station provide the following fields: a. Weather Station ID b. Mesonet ID c. Date in service d. Link to Mesonet weather station data e. HFTD Class f. Maximum wind gust speed measured at station g. Number of wind gust measurements over the life of the weather station: a) > 50 mph b) > 55 mph c) > 60 mph d) > 65 mph e) > 70 mph | As stated in PG&E’s October 13, 2026 extension request to MGRA, PG&E is unable to provide the requested weather station in the format requested by the October 15, 2026 due date. The subject matter experts necessary to compile, validate and produce the requested information are currently engaged in a Public Safety Power Shutoff (PSPS) event and are also compiling information for a previous PSPS event for the 10-day report. All data collected by PG&E's weather station network is available to the public through multiple channels provided below. The entire historical data can be acquired from Synoptic by any entity to perform analyses to support regulatory filings. Information relevant to this request is available through the following public resources: • PG&E Weather & Fire Detection: Provides links to the external interactive weather maps identified below and describes the weather information available through those tools, including humidity, precipitation, temperature, wind speeds and gusts, and red flag warnings. o Subpart (b), the PG&E mesonet ID is 229 and a summary of all stations with their first report date (in service) and end date can be found in Synoptic’s network viewer. See column “Station ID” for the station ID (subpart a). o Subpart (c), see Synoptic’s network viewer; See column “First Date” for date in service. o Subpart (d), Link to Mesonet weather station data: Follow the link to the Synoptic Weather Viewer and select a station to access its data. o Subpart (f), Maximum wind gust speed: Follow the linked weather tools and select a station to view available wind-gust observations. o Subpart (g), Wind-gust threshold counts: Historical wind-gust observations may be accessed through the linked tools, but the number of measurements above 50, 55, 60, 65, and 70 mph is not provided as a pre-calculated value.  As the PG&E weather station is available through Synoptic, the historical data can be downloaded and processed by any entity. • Once the PG&E weather stations are located on the Synoptic Weather Viewer, the public may cross reference the weather station locations with the CPUC’s High Fire-Threat District map (subpart e) at this website: Fire-Threat Maps and Fire-Safety Rulemaking. Consistent with PG&E’s October 13, 2026 extension request, PG&E will supplement this response with the requested spreadsheet by October 30, 2026, time permitting as we are in the peak of PSPS season. | Joseph Mitchell | 2026-10-12 | 2026-10-15 | 2026-10-15 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | Wind | Weather Stations; Wind Gust Data
60 | OEIS | 001 | OEIS_001 | 001 | OEIS_001_Q001Supp01 | Supp01 | Q01. KDMM Calculations a. Climate Escalation a. Provide Baseline Wildfire Risk, Baseline EPSS Risk, and Baseline PSPS Risk without climate factors for each Circuit Segment from 2025 to 2092. b. Provide the Wildfire Risk, PSPS Risk and EPSS Risk climate factors for each Circuit Segment from 2025 to 2092. c. Provide the baseline KDMMs with climate factors applied for each Circuit Segment from 2025 to 2092. d. Are there different values for each HFTD tier/county/Circuit Segment? e. Does climate impact to Fire Weather Index (FWI) affect both EPSS and PSPS or just PSPS? Core Capability 4 states just PSPS, however WP006 states PSPS and EPSS. f. Provide a sample calculation to demonstrate how Climate Factors are calculated with Fire Weather Index (FWI) and Heat Day multipliers. g. Which KDMMs is climate escalation applied to (Likelihood/Consequence/Risk)? b. Inflation Escalation a. Which KDMMs is inflation escalation applied to (Likelihood/Consequence/Risk)? c. Plan Tracking Objectives a. Do the risk reduction targets represent instantaneous risk reduction for all projects completed in the given year including inflation and climate escalation up to that year? If not, what do they represent? b. Are values in the Plan Tracking Objectives presented in nominal values for the given year or in year 2028 present value? d. Target/Timeline Table a. Footnote (d) indicates that risk values represent unmitigated and residual risk for all projects completed in a given year, however the risk columns are labeled as Change In Instant/Cumulative Risk. Are the Change in Risk columns reporting pre/post mitigation risk or risk reduction for all projects in a given year? b. Do the change in Instantaneous Wildfire and Outage Program Risk columns represent risk reduction for all projects completed in a given year, including climate and inflation escalation up to year 10? If not, what do they represent? c. Are the change in Wildfire and Outage Program Risk columns presented in nominal values or in year 2028 present value? e. Risk Model Impact Factor a. Do KDMM calculations in Tables 5, 8, 11, 12, 13 or 15 and the Model Risk Landscape JSON incorporate the Risk Model Impact Factor? b. How is the Risk Model Impact Factor applied? i. Is it applied to baseline KDMMs prior to calculations or to final values? ii. Provide an explanation and examples to demonstrate at what stage the Risk Model Impact Factor adjustment is applied to the following calculations if applicable: PMO, Plan Tracking Objectives, Target Timeline Table, etc. | Climate Escalation f. Sample calculation for “Climate_Risk_Score_Multiplier” for Wildfire Risk for circuit segment ALTO 1124432 for 2027: The Climate Risk Score Multiplier scales baseline 2025 wildfire risk for a distribution circuit segment to reflect projected climate change. It is the product of two multipliers: • FWI_Multiplier accounts for the projected change in the annual number of days with a Fire Weather Index (FWI) above the historical 95th percentile. It is applied only to the portion of distribution wildfire risk that occurs on Red Flag Warning (RFW) days. • Heat_Day_Multiplier accounts for the projected change in the frequency of continued heat events, which increase equipment failure rates. It is applied only to the portion of the circuit segment's wildfire risk that comes from equipment-related causes. Formula Climate_Risk_Score_Multiplier (Base year 2025) = FWI_Multiplier × Heat_Day_Multiplier = (RFW Multiplier × % Risk in RFW + 1 − % Risk in RFW) × (Heat Multiplier × % Risk from Equipment + 1 − % Risk from Equipment) where: RFW Multiplier = ratio of days above the historical 95th-percentile FWI in the given year to 2025 (circuit segment level) % Risk in RFW = share of distribution wildfire risk occurring on RFW days (system-wide) Heat Multiplier = ratio of the frequency of continued heat events in the given year to 2025 (division level) % Risk from Equipment = share of the circuit segment's wildfire risk attributable to equipment-related causes Step 1: RFW Multiplier (2027) Days per year above the historical 95th-percentile FWI for ALTO 1124432 Year Days above historical 95th-percentile FWI 2004 (historical baseline, center of the 1995–2014 period) 19.8 2030 (projection) 23.0 2050 (projection) 20.2 2080 (projection) 23.6 Values for years without data are estimated by straight-line interpolation between the nearest available years. For 2025 and 2027 those are 2004 and 2030: • Change in days from 2004 to 2030 = 23.0 − 19.8 = 3.2 days • Years from 2004 to 2030 = 2030 − 2004 = 26 years FWI days (2025) = 19.8 + 3.2 × (2025 − 2004) / 26 = 19.8 + 3.2 × 21/26 = 22.384615 FWI days (2027) = 19.8 + 3.2 × (2027 − 2004) / 26 = 19.8 + 3.2 × 23/26 = 22.630769 RFW Multiplier (2027) = FWI days (2027)/ FWI days (2025) = 22.630769 / 22.384615 = 1.010997 Step 2: % Risk in RFW • Distribution wildfire risk on RFW days = 13,936.6178 • Total distribution wildfire risk = 16,535.6850 % Risk in RFW = 13,936.6178 / 16,535.6850 = 0.842821 (84.28%) FWI_Multiplier = (RFW Multiplier × % Risk in RFW + 1 − % Risk in RFW) = 1.010997 × 0.842821 + 1 − 0.842821 = 1.009268 Step 3: Heat Multiplier (2027) ALTO 1124432 is in the North Bay division. The Heat Multiplier is provided at the division level. Heat Multiplier (North Bay, 2027, relative to 2025) = 1.024047 Step 4: % Risk from Equipment Source: WDRM model, circuit segment level. The table below gives wildfire risk by driver for ALTO 1124432. Driver Wildfire risk Equipment-related capacitor_bank_equipment_cause 0.003645 Yes dpd_equipment_cause 0.002603 Yes fuse_equipment_cause 0.026557 Yes other_equipment_type 0.048546 Yes primary_conductor_line_slap_cause 0.016993 Yes primary_conductor_other_cause 0.042813 Yes primary_conductor_wire_down_cause 0.068880 Yes secondary_conductor 0.021563 Yes support_structure_electrical_cause 0.073128 Yes support_structure_equipment_cause 0.027033 Yes switch_equipment_cause 0.004463 Yes transformer_equipment_cause 0.059927 Yes transformer_equipment_leaking 0.000210 Yes voltage_regulator_equipment_cause 0.000000 Yes animal_bird 0.016637 No animal_other 0.004242 No animal_squirrel 0.025397 No third_party_balloon 0.003381 No third_party_other 0.030997 No third_party_vehicle 0.031164 No vegetation_branch 0.346376 No vegetation_other 0.209073 No vegetation_trunk 0.607067 No Equipment-related total* 0.396362 All drivers total* 1.670700 *Totals are computed from unrounded values % Risk from Equipment = 0.396362 / 1.670700 = 0.237244 (23.72%) Heat_Day_Multiplier = (Heat Multiplier × % Risk from Equipment + 1 − % Risk from Equipment) = 1.024047 × 0.237244 + 1 − 0.237244 = 1.005705 Step 5: Climate Risk Score Multiplier (2027) Climate_Risk_Score_Multiplier = FWI_Multiplier × Heat_Day_Multiplier = (RFW Multiplier × % Risk in RFW + 1 − % Risk in RFW) × (Heat Multiplier × % Risk from Equipment + 1 − % Risk from Equipment) = (1.010997 × 0.842821 + 1 − 0.842821) × (1.024047 × 0.237244 + 1 − 0.237244) = 1.009268 × 1.005705 = 1.015026 | Dmitriy Lysak, Richard Cao, Adam Berlinerman | 2026-10-07 | 2026-10-23 | 2026-10-22 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-oeis-data-request-001.zip | 2.7 | Risk Modeling | KDMM Calculations | Climate Escalation; Climate Risk Multiplier
61 | MGRA | 002 | MGRA_002 | 006 | MGRA_002_Q006 | No | Repeat the analysis performed in GRC-2027-PhI_DR_MGRA_010-Q001 and GRC-2027-PhI_DR_MGRA_010-Q002 using updated wire-down data showing how many wires-down resulted in an energized wire down while DCD is enabled. | As described in Section 8.7.1.1, Protective Equipment and Device Settings, of PG&E's 2026–2028 Wildfire Mitigation Plan (WMP), the GM-06 Downed Conductor Detection (DCD) commitment established in the 2023–2025 WMP concluded in 2025. DCD remains part of PG&E's regular operational activities and is enabled in accordance with the Enhanced Powerline Safety Settings (EPSS) enablement criteria shown in Figure PG&E-8.7.1.1-1 of the 2026–2028 WMP. PG&E is providing “EUP-PhI_DR_MGRA_002-Q006Atch01.xlsx”, which identifies wire-down events from 2023 through 2025 in which a DCD target tripped. | Joseph Mitchell | 2026-10-12 | 2026-10-23 | 2026-10-23 |  | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | Mitigation Effectiveness Analysis | Downed Conductor Detection; Wire-Down Events
62 | MGRA | 002 | MGRA_002 | 001 | MGRA_002_Q001Supp01 | Supp01 | Please provide an Excel spreadsheet containing an entry for every active PG&E weather station. For each weather station provide the following fields: a. Weather Station ID b. Mesonet ID c. Date in service d. Link to Mesonet weather station data e. HFTD Class f. Maximum wind gust speed measured at station g. Number of wind gust measurements over the life of the weather station: a) > 50 mph b) > 55 mph c) > 60 mph d) > 65 mph e) > 70 mph | Please see “EUP-PhI_DR_MGRA_002-Q001Supp01Atch01.xlsx” for the requested information. Attachment includes the following fields: | Joseph Mitchell | 2026-10-12 | 2026-10-26 | 2026-10-26 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.7 | Risk Modeling | Wind | Weather Stations; Wind Gust Data
63 | MGRA | 002 | MGRA_002 | 002 | MGRA_002_Q002Supp01 | Supp01 | Please provide an Excel spreadsheet containing an entry for every circuit segment included in Plan EUP-01 (i.e. those listed in PGE_Initial_2026_09_30_T6_R0.csv). For each circuit segment provide: a. Circuit segment ID b. Nearest weather station distance < 3.0 miles? (Y/N) c. If nearest weather station distance < 3.0 miles, provide Weather Station ID. | Please see attachment “EUP-PhI_DR_MGRA_002-Q002Supp01Atch01.xlsx” for the requested information for all circuit segments included in PG&E’s PGE_Initial_2026_09_30_T6_R0.csv. The attachment includes the following fields: | Joseph Mitchell | 2026-10-12 | 2026-10-26 | 2026-10-26 | 1 | N | https://www.pge.com/assets/pge/docs/outages-and-safety/safety/eup-mgra-data-request-002.zip | 2.4 | Project Acceptance Framework | Wind | Circuit Segments; Weather Station Proximity