## Q1Q2
Mitigation Initiative | Avg CAP Cost Per Circuit Mile 2025 (Q01.a.1) | Avg CAP Cost Per Circuit Mile 2021 - Q2 2024 (Q01.a.2) | Projected Project Duration in Days Per Circuit Mile 2025 (Q02.a.i) 1 | Avg Project Duration in Days Per Circuit Mile 2021 - Q2 2024 (Q02.a.ii)
Branch Line Protection
Circuit Breaker Fast Curve Hardware
Covered Conductor | 892139 | 648553.9539 | 1218 | 520
Distribution open phase detection (DOPD)
Distribution pole replacements and reinforcements
Distribution traditional hardening
Early Fault Detection (EFD)
Fire Resistant Wrap Retrofits
High Impedance relays
Long Span Initiative
Microgrids, including Remote Grids
Rapid Earth Fault Current Limiter (REFCL) - GFN
Rapid Earth Fault Current Limiter (REFCL) - Grounding Conversions
Remote Automatic Recloser Setting Updates
Transmission Open Phase Detection (TOPD)
Transmission pole/tower replacements and reinforcements
Transmission traditional hardening
Tree Attachment Remediation
Undergrounding | 4555000 | 2253957.08 | 681 | 786
Vertical Switch Replacement
Vibration Damper Retrofits
1 Project duration is calculated in business days starting from from when a project is sent to SCE's planning team. Project duration includes time in which the project is awaiting next steps or necessary elements such as permitting, easements, etc. 2025 covered conductor projects are more complex and may require longer timeframes and more resources than projects in earlier years to complete. The 2025 data is a forecast based on SCE's best available information at this time.

## Q1.a.6
2023 Top 10 Projects with Highest Capital Cost Per Circuit Mile (Q01.a.6) | [6 empty] | 2023 Top 10 Projects with Lowest Capital Cost Per Circuit Mile (Q01.a.6)
Covered Conductor | [6 empty] | Covered Conductor
Rank | Project ID | Location | Project Length (Circuit Miles) | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1 | Rank | Project ID | Location | Project Length (Circuit Miles) | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1
1 | TD1662794 | Rurals | 0.087 | 1141852.2993 | 633 | 13124739.0724 | 1 | TD1871208 | San Joaquin Region | 0.545 | 14521.2896 | 477 | 26644.5681
2 | TD1732928 | North Valley | 0.06 | 618841.9437 | 622 | 10314032.3955 | 2 | TD1827254 | San Joaquin Region | 0.2 | 5889.04 | 699 | 29445.2
3 | TD1816593 | San Jacinto | 0.081 | 728368.1314 | 630 | 8992199.1527 | 3 | TD2040530 | North Coast | 0.86 | 28441.6304 | 67 | 33071.6633
4 | TD1943096 | San Joaquin Region | 0.009 | 68192.1326 | 483 | 7576903.6247 | 4 | TD1662576 | Desert | 0.44 | 39596.1121 | 888 | 89991.164
5 | TD1956592 | Desert | 0.01 | 74283.0582 | 390 | 7428305.8166 | 5 | TD1893634 | North Valley | 1.016 | 111228.3605 | 449 | 109476.7328
6 | TD1956567 | Desert | 0.041 | 250059.2127 | 350 | 6099005.1872 | 6 | TD1796674 | San Joaquin Region | 6.65 | 958670.4628 | 590 | 144160.9718
7 | TD1937840 | San Joaquin Region | 0.08 | 448590.4776 | 453 | 5607380.9702 | 7 | TD1796678 | San Joaquin Region | 6.12 | 966550.0378 | 709 | 157933.0127
8 | TD1797665 | Desert | 0.07 | 390416.046 | 531 | 5577372.0859 | 8 | TD2046534 | San Joaquin Region | 1.81 | 347698.9518 | 291 | 192098.8684
9 | TD1972187 | Desert | 0.06 | 305110.4573 | 318 | 5085174.2881 | 9 | TD1822413 | San Joaquin Region | 2.86 | 556523.7167 | 614 | 194588.7121
10 | TD1954659 | Desert | 0.01 | 48773.2981 | 401 | 4877329.8051 | 10 | TD2015660 | San Jacinto | 0.36 | 72429.721 | 232 | 201193.6694
Undergrounding | [6 empty] | Undergrounding
Rank | Project ID | Location | Project Length (Circuit Miles) | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1 | Rank | Project ID | Location | Project Length (Circuit Miles) | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1
1 | TD1750771 | Desert | 0.52 | 1163783 | 855 | 2238044.2308 | 1 | TD1800996 | Desert | 0.38 | 421990 | 763 | 1110500
2 | TD1801001 | Desert | 0.62 | 1060475 | 733 | 1710443.5484 | 2 | TD1799842 | Orange | 0.78 | 871458 | 764 | 1117253.8462
3 | TD1801006 | Desert | 0.58 | 889535 | 763 | 1533681.0345 | 3 | TD1800998 | Desert | 0.54 | 682400 | 763 | 1263703.7037
4 | TD1814780 | San Jacinto | 1.26 | 1922160 | 541 | 1525523.8095 | 4 | TD1825192 | San Jacinto | 1.77 | 2342656 | 530 | 1323534.4633
5 | TD1825192 | San Jacinto | 1.77 | 2342656 | 530 | 1323534.4633 | 5 | TD1814780 | San Jacinto | 1.26 | 1922160 | 541 | 1525523.8095
6 | TD1800998 | Desert | 0.54 | 682400 | 763 | 1263703.7037 | 6 | TD1801006 | Desert | 0.58 | 889535 | 763 | 1533681.0345
7 | TD1799842 | Orange | 0.78 | 871458 | 764 | 1117253.8462 | 7 | TD1801001 | Desert | 0.62 | 1060475 | 733 | 1710443.5484
8 | TD1800996 | Desert | 0.38 | 421990 | 763 | 1110500 | 8 | TD1750771 | Desert | 0.52 | 1163783 | 855 | 2238044.2308
9 | [6 empty] | 9
10 | [6 empty] | 10
1 Information provided in this column is extrapolated from individual work order information and is not representative of actual realized costs per circuit mile for the mitigation more broadly, as a given project may consist of multiple work orders. See response to Question 1.a.6 for a detailed explanation.

## Q2.a.v
2023 Top 10 Projects with Longest Duration Per Circuit Mile (Q02.a.v) | [6 empty] | 2023 Top 10 Projects with Shortest Duration Per Circuit Mile (Q02.a.v)
Covered Conductor | [6 empty] | Covered Conductor
Rank | Project ID | Location | Project Length (Circuit Miles) | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1 | Rank | Project ID | Location | Project Length (Circuit Miles)2 | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1
1 | TD1541218 | Rurals | 3.98 | 2513460.5868 | 1212 | 631522.7605 | 1 | TD2099949 | San Jacinto | 0.05 | 29416.09 | 72 | 588321.8
2 | TD1540530 | Desert | 0.39 | 384959.4611 | 1168 | 987075.5414 | 2 | TD2040530 | North Coast | 0.86 | 28441.6304 | 85 | 33071.6633
3 | TD1549073 | North Coast | 1.47 | 913807.5406 | 1140 | 621637.7827 | 3 | TD2126796 | North Valley | 0.08 | 192875.36 | 109 | 2410942
4 | TD1564145 | Desert | 0.09 | 57631.6559 | 1133 | 640351.7325 | 4 | TD2071083 | North Coast | 0.19 | 248099.43 | 116 | 1305786.4737
5 | TD1564143 | Desert | 0.07 | 120287.776 | 1129 | 1718396.8003 | 5 | TD2080858 | San Jacinto | 0.8 | 546467.04 | 121 | 683083.8
6 | TD1585003 | Rurals | 0.99 | 2925111.3595 | 1093 | 2954657.9389 | 6 | TD2113568 | San Jacinto | 0.19 | 253514.13 | 122 | 1334284.8947
7 | TD1596111 | Rurals | 1.1 | 1547096.6419 | 1092 | 1406451.4926 | 7 | TD2106961 | San Jacinto | 0.12 | 57529.82 | 122 | 479415.1667
8 | TD1592791 | Rurals | 0.93 | 1925650.6341 | 1079 | 2070592.0797 | 8 | TD2122662 | San Jacinto | 0.23 | 146405.7716 | 127 | 636546.833
9 | TD1593754 | Rurals | 1.14 | 1703647.3986 | 1077 | 1494427.5426 | 9 | TD2085900 | San Jacinto | 0.28 | 245565.99 | 132 | 877021.3929
10 | TD1607016 | Desert | 1.21 | 1781042.2044 | 1077 | 1471935.7061 | 10 | TD2118983 | San Jacinto | 0.25 | 56802.21 | 133 | 227208.84
Undergrounding | [6 empty] | Undergrounding
Rank | Project ID | Location | Project Length (Circuit Miles) | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1 | Rank | Project ID | Location | Project Length (Circuit Miles) | Project Capital Cost | Project Duration (days) | Capital Cost Per Circuit Mile1
1 | TD1750771 | Desert | 0.52 | 1163783 | 855 | 2238044.2308 | 1 | TD1825192 | San Jacinto | 1.77 | 2342656 | 530 | 1323534.4633
2 | TD1799842 | Orange | 0.78 | 871458 | 764 | 1117253.8462 | 2 | TD1814780 | San Jacinto | 1.26 | 1922160 | 541 | 1525523.8095
3 | TD1800996 | Desert | 0.38 | 421990 | 763 | 1110500 | 3 | TD1801001 | Desert | 0.62 | 1060475 | 733 | 1710443.5484
4 | TD1800998 | Desert | 0.54 | 682400 | 763 | 1263703.7037 | 4 | TD1801006 | Desert | 0.58 | 889535 | 763 | 1533681.0345
5 | TD1801006 | Desert | 0.58 | 889535 | 763 | 1533681.0345 | 5 | TD1800998 | Desert | 0.54 | 682400 | 763 | 1263703.7037
6 | TD1801001 | Desert | 0.62 | 1060475 | 733 | 1710443.5484 | 6 | TD1800996 | Desert | 0.38 | 421990 | 763 | 1110500
7 | TD1814780 | San Jacinto | 1.26 | 1922160 | 541 | 1525523.8095 | 7 | TD1799842 | Orange | 0.78 | 871458 | 764 | 1117253.8462
8 | TD1825192 | San Jacinto | 1.77 | 2342656 | 530 | 1323534.4633 | 8 | TD1750771 | Desert | 0.52 | 1163783 | 855 | 2238044.2308
9 | [6 empty] | 9
10 | [6 empty] | 10
1 Information provided in this column is extrapolated from individual work order information and is not representative of actual realized costs per circuit mile for the mitigation more broadly, as a given project may consist of multiple work orders. See response to Question 1.a.6 for a detailed explanation.

## Q3.a.i
Q3.a.i - List of Constraints Associated with Each Activity
Mitigation | Distribution (D) or Transmission (T) | Constraints [1]
Covered Conductor | D | Weather conditions
Undergrounding | D | Weather conditions
Branch Line Protection | D | See note 1
Distribution pole replacements and reinforcements | D | See note 1
Distribution traditional hardening [2] | D | N/A
Microgrids, including Remote Grids | D | Weather conditions and land availability
Remote Automatic Recloser Setting Updates | D | See note 1
Circuit Breaker Fast Curve Hardware | D | See note 1
Tree Attachment Remediation | D | Weather conditions
Long Span Initiative | D | See note 1
Vertical Switch Replacement | D | See note 1
Vibration Damper Retrofits | D | See note 1
Fire Resistant Wrap Retrofits | D | Inaccessbile location and poles with multiple risers [5]
REFCL - GFN [3] | D | Land availability, can only be deployed on circuits with phase-to-phase connected transformers or circuits where phase-to-neutral transformers can be economically converted, primary connected customer equipment upgrades may be required if underrated equipment is present, and requires communication network to function
REFCL - Grounding Conversions [3] | D | Land availability, can only be deployed on circuits with phase-to-phase connected transformers or circuits where phase-to-neutral transformers can be economically converted, primary connected customer equipment upgrades may be required if underrated equipment is present, requires communication network to function, and may have limitations based on system charging current values
High Impedance relays | D | No identified constraints
DOPD | D | Requires communication network to function
Early Fault Detection (EFD) | D, T | Requires communication network to function and cannot be constructed on certain pole configurations (i.e. poles with equipment)
Transmission Open Phase Detection (TOPD) | T | Only applicable on transmission lines with single conductor phase (no bundled conductors)
Transmission pole/tower replacements and reinforcements | T | Customer isssue (i.e. outage constraints), inaccessbile location, and system emergency (i.e. circuit load issue, outage constraints)
Transmission traditional hardening [4] | T | N/A
[1] SCE has responded to "constraints" primarily from the perspective of technical and engineering constraints. All mitigations may also face constraints from factors including material availability, lead times, permitting, easements, constructability, terrain, and cost.
[2] In Section 8.1.2.5 of SCE's 2023-2025 WMP, "traditional overhead hardening" is composed of Branch Line Protection and Long Span. Since both of those programs are already on this list, SCE is indicating "N/A" for these entries as they are redundant.
[3] SCE has provided two entries for REFCL as it has two distinct REFCL activities in its 2023-2025 WMP (SH-17 and SH-18).
[4] SCE does not have "Transmission Traditional Hardening" as an activity in its 2023-2025 WMP.
[5] Current constraints are based on pilot findings and they may be addressed by SCE in the future

## Q3.a.ii (D)
Mitigation Compatibility Table (Q03.a.ii) D | Covered Conductor | Undergrounding | Branch Line Protection | Dist. pole replacements and reinforcements | Dist. traditional hardening | Microgrids | Remote Grid [D] | Remote Automatic Recloser Setting Updates | Circuit Breaker Fast Curve Hardware | Tree Attachment Remediation | Long Span Initiative | Vertical Switch Replacement | Vibration Damper Retrofits | Fire Resistant Wrap Retrofits | REFCL - GFN (SH-17) | REFCL - Grounding Conversions (SH-18) | High Impedance relays | DOPD | Early Fault Detection (EFD)
Covered Conductor
Undergrounding | 4
Branch Line Protection | 1 | 4
Dist. pole replacements and reinforcements | 1 | 4 [B] | 2
Dist. traditional hardening | N/A [A] | N/A [A] | N/A [A] | N/A [A]
Microgrids | 2 | 2 | 2 | 2 | N/A [A]
Remote Grids [D] | 4 | 4 | 4 | 4 | N/A [A] | 4
Remote Automatic Recloser Setting Updates | 1 | 4 [B] | 1 | 2 | N/A [A] | 2 | 4
Circuit Breaker Fast Curve Hardware | 1 | 4 [B] | 1 | 2 | N/A [A] | 2 | 4 | 1
Tree Attachment Remediation | 1 | 4 | 1 | 4 | N/A [A] | 2 | 4 | 1 | 1
Long Span Initiative | NA [C] | 4 | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 4
Vertical Switch Replacement | 1 | 4 | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 4 | 1
Vibration Damper Retrofits | 1 | 4 | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 4 | 1 | 1
Fire Resistant Wrap Retrofits | 1 | 4 | 1 | 4 | N/A [A] | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 1
REFCL - GFN (SH-17) | 1 | 3 [B] | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
REFCL - Grounding Conversions (SH-18) | 1 | 3 [B] | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4
High Impedance relays | 1 | 4 [B] | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3
DOPD | 1 | 4 [B] | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 1
Early Fault Detection (EFD) | 1 | 3 {B] | 1 | 2 | N/A [A] | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[A] In Section 8.1.2.5 of SCE's 2023-2025 WMP, "traditional overhead hardening" is composed of Branch Line Protection and Long Span. Since both of those programs are already on this list, SCE is indicating "N/A" for these entries as they are redundant.
[B] Assumes that the circuitry downstream is 100% undergrounded
[C] Covered conductor is one of the remediation options for the Long Span Initiatve
[D] Compatibility is based on the overhead line removed by the remote grid and does not account for circuitry encompassed by the remote grid
Legend
1 - Mitigations are compatible and the combination will further reduce wildfire risk
2 - Mitigations are compatible, but the combination will not futher reduce wildfire risk
3 - Mitigations are compatible, but it is unknown if the combination will further reduce wildfire risk
4 - Mitigations are not compatible/combination is impractical

## Q3.a.ii (T)
Mitigation Compatibility Table (Q03.a.ii) T | Transmission Open Phase Detection (TOPD) | Transmission pole/tower replacements and reinforcements | Transmission traditional hardening | Transmission Early Fault Detection (EFD)
Transmission Open Phase Detection (TOPD)
Transmission pole/tower replacements and reinforcements | 2
Transmission traditional hardening | N/A [A] | N/A [A]
Transmission Early Fault Detection (EFD) | 1 | 2
[A] SCE does not have "Transmission Traditional Hardening" as an activity in its 2023-2025 WMP.
Legend
1 - Mitigations are compatible and the combination will further reduce wildfire risk
2 - Mitigations are compatible, but the combination will not futher reduce wildfire risk
3 - Mitigations are compatible, but it is unknown if the combination will further reduce wildfire risk
4 - Mitigations are not compatible/combination is impractical